## August 2026
Job Type | Job | Order No. | Crew | Parish | Order Status | Device | Feeder | Creation Time | Assigned Time | Acknowlege Time | Enroute Time | On-Site Time | Actual Comp. Time | Comp. Time | Final Comp. Time | Hazard List | Tree Contact | Weather Condition | Phase Change | Technician Notes
Non-Outage | J.E.26.07.36669 | C001871418 | Daniel Francis |  | Completed |  |  | 2026-08-01 00:37 | 2026-08-01 08:28 | 2026-08-01 08:50 | 2026-08-01 08:51 | 2026-08-01 09:17 | 2026-08-01 09:28 | 2026-08-01 09:28 | 2026-08-01 09:28 | Fire |  | Fair | No
Non-Outage | J.E.26.07.37711 | C001871417 | Tyrese Williams | St.Ann | Completed | Load_256141 | Cardiff Hall - 310 | 2026-08-01 00:37 | 2026-08-01 08:30 | 2026-08-01 09:08 | 2026-08-01 09:42 | 2026-08-01 09:42 | 2026-08-01 09:42 | 2026-08-01 09:42 | 2026-08-01 09:42 | BrokenPole |  | Fair | No | Premise found ok customer said he didn’t make any report
Outage | J.E.26.08.00015 | C001871420 | Shamour Haughton | St.James | Completed | Load_301836 | Bogue - 310 | 2026-08-01 00:58 | 2026-08-01 00:59 | 2026-08-01 01:04 | 2026-08-01 01:04 | 2026-08-01 01:34 | 2026-08-01 01:34 | 2026-08-01 01:35 | 2026-08-01 01:35 |  |  | Fair | No | Found 1,20amp junction fuse blown, refuse 20amp junction
Outage | J.E.26.07.39913 | C001871425 | Romeo Brissett | St.James | Completed | Load_241873 | Queens Drive - 710 | 2026-08-01 06:48 | 2026-08-01 06:58 | 2026-08-01 07:12 | 2026-08-01 07:20 | 2026-08-01 08:07 | 2026-08-01 08:01 | 2026-08-01 08:09 | 2026-08-01 08:09 | BrokenWire |  | Fair | No | Unable to located directions not clear and phone ring to voicemail.
Outage | J.E.26.07.40153 | C001871427 | Shamour Haughton | St.James | Completed | Load_269302 | Bogue - 610 | 2026-08-01 07:16 | 2026-08-01 07:20 | 2026-08-01 08:32 | 2026-08-01 08:33 | 2026-08-01 08:32 | 2026-08-01 08:32 | 2026-08-01 08:33 | 2026-08-01 08:33 |  |  | Fair | No | Related to previous call
Outage | J.E.26.07.40213 | C001871428 | Shamour Haughton | St.James | Completed | Load_243856 | Bogue - 610 | 2026-08-01 07:17 | 2026-08-01 07:20 | 2026-08-01 08:30 | 2026-08-01 08:30 | 2026-08-01 08:30 | 2026-08-01 08:30 | 2026-08-01 08:30 | 2026-08-01 08:30 |  |  | Fair | No | Related to previous call
Outage | J.E.26.07.40223 | C001871429 | Shamour Haughton | St.James | Completed | Load_255716 | Bogue - 610 | 2026-08-01 07:19 | 2026-08-01 07:20 | 2026-08-01 08:31 | 2026-08-01 08:32 | 2026-08-01 08:31 | 2026-08-01 08:31 | 2026-08-01 08:32 | 2026-08-01 08:32 |  |  | Fair | No | Related to previous call
Outage | J.E.26.07.39815 | C001871431 | Romeo Brissett | St.James | Completed | Load_245538 | Bogue - 510 | 2026-08-01 07:20 | 2026-08-02 07:39 | 2026-08-02 07:57 | 2026-08-02 09:13 | 2026-08-02 09:54 | 2026-08-02 11:00 | 2026-08-02 11:11 | 2026-08-02 11:11 | LeaningPole |  | Fair | No | Isolated (1)25KVA transformer, spliced and retention 1 span of secondary.
Outage | J.E.26.07.39412 | C001871433 | Oshane Warren | Westmoreland | Completed | Load_255148 | Paradise - 210 | 2026-08-01 07:22 | 2026-08-01 07:24 | 2026-08-01 10:43 | 2026-08-01 10:44 | 2026-08-01 11:00 | 2026-08-01 11:00 | 2026-08-01 11:02 | 2026-08-01 11:02 |  |  | Fair | No | Unable to locate or contact customer need direction
Outage | J.E.26.08.00005 | C001871432 | Clyde Brown | Clarendon | Completed | Load_259045 | May Pen - 110 | 2026-08-01 07:22 | 2026-08-01 07:23 | 2026-08-01 08:43 | 2026-08-01 08:43 | 2026-08-01 09:27 | 2026-08-01 10:03 | 2026-08-01 10:23 | 2026-08-01 10:23 |  |  | Fair | No | Blown 15 amps junction fuse at Morgan’s pass,line patrolled and no fault seen,blown fuse replaced
Non-Outage | J.E.26.07.39525 | C001871437 | Jowayne Newmans | Portland | Completed | Load_240419 | Port Antonio - 410 | 2026-08-01 07:28 | 2026-08-01 08:17 | 2026-08-01 08:31 | 2026-08-01 08:31 | 2026-08-01 09:33 | 2026-08-01 09:49 | 2026-08-01 09:50 | 2026-08-01 09:50 |  |  | Fair | No | Customer was experiencing low voltage 118v, 18v cause by corroded connection at secondary conductor, repair by reconnecting service wire to secondary conductor using two one bolt clamps. Voltage reading after repair 118v, 118v, 236v.
Non-Outage | J.E.26.07.40197 | C001871436 | Jowayne Newmans | Portland | Completed | Load_259696 | Port Antonio - 410 | 2026-08-01 07:28 | 2026-08-01 08:17 | 2026-08-01 09:50 | 2026-08-01 09:51 | 2026-08-01 10:28 | 2026-08-01 10:30 | 2026-08-01 10:30 | 2026-08-01 10:30 |  |  | Fair | No | After several attempts to contact customer phone rang without answer also unable to locate customer base on directions.
Non-Outage | J.E.26.07.36422 | C001871439 | Jowayne Newmans | Portland | Completed | Load_349987 | Port Antonio - 410 | 2026-08-01 07:30 | 2026-08-01 08:17 | 2026-08-01 10:58 | 2026-08-01 10:59 | 2026-08-01 11:55 | 2026-08-01 13:38 | 2026-08-01 13:38 | 2026-08-01 13:38 |  |  | Fair | No | Customer was facing low voltage 112v, 99v cause by splicing sleeves on secondary conductor, repair by jumping splicing sleeves using 12 one bolt clamps and 5ft of #2 aluminum conductor. Voltage reading after repair 110v, 112v, 220v.
Non-Outage | J.E.26.07.38336 | C001871438 | Jowayne Newmans | Portland | Completed | Load_247317 | Port Antonio - 410 | 2026-08-01 07:30 | 2026-08-01 08:17 | 2026-08-01 13:39 | 2026-08-01 13:39 | 2026-08-01 13:39 | 2026-08-01 13:41 | 2026-08-01 13:41 | 2026-08-01 13:41 |  |  | Fair | No | Customer stated that low voltage issues has been resolved.
Outage | J.E.26.07.39779 | C001871441 | Andre Williams | Trelawny | Completed | Load_263997 | Duncans - 210 | 2026-08-01 07:35 | 2026-08-01 07:36 | 2026-08-01 08:55 | 2026-08-01 08:55 | 2026-08-01 09:41 | 2026-08-01 09:52 | 2026-08-01 09:52 | 2026-08-01 09:52 | TreeContact |  | Fair | No | Premises with supply customer requesting bushing of line section.
Outage | J.E.26.07.39975 | C001871442 | Andre Williams | Trelawny | Completed | Load_246807 | Duncans - 210 | 2026-08-01 07:35 | 2026-08-01 07:36 | 2026-08-01 09:53 | 2026-08-01 10:00 | 2026-08-01 10:00 | 2026-08-01 10:01 | 2026-08-01 10:01 | 2026-08-01 10:01 |  |  | Fair | No | Premises ok customer reset breaker
Outage | J.E.26.08.00013 | C001871443 | Andre Williams | Trelawny | Completed | Load_292876 | Greenwood - 210 | 2026-08-01 07:35 | 2026-08-01 07:36 | 2026-08-01 07:49 | 2026-08-01 08:54 | 2026-08-01 08:54 | 2026-08-01 08:54 | 2026-08-01 08:55 | 2026-08-01 08:55 |  |  | Fair | No | Completed on previous job
Outage | J.E.26.08.00014 | C001871444 | Andre Williams | Trelawny | Completed | Load_302315 | Greenwood - 210 | 2026-08-01 07:35 | 2026-08-01 07:36 | 2026-08-01 07:49 | 2026-08-01 07:53 | 2026-08-01 08:17 | 2026-08-01 08:36 | 2026-08-01 08:53 | 2026-08-01 08:53 |  |  | Fair | No | Patrol line section reset 10 kva trip type transformer, circuit overload more than 20 customers in lane supply by transformer
Outage | J.E.26.07.40214 | C001871446 | Wayne Dillion | Manchester | Completed | Load_245839 | Spur Tree - 210 | 2026-08-01 07:37 | 2026-08-01 13:02 | 2026-08-01 16:57 | 2026-08-01 16:57 | 2026-08-01 17:11 | 2026-08-01 17:54 | 2026-08-01 17:54 | 2026-08-01 17:54 |  |  | Fair | No | Supply check and found customer single phasing other checks found one side of the meter burn please refer this call to field service for a meter change
Non-Outage | J.E.26.07.37329 | C001871448 | Wayne Dillion |  | Completed |  |  | 2026-08-01 07:38 | 2026-08-01 07:54 | 2026-08-01 10:33 | 2026-08-01 10:34 | 2026-08-01 10:33 | 2026-08-01 10:34 | 2026-08-01 10:34 | 2026-08-01 10:34 |  |  | Fair | No | Customer said supply ok problem has been resolved
Outage | J.E.26.07.38466 | C001871447 | Andrew Powell | St.Elizabeth | Completed | Load_266024 | Maggotty - 210 | 2026-08-01 07:38 | 2026-08-01 07:39 | 2026-08-01 11:17 | 2026-08-01 11:17 | 2026-08-01 11:29 | 2026-08-01 12:00 | 2026-08-01 12:02 | 2026-08-01 12:02 |  |  | Fair | No | No service wire found at location. Replace broken service wire using 90 feet #6 triplex, three clamps and three service sleeves, voltage reading 112v-114v phase to neutral 226v cross phase, meter #2834687.
Outage | J.E.26.07.38691 | C001871449 | Andrew Powell | St.Elizabeth | Completed | Load_266721 | Maggotty - 210 | 2026-08-01 07:38 | 2026-08-01 07:39 | 2026-08-01 09:59 | 2026-08-01 10:00 | 2026-08-01 10:49 | 2026-08-01 11:14 | 2026-08-01 11:16 | 2026-08-01 11:16 |  |  | SevereWind | No | No service wire found at location. Replace broken service wire using 50 feet #6 triplex, two clamps and two service sleeves, voltage leave 113v, meter #3006469.
Non-Outage | J.E.26.07.36890 | C001871452 | Wayne Dillion |  | Completed |  |  | 2026-08-01 07:41 | 2026-08-01 07:54 | 2026-08-01 10:43 | 2026-08-01 10:44 | 2026-08-01 10:44 | 2026-08-01 10:46 | 2026-08-01 10:47 | 2026-08-01 10:47 |  |  | Fair | No
Non-Outage | J.E.26.07.38793 | C001871450 | Wayne Dillion |  | Completed |  |  | 2026-08-01 07:41 | 2026-08-01 11:28 | 2026-08-01 13:34 | 2026-08-01 13:35 | 2026-08-01 13:34 | 2026-08-01 13:40 | 2026-08-01 13:40 | 2026-08-01 13:40 |  |  | Fair | No | Premises not found and customer phone not working
Non-Outage | J.E.26.07.40187 | C001871451 | Wayne Dillion |  | Completed |  |  | 2026-08-01 07:41 | 2026-08-01 07:53 | 2026-08-01 08:32 | 2026-08-01 08:33 | 2026-08-01 09:24 | 2026-08-01 09:50 | 2026-08-01 10:04 | 2026-08-01 10:04 | BrokenWire |  | Fair | No | Reconnect customer service wire that was broke down by a truck using 60 feet of number 6 triplex 3 linket 3 one bolt clamp voltage reading 112v 112v 225 v supply work ok
Outage | J.E.26.07.39341 | C001871457 | Ryan Richards | Manchester | Completed | Load_302040 | Spur Tree - 310 | 2026-08-01 07:44 | 2026-08-01 07:45 | 2026-08-01 13:34 | 2026-08-01 13:35 | 2026-08-01 14:24 | 2026-08-01 15:10 | 2026-08-01 15:10 | 2026-08-01 15:10 |  |  | Fair | No | Burn off phase found at pole remade burn off phase using 2 one bolt clamps voltage 116/115/232 volts
Outage | J.E.26.07.39743 | C001871455 | Ryan Richards | Manchester | Completed | Load_245662 | Kendal - 310 | 2026-08-01 07:44 | 2026-08-01 07:45 | 2026-08-01 11:13 | 2026-08-01 11:14 | 2026-08-01 12:37 | 2026-08-01 13:34 | 2026-08-01 13:34 | 2026-08-01 13:34 |  |  | Fair | No | Broken service wire found cause by broken mango and ackee tree cut trees splice and retention service wires using 40ft#6 triplex 3 penunion 2 one bolt clamps voltage leave with customer 113/112/226 volts
Outage | J.E.26.07.39885 | C001871453 | Ryan Richards | Manchester | Completed | Load_248836 | Spur Tree - 310 | 2026-08-01 07:44 | 2026-08-01 07:45 | 2026-08-01 08:17 | 2026-08-01 10:09 | 2026-08-01 10:09 | 2026-08-01 11:13 | 2026-08-01 11:13 | 2026-08-01 11:13 | Fire |  | Fair | No | 1 span of broken lower secondary phase found and burn transformer phase drop lead found open 25 kva transformer splice and retention broken phase using 10ft#2/0 aluminum 1#2/0 preform 2 one bolt clamps remade drop lead using 1#2/0 ampac and reclose transformer fuse….area was rechecked all customers are now with supply
Non-Outage | J.E.26.07.39775 | C001871458 | Hopeton Henry | St.Thomas | Completed | Load_244777 | Good Year - 110 | 2026-08-01 07:46 | 2026-08-01 07:47 | 2026-08-01 09:02 | 2026-08-01 12:14 | 2026-08-01 13:49 | 2026-08-01 13:50 | 2026-08-01 13:50 | 2026-08-01 13:50 | BrokenWire |  | Fair | No | Change defective service wire
Non-Outage | J.E.26.07.40245 | C001871463 | Romeo Brissett | St.James | Completed | Load_245936 | Queens Drive - 710 | 2026-08-01 07:49 | 2026-08-01 07:51 | 2026-08-01 09:47 | 2026-08-01 09:47 | 2026-08-01 09:47 | 2026-08-01 09:38 | 2026-08-01 09:47 | 2026-08-01 09:47 |  |  | Fair | No | Check and found ok.
Non-Outage | J.E.26.08.00046 | C001871462 | Romeo Brissett | St.James | Completed | Load_245936 | Queens Drive - 710 | 2026-08-01 07:49 | 2026-08-01 07:51 | 2026-08-01 09:48 | 2026-08-01 09:48 | 2026-08-01 09:48 | 2026-08-01 09:47 | 2026-08-01 09:49 | 2026-08-01 09:49 |  |  | Fair | No | Check and found ok
Non-Outage | J.E.26.07.11306 | C001871466 | Romeo Brissett | St.James | Completed | Load_258945 | Queens Drive - 710 | 2026-08-01 07:50 | 2026-08-01 07:51 | 2026-08-01 12:31 | 2026-08-01 12:31 | 2026-08-01 13:09 | 2026-08-01 14:18 | 2026-08-01 14:30 | 2026-08-01 14:30 |  |  | Fair | No | Isolated (1)25KVA transformer, removed illegal connections, repaired secondary jumper. Used 1 clamp V/R 113-114-228.
Non-Outage | J.E.26.07.11453 | C001871465 | Romeo Brissett | St.James | Completed | Load_253032 | Queens Drive - 710 | 2026-08-01 07:50 | 2026-08-01 07:51 | 2026-08-01 14:26 | 2026-08-01 14:31 | 2026-08-01 14:51 | 2026-08-01 02:47 | 2026-08-01 14:52 | 2026-08-01 14:52 |  |  | Fair | No | Premises was checked and found ok
Non-Outage | J.E.26.07.11512 | C001871464 | Romeo Brissett | St.James | Completed | Load_1002045 | Queens Drive - 710 | 2026-08-01 07:50 | 2026-08-01 07:51 | 2026-08-01 11:30 | 2026-08-01 11:31 | 2026-08-01 11:30 | 2026-08-01 00:25 | 2026-08-01 12:30 | 2026-08-01 12:30 |  |  | Fair | No | Isolated (1)25 kva transformer, removed illegal connections, repaired secondary jumper. Used 4ft of #2 and 4 clamps. 114-116-230
Outage | J.E.26.07.39546 | C001871469 | Ricky Hall | St.Catherine | Completed | Load_242473 | New Michelton - 410 | 2026-08-01 07:52 | 2026-08-01 07:53 | 2026-08-01 08:11 | 2026-08-01 12:45 | 2026-08-01 14:28 | 2026-08-01 14:55 | 2026-08-01 14:57 | 2026-08-01 14:57 |  |  | Fair | No | Defective 10 kva xfmr 2nd xfmr from Guys hill end
Outage | J.E.26.07.40240 | C001871468 | Ricky Hall | St.Catherine | Completed | Load_244967 | New Michelton - 410 | 2026-08-01 07:52 | 2026-08-01 07:54 | 2026-08-01 08:12 | 2026-08-01 14:58 | 2026-08-01 14:58 | 2026-08-01 14:58 | 2026-08-01 14:59 | 2026-08-01 14:59 |  |  | Fair | No | Call associated with outage #39546
Non-Outage | J.E.26.08.00050 | C001871470 | Romeo Brissett |  | Completed |  |  | 2026-08-01 07:57 | 2026-08-01 07:58 | 2026-08-01 08:09 | 2026-08-01 08:10 | 2026-08-01 08:20 | 2026-08-01 21:20 | 2026-08-01 09:46 | 2026-08-01 09:46 | BrokenWire |  | Fair | No | Isolated (1)50kva transformer, removed illegal connections, retention 1 span of secondary.
Outage | J.E.26.07.40123 | C001871471 | Wan Carlos Scarlett | Portmore | Completed | Load_239123 | Naggo Head - 510 | 2026-08-01 07:57 | 2026-08-01 07:58 | 2026-08-01 08:11 | 2026-08-01 08:11 | 2026-08-01 09:28 | 2026-08-01 09:30 | 2026-08-01 09:45 | 2026-08-01 09:45 |  |  | Fair | No | Customer state that they are an Adventist and would rather not to do anything at this time at the premises would like a team to visit tomorrow
Outage | J.E.26.07.39690 | C001871472 | Elvis Trowers | KSAN | Completed | Load_258776 | Hope - 510 | 2026-08-01 08:02 | 2026-08-01 08:03 | 2026-08-01 09:00 | 2026-08-01 09:01 | 2026-08-01 10:30 | 2026-08-01 10:39 | 2026-08-01 10:39 | 2026-08-01 10:39 | Fire |  | Fair | Yes | Premises checked and found ok upon arrival, no sparks or fire found, customer would like trees to be cut off her twisted wire, she have regular electricity supply.
Outage | J.E.26.07.39941 | C001871473 | Edward Royal | KSAS | Completed | Load_262317 | Greenwich - 310 | 2026-08-01 08:03 | 2026-08-01 08:03 | 2026-08-01 10:51 | 2026-08-01 14:10 | 2026-08-01 14:09 | 2026-08-01 14:13 | 2026-08-01 14:15 | 2026-08-01 14:15 |  |  | Fair | No | Spliced and reconnected transformer phase drop lead using 4 one bolt clamps and 4 inch 4 north cable on pole # and Debush transformer and secondary line
Outage | J.E.26.08.00028 | C001871474 | Eric Williams | KSAS | Completed | Load_248011 | Duhaney - 310 | 2026-08-01 08:03 | 2026-08-01 08:06 | 2026-08-01 08:44 | 2026-08-01 08:45 | 2026-08-01 09:47 | 2026-08-01 09:48 | 2026-08-01 09:49 | 2026-08-01 09:49 |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.38387 | C001871475 | Moses Elliston | St.Catherine | Completed | Load_257986 | Tredegar - 210 | 2026-08-01 08:07 | 2026-08-01 08:07 | 2026-08-01 10:57 | 2026-08-01 10:58 | 2026-08-01 10:57 | 2026-08-01 11:44 | 2026-08-01 11:46 | 2026-08-01 11:46 |  |  | EarthMovement | No | Broken 3 wire service repaired with 20’ #6 triplex,4 linkets,1 clamp
Outage | J.E.26.07.39945 | C001871476 | Eric Williams | KSAN | Completed | Load_250646 | Constant Spring - 210 | 2026-08-01 08:09 | 2026-08-01 08:10 | 2026-08-01 10:34 | 2026-08-01 10:35 | 2026-08-01 10:58 | 2026-08-01 11:16 | 2026-08-01 11:17 | 2026-08-01 11:17 |  |  | Fair | No | Found customer disconnected, customer was reconnected
Non-Outage | J.E.26.07.39279 | C001871479 | Wan Carlos Scarlett | St.Catherine | Completed | Load_576212 | Twickenham - 210 | 2026-08-01 08:17 | 2026-08-01 08:18 | 2026-08-01 09:52 | 2026-08-01 11:11 | 2026-08-01 11:42 | 2026-08-01 12:10 | 2026-08-01 12:11 | 2026-08-01 12:11 | BrokenWire |  | Fair | No | Found customer 3 wire service at pole with both phase corroded use 2 one bolt clamps at pole readings 116 116 232
Non-Outage | J.E.26.07.39867 | C001871480 | Wan Carlos Scarlett | Portmore | Completed | Load_239377 | Naggo Head - 610 | 2026-08-01 08:17 | 2026-08-01 08:18 | 2026-08-01 16:48 | 2026-08-01 16:49 | 2026-08-01 17:18 | 2026-08-01 17:49 | 2026-08-01 17:50 | 2026-08-01 17:50 |  |  | Fair | No | Customer confirmed no one is at home at this time would reschedule for a next visit when someone is at the premises, premises closed
Non-Outage | J.E.26.07.39837 | C001871481 | Donald Cunningham | St.Catherine | Completed | Load_241890 | Rhodens Pen - 210 | 2026-08-01 08:18 | 2026-08-01 08:20 | 2026-08-01 11:44 | 2026-08-01 11:45 | 2026-08-01 12:51 | 2026-08-01 13:15 | 2026-08-01 13:18 | 2026-08-01 13:18 | BrokenPole |  | Fair | No | No broken pole seen customer not reachable
Non-Outage | J.E.26.07.39386 | C001871482 | Wan Carlos Scarlett | St.Catherine | Completed | Load_293144 | Twickenham - 310 | 2026-08-01 08:19 | 2026-08-01 08:20 | 2026-08-01 09:45 | 2026-08-01 09:46 | 2026-08-01 10:36 | 2026-08-01 11:00 | 2026-08-01 11:10 | 2026-08-01 11:10 | BrokenPole |  | Fair | No | Found 30ft private broken pole advised customer to contact a licensed electrician to fix the issue #2 Triplex service wire is isolated at transformer pole
Non-Outage | J.E.26.06.24787 | C001871483 | Daniel Francis |  | Completed |  |  | 2026-08-01 08:25 | 2026-08-01 08:27 | 2026-08-01 09:29 | 2026-08-01 09:29 | 2026-08-01 10:32 | 2026-08-01 10:42 | 2026-08-01 10:44 | 2026-08-01 10:44 | LeaningPole |  | Fair | No | Found 35/6 pole leaning about 40degree construction DV guy missing single phase primary and neutral
Non-Outage | J.E.26.07.14639 | C001871484 | Daniel Francis | St.Ann | Completed | Load_246878 | Cardiff Hall - 310 | 2026-08-01 08:26 | 2026-08-01 08:27 | 2026-08-02 09:28 | 2026-08-02 09:29 | 2026-08-02 09:28 | 2026-08-02 09:29 | 2026-08-02 09:33 | 2026-08-02 09:33 | LeaningPole |  | Fair | No | Found 35/c6 with primary and secondary 100% decay
Non-Outage | J.E.26.07.34834 | C001871486 | Tyrese Williams | St.Ann | Completed | Load_248442 | Cardiff Hall - 310 | 2026-08-01 08:30 | 2026-08-01 08:32 | 2026-08-01 09:06 | 2026-08-01 09:44 | 2026-08-01 11:57 | 2026-08-01 12:19 | 2026-08-01 12:19 | 2026-08-01 12:19 | BrokenWire |  | Fair | No | Remade service joints at pole use 2 pg clamp
Non-Outage | J.E.26.07.37540 | C001871487 | Tyrese Williams | St.Ann | Completed | Load_247950 | Cardiff Hall - 310 | 2026-08-01 08:30 | 2026-08-01 08:32 | 2026-08-01 08:57 | 2026-08-01 09:04 | 2026-08-01 09:40 | 2026-08-01 09:41 | 2026-08-01 09:41 | 2026-08-01 09:41 | Fire |  | Fair | No | Premises found ok
Non-Outage | J.E.26.07.34103 | C001871489 | Christopher Edwards |  | Completed |  |  | 2026-08-01 08:37 | 2026-08-01 08:38 | 2026-08-01 08:41 | 2026-08-01 09:09 | 2026-08-01 09:20 | 2026-08-01 09:39 | 2026-08-01 09:39 | 2026-08-01 09:39 | LowHangingWires |  | Fair | No | Check and found okLow hanging wire belongs to the cable company
Non-Outage | J.E.26.07.37892 | C001871491 | Roxroy Needham |  | Completed |  |  | 2026-08-01 08:46 | 2026-08-01 08:51 | 2026-08-01 09:03 | 2026-08-01 09:04 | 2026-08-01 09:41 | 2026-08-01 09:41 | 2026-08-01 09:42 | 2026-08-01 09:42 | LeaningPole |  | Fair | No | Premises found ok call customer and customer say that JPS team come yesterday
Non-Outage | J.E.26.07.13977 | C001871493 | Roxroy Needham | St.Mary | Completed | Load_253985 | Oracabessa - 110 | 2026-08-01 08:48 | 2026-08-01 08:51 | 2026-08-01 10:23 | 2026-08-01 10:24 | 2026-08-01 10:23 | 2026-08-01 10:27 | 2026-08-01 10:27 | 2026-08-01 10:27 |  |  | Fair | No
Non-Outage | J.E.26.07.31431 | C001871494 | Roxroy Needham | St.Mary | Completed | Load_242851 | Oracabessa - 110 | 2026-08-01 08:50 | 2026-08-01 08:51 | 2026-08-01 09:42 | 2026-08-01 09:42 | 2026-08-01 10:17 | 2026-08-01 10:18 | 2026-08-01 10:23 | 2026-08-01 10:23 |  |  | Fair | No | Cut tree limb from service wire and clean and remake joint at pole use 1- 1bolt clamp
Non-Outage | J.E.26.08.00040 | C001871496 | Rusean Allen | KSAS | Completed | Load_253177 | Rockfort - 410 | 2026-08-01 09:40 | 2026-08-01 09:41 | 2026-08-01 11:41 | 2026-08-01 11:41 | 2026-08-01 11:51 | 2026-08-01 11:52 | 2026-08-01 11:52 | 2026-08-01 11:52 |  |  | Fair | No | Premises found locked
Non-Outage | J.E.26.07.36969 | C001871500 | Rusean Allen | KSAS | Completed | Load_300847 | Cane River - 410 | 2026-08-01 09:41 | 2026-08-01 09:42 | 2026-08-01 11:52 | 2026-08-01 11:53 | 2026-08-01 12:11 | 2026-08-01 12:13 | 2026-08-01 12:14 | 2026-08-01 12:14 |  |  | Fair | No | Hexing failure, customer having issues with hexing enclosure being full.Refer to field service department.
Non-Outage | J.E.26.07.38911 | C001871499 | Rusean Allen | KSAS | Completed | Load_242913 | Cane River - 410 | 2026-08-01 09:41 | 2026-08-01 09:41 | 2026-08-01 10:45 | 2026-08-01 10:46 | 2026-08-01 11:28 | 2026-08-01 11:36 | 2026-08-01 11:36 | 2026-08-01 11:36 |  |  | Fair | No | Burnt clamps found at pole. Clamps were changed. Voltage: 115 115 230
Non-Outage | J.E.26.07.38988 | C001871498 | Rusean Allen | KSAS | Completed | Load_242913 | Cane River - 410 | 2026-08-01 09:41 | 2026-08-01 09:41 | 2026-08-01 10:46 | 2026-08-01 11:36 | 2026-08-01 11:36 | 2026-08-01 11:39 | 2026-08-01 11:41 | 2026-08-01 11:41 |  |  | Fair | No | Related to 6 Caribbean terrace
Non-Outage | J.E.26.07.39211 | C001871497 | Rusean Allen | KSAS | Completed | Load_242523 | Greenwich - 310 | 2026-08-01 09:41 | 2026-08-01 09:41 | 2026-08-02 09:10 | 2026-08-02 09:11 | 2026-08-02 10:13 | 2026-08-02 10:14 | 2026-08-02 10:14 | 2026-08-02 10:14 |  |  | Fair | No | Premises Not found.
Outage | J.E.26.08.00031 | C001871501 | Wan Carlos Scarlett | Portmore | Completed | Load_243791 | Naggo Head - 510 | 2026-08-01 10:15 | 2026-08-01 10:15 | 2026-08-01 12:12 | 2026-08-01 12:12 | 2026-08-01 12:44 | 2026-08-01 14:23 | 2026-08-01 14:27 | 2026-08-01 14:27 |  |  | Fair | No | Found 4 span of open secondary neutral burn down use 100 ft #2 lume wire 6 one bolt clamps 4 splicing sleeve refuse 25 KVA transformer with 3 amps fuse no pole # was found power supply has been restored
Non-Outage | J.E.26.07.36788 | C001871503 | Tajay Bernard | St.James | Completed | Load_268987 | Orange Bay - 310 | 2026-08-01 10:24 | 2026-08-01 10:26 | 2026-08-01 15:54 | 2026-08-01 17:03 | 2026-08-01 17:25 | 2026-08-01 18:39 | 2026-08-01 18:41 | 2026-08-01 18:41 |  |  | Fair | No | Isolate 1 25kva Transformer to clean and remake transformer drop Leeds and 3 jumpers use at 3 poles.7 clamps was usedVoltage found 104/100/204Voltage left 109/107/216
Non-Outage | J.E.26.08.00038 | C001871502 | Tajay Bernard | St.James | Completed | Load_250447 | Bogue - 510 | 2026-08-01 10:24 | 2026-08-01 10:29 | 2026-08-01 13:57 | 2026-08-01 15:17 | 2026-08-01 15:40 | 2026-08-01 15:44 | 2026-08-01 15:44 | 2026-08-01 15:44 |  |  | Fair | No | Premise found closed
Non-Outage | J.E.26.07.34875 | C001871505 | Tajay Bernard | St.James | Completed | Load_1001405 | Orange Bay - 310 | 2026-08-01 10:25 | 2026-08-01 10:26 | 2026-08-01 10:55 | 2026-08-01 12:56 | 2026-08-01 13:40 | 2026-08-01 13:54 | 2026-08-01 13:54 | 2026-08-01 13:54 |  |  | Fair | No | Premises check and found okay voltage found 114/107/221
Non-Outage | J.E.26.08.00062 | C001871509 | Wan Carlos Scarlett | Portmore | Completed | Load_244905 | Naggo Head - 610 | 2026-08-01 11:13 | 2026-08-01 11:14 | 2026-08-01 13:44 | 2026-08-01 17:51 | 2026-08-01 17:59 | 2026-08-01 18:14 | 2026-08-01 18:33 | 2026-08-01 18:33 | LowHangingWires |  | Fair | No | Found 40 ft wooden pole with three phase main primary line and TD open secondary construction with street light pole #110015. Pole leaning towards road cause by vechile accident causing telecommunication wires to hang extremely low into main road approximately 5ft from ground need Maintenance Department assistance
Non-Outage | J.E.26.08.00066 | C001871510 | Wan Carlos Scarlett | Portmore | Completed | Load_557221 | Naggo Head - 610 | 2026-08-01 11:13 | 2026-08-01 11:14 | 2026-08-01 13:51 | 2026-08-01 15:26 | 2026-08-01 16:15 | 2026-08-01 16:46 | 2026-08-01 16:48 | 2026-08-01 16:48 | Fire |  | Fair | No | Found customer 3 wire service at pole with both phase and neutral corroded use 3 Penn union at pothead reading 115 116 231
Non-Outage | J.E.26.08.00044 | C001871511 | Donald Cunningham | St.Catherine | Completed | Load_259909 | Rhodens Pen - 410 | 2026-08-01 11:17 | 2026-08-01 11:18 | 2026-08-01 13:18 | 2026-08-01 13:19 | 2026-08-01 15:38 | 2026-08-01 16:14 | 2026-08-01 16:15 | 2026-08-01 16:15 |  |  | Fair | No | Corroded phase and neural in meter socket corrected voltage 114/2/228
Outage | J.E.26.07.40044 | C001871512 | Daniel Francis | St.Ann | Completed | Load_318637 | Roaring River - 410 | 2026-08-01 11:35 | 2026-08-01 11:36 | 2026-08-01 11:56 | 2026-08-01 11:56 | 2026-08-01 12:16 | 2026-08-01 13:28 | 2026-08-01 13:33 | 2026-08-01 13:33 |  |  | Fair | No | Replace blown junction fuse at pole. 0036588
Non-Outage | J.E.26.07.38774 | C001871514 | Horace Malcolm | St.James | Completed | Load_264284 | Bogue - 310 | 2026-08-01 11:41 | 2026-08-01 11:42 | 2026-08-01 12:13 | 2026-08-01 14:25 | 2026-08-01 14:38 | 2026-08-01 14:41 | 2026-08-01 14:44 | 2026-08-01 14:44 |  |  | Fair | No | Check and found customer meter burnt referred to field service voltage 114-117-232
Non-Outage | J.E.26.08.00084 | C001871518 | Michael Christian |  | Completed |  |  | 2026-08-01 12:12 | 2026-08-01 12:17 | 2026-08-01 12:27 | 2026-08-01 12:28 | 2026-08-01 13:19 | 2026-08-01 14:38 | 2026-08-01 14:38 | 2026-08-01 14:38 | BrokenWire |  | Fair | No | Found fire and wire open 3 transformer to disconnection and connection wire needed 100 ft # 2 are go C T replace 100 ft # 6 voltage 113 114 227 at meter
Non-Outage | J.E.26.08.00088 | C001871519 | Horace Malcolm |  | Completed |  |  | 2026-08-01 12:21 | 2026-08-01 12:22 | 2026-08-01 12:30 | 2026-08-01 12:30 | 2026-08-01 12:30 | 2026-08-01 12:34 | 2026-08-01 12:34 | 2026-08-01 12:34 |  |  | Fair | No | Check and found one 50kva transformer defective referred to field service
Non-Outage | J.E.26.07.40115 | C001871520 | Horace Malcolm | St.James | Completed | Load_264461 | Bogue - 310 | 2026-08-01 12:32 | 2026-08-01 12:33 | 2026-08-01 12:43 | 2026-08-01 12:44 | 2026-08-01 13:00 | 2026-08-01 14:23 | 2026-08-01 14:23 | 2026-08-01 14:23 |  |  | Fair | No | After checking transformer circuit found customers at the end of circuit have low voltage issue, voltage at end of transformer 104-103-207 voltage in middle of circuit 107-111-218 at the transformer pole voltage 119-119-239 transformer drop lead amp reading (x1)208.0 (x2)25.17 (x3)216.4 suspect circuit needs another transformer
Non-Outage | J.E.26.08.00088 | C001871521 | Horace Malcolm |  | Completed |  |  | 2026-08-01 12:36 | 2026-08-01 12:37 | 2026-08-01 12:40 | 2026-08-01 12:40 | 2026-08-01 12:40 | 2026-08-01 12:42 | 2026-08-01 12:43 | 2026-08-01 12:43 |  |  | Fair | No | Check and found one 50kva transformer defective suspect more than 50 customers affected referred to maintenance
Non-Outage | J.E.26.08.00108 | C001871528 | Marlon Authors |  | Completed |  |  | 2026-08-01 13:50 | 2026-08-02 08:56 | 2026-08-02 09:48 | 2026-08-02 09:49 | 2026-08-02 09:52 | 2026-08-02 09:54 | 2026-08-02 09:54 | 2026-08-02 09:54 |  |  | Fair | No | Customer said supply was restored
Outage | J.E.26.08.00148 | C001871530 | Andrew Powell | Manchester | Completed | Load_244230 | Spur Tree - 210 | 2026-08-01 13:51 | 2026-08-01 13:54 | 2026-08-01 16:16 | 2026-08-01 16:17 | 2026-08-01 18:16 | 2026-08-01 18:49 | 2026-08-01 18:51 | 2026-08-01 18:51 |  |  | Fair | No | Repair defective main breaker inside PMC box, voltage reading 115v-116v phase to neutral 231v cross phase.
Outage | J.E.26.08.00149 | C001871529 | Wayne Dillion | Manchester | Completed | Load_292220 | Spur Tree - 210 | 2026-08-01 13:51 | 2026-08-01 14:53 | 2026-08-01 16:30 | 2026-08-01 16:31 | 2026-08-01 16:30 | 2026-08-01 16:46 | 2026-08-01 16:56 | 2026-08-01 16:56 | Fire |  | Fair | No | Patrol and found clear replace one. 10am junction no pole number supply restore to customer successfully
Outage | J.E.26.08.00238 | C001871531 | Andrew Powell | St.Elizabeth | Completed | Load_255118 | Maggotty - 210 | 2026-08-01 13:51 | 2026-08-01 13:54 | 2026-08-01 15:01 | 2026-08-01 15:01 | 2026-08-01 15:01 | 2026-08-01 15:01 | 2026-08-01 15:02 | 2026-08-01 15:02 |  |  | Fair | No | Premises found okay customer stated that fault resolved supply restored.
Outage | J.E.26.08.00123 | C001871534 | Oshane Warren | Westmoreland | Completed | Load_268242 | Paradise - 110 | 2026-08-01 13:52 | 2026-08-01 13:54 | 2026-08-01 17:36 | 2026-08-01 17:37 | 2026-08-01 17:37 | 2026-08-01 17:37 | 2026-08-01 17:38 | 2026-08-01 17:38 |  |  | Fair | No | Unable to locate or contact customer need direction
Outage | J.E.26.08.00247 | C001871533 | Oshane Warren | Westmoreland | Completed | Load_266193 | Paradise - 210 | 2026-08-01 13:52 | 2026-08-01 13:54 | 2026-08-01 14:45 | 2026-08-01 17:46 | 2026-08-01 17:45 | 2026-08-01 18:31 | 2026-08-01 18:34 | 2026-08-01 18:34 |  |  | Fair | No | Reconnect service wire at pathead and secondary line used 3service connector used 80ft number 6 twisted wire voltage 113 114 228
Outage | J.E.26.08.00249 | C001871532 | Oshane Warren | Westmoreland | Completed | Load_254443 | Paradise - 210 | 2026-08-01 13:52 | 2026-08-01 13:54 | 2026-08-01 15:50 | 2026-08-01 16:09 | 2026-08-01 16:08 | 2026-08-01 16:12 | 2026-08-01 16:12 | 2026-08-01 16:12 | LowHangingWires |  | Rains | No | Internal problem advice to fix
Outage | J.E.26.08.00189 | C001871536 | Oshane Warren | Westmoreland | Completed | Load_261865 | Paradise - 110 | 2026-08-01 13:53 | 2026-08-01 13:54 | 2026-08-01 17:44 | 2026-08-01 17:45 | 2026-08-01 17:45 | 2026-08-01 17:45 | 2026-08-01 17:45 | 2026-08-01 17:45 |  |  | Fair | No | Unable to locate or contact customer need direction
Outage | J.E.26.08.00195 | C001871537 | Ryan Richards | Manchester | Completed | Load_255644 | Porus - 310 | 2026-08-01 13:53 | 2026-08-01 13:55 | 2026-08-01 15:11 | 2026-08-01 15:12 | 2026-08-01 16:37 | 2026-08-01 19:27 | 2026-08-01 19:27 | 2026-08-01 19:27 |  |  | Fair | No | 2 span of broken secondary lower phase and neutral found cause by log wood tree cutt log wood tree splice and retention broken phase and neutral using 50ft#2 aluminum 20ft#2/0 aluminum 1#2/0 preform 4 one bolt clamps and reclose transformer area was rechecked and all customers are now with supply
Outage | J.E.26.08.00240 | C001871538 | Damion Reid | Manchester | Completed | Load_303055 | Kendal - 210 | 2026-08-01 13:54 | 2026-08-01 14:46 | 2026-08-01 14:51 | 2026-08-01 14:51 | 2026-08-01 15:51 | 2026-08-01 16:33 | 2026-08-01 16:33 | 2026-08-01 16:33 |  |  | Fair | No | Area found ok
Outage | J.E.26.08.00179 | C001871540 | Hartley Chin | Clarendon | Completed | Load_237973 | Parnassus - 210 | 2026-08-01 14:03 | 2026-08-01 14:05 | 2026-08-01 15:23 | 2026-08-01 15:23 | 2026-08-01 16:03 | 2026-08-01 16:05 | 2026-08-01 16:08 | 2026-08-01 16:08 | BrokenWire |  | Fair | No | Premisis not found. Unable to contact customer. Area patrolled and found ok.
Outage | J.E.26.08.00183 | C001871543 | Richard Nicholas | St.Catherine | Completed | Load_260421 | Tredegar - 310 | 2026-08-01 14:03 | 2026-08-01 14:05 | 2026-08-01 18:24 | 2026-08-01 18:25 | 2026-08-01 18:24 | 2026-08-01 18:24 | 2026-08-01 18:27 | 2026-08-01 18:27 | BrokenPole |  | Fair | No | Broken 40ft class 6 pole ,broken in the half section of the pole.this is the 4th time I am going on this call and the pole still not change.
Outage | J.E.26.08.00246 | C001871542 | Richard Nicholas | St.Catherine | Completed | Load_245632 | Tredegar - 510 | 2026-08-01 14:03 | 2026-08-01 14:05 | 2026-08-01 14:17 | 2026-08-01 14:18 | 2026-08-01 15:17 | 2026-08-01 16:07 | 2026-08-01 16:09 | 2026-08-01 16:09 |  | Y | Fair | No | 25kva transformer stripped and tested,same found defective.pole #0079079.follow up to replace defective transformer required.
Outage | J.E.26.08.00153 | C001871545 | Wan Carlos Scarlett | Portmore | Completed | Load_264181 | Naggo Head - 610 | 2026-08-01 14:04 | 2026-08-01 14:04 | 2026-08-01 14:29 | 2026-08-01 14:29 | 2026-08-01 14:56 | 2026-08-01 15:23 | 2026-08-01 15:26 | 2026-08-01 15:26 |  |  | Fair | No | Reach on location contact customer they said no one is at the premises now they would reschedule for a next visit when someone is at premises, premises closed
Outage | J.E.26.08.00156 | C001871544 | Wan Carlos Scarlett | Portmore | Completed | Load_265721 | Naggo Head - 610 | 2026-08-01 14:04 | 2026-08-01 14:04 | 2026-08-01 14:10 | 2026-08-01 14:28 | 2026-08-01 14:28 | 2026-08-01 14:28 | 2026-08-01 14:29 | 2026-08-01 14:29 |  |  | Fair | No | Call related to outage earlier power supply has been restored
Outage | J.E.26.08.00192 | C001871546 | Roxroy Needham | St.Mary | Completed | Load_243245 | Oracabessa - 210 | 2026-08-01 14:05 | 2026-08-01 14:15 | 2026-08-01 14:40 | 2026-08-01 14:42 | 2026-08-01 14:42 | 2026-08-01 14:41 | 2026-08-01 14:44 | 2026-08-01 14:44 |  |  | Fair | No | Call customer and customer say that the light is ok
Outage | J.E.26.08.00162 | C001871547 | Cliton Henry | St.Mary | Completed | Load_243069 | Highgate - 210 | 2026-08-01 14:14 | 2026-08-01 14:16 | 2026-08-01 14:29 | 2026-08-01 14:29 | 2026-08-01 15:50 | 2026-08-01 15:54 | 2026-08-01 15:54 | 2026-08-01 15:54 |  |  | Fair | No | A blown 10 amp junction fuse found at Tremolesworth / Mosquito hole rd due tree contact. The branch was removed and szupply restored using 1-10 amp fuse.
Non-Outage | J.E.26.08.00114 | C001871550 | Romeo Brissett |  | Completed |  |  | 2026-08-01 14:15 | 2026-08-02 07:36 | 2026-08-02 08:04 | 2026-08-02 08:04 | 2026-08-02 08:37 | 2026-08-02 09:00 | 2026-08-02 09:13 | 2026-08-02 09:13 |  |  | Fair | No | Removed vegetation and Replaced (1)10KVA transformer fusew
Outage | J.E.26.08.00176 | C001871548 | Tajay Bernard | Hanover | Completed | Load_247675 | Orange Bay - 210 | 2026-08-01 14:15 | 2026-08-01 14:17 | 2026-08-01 20:23 | 2026-08-01 20:23 | 2026-08-01 20:34 | 2026-08-01 20:44 | 2026-08-01 20:44 | 2026-08-01 20:44 |  |  | Fair | No | Area check and found okay unable to locate customer on premises multiple phone calls to customer number went unanswered
Outage | J.E.26.08.00234 | C001871549 | Romeo Brissett | Hanover | Completed | Load_1001416 | Bogue - 510 | 2026-08-01 14:15 | 2026-08-02 07:36 | 2026-08-02 09:13 | 2026-08-02 12:46 | 2026-08-02 13:33 | 2026-08-02 13:10 | 2026-08-02 13:35 | 2026-08-02 13:35 |  |  | Fair | No | Check and found internal fault
Outage | J.E.26.08.00267 | C001871551 | Edward Royal | KSAS | Completed | Load_240764 | Duhaney - 410 | 2026-08-01 14:19 | 2026-08-01 14:20 | 2026-08-01 15:10 | 2026-08-01 15:11 | 2026-08-01 15:10 | 2026-08-01 15:18 | 2026-08-01 15:19 | 2026-08-01 15:19 |  |  | Fair | No | Replaced 30A junction fuse
Outage | J.E.26.08.00136 | C001871552 | Horace Malcolm | St.James | Completed | Load_557026 | Bogue - 310 | 2026-08-01 14:32 | 2026-08-01 14:36 | 2026-08-01 17:31 | 2026-08-01 17:31 | 2026-08-01 18:26 | 2026-08-01 18:33 | 2026-08-01 18:33 | 2026-08-01 18:33 |  |  | Fair | No | Check and found area ok supply restored
Outage | J.E.26.08.00224 | C001871555 | Horace Malcolm | St.James | Completed | Load_259946 | Bogue - 310 | 2026-08-01 14:32 | 2026-08-01 14:34 | 2026-08-01 17:21 | 2026-08-01 17:22 | 2026-08-01 17:21 | 2026-08-01 17:23 | 2026-08-01 17:23 | 2026-08-01 17:23 |  |  | Fair | No | Check and found ok related to previous call job number 00298
Outage | J.E.26.08.00225 | C001871554 | Horace Malcolm | St.James | Completed | Load_261336 | Bogue - 310 | 2026-08-01 14:32 | 2026-08-01 14:34 | 2026-08-01 17:23 | 2026-08-01 17:24 | 2026-08-01 17:23 | 2026-08-01 17:24 | 2026-08-01 17:24 | 2026-08-01 17:24 |  |  | Fair | No | Check and found ok related to previous call job number 00298
Outage | J.E.26.08.00330 | C001871553 | Jowayne Newmans | Portland | Completed | Load_253681 | Port Antonio - 310 | 2026-08-01 14:32 | 2026-08-01 14:34 | 2026-08-01 15:15 | 2026-08-01 15:15 | 2026-08-01 15:25 | 2026-08-01 16:17 | 2026-08-01 16:17 | 2026-08-01 16:17 |  |  | Fair | No | Patrol and found customers single phasing cause by burnt off jumper connection 115v, 0v. Repair by reconnecting jumper using 2 one bolt clamps. Voltage reading after repair 115v, 115v, 230v.
Outage | J.E.26.08.00226 | C001871558 | Horace Malcolm | St.James | Completed | Load_301836 | Bogue - 310 | 2026-08-01 14:33 | 2026-08-01 14:34 | 2026-08-01 16:14 | 2026-08-01 16:14 | 2026-08-01 16:14 | 2026-08-01 16:16 | 2026-08-01 16:16 | 2026-08-01 16:16 | BrokenPole |  | Fair | No | Check and 50kva transformer defective referred to maintenance
Outage | J.E.26.08.00279 | C001871559 | Horace Malcolm | St.James | Completed | Load_254205 | Bogue - 410 | 2026-08-01 14:33 | 2026-08-01 14:34 | 2026-08-01 15:49 | 2026-08-01 15:50 | 2026-08-01 16:11 | 2026-08-01 16:13 | 2026-08-01 16:13 | 2026-08-01 16:13 |  |  | Fair | No | Check and found premises ok supply restored
Outage | J.E.26.08.00298 | C001871557 | Horace Malcolm | St.James | Completed | Load_303208 | Bogue - 310 | 2026-08-01 14:33 | 2026-08-01 14:34 | 2026-08-01 16:17 | 2026-08-01 16:18 | 2026-08-01 16:33 | 2026-08-01 17:21 | 2026-08-01 17:21 | 2026-08-01 17:21 |  |  | Rains | No | Refused one 15amp junction fuse
Outage | J.E.26.08.00336 | C001871556 | Horace Malcolm | St.James | Completed | Load_570299 | Bogue - 310 | 2026-08-01 14:33 | 2026-08-01 14:34 | 2026-08-01 17:29 | 2026-08-01 17:30 | 2026-08-01 17:29 | 2026-08-01 17:30 | 2026-08-01 17:30 | 2026-08-01 17:30 |  |  | Fair | No | Unable to locate customer no directions given multiple calls to customer unavailable
Outage | J.E.26.08.00146 | C001871560 | Romeo Brissett | St.James | Completed | Load_245936 | Queens Drive - 710 | 2026-08-01 14:34 | 2026-08-01 14:35 | 2026-08-01 14:52 | 2026-08-01 14:53 | 2026-08-01 16:06 | 2026-08-01 16:50 | 2026-08-01 16:51 | 2026-08-01 16:51 |  |  | Fair | No | Isolated (1)25 kva transformer repaired transformer lead.
Outage | J.E.26.08.00323 | C001871563 | Tajay Bernard | Hanover | Completed | Load_259699 | Orange Bay - 310 | 2026-08-01 14:39 | 2026-08-01 14:40 | 2026-08-01 14:44 | 2026-08-01 14:45 | 2026-08-01 14:48 | 2026-08-01 14:49 | 2026-08-01 14:50 | 2026-08-01 14:50 |  |  | Fair | No | Reclose 1 30amp trip saver
Outage | J.E.26.08.00347 | C001871565 | Tajay Bernard | Hanover | Completed | Load_254647 | Orange Bay - 310 | 2026-08-01 14:39 | 2026-08-01 14:41 | 2026-08-01 15:56 | 2026-08-01 15:57 | 2026-08-01 15:57 | 2026-08-01 15:57 | 2026-08-01 15:57 | 2026-08-01 15:57 |  |  | Fair | No | This call belongs to st james
Outage | J.E.26.08.00346 | C001871569 | Hartley Chin | Clarendon | Completed | Load_253290 | Parnassus - 310 | 2026-08-01 14:43 | 2026-08-01 14:44 | 2026-08-01 16:08 | 2026-08-01 16:09 | 2026-08-01 16:13 | 2026-08-01 16:43 | 2026-08-01 16:59 | 2026-08-01 16:59 |  |  | Fair | No | Prem not found … unable to contact customer with… area patrolled and found okay …
Outage | J.E.26.08.00354 | C001871570 | Jowayne Newmans | Portland | Completed | Load_255997 | Port Antonio - 410 | 2026-08-01 14:45 | 2026-08-01 14:47 | 2026-08-01 16:56 | 2026-08-01 16:57 | 2026-08-01 17:26 | 2026-08-01 17:37 | 2026-08-01 17:37 | 2026-08-01 17:37 |  |  | Fair | No | Premises found with supply Meter socket voltage reading 120v 119v 239v
Outage | J.E.26.08.00165 | C001871571 | Tyrese Williams | St.Ann | Completed | Load_266317 | Cardiff Hall - 310 | 2026-08-01 14:51 | 2026-08-01 14:53 | 2026-08-01 15:01 | 2026-08-01 16:28 | 2026-08-01 17:04 | 2026-08-01 17:07 | 2026-08-01 17:07 | 2026-08-01 17:07 |  |  | Fair | No | Replace a 10amp junction fuse at pole
Outage | J.E.26.08.00349 | C001871572 | Tyrese Williams | St.Ann | Completed | Load_244116 | Cardiff Hall - 310 | 2026-08-01 14:51 | 2026-08-01 14:53 | 2026-08-01 15:01 | 2026-08-01 15:04 | 2026-08-01 16:23 | 2026-08-01 16:27 | 2026-08-01 16:27 | 2026-08-01 16:27 |  |  | Rains | No | Replace a 15 amp junction fuse at pole
Outage | J.E.26.08.00356 | C001871573 | Andrew Powell | St.Elizabeth | Completed | Load_261064 | Maggotty - 210 | 2026-08-01 14:55 | 2026-08-01 14:56 | 2026-08-01 15:04 | 2026-08-01 15:05 | 2026-08-01 15:22 | 2026-08-01 16:14 | 2026-08-01 16:16 | 2026-08-01 16:16 | BrokenPole |  | Fair | No | Retention one pole span of sagging secondary top phase conductor using one preform. Remade burnt off phase jumper joint using two clamps, restore supply okay.
Outage | J.E.26.08.00339 | C001871579 | Richard Nicholas | St.Catherine | Completed | Load_238161 | Tredegar - 510 | 2026-08-01 15:00 | 2026-08-01 15:02 | 2026-08-01 16:09 | 2026-08-01 16:10 | 2026-08-01 16:34 | 2026-08-01 17:05 | 2026-08-01 17:06 | 2026-08-01 17:06 |  |  | Fair | No | Replaced blown 10amp junctions fuse near to pole #0033614.
Outage | J.E.26.08.00169 | C001871581 | Omar King | St.Ann | Completed | Load_319432 | Roaring River - 410 | 2026-08-01 15:05 | 2026-08-01 15:07 | 2026-08-01 15:37 | 2026-08-01 15:38 | 2026-08-01 15:51 | 2026-08-01 15:51 | 2026-08-01 15:52 | 2026-08-01 15:52 |  |  | Fair | No | Problem as been resolved
Outage | J.E.26.08.00266 | C001871580 | Omar King | St.Ann | Completed | Load_251050 | Upper White River - 110 | 2026-08-01 15:05 | 2026-08-01 15:07 | 2026-08-01 15:33 | 2026-08-01 15:34 | 2026-08-01 15:36 | 2026-08-01 15:36 | 2026-08-01 15:36 | 2026-08-01 15:36 |  |  | Fair | No | Problem as been resolved
Outage | J.E.26.08.00369 | C001871584 | Javid Vernon | Westmoreland | Completed | Load_245455 | Paradise - 310 | 2026-08-01 15:05 | 2026-08-01 15:14 | 2026-08-01 15:54 | 2026-08-01 16:14 | 2026-08-01 16:13 | 2026-08-01 16:13 | 2026-08-01 16:16 | 2026-08-01 16:16 |  |  | Fair | No | Unable to locate customer and premises phone calls to customer number went unanswered no directions was given to find customer premises
Outage | J.E.26.08.00376 | C001871582 | Tyrese Williams | St.Ann | Completed | Load_242582 | Cardiff Hall - 310 | 2026-08-01 15:05 | 2026-08-01 15:13 | 2026-08-01 16:04 | 2026-08-01 17:07 | 2026-08-01 17:08 | 2026-08-01 17:08 | 2026-08-01 17:08 | 2026-08-01 17:08 | Fire |  | Fair | No | Premises found ok call related to the 10 amp junction fuse that was replaced
Outage | J.E.26.08.00365 | C001871585 | Cliton Henry | St.Mary | Completed | Load_238782 | Highgate -110 | 2026-08-01 15:06 | 2026-08-01 15:07 | 2026-08-01 15:54 | 2026-08-01 15:55 | 2026-08-01 17:47 | 2026-08-01 17:47 | 2026-08-01 17:53 | 2026-08-01 17:53 |  |  | Fair | No | A blown 10 amp junction fuse found at Jobs Hill pole 0010645 and a blown 2 amp fuse found for a 10 kva transformer at pole #614753 due to vines found on arrester lead. The vine was removed. Supply restored using 1-15 amp fuse at pole #0010645 and 1-2 amp fuse at the 10 kva transformer pole #614753.
Outage | J.E.26.08.00370 | C001871586 | Christopher Edwards | KSAN | Completed | Load_239302 | Constant Spring - 210 | 2026-08-01 15:12 | 2026-08-01 15:59 | 2026-08-01 16:02 | 2026-08-01 17:06 | 2026-08-01 17:06 | 2026-08-01 17:57 | 2026-08-01 17:57 | 2026-08-01 17:57 | BrokenWire |  | Fair | No | Splice and retention broken open secondary lineUsing :50ft #2 AA conductor (1) #2 preform 2 onebolt clamps Refuse blown 25 kva transformer pUsing (1) 2 amps
Outage | J.E.26.08.00141 | C001871587 | Javid Vernon | Westmoreland | Completed | Load_246606 | Paradise - 310 | 2026-08-01 15:13 | 2026-08-01 15:15 | 2026-08-01 15:54 | 2026-08-01 15:55 | 2026-08-01 15:54 | 2026-08-01 15:56 | 2026-08-01 15:57 | 2026-08-01 15:57 |  |  | Fair | No | This call belongs to st James
Outage | J.E.26.07.38835 | C001871588 | Tajay Bernard | Westmoreland | Completed | Load_249479 | Paradise - 310 | 2026-08-01 15:14 | 2026-08-01 15:15 | 2026-08-01 20:10 | 2026-08-01 20:44 | 2026-08-01 21:14 | 2026-08-01 21:31 | 2026-08-01 21:31 | 2026-08-01 21:31 |  |  | Fair | No | Customer has internal problems customer was advised
Outage | J.E.26.07.38747 | C001871589 | Tajay Bernard | Westmoreland | Completed | Load_266710 | Paradise - 310 | 2026-08-01 15:15 | 2026-08-01 15:16 | 2026-08-01 15:55 | 2026-08-01 15:55 | 2026-08-01 15:55 | 2026-08-01 15:55 | 2026-08-01 15:56 | 2026-08-01 15:56 | LeaningPole |  | Fair | No | Customer stated that the issue has been resolved
Outage | J.E.26.08.00401 | C001871591 | Tajay Bernard | Hanover | Completed | Load_253641 | Orange Bay - 210 | 2026-08-01 15:24 | 2026-08-01 15:25 | 2026-08-01 16:11 | 2026-08-01 18:42 | 2026-08-01 18:41 | 2026-08-01 20:06 | 2026-08-01 20:09 | 2026-08-01 20:09 |  |  | Fair | No | Remove vegetation and refuse a 8amp junction and a 25kva transformer use 3amp fuse
Non-Outage | J.E.26.08.00411 | C001871592 | Wayne Dillion |  | Completed |  |  | 2026-08-01 15:25 | 2026-08-01 15:27 | 2026-08-01 21:59 | 2026-08-01 22:00 | 2026-08-01 21:59 | 2026-08-01 22:00 | 2026-08-01 22:01 | 2026-08-01 22:01 |  |  | Fair | No | Customer was disconnected call customer care to reconnect customer
Outage | J.E.26.08.00239 | C001871593 | Andrew Powell | St.Elizabeth | Completed | Load_266721 | Maggotty - 210 | 2026-08-01 15:26 | 2026-08-01 19:42 | 2026-08-01 20:00 | 2026-08-01 20:03 | 2026-08-01 20:56 | 2026-08-01 21:34 | 2026-08-01 21:35 | 2026-08-01 21:35 |  |  | Fair | No | Remade corroded service wire joints at meter pothead 3 wire using three service sleeves, voltage reading 113v-113v phase to neutral 226v cross phase.
Outage | J.E.26.08.00185 | C001871596 | Omar King | St.Ann | Completed | Load_267166 | Roaring River - 210 | 2026-08-01 15:40 | 2026-08-01 15:43 | 2026-08-01 18:53 | 2026-08-01 18:53 | 2026-08-01 19:00 | 2026-08-01 19:17 | 2026-08-01 19:18 | 2026-08-01 19:18 |  |  | Fair | No | Found a 25 KVA transformer fuse blow cause by bird fuse as been replaced area is now with supply
Outage | J.E.26.08.00186 | C001871595 | Omar King | St.Ann | Completed | Load_262552 | Roaring River - 210 | 2026-08-01 15:40 | 2026-08-01 15:43 | 2026-08-01 16:52 | 2026-08-01 16:53 | 2026-08-01 18:51 | 2026-08-01 18:52 | 2026-08-01 18:53 | 2026-08-01 18:53 |  |  | Fair | No | Premises as been checked and problem as been found internal voltage reading at meter socket 115-114-229 Volts
Outage | J.E.26.08.00331 | C001871601 | Andre Smith | KSAS | Completed | Load_261859 | Hunts Bay - 210 | 2026-08-01 15:42 | 2026-08-01 15:47 | 2026-08-01 17:24 | 2026-08-01 22:45 | 2026-08-01 22:44 | 2026-08-01 22:45 | 2026-08-01 22:45 | 2026-08-01 22:45 |  |  | Fair | No | Premises found okay supply restored already
Outage | J.E.26.08.00337 | C001871600 | Andre Smith | KSAS | Completed | Load_253830 | Greenwich - 710 | 2026-08-01 15:42 | 2026-08-01 15:47 | 2026-08-01 17:24 | 2026-08-01 18:46 | 2026-08-01 19:02 | 2026-08-01 19:22 | 2026-08-01 19:23 | 2026-08-01 19:23 |  |  | Fair | No | Premises found okay internal problems customer advised
Outage | J.E.26.08.00406 | C001871599 | Andre Smith | KSAS | Completed | Load_251983 | Greenwich - 710 | 2026-08-01 15:42 | 2026-08-01 15:47 | 2026-08-01 17:00 | 2026-08-01 17:21 | 2026-08-01 17:36 | 2026-08-01 18:44 | 2026-08-01 18:44 | 2026-08-01 18:44 |  |  | Fair | No | Repair burnt service wire neutral supply restored 118V
Outage | J.E.26.08.00408 | C001871598 | Andre Smith | KSAS | Completed | Load_573768 | Three Miles - 510 | 2026-08-01 15:42 | 2026-08-01 15:47 | 2026-08-01 16:04 | 2026-08-01 16:04 | 2026-08-01 17:00 | 2026-08-01 17:00 | 2026-08-01 17:00 | 2026-08-01 17:00 |  |  | Fair | No | Replace blown transformer fuse 3A supply restored
Outage | J.E.26.08.00129 | C001871604 | Andre Smith | KSAS | Completed | Load_259291 | Washington Blvd - 310 | 2026-08-01 15:43 | 2026-08-01 15:47 | 2026-08-01 17:24 | 2026-08-01 19:23 | 2026-08-01 20:24 | 2026-08-01 20:58 | 2026-08-01 20:58 | 2026-08-01 20:58 |  |  | Fair | No | Reconnection done in ypp box supply restored
Outage | J.E.26.08.00416 | C001871602 | Damion Reid | Manchester | Completed | Load_246293 | Kendal - 210 | 2026-08-01 15:43 | 2026-08-01 15:44 | 2026-08-01 16:34 | 2026-08-01 16:35 | 2026-08-01 18:25 | 2026-08-01 18:50 | 2026-08-01 18:52 | 2026-08-01 18:52 |  |  | Fair | No | Two 30amp trip saver found down cause by lightning line patrol and reset trip saver
Outage | J.E.26.08.00418 | C001871605 | Wan Carlos Scarlett | Portmore | Completed | Load_268723 | Naggo Head - 510 | 2026-08-01 15:49 | 2026-08-01 15:52 | 2026-08-01 18:52 | 2026-08-01 20:10 | 2026-08-01 20:29 | 2026-08-01 21:16 | 2026-08-01 21:18 | 2026-08-01 21:18 |  |  | Fair | No | Found multiple customers getting supply from Hex box #04220 several customers experiencing single phasing need field service assistance call referred to Moses
Outage | J.E.26.08.00417 | C001871606 | Jowayne Newmans | Portland | Completed | Load_259052 | Port Antonio - 310 | 2026-08-01 15:51 | 2026-08-01 15:54 | 2026-08-01 17:37 | 2026-08-01 17:37 | 2026-08-01 18:29 | 2026-08-01 18:29 | 2026-08-01 19:07 | 2026-08-01 19:07 |  |  | Fair | No | Isolate 25KVA transformer to change corroded clamp that connects transformer drop lead .voltage reading before 105v 117v 222v After 118v 117v 235v
Outage | J.E.26.08.00359 | C001871607 | Neville Spencer | Clarendon | Completed | Load_262821 | May Pen - 110 | 2026-08-01 15:52 | 2026-08-01 15:54 | 2026-08-01 16:20 | 2026-08-01 16:20 | 2026-08-01 17:58 | 2026-08-01 19:56 | 2026-08-01 19:59 | 2026-08-01 19:59 |  |  | Fair | No | Splice and retention defective 3, wire service used 50 ft #6 triplex, 2 clamps reset trip 25 kva xmfr at pole # 056340 area restored.
Outage | J.E.26.08.00292 | C001871664 | Antony Levy | KSAS | Completed | Load_240304 | Up Park Camp - 310 | 2026-08-01 15:58 | 2026-08-01 16:00 | 2026-08-01 18:03 | 2026-08-01 18:03 | 2026-08-01 18:15 | 2026-08-01 18:59 | 2026-08-01 19:01 | 2026-08-01 19:01 |  |  | Fair | No | Cox stated no power ...line patrolled... burnt transformer switch bottom clamp found ... switch bottom clamp replaced and transformer reconnected
Non-Outage | J.E.26.08.00458 | C001871666 | Antony Levy |  | Completed |  |  | 2026-08-01 15:59 | 2026-08-01 16:00 | 2026-08-01 16:08 | 2026-08-01 16:09 | 2026-08-01 17:38 | 2026-08-01 18:02 | 2026-08-01 18:02 | 2026-08-01 18:02 | Fire |  | Fair | No | Cx stated no power... line patrolled 2 blown 15 amp fuses found and replaced... power restored
Outage | J.E.26.08.00438 | C001871689 | Javid Vernon | Westmoreland | Completed | Load_245897 | Paradise - 310 | 2026-08-01 16:12 | 2026-08-01 16:30 | 2026-08-01 17:10 | 2026-08-01 17:11 | 2026-08-01 18:18 | 2026-08-01 18:52 | 2026-08-01 18:52 | 2026-08-01 18:52 |  |  | Rains | No | Refuse one 20amp junction fuse
Outage | J.E.26.08.00471 | C001871691 | Wayne Dillion | St.Elizabeth | Completed | Load_269464 | Maggotty - 110 | 2026-08-01 16:16 | 2026-08-01 16:21 | 2026-08-01 17:57 | 2026-08-01 17:57 | 2026-08-01 18:39 | 2026-08-01 19:05 | 2026-08-01 19:04 | 2026-08-01 19:04 |  |  | Fair | No | Patrol and found clear replace two 30 amp junction fuse no pole number supply restore to area successfully
Outage | J.E.26.08.00474 | C001871692 | Andrew Powell | Manchester | Completed | Load_302601 | Spur Tree - 210 | 2026-08-01 16:17 | 2026-08-01 16:21 | 2026-08-01 18:51 | 2026-08-01 18:52 | 2026-08-01 18:51 | 2026-08-01 18:52 | 2026-08-01 18:52 | 2026-08-01 18:52 |  |  | Fair | No | Premises found okay customer stated that supply restored.
Non-Outage | J.E.26.08.00116 | C001871694 | Ricky Hall |  | Completed |  |  | 2026-08-01 16:18 | 2026-08-01 16:19 | 2026-08-01 16:27 | 2026-08-01 16:28 | 2026-08-01 17:58 | 2026-08-01 18:01 | 2026-08-01 18:07 | 2026-08-01 18:07 |  |  | Fair | No | No spark seen on arrival
Outage | J.E.26.08.00544 | C001871693 | Andrew Powell | Manchester | Completed | Load_1002349 | Spur Tree - 210 | 2026-08-01 16:18 | 2026-08-01 16:21 | 2026-08-01 18:54 | 2026-08-01 18:55 | 2026-08-01 18:55 | 2026-08-01 18:55 | 2026-08-01 18:55 | 2026-08-01 18:55 |  |  | Fair | No | Manchester called.
Outage | J.E.26.08.00585 | C001871696 | Andrew Powell | Manchester | Completed | Load_251627 | Spur Tree - 210 | 2026-08-01 16:20 | 2026-08-01 16:22 | 2026-08-01 18:56 | 2026-08-01 18:56 | 2026-08-01 18:56 | 2026-08-01 18:56 | 2026-08-01 18:56 | 2026-08-01 18:56 |  |  | Fair | No | Premises found okay customer stated that supply restored.
Non-Outage | J.E.26.08.00582 | C001871697 | Barnett Brown |  | Completed |  |  | 2026-08-01 16:25 | 2026-08-02 11:24 | 2026-08-02 13:50 | 2026-08-02 13:51 | 2026-08-02 14:37 | 2026-08-02 14:37 | 2026-08-02 15:22 | 2026-08-02 15:22 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.00469 | C001871698 | Ryan Richards | Manchester | Completed | Load_238981 | Spur Tree - 310 | 2026-08-01 16:25 | 2026-08-01 16:27 | 2026-08-01 19:28 | 2026-08-01 19:28 | 2026-08-01 21:30 | 2026-08-01 22:04 | 2026-08-01 22:04 | 2026-08-01 22:04 |  |  | Fair | No | Premises found ok customer having problems with prepaid meter field service crew required to carry out repair
Outage | J.E.26.08.00465 | C001871700 | Horace Malcolm | St.James | Completed | Load_257366 | Queens Drive - 710 | 2026-08-01 16:27 | 2026-08-01 18:30 | 2026-08-01 18:39 | 2026-08-01 18:39 | 2026-08-01 19:32 | 2026-08-01 21:05 | 2026-08-01 21:05 | 2026-08-01 21:05 | Fire |  | Fair | No | Repair #6 service wire supplying 3customers used 20ft #6 triplex wire 2clamps voltage 114-116-230 found about 250ft #6 triplex wire defective that supply around 8customers
Non-Outage | J.E.26.07.38377 | C001871704 | Horace Malcolm | St.James | Completed | Load_239852 | Queens Drive - 310 | 2026-08-01 16:28 | 2026-08-01 18:30 | 2026-08-01 23:02 | 2026-08-01 23:02 | 2026-08-01 23:02 | 2026-08-01 23:03 | 2026-08-01 23:03 | 2026-08-01 23:03 |  |  | Fair | No | Crew shift end
Non-Outage | J.E.26.07.38565 | C001871705 | Horace Malcolm | St.James | Completed | Load_238066 | Queens Drive - 710 | 2026-08-01 16:28 | 2026-08-01 18:30 | 2026-08-01 21:14 | 2026-08-01 21:15 | 2026-08-01 22:01 | 2026-08-01 22:09 | 2026-08-01 22:09 | 2026-08-01 22:09 |  |  | Fair | No | Unable to locate customer or premises multiple calls to customer unavailable
Non-Outage | J.E.26.07.38848 | C001871703 | Horace Malcolm | St.James | Completed | Load_302647 | Bogue - 410 | 2026-08-01 16:28 | 2026-08-01 18:30 | 2026-08-01 23:03 | 2026-08-01 23:04 | 2026-08-01 23:03 | 2026-08-01 23:04 | 2026-08-01 23:04 | 2026-08-01 23:04 |  |  | Fair | No | Crew shift ended
Non-Outage | J.E.26.08.00058 | C001871702 | Romeo Brissett | St.James | Completed | Load_245936 | Queens Drive - 710 | 2026-08-01 16:28 | 2026-08-01 16:29 | 2026-08-01 16:53 | 2026-08-01 16:54 | 2026-08-01 17:25 | 2026-08-01 18:18 | 2026-08-01 18:26 | 2026-08-01 18:26 |  |  | Fair | No | Repaired secondary neutral.
Non-Outage | J.E.26.07.37958 | C001871709 | Oshane Warren |  | Completed |  |  | 2026-08-01 16:31 | 2026-08-01 19:03 | 2026-08-01 21:22 | 2026-08-01 21:23 | 2026-08-01 21:22 | 2026-08-01 21:22 | 2026-08-01 21:23 | 2026-08-01 21:23 |  |  | Rains | No | St Elizabeth call
Non-Outage | J.E.26.08.00603 | C001871713 | Christopher Edwards |  | Completed |  |  | 2026-08-01 16:52 | 2026-08-01 16:57 | 2026-08-01 20:23 | 2026-08-01 20:37 | 2026-08-01 20:37 | 2026-08-01 20:37 | 2026-08-01 20:37 | 2026-08-01 20:37 | Fire |  | Fair | No | Related to previous call that was resolved
Outage | J.E.26.08.00615 | C001871712 | Donald Cunningham | St.Catherine | Completed | Load_259647 | Rhodens Pen - 410 | 2026-08-01 16:52 | 2026-08-01 17:50 | 2026-08-01 18:52 | 2026-08-01 18:53 | 2026-08-01 19:03 | 2026-08-01 19:34 | 2026-08-01 19:34 | 2026-08-01 19:34 |  |  | Fair | No | Area found ok with supply
Outage | J.E.26.08.00625 | C001871714 | Kaydon Taylor | KSAN | Completed | Load_244867 | Constant Spring - 410 | 2026-08-01 16:54 | 2026-08-01 16:55 | 2026-08-01 17:04 | 2026-08-01 17:06 | 2026-08-01 17:32 | 2026-08-01 18:13 | 2026-08-01 18:13 | 2026-08-01 18:13 |  |  | Fair | No | Defective switch at 12 norbrook terr 25kva transformer pole #0037099
Outage | J.E.26.08.00634 | C001871716 | Richard Nicholas | St.Catherine | Completed | Load_257738 | Tredegar - 210 | 2026-08-01 17:00 | 2026-08-01 17:02 | 2026-08-01 22:12 | 2026-08-01 22:12 | 2026-08-01 22:30 | 2026-08-01 22:30 | 2026-08-01 22:32 | 2026-08-01 22:32 | BrokenWire |  | Fair | No | Call is related to a broken 40ft pole in heartland however road and entrance to private premises make safe and a section of the community restored,and a section left without supply due to the broken pole.
Non-Outage | J.E.26.08.00665 | C001871718 | Javid Vernon |  | Completed |  |  | 2026-08-01 17:16 | 2026-08-01 17:52 | 2026-08-01 18:53 | 2026-08-01 18:53 | 2026-08-01 18:53 | 2026-08-01 18:54 | 2026-08-01 18:54 | 2026-08-01 18:54 | Fire |  | Fair | No | Related to previous call job #00438
Outage | J.E.26.08.00652 | C001871717 | Tyrese Williams | St.Ann | Completed | Load_262356 | Cardiff Hall - 210 | 2026-08-01 17:16 | 2026-08-01 17:18 | 2026-08-01 17:23 | 2026-08-01 17:23 | 2026-08-01 18:43 | 2026-08-01 18:57 | 2026-08-01 18:58 | 2026-08-01 18:58 | LeaningPole |  | Fair | No | Found a 30ft class 4, single primary open secondary wooden pole leaning
Outage | J.E.26.08.00639 | C001871719 | Wayne Dillion | St.Elizabeth | Completed | Load_253484 | Maggotty - 110 | 2026-08-01 17:17 | 2026-08-01 18:42 | 2026-08-01 20:16 | 2026-08-01 20:17 | 2026-08-01 20:16 | 2026-08-01 20:40 | 2026-08-01 20:59 | 2026-08-01 20:59 |  |  | Fair | No | Patrol and found clear replace one 30 amp junction fuse no pole number supply restore to area successfully
Outage | J.E.26.08.00674 | C001871720 | Andrew Powell | Manchester | Completed | Load_556203 | Spur Tree - 210 | 2026-08-01 17:20 | 2026-08-01 17:23 | 2026-08-01 18:57 | 2026-08-01 18:58 | 2026-08-01 19:27 | 2026-08-01 19:34 | 2026-08-01 19:35 | 2026-08-01 19:35 |  |  | Fair | No | Premises found okay supply at location.
Non-Outage | J.E.26.08.00659 | C001871722 | Swon Miller |  | Completed |  |  | 2026-08-01 17:21 | 2026-08-01 17:23 | 2026-08-01 17:29 | 2026-08-01 17:59 | 2026-08-01 18:51 | 2026-09-01 19:26 | 2026-08-01 19:26 | 2026-08-01 19:26 |  |  | Fair | No | Found 50 amp junction fuse blown cause by lightning replace 50 amp junction fuse no pole number available
Outage | J.E.26.08.00472 | C001871721 | Swon Miller | St.James | Completed | Load_572116 | Bogue - 510 | 2026-08-01 17:21 | 2026-08-01 17:23 | 2026-08-01 17:29 | 2026-08-01 19:27 | 2026-08-01 20:24 | 2026-08-19 08:37 | 2026-08-01 20:40 | 2026-08-01 20:40 |  |  | Fair | No | Check and found area okay customer states that they didn’t make any report.
Outage | J.E.26.08.00656 | C001871724 | Wan Carlos Scarlett | St.Catherine | Completed | Load_1000347 | Twickenham - 210 | 2026-08-01 17:23 | 2026-08-01 18:13 | 2026-08-01 21:48 | 2026-08-01 21:48 | 2026-08-01 23:29 | 2026-08-01 23:32 | 2026-08-01 23:34 | 2026-08-01 23:34 | Fire |  | Fair | No | Area unsafe to be working at this time area is volitile need daylight attention
Outage | J.E.26.08.00646 | C001871727 | Hartley Chin | Clarendon | Completed | Load_253290 | Parnassus - 310 | 2026-08-01 17:34 | 2026-08-01 17:35 | 2026-08-01 19:17 | 2026-08-01 19:34 | 2026-08-01 20:51 | 2026-08-01 21:06 | 2026-08-01 21:08 | 2026-08-01 21:08 |  |  | Fair | No | Unable to contact customer.. area patrolled was able to find meter .. voltage read 114v , 112v ..
Outage | J.E.26.08.00677 | C001871728 | Omar King | St.Ann | Completed | Load_264221 | Ocho Rios - 310 | 2026-08-01 17:36 | 2026-08-01 17:38 | 2026-08-01 19:18 | 2026-08-01 19:18 | 2026-08-01 20:31 | 2026-08-01 20:53 | 2026-08-01 20:54 | 2026-08-01 20:54 |  |  | Fair | No | Found a 10 amp junction fuse blow as been replaced area is now with supply
Non-Outage | J.E.26.08.00690 | C001871730 | Antony Levy | KSAN | Completed | Load_246169 | Hope - 410 | 2026-08-01 17:39 | 2026-08-01 17:48 | 2026-08-01 19:01 | 2026-08-01 19:02 | 2026-08-01 19:20 | 2026-08-01 20:20 | 2026-08-01 20:25 | 2026-08-01 20:25 |  |  | Fair | No | Cx stated only has one leg of power... readings took at pole and pot head found to be okay 118 118 239 ...... cx meter checked and is okay...fault found to be cx meter socket .... cx told to refer to electrician
Non-Outage | J.E.26.08.00343 | C001871733 | Marlon Brown |  | Completed |  |  | 2026-08-01 17:40 | 2026-08-01 17:41 | 2026-08-01 18:20 | 2026-08-01 18:21 | 2026-08-01 18:20 | 2026-08-01 18:21 | 2026-08-01 18:21 | 2026-08-01 18:21 |  |  | Fair | No | Manchester call
Outage | J.E.26.08.00117 | C001871734 | Marlon Brown | Trelawny | Completed | Load_302315 | Greenwood - 210 | 2026-08-01 17:40 | 2026-08-01 18:30 | 2026-08-01 19:56 | 2026-08-01 19:57 | 2026-08-01 20:40 | 2026-08-01 20:41 | 2026-08-01 20:41 | 2026-08-01 20:41 |  |  | Fair | No | Customer says her electricity has been restored.
Outage | J.E.26.08.00256 | C001871732 | Marlon Brown | Trelawny | Completed | Load_259170 | Duncans - 210 | 2026-08-01 17:40 | 2026-08-01 17:41 | 2026-08-01 18:27 | 2026-08-01 18:27 | 2026-08-01 19:08 | 2026-08-01 19:53 | 2026-08-01 19:53 | 2026-08-01 19:53 |  |  | Fair | No | Isolated 50kva transformer to repair burnt out joint at drop lead, use 2 pg clamps to effect repairs Voltage found at pothead 117/70=190vVoltage leaving at pothead pothead 117/118=235v
Outage | J.E.26.08.00637 | C001871731 | Marlon Brown | Trelawny | Completed | Load_259170 | Duncans - 210 | 2026-08-01 17:40 | 2026-08-01 17:41 | 2026-08-01 19:54 | 2026-08-01 19:54 | 2026-08-01 19:54 | 2026-08-01 19:55 | 2026-08-01 19:55 | 2026-08-01 19:55 |  |  | Fair | No | Same as call number 256.
Outage | J.E.26.08.00614 | C001871735 | Donald Cunningham | St.Catherine | Completed | Load_262747 | Rhodens Pen - 410 | 2026-08-01 17:46 | 2026-08-01 17:48 | 2026-08-01 19:34 | 2026-08-01 19:35 | 2026-08-01 19:46 | 2026-08-01 19:47 | 2026-08-01 19:59 | 2026-08-01 19:59 |  |  | Fair | No | Area found ok with supply
Outage | J.E.26.08.00687 | C001871736 | Oshane Warren | Westmoreland | Completed | Load_569997 | Paradise - 210 | 2026-08-01 17:51 | 2026-08-01 17:52 | 2026-08-01 18:50 | 2026-08-01 18:51 | 2026-08-01 19:21 | 2026-08-01 19:24 | 2026-08-01 19:24 | 2026-08-01 19:24 |  |  | Rains | No | Replace 3amp 25kva xformer fuse
Outage | J.E.26.08.00712 | C001871737 | Christopher Edwards | KSAN | Completed | Load_239691 | Constant Spring - 410 | 2026-08-01 17:53 | 2026-08-01 17:54 | 2026-08-01 17:58 | 2026-08-01 18:00 | 2026-08-01 19:30 | 2026-08-01 20:24 | 2026-08-01 20:37 | 2026-08-01 20:37 |  |  | Fair | No | Clear fallen bamboo off open secondary wiresRefuse blown 25 kva transformer Using (1) 2 amps
Non-Outage | J.E.26.08.00621 | C001871738 | Oshane Warren | Westmoreland | Completed | Load_292188 | Paradise - 210 | 2026-08-01 17:57 | 2026-08-01 18:02 | 2026-08-01 19:25 | 2026-08-01 19:26 | 2026-08-01 21:03 | 2026-08-01 21:20 | 2026-08-01 21:21 | 2026-08-01 21:21 |  |  | Rains | No | Reconnect back burnt off service wire at secondary line voltage 117 121 239
Non-Outage | J.E.26.07.39064 | C001871740 | Hartley Chin | Clarendon | Completed | Load_301251 | Monymusk - 410 | 2026-08-01 17:58 | 2026-08-01 17:59 | 2026-08-01 18:10 | 2026-08-01 18:11 | 2026-08-01 19:05 | 2026-08-01 19:11 | 2026-08-01 19:16 | 2026-08-01 19:16 |  |  | Fair | No | Requires Daylight Attention!!! Line patrolled and found okay to a point but unable to do detail patrol due to area being Forrest like with overgrown trees and bushes … unsafe to conduct proper patrol @ this hour 7:15 PM … requires daylight attention!!
Non-Outage | J.E.26.08.00060 | C001871741 | Christopher Edwards | KSAN | Completed | Load_249914 | Constant Spring - 410 | 2026-08-01 18:01 | 2026-08-01 18:02 | 2026-08-01 20:37 | 2026-08-01 20:38 | 2026-08-01 21:12 | 2026-08-01 21:59 | 2026-08-01 22:00 | 2026-08-01 22:00 |  |  | Fair | No | Remake corroded phase joint at poleUsing (1) one bolt eVoltage:115,114,230v
Non-Outage | J.E.26.08.00728 | C001871743 | Oshane Warren | Westmoreland | Completed | Load_258299 | Paradise - 210 | 2026-08-01 18:16 | 2026-08-01 19:03 | 2026-08-01 21:21 | 2026-08-01 21:22 | 2026-08-01 21:21 | 2026-08-01 21:21 | 2026-08-01 21:22 | 2026-08-01 21:22 |  |  | Rains | No | Check and find ok
Outage | J.E.26.08.00722 | C001871744 | Damion Reid | Manchester | Completed | Load_258689 | Kendal - 210 | 2026-08-01 18:34 | 2026-08-01 18:44 | 2026-08-01 18:52 | 2026-08-01 18:52 | 2026-08-01 19:21 | 2026-08-01 20:25 | 2026-08-01 20:27 | 2026-08-01 20:27 |  |  | Fair | No | Blown 30amp junction fuse found cause by lightning line patrol and replace blown fuse
Non-Outage | J.E.26.08.00746 | C001871747 | Tyrese Williams |  | Completed |  |  | 2026-08-01 18:43 | 2026-08-01 18:45 | 2026-08-01 20:14 | 2026-08-01 22:21 | 2026-08-01 22:23 | 2026-08-01 22:29 | 2026-08-01 22:29 | 2026-08-01 22:29 |  |  | Fair | No | Found a defective 25kva transformer at pole
Outage | J.E.26.08.00752 | C001871746 | Kenroy Dale | Manchester | Completed | Load_237923 | Porus - 310 | 2026-08-01 18:43 | 2026-08-02 08:07 | 2026-08-02 08:59 | 2026-08-02 09:08 | 2026-08-02 10:00 | 2026-08-02 10:23 | 2026-08-02 10:26 | 2026-08-02 10:26 |  |  | Fair | No | Blown 1 amp transformer fuse found for 5 kva transformer and 10 amp junction fuse also found line patrol tree branch found on primary conductor, tree branch was removed and blown fuse replaced area now with supply
Outage | J.E.26.08.00741 | C001871748 | Richard Nicholas | St.Catherine | Completed | Load_268985 | Tredegar - 210 | 2026-08-01 18:49 | 2026-08-01 18:53 | 2026-08-01 22:33 | 2026-08-01 22:44 | 2026-08-01 23:10 | 2026-08-01 23:11 | 2026-08-01 23:15 | 2026-08-01 23:15 |  |  | Fair | No | A 750kva pad mounted transformer left isolated after project manager Mr.parchment told the crew that a lot of smoke was coming from the transformer and also make humming sound.at the time when the crew arrived at the location Mr.parchment was on his cell phone talking to the relevant department that is in charge of the transformer.transformer left isolated.
Non-Outage | J.E.26.08.00737 | C001871751 | Tajay Bernard |  | Completed |  |  | 2026-08-01 18:57 | 2026-08-01 18:58 | 2026-08-01 21:32 | 2026-08-01 21:33 | 2026-08-01 22:22 | 2026-08-01 22:34 | 2026-08-01 22:35 | 2026-08-01 22:35 | Fire |  | Fair | No | Refuse 1 8amp junction fuse
Outage | J.E.26.08.00706 | C001871750 | Tajay Bernard | Hanover | Completed | Load_256375 | Orange Bay - 310 | 2026-08-01 18:57 | 2026-08-01 18:58 | 2026-08-01 22:35 | 2026-08-01 22:36 | 2026-08-01 22:35 | 2026-08-01 22:36 | 2026-08-01 22:37 | 2026-08-01 22:37 |  |  | Fair | No | Related to previous call job number 00737
Outage | J.E.26.08.00743 | C001871753 | Horace Malcolm | St.James | Completed | Load_252519 | Queens Drive - 710 | 2026-08-01 19:03 | 2026-08-01 19:04 | 2026-08-01 22:09 | 2026-08-01 22:10 | 2026-08-01 22:49 | 2026-08-01 22:53 | 2026-08-01 22:53 | 2026-08-01 22:53 |  |  | Fair | No | Change customer defective service wire used 90 ft #6/triplex wire and 3clamps voltage 116-116-232
Outage | J.E.26.08.00769 | C001871756 | Jowayne Newmans | Portland | Completed | Load_256965 | Port Antonio - 310 | 2026-08-01 19:11 | 2026-08-01 19:12 | 2026-08-01 20:44 | 2026-08-01 20:45 | 2026-08-01 21:01 | 2026-08-01 21:11 | 2026-08-01 21:12 | 2026-08-01 21:12 | Fire |  | Fair | No | Customer pothead corroded on load load side Advice customer to get electrician
Non-Outage | J.E.26.07.40228 | C001871757 | Roxroy Needham | St.Mary | Completed | Load_243989 | Blackstonedge - 110 | 2026-08-01 19:21 | 2026-08-01 19:21 | 2026-08-01 19:55 | 2026-08-01 19:56 | 2026-08-01 20:45 | 2026-08-01 20:46 | 2026-08-01 20:46 | 2026-08-01 20:46 |  |  | Fair | No | Not getting customer on phone
Outage | J.E.26.08.00779 | C001871759 | Tyrese Williams | St.Ann | Completed | Load_263852 | Cardiff Hall - 310 | 2026-08-01 19:35 | 2026-08-01 19:35 | 2026-08-01 20:14 | 2026-08-01 20:14 | 2026-08-01 21:27 | 2026-08-01 22:20 | 2026-08-01 22:20 | 2026-08-01 22:20 |  |  | Fair | No | Found a 25 kva transformer defective no pole number seen
Outage | J.E.26.08.00625 | C001871760 | Kaydon Taylor | KSAN | Completed | Load_244867 | Constant Spring - 410 | 2026-08-01 19:43 | 2026-08-01 19:44 | 2026-08-01 19:56 | 2026-08-01 19:57 | 2026-08-01 20:21 | 2026-08-01 22:25 | 2026-08-01 22:26 | 2026-08-01 22:26 | Fire |  | Fair | No | Change defective switch and disconnect defective lighting arrester. 8 amp fuse found blown and replace
Outage | J.E.26.08.00795 | C001871763 | Andre Smith | KSAS | Completed | Load_268312 | Duhaney - 410 | 2026-08-01 19:50 | 2026-08-01 19:54 | 2026-08-01 21:55 | 2026-08-01 21:55 | 2026-08-01 22:12 | 2026-08-01 22:13 | 2026-08-01 22:13 | 2026-08-01 22:13 |  |  | Fair | No | Replace blown junction fuse cause by defective lightening arrester supply restored
Outage | J.E.26.08.00796 | C001871762 | Andre Smith | KSAS | Completed | Load_240053 | Duhaney - 410 | 2026-08-01 19:50 | 2026-08-01 19:54 | 2026-08-01 21:11 | 2026-08-01 21:12 | 2026-08-01 21:34 | 2026-08-01 21:52 | 2026-08-01 21:54 | 2026-08-01 21:54 |  |  | Fair | No | Replace blown junction fuse cause by defective lightening arrester supply restored
Outage | J.E.26.08.00800 | C001871764 | Andre Smith | KSAS | Completed | Load_248351 | Duhaney - 410 | 2026-08-01 19:52 | 2026-08-01 19:54 | 2026-08-01 22:13 | 2026-08-01 22:13 | 2026-08-01 22:36 | 2026-08-01 22:36 | 2026-08-01 22:36 | 2026-08-01 22:36 |  |  | Fair | No | Premises found okay supply restored
Outage | J.E.26.08.00833 | C001871766 | Andrew Powell | St.Elizabeth | Completed | Load_1002242 | Maggotty - 210 | 2026-08-01 20:11 | 2026-08-01 20:12 | 2026-08-01 21:36 | 2026-08-01 21:37 | 2026-08-01 22:04 | 2026-08-01 22:11 | 2026-08-01 22:13 | 2026-08-01 22:13 | Fire |  | Fair | No | Found contamination on transformer primary bushing due to dust and moisture.
Non-Outage | J.E.26.08.00611 | C001871767 | Damion Reid | Manchester | Completed | Load_237809 | Kendal - 210 | 2026-08-01 20:26 | 2026-08-01 20:28 | 2026-08-01 20:49 | 2026-08-01 20:49 | 2026-08-01 22:10 | 2026-08-01 22:58 | 2026-08-01 23:01 | 2026-08-01 23:01 |  |  | Fair | No | Remade corroded service phase at secondary pole for 3 wire service using one 1 bolt clamp voltage reading at meter socket phase to neutral 112v-114v across phase 228v
Outage | J.E.26.08.00845 | C001871768 | Kenroy Dale | Manchester | Completed | Load_254054 | Kendal - 210 | 2026-08-01 20:35 | 2026-08-02 08:09 | 2026-08-02 14:38 | 2026-08-02 14:39 | 2026-08-02 15:30 | 2026-08-09 16:10 | 2026-08-02 16:11 | 2026-08-02 16:11 |  |  | Fair | No | Defective service wire found, conductor was splice and retention customer now with supply voltage 116/116/232
Outage | J.E.26.08.00647 | C001871771 | Hopeton Henry | St.Thomas | Completed | Load_269106 | Good Year - 210 | 2026-08-01 21:05 | 2026-08-01 21:06 | 2026-08-01 21:11 | 2026-08-01 21:12 | 2026-08-01 21:55 | 2026-08-01 01:00 | 2026-08-01 22:36 | 2026-08-01 22:36 |  |  | Fair | No | Found disconnected, Reconnected by jps escalations
Outage | J.E.26.08.00859 | C001871773 | Wan Carlos Scarlett | St.Catherine | Completed | Load_252020 | Twickenham - 210 | 2026-08-01 21:13 | 2026-08-01 21:18 | 2026-08-01 23:34 | 2026-08-01 23:34 | 2026-08-01 23:34 | 2026-08-01 23:34 | 2026-08-01 23:35 | 2026-08-01 23:35 | BrokenWire |  | Fair | No | Area unsafe to be working at this time area is volitile need daylight attention
Outage | J.E.26.08.00870 | C001871775 | Oshane Warren | Westmoreland | Completed | Load_257740 | Paradise - 310 | 2026-08-01 21:25 | 2026-08-02 07:07 | 2026-08-02 08:47 | 2026-08-02 08:48 | 2026-08-02 10:57 | 2026-08-02 01:00 | 2026-08-02 11:01 | 2026-08-02 11:01 |  |  | Fair | No | Replace 3amp 25kva xformer fuse
Outage | J.E.26.08.00860 | C001871776 | Clyde Brown | Clarendon | Completed | Load_254405 | Parnassus - 210 | 2026-08-01 21:28 | 2026-08-02 07:42 | 2026-08-02 08:26 | 2026-08-02 12:36 | 2026-08-02 12:35 | 2026-08-02 12:35 | 2026-08-02 12:40 | 2026-08-02 12:40 |  |  | Fair | No | Manchester call
Outage | J.E.26.08.00352 | C001871780 | Derrick Dawkins | St.James | Completed | Load_243806 | Bogue - 310 | 2026-08-01 21:43 | 2026-08-01 22:59 | 2026-08-01 23:11 | 2026-08-01 23:12 | 2026-08-01 23:21 | 2026-08-01 23:38 | 2026-08-01 23:46 | 2026-08-01 23:46 |  |  | Fair | No | Found 10kva transformer fuse blown replace 1.5amp fuse no pole number available
Outage | J.E.26.08.00874 | C001871782 | Tyrese Williams | St.Ann | Completed | Load_246928 | Cardiff Hall - 310 | 2026-08-01 22:12 | 2026-08-01 22:13 | 2026-08-01 22:29 | 2026-08-01 22:31 | 2026-08-01 22:31 | 2026-08-01 22:31 | 2026-08-01 22:32 | 2026-08-01 22:32 |  |  | Fair | No | Premises not four not getting customer on phone
Outage | J.E.26.08.00903 | C001871788 | Elvis Trowers | KSAN | Completed | Load_249195 | Hope - 510 | 2026-08-01 23:44 | 2026-08-02 09:30 | 2026-08-02 11:22 | 2026-08-02 11:23 | 2026-08-02 13:05 | 2026-08-02 15:54 | 2026-08-02 15:54 | 2026-08-02 15:54 | BrokenWire | Y | Fair | Yes | Areas found without electricity supply when checked and 2 blown fuses were found at separate locations, 1/10 amp junction fuse at pole #039719 and a 3 amp transformer fuse at pole #0110412.after tree contact was removed.
Outage | J.E.26.08.00931 | C001871790 | Delano Gayle | Portmore | Completed | Load_266997 | Naggo Head - 510 | 2026-08-02 00:05 | 2026-08-02 00:06 | 2026-08-02 00:28 | 2026-08-02 00:28 | 2026-08-02 02:56 | 2026-08-02 03:07 | 2026-08-02 03:08 | 2026-08-02 03:08 | Fire |  | Rains | No | Lightening arrester on 50kva transformer arcing on n off occasionally, need new lightening arrester
Outage | J.E.26.08.00656 | C001871792 | Rodclif Dawkins | St.Catherine | Completed | Load_1000347 | Twickenham - 210 | 2026-08-02 00:06 | 2026-08-02 10:30 | 2026-08-02 11:14 | 2026-08-02 11:15 | 2026-08-02 11:26 | 2026-08-02 14:12 | 2026-08-02 14:20 | 2026-08-02 14:20 | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Found blown junction fuse for single phase T-off. Patrolled line section and found blown fuse for 2 (100kva) transformers. No fault found on primary. Found and replaced 30amp for junction. On secondary circuit crew found burnt 4/0 triplex. Crew returned to base to get 2/0 triplex. Using 20ft of 2/0 triplex and 12-1bolt clamp used to bring out repairs. 8amp was found replaced. Area okay
Outage | J.E.26.08.00976 | C001871798 | Rusean Allen | KSAS | Completed | Load_238206 | Cane River - 410 | 2026-08-02 01:19 | 2026-08-02 01:20 | 2026-08-02 01:31 | 2026-08-02 01:32 | 2026-08-02 03:49 | 2026-08-02 03:51 | 2026-08-02 03:51 | 2026-08-02 03:51 |  |  | Fair | No | Maintenance department doing repairs
Outage | J.E.26.08.01198 | C001871801 | Delano Gayle | Portmore | Completed | Load_253042 | Naggo Head - 510 | 2026-08-02 02:26 | 2026-08-02 02:27 | 2026-08-02 04:29 | 2026-08-02 04:29 | 2026-08-02 04:30 | 2026-08-02 04:31 | 2026-08-02 04:31 | 2026-08-02 04:31 |  |  | Rains | No | Premises found okay related to call where 25amps junction fuse was replaced
Outage | J.E.26.08.01199 | C001871802 | Delano Gayle | Portmore | Completed | Load_240584 | Naggo Head - 510 | 2026-08-02 02:26 | 2026-08-02 02:28 | 2026-08-02 03:09 | 2026-08-02 03:09 | 2026-08-02 04:07 | 2026-08-02 04:29 | 2026-08-02 04:29 | 2026-08-02 04:29 | Fire |  | Rains | No | Blown 25amps junction no pole number, blown 100 kva transformer fuse no pole number, replace 25amps at junction and 7amps at transformer
Outage | J.E.26.08.01444 | C001871808 | Wan Carlos Scarlett | St.Catherine | Completed | Load_238362 | Duhaney - 210 | 2026-08-02 04:37 | 2026-08-02 07:22 | 2026-08-02 07:36 | 2026-08-02 07:37 | 2026-08-02 09:00 | 2026-08-02 10:38 | 2026-08-02 10:41 | 2026-08-02 10:41 |  |  | Fair | No | Refuse 65 Amp junction pole #601572 also refuse 25 Amps junction pole #080414 nothing was found on the primary line cause by lightning strike
Outage | J.E.26.08.01472 | C001871807 | Wan Carlos Scarlett | St.Catherine | Completed | Load_244601 | Duhaney - 210 | 2026-08-02 04:37 | 2026-08-02 07:31 | 2026-08-02 09:42 | 2026-08-02 10:42 | 2026-08-02 10:52 | 2026-08-02 10:52 | 2026-08-02 10:53 | 2026-08-02 10:53 |  |  | Fair | No | Refuse 20 Amps junction no pole # was found nothing was found on the primary line cause by lightning strike
Outage | J.E.26.08.01661 | C001871809 | Rusean Allen | KSAN | Completed | Load_254115 | West Kings House - 410 | 2026-08-02 04:52 | 2026-08-02 04:53 | 2026-08-02 05:01 | 2026-08-02 05:01 | 2026-08-02 05:01 | 2026-08-02 05:03 | 2026-08-02 05:04 | 2026-08-02 05:04 |  |  | Fair | No | Burnt crossarm found, 3phase primary line was de energized, fire was distinguish. Crossarm needs to be changed refer to maintenance department.
Non-Outage | J.E.26.08.00913 | C001871810 | Oshane Warren | Westmoreland | Completed | Load_240901 | Paradise - 310 | 2026-08-02 07:09 | 2026-08-02 07:10 | 2026-08-02 11:02 | 2026-08-02 11:02 | 2026-08-02 11:02 | 2026-08-02 11:02 | 2026-08-02 11:03 | 2026-08-02 11:03 |  |  | Fair | No | Replace 3amp 25kva xformer fuse
Outage | J.E.26.08.00884 | C001871811 | Romeo Brissett | Hanover | Completed | Load_262588 | Orange Bay - 210 | 2026-08-02 07:12 | 2026-08-02 07:13 | 2026-08-02 07:21 | 2026-08-02 07:23 | 2026-08-02 07:23 | 2026-08-02 07:22 | 2026-08-02 07:27 | 2026-08-02 07:27 |  |  | Fair | No | Unable to locate directions unclear, foreign number
Non-Outage | J.E.26.07.39064 | C001871812 | Neville Spencer | Clarendon | Completed | Load_301251 | Monymusk - 410 | 2026-08-02 07:18 | 2026-08-02 07:20 | 2026-08-02 08:39 | 2026-08-02 08:39 | 2026-08-02 09:37 | 2026-08-02 09:37 | 2026-08-02 12:52 | 2026-08-02 12:52 |  |  | Fair | No | Patrolled 12 kv line S & G and JPS crew noting found. Suspect from under ground cables, to pad mount xmfr there is ah problem voltage read at pad mount xmfr 34 251 251 239 390 430 . REF TO S M D .
Outage | J.E.26.08.01710 | C001871813 | Collin Robinson | Portland | Completed | Load_252323 | Port Antonio - 410 | 2026-08-02 07:19 | 2026-08-02 07:42 | 2026-08-02 07:55 | 2026-08-02 07:55 | 2026-08-02 09:11 | 2026-08-02 09:38 | 2026-08-02 09:38 | 2026-08-02 09:38 |  |  | Rains | No | Cut and clear tree branches from primary conductor and replace 10 amps junction fuse
Outage | J.E.26.08.01937 | C001871814 | Collin Robinson | Portland | Completed | Load_250580 | Port Antonio - 410 | 2026-08-02 07:19 | 2026-08-02 07:42 | 2026-08-02 09:38 | 2026-08-02 09:39 | 2026-08-02 09:51 | 2026-08-02 10:30 | 2026-08-02 10:30 | 2026-08-02 10:30 |  |  | Fair | No | Patrol and 20 amp trip saver open cause by bamboo limb resting on primary conductor across a cross country line section. Unable to remove bamboo limb resting on primary conductor because area is not accessible to do so. Refer call to maintenance for extension bushing to be done.
Outage | J.E.26.08.01947 | C001871815 | Collin Robinson | Portland | Completed | Load_577214 | Port Antonio - 310 | 2026-08-02 07:19 | 2026-08-02 07:42 | 2026-08-02 10:31 | 2026-08-02 10:31 | 2026-08-02 13:08 | 2026-08-02 13:42 | 2026-08-02 13:42 | 2026-08-02 13:42 |  |  | Rains | No | Patrol and found 20 amp trip saver open cause by tree branch touching primary conductor, repair by bushing one pole span of primary conductor and close 20 amp trip saver.
Outage | J.E.26.08.00812 | C001871817 | Floyd Taylor | Trelawny | Completed | Load_264646 | Duncans - 210 | 2026-08-02 07:21 | 2026-08-02 07:22 | 2026-08-02 12:24 |  | 2026-08-02 13:16 | 2026-08-02 13:23 | 2026-08-02 13:24 | 2026-08-02 13:24 |  |  | Fair | No | Found ok, customer said they got back light
Outage | J.E.26.08.00863 | C001871818 | Floyd Taylor | Trelawny | Completed | Load_292409 | Greenwood - 210 | 2026-08-02 07:21 | 2026-08-02 07:22 | 2026-08-02 09:36 | 2026-08-02 09:36 | 2026-08-02 10:49 | 2026-08-02 01:00 | 2026-08-02 10:52 | 2026-08-02 10:52 |  |  | Fair | No | isolate 50kva transformer, clean and remake transformer drop lead using 3pg clamps, voltage reading left 119,121,237
Outage | J.E.26.08.00930 | C001871816 | Floyd Taylor | Trelawny | Completed | Load_292876 | Greenwood - 210 | 2026-08-02 07:21 | 2026-08-02 07:22 | 2026-08-02 10:59 | 2026-08-02 11:00 | 2026-08-02 11:56 | 2026-08-02 12:23 | 2026-08-02 12:24 | 2026-08-02 12:24 |  |  | Fair | No | Customer found with light Checked joints at pole and pot head, voltage left 109,110,218
Outage | J.E.26.08.01245 | C001871820 | Wan Carlos Scarlett | Portmore | Completed | Load_265935 | Naggo Head - 510 | 2026-08-02 07:21 | 2026-08-02 07:23 | 2026-08-02 11:48 | 2026-08-02 13:13 | 2026-08-02 13:47 | 2026-08-02 14:20 | 2026-08-02 14:21 | 2026-08-02 14:21 |  |  | Fair | No | Call related to outage earlier customer confirmed that power supply has been restored
Outage | J.E.26.08.01614 | C001871819 | Floyd Taylor | Trelawny | Completed | Load_302315 | Greenwood - 210 | 2026-08-02 07:21 | 2026-08-02 07:23 | 2026-08-02 07:51 | 2026-08-02 07:51 | 2026-08-02 08:28 | 2026-08-02 09:18 | 2026-08-02 09:32 | 2026-08-02 09:32 |  |  | Fair | No | 10kva transformer tripped, it was reset voltage reading 109,107,216
Outage | J.E.26.08.01600 | C001871822 | Wan Carlos Scarlett | Portmore | Completed | Load_258914 | Duhaney - 210 | 2026-08-02 07:22 | 2026-08-02 07:23 | 2026-08-02 10:24 | 2026-08-02 11:47 | 2026-08-02 11:46 | 2026-08-02 11:46 | 2026-08-02 11:47 | 2026-08-02 11:47 |  |  | Fair | No | Call related to outage earlier customer confirmed that power supply has been restored check and found okay
Outage | J.E.26.08.01916 | C001871823 | Wan Carlos Scarlett | Portmore | Completed | Load_267573 | Twickenham - 210 | 2026-08-02 07:22 | 2026-08-02 07:23 | 2026-08-02 10:26 | 2026-08-02 10:55 | 2026-08-02 11:06 | 2026-08-02 11:45 | 2026-08-02 11:46 | 2026-08-02 11:46 |  |  | Fair | No | Refuse 40 Amps junction no pole # was found nothing was found on primary line cause by lightning strike
Outage | J.E.26.08.00857 | C001871830 | Stephen Taylor | St.Thomas | Completed | Load_254105 | Lysson - 410 | 2026-08-02 07:25 | 2026-08-02 07:27 | 2026-08-02 07:57 | 2026-08-02 07:58 | 2026-08-02 09:06 | 2026-08-02 09:06 | 2026-08-02 09:08 | 2026-08-02 09:08 | BrokenWire |  | Rains | No | Patrol area and power is in the area but several calls to single customer and no one answering the phone
Outage | J.E.26.08.01003 | C001871829 | Stephen Taylor | St.Thomas | Completed | Load_267304 | Lysson - 410 | 2026-08-02 07:25 | 2026-08-02 07:27 | 2026-08-02 09:08 | 2026-08-02 09:09 | 2026-08-02 10:15 | 2026-08-02 10:15 | 2026-08-02 10:36 | 2026-08-02 10:36 |  |  | Rains | No | Chlip saver 15 amp patrol clear bush off line with switch stick and close up back 15 amp chip saver safely all customer is now okay
Outage | J.E.26.08.01018 | C001871828 | Stephen Taylor | St.Thomas | Completed | Load_257367 | Lysson - 410 | 2026-08-02 07:25 | 2026-08-02 07:27 | 2026-08-02 11:46 | 2026-08-02 11:47 | 2026-08-02 13:37 | 2026-08-02 13:37 | 2026-08-02 13:38 | 2026-08-02 13:38 |  |  | Rains | No | Clean up single phase line 3 clamps Rdg 113—112–226
Outage | J.E.26.08.01764 | C001871831 | Roxroy Needham | St.Mary | Completed | Load_350137 | Oracabessa - 210 | 2026-08-02 07:25 | 2026-08-02 10:14 | 2026-08-02 10:27 | 2026-08-02 10:27 | 2026-08-02 12:12 | 2026-08-02 12:22 | 2026-08-02 12:23 | 2026-08-02 12:23 |  |  | Fair | No | Replace a 25 KVA transformer fuse with a 3 amps at pole
Outage | J.E.26.08.01974 | C001871827 | Stephen Taylor | St.Thomas | Completed | Load_241570 | Lysson - 410 | 2026-08-02 07:25 | 2026-08-02 07:27 | 2026-08-02 15:50 | 2026-08-02 15:50 | 2026-08-02 16:56 | 2026-08-02 16:56 | 2026-08-02 17:45 | 2026-08-02 17:45 |  |  | Fair | No | Patrol clear line and close up 25 kva transformer safely customer is now okay
Outage | J.E.26.08.01990 | C001871825 | Raymond Carr | St.Mary | Completed | Load_251918 | Oracabessa - 210 | 2026-08-02 07:25 | 2026-08-02 07:26 | 2026-08-02 08:00 | 2026-08-02 08:01 | 2026-08-02 09:11 | 2026-08-02 09:30 | 2026-08-02 09:34 | 2026-08-02 09:34 | Fire |  | Fair | No | Blown 15kva transformer fuse found at pole number 040506, line patrol and and cleared a span of banged secondary conductors. A 2 amp fuse was used to renew supply was restored.
Outage | J.E.26.08.00967 | C001871834 | Hopeton Henry | St.Thomas | Completed | Load_266155 | Good Year - 210 | 2026-08-02 07:27 | 2026-08-02 07:28 | 2026-08-02 07:39 | 2026-08-02 07:43 | 2026-08-02 08:18 | 2026-08-02 10:13 | 2026-08-02 10:14 | 2026-08-02 10:14 |  |  | Rains | No | Refuse 20 amp junction
Outage | J.E.26.08.00982 | C001871835 | Hopeton Henry | St.Thomas | Completed | Load_252054 | Good Year - 210 | 2026-08-02 07:27 | 2026-08-02 07:28 | 2026-08-02 07:39 | 2026-08-02 10:18 | 2026-08-02 10:17 | 2026-08-02 10:17 | 2026-08-02 10:18 | 2026-08-02 10:18 |  |  | Rains | No | Refuse 7 amp junction
Outage | J.E.26.08.01000 | C001871833 | Hopeton Henry | St.Thomas | Completed | Load_266440 | Good Year - 210 | 2026-08-02 07:27 | 2026-08-02 07:28 | 2026-08-02 07:39 | 2026-08-02 10:19 | 2026-08-02 10:18 | 2026-08-02 10:18 | 2026-08-02 10:19 | 2026-08-02 10:19 |  |  | Fair | No | Use 3 amp fuse at 25 kva transformer
Non-Outage | J.E.26.08.02082 | C001871836 | Swon Miller |  | Completed |  |  | 2026-08-02 07:30 | 2026-08-02 07:32 | 2026-08-02 07:48 | 2026-08-02 07:49 | 2026-08-02 07:48 | 2026-08-02 08:38 | 2026-08-02 08:45 | 2026-08-02 08:45 | Fire |  | Fair | No | Customer request disconnection from jps main to repair pothead.isolate customer from jps main
Non-Outage | J.E.26.08.01973 | C001871837 | Fitzroy Turner | KSAS | Completed | Load_254739 | Cane River - 610 | 2026-08-02 07:32 | 2026-08-02 07:34 | 2026-08-02 08:09 | 2026-08-02 09:51 | 2026-08-02 10:43 | 2026-08-02 10:44 | 2026-08-02 10:48 | 2026-08-02 10:48 |  |  | Fair | No | Found tree blown fuses one 65amp and two 25amps switch cause switches top jumper rest and cross arm. have switch top jumper removed and replaced two 25amp junction fuse and one 65amp fuses supply restored to the areas
Non-Outage | J.E.26.08.00379 | C001871838 | Horace Malcolm |  | Completed |  |  | 2026-08-02 07:35 | 2026-08-02 07:36 | 2026-08-02 08:55 | 2026-08-02 08:56 | 2026-08-02 09:50 | 2026-08-02 10:50 | 2026-08-02 10:50 | 2026-08-02 10:50 |  |  | Fair | No | Refused one 25kva transformer used one 2amp fuse
Non-Outage | J.E.26.08.01402 | C001871839 | Clyde Brown |  | Completed |  |  | 2026-08-02 07:35 | 2026-08-02 07:39 | 2026-08-02 08:26 | 2026-08-02 08:26 | 2026-08-02 09:29 | 2026-08-02 09:38 | 2026-08-02 09:51 | 2026-08-02 09:51 | BangingWires |  | SevereWind | No | Blown 20 amps junction fuse on Twickenham road,line patrolled and no fault seen,blown fuse replaced.
Outage | J.E.26.08.00347 | C001871840 | Horace Malcolm | Hanover | Completed | Load_254647 | Orange Bay - 310 | 2026-08-02 07:35 | 2026-08-02 07:38 | 2026-08-02 10:50 | 2026-08-02 10:51 | 2026-08-02 12:11 | 2026-08-02 12:48 | 2026-08-02 12:48 | 2026-08-02 12:48 |  |  | Fair | No | Refused one 10amp junction fuse
Outage | J.E.26.08.01910 | C001871841 | Clyde Brown | Clarendon | Completed | Load_245875 | Monymusk - 210 | 2026-08-02 07:35 | 2026-08-02 07:39 | 2026-08-02 08:26 | 2026-08-02 09:52 | 2026-08-02 09:51 | 2026-08-02 09:39 | 2026-08-02 09:55 | 2026-08-02 09:55 |  |  | SevereWind | No | Blown 20 amps junction fuse on Twickenham road,line patrolled and no fault seen ,heavy wind in area,blown fuse replaced
Outage | J.E.26.08.00824 | C001871843 | Michael Christian | St.James | Completed | Load_248508 | Rose Hall - 210 | 2026-08-02 07:39 | 2026-08-02 07:40 | 2026-08-02 10:39 | 2026-08-02 10:40 | 2026-08-02 11:45 | 2026-08-02 11:53 | 2026-08-02 11:54 | 2026-08-02 11:54 |  |  | Fair | No | Check and found okay voltage 112 113 225 at pothead
Outage | J.E.26.08.00826 | C001871842 | Michael Christian | St.James | Completed | Load_241873 | Queens Drive - 710 | 2026-08-02 07:39 | 2026-08-02 07:40 | 2026-08-02 09:09 | 2026-08-02 09:10 | 2026-08-02 10:37 | 2026-08-02 10:39 | 2026-08-02 10:39 | 2026-08-02 10:39 |  |  | Fair | No | Check and found okay no broken wire found
Outage | J.E.26.08.01849 | C001871844 | Clyde Brown | Clarendon | Completed | Load_242818 | Monymusk - 210 | 2026-08-02 07:39 | 2026-08-02 07:40 | 2026-08-02 08:26 | 2026-08-02 09:56 | 2026-08-02 10:06 | 2026-08-02 10:31 | 2026-08-02 10:35 | 2026-08-02 10:35 |  |  | SevereWind | No | Blown 15 amps junction fuse at Rocky settlement bus shed,line patrolled heavy wind in area and rain earlier but no fault seen,blown fuse replaced.
Outage | J.E.26.08.00742 | C001871845 | Swon Miller | St.James | Completed | Load_557015 | Bogue - 310 | 2026-08-02 07:40 | 2026-08-02 07:41 | 2026-08-02 08:45 | 2026-08-02 08:45 | 2026-08-02 09:18 | 2026-08-02 09:39 | 2026-08-02 09:41 | 2026-08-02 09:41 |  |  | Fair | No | Check and found areas okay voltage found 114/113/228 customer states that power supply has been restored voltage left 113/114/228
Outage | J.E.26.08.00885 | C001871847 | Clyde Brown | Clarendon | Completed | Load_253290 | Parnassus - 310 | 2026-08-02 07:40 | 2026-08-02 07:41 | 2026-08-02 08:26 | 2026-08-02 13:42 | 2026-08-02 13:42 | 2026-08-02 13:43 | 2026-08-02 13:45 | 2026-08-02 13:45 |  |  | Fair | No | Cannot be located customer not answering phone
Outage | J.E.26.08.01379 | C001871848 | Richard Nicholas | St.Catherine | Completed | Load_243052 | Tredegar - 410 | 2026-08-02 07:42 | 2026-08-02 17:18 | 2026-08-02 18:03 | 2026-08-02 18:03 | 2026-08-02 19:11 | 2026-08-02 19:11 | 2026-08-02 19:15 | 2026-08-02 19:15 |  |  | Fair | No | Replaced blown 50amp junctions fuse on pole #0078988,pole#0022315 30amp junctions,pole #0022310 15amp junctions and 50kva transformer 5amp fuse.
Outage | J.E.26.08.01424 | C001871850 | Richard Nicholas | St.Catherine | Completed | Load_238500 | Twickenham - 310 | 2026-08-02 07:42 | 2026-08-02 17:23 | 2026-08-02 19:17 | 2026-08-02 19:18 | 2026-08-02 19:41 | 2026-08-02 20:56 | 2026-08-02 20:59 | 2026-08-02 20:59 |  |  | Fair | No | Replaced blown 30amp junctions at pole #0024856,blown 40amp at pole #596618 and a 50kva transformer 5amp fuse on pole #0009724.
Outage | J.E.26.08.01592 | C001871853 | Nickolas Rodriques | St.Catherine | Completed | Load_1000959 | Tredegar - 410 | 2026-08-02 07:42 | 2026-08-02 07:44 | 2026-08-02 15:34 | 2026-08-02 15:46 | 2026-08-02 16:26 | 2026-08-02 17:00 | 2026-08-02 17:01 | 2026-08-02 17:01 |  |  | Fair | No | Checked and found three set of junction fuses blown, two 40 amp and one 25 amp. Patrol and found nothing on line. Repaired by replacing the fuses after completing patrol.
Outage | J.E.26.08.01593 | C001871852 | Nickolas Rodriques | St.Catherine | Completed | Load_242765 | Twickenham - 310 | 2026-08-02 07:42 | 2026-08-02 07:43 | 2026-08-02 17:02 | 2026-08-02 19:22 | 2026-08-02 19:36 | 2026-08-02 19:43 | 2026-08-02 19:44 | 2026-08-02 19:44 |  |  | Fair | No | Power restored. Call relates to the 40 amp junction fuses that were replaced earlier.
Outage | J.E.26.08.01615 | C001871851 | Nickolas Rodriques | St.Catherine | Completed | Load_260775 | Tredegar - 210 | 2026-08-02 07:42 | 2026-08-02 07:43 | 2026-08-02 09:14 | 2026-08-02 09:38 | 2026-08-02 10:40 | 2026-08-02 12:00 | 2026-08-02 12:17 | 2026-08-02 12:17 |  |  | Fair | No | Checked and found two junction fuses blown, 10 amp and 8 amp. Patrol and found nothing on line. Repaired by replacing the fuse after completing patrols.
Outage | J.E.26.08.01617 | C001871849 | Nickolas Rodriques | St.Catherine | Completed | Load_259866 | Tredegar - 210 | 2026-08-02 07:42 | 2026-08-02 07:43 | 2026-08-02 12:22 | 2026-08-02 12:25 | 2026-08-02 12:45 | 2026-08-02 12:51 | 2026-08-02 12:53 | 2026-08-02 12:53 |  |  | Fair | No | Checked and found two junction fuses blown from three phase lines, 40 amp and 30 amp.patrol and found nothing on line. Repaired by replacing the fuses after completing patrol.
Non-Outage | J.E.26.08.01292 | C001871855 | Wan Carlos Scarlett |  | Completed |  |  | 2026-08-02 07:45 | 2026-08-02 07:47 | 2026-08-02 11:47 | 2026-08-02 11:48 | 2026-08-02 12:14 | 2026-08-02 13:11 | 2026-08-02 13:13 | 2026-08-02 13:13 | BrokenWire |  | Fair | No | Refuse 20 Amp junction no pole # was found nothing was found on the primary line cause by lightning strike
Non-Outage | J.E.26.08.01613 | C001871857 | Wan Carlos Scarlett |  | Completed |  |  | 2026-08-02 07:45 | 2026-08-02 07:48 | 2026-08-02 09:41 | 2026-08-02 10:54 | 2026-08-02 10:54 | 2026-08-02 10:54 | 2026-08-02 10:55 | 2026-08-02 10:55 | Fire |  | Fair | No | Call related to outage earlier customer confirmed that power supply has been restored
Non-Outage | J.E.26.08.01654 | C001871856 | Wan Carlos Scarlett |  | Completed |  |  | 2026-08-02 07:45 | 2026-08-02 15:42 | 2026-08-02 15:46 | 2026-08-02 15:47 | 2026-08-02 16:48 | 2026-08-02 16:52 | 2026-08-02 16:52 | 2026-08-02 16:52 | Fire |  | Fair | No | Refuse 10 Amps junction pole #006462 nothing was found on primary line Refuse 25 KVA transformer with 3 Amp fuse nothing was found on secondary line cause by lightning strike
Outage | J.E.26.08.01525 | C001871864 | Fitzroy Turner | KSAS | Completed | Load_1002684 | Cane River - 410 | 2026-08-02 07:47 | 2026-08-02 07:49 | 2026-08-02 12:59 | 2026-08-02 13:10 | 2026-08-02 13:10 | 2026-08-02 13:10 | 2026-08-02 13:12 | 2026-08-02 13:12 | Fire |  | Fair | No | Found 15amp junction fuse blown at the intersection at mar drive and Saturn avenue same 15amp replaced supply restored to the area
Outage | J.E.26.08.01553 | C001871863 | Fitzroy Turner | KSAS | Completed | Load_1002691 | Cane River - 410 | 2026-08-02 07:47 | 2026-08-02 07:49 | 2026-08-02 12:59 | 2026-08-02 13:24 | 2026-08-02 13:24 | 2026-08-02 13:24 | 2026-08-02 13:26 | 2026-08-02 13:26 |  |  | Fair | No | Found 5amp for 50kva transformer fuse blown replaced 5 amp fuse supply restored to the areas
Outage | J.E.26.08.01740 | C001871862 | Fitzroy Turner | KSAS | Completed | Load_238206 | Cane River - 410 | 2026-08-02 07:47 | 2026-08-02 07:49 | 2026-08-02 16:37 | 2026-08-02 16:37 | 2026-08-02 17:55 | 2026-08-02 17:55 | 2026-08-02 17:56 | 2026-08-02 17:56 |  |  | Fair | No | Found 15 amp junction fuse blown replaced with same 15amp supply restored to customer
Outage | J.E.26.08.01877 | C001871861 | Fitzroy Turner | KSAS | Completed | Load_556760 | Cane River - 410 | 2026-08-02 07:47 | 2026-08-02 07:49 | 2026-08-02 13:28 | 2026-08-02 14:05 | 2026-08-02 14:04 | 2026-08-02 14:05 | 2026-08-02 14:08 | 2026-08-02 14:08 | found |  | Fair | No | Found 3amp fuse blown replaced same 3amp supply restored to the areas
Outage | J.E.26.08.01880 | C001871859 | Fitzroy Turner | KSAS | Completed | Load_556722 | Cane River - 410 | 2026-08-02 07:47 | 2026-08-02 07:49 | 2026-08-02 14:03 | 2026-08-02 14:10 | 2026-08-02 14:12 | 2026-08-02 14:12 | 2026-08-02 14:14 | 2026-08-02 14:14 |  |  | Fair | No | Found 30 amps junction fuse blown at the intersection at shooter hill and bull main road same 30amp fuse replaced supply restored to the areas
Outage | J.E.26.08.01966 | C001871860 | Fitzroy Turner | KSAS | Completed | Load_246106 | Cane River - 410 | 2026-08-02 07:47 | 2026-08-02 07:49 | 2026-08-02 14:04 | 2026-08-02 14:16 | 2026-08-02 14:16 | 2026-08-02 14:16 | 2026-08-02 14:18 | 2026-08-02 14:18 |  |  | Fair | No | Supply restored to customer after replaced blown junction fuse
Outage | J.E.26.08.00782 | C001871867 | Fitzroy Turner | KSAS | Completed | Load_1002666 | Cane River - 410 | 2026-08-02 07:48 | 2026-08-02 07:49 | 2026-08-02 12:31 | 2026-08-02 17:57 | 2026-08-02 17:57 | 2026-08-02 17:57 | 2026-08-02 17:59 | 2026-08-02 17:59 |  |  | Fair | No | Found two wires service phase and neutral burnt mid span use 5ft off #6 service to splice and retention with two one bolt clamps supply restored to customer
Outage | J.E.26.08.01026 | C001871869 | Fitzroy Turner | KSAS | Completed | Load_251825 | Cane River - 310 | 2026-08-02 07:48 | 2026-08-02 07:49 | 2026-08-02 17:59 | 2026-08-02 18:00 | 2026-08-02 18:51 | 2026-08-02 18:53 | 2026-08-02 18:59 | 2026-08-02 18:59 |  |  | Fair | No | Found 30 amps trip savor drop out along the line we change two burnt up fuses link and two 10 amps fuse supply restored to the areas after closed u trip savor
Outage | J.E.26.08.01398 | C001871866 | Fitzroy Turner | KSAS | Completed | Load_242300 | Cane River - 410 | 2026-08-02 07:48 | 2026-08-02 07:49 | 2026-08-02 14:26 | 2026-08-02 14:27 | 2026-08-02 16:31 | 2026-08-02 16:31 | 2026-08-02 16:34 | 2026-08-02 16:34 |  |  | Fair | No | Customer supply restored after replace blown (30 amps junction fuse at the intersection of bull bay main road and shoot hill rd
Outage | J.E.26.08.01707 | C001871868 | Fitzroy Turner | KSAS | Completed | Load_1002663 | Cane River - 310 | 2026-08-02 07:48 | 2026-08-02 07:49 | 2026-08-02 14:19 | 2026-08-02 14:19 | 2026-08-02 14:19 | 2026-08-02 14:20 | 2026-08-02 14:21 | 2026-08-02 14:21 |  |  | EarthMovement | No | Customer supply restored after 30 amp junction fuse found blown replaced blown 30 amp fuse supply restored
Outage | J.E.26.08.01989 | C001871872 | Tyrese Williams | St.Ann | Completed | Load_265383 | Cardiff Hall - 210 | 2026-08-02 07:48 | 2026-08-02 07:51 | 2026-08-02 08:01 | 2026-08-02 12:18 | 2026-08-02 12:17 | 2026-08-02 12:18 | 2026-08-02 12:18 | 2026-08-02 12:18 |  |  | Fair | No | Premises found ok power was restored
Outage | J.E.26.08.01996 | C001871870 | Tyrese Williams | St.Ann | Completed | Load_262356 | Cardiff Hall - 210 | 2026-08-02 07:48 | 2026-08-02 07:51 | 2026-08-02 07:58 | 2026-08-02 12:15 | 2026-08-02 12:15 | 2026-08-02 12:15 | 2026-08-02 12:16 | 2026-08-02 12:16 |  |  | Fair | No | Premises found ok power was restored
Outage | J.E.26.08.01981 | C001871874 | Tyrese Williams | St.Ann | Completed | Load_305076 | Cardiff Hall - 210 | 2026-08-02 07:49 | 2026-08-02 07:51 | 2026-08-02 08:02 | 2026-08-02 12:23 | 2026-08-02 12:23 | 2026-08-02 12:24 | 2026-08-02 12:24 | 2026-08-02 12:24 |  |  | Fair | No | Premises found ok power was restored
Outage | J.E.26.08.02025 | C001871875 | Tyrese Williams | St.Ann | Completed | Load_294603 | Cardiff Hall - 210 | 2026-08-02 07:49 | 2026-08-02 07:51 | 2026-08-02 08:03 | 2026-08-02 12:19 | 2026-08-02 12:19 | 2026-08-02 12:20 | 2026-08-02 12:20 | 2026-08-02 12:20 |  |  | Fair | No | Premises found ok power was restored
Outage | J.E.26.08.02317 | C001871873 | Tyrese Williams | St.Ann | Completed | Load_249331 | Cardiff Hall - 210 | 2026-08-02 07:49 | 2026-08-02 07:51 | 2026-08-02 08:01 | 2026-08-02 12:22 | 2026-08-02 12:21 | 2026-08-02 12:22 | 2026-08-02 12:22 | 2026-08-02 12:22 |  |  | Fair | No | Premises found ok power was restored
Outage | J.E.26.08.02304 | C001871876 | Tyrese Williams | St.Ann | Completed | Load_246928 | Cardiff Hall - 310 | 2026-08-02 07:50 | 2026-08-02 07:51 | 2026-08-02 08:05 | 2026-08-02 15:41 | 2026-08-02 15:41 | 2026-08-02 15:47 | 2026-08-02 15:47 | 2026-08-02 15:47 |  |  | Fair | No | Premises found ok call related to 30amp junction fuse
Non-Outage | J.E.26.07.39950 | C001871880 | Christopher Edwards | KSAN | Completed | Load_267312 | Constant Spring - 310 | 2026-08-02 07:51 | 2026-08-02 07:52 | 2026-08-02 12:35 | 2026-08-02 13:00 | 2026-08-02 12:59 | 2026-08-02 13:51 | 2026-08-02 13:52 | 2026-08-02 13:52 |  |  | Fair | No | Remake corroded phase joint Using (1) one bolt clamps Voltage:117,116,233v
Outage | J.E.26.08.00832 | C001871879 | Christopher Edwards | KSAN | Completed | Load_248982 | Constant Spring - 410 | 2026-08-02 07:51 | 2026-08-02 07:52 | 2026-08-02 13:52 | 2026-08-03 10:41 | 2026-08-03 10:41 | 2026-08-03 11:28 | 2026-08-03 11:29 | 2026-08-03 11:29 | TreeContact |  | Fair | No | Supply is in the area Customer is concerned about overgrown vegetation in area
Outage | J.E.26.08.01690 | C001871877 | Donald Cunningham | St.Catherine | Completed | Load_266605 | Tredegar - 510 | 2026-08-02 07:51 | 2026-08-02 15:37 | 2026-08-02 16:41 | 2026-08-02 16:41 | 2026-08-02 17:14 | 2026-08-02 17:14 | 2026-08-02 17:22 | 2026-08-02 17:22 |  |  | Fair | No | Supply in area customer not reachable
Outage | J.E.26.08.01830 | C001871878 | Christopher Edwards | KSAN | Completed | Load_239302 | Constant Spring - 210 | 2026-08-02 07:51 | 2026-08-02 07:52 | 2026-08-02 08:32 | 2026-08-02 09:00 | 2026-08-02 09:19 | 2026-08-02 09:49 | 2026-08-02 09:50 | 2026-08-02 09:50 |  |  | Fair | No | Customer break was tripped Reset breaker supply is now at the premises
Non-Outage | J.E.26.07.33791 | C001871883 | Christopher Edwards | KSAN | Completed | Load_262126 | Constant Spring - 210 | 2026-08-02 07:52 | 2026-08-02 07:52 | 2026-08-02 11:15 | 2026-08-02 11:15 | 2026-08-02 11:15 | 2026-08-02 11:51 | 2026-08-02 11:52 | 2026-08-02 11:52 |  |  | Fair | No | Remake corroded neutral joint At pole Using (1) one bolt clamps Voltage:114,115,230v
Non-Outage | J.E.26.07.39313 | C001871884 | Christopher Edwards | KSAN | Completed | Load_267514 | Constant Spring - 210 | 2026-08-02 07:52 | 2026-08-02 07:52 | 2026-08-02 09:50 | 2026-08-02 09:51 | 2026-08-02 10:22 | 2026-08-02 10:58 | 2026-08-02 11:15 | 2026-08-02 11:15 |  |  | Fair | No | Remake burnt neutral joint at poleUsing (2) one bolt clamps Voltage:116,115,230v
Non-Outage | J.E.26.07.39754 | C001871885 | Christopher Edwards | KSAN | Completed | Load_265225 | Constant Spring - 210 | 2026-08-02 07:52 | 2026-08-02 07:52 | 2026-08-02 08:04 | 2026-08-02 11:53 | 2026-08-02 11:52 | 2026-08-02 12:34 | 2026-08-02 12:35 | 2026-08-02 12:35 |  |  | Fair | No | Remake open secondary phase jumper joint Using (1) one bolt clamps Voltage:116115,230v
Outage | J.E.26.08.01354 | C001871886 | Kenroy Dale | Manchester | Completed | Load_255644 | Porus - 310 | 2026-08-02 08:02 | 2026-08-02 08:06 | 2026-08-02 10:26 | 2026-08-02 10:26 | 2026-08-02 11:17 | 2026-08-02 11:55 | 2026-08-02 11:58 | 2026-08-02 11:58 |  |  | Fair | No | Blown 2 amp transformer fuse found for 25 kva line patrol two span of secondary neutral found broken, conductor was splice and retention blown fuse replaced and area now with supply
Outage | J.E.26.08.00676 | C001871888 | Raheem Ricketts | Manchester | Completed | Load_246363 | Spur Tree - 210 | 2026-08-02 08:09 | 2026-08-02 11:04 | 2026-08-02 11:09 | 2026-08-02 11:10 | 2026-08-02 11:16 | 2026-08-02 11:20 | 2026-08-02 11:20 | 2026-08-02 11:20 |  |  | Fair | No | Check and found okay power was restored from yesterday
Outage | J.E.26.08.01920 | C001871887 | Marlon Authors | Manchester | Completed | Load_247150 | Spur Tree - 210 | 2026-08-02 08:09 | 2026-08-02 08:10 | 2026-08-02 10:10 | 2026-08-02 10:11 | 2026-08-02 10:37 | 2026-08-02 11:02 | 2026-08-02 11:02 | 2026-08-02 11:02 |  |  | Fair | No | Patrol and found bird attached to the conductor from the junction switch bottom. Remove same and replace one blown 20 amp junction fuse at pole #584760. Restored supply ok
Non-Outage | J.E.26.07.39668 | C001871889 | Richman Whyte | Westmoreland | Completed | Load_244638 | Paradise - 210 | 2026-08-02 08:10 | 2026-08-02 08:11 | 2026-08-02 10:14 | 2026-08-02 10:15 | 2026-08-02 11:25 | 2026-08-02 11:26 | 2026-08-02 11:27 | 2026-08-02 11:27 |  |  | Fair | No | Customer have internal problem advise to fix voltage 113 113 226
Non-Outage | J.E.26.07.39469 | C001871890 | Richman Whyte | Westmoreland | Completed | Load_292703 | Paradise - 210 | 2026-08-02 08:11 | 2026-08-02 08:11 | 2026-08-02 08:47 | 2026-08-02 08:47 | 2026-08-02 10:10 | 2026-08-02 10:13 | 2026-08-02 10:14 | 2026-08-02 10:14 |  |  | Fair | No | Check and found okay voltage 110 110 220
Outage | J.E.26.08.02339 | C001871891 | Oshane Warren | Westmoreland | Completed | Load_257740 | Paradise - 310 | 2026-08-02 08:18 | 2026-08-02 08:21 | 2026-08-02 11:01 | 2026-08-02 11:02 | 2026-08-02 11:01 | 2026-08-02 11:01 | 2026-08-02 11:02 | 2026-08-02 11:02 |  |  | Fair | No | Replace 3amp 25 kva xformer fuse
Non-Outage | J.E.26.07.39438 | C001871893 | Raheem Ricketts | St.Elizabeth | Completed | Load_255323 | Maggotty - 110 | 2026-08-02 08:23 | 2026-08-02 08:24 | 2026-08-02 08:44 | 2026-08-02 11:01 | 2026-08-02 11:01 | 2026-08-02 11:02 | 2026-08-02 11:03 | 2026-08-02 11:03 |  |  | Fair | No | Customer says problem has been solved and power has been restored
Non-Outage | J.E.26.07.39878 | C001871892 | Raheem Ricketts | St.Elizabeth | Completed | Load_264057 | Maggotty - 110 | 2026-08-02 08:23 | 2026-08-02 08:24 | 2026-08-02 08:44 | 2026-08-02 09:05 | 2026-08-02 10:37 | 2026-08-02 10:45 | 2026-08-02 10:45 | 2026-08-02 10:45 |  |  | Fair | No | Customer not responding
Non-Outage | J.E.26.07.38382 | C001871895 | Raheem Ricketts | St.Elizabeth | Completed | Load_243738 | Maggotty - 110 | 2026-08-02 08:24 | 2026-08-02 08:24 | 2026-08-02 08:44 | 2026-08-02 11:38 | 2026-08-02 11:50 | 2026-08-02 11:52 | 2026-08-02 11:52 | 2026-08-02 11:52 |  |  | Fair | No | Check and found customer 110,meter burn meter needs to change immediately
Non-Outage | J.E.26.07.38981 | C001871894 | Raheem Ricketts | St.Elizabeth | Completed | Load_264057 | Maggotty - 110 | 2026-08-02 08:24 | 2026-08-02 08:24 | 2026-08-02 08:44 | 2026-08-02 10:48 | 2026-08-02 10:47 | 2026-08-02 10:48 | 2026-08-02 10:49 | 2026-08-02 10:49 |  |  | Fair | No | Check and found okay
Outage | J.E.26.08.02403 | C001871896 | Milton Charlton | KSAN | Completed | Load_258776 | Hope - 510 | 2026-08-02 08:24 | 2026-08-03 07:28 | 2026-08-03 11:57 | 2026-08-03 11:58 | 2026-08-03 12:42 | 2026-08-03 12:45 | 2026-08-03 12:43 | 2026-08-03 12:43 | BangingWires |  | Fair | No | Found okay upon arrival. Customer has an internal problem.
Non-Outage | J.E.26.07.40093 | C001871906 | Barnett Brown | Manchester | Completed | Load_268212 | Spur Tree - 310 | 2026-08-02 08:28 | 2026-08-02 08:29 | 2026-08-02 11:53 | 2026-08-02 11:54 | 2026-08-02 13:00 | 2026-08-02 13:28 | 2026-08-02 13:29 | 2026-08-02 13:29 |  |  | Fair | No | Open 10 kva transformer, remade drop lead, voltage 113 113 226
Non-Outage | J.E.26.08.00048 | C001871905 | Barnett Brown | Manchester | Completed | Load_259688 | Spur Tree - 310 | 2026-08-02 08:28 | 2026-08-02 08:29 | 2026-08-02 09:07 | 2026-08-02 09:07 | 2026-08-02 10:24 | 2026-08-02 11:50 | 2026-08-02 11:52 | 2026-08-02 11:52 |  |  | Fair | No | Open 25 kva transformer, splice and retention 2 span secondary neutral
Outage | J.E.26.08.01632 | C001871897 | Dwayne Cohen | KSAN | Completed | Load_267439 | West Kings House - 410 | 2026-08-02 08:28 | 2026-08-02 08:30 | 2026-08-02 09:55 | 2026-08-02 09:55 | 2026-08-02 09:55 | 2026-08-02 09:55 | 2026-08-02 09:56 | 2026-08-02 09:56 |  |  | Fair | No | Refuse two blown 50amps junction by the intersection of Hope and Winchester .
Outage | J.E.26.08.01661 | C001871904 | Dwayne Cohen | KSAN | Completed |  |  | 2026-08-02 08:28 | 2026-08-02 08:30 | 2026-08-02 09:56 | 2026-08-02 09:57 | 2026-08-02 11:36 | 2026-08-02 11:37 | 2026-08-02 11:40 | 2026-08-02 11:40 | Fire |  | Rains | No | Change burnt dead-end insulator and clamps and refuse blown 65amps junction, supply now restore.
Outage | J.E.26.08.01827 | C001871898 | Dwayne Cohen | KSAN | Completed | Load_267439 | West Kings House - 410 | 2026-08-02 08:28 | 2026-08-02 08:30 | 2026-08-02 09:23 | 2026-08-02 09:23 | 2026-08-02 09:23 | 2026-08-02 09:50 | 2026-08-02 09:54 | 2026-08-02 09:54 |  |  | Fair | No | Refuse two blown 50amps junction by the intersection of Hope Road and Winchester Road .
Outage | J.E.26.08.01881 | C001871903 | Elvis Trowers | KSAN | Completed | Load_261862 | Washington Blvd - 410 | 2026-08-02 08:28 | 2026-08-02 09:37 | 2026-08-02 09:55 | 2026-08-02 09:55 | 2026-08-02 10:31 | 2026-08-02 11:20 | 2026-08-02 11:20 | 2026-08-02 11:20 |  | Y | Fair | Yes | Premises was found without electricity supply when checked and 2 transformer fuses was found blown and replace after tree contact was removed at pole #0098373, which is 2/5 amp fuses.
Outage | J.E.26.08.02448 | C001871899 | Dwayne Cohen | KSAN | Completed | Load_244103 | Washington Blvd - 610 | 2026-08-02 08:28 | 2026-08-02 08:31 | 2026-08-02 08:45 | 2026-08-02 08:45 | 2026-08-02 09:02 | 2026-08-02 09:07 | 2026-08-02 09:23 | 2026-08-02 09:23 |  |  | Fair | No | Refuse blown junction with a 15amps fuse , supply now restore.
Outage | J.E.26.08.01255 | C001871910 | Rodclif Dawkins | Portmore | Completed | Load_250240 | Naggo Head - 510 | 2026-08-02 08:50 | 2026-08-02 10:30 | 2026-08-02 15:34 | 2026-08-02 15:35 | 2026-08-02 15:44 | 2026-08-02 15:59 | 2026-08-02 16:10 | 2026-08-02 16:10 |  |  | Fair | No | Found blown junction fuse for single phase T-Off and along with blown fuse for 25kva transformer. No faults found at time visit . Found and replaced 5amp at junction and 3amp at transformer area okay
Outage | J.E.26.08.01778 | C001871912 | Fitzroy Turner | KSAS | Completed | Load_254610 | Cane River - 610 | 2026-08-02 09:10 | 2026-08-02 09:10 | 2026-08-02 10:50 | 2026-08-02 10:50 | 2026-08-02 11:12 | 2026-08-02 12:22 | 2026-08-02 12:24 | 2026-08-02 12:24 |  |  | Fair | No | Customer supply restored
Outage | J.E.26.08.01883 | C001871911 | Fitzroy Turner | KSAS | Completed | Load_253428 | Cane River - 610 | 2026-08-02 09:10 | 2026-08-02 09:10 | 2026-08-02 12:24 | 2026-08-02 12:25 | 2026-08-02 12:24 | 2026-08-02 12:24 | 2026-08-02 12:27 | 2026-08-02 12:27 |  |  | Fair | No | Found tree 25amp junction fuse blown at at the main gate to yatch club replaced with same 25amp supply restored to customer
Outage | J.E.26.08.01942 | C001871913 | Rusean Allen | KSAS | Completed | Load_573491 | Duhaney - 410 | 2026-08-02 09:10 | 2026-08-02 09:11 | 2026-08-02 12:35 | 2026-08-02 12:36 | 2026-08-02 12:37 | 2026-08-02 12:38 | 2026-08-02 12:38 | 2026-08-02 12:38 |  |  | Fair | No | Related to riverton meadows
Outage | J.E.26.08.01307 | C001871914 | Rusean Allen | KSAS | Completed | Load_270125 | Duhaney - 410 | 2026-08-02 09:11 | 2026-08-02 09:11 | 2026-08-02 10:14 | 2026-08-02 10:15 | 2026-08-02 11:39 | 2026-08-02 12:35 | 2026-08-02 12:35 | 2026-08-02 12:35 |  |  | Fair | No | 3x 30amp fuse found 3x 30amp fuse replaced.
Outage | J.E.26.08.01991 | C001871916 | Rodclif Dawkins | KSAS | Completed | Load_405457 | Duhaney - 210 | 2026-08-02 09:13 | 2026-08-02 10:30 | 2026-08-02 14:20 | 2026-08-02 14:22 | 2026-08-02 14:28 | 2026-08-02 14:50 | 2026-08-02 14:50 | 2026-08-02 14:50 |  |  | Fair | No | Found blown fuse for 100kva transformer. Crew found no fault at time. 25amp found, replaced with 15amp . At metering point found 25amp blown, replaced with 25amp . Pump restored
Outage | J.E.26.08.02750 | C001871917 | Raheem Ricketts | St.Elizabeth | Completed | Load_243863 | Maggotty - 110 | 2026-08-02 09:16 | 2026-08-02 09:17 | 2026-08-02 10:51 | 2026-08-02 10:51 | 2026-08-02 10:51 | 2026-08-02 10:54 | 2026-08-02 10:55 | 2026-08-02 10:55 |  |  | Fair | No | Unable to locate customer cell phone went straight voicemail after several calls
Outage | J.E.26.08.02792 | C001871918 | Raheem Ricketts | St.Elizabeth | Completed | Load_264254 | Maggotty - 110 | 2026-08-02 09:16 | 2026-08-02 09:17 | 2026-08-02 11:29 | 2026-08-02 11:29 | 2026-08-02 11:29 | 2026-08-02 11:34 | 2026-08-02 11:34 | 2026-08-02 11:34 |  |  | Fair | No | Check and okay customer say they didn’t make any report and power is at their premises
Outage | J.E.26.08.02764 | C001871920 | Floyd Taylor | Trelawny | Completed | Load_253461 | Duncans - 210 | 2026-08-02 09:25 | 2026-08-02 09:27 | 2026-08-02 13:38 | 2026-08-02 13:38 | 2026-08-02 14:08 | 2026-08-02 14:26 | 2026-08-02 14:26 | 2026-08-02 14:26 |  |  | Fair | No | Found customer with light
Outage | J.E.26.08.02649 | C001871921 | Raymond Carr | St.Mary | Completed | Load_349421 | Oracabessa - 210 | 2026-08-02 09:26 | 2026-08-02 09:28 | 2026-08-02 09:37 | 2026-08-02 09:37 | 2026-08-02 09:40 | 2026-08-02 09:55 | 2026-08-02 09:53 | 2026-08-02 09:53 | BrokenWire |  | Fair | No | Two blown junction fuse at pole number 0013806, also switch top jumper found burnt off from main line. A fuse holder will be required, as one is completely destroyed.
Outage | J.E.26.08.02657 | C001871922 | Raymond Carr | St.Mary | Completed | Load_249380 | Highgate - 210 | 2026-08-02 09:27 | 2026-08-02 09:28 | 2026-08-02 10:36 | 2026-08-02 10:37 | 2026-08-02 11:17 | 2026-08-02 11:21 | 2026-08-02 11:47 | 2026-08-02 11:47 |  |  | Fair | No | Blown 50 kva transformer fuse found at pole number 0010709, line patrol and found okay, however after several tests close 50 kva transformer found to be defective, kindly refer to maintenance department for replacement.
Outage | J.E.26.08.02737 | C001871923 | Tyrese Williams | St.Ann | Completed | Load_248406 | Cardiff Hall - 310 | 2026-08-02 09:27 | 2026-08-02 09:28 | 2026-08-02 11:15 | 2026-08-02 12:26 | 2026-08-02 13:22 | 2026-08-02 13:22 | 2026-08-02 13:24 | 2026-08-02 13:24 | BrokenWire | Y | Fair | No | Cut tree from line Splice and retention 2 span of secondary phase and neutral use 35ft of #2AA and 2 pg clamp
Non-Outage | J.E.26.08.00106 | C001871924 | Kenroy Dale | Manchester | Completed | Load_251769 | Porus - 310 | 2026-08-02 09:33 | 2026-08-02 10:24 | 2026-08-02 21:04 | 2026-08-02 22:55 | 2026-08-02 23:29 | 2026-08-02 23:30 | 2026-08-02 23:31 | 2026-08-02 23:31 |  |  | Fair | No | Supply found okay voltage reading 116/114/230 customers have internal problems
Outage | J.E.26.08.01640 | C001871925 | Donald Cunningham | St.Catherine | Completed | Load_248459 | Tredegar - 510 | 2026-08-02 09:34 | 2026-08-02 15:38 | 2026-08-02 15:42 | 2026-08-02 15:42 | 2026-08-02 16:32 | 2026-08-02 16:40 | 2026-08-02 16:40 | 2026-08-02 16:40 | BrokenWire |  | Fair | No | Premises found ok supply restored
Outage | J.E.26.08.02060 | C001871926 | Rodclif Dawkins | St.Catherine | Completed | Load_238192 | Naggo Head - 510 | 2026-08-02 09:35 | 2026-08-02 10:41 | 2026-08-02 14:51 | 2026-08-02 14:52 | 2026-08-02 15:33 | 2026-08-02 15:33 | 2026-08-02 15:34 | 2026-08-02 15:34 | Fire |  | Fair | No | Customer found okay
Outage | J.E.26.08.02599 | C001871927 | Roxroy Needham | St.Mary | Completed | Load_269849 | Oracabessa - 210 | 2026-08-02 09:36 | 2026-08-02 15:26 | 2026-08-02 15:45 | 2026-08-02 18:26 | 2026-08-02 19:22 | 2026-08-02 19:27 | 2026-08-02 19:29 | 2026-08-02 19:29 |  |  | Fair | No | Premises found ok customer have internal problem
Outage | J.E.26.08.02779 | C001871930 | Nickolas Rodriques | St.Catherine | Completed | Load_254399 | Tredegar - 310 | 2026-08-02 09:52 | 2026-08-02 14:14 | 2026-08-02 14:22 | 2026-08-02 14:55 | 2026-08-02 15:17 | 2026-08-02 15:32 | 2026-08-02 15:34 | 2026-08-02 15:34 | Fire |  | Fair | No | Checked and found a 20 amp and 8 amp fuses blown from the same line. Patrol and found nothing on line. Repaired by replacing the fuses after completing patrol.
Outage | J.E.26.08.02791 | C001871929 | Nickolas Rodriques | St.Catherine | Completed | Load_258321 | Tredegar - 210 | 2026-08-02 09:52 | 2026-08-02 09:53 | 2026-08-02 12:58 | 2026-08-02 12:59 | 2026-08-02 13:17 | 2026-08-02 13:46 | 2026-08-02 13:56 | 2026-08-02 13:56 | Fire |  | Fair | No | Checked and found a 20 amp junction fuse blown caused by bird. Patrol and found nothing on line. Repaired by replacing the fuse after completing patrol.
Outage | J.E.26.08.01182 | C001871933 | Steven Ennis | KSAS | Completed | Load_251504 | Hunts Bay - 510 | 2026-08-02 09:55 | 2026-08-02 09:57 | 2026-08-02 12:29 | 2026-08-02 12:29 | 2026-08-02 12:29 | 2026-08-02 12:30 | 2026-08-02 12:30 | 2026-08-02 12:30 |  |  | Fair | No | Premises found okay and with supply
Outage | J.E.26.08.02781 | C001871931 | Steven Ennis | KSAS | Completed | Load_261950 | Hunts Bay - 510 | 2026-08-02 09:55 | 2026-08-02 09:57 | 2026-08-02 11:49 | 2026-08-02 19:17 | 2026-08-02 19:16 | 2026-08-02 19:17 | 2026-08-02 19:17 | 2026-08-02 19:17 |  |  | Fair | No | Found 3 span open secondary broken .. use 8 one bolt clamps, and 30ft AAAC to make repairs..
Outage | J.E.26.08.02786 | C001871935 | Steven Ennis | KSAS | Completed | Load_263200 | Hunts Bay - 310 | 2026-08-02 09:55 | 2026-08-02 09:57 | 2026-08-02 14:00 | 2026-08-02 14:01 | 2026-08-02 15:37 | 2026-08-02 15:40 | 2026-08-02 16:10 | 2026-08-02 16:10 |  |  | Fair | No | Found 9 fuse blown… 3 junction 65amps, 2 junction 50 amps, 3 8amps fuse and 1 5amps fuse… all fuses refused and change defective insulator and change defective drop out switch and also changed damaged arrestor …area back with supply..
Outage | J.E.26.08.02793 | C001871934 | Steven Ennis | KSAS | Completed | Load_242317 | Hunts Bay - 310 | 2026-08-02 09:55 | 2026-08-02 09:57 | 2026-08-02 12:38 | 2026-08-02 13:37 | 2026-08-02 13:37 | 2026-08-02 13:41 | 2026-08-02 13:42 | 2026-08-02 13:42 |  | Y | Fair | No | Area patrolled and found conductor had fallen out one insulator, use gloves to places back conductor and tie wire to make corrections, also cut tree from primary, and also connect burnt off switch bottom,Mathew use 3 40amps fuse to close back junction… area back with supply
Outage | J.E.26.08.01257 | C001871944 | Steven Ennis | KSAS | Completed | Load_254974 | Hunts Bay - 310 | 2026-08-02 09:56 | 2026-08-02 09:57 | 2026-08-02 13:43 | 2026-08-02 13:44 | 2026-08-02 13:43 | 2026-08-02 13:44 | 2026-08-02 13:44 | 2026-08-02 13:44 |  |  | Fair | No | Premises found ok and with supply
Outage | J.E.26.08.01261 | C001871941 | Steven Ennis | KSAS | Completed | Load_268768 | Hunts Bay - 310 | 2026-08-02 09:56 | 2026-08-02 09:57 | 2026-08-02 16:43 | 2026-08-02 16:43 | 2026-08-02 16:47 | 2026-08-02 17:19 | 2026-08-02 17:19 | 2026-08-02 17:19 | BrokenWire |  | Fair | No | Found fuse blown at junction.. use 10 amps fuse to close back junction.. customer back with supply
Outage | J.E.26.08.01634 | C001871940 | Steven Ennis | KSAS | Completed | Load_262444 | Hunts Bay - 310 | 2026-08-02 09:56 | 2026-08-02 09:57 | 2026-08-02 16:38 | 2026-08-02 16:39 | 2026-08-02 16:38 | 2026-08-02 16:39 | 2026-08-02 16:39 | 2026-08-02 16:39 |  |  | Fair | No | Found 30amps fuse at junction blown,, line patrolled and no fault found… use 30amps fuse to close junction..
Outage | J.E.26.08.01837 | C001871937 | Steven Ennis | KSAS | Completed | Load_244159 | Hunts Bay - 310 | 2026-08-02 09:56 | 2026-08-02 09:57 | 2026-08-02 17:59 | 2026-08-02 17:59 | 2026-08-02 17:59 | 2026-08-02 19:14 | 2026-08-02 19:14 | 2026-08-02 19:14 |  |  | Fair | No | Found 3 span open secondary broken .. use 8 one bolt clamps, and 30ft AAAC to make repairs..
Outage | J.E.26.08.01853 | C001871936 | Steven Ennis | KSAS | Completed | Load_258287 | Hunts Bay - 310 | 2026-08-02 09:56 | 2026-08-02 09:57 | 2026-08-02 17:20 | 2026-08-02 17:20 | 2026-08-02 17:20 | 2026-08-02 17:21 | 2026-08-02 17:21 | 2026-08-02 17:21 |  |  | Fair | No | Premises found ok and with supply…
Outage | J.E.26.08.02678 | C001871945 | Andre Smith | KSAS | Completed | Load_1003920 | Hunts Bay - 110 | 2026-08-02 09:56 | 2026-08-02 17:26 | 2026-08-02 17:39 | 2026-08-02 17:40 | 2026-08-02 17:52 | 2026-08-02 18:25 | 2026-08-02 18:25 | 2026-08-02 18:25 |  |  | Fair | No | Replace blown junction fuses 50A/80A supply restored
Outage | J.E.26.08.02940 | C001871946 | Steven Ennis | KSAS | Completed | Load_293995 | Hunts Bay - 510 | 2026-08-02 09:58 | 2026-08-02 09:59 | 2026-08-02 10:24 | 2026-08-02 10:25 | 2026-08-02 11:23 | 2026-08-02 11:41 | 2026-08-02 11:42 | 2026-08-02 11:42 |  |  | Fair | No | Found 2 30amps junction blown… area patrol and no fault found.. use 2 30amps to close back cct… area back with supply
Outage | J.E.26.08.02922 | C001871949 | Raheem Ricketts | St.Elizabeth | Completed | Load_253514 | Maggotty - 110 | 2026-08-02 10:04 | 2026-08-02 10:05 | 2026-08-02 11:35 | 2026-08-02 11:35 | 2026-08-02 11:35 | 2026-08-02 11:36 | 2026-08-02 11:37 | 2026-08-02 11:37 |  |  | Fair | No | Check and found okay
Outage | J.E.26.08.02968 | C001871950 | Delano Gayle | St.Catherine | Completed | Load_269534 | Twickenham - 210 | 2026-08-02 10:13 | 2026-08-03 02:59 | 2026-08-03 05:51 | 2026-08-03 05:51 | 2026-08-03 06:11 | 2026-08-03 06:15 | 2026-08-03 06:15 | 2026-08-03 06:15 |  |  | Fair | No | Blown 25kva transformer fuse no pole number, H1 bushing on transformer is the porcelain type which is cracked and needs to be rectified as upon replacing 3amps fuse and closing circuit sparks can be seen coming from off bushing send call to maintenance
Outage | J.E.26.08.02462 | C001871954 | Clyde Brown | Clarendon | Completed | Load_241995 | Parnassus - 210 | 2026-08-02 10:17 | 2026-08-02 10:23 | 2026-08-02 10:36 | 2026-08-02 11:16 | 2026-08-02 12:23 | 2026-08-02 12:28 | 2026-08-02 12:32 | 2026-08-02 12:32 |  |  | Fair | No | Blown 3 amps fuse for 25 kva transformer,line patrolled and no fault seen,blown fuse replaced
Outage | J.E.26.08.02589 | C001871953 | Clyde Brown | Clarendon | Completed | Load_244771 | Parnassus - 210 | 2026-08-02 10:17 | 2026-08-02 10:23 | 2026-08-02 10:36 | 2026-08-02 12:33 | 2026-08-02 12:32 | 2026-08-02 12:28 | 2026-08-02 12:34 | 2026-08-02 12:34 |  |  | Fair | No | Blown 3 amps fuse for 25kva transformer,line patrolled and no fault seen,blown fuse replaced.
Outage | J.E.26.08.02611 | C001871952 | Clyde Brown | Clarendon | Completed | Load_254041 | Parnassus - 310 | 2026-08-02 10:17 | 2026-08-02 10:23 | 2026-08-02 10:36 | 2026-08-02 10:36 | 2026-08-02 11:04 | 2026-08-02 11:08 | 2026-08-02 11:15 | 2026-08-02 11:15 |  |  | Fair | No | Blown 20 amps junction fuse at phase 1 Hayes new Town,line patrolled and no fault seen,blown fuse replaced.
Outage | J.E.26.08.02935 | C001871956 | Richard Nicholas | St.Catherine | Completed | Load_252934 | Rhodens Pen - 210 | 2026-08-02 10:21 | 2026-08-02 10:23 | 2026-08-02 10:36 | 2026-08-02 10:37 | 2026-08-02 12:43 | 2026-08-02 13:19 | 2026-08-02 13:20 | 2026-08-02 13:20 |  |  | Fair | No | Replaced blown 25amp junctions fuse at the intersection of church pen and sharper lane.
Outage | J.E.26.08.03010 | C001871957 | Ricky Hall | St.Catherine | Completed | Load_557324 | Twickenham - 410 | 2026-08-02 10:21 | 2026-08-02 15:30 | 2026-08-02 15:47 | 2026-08-02 15:58 | 2026-08-02 17:05 | 2026-08-02 17:42 | 2026-08-02 17:42 | 2026-08-02 17:42 |  |  | Rains | No | Replace 2 blown 30 amps junction fuse
Outage | J.E.26.08.03029 | C001871959 | Wan Carlos Scarlett | St.Catherine | Completed | Load_247125 | Twickenham - 210 | 2026-08-02 10:23 | 2026-08-02 10:39 | 2026-08-02 14:21 | 2026-08-02 14:22 | 2026-08-02 15:17 | 2026-08-02 15:38 | 2026-08-02 15:44 | 2026-08-02 15:44 | BrokenWire |  | Fair | No | Refuse 25 KVA transformer with a 3 amps fuse no pole # was found nothing was found on secondary line suspect lightning strike
Outage | J.E.26.08.03035 | C001871961 | Richard Nicholas | St.Catherine | Completed | Load_261455 | Rhodens Pen - 410 | 2026-08-02 10:24 | 2026-08-02 10:24 | 2026-08-02 13:20 | 2026-08-02 13:21 | 2026-08-02 14:19 | 2026-08-02 14:45 | 2026-08-02 14:50 | 2026-08-02 14:50 |  |  | Fair | No | Blown junctions fuse identified on a pole that is actually located ona church premises however due to several motor vehicle that is park under the switch pole it is unable to operate at the time when visited.its best to revisit after church service is over.follow up required.
Outage | J.E.26.08.01033 | C001871965 | Dwayne Cohen | KSAN | Completed | Load_244867 | Washington Blvd - 510 | 2026-08-02 10:26 | 2026-08-02 10:38 | 2026-08-02 12:25 | 2026-08-02 13:58 | 2026-08-02 13:58 | 2026-08-02 13:55 | 2026-08-02 13:58 | 2026-08-02 13:58 |  |  | Fair | No | 25KVA Transformer found defective.
Outage | J.E.26.08.01829 | C001871963 | Dwayne Cohen | KSAN | Completed | Load_266172 | Washington Blvd - 610 | 2026-08-02 10:26 | 2026-08-02 10:38 | 2026-08-02 12:30 | 2026-08-02 12:31 | 2026-08-02 13:12 | 2026-08-02 13:18 | 2026-08-02 13:22 | 2026-08-02 13:22 |  |  | Fair | No | Refuse 3amps transformer link, supply now restore.
Outage | J.E.26.08.02521 | C001871964 | Dwayne Cohen | KSAN | Completed | Load_302283 | Washington Blvd - 510 | 2026-08-02 10:26 | 2026-08-02 10:38 | 2026-08-02 11:46 | 2026-08-02 11:46 | 2026-08-02 12:09 | 2026-08-02 12:24 | 2026-08-02 12:25 | 2026-08-02 12:25 |  |  | Fair | No | Refuse two blown 10amps transformer fuse , supply is now restore.
Outage | J.E.26.08.02927 | C001871962 | Dwayne Cohen | KSAN | Completed | Load_261793 | Washington Blvd - 610 | 2026-08-02 10:26 | 2026-08-02 10:38 | 2026-08-02 11:42 | 2026-08-02 13:59 | 2026-08-02 14:08 | 2026-08-02 14:09 | 2026-08-02 14:13 | 2026-08-02 14:13 | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Customer suspect illegal connection on there service wire , please refer this report to FIELD SERVICE DEPARTMENT.
Outage | J.E.26.08.02870 | C001871966 | Romeo Brissett | Hanover | Completed | Load_255828 | Orange Bay - 310 | 2026-08-02 10:30 | 2026-08-02 10:32 | 2026-08-02 13:35 | 2026-08-02 13:36 | 2026-08-02 14:21 | 2026-08-02 15:56 | 2026-08-02 16:02 | 2026-08-02 16:02 |  |  | Fair | No | Cut and removed bamboo, replaced (1)8amps junction fuse.
Outage | J.E.26.08.01934 | C001871967 | Andre Smith | KSAN | Completed | Load_241594 | Washington Blvd - 310 | 2026-08-02 10:37 | 2026-08-02 17:28 | 2026-08-02 18:25 | 2026-08-02 18:26 | 2026-08-02 18:43 | 2026-08-02 18:44 | 2026-08-02 18:44 | 2026-08-02 18:44 | BrokenPole |  | Fair | No | Replace blown junction fuses 15A /30A supply restored
Outage | J.E.26.08.02115 | C001871968 | Jermaine Douglas | KSAS | Completed | Load_265504 | Up Park Camp - 310 | 2026-08-02 10:37 | 2026-08-02 10:39 | 2026-08-02 11:47 | 2026-08-02 11:47 | 2026-08-02 12:05 | 2026-08-02 12:45 | 2026-08-02 12:53 | 2026-08-02 12:53 |  |  | Fair | No | By swallow field rd, 3 phase return two fuse found blown by pole #0007330 2x10amps fuse used and by pole# 0052953, bank of 3x50kva transformer, 2x5amps fuse to restore power.
Outage | J.E.26.08.03054 | C001871970 | Marlon Authors | Manchester | Completed | Load_240150 | Spur Tree - 210 | 2026-08-02 10:48 | 2026-08-02 10:49 | 2026-08-02 11:09 | 2026-08-02 11:09 | 2026-08-02 12:29 | 2026-08-02 13:15 | 2026-08-02 13:15 | 2026-08-02 13:15 |  |  | Fair | No | Patrol and found vegetation touching the primary conductor whenever the wind blows. Cut and remove same and replace one blown 20 amp junction fuse at pole #045705. Restored supply ok
Non-Outage | J.E.26.08.02900 | C001871971 | Raheem Ricketts | Manchester | Completed | Load_244726 | Spur Tree - 210 | 2026-08-02 10:49 | 2026-08-02 16:10 | 2026-08-02 16:17 | 2026-08-02 16:18 | 2026-08-02 16:17 | 2026-08-02 16:18 | 2026-08-02 16:18 | 2026-08-02 16:18 |  |  | Fair | No | Unable to locate customer cell phone went straight voicemail after several calls
Outage | J.E.26.08.01534 | C001871980 | Jermaine Douglas | KSAS | Completed | Load_256552 | Greenwich - 510 | 2026-08-02 10:49 | 2026-08-02 10:50 | 2026-08-02 19:32 | 2026-08-02 19:32 | 2026-08-02 19:52 | 2026-08-02 20:04 | 2026-08-02 20:04 | 2026-08-02 20:04 |  |  | Fair | No | Customer found okay
Outage | J.E.26.08.01598 | C001871975 | Jermaine Douglas | KSAS | Completed | Load_242760 | Greenwich - 710 | 2026-08-02 10:49 | 2026-08-02 10:50 | 2026-08-02 20:04 | 2026-08-02 20:41 | 2026-08-02 20:49 | 2026-08-02 20:58 | 2026-08-02 20:58 | 2026-08-02 20:58 |  |  | Fair | No | Customer found okay
Outage | J.E.26.08.01767 | C001871978 | Jermaine Douglas | KSAS | Completed | Load_243869 | Greenwich - 510 | 2026-08-02 10:49 | 2026-08-02 10:50 | 2026-08-02 22:17 | 2026-08-02 22:18 | 2026-08-02 22:53 | 2026-08-02 23:03 | 2026-08-02 23:04 | 2026-08-02 23:04 |  |  | Fair | No
Outage | J.E.26.08.01824 | C001871981 | Jermaine Douglas | KSAS | Completed | Load_254591 | Greenwich - 410 | 2026-08-02 10:49 | 2026-08-02 10:50 | 2026-08-02 17:36 | 2026-08-02 17:36 | 2026-08-02 17:36 | 2026-08-02 17:37 | 2026-08-02 17:38 | 2026-08-02 17:38 |  |  | Fair | No | Call related to defective 100kva transformer by orchard rd
Outage | J.E.26.08.01917 | C001871977 | Jermaine Douglas | KSAS | Completed | Load_289826 | Greenwich - 510 | 2026-08-02 10:49 | 2026-08-02 10:50 | 2026-08-02 22:04 | 2026-08-02 22:05 | 2026-08-02 22:06 | 2026-08-02 22:10 | 2026-08-02 22:10 | 2026-08-02 22:10 |  |  | Fair | No | Call related to burnt off jumper by west rd and eight intersection.
Outage | J.E.26.08.02038 | C001871972 | Jermaine Douglas | KSAS | Completed | Load_243158 | Greenwich - 710 | 2026-08-02 10:49 | 2026-08-02 10:50 | 2026-08-02 17:42 | 2026-08-02 17:42 | 2026-08-02 18:00 | 2026-08-02 19:14 | 2026-08-02 19:17 | 2026-08-02 19:17 |  |  | Fair | No | By pole#0068901 3 phase return primary by kew rd 2x30amps fuse found blown and one drop out switch defective. Repairs were done and power restored.
Outage | J.E.26.08.02884 | C001871976 | Jermaine Douglas | KSAS | Completed | Load_290286 | Greenwich - 510 | 2026-08-02 10:49 | 2026-08-02 10:50 | 2026-08-02 22:10 | 2026-08-02 22:11 | 2026-08-02 22:16 | 2026-08-02 22:17 | 2026-08-02 22:17 | 2026-08-02 22:17 |  |  | Fair | No | Call related to.burnt off jumper by eight street.
Outage | J.E.26.08.02953 | C001871974 | Jermaine Douglas | KSAS | Completed | Load_290958 | Greenwich - 510 | 2026-08-02 10:49 | 2026-08-02 10:50 | 2026-08-02 20:58 | 2026-08-02 20:59 | 2026-08-02 21:29 | 2026-08-02 22:04 | 2026-08-02 22:04 | 2026-08-02 22:04 |  |  | Fair | No | Two phase return primary, one switch to jumper found burnt off by west rd and eight street intersection, one hot line clamp and 2x30amps fuse.
Outage | J.E.26.08.03017 | C001871979 | Jermaine Douglas | KSAS | Completed | Load_239610 | Greenwich - 410 | 2026-08-02 10:49 | 2026-08-02 10:50 | 2026-08-02 16:02 | 2026-08-02 16:02 | 2026-08-02 16:50 | 2026-08-02 17:33 | 2026-08-02 17:36 | 2026-08-02 17:36 |  |  | Fair | No | By Orchard rd at pole #0079148, bank of 3 transformer 2x50kva and 1x100kva. The 100kva transformer found defective.
Outage | J.E.26.08.03046 | C001871982 | Collin Robinson | Portland | Completed | Load_256293 | Port Antonio - 310 | 2026-08-02 10:50 | 2026-08-02 17:33 | 2026-08-03 13:02 | 2026-08-03 13:03 | 2026-08-03 13:16 | 2026-08-03 13:18 | 2026-08-03 13:19 | 2026-08-03 13:19 |  |  | Fair | No | Information received from customer that issue was resolve
Outage | J.E.26.08.03019 | C001871983 | Collin Robinson | Portland | Completed | Load_256564 | Port Antonio - 310 | 2026-08-02 10:51 | 2026-08-02 10:54 | 2026-08-02 13:50 | 2026-08-02 13:51 | 2026-08-02 14:17 | 2026-08-02 14:37 | 2026-08-02 14:38 | 2026-08-02 14:38 | Fire |  | Rains | No | Found customer without electricity cause by corroded service wire, repair by replacing 15ft of #6 twisted service wire and 2 one bolt clamps. Voltage reading after repair 115v.
Outage | J.E.26.08.02954 | C001871984 | Collin Robinson | Portland | Completed | Load_263392 | Port Antonio - 310 | 2026-08-02 10:53 | 2026-08-02 10:54 | 2026-08-03 13:22 | 2026-08-03 13:23 | 2026-08-03 13:33 | 2026-08-03 13:39 | 2026-08-03 13:39 | 2026-08-03 13:39 |  |  | Fair | No | Unable to locate customer
Outage | J.E.26.08.02806 | C001871987 | Kenroy Dale | Manchester | Completed | Load_270122 | Kendal - 210 | 2026-08-02 10:58 | 2026-08-02 10:59 | 2026-08-02 11:58 | 2026-08-02 11:59 | 2026-08-02 13:56 | 2026-08-02 14:36 | 2026-08-02 14:38 | 2026-08-02 14:38 |  |  | Fair | No | Blown 3 amp transformer fuse found cause from dislodged neutral conductor, conductor was retention blown fuse replaced and area now with supply
Outage | J.E.26.08.00914 | C001871990 | Tyrese Williams | St.Ann | Completed | Load_238163 | Cardiff Hall - 310 | 2026-08-02 11:28 | 2026-08-02 11:29 | 2026-08-02 12:00 | 2026-08-02 15:40 | 2026-08-02 15:39 | 2026-08-02 15:40 | 2026-08-02 15:40 | 2026-08-02 15:40 |  |  | Fair | No | Replace a 30 amp junction fuse at pole
Outage | J.E.26.08.01923 | C001871991 | Daniel Francis | St.Ann | Completed | Load_245545 | Roaring River - 210 | 2026-08-02 11:28 | 2026-08-02 11:29 | 2026-08-02 14:03 | 2026-08-02 14:03 | 2026-08-02 14:03 | 2026-08-02 14:04 | 2026-08-02 14:08 | 2026-08-02 14:08 |  |  | Fair | No | Patrol and found junction blown at lime hall square one 25amp fuse replace
Outage | J.E.26.08.03167 | C001871993 | Raheem Ricketts | St.Elizabeth | Completed | Load_259003 | Maggotty - 210 | 2026-08-02 11:38 | 2026-08-02 12:29 | 2026-08-02 12:37 | 2026-08-02 12:39 | 2026-08-02 13:30 | 2026-08-02 13:43 | 2026-08-02 13:44 | 2026-08-02 13:44 | Fire |  | Fair | No | Check an found okay customer experiencing internal problem
Non-Outage | J.E.26.08.02971 | C001871994 | Barnett Brown | Manchester | Completed | Load_259688 | Spur Tree - 310 | 2026-08-02 11:47 | 2026-08-02 11:48 | 2026-08-02 15:22 | 2026-08-02 15:23 | 2026-08-02 17:26 | 2026-08-02 17:26 | 2026-08-02 18:23 | 2026-08-02 18:23 |  |  | Fair | No | Related to call done earlier where secondary neutral splice and retention
Non-Outage | J.E.26.08.03174 | C001871996 | Swon Miller |  | Completed |  |  | 2026-08-02 11:50 | 2026-08-02 11:52 | 2026-08-02 12:03 | 2026-08-02 12:04 | 2026-08-02 14:01 | 2026-08-26 02:28 | 2026-08-02 14:33 | 2026-08-02 14:33 | Fire |  | Fair | No | Found wooden pole burnt cause by guy wire touching secondary phase cut and remove the tip of the guy wire voltage found 115/116/232 voltage left 115/116/232
Outage | J.E.26.08.03077 | C001871997 | Horace Malcolm | St.James | Completed | Load_292851 | Bogue - 610 | 2026-08-02 11:50 | 2026-08-02 11:51 | 2026-08-02 14:06 | 2026-08-02 14:06 | 2026-08-02 15:47 | 2026-08-02 17:02 | 2026-08-02 17:02 | 2026-08-02 17:02 |  |  | Fair | No | Retention one pole span secondary both phases and nuetral and replace one 15kva transformer fuse used one 1.5amp fuse
Outage | J.E.26.08.03178 | C001872000 | Horace Malcolm | St.James | Completed | Load_267384 | Bogue - 510 | 2026-08-02 12:03 | 2026-08-02 12:06 | 2026-08-02 12:48 | 2026-08-02 12:48 | 2026-08-02 13:23 | 2026-08-02 14:06 | 2026-08-02 14:06 | 2026-08-02 14:06 |  |  | Rains | No | Clean and remake joints at customer pothead use one clamp voltage 117-119-236
Outage | J.E.26.08.03196 | C001872002 | Marlon Authors | St.Elizabeth | Completed | Load_254040 | Maggotty - 110 | 2026-08-02 12:10 | 2026-08-02 12:31 | 2026-08-02 17:06 | 2026-08-02 18:33 | 2026-08-02 18:37 | 2026-08-02 19:05 | 2026-08-02 19:05 | 2026-08-02 19:05 |  |  | Fair | No | Patrol and found clear. Replace one blown 15 amp junction fuse at pole #057215. Restored supply okay
Outage | J.E.26.08.03228 | C001872001 | Raheem Ricketts | St.Elizabeth | Completed | Load_265170 | Maggotty - 210 | 2026-08-02 12:10 | 2026-08-02 12:19 | 2026-08-02 12:37 | 2026-08-02 13:44 | 2026-08-02 13:44 | 2026-08-02 13:44 | 2026-08-02 13:44 | 2026-08-02 13:44 | BrokenWire |  | Fair | No | Call related
Outage | J.E.26.08.03155 | C001872004 | Richman Whyte | Westmoreland | Completed | Load_268175 | Paradise - 110 | 2026-08-02 12:17 | 2026-08-02 12:18 | 2026-08-02 15:02 | 2026-08-02 15:03 | 2026-08-02 15:02 | 2026-08-02 15:02 | 2026-08-02 15:03 | 2026-08-02 15:03 |  |  | Fair | No | Replace ten amp junction fuse
Outage | J.E.26.08.03189 | C001872003 | Richman Whyte | Westmoreland | Completed | Load_265090 | Paradise - 110 | 2026-08-02 12:17 | 2026-08-02 12:18 | 2026-08-02 14:24 | 2026-08-02 14:24 | 2026-08-02 14:46 | 2026-08-02 15:00 | 2026-08-02 15:01 | 2026-08-02 15:01 |  |  | Fair | No | Replace ten amp junction fuse
Outage | J.E.26.08.03287 | C001872005 | Kenroy Dale | Manchester | Completed | Load_259776 | Porus - 310 | 2026-08-02 12:34 | 2026-08-02 12:35 | 2026-08-02 18:43 | 2026-08-02 19:02 | 2026-08-02 20:35 | 2026-08-02 21:03 | 2026-08-02 21:04 | 2026-08-02 21:04 |  |  | Fair | No | Supply found okay voltage reading 118/118/236
Outage | J.E.26.08.03247 | C001872006 | Collin Robinson | Portland | Completed | Load_261270 | Port Antonio - 310 | 2026-08-02 12:35 | 2026-08-02 13:14 | 2026-08-02 14:40 | 2026-08-02 14:40 | 2026-08-02 15:51 | 2026-08-02 16:12 | 2026-08-02 16:12 | 2026-08-02 16:12 |  |  | Fair | No | Clear tree from primary conductor and replace 20 amps junction at pole 524004
Outage | J.E.26.08.03290 | C001872007 | Collin Robinson | Portland | Completed | Load_239005 | Port Antonio - 410 | 2026-08-02 12:35 | 2026-08-02 13:14 | 2026-08-02 16:16 | 2026-08-02 16:16 | 2026-08-02 16:40 | 2026-08-02 16:45 | 2026-08-02 16:45 | 2026-08-02 16:45 |  |  | Fair | No | Visit Area and found Area with supply
Outage | J.E.26.08.03179 | C001872010 | Stephen Taylor | St.Thomas | Completed | Load_248600 | Lysson - 410 | 2026-08-02 12:40 | 2026-08-02 12:41 | 2026-08-02 13:39 | 2026-08-02 13:39 | 2026-08-02 13:39 | 2026-08-02 13:39 | 2026-08-02 15:50 | 2026-08-02 15:50 |  |  | Fair | No | Patrol clear line with switch stick and close up junction with a 10 amp fuse safely all customer is now okay
Outage | J.E.26.08.03307 | C001872011 | Clyde Brown | Clarendon | Completed | Load_569799 | Parnassus - 310 | 2026-08-02 12:42 | 2026-08-02 13:20 | 2026-08-02 13:48 | 2026-08-02 15:26 | 2026-08-02 16:03 | 2026-08-02 16:13 | 2026-08-02 16:21 | 2026-08-02 16:21 |  |  | Fair | No | Corroded joint at secondary line for 3 wire service connection remade with one bolt clamp voltage left 115/115 and 230V
Outage | J.E.26.08.01759 | C001872013 | Richard Nicholas | St.Catherine | Completed | Load_259014 | Tredegar - 210 | 2026-08-02 12:52 | 2026-08-02 15:17 | 2026-08-02 17:15 | 2026-08-02 17:16 | 2026-08-02 18:00 | 2026-08-02 18:00 | 2026-08-02 18:01 | 2026-08-02 18:01 | BrokenWire |  | Fair | No | Area was already refer to the maintenance department.
Outage | J.E.26.08.03188 | C001872014 | Fitzroy Turner | KSAS | Completed | Load_244328 | Cane River - 610 | 2026-08-02 13:17 | 2026-08-02 13:17 | 2026-08-02 19:00 | 2026-08-02 19:00 | 2026-08-02 19:32 | 2026-08-02 19:32 | 2026-08-02 19:34 | 2026-08-02 19:34 |  |  | EarthMovement | No | Found 30 amps junction fuse blown at the intersection of port royal road and JDF gate same 30 amp replaced supply restored to customer
Outage | J.E.26.08.03334 | C001872015 | Clyde Brown | Clarendon | Completed | Load_301191 | Monymusk - 210 | 2026-08-02 13:17 | 2026-08-02 13:18 | 2026-08-02 13:48 | 2026-08-02 13:48 | 2026-08-02 15:12 | 2026-08-02 14:58 | 2026-08-02 15:16 | 2026-08-02 15:16 |  |  | Fair | No | Blown 3 amps fuse for 25kva transformer,line patrolled and no fault seen,blown fuse replaced.
Non-Outage | J.E.26.07.35544 | C001872019 | Marlon Authors | St.Elizabeth | Completed | Load_248131 | Maggotty - 110 | 2026-08-02 13:23 | 2026-08-02 13:24 | 2026-08-02 15:51 | 2026-08-02 15:51 | 2026-08-02 15:51 | 2026-08-02 16:16 | 2026-08-02 16:16 | 2026-08-02 16:16 |  |  | Fair | No | Patrol and found clear. Replace three blown five amps fuses that protects 50 kva transformers in bankers three. Restored supply okay
Outage | J.E.26.08.03401 | C001872020 | Michael Christian | St.James | Completed | Load_302222 | Queens Drive - 710 | 2026-08-02 13:28 | 2026-08-02 13:28 | 2026-08-02 14:55 | 2026-08-02 14:56 | 2026-08-02 15:49 | 2026-08-02 15:50 | 2026-08-02 15:51 | 2026-08-02 15:51 |  |  | Fair | No | Check and found okay
Outage | J.E.26.08.03104 | C001872021 | Roxroy Needham | St.Mary | Completed | Load_252727 | Oracabessa - 110 | 2026-08-02 13:30 | 2026-08-02 15:26 | 2026-08-02 15:44 | 2026-08-02 19:29 | 2026-08-02 20:13 | 2026-08-02 21:31 | 2026-08-02 21:32 | 2026-08-02 21:32 | Fire | Y | Fair | No | Cute tree from line and repair 2 span of secondary line used 60 ft of # 2 aa wire and replace a 25 KVA transformer fuse with a 3 amps at pole
Outage | J.E.26.08.02490 | C001872023 | Edward Royal | KSAS | Completed | Load_268669 | Rockfort - 410 | 2026-08-02 13:32 | 2026-08-02 16:15 | 2026-08-02 17:59 | 2026-08-02 18:00 | 2026-08-02 17:59 | 2026-08-02 18:20 | 2026-08-02 18:20 | 2026-08-02 18:20 |  |  | Fair | No | Replaced 20A junction fuse 5A transformer fuse pole#0002780
Outage | J.E.26.08.03374 | C001872022 | Kenroy Dale | Manchester | Completed | Load_255644 | Porus - 310 | 2026-08-02 13:32 | 2026-08-02 13:32 | 2026-08-02 16:12 | 2026-08-02 16:38 | 2026-08-02 18:19 | 2026-08-02 18:41 | 2026-08-02 18:42 | 2026-08-02 18:42 |  |  | Fair | No | Area checked and found with supply call related to earlier outage today
Outage | J.E.26.08.03433 | C001872024 | Richman Whyte | Westmoreland | Completed | Load_268175 | Paradise - 110 | 2026-08-02 13:46 | 2026-08-02 13:47 | 2026-08-02 15:01 | 2026-08-02 15:02 | 2026-08-02 15:01 | 2026-08-02 15:01 | 2026-08-02 15:02 | 2026-08-02 15:02 |  |  | Fair | No | Replace ten amp junction fuse
Outage | J.E.26.08.03400 | C001872025 | Steven Ennis | KSAS | Completed | Load_249873 | Hunts Bay - 510 | 2026-08-02 14:03 | 2026-08-02 14:04 | 2026-08-02 17:49 | 2026-08-02 17:49 | 2026-08-02 17:49 | 2026-08-25 17:50 | 2026-08-02 17:50 | 2026-08-02 17:50 |  |  | Fair | No | Found 3 10amps fuse blown, no fault seen. Refused using 3 10amps .
Outage | J.E.26.08.02885 | C001872026 | Raymond Carr | St.Mary | Completed | Load_251918 | Oracabessa - 210 | 2026-08-02 14:04 | 2026-08-03 07:22 | 2026-08-03 08:43 | 2026-08-03 08:43 | 2026-08-03 08:43 | 2026-08-03 08:00 | 2026-08-03 08:44 | 2026-08-03 08:44 |  |  | SevereWind | No | Customer reported that supply was restored.
Outage | J.E.26.08.03426 | C001872028 | Clyde Brown | Clarendon | Completed | Load_263552 | Parnassus - 210 | 2026-08-02 14:05 | 2026-08-02 14:06 | 2026-08-02 15:12 | 2026-08-02 18:25 | 2026-08-02 18:25 | 2026-08-02 19:55 | 2026-08-02 20:46 | 2026-08-02 20:46 | BrokenWire |  | Fair | No | Broken 3 wire service same spliced and retention with 16ft-#6 service wire voltage left 112/112 and 225V
Outage | J.E.26.08.03455 | C001872029 | Raymond Carr | St.Mary | Completed | Load_256176 | Oracabessa - 210 | 2026-08-02 14:05 | 2026-08-03 07:22 | 2026-08-03 09:16 | 2026-08-03 09:17 | 2026-08-03 10:00 | 2026-08-03 09:41 | 2026-08-03 10:02 | 2026-08-03 10:02 |  |  | Fair | No | Digicel rep reported supply is okay.
Non-Outage | J.E.26.08.02812 | C001872030 | Dwayne Cohen | KSAN | Completed | Load_239894 | Constant Spring - 210 | 2026-08-02 14:07 | 2026-08-02 14:08 | 2026-08-02 14:13 | 2026-08-02 14:13 | 2026-08-02 14:30 | 2026-08-02 15:05 | 2026-08-02 15:07 | 2026-08-02 15:07 |  |  | Fair | No | Change defective arrester and refuse 8amps transformer link, supply is now restore.
Outage | J.E.26.08.01933 | C001872031 | Steven Ennis | KSAS | Completed | Load_249873 | Hunts Bay - 510 | 2026-08-02 14:09 | 2026-08-02 14:10 | 2026-08-02 17:51 | 2026-08-02 17:51 | 2026-08-02 17:51 | 2026-08-02 17:51 | 2026-08-02 17:52 | 2026-08-02 17:52 |  |  | Fair | No | Premises found okay and with supply
Outage | J.E.26.08.02791 | C001872032 | Nickolas Rodriques | St.Catherine | Completed | Load_258321 | Tredegar - 210 | 2026-08-02 14:11 | 2026-08-02 14:12 | 2026-08-02 14:22 | 2026-08-02 14:31 | 2026-08-02 14:31 | 2026-08-02 14:46 | 2026-08-02 14:55 | 2026-08-02 14:55 | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Checked and found a 30 amp and a 20 amp fuses blown from same line caused by bird. Patrol and found nothing on line. Repaired by replacing the fuse after completing patrol.
Outage | J.E.26.08.02326 | C001872036 | Donald Cunningham | St.Catherine | Completed | Load_247500 | Tredegar - 510 | 2026-08-02 14:39 | 2026-08-02 15:47 | 2026-08-02 17:22 | 2026-08-02 17:23 | 2026-08-02 18:08 | 2026-08-02 18:09 | 2026-08-02 18:17 | 2026-08-02 18:17 |  |  | Fair | No | Premises found ok supply restored
Outage | J.E.26.08.03487 | C001872037 | Richard Samuda | Manchester | Completed | Load_264418 | Porus - 310 | 2026-08-02 14:43 | 2026-08-03 07:14 | 2026-08-03 07:34 | 2026-08-03 07:57 | 2026-08-03 08:15 | 2026-08-03 08:29 | 2026-08-03 08:32 | 2026-08-03 08:32 |  |  | Fair | No | Found ok
Outage | J.E.26.08.03529 | C001872038 | Hartley Chin | Clarendon | Completed | Load_249064 | May Pen - 110 | 2026-08-02 14:44 | 2026-08-02 15:50 | 2026-08-02 16:10 | 2026-08-02 16:17 | 2026-08-02 16:17 | 2026-08-02 16:17 | 2026-08-02 16:23 | 2026-08-02 16:23 | BrokenWire |  | SevereWind | No | Wrong parish … St. Ann
Outage | J.E.26.08.03550 | C001872041 | Clyde Brown | Clarendon | Completed | Load_253290 | Parnassus - 310 | 2026-08-02 15:02 | 2026-08-02 15:07 | 2026-08-02 15:12 | 2026-08-02 15:21 | 2026-08-02 15:20 | 2026-08-02 15:13 | 2026-08-02 15:22 | 2026-08-02 15:22 |  |  | Fair | No | Cannot be located customer not answering phone since last week
Outage | J.E.26.08.03569 | C001872040 | Clyde Brown | Clarendon | Completed | Load_406117 | Parnassus - 210 | 2026-08-02 15:02 | 2026-08-02 15:07 | 2026-08-02 15:12 | 2026-08-02 16:22 | 2026-08-02 17:20 | 2026-08-02 18:02 | 2026-08-02 18:10 | 2026-08-02 18:10 |  |  | SevereWind | No | Blown 30 amps junction fuse at Clarendon park caused by low primary conductor touching 3wire service line ,service lowered and blown fuse replaced
Outage | J.E.26.08.03573 | C001872042 | Rusean Allen | KSAS | Completed | Load_249201 | Cane River - 310 | 2026-08-02 15:06 | 2026-08-03 08:03 | 2026-08-03 12:27 | 2026-08-03 12:28 | 2026-08-03 12:52 | 2026-08-03 12:58 | 2026-08-03 12:58 | 2026-08-03 12:58 | BrokenWire |  | Fair | No | Hexing failure Hex04864 Defective service wire needs to changed customer has no power 300ft of #6 service wire required. Refer to field service department.
Outage | J.E.26.08.03559 | C001872044 | Kenroy Dale | Manchester | Completed | Load_301405 | Porus - 310 | 2026-08-02 15:22 | 2026-08-02 19:31 | 2026-08-02 21:50 | 2026-08-02 21:51 | 2026-08-02 22:23 | 2026-08-02 22:52 | 2026-08-02 22:55 | 2026-08-02 22:55 |  |  | Fair | No | Blown 5 amp fuse found for 50 kva transformer (twisted secondary) line patrol nothing found blown blown fuse was replaced and area now with supply
Outage | J.E.26.08.02316 | C001872045 | Rodclif Dawkins | St.Catherine | Completed | Load_262395 | Naggo Head - 510 | 2026-08-02 15:24 | 2026-08-02 15:25 | 2026-08-02 16:57 | 2026-08-02 16:58 | 2026-08-02 16:58 | 2026-08-02 16:58 | 2026-08-02 17:02 | 2026-08-02 17:02 |  |  | Fair | No | At location crew found blown fuse for single phase T-off . Patrol line section and found blown fuse for 25kva transformer. Crew observed defective lightening arrester. Arrester replaced found and replaced 15amp at junction and 25kva transformer, found and replaced 3amp . Area okay
Non-Outage | J.E.26.08.03280 | C001872046 | Richman Whyte |  | Completed |  |  | 2026-08-02 15:25 | 2026-08-02 15:44 | 2026-08-02 17:49 | 2026-08-02 17:50 | 2026-08-02 17:49 | 2026-08-02 17:50 | 2026-08-02 17:50 | 2026-08-02 17:50 |  |  | Fair | No | St James call
Outage | J.E.26.08.03112 | C001872047 | Raymond Carr | St.Mary | Completed | Load_265110 | Oracabessa - 210 | 2026-08-02 15:27 | 2026-08-03 07:22 | 2026-08-03 08:41 | 2026-08-03 08:42 | 2026-08-03 08:41 | 2026-08-03 08:00 | 2026-08-03 08:43 | 2026-08-03 08:43 |  |  | SevereWind | No | Customer reported that supply was restored .
Outage | J.E.26.08.03139 | C001872048 | Roxroy Needham | St.Mary | Completed | Load_243245 | Oracabessa - 210 | 2026-08-02 15:27 | 2026-08-02 15:28 | 2026-08-02 15:38 | 2026-08-02 15:48 | 2026-08-02 16:57 | 2026-08-02 18:23 | 2026-08-02 18:25 | 2026-08-02 18:25 |  |  | Fair | No | Change service wire used 70ft of # 6 service wire 6 pg clamp voltage left at meter 118-119-241
Outage | J.E.26.08.03035 | C001872049 | Richard Nicholas | St.Catherine | Completed |  |  | 2026-08-02 15:28 | 2026-08-02 15:49 | 2026-08-02 16:21 | 2026-08-02 16:21 | 2026-08-02 16:39 | 2026-08-02 17:14 | 2026-08-02 17:15 | 2026-08-02 17:15 |  |  | EarthMovement | No | Replaced blown 15amp junctions fuse on pole #517741
Non-Outage | J.E.26.08.03520 | C001872052 | Raymond Carr |  | Completed |  |  | 2026-08-02 15:29 | 2026-08-02 15:31 | 2026-08-02 16:36 | 2026-08-02 16:37 | 2026-08-02 17:56 | 2026-08-02 17:49 | 2026-08-02 17:58 | 2026-08-02 17:58 | BrokenWire |  | Fair | No | Customer reported that supply is okay.
Outage | J.E.26.08.02505 | C001872051 | Raymond Carr | St.Mary | Completed | Load_252354 | Highgate -110 | 2026-08-02 15:29 | 2026-08-02 15:31 | 2026-08-02 15:39 | 2026-08-02 15:39 | 2026-08-02 16:19 | 2026-08-02 16:32 | 2026-08-02 16:34 | 2026-08-02 16:34 |  |  | Fair | No | Blown junction fuse found, line patrol and found primary conductor dislodged, however due to leaning pole, unable to climb. Bucket truck needed.
Non-Outage | J.E.26.08.03127 | C001872056 | Raymond Carr |  | Completed |  |  | 2026-08-02 15:30 | 2026-08-02 15:32 | 2026-08-02 17:58 | 2026-08-02 17:58 | 2026-08-02 18:36 | 2026-08-02 18:21 | 2026-08-02 18:38 | 2026-08-02 18:38 | Fire |  | Fair | No | Several calls to contact number went unanswered.
Outage | J.E.26.08.03530 | C001872055 | Nickolas Rodriques | St.Catherine | Completed | Load_568940 | Twickenham - 310 | 2026-08-02 15:30 | 2026-08-02 17:02 | 2026-08-02 19:44 | 2026-08-02 19:52 | 2026-08-02 20:42 | 2026-08-02 21:13 | 2026-08-02 21:21 | 2026-08-02 21:21 |  |  | Fair | No | Found premises with electricity. The customer confirmed that the power outage was restored.
Outage | J.E.26.08.03098 | C001872062 | Rodclif Dawkins | St.Catherine | Completed | Load_253337 | Twickenham - 210 | 2026-08-02 15:33 | 2026-08-02 15:34 | 2026-08-02 16:43 | 2026-08-02 17:46 | 2026-08-02 17:46 | 2026-08-02 17:46 | 2026-08-02 17:47 | 2026-08-02 17:47 |  |  | Fair | No | Customer found okay
Outage | J.E.26.08.03446 | C001872061 | Rodclif Dawkins | Portmore | Completed | Load_266484 | Twickenham - 410 | 2026-08-02 15:33 | 2026-08-02 15:34 | 2026-08-02 17:02 | 2026-08-02 17:03 | 2026-08-02 17:43 | 2026-08-02 17:43 | 2026-08-02 17:45 | 2026-08-02 17:45 |  |  | Fair | No | Customer found okay at time of crew’s visit
Outage | J.E.26.08.03078 | C001872063 | Romeo Brissett | Hanover | Completed | Load_252019 | Orange Bay - 310 | 2026-08-02 15:34 | 2026-08-02 15:35 | 2026-08-02 16:02 | 2026-08-02 16:02 | 2026-08-02 16:02 | 2026-08-02 16:00 | 2026-08-02 16:07 | 2026-08-02 16:07 |  |  | Fair | No | Check and found ok
Non-Outage | J.E.26.08.03462 | C001872066 | Kaydon Taylor |  | Completed |  |  | 2026-08-02 15:36 | 2026-08-02 15:58 | 2026-08-02 20:35 | 2026-08-02 22:11 | 2026-08-02 22:11 | 2026-08-02 22:12 | 2026-08-02 22:12 | 2026-08-02 22:12 | BrokenPole |  | Fair | No | Streetlight
Outage | J.E.26.08.03084 | C001872068 | Antony Levy | KSAN | Completed | Load_258537 | Washington Blvd - 610 | 2026-08-02 15:41 | 2026-08-02 15:59 | 2026-08-02 16:13 | 2026-08-02 16:14 | 2026-08-02 17:28 | 2026-08-02 17:43 | 2026-08-02 17:44 | 2026-08-02 17:44 | Fire |  | Fair | No | Area inaccessible with truck van needed... twisted secondary very narrow lane.
Non-Outage | J.E.26.08.03477 | C001872071 | Kaydon Taylor |  | Completed |  |  | 2026-08-02 15:42 | 2026-08-02 15:57 | 2026-08-02 17:46 | 2026-08-02 17:46 | 2026-08-02 19:03 | 2026-08-02 20:33 | 2026-08-02 20:33 | 2026-08-02 20:33 | BrokenWire |  | Fair | No | Isolate 25kva transformer at pole #0000631 to carry out repair on broken neutral wire. 100’ of #2aaa conductor wire, 1 #2 preform and 3 clamps. Carry light bushing also
Outage | J.E.26.08.03376 | C001872073 | Antony Levy | KSAN | Completed | Load_257446 | Constant Spring - 210 | 2026-08-02 15:42 | 2026-08-02 15:55 | 2026-08-02 17:44 | 2026-08-02 17:45 | 2026-08-02 18:51 | 2026-08-02 18:52 | 2026-08-02 18:53 | 2026-08-02 18:53 |  |  | Fair | No | Premises found okay unable to reach customer by phone but check line section .
Outage | J.E.26.08.03459 | C001872072 | Christopher Edwards | KSAN | Completed | Load_292076 | Constant Spring - 310 | 2026-08-02 15:42 | 2026-08-03 07:13 | 2026-08-03 08:21 | 2026-08-03 08:42 | 2026-08-03 08:44 | 2026-08-03 09:57 | 2026-08-03 09:57 | 2026-08-03 09:57 |  |  | Fair | No | Unable to reach customer by phone Observed supply is in the area
Outage | J.E.26.08.03595 | C001872070 | Oshane Warren | Westmoreland | Completed | Load_256685 | Paradise - 310 | 2026-08-02 15:42 | 2026-08-02 16:03 | 2026-08-02 16:36 | 2026-08-02 16:37 | 2026-08-02 18:46 | 2026-08-02 19:01 | 2026-08-02 19:02 | 2026-08-02 19:02 |  |  | Fair | No | Internal problem advice to fix
Outage | J.E.26.08.03213 | C001872075 | Dwayne Cohen | KSAN | Completed | Load_555968 | Hope - 510 | 2026-08-02 15:43 | 2026-08-02 20:16 | 2026-08-02 20:26 | 2026-08-02 20:26 | 2026-08-02 21:25 | 2026-08-02 21:25 | 2026-08-02 21:26 | 2026-08-02 21:26 |  |  | Fair | No | Low hanging wires belonging to Flow & Digicel , customer were advised.
Outage | J.E.26.08.03439 | C001872074 | Antony Levy | KSAN | Completed | Load_574897 | Washington Blvd - 610 | 2026-08-02 15:43 | 2026-08-02 16:14 | 2026-08-02 22:40 | 2026-08-02 23:05 | 2026-08-02 23:06 | 2026-08-02 23:06 | 2026-08-02 23:07 | 2026-08-02 23:07 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.02558 | C001872077 | Dwayne Cohen | KSAN | Completed | Load_267839 | Constant Spring - 210 | 2026-08-02 15:44 | 2026-08-03 07:59 | 2026-08-03 08:48 | 2026-08-03 08:49 | 2026-08-03 09:07 | 2026-08-03 09:16 | 2026-08-03 09:16 | 2026-08-03 09:16 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.03579 | C001872080 | Omar King | St.Ann | Completed | Load_270007 | Roaring River - 210 | 2026-08-02 15:48 | 2026-08-02 16:26 | 2026-08-02 19:26 | 2026-08-02 19:26 | 2026-08-02 20:58 | 2026-08-02 21:06 | 2026-08-02 21:06 | 2026-08-02 21:06 |  |  | Fair | No | Found two 25 amp junction fuse blow cause by falling tree limb . Tree limb as been removed and fuse as been replaced area is now with supply
Non-Outage | J.E.26.07.27170 | C001872082 | Raheem Ricketts | Manchester | Completed | Load_270226 | Spur Tree - 210 | 2026-08-02 15:49 | 2026-08-02 15:55 | 2026-08-02 16:08 | 2026-08-02 16:23 | 2026-08-02 16:22 | 2026-08-02 16:23 | 2026-08-02 16:24 | 2026-08-02 16:24 |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.07.27742 | C001872083 | Raheem Ricketts | Manchester | Completed | Load_248014 | Spur Tree - 210 | 2026-08-02 15:49 | 2026-08-02 15:55 | 2026-08-02 16:08 | 2026-08-02 19:48 | 2026-08-02 19:48 | 2026-08-02 19:48 | 2026-08-02 19:48 | 2026-08-02 19:48 |  |  | Fair | No | Unable to communicate with customer
Non-Outage | J.E.26.07.31119 | C001872084 | Raheem Ricketts | Manchester | Completed | Load_242011 | Spur Tree - 210 | 2026-08-02 15:49 | 2026-08-02 15:55 | 2026-08-02 16:08 | 2026-08-02 20:02 | 2026-08-02 20:06 | 2026-08-02 21:04 | 2026-08-02 21:05 | 2026-08-02 21:05 |  | Y | Fair | No | Isolate 25kva to retention secondary neutral and remake transformer drop lead joint at pole
Non-Outage | J.E.26.07.39030 | C001872085 | Raheem Ricketts | Manchester | Completed | Load_302835 | Spur Tree - 210 | 2026-08-02 15:49 | 2026-08-02 15:55 | 2026-08-02 16:08 | 2026-08-02 21:25 | 2026-08-02 21:25 | 2026-08-02 21:26 | 2026-08-02 21:27 | 2026-08-02 21:27 |  |  | Fair | No | Unable To contact customer cell number went straight to voicemail after several calls
Non-Outage | J.E.26.08.00056 | C001872086 | Raheem Ricketts | Manchester | Completed | Load_292982 | Spur Tree - 210 | 2026-08-02 15:49 | 2026-08-02 15:55 | 2026-08-02 16:08 | 2026-08-02 21:06 | 2026-08-02 21:05 | 2026-08-02 21:06 | 2026-08-02 21:07 | 2026-08-02 21:07 |  |  | Fair | No | Customer requested daylight attention premises closed
Non-Outage | J.E.26.08.03392 | C001872087 | Wan Carlos Scarlett |  | Completed |  |  | 2026-08-02 15:58 | 2026-08-02 15:59 | 2026-08-02 16:23 | 2026-08-02 17:14 | 2026-08-02 17:14 | 2026-08-02 17:15 | 2026-08-02 17:15 | 2026-08-02 17:15 | Fire |  | Fair | No | Call related to outage earlier customer confirmed power supply has been restored
Non-Outage | J.E.26.08.00102 | C001872089 | Horace Malcolm |  | Completed |  |  | 2026-08-02 16:00 | 2026-08-02 16:01 | 2026-08-02 17:02 | 2026-08-02 17:03 | 2026-08-02 18:19 | 2026-08-02 18:37 | 2026-08-02 18:38 | 2026-08-02 18:38 |  |  | Fair | No | Check and found area ok unable to locate customer multiple calls to customer unavailable
Non-Outage | J.E.26.08.03508 | C001872088 | Kaydon Taylor |  | Completed |  |  | 2026-08-02 16:00 | 2026-08-02 16:13 | 2026-08-02 20:33 | 2026-08-02 20:33 | 2026-08-02 20:33 | 2026-08-02 20:33 | 2026-08-02 20:34 | 2026-08-02 20:34 | BrokenWire |  | Fair | No | Found okay
Outage | J.E.26.08.02368 | C001872090 | Nickolas Rodriques | St.Catherine | Completed | Load_239901 | Tredegar - 510 | 2026-08-02 16:01 | 2026-08-02 18:56 | 2026-08-02 22:44 | 2026-08-02 22:48 | 2026-08-02 23:37 | 2026-08-02 23:38 | 2026-08-02 23:40 | 2026-08-02 23:40 |  |  | Fair | No | Found customer with electricity. Customer confirmed that the power outage was restored earlier.
Outage | J.E.26.08.03694 | C001872091 | Richard Nicholas | St.Catherine | Completed | Load_248086 | Twickenham - 210 | 2026-08-02 16:01 | 2026-08-02 18:04 | 2026-08-02 20:59 | 2026-08-02 21:00 | 2026-08-02 21:31 | 2026-08-02 21:57 | 2026-08-02 21:59 | 2026-08-02 21:59 |  |  | Fair | No | Replaced blown 25amp x2 junctions fuse at 3phase T-off to the tax office.
Outage | J.E.26.08.03601 | C001872094 | Steven Ennis | KSAS | Completed | Load_267402 | Hunts Bay - 310 | 2026-08-02 16:05 | 2026-08-02 16:06 | 2026-08-02 16:26 | 2026-08-02 16:27 | 2026-08-02 16:30 | 2026-08-02 16:37 | 2026-08-02 16:38 | 2026-08-02 16:38 |  |  | Fair | No | Found 30amps fuse at junction blown,, line patrolled and no fault found… use 30amps fuse to close junction..
Outage | J.E.26.08.02992 | C001872095 | Omar King | St.Ann | Completed | Load_263359 | Roaring River - 410 | 2026-08-02 16:07 | 2026-08-02 16:26 | 2026-08-02 17:24 | 2026-08-02 17:24 | 2026-08-02 19:17 | 2026-08-02 19:24 | 2026-08-02 19:26 | 2026-08-02 19:26 |  |  | Fair | No | Found 10 amp junction fuse blow cause by bird fuse as been replaced area is now with supply
Non-Outage | J.E.26.08.01329 | C001872096 | Antony Levy |  | Completed |  |  | 2026-08-02 16:08 | 2026-08-02 16:16 | 2026-08-02 18:53 | 2026-08-02 18:54 | 2026-08-02 19:53 | 2026-08-02 19:53 | 2026-08-02 19:59 | 2026-08-02 19:59 | Fire |  | Fair | No | Premises found okay fire was during the rain last night.
Outage | J.E.26.08.01308 | C001872097 | Antony Levy | KSAS | Completed | Load_242584 | Duhaney - 310 | 2026-08-02 16:09 | 2026-08-02 18:02 | 2026-08-02 20:32 | 2026-08-02 20:32 | 2026-08-02 21:11 | 2026-08-02 21:28 | 2026-08-02 21:29 | 2026-08-02 21:29 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.02588 | C001872098 | Nickolas Rodriques | St.Catherine | Completed | Load_247812 | Twickenham - 310 | 2026-08-02 16:09 | 2026-08-02 16:13 | 2026-08-02 18:10 | 2026-08-02 18:19 | 2026-08-02 18:45 | 2026-08-02 19:13 | 2026-08-02 19:17 | 2026-08-02 19:17 |  |  | Fair | No | Checked and found a 25 amp junction fuse blown. Patrol and found nothing on line. Repaired by replacing the fuse after completing patrol.
Outage | J.E.26.07.39987 | C001872099 | Romeo Brissett | St.James | Completed | Load_238713 | Bogue - 510 | 2026-08-02 16:12 | 2026-08-02 16:13 | 2026-08-02 16:16 | 2026-08-02 16:17 | 2026-08-02 17:59 | 2026-08-02 19:00 | 2026-08-02 19:13 | 2026-08-02 19:13 |  |  | Fair | No | Spliced and retention customer service wire, used 30ft of#6 and 4 clamps, V/R 116-117-234
Outage | J.E.26.08.01410 | C001872100 | Edward Royal | KSAS | Completed | Load_261801 | Rockfort - 410 | 2026-08-02 16:16 | 2026-08-02 16:19 | 2026-08-02 18:35 | 2026-08-02 18:35 | 2026-08-02 18:35 | 2026-08-02 18:37 | 2026-08-02 18:38 | 2026-08-02 18:38 | BrokenPole |  | Fair | No | When arrived at the location the area was with supply. Premises found ok
Outage | J.E.26.08.01980 | C001872101 | Edward Royal | KSAS | Completed | Load_268171 | Rockfort - 210 | 2026-08-02 16:16 | 2026-08-02 16:19 | 2026-08-02 18:40 | 2026-08-02 18:41 | 2026-08-02 19:08 | 2026-08-02 19:22 | 2026-08-02 19:22 | 2026-08-02 19:22 |  |  | Fair | No | Replaced 4 junction fuse (25A)(30A)(20A)(20A) and 2 transformer fuse 2 (5A) pole #0211318
Outage | J.E.26.08.01265 | C001872105 | Edward Royal | KSAS | Completed | Load_243474 | Rockfort - 410 | 2026-08-02 16:17 | 2026-08-02 16:19 | 2026-08-02 20:01 | 2026-08-02 20:02 | 2026-08-02 20:06 | 2026-08-02 20:20 | 2026-08-02 20:22 | 2026-08-02 20:22 |  |  | Fair | No | Replaced 2 (30A)junction fuse pole #0081555
Outage | J.E.26.08.01467 | C001872107 | Edward Royal | KSAS | Completed | Load_267604 | Rockfort - 410 | 2026-08-02 16:17 | 2026-08-02 16:19 | 2026-08-02 19:37 | 2026-08-02 19:38 | 2026-08-02 19:48 | 2026-08-02 20:00 | 2026-08-02 20:01 | 2026-08-02 20:01 |  |  | Fair | No | Replaced 25kva transformer fuse (3A) pole #0167279
Outage | J.E.26.08.01499 | C001872106 | Edward Royal | KSAS | Completed | Load_258390 | Rockfort - 410 | 2026-08-02 16:17 | 2026-08-02 16:19 | 2026-08-02 19:31 | 2026-08-02 19:31 | 2026-08-02 19:31 | 2026-08-02 19:32 | 2026-08-02 19:32 | 2026-08-02 19:32 |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.08.01895 | C001872109 | Edward Royal | KSAS | Completed | Load_239504 | Rockfort - 410 | 2026-08-02 16:17 | 2026-08-02 16:19 | 2026-08-02 19:35 | 2026-08-02 19:36 | 2026-08-02 19:35 | 2026-08-02 19:36 | 2026-08-02 19:37 | 2026-08-02 19:37 |  |  | Fair | No | Premises found ok related to outage on crescent road
Outage | J.E.26.08.01931 | C001872103 | Edward Royal | KSAS | Completed | Load_259549 | Rockfort - 210 | 2026-08-02 16:17 | 2026-08-02 16:19 | 2026-08-02 19:25 | 2026-08-02 19:26 | 2026-08-02 19:25 | 2026-08-02 19:26 | 2026-08-02 19:27 | 2026-08-02 19:27 |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.08.02943 | C001872102 | Edward Royal | KSAS | Completed | Load_253224 | Rockfort - 210 | 2026-08-02 16:17 | 2026-08-02 16:19 | 2026-08-02 19:22 | 2026-08-02 19:23 | 2026-08-02 19:23 | 2026-08-02 19:23 | 2026-08-02 19:23 | 2026-08-02 19:23 |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.08.03491 | C001872104 | Edward Royal | KSAS | Completed | Load_259549 | Rockfort - 210 | 2026-08-02 16:17 | 2026-08-02 16:19 | 2026-08-02 19:27 | 2026-08-02 19:27 | 2026-08-02 19:27 | 2026-08-02 19:28 | 2026-08-02 19:28 | 2026-08-02 19:28 | Fire |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.08.01300 | C001872111 | Wan Carlos Scarlett | Portmore | Completed | Load_241406 | Naggo Head - 510 | 2026-08-02 16:19 | 2026-08-02 16:20 | 2026-08-02 16:52 | 2026-08-02 16:53 | 2026-08-02 16:52 | 2026-08-02 17:11 | 2026-08-02 17:14 | 2026-08-02 17:14 |  |  | Fair | No | Refuse 10 Amps junction pole#006384 nothing was found on primary line Refuse 25 KVA transformer with 3 amp fuse pole #006452 nothing was found on secondary line cause by lightning strike
Outage | J.E.26.08.02050 | C001872110 | Wan Carlos Scarlett | St.Catherine | Completed | Load_270121 | Naggo Head - 510 | 2026-08-02 16:19 | 2026-08-02 16:20 | 2026-08-02 17:37 | 2026-08-02 17:37 | 2026-08-02 18:02 | 2026-08-02 18:07 | 2026-08-02 18:08 | 2026-08-02 18:08 |  |  | Fair | No | Customer confirmed that power supply was restored check and found okay
Outage | J.E.26.08.03495 | C001872113 | Hopeton Henry | St.Thomas | Completed | Load_256603 | Good Year - 210 | 2026-08-02 16:20 | 2026-08-02 16:39 | 2026-08-02 17:41 | 2026-08-02 17:42 | 2026-08-02 20:51 | 2026-08-02 22:04 | 2026-08-02 22:05 | 2026-08-02 22:05 |  |  | Fair | No | Refuse 25 kva transformer for
Outage | J.E.26.08.03706 | C001872112 | Derrick Grubb | St.Thomas | Completed | Load_268030 | Lysson - 410 | 2026-08-02 16:20 | 2026-08-03 07:58 | 2026-08-03 11:20 | 2026-08-03 11:20 | 2026-08-03 11:39 | 2026-08-03 11:57 | 2026-08-03 11:57 | 2026-08-03 11:57 |  |  | Fair | No | Patrol, found no visible faults on the line and refuse one 10kva transformer at pole number 0005149. Power restored.
Outage | J.E.26.08.03494 | C001872114 | Hopeton Henry | St.Thomas | Completed | Load_269083 | Good Year - 210 | 2026-08-02 16:21 | 2026-08-02 16:39 | 2026-08-02 17:41 | 2026-08-02 22:05 | 2026-08-02 22:05 | 2026-08-02 22:05 | 2026-08-02 22:06 | 2026-08-02 22:06 |  |  | Fair | No | Refuse 25 kva transformer
Outage | J.E.26.08.03396 | C001872115 | Stephen Taylor | St.Thomas | Completed | Load_266649 | Lysson - 410 | 2026-08-02 16:24 | 2026-08-02 16:38 | 2026-08-02 17:46 | 2026-08-02 17:47 | 2026-08-02 17:46 | 2026-08-02 17:47 | 2026-08-02 17:48 | 2026-08-02 17:48 |  |  | Fair | No | Patrol area and power is in the area but several calls to single customer and no one answering the phone need more information to locate customer
Outage | J.E.26.08.02412 | C001872116 | Raymond Lewis | St.Ann | Completed | Load_268800 | Cardiff Hall - 210 | 2026-08-02 16:29 | 2026-08-02 16:35 | 2026-08-02 17:18 | 2026-08-02 17:19 | 2026-08-02 17:53 | 2026-08-02 18:48 | 2026-08-02 18:48 | 2026-08-02 18:48 | Fire |  | Fair | No | Open 25 Iva x former to spice and retention 2 span secondary neutral
Outage | J.E.26.08.02665 | C001872117 | Raymond Lewis | St.Ann | Completed | Load_573812 | Cardiff Hall - 210 | 2026-08-02 16:29 | 2026-08-02 16:33 | 2026-08-02 18:52 | 2026-08-02 18:52 | 2026-08-02 19:00 | 2026-08-02 19:01 | 2026-08-02 19:02 | 2026-08-02 19:02 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.03554 | C001872123 | Raymond Lewis | St.Ann | Completed | Load_294276 | Cardiff Hall - 210 | 2026-08-02 16:30 | 2026-08-02 16:33 | 2026-08-02 19:11 | 2026-08-02 19:12 | 2026-08-02 20:19 | 2026-08-02 20:33 | 2026-08-02 20:34 | 2026-08-02 20:34 |  |  | Fair | No | Patrol primary line refuse and close 25 A junction fuse
Outage | J.E.26.08.02063 | C001872125 | Raymond Lewis | St.Ann | Completed | Load_573804 | Cardiff Hall - 210 | 2026-08-02 16:32 | 2026-08-02 16:33 | 2026-08-02 19:03 | 2026-08-02 19:04 | 2026-08-02 19:03 | 2026-08-02 19:05 | 2026-08-02 19:05 | 2026-08-02 19:05 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.02117 | C001872127 | Raymond Lewis | St.Ann | Completed | Load_261621 | Cardiff Hall - 210 | 2026-08-02 16:32 | 2026-08-02 16:33 | 2026-08-02 19:05 | 2026-08-02 19:05 | 2026-08-02 19:07 | 2026-08-02 19:08 | 2026-08-02 19:08 | 2026-08-02 19:08 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.03271 | C001872128 | Raymond Lewis | St.Ann | Completed | Load_268800 | Cardiff Hall - 210 | 2026-08-02 16:35 | 2026-08-02 16:36 | 2026-08-02 18:48 | 2026-08-02 18:49 | 2026-08-02 18:48 | 2026-08-02 18:51 | 2026-08-02 18:51 | 2026-08-02 18:51 | BrokenWire |  | Fair | No | Supply restored
Non-Outage | J.E.26.08.02587 | C001872129 | Omar King |  | Completed |  |  | 2026-08-02 16:37 | 2026-08-02 16:37 | 2026-08-02 20:58 | 2026-08-03 02:22 | 2026-08-03 02:22 | 2026-08-03 02:22 | 2026-08-03 02:22 | 2026-08-03 02:22 | BrokenWire |  | Fair | No | Found secondary neutral broken unable to carry out repair due to gully and heavy bush in the area need daylight attention majority customer as been restored
Outage | J.E.26.08.03529 | C001872131 | Omar King | Clarendon | Completed | Load_249064 | May Pen - 110 | 2026-08-02 16:47 | 2026-08-02 16:48 | 2026-08-02 20:58 | 2026-08-02 23:19 | 2026-08-03 01:12 | 2026-08-03 02:21 | 2026-08-03 02:22 | 2026-08-03 02:22 | BrokenWire |  | Fair | No | Found secondary neutral broken unable to carry out repair due to gully and heavy bush in the area need daylight attention majority customer as been restored
Outage | J.E.26.08.03743 | C001872132 | Nickolas Rodriques | St.Catherine | Completed | Load_242685 | Twickenham - 310 | 2026-08-02 16:48 | 2026-08-02 18:52 | 2026-08-02 21:27 | 2026-08-02 21:29 | 2026-08-02 22:22 | 2026-08-02 22:41 | 2026-08-02 22:43 | 2026-08-02 22:43 |  |  | Fair | No | Power restored. Found customer with electricity.
Outage | J.E.26.08.03714 | C001872133 | Shamour Haughton | St.James | Completed | Load_303189 | Bogue - 310 | 2026-08-02 16:49 | 2026-08-02 16:50 | 2026-08-02 18:53 | 2026-08-02 18:53 | 2026-08-02 18:53 | 2026-08-02 18:53 | 2026-08-02 18:53 | 2026-08-02 18:53 |  |  | Fair | No | Related to previous call
Outage | J.E.26.08.01332 | C001872134 | Nickolas Rodriques | St.Catherine | Completed | Load_269823 | Tredegar - 410 | 2026-08-02 16:50 | 2026-08-02 16:54 | 2026-08-02 17:01 | 2026-08-02 17:19 | 2026-08-02 17:26 | 2026-08-02 18:08 | 2026-08-02 18:09 | 2026-08-02 18:09 |  |  | Fair | No | Checked and found two junction fuses blown, a 30 amp and 15 amp from the same line. Patrol and found nothing on line. Repaired by replacing the fuses after completing patrol.
Non-Outage | J.E.26.08.00636 | C001872136 | Michael Christian | St.James | Completed | Load_253053 | Queens Drive - 310 | 2026-08-02 16:51 | 2026-08-02 16:52 | 2026-08-02 17:22 | 2026-08-02 19:58 | 2026-08-02 20:39 | 2026-08-02 20:55 | 2026-08-02 20:55 | 2026-08-02 20:55 | BangingWires |  | Fair | No | Check and found okay no banging wire found
Non-Outage | J.E.26.08.00739 | C001872135 | Michael Christian | St.James | Completed | Load_252519 | Queens Drive - 710 | 2026-08-02 16:51 | 2026-08-02 16:52 | 2026-08-02 17:22 | 2026-08-02 20:55 | 2026-08-02 22:00 | 2026-08-02 22:17 | 2026-08-02 22:17 | 2026-08-02 22:17 |  |  | Fair | No | Use 1 clamp at customer service wire at pole voltage 112 114 227 at pothead
Non-Outage | J.E.26.08.00821 | C001872137 | Michael Christian | St.James | Completed | Load_248508 | Rose Hall - 210 | 2026-08-02 16:51 | 2026-08-02 16:52 | 2026-08-02 17:22 | 2026-08-02 19:11 | 2026-08-02 19:54 | 2026-08-02 19:56 | 2026-08-02 19:56 | 2026-08-02 19:56 |  |  | Fair | No | Check and found okay voltage 111 113 226 at pothead
Non-Outage | J.E.26.08.03198 | C001872138 | Michael Christian | St.James | Completed | Load_260155 | Queens Drive - 710 | 2026-08-02 16:51 | 2026-08-02 16:52 | 2026-08-02 17:22 | 2026-08-02 17:27 | 2026-08-02 18:02 | 2026-08-02 19:10 | 2026-08-02 19:10 | 2026-08-02 19:10 |  |  | Fair | No | Found customer service wire broken use 2 clamps at customer service wire at pole voltage 111 110 222 at pothead
Outage | J.E.26.08.02882 | C001872139 | Wan Carlos Scarlett | Portmore | Completed | Load_254462 | Twickenham - 410 | 2026-08-02 16:51 | 2026-08-02 16:52 | 2026-08-02 17:16 | 2026-08-02 17:16 | 2026-08-02 17:17 | 2026-08-02 17:25 | 2026-08-02 17:26 | 2026-08-02 17:26 |  |  | Fair | No | Call related to outage earlier customer confirmed that power supply has been restored check and found okay
Non-Outage | J.E.26.08.00372 | C001872141 | Dwayne Samuels | Trelawny | Completed | Load_259170 | Duncans - 210 | 2026-08-02 16:53 | 2026-08-02 16:54 | 2026-08-02 20:37 | 2026-08-02 20:38 | 2026-08-02 21:22 | 2026-08-02 21:38 | 2026-08-02 21:39 | 2026-08-02 21:39 |  |  | Fair | No | Check and found voltage ok 116v 114v 230v
Non-Outage | J.E.26.08.02957 | C001872142 | Dwayne Samuels | Trelawny | Completed | Load_252699 | Duncans - 210 | 2026-08-02 16:53 | 2026-08-02 16:54 | 2026-08-02 19:43 | 2026-08-02 19:44 | 2026-08-02 20:22 | 2026-08-02 20:37 | 2026-08-02 20:37 | 2026-08-02 20:37 |  |  | Fair | No | Check and found working ok voltage found 119v/117v/236v
Outage | J.E.26.08.02826 | C001872140 | Wan Carlos Scarlett | Portmore | Completed | Load_238584 | Twickenham - 410 | 2026-08-02 16:53 | 2026-08-02 16:54 | 2026-08-02 17:07 | 2026-08-02 17:26 | 2026-08-02 17:26 | 2026-08-02 17:35 | 2026-08-02 17:36 | 2026-08-02 17:36 |  |  | Fair | No | Call related to outage earlier customer confirmed that power supply has been restored check and found okay
Outage | J.E.26.08.03762 | C001872143 | Ricky Hall | St.Catherine | Completed | Load_249625 | Tredegar - 310 | 2026-08-02 17:02 | 2026-08-02 17:06 | 2026-08-02 18:09 | 2026-08-02 18:10 | 2026-08-02 18:19 | 2026-08-02 19:29 | 2026-08-02 19:40 | 2026-08-02 19:40 | Fire |  | SevereWind | No | Splice and retention broken secondary lines use 1 automatic splice 2 clamps
Outage | J.E.26.08.02912 | C001872144 | Raymond Lewis | St.Ann | Completed | Load_261713 | Cardiff Hall - 310 | 2026-08-02 17:05 | 2026-08-02 17:06 | 2026-08-02 20:19 | 2026-08-02 20:55 | 2026-08-02 20:55 | 2026-08-02 20:56 | 2026-08-02 20:56 | 2026-08-02 20:56 | Fire |  | Fair | No | Phone not answering and no good directions
Non-Outage | J.E.26.08.02920 | C001872145 | Ricky Hall |  | Completed |  |  | 2026-08-02 17:07 | 2026-08-02 17:07 | 2026-08-02 18:08 | 2026-08-02 18:09 | 2026-08-02 18:08 | 2026-08-02 18:08 | 2026-08-02 18:09 | 2026-08-02 18:09 |  |  | Fair | No | Call associated with outage #03010
Outage | J.E.26.08.01715 | C001872147 | Rodclif Dawkins | St.Catherine | Completed | Load_244929 | Duhaney - 210 | 2026-08-02 17:12 | 2026-08-02 17:13 | 2026-08-02 17:47 | 2026-08-02 18:56 | 2026-08-02 19:37 | 2026-08-02 20:00 | 2026-08-02 20:00 | 2026-08-02 20:00 |  |  | Fair | No | Found 1 blown fuse from 2phase line section at pole# 208587. Line section patrolled and crew found blown fuse on Single phase line section at, no faults seen at time found. At 2 phase junction found and replaced 20amp. At single phase found and replaced 15amp. . Area found okay
Outage | J.E.26.08.03480 | C001872148 | Collin Robinson | Portland | Completed | Load_258764 | Port Antonio - 410 | 2026-08-02 17:14 | 2026-08-02 17:17 | 2026-08-02 17:35 | 2026-08-02 17:36 | 2026-08-02 18:13 | 2026-08-02 18:22 | 2026-08-02 18:22 | 2026-08-02 18:22 |  |  | Rains | No | Replace 2 amps fuse at pole 565414
Outage | J.E.26.08.02257 | C001872149 | Jvunalle Scully | St.Catherine | Completed | Load_243415 | Naggo Head - 510 | 2026-08-02 17:15 | 2026-08-02 17:16 | 2026-08-02 17:20 | 2026-08-02 17:21 | 2026-08-02 17:44 | 2026-08-02 17:44 | 2026-08-02 17:45 | 2026-08-02 17:45 |  |  | Fair | No | Related to power outage earlier
Outage | J.E.26.08.02311 | C001872151 | Jvunalle Scully | St.Catherine | Completed | Load_557082 | Naggo Head - 510 | 2026-08-02 17:16 | 2026-08-02 17:17 | 2026-08-02 20:19 | 2026-08-02 20:20 | 2026-08-02 20:49 | 2026-08-02 20:57 | 2026-08-02 20:58 | 2026-08-02 20:58 |  |  | Fair | No | After customer did internal checks and found supply was restored from earlier
Outage | J.E.26.08.02327 | C001872152 | Jvunalle Scully | St.Catherine | Completed | Load_266808 | Naggo Head - 510 | 2026-08-02 17:16 | 2026-08-02 17:17 | 2026-08-02 20:59 | 2026-08-02 21:00 | 2026-08-02 22:05 | 2026-08-02 22:05 | 2026-08-02 22:05 | 2026-08-02 22:05 |  |  | Fair | No | Ok
Outage | J.E.26.08.03096 | C001872150 | Collin Robinson | Portland | Completed | Load_249256 | Port Antonio - 410 | 2026-08-02 17:16 | 2026-08-02 17:17 | 2026-08-03 09:25 | 2026-08-03 09:26 | 2026-08-03 09:26 | 2026-08-03 09:29 | 2026-08-03 09:29 | 2026-08-03 09:29 |  |  | Rains | No | Information received customer that issue was resolve
Outage | J.E.26.08.02343 | C001872153 | Jvunalle Scully | St.Catherine | Completed | Load_238784 | Naggo Head - 510 | 2026-08-02 17:17 | 2026-08-02 17:18 | 2026-08-02 19:40 | 2026-08-02 19:40 | 2026-08-02 20:18 | 2026-08-02 20:18 | 2026-08-02 20:19 | 2026-08-02 20:19 |  |  | Fair | No | Found with supply
Outage | J.E.26.08.02364 | C001872154 | Jvunalle Scully | St.Catherine | Completed | Load_250373 | Naggo Head - 510 | 2026-08-02 17:17 | 2026-08-02 17:18 | 2026-08-02 17:45 | 2026-08-02 17:46 | 2026-08-02 19:03 | 2026-08-02 19:37 | 2026-08-02 19:39 | 2026-08-02 19:39 |  |  | Fair | No | Lightning arrester failed. Same replaced and line energized supplying 1 25kva transformer. 5amp fuse used
Outage | J.E.26.08.03312 | C001872156 | Collin Robinson | Portland | Completed | Load_353327 | Port Antonio - 310 | 2026-08-02 17:18 | 2026-08-02 17:19 | 2026-08-02 20:23 | 2026-08-02 20:23 | 2026-08-02 21:05 | 2026-08-02 21:06 | 2026-08-02 21:07 | 2026-08-02 21:07 |  |  | Fair | No | Unable to locate customer base on directions.
Outage | J.E.26.08.03790 | C001872157 | Collin Robinson | Portland | Completed | Load_266274 | Port Antonio - 410 | 2026-08-02 17:18 | 2026-08-02 17:19 | 2026-08-02 18:22 | 2026-08-02 18:23 | 2026-08-02 19:03 | 2026-08-02 19:09 | 2026-08-02 19:09 | 2026-08-02 19:09 |  |  | Fair | No | Patrol secondary line section and found open secondary conductor phase and neutral twist together .entangle conductors and reset 10 KVA transformer
Outage | J.E.26.08.03798 | C001872158 | Richard Nicholas | St.Catherine | Completed | Load_256489 | Tredegar - 410 | 2026-08-02 17:20 | 2026-08-02 18:22 | 2026-08-02 21:59 | 2026-08-02 21:59 | 2026-08-02 22:19 | 2026-08-02 22:27 | 2026-08-02 22:30 | 2026-08-02 22:30 | Fire |  | Fair | No | At the intersection of old market st. and French st.pole #0009786 a burnt knife switch observed on the pole.the polymer on the road phase switch burnt.follow up to replace same.
Outage | J.E.26.08.03786 | C001872161 | Wan Carlos Scarlett | Portmore | Completed | Load_262495 | Naggo Head - 610 | 2026-08-02 17:40 | 2026-08-02 17:42 | 2026-08-02 18:08 | 2026-08-02 18:09 | 2026-08-02 18:34 | 2026-08-02 18:37 | 2026-08-02 18:38 | 2026-08-02 18:38 |  |  | Fair | No | Pole changing in place maintenance crew on site
Outage | J.E.26.08.03736 | C001872162 | Edward Royal | KSAS | Completed | Load_253224 | Rockfort - 210 | 2026-08-02 17:41 | 2026-08-02 17:42 | 2026-08-02 19:32 | 2026-08-02 19:33 | 2026-08-02 19:32 | 2026-08-02 19:33 | 2026-08-02 19:33 | 2026-08-02 19:33 |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.08.03819 | C001872163 | Rodclif Dawkins | St.Catherine | Completed | Load_269801 | Twickenham - 210 | 2026-08-02 17:44 | 2026-08-02 17:46 | 2026-08-02 18:01 | 2026-08-02 18:02 | 2026-08-02 18:26 | 2026-08-02 18:37 | 2026-08-02 18:42 | 2026-08-02 18:42 | BrokenWire |  | Fair | No | Found blown fuse for single phase line section. Line section patrolled, crew observed no faults at time . Found 30amp replaced with 25amp. Area found okay
Outage | J.E.26.08.01755 | C001872166 | Rodclif Dawkins | St.Catherine | Completed | Load_248173 | Twickenham - 210 | 2026-08-02 17:46 | 2026-08-02 17:46 | 2026-08-02 22:19 | 2026-08-02 22:20 | 2026-08-02 22:20 | 2026-08-02 22:20 | 2026-08-02 22:20 | 2026-08-02 22:20 |  |  | Fair | No | Found 1 blown junction fuse from 2phase line section at. Line section patrolled and crew found 1 blown fuse on single phase line section and blown fuse for 100kva transformer. No faults seen at time of patrol. Found and replaced 40amp at 2phase junction. At single phase found 8amp. Replaced with 5amp. 8amp was replaced at 100kva transformer. Area okay
Outage | J.E.26.08.01777 | C001872167 | Rodclif Dawkins | St.Catherine | Completed | Load_246443 | Twickenham - 210 | 2026-08-02 17:46 | 2026-08-02 17:46 | 2026-08-02 22:21 | 2026-08-02 22:21 | 2026-08-02 22:21 | 2026-08-02 22:21 | 2026-08-02 22:21 | 2026-08-02 22:21 |  |  | Fair | No | Found 1 blown junction fuse from 2phase line section at. Line section patrolled and crew found 1 blown fuse on single phase line section and blown fuse for 100kva transformer. No faults seen at time of patrol. Found and replaced 40amp at 2phase junction. At single phase found 8amp. Replaced with 5amp. 8amp was replaced at 100kva transformer. Area okay
Outage | J.E.26.08.01782 | C001872164 | Rodclif Dawkins | St.Catherine | Completed | Load_257164 | Twickenham - 210 | 2026-08-02 17:46 | 2026-08-02 17:46 | 2026-08-02 21:12 | 2026-08-02 21:12 | 2026-08-02 22:13 | 2026-08-02 22:13 | 2026-08-02 22:19 | 2026-08-02 22:19 |  |  | Fair | No | Found 1 blown junction fuse from 2phase line section at. Line section patrolled and crew found 1 blown fuse on single phase line section and blown fuse for 100kva transformer. No faults seen at time of patrol. Found and replaced 40amp at 2phase junction. At single phase found 8amp. Replaced with 5amp. 8amp was replaced at 100kva transformer. Area okay
Outage | J.E.26.08.01908 | C001872170 | Steven Ennis | KSAS | Completed | Load_261950 | Hunts Bay - 510 | 2026-08-02 17:46 | 2026-08-02 17:47 | 2026-08-02 19:15 | 2026-08-02 19:15 | 2026-08-02 19:15 | 2026-08-02 19:15 | 2026-08-02 19:15 | 2026-08-02 19:15 |  |  | Fair | No | Found 3 span open secondary broken .. use 8 one bolt clamps, and 30ft AAAC to make repairs..
Outage | J.E.26.08.02941 | C001872165 | Fitzroy Turner | KSAS | Completed | Load_269005 | Hunts Bay - 310 | 2026-08-02 17:46 | 2026-08-03 07:58 | 2026-08-03 13:36 | 2026-08-03 13:36 | 2026-08-03 14:03 | 2026-08-03 14:04 | 2026-08-03 14:05 | 2026-08-03 14:05 |  |  | Fair | No | Found 15kVA transformer switches top burnt off use 2ft of #4 copper to carry out repair supply restored to areas
Outage | J.E.26.08.03342 | C001872169 | Fitzroy Turner | KSAS | Completed | Load_301272 | Hunts Bay - 510 | 2026-08-02 17:46 | 2026-08-03 07:58 | 2026-08-03 11:54 | 2026-08-03 12:59 | 2026-08-03 13:00 | 2026-08-03 13:23 | 2026-08-03 13:25 | 2026-08-03 13:25 |  |  | Fair | No | Found two 10 amps fuses blown for bank of three 100kva transformer replaced two 10amps fuse supply restored to areas
Outage | J.E.26.08.03735 | C001872171 | Antony Levy | KSAN | Completed | Load_266172 | Washington Blvd - 610 | 2026-08-02 17:49 | 2026-08-02 18:10 | 2026-08-02 19:59 | 2026-08-02 20:00 | 2026-08-02 20:29 | 2026-08-02 20:30 | 2026-08-02 20:30 | 2026-08-02 20:30 |  |  | Fair | No | Customer meter was off power restored.
Outage | J.E.26.08.03532 | C001872172 | Shamour Haughton | St.James | Completed | Load_303189 | Bogue - 310 | 2026-08-02 17:50 | 2026-08-02 17:51 | 2026-08-02 18:00 | 2026-08-02 18:01 | 2026-08-02 18:49 | 2026-08-02 18:49 | 2026-08-02 18:51 | 2026-08-02 18:51 |  |  | Fair | No | Found 1,50kva fuse blown and switch barrel burn up, change barrel and refuse 50kva use 1,5amp fuse
Outage | J.E.26.08.03218 | C001872175 | Fitzroy Turner | KSAS | Completed | Load_257326 | Cane River - 610 | 2026-08-02 17:57 | 2026-08-02 17:57 | 2026-08-02 20:59 | 2026-08-02 20:59 | 2026-08-02 20:59 | 2026-08-02 20:59 | 2026-08-02 21:00 | 2026-08-02 21:00 | BrokenPole |  | Fair | No | Maintenance crew in areas working
Outage | J.E.26.08.03859 | C001872178 | Dwayne Cohen | KSAN | Completed | Load_252660 | Hope - 410 | 2026-08-02 18:15 | 2026-08-02 19:17 | 2026-08-02 19:21 | 2026-08-02 19:22 | 2026-08-02 20:09 | 2026-08-02 20:09 | 2026-08-02 20:13 | 2026-08-02 20:13 | Fire |  | Fair | No | Customer found okay, customer mention that electrician resulted the issue.
Outage | J.E.26.08.02068 | C001872180 | Jvunalle Scully | St.Catherine | Completed | Load_257588 | Naggo Head - 510 | 2026-08-02 18:21 | 2026-08-02 18:22 | 2026-08-02 22:14 | 2026-08-02 22:15 | 2026-08-02 22:57 | 2026-08-02 22:57 | 2026-08-02 22:58 | 2026-08-02 22:58 |  |  | Fair | No | Ok
Non-Outage | J.E.26.08.03870 | C001872181 | Richard Nicholas |  | Completed |  |  | 2026-08-02 18:29 | 2026-08-02 18:47 | 2026-08-02 22:30 | 2026-08-02 22:30 | 2026-08-02 22:48 | 2026-08-02 23:14 | 2026-08-02 23:15 | 2026-08-02 23:15 |  |  | Fair | No | Replaced blown 50kva transformer 5amp fuse on pole #0097213
Outage | J.E.26.08.03836 | C001872182 | Dwayne Samuels | Trelawny | Completed | Load_259857 | Martha Brae - 110 | 2026-08-02 18:30 | 2026-08-02 18:31 | 2026-08-02 18:41 | 2026-08-02 18:47 | 2026-08-02 19:18 | 2026-08-02 19:43 | 2026-08-02 19:43 | 2026-08-02 19:43 |  |  | Fair | No | Corrosion at pothead was the cause of customer no supply use 1 one bolt clamp at same for repair voltage found on arrival 121v/110v/226v voltage left 120v/120v/240v
Outage | J.E.26.08.03882 | C001872184 | Hopeton Henry | St.Thomas | Completed | Load_256603 | Good Year - 210 | 2026-08-02 18:37 | 2026-08-02 18:38 | 2026-08-02 22:07 | 2026-08-02 22:08 | 2026-08-02 22:11 | 2026-08-02 22:12 | 2026-08-02 22:12 | 2026-08-02 22:12 |  |  | Fair | No | Check and found ok
Outage | J.E.26.08.02556 | C001872190 | Andre Smith | KSAN | Completed | Load_264650 | Washington Blvd - 310 | 2026-08-02 18:52 | 2026-08-02 18:53 | 2026-08-02 21:32 | 2026-08-02 21:32 | 2026-08-02 21:52 | 2026-08-02 22:05 | 2026-08-02 22:05 | 2026-08-02 22:05 |  |  | Fair | No | Premises found okay supply restored already
Outage | J.E.26.08.03729 | C001872189 | Andre Smith | KSAN | Completed | Load_268663 | Washington Blvd - 710 | 2026-08-02 18:52 | 2026-08-02 18:53 | 2026-08-02 19:35 | 2026-08-02 19:36 | 2026-08-02 20:24 | 2026-08-02 21:28 | 2026-08-02 21:28 | 2026-08-02 21:28 |  |  | Fair | No | Premises found okay supply restored already
Outage | J.E.26.08.03833 | C001872191 | Andre Smith | KSAN | Completed | Load_242589 | Washington Blvd - 710 | 2026-08-02 18:52 | 2026-08-02 18:53 | 2026-08-02 19:30 | 2026-08-02 19:31 | 2026-08-02 19:31 | 2026-08-02 19:31 | 2026-08-02 19:31 | 2026-08-02 19:31 |  |  | Fair | No | Replace blown junction fuses cause by kite on conductors 15A/2 and 30A/2 supply restored
Outage | J.E.26.08.03858 | C001872188 | Edward Royal | KSAN | Completed | Load_265054 | Washington Blvd - 710 | 2026-08-02 18:52 | 2026-08-03 08:10 | 2026-08-03 14:43 | 2026-08-03 14:43 | 2026-08-03 14:43 | 2026-08-03 14:46 | 2026-08-03 14:47 | 2026-08-03 14:47 | LowHangingWires |  | Fair | No | Class 6 30 ft rotten pole on it open secondary tripe x service cable reffered to maintenance
Outage | J.E.26.08.03876 | C001872187 | Andre Smith | KSAN | Completed | Load_293862 | Washington Blvd - 710 | 2026-08-02 18:52 | 2026-08-02 18:53 | 2026-08-02 18:59 | 2026-08-02 19:00 | 2026-08-02 19:28 | 2026-08-02 19:30 | 2026-08-02 19:30 | 2026-08-02 19:30 |  |  | Fair | No | Replace blown junction fuses cause by kite on conductors 15A/2 and 30A/2 supply restored
Outage | J.E.26.08.03102 | C001872192 | Andre Smith | KSAS | Completed | Load_290946 | Hunts Bay - 810 | 2026-08-02 18:53 | 2026-08-02 18:53 | 2026-08-02 22:31 | 2026-08-02 22:31 | 2026-08-02 22:31 | 2026-08-02 22:31 | 2026-08-02 22:31 | 2026-08-02 22:31 |  |  | Fair | No | Supply restored with the assistance of callcenter
Outage | J.E.26.08.03184 | C001872193 | Andre Smith | KSAS | Completed | Load_245974 | Hunts Bay - 810 | 2026-08-02 18:53 | 2026-08-02 18:53 | 2026-08-02 22:05 | 2026-08-02 22:05 | 2026-08-02 22:30 | 2026-08-02 22:30 | 2026-08-02 22:31 | 2026-08-02 22:31 |  |  | Fair | No | Supply restored with the assistance of callcenter
Outage | J.E.26.08.03182 | C001872194 | Wan Carlos Scarlett | Portmore | Completed | Load_254722 | Twickenham - 410 | 2026-08-02 18:56 | 2026-08-02 18:57 | 2026-08-02 19:09 | 2026-08-02 19:10 | 2026-08-02 19:24 | 2026-08-02 20:10 | 2026-08-02 20:16 | 2026-08-02 20:16 |  |  | Fair | No | Refuse 10 Amp junction pole#006623 nothing was found on primary line refuse 50 KVA transformer with a 5 Amp nothing was found on secondary line cause by lightning strike
Outage | J.E.26.08.01311 | C001872198 | Wan Carlos Scarlett | Portmore | Completed | Load_254722 | Naggo Head - 510 | 2026-08-02 18:57 | 2026-08-02 18:57 | 2026-08-02 19:11 | 2026-08-02 20:29 | 2026-08-02 20:41 | 2026-08-02 20:43 | 2026-08-02 20:45 | 2026-08-02 20:45 |  |  | Fair | No | Call related to outage earlier customer confirmed that power supply has been restored
Outage | J.E.26.08.01421 | C001872196 | Wan Carlos Scarlett | Portmore | Completed | Load_250002 | Naggo Head - 510 | 2026-08-02 18:57 | 2026-08-02 18:57 | 2026-08-02 19:11 | 2026-08-02 20:16 | 2026-08-02 20:26 | 2026-08-02 20:28 | 2026-08-02 20:29 | 2026-08-02 20:29 |  |  | Fair | No | Call related to outage earlier customer confirmed that power supply has been restored check and found okay
Outage | J.E.26.08.01452 | C001872195 | Wan Carlos Scarlett | Portmore | Completed | Load_255767 | Naggo Head - 510 | 2026-08-02 18:57 | 2026-08-02 18:57 | 2026-08-02 20:29 | 2026-08-02 21:18 | 2026-08-02 21:18 | 2026-08-02 21:18 | 2026-08-02 21:20 | 2026-08-02 21:20 |  |  | Fair | No | Call related to outage earlier customer confirmed that power supply has been restored
Outage | J.E.26.08.03906 | C001872199 | Clyde Brown | Clarendon | Completed | Load_572086 | Parnassus - 310 | 2026-08-02 18:59 | 2026-08-02 19:01 | 2026-08-02 20:50 | 2026-08-02 20:50 | 2026-08-02 20:50 | 2026-08-02 20:50 | 2026-08-02 20:55 | 2026-08-02 20:55 |  |  | Fair | No | Exim box to sent to field service
Outage | J.E.26.08.03341 | C001872201 | Jvunalle Scully | St.Catherine | Completed | Load_556875 | Twickenham - 210 | 2026-08-02 19:18 | 2026-08-02 19:19 | 2026-08-02 22:58 | 2026-08-02 22:59 | 2026-08-02 22:58 | 2026-08-02 22:59 | 2026-08-02 23:00 | 2026-08-02 23:00 |  |  | Fair | No | No answer to phone
Outage | J.E.26.08.03912 | C001872203 | Andre Smith | KSAN | Completed | Load_245333 | Washington Blvd - 710 | 2026-08-02 19:27 | 2026-08-02 19:28 | 2026-08-02 19:32 | 2026-08-02 19:33 | 2026-08-02 19:33 | 2026-08-02 19:34 | 2026-08-02 19:34 | 2026-08-02 19:34 |  |  | Fair | No | Premises found okay supply restored already
Outage | J.E.26.08.03741 | C001872204 | Richard Samuda | Manchester | Completed | Load_261236 | Porus - 310 | 2026-08-02 19:29 | 2026-08-03 07:14 | 2026-08-03 08:32 | 2026-08-03 09:01 | 2026-08-03 09:00 | 2026-08-03 21:56 | 2026-08-03 09:56 | 2026-08-03 09:56 |  |  | Fair | No | Remake secondary upper phase jumper that was broken causing area to experience single phase using two 1bolt clamps and 3ft of aluminum #2 wire customer back to normal
Outage | J.E.26.08.01521 | C001872205 | Rodclif Dawkins | St.Catherine | Completed | Load_268043 | Twickenham - 210 | 2026-08-02 19:33 | 2026-08-02 19:34 | 2026-08-02 20:00 | 2026-08-02 20:01 | 2026-08-02 20:11 | 2026-08-02 20:46 | 2026-08-02 20:55 | 2026-08-02 20:55 |  |  | Fair | No | Found 1 blown junction fuse from 2phase line section. Line section patrolled and crew found 2 blown fuse for (2)50kva transformers on line section. No faults observed at time. Found and replaced 15amp at junction and at transformers (2) 5amp . Area okay
Outage | J.E.26.08.01253 | C001872209 | Wan Carlos Scarlett | Portmore | Completed | Load_248381 | Naggo Head - 510 | 2026-08-02 19:43 | 2026-08-03 10:06 | 2026-08-03 13:04 | 2026-08-03 14:00 | 2026-08-03 14:03 | 2026-08-03 14:13 | 2026-08-03 14:17 | 2026-08-03 14:17 |  |  | Fair | No | Call related to outage earlier J.E 26.08.04.125 power supply has been restored
Outage | J.E.26.08.01674 | C001872210 | Wan Carlos Scarlett | Portmore | Completed | Load_246869 | Naggo Head - 510 | 2026-08-02 19:43 | 2026-08-02 19:44 | 2026-08-02 21:20 | 2026-08-02 21:21 | 2026-08-02 21:42 | 2026-08-02 22:18 | 2026-08-02 22:39 | 2026-08-02 22:39 |  |  | Fair | No | Refuse 8 Amp junction no pole # was found nothing was found on primary line cause by lightning strike
Outage | J.E.26.08.03805 | C001872211 | Raymond Lewis | St.Ann | Completed | Load_269771 | Cardiff Hall - 310 | 2026-08-02 19:44 | 2026-08-02 19:45 | 2026-08-02 21:25 | 2026-08-02 21:33 | 2026-08-02 21:32 | 2026-08-02 21:40 | 2026-08-02 21:41 | 2026-08-02 21:41 |  |  | Fair | No | Refuse and close. 25A Junction fuse
Outage | J.E.26.08.03961 | C001872212 | Horace Malcolm | St.James | Completed | Load_292067 | Bogue - 610 | 2026-08-02 19:45 | 2026-08-02 19:47 | 2026-08-02 20:53 | 2026-08-02 20:54 | 2026-08-02 22:18 | 2026-08-02 22:52 | 2026-08-02 22:52 | 2026-08-02 22:52 |  |  | Fair | No | Unable to locate customer multiple phone calls to customer unavailable unable locate premises from directions given
Outage | J.E.26.08.03891 | C001872213 | Raymond Carr | St.Mary | Completed | Load_240997 | Highgate -110 | 2026-08-02 19:47 | 2026-08-02 19:48 | 2026-08-02 19:59 | 2026-08-02 20:00 | 2026-08-02 20:32 | 2026-08-02 20:04 | 2026-08-02 20:33 | 2026-08-02 20:33 | Fire |  | Fair | No | Customer reported that supply is okay, however streetlight is not working.
Outage | J.E.26.08.03908 | C001872214 | Raymond Carr | St.Mary | Completed | Load_249622 | Highgate -110 | 2026-08-02 19:47 | 2026-08-02 19:48 | 2026-08-02 20:34 | 2026-08-02 20:34 | 2026-08-02 20:57 | 2026-08-02 21:00 | 2026-08-02 20:59 | 2026-08-02 20:59 | BrokenWire |  | Fair | No | Several calls to contact number went unanswered.
Outage | J.E.26.08.03926 | C001872215 | Raymond Carr | St.Mary | Completed | Load_267206 | Highgate - 210 | 2026-08-02 19:47 | 2026-08-02 19:48 | 2026-08-02 20:59 | 2026-08-02 20:59 | 2026-08-02 22:03 | 2026-08-02 22:21 | 2026-08-02 22:17 | 2026-08-02 22:17 |  |  | Fair | No | Several calls to contact number went straight to voicemail.
Outage | J.E.26.08.03952 | C001872219 | Donald Cunningham | St.Catherine | Completed | Load_265928 | Tredegar - 510 | 2026-08-02 20:10 | 2026-08-02 20:50 | 2026-08-02 21:12 | 2026-08-02 21:12 | 2026-08-02 22:00 | 2026-08-02 22:37 | 2026-08-02 22:38 | 2026-08-02 22:38 |  |  | Fair | No | Blown junction fuse found and replace with 10 amp fuse
Outage | J.E.26.08.01462 | C001872222 | Edward Royal | KSAS | Completed | Load_259880 | Rockfort - 410 | 2026-08-02 20:11 | 2026-08-02 20:12 | 2026-08-02 20:49 | 2026-08-02 20:50 | 2026-08-02 20:50 | 2026-08-02 20:51 | 2026-08-02 20:51 | 2026-08-02 20:51 | Fire |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.03263 | C001872223 | Edward Royal | KSAS | Completed | Load_259880 | Rockfort - 410 | 2026-08-02 20:11 | 2026-08-02 20:12 | 2026-08-02 20:47 | 2026-08-02 20:48 | 2026-08-02 20:47 | 2026-08-02 20:48 | 2026-08-02 20:49 | 2026-08-02 20:49 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.03000 | C001872224 | Wan Carlos Scarlett | Portmore | Completed | Load_248790 | Twickenham - 310 | 2026-08-02 20:13 | 2026-08-02 20:14 | 2026-08-02 20:46 | 2026-08-02 20:46 | 2026-08-02 20:57 | 2026-08-02 21:09 | 2026-08-02 21:18 | 2026-08-02 21:18 |  |  | Fair | No | Refuse 20 amp junction no pole# was found nothing was found on primary line cause by lightning strike
Outage | J.E.26.08.01220 | C001872228 | Edward Royal | KSAS | Completed | Load_263972 | Rockfort - 410 | 2026-08-02 20:14 | 2026-08-02 20:15 | 2026-08-02 21:33 | 2026-08-02 21:33 | 2026-08-02 21:33 | 2026-08-02 21:40 | 2026-08-02 21:40 | 2026-08-02 21:40 |  |  | Fair | No | Replaced 8A junction fuse pole #551399
Outage | J.E.26.08.01722 | C001872229 | Edward Royal | KSAS | Completed | Load_267192 | Rockfort - 410 | 2026-08-02 20:14 | 2026-08-02 20:15 | 2026-08-02 20:55 | 2026-08-02 20:55 | 2026-08-02 20:55 | 2026-08-02 20:56 | 2026-08-02 20:56 | 2026-08-02 20:56 | Fire |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.01953 | C001872230 | Edward Royal | KSAS | Completed | Load_243474 | Rockfort - 410 | 2026-08-02 20:14 | 2026-08-02 20:15 | 2026-08-02 20:35 | 2026-08-02 20:37 | 2026-08-02 20:36 | 2026-08-02 20:37 | 2026-08-02 20:37 | 2026-08-02 20:37 |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.08.03732 | C001872225 | Edward Royal | KSAS | Completed | Load_246529 | Rockfort - 410 | 2026-08-02 20:14 | 2026-08-02 20:15 | 2026-08-02 20:34 | 2026-08-02 20:36 | 2026-08-02 20:35 | 2026-08-02 20:36 | 2026-08-02 20:36 | 2026-08-02 20:36 |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.08.03898 | C001872226 | Edward Royal | KSAS | Completed | Load_246529 | Rockfort - 410 | 2026-08-02 20:14 | 2026-08-02 20:15 | 2026-08-02 20:42 | 2026-08-02 20:43 | 2026-08-02 20:42 | 2026-08-02 20:43 | 2026-08-02 20:44 | 2026-08-02 20:44 |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.08.01508 | C001872233 | Antony Levy | KSAN | Completed | Load_247559 | Constant Spring - 210 | 2026-08-02 20:16 | 2026-08-02 20:26 | 2026-08-02 21:29 | 2026-08-02 21:30 | 2026-08-02 21:55 | 2026-08-02 21:56 | 2026-08-02 21:56 | 2026-08-02 21:56 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.02446 | C001872232 | Dwayne Cohen | KSAS | Completed | Load_240463 | Up Park Camp - 410 | 2026-08-02 20:16 | 2026-08-02 20:18 | 2026-08-02 21:26 | 2026-08-02 21:27 | 2026-08-02 22:18 | 2026-08-02 22:18 | 2026-08-02 22:30 | 2026-08-02 22:30 |  |  | Fair | No | Refuse two 20amps junction by the Latham Ave and Old Hope Road
Outage | J.E.26.08.03903 | C001872235 | Derrick Grubb | St.Thomas | Completed | Load_264443 | Lysson - 410 | 2026-08-02 20:24 | 2026-08-03 07:57 | 2026-08-03 10:43 | 2026-08-03 10:44 | 2026-08-03 11:06 | 2026-08-03 11:19 | 2026-08-03 11:19 | 2026-08-03 11:19 |  |  | Fair | No | Troubleshoot and found one 25kva transformer defective and needs to be replaced. Pole number 200420. Please refer to maintenance team.
Outage | J.E.26.08.01610 | C001872237 | Jvunalle Scully | St.Catherine | Completed | Load_243280 | Duhaney - 210 | 2026-08-02 20:28 | 2026-08-02 20:29 | 2026-08-02 22:06 | 2026-08-02 22:06 | 2026-08-02 22:14 | 2026-08-02 22:14 | 2026-08-02 22:14 | 2026-08-02 22:14 |  |  | Fair | No
Outage | J.E.26.08.02986 | C001872239 | Rodclif Dawkins | Portmore | Completed | Load_266759 | Twickenham - 210 | 2026-08-02 20:35 | 2026-08-02 20:36 | 2026-08-02 22:21 | 2026-08-02 22:22 | 2026-08-02 22:31 | 2026-08-02 22:48 | 2026-08-02 22:52 | 2026-08-02 22:52 |  |  | Fair | No | Found blown fuse for single phase line section supplying 100kva transformer. 100kva transformer fuse was blown . Patrol revealed no faults at time. Found 10amp at junction,replaced with same. Found and replaced 8amp at transformer. Area okay
Outage | J.E.26.08.03893 | C001872243 | Raymond Lewis | St.Ann | Completed | Load_256510 | Cardiff Hall - 210 | 2026-08-02 20:43 | 2026-08-02 21:23 | 2026-08-02 22:09 | 2026-08-02 22:10 | 2026-08-02 22:09 | 2026-08-02 22:11 | 2026-08-02 22:43 | 2026-08-02 22:43 | Fire |  | Fair | No | No fire seen and 30 ft ploe need to straighten
Outage | J.E.26.08.04012 | C001872246 | Derrick Dawkins | St.James | Completed | Load_262774 | Bogue - 610 | 2026-08-02 21:06 | 2026-08-02 22:58 | 2026-08-02 23:29 | 2026-08-02 23:29 | 2026-08-03 00:08 | 2026-08-03 00:13 | 2026-08-03 00:41 | 2026-08-03 00:41 |  |  | Fair | No | Check found premises ok
Outage | J.E.26.08.04023 | C001872248 | Derrick Dawkins | St.James | Completed | Load_253101 | Bogue - 610 | 2026-08-02 21:06 | 2026-08-02 22:58 | 2026-08-03 00:42 | 2026-08-03 00:42 | 2026-08-03 00:42 | 2026-08-03 00:29 | 2026-08-03 00:44 | 2026-08-03 00:44 |  |  | Fair | No | Found premises ok
Outage | J.E.26.08.04025 | C001872247 | Derrick Dawkins | St.James | Completed | Load_247962 | Bogue - 610 | 2026-08-02 21:06 | 2026-08-02 22:58 | 2026-08-03 00:44 | 2026-08-03 00:45 | 2026-08-03 00:44 | 2026-08-03 00:47 | 2026-08-03 00:48 | 2026-08-03 00:48 |  |  | Fair | No | Found premises ok
Non-Outage | J.E.26.08.04018 | C001872249 | Romeo Brissett |  | Completed |  |  | 2026-08-02 21:21 | 2026-08-02 21:44 | 2026-08-02 21:48 | 2026-08-02 21:48 | 2026-08-02 22:48 | 2026-08-03 00:18 | 2026-08-03 00:36 | 2026-08-03 00:36 | Fire |  | Fair | No | Isolated (1)50kva transformer, removed illegal connections, spliced and retention 1 span of secondary.
Outage | J.E.26.08.04054 | C001872250 | Antony Levy | KSAN | Completed | Load_257446 | Constant Spring - 210 | 2026-08-02 21:33 | 2026-08-02 21:40 | 2026-08-02 21:57 | 2026-08-02 21:58 | 2026-08-02 22:12 | 2026-08-02 22:22 | 2026-08-02 22:26 | 2026-08-02 22:26 | Fire |  | Fair | No | Unable to reach customer by phone patrolled street no fire seen.
Non-Outage | J.E.26.07.14576 | C001872254 | Raheem Ricketts | Manchester | Completed | Load_262926 | Spur Tree - 210 | 2026-08-02 22:08 | 2026-08-02 22:09 | 2026-08-02 22:26 | 2026-08-02 22:27 | 2026-08-02 22:51 | 2026-08-02 22:53 | 2026-08-02 22:53 | 2026-08-02 22:53 |  |  | Fair | No | Unable to contact customer however check area and found 25,kva trips reset 25,kva
Non-Outage | J.E.26.08.04083 | C001872260 | Christopher Edwards |  | Completed |  |  | 2026-08-02 22:47 | 2026-08-02 22:48 | 2026-08-02 23:34 | 2026-08-02 23:34 | 2026-08-02 23:45 | 2026-08-03 00:32 | 2026-08-03 00:33 | 2026-08-03 00:33 | Fire |  | Fair | No | Isolate 25 kva transformer To remake burnt open secondary phase jumper joint Using (2) one bolt clamps Voltage:116,115,230v
Outage | J.E.26.08.02103 | C001872263 | Delano Gayle | St.Catherine | Completed | Load_240110 | Naggo Head - 510 | 2026-08-02 23:17 | 2026-08-02 23:22 | 2026-08-03 05:18 | 2026-08-03 05:18 | 2026-08-03 05:24 | 2026-08-03 05:25 | 2026-08-03 05:25 | 2026-08-03 05:25 |  |  | Fair | No | Premises found okay power was restored to premises
Outage | J.E.26.08.03367 | C001872262 | Delano Gayle | St.Catherine | Completed | Load_254806 | Twickenham - 210 | 2026-08-02 23:17 | 2026-08-02 23:22 | 2026-08-03 03:18 | 2026-08-03 03:19 | 2026-08-03 04:06 | 2026-08-03 04:46 | 2026-08-03 04:46 | 2026-08-03 04:46 |  |  | Fair | No | Blown junction on main no pole#, Burnt fuse holder, replace fuse holder and 15amps fuse
Outage | J.E.26.08.03934 | C001872261 | Delano Gayle | St.Catherine | Completed | Load_258914 | Twickenham - 210 | 2026-08-02 23:17 | 2026-08-02 23:22 | 2026-08-03 04:47 | 2026-08-03 04:47 | 2026-08-03 05:06 | 2026-08-03 05:17 | 2026-08-03 05:17 | 2026-08-03 05:17 |  |  | Fair | No | Blown junction on main no pole#, patrolled line section and found okay for closure replace 15amps fuse
Outage | J.E.26.08.02110 | C001872266 | Delano Gayle | St.Catherine | Completed | Load_256303 | Naggo Head - 510 | 2026-08-02 23:18 | 2026-08-02 23:22 | 2026-08-03 05:26 | 2026-08-03 05:26 | 2026-08-03 05:33 | 2026-08-03 05:35 | 2026-08-03 05:35 | 2026-08-03 05:35 |  |  | Fair | No | Premises found okay power was restored
Outage | J.E.26.08.02226 | C001872265 | Delano Gayle | St.Catherine | Completed | Load_239701 | Naggo Head - 510 | 2026-08-02 23:18 | 2026-08-02 23:22 | 2026-08-03 05:35 | 2026-08-03 05:36 | 2026-08-03 05:43 | 2026-08-03 05:47 | 2026-08-03 05:47 | 2026-08-03 05:47 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.04104 | C001872268 | Derrick Dawkins | St.James | Completed | Load_258936 | Queens Drive - 710 | 2026-08-02 23:26 | 2026-08-02 23:27 | 2026-08-03 00:54 | 2026-08-03 00:54 | 2026-08-03 01:35 | 2026-08-03 01:38 | 2026-08-03 01:40 | 2026-08-03 01:40 | BrokenWire |  | Fair | No | Cannot locate customer
Outage | J.E.26.08.02933 | C001872269 | Christopher Edwards | KSAS | Completed | Load_259746 | Rockfort - 410 | 2026-08-02 23:54 | 2026-08-02 23:57 | 2026-08-03 02:09 | 2026-08-03 02:10 | 2026-08-03 02:09 | 2026-08-03 02:09 | 2026-08-03 02:10 | 2026-08-03 02:10 | Fire |  | Fair | No | Related to previous call that was resolved
Outage | J.E.26.08.03266 | C001872270 | Fitzroy Turner | KSAS | Completed | Load_247846 | Hunts Bay - 210 | 2026-08-02 23:54 | 2026-08-03 07:58 | 2026-08-03 11:55 | 2026-08-03 11:55 | 2026-08-03 11:59 | 2026-08-03 12:32 | 2026-08-03 12:35 | 2026-08-03 12:35 | BrokenWire |  | Fair | No | Found bank of three 100kva transformer one switches top burnt off use one hot line clamps and 5ft off #4 copper to remove switches connected one 10 amp fuse and one fuse link supply restored to the areas
Outage | J.E.26.08.02800 | C001872272 | Christopher Edwards | KSAS | Completed | Load_254827 | Hunts Bay - 110 | 2026-08-02 23:55 | 2026-08-02 23:57 | 2026-08-03 00:51 | 2026-08-03 00:52 | 2026-08-03 01:21 | 2026-08-03 02:08 | 2026-08-03 02:09 | 2026-08-03 02:09 |  |  | Fair | No | Refuse blown junction fuseUsing (1) 30 amps
Outage | J.E.26.08.02859 | C001872271 | Christopher Edwards | KSAS | Completed | Load_269328 | Rockfort - 410 | 2026-08-02 23:55 | 2026-08-02 23:57 | 2026-08-03 02:10 | 2026-08-03 02:11 | 2026-08-03 02:32 | 2026-08-03 02:50 | 2026-08-03 02:50 | 2026-08-03 02:50 |  |  | Fair | No | Refuse blown 50 kva transformer Using (1) 5 amps
Outage | J.E.26.08.03834 | C001872273 | Christopher Edwards | KSAN | Completed | Load_248268 | Constant Spring - 410 | 2026-08-02 23:56 | 2026-08-02 23:57 | 2026-08-03 00:34 | 2026-08-03 00:34 | 2026-08-03 00:40 | 2026-08-03 00:51 | 2026-08-03 00:51 | 2026-08-03 00:51 |  |  | Fair | No | Refuse blown junction fuseUsing (1) 8 amps
Outage | J.E.26.08.03101 | C001872277 | Wan Carlos Scarlett | Portmore | Completed | Load_240584 | Twickenham - 210 | 2026-08-03 06:04 | 2026-08-03 10:14 | 2026-08-03 10:50 | 2026-08-03 11:25 | 2026-08-03 11:25 | 2026-08-03 12:02 | 2026-08-03 12:03 | 2026-08-03 12:03 | Fire |  | Fair | No | Refuse 25 KVA transformer with a 3 amp fuse pole# 618681 nothing found on secondary line cause by lightning strike
Outage | J.E.26.08.04111 | C001872280 | Derrick Grubb | St.Thomas | Completed | Load_251732 | Good Year - 210 | 2026-08-03 07:04 | 2026-08-03 07:53 | 2026-08-03 08:43 | 2026-08-03 08:43 | 2026-08-03 10:33 | 2026-08-03 10:41 | 2026-08-03 10:41 | 2026-08-03 10:41 | BrokenWire |  | Fair | No | Fire was caused by an illegal wire making contact with cable wires. Illegal wire was removed.
Outage | J.E.26.08.03927 | C001872282 | Milton Charlton | KSAN | Completed | Load_243219 | Hope - 510 | 2026-08-03 07:13 | 2026-08-03 07:47 | 2026-08-03 11:07 | 2026-08-03 11:08 | 2026-08-03 11:55 | 2026-08-03 | 2026-08-03 11:57 | 2026-08-03 11:57 |  |  | Fair | No | Found one 30 amps junction fuse blown at pole #039971 and one 3 amps transformer fuse at pole #0101505 refused using one 30 amps fuse and one 3 amps fuse and reclosed junction and transformer switches.
Outage | J.E.26.08.03997 | C001872283 | Milton Charlton | KSAN | Completed | Load_263440 | Hope - 510 | 2026-08-03 07:13 | 2026-08-03 07:48 | 2026-08-03 10:39 | 2026-08-03 10:40 | 2026-08-03 11:04 | 2026-08-03 11:00 | 2026-08-03 11:07 | 2026-08-03 11:07 |  |  | Fair | No | Customer meter # 2402425 is single phasing. readings at meter socket 116-116-233 volts. Meter is defective.Refer to field service.
Outage | J.E.26.08.04117 | C001872284 | Milton Charlton | KSAN | Completed | Load_267149 | Hope - 410 | 2026-08-03 07:13 | 2026-08-03 07:48 | 2026-08-03 09:52 | 2026-08-03 09:53 | 2026-08-03 10:37 | 2026-08-03 10:15 | 2026-08-03 10:38 | 2026-08-03 10:38 |  |  | EarthMovement | No | Found okay upon arrival. Readings at meter socket 115-116-232 volts. Customer has an internal problem.
Outage | J.E.26.08.04200 | C001872285 | Ryan Richards | Manchester | Completed | Load_266029 | Kendal - 210 | 2026-08-03 07:14 | 2026-08-03 07:27 | 2026-08-03 07:41 | 2026-08-03 11:20 | 2026-08-03 11:20 | 2026-08-03 11:30 | 2026-08-03 11:30 | 2026-08-03 11:30 | BangingWires |  | Fair | No | 1 span of banging secondary phase and neutral found open 25 kva transformer retention neutral using 1#2 preform and 1 one bolt clamp and reclose transformer all customers are now with supply
Outage | J.E.26.08.04030 | C001872289 | Evan Spaulding | St.Mary | Completed | Load_266718 | Highgate -110 | 2026-08-03 07:26 | 2026-08-03 08:23 | 2026-08-03 09:25 | 2026-08-03 09:25 | 2026-08-03 09:25 | 2026-08-03 10:04 | 2026-08-03 10:05 | 2026-08-03 10:05 |  | Y | Rains | No | Splice and retention one span secondary conductor using 20ft 2/0 AAAC conductor,2-2/0 splicing sleeves and 2-1 bolt clamps
Outage | J.E.26.08.04048 | C001872290 | Evan Spaulding | St.Mary | Completed | Load_238360 | Highgate - 210 | 2026-08-03 07:26 | 2026-08-03 07:29 | 2026-08-03 10:05 | 2026-08-03 10:06 | 2026-08-03 10:36 | 2026-08-03 10:44 | 2026-08-03 10:45 | 2026-08-03 10:45 |  |  | Fair | No | Replace 1-3 amps Transformer fuse at pole number 0013075.
Outage | J.E.26.08.03084 | C001872291 | Christopher Edwards | KSAN | Completed | Load_258537 | Washington Blvd - 610 | 2026-08-03 07:28 | 2026-08-03 08:25 | 2026-08-03 09:57 | 2026-08-03 09:58 | 2026-08-03 09:57 | 2026-08-03 10:38 | 2026-08-03 10:40 | 2026-08-03 10:40 | Fire |  | Fair | No | Burnt 2 twisted wireRequired approximately 60ft #2 twisted wire To splice burnt twisted wireApproximately 5 customers are affected by burnt wire
Non-Outage | J.E.26.08.03364 | C001872292 | Fitzroy Turner |  | Completed |  |  | 2026-08-03 07:29 | 2026-08-03 18:47 | 2026-08-03 20:44 | 2026-08-03 20:44 | 2026-08-03 20:44 | 2026-08-03 20:45 | 2026-08-03 20:47 | 2026-08-03 20:47 | BrokenWire |  | Fair | No | Supply restored to the areas after repair was carry out and broken wires j
Non-Outage | J.E.26.08.04228 | C001872293 | Fitzroy Turner |  | Completed |  |  | 2026-08-03 07:29 | 2026-08-03 07:58 | 2026-08-03 10:21 | 2026-08-03 10:22 | 2026-08-03 10:22 | 2026-08-03 10:22 | 2026-08-03 10:27 | 2026-08-03 10:27 |  |  | Fair | No | Found blown 20 amps junction fuse at the intersection of dealing st and west st and one 10 amps fuse in 100kva transformer and darlings st supply restored to the areas
Outage | J.E.26.08.04224 | C001872294 | Roxroy Needham | St.Ann | Completed | Load_575875 | Cardiff Hall - 210 | 2026-08-03 07:29 | 2026-08-03 07:31 | 2026-08-03 10:29 | 2026-08-03 10:29 | 2026-08-03 10:57 | 2026-08-03 10:58 | 2026-08-03 10:58 | 2026-08-03 10:58 |  |  | Fair | No | Premises not found not getting customer on phone
Non-Outage | J.E.26.08.03862 | C001872297 | Roxroy Needham | St.Ann | Completed | Load_256510 | Cardiff Hall - 210 | 2026-08-03 07:30 | 2026-08-03 07:31 | 2026-08-03 08:12 | 2026-08-03 08:12 | 2026-08-03 09:40 | 2026-08-03 10:27 | 2026-08-03 10:29 | 2026-08-03 10:29 | Fire | Y | Rains | No | Open a 25 KVA transformer at pole and retention 2 span of secondary line
Outage | J.E.26.08.03020 | C001872296 | Rusean Allen | KSAS | Completed | Load_240326 | Hunts Bay - 210 | 2026-08-03 07:30 | 2026-08-04 07:49 | 2026-08-04 10:48 | 2026-08-04 10:49 | 2026-08-04 11:12 | 2026-08-04 11:14 | 2026-08-04 11:15 | 2026-08-04 11:15 | Fire |  | Fair | No | Premises okay
Outage | J.E.26.08.03589 | C001872295 | Edward Royal | KSAS | Completed | Load_244976 | Duhaney - 410 | 2026-08-03 07:30 | 2026-08-03 08:12 | 2026-08-03 11:56 | 2026-08-03 11:56 | 2026-08-03 11:56 | 2026-08-03 11:59 | 2026-08-03 11:59 | 2026-08-03 11:59 |  |  | Fair | No | Customer was reconnected by escalation
Non-Outage | J.E.26.08.01964 | C001872301 | Edward Royal |  | Completed |  |  | 2026-08-03 07:35 | 2026-08-03 21:38 | 2026-08-03 22:10 | 2026-08-03 22:11 | 2026-08-03 22:10 | 2026-08-03 22:11 | 2026-08-03 22:11 | 2026-08-03 22:11 | BrokenPole |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.03385 | C001872299 | Edward Royal | KSAS | Completed | Load_301416 | Greenwich - 410 | 2026-08-03 07:35 | 2026-08-03 08:18 | 2026-08-03 11:59 | 2026-08-03 12:00 | 2026-08-03 12:00 | 2026-08-03 12:00 | 2026-08-03 12:00 | 2026-08-03 12:00 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.04091 | C001872300 | Richard Watson | St.Elizabeth | Completed | Load_254040 | Maggotty - 110 | 2026-08-03 07:35 | 2026-08-03 07:36 | 2026-08-03 08:07 | 2026-08-03 08:08 | 2026-08-03 08:40 | 2026-08-03 08:42 | 2026-08-03 08:42 | 2026-08-03 08:42 |  |  | Fair | No | Premises and area found with electricity.
Outage | J.E.26.08.04205 | C001872298 | Jermaine Douglas | KSAS | Completed | Load_268158 | Greenwich - 410 | 2026-08-03 07:35 | 2026-08-03 21:29 | 2026-08-03 21:36 | 2026-08-03 21:37 | 2026-08-03 21:45 | 2026-08-03 21:49 | 2026-08-03 21:49 | 2026-08-03 21:49 |  |  | Fair | No | Bank of 3 transformer 2x50kva and 1x100kva, fuse for the lighting transformer found blown at pole#0133940, 8 amps fuse replaced and power restored.
Non-Outage | J.E.26.07.34907 | C001872303 | Javid Vernon | Westmoreland | Completed | Load_245109 | Paradise - 210 | 2026-08-03 07:37 | 2026-08-03 12:17 | 2026-08-03 13:30 | 2026-08-03 13:31 | 2026-08-03 14:37 | 2026-08-03 14:58 | 2026-08-03 14:58 | 2026-08-03 14:58 |  |  | Fair | No | Clean and remake joints at JPS pole use two clamps voltage found 108/77/185 voltage left 108/107/215
Non-Outage | J.E.26.08.03546 | C001872302 | Javid Vernon | Westmoreland | Completed | Load_252147 | Paradise - 210 | 2026-08-03 07:37 | 2026-08-03 12:17 | 2026-08-03 12:31 | 2026-08-03 12:31 | 2026-08-03 13:10 | 2026-08-03 13:30 | 2026-08-03 13:30 | 2026-08-03 13:30 |  |  | Fair | No | Reconnect customer service neutral use one clamp voltage found 216 voltage left105/111/216
Non-Outage | J.E.26.07.31239 | C001872305 | Swon Miller | St.James | Completed | Load_270006 | Queens Drive - 810 | 2026-08-03 07:38 | 2026-08-03 07:40 | 2026-08-03 07:55 | 2026-08-03 08:09 | 2026-08-03 08:28 | 2026-08-18 08:44 | 2026-08-03 08:46 | 2026-08-03 08:46 |  |  | Fair | No | Check and found okay customer states that the problem has been resolved voltage found 115/115/231 voltage left 115/115/231
Non-Outage | J.E.26.07.37313 | C001872306 | Swon Miller | St.James | Completed | Load_245936 | Queens Drive - 710 | 2026-08-03 07:38 | 2026-08-03 07:40 | 2026-08-03 08:46 | 2026-08-03 08:47 | 2026-08-03 09:07 | 2026-08-18 11:00 | 2026-08-03 11:08 | 2026-08-03 11:08 |  |  | Fair | No | Found customer with low voltage at the end of the line voltage found 101/102 /204 transfer customers to a another circuit voltage after reconnection 112/114/228 voltage at the end of the circuit 106/107/214 illegal connections needs to be removed plz refer losses team needed in the area badly (Nelly Drive)
Non-Outage | J.E.26.07.32420 | C001872307 | Swon Miller | St.James | Completed | Load_247453 | Queens Drive - 710 | 2026-08-03 07:39 | 2026-08-03 07:40 | 2026-08-03 11:11 | 2026-08-03 11:12 | 2026-08-03 11:58 | 2026-08-25 00:43 | 2026-08-03 12:49 | 2026-08-03 12:49 |  |  | Fair | No | Found customer with low voltage at the end of the circuit voltage found 104/101/205 losses team is urgently needed in the area to remove illegal connections pls refer to the losses department voltage left 104/101/205
Outage | J.E.26.08.04252 | C001872313 | Roxroy Needham | St.Ann | Completed | Load_246247 | Roaring River - 210 | 2026-08-03 07:40 | 2026-08-03 07:41 | 2026-08-03 10:59 | 2026-08-03 11:00 | 2026-08-03 12:03 | 2026-08-03 12:03 | 2026-08-03 12:05 | 2026-08-03 12:05 |  |  | Fair | No | Replace a 20 amps junction fuse at pole
Non-Outage | J.E.26.08.03371 | C001872317 | Fitzroy Turner |  | Completed |  |  | 2026-08-03 07:42 | 2026-08-03 07:58 | 2026-08-03 20:51 | 2026-08-03 20:51 | 2026-08-03 20:51 | 2026-08-03 20:51 | 2026-08-03 20:52 | 2026-08-03 20:52 | BrokenWire |  | Fair | No | Supply restored to the areas after repair was carry out and broken wires
Non-Outage | J.E.26.08.04166 | C001872316 | Fitzroy Turner |  | Completed |  |  | 2026-08-03 07:42 | 2026-08-03 07:58 | 2026-08-03 10:29 | 2026-08-03 10:30 | 2026-08-03 10:33 | 2026-08-03 10:45 | 2026-08-03 10:46 | 2026-08-03 10:46 |  |  | Fair | No | Customer supply restored after closing 20 amps junction fuses at west st
Outage | J.E.26.08.03237 | C001872318 | Rusean Allen | KSAS | Completed | Load_247100 | Rockfort - 410 | 2026-08-03 07:42 | 2026-08-03 08:04 | 2026-08-03 10:07 | 2026-08-03 10:07 | 2026-08-03 11:14 | 2026-08-03 11:16 | 2026-08-03 11:16 | 2026-08-03 11:16 |  |  | Fair | No
Outage | J.E.26.08.04174 | C001872315 | Fitzroy Turner | KSAS | Completed | Load_266467 | Hunts Bay - 310 | 2026-08-03 07:42 | 2026-08-03 07:58 | 2026-08-03 13:31 | 2026-08-03 13:31 | 2026-08-03 13:32 | 2026-08-03 13:33 | 2026-08-03 13:34 | 2026-08-03 13:34 |  |  | Fair | No | Supply restored after replace 30amps junction fuse at pole # 551766
Non-Outage | J.E.26.08.03561 | C001872321 | Elvis Trowers |  | Completed |  |  | 2026-08-03 07:48 | 2026-08-03 08:18 | 2026-08-03 11:05 | 2026-08-03 11:06 | 2026-08-03 11:26 | 2026-08-03 11:39 | 2026-08-03 11:39 | 2026-08-03 11:39 |  |  | Fair | Yes | Areas checked and found ok with regular electricity supply though customer couldn’t be contacted by telephone either after several calls.
Non-Outage | J.E.25.12.39984 | C001872332 | Tajay Bernard | Hanover | Completed | Load_1001394 | Orange Bay - 310 | 2026-08-03 07:50 | 2026-08-03 07:51 | 2026-08-03 08:23 | 2026-08-03 11:23 | 2026-08-03 11:23 | 2026-08-03 13:27 | 2026-08-03 13:29 | 2026-08-03 13:29 |  |  | Fair | No | Clean and remake joint at customer pothead head use 1 clamp voltage found 114Voltage left 114/112/216
Non-Outage | J.E.26.01.23610 | C001872331 | Tajay Bernard | Hanover | Completed | Load_244774 | Orange Bay - 310 | 2026-08-03 07:50 | 2026-08-03 07:51 | 2026-08-03 08:11 | 2026-08-03 08:11 | 2026-08-03 08:11 | 2026-08-03 08:12 | 2026-08-03 08:12 | 2026-08-03 08:12 |  |  | Fair | No | This call belongs to Westmoreland
Non-Outage | J.E.26.01.25681 | C001872329 | Tajay Bernard | Hanover | Completed | Load_269526 | Orange Bay - 310 | 2026-08-03 07:50 | 2026-08-03 07:51 | 2026-08-03 11:21 | 2026-08-03 11:22 | 2026-08-03 11:21 | 2026-08-03 11:22 | 2026-08-03 11:22 | 2026-08-03 11:22 |  |  | EarthMovement | No | This call belongs to st james
Non-Outage | J.E.26.01.26246 | C001872327 | Tajay Bernard | Hanover | Completed | Load_253661 | Orange Bay - 310 | 2026-08-03 07:50 | 2026-08-03 07:51 | 2026-08-03 08:16 | 2026-08-03 13:30 | 2026-08-03 13:30 | 2026-08-03 13:30 | 2026-08-03 13:30 | 2026-08-03 13:30 |  |  | Fair | No | Customer stated that the issue has been resolved
Non-Outage | J.E.26.02.34717 | C001872323 | Tajay Bernard | Hanover | Completed | Load_241881 | Orange Bay - 310 | 2026-08-03 07:50 | 2026-08-03 07:51 | 2026-08-03 13:31 | 2026-08-03 13:32 | 2026-08-03 13:56 | 2026-08-03 14:09 | 2026-08-03 14:09 | 2026-08-03 14:09 |  |  | Fair | No | Premises found okay customer has internal problems
Non-Outage | J.E.26.03.06331 | C001872324 | Tajay Bernard | Hanover | Completed | Load_239612 | Orange Bay - 310 | 2026-08-03 07:50 | 2026-08-03 07:51 | 2026-08-03 08:01 | 2026-08-03 09:34 | 2026-08-03 10:55 | 2026-08-03 11:19 | 2026-08-03 11:20 | 2026-08-03 11:20 |  |  | Fair | No | Premises check and found okay customer has internal problems. Voltage found 109/110/219
Non-Outage | J.E.26.03.08734 | C001872325 | Tajay Bernard | Hanover | Completed | Load_293082 | Orange Bay - 310 | 2026-08-03 07:50 | 2026-08-03 07:51 | 2026-08-03 08:19 | 2026-08-03 08:33 | 2026-08-03 09:08 | 2026-08-03 09:33 | 2026-08-03 09:34 | 2026-08-03 09:34 |  |  | Fair | No | Clean and remake joints at customer pothead used 2 clampsVoltage found 103/112/215Voltage left 110/112/222
Non-Outage | J.E.26.03.10396 | C001872322 | Tajay Bernard | Hanover | Completed | Load_247660 | Orange Bay - 310 | 2026-08-03 07:50 | 2026-08-03 07:51 | 2026-08-03 08:13 | 2026-08-03 08:13 | 2026-08-03 08:13 | 2026-08-03 08:13 | 2026-08-03 08:13 | 2026-08-03 08:13 |  |  | Fair | No | This call belongs to st james
Outage | J.E.26.08.04164 | C001872335 | Rusean Allen | KSAS | Completed | Load_241686 | Rockfort - 410 | 2026-08-03 07:57 | 2026-08-03 08:02 | 2026-08-03 11:33 | 2026-08-03 11:37 | 2026-08-03 11:37 | 2026-08-03 11:38 | 2026-08-03 11:38 | 2026-08-03 11:38 |  |  | Fair | No | Internal issues, electrician in process of doing repairs.
Outage | J.E.26.08.04253 | C001872337 | Roxroy Needham | St.Ann | Completed | Load_255760 | Cardiff Hall - 310 | 2026-08-03 07:57 | 2026-08-03 07:59 | 2026-08-03 12:04 | 2026-08-03 12:10 | 2026-08-03 12:29 | 2026-08-03 12:38 | 2026-08-03 12:38 | 2026-08-03 12:38 |  | Y | Fair | No | Replace a 25 amps junction fuse at pole
Outage | J.E.26.08.04189 | C001872338 | Ricky Hall | St.Catherine | Completed | Load_242773 | Tredegar - 310 | 2026-08-03 07:58 | 2026-08-03 09:12 | 2026-08-03 10:32 | 2026-08-03 10:32 | 2026-08-03 11:00 | 2026-08-03 11:02 | 2026-08-03 11:03 | 2026-08-03 11:03 |  |  | Fair | No | Area found with supply
Non-Outage | J.E.26.08.00072 | C001872339 | Horace Malcolm | St.James | Completed | Load_248632 | Bogue - 510 | 2026-08-03 08:00 | 2026-08-03 08:02 | 2026-08-03 08:16 | 2026-08-03 08:17 | 2026-08-03 08:54 | 2026-08-03 09:52 | 2026-08-03 09:52 | 2026-08-03 09:52 |  |  | Fair | No | Clean and remake joints at pole and pothead used two clamps voltage 113-113-226
Non-Outage | J.E.26.08.00327 | C001872341 | Horace Malcolm | St.James | Completed | Load_237651 | Orange Bay - 310 | 2026-08-03 08:00 | 2026-08-03 08:02 | 2026-08-03 12:22 | 2026-08-03 12:23 | 2026-08-03 12:50 | 2026-08-03 13:41 | 2026-08-03 13:41 | 2026-08-03 13:41 |  |  | Fair | No | Changed burnt clamp on customer phase service wire at pole used 1clamp113-115-228
Non-Outage | J.E.26.08.04116 | C001872340 | Horace Malcolm | St.James | Completed | Load_262522 | Bogue - 510 | 2026-08-03 08:00 | 2026-08-03 08:02 | 2026-08-03 09:53 | 2026-08-03 09:53 | 2026-08-03 10:49 | 2026-08-03 12:19 | 2026-08-03 12:19 | 2026-08-03 12:19 |  |  | Fair | No | Clean and remake joints at customer pothead and pole and splice customer service nuetral used 10ft #6 triplex wire 2clamps voltage 117-115-232
Outage | J.E.26.08.04096 | C001872343 | Rusean Allen | KSAS | Completed | Load_243736 | Cane River - 310 | 2026-08-03 08:00 | 2026-08-03 08:02 | 2026-08-03 11:01 | 2026-08-03 13:20 | 2026-08-03 13:23 | 2026-08-03 13:23 | 2026-08-03 13:24 | 2026-08-03 13:24 |  |  | Fair | No | Premises okay
Outage | J.E.26.08.04107 | C001872342 | Rusean Allen | KSAS | Completed | Load_242965 | Cane River - 410 | 2026-08-03 08:00 | 2026-08-03 08:02 | 2026-08-03 10:53 | 2026-08-03 13:27 | 2026-08-03 13:48 | 2026-08-03 13:49 | 2026-08-03 13:49 | 2026-08-03 13:49 |  |  | Fair | No | Meter was reconnected by customer service
Outage | J.E.26.08.03313 | C001872350 | Wan Carlos Scarlett | St.Catherine | Completed | Load_264593 | Twickenham - 210 | 2026-08-03 08:01 | 2026-08-03 08:05 | 2026-08-03 10:10 | 2026-08-03 10:11 | 2026-08-03 10:17 | 2026-08-03 10:35 | 2026-08-03 10:37 | 2026-08-03 10:37 | Fire |  | Fair | No | Refuse 50 KVA transformer with 5 Amp fuse no pole # was found nothing was found on secondary line cause by lightning strike
Outage | J.E.26.08.03887 | C001872348 | Wan Carlos Scarlett | St.Catherine | Completed | Load_244821 | Twickenham - 210 | 2026-08-03 08:01 | 2026-08-03 08:05 | 2026-08-03 08:09 | 2026-08-03 08:10 | 2026-08-03 09:26 | 2026-08-03 10:09 | 2026-08-03 10:10 | 2026-08-03 10:10 |  |  | Fair | No | Refuse 25 KVA transformer with a 3 Amp fuse no pole # was found nothing was found on secondary line
Outage | J.E.26.08.04279 | C001872352 | Fitzroy Turner | KSAS | Completed | Load_251115 | Rockfort - 410 | 2026-08-03 08:03 | 2026-08-04 08:10 | 2026-08-04 11:23 | 2026-08-04 11:24 | 2026-08-04 11:24 | 2026-08-04 12:06 | 2026-08-04 12:14 | 2026-08-04 12:14 |  |  | Fair | No | Found two 30 amps junction fuse blown at the intersection of water lane highhobourn st 30amps fuse replaced supply restored to customer
Non-Outage | J.E.26.02.16213 | C001872361 | Shamour Haughton | St.James | Completed | Load_255698 | Bogue - 310 | 2026-08-03 08:05 | 2026-08-03 08:06 | 2026-08-03 10:14 | 2026-08-03 10:15 | 2026-08-03 10:16 | 2026-08-03 10:16 | 2026-08-03 10:18 | 2026-08-03 10:18 |  |  | Fair | No | Customer states that issue was rectified
Non-Outage | J.E.26.02.16368 | C001872359 | Shamour Haughton | St.James | Completed | Load_239982 | Bogue - 310 | 2026-08-03 08:05 | 2026-08-03 08:06 | 2026-08-03 10:27 | 2026-08-03 11:28 | 2026-08-03 12:05 | 2026-08-03 12:05 | 2026-08-03 12:09 | 2026-08-03 12:09 |  |  | Fair | No | Found customer service wire disconnect at pole, reconnect service wire at pole use 2 clamps, voltage left 117,115,232
Non-Outage | J.E.26.02.23295 | C001872358 | Shamour Haughton | St.James | Completed | Load_260312 | Bogue - 310 | 2026-08-03 08:05 | 2026-08-03 08:06 | 2026-08-03 10:20 | 2026-08-03 10:20 | 2026-08-03 10:22 | 2026-08-03 10:22 | 2026-08-03 10:24 | 2026-08-03 10:24 |  |  | Fair | No | Customer states that the report was from hurricane Melissa and the issue was rectified
Non-Outage | J.E.26.02.24342 | C001872360 | Shamour Haughton | St.James | Completed | Load_248472 | Bogue - 310 | 2026-08-03 08:05 | 2026-08-03 08:06 | 2026-08-03 10:25 | 2026-08-03 10:25 | 2026-08-03 10:25 | 2026-08-03 10:25 | 2026-08-03 10:26 | 2026-08-03 10:26 |  |  | Fair | No | Customer states that pose was rectified
Non-Outage | J.E.26.02.34534 | C001872356 | Shamour Haughton | St.James | Completed | Load_261708 | Bogue - 310 | 2026-08-03 08:05 | 2026-08-03 08:06 | 2026-08-03 12:11 | 2026-08-03 12:12 | 2026-08-03 12:11 | 2026-08-03 12:12 | 2026-08-03 12:13 | 2026-08-03 12:13 |  |  | Fair | No | Found okay, customer state that report was rectified
Non-Outage | J.E.26.02.39553 | C001872357 | Shamour Haughton | St.James | Completed | Load_292555 | Bogue - 310 | 2026-08-03 08:05 | 2026-08-03 08:06 | 2026-08-03 10:36 | 2026-08-03 10:37 | 2026-08-03 11:13 | 2026-08-03 11:14 | 2026-08-03 11:24 | 2026-08-03 11:24 |  |  | Fair | No | Check and found customer experiencing internal issue, voltage left 110,114,225
Non-Outage | J.E.26.06.38370 | C001872367 | Shamour Haughton | St.James | Completed | Load_245107 | Bogue - 310 | 2026-08-03 08:06 | 2026-08-03 08:07 | 2026-08-03 08:52 | 2026-08-03 08:53 | 2026-08-03 09:39 | 2026-08-03 09:42 | 2026-08-03 09:45 | 2026-08-03 09:45 |  |  | Fair | No | Check and found okay, voltage left 114,117,231
Outage | J.E.26.08.04137 | C001872365 | Ricky Hall | St.Catherine | Completed | Load_247685 | Tredegar - 510 | 2026-08-03 08:06 | 2026-08-03 08:07 | 2026-08-03 09:37 | 2026-08-03 09:37 | 2026-08-03 10:01 | 2026-08-03 10:02 | 2026-08-03 10:02 | 2026-08-03 10:02 |  |  | Fair | No | Area found with supply
Outage | J.E.26.08.04138 | C001872364 | Ricky Hall | St.Catherine | Completed | Load_251832 | Tredegar - 510 | 2026-08-03 08:06 | 2026-08-03 08:07 | 2026-08-03 10:02 | 2026-08-03 10:03 | 2026-08-03 10:02 | 2026-08-03 10:03 | 2026-08-03 10:03 | 2026-08-03 10:03 |  |  | Fair | No | Area found with supply
Outage | J.E.26.08.04141 | C001872362 | Ricky Hall | St.Catherine | Completed | Load_248459 | Tredegar - 510 | 2026-08-03 08:06 | 2026-08-03 08:07 | 2026-08-03 09:12 | 2026-08-03 09:12 | 2026-08-03 09:22 | 2026-08-03 09:36 | 2026-08-03 09:37 | 2026-08-03 09:37 |  |  | Fair | No | Premises closed
Outage | J.E.26.08.04145 | C001872363 | Ricky Hall | St.Catherine | Completed | Load_267269 | Tredegar - 510 | 2026-08-03 08:06 | 2026-08-03 08:07 | 2026-08-03 08:11 | 2026-08-03 08:13 | 2026-08-03 08:58 | 2026-08-03 09:07 | 2026-08-03 09:08 | 2026-08-03 09:08 |  |  | Fair | No | Premises not located area found with supply
Non-Outage | J.E.26.08.02597 | C001872368 | Hopeton Henry | St.Thomas | Completed | Load_253268 | Lysson - 410 | 2026-08-03 08:07 | 2026-08-03 08:08 | 2026-08-03 10:09 | 2026-08-03 12:26 | 2026-08-04 09:02 | 2026-08-04 09:03 | 2026-08-04 09:04 | 2026-08-04 09:04 |  |  | Fair | No | Reconnect service at pole 115-115-230 volts
Non-Outage | J.E.26.08.03472 | C001872370 | Hopeton Henry | St.Thomas | Completed | Load_268360 | Lysson - 410 | 2026-08-03 08:07 | 2026-08-03 08:08 | 2026-08-03 10:09 | 2026-08-03 11:59 | 2026-08-03 11:59 | 2026-08-03 11:59 | 2026-08-03 12:26 | 2026-08-03 12:26 |  |  | Fair | Yes | Use 3 connector at pot head 120-111-238 volts
Non-Outage | J.E.26.08.03474 | C001872372 | Hopeton Henry | St.Thomas | Completed | Load_268360 | Lysson - 410 | 2026-08-03 08:07 | 2026-08-03 08:08 | 2026-08-03 10:09 | 2026-08-03 11:57 | 2026-08-03 11:57 | 2026-08-03 11:57 | 2026-08-03 11:58 | 2026-08-03 11:58 |  |  | Fair | Yes | Use 3 connector at pot head 111-120-238 volts
Non-Outage | J.E.26.08.03838 | C001872371 | Edward Royal |  | Completed |  |  | 2026-08-03 08:07 | 2026-08-03 08:11 | 2026-08-03 11:02 | 2026-08-03 11:03 | 2026-08-03 11:02 | 2026-08-03 11:03 | 2026-08-03 11:03 | 2026-08-03 11:03 |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.08.01713 | C001872377 | Edward Royal |  | Completed |  |  | 2026-08-03 08:08 | 2026-08-03 08:11 | 2026-08-03 11:06 | 2026-08-03 11:08 | 2026-08-03 11:08 | 2026-08-03 11:08 | 2026-08-03 11:08 | 2026-08-03 11:08 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.00261 | C001872375 | Edward Royal | KSAS | Completed | Load_260717 | Three Miles - 410 | 2026-08-03 08:08 | 2026-08-03 08:11 | 2026-08-03 12:02 | 2026-08-03 12:03 | 2026-08-03 12:02 | 2026-08-03 12:03 | 2026-08-03 12:03 | 2026-08-03 12:03 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.01228 | C001872376 | Edward Royal | KSAS | Completed | Load_575133 | Three Miles - 510 | 2026-08-03 08:08 | 2026-08-03 08:11 | 2026-08-03 11:04 | 2026-08-03 11:05 | 2026-08-03 11:04 | 2026-08-03 11:05 | 2026-08-03 11:05 | 2026-08-03 11:05 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.01645 | C001872374 | Ricky Hall | St.Catherine | Completed | Load_251407 | Tredegar - 210 | 2026-08-03 08:08 | 2026-08-03 08:09 | 2026-08-03 08:27 | 2026-08-03 10:04 | 2026-08-03 10:31 | 2026-08-03 10:31 | 2026-08-03 10:32 | 2026-08-03 10:32 |  |  | Fair | No | Issue was resolved on previous shift
Outage | J.E.26.08.04290 | C001872378 | Richard Watson | St.Elizabeth | Completed | Load_250325 | Maggotty - 110 | 2026-08-03 08:09 | 2026-08-03 08:10 | 2026-08-03 09:07 | 2026-08-03 09:08 | 2026-08-03 09:19 | 2026-08-03 09:21 | 2026-08-03 09:22 | 2026-08-03 09:22 |  |  | Fair | No | Found okay, supply found at premises.
Outage | J.E.26.08.04291 | C001872381 | Richard Watson | St.Elizabeth | Completed | Load_253484 | Maggotty - 110 | 2026-08-03 08:09 | 2026-08-03 08:10 | 2026-08-03 09:38 | 2026-08-03 09:38 | 2026-08-03 09:59 | 2026-08-03 10:01 | 2026-08-03 10:01 | 2026-08-03 10:01 |  |  | Fair | No | Customer contacted by and stated that the supply was restored.
Outage | J.E.26.08.04292 | C001872379 | Richard Watson | St.Elizabeth | Completed | Load_258699 | Maggotty - 110 | 2026-08-03 08:09 | 2026-08-03 08:10 | 2026-08-03 09:22 | 2026-08-03 09:23 | 2026-08-03 09:34 | 2026-08-03 09:38 | 2026-08-03 09:38 | 2026-08-03 09:38 |  |  | Fair | No | Found okay, supply is at premises.
Outage | J.E.26.08.04295 | C001872380 | Dwayne Cohen | KSAN | Completed | Load_557733 | Washington Blvd - 610 | 2026-08-03 08:09 | 2026-08-03 08:11 | 2026-08-03 09:17 | 2026-08-03 09:17 | 2026-08-03 09:17 | 2026-08-03 09:25 | 2026-08-03 09:26 | 2026-08-03 09:26 |  |  | Fair | No | Refuse 8amps transformer link , supply now restore.
Non-Outage | J.E.26.04.03611 | C001872394 | Orville Lee | Portmore | Completed | Load_259348 | Naggo Head - 610 | 2026-08-03 08:10 | 2026-08-03 08:12 | 2026-08-03 08:20 | 2026-08-03 11:22 | 2026-08-03 11:35 | 2026-08-03 11:37 | 2026-08-03 11:49 | 2026-08-03 11:49 |  |  | Fair | No | Premises found ok upon arrival Customer get an electrician to solve the problem to correct the issue 117v116v234v
Non-Outage | J.E.26.04.13606 | C001872392 | Orville Lee | Portmore | Completed | Load_576156 | Naggo Head - 610 | 2026-08-03 08:10 | 2026-08-03 08:12 | 2026-08-03 08:20 | 2026-08-03 15:27 | 2026-08-03 16:29 | 2026-08-03 17:18 | 2026-08-03 17:19 | 2026-08-03 17:19 |  |  | Fair | No | Checks made and found pothead corroded Three pen union usedVoltage 120v120v240v
Non-Outage | J.E.26.04.14346 | C001872389 | Orville Lee | Portmore | Completed | Load_256038 | Naggo Head - 610 | 2026-08-03 08:10 | 2026-08-03 08:12 | 2026-08-03 08:20 | 2026-08-03 11:54 | 2026-08-03 12:00 | 2026-08-03 12:10 | 2026-08-03 12:10 | 2026-08-03 12:10 |  |  | Fair | No | Premises found ok upon arrival Voltage117v118v234v
Non-Outage | J.E.26.04.14674 | C001872388 | Orville Lee | Portmore | Completed | Load_259274 | Naggo Head - 510 | 2026-08-03 08:10 | 2026-08-03 08:12 | 2026-08-03 08:20 | 2026-08-03 12:23 | 2026-08-03 12:26 | 2026-08-03 12:50 | 2026-08-03 12:50 | 2026-08-03 12:50 |  |  | Fair | No | Premises closed gated community Call to customer unanswered 116117234
Non-Outage | J.E.26.04.21016 | C001872385 | Orville Lee | Portmore | Completed | Load_253186 | Naggo Head - 610 | 2026-08-03 08:10 | 2026-08-03 08:12 | 2026-08-03 08:20 | 2026-08-03 10:28 | 2026-08-03 10:51 | 2026-08-03 11:05 | 2026-08-03 11:07 | 2026-08-03 11:07 |  |  | Fair | No | Premises found ok upon arrival Voltage 116v117v233v
Non-Outage | J.E.26.04.26467 | C001872383 | Orville Lee | Portmore | Completed | Load_256476 | Naggo Head - 610 | 2026-08-03 08:10 | 2026-08-03 08:12 | 2026-08-03 08:20 | 2026-08-03 10:12 | 2026-08-03 10:21 | 2026-08-03 10:27 | 2026-08-03 10:27 | 2026-08-03 10:27 |  |  | Fair | No | Premise closed. Multiple calls to customer went to voicemail Voltage 118V
Non-Outage | J.E.26.07.39163 | C001872384 | Error Coore | Manchester | Completed | Load_254581 | Spur Tree - 310 | 2026-08-03 08:10 | 2026-08-03 08:11 | 2026-08-03 11:17 | 2026-08-03 12:05 | 2026-08-03 12:43 | 2026-08-03 13:10 | 2026-08-03 13:12 | 2026-08-03 13:12 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.39441 | C001872387 | Error Coore | Manchester | Completed | Load_1002510 | Kendal - 310 | 2026-08-03 08:10 | 2026-08-03 08:11 | 2026-08-03 08:47 | 2026-08-03 08:47 | 2026-08-03 09:09 | 2026-08-03 09:28 | 2026-08-03 09:29 | 2026-08-03 09:29 |  |  | Fair | No | Premises found ok customer have internal problem voltage reading 117/117/234 volts
Non-Outage | J.E.26.07.39573 | C001872390 | Error Coore | Manchester | Completed | Load_259688 | Spur Tree - 310 | 2026-08-03 08:10 | 2026-08-03 08:11 | 2026-08-03 08:33 | 2026-08-03 09:32 | 2026-08-03 10:18 | 2026-08-03 11:14 | 2026-08-03 11:16 | 2026-08-03 11:16 |  |  | Fair | No | Found customer with wrap connection at pothead remade wrap connection using 3 service sleeve voltage reading 114/115/229 volts
Non-Outage | J.E.26.07.39764 | C001872393 | Error Coore | Manchester | Completed | Load_259688 | Spur Tree - 310 | 2026-08-03 08:10 | 2026-08-03 08:11 | 2026-08-03 11:17 | 2026-08-03 11:18 | 2026-08-03 11:50 | 2026-08-03 12:01 | 2026-08-03 12:04 | 2026-08-03 12:04 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.03.39175 | C001872395 | Orville Lee | Portmore | Completed | Load_557221 | Naggo Head - 610 | 2026-08-03 08:11 | 2026-08-03 08:12 | 2026-08-03 08:20 | 2026-08-03 08:22 | 2026-08-03 09:57 | 2026-08-03 10:07 | 2026-08-03 10:11 | 2026-08-03 10:11 |  |  | Fair | No | Premise closedMeter 2196950 was changed on 13/04/26 to 3016808Voltage 118V118V236VContinuity test was done on meter
Non-Outage | J.E.26.08.03265 | C001872397 | Locksley Allen | St.Mary | Completed | Load_251918 | Oracabessa - 210 | 2026-08-03 08:11 | 2026-08-03 08:13 | 2026-08-03 15:37 | 2026-08-03 16:00 | 2026-08-03 15:59 | 2026-08-03 16:12 | 2026-08-03 16:17 | 2026-08-03 16:17 |  |  | Fair | No | No low voltage problem at premises Voltage at meter socket phase to phase 232v. Phase to neutral 114&119vMeter left working. Customer was advised to get an electrician to check inside.
Non-Outage | J.E.26.08.03999 | C001872398 | Wayne Dillion | Manchester | Completed | Load_302937 | Spur Tree - 210 | 2026-08-03 08:11 | 2026-08-03 08:13 | 2026-08-03 08:35 | 2026-08-03 08:35 | 2026-08-03 09:03 | 2026-08-03 09:47 | 2026-08-03 09:48 | 2026-08-03 09:48 |  |  | Fair | No | Supply check and found customer single phasing. Further checks reveals illegal connection pulling the down ground against the bottom phase. Cut and remove same and supply restored to the area reading 112v, 111v and cross phase 223volts.
Non-Outage | J.E.26.08.04176 | C001872396 | Raymond Carr | St.Mary | Completed | Load_349421 | Oracabessa - 210 | 2026-08-03 08:11 | 2026-08-03 08:12 | 2026-08-03 11:48 | 2026-08-03 11:48 | 2026-08-03 11:48 | 2026-08-03 12:00 | 2026-08-03 11:53 | 2026-08-03 11:53 | Fire |  | Fair | No | Fault was corrected yesterday.
Non-Outage | J.E.26.08.02560 | C001872399 | Locksley Allen | St.Mary | Completed | Load_246744 | Oracabessa - 210 | 2026-08-03 08:12 | 2026-08-03 08:13 | 2026-08-03 13:59 | 2026-08-03 15:33 | 2026-08-03 15:33 | 2026-08-03 15:39 | 2026-08-03 15:36 | 2026-08-03 15:36 |  |  | Fair | No | No on and off problem found at premises.Voltage at meter socket phase to phase 238v. Phase to neutral 119&119vMeter left working. Customer said it’s the prepaid sys
Non-Outage | J.E.26.08.04050 | C001872402 | Locksley Allen | St.Mary | Completed | Load_247177 | Blackstonedge - 110 | 2026-08-03 08:12 | 2026-08-03 08:13 | 2026-08-03 10:45 | 2026-08-03 11:47 | 2026-08-03 11:46 | 2026-08-03 12:40 | 2026-08-03 12:43 | 2026-08-03 12:43 |  |  | Fair | No | Meter socket defective and needs to change urgently Voltage at panel phase to phase 237v. Phase to neutral 118&119Pothead and pole found corroded, clean up connectors at pole and pothead Meter left working
Non-Outage | J.E.26.05.15202 | C001872408 | Orville Lee | St.Catherine | Completed | Load_259441 | Duhaney - 210 | 2026-08-03 08:13 | 2026-08-03 08:14 | 2026-08-03 08:20 | 2026-08-03 13:45 | 2026-08-03 14:14 | 2026-08-03 14:22 | 2026-08-03 14:23 | 2026-08-03 14:23 |  |  | Fair | No | Premise found ok upon arrival Voltage 117V116V234V
Non-Outage | J.E.26.05.34753 | C001872407 | Orville Lee | Portmore | Completed | Load_259007 | Naggo Head - 610 | 2026-08-03 08:13 | 2026-08-03 08:14 | 2026-08-03 08:20 | 2026-08-03 11:08 | 2026-08-03 11:14 | 2026-08-03 11:15 | 2026-08-03 11:22 | 2026-08-03 11:22 |  |  | Fair | No | Premises found ok upon arrival Voltage 116v117v231v
Non-Outage | J.E.26.07.06969 | C001872412 | Edward Royal | KSAN | Completed | Load_557676 | West Kings House - 310 | 2026-08-03 08:13 | 2026-08-03 08:23 | 2026-08-03 11:11 | 2026-08-03 11:11 | 2026-08-03 11:11 | 2026-08-03 11:11 | 2026-08-03 11:11 | 2026-08-03 11:11 |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.07.39554 | C001872405 | Nicholas Dillon | St.Elizabeth | Completed | Load_262625 | Maggotty - 210 | 2026-08-03 08:13 | 2026-08-03 08:13 | 2026-08-03 09:28 | 2026-08-03 11:11 | 2026-08-03 11:11 | 2026-08-03 11:45 | 2026-08-03 11:46 | 2026-08-03 11:46 |  |  | Fair | Yes | Check and found corrosion at pothead clean joint and use 3 pen union before I left voltage is 116 115 phase to phase 231
Non-Outage | J.E.26.08.01644 | C001872410 | Fredrick Hamilton | KSAN | Completed | Load_267439 | West Kings House - 410 | 2026-08-03 08:13 | 2026-08-03 08:22 | 2026-08-03 08:26 | 2026-08-03 08:36 | 2026-08-03 08:36 | 2026-08-03 08:39 | 2026-08-03 08:39 | 2026-08-03 08:39 |  |  | Fair | No | Customer contacted and stated that power was restored fully previously Premises is ok
Non-Outage | J.E.26.08.03220 | C001872406 | Nicholas Dillon | St.Elizabeth | Completed | Load_245953 | Maggotty - 210 | 2026-08-03 08:13 | 2026-08-03 08:13 | 2026-08-03 09:29 | 2026-08-03 09:41 | 2026-08-03 09:52 | 2026-08-03 10:38 | 2026-08-03 10:39 | 2026-08-03 10:39 |  |  | Fair | Yes | Check and found neutral wire corrode at pole clean joint and use 2 one bolt clamp before I left voltage is 114 112 phase to phase 227
Non-Outage | J.E.26.08.03931 | C001872404 | Nicholas Dillon | St.Elizabeth | Completed | Load_248429 | Maggotty - 210 | 2026-08-03 08:13 | 2026-08-03 08:13 | 2026-08-03 11:06 | 2026-08-03 11:06 | 2026-08-03 11:06 | 2026-09-01 11:06 | 2026-08-03 11:08 | 2026-08-03 11:08 |  |  | Fair | No
Non-Outage | J.E.26.08.04305 | C001872411 | Javid Vernon | Westmoreland | Completed | Load_247902 | Paradise - 210 | 2026-08-03 08:13 | 2026-08-03 12:17 | 2026-08-03 15:02 | 2026-08-03 15:03 | 2026-08-03 15:02 | 2026-08-03 15:04 | 2026-08-03 15:05 | 2026-08-03 15:05 |  |  | Fair | No | Unable to locate customer and premises phone calls to customer number went unanswered and no good direction was given
Non-Outage | J.E.26.08.03052 | C001872413 | Fredrick Hamilton | KSAN | Completed | Load_262358 | West Kings House - 410 | 2026-08-03 08:14 | 2026-08-03 08:22 | 2026-08-03 08:26 | 2026-08-03 12:31 | 2026-08-03 12:45 | 2026-08-03 12:05 | 2026-08-03 13:10 | 2026-08-03 13:10 |  |  | Fair | No | Customer defect detected at location burnt wires at pothead customer advised to have same corrected 103v/111v obtained
Non-Outage | J.E.26.08.03395 | C001872414 | Dwayne Cohen | KSAN | Completed | Load_245677 | West Kings House - 410 | 2026-08-03 08:14 | 2026-08-03 08:19 | 2026-08-03 09:37 | 2026-08-03 09:38 | 2026-08-03 10:15 | 2026-08-03 10:30 | 2026-08-03 10:37 | 2026-08-03 10:37 |  |  | Fair | No | Repair burnt joint by transformer drop lead by using one 4/0 to 4/0 ampact , supply now restore.
Non-Outage | J.E.26.03.25506 | C001872419 | Royston Montague | St.Catherine | Completed | Load_238494 | New Michelton - 310 | 2026-08-03 08:16 | 2026-08-03 08:17 | 2026-08-03 08:21 | 2026-08-03 10:42 | 2026-08-03 11:38 | 2026-08-03 13:35 | 2026-08-03 13:35 | 2026-08-03 13:35 |  |  | Fair | No | Damage conductor . Same repair. Voltage found 116v voltage after voltage completion are, 235v 116v 117v
Non-Outage | J.E.26.03.25570 | C001872420 | Royston Montague | St.Catherine | Completed | Load_264405 | New Michelton - 310 | 2026-08-03 08:16 | 2026-08-03 08:17 | 2026-08-03 08:21 | 2026-08-03 16:14 | 2026-08-03 16:19 | 2026-08-03 16:19 | 2026-08-03 16:20 | 2026-08-03 16:20 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.03.28872 | C001872415 | Royston Montague | St.Catherine | Completed | Load_239795 | New Michelton - 210 | 2026-08-03 08:16 | 2026-08-03 08:17 | 2026-08-03 08:21 | 2026-08-03 16:20 | 2026-08-03 17:28 | 2026-08-03 17:35 | 2026-08-03 17:35 | 2026-08-03 17:35 |  |  | Fair | No | Not locating this premises, customer hang up when ask about status of location , several attempts to call back customer go without answer.
Non-Outage | J.E.26.03.33870 | C001872417 | Royston Montague | St.Catherine | Completed | Load_243352 | New Michelton - 310 | 2026-08-03 08:16 | 2026-08-03 08:17 | 2026-08-03 08:21 | 2026-08-03 13:40 | 2026-08-03 13:40 | 2026-08-03 13:41 | 2026-08-03 13:41 | 2026-08-03 13:41 |  |  | Fair | No | Not locating this premises. Multiple calls to customer phone go without answer. GPS coordinate on job not working.
Non-Outage | J.E.26.03.35014 | C001872416 | Royston Montague | St.Catherine | Completed | Load_248631 | Tredegar - 210 | 2026-08-03 08:16 | 2026-08-03 08:17 | 2026-08-03 08:21 | 2026-08-03 08:34 | 2026-08-03 09:29 | 2026-08-03 09:29 | 2026-08-03 09:29 | 2026-08-03 09:29 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.07.36055 | C001872421 | Andre Williams | Trelawny | Completed | Load_250171 | Greenwood - 210 | 2026-08-03 08:16 | 2026-08-03 08:17 | 2026-08-03 13:03 | 2026-08-03 13:03 | 2026-08-03 13:03 | 2026-08-03 13:04 | 2026-08-03 13:04 | 2026-08-03 13:04 |  |  | Fair | No | Customer low voltage issues resolved.
Non-Outage | J.E.26.07.38630 | C001872429 | Andre Williams | Trelawny | Completed | Load_302838 | Greenwood - 110 | 2026-08-03 08:16 | 2026-08-03 08:17 | 2026-08-03 08:22 | 2026-08-03 11:19 | 2026-08-03 12:40 | 2026-08-03 12:46 | 2026-08-03 12:47 | 2026-08-03 12:47 |  |  | Fair | No | Customer meter socket defective customer was advise voltage at meter. 111+114=225
Non-Outage | J.E.26.07.39331 | C001872428 | Andre Williams | Trelawny | Completed | Load_262457 | Greenwood - 110 | 2026-08-03 08:16 | 2026-08-03 08:17 | 2026-08-03 12:56 | 2026-08-03 12:56 | 2026-08-03 12:56 | 2026-08-03 13:00 | 2026-08-03 13:01 | 2026-08-03 13:01 |  |  | Fair | No | Customer was experiencing on and off supply during last week, customer says premises now with steady supply
Non-Outage | J.E.26.07.40260 | C001872427 | Andre Williams | Trelawny | Completed | Load_238453 | Greenwood - 110 | 2026-08-03 08:16 | 2026-08-03 08:17 | 2026-08-03 13:07 | 2026-08-03 13:07 | 2026-08-03 13:48 | 2026-08-03 14:07 | 2026-08-03 14:07 | 2026-08-03 14:07 |  |  | Fair | No | Clean coroded joint and change clamp at Jps pole
Non-Outage | J.E.26.08.00096 | C001872426 | Andre Williams | Trelawny | Completed | Load_255240 | Greenwood - 110 | 2026-08-03 08:16 | 2026-08-03 08:17 | 2026-08-03 08:23 | 2026-08-03 09:21 | 2026-08-03 09:56 | 2026-08-03 10:12 | 2026-08-03 10:12 | 2026-08-03 10:12 |  |  | Fair | No | Voltage on line 112+103=215 reffer to loses multiple illegal connections on phase with 103 volts
Non-Outage | J.E.26.08.00429 | C001872424 | Andre Williams | Trelawny | Completed | Load_292760 | Greenwood - 110 | 2026-08-03 08:16 | 2026-08-03 08:17 | 2026-08-03 10:14 | 2026-08-03 10:16 | 2026-08-03 10:42 | 2026-08-03 11:13 | 2026-08-03 11:14 | 2026-08-03 11:14 |  |  | Fair | No | Illegal conection near customer causing voltage drop at end of of line 101+102=203 voltage at transformer 115+115=230, reffer to loses to remove illegal wires
Non-Outage | J.E.26.08.04033 | C001872425 | Andre Williams | Trelawny | Completed | Load_251599 | Greenwood - 110 | 2026-08-03 08:16 | 2026-08-03 08:17 | 2026-08-03 08:24 | 2026-08-03 08:37 | 2026-08-03 09:04 | 2026-08-03 09:20 | 2026-08-03 09:20 | 2026-08-03 09:20 |  |  | Fair | No | Voltage at pothead, 113+112=225 volts no low voltage detected or single phase
Non-Outage | J.E.26.07.36063 | C001872444 | Andre Williams | Trelawny | Completed | Load_292409 | Greenwood - 210 | 2026-08-03 08:17 | 2026-08-03 08:19 | 2026-08-03 08:22 | 2026-08-03 12:53 | 2026-08-03 12:52 | 2026-08-03 12:55 | 2026-08-03 12:55 | 2026-08-03 12:55 |  |  | EarthMovement | No | Premises ok and with supply low voltage issue resolved the night before
Non-Outage | J.E.26.07.08405 | C001872445 | Evan Spaulding | St.Mary | Completed | Load_242932 | Annotto Bay - 210 | 2026-08-03 08:18 | 2026-08-03 08:20 | 2026-08-03 12:14 | 2026-08-03 12:15 | 2026-08-03 12:14 | 2026-08-03 12:15 | 2026-08-03 12:15 | 2026-08-03 12:15 |  |  | Fair | No | Issue was resolved.
Non-Outage | J.E.26.04.18957 | C001872447 | Royston Montague | St.Catherine | Completed | Load_269697 | New Michelton - 210 | 2026-08-03 08:19 | 2026-08-03 08:25 | 2026-08-03 08:30 | 2026-08-03 13:42 | 2026-08-03 14:11 | 2026-08-03 14:23 | 2026-08-03 14:24 | 2026-08-03 14:24 |  |  | Fair | No | Full voltage found 107v 110v 218v , customer confirmed all is well now.
Non-Outage | J.E.26.04.19581 | C001872446 | Royston Montague | St.Catherine | Completed | Load_259725 | New Michelton - 310 | 2026-08-03 08:19 | 2026-08-03 08:25 | 2026-08-03 08:30 | 2026-08-03 15:28 | 2026-08-03 16:13 | 2026-08-03 16:14 | 2026-08-03 16:14 | 2026-08-03 16:14 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.05.11514 | C001872448 | Royston Montague | St.Catherine | Completed | Load_252586 | New Michelton - 210 | 2026-08-03 08:20 | 2026-08-03 08:25 | 2026-08-03 08:30 | 2026-08-03 14:25 | 2026-08-03 15:27 | 2026-08-03 15:27 | 2026-08-03 15:27 | 2026-08-03 15:27 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.08.00098 | C001872450 | Roemello Brown | Trelawny | Completed | Load_252699 | Duncans - 210 | 2026-08-03 08:20 | 2026-08-03 08:21 | 2026-08-03 10:24 | 2026-08-03 14:08 | 2026-08-03 14:14 | 2026-08-03 14:14 | 2026-08-03 14:15 | 2026-08-03 14:15 |  |  | Fair | No | Premises found working okayVoltage found 116/116/232Voltage leave 116/116/232
Non-Outage | J.E.26.07.37354 | C001872451 | Roemello Brown |  | Completed |  |  | 2026-08-03 08:21 | 2026-08-03 08:21 | 2026-08-03 10:26 | 2026-08-03 10:29 | 2026-08-03 10:53 | 2026-08-03 11:32 | 2026-08-03 11:33 | 2026-08-03 11:33 |  |  | Fair | No | Corrosion at the pole side have clamps change Voltage found 117/89/206Voltage leave 117/117/234
Outage | J.E.26.08.04113 | C001872461 | Horace Malcolm | St.James | Completed | Load_262522 | Bogue - 510 | 2026-08-03 08:23 | 2026-08-03 08:24 | 2026-08-03 12:19 | 2026-08-03 12:20 | 2026-08-03 12:19 | 2026-08-03 12:22 | 2026-08-03 12:22 | 2026-08-03 12:22 |  |  | Fair | No | Check and found ok related to previous call job numbers 04416
Outage | J.E.26.08.03961 | C001872463 | Derrick Dawkins | St.James | Completed | Load_292067 | Bogue - 610 | 2026-08-03 08:24 | 2026-08-03 15:44 | 2026-08-03 18:47 | 2026-08-03 19:03 | 2026-08-03 20:17 | 2026-08-03 20:23 | 2026-08-03 20:24 | 2026-08-03 20:24 |  |  | Fair | No | Customer is more than 100 ft away from the jps pole refer back to field service
Outage | J.E.26.08.04319 | C001872462 | Dwayne Cohen | KSAN | Completed | Load_262972 | Washington Blvd - 610 | 2026-08-03 08:24 | 2026-08-03 08:26 | 2026-08-03 09:26 | 2026-08-03 09:27 | 2026-08-03 09:34 | 2026-08-03 09:35 | 2026-08-03 09:37 | 2026-08-03 09:37 |  |  | Fair | No | 15KVA Hexing Transformer found DEFECTIVE, business complex without supply.
Outage | J.E.26.08.04282 | C001872464 | Derrick Grubb | St.Thomas | Completed | Load_244001 | Good Year - 110 | 2026-08-03 08:25 | 2026-08-03 08:26 | 2026-08-03 14:01 | 2026-08-03 14:02 | 2026-08-03 15:22 | 2026-08-03 15:24 | 2026-08-03 15:24 | 2026-08-03 15:24 |  |  | Fair | No | Premises not located. Several calls to customer phone went unanswered.
Outage | J.E.26.08.04316 | C001872465 | Derrick Grubb | St.Thomas | Completed | Load_259414 | Good Year - 210 | 2026-08-03 08:25 | 2026-08-03 08:26 | 2026-08-03 11:59 | 2026-08-03 12:00 | 2026-08-03 12:49 | 2026-08-03 13:30 | 2026-08-03 13:30 | 2026-08-03 13:30 |  |  | Fair | No | Troubleshoot, voltage readings 98v, 117v, 220v. Bucket truck needed to carry out further checks.
Non-Outage | J.E.26.08.01360 | C001872478 | Fredrick Hamilton | KSAS | Completed | Load_242584 | Duhaney - 310 | 2026-08-03 08:27 | 2026-08-03 08:29 | 2026-08-03 08:39 | 2026-08-03 11:09 | 2026-08-03 11:14 | 2026-08-03 11:18 | 2026-08-03 11:18 | 2026-08-03 11:18 |  |  | Fair | No | Premises was visited and customer stated that power was restored fully Premises is ok
Non-Outage | J.E.26.08.03320 | C001872472 | Fredrick Hamilton | KSAS | Completed | Load_262405 | Duhaney - 310 | 2026-08-03 08:27 | 2026-08-03 08:29 | 2026-08-03 08:39 | 2026-08-03 09:00 | 2026-08-03 09:00 | 2026-08-03 09:01 | 2026-08-03 09:01 | 2026-08-03 09:01 |  |  | Fair | No | Customer was contacted and stated that power was restored fully Premises is ok
Non-Outage | J.E.26.08.03701 | C001872471 | Fredrick Hamilton | KSAN | Completed | Load_243463 | Hope - 510 | 2026-08-03 08:27 | 2026-08-03 08:29 | 2026-08-03 08:39 | 2026-08-03 13:14 | 2026-08-03 13:45 | 2026-08-03 13:47 | 2026-08-03 13:48 | 2026-08-03 13:48 |  |  | Fair | No | Premises found locked multiple calls to customer went to voicemail
Non-Outage | J.E.26.08.03718 | C001872470 | Milton Charlton | KSAN | Completed | Load_243463 | Hope - 510 | 2026-08-03 08:27 | 2026-08-04 08:19 | 2026-08-04 10:56 | 2026-08-04 10:57 | 2026-08-04 11:24 | 2026-08-04 11:25 | 2026-08-04 11:25 | 2026-08-04 11:25 |  |  | Fair | No | Found okay upon arrival. Readings at meter socket 118-119-238 volts.
Non-Outage | J.E.26.08.01075 | C001872479 | Fredrick Hamilton | KSAN | Completed | Load_579231 | Hope - 410 | 2026-08-03 08:28 | 2026-08-03 08:29 | 2026-08-03 08:39 | 2026-08-03 08:56 | 2026-08-03 08:56 | 2026-08-03 08:58 | 2026-08-03 08:58 | 2026-08-03 08:58 |  |  | Fair | No | Customer contacted and stated that power was restored fully previously Premises is ok
Non-Outage | J.E.26.08.01075 | C001872481 | Fredrick Hamilton | KSAN | Completed | Load_579231 | Hope - 410 | 2026-08-03 08:28 | 2026-08-03 08:31 | 2026-08-03 08:39 | 2026-08-03 09:02 | 2026-08-03 09:02 | 2026-08-03 09:03 | 2026-08-03 09:03 | 2026-08-03 09:03 |  |  | EarthMovement | No | Customer was contacted and stated that power was restored fully previously premises is ok
Non-Outage | J.E.26.08.01286 | C001872480 | Fredrick Hamilton | KSAN | Completed | Load_239167 | Washington Blvd - 410 | 2026-08-03 08:28 | 2026-08-03 08:29 | 2026-08-03 08:39 | 2026-08-03 12:29 | 2026-08-03 12:29 | 2026-08-03 12:30 | 2026-08-03 12:30 | 2026-08-03 12:30 |  |  | Fair | No | Multiple calls to customer went unanswered Premises found locked
Non-Outage | J.E.26.07.32477 | C001872486 | Rochaine Hussey | KSAN | Completed | Load_269867 | Constant Spring - 410 | 2026-08-03 08:29 | 2026-08-03 08:30 | 2026-08-03 10:05 | 2026-08-03 12:45 | 2026-08-03 12:55 | 2026-08-03 12:56 | 2026-08-03 12:56 | 2026-08-03 12:56 |  |  | Fair | No | Customer said issue was already resolved
Non-Outage | J.E.26.07.32960 | C001872484 | Rochaine Hussey | KSAN | Completed | Load_264054 | Constant Spring - 410 | 2026-08-03 08:29 | 2026-08-03 08:30 | 2026-08-03 10:01 | 2026-08-03 16:35 | 2026-08-03 16:34 | 2026-08-03 16:35 | 2026-08-03 16:35 | 2026-08-03 16:35 |  |  | Fair | No | Customer say the issue was resolved and Premesis is now found okay
Non-Outage | J.E.26.07.35505 | C001872485 | Rochaine Hussey | KSAN | Completed | Load_264612 | Constant Spring - 410 | 2026-08-03 08:29 | 2026-08-03 08:30 | 2026-08-03 11:08 | 2026-08-03 11:09 | 2026-08-03 12:37 | 2026-08-03 12:39 | 2026-08-03 12:39 | 2026-08-03 12:39 |  |  | Fair | No | 60ft of service wire was changed 3 clamp used109/113/222vIssue resolved
Non-Outage | J.E.26.08.02981 | C001872482 | Rochaine Hussey | KSAN | Completed | Load_264584 | Constant Spring - 410 | 2026-08-03 08:29 | 2026-08-03 08:30 | 2026-08-03 13:13 | 2026-08-03 13:14 | 2026-08-03 13:33 | 2026-08-03 14:19 | 2026-08-03 14:21 | 2026-08-03 14:21 |  |  | Fair | No | 25kv transformer was isolated Drop leads were cleaned 4 clamp usedIssue resolved 112/113/225v
Non-Outage | J.E.26.08.03901 | C001872483 | Rochaine Hussey | KSAN | Completed | Load_255038 | Constant Spring - 410 | 2026-08-03 08:29 | 2026-08-03 08:30 | 2026-08-03 09:59 | 2026-08-03 14:27 | 2026-08-03 14:26 | 2026-08-03 14:27 | 2026-08-03 14:27 | 2026-08-03 14:27 |  |  | Fair | No | Customer said issue was already resolved
Non-Outage | J.E.26.08.03484 | C001872500 | Odeanie Davis | KSAS | Completed | Load_244455 | Cane River - 610 | 2026-08-03 08:32 | 2026-08-03 08:33 | 2026-08-03 12:19 | 2026-08-03 14:45 | 2026-08-03 14:45 | 2026-08-03 15:22 | 2026-08-03 14:46 | 2026-08-03 14:46 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.03954 | C001872499 | Odeanie Davis | KSAS | Completed | Load_1002886 | Rockfort - 410 | 2026-08-03 08:32 | 2026-08-03 08:33 | 2026-08-03 12:19 | 2026-08-03 12:55 | 2026-08-03 12:59 | 2026-08-03 13:19 | 2026-08-03 13:19 | 2026-08-03 13:19 |  |  | Fair | No | 119v/84v at arrival, loose connection in meter socket corrected, 113v/113v & 226v after correction
Non-Outage | J.E.26.08.04161 | C001872497 | Odeanie Davis | KSAS | Completed | Load_241686 | Rockfort - 410 | 2026-08-03 08:32 | 2026-08-03 08:33 | 2026-08-03 11:11 | 2026-08-03 11:12 | 2026-08-03 11:11 | 2026-08-03 12:16 | 2026-08-03 12:16 | 2026-08-03 12:16 |  |  | Fair | No | 78v at arrival, open circuit at pothead and on customer’s line corrected, 4 penn union & 40ft twisted wire, 115v after correction
Non-Outage | J.E.26.08.04168 | C001872498 | Odeanie Davis | KSAS | Completed | Load_239845 | Rockfort - 410 | 2026-08-03 08:32 | 2026-08-03 08:33 | 2026-08-03 10:25 | 2026-08-03 10:25 | 2026-08-03 10:27 | 2026-08-03 11:08 | 2026-08-03 11:08 | 2026-08-03 11:08 |  |  | Fair | No | 99v at arrival, open circuit at secondary corrected, 2 penn union, 117v after correction
Non-Outage | J.E.26.08.04242 | C001872490 | Elvis Trowers | KSAS | Completed | Load_270202 | Greenwich - 510 | 2026-08-03 08:32 | 2026-08-03 08:37 | 2026-08-03 09:15 | 2026-08-03 09:16 | 2026-08-03 10:23 | 2026-08-03 11:03 | 2026-08-03 11:03 | 2026-08-03 11:03 |  |  | Fair | Yes | Happened to be internal when checked, customer was advised to contact an electrician to change breaker, voltage when checked was left at 112 +113=225 volts.
Non-Outage | J.E.26.08.04286 | C001872489 | Odeanie Davis | KSAS | Completed | Load_256788 | Rockfort - 410 | 2026-08-03 08:32 | 2026-08-03 08:33 | 2026-08-03 09:27 | 2026-08-03 09:29 | 2026-08-03 10:04 | 2026-08-03 10:10 | 2026-08-03 10:11 | 2026-08-03 10:11 |  |  | Fair | No | 113v/112v at arrival, open neutral at pothead corrected, 3 penn union, 115v/115v & 230v after correction
Non-Outage | J.E.26.08.01857 | C001872502 | Andrae Clarke | Portland | Completed | Load_239340 | Port Antonio - 410 | 2026-08-03 08:33 | 2026-08-03 08:38 | 2026-08-03 11:13 | 2026-08-03 11:14 | 2026-08-03 11:57 | 2026-08-03 00:35 | 2026-08-03 11:59 | 2026-08-03 11:59 |  |  | Fair | No | Check voltage 117/119/236Premises found ok
Non-Outage | J.E.26.08.03302 | C001872503 | Edward Royal | KSAS | Completed | Load_248351 | Duhaney - 410 | 2026-08-03 08:33 | 2026-08-03 08:34 | 2026-08-03 11:17 | 2026-08-03 11:17 | 2026-08-03 11:20 | 2026-08-03 11:21 | 2026-08-03 11:21 | 2026-08-03 11:21 | LowHangingWires |  | Fair | No | Customer have internal problems customer have defective stanchion pole advise customer to get a electrician to fix the problem
Non-Outage | J.E.26.08.04212 | C001872501 | Andrae Clarke | Portland | Completed | Load_256293 | Port Antonio - 310 | 2026-08-03 08:33 | 2026-08-03 08:38 | 2026-08-03 08:53 | 2026-08-03 08:53 | 2026-08-03 10:31 | 2026-08-03 10:32 | 2026-08-03 11:13 | 2026-08-03 11:13 |  |  | Fair | No | Replace broken wires use fifty ft of wire Three one bolt clamp Check voltage 119/123/241
Non-Outage | J.E.26.08.02563 | C001872507 | Odeanie Davis | KSAS | Completed | Load_259388 | Hunts Bay - 310 | 2026-08-03 08:34 | 2026-08-03 08:35 | 2026-08-03 12:19 | 2026-08-03 14:23 | 2026-08-03 14:42 | 2026-08-03 14:52 | 2026-08-03 14:44 | 2026-08-03 14:44 |  |  | Fair | No | Customer stated that it was a community outage and the power came back and they don’t have any power issues at this time
Non-Outage | J.E.26.08.02772 | C001872506 | Odeanie Davis | KSAS | Completed | Load_238569 | Rockfort - 410 | 2026-08-03 08:34 | 2026-08-03 08:35 | 2026-08-03 12:19 | 2026-08-03 14:44 | 2026-08-03 14:44 | 2026-08-03 15:09 | 2026-08-03 14:45 | 2026-08-03 14:45 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.02898 | C001872504 | Odeanie Davis | KSAS | Completed | Load_266339 | Rockfort - 410 | 2026-08-03 08:34 | 2026-08-03 08:35 | 2026-08-03 08:49 | 2026-08-03 08:50 | 2026-08-03 08:49 | 2026-08-03 09:14 | 2026-08-03 09:14 | 2026-08-03 09:14 |  |  | Fair | No | Drop lead from transformer seen burnt, field service team needed
Non-Outage | J.E.26.08.02831 | C001872510 | Odeanie Davis | KSAS | Completed | Load_268171 | Rockfort - 210 | 2026-08-03 08:36 | 2026-08-03 08:37 | 2026-08-03 12:19 | 2026-08-03 13:19 | 2026-08-03 13:19 | 2026-08-03 13:30 | 2026-08-03 13:20 | 2026-08-03 13:20 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.02983 | C001872509 | Odeanie Davis | KSAS | Completed | Load_242913 | Cane River - 410 | 2026-08-03 08:36 | 2026-08-03 08:37 | 2026-08-03 12:19 | 2026-08-03 13:21 | 2026-08-03 13:26 | 2026-08-03 14:22 | 2026-08-03 14:22 | 2026-08-03 14:22 |  |  | Fair | No | 113v/117v at arrival, corrosion at secondary corrected, 2 one bolt clamps, 115v/115v 230v after correction.
Outage | J.E.26.08.02816 | C001872519 | Christopher West | KSAS | Completed | Load_253196 | Duhaney - 210 | 2026-08-03 08:37 | 2026-08-03 08:38 | 2026-08-03 10:25 | 2026-08-03 10:26 | 2026-08-03 11:11 | 2026-08-03 11:20 | 2026-08-03 11:26 | 2026-08-03 11:26 |  |  | Fair | No | Found ok.
Outage | J.E.26.08.03421 | C001872522 | Christopher West | KSAS | Completed | Load_294474 | Duhaney - 210 | 2026-08-03 08:37 | 2026-08-03 08:38 | 2026-08-03 09:07 | 2026-08-03 09:08 | 2026-08-03 10:10 | 2026-08-03 10:11 | 2026-08-03 10:11 | 2026-08-03 10:11 |  |  | Fair | No | Premises found ok.
Outage | J.E.26.08.04284 | C001872524 | Collin Robinson | Portland | Completed | Load_349987 | Port Antonio - 410 | 2026-08-03 08:41 | 2026-08-03 08:43 | 2026-08-03 09:31 | 2026-08-03 09:32 | 2026-08-03 11:00 | 2026-08-03 11:40 | 2026-08-03 11:40 | 2026-08-03 11:40 |  |  | Fair | No | Customer was facing low voltage 99v, 118v went ahead and jump slicing sleeves and reconnect jumper
Outage | J.E.26.08.04367 | C001872581 | Kenroy Dale | Manchester | Completed | Load_251843 | Kendal - 210 | 2026-08-03 09:13 | 2026-08-03 21:20 | 2026-08-03 22:28 | 2026-08-03 22:29 | 2026-08-03 22:39 | 2026-08-03 22:39 | 2026-08-03 22:43 | 2026-08-03 22:43 | BrokenPole,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Badly leaning 35 class 6 CV concrete pole found, pole need urgent attention
Outage | J.E.26.08.04436 | C001872582 | Wayne Dillion | Manchester | Completed | Load_265085 | Spur Tree - 210 | 2026-08-03 09:16 | 2026-08-03 09:18 | 2026-08-03 10:03 | 2026-08-03 10:03 | 2026-08-03 10:03 | 2026-08-03 10:11 | 2026-08-03 10:11 | 2026-08-03 10:11 |  |  | Fair | No | Please refer this call to field service hexing box in area one customer without supply. No broken wire at hexing box #29171094.
Non-Outage | J.E.26.08.04370 | C001872594 | Jermaine Douglas |  | Completed |  |  | 2026-08-03 09:17 | 2026-08-03 21:29 | 2026-08-03 21:49 | 2026-08-03 21:50 | 2026-08-04 01:48 | 2026-08-04 01:48 | 2026-08-04 01:50 | 2026-08-04 01:50 | BrokenWire |  | Fair | No | Related to blown transformer fuse by opp 8 old hope rd.
Outage | J.E.26.08.04410 | C001872583 | Richard Watson | St.Elizabeth | Completed | Load_292920 | Maggotty - 110 | 2026-08-03 09:17 | 2026-08-03 09:18 | 2026-08-03 10:01 | 2026-08-03 10:02 | 2026-08-03 10:43 | 2026-08-03 11:21 | 2026-08-03 11:22 | 2026-08-03 11:22 | BrokenWire |  | Fair | No | Replace approximately 60ft of #6 triplex service wire, also use two #6-#6 service sleeves and two 1bolt clamps, voltage left inside meter socket 112v, 2wire service, customer was without electricity since the passage of hurricane Melissa.
Outage | J.E.26.08.04544 | C001872610 | Shamour Haughton | St.James | Completed | Load_557019 | Bogue - 310 | 2026-08-03 09:22 | 2026-08-03 09:23 | 2026-08-03 09:45 | 2026-08-03 09:46 | 2026-08-03 10:09 | 2026-08-03 10:09 | 2026-08-03 10:12 | 2026-08-03 10:12 | Fire |  | Fair | No | Found 30ft pole broken and leaning on customer fencing, after passing the bridge, it’s the 3rd left turn, please refer to maintenance
Non-Outage | J.E.26.08.04361 | C001872623 | Raymond Carr |  | Completed |  |  | 2026-08-03 09:30 | 2026-08-03 09:32 | 2026-08-03 10:05 | 2026-08-03 10:05 | 2026-08-03 11:19 | 2026-08-03 11:46 | 2026-08-03 11:44 | 2026-08-03 11:44 | BangingWires |  | SevereWind | No | Two spans of secondary found banged together, same was cleared and supply has been normalize.
Non-Outage | J.E.26.08.04374 | C001872624 | Raymond Carr |  | Completed |  |  | 2026-08-03 09:30 | 2026-08-03 09:32 | 2026-08-03 11:44 | 2026-08-03 11:45 | 2026-08-03 11:45 | 2026-08-03 | 2026-08-03 11:48 | 2026-08-03 11:48 | LeaningPole |  | Fair | No | Kindly refer leaning pole to maintenance department.
Outage | J.E.26.08.04667 | C001872625 | Richard Samuda | Manchester | Completed | Load_265086 | Spur Tree - 310 | 2026-08-03 09:30 | 2026-08-03 09:35 | 2026-08-03 09:58 | 2026-08-03 10:45 | 2026-08-03 11:06 | 2026-08-03 11:33 | 2026-08-03 11:34 | 2026-08-03 11:34 |  |  | Fair | No | Found 20amp junction blown caused by bushing crew cut bamboo on line replaced fuse customer back to normal
Non-Outage | J.E.26.08.04661 | C001872635 | Rusean Allen |  | Completed |  |  | 2026-08-03 09:33 | 2026-08-03 09:34 | 2026-08-03 11:55 | 2026-08-03 11:56 | 2026-08-03 11:55 | 2026-08-03 12:07 | 2026-08-03 12:08 | 2026-08-03 12:08 |  |  | Fair | No | 1x 30amp fuse found 1x 30amp fuse replaced.
Non-Outage | J.E.26.08.04666 | C001872634 | Roemello Brown | Trelawny | Completed | Load_255424 | Duncans - 210 | 2026-08-03 09:33 | 2026-08-03 09:34 | 2026-08-03 10:28 | 2026-08-03 11:33 | 2026-08-03 12:42 | 2026-08-03 12:42 | 2026-08-03 13:16 | 2026-08-03 13:16 |  |  | Fair | No | Neutral burn off at pole have it re-join Voltage found 168/62/230Voltage leave 116/114/230
Outage | J.E.26.08.04565 | C001872636 | Derrick Grubb | St.Thomas | Completed | Load_245426 | Good Year - 110 | 2026-08-03 09:35 | 2026-08-03 09:36 | 2026-08-03 13:30 | 2026-08-03 13:31 | 2026-08-03 13:56 | 2026-08-03 13:59 | 2026-08-03 13:59 | 2026-08-03 13:59 | BrokenWire |  | Fair | No | International issues found, customer were advised.
Outage | J.E.26.08.04576 | C001872637 | Stephen Taylor | St.Thomas | Completed | Load_252161 | Good Year - 110 | 2026-08-03 09:35 | 2026-08-03 15:52 | 2026-08-03 20:59 | 2026-08-03 21:00 | 2026-08-03 21:00 | 2026-08-03 21:00 | 2026-08-03 21:01 | 2026-08-03 21:01 |  |  | Fair | No | Call to customer and customer said power is back now and okay
Outage | J.E.26.08.03044 | C001872639 | Wan Carlos Scarlett | St.Catherine | Completed | Load_257449 | Twickenham - 210 | 2026-08-03 09:36 | 2026-08-03 09:37 | 2026-08-03 10:18 | 2026-08-03 10:38 | 2026-08-03 10:49 | 2026-08-03 11:15 | 2026-08-03 11:19 | 2026-08-03 11:19 |  |  | Fair | No | Refuse 10 Amp junction pole# 009980 nothing was found on primary line cause by lightning strike
Non-Outage | J.E.26.07.39652 | C001872647 | Edward Royal | KSAS | Completed | Load_261609 | Three Miles - 410 | 2026-08-03 09:40 | 2026-08-03 09:40 | 2026-08-03 12:02 | 2026-08-03 12:05 | 2026-08-03 12:09 | 2026-08-03 12:11 | 2026-08-03 12:11 | 2026-08-03 12:11 |  |  | Fair | No | Premises found close unable to communicate
Non-Outage | J.E.26.08.00461 | C001872660 | Daniel Lobar | Trelawny | Completed | Load_262699 | Duncans - 210 | 2026-08-03 09:47 | 2026-08-03 09:49 | 2026-08-04 13:16 | 2026-08-04 13:16 | 2026-08-04 13:18 | 2026-08-04 13:18 | 2026-08-04 13:18 | 2026-08-04 13:18 |  |  | Fair | No
Outage | J.E.26.08.04330 | C001872665 | Christopher Levy | KSAS | Completed | Load_259746 | Rockfort - 410 | 2026-08-03 09:47 | 2026-08-03 18:12 | 2026-08-03 18:29 | 2026-08-03 18:30 | 2026-08-03 20:26 | 2026-08-03 21:47 | 2026-08-03 21:56 | 2026-08-03 21:56 | BrokenWire |  | Fair | No | Twisted secondary and open secondary burn down. Repair circuit using 100 ft #2 service wire .splice twisted secondary 3 different places, remade 2 secondary jumpers ,splice and tension 2 triplex services. Use 10 one bolt clamps, one d-iron and 5 ft of #6 to repair service. A 50kva transformer was opened to carry out repairs . After repairs were completed the 50kva transformer was closed and customer power restored.
Outage | J.E.26.08.04341 | C001872667 | Jermaine Douglas | KSAS | Completed | Load_248302 | Greenwich - 410 | 2026-08-03 09:48 | 2026-08-03 09:52 | 2026-08-03 10:29 | 2026-08-03 10:30 | 2026-08-03 10:43 | 2026-08-03 10:48 | 2026-08-03 10:48 | 2026-08-03 10:48 |  |  | Fair | No | Customer found ok
Outage | J.E.26.08.04368 | C001872669 | Jermaine Douglas | KSAS | Completed | Load_256112 | Greenwich - 410 | 2026-08-03 09:48 | 2026-08-03 09:52 | 2026-08-03 10:05 | 2026-08-03 10:06 | 2026-08-03 10:11 | 2026-08-03 10:12 | 2026-08-03 10:12 | 2026-08-03 10:12 |  | Y | Fair | No | Customer found okay
Outage | J.E.26.08.04417 | C001872668 | Jermaine Douglas | KSAS | Completed | Load_238938 | Greenwich - 410 | 2026-08-03 09:48 | 2026-08-03 09:52 | 2026-08-03 10:49 | 2026-08-03 10:49 | 2026-08-03 11:26 | 2026-08-03 11:56 | 2026-08-03 11:56 | 2026-08-03 11:56 |  |  | Fair | No | Bank transformer 415 secondary, voltage readings 240vX3, 414v,415v, 414v. Customer was advised to get an electrician to carry checks.
Non-Outage | J.E.26.08.04716 | C001872670 | Jermaine Douglas | KSAS | Completed | Load_1003092 | Hunts Bay - 310 | 2026-08-03 09:51 | 2026-08-03 09:52 | 2026-08-03 11:57 | 2026-08-03 11:58 | 2026-08-03 12:23 | 2026-08-03 13:40 | 2026-08-03 13:40 | 2026-08-03 13:40 |  |  | SevereWind | No | Primary instrument fuse found blown, one 20amps fuse used to restore power.
Outage | J.E.26.08.04303 | C001872679 | Rusean Allen | KSAS | Completed | Load_300870 | Cane River - 410 | 2026-08-03 09:54 | 2026-08-03 09:55 | 2026-08-03 11:45 | 2026-08-03 11:45 | 2026-08-03 11:46 | 2026-08-03 11:52 | 2026-08-03 11:52 | 2026-08-03 11:52 |  |  | Fair | No | Found a 3 amps fuse Replace a 3 amps fuse
Non-Outage | J.E.26.07.40021 | C001872688 | Junior Scarlett | St.James | Completed | Load_239941 | Bogue - 610 | 2026-08-03 10:00 | 2026-08-03 10:01 | 2026-08-03 10:07 | 2026-08-03 13:08 | 2026-08-03 14:09 | 2026-08-03 15:00 | 2026-08-03 15:16 | 2026-08-03 15:16 |  |  | Fair | No | Gate lockVoltage found 114v 112v 224v
Non-Outage | J.E.26.08.04510 | C001872690 | Junior Scarlett | St.James | Completed | Load_252666 | Bogue - 510 | 2026-08-03 10:00 | 2026-08-03 10:01 | 2026-08-03 10:07 | 2026-08-03 10:25 | 2026-08-03 11:11 | 2026-08-03 11:42 | 2026-08-03 11:42 | 2026-08-03 11:42 |  |  | Fair | No | Gate lockedVoltage found 115v114v 228v
Non-Outage | J.E.26.08.04604 | C001872687 | Junior Scarlett | St.James | Completed | Load_243524 | Bogue - 510 | 2026-08-03 10:00 | 2026-08-03 10:01 | 2026-08-03 10:07 | 2026-08-03 11:55 | 2026-08-03 12:16 | 2026-08-03 12:33 | 2026-08-03 12:33 | 2026-08-03 12:33 |  |  | Fair | No | Require emergency team A small Area experience low voltage Voltage found 101v 112v 217v
Outage | J.E.26.08.02044 | C001872691 | Christopher West | St.Catherine | Completed | Load_242822 | Naggo Head - 510 | 2026-08-03 10:00 | 2026-08-03 10:01 | 2026-08-03 11:26 | 2026-08-03 11:26 | 2026-08-03 12:04 | 2026-08-03 13:12 | 2026-08-03 13:20 | 2026-08-03 13:20 |  |  | Fair | No | Service line supplying 3 meters had corroded connections, used 3 clamps for repairs, V/R 118v x2 236v, customers now ok.
Outage | J.E.26.08.04407 | C001872692 | Jermaine Douglas | KSAS | Completed | Load_291801 | Hunts Bay - 810 | 2026-08-03 10:01 | 2026-08-03 10:02 | 2026-08-03 10:13 | 2026-08-03 10:13 | 2026-08-03 10:28 | 2026-08-03 10:29 | 2026-08-03 10:29 | 2026-08-03 10:29 |  |  | Fair | No | Customer found ok
Non-Outage | J.E.26.08.04301 | C001872697 | Fitzroy Turner |  | Completed |  |  | 2026-08-03 10:02 | 2026-08-03 10:04 | 2026-08-03 10:48 | 2026-08-03 10:49 | 2026-08-03 11:05 | 2026-08-03 11:09 | 2026-08-03 11:14 | 2026-08-03 11:14 |  |  | Fair | No | Found 50amps junction fuse blown along Spanish town road close to maxfield Ave 50amp fuse replaced supply restored to the areas
Outage | J.E.26.08.04398 | C001872699 | Fitzroy Turner | KSAS | Completed | Load_1002953 | Hunts Bay - 210 | 2026-08-03 10:03 | 2026-08-03 10:04 | 2026-08-03 16:22 | 2026-08-03 16:23 | 2026-08-03 16:50 | 2026-08-03 19:36 | 2026-08-03 20:25 | 2026-08-03 20:25 |  |  | Fair | No | Found 3 span primary line cut down use 350ft #2 aluminum and 4 splicing sleeve and 4 #2 ampact to carry out repair.at at the intersection of Barry st and dukes st at LAB 6/422 switches top burnt off use one 4/0 crimping sleeve and one 4/0 ampact to carry out repair SWITCHES POINT LAB6-374 insulation point.
Outage | J.E.26.08.04784 | C001872698 | Collin Robinson | Portland | Completed | Load_260170 | Port Antonio - 410 | 2026-08-03 10:03 | 2026-08-03 10:06 | 2026-08-03 12:36 | 2026-08-03 12:36 | 2026-08-03 13:00 | 2026-08-03 13:01 | 2026-08-03 13:02 | 2026-08-03 13:02 |  |  | Fair | No | Unable to locate
Outage | J.E.26.08.03081 | C001872700 | Wan Carlos Scarlett | Portmore | Completed | Load_257194 | Twickenham - 210 | 2026-08-03 10:04 | 2026-08-03 10:05 | 2026-08-03 12:23 | 2026-08-03 12:29 | 2026-08-03 12:44 | 2026-08-03 13:01 | 2026-08-03 13:02 | 2026-08-03 13:02 | LeakingTransformer |  | Fair | No | Refuse 8 amp junction no pole # was found nothing was found on primary line cause by lightning strike
Outage | J.E.26.08.04697 | C001872705 | Dwayne Cohen | KSAN | Completed | Load_250346 | West Kings House - 410 | 2026-08-03 10:11 | 2026-08-03 10:12 | 2026-08-03 10:37 | 2026-08-03 10:37 | 2026-08-03 10:47 | 2026-08-03 10:49 | 2026-08-03 10:53 | 2026-08-03 10:53 | BrokenWire |  | Fair | No | (Bank of 3 transformers ) ….167KVA lighting Transformer found leaking heavily need to change ASAP.
Outage | J.E.26.08.04331 | C001872713 | Wan Carlos Scarlett | Portmore | Completed | Load_256638 | Naggo Head - 510 | 2026-08-03 10:15 | 2026-08-03 10:16 | 2026-08-03 12:03 | 2026-08-03 12:04 | 2026-08-03 12:03 | 2026-08-03 12:26 | 2026-08-03 12:28 | 2026-08-03 12:28 |  |  | Fair | No | Refuse 20 Amp junction no pole # was found on primary nothing was found on primary line refuse 167 KVA Transformer with a 15 amp fuse no pole # was found nothing was found on secondary line cause by lightning strike
Outage | J.E.26.08.04746 | C001872715 | Daniel Francis | St.Ann | Completed | Load_246241 | Roaring River - 410 | 2026-08-03 10:16 | 2026-08-03 10:18 | 2026-08-03 11:33 | 2026-08-03 11:34 | 2026-08-03 11:33 | 2026-08-03 12:30 | 2026-08-03 12:32 | 2026-08-03 12:32 |  |  | Fair | No | Remade switch bottom jumper
Non-Outage | J.E.26.08.04701 | C001872717 | Daniel Francis |  | Completed |  |  | 2026-08-03 10:17 | 2026-08-03 10:18 | 2026-08-03 10:32 | 2026-08-03 10:33 | 2026-08-03 10:32 | 2026-08-03 10:58 | 2026-08-03 11:06 | 2026-08-03 11:06 | Fire |  | SevereWind | No | Found secondary phase resting close neutral cause by defective cross arm need replacement
Outage | J.E.26.08.04801 | C001872770 | Richman Whyte | Westmoreland | Completed | Load_259377 | Paradise - 310 | 2026-08-03 10:34 | 2026-08-03 10:35 | 2026-08-03 10:59 | 2026-08-03 10:59 | 2026-08-03 10:59 | 2026-08-03 10:59 | 2026-08-03 10:59 | 2026-08-03 10:59 |  |  | Fair | No | St James call
Outage | J.E.26.08.04817 | C001872769 | Ryan Richards | Manchester | Completed | Load_253480 | Kendal - 210 | 2026-08-03 10:34 | 2026-08-03 10:35 | 2026-08-03 11:14 | 2026-08-03 11:31 | 2026-08-03 13:18 | 2026-08-03 14:48 | 2026-08-03 14:48 | 2026-08-03 14:48 |  |  | Fair | No | Trip 40 amp trip savers found trip at Troy LAB6-817 line patrol nothing found trip Saver was reclose all customers are now with supply
Outage | J.E.26.08.04858 | C001872786 | Evan Spaulding | St.Mary | Completed | Load_250415 | Annotto Bay - 210 | 2026-08-03 10:45 | 2026-08-03 10:46 | 2026-08-03 10:52 | 2026-08-03 10:53 | 2026-08-03 11:27 | 2026-08-03 12:12 | 2026-08-03 12:14 | 2026-08-03 12:14 |  | Y | Rains | No | Cut coconut tree limbs from line and replace 1-25 amps junction fuse at pole number 0005305.
Outage | J.E.26.08.01845 | C001872794 | Ricky Hall | St.Catherine | Completed | Load_261693 | Tredegar - 510 | 2026-08-03 10:47 | 2026-08-03 10:59 | 2026-08-03 11:05 | 2026-08-03 12:01 | 2026-08-03 12:00 | 2026-08-03 12:00 | 2026-08-03 12:01 | 2026-08-03 12:01 |  |  | Fair | No | Call was duplicated
Outage | J.E.26.08.02924 | C001872787 | Wan Carlos Scarlett | St.Catherine | Completed | Load_260900 | Twickenham - 210 | 2026-08-03 10:47 | 2026-08-03 10:48 | 2026-08-03 11:03 | 2026-08-03 11:20 | 2026-08-03 11:23 | 2026-08-03 11:23 | 2026-08-03 11:24 | 2026-08-03 11:24 |  |  | Fair | No | Customer confirmed power supply was restored from yesterday check and found okay
Outage | J.E.26.08.04283 | C001872788 | Wan Carlos Scarlett | St.Catherine | Completed | Load_291212 | Twickenham - 210 | 2026-08-03 10:47 | 2026-08-03 10:48 | 2026-08-03 10:56 | 2026-08-03 14:18 | 2026-08-03 14:51 | 2026-08-03 15:25 | 2026-08-03 15:26 | 2026-08-03 15:26 |  |  | Fair | No | Reach on location been calling customer but got no answer premises closed
Outage | J.E.26.08.01845 | C001872795 | Ricky Hall | St.Catherine | Completed | Load_261693 | Tredegar - 510 | 2026-08-03 10:48 | 2026-08-03 10:59 | 2026-08-03 11:05 | 2026-08-03 11:06 | 2026-08-03 11:34 | 2026-08-03 11:58 | 2026-08-03 11:59 | 2026-08-03 11:59 |  |  | Fair | No | Splice and reconnect 3W service mid span use 10’#6/triplex 3 pen union 118/117/235
Outage | J.E.26.08.01845 | C001872800 | Ricky Hall | St.Catherine | Completed | Load_261693 | Tredegar - 510 | 2026-08-03 10:48 | 2026-08-03 10:59 | 2026-08-03 11:07 | 2026-08-03 12:01 | 2026-08-03 12:01 | 2026-08-03 12:01 | 2026-08-03 12:01 | 2026-08-03 12:01 |  |  | Fair | No | Call was duplicated
Outage | J.E.26.08.02825 | C001872797 | Ricky Hall | St.Catherine | Completed | Load_573434 | Tredegar - 510 | 2026-08-03 10:48 | 2026-08-03 10:59 | 2026-08-03 13:38 | 2026-08-03 14:13 | 2026-08-03 14:33 | 2026-08-03 14:34 | 2026-08-03 14:34 | 2026-08-03 14:34 |  |  | Fair | No | Premises closed
Outage | J.E.26.08.03971 | C001872798 | Ricky Hall | St.Catherine | Completed | Load_269173 | Tredegar - 510 | 2026-08-03 10:48 | 2026-08-03 10:59 | 2026-08-03 13:38 | 2026-08-03 13:39 | 2026-08-03 14:12 | 2026-08-03 14:12 | 2026-08-03 14:12 | 2026-08-03 14:12 |  |  | Fair | No | Area found with supply
Outage | J.E.26.08.04862 | C001872796 | Ricky Hall | St.Catherine | Completed | Load_247500 | Tredegar - 510 | 2026-08-03 10:48 | 2026-08-03 10:59 | 2026-08-03 12:02 | 2026-08-03 13:38 | 2026-08-03 13:37 | 2026-08-03 13:38 | 2026-08-03 13:38 | 2026-08-03 13:38 |  |  | Fair | No | Call was duplicated
Outage | J.E.26.08.04862 | C001872799 | Ricky Hall | St.Catherine | Completed | Load_247500 | Tredegar - 510 | 2026-08-03 10:48 | 2026-08-03 10:59 | 2026-08-03 12:02 | 2026-08-03 12:02 | 2026-08-03 12:29 | 2026-08-03 13:36 | 2026-08-03 13:37 | 2026-08-03 13:37 |  |  | SevereWind | No | Retention banging secondary lines use replace blow 2 amps junction fuse 25 kva
Outage | J.E.26.08.04293 | C001872802 | Daniel Francis | St.Ann | Completed | Load_242214 | Cardiff Hall - 210 | 2026-08-03 10:50 | 2026-08-03 10:55 | 2026-08-03 14:57 | 2026-08-03 14:57 | 2026-08-03 14:57 | 2026-08-03 14:49 | 2026-08-03 15:00 | 2026-08-03 15:00 |  |  | Fair | No | Internal fault
Outage | J.E.26.08.04618 | C001872803 | Daniel Francis | St.Ann | Completed | Load_258977 | Ocho Rios - 310 | 2026-08-03 10:51 | 2026-08-03 10:55 | 2026-08-03 13:43 | 2026-08-03 13:44 | 2026-08-03 13:43 | 2026-08-03 13:44 | 2026-08-03 13:47 | 2026-08-03 13:47 |  |  | Fair | No | Please refer to fiieldservice
Outage | J.E.26.08.04755 | C001872812 | Shamour Haughton | St.James | Completed | Load_269068 | Bogue - 310 | 2026-08-03 10:54 | 2026-08-03 10:56 | 2026-08-03 14:07 | 2026-08-03 14:07 | 2026-08-03 14:07 | 2026-08-03 14:07 | 2026-08-03 14:07 | 2026-08-03 14:07 |  |  | Fair | No | Related to previous calls
Outage | J.E.26.08.04831 | C001872811 | Shamour Haughton | St.James | Completed | Load_249176 | Bogue - 310 | 2026-08-03 10:54 | 2026-08-03 10:56 | 2026-08-03 12:15 | 2026-08-03 12:15 | 2026-08-03 13:29 | 2026-08-03 13:55 | 2026-08-03 13:59 | 2026-08-03 13:59 |  |  | Fair | No | Found 1,50amp junction fuse blown, refuse 80amp junction
Outage | J.E.26.08.04776 | C001872817 | Derrick Dawkins | St.James | Completed | Load_249158 | Bogue - 610 | 2026-08-03 10:57 | 2026-08-03 15:44 | 2026-08-03 17:42 | 2026-08-03 17:42 | 2026-08-03 17:42 | 2026-08-03 17:42 | 2026-08-03 17:43 | 2026-08-03 17:43 |  |  | Rains | No | Checked and found ok
Outage | J.E.26.08.04849 | C001872818 | Derrick Dawkins | St.James | Completed | Load_239941 | Bogue - 610 | 2026-08-03 10:58 | 2026-08-03 15:44 | 2026-08-03 17:43 | 2026-08-03 17:54 | 2026-08-03 17:54 | 2026-08-03 18:39 | 2026-08-03 18:40 | 2026-08-03 18:40 | BrokenWire |  | Fair | No | Found customer service wire burned due to slack connection clean and remade joint voltage 117/116=235
Outage | J.E.26.08.04899 | C001872819 | Fitzroy Turner | KSAS | Completed | Load_267774 | Hunts Bay - 510 | 2026-08-03 10:59 | 2026-08-03 11:21 | 2026-08-04 01:52 | 2026-08-04 01:53 | 2026-08-04 01:53 | 2026-08-04 01:53 | 2026-08-04 01:54 | 2026-08-04 01:54 |  |  | Fair | No | Customer supply restored after change defective drop out switch
Outage | J.E.26.08.04917 | C001872821 | Rusean Allen | KSAS | Completed | Load_257326 | Cane River - 610 | 2026-08-03 11:02 | 2026-08-03 11:04 | 2026-08-03 12:08 | 2026-08-03 12:09 | 2026-08-03 12:17 | 2026-08-03 12:24 | 2026-08-03 12:25 | 2026-08-03 12:25 |  |  | Fair | No | 1x 5amp fuse found 1x 5amp fuse replaced
Outage | J.E.26.08.04897 | C001872829 | Roxroy Needham | St.Ann | Completed | Load_239695 | Cardiff Hall - 310 | 2026-08-03 11:03 | 2026-08-03 11:14 | 2026-08-03 14:41 | 2026-08-03 14:42 | 2026-08-03 14:41 | 2026-08-03 14:34 | 2026-08-03 14:42 | 2026-08-03 14:42 |  |  | Fair | No | Premises found ok call customer and customer say that the light is ok
Non-Outage | J.E.26.08.04461 | C001872833 | Nicholas Dillon | St.Elizabeth | Completed | Load_247837 | Maggotty - 110 | 2026-08-03 11:04 | 2026-08-03 11:05 | 2026-08-03 14:56 | 2026-08-03 14:56 | 2026-08-03 14:57 | 2026-08-03 14:57 | 2026-08-03 15:01 | 2026-08-03 15:01 |  |  | Fair | No | Check voltage before at meter 96 109 phase to phase 204 whole area experiencing low voltage. Refer to maintenance to replace damage transformer
Outage | J.E.26.08.04416 | C001872831 | Neville Spencer | Clarendon | Completed | Load_251560 | Parnassus - 310 | 2026-08-03 11:04 | 2026-08-03 11:07 | 2026-08-03 12:13 | 2026-08-03 12:14 | 2026-08-03 12:42 | 2026-08-03 13:28 | 2026-08-03 13:30 | 2026-08-03 13:30 |  |  | Fair | No | Cleared bird from xmfr pole renew blown 10 amp j/ fuse at pole # 013732 & 20 amp j/ fuses area restored.
Outage | J.E.26.08.04419 | C001872830 | Neville Spencer | Clarendon | Completed | Load_406285 | Parnassus - 310 | 2026-08-03 11:04 | 2026-08-03 11:07 | 2026-08-03 13:30 | 2026-08-03 13:31 | 2026-08-03 13:30 | 2026-08-03 13:30 | 2026-08-03 13:34 | 2026-08-03 13:34 | Fire |  | Fair | No | Cleared bird from xmfr pole renew blown 10 amp j/ fuse at pole #. 013732 & 20 amp j/ fuse area restored.
Outage | J.E.26.08.04748 | C001872832 | Neville Spencer | Clarendon | Completed | Load_252849 | Parnassus - 310 | 2026-08-03 11:04 | 2026-08-03 11:07 | 2026-08-03 11:26 | 2026-08-03 11:26 | 2026-08-03 11:43 | 2026-08-03 11:43 | 2026-08-03 12:13 | 2026-08-03 12:13 | Fire |  | Fair | No | Found slack phase and neutral Conductor. Open 25 kva xmfr at pole # 0124148 retention 2 spans of secondary phase and neutral conductor supply restored.
Outage | J.E.26.08.04835 | C001872836 | Collin Robinson | Portland | Completed | Load_572639 | Port Antonio - 410 | 2026-08-03 11:09 | 2026-08-03 11:22 | 2026-08-03 11:40 | 2026-08-03 11:41 | 2026-08-03 12:29 | 2026-08-03 12:36 | 2026-08-03 12:36 | 2026-08-03 12:36 |  |  | Fair | No | Customer meter and meter socket burn Advice customer to get electrician to change socket
Outage | J.E.26.08.04297 | C001872837 | Fitzroy Turner | KSAS | Completed | Load_239100 | Hunts Bay - 410 | 2026-08-03 11:10 | 2026-08-03 11:20 | 2026-08-03 12:35 | 2026-08-03 13:27 | 2026-08-03 13:26 | 2026-08-03 13:27 | 2026-08-03 13:29 | 2026-08-03 13:29 |  |  | Fair | No | Found 30 amps junction fuse blown at pole #551766 replaced one 30amps junction fuse supply restored to the areas
Outage | J.E.26.08.04455 | C001872844 | Jermaine Douglas | KSAS | Completed | Load_256501 | Hunts Bay - 310 | 2026-08-03 11:19 | 2026-08-03 11:20 | 2026-08-03 13:44 | 2026-08-03 13:44 | 2026-08-03 14:20 | 2026-08-03 15:12 | 2026-08-03 15:12 | 2026-08-03 15:12 |  |  | Fair | No | Defective 25kva lightning arrester replaced using one 18kv arrestor and one 2 amps fuse.
Outage | J.E.26.08.04808 | C001872845 | Richard Nicholas | St.Catherine | Completed | Load_240706 | Twickenham - 310 | 2026-08-03 11:20 | 2026-08-04 11:38 | 2026-08-04 13:01 | 2026-08-04 13:02 | 2026-08-04 13:32 | 2026-08-04 14:39 | 2026-08-04 14:40 | 2026-08-04 14:40 |  |  | Fair | No | Remade slack 3w phase and neutral joint at pothead,3 clamp was use.voltage reading 118,122 and 240v.
Outage | J.E.26.08.04839 | C001872846 | Christopher West | St.Catherine | Completed | Load_259799 | Twickenham - 310 | 2026-08-03 11:20 | 2026-08-04 09:05 | 2026-08-04 09:47 | 2026-08-04 09:48 | 2026-08-04 09:47 | 2026-08-04 09:48 | 2026-08-04 09:55 | 2026-08-04 09:55 |  |  | Fair | No | Premises found ok.
Outage | J.E.26.08.04842 | C001872847 | Fitzroy Turner | KSAS | Completed | Load_262052 | Hunts Bay - 510 | 2026-08-03 11:21 | 2026-08-03 11:34 | 2026-08-03 11:50 | 2026-08-03 11:51 | 2026-08-03 11:51 | 2026-08-03 11:51 | 2026-08-03 11:51 | 2026-08-03 11:51 |  |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.08.04582 | C001872850 | Roxroy Needham | St.Ann | Completed | Load_250923 | Cardiff Hall - 310 | 2026-08-03 11:25 | 2026-08-03 11:37 | 2026-08-03 14:40 | 2026-08-03 14:40 | 2026-08-03 14:40 | 2026-08-03 14:38 | 2026-08-03 14:41 | 2026-08-03 14:41 |  |  | Fair | No | Premises found ok call customer and customer say that the light is ok
Outage | J.E.26.08.04689 | C001872857 | Swon Miller | St.James | Completed | Load_574245 | Rose Hall - 210 | 2026-08-03 11:31 | 2026-08-03 11:32 | 2026-08-03 14:03 | 2026-08-03 14:05 | 2026-08-03 14:04 | 2026-08-11 02:08 | 2026-08-03 14:14 | 2026-08-03 14:14 |  |  | Fair | No | Check and found 2,50 amp junction fuse blown cause by contamination replace 2 50 amp junction fuse at pole number 433496
Outage | J.E.26.08.04964 | C001872858 | Swon Miller | St.James | Completed | Load_259452 | Rose Hall - 210 | 2026-08-03 11:31 | 2026-08-03 11:32 | 2026-08-03 12:50 | 2026-08-03 14:15 | 2026-08-03 14:46 | 2026-08-18 02:40 | 2026-08-03 14:53 | 2026-08-03 14:53 | Fire |  | Fair | No | Check and found area okay no fire found
Outage | J.E.26.08.04961 | C001872861 | Rusean Allen | KSAN | Completed | Load_269301 | West Kings House - 410 | 2026-08-03 11:33 | 2026-08-03 11:34 | 2026-08-03 12:21 | 2026-08-03 13:02 | 2026-08-03 13:08 | 2026-08-03 13:10 | 2026-08-03 13:11 | 2026-08-03 13:11 |  |  | Fair | No | Meter was reconnected by customer service department
Non-Outage | J.E.26.08.04543 | C001872864 | Moses Elliston |  | Completed |  |  | 2026-08-03 11:38 | 2026-08-03 11:38 | 2026-08-03 12:26 | 2026-08-03 16:09 | 2026-08-03 16:09 | 2026-08-03 15:30 | 2026-08-03 16:10 | 2026-08-03 16:10 |  |  | Fair | No | Credit added to prepaid account
Outage | J.E.26.08.05003 | C001872865 | Milton Charlton | KSAN | Completed | Load_265695 | Hope - 510 | 2026-08-03 11:38 | 2026-08-03 11:41 | 2026-08-03 12:44 | 2026-08-03 12:45 | 2026-08-03 13:54 | 2026-08-03 14:05 | 2026-08-03 14:27 | 2026-08-03 14:27 |  |  | Fair | No | Unable to locate meter #1924983that is on the report Meter# at the premises is #3027466 this meter is disconnected for an amount over 200,000.00. Meter mix up . Refer to field service.
Outage | J.E.26.08.04787 | C001872867 | Moses Elliston | St.Catherine | Completed | Load_293139 | Rhodens Pen - 210 | 2026-08-03 11:40 | 2026-08-03 11:40 | 2026-08-04 10:34 | 2026-08-04 10:34 | 2026-08-04 10:34 | 2026-08-04 10:34 | 2026-08-04 10:35 | 2026-08-04 10:35 |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.08.04721 | C001872868 | Moses Elliston | St.Catherine | Completed | Load_239209 | Tredegar - 510 | 2026-08-03 11:41 | 2026-08-03 11:41 | 2026-08-03 17:42 | 2026-08-03 17:43 | 2026-08-03 17:42 | 2026-08-03 17:45 | 2026-08-03 17:46 | 2026-08-03 17:46 |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.08.04859 | C001872872 | Christopher West | St.Catherine | Completed | Load_262197 | Twickenham - 210 | 2026-08-03 11:45 | 2026-08-03 11:46 | 2026-08-03 13:37 | 2026-08-03 13:38 | 2026-08-03 14:29 | 2026-08-03 14:52 | 2026-08-03 14:52 | 2026-08-03 14:52 |  |  | Fair | No | Found ok.
Non-Outage | J.E.26.07.19940 | C001872875 | Vivian Gordon | St.James | Completed | Load_239760 | Bogue - 610 | 2026-08-03 11:47 | 2026-08-03 11:48 | 2026-08-03 12:41 | 2026-08-03 12:42 | 2026-08-03 12:41 | 2026-08-03 12:44 | 2026-08-03 12:46 | 2026-08-03 12:46 |  |  | Fair | No | Premises found locked. No occupant seen. Meter looks damaged from outside. Inaccessible.
Outage | J.E.26.07.22999 | C001872874 | Vivian Gordon | St.James | Completed | Load_556247 | Bogue - 610 | 2026-08-03 11:47 | 2026-08-03 11:48 | 2026-08-03 15:03 | 2026-08-03 15:04 | 2026-08-03 15:03 | 2026-08-03 13:01 | 2026-08-03 15:06 | 2026-08-03 15:06 |  |  | Fair | No | Open circuit found corrected. Customer advised.
Outage | J.E.26.07.24045 | C001872873 | Vivian Gordon | St.James | Completed | Load_556273 | Bogue - 610 | 2026-08-03 11:47 | 2026-08-03 11:48 | 2026-08-03 14:30 | 2026-08-03 14:30 | 2026-08-03 14:30 | 2026-08-03 14:37 | 2026-08-03 14:38 | 2026-08-03 14:38 |  |  | Fair | No | Single phase detected. Same corrected
Outage | J.E.26.08.04941 | C001872881 | Milton Charlton | KSAN | Completed | Load_568478 | Hope - 510 | 2026-08-03 11:49 | 2026-08-03 12:00 | 2026-08-03 14:27 | 2026-08-03 14:27 | 2026-08-03 16:22 | 2026-08-03 16:30 | 2026-08-03 16:23 | 2026-08-03 16:23 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.04991 | C001872884 | Rusean Allen | KSAS | Completed | Load_300874 | Cane River - 410 | 2026-08-03 11:50 | 2026-08-03 12:00 | 2026-08-03 13:11 | 2026-08-03 13:12 | 2026-08-03 13:17 | 2026-08-03 13:18 | 2026-08-03 13:18 | 2026-08-03 13:18 | BrokenWire |  | Fair | No | Maintenance department already aware of broken pole
Outage | J.E.26.08.04993 | C001872885 | Rusean Allen | KSAS | Completed | Load_242965 | Cane River - 410 | 2026-08-03 11:50 | 2026-08-03 12:00 | 2026-08-03 12:21 | 2026-08-03 13:51 | 2026-08-03 16:27 | 2026-08-03 16:28 | 2026-08-03 16:28 | 2026-08-03 16:28 | BrokenWire |  | Fair | No | Meter was reconnected by customer service
Non-Outage | J.E.26.08.04672 | C001872892 | Roxroy Needham |  | Completed |  |  | 2026-08-03 11:52 | 2026-08-03 11:55 | 2026-08-03 12:04 | 2026-08-03 12:38 | 2026-08-03 12:38 | 2026-08-03 12:39 | 2026-08-03 12:39 | 2026-08-03 12:39 | BrokenWire |  | Fair | No | Premises found ok
Outage | J.E.26.08.04125 | C001872893 | Wan Carlos Scarlett | Portmore | Completed | Load_248381 | Naggo Head - 510 | 2026-08-03 11:53 | 2026-08-03 11:55 | 2026-08-03 13:04 | 2026-08-03 13:04 | 2026-08-03 13:31 | 2026-08-03 13:43 | 2026-08-03 13:59 | 2026-08-03 13:59 |  |  | Fair | No | Refuse 25 KVA transformer with 3 Amp fuse no pole # was found nothing was found on primary line
Outage | J.E.26.07.23444 | C001872898 | Vivian Gordon | St.James | Completed | Load_269651 | Bogue - 310 | 2026-08-03 11:56 | 2026-08-03 11:59 | 2026-08-04 12:09 | 2026-08-04 12:09 | 2026-08-04 12:09 | 2026-08-04 12:12 | 2026-08-04 12:13 | 2026-08-04 12:13 |  |  | Fair | No | Supply found corrected
Outage | J.E.26.07.24759 | C001872895 | Vivian Gordon | St.James | Completed | Load_262175 | Bogue - 310 | 2026-08-03 11:56 | 2026-08-03 11:59 | 2026-08-03 16:31 | 2026-08-03 16:32 | 2026-08-03 16:32 | 2026-08-03 16:16 | 2026-08-03 16:36 | 2026-08-03 16:36 |  |  | Fair | No | Open circuit corrected. No occupant seen.
Outage | J.E.26.07.38539 | C001872896 | Vivian Gordon | St.James | Completed | Load_249504 | Bogue - 310 | 2026-08-03 11:56 | 2026-08-03 11:59 | 2026-08-03 13:41 | 2026-08-03 13:42 | 2026-08-03 13:42 | 2026-08-03 13:25 | 2026-08-03 13:49 | 2026-08-03 13:49 | Wire cluster Traffic |  | Fair | No | Single phasing detected and corrected.
Non-Outage | J.E.26.06.31587 | C001872909 | Vivian Gordon |  | Completed |  |  | 2026-08-03 11:57 | 2026-08-03 11:59 | 2026-08-04 12:14 | 2026-08-04 12:15 | 2026-08-04 12:14 | 2026-08-04 12:15 | 2026-08-04 12:16 | 2026-08-04 12:16 |  |  | Fair | No | Supply found corrected
Non-Outage | J.E.26.07.35998 | C001872905 | Vivian Gordon |  | Completed |  |  | 2026-08-03 11:57 | 2026-08-03 11:59 | 2026-08-03 14:53 | 2026-08-03 14:53 | 2026-08-03 14:53 | 2026-08-03 14:41 | 2026-08-03 14:56 | 2026-08-03 14:56 |  |  | Fair | No | Premises found working ok . Customer advised.
Outage | J.E.26.07.15723 | C001872902 | Vivian Gordon | St.James | Completed | Load_1002490 | Bogue - 310 | 2026-08-03 11:57 | 2026-08-03 11:59 | 2026-08-04 13:50 | 2026-08-04 13:51 | 2026-08-04 13:51 | 2026-08-04 13:51 | 2026-08-04 13:52 | 2026-08-04 13:52 |  |  | Fair | No | Supply found connected
Outage | J.E.26.07.37830 | C001872901 | Vivian Gordon | St James | Completed | Load_246939 | Bogue - 610 | 2026-08-03 11:57 | 2026-08-03 11:59 | 2026-08-04 12:54 | 2026-08-04 12:55 | 2026-08-04 12:54 | 2026-08-04 01:00 | 2026-08-04 12:57 | 2026-08-04 12:57 |  |  | Fair | No
Non-Outage | J.E.26.08.04956 | C001872912 | Edward Royal | KSAS | Completed | Load_256024 | Hunts Bay - 210 | 2026-08-03 12:00 | 2026-08-03 12:01 | 2026-08-03 13:50 | 2026-08-03 13:51 | 2026-08-03 13:50 | 2026-08-03 13:56 | 2026-08-03 13:56 | 2026-08-03 13:56 |  |  | Fair | No | Replaced 15A junction fuse pole#0060654
Outage | J.E.26.08.05049 | C001872913 | Roxroy Needham | St.Ann | Completed | Load_257202 | Cardiff Hall - 210 | 2026-08-03 12:01 | 2026-08-03 12:05 | 2026-08-03 14:42 | 2026-08-03 14:43 | 2026-08-03 15:34 | 2026-08-03 16:03 | 2026-08-03 16:06 | 2026-08-03 16:06 |  |  | Fair | No | Replace a 8 amps junction fuse at pole
Outage | J.E.26.08.05051 | C001872916 | Roxroy Needham | St.Ann | Completed | Load_246914 | Cardiff Hall - 310 | 2026-08-03 12:04 | 2026-08-03 12:27 | 2026-08-03 12:39 | 2026-08-03 12:39 | 2026-08-03 13:52 | 2026-08-03 14:39 | 2026-08-03 14:40 | 2026-08-03 14:40 |  | Y | Fair | No | Replace a 30 amps junction fuse at pole
Outage | J.E.26.08.04896 | C001872920 | Raymond Carr | St.Mary | Completed | Load_250654 | Oracabessa - 210 | 2026-08-03 12:07 | 2026-08-03 12:28 | 2026-08-03 13:52 | 2026-08-03 13:53 | 2026-08-03 15:03 | 2026-08-03 15:00 | 2026-08-03 15:26 | 2026-08-03 15:26 |  |  | Fair | No | Premises not located.
Outage | J.E.26.08.05058 | C001872921 | Edward Royal | KSAS | Completed | Load_239084 | Three Miles - 410 | 2026-08-03 12:12 | 2026-08-03 13:34 | 2026-08-03 15:03 | 2026-08-03 15:04 | 2026-08-03 15:03 | 2026-08-03 15:06 | 2026-08-03 15:06 | 2026-08-03 15:06 |  |  | Fair | No | Meter need to be check meter only giving single phase reffered to field service
Outage | J.E.26.08.05070 | C001872925 | Richard Watson | St.Elizabeth | Completed | Load_265735 | Maggotty - 110 | 2026-08-03 12:12 | 2026-08-03 12:13 | 2026-08-03 12:44 | 2026-08-03 12:45 | 2026-08-03 13:26 | 2026-08-03 13:38 | 2026-08-03 13:48 | 2026-08-03 13:48 | Fire |  | Fair | No | No sparks or fire found at location ,however customer was actually requesting reconnection after hurricane Melissa and requires approximately 200ft of #6 triplex, which we have insufficient amount at the moment. Follow up required.
Non-Outage | J.E.26.08.05069 | C001872927 | Richard Samuda | Manchester | Completed | Load_294633 | Spur Tree - 310 | 2026-08-03 12:14 | 2026-08-03 12:16 | 2026-08-03 12:30 | 2026-08-03 12:31 | 2026-08-03 12:31 | 2026-08-03 12:32 | 2026-08-03 12:32 | 2026-08-03 12:32 | Fire |  | Fair | No | Premises not found
Non-Outage | J.E.26.08.05048 | C001872930 | Richard Samuda |  | Completed |  |  | 2026-08-03 12:17 | 2026-08-03 12:18 | 2026-08-03 12:32 | 2026-08-03 12:33 | 2026-08-03 12:49 | 2026-08-03 02:32 | 2026-08-03 14:33 | 2026-08-03 14:33 |  |  | Fair | No | Changed corroded 1bolt clamp on customer secondary line leading to customer premises voltage 112,114 226
Non-Outage | J.E.26.08.05037 | C001872940 | Edward Royal |  | Completed |  |  | 2026-08-03 12:19 | 2026-08-03 12:22 | 2026-08-03 12:39 | 2026-08-03 12:39 | 2026-08-03 12:48 | 2026-08-03 12:56 | 2026-08-03 12:56 | 2026-08-03 12:56 | LeakingTransformer |  | Fair | No | 50 kva transformer leaking oil also class 4 40 ft pole need to be change on it single phase primary 2north tripe x cable 3rd party cable street light pole #0020166
Outage | J.E.26.08.05078 | C001872939 | Dwayne Cohen | KSAS | Completed | Load_240391 | Duhaney - 310 | 2026-08-03 12:19 | 2026-08-03 12:20 | 2026-08-03 12:33 | 2026-08-03 12:33 | 2026-08-03 13:30 | 2026-08-03 13:57 | 2026-08-03 14:00 | 2026-08-03 14:00 |  |  | Fair | No | Refuse blown 3amps transformer link, supply now restore.
Non-Outage | J.E.26.07.25119 | C001872941 | Edward Royal | KSAN | Completed | Load_237958 | Washington Blvd - 310 | 2026-08-03 12:20 | 2026-08-03 12:21 | 2026-08-03 13:57 | 2026-08-03 13:58 | 2026-08-03 13:57 | 2026-08-03 13:58 | 2026-08-03 13:58 | 2026-08-03 13:58 |  |  | Fair | No | Premises found close unable to communicate with customer
Outage | J.E.26.08.05103 | C001872949 | Raymond Carr | St.Ann | Completed | Load_270210 | Upper White River - 110 | 2026-08-03 12:26 | 2026-08-03 12:28 | 2026-08-03 12:34 | 2026-08-03 12:34 | 2026-08-03 13:42 | 2026-08-03 13:42 | 2026-08-03 13:52 | 2026-08-03 13:52 | BrokenWire |  | Fair | No | Supply found okay, however customer was advised to have an electrician fixed pothead, and replaced broken conduits.
Outage | J.E.26.08.05089 | C001872959 | Wayne Dillion | St.Elizabeth | Completed | Load_261202 | Maggotty - 210 | 2026-08-03 12:36 | 2026-08-03 12:36 | 2026-08-03 13:51 | 2026-08-03 13:52 | 2026-08-03 13:58 | 2026-08-03 14:50 | 2026-08-03 14:51 | 2026-08-03 14:51 |  |  | Fair | No | Supply check and found customer service wire damaged by tree branches. Cut and remove tree branches and splice and retention service wire using 10ft of #6 triplex service wire, 4 clamps and 1 linkets. Supply leave working okay reading 109v, 110v and cross phase 220volts.
Outage | J.E.26.08.04682 | C001872969 | Edward Royal | KSAS | Completed | Load_301332 | Hunts Bay - 410 | 2026-08-03 12:42 | 2026-08-03 12:48 | 2026-08-03 13:58 | 2026-08-03 13:59 | 2026-08-03 14:15 | 2026-08-03 14:16 | 2026-08-03 14:31 | 2026-08-03 14:31 |  |  | Fair | No | Replaced 2 15A junction fuse
Outage | J.E.26.08.04707 | C001872970 | Fitzroy Turner | KSAS | Completed | Load_268037 | Hunts Bay - 210 | 2026-08-03 12:43 | 2026-08-03 12:48 | 2026-08-03 21:27 | 2026-08-03 21:27 | 2026-08-03 21:27 | 2026-08-03 21:40 | 2026-08-03 21:42 | 2026-08-03 21:42 |  |  | Fair | No | Found bank of three 100kva transformer drop leads burnt off. One 4/0 ampact to carry out repair supply restored to areas
Outage | J.E.26.08.04877 | C001872976 | Elvis Trowers | KSAS | Completed | Load_253978 | Greenwich - 510 | 2026-08-03 12:47 | 2026-08-04 07:52 | 2026-08-04 09:44 | 2026-08-04 09:45 | 2026-08-04 10:24 | 2026-08-04 11:23 | 2026-08-04 11:23 | 2026-08-04 11:23 |  |  | Fair | Yes | Areas was found without electricity supply when checked, and 2 fuses were found blown at separate locations during patrol, 1/10 amp at pole #0210174 and a 5 amp transformer fuse pole #————.
Outage | J.E.26.08.05105 | C001872974 | Jermaine Douglas | KSAS | Completed | Load_260737 | Greenwich - 410 | 2026-08-03 12:47 | 2026-08-03 12:48 | 2026-08-03 15:12 | 2026-08-03 15:13 | 2026-08-03 15:54 | 2026-08-03 16:17 | 2026-08-03 16:17 | 2026-08-03 16:17 |  |  | Fair | No
Outage | J.E.26.08.04332 | C001872977 | Edward Royal | KSAS | Completed | Load_241547 | Up Park Camp - 310 | 2026-08-03 12:48 | 2026-08-03 12:53 | 2026-08-03 15:01 | 2026-08-03 15:02 | 2026-08-03 15:01 | 2026-08-03 15:02 | 2026-08-03 15:02 | 2026-08-03 15:02 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.04334 | C001872978 | Elvis Trowers | KSAS | Completed | Load_255166 | Greenwich - 710 | 2026-08-03 12:48 | 2026-08-03 12:53 | 2026-08-03 14:27 | 2026-08-03 14:27 | 2026-08-03 14:39 | 2026-08-03 14:47 | 2026-08-03 14:47 | 2026-08-03 14:47 |  |  | Fair | Yes | Happened to be a disconnection when escalation service department was called.
Outage | J.E.26.08.04805 | C001872979 | Neville Spencer | Clarendon | Completed | Load_237973 | Parnassus - 210 | 2026-08-03 12:51 | 2026-08-03 13:40 | 2026-08-03 14:32 | 2026-08-03 15:06 | 2026-08-03 15:09 | 2026-08-03 15:09 | 2026-08-03 15:23 | 2026-08-03 15:23 | BrokenWire |  | Fair | No | Remade broken off phase joints at secondary on 3, wire service used 1, clamp voltage reading 114. 117. 232 supply restored.
Outage | J.E.26.08.01163 | C001872987 | Edward Royal | KSAS | Completed | Load_244887 | Hunts Bay - 310 | 2026-08-03 13:01 | 2026-08-03 21:39 | 2026-08-03 22:11 | 2026-08-03 22:12 | 2026-08-03 22:11 | 2026-08-03 22:12 | 2026-08-03 22:12 | 2026-08-03 22:12 |  |  | Fair | No | Premises found close
Outage | J.E.26.08.05140 | C001872988 | Fitzroy Turner | KSAS | Completed | Load_262052 | Hunts Bay - 510 | 2026-08-03 13:02 | 2026-08-03 13:18 | 2026-08-03 20:56 | 2026-08-03 20:56 | 2026-08-03 20:56 | 2026-08-03 20:57 | 2026-08-03 20:58 | 2026-08-03 20:58 |  |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.08.05136 | C001872992 | Raheem Ricketts | Manchester | Completed | Load_266341 | Spur Tree - 210 | 2026-08-03 13:09 | 2026-08-03 16:46 | 2026-08-03 19:21 | 2026-08-03 19:21 | 2026-08-03 19:21 | 2026-08-03 19:22 | 2026-08-03 19:23 | 2026-08-03 19:23 | BrokenWire |  | EarthMovement | No | Unable communicate with customer cell number is out of service
Non-Outage | J.E.26.08.05154 | C001873000 | Odeanie Davis | KSAS | Completed | Load_259601 | Hunts Bay - 810 | 2026-08-03 13:15 | 2026-08-03 13:18 | 2026-08-04 08:49 | 2026-08-04 08:50 | 2026-08-04 08:54 | 2026-08-04 09:54 | 2026-08-04 09:54 | 2026-08-04 09:54 |  |  | Fair | No | 113v/123v at arrival, open circuit at pothead corrected, 3 penn union , 118v/119v & 237v after correction
Outage | J.E.26.08.05188 | C001873026 | Milton Charlton | KSAN | Completed | Load_258537 | Washington Blvd - 610 | 2026-08-03 13:33 | 2026-08-03 16:09 | 2026-08-03 16:24 | 2026-08-03 16:24 | 2026-08-03 17:37 | 2026-08-03 17:45 | 2026-08-03 17:43 | 2026-08-03 17:43 |  |  | Fair | No | Isolate 50 kva transformer at pole #0098440 to fix broken twisted secondary upon observation twisted phase and neutral burn off in more one area need about 150ft of 2# triplex twisted and bucket truck wire is on concrete pole . Disconnect #2 triplex. About 18 are more customers are whit out power.
Outage | J.E.26.08.05022 | C001873040 | Derrick Dawkins | St.James | Completed | Load_248986 | Bogue - 410 | 2026-08-03 13:55 | 2026-08-03 15:44 | 2026-08-03 15:48 | 2026-08-03 15:48 | 2026-08-03 16:37 | 2026-08-03 17:07 | 2026-08-03 17:10 | 2026-08-03 17:10 |  |  | Fair | No | Found customer pothead corroded clean and reconnected pothead
Outage | J.E.26.08.05100 | C001873041 | Daniel Francis | St.Ann | Completed | Load_267230 | Ocho Rios - 410 | 2026-08-03 13:55 | 2026-08-03 13:57 | 2026-08-03 15:00 | 2026-08-03 15:01 | 2026-08-03 15:00 | 2026-08-03 16:26 | 2026-08-03 16:31 | 2026-08-03 16:31 |  |  | Fair | No | Found secondary phase conducter broken replace 1span useing 70ft of 2/0aac conducter
Outage | J.E.26.08.04201 | C001873049 | Wan Carlos Scarlett | Portmore | Completed | Load_260715 | Naggo Head - 510 | 2026-08-03 14:02 | 2026-08-03 14:03 | 2026-08-03 15:27 | 2026-08-03 15:27 | 2026-08-03 16:06 | 2026-08-03 16:32 | 2026-08-03 16:35 | 2026-08-03 16:35 |  |  | Fair | No | Refuse 25 KVA transformer with 3 amp fuse no pole # was found nothing was found on primary line cause by lightning strike
Outage | J.E.26.08.05263 | C001873052 | Elvis Trowers | KSAN | Completed | Load_253397 | Washington Blvd - 810 | 2026-08-03 14:09 | 2026-08-03 14:10 | 2026-08-03 14:47 | 2026-08-03 14:47 | 2026-08-03 14:56 | 2026-08-03 15:11 | 2026-08-03 15:11 | 2026-08-03 15:11 | Fire | Y | SevereWind | Yes | Major secondary bushings that is required for this location, trees growing through and over hanging secondary needs to be cut, and vehicles that are parked alongside the need to be moved, customer was advised to contact the owners to get the vehicles moved.
Outage | J.E.26.08.05277 | C001873053 | Shamour Haughton | St.James | Completed | Load_257188 | Bogue - 310 | 2026-08-03 14:12 | 2026-08-03 15:43 | 2026-08-03 15:47 | 2026-08-03 15:48 | 2026-08-03 15:47 | 2026-08-03 15:54 | 2026-08-03 15:55 | 2026-08-03 15:55 |  |  | Fair | No | Hex 01028, customer service wire has been torn down from Melissa, please refer to field service
Outage | J.E.26.08.05207 | C001873059 | Antony Levy | KSAS | Completed | Load_244205 | Duhaney - 310 | 2026-08-03 14:18 | 2026-08-03 16:10 | 2026-08-03 16:29 | 2026-08-03 16:29 | 2026-08-03 17:21 | 2026-08-03 17:58 | 2026-08-03 17:58 | 2026-08-03 17:58 | BrokenWire |  | Fair | No | Customer stated that service wire is too low... service wire tensioned and reattached to cx station cx okay
Outage | J.E.26.08.05182 | C001873097 | Roxroy Needham | St.Ann | Completed | Load_242214 | Cardiff Hall - 210 | 2026-08-03 14:47 | 2026-08-03 14:49 | 2026-08-03 16:17 | 2026-08-03 18:02 | 2026-08-03 18:45 | 2026-08-03 18:58 | 2026-08-03 18:58 | 2026-08-03 18:58 |  |  | Fair | No | Replace a 30 amps junction fuse at pole
Outage | J.E.26.08.05228 | C001873109 | Neville Spencer | Clarendon | Completed | Load_263678 | May Pen - 210 | 2026-08-03 14:59 | 2026-08-03 14:59 | 2026-08-03 15:23 | 2026-08-03 15:24 | 2026-08-03 16:14 | 2026-08-03 16:14 | 2026-08-03 17:01 | 2026-08-03 17:01 |  |  | Fair | No | Removed defective lightning arrester from 25 kva xmfr in bank of 3 at pole #0129578 .Also renew blown 3 amp fuse supply restored.
Non-Outage | J.E.26.07.25119 | C001873117 | Edward Royal | KSAN | Completed | Load_237958 | Washington Blvd - 310 | 2026-08-03 15:04 | 2026-08-03 15:05 | 2026-08-03 15:25 | 2026-08-03 15:25 | 2026-08-03 16:01 | 2026-08-03 16:14 | 2026-08-03 16:14 | 2026-08-03 16:14 |  |  | Fair | No | Defective meter need to be change reffered to field service
Outage | J.E.26.08.05351 | C001873128 | Oshane Warren | Westmoreland | Completed | Load_238134 | Paradise - 110 | 2026-08-03 15:12 | 2026-08-04 07:32 | 2026-08-04 07:41 | 2026-08-04 07:41 | 2026-08-04 09:30 | 2026-08-04 09:50 | 2026-08-04 09:50 | 2026-08-04 09:50 |  |  | Fair | No | Reconnect service wire at pathead and secondary line used 30ft of number 6twisted wire used 3service connector and 3pg clamps
Non-Outage | J.E.26.08.03131 | C001873148 | Denton Williams |  | Completed |  |  | 2026-08-03 15:18 | 2026-08-03 15:19 | 2026-08-03 21:33 | 2026-08-03 21:34 | 2026-08-03 21:34 | 2026-08-03 21:34 | 2026-08-03 22:10 | 2026-08-03 22:10 |  |  | Fair | No | Premises close. Unreachable via telephone
Non-Outage | J.E.26.08.05237 | C001873147 | Denton Williams |  | Completed |  |  | 2026-08-03 15:18 | 2026-08-03 15:19 | 2026-08-03 18:04 | 2026-08-03 18:05 | 2026-08-03 19:33 | 2026-08-03 19:57 | 2026-08-03 19:59 | 2026-08-03 19:59 |  | Y | Fair | No | Line need bushing, use one 8amp fuse to energize blown junction fuse
Outage | J.E.26.08.03281 | C001873146 | Denton Williams | Portland | Completed | Load_260170 | Port Antonio - 410 | 2026-08-03 15:18 | 2026-08-03 15:19 | 2026-08-03 20:01 | 2026-08-03 20:01 | 2026-08-03 21:07 | 2026-08-03 21:07 | 2026-08-03 21:09 | 2026-08-03 21:09 |  | Y | Fair | No | Use one 2amp to energize a 10 kva transformer
Outage | J.E.26.08.05124 | C001873145 | Denton Williams | Portland | Completed | Load_255956 | Port Antonio - 410 | 2026-08-03 15:18 | 2026-08-03 15:19 | 2026-08-03 15:51 | 2026-08-03 17:54 | 2026-08-03 17:54 | 2026-08-03 17:54 | 2026-08-03 17:57 | 2026-08-03 17:57 |  | Y | Fair | No | Remove vines from line and replace one 30 amp junction fuse
Outage | J.E.26.08.04206 | C001873149 | Kemark Slue | St.Catherine | Completed | Load_265936 | Tredegar - 210 | 2026-08-03 15:19 | 2026-08-03 15:55 | 2026-08-03 17:38 | 2026-08-03 22:05 | 2026-08-03 22:05 | 2026-08-03 22:05 | 2026-08-03 22:06 | 2026-08-03 22:06 |  |  | Fair | No | Upon arrival at the location the crew discovered that a section of the community was without supply further patrol revealed that the middle primary phase that’s connected to junction switch supplying the community was disconnected, isolate said junction and use live line techniques to remake jumper and re-energized the line section.
Non-Outage | J.E.26.08.05379 | C001873150 | Raheem Ricketts |  | Completed |  |  | 2026-08-03 15:20 | 2026-08-03 15:21 | 2026-08-03 15:28 | 2026-08-03 15:33 | 2026-08-03 17:12 | 2026-08-03 18:49 | 2026-08-03 18:49 | 2026-08-03 18:49 | Fire |  | Fair | No | Escalated to maintenance Team
Outage | J.E.26.08.04978 | C001873157 | Neville Spencer | Clarendon | Completed | Load_256590 | Parnassus - 310 | 2026-08-03 15:21 | 2026-08-03 15:32 | 2026-08-03 17:05 | 2026-08-03 17:06 | 2026-08-03 17:05 | 2026-08-03 17:05 | 2026-08-03 17:06 | 2026-08-03 17:06 |  |  | Fair | No | Area restored at 1 . 27 pm.
Outage | J.E.26.08.05035 | C001873156 | Neville Spencer | Clarendon | Completed | Load_252849 | Parnassus - 310 | 2026-08-03 15:21 | 2026-08-03 15:32 | 2026-08-03 17:07 | 2026-08-03 17:08 | 2026-08-03 17:08 | 2026-08-03 17:08 | 2026-08-03 17:09 | 2026-08-03 17:09 |  |  | Fair | No | Found ok.
Outage | J.E.26.08.05120 | C001873153 | Hartley Chin | Clarendon | Completed | Load_249917 | Parnassus - 210 | 2026-08-03 15:21 | 2026-08-04 07:38 | 2026-08-04 13:58 | 2026-08-04 16:59 | 2026-08-04 17:23 | 2026-08-04 17:35 | 2026-08-04 17:36 | 2026-08-04 17:36 | Fire |  | Fair | No | Found 10 KVA transformer trip due to banging wire removed banging wires then reset transformer
Outage | J.E.26.08.05212 | C001873155 | Hartley Chin | Clarendon | Completed | Load_259354 | Parnassus - 310 | 2026-08-03 15:21 | 2026-08-04 07:38 | 2026-08-04 08:03 | 2026-08-04 10:12 | 2026-08-04 10:59 | 2026-08-04 11:23 | 2026-08-04 11:24 | 2026-08-04 11:24 |  |  | Fair | No | Found blown 2 amp fuse on 15KVA transformer @ pole # 0107564 line patrolled and found okay , transformer refused …
Outage | J.E.26.08.05213 | C001873154 | Neville Spencer | Clarendon | Completed | Load_245674 | Parnassus - 210 | 2026-08-03 15:21 | 2026-08-03 15:32 | 2026-08-03 17:10 | 2026-08-03 17:11 | 2026-08-03 17:22 | 2026-08-03 17:22 | 2026-08-03 17:34 | 2026-08-03 17:34 |  |  | Fair | No | Cleared creeper from xmfr pole renew blown 3 amp fuse protecting 25 kva xmfr in bank of 2 at pole #, 0112768 supply restored.
Outage | J.E.26.08.05260 | C001873152 | Hartley Chin | Clarendon | Completed | Load_260393 | Monymusk - 410 | 2026-08-03 15:21 | 2026-08-04 07:38 | 2026-08-04 08:08 | 2026-08-04 08:09 | 2026-08-04 09:27 | 2026-08-04 10:12 | 2026-08-04 10:12 | 2026-08-04 10:12 | BrokenWire |  | SevereWind | No | Replace 70 ft service wire .. voltage read 111v , 113v .. use 4 clamp …
Non-Outage | J.E.26.08.05119 | C001873168 | Roxroy Needham |  | Completed |  |  | 2026-08-03 15:25 | 2026-08-03 15:26 | 2026-08-03 16:21 | 2026-08-03 16:22 | 2026-08-03 17:43 | 2026-08-03 18:00 | 2026-08-03 18:02 | 2026-08-03 18:02 | LeaningPole | Y | Fair | No | Retention 2 service wire from pole to pothead
Outage | J.E.26.08.04602 | C001873169 | Omar King |  | Completed | Load_243438 | Cardiff Hall - 310 | 2026-08-03 15:25 | 2026-08-03 22:50 | 2026-08-04 02:30 | 2026-08-04 02:31 | 2026-08-04 04:17 | 2026-08-04 04:17 | 2026-08-04 04:17 | 2026-08-04 04:17 |  |  | Fair | No | Unable to find customer call several times no answer directions not sufficient
Outage | J.E.26.08.05356 | C001873167 | Roxroy Needham | St.Ann | Completed | Load_242202 | Cardiff Hall - 310 | 2026-08-03 15:25 | 2026-08-03 15:26 | 2026-08-03 19:46 | 2026-08-03 19:47 | 2026-08-03 21:10 | 2026-08-03 21:35 | 2026-08-03 21:43 | 2026-08-03 21:43 |  |  | Fair | No | Reconnect service wire at pole used 1 pg clamp premises locked not getting customer voltage
Outage | J.E.26.08.05363 | C001873166 | Roxroy Needham | St.Ann | Completed | Load_266408 | Cardiff Hall - 210 | 2026-08-03 15:25 | 2026-08-03 15:26 | 2026-08-03 16:08 | 2026-08-03 19:00 | 2026-08-03 19:45 | 2026-08-03 19:42 | 2026-08-03 19:46 | 2026-08-03 19:46 | Fire |  | Fair | No | Premises found locked not getting customer on phone
Non-Outage | J.E.26.08.04047 | C001873177 | Derrick Dawkins |  | Completed |  |  | 2026-08-03 15:31 | 2026-08-03 15:52 | 2026-08-03 17:10 | 2026-08-03 17:12 | 2026-08-03 17:39 | 2026-08-03 17:40 | 2026-08-03 17:42 | 2026-08-03 17:42 |  |  | Rains | No | Checked and found ok
Non-Outage | J.E.26.08.04173 | C001873178 | Dean- Smith |  | Completed |  |  | 2026-08-03 15:31 | 2026-08-03 15:32 | 2026-08-03 22:55 | 2026-08-03 22:55 | 2026-08-03 22:55 | 2026-08-03 22:55 | 2026-08-03 22:55 | 2026-08-03 22:55 |  |  | Fair | No | Need daylight attention
Outage | J.E.26.08.04395 | C001873176 | Dean- Smith | Hanover | Completed | Load_302836 | Orange Bay - 310 | 2026-08-03 15:31 | 2026-08-03 15:32 | 2026-08-03 21:17 | 2026-08-03 21:17 | 2026-08-03 22:54 | 2026-08-03 22:54 | 2026-08-03 22:55 | 2026-08-03 22:55 |  |  | Fair | No | Check and found ok
Outage | J.E.26.08.04851 | C001873175 | Dean- Smith | Hanover | Completed | Load_573736 | Orange Bay - 210 | 2026-08-03 15:31 | 2026-08-03 15:32 | 2026-08-03 15:53 | 2026-08-03 15:54 | 2026-08-03 18:55 | 2026-08-03 18:55 | 2026-08-03 19:34 | 2026-08-03 19:34 |  |  | Fair | No | Defective 50kva transformer,secondary procelain part of bushing burnt out. Same need to be replace unless someone decide to go inside of the transformer tank..... from tank hill, left at Baltimore ave, second left turn. Continue to 50kva ... voltage left 108v, 70v.
Outage | J.E.26.08.04457 | C001873187 | Wan Carlos Scarlett | Portmore | Completed | Load_243572 | Naggo Head - 610 | 2026-08-03 15:33 | 2026-08-03 15:39 | 2026-08-03 19:59 | 2026-08-03 19:59 | 2026-08-03 21:21 | 2026-08-03 21:23 | 2026-08-03 21:26 | 2026-08-03 21:26 | BrokenWire |  | Fair | No | Found cable and wireless wire on the ground was calling customer to advise customer to contact cable and wireless for assistance
Outage | J.E.26.08.05009 | C001873186 | Wan Carlos Scarlett | Portmore | Completed | Load_576085 | Naggo Head - 510 | 2026-08-03 15:33 | 2026-08-03 15:39 | 2026-08-03 15:52 | 2026-08-03 18:36 | 2026-08-03 18:41 | 2026-08-03 19:09 | 2026-08-03 19:14 | 2026-08-03 19:14 | Fire |  | Fair | No | Refuse 100 KVA transformer with 10 Amp fuse pole #013495 nothing was found on secondary line cause by lightning strike
Outage | J.E.26.08.03747 | C001873188 | Wan Carlos Scarlett | Portmore | Completed | Load_576173 | Naggo Head - 510 | 2026-08-03 15:35 | 2026-08-03 15:39 | 2026-08-03 16:47 | 2026-08-03 21:27 | 2026-08-03 22:17 | 2026-08-03 22:27 | 2026-08-03 22:29 | 2026-08-03 22:29 | BrokenWire |  | Fair | No | Found cable and wireless wire broken and on the ground been calling customer to advise customer to contact cable provider for assistance
Outage | J.E.26.08.05187 | C001873189 | Wan Carlos Scarlett | Portmore | Completed | Load_260715 | Naggo Head - 510 | 2026-08-03 15:35 | 2026-08-03 15:39 | 2026-08-03 15:52 | 2026-08-03 16:36 | 2026-08-03 16:38 | 2026-08-03 16:42 | 2026-08-03 16:46 | 2026-08-03 16:46 |  |  | Fair | No | Call related to outage earlier customer confirmed that power supply has restored
Outage | J.E.26.08.05392 | C001873190 | Wan Carlos Scarlett | Portmore | Completed | Load_268305 | Naggo Head - 610 | 2026-08-03 15:35 | 2026-08-03 15:39 | 2026-08-03 16:47 | 2026-08-03 16:47 | 2026-08-03 17:40 | 2026-08-03 18:28 | 2026-08-03 18:34 | 2026-08-03 18:34 | Fire |  | Fair | No | Found street light neutral wire burn off and touching the lower phase causing spark customer concerned reconnect street light neutral issue was resolved
Outage | J.E.26.08.04904 | C001873195 | Shamour Haughton | St.James | Completed | Load_258445 | Rose Hall - 110 | 2026-08-03 15:37 | 2026-08-03 15:43 | 2026-08-03 16:01 | 2026-08-03 16:01 | 2026-08-03 16:01 | 2026-08-03 16:01 | 2026-08-03 16:02 | 2026-08-03 16:02 |  |  | Fair | No | Related to previous call
Outage | J.E.26.08.04971 | C001873196 | Shamour Haughton | St.James | Completed | Load_258825 | Bogue - 310 | 2026-08-03 15:37 | 2026-08-03 15:43 | 2026-08-03 17:56 | 2026-08-03 17:56 | 2026-08-03 17:56 | 2026-08-03 18:18 | 2026-08-03 18:21 | 2026-08-03 18:21 |  |  | Fair | No | Customer experiencing internal issue, customer has gotten there electrician
Non-Outage | J.E.26.08.04841 | C001873199 | Shamour Haughton |  | Completed |  |  | 2026-08-03 15:38 | 2026-08-03 15:43 | 2026-08-03 15:58 | 2026-08-03 15:59 | 2026-08-03 15:58 | 2026-08-03 15:58 | 2026-08-03 15:59 | 2026-08-03 15:59 |  |  | Fair | No | Related to previous call
Outage | J.E.26.08.05316 | C001873198 | Derrick Dawkins | St.James | Completed | Load_245028 | Bogue - 610 | 2026-08-03 15:38 | 2026-08-03 15:44 | 2026-08-03 18:40 | 2026-08-03 18:54 | 2026-08-03 19:01 | 2026-08-03 19:02 | 2026-08-03 19:02 | 2026-08-03 19:02 |  |  | Fair | No | Call to customer went unanswered unable to locate
Non-Outage | J.E.26.08.04924 | C001873200 | Kemark Slue | St.Catherine | Completed | Load_260791 | Twickenham - 310 | 2026-08-03 15:39 | 2026-08-03 16:47 | 2026-08-03 21:39 | 2026-08-03 22:06 | 2026-08-03 22:48 | 2026-08-03 22:49 | 2026-08-03 22:50 | 2026-08-03 22:50 |  |  | Fair | No | Upon arrival at the location the crew discovered that 50 amps middle junction was blown resulting from a bird, refuse link and re-energized line section.
Outage | J.E.26.08.05287 | C001873202 | Marlon Brown | Trelawny | Completed | Load_292760 | Greenwood - 110 | 2026-08-03 15:42 | 2026-08-03 15:45 | 2026-08-03 17:43 | 2026-08-03 17:44 | 2026-08-03 18:47 | 2026-08-03 19:03 | 2026-08-03 19:03 | 2026-08-03 19:03 |  |  | Fair | No | Reconnect service wire at pothead.
Outage | J.E.26.08.05364 | C001873203 | Marlon Brown | Trelawny | Completed | Load_242775 | Martha Brae - 110 | 2026-08-03 15:42 | 2026-08-03 15:45 | 2026-08-03 16:09 | 2026-08-03 16:10 | 2026-08-03 16:52 | 2026-08-03 17:42 | 2026-08-03 17:42 | 2026-08-03 17:42 | BrokenWire |  | Fair | No | Isolated bank of 2 10kva transformers to clear 4/0 quad from roadway. Customer advised to have their poles replaced to accommodate wires on.
Outage | J.E.26.08.04861 | C001873207 | Marlon Brown | Trelawny | Completed | Load_574709 | Greenwood - 210 | 2026-08-03 15:45 | 2026-08-03 15:47 | 2026-08-03 16:02 | 2026-08-03 16:03 | 2026-08-03 16:02 | 2026-08-03 16:03 | 2026-08-03 16:03 | 2026-08-03 16:03 |  |  | Fair | No | St James call
Non-Outage | J.E.26.08.04093 | C001873213 | Clyde Brown | Clarendon | Completed | Load_245015 | May Pen - 110 | 2026-08-03 15:48 | 2026-08-03 15:54 | 2026-08-03 16:32 | 2026-08-03 19:58 | 2026-08-03 21:57 | 2026-08-03 09:48 | 2026-08-03 22:01 | 2026-08-03 22:01 |  |  | Fair | No | Cannot locate customer resident or location
Non-Outage | J.E.26.08.04954 | C001873212 | Clyde Brown | Clarendon | Completed | Load_243522 | May Pen - 110 | 2026-08-03 15:48 | 2026-08-03 15:54 | 2026-08-03 16:32 | 2026-08-03 16:33 | 2026-08-03 18:01 | 2026-08-03 18:24 | 2026-08-03 18:31 | 2026-08-03 18:31 |  |  | Fair | No | Broken secondary 3 wire service neutral broken same spliced with 8ft-#6 service neutral and 1-clamp
Non-Outage | J.E.26.07.39932 | C001873215 | Clyde Brown | Clarendon | Completed | Load_239018 | May Pen - 110 | 2026-08-03 15:49 | 2026-08-03 15:54 | 2026-08-03 16:32 | 2026-08-03 19:55 | 2026-08-03 19:55 | 2026-08-03 19:54 | 2026-08-03 19:58 | 2026-08-03 19:58 | BrokenWire |  | Fair | No | Cannot be located customer not answering phone
Non-Outage | J.E.26.07.40032 | C001873214 | Clyde Brown | Clarendon | Completed | Load_568397 | May Pen - 110 | 2026-08-03 15:49 | 2026-08-03 15:54 | 2026-08-03 16:32 | 2026-08-03 18:56 | 2026-08-03 19:48 | 2026-08-03 19:48 | 2026-08-03 19:54 | 2026-08-03 19:54 |  |  | Fair | No | Phase wire dislodge for 3 wire service connection remade with one clamp,voltage left 113/112 and 225V
Outage | J.E.26.08.04316 | C001873216 | Stephen Taylor | St.Thomas | Completed | Load_259414 | Good Year - 210 | 2026-08-03 15:50 | 2026-08-03 15:51 | 2026-08-03 17:29 | 2026-08-03 17:30 | 2026-08-03 18:57 | 2026-08-03 18:57 | 2026-08-03 18:59 | 2026-08-03 18:59 |  |  | Fair | No | Premese found okay Rdg 113–112–226
Outage | J.E.26.08.04814 | C001873231 | Nickolas Rodriques | St.Catherine | Completed | Load_288492 | Rhodens Pen - 210 | 2026-08-03 15:53 | 2026-08-03 15:56 | 2026-08-03 16:13 | 2026-08-03 19:10 | 2026-08-03 19:56 | 2026-08-03 20:31 | 2026-08-03 20:42 | 2026-08-03 20:42 | BrokenWire |  | Fair | No | Checked and found customer without power. All necessary checks were done and it was found that the issue is stemming from the hexing box (HEX 01973). (No broken wire was seen upon arrival). Refer to field service.
Outage | J.E.26.08.05013 | C001873226 | Shamour Haughton | St.James | Completed | Load_248812 | Rose Hall - 210 | 2026-08-03 15:53 | 2026-08-03 15:54 | 2026-08-03 18:28 | 2026-08-03 18:29 | 2026-08-03 18:28 | 2026-08-03 18:29 | 2026-08-03 18:30 | 2026-08-03 18:30 |  |  | Fair | No | Customer states that issue was resolved
Outage | J.E.26.08.05080 | C001873227 | Shamour Haughton | St.James | Completed | Load_261827 | Queens Drive - 710 | 2026-08-03 15:53 | 2026-08-03 15:54 | 2026-08-03 18:34 | 2026-08-03 18:34 | 2026-08-03 19:12 | 2026-08-03 19:12 | 2026-08-03 19:16 | 2026-08-03 19:16 |  |  | Fair | No | Found customer meter damage, meter needs changing urgently, voltage left114,116,231
Outage | J.E.26.08.05095 | C001873228 | Shamour Haughton | St.James | Completed | Load_245566 | Queens Drive - 710 | 2026-08-03 15:53 | 2026-08-03 15:54 | 2026-08-03 16:00 | 2026-08-03 16:00 | 2026-08-03 16:00 | 2026-08-03 16:00 | 2026-08-03 16:00 | 2026-08-03 16:00 |  |  | Fair | No
Outage | J.E.26.08.05285 | C001873230 | Kemark Slue | St.Catherine | Completed | Load_255497 | Twickenham - 410 | 2026-08-03 15:53 | 2026-08-03 15:56 | 2026-08-03 16:07 | 2026-08-03 16:08 | 2026-08-03 18:26 | 2026-08-03 19:49 | 2026-08-03 20:15 | 2026-08-03 20:15 |  |  | Fair | No | Upon arrival at the location the crew discovered that 30 amps junction fuse at the underground cable both sides were blown, further patrol revealed that another junction was blown consisting of a 30 amps as well and a 10 amps D type fuse in another junction for said line section that had a defective lightening arrester, refuse underground cable junction with 30 amps, refuse the 30 amps from there with a 25 amps and replace the 10 D with 15 k and re-energized line section.
Outage | J.E.26.08.05399 | C001873229 | Kemark Slue | St.Catherine | Completed | Load_265936 | Tredegar - 210 | 2026-08-03 15:53 | 2026-08-03 15:56 | 2026-08-03 17:38 | 2026-08-03 20:16 | 2026-08-03 20:15 | 2026-08-03 21:45 | 2026-08-03 22:05 | 2026-08-03 22:05 |  |  | Fair | No | Upon arrival at the location the crew discovered that a section of the community was without supply further patrol revealed that the middle primary phase that’s connected to junction switch supplying the community was disconnected, isolate said junction and use live line techniques to remake jumper and re-energized the line section.
Non-Outage | J.E.26.08.05389 | C001873232 | Selvin White |  | Completed |  |  | 2026-08-03 15:54 | 2026-08-03 16:42 | 2026-08-03 16:50 | 2026-08-03 17:20 | 2026-08-03 19:19 | 2026-08-03 22:28 | 2026-08-03 22:33 | 2026-08-03 22:33 | Fire |  | Fair | No | Carry out switching at LAB 6-1325 with the permission of J. Clarke at system control in order to replace 3 burnt drop out switches at Coke Drive and also to splice stranded out conductor. Supply restored to all customers.
Outage | J.E.26.08.05295 | C001873241 | Antony Levy | KSAN | Completed | Load_240425 | Washington Blvd - 810 | 2026-08-03 15:57 | 2026-08-03 16:00 | 2026-08-03 19:20 | 2026-08-03 19:21 | 2026-08-03 20:11 | 2026-08-03 20:52 | 2026-08-03 20:53 | 2026-08-03 20:53 |  |  | Fair | No | Cx stated no power .... blown 50kva transformer found ...dislodged secondary phase found of 2 phase and neutral touching street light bracket... phase reinstalled with tie wire and transformer refused
Outage | J.E.26.08.05368 | C001873237 | Antony Levy | KSAN | Completed | Load_253684 | Constant Spring - 210 | 2026-08-03 15:57 | 2026-08-03 16:00 | 2026-08-03 17:58 | 2026-08-03 17:59 | 2026-08-03 18:21 | 2026-08-03 18:33 | 2026-08-03 18:39 | 2026-08-03 18:39 | BrokenWire |  | Fair | No | Premises found okay
Outage | J.E.26.08.05401 | C001873233 | Milton Charlton | KSAN | Completed | Load_574898 | Washington Blvd - 810 | 2026-08-03 15:57 | 2026-08-03 19:04 | 2026-08-03 20:13 | 2026-08-03 20:14 | 2026-08-03 20:39 | 2026-08-03 20:45 | 2026-08-03 20:40 | 2026-08-03 20:40 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.04598 | C001873249 | Nickolas Rodriques | St.Catherine | Completed | Load_291829 | Rhodens Pen - 210 | 2026-08-03 16:09 | 2026-08-03 16:14 | 2026-08-03 20:42 | 2026-08-03 20:45 | 2026-08-03 21:42 | 2026-08-03 22:30 | 2026-08-03 22:31 | 2026-08-03 22:31 |  |  | Fair | No | Customer was disconnected due to non payment of bill. The escalation team was contacted and reconnected the customer after the bill was paid. The customer confirmed that service was restored.
Outage | J.E.26.08.05032 | C001873248 | Nickolas Rodriques | St.Catherine | Completed | Load_556349 | Rhodens Pen - 210 | 2026-08-03 16:09 | 2026-08-03 16:14 | 2026-08-03 16:19 | 2026-08-03 16:20 | 2026-08-03 17:30 | 2026-08-03 18:33 | 2026-08-03 18:40 | 2026-08-03 18:40 |  |  | Fair | No | Kingston call. Customer is reporting a defective streetlight light located at 46 Half Way Tree Road.
Outage | J.E.26.08.04902 | C001873252 | Raymond Lewis | St.Ann | Completed | Load_245545 | Roaring River - 210 | 2026-08-03 16:10 | 2026-08-03 16:12 | 2026-08-03 22:29 | 2026-08-03 22:29 | 2026-08-03 22:29 | 2026-08-03 22:30 | 2026-08-03 22:31 | 2026-08-03 22:31 | Fire |  | Fair | No | Customer need and electrician
Outage | J.E.26.08.05100 | C001873251 | Raymond Lewis | St.Ann | Completed | Load_267230 | Ocho Rios - 410 | 2026-08-03 16:10 | 2026-08-03 16:12 | 2026-08-03 19:39 | 2026-08-03 19:40 | 2026-08-03 21:18 | 2026-08-03 21:20 | 2026-08-03 21:20 | 2026-08-03 21:20 |  |  | Fair | No | Supply was restored
Outage | J.E.26.08.05199 | C001873250 | Raymond Lewis | St.Ann | Completed | Load_245229 | Roaring River - 210 | 2026-08-03 16:10 | 2026-08-03 16:12 | 2026-08-03 16:48 | 2026-08-03 16:49 | 2026-08-03 16:48 | 2026-08-03 16:53 | 2026-08-03 16:54 | 2026-08-03 16:54 |  |  | Fair | No | Customer Errol Reid said supply restored
Non-Outage | J.E.26.08.02587 | C001873255 | Raymond Lewis |  | Completed |  |  | 2026-08-03 16:11 | 2026-08-03 16:12 | 2026-08-03 16:59 | 2026-08-03 17:00 | 2026-08-03 18:45 | 2026-08-03 19:37 | 2026-08-03 19:39 | 2026-08-03 19:39 |  |  | Fair | No | Need 100 ft #2 conductor to complete job
Outage | J.E.26.08.05020 | C001873253 | Barnett Brown | Manchester | Completed | Load_242141 | Kendal - 210 | 2026-08-03 16:11 | 2026-08-04 07:38 | 2026-08-04 11:30 | 2026-08-04 11:31 | 2026-08-04 11:33 | 2026-08-04 12:14 | 2026-08-04 12:17 | 2026-08-04 12:17 |  |  | Fair | No | Customer has internal problem
Outage | J.E.26.08.05291 | C001873256 | Raheem Ricketts | Manchester | Completed | Load_254566 | Spur Tree - 310 | 2026-08-03 16:11 | 2026-08-03 16:46 | 2026-08-03 19:18 | 2026-08-03 19:20 | 2026-08-03 19:19 | 2026-08-03 19:20 | 2026-08-03 19:20 | 2026-08-03 19:20 |  |  | Fair | No | Manchester call
Outage | J.E.26.08.05408 | C001873254 | Kenroy Dale | Manchester | Completed | Load_237809 | Kendal - 210 | 2026-08-03 16:11 | 2026-08-03 16:11 | 2026-08-03 16:37 | 2026-08-03 16:39 | 2026-08-03 18:05 | 2026-08-03 19:54 | 2026-08-03 19:58 | 2026-08-03 19:58 |  |  | Fair | No | Blown 3 amp transformer fuse found for 25 kva transformer line patrol 2 span of secondary neutral and phase found broken conductors was splice and retention blown fuse was replaced and area now with supply
Outage | J.E.26.08.05334 | C001873261 | Andre Smith | KSAS | Completed | Load_258423 | Three Miles - 410 | 2026-08-03 16:13 | 2026-08-03 16:17 | 2026-08-03 17:32 | 2026-08-03 17:33 | 2026-08-03 17:51 | 2026-08-03 18:09 | 2026-08-03 18:09 | 2026-08-03 18:09 | BrokenWire |  | Fair | Yes | Burnt customer meter and meter socket customer advised of repairs
Outage | J.E.26.08.04712 | C001873263 | Neville Spencer | Clarendon | Completed | Load_252119 | Parnassus - 210 | 2026-08-03 16:14 | 2026-08-03 16:20 | 2026-08-03 19:49 | 2026-08-03 19:49 | 2026-08-03 22:04 | 2026-08-03 22:04 | 2026-08-03 22:05 | 2026-08-03 22:05 |  |  | Fair | No | Not located.
Outage | J.E.26.08.05345 | C001873262 | Raheem Ricketts | Manchester | Completed | Load_266064 | Spur Tree - 210 | 2026-08-03 16:14 | 2026-08-03 16:46 | 2026-08-03 19:23 | 2026-08-03 19:24 | 2026-08-03 19:23 | 2026-08-03 19:24 | 2026-08-03 19:24 | 2026-08-03 19:24 |  |  | Fair | No | Manchester call
Outage | J.E.26.08.05214 | C001873264 | Andre Smith | KSAS | Completed | Load_260949 | Three Miles - 410 | 2026-08-03 16:16 | 2026-08-03 16:17 | 2026-08-03 16:28 | 2026-08-03 16:28 | 2026-08-03 17:06 | 2026-08-03 17:32 | 2026-08-03 17:32 | 2026-08-03 17:32 | TreeContact |  | Fair | No | Cut tree and replace blown junction fuse 10A supply restored
Outage | J.E.26.08.05397 | C001873268 | Milton Charlton | KSAS | Completed | Load_268141 | Greenwich - 710 | 2026-08-03 16:17 | 2026-08-03 21:15 | 2026-08-04 09:39 | 2026-08-04 09:39 | 2026-08-04 10:00 | 2026-08-04 09:45 | 2026-08-04 10:02 | 2026-08-04 10:02 |  |  | Fair | No | Found okay upon arrival. Customer had an internal problem meter was removed to repair pothead wires that was burnt.
Outage | J.E.26.08.05412 | C001873271 | Neckell Ormsby | St.Mary | Completed | Load_258392 | Highgate - 210 | 2026-08-03 16:24 | 2026-08-03 16:27 | 2026-08-03 16:51 | 2026-08-03 16:51 | 2026-08-03 17:31 | 2026-08-03 17:52 | 2026-08-03 18:02 | 2026-08-03 18:02 |  |  | Fair | No | Customer was disconnected however unable to get to call center to find out the stats of meter please refer to field service to check meter
Non-Outage | J.E.26.08.04204 | C001873282 | Neckell Ormsby |  | Completed |  |  | 2026-08-03 16:35 | 2026-08-03 16:36 | 2026-08-03 18:40 | 2026-08-03 18:41 | 2026-08-03 19:07 | 2026-08-03 19:25 | 2026-08-03 19:25 | 2026-08-03 19:25 | TreeContact |  | Fair | No | Unable to locate customer after several calls however found supply in area lago close also see evidence of fallen tree
Outage | J.E.26.08.05456 | C001873281 | Neckell Ormsby | St.Mary | Completed | Load_249380 | Highgate - 210 | 2026-08-03 16:35 | 2026-08-03 16:36 | 2026-08-03 18:03 | 2026-08-03 18:03 | 2026-08-03 18:21 | 2026-08-03 18:33 | 2026-08-03 18:40 | 2026-08-03 18:40 |  |  | Fair | No | Unable to locate customer after several calls also unable to locate Amrit’s academy
Outage | J.E.26.08.04960 | C001873285 | Wan Carlos Scarlett | Portmore | Completed | Load_413017 | Naggo Head - 510 | 2026-08-03 16:40 | 2026-08-03 16:42 | 2026-08-03 19:14 | 2026-08-03 19:14 | 2026-08-03 19:53 | 2026-08-03 19:55 | 2026-08-03 19:57 | 2026-08-03 19:57 |  |  | Fair | No | Found customer with internal problem advised customer to get a licensed electrician to fix the problem.found customer under ground cable from meter socket to customer breaker defective
Outage | J.E.26.08.05278 | C001873286 | Edward Royal | KSAS | Completed | Load_258287 | Hunts Bay - 310 | 2026-08-03 16:42 | 2026-08-03 16:45 | 2026-08-03 18:18 | 2026-08-03 18:19 | 2026-08-03 18:18 | 2026-08-03 18:32 | 2026-08-03 18:33 | 2026-08-03 18:33 |  |  | Fair | No | Replaced 2 40A junction fuse
Outage | J.E.26.08.05304 | C001873287 | Rusean Allen | KSAS | Completed | Load_263277 | Hunts Bay - 310 | 2026-08-03 16:42 | 2026-08-04 07:49 | 2026-08-04 09:21 | 2026-08-04 09:21 | 2026-08-04 09:45 | 2026-08-04 09:49 | 2026-08-04 09:50 | 2026-08-04 09:50 |  |  | Fair | No | Found a 10 amp fuse Replace a 10 amp fuse
Outage | J.E.26.08.05350 | C001873288 | Edward Royal | KSAS | Completed | Load_242055 | Hunts Bay - 310 | 2026-08-03 16:42 | 2026-08-03 16:45 | 2026-08-03 18:05 | 2026-08-03 18:05 | 2026-08-03 18:05 | 2026-08-03 18:05 | 2026-08-03 18:05 | 2026-08-03 18:05 |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.08.05352 | C001873291 | Edward Royal | KSAS | Completed | Load_246463 | Hunts Bay - 310 | 2026-08-03 16:42 | 2026-08-03 16:45 | 2026-08-03 18:03 | 2026-08-03 18:04 | 2026-08-03 18:04 | 2026-08-03 18:04 | 2026-08-03 18:05 | 2026-08-03 18:05 |  |  | Fair | No | Replaced 3 junction fuse 65A 2 15a
Outage | J.E.26.08.05439 | C001873292 | Edward Royal | KSAS | Completed | Load_244176 | Hunts Bay - 310 | 2026-08-03 16:42 | 2026-08-03 16:45 | 2026-08-03 16:49 | 2026-08-03 16:50 | 2026-08-03 17:40 | 2026-08-03 18:02 | 2026-08-03 18:03 | 2026-08-03 18:03 |  |  | Fair | No | Replaced 3A transformer fuse
Outage | J.E.26.08.05494 | C001873295 | Raheem Ricketts | Manchester | Completed | Load_238812 | Spur Tree - 210 | 2026-08-03 16:48 | 2026-08-03 16:54 | 2026-08-03 19:30 | 2026-08-03 19:31 | 2026-08-03 19:30 | 2026-08-03 19:31 | 2026-08-03 19:31 | 2026-08-03 19:31 |  |  | Fair | No | Call related to outage
Outage | J.E.26.08.05500 | C001873296 | Raheem Ricketts | Manchester | Completed | Load_258714 | Spur Tree - 210 | 2026-08-03 16:49 | 2026-08-03 16:53 | 2026-08-03 19:14 | 2026-08-03 19:15 | 2026-08-03 19:14 | 2026-08-03 19:16 | 2026-08-03 19:16 | 2026-08-03 19:16 |  |  | Fair | No | Call related to outage
Non-Outage | J.E.26.08.00086 | C001873303 | Neville Spencer | Clarendon | Completed | Load_252995 | Parnassus - 210 | 2026-08-03 16:53 | 2026-08-03 16:54 | 2026-08-03 17:35 | 2026-08-03 17:35 | 2026-08-03 18:02 | 2026-08-03 18:03 | 2026-08-03 18:05 | 2026-08-03 18:05 |  |  | Fair | No | Premises closed.
Outage | J.E.26.08.05576 | C001873304 | Raheem Ricketts | Manchester | Completed | Load_269073 | Spur Tree - 210 | 2026-08-03 16:54 | 2026-08-03 16:55 | 2026-08-03 19:10 | 2026-08-03 19:10 | 2026-08-03 19:10 | 2026-08-03 19:14 | 2026-08-03 19:14 | 2026-08-03 19:14 |  |  | Fair | No | Call related to outage in stanta
Outage | J.E.26.08.05329 | C001873308 | Edward Royal | KSAS | Completed | Load_250004 | Hunts Bay - 510 | 2026-08-03 16:59 | 2026-08-03 17:06 | 2026-08-03 19:56 | 2026-08-03 19:56 | 2026-08-03 19:56 | 2026-08-03 19:56 | 2026-08-03 19:57 | 2026-08-03 19:57 | Fire |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.05452 | C001873312 | Antony Levy | KSAN | Completed | Load_245669 | Constant Spring - 210 | 2026-08-03 17:07 | 2026-08-03 17:08 | 2026-08-03 18:40 | 2026-08-03 18:40 | 2026-08-03 19:02 | 2026-08-03 19:20 | 2026-08-03 19:20 | 2026-08-03 19:20 |  |  | Fair | No | Customer stated no power.... line patrolled blown 5 amp fuse found at pole # 0011173 .... line patrolled futhur and vegetation seen near line.... line test closed with 5 amp fuse and held cx has power ... line section needs URGENT bushing
Outage | J.E.26.08.05553 | C001873321 | Stephen Taylor | St.Thomas | Completed | Load_260844 | Good Year - 110 | 2026-08-03 17:08 | 2026-08-03 17:09 | 2026-08-03 18:59 | 2026-08-03 19:00 | 2026-08-03 18:59 | 2026-08-03 18:59 | 2026-08-03 19:01 | 2026-08-03 19:01 | BrokenWire |  | Fair | No | Customer advise to fix up meter socket them contact back jps for connection
Outage | J.E.26.08.05534 | C001873322 | Roxroy Needham | St.Ann | Completed | Load_265457 | Cardiff Hall - 210 | 2026-08-03 17:09 | 2026-08-03 17:26 | 2026-08-03 21:43 | 2026-08-03 21:43 | 2026-08-03 22:43 | 2026-08-03 22:43 | 2026-08-03 22:46 | 2026-08-03 22:46 | Fire |  | Fair | No | Found JPS meter burn need to change
Non-Outage | J.E.26.08.05344 | C001873324 | Moses Elliston | St.Catherine | Completed | Load_1000940 | Tredegar - 410 | 2026-08-03 17:12 | 2026-08-03 17:14 | 2026-08-03 17:40 | 2026-08-03 17:41 | 2026-08-03 17:41 | 2026-08-03 17:20 | 2026-08-03 17:42 | 2026-08-03 17:42 |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.08.05319 | C001873328 | Moses Elliston | Portmore | Completed | Load_264280 | Naggo Head - 610 | 2026-08-03 17:12 | 2026-08-03 17:14 | 2026-08-03 17:39 | 2026-08-03 17:40 | 2026-08-03 17:39 | 2026-08-03 15:55 | 2026-08-03 17:40 | 2026-08-03 17:40 |  |  | EarthMovement | No | Credit added to prepaid account.
Outage | J.E.26.08.05568 | C001873323 | Roxroy Needham | St.Ann | Completed | Load_556116 | Cardiff Hall - 210 | 2026-08-03 17:12 | 2026-08-03 17:26 | 2026-08-03 18:02 | 2026-08-03 18:58 | 2026-08-03 18:58 | 2026-08-03 18:56 | 2026-08-03 18:59 | 2026-08-03 18:59 |  |  | Fair | No | Premises found ok call customer and customer say that the light is ok
Outage | J.E.26.08.05629 | C001873335 | Antony Levy | KSAN | Completed | Load_245931 | Washington Blvd - 810 | 2026-08-03 17:29 | 2026-08-03 19:02 | 2026-08-03 20:53 | 2026-08-03 20:53 | 2026-08-03 20:53 | 2026-08-03 20:59 | 2026-08-03 20:59 | 2026-08-03 20:59 |  |  | Fair | No | Cx stated no power .... blown 50kva transformer found ...dislodged secondary phase found of 2 phase and neutral touching street light bracket... phase reinstalled with tie wire and transformer refused
Outage | J.E.26.08.05448 | C001873338 | Dean- Smith | Hanover | Completed | Load_252795 | Orange Bay - 310 | 2026-08-03 17:48 | 2026-08-03 17:50 | 2026-08-03 19:35 | 2026-08-03 20:53 | 2026-08-03 20:53 | 2026-08-03 20:53 | 2026-08-03 21:16 | 2026-08-03 21:16 |  |  | Fair | No | Reset 10kva transformer. Pole number n/a
Outage | J.E.26.08.05586 | C001873339 | Marlon Brown | Trelawny | Completed | Load_302355 | Duncans - 110 | 2026-08-03 17:48 | 2026-08-03 17:50 | 2026-08-03 19:04 | 2026-08-03 19:05 | 2026-08-03 20:20 | 2026-08-03 20:23 | 2026-08-03 20:23 | 2026-08-03 20:23 |  |  | Fair | No | Unable to locate customer via telephone nor direction
Outage | J.E.26.08.04861 | C001873340 | Shamour Haughton | Trelawny | Completed | Load_574709 | Greenwood - 210 | 2026-08-03 17:51 | 2026-08-03 17:54 | 2026-08-03 18:22 | 2026-08-03 18:22 | 2026-08-03 18:22 | 2026-08-03 18:22 | 2026-08-03 18:22 | 2026-08-03 18:22 |  |  | Fair | No | Related to previous call
Outage | J.E.26.08.04572 | C001873344 | Christopher Levy | KSAS | Completed | Load_301329 | Hunts Bay - 410 | 2026-08-03 18:00 | 2026-08-03 18:09 | 2026-08-03 21:58 | 2026-08-03 21:59 | 2026-08-03 21:59 | 2026-08-03 18:03 | 2026-08-03 22:00 | 2026-08-03 22:00 |  |  | Fair | No | Customer stated that power was restored
Outage | J.E.26.08.04573 | C001873343 | Christopher Levy | KSAS | Completed | Load_289024 | Hunts Bay - 410 | 2026-08-03 18:00 | 2026-08-03 18:09 | 2026-08-03 21:56 | 2026-08-03 21:57 | 2026-08-03 21:57 | 2026-08-03 18:10 | 2026-08-03 21:58 | 2026-08-03 21:58 |  |  | Fair | No | Customers said premises power was restored.
Outage | J.E.26.08.03318 | C001873348 | Fitzroy Turner | KSAS | Completed | Load_1002854 | Rockfort - 210 | 2026-08-03 18:05 | 2026-08-04 07:53 | 2026-08-04 13:35 | 2026-08-04 13:44 | 2026-08-04 13:43 | 2026-08-04 13:44 | 2026-08-04 13:44 | 2026-08-04 13:44 |  |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.08.03360 | C001873349 | Fitzroy Turner | KSAS | Completed | Load_267316 | Rockfort - 410 | 2026-08-03 18:06 | 2026-08-04 07:53 | 2026-08-04 13:44 | 2026-08-04 13:45 | 2026-08-04 13:44 | 2026-08-04 13:45 | 2026-08-04 13:45 | 2026-08-04 13:45 |  |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.08.05196 | C001873351 | Edward Royal | KSAS | Completed | Load_240722 | Rockfort - 410 | 2026-08-03 18:06 | 2026-08-04 12:20 | 2026-08-04 15:54 | 2026-08-04 15:55 | 2026-08-04 17:30 | 2026-08-04 17:31 | 2026-08-04 17:31 | 2026-08-04 17:31 |  |  | Fair | No
Outage | J.E.26.08.05359 | C001873354 | Christopher Levy | KSAS | Completed | Load_259746 | Rockfort - 410 | 2026-08-03 18:08 | 2026-08-03 18:09 | 2026-08-03 22:03 | 2026-08-03 22:03 | 2026-08-03 22:03 | 2026-08-03 21:22 | 2026-08-03 22:05 | 2026-08-03 22:05 |  |  | Fair | No | Customer power was restored broken service wire repaired
Outage | J.E.26.08.05223 | C001873359 | Edward Royal | KSAS | Completed | Load_246603 | Rockfort - 210 | 2026-08-03 18:16 | 2026-08-03 18:21 | 2026-08-03 22:13 | 2026-08-03 22:14 | 2026-08-03 22:13 | 2026-08-03 22:13 | 2026-08-03 22:13 | 2026-08-03 22:13 |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.08.05229 | C001873358 | Edward Royal | KSAS | Completed | Load_244455 | Rockfort - 210 | 2026-08-03 18:16 | 2026-08-03 18:21 | 2026-08-03 22:14 | 2026-08-03 22:14 | 2026-08-03 22:14 | 2026-08-03 22:14 | 2026-08-03 22:14 | 2026-08-03 22:14 |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.08.05421 | C001873357 | Edward Royal | KSAS | Completed | Load_259162 | Cane River - 310 | 2026-08-03 18:16 | 2026-08-03 18:21 | 2026-08-03 19:54 | 2026-08-03 19:55 | 2026-08-03 19:54 | 2026-08-03 19:55 | 2026-08-03 19:55 | 2026-08-03 19:55 |  |  | Fair | No | Premises not found unable to communicate with customer
Outage | J.E.26.08.05631 | C001873356 | Edward Royal | KSAS | Completed | Load_243363 | Cane River - 310 | 2026-08-03 18:16 | 2026-08-03 18:21 | 2026-08-03 22:12 | 2026-08-03 22:13 | 2026-08-03 22:12 | 2026-08-03 22:13 | 2026-08-03 22:13 | 2026-08-03 22:13 | LowHangingWires |  | Fair | No | Premises not found unable to communicate with customer
Outage | J.E.26.08.04281 | C001873364 | Edward Royal | KSAS | Completed | Load_556760 | Cane River - 410 | 2026-08-03 18:17 | 2026-08-03 18:21 | 2026-08-03 19:46 | 2026-08-03 19:47 | 2026-08-03 19:46 | 2026-08-03 19:47 | 2026-08-03 19:48 | 2026-08-03 19:48 |  |  | Fair | No | Meter not responding meter need to be check reffered to field service
Outage | J.E.26.08.05175 | C001873362 | Edward Royal | KSAS | Completed | Load_266609 | Cane River - 310 | 2026-08-03 18:17 | 2026-08-03 18:21 | 2026-08-03 19:50 | 2026-08-03 19:51 | 2026-08-03 19:50 | 2026-08-03 19:51 | 2026-08-03 19:52 | 2026-08-03 19:52 | Fire |  | Fair | No | Premises not found when contacted customer said that she live in st Elizabeth
Outage | J.E.26.08.05202 | C001873361 | Edward Royal | KSAS | Completed | Load_253227 | Rockfort - 210 | 2026-08-03 18:17 | 2026-08-03 18:21 | 2026-08-03 19:53 | 2026-08-03 19:58 | 2026-08-03 20:39 | 2026-08-03 22:10 | 2026-08-03 22:10 | 2026-08-03 22:10 |  |  | Fair | No | Replaced 100A junction fuse spliced and reconnected primary line using 20ft open number 2 conductor and 3 single bolt clamp replaced 2 30A junction fuse
Outage | J.E.26.08.05203 | C001873360 | Edward Royal | KSAS | Completed | Load_254610 | Rockfort - 210 | 2026-08-03 18:17 | 2026-08-04 13:18 | 2026-08-04 13:46 | 2026-08-04 13:46 | 2026-08-04 13:46 | 2026-08-04 13:46 | 2026-08-04 13:46 | 2026-08-04 13:46 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.03910 | C001873367 | Edward Royal | KSAS | Completed | Load_257065 | Cane River - 410 | 2026-08-03 18:18 | 2026-08-03 18:21 | 2026-08-03 19:39 | 2026-08-03 19:40 | 2026-08-03 19:39 | 2026-08-03 19:41 | 2026-08-03 19:41 | 2026-08-03 19:41 |  |  | Fair | No | Maintenance team is already notified about broken pole
Outage | J.E.26.08.04100 | C001873366 | Edward Royal | KSAS | Completed | Load_1002654 | Cane River - 310 | 2026-08-03 18:18 | 2026-08-03 18:21 | 2026-08-03 19:42 | 2026-08-03 19:42 | 2026-08-03 19:42 | 2026-08-03 19:42 | 2026-08-03 19:43 | 2026-08-03 19:43 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.04103 | C001873365 | Edward Royal | KSAS | Completed | Load_300837 | Cane River - 410 | 2026-08-03 18:18 | 2026-08-03 18:21 | 2026-08-03 19:43 | 2026-08-03 19:44 | 2026-08-03 19:43 | 2026-08-03 19:44 | 2026-08-03 19:44 | 2026-08-03 19:44 |  |  | Fair | No | Premises not found unable to communicate with customer
Outage | J.E.26.08.05578 | C001873369 | Kenroy Dale | Manchester | Completed | Load_303036 | Kendal - 210 | 2026-08-03 18:36 | 2026-08-03 18:37 | 2026-08-03 21:20 | 2026-08-03 21:30 | 2026-08-03 21:43 | 2026-08-03 21:45 | 2026-08-03 21:47 | 2026-08-03 21:47 |  |  | Fair | No | Was unable to carry out due to premises inaccessible daylight attention required
Outage | J.E.26.08.05738 | C001873371 | Oshane Warren | Westmoreland | Completed | Load_570234 | Paradise - 110 | 2026-08-03 18:44 | 2026-08-04 07:32 | 2026-08-04 10:11 | 2026-08-04 10:12 | 2026-08-04 10:28 | 2026-08-04 10:29 | 2026-08-04 10:30 | 2026-08-04 10:30 | BrokenWire |  | Fair | No | Truck tore down service wire and customer stangtion customer needs to carry out repairs in order to get reconnected
Outage | J.E.26.08.05556 | C001873379 | Neckell Ormsby | St.Mary | Completed | Load_265280 | Highgate - 210 | 2026-08-03 18:47 | 2026-08-03 18:48 | 2026-08-03 19:26 | 2026-08-03 19:26 | 2026-08-03 19:44 | 2026-08-03 19:48 | 2026-08-03 19:48 | 2026-08-03 19:48 |  |  | Fair | No | Customer said supply came back and everything was good
Outage | J.E.26.08.05577 | C001873377 | Cliton Henry | St.Mary | Completed | Load_237637 | Blackstonedge - 110 | 2026-08-03 18:47 | 2026-08-03 18:48 | 2026-08-03 19:39 | 2026-08-03 19:39 | 2026-08-03 19:41 | 2026-08-03 19:48 | 2026-08-03 19:49 | 2026-08-03 19:49 |  |  | Fair | No | The customer supply ok however a defective meter replacement was required kindly refer Field Service Department for a replacement.
Outage | J.E.26.08.05684 | C001873378 | Cliton Henry | St.Mary | Completed | Load_269808 | Oracabessa - 110 | 2026-08-03 18:47 | 2026-08-03 18:48 | 2026-08-03 19:08 | 2026-08-03 19:08 | 2026-08-03 19:33 | 2026-08-03 19:38 | 2026-08-03 19:38 | 2026-08-03 19:38 | TreeContact |  | Fair | No | Unable to locate customer. The customer contact number provided went unanswered
Outage | J.E.26.08.04396 | C001873380 | Andre Smith | KSAS | Completed | Load_252859 | Hunts Bay - 810 | 2026-08-03 18:49 | 2026-08-03 18:57 | 2026-08-03 20:30 | 2026-08-03 20:31 | 2026-08-03 20:43 | 2026-08-03 21:08 | 2026-08-03 21:09 | 2026-08-03 21:09 |  |  | Fair | No | Premises found okay supply restored already
Outage | J.E.26.08.04880 | C001873381 | Andre Smith | KSAS | Completed | Load_244836 | Hunts Bay - 710 | 2026-08-03 18:49 | 2026-08-03 18:57 | 2026-08-03 19:14 | 2026-08-03 19:15 | 2026-08-03 19:51 | 2026-08-03 20:31 | 2026-08-03 20:31 | 2026-08-03 20:31 |  |  | Fair | No | Repair burnt switch top junction supply restored
Outage | J.E.26.08.05752 | C001873382 | Javid Vernon | Westmoreland | Completed | Load_260662 | Paradise - 210 | 2026-08-03 18:52 | 2026-08-03 18:52 | 2026-08-03 18:59 | 2026-08-03 18:59 | 2026-08-03 19:45 | 2026-08-03 19:50 | 2026-08-03 19:50 | 2026-08-03 19:50 | Fire |  | Fair | No | Area check and found okay no fire was found on JPS line
Outage | J.E.26.08.05276 | C001873389 | Andre Smith | KSAS | Completed | Load_239210 | Hunts Bay - 710 | 2026-08-03 18:53 | 2026-08-03 18:55 | 2026-08-03 21:09 | 2026-08-03 21:09 | 2026-08-03 21:56 | 2026-08-03 21:57 | 2026-08-03 21:57 | 2026-08-03 21:57 |  |  | Fair | No | Repair burnt switch top junction supply restored
Outage | J.E.26.08.05650 | C001873387 | Andre Smith | KSAS | Completed | Load_261859 | Hunts Bay - 210 | 2026-08-03 18:53 | 2026-08-03 18:56 | 2026-08-03 21:58 | 2026-08-03 21:59 | 2026-08-03 22:27 | 2026-08-03 22:29 | 2026-08-03 22:29 | 2026-08-03 22:29 |  |  | Fair | No | Premises found okay supply restored already
Outage | J.E.26.08.05747 | C001873388 | Christopher Levy | KSAS | Completed | Load_244754 | Rockfort - 410 | 2026-08-03 18:53 | 2026-08-03 18:56 | 2026-08-03 22:08 | 2026-08-03 22:10 | 2026-08-03 22:39 | 2026-08-04 00:20 | 2026-08-04 00:28 | 2026-08-04 00:28 | Fire |  | Fair | No | Service wire badly burnt and pothead terminations corroded. 70ft of #6 triplex replaced and three meters reconnected spot bushing was also necessary to clear service wire at to pole for connection
Non-Outage | J.E.26.08.05211 | C001873390 | Milton Charlton |  | Completed |  |  | 2026-08-03 18:54 | 2026-08-03 18:55 | 2026-08-03 20:40 | 2026-08-03 20:40 | 2026-08-03 21:30 | 2026-08-03 20:55 | 2026-08-03 21:39 | 2026-08-03 21:39 |  |  | Fair | No | Found okay upon arrival. Customer has an internal problem.
Non-Outage | J.E.26.08.05706 | C001873401 | Shamour Haughton | St.James | Completed | Load_266674 | Bogue - 410 | 2026-08-03 19:04 | 2026-08-03 19:04 | 2026-08-03 19:17 | 2026-08-03 19:17 | 2026-08-03 22:54 | 2026-08-03 22:54 | 2026-08-03 22:55 | 2026-08-03 22:55 |  |  | Fair | No | Found customer service wire burnt off at pole, remake joint using 1 clamp
Outage | J.E.26.08.05729 | C001873403 | Derrick Dawkins | St.James | Completed | Load_239154 | Bogue - 610 | 2026-08-03 19:06 | 2026-08-03 19:08 | 2026-08-03 20:24 | 2026-08-03 20:25 | 2026-08-03 22:49 | 2026-08-03 21:11 | 2026-08-03 22:52 | 2026-08-03 22:52 |  |  | Fair | No | Check and found premises ok
Outage | J.E.26.08.05736 | C001873402 | Derrick Dawkins | St.James | Completed | Load_1001851 | Bogue - 510 | 2026-08-03 19:06 | 2026-08-03 19:08 | 2026-08-03 22:52 | 2026-08-03 22:52 | 2026-08-03 22:52 | 2026-08-03 22:02 | 2026-08-03 22:56 | 2026-08-03 22:56 |  |  | Fair | No | Found 50kva transformer fuse blown due to vegetation removed vegetation and replaced 5amp fuse no pole number available
Outage | J.E.26.08.05284 | C001873421 | Fitzroy Turner | KSAS | Completed | Load_259784 | Hunts Bay - 510 | 2026-08-03 19:45 | 2026-08-03 19:54 | 2026-08-04 01:47 | 2026-08-04 01:48 | 2026-08-04 01:47 | 2026-08-04 01:48 | 2026-08-04 01:49 | 2026-08-04 01:49 | BrokenPole |  | Fair | No | Customer supply restored after changing tree drop out switches and tree 30amps fuses
Outage | J.E.26.08.05822 | C001873426 | Michael Paterson | Westmoreland | Completed | Load_250155 | Paradise - 310 | 2026-08-03 19:58 | 2026-08-03 20:28 | 2026-08-03 21:09 | 2026-08-03 21:09 | 2026-08-03 22:35 | 2026-08-03 22:35 | 2026-08-03 22:37 | 2026-08-03 22:37 |  |  | Fair | No | Customer not responding to phone calls
Non-Outage | J.E.26.08.00086 | C001873438 | Neville Spencer | Clarendon | Completed | Load_252995 | Parnassus - 210 | 2026-08-03 20:28 | 2026-08-03 20:29 | 2026-08-03 22:05 | 2026-08-03 22:05 | 2026-08-03 22:05 | 2026-08-03 22:05 | 2026-08-03 22:08 | 2026-08-03 22:08 |  |  | Fair | No | Open 3 switches repair burnt up star point used 15 ft 2/0 PVC copper , 2 clamps supply restored.
Non-Outage | J.E.26.08.05377 | C001873437 | Michael Paterson | Westmoreland | Completed | Load_241436 | Paradise - 310 | 2026-08-03 20:28 | 2026-08-03 20:29 | 2026-08-03 21:07 | 2026-08-03 21:07 | 2026-08-03 21:07 | 2026-08-03 21:08 | 2026-08-03 21:08 | 2026-08-03 21:08 |  |  | Fair | No | No direction given, customer not responding to phone calls
Outage | J.E.26.08.05277 | C001873439 | Vivian Gordon | St.James | Completed | Load_257188 | Bogue - 310 | 2026-08-03 20:30 | 2026-08-03 20:33 | 2026-08-04 17:05 | 2026-08-04 17:06 | 2026-08-04 17:05 | 2026-08-04 16:02 | 2026-08-04 17:11 | 2026-08-04 17:11 | Traffic along road way |  | Fair | No | Replace 100ft service drop and connected meter in enclosure. Customer advised.
Outage | J.E.26.08.05080 | C001873440 | Vivian Gordon | St.James | Completed | Load_261827 | Queens Drive - 710 | 2026-08-03 20:31 | 2026-08-03 20:33 | 2026-08-04 14:42 | 2026-08-04 14:42 | 2026-08-04 14:42 | 2026-08-04 14:42 | 2026-08-04 14:47 | 2026-08-04 14:47 |  |  | Fair | No | Defective meter displaying error. Same was changed. New mtr#3024837. Ts#1784360. Installer seal#04839978
Outage | J.E.26.08.04969 | C001873446 | Swon Miller | St.James | Completed | Load_263692 | Queens Drive - 710 | 2026-08-03 20:39 | 2026-08-04 08:15 | 2026-08-04 08:18 | 2026-08-04 08:18 | 2026-08-04 08:32 | 2026-08-18 08:51 | 2026-08-04 08:52 | 2026-08-04 08:52 |  |  | Fair | No | Customer living at the address recently moved and got light disconnected line side voltage found 113/114/227 voltage left 113/114/227
Non-Outage | J.E.26.08.05951 | C001873447 | Milton Charlton |  | Completed |  |  | 2026-08-03 20:40 | 2026-08-03 20:42 | 2026-08-03 21:39 | 2026-08-03 21:39 | 2026-08-03 21:51 | 2026-08-03 22:10 | 2026-08-03 22:30 | 2026-08-03 22:30 | BrokenPole |  | Fair | No | Reconnect customer meter that was disconnected. Reconnection was done by JPS escalation.
Outage | J.E.26.08.05569 | C001873449 | Moses Elliston | St.Catherine | Completed | Load_255950 | Tredegar - 210 | 2026-08-03 20:44 | 2026-08-04 11:57 | 2026-08-04 15:26 | 2026-08-04 15:27 | 2026-08-04 16:25 | 2026-08-04 16:00 | 2026-08-04 16:27 | 2026-08-04 16:27 | BrokenWire |  | Fair | No | Crew already attended.
Outage | J.E.26.08.05966 | C001873451 | Marlon Brown | Trelawny | Completed | Load_255801 | Martha Brae - 210 | 2026-08-03 20:50 | 2026-08-03 20:51 | 2026-08-03 20:56 | 2026-08-03 20:56 | 2026-08-03 22:24 | 2026-08-03 22:36 | 2026-08-03 22:36 | 2026-08-03 22:36 |  |  | Fair | No | Refer to Field Service Department as there’s no voltage at pothead. Customer is connected to HEX box number 06974Voltage found at pothead none Voltage leaving at pothead none.
Outage | J.E.26.08.01943 | C001873453 | Nickolas Rodriques | St.Catherine | Completed | Load_253668 | Tredegar - 210 | 2026-08-03 20:51 | 2026-08-03 21:06 | 2026-08-04 01:06 | 2026-08-04 01:07 | 2026-08-04 01:48 | 2026-08-04 02:34 | 2026-08-04 02:36 | 2026-08-04 02:36 |  |  | Fair | No | Power was restored. Customer confirmed that the area outage was restored.
Non-Outage | J.E.26.08.05854 | C001873458 | Rusean Allen |  | Completed |  |  | 2026-08-03 21:10 | 2026-08-03 22:48 | 2026-08-04 02:23 | 2026-08-04 02:24 | 2026-08-04 02:29 | 2026-08-04 02:30 | 2026-08-04 02:31 | 2026-08-04 02:31 |  |  | Fair | No | More information needed
Outage | J.E.26.08.05973 | C001873459 | Rusean Allen | KSAN | Completed | Load_246237 | Constant Spring - 410 | 2026-08-03 21:10 | 2026-08-03 22:48 | 2026-08-04 01:16 | 2026-08-04 01:17 | 2026-08-04 01:59 | 2026-08-04 02:22 | 2026-08-04 02:23 | 2026-08-04 02:23 |  |  | Fair | No | Broken transformer drop lead wire found, wire was spliced and reconnected.
Outage | J.E.26.08.05790 | C001873466 | Clyde Brown | Clarendon | Completed | Load_256703 | May Pen - 110 | 2026-08-03 21:15 | 2026-08-03 21:17 | 2026-08-03 22:00 | 2026-08-04 10:36 | 2026-08-04 10:36 | 2026-08-04 10:30 | 2026-08-04 10:39 | 2026-08-04 10:39 | BangingWires | Y | Fair | No | 25kva transformer tripped caused by men cut tree on secondary line,line cleared and transformer reset.
Outage | J.E.26.08.05861 | C001873464 | Clyde Brown | Clarendon | Completed | Load_1003304 | May Pen - 110 | 2026-08-03 21:15 | 2026-08-03 21:17 | 2026-08-03 22:00 | 2026-08-04 08:40 | 2026-08-04 10:18 | 2026-08-04 10:30 | 2026-08-04 10:35 | 2026-08-04 10:35 |  | Y | Fair | No | Men cut tree on line and caused 10 kva transformer to tripped ,line cleared From secondary line and transformer reset.
Outage | J.E.26.08.05984 | C001873465 | Elvis Trowers | KSAN | Completed | Load_262209 | Washington Blvd - 310 | 2026-08-03 21:15 | 2026-08-04 07:58 | 2026-08-04 08:44 | 2026-08-04 08:44 | 2026-08-04 09:02 | 2026-08-04 09:06 | 2026-08-04 09:07 | 2026-08-04 09:07 |  |  | Fair | Yes | Premises checked and found ok upon arrival, customer was also spoken with, however she said that the power supply was restored last night.
Non-Outage | J.E.26.08.05347 | C001873467 | Rusean Allen |  | Completed |  |  | 2026-08-03 21:19 | 2026-08-04 09:59 | 2026-08-04 11:15 | 2026-08-04 11:16 | 2026-08-04 11:53 | 2026-08-04 12:12 | 2026-08-04 12:12 | 2026-08-04 12:12 | Fire |  | Fair | No | 1x 15amp fuse found 1x 15amp fuse replaced.
Outage | J.E.26.08.05532 | C001873468 | Hartley Chin | Clarendon | Completed | Load_254286 | Parnassus - 210 | 2026-08-03 21:26 | 2026-08-04 07:38 | 2026-08-04 13:58 | 2026-08-04 13:59 | 2026-08-04 15:30 | 2026-08-04 16:57 | 2026-08-04 16:58 | 2026-08-04 16:58 | BrokenWire |  | Fair | No | Isolate 25 KVA transformer to repair broken neutral. Neutral repaired and close transformer
Outage | J.E.26.08.05633 | C001873475 | Antony Levy | KSAN | Completed | Load_253684 | Constant Spring - 210 | 2026-08-03 22:00 | 2026-08-03 22:01 | 2026-08-03 22:08 | 2026-08-03 22:09 | 2026-08-03 22:44 | 2026-08-03 22:44 | 2026-08-03 22:44 | 2026-08-03 22:44 |  |  | Fair | No
Outage | J.E.26.08.06005 | C001873478 | Wan Carlos Scarlett | Portmore | Completed | Load_238728 | Naggo Head - 610 | 2026-08-03 22:09 | 2026-08-03 22:13 | 2026-08-04 08:51 | 2026-08-04 08:51 | 2026-08-04 10:05 | 2026-08-04 11:22 | 2026-08-04 11:27 | 2026-08-04 11:27 | Fire |  | Fair | No | Refuse 25amp junction no pole # was found reconnected switch jumper to transformer bushing use one bolt clamp at pole
Outage | J.E.26.08.06010 | C001873480 | Oshane Warren | Westmoreland | Completed | Load_238396 | Paradise - 110 | 2026-08-03 22:44 | 2026-08-04 07:32 | 2026-08-04 11:16 | 2026-08-04 11:17 | 2026-08-04 11:16 | 2026-08-04 11:21 | 2026-08-04 11:23 | 2026-08-04 11:23 | LeaningPole |  | Fair | No | Concrete pole with primary and secondary on it leaning on customers fence refer to maintenance
Non-Outage | J.E.26.08.05441 | C001873482 | Omar King |  | Completed |  |  | 2026-08-03 22:46 | 2026-08-03 22:49 | 2026-08-04 01:53 | 2026-08-04 01:54 | 2026-08-04 02:29 | 2026-08-04 02:30 | 2026-08-04 02:30 | 2026-08-04 02:30 |  |  | Fair | No | Unable to find customer call several times no answer directions not sufficient
Outage | J.E.26.08.05415 | C001873481 | Omar King | St.Ann | Completed | Load_264147 | Cardiff Hall - 210 | 2026-08-03 22:46 | 2026-08-03 22:50 | 2026-08-04 01:34 | 2026-08-04 01:35 | 2026-08-04 01:52 | 2026-08-04 01:53 | 2026-08-04 01:53 | 2026-08-04 01:53 |  |  | Fair | No | Customer request a day visit
Outage | J.E.26.08.05427 | C001873483 | Tyrese Williams | St.Ann | Completed | Load_261514 | Cardiff Hall - 310 | 2026-08-03 22:46 | 2026-08-04 07:40 | 2026-08-04 08:05 | 2026-08-04 10:04 | 2026-08-04 10:07 | 2026-08-04 10:08 | 2026-08-04 10:08 | 2026-08-04 10:08 |  |  | Fair | No | Premises found ok customer said power was restored
Outage | J.E.26.08.06014 | C001873484 | Omar King | St.Ann | Completed | Load_573920 | Cardiff Hall - 310 | 2026-08-03 22:46 | 2026-08-03 22:48 | 2026-08-03 23:15 | 2026-08-03 23:16 | 2026-08-04 00:30 | 2026-08-04 01:33 | 2026-08-04 01:34 | 2026-08-04 01:34 |  |  | Fair | No | Found one bolt clamp with corrosion at pole repair as been carry out customer is now with supply voltage reading 119-119-238 Volts
Outage | J.E.26.08.05913 | C001873485 | Michael Christian | St.James | Completed | Load_258936 | Queens Drive - 710 | 2026-08-03 22:59 | 2026-08-03 23:00 | 2026-08-04 02:45 | 2026-08-04 02:45 | 2026-08-04 03:45 | 2026-08-04 04:04 | 2026-08-04 04:04 | 2026-08-04 04:04 | BrokenWire |  | Fair | No | Found bunt wire needs 80 ft wire send to field service urgent
Outage | J.E.26.08.06017 | C001873486 | Michael Christian | St.James | Completed | Load_245028 | Bogue - 610 | 2026-08-03 23:00 | 2026-08-03 23:01 | 2026-08-04 02:43 | 2026-08-04 02:44 | 2026-08-04 02:43 | 2026-08-04 02:44 | 2026-08-04 02:45 | 2026-08-04 02:45 |  |  | Fair | No | Reset 1 10 kava cause by broken wire
Outage | J.E.26.08.05507 | C001873488 | Michael Christian | St.James | Completed | Load_245028 | Bogue - 610 | 2026-08-03 23:01 | 2026-08-03 23:02 | 2026-08-03 23:59 | 2026-08-04 00:01 | 2026-08-04 01:21 | 2026-08-04 02:43 | 2026-08-04 02:43 | 2026-08-04 02:43 |  |  | Fair | No | Found 1 10 kava out cause by broken wire replace use 2 clamps and reset
Outage | J.E.26.08.06022 | C001873489 | Nickolas Rodriques | St.Catherine | Completed | Load_262197 | Twickenham - 210 | 2026-08-03 23:06 | 2026-08-03 23:08 | 2026-08-04 03:00 | 2026-08-04 03:01 | 2026-08-04 03:38 | 2026-08-04 04:06 | 2026-08-04 04:09 | 2026-08-04 04:09 | BrokenWire |  | Fair | No | Checked and found a 3 amp transformer fuse blown caused by defective fuse holder. Repaired by replacing the fuse and a fuse holder after completing patrol.
Outage | J.E.26.08.05712 | C001873492 | Nickolas Rodriques | Portmore | Completed | Load_266759 | Naggo Head - 510 | 2026-08-03 23:09 | 2026-08-03 23:10 | 2026-08-04 00:52 | 2026-08-04 04:10 | 2026-08-04 04:23 | 2026-08-04 04:29 | 2026-08-04 04:46 | 2026-08-04 04:46 | BrokenWire |  | Fair | No | Customer stated that he is single phasing. Daylight attention required for power quality.
Outage | J.E.26.08.05580 | C001873494 | Rodclif Dawkins | Portmore | Completed | Load_260555 | Naggo Head - 610 | 2026-08-03 23:10 | 2026-08-04 16:04 | 2026-08-04 16:49 | 2026-08-04 16:50 | 2026-08-04 16:58 | 2026-08-04 17:16 | 2026-08-04 17:17 | 2026-08-04 17:17 | BrokenWire |  | Fair | No | Customer found okay
Non-Outage | J.E.26.08.06175 | C001873567 | Evan Spaulding |  | Completed |  |  | 2026-08-04 07:26 | 2026-08-04 07:32 | 2026-08-04 13:46 | 2026-08-04 13:47 | 2026-08-04 13:47 | 2026-08-04 13:50 | 2026-08-04 13:51 | 2026-08-04 13:51 | Fire |  | Fair | No | Premises not found,customer not answering phone calls to give proper directions.
Outage | J.E.26.08.06179 | C001873570 | Raymond Carr | St.Ann | Completed | Load_249600 | Upper White River - 110 | 2026-08-04 07:32 | 2026-08-04 07:36 | 2026-08-04 08:44 | 2026-08-04 08:44 | 2026-08-04 10:36 | 2026-08-04 11:00 | 2026-08-04 11:24 | 2026-08-04 11:24 |  |  | SevereWind | No | Blown 25 kva transformer fuse found, line patrol and found 2 spans of secondary conductors banged together were cleared, however after several tests close 25 kva transformer found to be defective. Refer to maintenance department for replacement. About 23 customers are affected.
Outage | J.E.26.08.05972 | C001873571 | Clyde Brown | Clarendon | Completed | Load_257284 | Parnassus - 310 | 2026-08-04 07:34 | 2026-08-05 07:48 | 2026-08-05 08:44 | 2026-08-05 11:29 | 2026-08-05 11:29 | 2026-08-05 11:30 | 2026-08-05 11:32 | 2026-08-05 11:32 |  |  | Fair | No | Cannot be located customer not answering phone
Outage | J.E.26.08.06006 | C001873573 | Hartley Chin | Clarendon | Completed | Load_247306 | Monymusk - 410 | 2026-08-04 07:34 | 2026-08-04 07:35 | 2026-08-04 11:24 | 2026-08-04 11:25 | 2026-08-04 12:38 | 2026-08-04 13:28 | 2026-08-04 13:30 | 2026-08-04 13:30 |  |  | SevereWind | No | Found blown 2 amp fuse on 15 KVA transformer @ pole # 0210789 line patrolled and found okay , transformer refused…
Outage | J.E.26.08.06025 | C001873572 | Clyde Brown | Clarendon | Completed | Load_269757 | Monymusk - 210 | 2026-08-04 07:34 | 2026-08-05 07:48 | 2026-08-05 08:44 | 2026-08-05 11:34 | 2026-08-05 12:44 | 2026-08-05 12:40 | 2026-08-05 12:51 | 2026-08-05 12:51 |  |  | Fair | No | Corrosion at 2 wire service pothead connection remade with 1- clamp.voltage left 111V.
Outage | J.E.26.08.06178 | C001873574 | Clyde Brown | Clarendon | Completed | Load_265610 | May Pen - 210 | 2026-08-04 07:34 | 2026-08-05 07:48 | 2026-08-05 08:44 | 2026-08-05 09:28 | 2026-08-05 09:27 | 2026-08-05 09:29 | 2026-08-05 09:30 | 2026-08-05 09:30 |  |  | Fair | No | Cannot be located customer not answering phone
Outage | J.E.26.08.05291 | C001873575 | Damion Reid | Manchester | Completed | Load_254566 | Spur Tree - 310 | 2026-08-04 07:35 | 2026-08-04 07:36 | 2026-08-04 08:19 | 2026-08-04 08:20 | 2026-08-04 09:41 | 2026-08-04 10:30 | 2026-08-04 10:31 | 2026-08-04 10:31 |  |  | Fair | No | Blown 3amp fuse found for 25kva transformer cause by contamination line patrol and replace blown fuse
Outage | J.E.26.08.06164 | C001873576 | Raymond Lewis | St.Ann | Completed | Load_555713 | Roaring River - 210 | 2026-08-04 07:36 | 2026-08-04 07:39 | 2026-08-04 11:09 | 2026-08-04 11:09 | 2026-08-04 14:46 | 2026-08-28 15:00 | 2026-08-04 15:01 | 2026-08-04 15:01 |  |  | SevereWind | No | Replace burn up fuse holder 25 A
Outage | J.E.26.08.06177 | C001873579 | Derrick Grubb | St.Thomas | Completed | Load_243367 | Good Year - 210 | 2026-08-04 07:38 | 2026-08-04 07:40 | 2026-08-04 08:06 | 2026-08-04 12:11 | 2026-08-04 13:27 | 2026-08-04 14:17 | 2026-08-04 14:18 | 2026-08-04 14:18 |  |  | Fair | No | Clear corrosion at customer pothead using two one bolt clamps. Voltage readings when leaving 119v, 118v, 238v.
Non-Outage | J.E.26.08.02587 | C001873580 | Raymond Lewis |  | Completed |  |  | 2026-08-04 07:39 | 2026-08-04 07:39 | 2026-08-04 08:01 | 2026-08-04 08:01 | 2026-08-04 09:19 | 2026-08-04 23:07 | 2026-08-04 11:08 | 2026-08-04 11:08 |  |  | Fair | No | Open 25 kva x former to splice and retention 2 span secondary neutral
Outage | J.E.26.08.05578 | C001873581 | Barnett Brown | Manchester | Completed | Load_303036 | Kendal - 210 | 2026-08-04 07:39 | 2026-08-04 07:40 | 2026-08-04 09:19 | 2026-08-04 09:20 | 2026-08-04 10:38 | 2026-08-04 11:28 | 2026-08-04 11:30 | 2026-08-04 11:30 |  |  | Fair | No | Replace blown 3 amp fuse with 8 amp for 100 kva transformer
Non-Outage | J.E.26.08.04889 | C001873583 | Fitzroy Turner |  | Completed |  |  | 2026-08-04 07:43 | 2026-08-04 07:48 | 2026-08-04 09:58 | 2026-08-04 12:24 | 2026-08-04 13:32 | 2026-08-04 13:40 | 2026-08-04 13:43 | 2026-08-04 13:43 |  |  | Fair | No | Found tree phase primary one fuse blown and one switches bottom burnt off use one clamp and 3 20amp fuse to carry out repair supply restored to customer
Outage | J.E.26.08.04296 | C001873590 | Rusean Allen | KSAS | Completed | Load_262052 | Hunts Bay - 510 | 2026-08-04 07:44 | 2026-08-04 07:48 | 2026-08-04 10:47 | 2026-08-04 10:47 | 2026-08-04 10:47 | 2026-08-04 10:47 | 2026-08-04 10:48 | 2026-08-04 10:48 |  |  | Fair | No | Premises okay
Outage | J.E.26.08.04309 | C001873591 | Rusean Allen | KSAS | Completed | Load_242843 | Hunts Bay - 510 | 2026-08-04 07:44 | 2026-08-04 07:48 | 2026-08-04 09:52 | 2026-08-04 09:53 | 2026-08-04 10:00 | 2026-08-04 10:01 | 2026-08-04 10:01 | 2026-08-04 10:01 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.04606 | C001873587 | Rusean Allen | KSAS | Completed | Load_246076 | Hunts Bay - 110 | 2026-08-04 07:44 | 2026-08-04 07:48 | 2026-08-04 10:04 | 2026-08-04 10:04 | 2026-08-04 10:15 | 2026-08-04 10:40 | 2026-08-04 10:41 | 2026-08-04 10:41 |  |  | Fair | No | 3x 10amp fuse found 3x 10amp fuse replaced
Outage | J.E.26.08.06059 | C001873586 | Daniel Lobar | Trelawny | Completed | Load_555931 | Martha Brae - 210 | 2026-08-04 07:44 | 2026-08-04 08:38 | 2026-08-04 12:28 | 2026-08-04 12:28 | 2026-08-04 12:40 | 2026-08-04 13:10 | 2026-08-04 13:15 | 2026-08-04 13:15 |  |  | Fair | No | Replace corroded clamps on service side of customer pot head. Left voltage readings; 115, 114 and 229 across phases
Outage | J.E.26.08.06107 | C001873589 | Floyd Taylor | Trelawny | Completed | Load_302315 | Greenwood - 210 | 2026-08-04 07:44 | 2026-08-04 07:45 | 2026-08-04 08:13 | 2026-08-04 08:13 | 2026-08-04 08:40 | 2026-08-04 09:52 | 2026-08-04 09:52 | 2026-08-04 09:52 |  |  | Fair | No | Remove illegal connection from line reset 10kva transformer, voltage readings left 105,107,2118
Outage | J.E.26.08.06188 | C001873584 | Rusean Allen | KSAS | Completed | Load_265823 | Hunts Bay - 210 | 2026-08-04 07:44 | 2026-08-05 09:10 | 2026-08-05 09:50 | 2026-08-05 09:50 | 2026-08-05 10:38 | 2026-08-05 10:39 | 2026-08-05 10:39 | 2026-08-05 10:39 |  |  | Fair | No | Found okay
Outage | J.E.26.08.05415 | C001873592 | Tyrese Williams | St.Ann | Completed | Load_264147 | Cardiff Hall - 210 | 2026-08-04 07:45 | 2026-08-04 07:53 | 2026-08-04 08:05 | 2026-08-04 08:06 | 2026-08-04 09:31 | 2026-08-04 10:00 | 2026-08-04 10:00 | 2026-08-04 10:00 |  |  | Fair | No | Remade service wire joint at pothead use 1 pg clamp voltage check 16/120/236
Non-Outage | J.E.26.08.04791 | C001873593 | Orville Lee | Portmore | Completed | Load_243335 | Naggo Head - 610 | 2026-08-04 07:46 | 2026-08-04 07:49 | 2026-08-04 08:45 | 2026-08-04 11:04 | 2026-08-04 11:28 | 2026-08-04 14:19 | 2026-08-04 14:21 | 2026-08-04 14:21 |  |  | Fair | No | Check made and found voltage unbalanced Voltage at Pothead 119V105VVoltage Tee connection load119V105VVoltage at drop lead with load119V X1-X2110V X2-X3Voltage at transformer lug without load120V114VVoltage at transformer lug without load 118V X1-X2118V X2-X3Refer to maintenance for further inspection
Non-Outage | J.E.26.08.06157 | C001873594 | Orville Lee | St.Catherine | Completed | Load_259899 | Twickenham - 210 | 2026-08-04 07:46 | 2026-08-04 07:49 | 2026-08-04 08:45 | 2026-08-05 10:07 | 2026-08-05 10:22 | 2026-08-05 10:31 | 2026-08-05 10:33 | 2026-08-05 10:33 |  |  | Fair | No | Premise found ok upon arrival Voltage 115V116V231VCustomer was reporting a buzzing sound at a transformer connection
Outage | J.E.26.08.06001 | C001873597 | Elvis Trowers | KSAN | Completed | Load_567702 | Washington Blvd - 310 | 2026-08-04 07:50 | 2026-08-04 07:55 | 2026-08-04 09:21 | 2026-08-04 09:21 | 2026-08-04 09:29 | 2026-08-04 09:35 | 2026-08-04 09:35 | 2026-08-04 09:35 |  |  | Fair | Yes | Premises checked and found ok upon arrival, customer was also spoken with.
Outage | J.E.26.08.06201 | C001873598 | Roxroy Needham | St.Ann | Completed | Load_265652 | Roaring River - 410 | 2026-08-04 07:52 | 2026-08-05 00:45 | 2026-08-05 01:01 | 2026-08-05 01:01 | 2026-08-05 01:01 | 2026-08-05 01:01 | 2026-08-05 01:02 | 2026-08-05 01:02 |  |  | Fair | No | Premises found ok call customer and customer say that the light is ok
Non-Outage | J.E.26.08.05102 | C001873604 | Andrae Clarke | Portland | Completed | Load_267280 | Port Antonio - 410 | 2026-08-04 07:54 | 2026-08-04 08:19 | 2026-08-04 11:52 | 2026-08-04 12:14 | 2026-08-04 12:14 | 2026-08-04 13:15 | 2026-08-04 13:05 | 2026-08-04 13:05 |  |  | Fair | No | Repair broken neutral two one bolt clamp Check voltage 119/121/230
Non-Outage | J.E.26.08.05138 | C001873602 | Andrae Clarke | Portland | Completed | Load_251260 | Port Antonio - 410 | 2026-08-04 07:54 | 2026-08-04 08:19 | 2026-08-04 08:43 | 2026-08-04 08:45 | 2026-08-04 08:44 | 2026-08-04 08:40 | 2026-08-04 08:50 | 2026-08-04 08:50 |  | Y | Fair | No | 190 leg not working and trees resting on primary lineCustomer requesting an Emergency Crew to assist with get tree cutRefer to Emergency Crew
Non-Outage | J.E.26.08.05174 | C001873603 | Andrae Clarke | Portland | Completed | Load_259696 | Port Antonio - 410 | 2026-08-04 07:54 | 2026-08-04 08:19 | 2026-08-04 11:00 | 2026-08-04 11:01 | 2026-08-04 11:41 | 2026-08-04 11:40 | 2026-08-04 11:43 | 2026-08-04 11:43 |  |  | Fair | No | Check voltage 117/118/236Premises okay Customer needs to change meter socket
Non-Outage | J.E.26.08.05192 | C001873600 | Andrae Clarke | Portland | Completed | Load_260170 | Port Antonio - 410 | 2026-08-04 07:54 | 2026-08-04 08:19 | 2026-08-04 11:46 | 2026-08-04 14:06 | 2026-08-04 14:06 | 2026-08-04 14:18 | 2026-08-04 14:11 | 2026-08-04 14:11 |  |  | Fair | No | Unable to locate the customer Made several calls and got no response
Non-Outage | J.E.26.08.05471 | C001873601 | Andrae Clarke | Portland | Completed | Load_249717 | Port Antonio - 410 | 2026-08-04 07:54 | 2026-08-04 08:19 | 2026-08-04 08:57 | 2026-08-04 08:58 | 2026-08-04 10:20 | 2026-08-04 10:27 | 2026-08-04 11:00 | 2026-08-04 11:00 |  |  | Fair | No | Check voltage repair corroded wires Use two one bolt clamp Check voltage 122/121/242
Non-Outage | J.E.26.08.05275 | C001873605 | Orville Lee | St.Catherine | Completed | Load_245048 | Twickenham - 210 | 2026-08-04 07:56 | 2026-08-04 07:57 | 2026-08-04 08:45 | 2026-08-05 10:35 | 2026-08-05 10:43 | 2026-08-05 11:02 | 2026-08-05 11:04 | 2026-08-05 11:04 |  |  | Fair | No | Checks made and found pothead corroded 1-Penn union 1-one bolt clamp usedVoltage 115V
Non-Outage | J.E.26.08.05600 | C001873607 | Orville Lee | Portmore | Completed | Load_261745 | Naggo Head - 610 | 2026-08-04 07:56 | 2026-08-04 07:57 | 2026-08-04 08:45 | 2026-08-04 08:56 | 2026-08-04 09:26 | 2026-08-04 10:00 | 2026-08-04 10:02 | 2026-08-04 10:02 |  |  | Fair | No | Checks made and found pothead and secondary line corroded 3 one bolt clamps and 3 Penn union used Voltage 119V119V238V
Non-Outage | J.E.26.08.05637 | C001873606 | Orville Lee | Portmore | Completed | Load_264803 | Naggo Head - 510 | 2026-08-04 07:56 | 2026-08-04 07:57 | 2026-08-04 08:45 | 2026-08-05 09:17 | 2026-08-05 09:30 | 2026-08-05 10:05 | 2026-08-05 10:06 | 2026-08-05 10:06 |  |  | Fair | No | Changed clamps at pothead Voltage 116V117V233VCustomer request for defective street light to be replaced at her gate
Non-Outage | J.E.26.08.05727 | C001873608 | Orville Lee | St.Catherine | Completed | Load_576115 | Twickenham - 210 | 2026-08-04 07:56 | 2026-08-04 07:57 | 2026-08-04 08:45 | 2026-08-05 14:41 | 2026-08-05 14:42 | 2026-08-05 15:29 | 2026-08-05 15:30 | 2026-08-05 15:30 |  |  | Fair | No | Open secondary neutral wire burstOpen secondary neutral wire reconnected Voltage 116V117V233V
Non-Outage | J.E.26.08.05805 | C001873609 | Orville Lee | Portmore | Completed | Load_258707 | Naggo Head - 510 | 2026-08-04 07:56 | 2026-08-04 07:57 | 2026-08-04 08:45 | 2026-08-04 15:58 | 2026-08-04 16:24 | 2026-08-04 16:41 | 2026-08-04 16:42 | 2026-08-04 16:42 |  |  | Fair | No | Checks made and found take of wire disconnected 3 one bolt clamps used Voltage 116V117V234V
Non-Outage | J.E.26.08.06062 | C001873611 | Orville Lee | Portmore | Completed | Load_254353 | Naggo Head - 610 | 2026-08-04 07:56 | 2026-08-04 07:57 | 2026-08-04 08:45 | 2026-08-04 10:04 | 2026-08-04 10:45 | 2026-08-04 11:02 | 2026-08-04 11:02 | 2026-08-04 11:02 |  |  | Fair | No | Check made and found pothead and secondary line corroded Voltage 119V119V238V
Non-Outage | J.E.26.08.06147 | C001873612 | Orville Lee | St.Catherine | Completed | Load_241076 | Twickenham - 210 | 2026-08-04 07:56 | 2026-08-04 07:57 | 2026-08-04 08:45 | 2026-08-05 13:41 | 2026-08-05 13:48 | 2026-08-05 14:11 | 2026-08-05 14:12 | 2026-08-05 14:12 |  |  | Fair | No | Changed corroded clamps at pothead and secondary line4 one bolt clamps used and 2 Penn union voltage 114V115V230V
Outage | J.E.26.08.06213 | C001873615 | Raymond Carr | St.Mary | Completed | Load_239058 | Blackstonedge - 110 | 2026-08-04 07:58 | 2026-08-04 08:00 | 2026-08-04 11:24 | 2026-08-04 11:24 | 2026-08-04 12:01 | 2026-08-04 | 2026-08-04 12:03 | 2026-08-04 12:03 |  |  | Fair | No | Customer reported that he is in Kingston,however several calls to his caretaker contact number went unanswered
Non-Outage | J.E.26.08.03587 | C001873624 | Royston Montague | St.Catherine | Completed | Load_250288 | Tredegar - 410 | 2026-08-04 08:00 | 2026-08-04 08:02 | 2026-08-04 08:41 | 2026-08-04 14:56 | 2026-08-04 15:15 | 2026-08-04 15:15 | 2026-08-04 15:15 | 2026-08-04 15:15 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.08.04037 | C001873625 | Royston Montague | St.Catherine | Completed | Load_239039 | Tredegar - 210 | 2026-08-04 08:00 | 2026-08-04 08:02 | 2026-08-04 08:41 | 2026-08-04 09:30 | 2026-08-04 09:46 | 2026-08-04 09:46 | 2026-08-04 09:46 | 2026-08-04 09:46 |  |  | Fair | No | Customer confirmed issue resolved
Non-Outage | J.E.26.08.04039 | C001873626 | Royston Montague | St.Catherine | Completed | Load_255950 | Tredegar - 210 | 2026-08-04 08:00 | 2026-08-04 08:02 | 2026-08-04 08:41 | 2026-08-04 11:16 | 2026-08-04 11:15 | 2026-08-04 11:51 | 2026-08-04 11:51 | 2026-08-04 11:51 | LowHangingWires |  | Fair | No | Damage twisted wire. #6, same change, voltage found 114v voltage after job completion are 229v 114v 113v
Non-Outage | J.E.26.08.04052 | C001873623 | Royston Montague | St.Catherine | Completed | Load_239039 | Tredegar - 210 | 2026-08-04 08:00 | 2026-08-04 08:02 | 2026-08-04 08:41 | 2026-08-04 09:12 | 2026-08-04 09:25 | 2026-08-04 09:26 | 2026-08-04 09:26 | 2026-08-04 09:26 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.08.04977 | C001873622 | Royston Montague | St.Catherine | Completed | Load_269657 | Tredegar - 410 | 2026-08-04 08:00 | 2026-08-04 08:02 | 2026-08-04 08:41 | 2026-08-04 13:41 | 2026-08-04 13:41 | 2026-08-04 13:41 | 2026-08-04 13:41 | 2026-08-04 13:41 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.08.05085 | C001873620 | Royston Montague | St.Catherine | Completed | Load_267229 | Tredegar - 210 | 2026-08-04 08:00 | 2026-08-04 08:02 | 2026-08-04 08:41 | 2026-08-04 11:55 | 2026-08-04 12:41 | 2026-08-04 12:50 | 2026-08-04 12:50 | 2026-08-04 12:50 | Fire |  | Fair | No | Premises found ok. Customer confirmed an emergency team visited.
Non-Outage | J.E.26.08.05098 | C001873619 | Royston Montague | St.Catherine | Completed | Load_265936 | Tredegar - 210 | 2026-08-04 08:00 | 2026-08-04 08:02 | 2026-08-04 08:41 | 2026-08-04 08:59 | 2026-08-04 09:07 | 2026-08-04 09:08 | 2026-08-04 09:08 | 2026-08-04 09:08 |  |  | Fair | No | Customer confirmed issue resolved last night.
Non-Outage | J.E.26.08.05162 | C001873621 | Royston Montague | St.Catherine | Completed | Load_1000958 | Tredegar - 410 | 2026-08-04 08:00 | 2026-08-04 08:02 | 2026-08-04 08:41 | 2026-08-05 13:45 | 2026-08-05 14:46 | 2026-08-05 14:47 | 2026-08-05 14:48 | 2026-08-05 14:48 |  |  | Fair | No | Not locating this customer. Person who answer the phone said they did not make an report. GPS coordinate on job not working.
Non-Outage | J.E.26.08.05324 | C001873617 | Royston Montague | St.Catherine | Completed | Load_249355 | Tredegar - 310 | 2026-08-04 08:00 | 2026-08-04 08:02 | 2026-08-04 08:41 | 2026-08-04 15:16 | 2026-08-04 16:12 | 2026-08-04 16:13 | 2026-08-04 16:13 | 2026-08-04 16:13 |  |  | Fair | No | Not locating this premises, Multiple calls to customer phone go without answer. GPS coordinate on job not working.
Non-Outage | J.E.26.08.05372 | C001873618 | Royston Montague | St.Catherine | Completed | Load_269657 | Tredegar - 410 | 2026-08-04 08:00 | 2026-08-04 08:02 | 2026-08-04 08:41 | 2026-08-04 12:51 | 2026-08-04 13:33 | 2026-08-04 13:41 | 2026-08-04 13:41 | 2026-08-04 13:41 |  |  | Fair | No | Customer confirmed issue resolved.
Outage | J.E.26.08.05967 | C001873627 | Edward Royal | KSAS | Completed | Load_254610 | Rockfort - 210 | 2026-08-04 08:01 | 2026-08-04 12:21 | 2026-08-04 13:46 | 2026-08-04 13:47 | 2026-08-04 13:46 | 2026-08-04 13:47 | 2026-08-04 13:47 | 2026-08-04 13:47 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.05592 | C001873632 | Christopher Edwards | KSAN | Completed | Load_265024 | Constant Spring - 410 | 2026-08-04 08:03 | 2026-08-04 08:09 | 2026-08-04 08:29 | 2026-08-04 08:47 | 2026-08-04 09:11 | 2026-08-04 10:26 | 2026-08-04 10:26 | 2026-08-04 10:26 |  |  | Fair | No | Customer breaker was tripped Supply has returned to premises
Outage | J.E.26.08.06193 | C001873631 | Dwayne Cohen | KSAN | Completed | Load_261862 | Washington Blvd - 410 | 2026-08-04 08:03 | 2026-08-04 08:04 | 2026-08-04 08:51 | 2026-08-04 09:32 | 2026-08-04 09:32 | 2026-08-04 09:31 | 2026-08-04 09:32 | 2026-08-04 09:32 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.06160 | C001873633 | Dwayne Cohen | KSAN | Completed | Load_241137 | Washington Blvd - 610 | 2026-08-04 08:04 | 2026-08-04 08:08 | 2026-08-04 08:12 | 2026-08-04 08:13 | 2026-08-04 08:43 | 2026-08-04 08:44 | 2026-08-04 08:51 | 2026-08-04 08:51 | Fire |  | Fair | No | Refuse blown 3amps transformer link, supply now restore.
Outage | J.E.26.08.05446 | C001873638 | Fitzroy Turner | KSAS | Completed | Load_260363 | Rockfort - 410 | 2026-08-04 08:09 | 2026-08-04 08:10 | 2026-08-04 12:06 | 2026-08-04 12:15 | 2026-08-04 12:14 | 2026-08-04 12:14 | 2026-08-04 12:16 | 2026-08-04 12:16 |  |  | Fair | No | Found 10amps fuse for 100kva transformer blown.replace one 10 amp fuse supply restored to customer
Non-Outage | J.E.26.07.32805 | C001873642 | Oraine Minto | St.Ann | Completed | Load_240309 | Ocho Rios - 310 | 2026-08-04 08:10 | 2026-08-04 08:12 | 2026-08-04 14:24 | 2026-08-04 14:24 | 2026-08-04 14:24 | 2026-08-04 14:55 | 2026-08-04 14:58 | 2026-08-04 14:58 |  |  | Fair | No | Refer to emergency Bucket truck required Top phase out of reach Customer states that entire are experiencing low voltage at nights Street light disconnected Pole# 16520731v 117v
Non-Outage | J.E.26.07.36479 | C001873640 | Oraine Minto | St.Ann | Completed | Load_239586 | Ocho Rios - 310 | 2026-08-04 08:10 | 2026-08-04 08:12 | 2026-08-04 12:44 | 2026-08-04 12:47 | 2026-08-04 12:46 | 2026-08-04 12:46 | 2026-08-04 12:47 | 2026-08-04 12:47 |  |  | Fair | No | Issue resolved
Non-Outage | J.E.26.07.36489 | C001873643 | Oraine Minto | St.Ann | Completed | Load_268995 | Ocho Rios - 310 | 2026-08-04 08:10 | 2026-08-04 08:12 | 2026-08-05 10:00 | 2026-08-05 10:00 | 2026-08-05 10:38 | 2026-08-05 10:40 | 2026-08-05 10:41 | 2026-08-05 10:41 |  |  | Fair | No | Customer states that he had not heard of an issue in the area for the last two days
Non-Outage | J.E.26.07.36597 | C001873645 | Oraine Minto | St.Ann | Completed | Load_250046 | Ocho Rios - 310 | 2026-08-04 08:10 | 2026-08-04 08:12 | 2026-08-04 12:56 | 2026-08-04 12:56 | 2026-08-04 12:56 | 2026-08-04 12:56 | 2026-08-04 12:56 | 2026-08-04 12:56 |  |  | Fair | No | Power was restored
Non-Outage | J.E.26.07.36658 | C001873644 | Oraine Minto | St.Ann | Completed | Load_244721 | Ocho Rios - 310 | 2026-08-04 08:10 | 2026-08-04 08:12 | 2026-08-04 12:51 | 2026-08-04 12:52 | 2026-08-04 12:52 | 2026-08-04 12:52 | 2026-08-04 12:53 | 2026-08-04 12:53 |  |  | Fair | No | Issue resolved
Non-Outage | J.E.26.07.37001 | C001873646 | Oraine Minto | St.Ann | Completed | Load_243646 | Ocho Rios - 310 | 2026-08-04 08:10 | 2026-08-04 08:12 | 2026-08-04 12:58 | 2026-08-04 12:59 | 2026-08-04 12:59 | 2026-08-04 13:00 | 2026-08-04 13:00 | 2026-08-04 13:00 |  |  | Fair | No | Power was restored
Non-Outage | J.E.26.08.04236 | C001873648 | Odeanie Davis | KSAS | Completed | Load_289600 | Greenwich - 510 | 2026-08-04 08:12 | 2026-08-04 08:14 | 2026-08-04 12:23 | 2026-08-04 12:23 | 2026-08-04 12:23 | 2026-08-04 12:28 | 2026-08-04 12:24 | 2026-08-04 12:24 |  |  | Fair | No | 124v/124v & 249v at location from rammi box. Rammi team needed
Non-Outage | J.E.26.08.04238 | C001873647 | Odeanie Davis | KSAS | Completed | Load_300929 | Greenwich - 410 | 2026-08-04 08:12 | 2026-08-04 08:14 | 2026-08-04 11:42 | 2026-08-04 13:57 | 2026-08-04 13:57 | 2026-08-04 13:57 | 2026-08-04 13:58 | 2026-08-04 13:58 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.04264 | C001873650 | Odeanie Davis | KSAS | Completed | Load_259853 | Greenwich - 410 | 2026-08-04 08:12 | 2026-08-04 08:14 | 2026-08-04 11:42 | 2026-08-04 13:58 | 2026-08-04 13:58 | 2026-08-04 14:31 | 2026-08-04 16:29 | 2026-08-04 16:29 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.04271 | C001873649 | Odeanie Davis | KSAS | Completed | Load_246165 | Greenwich - 410 | 2026-08-04 08:12 | 2026-08-04 08:14 | 2026-08-04 12:23 | 2026-08-04 12:25 | 2026-08-04 12:24 | 2026-08-04 13:37 | 2026-08-04 13:56 | 2026-08-04 13:56 |  |  | Fair | No | 115v/118v & 233v at location, open neutral on customer line corrected, however Customer has defective wires at location, customer was advised to contact their electrician.
Non-Outage | J.E.26.08.04364 | C001873651 | Odeanie Davis | KSAS | Completed | Load_254629 | Up Park Camp - 310 | 2026-08-04 08:12 | 2026-08-04 08:14 | 2026-08-04 09:54 | 2026-08-04 09:56 | 2026-08-04 09:56 | 2026-08-04 10:36 | 2026-08-04 10:37 | 2026-08-04 10:37 |  |  | Fair | No | 119v/119v & 238v, 207v on 190 phase, meter found burnt on line side, meter lugs were hot to the touch, customer was advised to contact their electrician,
Non-Outage | J.E.26.08.04379 | C001873655 | Odeanie Davis | KSAS | Completed | Load_289600 | Up Park Camp - 310 | 2026-08-04 08:12 | 2026-08-04 08:14 | 2026-08-04 12:19 | 2026-08-04 12:20 | 2026-08-04 12:19 | 2026-08-04 12:22 | 2026-08-04 12:23 | 2026-08-04 12:23 |  |  | Fair | No | 124v/124v & 249v at location from rammi box. Rammi team needed
Non-Outage | J.E.26.08.04622 | C001873657 | Odeanie Davis | KSAS | Completed | Load_1002801 | Up Park Camp - 310 | 2026-08-04 08:12 | 2026-08-04 08:14 | 2026-08-04 11:01 | 2026-08-04 11:01 | 2026-08-04 11:04 | 2026-08-04 11:20 | 2026-08-04 11:13 | 2026-08-04 11:13 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.04627 | C001873659 | Odeanie Davis | KSAS | Completed | Load_248899 | Up Park Camp - 310 | 2026-08-04 08:12 | 2026-08-04 08:14 | 2026-08-04 11:29 | 2026-08-04 11:29 | 2026-08-04 11:30 | 2026-08-04 11:44 | 2026-08-04 11:31 | 2026-08-04 11:31 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.04658 | C001873665 | Locksley Allen | St.Mary | Completed | Load_242057 | Oracabessa - 210 | 2026-08-04 08:12 | 2026-08-04 08:40 | 2026-08-04 14:01 | 2026-08-04 14:02 | 2026-08-04 14:18 | 2026-08-04 14:23 | 2026-08-04 14:21 | 2026-08-04 14:21 |  |  | Fair | No | Gate lock,no one is at
Non-Outage | J.E.26.08.04681 | C001873658 | Odeanie Davis | KSAS | Completed | Load_258805 | Up Park Camp - 310 | 2026-08-04 08:12 | 2026-08-04 08:14 | 2026-08-04 10:38 | 2026-08-04 10:48 | 2026-08-04 10:54 | 2026-08-04 11:05 | 2026-08-04 10:55 | 2026-08-04 10:55 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.04688 | C001873660 | Odeanie Davis | KSAS | Completed | Load_259163 | Greenwich - 510 | 2026-08-04 08:12 | 2026-08-04 08:14 | 2026-08-04 11:14 | 2026-08-04 11:14 | 2026-08-04 11:24 | 2026-08-04 11:31 | 2026-08-04 11:28 | 2026-08-04 11:28 |  |  | Fair | No | Customer stated that the issue was resolved
Non-Outage | J.E.26.08.04691 | C001873664 | Odeanie Davis | KSAS | Completed | Load_243671 | Greenwich - 510 | 2026-08-04 08:12 | 2026-08-04 08:14 | 2026-08-04 10:38 | 2026-08-04 10:40 | 2026-08-04 10:41 | 2026-08-04 10:49 | 2026-08-04 10:46 | 2026-08-04 10:46 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.04800 | C001873663 | Locksley Allen | St.Mary | Completed | Load_240627 | Oracabessa - 110 | 2026-08-04 08:12 | 2026-08-04 08:40 | 2026-08-04 11:39 | 2026-08-04 11:55 | 2026-08-04 11:54 | 2026-08-04 12:36 | 2026-08-04 12:40 | 2026-08-04 12:40 |  |  | Fair | No | Pothead and pole found corroded. Clean up pothead and pole Voltage at meter socket phase to phase 234v. Phase to neutral 113&120Customer needs to change meter socket. Meter left working
Non-Outage | J.E.26.08.05029 | C001873661 | Locksley Allen | St.Mary | Completed | Load_256378 | Oracabessa - 210 | 2026-08-04 08:12 | 2026-08-04 08:40 | 2026-08-04 12:42 | 2026-08-04 13:41 | 2026-08-04 13:40 | 2026-08-04 13:57 | 2026-08-04 14:00 | 2026-08-04 14:00 |  |  | Fair | No | Meter found blank. Clean up connectors at pole and pothead Voltage at meter socket phase to phase 221v. Phase to neutral 110&111vMeter left working
Non-Outage | J.E.26.08.05361 | C001873662 | Locksley Allen | St.Mary | Completed | Load_238360 | Highgate - 210 | 2026-08-04 08:12 | 2026-08-04 08:40 | 2026-08-04 08:55 | 2026-08-04 09:35 | 2026-08-04 09:35 | 2026-08-04 10:04 | 2026-08-04 10:09 | 2026-08-04 10:09 |  |  | Fair | No | Pothead and pole found corroded,clean up connectors at pole and pothead Voltage at meter socket phase to phase 213v. Phase to neutral 113&101vMeter left working
Non-Outage | J.E.26.08.04318 | C001873667 | Locksley Allen | St.Mary | Completed | Load_269698 | Oracabessa - 110 | 2026-08-04 08:13 | 2026-08-04 08:45 | 2026-08-04 10:11 | 2026-08-04 11:04 | 2026-08-04 11:03 | 2026-08-04 11:32 | 2026-08-04 11:38 | 2026-08-04 11:38 |  |  | Fair | No | Service wire is defective,unable to change wire because of vehicle traffic,very busy. Bucket truck is needed to change wire at another time.10ft of service wire was use to connect to neighbor’s pothead.Voltage at meter socket phase to phase 232v. Phase to neutral 119&114vMeter left working. 4 clamps used to connect wire
Outage | J.E.26.08.06124 | C001873671 | Michael Christian | St.James | Completed | Load_245028 | Bogue - 610 | 2026-08-04 08:14 | 2026-08-04 09:00 | 2026-08-04 10:05 | 2026-08-04 10:18 | 2026-08-04 10:54 | 2026-08-04 12:05 | 2026-08-04 12:05 | 2026-08-04 12:05 |  |  | Fair | No | Found 1 10 kava transformer out cause by customer service wire voltage 110 112 222 at meter
Outage | J.E.26.08.06226 | C001873672 | Raymond Lewis | St.Ann | Completed | Load_413093 | Roaring River - 210 | 2026-08-04 08:15 | 2026-08-04 08:17 | 2026-08-04 15:02 | 2026-08-04 15:02 | 2026-08-04 15:02 | 2026-08-04 15:03 | 2026-08-04 15:03 | 2026-08-04 15:03 |  |  | Fair | No | Supply restored
Non-Outage | J.E.26.08.04875 | C001873681 | Odaine Johnson | Clarendon | Completed | Load_252995 | Parnassus - 210 | 2026-08-04 08:16 | 2026-08-04 08:18 | 2026-08-04 08:47 | 2026-08-04 14:49 | 2026-08-05 09:12 | 2026-08-05 09:13 | 2026-08-05 09:13 | 2026-08-05 09:13 |  |  | Fair | No | Premises okay, customer said problem was resolved
Non-Outage | J.E.26.08.05018 | C001873680 | Odaine Johnson | Clarendon | Completed | Load_249064 | May Pen - 110 | 2026-08-04 08:16 | 2026-08-04 08:18 | 2026-08-05 13:01 | 2026-08-05 13:04 | 2026-08-05 13:32 | 2026-08-05 13:33 | 2026-08-05 13:33 | 2026-08-05 13:33 |  |  | Flood | No | Contacted customer and customer stated that the issue was resolved already
Non-Outage | J.E.26.08.05255 | C001873679 | Odaine Johnson | Clarendon | Completed | Load_267881 | Monymusk - 410 | 2026-08-04 08:16 | 2026-08-04 08:18 | 2026-08-04 08:47 | 2026-08-04 11:45 | 2026-08-04 12:09 | 2026-08-04 12:17 | 2026-08-04 12:18 | 2026-08-04 12:18 |  |  | Fair | No | Corroded phase found at pole remade connection using 1 one bolt clamp voltage reading 112 volts
Non-Outage | J.E.26.08.05724 | C001873677 | Odaine Johnson | Clarendon | Completed | Load_241202 | May Pen - 110 | 2026-08-04 08:16 | 2026-08-04 08:18 | 2026-08-05 12:59 | 2026-08-05 12:59 | 2026-08-05 13:02 | 2026-08-05 13:02 | 2026-08-05 13:03 | 2026-08-05 13:03 |  |  | Fair | No | Try to contact customer but no answer and try to follow direction given but still did not find location
Non-Outage | J.E.26.08.05762 | C001873674 | Odaine Johnson | Clarendon | Completed | Load_250072 | May Pen - 210 | 2026-08-04 08:16 | 2026-08-04 08:18 | 2026-08-04 08:47 | 2026-08-04 13:36 | 2026-08-04 14:13 | 2026-08-04 14:36 | 2026-08-04 14:37 | 2026-08-04 14:37 |  |  | Fair | No | Corroded phase found at pole remade connection using 1 one bolt clamp voltage reading 110/111/221 volts
Non-Outage | J.E.26.08.05956 | C001873675 | Odaine Johnson | Clarendon | Completed | Load_267245 | Parnassus - 210 | 2026-08-04 08:16 | 2026-08-04 08:18 | 2026-08-04 08:47 | 2026-08-04 13:35 | 2026-08-04 13:34 | 2026-08-04 13:34 | 2026-08-04 13:35 | 2026-08-04 13:35 |  |  | Fair | No | Corroded neutral found at pole remade connection using 1 one bolt clamp voltage reading 116/114/230 volts
Non-Outage | J.E.26.08.06224 | C001873673 | Odaine Johnson | Clarendon | Completed | Load_257284 | Parnassus - 310 | 2026-08-04 08:16 | 2026-08-04 08:18 | 2026-08-04 08:47 | 2026-08-04 11:00 | 2026-08-04 10:59 | 2026-08-04 10:59 | 2026-08-04 11:00 | 2026-08-04 11:00 |  |  | Fair | No | Burn off phase found at pole remade connection using 1 one bolt clamp voltage reading 110/109/220 volts
Non-Outage | J.E.26.08.06224 | C001873676 | Odaine Johnson | Clarendon | Completed | Load_257284 | Parnassus - 310 | 2026-08-04 08:16 | 2026-08-04 08:18 | 2026-08-04 08:46 | 2026-08-04 10:55 | 2026-08-04 10:58 | 2026-08-04 10:58 | 2026-08-04 10:59 | 2026-08-04 10:59 |  |  | Fair | No | Burn off phase found at pole remade connection using 1 one bolt clamp voltage reading 110/119/220 volts
Non-Outage | J.E.26.07.37201 | C001873686 | Oshane Warren |  | Completed |  |  | 2026-08-04 08:17 | 2026-08-04 08:18 | 2026-08-04 12:09 | 2026-08-04 12:09 | 2026-08-04 12:09 | 2026-08-04 12:18 | 2026-08-04 12:19 | 2026-08-04 12:19 | BrokenPole |  | Fair | No | Check and find ok
Non-Outage | J.E.26.08.04323 | C001873682 | Odaine Johnson | Clarendon | Completed | Load_238006 | Parnassus - 210 | 2026-08-04 08:17 | 2026-08-04 08:18 | 2026-08-05 13:33 | 2026-08-05 13:34 | 2026-08-05 13:49 | 2026-08-05 13:50 | 2026-08-05 13:52 | 2026-08-05 13:52 |  |  | Fair | No | Customer wire customer off on a pole that on a hill about 30ft in the air a bucket truck is needed
Non-Outage | J.E.26.08.04459 | C001873683 | Odaine Johnson | Clarendon | Completed | Load_247306 | Monymusk - 410 | 2026-08-04 08:17 | 2026-08-04 08:18 | 2026-08-04 08:46 | 2026-08-04 11:04 | 2026-08-04 11:43 | 2026-08-04 11:43 | 2026-08-04 11:44 | 2026-08-04 11:44 |  |  | Fair | No | Transformer fuse blown, emergency team needed
Non-Outage | J.E.26.08.04775 | C001873688 | Milton Charlton |  | Completed |  |  | 2026-08-04 08:18 | 2026-08-04 08:21 | 2026-08-04 10:03 | 2026-08-04 10:55 | 2026-08-04 10:55 | 2026-08-04 10:40 | 2026-08-04 10:56 | 2026-08-04 10:56 | LeakingTransformer |  | Fair | No | Found okay upon arrival. Matter was resolved. Customer states that J.P.S crew resolved the problem yesterday.
Non-Outage | J.E.26.08.04821 | C001873687 | Milton Charlton | KSAN | Completed | Load_250346 | West Kings House - 410 | 2026-08-04 08:18 | 2026-08-04 08:21 | 2026-08-04 11:25 | 2026-08-04 11:25 | 2026-08-04 12:43 | 2026-08-04 12:20 | 2026-08-04 12:46 | 2026-08-04 12:46 | LeakingTransformer |  | Fair | No | Found okay upon arrival. No oil was seen leaking from transformers at this location.
Outage | J.E.26.08.06012 | C001873690 | Romeo Brissett | Hanover | Completed | Load_243389 | Orange Bay - 310 | 2026-08-04 08:20 | 2026-08-04 08:22 | 2026-08-04 09:39 | 2026-08-04 09:39 | 2026-08-04 10:00 | 2026-08-04 11:14 | 2026-08-04 11:16 | 2026-08-04 11:16 |  |  | Fair | No | Removed tree limbs, retention secondary and replaced (1)25KVA transformer fuse.
Outage | J.E.26.08.06221 | C001873689 | Derrick Grubb | St.Thomas | Completed | Load_259414 | Good Year - 210 | 2026-08-04 08:20 | 2026-08-04 08:21 | 2026-08-04 08:34 | 2026-08-04 08:35 | 2026-08-04 09:01 | 2026-08-04 12:10 | 2026-08-04 12:10 | 2026-08-04 12:10 |  |  | Fair | No | Troubleshoot and found circuit overload. Circuit needs upgrade. Reading at the end of the circuit 105v, 113v, 217v.
Outage | J.E.26.08.01868 | C001873692 | Richard Nicholas | St.Catherine | Completed | Load_256392 | Tredegar - 410 | 2026-08-04 08:21 | 2026-08-04 08:22 | 2026-08-04 16:07 | 2026-08-04 16:08 | 2026-08-04 16:43 | 2026-08-04 16:43 | 2026-08-04 16:44 | 2026-08-04 16:44 |  |  | Fair | No | Not located
Outage | J.E.26.08.03079 | C001873691 | Richard Nicholas | St.Catherine | Completed | Load_246786 | Tredegar - 410 | 2026-08-04 08:21 | 2026-08-04 08:22 | 2026-08-04 08:50 | 2026-08-04 08:50 | 2026-08-04 11:30 | 2026-08-04 11:47 | 2026-08-04 11:48 | 2026-08-04 11:48 |  |  | Fair | No | Supply found ok in the area however premises found locked.
Outage | J.E.26.08.03850 | C001873693 | Nickolas Rodriques | St.Catherine | Completed | Load_259256 | Tredegar - 410 | 2026-08-04 08:21 | 2026-08-04 16:59 | 2026-08-05 08:22 | 2026-08-05 08:22 | 2026-08-05 09:21 | 2026-08-05 09:37 | 2026-08-05 09:40 | 2026-08-05 09:40 |  |  | Flood | No | The customer was located and confirmed that the power outage was resolved.
Outage | J.E.26.08.04153 | C001873694 | Richard Nicholas | St.Catherine | Completed | Load_244526 | Tredegar - 210 | 2026-08-04 08:21 | 2026-08-04 08:22 | 2026-08-04 16:48 | 2026-08-04 16:49 | 2026-08-04 17:22 | 2026-08-04 17:39 | 2026-08-04 17:39 | 2026-08-04 17:39 |  |  | Fair | No | Found ok
Outage | J.E.26.08.04468 | C001873695 | Richard Nicholas | St.Catherine | Completed | Load_1000959 | Tredegar - 410 | 2026-08-04 08:21 | 2026-08-04 11:39 | 2026-08-04 11:53 | 2026-08-04 11:54 | 2026-08-04 12:15 | 2026-08-04 12:57 | 2026-08-04 12:58 | 2026-08-04 12:58 |  |  | Fair | No | Premises and the area checked,same found ok.
Non-Outage | J.E.26.08.04173 | C001873696 | Romeo Brissett |  | Completed |  |  | 2026-08-04 08:22 | 2026-08-04 08:23 | 2026-08-04 09:09 | 2026-08-04 09:10 | 2026-08-04 09:38 | 2026-08-04 09:28 | 2026-08-04 09:39 | 2026-08-04 09:39 |  |  | Fair | No | Check and found ok, customer stated issue was resolved.
Non-Outage | J.E.26.08.04591 | C001873706 | Oraine Minto | St.Ann | Completed | Load_240861 | Roaring River - 210 | 2026-08-04 08:27 | 2026-08-04 08:28 | 2026-08-05 12:40 | 2026-08-05 12:41 | 2026-08-05 12:40 | 2026-08-05 12:42 | 2026-08-05 12:42 | 2026-08-05 12:42 |  |  | Fair | No | Customer states that entire area was experiencing it how issue is resolved now
Non-Outage | J.E.26.08.04998 | C001873699 | Oraine Minto | St.Ann | Completed | Load_242953 | Roaring River - 410 | 2026-08-04 08:27 | 2026-08-04 08:28 | 2026-08-04 13:07 | 2026-08-04 13:08 | 2026-08-04 13:07 | 2026-08-04 13:07 | 2026-08-04 13:09 | 2026-08-04 13:09 |  |  | Fair | No | Refer to emergency All customers in the are is affected by this low voltage stated by the customer
Non-Outage | J.E.26.08.05940 | C001873700 | Oraine Minto | St.Ann | Completed | Load_267559 | Roaring River - 410 | 2026-08-04 08:27 | 2026-08-04 08:28 | 2026-08-04 13:03 | 2026-08-04 13:04 | 2026-08-04 13:04 | 2026-08-04 13:04 | 2026-08-04 13:05 | 2026-08-04 13:05 |  |  | Fair | No | Customer states that it came last night and it ok now
Outage | J.E.26.08.06097 | C001873705 | Michael Christian | St.James | Completed | Load_237651 | Bogue - 510 | 2026-08-04 08:27 | 2026-08-04 08:59 | 2026-08-04 09:08 | 2026-08-04 09:09 | 2026-08-04 09:15 | 2026-08-04 09:17 | 2026-08-04 09:17 | 2026-08-04 09:17 |  |  | Fair | No | Check and found
Non-Outage | J.E.26.08.04596 | C001873709 | Dwain Samuels | Westmoreland | Completed | Load_242624 | Paradise - 110 | 2026-08-04 08:29 | 2026-08-04 08:35 | 2026-08-04 08:43 | 2026-08-04 12:12 | 2026-08-04 12:19 | 2026-08-04 12:41 | 2026-08-04 12:43 | 2026-08-04 12:43 |  |  | Fair | No | The whole area is been affected by low voltage . Check multiple customers voltages
Non-Outage | J.E.26.08.05969 | C001873710 | Oshane Warren | Westmoreland | Completed | Load_247446 | Paradise - 110 | 2026-08-04 08:29 | 2026-08-04 16:42 | 2026-08-04 16:59 | 2026-08-04 16:59 | 2026-08-04 21:45 | 2026-08-04 22:56 | 2026-08-04 22:57 | 2026-08-04 22:57 |  |  | Rains | No | Open 25kva xformer and top up xformer voltage 108 109 217
Non-Outage | J.E.26.08.06077 | C001873712 | Dwain Samuels | Westmoreland | Completed | Load_241991 | Paradise - 110 | 2026-08-04 08:29 | 2026-08-04 08:35 | 2026-08-04 08:43 | 2026-08-04 11:16 | 2026-08-04 11:36 | 2026-08-04 11:59 | 2026-08-04 12:00 | 2026-08-04 12:00 |  |  | Fair | No | Found working okay. Voltage check 118-118-236
Outage | J.E.26.08.05574 | C001873711 | Swon Miller | St.James | Completed | Load_266902 | Rose Hall - 210 | 2026-08-04 08:29 | 2026-08-04 08:30 | 2026-08-04 10:53 | 2026-08-04 10:53 | 2026-08-04 10:58 | 2026-08-26 11:03 | 2026-08-04 11:04 | 2026-08-04 11:04 |  |  | Fair | No | Call related to previous
Non-Outage | J.E.26.02.22265 | C001873714 | Dwain Samuels | Westmoreland | Completed | Load_263330 | Orange Bay - 210 | 2026-08-04 08:30 | 2026-08-04 08:35 | 2026-08-04 08:43 | 2026-08-04 11:03 | 2026-08-04 11:02 | 2026-08-04 11:04 | 2026-08-04 11:05 | 2026-08-04 11:05 |  |  | Fair | No | Found working okay. Voltage check 115-114-229
Non-Outage | J.E.26.02.22745 | C001873715 | Dwain Samuels | Westmoreland | Completed | Load_268696 | Orange Bay - 210 | 2026-08-04 08:30 | 2026-08-04 08:35 | 2026-08-04 08:43 | 2026-08-04 11:09 | 2026-08-04 11:08 | 2026-08-04 11:13 | 2026-08-04 11:14 | 2026-08-04 11:14 |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.02.22784 | C001873717 | Dwain Samuels | Westmoreland | Completed | Load_292869 | Paradise - 210 | 2026-08-04 08:30 | 2026-08-04 08:35 | 2026-08-04 08:43 | 2026-08-04 10:29 | 2026-08-04 10:28 | 2026-08-04 10:31 | 2026-08-04 10:31 | 2026-08-04 10:31 |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.02.27225 | C001873718 | Dwain Samuels | Westmoreland | Completed | Load_254355 | Paradise - 210 | 2026-08-04 08:30 | 2026-08-04 08:35 | 2026-08-04 08:43 | 2026-08-04 10:41 | 2026-08-04 10:40 | 2026-08-04 10:42 | 2026-08-04 10:43 | 2026-08-04 10:43 |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.02.35305 | C001873716 | Dwain Samuels | Westmoreland | Completed | Load_257539 | Paradise - 210 | 2026-08-04 08:30 | 2026-08-04 08:35 | 2026-08-04 08:43 | 2026-08-04 10:52 | 2026-08-04 10:51 | 2026-08-04 10:56 | 2026-08-04 10:57 | 2026-08-04 10:57 |  |  | Fair | No | Customer said supply was restored. Customer problem is not getting an light bill
Non-Outage | J.E.26.02.36551 | C001873720 | Dwain Samuels | Westmoreland | Completed | Load_292088 | Paradise - 210 | 2026-08-04 08:30 | 2026-08-04 08:35 | 2026-08-04 08:43 | 2026-08-05 10:40 | 2026-08-05 10:40 | 2026-08-05 10:40 | 2026-08-05 10:41 | 2026-08-05 10:41 |  |  | Fair | No | Called and customer said that the supply was restored
Outage | J.E.26.08.04118 | C001873719 | Barrington Brown | St.James | Completed | Load_247579 | Bogue - 310 | 2026-08-04 08:30 | 2026-08-04 08:31 | 2026-08-04 09:22 | 2026-08-04 09:22 | 2026-08-04 10:23 | 2026-08-04 10:34 | 2026-08-04 10:34 | 2026-08-04 10:34 |  |  | Fair | No | Checked and found ok
Outage | J.E.26.08.05338 | C001873713 | Swon Miller | St.James | Completed | Load_249364 | Rose Hall - 210 | 2026-08-04 08:30 | 2026-08-04 08:30 | 2026-08-04 11:07 | 2026-08-04 11:07 | 2026-08-04 11:11 | 2026-08-26 11:12 | 2026-08-04 11:13 | 2026-08-04 11:13 |  |  | Fair | No | This call belongs to trelawny
Non-Outage | J.E.26.02.42742 | C001873722 | Dwain Samuels | Westmoreland | Completed | Load_267763 | Paradise - 210 | 2026-08-04 08:31 | 2026-08-04 08:35 | 2026-08-04 08:43 | 2026-08-04 09:56 | 2026-08-04 09:58 | 2026-08-04 10:02 | 2026-08-04 10:02 | 2026-08-04 10:02 |  |  | Fair | No | Found working okay. Voltage check 117-116-233
Outage | J.E.26.08.05781 | C001873721 | Barrington Brown | St.James | Completed | Load_266659 | Bogue - 310 | 2026-08-04 08:31 | 2026-08-04 08:31 | 2026-08-04 10:35 | 2026-08-04 10:36 | 2026-08-04 11:25 | 2026-08-04 11:46 | 2026-08-04 11:46 | 2026-08-04 11:46 |  |  | Fair | No | Checked and found ok
Outage | J.E.26.08.06230 | C001873723 | Edward Royal | KSAS | Completed | Load_246603 | Rockfort - 210 | 2026-08-04 08:31 | 2026-08-04 08:33 | 2026-08-04 13:36 | 2026-08-04 13:36 | 2026-08-04 13:36 | 2026-08-04 13:44 | 2026-08-04 13:45 | 2026-08-04 13:45 |  |  | Fair | No | Replaced 10A junction fuse pole #0055510
Non-Outage | J.E.26.08.05652 | C001873729 | Barrington Brown | St.James | Completed | Load_269969 | Bogue - 310 | 2026-08-04 08:33 | 2026-08-04 08:35 | 2026-08-04 14:46 | 2026-08-04 14:46 | 2026-08-04 15:29 | 2026-08-04 15:30 | 2026-08-04 15:30 | 2026-08-04 15:30 |  |  | Fair | No | Crew removed illegal connections then retention open secondary
Non-Outage | J.E.26.08.06145 | C001873728 | Shamour Haughton | St.James | Completed | Load_245423 | Bogue - 310 | 2026-08-04 08:33 | 2026-08-04 15:34 | 2026-08-04 18:05 | 2026-08-04 18:06 | 2026-08-04 18:50 | 2026-08-04 18:57 | 2026-08-04 19:07 | 2026-08-04 19:07 |  |  | Fair | No | Found customer experiencing single phasing, EG BOX 01102
Non-Outage | J.E.26.08.04743 | C001873730 | Barrington Brown | St.James | Completed | Load_260912 | Bogue - 310 | 2026-08-04 08:34 | 2026-08-04 08:35 | 2026-08-04 11:46 | 2026-08-04 11:47 | 2026-08-04 13:03 | 2026-08-04 14:46 | 2026-08-04 14:46 | 2026-08-04 14:46 |  |  | Fair | No | Crew found customer with 118v/118v/236v off load while 101v/97v/198v on load. #6 triplex traveled a great distance from the transformer pole to customer meter point. Crew tapped up transformer and customer voltage improved. Crew also did spot bushing and replace two clamps at transformer pole. However to avoid customer experience issues again refer to maintenance department to replace transformer that was fallen in the hurricane to give customer best supply.
Non-Outage | J.E.26.08.03980 | C001873732 | Junior Scarlett | St.James | Completed | Load_264886 | Bogue - 310 | 2026-08-04 08:35 | 2026-08-04 08:37 | 2026-08-04 08:41 | 2026-08-04 09:02 | 2026-08-04 10:18 | 2026-08-04 11:03 | 2026-08-04 11:03 | 2026-08-04 11:03 |  |  | Fair | No | Broken neutral Reattach wireInstall two clampVoltage found 101v 113v 224vVoltage leave 113v 113v 226vJob completed
Non-Outage | J.E.26.08.05246 | C001873733 | Junior Scarlett | St.James | Completed | Load_260391 | Bogue - 310 | 2026-08-04 08:35 | 2026-08-04 08:37 | 2026-08-04 08:41 | 2026-08-04 11:06 | 2026-08-04 11:33 | 2026-08-04 12:23 | 2026-08-04 12:07 | 2026-08-04 12:07 |  |  | Fair | No | Phase burn offReattach wire Install one clampVoltage found 113v 11v 113v Voltage leave 113v 113v 227vJob completed
Non-Outage | J.E.26.08.05266 | C001873734 | Junior Scarlett | St.James | Completed | Load_237885 | Queens Drive - 710 | 2026-08-04 08:35 | 2026-08-04 08:37 | 2026-08-04 08:41 | 2026-08-04 12:08 | 2026-08-04 12:22 | 2026-08-04 12:33 | 2026-08-04 12:34 | 2026-08-04 12:34 |  |  | Fair | No | Unable to locate Voltage from transformer 115v 116v 230v
Non-Outage | J.E.26.08.06044 | C001873736 | Junior Scarlett | St.James | Completed | Load_264461 | Bogue - 310 | 2026-08-04 08:35 | 2026-08-04 08:37 | 2026-08-04 08:41 | 2026-08-04 13:46 | 2026-08-04 14:55 | 2026-08-04 15:44 | 2026-08-04 15:45 | 2026-08-04 15:45 |  |  | Fair | No | Check and found okVoltage found 112v 111v 221v
Non-Outage | J.E.26.08.05676 | C001873738 | Swon Miller | St.James | Completed | Load_266902 | Rose Hall - 210 | 2026-08-04 08:37 | 2026-08-04 08:38 | 2026-08-04 08:53 | 2026-08-04 08:53 | 2026-08-04 10:16 | 2026-08-19 10:52 | 2026-08-04 10:53 | 2026-08-04 10:53 |  |  | Fair | No | Found 50 kva transformer drop lead burnt off cause by slack connection open 50 kva transformer to carry out repairs clean and remake joints use 2 pg voltage found 115 close up 50 kva transformer voltage left 115/116/232 also the secondary line is hanging low over by customer premises customer requested for the line to be removed from over the premises a 35 ft class 6 intermediate pole is needed in the middle because the span is too long please refer to maintenance/kerron Frazier
Outage | J.E.26.08.05290 | C001873739 | Richard Watson | St.Elizabeth | Completed | Load_239283 | Maggotty - 110 | 2026-08-04 08:38 | 2026-08-04 08:40 | 2026-08-04 13:46 | 2026-08-04 13:53 | 2026-08-04 13:59 | 2026-08-04 14:04 | 2026-08-04 14:04 | 2026-08-04 14:04 |  |  | Fair | No | Customer contacted and stated that two customers connected to hexing box is out of supply, please refer to Field service department for investigation.
Outage | J.E.26.08.05070 | C001873740 | Richard Watson | St.Elizabeth | Completed | Load_265735 | Maggotty - 110 | 2026-08-04 08:39 | 2026-08-04 08:40 | 2026-08-04 08:49 | 2026-08-04 09:34 | 2026-08-04 10:37 | 2026-08-04 11:35 | 2026-08-04 11:40 | 2026-08-04 11:40 |  |  | Fair | No | Replace approximately 200ft of #6triplex service wire, also use three 1bolt clamps and three #6-#6 service sleeves, voltage left inside meter socket 110v, 110v, 220v, customer was without supply since hurricane Melissa.
Non-Outage | J.E.26.07.39589 | C001873741 | Daniel Lobar | Trelawny | Completed | Load_292446 | Martha Brae - 210 | 2026-08-04 08:40 | 2026-08-04 08:41 | 2026-08-04 11:31 | 2026-08-04 11:31 | 2026-08-04 11:35 | 2026-08-04 12:20 | 2026-08-04 12:23 | 2026-08-04 12:23 |  |  | Fair | No | Splice and retention #6 service wire
Non-Outage | J.E.26.08.01871 | C001873747 | Fredrick Hamilton | KSAN | Completed | Load_261910 | Washington Blvd - 410 | 2026-08-04 08:40 | 2026-08-04 08:41 | 2026-08-04 08:51 | 2026-08-04 12:56 | 2026-08-04 12:57 | 2026-08-04 12:58 | 2026-08-04 12:58 | 2026-08-04 12:58 |  |  | Fair | No | Customer contacted and stated that power was restored fully to premises Premises is ok
Non-Outage | J.E.26.08.04431 | C001873745 | Fredrick Hamilton | KSAN | Completed | Load_252360 | Constant Spring - 210 | 2026-08-04 08:40 | 2026-08-04 08:41 | 2026-08-04 08:51 | 2026-08-04 13:17 | 2026-08-04 13:22 | 2026-08-04 13:29 | 2026-08-04 13:29 | 2026-08-04 13:29 |  |  | Fair | No | 248v/123v/123v obtained High voltage detected please have emergency inspect transformer Multiple customers are affected
Non-Outage | J.E.26.08.05239 | C001873744 | Fredrick Hamilton | KSAN | Completed | Load_575134 | Constant Spring - 210 | 2026-08-04 08:40 | 2026-08-04 08:41 | 2026-08-04 08:51 | 2026-08-04 14:08 | 2026-08-04 14:10 | 2026-08-04 14:14 | 2026-08-04 14:14 | 2026-08-04 14:14 |  |  | Fair | No | Premises locked customer to reschedule another report to facilitate inspection Customer was contacted
Non-Outage | J.E.26.08.05250 | C001873749 | Fredrick Hamilton | KSAN | Completed | Load_239951 | Washington Blvd - 410 | 2026-08-04 08:40 | 2026-08-04 08:42 | 2026-08-04 08:51 | 2026-08-04 15:06 | 2026-08-04 15:19 | 2026-08-04 15:32 | 2026-08-04 15:32 | 2026-08-04 15:32 |  |  | Fair | No | Please assign to emergency fuse link need to be open to carry out repairs Multiple shops experiencing low voltage
Non-Outage | J.E.26.08.05300 | C001873743 | Fredrick Hamilton | KSAN | Completed | Load_262718 | Constant Spring - 210 | 2026-08-04 08:40 | 2026-08-04 08:41 | 2026-08-04 08:51 | 2026-08-04 13:56 | 2026-08-04 14:01 | 2026-08-04 14:03 | 2026-08-04 14:03 | 2026-08-04 14:03 |  |  | Fair | No | Please have crew inspect hexing box customer pothead in good condition Internal inspection was done by customer electrician 238v/117v118v obtained
Non-Outage | J.E.26.08.05614 | C001873748 | Fredrick Hamilton | KSAN | Completed | Load_240425 | Washington Blvd - 810 | 2026-08-04 08:40 | 2026-08-04 08:42 | 2026-08-04 08:51 | 2026-08-04 12:45 | 2026-08-04 12:50 | 2026-08-04 12:54 | 2026-08-04 12:54 | 2026-08-04 12:54 |  |  | Fair | No | Customer visited however customer stated that power was restored fully yesterday
Non-Outage | J.E.26.08.05643 | C001873746 | Fredrick Hamilton | KSAN | Completed | Load_253684 | Constant Spring - 210 | 2026-08-04 08:40 | 2026-08-04 08:41 | 2026-08-04 08:51 | 2026-08-04 13:32 | 2026-08-04 13:46 | 2026-08-04 13:50 | 2026-08-04 13:50 | 2026-08-04 13:50 |  |  | Fair | No | Emergency crew required secondary phase line down at location Pole#197258Please assign to relevant crewSecondary line still live
Non-Outage | J.E.26.08.05694 | C001873742 | Daniel Lobar | Trelawny | Completed | Load_247797 | Martha Brae - 210 | 2026-08-04 08:40 | 2026-08-04 08:41 | 2026-08-04 10:43 | 2026-08-04 10:44 | 2026-08-04 11:12 | 2026-08-04 11:16 | 2026-08-04 11:28 | 2026-08-04 11:28 | LowHangingWires |  | Fair | No | An overhead guy is recommended for the secondary dead-end the low hanging conductor is 4/0 triplex service wire which is pulling away the pole, there as a result of this the wire is hanging low in the mid span
Non-Outage | J.E.26.07.39464 | C001873754 | Fredrick Hamilton | KSAS | Completed | Load_267072 | Duhaney - 310 | 2026-08-04 08:41 | 2026-08-04 08:43 | 2026-08-04 08:51 | 2026-08-04 11:08 | 2026-08-04 11:22 | 2026-08-04 11:40 | 2026-08-04 11:40 | 2026-08-04 11:40 |  |  | Fair | No | 217v/105.9v/110.6v low voltage affecting multiple customers please have emergency inspect transformer
Non-Outage | J.E.26.08.01050 | C001873753 | Fredrick Hamilton | KSAS | Completed | Load_247896 | Duhaney - 310 | 2026-08-04 08:41 | 2026-08-04 08:43 | 2026-08-04 08:51 | 2026-08-04 11:41 | 2026-08-04 11:44 | 2026-08-04 11:45 | 2026-08-04 11:45 | 2026-08-04 11:45 |  |  | Fair | No | Customer contacted and stated that power was restored fully Premises is ok
Non-Outage | J.E.26.08.04937 | C001873751 | Fredrick Hamilton | KSAS | Completed | Load_262259 | Duhaney - 310 | 2026-08-04 08:41 | 2026-08-04 08:42 | 2026-08-04 08:51 | 2026-08-04 12:24 | 2026-08-04 12:23 | 2026-08-04 12:26 | 2026-08-04 12:26 | 2026-08-04 12:26 |  |  | Fair | No | Premises inaccessible customer contacted and advised to make another report to facilitate inspection
Non-Outage | J.E.26.08.06040 | C001873752 | Fredrick Hamilton | KSAS | Completed | Load_262024 | Duhaney - 310 | 2026-08-04 08:41 | 2026-08-04 08:42 | 2026-08-04 08:51 | 2026-08-04 11:47 | 2026-08-04 11:55 | 2026-08-04 12:19 | 2026-08-04 12:19 | 2026-08-04 12:19 |  |  | Fair | No | 234.1v/116v/117v obtained 3 penunion used at pothead Corrosion detected at pothead
Outage | J.E.26.08.06244 | C001873750 | Oshane Warren | Westmoreland | Completed | Load_242110 | Paradise - 110 | 2026-08-04 08:41 | 2026-08-04 08:41 | 2026-08-04 13:26 | 2026-08-04 13:26 | 2026-08-04 13:26 | 2026-08-04 13:26 | 2026-08-04 13:27 | 2026-08-04 13:27 |  |  | Fair | No | Check and find ok
Outage | J.E.26.08.06250 | C001873759 | Dwayne Cohen | KSAN | Completed | Load_247199 | Constant Spring - 210 | 2026-08-04 08:42 | 2026-08-04 08:44 | 2026-08-04 10:53 | 2026-08-04 10:54 | 2026-08-04 10:54 | 2026-08-04 10:55 | 2026-08-04 10:56 | 2026-08-04 10:56 |  |  | Fair | No | Premises found okay
Non-Outage | J.E.26.07.39762 | C001873762 | Floyd Taylor | Trelawny | Completed | Load_1001717 | Greenwood - 210 | 2026-08-04 08:43 | 2026-08-04 08:44 | 2026-08-04 09:58 | 2026-08-04 09:59 | 2026-08-04 10:20 | 2026-08-04 11:04 | 2026-08-04 11:05 | 2026-08-04 11:05 |  |  | Fair | No | Internal issues customer meter planel burn up.
Non-Outage | J.E.26.08.05811 | C001873761 | Floyd Taylor | Trelawny | Completed | Load_292370 | Greenwood - 210 | 2026-08-04 08:43 | 2026-08-04 08:44 | 2026-08-04 09:53 | 2026-08-04 11:06 | 2026-08-04 11:43 | 2026-08-04 12:18 | 2026-08-04 12:18 | 2026-08-04 12:18 |  |  | Fair | No | Customer was advised to get a licensed electrician to fix the issue.
Outage | J.E.26.08.06238 | C001873760 | Elvis Trowers | KSAN | Completed | Load_293895 | Washington Blvd - 710 | 2026-08-04 08:43 | 2026-08-04 08:44 | 2026-08-04 11:24 | 2026-08-04 11:25 | 2026-08-04 11:51 | 2026-08-04 12:22 | 2026-08-04 12:22 | 2026-08-04 12:22 |  |  | Fair | Yes | This location needs to be visit by field service department, I was told by escalation service department, meter not communicating.
Outage | J.E.26.08.06243 | C001873763 | Tyrese Williams | St.Ann | Completed | Load_258820 | Cardiff Hall - 210 | 2026-08-04 08:45 | 2026-08-04 08:52 | 2026-08-04 10:00 | 2026-08-04 10:09 | 2026-08-04 10:39 | 2026-08-04 10:41 | 2026-08-04 10:42 | 2026-08-04 10:42 |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.05.19541 | C001873768 | Nicholas Dillon | St.Elizabeth | Completed | Load_251686 | Paradise - 310 | 2026-08-04 08:47 | 2026-08-04 08:49 | 2026-08-04 10:32 | 2026-08-04 11:51 | 2026-08-04 11:50 | 2026-08-04 11:53 | 2026-08-04 11:56 | 2026-08-04 11:56 |  |  | Fair | No | Check voltage before at pole 118 118 phase to phase 237. High leg 208. Premises found working ok
Non-Outage | J.E.26.05.31915 | C001873769 | Nicholas Dillon | St.Elizabeth | Completed | Load_260786 | Maggotty - 110 | 2026-08-04 08:47 | 2026-08-04 08:49 | 2026-08-04 10:32 | 2026-08-05 07:39 | 2026-08-05 07:39 | 2026-08-05 07:39 | 2026-08-05 07:43 | 2026-08-05 07:43 | LeaningPole |  | Fair | No | Check voltage before at meter 116 113 phase to phase 230 . Premises found working ok
Non-Outage | J.E.26.05.33666 | C001873770 | Nicholas Dillon | St.Elizabeth | Completed | Load_265034 | Maggotty - 110 | 2026-08-04 08:47 | 2026-08-04 08:49 | 2026-08-04 10:32 | 2026-08-04 11:40 | 2026-08-04 11:48 | 2026-08-04 11:48 | 2026-08-04 11:50 | 2026-08-04 11:50 |  |  | Fair | Yes | Check and found corrosion at pole clean corrosion use 3 one bolt clamp before I left voltage is 119 117 phase to phase 236
Non-Outage | J.E.26.06.30805 | C001873771 | Nicholas Dillon | St.Elizabeth | Completed | Load_249683 | Maggotty - 110 | 2026-08-04 08:47 | 2026-08-04 08:49 | 2026-08-04 10:32 | 2026-08-04 12:00 | 2026-08-04 12:00 | 2026-08-04 12:00 | 2026-08-04 12:01 | 2026-08-04 12:01 |  |  | Fair | No | Wrong assessment
Non-Outage | J.E.26.06.36531 | C001873772 | Nicholas Dillon | St.Elizabeth | Completed | Load_266765 | Maggotty - 110 | 2026-08-04 08:48 | 2026-08-04 08:49 | 2026-08-04 10:32 | 2026-08-05 18:11 | 2026-08-05 18:11 | 2026-08-05 18:11 | 2026-08-05 18:12 | 2026-08-05 18:12 |  |  | Fair | Yes | Check and found corrosion at pole clean corrosion use 1 one bolt clamp before I left voltage is 116 114 phase to phase 230
Non-Outage | J.E.26.07.00304 | C001873773 | Nicholas Dillon | St.Elizabeth | Completed | Load_240752 | Maggotty - 110 | 2026-08-04 08:48 | 2026-08-04 08:49 | 2026-08-04 10:32 | 2026-08-04 11:28 | 2026-08-04 11:33 | 2026-08-04 11:33 | 2026-08-04 11:34 | 2026-08-04 11:34 |  |  | Fair | No | Check voltage before at meter 115 117 phase to phase 233. Premises found working ok
Non-Outage | J.E.26.07.01843 | C001873774 | Nicholas Dillon | St.Elizabeth | Completed | Load_1002136 | Maggotty - 110 | 2026-08-04 08:48 | 2026-08-04 08:49 | 2026-08-04 10:32 | 2026-08-04 19:51 | 2026-08-04 19:50 | 2026-08-04 19:50 | 2026-08-04 19:52 | 2026-08-04 19:52 |  |  | Fair | No | Check voltage before at meter 115 115 phase to phase 230
Non-Outage | J.E.26.07.04723 | C001873777 | Nicholas Dillon | St.Elizabeth | Completed | Load_243624 | Maggotty - 110 | 2026-08-04 08:48 | 2026-08-04 08:49 | 2026-08-04 10:32 | 2026-08-04 10:45 | 2026-08-04 11:04 | 2026-08-04 11:04 | 2026-08-04 11:10 | 2026-08-04 11:10 |  |  | Fair | Yes | Check and found corrosion at pole clean joint and use 1 one bolt clamp before I left voltage 114 112 phase to phase 227
Non-Outage | J.E.26.07.27265 | C001873779 | Roemello Brown | Trelawny | Completed | Load_1001715 | Greenwood - 210 | 2026-08-04 08:48 | 2026-08-04 08:50 | 2026-08-04 13:16 | 2026-08-04 13:18 | 2026-08-04 13:40 | 2026-08-04 13:40 | 2026-08-04 14:19 | 2026-08-04 14:19 |  |  | Fair | No | Neutral broke off at the pole side have it reclamp Voltage found 118/118/237Voltage leave 118/118/237
Non-Outage | J.E.26.07.32699 | C001873778 | Roemello Brown | Trelawny | Completed | Load_292409 | Greenwood - 210 | 2026-08-04 08:48 | 2026-08-04 08:50 | 2026-08-04 10:34 | 2026-08-04 10:35 | 2026-08-04 10:56 | 2026-08-04 12:46 | 2026-08-04 12:57 | 2026-08-04 12:57 |  |  | Fair | No | One leg on the secondary line giving me a low reading please send emergency team to assist please Voltage found 116/103/219Voltage leave 116/103/219
Non-Outage | J.E.26.07.38965 | C001873776 | Roemello Brown | Trelawny | Completed | Load_257344 | Greenwood - 210 | 2026-08-04 08:48 | 2026-08-04 08:50 | 2026-08-04 14:59 | 2026-08-04 15:00 | 2026-08-04 15:20 | 2026-08-04 15:27 | 2026-08-04 15:29 | 2026-08-04 15:29 |  |  | Fair | No | Customer meter socket defective inform the customer to get an private electrician to have the meter socket replaced Voltage found 117/117/235Voltage leave 117/117/235
Non-Outage | J.E.26.07.39254 | C001873775 | Roemello Brown | Trelawny | Completed | Load_292751 | Greenwood - 210 | 2026-08-04 08:48 | 2026-08-04 08:50 | 2026-08-04 10:34 | 2026-08-04 12:58 | 2026-08-04 13:16 | 2026-08-04 13:16 | 2026-08-04 13:17 | 2026-08-04 13:17 |  |  | Fair | No | Corrosion at the pole an at the pothead have clamps change Voltage found 122/107/229Voltage leave 114/114/229
Non-Outage | J.E.26.08.05916 | C001873781 | Roemello Brown | Trelawny | Completed | Load_256777 | Greenwood - 110 | 2026-08-04 08:49 | 2026-08-04 08:50 | 2026-08-04 09:20 | 2026-08-04 09:30 | 2026-08-04 09:39 | 2026-08-04 09:39 | 2026-08-04 10:16 | 2026-08-04 10:16 |  |  | Fair | No | Service wire broke off at the pole side have it reclamp Voltage found 118/29/89Voltage leave 122/119/241
Non-Outage | J.E.26.04.04957 | C001873789 | Wayne Dillion | St.Elizabeth | Completed | Load_242357 | Maggotty - 210 | 2026-08-04 08:53 | 2026-08-04 08:55 | 2026-08-04 09:55 | 2026-08-04 09:56 | 2026-08-04 09:55 | 2026-08-04 09:56 | 2026-08-04 09:56 | 2026-08-04 09:56 | BrokenWire |  | Fair | No | Customer said problems has been resolved
Non-Outage | J.E.26.07.09258 | C001873788 | Wayne Dillion | St.Elizabeth | Completed | Load_258769 | Spur Tree - 210 | 2026-08-04 08:53 | 2026-08-04 08:55 | 2026-08-04 09:58 | 2026-08-04 09:59 | 2026-08-04 09:59 | 2026-08-04 09:59 | 2026-08-04 09:59 | 2026-08-04 09:59 | BrokenWire |  | Fair | No | Customer said problem has been resolved
Non-Outage | J.E.26.05.34075 | C001873790 | Wayne Dillion | Manchester | Completed | Load_268806 | Spur Tree - 210 | 2026-08-04 08:54 | 2026-08-04 08:55 | 2026-08-04 09:28 | 2026-08-04 09:29 | 2026-08-04 09:28 | 2026-08-04 09:29 | 2026-08-04 09:29 | 2026-08-04 09:29 | BrokenPole |  | Fair | No | Customer reporting a defective street light
Non-Outage | J.E.26.07.04901 | C001873791 | Wayne Dillion | Manchester | Completed | Load_245839 | Spur Tree - 210 | 2026-08-04 08:54 | 2026-08-04 08:55 | 2026-08-04 09:22 | 2026-08-04 09:22 | 2026-08-04 09:22 | 2026-08-04 09:22 | 2026-08-04 09:23 | 2026-08-04 09:23 | BrokenPole |  | Fair | No | Customer said Problem has been resolved
Non-Outage | J.E.26.07.19036 | C001873792 | Wayne Dillion | St.Elizabeth | Completed | Load_292078 | Maggotty - 210 | 2026-08-04 08:54 | 2026-08-04 08:55 | 2026-08-04 09:15 | 2026-08-04 09:16 | 2026-08-04 09:15 | 2026-08-04 09:18 | 2026-08-04 09:18 | 2026-08-04 09:18 | BrokenPole |  | Fair | No | Please refer call to maintenance to remove a pole that lay on the road side that customer requested to be removed
Non-Outage | J.E.26.08.05358 | C001873800 | Michael Christian | St.James | Completed | Load_259225 | Bogue - 610 | 2026-08-04 09:00 | 2026-08-04 09:01 | 2026-08-04 09:20 | 2026-08-04 09:21 | 2026-08-04 10:05 | 2026-08-04 10:17 | 2026-08-04 10:17 | 2026-08-04 10:17 |  |  | Fair | No | Check and found okay voltage 112 114 227 at pothead
Non-Outage | J.E.26.08.05978 | C001873799 | Michael Christian | St.James | Completed | Load_258893 | Bogue - 610 | 2026-08-04 09:00 | 2026-08-04 09:01 | 2026-08-04 12:05 | 2026-08-04 12:06 | 2026-08-04 13:09 | 2026-08-04 13:32 | 2026-08-04 13:33 | 2026-08-04 13:33 |  |  | Fair | No | Not found call customer answer
Non-Outage | J.E.26.08.04629 | C001873809 | Richard Nicholas |  | Completed |  |  | 2026-08-04 09:05 | 2026-08-04 13:48 | 2026-08-04 14:41 | 2026-08-04 14:42 | 2026-08-04 15:00 | 2026-08-04 16:04 | 2026-08-04 16:06 | 2026-08-04 16:06 |  |  | Fair | No | Replaced blown 167kva transformer 15amp fuse on pole #0101585 and blown 25amp junctions fuse on pole #550546.
Non-Outage | J.E.26.08.04916 | C001873815 | Rusean Allen | KSAS | Completed | Load_265897 | Hunts Bay - 510 | 2026-08-04 09:12 | 2026-08-04 09:13 | 2026-08-04 10:42 | 2026-08-04 10:42 | 2026-08-04 10:45 | 2026-08-04 10:45 | 2026-08-04 10:46 | 2026-08-04 10:46 |  |  | Fair | No | Found okay
Outage | J.E.26.08.06270 | C001873825 | Elvis Trowers | KSAN | Completed | Load_257312 | Washington Blvd - 310 | 2026-08-04 09:18 | 2026-08-04 09:19 | 2026-08-04 13:09 | 2026-08-04 13:10 | 2026-08-04 14:06 | 2026-08-04 14:27 | 2026-08-04 14:27 | 2026-08-04 14:27 |  |  | Fair | Yes | Happened to be internal when checked , voltage when checked was left at 110+109=219 volts, customer was also advised to contact an electrician.
Outage | J.E.26.08.06267 | C001873827 | Dwayne Cohen | KSAN | Completed | Load_265722 | Washington Blvd - 810 | 2026-08-04 09:19 | 2026-08-04 09:43 | 2026-08-04 10:57 | 2026-08-04 10:58 | 2026-08-04 11:17 | 2026-08-04 12:20 | 2026-08-04 12:25 | 2026-08-04 12:25 | Fire |  | Fair | No | Repair broken secondary conductor by using 10ft of 2/0 Quad and four onebolt clamps.
Outage | J.E.26.08.06283 | C001873828 | Oshane Warren | St.Elizabeth | Completed | Load_260524 | Maggotty - 110 | 2026-08-04 09:20 | 2026-08-04 11:43 | 2026-08-04 13:38 | 2026-08-04 13:39 | 2026-08-04 15:02 | 2026-08-04 15:34 | 2026-08-04 15:35 | 2026-08-04 15:35 |  |  | Fair | No | Reconnect service wire at pathead and secondary line used 45ft of number 6twisted wire 3service connector and used 3pg clamps
Outage | J.E.26.08.05305 | C001873841 | Wan Carlos Scarlett | Portmore | Completed | Load_257194 | Naggo Head - 510 | 2026-08-04 09:34 | 2026-08-04 09:35 | 2026-08-04 09:51 | 2026-08-04 12:41 | 2026-08-04 13:35 | 2026-08-04 13:42 | 2026-08-04 13:42 | 2026-08-04 13:42 |  |  | Fair | No | Customer confirm that power supply has been restored
Outage | J.E.26.08.05701 | C001873840 | Wan Carlos Scarlett | Portmore | Completed | Load_257194 | Naggo Head - 510 | 2026-08-04 09:34 | 2026-08-04 09:35 | 2026-08-04 09:50 | 2026-08-04 12:03 | 2026-08-04 12:24 | 2026-08-04 12:40 | 2026-08-04 12:41 | 2026-08-04 12:41 |  |  | Fair | No | Customer confirm that power supply has been restored
Outage | J.E.26.08.05712 | C001873839 | Wan Carlos Scarlett | Portmore | Completed | Load_266759 | Naggo Head - 510 | 2026-08-04 09:34 | 2026-08-04 09:35 | 2026-08-04 10:12 | 2026-08-04 11:28 | 2026-08-04 11:28 | 2026-08-04 12:01 | 2026-08-04 12:03 | 2026-08-04 12:03 | BrokenWire |  | Fair | No | Found customer 3 wire service at pole with one of the phase broken off use one bolt clamp at open secondary line phase readings 15-116-231
Outage | J.E.26.08.06026 | C001873838 | Wan Carlos Scarlett | Portmore | Completed | Load_241627 | Naggo Head - 510 | 2026-08-04 09:34 | 2026-08-04 09:35 | 2026-08-04 13:42 | 2026-08-04 13:43 | 2026-08-04 14:40 | 2026-08-04 14:40 | 2026-08-04 14:42 | 2026-08-04 14:42 |  |  | Fair | No | Found 25KVA transformer drop lead wire to open secondary line phase burn off use 2 one bolt clamps at pole readings 115-116-231
Outage | J.E.26.08.06239 | C001873837 | Wan Carlos Scarlett | Portmore | Completed | Load_265520 | Naggo Head - 510 | 2026-08-04 09:34 | 2026-08-04 09:35 | 2026-08-04 09:52 | 2026-08-04 14:43 | 2026-08-04 15:22 | 2026-08-04 16:16 | 2026-08-04 16:18 | 2026-08-04 16:18 |  |  | Fair | No | Found 1 span of open secondary lower phase burn out from the one bolt clamp jumper use 2 one bolt clamps readings 116 117 233
Outage | J.E.26.08.05345 | C001873842 | Damion Reid | Manchester | Completed | Load_266064 | Spur Tree - 210 | 2026-08-04 09:37 | 2026-08-04 09:38 | 2026-08-04 10:31 | 2026-08-04 10:32 | 2026-08-04 10:57 | 2026-08-04 12:26 | 2026-08-04 12:30 | 2026-08-04 12:30 |  |  | Fair | No | Blown 20amp an blown 10amp junction fuse found line patrol nothing was found blown fuse replace (customer requesting maintenance team check PT meter)
Outage | J.E.26.08.06305 | C001873843 | Omar King | St.Ann | Completed | Load_269625 | Roaring River - 410 | 2026-08-04 09:41 | 2026-08-04 15:04 | 2026-08-04 15:56 | 2026-08-04 15:56 | 2026-08-04 16:22 | 2026-08-04 16:23 | 2026-08-04 16:23 | 2026-08-04 16:23 | Fire |  | Fair | No | Unable to find customer call several times no answer directions not sufficient
Non-Outage | J.E.26.08.04846 | C001873859 | Christopher Edwards | KSAN | Completed | Load_250006 | Constant Spring - 410 | 2026-08-04 09:49 | 2026-08-04 10:45 | 2026-08-04 10:59 | 2026-08-04 11:00 | 2026-08-04 11:07 | 2026-08-04 11:50 | 2026-08-04 11:51 | 2026-08-04 11:51 |  |  | Fair | No | Burnt mid span joint Remake joint using (1) one bolt clamps Voltage:116,115,230vAlso area requires,I’d bushing on the secondary lines
Non-Outage | J.E.26.08.05184 | C001873858 | Christopher Edwards | KSAN | Completed | Load_249915 | Constant Spring - 410 | 2026-08-04 09:49 | 2026-08-04 10:45 | 2026-08-04 13:56 | 2026-08-04 13:59 | 2026-08-04 14:32 | 2026-08-04 14:54 | 2026-08-04 14:59 | 2026-08-04 14:59 |  |  | Fair | No | Open secondary neutral has multiple splices sleeves Required bucket truck to rectify issue Customers are currently having high and low voltage
Non-Outage | J.E.26.08.05953 | C001873857 | Christopher Edwards | KSAN | Completed | Load_246237 | Constant Spring - 410 | 2026-08-04 09:49 | 2026-08-04 10:45 | 2026-08-04 11:52 | 2026-08-04 11:56 | 2026-08-04 12:11 | 2026-08-04 13:56 | 2026-08-04 13:56 | 2026-08-04 13:56 |  |  | Fair | No | Isolate 100 kva transformer To remake burnt neutral jumper joint Using (2) one bolt clamps Voltage:115,114,230v
Non-Outage | J.E.26.08.05315 | C001873867 | Edward Royal | KSAS | Completed | Load_265037 | Rockfort - 210 | 2026-08-04 09:57 | 2026-08-04 09:58 | 2026-08-04 12:22 | 2026-08-04 12:23 | 2026-08-04 12:22 | 2026-08-04 13:29 | 2026-08-04 13:30 | 2026-08-04 13:30 |  |  | Fair | No | Spliced and reconnected primary line using 40 ft open number 2 2 single bolt clamp replaced 30A junction fuse 3A transformer fuse
Outage | J.E.26.08.06265 | C001873873 | Moses Elliston | St.Catherine | Completed | Load_247080 | Twickenham - 310 | 2026-08-04 10:04 | 2026-08-04 10:05 | 2026-08-05 12:19 | 2026-08-05 12:19 | 2026-08-05 12:19 | 2026-08-05 12:20 | 2026-08-05 12:21 | 2026-08-05 12:21 |  |  | Fair | No | Defective collector changed to # 31684719 due to non communication
Non-Outage | J.E.26.08.06294 | C001873874 | Romeo Brissett | Hanover | Completed | Load_261941 | Orange Bay - 210 | 2026-08-04 10:05 | 2026-08-04 11:31 | 2026-08-04 11:50 | 2026-08-04 11:50 | 2026-08-04 14:27 | 2026-08-04 14:30 | 2026-08-04 14:36 | 2026-08-04 14:36 |  |  | Fair | No | Isolated (3)50kva transformer drop out switches.
Outage | J.E.26.08.06253 | C001873875 | Shamour Haughton | St.James | Completed | Load_261336 | Bogue - 310 | 2026-08-04 10:06 | 2026-08-04 20:08 | 2026-08-04 21:38 | 2026-08-04 21:38 | 2026-08-04 21:38 | 2026-08-04 21:38 | 2026-08-04 21:40 | 2026-08-04 21:40 |  |  | Fair | No | Customer keeps going voicemail, unable to locate customer
Outage | J.E.26.08.06360 | C001873876 | Edward Royal | KSAS | Completed | Load_242913 | Cane River - 410 | 2026-08-04 10:06 | 2026-08-04 10:08 | 2026-08-04 13:47 | 2026-08-04 13:47 | 2026-08-04 13:47 | 2026-08-04 13:47 | 2026-08-04 13:47 | 2026-08-04 13:47 | Fire |  | Fair | No | Related to plan outage
Outage | J.E.26.08.06364 | C001873882 | Elvis Trowers | KSAN | Completed | Load_293877 | Washington Blvd - 710 | 2026-08-04 10:07 | 2026-08-04 10:08 | 2026-08-04 12:43 | 2026-08-04 12:59 | 2026-08-04 12:59 | 2026-08-04 13:07 | 2026-08-04 13:07 | 2026-08-04 13:07 |  |  | Fair | Yes | Field service to visit, meter not communicating.
Outage | J.E.26.08.06266 | C001873883 | Moses Elliston | St.Catherine | Completed | Load_242663 | New Michelton - 210 | 2026-08-04 10:09 | 2026-08-04 10:10 | 2026-08-04 13:59 | 2026-08-04 14:00 | 2026-08-04 13:59 | 2026-08-04 11:20 | 2026-08-04 14:01 | 2026-08-04 14:01 |  |  | Fair | No | Supply ok at premises.
Non-Outage | J.E.26.08.06327 | C001873888 | Richard Nicholas | St.Catherine | Completed | Load_250121 | Tredegar - 310 | 2026-08-04 10:13 | 2026-08-04 10:13 | 2026-08-04 11:51 | 2026-08-04 11:51 | 2026-08-04 11:51 | 2026-08-04 11:51 | 2026-08-04 11:53 | 2026-08-04 11:53 |  |  | Fair | No | Remade burnt off center T-off primary to kfc,jumper. One clamp was used.
Outage | J.E.26.08.06348 | C001873889 | Wayne Dillion | Manchester | Completed | Load_239635 | Spur Tree - 210 | 2026-08-04 10:14 | 2026-08-04 10:15 | 2026-08-04 11:03 | 2026-08-04 11:04 | 2026-08-04 11:35 | 2026-08-04 12:20 | 2026-08-04 12:20 | 2026-08-04 12:20 |  |  | Fair | No | Patrol and found one blown 2amp fuse that protects 15kva hexing transformer circuit at pole #501621. Further checks reveals that transformer is defective and 12 customers are affected. Please refer same to the maintenance department for replacement.
Outage | J.E.26.08.06375 | C001873894 | Edward Royal | KSAS | Completed | Load_254610 | Rockfort - 210 | 2026-08-04 10:19 | 2026-08-04 10:21 | 2026-08-04 13:31 | 2026-08-04 13:32 | 2026-08-04 13:31 | 2026-08-04 13:32 | 2026-08-04 13:32 | 2026-08-04 13:32 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.06368 | C001873904 | Edward Royal | KSAS | Completed | Load_300870 | Cane River - 410 | 2026-08-04 10:22 | 2026-08-04 10:23 | 2026-08-04 14:59 | 2026-08-04 14:59 | 2026-08-04 14:59 | 2026-08-04 15:01 | 2026-08-04 15:01 | 2026-08-04 15:01 |  |  | Fair | No | Customer have internal problems customer have faulty change over switch advise customer to get a electrician to fix the problem
Outage | J.E.26.08.06427 | C001873913 | Richard Watson | St.Elizabeth | Completed | Load_238611 | Maggotty - 110 | 2026-08-04 10:30 | 2026-08-04 11:43 | 2026-08-04 11:56 | 2026-08-04 13:13 | 2026-08-04 13:35 | 2026-08-04 13:44 | 2026-08-04 13:45 | 2026-08-04 13:45 |  |  | Fair | No | Check and found that customer was disconnected for outstanding balance for meter#2614311
Non-Outage | J.E.26.07.36691 | C001873915 | Oraine Minto | St.Ann | Completed | Load_249152 | Cardiff Hall - 210 | 2026-08-04 10:31 | 2026-08-04 10:32 | 2026-08-04 10:40 | 2026-08-04 12:16 | 2026-08-04 12:16 | 2026-08-04 12:38 | 2026-08-04 12:40 | 2026-08-04 12:40 |  |  | Fair | No | Refer to emergency Car park in the work area unable to complete task Voltage that was found was 218v phase to phase 107v 108v A back to back secondary on the pole but car under the pole where work is to be done Refer to emergencyTransformer need to turn up
Outage | J.E.26.08.06455 | C001873924 | Raymond Lewis | St.Ann | Completed | Load_245610 | Roaring River - 210 | 2026-08-04 10:38 | 2026-08-04 10:39 | 2026-08-04 15:06 | 2026-08-04 15:07 | 2026-08-04 15:48 | 2026-08-04 15:50 | 2026-08-04 15:50 | 2026-08-04 15:50 | Fire |  | Fair | No | Remade neutral joint 3 wire service at ploe
Non-Outage | J.E.26.08.03230 | C001873946 | Rochaine Hussey | KSAS | Completed | Load_240053 | Duhaney - 410 | 2026-08-04 10:49 | 2026-08-04 10:51 | 2026-08-04 12:34 | 2026-08-04 13:18 | 2026-08-04 13:17 | 2026-08-04 15:03 | 2026-08-04 15:03 | 2026-08-04 15:03 |  |  | Fair | No | Customer say the Premesis is okay and power was restored
Non-Outage | J.E.26.08.03232 | C001873945 | Rochaine Hussey | KSAS | Completed | Load_573722 | Duhaney - 410 | 2026-08-04 10:49 | 2026-08-04 10:51 | 2026-08-04 12:33 | 2026-08-04 15:04 | 2026-08-04 15:04 | 2026-08-04 15:04 | 2026-08-04 15:04 | 2026-08-04 15:04 |  |  | Fair | No | Customer say the issue was resolved
Non-Outage | J.E.26.08.03240 | C001873943 | Rochaine Hussey | KSAS | Completed | Load_248351 | Duhaney - 410 | 2026-08-04 10:49 | 2026-08-04 10:51 | 2026-08-04 11:33 | 2026-08-04 11:34 | 2026-08-04 11:33 | 2026-08-04 12:03 | 2026-08-04 12:03 | 2026-08-04 12:03 |  |  | Fair | No | Customer say the issue was fixed and the power was restored
Non-Outage | J.E.26.08.03244 | C001873944 | Rochaine Hussey | KSAS | Completed | Load_249073 | Duhaney - 410 | 2026-08-04 10:49 | 2026-08-04 10:51 | 2026-08-04 12:33 | 2026-08-04 15:05 | 2026-08-04 15:04 | 2026-08-04 15:16 | 2026-08-04 15:16 | 2026-08-04 15:16 |  |  | Fair | No | Customer say the issue was fixed and power was restored
Non-Outage | J.E.26.08.03249 | C001873942 | Rochaine Hussey | KSAS | Completed | Load_240053 | Duhaney - 410 | 2026-08-04 10:49 | 2026-08-04 10:51 | 2026-08-04 12:33 | 2026-08-04 15:51 | 2026-08-04 15:50 | 2026-08-04 16:00 | 2026-08-04 16:00 | 2026-08-04 16:00 |  |  | Fair | No | Customer say the issue was resolved
Non-Outage | J.E.26.08.03254 | C001873941 | Rochaine Hussey | KSAS | Completed | Load_573722 | Duhaney - 410 | 2026-08-04 10:49 | 2026-08-04 10:51 | 2026-08-04 11:31 | 2026-08-05 11:31 | 2026-08-05 11:31 | 2026-08-05 12:21 | 2026-08-05 12:21 | 2026-08-05 12:21 |  |  | Fair | No | Customer say the issue was already resolved
Non-Outage | J.E.26.08.03257 | C001873939 | Rochaine Hussey | KSAS | Completed | Load_248574 | Duhaney - 410 | 2026-08-04 10:49 | 2026-08-04 10:51 | 2026-08-05 15:03 | 2026-08-05 15:04 | 2026-08-05 15:03 | 2026-08-05 15:05 | 2026-08-05 15:05 | 2026-08-05 15:05 |  |  | Fair | No | Customer was called multiple times no answer Unable to locate
Non-Outage | J.E.26.08.03275 | C001873940 | Rochaine Hussey | KSAS | Completed | Load_243956 | Duhaney - 410 | 2026-08-04 10:49 | 2026-08-04 10:51 | 2026-08-04 11:30 | 2026-08-04 16:01 | 2026-08-04 16:00 | 2026-08-05 09:11 | 2026-08-05 09:12 | 2026-08-05 09:12 |  |  | Fair | No | Customer say the issue was resolved
Non-Outage | J.E.26.08.03292 | C001873938 | Rochaine Hussey | KSAS | Completed | Load_573722 | Duhaney - 410 | 2026-08-04 10:49 | 2026-08-04 10:51 | 2026-08-04 11:28 | 2026-08-04 15:17 | 2026-08-04 15:17 | 2026-08-04 15:50 | 2026-08-04 15:50 | 2026-08-04 15:50 |  |  | Fair | No | Customer say the issue was resolved
Non-Outage | J.E.26.08.03331 | C001873937 | Rochaine Hussey | KSAS | Completed | Load_270125 | Duhaney - 410 | 2026-08-04 10:49 | 2026-08-04 10:51 | 2026-08-04 11:27 | 2026-08-04 12:20 | 2026-08-04 12:19 | 2026-08-04 12:32 | 2026-08-04 12:33 | 2026-08-04 12:33 |  |  | Fair | No | Issue was resolved
Outage | J.E.26.08.05930 | C001873957 | Denton Williams | Portland | Completed | Load_247771 | Port Antonio - 310 | 2026-08-04 10:59 | 2026-08-04 11:00 | 2026-08-04 13:02 | 2026-08-04 13:03 | 2026-08-04 13:16 | 2026-08-04 13:54 | 2026-08-04 13:58 | 2026-08-04 13:58 |  |  | Fair | Yes | Corrosion at pothead. Replaced one clamp to corrosion fault.Voltage readings leave —118v, 118v & 237v.
Outage | J.E.26.08.06037 | C001873956 | Denton Williams | Portland | Completed | Load_349124 | Port Antonio - 410 | 2026-08-04 10:59 | 2026-08-04 11:00 | 2026-08-04 12:35 | 2026-08-04 12:36 | 2026-08-04 12:55 | 2026-08-04 13:01 | 2026-08-04 13:02 | 2026-08-04 13:02 |  |  | Fair | No | Check and found customer electrical supply okay.
Outage | J.E.26.08.06166 | C001873955 | Denton Williams | Portland | Completed | Load_267688 | Port Antonio - 410 | 2026-08-04 10:59 | 2026-08-04 11:00 | 2026-08-04 11:03 | 2026-08-04 11:04 | 2026-08-04 11:41 | 2026-08-04 12:26 | 2026-08-04 12:33 | 2026-08-04 12:33 |  |  | Fair | No | Defective wooden cross arm causing a 25kva transformer switch to be dislodged. Temporary measure was taken to affix switch back to cross arm. Cross arm need replacement, please refer to Portland maintenance team.
Outage | J.E.26.08.06264 | C001873954 | Denton Williams | Portland | Completed | Load_349987 | Port Antonio - 410 | 2026-08-04 10:59 | 2026-08-04 11:00 | 2026-08-04 13:59 | 2026-08-04 15:43 | 2026-08-04 16:05 | 2026-08-04 16:16 | 2026-08-04 16:16 | 2026-08-04 16:16 |  |  | Fair | No | Area was previously visited and customer complain was fixed. Customer stated that one room is without electricity. Customer was advised to contact a licensed electrician.
Outage | J.E.26.08.06357 | C001873964 | Rusean Allen | KSAS | Completed | Load_267774 | Hunts Bay - 510 | 2026-08-04 11:03 | 2026-08-05 08:46 | 2026-08-05 11:35 | 2026-08-05 11:36 | 2026-08-05 11:58 | 2026-08-05 11:58 | 2026-08-05 11:58 | 2026-08-05 11:58 |  |  | Fair | No
Outage | J.E.26.08.06289 | C001873965 | Clyde Brown | Clarendon | Completed | Load_247364 | May Pen - 110 | 2026-08-04 11:06 | 2026-08-04 11:06 | 2026-08-04 12:55 | 2026-08-04 12:55 | 2026-08-04 14:00 | 2026-08-04 13:55 | 2026-08-04 14:05 | 2026-08-04 14:05 |  |  | Fair | No | Blown 3 amps fuse for 25 kva transformer,line patrolled and no fault seen blown fuse replaced
Outage | J.E.26.08.06584 | C001873975 | Oshane Warren | Westmoreland | Completed | Load_261865 | Paradise - 110 | 2026-08-04 11:15 | 2026-08-04 11:20 | 2026-08-04 12:29 | 2026-08-04 13:35 | 2026-08-04 13:35 | 2026-08-04 13:35 | 2026-08-04 13:36 | 2026-08-04 13:36 |  |  | Fair | No | Customer was disconnected for none payment of bill
Outage | J.E.26.08.06575 | C001873985 | Clyde Brown | Clarendon | Completed | Load_242082 | Parnassus - 310 | 2026-08-04 11:23 | 2026-08-05 07:48 | 2026-08-05 08:44 | 2026-08-05 08:44 | 2026-08-05 09:23 | 2026-08-05 09:24 | 2026-08-05 09:27 | 2026-08-05 09:27 | Fire |  | Fair | No | Found ok,no fire seen
Outage | J.E.26.08.06420 | C001873986 | Rusean Allen | KSAS | Completed | Load_245002 | Rockfort - 410 | 2026-08-04 11:26 | 2026-08-04 11:27 | 2026-08-04 12:49 | 2026-08-04 12:50 | 2026-08-04 12:51 | 2026-08-04 12:55 | 2026-08-04 12:55 | 2026-08-04 12:55 |  |  | Fair | No | 1x 10amp fuse found 1x 10amp fuse replaced.
Non-Outage | J.E.26.08.04916 | C001873995 | Rusean Allen | KSAS | Completed | Load_265897 | Hunts Bay - 510 | 2026-08-04 11:36 | 2026-08-04 11:37 | 2026-08-04 12:13 | 2026-08-04 12:13 | 2026-08-04 12:14 | 2026-08-04 12:39 | 2026-08-04 12:39 | 2026-08-04 12:39 |  |  | Fair | No | 2 defective 10KVA transformers found, transformers needs to be changed Refer to maintenance department.
Outage | J.E.26.08.06619 | C001873998 | Wayne Dillion | St.Elizabeth | Completed | Load_292118 | Maggotty - 210 | 2026-08-04 11:38 | 2026-08-04 11:38 | 2026-08-04 14:02 | 2026-08-04 14:03 | 2026-08-04 14:02 | 2026-08-04 14:30 | 2026-08-04 14:32 | 2026-08-04 14:32 |  |  | Fair | No | Reconnect customer using 70 feet of number 6 triplex 3 linket 3 one bolt clamp voltage reading 111v, 110v, 221v supply working ok.
Outage | J.E.26.08.06335 | C001874002 | Swon Miller | St.James | Completed | Load_264470 | Queens Drive - 710 | 2026-08-04 11:40 | 2026-08-04 11:41 | 2026-08-04 11:56 | 2026-08-04 12:04 | 2026-08-04 13:09 | 2026-08-19 13:32 | 2026-08-04 13:34 | 2026-08-04 13:34 |  |  | Fair | No | Check and found areas okay voltage found 116/114/231 customer states that power supply has been restored
Outage | J.E.26.08.06336 | C001874001 | Swon Miller | St.James | Completed | Load_248976 | Queens Drive - 710 | 2026-08-04 11:40 | 2026-08-04 11:41 | 2026-08-04 11:56 | 2026-08-04 13:35 | 2026-08-04 13:43 | 2026-08-26 01:50 | 2026-08-04 13:58 | 2026-08-04 13:58 |  |  | Fair | No | Call related to previous
Outage | J.E.26.08.06497 | C001874000 | Swon Miller | St.James | Completed | Load_260605 | Queens Drive - 710 | 2026-08-04 11:40 | 2026-08-04 11:41 | 2026-08-04 11:56 | 2026-08-04 13:58 | 2026-08-04 14:40 | 2026-08-18 14:50 | 2026-08-04 14:50 | 2026-08-04 14:50 | Fire |  | Fair | No | Unable to locate customer phone calls to customer number went unanswered
Outage | J.E.26.08.06577 | C001874007 | Derrick Dawkins | St.James | Completed | Load_240857 | Bogue - 610 | 2026-08-04 11:42 | 2026-08-04 15:50 | 2026-08-04 16:30 | 2026-08-04 16:30 | 2026-08-04 18:08 | 2026-08-04 18:16 | 2026-08-04 18:17 | 2026-08-04 18:17 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.06586 | C001874008 | Romeo Brissett | St.James | Completed | Load_257498 | Bogue - 610 | 2026-08-04 11:42 | 2026-08-04 22:19 | 2026-08-04 22:45 | 2026-08-04 22:45 | 2026-08-04 23:17 | 2026-08-04 23:30 | 2026-08-04 23:34 | 2026-08-04 23:34 | LeaningPole |  | Fair | No | Patrolled and found light in the area, (1)40ft pole found leaning with 2/0 twisted. Need to be straighten. Please send to maintenance.
Outage | J.E.26.08.06538 | C001874009 | Daniel Lobar | Trelawny | Completed | Load_1001447 | Martha Brae - 110 | 2026-08-04 11:44 | 2026-08-04 11:45 | 2026-08-04 13:33 | 2026-08-04 13:33 | 2026-08-04 13:45 | 2026-08-14 15:48 | 2026-08-04 15:48 | 2026-08-04 15:48 |  |  | Fair | No
Outage | J.E.26.08.06564 | C001874010 | Daniel Lobar | Trelawny | Completed | Load_261734 | Duncans - 210 | 2026-08-04 11:44 | 2026-08-04 11:45 | 2026-08-04 13:23 | 2026-08-04 13:24 | 2026-08-04 13:24 | 2026-08-04 13:25 | 2026-08-04 13:25 | 2026-08-04 13:25 |  |  | Fair | No
Outage | J.E.26.08.06510 | C001874012 | Floyd Taylor | Trelawny | Completed | Load_255065 | Greenwood - 210 | 2026-08-04 11:46 | 2026-08-04 11:47 | 2026-08-04 12:25 | 2026-08-04 12:26 | 2026-08-04 12:59 | 2026-08-04 12:59 | 2026-08-04 12:59 | 2026-08-04 12:59 |  |  | Fair | No | Customer service was restored
Outage | J.E.26.08.06552 | C001874013 | Floyd Taylor | Trelawny | Completed | Load_1001716 | Greenwood - 210 | 2026-08-04 11:46 | 2026-08-04 11:47 | 2026-08-04 13:01 | 2026-08-04 13:02 | 2026-08-04 13:01 | 2026-08-04 13:02 | 2026-08-04 13:02 | 2026-08-04 13:02 |  |  | Fair | No | Customer service was restored
Outage | J.E.26.08.06592 | C001874011 | Floyd Taylor | Trelawny | Completed | Load_256148 | Greenwood - 210 | 2026-08-04 11:46 | 2026-08-04 11:47 | 2026-08-04 12:27 | 2026-08-04 13:00 | 2026-08-04 12:59 | 2026-08-04 13:00 | 2026-08-04 13:01 | 2026-08-04 13:01 |  |  | EarthMovement | No | Customer service was restored
Outage | J.E.26.08.05311 | C001874028 | Rodclif Dawkins | Portmore | Completed | Load_269220 | Naggo Head - 610 | 2026-08-04 12:03 | 2026-08-04 16:04 | 2026-08-04 17:16 | 2026-08-04 17:18 | 2026-08-04 17:31 | 2026-08-04 17:52 | 2026-08-04 17:54 | 2026-08-04 17:54 |  |  | Fair | No | Found 2 blown fuse and 1 missing link from bank of 3,100kva transformer. No faults seen or observed at the time of fit. Replaced link and replaced 10amp fuse . Customer okay
Outage | J.E.26.08.06361 | C001874032 | Moses Elliston | St.Catherine | Completed | Load_261113 | Tredegar - 310 | 2026-08-04 12:15 | 2026-08-04 12:16 | 2026-08-04 16:29 | 2026-08-04 16:30 | 2026-08-04 22:56 | 2026-08-04 17:00 | 2026-08-04 22:58 | 2026-08-04 22:58 |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.08.05286 | C001874033 | Moses Elliston | St.Catherine | Completed | Load_238151 | Twickenham - 310 | 2026-08-04 12:16 | 2026-08-04 12:16 | 2026-08-04 13:52 | 2026-08-04 13:52 | 2026-08-04 13:52 | 2026-08-04 13:20 | 2026-08-04 13:54 | 2026-08-04 13:54 |  |  | Fair | No | Burnt 3 wire service phase repaired with 1 clamp.
Outage | J.E.26.08.06621 | C001874038 | Omar King | St.Ann | Completed | Load_257528 | Roaring River - 210 | 2026-08-04 12:20 | 2026-08-04 15:04 | 2026-08-04 22:10 | 2026-08-04 22:10 | 2026-08-05 08:56 | 2026-08-05 08:56 | 2026-08-05 08:57 | 2026-08-05 08:57 |  |  | Flood | No | Customer said she as supply
Outage | J.E.26.08.06699 | C001874044 | Selvin White | St.Elizabeth | Completed | Load_265728 | Maggotty - 110 | 2026-08-04 12:24 | 2026-08-04 15:38 | 2026-08-04 16:36 | 2026-08-04 16:36 | 2026-08-04 16:48 | 2026-08-04 16:55 | 2026-08-04 16:59 | 2026-08-04 16:59 |  |  | Fair | No | Please refer reconnection to C . Johnson at the field service department so premises can be checked by the field service technicians before a decision can be made to restore supply .. Customer says supply is for downstairs of the building but upstairs is still damaged.
Outage | J.E.26.08.06660 | C001874045 | Rusean Allen | KSAS | Completed | Load_238432 | Hunts Bay - 210 | 2026-08-04 12:25 | 2026-08-04 12:26 | 2026-08-04 12:56 | 2026-08-04 12:56 | 2026-08-04 13:50 | 2026-08-04 14:23 | 2026-08-04 14:23 | 2026-08-04 14:23 |  |  | Fair | No | 1x 10amp fuse found 1x 10amp fuse replaced.
Outage | J.E.26.08.06700 | C001874046 | Selvin White | St.Elizabeth | Completed | Load_259624 | Maggotty - 110 | 2026-08-04 12:25 | 2026-08-04 15:38 | 2026-08-04 16:59 | 2026-08-04 17:00 | 2026-08-04 18:21 | 2026-08-04 18:33 | 2026-08-04 18:36 | 2026-08-04 18:36 |  |  | Fair | No | Bucket truck is required to connect customer service wire at concrete pole with secondary conductor top phase very close to primary conductor.
Non-Outage | J.E.26.08.06262 | C001874053 | Derrick Grubb | St.Thomas | Completed | Load_238488 | Good Year - 210 | 2026-08-04 12:27 | 2026-08-05 09:02 | 2026-08-05 09:44 | 2026-08-05 09:45 | 2026-08-05 10:17 | 2026-08-05 12:08 | 2026-08-05 12:08 | 2026-08-05 12:08 |  |  | Fair | No | Customer was experiencing high voltage. Top down transformer. Voltage readings when leaving 118v, 117v, 207v, 239v, 233v, 237v.
Non-Outage | J.E.26.08.06276 | C001874054 | Hopeton Henry | St.Thomas | Completed | Load_262524 | Lysson - 410 | 2026-08-04 12:27 | 2026-08-04 12:29 | 2026-08-04 13:28 | 2026-08-04 13:37 | 2026-08-04 14:42 | 2026-08-05 11:22 | 2026-08-05 11:23 | 2026-08-05 11:23 |  |  | Fair | No | Use 2 clamps at pole 115-117-233 volts
Non-Outage | J.E.26.08.06611 | C001874055 | Hopeton Henry | St.Thomas | Completed | Load_327665 | Lysson - 410 | 2026-08-04 12:27 | 2026-08-04 12:29 | 2026-08-04 13:28 | 2026-08-05 11:24 | 2026-08-05 11:45 | 2026-08-05 11:45 | 2026-08-05 11:46 | 2026-08-05 11:46 |  |  | Fair | No | Customer not located
Outage | J.E.26.08.05413 | C001874056 | Rodclif Dawkins | Portmore | Completed | Load_245734 | Naggo Head - 610 | 2026-08-04 12:27 | 2026-08-04 16:04 | 2026-08-04 17:25 | 2026-08-04 17:55 | 2026-08-04 18:11 | 2026-08-04 18:31 | 2026-08-04 18:32 | 2026-08-04 18:32 |  |  | Fair | No | Found blown junction fuse from single phase line section. No faults observed. Found and replaced 8amp fuse cell site restored
Outage | J.E.26.08.06641 | C001874050 | Stephen Taylor | St.Thomas | Completed | Load_577136 | Lysson - 410 | 2026-08-04 12:27 | 2026-08-04 15:28 | 2026-08-04 19:15 | 2026-08-04 19:16 | 2026-08-04 19:16 | 2026-08-04 19:16 | 2026-08-04 19:17 | 2026-08-04 19:17 |  |  | Fair | No | Need more information a lot of calls to customer no one answered the phone power is in the area
Outage | J.E.26.08.06709 | C001874051 | Derrick Grubb | St.Thomas | Completed | Load_238431 | Good Year - 110 | 2026-08-04 12:27 | 2026-08-04 12:28 | 2026-08-04 14:25 | 2026-08-04 14:25 | 2026-08-04 14:33 | 2026-08-04 15:26 | 2026-08-04 15:26 | 2026-08-04 15:26 |  |  | Fair | No | Patrol, found no visible faults on the line and refuse 15amp junction at pole number 0004670. Power restored.
Non-Outage | J.E.26.08.05166 | C001874060 | Dwayne Cohen | KSAS | Completed | Load_254756 | Duhaney - 310 | 2026-08-04 12:34 | 2026-08-04 12:36 | 2026-08-04 12:48 | 2026-08-04 12:49 | 2026-08-04 13:35 | 2026-08-04 14:20 | 2026-08-04 14:24 | 2026-08-04 14:24 | TreeContact |  | Fair | No | Remove cut tree from open secondary circuit.
Non-Outage | J.E.26.08.06725 | C001874061 | Raymond Carr |  | Completed |  |  | 2026-08-04 12:35 | 2026-08-04 12:48 | 2026-08-04 12:57 | 2026-08-04 12:58 | 2026-08-04 14:03 | 2026-08-04 14:35 | 2026-08-04 14:42 | 2026-08-04 14:42 |  |  | Fair | No | Voltage readings at dead end 98/88/186, however transformer tap position carried 4. Voltage readings 104/117/221. 25 kva transformer is unable to manage load. Kindly refer to maintenance department.
Outage | J.E.26.08.06751 | C001874068 | Damion Reid | Manchester | Completed | Load_259740 | Spur Tree - 310 | 2026-08-04 12:41 | 2026-08-04 12:46 | 2026-08-04 12:51 | 2026-08-04 12:52 | 2026-08-04 13:49 | 2026-08-04 13:50 | 2026-08-04 13:53 | 2026-08-04 13:53 |  |  | Fair | No | Burnt off primary phase jumper found cause by defective one bolt clamp de energize line section replace defective clamp and restore power
Non-Outage | J.E.26.08.06473 | C001874073 | Michael Christian |  | Completed |  |  | 2026-08-04 12:43 | 2026-08-04 12:45 | 2026-08-04 13:33 | 2026-08-04 13:34 | 2026-08-04 14:57 | 2026-08-04 15:07 | 2026-08-04 15:07 | 2026-08-04 15:07 |  |  | Fair | No | Found 1 8 amp and 1 25 kava transformer out cause by lightning and rain replace 1 8 amp 1 2 amp in 1 25 kava
Outage | J.E.26.08.06618 | C001874074 | Kaydon Taylor | KSAN | Completed | Load_260219 | Constant Spring - 410 | 2026-08-04 12:47 | 2026-08-04 15:31 | 2026-08-04 15:57 | 2026-08-04 16:00 | 2026-08-04 17:23 | 2026-08-04 17:41 | 2026-08-04 17:41 | 2026-08-04 17:41 | BrokenWire |  | Fair | No | One clamp at pole
Outage | J.E.26.08.06720 | C001874075 | Eric Williams | KSAN | Completed | Load_254454 | Washington Blvd - 410 | 2026-08-04 12:47 | 2026-08-04 15:25 | 2026-08-04 20:57 | 2026-08-04 20:58 | 2026-08-04 21:20 | 2026-08-04 21:21 | 2026-08-04 21:22 | 2026-08-04 21:22 |  |  | Fair | No | Premises closed, calls to customer went unanswered
Outage | J.E.26.08.05800 | C001874080 | Richard Nicholas | St.Catherine | Completed | Load_260775 | Tredegar - 210 | 2026-08-04 12:59 | 2026-08-04 13:01 | 2026-08-04 21:53 | 2026-08-04 21:54 | 2026-08-04 22:34 | 2026-08-04 22:54 | 2026-08-04 22:55 | 2026-08-04 22:55 |  |  | Fair | No | Found ok
Outage | J.E.26.08.06103 | C001874082 | Christopher West | St.Catherine | Completed | Load_1000612 | Rhodens Pen - 210 | 2026-08-04 12:59 | 2026-08-05 09:21 | 2026-08-05 09:44 | 2026-08-05 11:08 | 2026-08-05 11:24 | 2026-08-05 11:36 | 2026-08-05 11:56 | 2026-08-05 11:56 |  |  | Fair | No
Outage | J.E.26.08.06142 | C001874083 | Richard Nicholas | St.Catherine | Completed | Load_259014 | Tredegar - 210 | 2026-08-04 12:59 | 2026-08-04 13:01 | 2026-08-04 19:33 | 2026-08-04 19:34 | 2026-08-04 20:44 | 2026-08-04 21:47 | 2026-08-04 21:49 | 2026-08-04 21:49 |  |  | Fair | No | Retention 2 span of low hanging and banging secondary phase and neutral conductors.3 jhook was use to balance same on a wooden pole.
Non-Outage | J.E.26.08.05179 | C001874084 | Richard Nicholas |  | Completed |  |  | 2026-08-04 13:00 | 2026-08-04 13:01 | 2026-08-04 17:40 | 2026-08-04 17:40 | 2026-08-04 18:42 | 2026-08-04 19:28 | 2026-08-04 19:32 | 2026-08-04 19:32 |  |  | Fair | No | Replaced blown 15amp junctions fuse at the 3phase T-off to the warehouse and blown 100kva transformer 10amp fuse and blown 50kva transformer 5amp fuse at the warehouse.
Outage | J.E.26.08.05016 | C001874085 | Moses Elliston | St.Catherine | Completed | Load_256848 | Tredegar - 510 | 2026-08-04 13:00 | 2026-08-05 09:22 | 2026-08-05 09:40 | 2026-08-05 09:41 | 2026-08-05 09:40 | 2026-08-05 09:47 | 2026-08-05 09:48 | 2026-08-05 09:48 |  |  | Fair | No | Supply ok at premises
Outage | J.E.26.08.06642 | C001874086 | Shamour Haughton | St.James | Completed | Load_301674 | Bogue - 310 | 2026-08-04 13:00 | 2026-08-04 15:34 | 2026-08-04 15:43 | 2026-08-04 15:47 | 2026-08-04 16:24 | 2026-08-04 16:48 | 2026-08-04 16:53 | 2026-08-04 16:53 |  |  | Fair | No | Found 1,50amp junction fuse blown, refuse 50amp junction
Outage | J.E.26.08.06574 | C001874089 | Shamour Haughton | St.James | Completed | Load_301847 | Bogue - 310 | 2026-08-04 13:01 | 2026-08-04 15:34 | 2026-08-04 18:03 | 2026-08-04 18:04 | 2026-08-04 18:03 | 2026-08-04 18:03 | 2026-08-04 18:04 | 2026-08-04 18:04 |  |  | Fair | No | Related to previous call
Outage | J.E.26.08.06609 | C001874088 | Shamour Haughton | St.James | Completed | Load_1002051 | Bogue - 310 | 2026-08-04 13:01 | 2026-08-04 15:34 | 2026-08-04 16:54 | 2026-08-04 16:55 | 2026-08-04 16:54 | 2026-08-04 16:54 | 2026-08-04 16:55 | 2026-08-04 16:55 |  |  | Fair | No | Related to previous call
Outage | J.E.26.08.06657 | C001874087 | Derrick Dawkins | St.James | Completed | Load_243887 | Bogue - 510 | 2026-08-04 13:01 | 2026-08-04 15:48 | 2026-08-04 16:30 | 2026-08-04 18:18 | 2026-08-04 18:34 | 2026-08-04 18:35 | 2026-08-04 18:35 | 2026-08-04 18:35 |  |  | Fair | No | Calls to customer went unanswered cannot locate
Outage | J.E.26.08.06742 | C001874096 | Stephen Taylor | St.Thomas | Completed | Load_269082 | Lysson - 410 | 2026-08-04 13:09 | 2026-08-04 15:28 | 2026-08-04 19:12 | 2026-08-04 19:13 | 2026-08-04 19:12 | 2026-08-04 19:12 | 2026-08-04 19:14 | 2026-08-04 19:14 | LeaningPole |  | Fair | No | Jps class 4 pole lean and need to be straightened by the jps maintenance team urgent
Non-Outage | J.E.26.07.29397 | C001874102 | Nickolas Rodriques | St.Catherine | Completed | Load_240957 | Twickenham - 210 | 2026-08-04 13:19 | 2026-08-04 15:59 | 2026-08-04 18:46 | 2026-08-04 18:47 | 2026-08-04 19:08 | 2026-08-04 19:38 | 2026-08-04 19:42 | 2026-08-04 19:42 |  |  | Fair | No | Customer stated that he’s experiencing unstable voltage, reading found (112). Two one-bolt clamps were replaced at pothead. Current reading (113). The customer confirmed that all is well now.
Non-Outage | J.E.26.08.06706 | C001874108 | Elvis Trowers |  | Completed |  |  | 2026-08-04 13:26 | 2026-08-04 13:27 | 2026-08-04 14:31 | 2026-08-04 14:31 | 2026-08-04 14:41 | 2026-08-04 14:44 | 2026-08-04 14:44 | 2026-08-04 14:44 |  |  | Fair | Yes | Premises not located and customer could not be contacted by telephone either after several calls, and there’s no fix address.
Outage | J.E.26.08.04337 | C001874112 | Rodclif Dawkins | Portmore | Completed | Load_268062 | Naggo Head - 510 | 2026-08-04 13:31 | 2026-08-04 16:04 | 2026-08-04 21:47 | 2026-08-04 22:11 | 2026-08-04 22:11 | 2026-08-04 22:11 | 2026-08-04 22:12 | 2026-08-04 22:12 |  |  | Fair | No | Calls to number provided for association went unanswered to voicemail mail.
Outage | J.E.26.08.06902 | C001874124 | Cliton Henry | St.Ann | Completed | Load_269586 | Upper White River - 110 | 2026-08-04 13:44 | 2026-08-04 15:11 | 2026-08-04 15:28 | 2026-08-04 15:28 | 2026-08-04 16:26 | 2026-08-04 16:45 | 2026-08-04 16:49 | 2026-08-04 16:49 |  |  | Fair | No | A blown 30 amp junction fuse found at Wood Park Square towards Derry due to tree contact. The branch was removed and supply restored using 1- 30 amp fuse
Outage | J.E.26.08.06865 | C001874130 | Damion Reid | Manchester | Completed | Load_1002354 | Spur Tree - 310 | 2026-08-04 13:52 | 2026-08-04 13:54 | 2026-08-04 13:57 | 2026-08-04 13:58 | 2026-08-04 14:18 | 2026-08-04 15:14 | 2026-08-04 15:19 | 2026-08-04 15:19 | BrokenPole |  | Fair | No | Fire not from JPS action isolate line section to assist fire team with extinguished the fire
Non-Outage | J.E.26.08.06851 | C001874144 | Hopeton Henry | St.Thomas | Completed | Load_257871 | Good Year - 110 | 2026-08-04 14:03 | 2026-08-04 14:04 | 2026-08-05 09:26 | 2026-08-05 12:32 | 2026-08-05 13:11 | 2026-08-05 13:12 | 2026-08-05 13:12 | 2026-08-05 13:12 |  |  | Fair | No | Premises closed,
Non-Outage | J.E.26.08.06893 | C001874145 | Hopeton Henry | St.Thomas | Completed | Load_270158 | Lysson - 410 | 2026-08-04 14:03 | 2026-08-04 14:04 | 2026-08-05 09:26 | 2026-08-05 11:47 | 2026-08-05 11:46 | 2026-08-05 12:31 | 2026-08-05 12:32 | 2026-08-05 12:32 | LowHangingWires |  | Fair | No | Remove retired service wire
Non-Outage | J.E.26.08.05809 | C001874164 | Denton Williams | Portland | Completed | Load_241315 | Port Antonio - 410 | 2026-08-04 14:21 | 2026-08-04 14:29 | 2026-08-04 16:27 | 2026-08-04 16:27 | 2026-08-04 16:27 | 2026-08-04 16:46 | 2026-08-04 16:54 | 2026-08-04 16:54 | LowHangingWires |  | Fair | No | Disconnect and remove service line that encroached on customer property. Also, wire was hanging on the customer zinc fence which was causing fire.The affected customer was advised to relocate meter within 100ft from JPS lines. Customer meter is approximately 400ft from JPS service lines. Advise was given.
Non-Outage | J.E.26.08.05455 | C001874174 | Denton Williams |  | Completed |  |  | 2026-08-04 14:30 | 2026-08-04 14:31 | 2026-08-04 16:17 | 2026-08-04 16:18 | 2026-08-04 16:17 | 2026-08-04 16:19 | 2026-08-04 16:26 | 2026-08-04 16:26 | BrokenPole |  | Fair | No | Dead end pole( with T) open secondary wires badly rotten. We are recommending a pole replacement. Refer to Portland maintenance.
Outage | J.E.26.08.07004 | C001874177 | Dean- Smith | Hanover | Completed | Load_239783 | Orange Bay - 310 | 2026-08-04 14:34 | 2026-08-04 19:03 | 2026-08-04 22:37 | 2026-08-04 22:38 | 2026-08-04 22:37 | 2026-08-04 22:38 | 2026-08-04 22:39 | 2026-08-04 22:39 | BrokenWire |  | Fair | No | Area was restored
Non-Outage | J.E.26.08.06218 | C001874207 | Cliton Henry | St.Ann | Completed | Load_240033 | Upper White River - 110 | 2026-08-04 15:11 | 2026-08-04 15:12 | 2026-08-04 16:52 | 2026-08-04 16:53 | 2026-08-04 17:39 | 2026-08-04 17:46 | 2026-08-04 17:46 | 2026-08-04 17:46 | LowHangingWires |  | Fair | No | Two (2) 35-c6 wood pole found leaning and cause the primary and the secondary conductors to hang low. Kindly refer to St. Mary Operations to straighten poles and raise conductors.
Non-Outage | J.E.26.08.06332 | C001874206 | Cliton Henry | St.Mary | Completed | Load_576565 | Oracabessa - 210 | 2026-08-04 15:11 | 2026-08-04 15:12 | 2026-08-04 17:47 | 2026-08-04 17:48 | 2026-08-04 17:50 | 2026-08-04 19:08 | 2026-08-04 19:15 | 2026-08-04 19:15 |  |  | Fair | No | The customer for Meter # 2240423 was advised to get a licensed electrician to check private line to customer house.
Non-Outage | J.E.26.08.06632 | C001874205 | Cliton Henry | St.Mary | Completed | Load_350817 | Oracabessa - 110 | 2026-08-04 15:11 | 2026-08-04 15:12 | 2026-08-04 19:19 | 2026-08-04 19:19 | 2026-08-04 20:06 | 2026-08-04 20:43 | 2026-08-04 20:44 | 2026-08-04 20:44 |  |  | Fair | No | A burnt off neutral conductor found was reconnected using 1- one bolt clamp. Voltages left 119-119/238 volts.
Non-Outage | J.E.26.08.06984 | C001874208 | Cliton Henry |  | Completed |  |  | 2026-08-04 15:11 | 2026-08-04 15:12 | 2026-08-04 20:52 | 2026-08-04 20:56 | 2026-08-04 20:56 | 2026-08-04 21:03 | 2026-08-04 21:03 | 2026-08-04 21:03 | LowHangingWires |  | Fair | No | Broken pole leaning in a tree with secondary conductors. Kindly refer St.Mary Operations for a replacement.
Non-Outage | J.E.26.08.06471 | C001874209 | Omar King | St.Ann | Completed | Load_555714 | Roaring River - 210 | 2026-08-04 15:13 | 2026-08-04 15:14 | 2026-08-04 16:23 | 2026-08-04 16:24 | 2026-08-04 18:09 | 2026-08-04 18:09 | 2026-08-04 18:09 | 2026-08-04 18:09 |  |  | Fair | No | Problem as been resolved
Outage | J.E.26.08.06840 | C001874217 | Richard Samuda | Manchester | Completed | Load_244764 | Kendal - 310 | 2026-08-04 15:16 | 2026-08-04 15:19 | 2026-08-04 15:27 | 2026-08-04 16:32 | 2026-08-04 17:06 | 2026-08-04 05:44 | 2026-08-04 17:45 | 2026-08-04 17:45 |  |  | Fair | No | Reconnect jumper that was broken causing area to experience single phasing voltage 112, 111 223
Outage | J.E.26.08.07086 | C001874224 | Javid Vernon | Westmoreland | Completed | Load_244541 | Paradise - 310 | 2026-08-04 15:20 | 2026-08-04 15:25 | 2026-08-04 17:35 | 2026-08-04 17:36 | 2026-08-04 17:36 | 2026-08-04 17:37 | 2026-08-04 17:37 | 2026-08-04 17:37 |  |  | Fair | No | Related to previous call job #07099
Outage | J.E.26.08.07087 | C001874222 | Javid Vernon | Westmoreland | Completed | Load_266113 | Paradise - 310 | 2026-08-04 15:20 | 2026-08-04 15:25 | 2026-08-04 17:38 | 2026-08-04 17:38 | 2026-08-04 18:33 | 2026-08-04 18:59 | 2026-08-04 19:01 | 2026-08-04 19:01 |  |  | Fair | No | Refuse one 8amp junction fuse and one 25kva transformer use 3amp fuse voltage left at transformer 110/110/220
Outage | J.E.26.08.07099 | C001874223 | Javid Vernon | Westmoreland | Completed | Load_252131 | Paradise - 310 | 2026-08-04 15:20 | 2026-08-04 15:25 | 2026-08-04 15:37 | 2026-08-04 15:38 | 2026-08-04 16:12 | 2026-08-04 17:33 | 2026-08-04 17:34 | 2026-08-04 17:34 |  |  | Rains | No | Refuse one 50amp junction fuse
Outage | J.E.26.08.07066 | C001874225 | Javid Vernon | Westmoreland | Completed | Load_270152 | Paradise - 310 | 2026-08-04 15:21 | 2026-08-04 15:25 | 2026-08-04 17:35 | 2026-08-04 17:35 | 2026-08-04 17:35 | 2026-08-04 17:35 | 2026-08-04 17:36 | 2026-08-04 17:36 |  |  | Fair | No | Related to previous call job #07099
Outage | J.E.26.08.06834 | C001874226 | Javid Vernon | Westmoreland | Completed | Load_256259 | Paradise - 310 | 2026-08-04 15:22 | 2026-08-04 15:25 | 2026-08-04 22:06 | 2026-08-04 22:07 | 2026-08-04 22:42 | 2026-08-04 22:50 | 2026-08-04 22:50 | 2026-08-04 22:50 |  |  | Fair | No | Premises check and found okay customer stated that the power was restored
Outage | J.E.26.08.05188 | C001874228 | Eric Williams | KSAN | Completed | Load_258537 | Washington Blvd - 610 | 2026-08-04 15:24 | 2026-08-04 15:25 | 2026-08-04 16:29 | 2026-08-04 16:35 | 2026-08-04 17:12 | 2026-08-04 20:48 | 2026-08-04 20:57 | 2026-08-04 20:57 |  |  | Fair | No | Change 200 ft burnt triplex at castle heights using 6 - one bolt clamps 1 - #2 pree-form, section restored.
Outage | J.E.26.08.06835 | C001874234 | Marlon Authors | Manchester | Completed | Load_264309 | Spur Tree - 210 | 2026-08-04 15:26 | 2026-08-04 15:27 | 2026-08-04 16:57 | 2026-08-04 16:57 | 2026-08-04 16:57 | 2026-08-04 16:58 | 2026-08-04 16:58 | 2026-08-04 16:58 |  |  | Fair | No | Customer said she reset the breaker and supply restored
Outage | J.E.26.08.06901 | C001874236 | Stephen Taylor | St.Thomas | Completed | Load_244001 | Good Year - 110 | 2026-08-04 15:28 | 2026-08-04 15:29 | 2026-08-04 18:02 | 2026-08-04 18:03 | 2026-08-04 19:09 | 2026-08-04 19:09 | 2026-08-04 19:10 | 2026-08-04 19:10 |  |  | Fair | No | Customer meter socket defective and need to be change by a technician of jps
Outage | J.E.26.08.06906 | C001874237 | Stephen Taylor | St.Thomas | Completed | Load_244777 | Good Year - 110 | 2026-08-04 15:28 | 2026-08-04 15:29 | 2026-08-04 15:53 | 2026-08-04 15:53 | 2026-08-04 17:59 | 2026-08-04 17:59 | 2026-08-04 18:01 | 2026-08-04 18:01 | LeaningPole |  | Fair | No | Patrol area and power is in the area but dere is a lean cable & wireless pole found leaning in the area
Outage | J.E.26.08.06970 | C001874241 | Kaydon Taylor | KSAN | Completed | Load_246237 | Constant Spring - 410 | 2026-08-04 15:29 | 2026-08-04 15:31 | 2026-08-04 17:42 | 2026-08-04 17:55 | 2026-08-04 18:15 | 2026-08-04 18:43 | 2026-08-04 18:43 | 2026-08-04 18:43 | BrokenWire |  | Fair | No | One clamp at pothead V 114-115-238
Outage | J.E.26.08.07097 | C001874240 | Eric Williams | KSAN | Completed | Load_248765 | West Kings House - 410 | 2026-08-04 15:29 | 2026-08-04 15:31 | 2026-08-04 21:22 | 2026-08-04 21:22 | 2026-08-04 21:45 | 2026-08-04 21:51 | 2026-08-04 21:51 | 2026-08-04 21:51 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.06539 | C001874242 | Shamour Haughton | St.James | Completed | Load_249176 | Bogue - 310 | 2026-08-04 15:31 | 2026-08-04 15:33 | 2026-08-04 17:06 | 2026-08-04 17:06 | 2026-08-04 17:06 | 2026-08-04 17:06 | 2026-08-04 17:07 | 2026-08-04 17:07 |  |  | Fair | No | Related to previous call
Outage | J.E.26.08.06593 | C001874243 | Shamour Haughton | St.James | Completed | Load_247422 | Bogue - 310 | 2026-08-04 15:31 | 2026-08-04 15:33 | 2026-08-04 18:01 | 2026-08-04 18:01 | 2026-08-04 18:01 | 2026-08-04 18:01 | 2026-08-04 18:01 | 2026-08-04 18:01 |  |  | Fair | No | Related to previous call
Outage | J.E.26.08.06846 | C001874249 | Shamour Haughton | St.James | Completed | Load_249176 | Bogue - 310 | 2026-08-04 15:31 | 2026-08-04 15:33 | 2026-08-04 17:52 | 2026-08-04 17:53 | 2026-08-04 17:52 | 2026-08-04 17:52 | 2026-08-04 17:53 | 2026-08-04 17:53 |  |  | Fair | No | Related to previous call
Outage | J.E.26.08.06891 | C001874248 | Hartley Chin | Clarendon | Completed | Load_249917 | Parnassus - 210 | 2026-08-04 15:31 | 2026-08-04 15:44 | 2026-08-04 17:42 | 2026-08-04 17:42 | 2026-08-04 17:42 | 2026-08-04 17:42 | 2026-08-04 17:42 | 2026-08-04 17:42 |  |  | Fair | No | Call related to 05120
Outage | J.E.26.08.07012 | C001874244 | Derrick Dawkins | St.James | Completed | Load_253305 | Bogue - 610 | 2026-08-04 15:31 | 2026-08-04 15:49 | 2026-08-04 20:50 | 2026-08-04 20:51 | 2026-08-04 21:06 | 2026-08-04 22:00 | 2026-08-04 22:00 | 2026-08-04 22:00 | BangingWires |  | Fair | No | Found 1 phase secondary burned down due to vehicle accident open 50 kva transformer to carry out repairs splice and retention used 2 pg clamp no pole # available
Outage | J.E.26.08.07098 | C001874245 | Shamour Haughton | St.James | Completed | Load_264619 | Bogue - 310 | 2026-08-04 15:31 | 2026-08-04 15:33 | 2026-08-04 19:12 | 2026-08-04 19:12 | 2026-08-04 19:26 | 2026-08-04 19:27 | 2026-08-04 19:29 | 2026-08-04 19:29 |  |  | Fair | No | Found 1,25kva tripped, reset 25kva
Outage | J.E.26.08.07101 | C001874247 | Shamour Haughton | St.James | Completed | Load_267894 | Bogue - 310 | 2026-08-04 15:31 | 2026-08-04 15:33 | 2026-08-04 18:00 | 2026-08-04 18:00 | 2026-08-04 18:00 | 2026-08-04 18:00 | 2026-08-04 18:01 | 2026-08-04 18:01 |  |  | Fair | No | Related to previous call
Outage | J.E.26.08.06572 | C001874253 | Hartley Chin | Clarendon | Completed | Load_251249 | Monymusk - 410 | 2026-08-04 15:32 | 2026-08-04 15:42 | 2026-08-04 17:45 | 2026-08-04 17:45 | 2026-08-04 19:34 | 2026-08-04 19:35 | 2026-08-04 19:42 | 2026-08-04 19:42 |  |  | Fair | No | Found ok. Customer made a report about a broken pole and conductor on ground. Line patrolled and found ok on Gibraltar Street. Customer made report for sister.
Outage | J.E.26.08.06639 | C001874251 | Shamour Haughton | St.James | Completed | Load_269068 | Bogue - 310 | 2026-08-04 15:32 | 2026-08-04 15:33 | 2026-08-04 17:55 | 2026-08-04 17:55 | 2026-08-04 17:55 | 2026-08-04 17:55 | 2026-08-04 17:55 | 2026-08-04 17:55 |  |  | Fair | No | Related to previous call
Outage | J.E.26.08.06966 | C001874250 | Shamour Haughton | St.James | Completed | Load_1001936 | Bogue - 310 | 2026-08-04 15:32 | 2026-08-04 15:33 | 2026-08-04 19:31 | 2026-08-04 19:31 | 2026-08-04 19:31 | 2026-08-04 19:31 | 2026-08-04 19:32 | 2026-08-04 19:32 |  |  | Fair | No | Related to previous call
Outage | J.E.26.08.06241 | C001874254 | Hartley Chin | Clarendon | Completed | Load_267388 | Parnassus - 310 | 2026-08-04 15:33 | 2026-08-04 15:41 | 2026-08-04 21:13 | 2026-08-04 21:16 | 2026-08-04 21:48 | 2026-08-04 21:49 | 2026-08-04 21:52 | 2026-08-04 21:52 |  |  | Fair | No | Unable to contact customer area patrolled found meter and found ok
Outage | J.E.26.08.06865 | C001874256 | Richard Samuda | Manchester | Completed | Load_1002354 | Spur Tree - 310 | 2026-08-04 15:35 | 2026-08-04 15:35 | 2026-08-04 15:51 | 2026-08-04 15:52 | 2026-08-04 16:25 | 2026-08-04 04:27 | 2026-08-04 16:27 | 2026-08-04 16:27 | BrokenPole |  | Fair | No | Pole does not belong to jps pole belong to cable company
Non-Outage | J.E.26.08.05002 | C001874260 | Daniel Francis | St.Ann | Completed | Load_250070 | Cardiff Hall - 310 | 2026-08-04 15:36 | 2026-08-04 15:38 | 2026-08-04 18:46 | 2026-08-04 18:46 | 2026-08-04 19:30 | 2026-08-04 19:51 | 2026-08-04 19:54 | 2026-08-04 19:54 |  |  | Fair | No | Found ok voltage 206/117/116/239/233/238/
Non-Outage | J.E.26.08.05149 | C001874257 | Daniel Francis | St.Ann | Completed | Load_260188 | Cardiff Hall - 210 | 2026-08-04 15:36 | 2026-08-04 15:38 | 2026-08-04 21:02 | 2026-08-04 21:03 | 2026-08-04 22:16 | 2026-08-04 22:17 | 2026-08-04 22:19 | 2026-08-04 22:19 |  |  | Fair | No | Remade secondary jumper phase
Non-Outage | J.E.26.08.05321 | C001874259 | Richard Samuda | Manchester | Completed | Load_246342 | Porus - 310 | 2026-08-04 15:36 | 2026-08-04 15:41 | 2026-08-04 17:47 | 2026-08-04 17:47 | 2026-08-04 18:16 | 2026-08-04 06:17 | 2026-08-04 18:17 | 2026-08-04 18:17 |  |  | Fair | No | Call to phone no answer premises not found
Non-Outage | J.E.26.08.06307 | C001874261 | Richard Samuda | Manchester | Completed | Load_1002354 | Spur Tree - 310 | 2026-08-04 15:36 | 2026-08-04 15:41 | 2026-08-04 16:28 | 2026-08-04 16:28 | 2026-08-04 16:28 | 2026-08-04 04:29 | 2026-08-04 16:29 | 2026-08-04 16:29 | Fire |  | Fair | No | Customer said they didn’t make a call
Non-Outage | J.E.26.08.06374 | C001874258 | Daniel Francis | St.Ann | Completed | Load_266408 | Cardiff Hall - 210 | 2026-08-04 15:36 | 2026-08-04 15:38 | 2026-08-04 19:56 | 2026-08-04 19:57 | 2026-08-04 20:59 | 2026-08-04 21:00 | 2026-08-04 21:02 | 2026-08-04 21:02 |  |  | Fair | No | Un able to located customer not answering phone
Non-Outage | J.E.26.08.02290 | C001874264 | Andrew Henderson | St.Ann | Completed | Load_263239 | Cardiff Hall - 210 | 2026-08-04 15:36: 2026-08-04 15:37; 2026-08-04 15:38: 2026-08-04 15:43; 2026-08-04 21:02: 2026-08-04 16:10; 2026-08-04 21:02: 2026-08-04 16:10
Non-Outage | J.E.26.08.04452 | C001874263 | Andrew Henderson | St.Ann | Completed | Load_245502 | Cardiff Hall - 210 | 2026-08-04 15:36: 2026-08-04 15:37; 2026-08-04 15:38: 2026-08-04 15:42; 2026-08-04 21:02: 2026-08-04 16:05; 2026-08-04 21:02: 2026-08-04 16:05
Non-Outage | J.E.26.08.04625 | C001874262 | Daniel Francis | St.Ann | Completed | Load_1007080 | Cardiff Hall - 210 | 2026-08-04 15:37 | 2026-08-04 15:38 | 2026-08-04 17:43 | 2026-08-04 17:43 | 2026-08-04 17:43 | 2026-08-04 18:39 | 2026-08-04 18:44 | 2026-08-04 18:44 |  |  | Fair | No | Remade joint at pothead voltage 118/117/235 customer still experiencing dim&brite customer connect Lin hexing box
Non-Outage | J.E.26.08.06183 | C001874265 | Neville Spencer |  | Completed |  |  | 2026-08-04 15:37 | 2026-08-04 15:40 | 2026-08-04 15:44 | 2026-08-04 15:45 | 2026-08-04 18:42 | 2026-08-04 20:06 | 2026-08-04 20:12 | 2026-08-04 20:12 |  |  | Fair | No | Found defective x for switch change used 1, drop out switch,Also renew blown 8 amp J/ fuse at pole # 036390 area restored
Non-Outage | J.E.26.08.03616 | C001874267 | Ryan Richards | Manchester | Completed | Load_237809 | Kendal - 210 | 2026-08-04 15:38 | 2026-08-04 15:41 | 2026-08-04 16:10 | 2026-08-04 16:10 | 2026-08-04 18:30 | 2026-08-04 19:14 | 2026-08-04 19:15 | 2026-08-04 19:15 |  |  | Fair | No | 8 customer at the end of the line having low voltage line was checked 1 neutral splicing sleeve found corroded splicing sleeve was jumped out voltage 113/109/222 volts all customers supply now working ok
Outage | J.E.26.08.05677 | C001874266 | Hartley Chin | Clarendon | Completed | Load_249917 | Parnassus - 210 | 2026-08-04 15:38 | 2026-08-04 15:40 | 2026-08-04 17:36 | 2026-08-04 17:36 | 2026-08-04 17:36 | 2026-08-04 17:36 | 2026-08-04 17:37 | 2026-08-04 17:37 |  |  | Fair | No | Call related to 05120
Non-Outage | J.E.26.08.00867 | C001874269 | Ryan Richards | Manchester | Completed | Load_254054 | Kendal - 210 | 2026-08-04 15:39 | 2026-08-04 15:41 | 2026-08-04 19:15 | 2026-08-04 19:16 | 2026-08-04 21:11 | 2026-08-04 22:31 | 2026-08-04 23:31 | 2026-08-04 23:31 |  |  | Fair | No | Rotten service wire found replace 70ft#6 triplex 3 penunion 2 one bolt clamps voltage 111/113/224 volts
Outage | J.E.26.08.07090 | C001874273 | Floyd Taylor | Trelawny | Completed | Load_1001716 | Greenwood - 210 | 2026-08-04 15:42 | 2026-08-04 15:45 | 2026-08-04 15:56 | 2026-08-04 15:56 | 2026-08-04 16:49 | 2026-08-04 17:14 | 2026-08-04 17:15 | 2026-08-04 17:15 |  |  | Fair | No | Found the area with light resident say power went in the area but it as returned
Outage | J.E.26.08.06554 | C001874277 | Floyd Taylor | Trelawny | Completed | Load_261119 | Greenwood - 110 | 2026-08-04 15:43 | 2026-08-04 15:45 | 2026-08-04 20:32 | 2026-08-04 20:33 | 2026-08-04 21:05 | 2026-08-04 21:05 | 2026-08-04 21:05 | 2026-08-04 21:05 |  |  | Fair | No | Customer say power was restored
Outage | J.E.26.08.06697 | C001874274 | Floyd Taylor | Trelawny | Completed | Load_243986 | Greenwood - 110 | 2026-08-04 15:43 | 2026-08-04 15:45 | 2026-08-04 21:06 | 2026-08-04 21:07 | 2026-08-04 21:33 | 2026-08-04 21:54 | 2026-08-04 21:55 | 2026-08-04 21:55 |  |  | Fair | No | Remake joint at pole using 1 pg clamps voltage readings left 114,117,231
Outage | J.E.26.08.06573 | C001874279 | Floyd Taylor | Trelawny | Completed | Load_258502 | Greenwood - 110 | 2026-08-04 15:44 | 2026-08-04 15:45 | 2026-08-04 18:17 | 2026-08-04 18:17 | 2026-08-04 18:19 | 2026-08-04 18:20 | 2026-08-04 18:20 | 2026-08-04 18:20 |  |  | Fair | No | Found customer with light
Outage | J.E.26.08.06615 | C001874278 | Floyd Taylor | Trelawny | Completed | Load_248030 | Greenwood - 110 | 2026-08-04 15:44 | 2026-08-04 15:45 | 2026-08-04 19:09 | 2026-08-04 19:09 | 2026-08-04 20:05 | 2026-08-04 20:30 | 2026-08-04 20:32 | 2026-08-04 20:32 |  |  | Fair | No | Splice and retention customer service wire service using about 20ft#6 voltage readings left 116,115,234
Outage | J.E.26.08.06205 | C001874285 | Hartley Chin | Clarendon | Completed | Load_238810 | Parnassus - 310 | 2026-08-04 15:45 | 2026-08-04 15:45 | 2026-08-04 21:15 | 2026-08-04 21:52 | 2026-08-04 22:14 | 2026-08-04 22:47 | 2026-08-04 22:47 | 2026-08-04 22:47 |  |  | Fair | No | Found ok
Outage | J.E.26.08.04881 | C001874291 | Nickolas Rodriques | St.Catherine | Completed | Load_254806 | Twickenham - 210 | 2026-08-04 15:47 | 2026-08-04 15:51 | 2026-08-04 17:58 | 2026-08-04 17:59 | 2026-08-04 18:21 | 2026-08-04 18:44 | 2026-08-04 18:46 | 2026-08-04 18:46 |  |  | Fair | No | Customer confirmed that the area outage was restored.
Outage | J.E.26.08.04884 | C001874290 | Nickolas Rodriques | St.Catherine | Completed | Load_240832 | Twickenham - 210 | 2026-08-04 15:47 | 2026-08-04 15:51 | 2026-08-04 16:01 | 2026-08-04 16:19 | 2026-08-04 16:56 | 2026-08-04 17:06 | 2026-08-04 17:08 | 2026-08-04 17:08 |  |  | Fair | No | Found customer wither electricity. Customer confirmed that the power outage was restored.
Outage | J.E.26.08.04885 | C001874289 | Nickolas Rodriques | St.Catherine | Completed | Load_238469 | Twickenham - 210 | 2026-08-04 15:47 | 2026-08-04 15:51 | 2026-08-04 17:09 | 2026-08-04 17:17 | 2026-08-04 17:33 | 2026-08-04 17:43 | 2026-08-04 17:51 | 2026-08-04 17:51 |  |  | Fair | No | Customer was located and confirmed that the power outage was restored.
Outage | J.E.26.08.05063 | C001874288 | Nickolas Rodriques | St.Catherine | Completed | Load_265092 | Twickenham - 210 | 2026-08-04 15:47 | 2026-08-04 15:51 | 2026-08-05 09:44 | 2026-08-05 09:45 | 2026-08-05 10:01 | 2026-08-05 10:24 | 2026-08-05 10:26 | 2026-08-05 10:26 |  |  | Fair | No | Customer was located and confirmed that the power was restored by another team.
Outage | J.E.26.08.06080 | C001874287 | Nickolas Rodriques | St.Catherine | Completed | Load_267949 | Twickenham - 210 | 2026-08-04 15:47 | 2026-08-04 15:51 | 2026-08-04 22:08 | 2026-08-04 22:09 | 2026-08-04 22:30 | 2026-08-04 22:42 | 2026-08-04 22:43 | 2026-08-04 22:43 |  |  | Fair | No | Found premises with electricity. Customer was contacted and confirmed that the power was restored.
Outage | J.E.26.08.06546 | C001874286 | Delano Gayle | St.Catherine | Completed | Load_254806 | Twickenham - 210 | 2026-08-04 15:47 | 2026-08-05 00:01 | 2026-08-05 02:29 | 2026-08-05 02:29 | 2026-08-05 02:37 | 2026-08-05 02:37 | 2026-08-05 02:38 | 2026-08-05 02:38 |  |  | Fair | No | Premises found okay power was restored
Outage | J.E.26.08.02404 | C001874294 | Nickolas Rodriques | St.Catherine | Completed | Load_260019 | Naggo Head - 510 | 2026-08-04 15:48 | 2026-08-04 15:51 | 2026-08-05 11:29 | 2026-08-05 11:31 | 2026-08-05 12:34 | 2026-08-05 12:53 | 2026-08-05 12:55 | 2026-08-05 12:55 |  |  | Fair | No | Unable to communicate with the customer after several attempts.
Outage | J.E.26.08.04754 | C001874293 | Nickolas Rodriques | St.Catherine | Completed | Load_250314 | Twickenham - 210 | 2026-08-04 15:48 | 2026-08-04 15:51 | 2026-08-05 12:56 | 2026-08-05 12:56 | 2026-08-05 13:26 | 2026-08-05 13:36 | 2026-08-05 13:49 | 2026-08-05 13:49 |  |  | Fair | No | Customer stated that she is without electricity. Checks were done and it was found that the customer service wires from meter is burnt. Reading found at pothead (114-116-230). Isolate service wire for safety. Customer was advised to consult an electrician to do repairs.
Outage | J.E.26.08.03920 | C001874295 | Nickolas Rodriques | St.Catherine | Completed | Load_250931 | Twickenham - 210 | 2026-08-04 15:49 | 2026-08-04 15:51 | 2026-08-04 21:44 | 2026-08-04 21:44 | 2026-08-04 22:02 | 2026-08-04 22:06 | 2026-08-04 22:07 | 2026-08-04 22:07 |  |  | Fair | No | The area outage was restored.
Outage | J.E.26.08.04072 | C001874296 | Nickolas Rodriques | St.Catherine | Completed | Load_240390 | Twickenham - 210 | 2026-08-04 15:49 | 2026-08-04 15:51 | 2026-08-04 21:00 | 2026-08-04 21:00 | 2026-08-04 21:26 | 2026-08-04 21:42 | 2026-08-04 21:43 | 2026-08-04 21:43 |  |  | Fair | No | Customer was located and confirmed that the power outage was restored.
Outage | J.E.26.08.05180 | C001874298 | Nickolas Rodriques | St.Catherine | Completed | Load_245769 | Twickenham - 210 | 2026-08-04 15:49 | 2026-08-04 15:51 | 2026-08-04 19:42 | 2026-08-04 19:44 | 2026-08-04 20:03 | 2026-08-04 20:48 | 2026-08-04 20:59 | 2026-08-04 20:59 |  |  | Fair | No | Checked and found a 10 amp junction fuse blown and a 5 amp transformer fuse blown. Patrol and found nothing on line. Repaired by replacing the fuses after completing patrol.
Outage | J.E.26.08.06317 | C001874301 | Shamour Haughton | St.James | Completed | Load_242384 | Bogue - 310 | 2026-08-04 15:53 | 2026-08-04 15:56 | 2026-08-04 19:36 | 2026-08-04 19:36 | 2026-08-04 19:36 | 2026-08-04 19:36 | 2026-08-04 19:37 | 2026-08-04 19:37 |  |  | Fair | No | Customer states that they didn’t make a report
Outage | J.E.26.08.06560 | C001874300 | Shamour Haughton | St.James | Completed | Load_249162 | Bogue - 310 | 2026-08-04 15:53 | 2026-08-04 15:56 | 2026-08-04 17:54 | 2026-08-04 17:54 | 2026-08-04 17:54 | 2026-08-04 17:54 | 2026-08-04 17:54 | 2026-08-04 17:54 |  |  | Fair | No | Related to previous call
Outage | J.E.26.08.07137 | C001874305 | Delano Gayle | St.Catherine | Completed | Load_242587 | Twickenham - 210 | 2026-08-04 15:55 | 2026-08-04 23:15 | 2026-08-05 05:42 | 2026-08-05 05:43 | 2026-08-05 05:59 | 2026-08-05 06:06 | 2026-08-05 06:06 | 2026-08-05 06:06 |  |  | Fair | No | Premises found okay power was restored
Outage | J.E.26.08.06461 | C001874307 | Derrick Dawkins | St.James | Completed | Load_254053 | Bogue - 510 | 2026-08-04 15:59 | 2026-08-04 16:00 | 2026-08-04 18:31 | 2026-08-04 18:36 | 2026-08-04 18:59 | 2026-08-04 19:00 | 2026-08-04 19:01 | 2026-08-04 19:01 |  |  | Fair | No | Customer stated he didn’t make a report
Outage | J.E.26.08.06535 | C001874310 | Floyd Taylor | St.James | Completed | Load_267183 | Rose Hall - 110 | 2026-08-04 16:01 | 2026-08-04 17:50 | 2026-08-04 18:21 | 2026-08-04 18:21 | 2026-08-04 18:52 | 2026-08-04 19:07 | 2026-08-04 19:09 | 2026-08-04 19:09 |  |  | Fair | No | Clean and remake joints at pothead voltage readings left 117,119,236
Outage | J.E.26.08.07132 | C001874312 | Floyd Taylor | Trelawny | Completed | Load_247137 | Greenwood - 210 | 2026-08-04 16:03 | 2026-08-04 16:08 | 2026-08-04 17:16 | 2026-08-04 17:16 | 2026-08-04 18:00 | 2026-08-04 18:16 | 2026-08-04 18:17 | 2026-08-04 18:17 |  |  | Fair | No | Customer having internal issues voltage readings left 116,115,234
Outage | J.E.26.08.05030 | C001874313 | Rodclif Dawkins | Portmore | Completed | Load_576155 | Naggo Head - 610 | 2026-08-04 16:04 | 2026-08-04 16:08 | 2026-08-04 19:10 | 2026-08-04 19:11 | 2026-08-04 19:11 | 2026-08-04 19:11 | 2026-08-04 19:12 | 2026-08-04 19:12 |  |  | Fair | No | Please refer to Moses Elleston, customer is prepaid
Outage | J.E.26.08.05135 | C001874314 | Rodclif Dawkins | Portmore | Completed | Load_266533 | Naggo Head - 510 | 2026-08-04 16:04 | 2026-08-04 16:08 | 2026-08-04 19:12 | 2026-08-04 19:40 | 2026-08-04 20:45 | 2026-08-04 20:55 | 2026-08-04 20:59 | 2026-08-04 20:59 |  |  | Fair | No | Found triplex #6 service wire supplying 2, 3wire customer with wrapped joints at pothead. Using 7 penunion joints remade
Outage | J.E.26.08.05206 | C001874315 | Rodclif Dawkins | Portmore | Completed | Load_240584 | Naggo Head - 510 | 2026-08-04 16:04 | 2026-08-04 16:08 | 2026-08-04 21:53 | 2026-08-04 22:36 | 2026-08-04 22:46 | 2026-08-04 22:46 | 2026-08-04 22:47 | 2026-08-04 22:47 |  |  | Fair | No | Customer found okay
Non-Outage | J.E.26.08.00052 | C001874316 | Junior Scarlett | St.James | Completed | Load_268573 | Queens Drive - 710 | 2026-08-04 16:05 | 2026-08-04 16:06 | 2026-08-04 16:23 | 2026-08-04 16:24 | 2026-08-04 16:32 | 2026-08-04 05:18 | 2026-08-04 17:19 | 2026-08-04 17:19 |  |  | Fair | No | Corrosion at pole and potheadInstall 3 clampInstall 3 pen unionVoltage found 115v 101v 220vVoltage leave 115v 115v 230vJob completed
Outage | J.E.26.08.05348 | C001874319 | Rodclif Dawkins | Portmore | Completed | Load_244789 | Naggo Head - 510 | 2026-08-04 16:06 | 2026-08-04 16:08 | 2026-08-04 19:12 | 2026-08-04 21:21 | 2026-08-04 21:48 | 2026-08-04 22:10 | 2026-08-04 22:10 | 2026-08-04 22:10 |  |  | Fair | No | Customer found okay
Outage | J.E.26.08.06736 | C001874317 | Dean- Smith | Hanover | Completed | Load_292318 | Orange Bay - 310 | 2026-08-04 16:06 | 2026-08-04 16:07 | 2026-08-04 22:42 | 2026-08-04 22:42 | 2026-08-04 22:42 | 2026-08-04 22:42 | 2026-08-04 22:43 | 2026-08-04 22:43 |  |  | Fair | No | Unable to locate
Outage | J.E.26.08.07153 | C001874318 | Dean- Smith | Hanover | Completed | Load_303169 | Orange Bay - 210 | 2026-08-04 16:06 | 2026-08-04 16:07 | 2026-08-04 16:21 | 2026-08-04 16:21 | 2026-08-04 18:46 | 2026-08-04 18:46 | 2026-08-04 19:24 | 2026-08-04 19:24 |  |  | Fair | No | Found, Spool broken , conductor in conductor with grounding on concrete pole... corrected same by replacing pool and grounding wire. Replace 8amp 100kva transformer fuse. Pole number n/a
Outage | J.E.26.08.05735 | C001874320 | Rodclif Dawkins | Portmore | Completed | Load_269887 | Naggo Head - 510 | 2026-08-04 16:07 | 2026-08-04 16:10 | 2026-08-04 19:13 | 2026-08-04 22:48 | 2026-08-04 22:47 | 2026-08-04 22:48 | 2026-08-04 22:50 | 2026-08-04 22:50 | BrokenPole |  | Fair | No | Found 30/6 pole broken. However new pole was erected and conductors transferred to it, pole top cut and pole tied to new pole. Third party communication cables are still anchored on pole along with citizen security camera
Outage | J.E.26.08.06755 | C001874321 | Rodclif Dawkins | Portmore | Completed | Load_243335 | Naggo Head - 610 | 2026-08-04 16:07 | 2026-08-04 16:10 | 2026-08-04 19:23 | 2026-08-04 22:13 | 2026-08-04 22:34 | 2026-08-04 22:34 | 2026-08-04 22:35 | 2026-08-04 22:35 |  |  | Fair | No | Customer found okay
Outage | J.E.26.08.06816 | C001874322 | Rodclif Dawkins | Portmore | Completed | Load_261160 | Naggo Head - 510 | 2026-08-04 16:07 | 2026-08-04 16:10 | 2026-08-04 19:13 | 2026-08-04 21:00 | 2026-08-04 21:00 | 2026-08-04 21:00 | 2026-08-04 21:18 | 2026-08-04 21:18 | Fire |  | Fair | No | Found slack guy wire. Guy wire was defective, so it was removed . Please refer to maintenance to have guy replaced .
Outage | J.E.26.08.07106 | C001874323 | Rodclif Dawkins | Portmore | Completed | Load_268747 | Naggo Head - 510 | 2026-08-04 16:07 | 2026-08-04 16:10 | 2026-08-04 19:34 | 2026-08-04 22:51 | 2026-08-04 22:51 | 2026-08-04 22:51 | 2026-08-04 22:55 | 2026-08-04 22:55 |  |  | Fair | No | Daylight attention required. Crew observed switch top jumper broken from arrester top, which is located on cross arm. Also 2 blown fuse observed Live line technique required for job.
Non-Outage | J.E.26.08.02418 | C001874330 | Delano Gayle |  | Completed |  |  | 2026-08-04 16:11 | 2026-08-04 23:15 | 2026-08-05 03:41 | 2026-08-05 03:42 | 2026-08-05 05:28 | 2026-08-05 05:42 | 2026-08-05 05:42 | 2026-08-05 05:42 |  |  | Fair | No | Premises not found no answer from customer phone
Non-Outage | J.E.26.08.04384 | C001874334 | Rodclif Dawkins |  | Completed |  |  | 2026-08-04 16:12 | 2026-08-04 16:17 | 2026-08-04 19:24 | 2026-08-04 19:24 | 2026-08-04 19:24 | 2026-08-04 19:24 | 2026-08-04 19:25 | 2026-08-04 19:25 |  |  | Fair | No | Refer to Moses Elleston. Prepaid customer
Non-Outage | J.E.26.08.04883 | C001874333 | Delano Gayle |  | Completed |  |  | 2026-08-04 16:12 | 2026-08-04 23:15 | 2026-08-05 02:38 | 2026-08-05 02:39 | 2026-08-05 02:55 | 2026-08-05 02:58 | 2026-08-05 02:58 | 2026-08-05 02:58 |  |  | Fair | No | Premises found okay power restored
Outage | J.E.26.08.03187 | C001874331 | Delano Gayle |  | Completed | Load_289527 | Twickenham - 210 | 2026-08-04 16:12 | 2026-08-04 23:15 | 2026-08-05 02:59 | 2026-08-05 03:00 | 2026-08-05 03:35 | 2026-08-05 03:41 | 2026-08-05 03:41 | 2026-08-05 03:41 |  |  | Fair | No | Premises/area found okay
Non-Outage | J.E.26.07.37070 | C001874342 | Michael Paterson |  | Completed |  |  | 2026-08-04 16:25 | 2026-08-04 16:26 | 2026-08-04 17:54 | 2026-08-04 17:55 | 2026-08-04 18:23 | 2026-08-04 18:24 | 2026-08-04 18:24 | 2026-08-04 18:24 | Fire |  | Fair | No | Customer confirm ok via phone call
Non-Outage | J.E.26.02.24215 | C001874347 | Oshane Warren | Westmoreland | Completed | Load_249830 | Paradise - 110 | 2026-08-04 16:27 | 2026-08-04 16:29 | 2026-08-04 16:40 | 2026-08-04 16:40 | 2026-08-04 16:40 | 2026-08-04 16:40 | 2026-08-04 16:40 | 2026-08-04 16:40 |  |  | Rains | No | Check and find ok
Non-Outage | J.E.26.02.26115 | C001874345 | Oshane Warren | Westmoreland | Completed | Load_249830 | Paradise - 110 | 2026-08-04 16:27 | 2026-08-04 16:29 | 2026-08-04 16:42 | 2026-08-04 16:43 | 2026-08-04 16:42 | 2026-08-04 16:43 | 2026-08-04 16:43 | 2026-08-04 16:43 |  |  | Rains | No | Customer states that matter is resolved
Non-Outage | J.E.26.02.36128 | C001874346 | Oshane Warren | Westmoreland | Completed | Load_292031 | Orange Bay - 310 | 2026-08-04 16:27 | 2026-08-04 16:30 | 2026-08-04 22:59 | 2026-08-04 22:59 | 2026-08-04 22:59 | 2026-08-04 22:59 | 2026-08-04 22:59 | 2026-08-04 22:59 |  |  | Rains | No | Unable to locate or contact customer
Non-Outage | J.E.26.03.08459 | C001874344 | Oshane Warren | Westmoreland | Completed | Load_266295 | Orange Bay - 310 | 2026-08-04 16:27 | 2026-08-04 16:30 | 2026-08-04 16:54 | 2026-08-04 16:54 | 2026-08-04 16:54 | 2026-08-04 16:54 | 2026-08-04 16:55 | 2026-08-04 16:55 |  |  | Rains | No | Check and find ok
Non-Outage | J.E.26.08.03881 | C001874343 | Dwayne Cohen | KSAS | Completed | Load_237666 | Greenwich - 310 | 2026-08-04 16:27 | 2026-08-05 08:12 | 2026-08-05 08:20 | 2026-08-05 08:20 | 2026-08-05 08:57 | 2026-08-05 09:29 | 2026-08-05 09:30 | 2026-08-05 09:30 |  |  | Fair | No | Change defective arrester and refuse blown 5amps transformer link, supply now restore.
Non-Outage | J.E.26.08.04391 | C001874348 | Edward Royal | KSAS | Completed | Load_250004 | Hunts Bay - 510 | 2026-08-04 16:28 | 2026-08-04 16:29 | 2026-08-04 17:31 | 2026-08-04 17:32 | 2026-08-04 17:31 | 2026-08-04 17:32 | 2026-08-04 17:32 | 2026-08-04 17:32 |  |  | Fair | No | Replaced 15A transformer fuse
Non-Outage | J.E.26.02.23646 | C001874349 | Oshane Warren | Westmoreland | Completed | Load_258236 | Paradise - 110 | 2026-08-04 16:29 | 2026-08-04 16:30 | 2026-08-04 16:38 | 2026-08-04 16:38 | 2026-08-04 16:38 | 2026-08-04 16:38 | 2026-08-04 16:38 | 2026-08-04 16:38 |  |  | Rains | No | Check and find ok
Non-Outage | J.E.26.08.06480 | C001874351 | Omar King | St.Ann | Completed | Load_245610 | Roaring River - 210 | 2026-08-04 16:32 | 2026-08-04 16:33 | 2026-08-04 18:09 | 2026-08-04 18:10 | 2026-08-04 19:15 | 2026-08-04 19:16 | 2026-08-04 19:17 | 2026-08-04 19:17 |  |  | Fair | No | Unable to find customer call several times no answer directions not sufficient
Non-Outage | J.E.26.08.06486 | C001874352 | Omar King | St.Ann | Completed | Load_253430 | Roaring River - 210 | 2026-08-04 16:32 | 2026-08-04 16:33 | 2026-08-04 20:11 | 2026-08-04 20:12 | 2026-08-04 21:03 | 2026-08-04 22:09 | 2026-08-04 22:10 | 2026-08-04 22:10 |  |  | Fair | No | Found customer service wire broken from secondary line as been repaired customer is now with supply
Non-Outage | J.E.26.08.07080 | C001874350 | Omar King | St.Ann | Completed | Load_247974 | Roaring River - 210 | 2026-08-04 16:32 | 2026-08-04 16:33 | 2026-08-04 19:17 | 2026-08-04 19:17 | 2026-08-04 20:07 | 2026-08-04 20:11 | 2026-08-04 20:11 | 2026-08-04 20:11 |  |  | Fair | No | After reaching the location I do a voltage reading at customer meter socket. Reading show 110-108-219 V . I advise customer to use electrician to resolve matter
Outage | J.E.26.08.06737 | C001874355 | Kemark Slue | St.Catherine | Completed | Load_263003 | New Michelton - 410 | 2026-08-04 16:35 | 2026-08-04 16:48 | 2026-08-04 18:49 | 2026-08-04 18:49 | 2026-08-04 20:28 | 2026-08-04 21:58 | 2026-08-04 23:05 | 2026-08-04 23:05 |  | Y | Fair | No | Upon arrival at the location the crew discovered that a 10 amps junction fuse for a single line section was blown, further patrol revealed that a bamboo tree had made contact with the said primary conductor after another junction that had a 10 D fuse that was changed to a 8 K, remove bamboo tree, refuse main junction and re-energized line section.
Non-Outage | J.E.26.08.05743 | C001874357 | Rodclif Dawkins |  | Completed |  |  | 2026-08-04 16:36 | 2026-08-04 16:49 | 2026-08-04 19:23 | 2026-08-04 19:32 | 2026-08-04 19:32 | 2026-08-04 19:32 | 2026-08-04 19:32 | 2026-08-04 19:32 | Fire |  | Fair | No | Calls went to voicemail. Unable to locate premises
Outage | J.E.26.08.05194 | C001874361 | Christopher West | St.Catherine | Completed | Load_265584 | Tredegar - 510 | 2026-08-04 16:36 | 2026-08-05 09:31 | 2026-08-05 15:03 | 2026-08-05 15:04 | 2026-08-05 15:03 | 2026-08-05 15:03 | 2026-08-05 15:04 | 2026-08-05 15:04 |  |  | Fair | No | Assign to evening crew
Outage | J.E.26.08.05340 | C001874360 | Richard Grant | St.Catherine | Completed | Load_253596 | New Michelton - 210 | 2026-08-04 16:36 | 2026-08-05 07:54 | 2026-08-05 08:25 | 2026-08-05 08:25 | 2026-08-05 09:27 | 2026-08-05 10:09 | 2026-08-05 10:09 | 2026-08-05 10:09 |  |  | Fair | No | Checks revealed customer meter has been discontinued for nonpayment. Customer was advised.
Outage | J.E.26.08.06630 | C001874358 | Milton Charlton | KSAS | Completed | Load_259337 | Rockfort - 210 | 2026-08-04 16:36 | 2026-08-04 20:40 | 2026-08-04 20:52 | 2026-08-04 20:54 | 2026-08-04 21:57 | 2026-08-04 22:00 | 2026-08-04 21:58 | 2026-08-04 21:58 | Fire |  | Fair | No | Found okay upon arrival. No fire seen on premises.
Outage | J.E.26.08.07102 | C001874364 | Donald Cunningham | St.Catherine | Completed | Load_568118 | Rhodens Pen - 210 | 2026-08-04 16:37 | 2026-08-04 16:45 | 2026-08-04 21:15 | 2026-08-04 21:15 | 2026-08-04 21:59 | 2026-08-04 21:59 | 2026-08-04 22:05 | 2026-08-04 22:05 |  |  | Fair | No | Premises closed customer not reachable
Outage | J.E.26.08.07140 | C001874363 | Hartley Chin | St.Catherine | Completed | Load_245394 | Rhodens Pen - 310 | 2026-08-04 16:37 | 2026-08-04 16:44 | 2026-08-04 19:48 | 2026-08-04 19:48 | 2026-08-04 20:40 | 2026-08-04 21:12 | 2026-08-04 21:13 | 2026-08-04 21:13 |  |  | Fair | No | Damage service wire. Change approximately 80ft of #2 triplex
Outage | J.E.26.08.07160 | C001874362 | Richard Grant | St.Catherine | Completed | Load_259127 | Tredegar - 310 | 2026-08-04 16:37 | 2026-08-05 11:10 | 2026-08-05 13:53 | 2026-08-05 13:53 | 2026-08-05 14:23 | 2026-08-05 14:24 | 2026-08-05 14:24 | 2026-08-05 14:24 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.06886 | C001874365 | Donald Cunningham | St.Catherine | Completed | Load_250865 | Rhodens Pen - 210 | 2026-08-04 16:38 | 2026-08-04 16:45 | 2026-08-04 18:59 | 2026-08-04 19:00 | 2026-08-04 20:58 | 2026-08-04 20:58 | 2026-08-04 21:14 | 2026-08-04 21:14 |  |  | Fair | No | Corroded phase by pole corrected one clamp use voltage readings by meter socket 116 volt
Non-Outage | J.E.26.08.06820 | C001874366 | Richard Nicholas |  | Completed |  |  | 2026-08-04 16:40 | 2026-08-04 16:45 | 2026-08-04 22:55 | 2026-08-04 22:55 | 2026-08-04 23:20 | 2026-08-04 23:20 | 2026-08-04 23:22 | 2026-08-04 23:22 |  |  | Fair | No | Customer is unable to add credit to the prepaid rammy account,please refer to Mr.moses.customer is expecting to have baby this week and is asking for urgent help.
Outage | J.E.26.08.04619 | C001874367 | Donald Cunningham | St.Catherine | Completed | Load_262964 | Rhodens Pen - 410 | 2026-08-04 16:41 | 2026-08-04 16:45 | 2026-08-04 17:22 | 2026-08-04 17:22 | 2026-08-04 18:52 | 2026-08-04 18:56 | 2026-08-04 18:57 | 2026-08-04 18:57 |  |  | Fair | No | Premises closed customer not reachable
Outage | J.E.26.08.06745 | C001874379 | Edward Royal | KSAS | Completed | Load_244650 | Hunts Bay - 310 | 2026-08-04 16:47 | 2026-08-05 08:33 | 2026-08-05 10:30 | 2026-08-05 10:31 | 2026-08-05 10:30 | 2026-08-05 10:50 | 2026-08-05 10:51 | 2026-08-05 10:51 |  |  | Fair | No | Replaced 2 15A junction fuse
Outage | J.E.26.08.06836 | C001874378 | Edward Royal | KSAS | Completed | Load_247227 | Hunts Bay - 510 | 2026-08-04 16:47 | 2026-08-05 09:24 | 2026-08-05 15:50 | 2026-08-05 16:49 | 2026-08-05 16:48 | 2026-08-05 16:49 | 2026-08-05 16:49 | 2026-08-05 16:49 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.06837 | C001874377 | Rusean Allen | KSAS | Completed | Load_256732 | Hunts Bay - 310 | 2026-08-04 16:47 | 2026-08-05 09:12 | 2026-08-05 12:32 | 2026-08-05 12:33 | 2026-08-05 12:36 | 2026-08-05 12:36 | 2026-08-05 12:37 | 2026-08-05 12:37 |  |  | Fair | No | Found okay
Outage | J.E.26.08.07174 | C001874386 | Denton Williams | Portland | Completed | Load_250602 | Port Antonio - 410 | 2026-08-04 16:49 | 2026-08-04 16:50 | 2026-08-04 16:55 | 2026-08-04 16:59 | 2026-08-04 16:59 | 2026-08-04 16:59 | 2026-08-04 17:02 | 2026-08-04 17:02 |  |  | Fair | No | Customer confirmed that electrical supply has been restored at site. Maintenance team was having a planned power outage in the area.
Non-Outage | J.E.26.08.04854 | C001874387 | Michael Paterson | Westmoreland | Completed | Load_267763 | Paradise - 210 | 2026-08-04 16:51 | 2026-08-04 16:53 | 2026-08-04 19:02 | 2026-08-04 20:04 | 2026-08-04 20:04 | 2026-08-04 20:13 | 2026-08-04 20:14 | 2026-08-04 20:14 |  |  | Fair | No | Assessment done at location, voltage readings taken, 96v, 100v, 196v, customer resides in a lane six pole span from 25kva xfmr, total customer count In lane 40, this doesn’t not include illegal connections, total customer count on circuit 70, please refer to Mr Eglan Richard’s, matter needs urgent attention.
Non-Outage | J.E.26.08.06248 | C001874389 | Michael Paterson | Westmoreland | Completed | Load_241658 | Paradise - 210 | 2026-08-04 16:51 | 2026-08-04 16:53 | 2026-08-04 20:14 | 2026-08-04 20:15 | 2026-08-04 20:14 | 2026-08-04 20:17 | 2026-08-04 20:17 | 2026-08-04 20:17 |  |  | Fair | No | Assessment done at location, found meter damage, meter single phasing, voltage reading 120v, 120v, 240v, please refer to Mr Chessane Beckford at paradise to address matter speedily.
Non-Outage | J.E.26.08.06424 | C001874390 | Michael Paterson | Westmoreland | Completed | Load_247902 | Paradise - 210 | 2026-08-04 16:51 | 2026-08-04 16:53 | 2026-08-04 18:46 | 2026-08-04 18:46 | 2026-08-04 18:46 | 2026-08-04 18:46 | 2026-08-04 18:49 | 2026-08-04 18:49 |  |  | Fair | No | Customer mentioned that his request was resolved, he mentioned that he want his account disconnected as he is no longer operating business at this location.
Non-Outage | J.E.26.08.06613 | C001874391 | Michael Paterson | Westmoreland | Completed | Load_242476 | Paradise - 210 | 2026-08-04 16:51 | 2026-08-04 16:53 | 2026-08-04 21:59 | 2026-08-04 21:59 | 2026-08-04 22:02 | 2026-08-04 22:03 | 2026-08-04 22:03 | 2026-08-04 22:03 |  |  | Fair | No | Customer confirm ok, via phone call
Non-Outage | J.E.26.08.06708 | C001874392 | Michael Paterson | Westmoreland | Completed | Load_238020 | Paradise - 210 | 2026-08-04 16:51 | 2026-08-04 16:53 | 2026-08-04 20:59 | 2026-08-04 21:01 | 2026-08-04 21:00 | 2026-08-04 21:01 | 2026-08-04 21:03 | 2026-08-04 21:03 |  |  | Fair | No | Customer request day light attention, premise close, no one home.
Outage | J.E.26.08.07164 | C001874393 | Milton Charlton | KSAS | Completed | Load_254338 | Greenwich - 410 | 2026-08-04 16:51 | 2026-08-04 16:54 | 2026-08-04 17:55 | 2026-08-04 17:59 | 2026-08-04 18:34 | 2026-08-04 18:35 | 2026-08-04 18:36 | 2026-08-04 18:36 |  |  | Fair | No | Found two 3 amps transformer fuse blown at pole #0181062. Refused using two 3 amps fuse and reclosed transformer switches.
Outage | J.E.26.08.07172 | C001874388 | Edward Royal | KSAS | Completed | Load_248083 | Greenwich - 410 | 2026-08-04 16:51 | 2026-08-04 20:40 | 2026-08-04 20:46 | 2026-08-04 20:47 | 2026-08-04 20:46 | 2026-08-04 22:12 | 2026-08-04 22:39 | 2026-08-04 22:39 |  |  | Fair | No | Spliced and reconnected primary line using 60ft open number 2 conductor and 4 single bolt clamp
Non-Outage | J.E.26.08.06800 | C001874394 | Michael Paterson | Westmoreland | Completed | Load_247661 | Paradise - 210 | 2026-08-04 16:52 | 2026-08-04 16:53 | 2026-08-04 18:54 | 2026-08-04 18:54 | 2026-08-04 20:01 | 2026-08-04 20:02 | 2026-08-04 20:02 | 2026-08-04 20:02 |  |  | Fair | No | Reconnection completed,voltage reading, 120v, 120v, 240v.
Outage | J.E.26.08.07208 | C001874399 | Derrick Dawkins | St.James | Completed | Load_262376 | Bogue - 510 | 2026-08-04 16:54 | 2026-08-04 16:56 | 2026-08-04 18:36 | 2026-08-04 19:01 | 2026-08-04 19:36 | 2026-08-04 20:07 | 2026-08-04 20:07 | 2026-08-04 20:07 | BrokenWire |  | Fair | No | Found neutral burn off due to banging wire clean and remade joint use 1 pg clamp voltage 119/119=238
Non-Outage | J.E.26.08.04081 | C001874401 | Delano Gayle |  | Completed |  |  | 2026-08-04 16:57 | 2026-08-04 23:15 | 2026-08-05 02:58 | 2026-08-05 02:59 | 2026-08-05 02:59 | 2026-08-05 02:59 | 2026-08-05 02:59 | 2026-08-05 02:59 | BangingWires |  | Fair | No | Premises found okay
Non-Outage | J.E.26.08.07170 | C001874416 | Kaydon Taylor |  | Completed |  |  | 2026-08-04 17:25 | 2026-08-04 20:07 | 2026-08-04 20:29 | 2026-08-04 21:36 | 2026-08-04 22:23 | 2026-08-04 22:23 | 2026-08-04 22:23 | 2026-08-04 22:23 | BrokenWire |  | Fair | No | Daylight attention
Outage | J.E.26.08.07242 | C001874417 | Richard Samuda | Manchester | Completed | Load_268058 | Spur Tree - 310 | 2026-08-04 17:28 | 2026-08-04 17:29 | 2026-08-04 18:18 | 2026-08-04 18:35 | 2026-08-04 18:56 | 2026-08-04 06:57 | 2026-08-04 18:57 | 2026-08-04 18:57 |  |  | Fair | No | Call to phone no answer premises not found
Non-Outage | J.E.26.08.03848 | C001874419 | Clyde Brown | St.Catherine | Completed | Load_254206 | Rhodens Pen - 310 | 2026-08-04 17:30 | 2026-08-05 07:48 | 2026-08-05 08:44 | 2026-08-05 09:33 | 2026-08-05 10:30 | 2026-08-05 11:16 | 2026-08-05 11:24 | 2026-08-05 11:24 |  |  | Fair | No | Corroded joints at pothead and secondary line connection remade with 6 -clamps,voltage left 113/113 and 226V
Outage | J.E.26.08.07193 | C001874420 | Stephen Taylor | St.Thomas | Completed | Load_252203 | Good Year - 210 | 2026-08-04 17:31 | 2026-08-04 17:33 | 2026-08-04 19:19 | 2026-08-04 19:20 | 2026-08-04 19:19 | 2026-08-04 19:20 | 2026-08-04 19:20 | 2026-08-04 19:20 |  |  | Fair | No | Contact customer and customer say that power is back now and okay
Outage | J.E.26.08.07133 | C001874422 | Javid Vernon | Westmoreland | Completed | Load_292735 | Paradise - 310 | 2026-08-04 17:33 | 2026-08-04 17:36 | 2026-08-04 20:56 | 2026-08-04 20:57 | 2026-08-04 21:47 | 2026-08-04 22:00 | 2026-08-04 22:02 | 2026-08-04 22:02 |  |  | Fair | No | Area check and found okay unable to locate customer and premises phone calls to customer number went unanswered and no good directions were given
Outage | J.E.26.08.07134 | C001874423 | Javid Vernon | Westmoreland | Completed | Load_246302 | Paradise - 310 | 2026-08-04 17:33 | 2026-08-04 17:36 | 2026-08-04 19:06 | 2026-08-04 19:07 | 2026-08-04 20:17 | 2026-08-04 20:51 | 2026-08-04 20:52 | 2026-08-04 20:52 |  |  | Fair | No | Replace 80ft #6 triplex wire and use 4 clamps voltage left 113/115/228
Outage | J.E.26.08.07248 | C001874421 | Oshane Warren | Westmoreland | Completed | Load_570234 | Paradise - 110 | 2026-08-04 17:33 | 2026-08-04 17:37 | 2026-08-04 21:20 | 2026-08-04 22:58 | 2026-08-04 22:58 | 2026-08-04 22:58 | 2026-08-04 22:58 | 2026-08-04 22:58 |  |  | Rains | No | Customer needs to carry out repair in order to get reconnected
Outage | J.E.26.08.07205 | C001874426 | Dean- Smith | Hanover | Completed | Load_252846 | Orange Bay - 210 | 2026-08-04 17:42 | 2026-08-04 17:43 | 2026-08-04 19:25 | 2026-08-04 19:26 | 2026-08-04 19:58 | 2026-08-04 19:58 | 2026-08-04 19:58 | 2026-08-04 19:58 |  |  | Fair | No
Outage | J.E.26.08.04813 | C001874429 | Radcliffe Coleman | St.Catherine | Completed | Load_260620 | Tredegar - 410 | 2026-08-04 17:57 | 2026-08-05 08:39 | 2026-08-05 09:32 | 2026-08-05 09:33 | 2026-08-05 10:01 | 2026-08-05 10:33 | 2026-08-05 10:41 | 2026-08-05 10:41 |  |  | Fair | No | Two blown fuse (5A) were found at the location for a bank of three (3-50kva). The bank was checked and no visible fault found. The same value fuses found were replaced and location left okay.
Outage | J.E.26.08.07292 | C001874435 | Richard Grant | St.Catherine | Completed | Load_302434 | New Michelton - 410 | 2026-08-04 18:15 | 2026-08-05 07:55 | 2026-08-05 12:54 | 2026-08-05 12:54 | 2026-08-05 13:52 | 2026-08-05 13:53 | 2026-08-05 13:53 | 2026-08-05 13:53 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.07295 | C001874434 | Richard Grant | St.Catherine | Completed | Load_268424 | New Michelton - 410 | 2026-08-04 18:15 | 2026-08-05 07:55 | 2026-08-05 11:11 | 2026-08-05 11:12 | 2026-08-05 11:41 | 2026-08-05 11:41 | 2026-08-05 11:41 | 2026-08-05 11:41 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.07296 | C001874433 | Richard Grant | St.Catherine | Completed | Load_248088 | New Michelton - 410 | 2026-08-04 18:15 | 2026-08-05 07:56 | 2026-08-05 10:09 | 2026-08-05 10:10 | 2026-08-05 11:02 | 2026-08-05 11:11 | 2026-08-05 11:11 | 2026-08-05 11:11 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.07302 | C001874436 | Romeo Brissett | St.James | Completed | Load_292851 | Bogue - 610 | 2026-08-04 18:17 | 2026-08-04 22:19 | 2026-08-04 23:36 | 2026-08-04 23:37 | 2026-08-05 00:35 | 2026-08-05 01:30 | 2026-08-05 01:34 | 2026-08-05 01:34 |  |  | Fair | No | Cut and removed bamboo, replaced (1)10amps junction fuse
Non-Outage | J.E.26.08.05760 | C001874441 | Michael Christian | St.James | Completed | Load_243792 | Queens Drive - 710 | 2026-08-04 18:20 | 2026-08-04 18:23 | 2026-08-04 20:04 | 2026-08-04 20:05 | 2026-08-04 20:45 | 2026-08-04 20:58 | 2026-08-04 20:58 | 2026-08-04 20:58 |  |  | Fair | No | Internal fault voltage 110 109 220 at meter
Non-Outage | J.E.26.08.07047 | C001874438 | Michael Christian | St.James | Completed | Load_257366 | Queens Drive - 710 | 2026-08-04 18:20 | 2026-08-04 18:23 | 2026-08-04 18:43 | 2026-08-04 18:44 | 2026-08-04 19:20 | 2026-08-04 19:23 | 2026-08-04 19:23 | 2026-08-04 19:23 |  |  | Fair | No | Not found call customer answer
Non-Outage | J.E.26.08.07166 | C001874437 | Michael Christian | St.James | Completed | Load_246347 | Queens Drive - 710 | 2026-08-04 18:20 | 2026-08-04 18:23 | 2026-08-04 19:24 | 2026-08-04 19:24 | 2026-08-04 19:56 | 2026-08-04 20:04 | 2026-08-04 20:04 | 2026-08-04 20:04 |  |  | Fair | No | Check and found okay voltage 112 111 223 at pothead
Non-Outage | J.E.26.08.07290 | C001874443 | Derrick Dawkins | St.James | Completed | Load_302133 | Bogue - 610 | 2026-08-04 18:21 | 2026-08-04 18:24 | 2026-08-04 20:07 | 2026-08-04 20:08 | 2026-08-04 20:27 | 2026-08-04 20:43 | 2026-08-04 20:44 | 2026-08-04 20:44 |  |  | Fair | No | Found transformer fuse blown 25 kva due to vegetation replace a 3 amp fuse
Non-Outage | J.E.26.08.06504 | C001874446 | Shamour Haughton |  | Completed |  |  | 2026-08-04 18:27 | 2026-08-04 20:07 | 2026-08-04 20:31 | 2026-08-04 20:36 | 2026-08-04 21:33 | 2026-08-04 21:33 | 2026-08-04 21:33 | 2026-08-04 21:33 | BangingWires |  | Fair | No | No fire found at location , area has power
Outage | J.E.26.08.06556 | C001874449 | Shamour Haughton | St.James | Completed | Load_289673 | Bogue - 310 | 2026-08-04 18:27 | 2026-08-04 18:28 | 2026-08-04 19:10 | 2026-08-04 19:10 | 2026-08-04 19:10 | 2026-08-04 19:10 | 2026-08-04 19:10 | 2026-08-04 19:10 |  |  | Fair | No | Related to previous call
Outage | J.E.26.08.06830 | C001874447 | Shamour Haughton | St.James | Completed | Load_266423 | Bogue - 310 | 2026-08-04 18:27 | 2026-08-04 18:28 | 2026-08-04 19:39 | 2026-08-04 19:40 | 2026-08-04 20:03 | 2026-08-04 20:04 | 2026-08-04 20:04 | 2026-08-04 20:04 |  |  | Fair | No | Check and found area with light, customer number going voicemail
Outage | J.E.26.08.06961 | C001874448 | Shamour Haughton | St.James | Completed | Load_254099 | Bogue - 310 | 2026-08-04 18:27 | 2026-08-04 18:28 | 2026-08-04 20:21 | 2026-08-04 20:21 | 2026-08-04 20:21 | 2026-08-04 20:21 | 2026-08-04 20:22 | 2026-08-04 20:22 |  |  | Fair | No | Unable to locate customer, cell number went unanswered after several attempts
Non-Outage | J.E.26.08.05130 | C001874450 | Michael Christian | St.James | Completed | Load_246347 | Queens Drive - 710 | 2026-08-04 18:29 | 2026-08-04 18:30 | 2026-08-04 20:59 | 2026-08-04 21:00 | 2026-08-04 21:28 | 2026-08-04 21:34 | 2026-08-04 21:34 | 2026-08-04 21:34 |  |  | Fair | No | Found customer service wire broken cause by cable men use 2 clamps voltage 111 112 223 at meter
Outage | J.E.26.08.07303 | C001874454 | Marlon Authors | Manchester | Completed | Load_249149 | Spur Tree - 210 | 2026-08-04 18:52 | 2026-08-04 18:54 | 2026-08-04 21:28 | 2026-08-04 21:29 | 2026-08-04 21:50 | 2026-08-04 22:37 | 2026-08-04 22:37 | 2026-08-04 22:37 |  |  | Fair | No | Supply checked and found service wire neutral broken at pothead. Repair same using three linkets, supply leave working okay rdg 112v,108v and cross phased 220 volts
Non-Outage | J.E.26.08.07344 | C001874456 | Dean- Smith |  | Completed |  |  | 2026-08-04 19:02 | 2026-08-04 20:04 | 2026-08-04 22:40 | 2026-08-04 22:41 | 2026-08-04 22:40 | 2026-08-04 22:40 | 2026-08-04 22:41 | 2026-08-04 22:41 | BrokenWire |  | Fair | No | Area was restored
Outage | J.E.26.08.07299 | C001874457 | Milton Charlton | KSAS | Completed | Load_254591 | Greenwich - 410 | 2026-08-04 19:11 | 2026-08-04 19:12 | 2026-08-04 20:43 | 2026-08-04 20:44 | 2026-08-04 20:44 | 2026-08-04 20:45 | 2026-08-04 20:51 | 2026-08-04 20:51 |  |  | Fair | No | Found one 25 amps, one 15 amps junction fuse at pole# ( no pole#) and one 10 amps, one 5 amps transformer fuse at pole # 0079148. Refuse using one 25 amps, one 15, one 10 amps and 5 amps fuses and reclosed both junction and both transformers switches.
Outage | J.E.26.08.07323 | C001874459 | Kaydon Taylor | KSAN | Completed | Load_240017 | Constant Spring - 410 | 2026-08-04 19:19 | 2026-08-04 19:32 | 2026-08-04 19:57 | 2026-08-04 21:34 | 2026-08-04 21:34 | 2026-08-04 21:35 | 2026-08-04 21:35 | 2026-08-04 21:35 |  |  | Fair | No | Premises not located
Outage | J.E.26.08.07127 | C001874460 | Clyde Brown | Clarendon | Completed | Load_265466 | Parnassus - 210 | 2026-08-04 19:20 | 2026-08-05 07:48 | 2026-08-05 08:44 | 2026-08-05 13:14 | 2026-08-05 16:10 | 2026-08-05 16:10 | 2026-08-05 16:17 | 2026-08-05 16:17 |  |  | Fair | No | Defective meter socket need to be change ,customer advised,voltage 114V in meter socket.
Outage | J.E.26.08.07272 | C001874462 | Nickolas Rodriques | KSAS | Completed | Load_254412 | Duhaney - 210 | 2026-08-04 19:26 | 2026-08-05 08:11 | 2026-08-05 13:49 | 2026-08-05 13:50 | 2026-08-05 14:09 | 2026-08-05 15:27 | 2026-08-05 15:29 | 2026-08-05 15:29 | BrokenWire |  | Fair | No | Checked and found a 25 KVA transformer tripped caused by #2 twisted contacting where connections are. Repaired by clearing the wire and energized the transformer after completing patrol.
Non-Outage | J.E.26.08.07426 | C001874467 | Romeo Brissett |  | Completed |  |  | 2026-08-04 19:52 | 2026-08-04 22:19 | 2026-08-05 01:34 | 2026-08-05 01:35 | 2026-08-05 01:34 | 2026-08-05 01:28 | 2026-08-05 01:35 | 2026-08-05 01:35 |  |  | Fair | No | Check and found ok
Outage | J.E.26.08.06476 | C001874468 | Shamour Haughton | St.James | Completed | Load_301752 | Bogue - 310 | 2026-08-04 19:52 | 2026-08-04 19:54 | 2026-08-04 20:06 | 2026-08-04 20:06 | 2026-08-04 20:15 | 2026-08-04 20:15 | 2026-08-04 20:15 | 2026-08-04 20:15 |  |  | Fair | No | Check and found okay
Outage | J.E.26.08.07398 | C001874470 | Dean- Smith | Hanover | Completed | Load_242732 | Orange Bay - 310 | 2026-08-04 19:55 | 2026-08-04 19:56 | 2026-08-04 20:09 | 2026-08-04 20:10 | 2026-08-04 21:29 | 2026-08-04 21:29 | 2026-08-04 22:36 | 2026-08-04 22:36 | BrokenWire |  | Fair | No | Truck broke #2 triplex service wire, repair same. Opened and closed 25kva transformer to do repair. Voltage left 120v,120v,240v.
Outage | J.E.26.08.07458 | C001874474 | Neville Spencer | Clarendon | Completed | Load_348670 | May Pen - 110 | 2026-08-04 20:12 | 2026-08-04 20:16 | 2026-08-04 20:26 | 2026-08-04 20:27 | 2026-08-04 20:50 | 2026-08-04 20:51 | 2026-08-04 21:01 | 2026-08-04 21:01 | Fire |  | Fair | No | Found 35 c 6 wooden leaning badly, construction C V with single phase primary line and open secondary. Conductor very low across road way pole NEED to guy urgently. Need guy block and rod.
Non-Outage | J.E.26.08.05724 | C001874475 | Neville Spencer | Clarendon | Completed | Load_241202 | May Pen - 110 | 2026-08-04 20:14 | 2026-08-04 20:16 | 2026-08-04 21:03 | 2026-08-04 21:04 | 2026-08-04 21:40 | 2026-08-04 21:40 | 2026-08-04 21:44 | 2026-08-04 21:44 |  |  | Fair | No | Premises closed.
Outage | J.E.26.08.07409 | C001874484 | Kenroy Dale | Manchester | Completed | Load_241983 | Kendal - 210 | 2026-08-04 20:30 | 2026-08-05 07:12 | 2026-08-05 07:40 | 2026-08-05 07:57 | 2026-08-05 09:23 | 2026-08-05 10:40 | 2026-08-05 10:53 | 2026-08-05 10:53 |  |  | Fair | No | Open 25 kva transformer to splice and retention 2 span of secondary neutral transformer re-closed and area now with supply (cross country line)
Outage | J.E.26.08.07479 | C001874485 | Nickolas Rodriques | St.Catherine | Completed | Load_240686 | Twickenham - 210 | 2026-08-04 20:33 | 2026-08-05 08:07 | 2026-08-05 16:12 | 2026-08-05 16:12 | 2026-08-05 17:00 | 2026-08-05 17:30 | 2026-08-05 17:30 | 2026-08-05 17:30 | BrokenWire |  | Fair | No | Checked and found customer without electricity caused by defective service wire. Repaired by replacing 40 ft of #6 twisted using two service sleeves and four clamps, current reading is (117-117-234).
Outage | J.E.26.08.07214 | C001874503 | Roxroy Needham | St.Ann | Completed | Load_252832 | Cardiff Hall - 210 | 2026-08-04 21:17 | 2026-08-05 00:45 | 2026-08-05 00:56 | 2026-08-05 01:03 | 2026-08-05 01:03 | 2026-08-05 01:03 | 2026-08-05 01:05 | 2026-08-05 01:05 |  |  | Fair | No | Premises found ok call customer Wayne habbib and he say JPS team came before and the light is ok
Outage | J.E.26.08.07357 | C001874504 | Daniel Francis | St.Ann | Completed | Load_245873 | Cardiff Hall - 210 | 2026-08-04 21:17 | 2026-08-04 21:18 | 2026-08-04 22:19 | 2026-08-04 22:20 | 2026-08-04 22:32 | 2026-08-04 22:57 | 2026-08-04 23:02 | 2026-08-04 23:02 |  |  | Fair | No | Patrol and renew junction fu at pole# 616430 two 25amp
Outage | J.E.26.08.06698 | C001874507 | Milton Charlton | KSAS | Completed | Load_266992 | Cane River - 410 | 2026-08-04 21:30 | 2026-08-04 21:34 | 2026-08-04 21:58 | 2026-08-04 21:59 | 2026-08-04 22:27 | 2026-08-04 22:30 | 2026-08-04 22:30 | 2026-08-04 22:30 |  |  | Fair | No | Found three 10 amps transformer fuse blown at pole # ( no pole #). Refused using three 10 amps fuse and reclosed all three transformer switches.
Outage | J.E.26.08.07484 | C001874522 | Christopher Edwards | KSAS | Completed | Load_574063 | Cane River - 410 | 2026-08-04 22:00 | 2026-08-04 22:03 | 2026-08-04 23:53 | 2026-08-05 02:04 | 2026-08-05 02:09 | 2026-08-05 02:09 | 2026-08-05 02:10 | 2026-08-05 02:10 |  |  | Fair | No | Premises not located
Outage | J.E.26.08.07180 | C001874527 | Christopher Edwards | KSAS | Completed | Load_246603 | Rockfort - 210 | 2026-08-04 22:05 | 2026-08-04 22:07 | 2026-08-04 23:41 | 2026-08-04 23:49 | 2026-08-04 23:49 | 2026-08-04 23:52 | 2026-08-04 23:53 | 2026-08-04 23:53 |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Outage | J.E.26.08.07298 | C001874526 | Christopher Edwards | KSAS | Completed | Load_250013 | Rockfort - 210 | 2026-08-04 22:05 | 2026-08-04 22:07 | 2026-08-04 22:13 | 2026-08-04 22:28 | 2026-08-04 23:05 | 2026-08-04 23:48 | 2026-08-04 23:48 | 2026-08-04 23:48 |  |  | Fair | No | Refuse blown junction fuseUsing (1) 15 amps
Outage | J.E.26.08.07518 | C001874532 | Daniel Francis | St.Ann | Completed | Load_266713 | Cardiff Hall - 210 | 2026-08-04 22:09 | 2026-08-04 22:13 | 2026-08-04 23:33 | 2026-08-04 23:34 | 2026-08-04 23:33 | 2026-08-04 23:34 | 2026-08-04 23:37 | 2026-08-04 23:37 |  |  | Fair | No | Day light attention needed multiple pothead on pole
Outage | J.E.26.08.07294 | C001874547 | Elvis Trowers | KSAN | Completed | Load_239951 | Washington Blvd - 410 | 2026-08-04 22:59 | 2026-08-05 08:14 | 2026-08-05 09:10 | 2026-08-05 09:11 | 2026-08-05 10:14 | 2026-08-05 10:53 | 2026-08-05 10:53 | 2026-08-05 10:53 |  |  | Fair | Yes | Premises was found without electricity supply when checked and a blown 10 amp transformer fuse was found and replaced after patrol was completed pole #————in bank consist of 3/100 kva.
Outage | J.E.26.08.07286 | C001874551 | Milton Charlton | KSAN | Completed | Load_238530 | Hope - 410 | 2026-08-04 23:00 | 2026-08-05 08:05 | 2026-08-05 08:37 | 2026-08-05 08:38 | 2026-08-05 10:16 | 2026-08-05 21:40 | 2026-08-05 10:24 | 2026-08-05 10:24 | BrokenPole |  | Fair | No | Found okay upon arrival.30ft wooden pole rotten at the foot and leaning towards customer house. Pole is held up by customer service wire. Pole has open wire secondary and two #6 service wire. Need immediate attention.
Outage | J.E.26.08.07314 | C001874550 | Milton Charlton | KSAN | Completed | Load_248575 | Hope - 510 | 2026-08-04 23:00 | 2026-08-05 08:04 | 2026-08-05 10:53 | 2026-08-05 10:54 | 2026-08-05 11:38 | 2026-08-05 11:40 | 2026-08-05 11:39 | 2026-08-05 11:39 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.07545 | C001874553 | Christopher Edwards | KSAS | Completed | Load_245842 | Rockfort - 210 | 2026-08-04 23:00 | 2026-08-04 23:06 | 2026-08-05 02:03 | 2026-08-05 02:11 | 2026-08-05 02:37 | 2026-08-05 02:55 | 2026-08-05 02:55 | 2026-08-05 02:55 | Fire |  | Fair | No | Refuse blown 50 kva transformer using (1) 5 amps
Non-Outage | J.E.26.08.07556 | C001874556 | Edward Royal |  | Completed |  |  | 2026-08-04 23:03 | 2026-08-05 09:27 | 2026-08-05 12:39 | 2026-08-05 12:40 | 2026-08-05 13:03 | 2026-08-05 14:01 | 2026-08-05 14:01 | 2026-08-05 14:01 | BrokenWire |  | Fair | No | Spliced and reconnected drop lead to secondary phase using 2 single bolt clamp
Outage | J.E.26.08.07300 | C001874557 | Christopher Edwards | KSAS | Completed | Load_240902 | Rockfort - 210 | 2026-08-04 23:08 | 2026-08-04 23:09 | 2026-08-04 23:44 | 2026-08-04 23:53 | 2026-08-05 00:13 | 2026-08-05 00:31 | 2026-08-05 00:35 | 2026-08-05 00:35 |  |  | Fair | No | Refuse blown junction Fuse using (1) 25 amps
Outage | J.E.26.08.07575 | C001874558 | Delano Gayle | St.Catherine | Completed | Load_576141 | Twickenham - 210 | 2026-08-04 23:14 | 2026-08-04 23:18 | 2026-08-04 23:29 | 2026-08-04 23:29 | 2026-08-05 02:17 | 2026-08-05 02:28 | 2026-08-05 02:28 | 2026-08-05 02:28 | Fire |  | Fair | No | Area patrolled and found okay no fire seen
Non-Outage | J.E.26.08.04384 | C001874559 | Moses Elliston |  | Completed |  |  | 2026-08-04 23:16 | 2026-08-04 23:17 | 2026-08-05 09:55 | 2026-08-05 09:55 | 2026-08-05 09:55 | 2026-08-05 09:55 | 2026-08-05 09:56 | 2026-08-05 09:56 |  |  | Fair | No | Supply ok at premises
Outage | J.E.26.08.05030 | C001874561 | Moses Elliston | Portmore | Completed | Load_576155 | Naggo Head - 610 | 2026-08-04 23:21 | 2026-08-04 23:22 | 2026-08-05 09:34 | 2026-08-05 09:35 | 2026-08-05 09:34 | 2026-08-05 09:35 | 2026-08-05 09:36 | 2026-08-05 09:36 |  |  | Fair | No | Supply ok at premises.
Non-Outage | J.E.26.08.07592 | C001874568 | Christopher Edwards |  | Completed |  |  | 2026-08-05 00:10 | 2026-08-05 00:11 | 2026-08-05 00:35 | 2026-08-05 00:36 | 2026-08-05 00:54 | 2026-08-05 02:01 | 2026-08-05 02:02 | 2026-08-05 02:02 | Fire |  | Fair | No | Splice and retention broken open secondary wireUsing:40ft #2 AA conductor (1) #2 preform 2 one bolt clamps Refuse blown 100 kva transformer Using (1) 10 amps
Non-Outage | J.E.26.08.07596 | C001874569 | Christopher Edwards |  | Completed |  |  | 2026-08-05 00:11 | 2026-08-05 00:12 | 2026-08-05 01:13 | 2026-08-05 02:03 | 2026-08-05 02:02 | 2026-08-05 02:02 | 2026-08-05 02:03 | 2026-08-05 02:03 | Fire |  | Fair | No | Related to previous call that was resolved
Outage | J.E.26.08.07358 | C001874587 | Roxroy Needham | St.Ann | Completed | Load_248462 | Cardiff Hall - 210 | 2026-08-05 00:45 | 2026-08-05 00:46 | 2026-08-05 00:57 | 2026-08-05 00:58 | 2026-08-05 00:59 | 2026-08-05 01:00 | 2026-08-05 01:01 | 2026-08-05 01:01 |  |  | Fair | No | Premises found ok call customer and customer say that the light is back
Outage | J.E.26.08.07408 | C001874631 | Kenroy Dale | Manchester | Completed | Load_263608 | Kendal - 210 | 2026-08-05 07:11 | 2026-08-05 07:14 | 2026-08-05 13:02 | 2026-08-05 13:35 | 2026-08-05 14:29 | 2026-08-05 14:29 | 2026-08-05 14:32 | 2026-08-05 14:32 |  |  | Fair | No | Effort to contact customer multiple times was unsuccessful area visited and still not found was advised to write off call by dispatcher
Outage | J.E.26.08.07151 | C001874633 | Ryan Richards | Manchester | Completed | Load_260436 | Kendal - 310 | 2026-08-05 07:15 | 2026-08-05 07:16 | 2026-08-05 14:03 | 2026-08-05 14:05 | 2026-08-05 14:16 | 2026-08-05 14:38 | 2026-08-05 14:38 | 2026-08-05 14:38 |  |  | Fair | No | Unable to locate customer multiple efforts made to contact customer but unsuccessful
Outage | J.E.26.08.07242 | C001874634 | Ryan Richards | Manchester | Completed | Load_268058 | Spur Tree - 310 | 2026-08-05 07:15 | 2026-08-05 07:16 | 2026-08-05 07:41 | 2026-08-05 07:41 | 2026-08-05 10:19 | 2026-08-05 11:24 | 2026-08-05 11:25 | 2026-08-05 11:25 |  |  | Fair | No | Blown 7 amp junction fuse and corroded phase and neutral found at pothead and pole line patrol nothing else was found 7 amp junction fuse was replaced and corroded phase and neutral at pothead and pole remade using 6 one bolt clamps voltage 119/120/240 volts
Non-Outage | J.E.26.08.07534 | C001874636 | Derrick Grubb | St.Thomas | Completed | Load_266044 | Good Year - 210 | 2026-08-05 07:26 | 2026-08-05 07:27 | 2026-08-05 12:10 | 2026-08-05 12:11 | 2026-08-05 12:27 | 2026-08-05 12:30 | 2026-08-05 12:30 | 2026-08-05 12:30 |  |  | Fair | No | Premises not located. Contact number provided not working.
Outage | J.E.26.08.07483 | C001874637 | Tajay Bernard | Hanover | Completed | Load_261211 | Orange Bay - 310 | 2026-08-05 07:30 | 2026-08-05 07:32 | 2026-08-05 09:13 | 2026-08-05 09:14 | 2026-08-05 09:14 | 2026-08-05 09:14 | 2026-08-05 09:14 | 2026-08-05 09:14 |  |  | Fair | No | Customer stated that power was restored
Outage | J.E.26.08.07490 | C001874639 | Tajay Bernard | Trelawny | Completed | Load_259574 | Greenwood - 110 | 2026-08-05 07:30 | 2026-08-05 07:32 | 2026-08-05 09:30 | 2026-08-05 09:31 | 2026-08-05 09:30 | 2026-08-05 09:31 | 2026-08-05 09:31 | 2026-08-05 09:31 |  |  | Fair | No | This cal belongs to trelawny
Outage | J.E.26.08.07562 | C001874640 | Tajay Bernard | Hanover | Completed | Load_253913 | Orange Bay - 310 | 2026-08-05 07:30 | 2026-08-05 07:32 | 2026-08-05 08:54 | 2026-08-05 08:56 | 2026-08-05 09:05 | 2026-08-05 09:08 | 2026-08-05 09:08 | 2026-08-05 09:08 |  |  | Fair | No | Related to previous call Job #07564
Outage | J.E.26.08.07564 | C001874638 | Tajay Bernard | Hanover | Completed | Load_253913 | Orange Bay - 310 | 2026-08-05 07:30 | 2026-08-05 07:32 | 2026-08-05 07:42 | 2026-08-05 07:43 | 2026-08-05 08:42 | 2026-08-05 08:53 | 2026-08-05 08:53 | 2026-08-05 08:53 |  |  | Fair | No | Refuse 1 25kva Transformer use 3amp fuse
Outage | J.E.26.08.07606 | C001874641 | Tajay Bernard | Hanover | Completed | Load_265304 | Orange Bay - 310 | 2026-08-05 07:30 | 2026-08-05 07:32 | 2026-08-05 09:15 | 2026-08-05 09:32 | 2026-08-05 10:47 | 2026-08-05 11:05 | 2026-08-05 11:07 | 2026-08-05 11:07 |  |  | Fair | No | Refuse 1 15kva transformer use 1.5amp fuse
Outage | J.E.26.08.07614 | C001874642 | Tajay Bernard | Hanover | Completed | Load_252433 | Orange Bay - 210 | 2026-08-05 07:30 | 2026-08-05 07:32 | 2026-08-05 11:07 | 2026-08-05 11:08 | 2026-08-05 12:40 | 2026-08-05 12:53 | 2026-08-05 12:58 | 2026-08-05 12:58 |  |  | Fair | No | Refuse 1 20amp junction fuse
Outage | J.E.26.08.07518 | C001874643 | Tyrese Williams | St.Ann | Completed | Load_266713 | Cardiff Hall - 210 | 2026-08-05 07:31 | 2026-08-05 07:34 | 2026-08-05 08:17 | 2026-08-05 09:00 | 2026-08-05 09:36 | 2026-08-05 09:48 | 2026-08-05 09:49 | 2026-08-05 09:49 |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.08.07557 | C001874644 | Omar King | St.Ann | Completed | Load_262552 | Roaring River - 210 | 2026-08-05 07:31 | 2026-08-05 07:34 | 2026-08-05 09:06 | 2026-08-05 09:06 | 2026-08-05 11:12 | 2026-08-05 11:32 | 2026-08-05 11:32 | 2026-08-05 11:32 |  |  | Fair | No | On arrival at the GNOG site I do a voltage reading 114-115-229 Volts was found customer as internal problem
Non-Outage | J.E.26.08.00100 | C001874646 | Richard Watson | St.Elizabeth | Completed | Load_266721 | Maggotty - 210 | 2026-08-05 07:33 | 2026-08-05 07:34 | 2026-08-05 09:53 | 2026-08-05 09:54 | 2026-08-05 10:43 | 2026-08-05 11:11 | 2026-08-05 11:14 | 2026-08-05 11:14 |  |  | Fair | No | Found okay, however neutral connection at pothead remade, use one #6-#6 service sleeve, voltage left inside meter socket 108v, 113v, 221v.
Non-Outage | J.E.26.08.05565 | C001874645 | Richard Watson | St.Elizabeth | Completed | Load_264057 | Maggotty - 110 | 2026-08-05 07:33 | 2026-08-05 07:34 | 2026-08-05 08:40 | 2026-08-05 08:40 | 2026-08-05 08:50 | 2026-08-05 09:13 | 2026-08-05 09:22 | 2026-08-05 09:22 |  |  | Fair | No | Customer has a prepaid meter and her account is okay, however the meter is disconnected (meter open) and the system is currently down, customer is currently out of supply, field service personnel advised.
Non-Outage | J.E.26.07.20867 | C001874649 | Richard Watson | St.Elizabeth | Completed | Load_241146 | Maggotty - 110 | 2026-08-05 07:34 | 2026-08-05 07:34 | 2026-08-05 09:28 | 2026-08-05 09:29 | 2026-08-05 09:37 | 2026-08-05 09:41 | 2026-08-05 09:44 | 2026-08-05 09:44 |  |  | Fair | No | Premises locked, one meter not displaying at premises unable to access meters, please refer to afternoon crew as customer would present at about 4pm.
Non-Outage | J.E.26.07.32290 | C001874647 | Richard Watson | St.Elizabeth | Completed | Load_270212 | Maggotty - 110 | 2026-08-05 07:34 | 2026-08-05 07:34 | 2026-08-05 12:12 | 2026-08-05 12:12 | 2026-08-05 12:52 | 2026-08-05 12:57 | 2026-08-05 12:57 | 2026-08-05 12:57 |  |  | Fair | No | Customer not at premises, please refer to afternoon crew.
Non-Outage | J.E.26.07.38284 | C001874648 | Richard Watson | St.Elizabeth | Completed | Load_247338 | Maggotty - 110 | 2026-08-05 07:34 | 2026-08-05 07:34 | 2026-08-05 12:57 | 2026-08-05 12:58 | 2026-08-05 13:25 | 2026-08-05 13:28 | 2026-08-05 13:28 | 2026-08-05 13:28 |  |  | Fair | No | Customer contacted by phone and stated that the issue was resolved.
Outage | J.E.26.08.07627 | C001874650 | Evan Spaulding | St.Mary | Completed | Load_268674 | Annotto Bay - 310 | 2026-08-05 07:37 | 2026-08-05 07:38 | 2026-08-05 09:15 | 2026-08-05 09:15 | 2026-08-05 09:29 | 2026-08-05 09:48 | 2026-08-05 09:49 | 2026-08-05 09:49 |  |  | Fair | No | Use 2-1 bolt clamps at pot head , voltage left 116v.
Outage | J.E.26.08.07619 | C001874651 | Clyde Brown | Clarendon | Completed | Load_242439 | Parnassus - 210 | 2026-08-05 07:46 | 2026-08-05 07:48 | 2026-08-05 08:44 | 2026-08-05 16:32 | 2026-08-05 17:17 | 2026-08-05 18:28 | 2026-08-05 17:33 | 2026-08-05 17:33 |  |  | Fair | No | Blown 3 amps fuse for 25kva transformer,line patrolled and no fault seen,blown fuse replaced.
Outage | J.E.26.08.07415 | C001874652 | Richard Grant | St.Catherine | Completed | Load_257579 | New Michelton - 210 | 2026-08-05 07:49 | 2026-08-05 07:56 | 2026-08-05 11:42 | 2026-08-05 11:42 | 2026-08-05 12:31 | 2026-08-05 12:54 | 2026-08-05 12:54 | 2026-08-05 12:54 |  |  | Fair | No | Checks revealed customer has defective meter socket. Customer was advised.
Non-Outage | J.E.26.08.06153 | C001874654 | Omar King | St.Ann | Completed | Load_257020 | Ocho Rios - 510 | 2026-08-05 07:51 | 2026-08-05 07:52 | 2026-08-05 14:37 | 2026-08-05 14:38 | 2026-08-05 14:51 | 2026-08-05 14:57 | 2026-08-05 14:57 | 2026-08-05 14:57 | BrokenPole |  | Fair | No | Found junction switch defective temporary work as been done to restore customer please refer to maintenance
Non-Outage | J.E.26.08.07532 | C001874656 | Roxroy Needham | St.Ann | Completed | Load_249809 | Roaring River - 210 | 2026-08-05 07:51 | 2026-08-05 23:06 | 2026-08-06 03:25 | 2026-08-06 05:04 | 2026-08-06 05:04 | 2026-08-06 06:00 | 2026-08-06 05:05 | 2026-08-06 05:05 |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.08.06505 | C001874657 | Eric Williams | KSAS | Completed | Load_255298 | Hunts Bay - 310 | 2026-08-05 07:51 | 2026-08-05 15:42 | 2026-08-05 18:21 | 2026-08-05 18:21 | 2026-08-05 18:21 | 2026-08-05 18:21 | 2026-08-05 18:22 | 2026-08-05 18:22 |  |  | Fair | No | Premises found okay
Non-Outage | J.E.26.08.07540 | C001874658 | Raymond Carr | St.Mary | Completed | Load_245290 | Blackstonedge - 110 | 2026-08-05 07:52 | 2026-08-05 07:54 | 2026-08-05 09:38 | 2026-08-05 09:39 | 2026-08-05 11:20 | 2026-08-05 11:54 | 2026-08-05 11:59 | 2026-08-05 11:59 |  |  | Fair | No | Blown 25 kva transformer fuse found at pole number 0100670, line patrol and found one span of secondary conductors banged together, caused by vehicle contact. Same was cleared, a 2 amp fuse was used to renew supply was restored.
Non-Outage | J.E.26.08.06890 | C001874659 | Raymond Carr | St.Ann | Completed | Load_269586 | Upper White River - 110 | 2026-08-05 07:53 | 2026-08-05 07:54 | 2026-08-05 08:25 | 2026-08-05 08:25 | 2026-08-05 09:37 | 2026-08-05 09:00 | 2026-08-05 09:38 | 2026-08-05 09:38 |  |  | Fair | No | Supply verified okay by Mr Dunkley.
Non-Outage | J.E.26.08.07327 | C001874660 | Denton Williams | Portland | Completed | Load_249080 | Port Antonio - 410 | 2026-08-05 07:54 | 2026-08-05 07:56 | 2026-08-05 08:31 | 2026-08-05 08:31 | 2026-08-05 10:04 | 2026-08-05 10:04 | 2026-08-05 10:06 | 2026-08-05 10:06 |  |  | Fair | No | Customer stated that she did not call to JPS
Non-Outage | J.E.26.05.06535 | C001874664 | Richman Whyte | Westmoreland | Completed | Load_250446 | Paradise - 210 | 2026-08-05 07:56 | 2026-08-05 07:58 | 2026-08-05 11:03 | 2026-08-05 11:03 | 2026-08-05 11:03 | 2026-08-05 11:03 | 2026-08-05 11:04 | 2026-08-05 11:04 |  |  | Fair | No | Clean corrosion on service wire at secondary line use 1pg clamp
Non-Outage | J.E.26.08.06717 | C001874661 | Tyrese Williams | St.Ann | Completed | Load_262327 | Cardiff Hall - 310 | 2026-08-05 07:56 | 2026-08-05 07:57 | 2026-08-05 08:16 | 2026-08-05 09:49 | 2026-08-05 10:45 | 2026-08-05 10:45 | 2026-08-05 10:45 | 2026-08-05 10:45 |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.08.07621 | C001874663 | Horace Malcolm | St.James | Completed | Load_263018 | Bogue - 610 | 2026-08-05 07:56 | 2026-08-05 08:02 | 2026-08-05 08:29 | 2026-08-05 08:30 | 2026-08-05 11:17 | 2026-08-05 11:54 | 2026-08-05 11:54 | 2026-08-05 11:54 |  |  | Rains | No | Check and found one 15kva transformer defective need maintenance
Non-Outage | J.E.26.03.01314 | C001874674 | Richman Whyte | Westmoreland | Completed | Load_292432 | Paradise - 210 | 2026-08-05 07:57 | 2026-08-05 07:58 | 2026-08-05 14:40 | 2026-08-05 14:41 | 2026-08-05 14:40 | 2026-08-05 14:41 | 2026-08-05 14:42 | 2026-08-05 14:42 |  |  | Fair | No | Customer has internal problem advise to fix
Non-Outage | J.E.26.03.05941 | C001874672 | Richman Whyte | Westmoreland | Completed | Load_263330 | Paradise - 210 | 2026-08-05 07:57 | 2026-08-05 07:58 | 2026-08-05 08:58 | 2026-08-05 08:58 | 2026-08-05 08:58 | 2026-08-05 08:58 | 2026-08-05 08:59 | 2026-08-05 08:59 |  |  | EarthMovement | No | Check and found okay
Non-Outage | J.E.26.04.08229 | C001874673 | Richman Whyte | Westmoreland | Completed | Load_252147 | Paradise - 210 | 2026-08-05 07:57 | 2026-08-05 07:58 | 2026-08-05 09:02 | 2026-08-05 09:02 | 2026-08-05 09:02 | 2026-08-05 09:02 | 2026-08-05 09:03 | 2026-08-05 09:03 |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.04.11890 | C001874671 | Richman Whyte | Westmoreland | Completed | Load_249880 | Paradise - 210 | 2026-08-05 07:57 | 2026-08-05 07:58 | 2026-08-05 09:57 | 2026-08-05 09:58 | 2026-08-05 09:57 | 2026-08-05 10:30 | 2026-08-05 10:30 | 2026-08-05 10:30 |  |  | Fair | No | Remade secondary jumper use 6 one boult clamps voltage #110 110 205 220 220 222
Non-Outage | J.E.26.04.11899 | C001874668 | Richman Whyte | Westmoreland | Completed | Load_249880 | Paradise - 210 | 2026-08-05 07:57 | 2026-08-05 07:58 | 2026-08-05 08:41 | 2026-08-05 08:42 | 2026-08-05 08:41 | 2026-08-05 08:41 | 2026-08-05 08:42 | 2026-08-05 08:42 |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.04.13316 | C001874670 | Richman Whyte | Westmoreland | Completed | Load_247022 | Paradise - 210 | 2026-08-05 07:57 | 2026-08-05 07:58 | 2026-08-05 08:47 | 2026-08-05 08:48 | 2026-08-05 08:47 | 2026-08-05 08:47 | 2026-08-05 08:48 | 2026-08-05 08:48 |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.05.00457 | C001874669 | Richman Whyte | Westmoreland | Completed | Load_251128 | Paradise - 210 | 2026-08-05 07:57 | 2026-08-05 07:58 | 2026-08-05 08:45 | 2026-08-05 08:45 | 2026-08-05 08:45 | 2026-08-05 08:45 | 2026-08-05 08:46 | 2026-08-05 08:46 |  |  | Fair | No | Change and found okay
Non-Outage | J.E.26.05.01137 | C001874665 | Richman Whyte | Westmoreland | Completed | Load_292155 | Paradise - 210 | 2026-08-05 07:57 | 2026-08-05 07:58 | 2026-08-05 14:42 | 2026-08-05 14:42 | 2026-08-05 14:42 | 2026-08-05 14:42 | 2026-08-05 14:43 | 2026-08-05 14:43 |  |  | Fair | No | Check and found ok
Non-Outage | J.E.26.05.01160 | C001874666 | Richman Whyte | Westmoreland | Completed | Load_252147 | Paradise - 210 | 2026-08-05 07:57 | 2026-08-05 07:58 | 2026-08-05 14:43 | 2026-08-05 14:43 | 2026-08-05 14:43 | 2026-08-05 14:43 | 2026-08-05 14:43 | 2026-08-05 14:43 |  |  | Fair | No | Check and found ok
Non-Outage | J.E.26.08.07271 | C001874667 | Evan Spaulding | St.Mary | Completed | Load_239259 | Annotto Bay - 310 | 2026-08-05 07:57 | 2026-08-05 07:57 | 2026-08-05 08:08 | 2026-08-05 08:08 | 2026-08-05 08:56 | 2026-08-05 09:13 | 2026-08-05 09:15 | 2026-08-05 09:15 |  |  | Fair | No | Bank of three Transformers at premises but customer only using 110 ,220 supply,voltage found 119v,115, 234v.
Non-Outage | J.E.26.08.07170 | C001874675 | Elvis Trowers |  | Completed |  |  | 2026-08-05 07:59 | 2026-08-05 11:25 | 2026-08-05 12:15 | 2026-08-05 12:16 | 2026-08-05 12:59 | 2026-08-05 14:12 | 2026-08-05 14:13 | 2026-08-05 14:13 | BrokenWire |  | Fair | Yes | Broken primary neural wire was found on ground and about 150’ feet of #2AA wire was used, 3 clamps and 2 preforms was used to complete repairs.
Non-Outage | J.E.26.07.27617 | C001874690 | Royston Montague | St.Catherine | Completed | Load_256389 | Rhodens Pen - 210 | 2026-08-05 08:02 | 2026-08-05 08:04 | 2026-08-05 08:18 | 2026-08-05 11:27 | 2026-08-05 11:36 | 2026-08-05 11:40 | 2026-08-05 11:41 | 2026-08-05 11:41 |  |  | Fair | No | Slack wire in meter socket, same corrected. Voltage 227v 110v 112v .
Non-Outage | J.E.26.07.31105 | C001874689 | Royston Montague | St.Catherine | Completed | Load_252253 | Rhodens Pen - 210 | 2026-08-05 08:02 | 2026-08-05 08:04 | 2026-08-05 08:18 | 2026-08-05 11:55 | 2026-08-05 12:02 | 2026-08-05 12:21 | 2026-08-05 12:21 | 2026-08-05 12:21 |  |  | Fair | No | Faulty joints on customer load side. Same asked to get an electrician to repair. Voltage 228v 113v 114v
Non-Outage | J.E.26.07.34666 | C001874688 | Royston Montague | St.Catherine | Completed | Load_260217 | Rhodens Pen - 210 | 2026-08-05 08:02 | 2026-08-05 08:04 | 2026-08-05 08:18 | 2026-08-05 12:21 | 2026-08-05 12:46 | 2026-08-05 13:42 | 2026-08-05 13:43 | 2026-08-05 13:43 |  |  | Fair | No | Full voltage found. 110v
Non-Outage | J.E.26.07.37164 | C001874686 | Royston Montague | St.Catherine | Completed | Load_250865 | Rhodens Pen - 210 | 2026-08-05 08:02 | 2026-08-05 08:04 | 2026-08-05 08:18 | 2026-08-05 11:14 | 2026-08-05 11:22 | 2026-08-05 11:25 | 2026-08-05 11:26 | 2026-08-05 11:26 |  |  | Fair | No | Premises found ok. Customer confirmed a team visited few days ago. Voltage 116v
Non-Outage | J.E.26.07.38772 | C001874681 | Royston Montague | St.Catherine | Completed | Load_556367 | Rhodens Pen - 210 | 2026-08-05 08:02 | 2026-08-05 08:04 | 2026-08-05 08:18 | 2026-08-05 08:42 | 2026-08-05 08:55 | 2026-08-05 08:56 | 2026-08-05 08:56 | 2026-08-05 08:56 |  |  | Fair | No | Customer only getting one hot leg from rami box. Please assign this job to relevant team thanks.
Non-Outage | J.E.26.07.39402 | C001874680 | Royston Montague | St.Catherine | Completed | Load_258149 | Rhodens Pen - 210 | 2026-08-05 08:02 | 2026-08-05 08:04 | 2026-08-05 08:18 | 2026-08-05 13:43 | 2026-08-05 13:43 | 2026-08-05 13:44 | 2026-08-05 13:44 | 2026-08-05 13:44 |  |  | Fair | No | Corrosion at pothead, same corrected. Voltage 212v 105v 105v
Non-Outage | J.E.26.08.00110 | C001874684 | Royston Montague | St.Catherine | Completed | Load_305217 | Rhodens Pen - 210 | 2026-08-05 08:02 | 2026-08-05 08:04 | 2026-08-05 08:18 | 2026-08-05 11:43 | 2026-08-05 11:42 | 2026-08-05 11:54 | 2026-08-05 11:54 | 2026-08-05 11:54 |  |  | Fair | No | Rami system in area, please assign this job to the relevant team thanks.
Non-Outage | J.E.26.08.07450 | C001874677 | Royston Montague | St.Catherine | Completed | Load_251734 | Rhodens Pen - 210 | 2026-08-05 08:02 | 2026-08-05 08:04 | 2026-08-05 08:18 | 2026-08-05 10:55 | 2026-08-05 11:01 | 2026-08-05 11:13 | 2026-08-05 11:13 | 2026-08-05 11:13 |  |  | Fair | No | Slack connection at customer take off point. Same corrected. Voltage 232v 115v 115v
Outage | J.E.26.08.06398 | C001874682 | Fitzroy Turner | KSAS | Completed | Load_244455 | Rockfort - 210 | 2026-08-05 08:02 | 2026-08-05 08:22 | 2026-08-05 08:55 | 2026-08-05 08:55 | 2026-08-05 09:17 | 2026-08-05 09:18 | 2026-08-05 09:18 | 2026-08-05 09:18 |  |  | Fair | No | The area found with electricity supply
Outage | J.E.26.08.06687 | C001874687 | Fitzroy Turner | KSAS | Completed | Load_253227 | Rockfort - 210 | 2026-08-05 08:02 | 2026-08-05 08:06 | 2026-08-05 09:29 | 2026-08-05 09:32 | 2026-08-05 09:34 | 2026-08-05 09:35 | 2026-08-05 09:35 | 2026-08-05 09:35 |  |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.08.07608 | C001874678 | Richman Whyte | Westmoreland | Completed | Load_258517 | Paradise - 210 | 2026-08-05 08:02 | 2026-08-05 08:02 | 2026-08-05 12:07 | 2026-08-05 12:07 | 2026-08-05 12:07 | 2026-08-05 12:22 | 2026-08-05 12:23 | 2026-08-05 12:23 |  |  | Fair | No | Replace 25kva transformer fuse
Non-Outage | J.E.26.07.22481 | C001874694 | Royston Montague | St.Catherine | Completed | Load_252827 | Rhodens Pen - 210 | 2026-08-05 08:03 | 2026-08-05 08:04 | 2026-08-05 08:18 | 2026-08-05 10:41 | 2026-08-05 10:41 | 2026-08-05 10:52 | 2026-08-05 10:52 | 2026-08-05 10:52 |  |  | Fair | No | Customer asked to get an electrician to check load side. Voltage in area and premises 217v 107v 108v
Non-Outage | J.E.26.07.25156 | C001874693 | Royston Montague | St.Catherine | Completed | Load_246418 | Rhodens Pen - 210 | 2026-08-05 08:03 | 2026-08-05 08:04 | 2026-08-05 08:18 | 2026-08-05 08:57 | 2026-08-05 10:11 | 2026-08-05 10:29 | 2026-08-05 10:30 | 2026-08-05 10:30 |  |  | Fair | No | Faulty joints at customer take off point. Same correct, voltage found 114v 97v voltage after 113v 115v
Outage | J.E.26.08.07330 | C001874698 | Oshane Warren | Westmoreland | Completed | Load_244662 | Paradise - 310 | 2026-08-05 08:03 | 2026-08-05 08:05 | 2026-08-05 09:03 | 2026-08-05 09:04 | 2026-08-05 11:42 | 2026-08-05 11:48 | 2026-08-05 11:49 | 2026-08-05 11:49 |  |  | Rains | No | Replace 25 amp junction fuse
Non-Outage | J.E.26.06.24279 | C001874699 | Oshane Warren | Westmoreland | Completed | Load_268438 | Paradise - 310 | 2026-08-05 08:04 | 2026-08-05 08:05 | 2026-08-05 13:40 | 2026-08-05 13:40 | 2026-08-05 14:04 | 2026-08-05 14:05 | 2026-08-05 14:06 | 2026-08-05 14:06 |  |  | Fair | No | Internal problem advice to fix
Outage | J.E.26.08.07192 | C001874701 | Nickolas Rodriques | St.Catherine | Completed | Load_251909 | Twickenham - 210 | 2026-08-05 08:06 | 2026-08-05 08:09 | 2026-08-05 20:18 | 2026-08-05 20:18 | 2026-08-05 20:33 | 2026-08-05 20:58 | 2026-08-05 21:03 | 2026-08-05 21:03 |  |  | Fair | No | Checked and found customer without power caused by corroded connection. Repaired by replacing one clamp at pole. Current reading (116)
Outage | J.E.26.08.07448 | C001874703 | Nickolas Rodriques | St.Catherine | Completed | Load_241011 | Twickenham - 210 | 2026-08-05 08:06 | 2026-08-05 08:10 | 2026-08-05 08:17 | 2026-08-05 17:37 | 2026-08-05 18:26 | 2026-08-05 18:27 | 2026-08-05 18:28 | 2026-08-05 18:28 |  |  | Fair | No | Power restored. Customer confirmed that the power outage was later restored.
Outage | J.E.26.08.07258 | C001874707 | Rusean Allen | KSAN | Completed | Load_268911 | Washington Blvd - 710 | 2026-08-05 08:07 | 2026-08-05 23:16 | 2026-08-06 01:39 | 2026-08-06 01:39 | 2026-08-06 02:05 | 2026-08-06 02:09 | 2026-08-06 02:10 | 2026-08-06 02:10 | BrokenWire |  | Fair | No | Broken stanchion pole found, wire was disconnected at pole. Customer was advised to contact electrician to conduct repairs.
Outage | J.E.26.08.07335 | C001874708 | Dwayne Cohen | KSAN | Completed | Load_575407 | Washington Blvd - 710 | 2026-08-05 08:07 | 2026-08-05 08:10 | 2026-08-05 11:49 | 2026-08-05 12:18 | 2026-08-05 13:01 | 2026-08-05 13:44 | 2026-08-05 13:46 | 2026-08-05 13:46 |  |  | Fair | No | Customer Hexing meter is OFF, call center representative unable to communicate with meter. Refer this report to Field Service Department
Outage | J.E.26.08.07163 | C001874711 | Dwayne Cohen | KSAS | Completed | Load_301920 | Hunts Bay - 810 | 2026-08-05 08:08 | 2026-08-05 08:11 | 2026-08-05 10:49 | 2026-08-05 10:50 | 2026-08-05 11:03 | 2026-08-05 11:05 | 2026-08-05 11:05 | 2026-08-05 11:05 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.07241 | C001874709 | Rusean Allen | KSAS | Completed | Load_248058 | Hunts Bay - 510 | 2026-08-05 08:08 | 2026-08-05 08:11 | 2026-08-05 11:41 | 2026-08-05 12:03 | 2026-08-05 12:02 | 2026-08-05 12:04 | 2026-08-05 12:04 | 2026-08-05 12:04 |  |  | Fair | No | Switch top burnt off in main line, refer to in-house team
Outage | J.E.26.08.07316 | C001874710 | Dwayne Cohen | KSAS | Completed | Load_253656 | Hunts Bay - 810 | 2026-08-05 08:08 | 2026-08-05 08:10 | 2026-08-05 09:39 | 2026-08-05 09:39 | 2026-08-05 10:11 | 2026-08-05 10:47 | 2026-08-05 10:49 | 2026-08-05 10:49 |  |  | Fair | No | Change defective transformer arrester and refuse blown 3amps link, supply restore.
Non-Outage | J.E.26.08.07488 | C001874713 | Milton Charlton | KSAN | Completed | Load_567816 | Hope - 510 | 2026-08-05 08:09 | 2026-08-05 08:10 | 2026-08-05 10:25 | 2026-08-05 10:26 | 2026-08-05 10:48 | 2026-08-05 10:50 | 2026-08-05 10:53 | 2026-08-05 10:53 | BrokenPole |  | Fair | No | 30ft wooden pole with meter socket and meter #4201162 feeding two cable cabinet broken in motor vehicle accident pole belongs to telephone company. #6 triplex connected to broken pole feeding meter.
Outage | J.E.26.08.06288 | C001874714 | Wan Carlos Scarlett | Portmore | Completed | Load_257531 | Naggo Head - 510 | 2026-08-05 08:12 | 2026-08-05 08:16 | 2026-08-05 08:29 | 2026-08-05 11:19 | 2026-08-05 12:19 | 2026-08-05 12:40 | 2026-08-05 14:22 | 2026-08-05 14:22 |  |  | Fair | No | Refuse 20amp junction no pole # was found suspect lightning take out the power supply and refuse 2,50KVA transformer with 2,5amp fuse no pole # was found power supply has been restored
Outage | J.E.26.08.06616 | C001874715 | Wan Carlos Scarlett | Portmore | Completed | Load_257946 | Naggo Head - 610 | 2026-08-05 08:12 | 2026-08-05 08:16 | 2026-08-05 08:28 | 2026-08-05 10:35 | 2026-08-05 10:56 | 2026-08-05 11:15 | 2026-08-05 11:16 | 2026-08-05 11:16 |  |  | Fair | No | Found customer 3 wire service at pole with one of the phase broken off use one bolt clamp at open secondary line phase readings 114-113-229
Outage | J.E.26.08.07188 | C001874718 | Wan Carlos Scarlett | Portmore | Completed | Load_269220 | Naggo Head - 610 | 2026-08-05 08:13 | 2026-08-05 08:16 | 2026-08-05 08:20 | 2026-08-05 08:21 | 2026-08-05 09:32 | 2026-08-05 10:24 | 2026-08-05 10:26 | 2026-08-05 10:26 |  |  | Fair | No | Found 25KVA transformer drop lead wire to open secondary line phase burn off use 2 one bolt clamps at pole readings 117-116-234
Outage | J.E.26.08.07374 | C001874720 | Wan Carlos Scarlett | Portmore | Completed | Load_251619 | Naggo Head - 610 | 2026-08-05 08:13 | 2026-08-05 08:16 | 2026-08-05 08:22 | 2026-08-05 14:32 | 2026-08-05 15:24 | 2026-08-05 15:34 | 2026-08-05 15:35 | 2026-08-05 15:35 |  |  | Fair | No | Customer not available at this time premises closed
Non-Outage | J.E.26.08.07462 | C001874729 | Christopher Edwards | KSAN | Completed | Load_252373 | Constant Spring - 210 | 2026-08-05 08:22 | 2026-08-05 08:27 | 2026-08-05 10:32 | 2026-08-05 10:32 | 2026-08-05 11:02 | 2026-08-05 11:29 | 2026-08-05 11:30 | 2026-08-05 11:30 |  |  | Fair | Yes | Broken open secondary phaseRequired bushing on the open secondary lines Before broken wire can be splice and connected Isolate 25 kva transformer To disconnect broken open secondary wire Approximately 5 customers are experiencing single phasing as a result of broken wire
Outage | J.E.26.08.06346 | C001874727 | Rusean Allen | KSAS | Completed | Load_259746 | Rockfort - 410 | 2026-08-05 08:22 | 2026-08-05 08:23 | 2026-08-05 12:06 | 2026-08-05 12:07 | 2026-08-05 12:08 | 2026-08-05 12:09 | 2026-08-05 12:09 | 2026-08-05 12:09 |  |  | Fair | No | Premises not found
Outage | J.E.26.08.06647 | C001874725 | Edward Royal | KSAS | Completed | Load_267301 | Rockfort - 310 | 2026-08-05 08:22 | 2026-08-05 08:26 | 2026-08-05 14:50 | 2026-08-05 14:50 | 2026-08-05 14:50 | 2026-08-05 14:50 | 2026-08-05 14:50 | 2026-08-05 14:50 | Fire |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.07126 | C001874724 | Edward Royal | KSAS | Completed | Load_268171 | Rockfort - 210 | 2026-08-05 08:22 | 2026-08-05 09:33 | 2026-08-05 14:10 | 2026-08-05 14:11 | 2026-08-05 14:27 | 2026-08-05 14:45 | 2026-08-05 14:46 | 2026-08-05 14:46 |  |  | Fair | No | Replaced 3 50KVA transformers fuse 3 (5A) pole #0211318
Outage | J.E.26.08.07320 | C001874723 | Edward Royal | KSAS | Completed | Load_253994 | Rockfort - 410 | 2026-08-05 08:22 | 2026-08-05 08:25 | 2026-08-05 20:04 | 2026-08-05 20:05 | 2026-08-05 20:04 | 2026-08-05 20:30 | 2026-08-05 20:42 | 2026-08-05 20:42 | BrokenWire |  | Fair | No | Spliced and reconnected service phase using 1 single bolt clamp
Outage | J.E.26.08.07613 | C001874722 | Edward Royal | KSAS | Completed | Load_245842 | Rockfort - 210 | 2026-08-05 08:22 | 2026-08-05 08:28 | 2026-08-05 14:04 | 2026-08-05 14:05 | 2026-08-05 14:04 | 2026-08-05 14:05 | 2026-08-05 14:05 | 2026-08-05 14:05 |  |  | Fair | No | Premises found ok related to outage
Non-Outage | J.E.26.08.07605 | C001874730 | Christopher Edwards | KSAN | Completed | Load_264129 | Constant Spring - 210 | 2026-08-05 08:23 | 2026-08-05 08:27 | 2026-08-05 08:36 | 2026-08-05 09:09 | 2026-08-05 09:44 | 2026-08-05 10:30 | 2026-08-05 10:32 | 2026-08-05 10:32 |  |  | Fair | No | Removed Illegal connections at transformer poleThat was causing a short circuit on the secondary line Voltage:116,115,230v
Non-Outage | J.E.26.08.05138 | C001874731 | Denton Williams | Portland | Completed | Load_251260 | Port Antonio - 410 | 2026-08-05 08:25 | 2026-08-05 08:25 | 2026-08-05 10:07 | 2026-08-05 10:08 | 2026-08-05 10:18 | 2026-08-05 10:38 | 2026-08-05 10:49 | 2026-08-05 10:49 | TreeContact | Y | Fair | No | Use one 15 amp fuse to close one of three fuse to a pad mounted transformer. Pad mounted substation and the main line leads to it need bushing. Refer to Portland maintenance.
Non-Outage | J.E.26.08.07021 | C001874734 | Andrae Dawkins | St.James | Completed | Load_261423 | Bogue - 310 | 2026-08-05 08:26 | 2026-08-05 08:28 | 2026-08-05 09:01 | 2026-08-05 10:14 | 2026-08-05 10:17 | 2026-08-05 10:19 | 2026-08-05 10:20 | 2026-08-05 10:20 |  |  | Fair | No | Check and found okay customer said that the problem was already resolved
Non-Outage | J.E.26.08.07371 | C001874737 | Andrae Dawkins | St.James | Completed | Load_257366 | Queens Drive - 710 | 2026-08-05 08:27 | 2026-08-05 08:28 | 2026-08-05 09:05 | 2026-08-05 11:52 | 2026-08-05 11:52 | 2026-08-05 11:47 | 2026-08-05 11:57 | 2026-08-05 11:57 |  |  | Fair | No | Found customer singlephasing due to corrosion at pothead clean and remade joints voltage found 111/85/222 voltage left 111/111/222
Non-Outage | J.E.26.08.07474 | C001874739 | Andrae Dawkins | St.James | Completed | Load_246347 | Queens Drive - 710 | 2026-08-05 08:27 | 2026-08-05 08:28 | 2026-08-05 09:08 | 2026-08-05 12:08 | 2026-08-05 12:09 | 2026-08-05 12:09 | 2026-08-05 12:12 | 2026-08-05 12:12 |  |  | Fair | No | Check and found ok customer said that the problem was already resolved from last night
Outage | J.E.26.08.07554 | C001874742 | Fitzroy Turner | KSAS | Completed | Load_263100 | Cane River - 410 | 2026-08-05 08:28 | 2026-08-05 08:39 | 2026-08-05 11:07 | 2026-08-05 11:53 | 2026-08-05 11:52 | 2026-08-05 11:52 | 2026-08-05 11:53 | 2026-08-05 11:53 |  |  | Fair | No | Unable to communicate with customer meter.please send email to field service department to have issues resolved
Non-Outage | J.E.26.07.38529 | C001874745 | Neville Spencer | Clarendon | Completed | Load_243522 | May Pen - 110 | 2026-08-05 08:30 | 2026-08-05 08:32 | 2026-08-05 13:48 | 2026-08-05 13:49 | 2026-08-05 13:55 | 2026-08-05 13:55 | 2026-08-05 13:58 | 2026-08-05 13:58 | Fire |  | Fair | No | Customer internal fault advised.voltage reading 112 116 229.
Non-Outage | J.E.26.07.38696 | C001874746 | Neville Spencer | Clarendon | Completed | Load_241326 | May Pen - 110 | 2026-08-05 08:30 | 2026-08-05 08:32 | 2026-08-05 11:18 | 2026-08-05 11:19 | 2026-08-05 11:44 | 2026-08-05 11:44 | 2026-08-05 12:31 | 2026-08-05 12:31 |  |  | Fair | No | Remade corrded phase and neutral joints at pothead on 3, wire service used 3, 66/6 sleeves voltage reading 116 119 234 .
Non-Outage | J.E.26.07.39545 | C001874747 | Neville Spencer | Clarendon | Completed | Load_258559 | May Pen - 110 | 2026-08-05 08:30 | 2026-08-05 08:32 | 2026-08-05 12:40 | 2026-08-05 12:40 | 2026-08-05 13:27 | 2026-08-05 13:42 | 2026-08-05 13:48 | 2026-08-05 13:48 |  |  | Fair | No | Remade broken off phase at secondary on 3, wire service used 2, clamps reset trip voltage reading 114 116 231 supply restored.
Non-Outage | J.E.26.07.39583 | C001874750 | Neville Spencer | Clarendon | Completed | Load_238064 | May Pen - 110 | 2026-08-05 08:30 | 2026-08-05 08:32 | 2026-08-05 08:48 | 2026-08-05 08:48 | 2026-08-05 10:52 | 2026-08-05 10:53 | 2026-08-05 11:18 | 2026-08-05 11:18 |  |  | Fair | No | Remade corrded netural joint at pothead on 3, wire service used 1, 6/6 sleeve voltage reading 110 112 223 supply restored.
Non-Outage | J.E.26.07.40006 | C001874748 | Neville Spencer | Clarendon | Completed | Load_247989 | May Pen - 110 | 2026-08-05 08:30 | 2026-08-05 08:32 | 2026-08-05 13:58 | 2026-08-05 13:59 | 2026-08-05 15:02 | 2026-08-05 15:03 | 2026-08-05 15:05 | 2026-08-05 15:05 |  |  | Fair | No | Customer not located.
Non-Outage | J.E.26.08.05250 | C001874744 | Elvis Trowers | KSAN | Completed | Load_239951 | Washington Blvd - 410 | 2026-08-05 08:30 | 2026-08-05 08:30 | 2026-08-05 10:54 | 2026-08-05 10:54 | 2026-08-05 10:54 | 2026-08-05 10:56 | 2026-08-05 10:56 | 2026-08-05 10:56 |  |  | Fair | Yes | Premises checked and found ok, call related.
Outage | J.E.26.08.07460 | C001874749 | Fitzroy Turner | KSAS | Completed | Load_300878 | Cane River - 410 | 2026-08-05 08:30 | 2026-08-05 08:34 | 2026-08-05 13:26 | 2026-08-05 13:27 | 2026-08-05 13:26 | 2026-08-05 13:27 | 2026-08-05 13:28 | 2026-08-05 13:28 |  |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.08.07104 | C001874755 | Fitzroy Turner | KSAS | Completed | Load_1002669 | Rockfort - 210 | 2026-08-05 08:31 | 2026-08-05 08:34 | 2026-08-05 09:28 | 2026-08-05 13:51 | 2026-08-05 13:50 | 2026-08-05 14:36 | 2026-08-05 14:37 | 2026-08-05 14:37 |  |  | Fair | No | Customer premises found with electricity supply
Non-Outage | J.E.26.02.43611 | C001874756 | Dwain Samuels | Westmoreland | Completed | Load_250735 | Paradise - 210 | 2026-08-05 08:32 | 2026-08-05 08:34 | 2026-08-05 08:39 | 2026-08-05 10:59 | 2026-08-05 10:59 | 2026-08-05 10:59 | 2026-08-05 11:00 | 2026-08-05 11:00 |  |  | Fair | No | Called customer said issue was resolved. Not having any problems with electricity now
Non-Outage | J.E.26.08.02853 | C001874758 | Rochaine Hussey | KSAN | Completed | Load_255111 | Hope - 510 | 2026-08-05 08:32 | 2026-08-05 08:33 | 2026-08-05 09:28 | 2026-08-05 12:39 | 2026-08-05 12:39 | 2026-08-05 12:41 | 2026-08-05 12:41 | 2026-08-05 12:41 |  |  | Fair | No | Customer say power was restored
Non-Outage | J.E.26.08.07445 | C001874757 | Dwain Samuels | Westmoreland | Completed | Load_262801 | Paradise - 110 | 2026-08-05 08:32 | 2026-08-05 08:34 | 2026-08-05 08:39 | 2026-08-05 09:10 | 2026-08-05 10:11 | 2026-08-05 10:35 | 2026-08-05 10:37 | 2026-08-05 10:37 |  |  | Fair | No | Area affected by low voltage. Transformer serving too far. Voltage check 111-105-216
Non-Outage | J.E.26.08.06583 | C001874759 | Rochaine Hussey | KSAN | Completed | Load_574551 | Hope - 410 | 2026-08-05 08:33 | 2026-08-05 08:33 | 2026-08-05 09:29 | 2026-08-05 09:30 | 2026-08-05 09:29 | 2026-08-05 09:31 | 2026-08-05 09:31 | 2026-08-05 09:31 |  |  | Fair | No | Customer say they didn’t make a report and that the Premesis is found okay
Non-Outage | J.E.26.08.06623 | C001874760 | Rochaine Hussey | KSAN | Completed | Load_248378 | Hope - 410 | 2026-08-05 08:33 | 2026-08-05 08:33 | 2026-08-05 12:41 | 2026-08-05 14:11 | 2026-08-05 14:11 | 2026-08-05 14:50 | 2026-08-05 14:51 | 2026-08-05 14:51 |  |  | Fair | No | Slack connection found in meter socket Issue resolved 116/117/234v
Outage | J.E.26.08.07453 | C001874761 | Fitzroy Turner | KSAS | Completed | Load_266521 | Rockfort - 210 | 2026-08-05 08:33 | 2026-08-05 08:34 | 2026-08-05 09:27 | 2026-08-05 09:28 | 2026-08-05 09:30 | 2026-08-05 09:30 | 2026-08-05 09:31 | 2026-08-05 09:31 |  |  | Fair | No | Customer premises found with electricity supply
Non-Outage | J.E.26.08.06702 | C001874763 | Fredrick Hamilton | KSAN | Completed | Load_239185 | Washington Blvd - 610 | 2026-08-05 08:34 | 2026-08-05 08:36 | 2026-08-05 08:41 | 2026-08-05 11:45 | 2026-08-05 12:01 | 2026-08-05 12:13 | 2026-08-05 12:14 | 2026-08-05 12:14 |  |  | Fair | No | Corrosion defect detected in customer meter socket Customer advised
Non-Outage | J.E.26.08.06978 | C001874766 | Fredrick Hamilton | KSAN | Completed | Load_256909 | Washington Blvd - 810 | 2026-08-05 08:34 | 2026-08-05 08:36 | 2026-08-05 08:41 | 2026-08-05 11:38 | 2026-08-05 11:38 | 2026-08-05 11:44 | 2026-08-05 11:44 | 2026-08-05 11:44 |  |  | Fair | No | 245v/123.9v/120.8v obtained Please have emergency inspect transformer fluctuating voltage affecting customers
Non-Outage | J.E.26.08.07382 | C001874765 | Fredrick Hamilton | KSAN | Completed | Load_256909 | Washington Blvd - 810 | 2026-08-05 08:34 | 2026-08-05 08:36 | 2026-08-05 08:41 | 2026-08-05 11:16 | 2026-08-05 11:20 | 2026-08-05 11:37 | 2026-08-05 11:37 | 2026-08-05 11:37 |  |  | Fair | No | 246v/124v/121v obtained Please have emergency check transformer multiple customers experiencing low voltage
Non-Outage | J.E.26.08.07082 | C001874768 | Fredrick Hamilton | KSAS | Completed | Load_258800 | Duhaney - 310 | 2026-08-05 08:35 | 2026-08-05 08:55 | 2026-08-05 09:11 | 2026-08-05 10:59 | 2026-08-05 11:00 | 2026-08-05 11:15 | 2026-08-05 11:15 | 2026-08-05 11:15 |  |  | Fair | No | 243v121v/121v obtained Please send field service error code 220 seen on meter Customer has full at location
Non-Outage | J.E.26.08.07598 | C001874769 | Fredrick Hamilton | KSAS | Completed | Load_262259 | Duhaney - 310 | 2026-08-05 08:35 | 2026-08-05 08:53 | 2026-08-05 08:56 | 2026-08-05 09:43 | 2026-08-05 10:02 | 2026-08-05 10:57 | 2026-08-05 10:57 | 2026-08-05 10:57 |  |  | Fair | No | 236.4v/118.5v/117v obtained Pole#217892Defective neutral detected at pothead same was corrected Clamps changed at pole 3 penunion and 2 clamps used
Outage | J.E.26.08.04756 | C001874767 | Edward Royal | KSAS | Completed | Load_258045 | Rockfort - 410 | 2026-08-05 08:35 | 2026-08-05 08:39 | 2026-08-05 20:42 | 2026-08-05 20:43 | 2026-08-05 20:53 | 2026-08-05 21:33 | 2026-08-05 21:33 | 2026-08-05 21:33 |  |  | Fair | No | Spliced and reconnected service phase using 2 single bolt clamp
Non-Outage | J.E.26.08.06741 | C001874789 | Roemello Brown | Trelawny | Completed | Load_267437 | Greenwood - 110 | 2026-08-05 08:40 | 2026-08-05 08:42 | 2026-08-05 14:45 | 2026-08-05 14:46 | 2026-08-05 15:13 | 2026-08-05 15:13 | 2026-08-05 15:31 | 2026-08-05 15:31 |  |  | Fair | No | Customer meter socket defective inform the customer to get an private electrician to get it changed Voltage found 114/110/224Voltage leave 114/110/224
Non-Outage | J.E.26.08.06924 | C001874790 | Roemello Brown | Trelawny | Completed | Load_267437 | Greenwood - 110 | 2026-08-05 08:40 | 2026-08-05 08:42 | 2026-08-05 15:46 | 2026-08-05 15:46 | 2026-08-05 15:46 | 2026-08-05 15:46 | 2026-08-05 16:14 | 2026-08-05 16:14 |  |  | Fair | No | Corrosion at the pothead have linkets installed Voltage found 108/110/218Voltage leave 111/110/221
Non-Outage | J.E.26.08.06995 | C001874787 | Roemello Brown | Trelawny | Completed | Load_1001528 | Duncans - 110 | 2026-08-05 08:40 | 2026-08-05 08:42 | 2026-08-05 10:07 | 2026-08-05 11:10 | 2026-08-05 11:09 | 2026-08-05 11:09 | 2026-08-05 11:12 | 2026-08-05 11:12 |  |  | Fair | No | This is an hexing box please send field service team to have the box check out voltage low Voltage found 103/110/213Voltage leave 103/110/213Hex#06372Hx# 27121822
Non-Outage | J.E.26.08.06999 | C001874788 | Roemello Brown | Trelawny | Completed | Load_269256 | Duncans - 210 | 2026-08-05 08:40 | 2026-08-05 08:42 | 2026-08-05 10:07 | 2026-08-05 11:13 | 2026-08-05 11:12 | 2026-08-05 11:12 | 2026-08-05 11:14 | 2026-08-05 11:14 |  |  | Fair | No | This is an hexing box please send field service team to have box check outVoltage low Voltage found 103/110/213Voltage leave 103/110/213Hex# 06372Hx# 27121822
Non-Outage | J.E.26.08.07002 | C001874785 | Roemello Brown | Trelawny | Completed | Load_260728 | Martha Brae - 110 | 2026-08-05 08:40 | 2026-08-05 08:42 | 2026-08-05 10:07 | 2026-08-05 10:48 | 2026-08-05 11:05 | 2026-08-05 11:05 | 2026-08-05 11:09 | 2026-08-05 11:09 |  |  | Fair | No | This is an hexing box please send field service team to have the box checked out voltage low Voltage found 110/103/213Voltage leave 110/103/213Hex# 06372Hx# 27121822
Outage | J.E.26.08.07519 | C001874784 | Edward Royal | KSAS | Completed | Load_1002886 | Rockfort - 410 | 2026-08-05 08:40 | 2026-08-05 08:41 | 2026-08-05 08:55 | 2026-08-05 09:03 | 2026-08-05 09:02 | 2026-08-05 09:03 | 2026-08-05 09:03 | 2026-08-05 09:03 |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.07.37935 | C001874793 | Roemello Brown | Trelawny | Completed | Load_294320 | Greenwood - 110 | 2026-08-05 08:41 | 2026-08-05 08:42 | 2026-08-05 10:03 | 2026-08-05 13:28 | 2026-08-05 14:43 | 2026-08-05 14:43 | 2026-08-05 14:45 | 2026-08-05 14:45 |  |  | Fair | No | Premises found working okayVoltage found 116/116/232Voltage leave 116/116/232
Non-Outage | J.E.26.07.39066 | C001874794 | Roemello Brown | Trelawny | Completed | Load_241008 | Martha Brae - 110 | 2026-08-05 08:41 | 2026-08-05 08:42 | 2026-08-05 10:11 | 2026-08-05 12:51 | 2026-08-05 12:59 | 2026-08-05 13:14 | 2026-08-05 13:19 | 2026-08-05 13:19 |  |  | Fair | No | Customer meter socket corroded inform customer to get an private electrician to have meter socket replaced Voltage found 116/118/235Voltage leave 116/118/235
Non-Outage | J.E.26.08.04648 | C001874792 | Roemello Brown | Trelawny | Completed | Load_252746 | Duncans - 110 | 2026-08-05 08:41 | 2026-08-05 08:42 | 2026-08-05 10:13 | 2026-08-05 11:15 | 2026-08-05 11:28 | 2026-08-05 11:28 | 2026-08-05 11:41 | 2026-08-05 11:41 |  |  | Fair | No | Premises found working okay I informed the person at the premises to tell the owner to get an electrician to check their premises Voltage found 117/117/235Voltage leave 117/117/235
Non-Outage | J.E.26.08.05307 | C001874791 | Roemello Brown | Trelawny | Completed | Load_302351 | Duncans - 110 | 2026-08-05 08:41 | 2026-08-05 08:42 | 2026-08-05 11:42 | 2026-08-05 11:45 | 2026-08-05 12:12 | 2026-08-05 12:12 | 2026-08-05 12:35 | 2026-08-05 12:35 |  |  | Fair | No | Premises found working okayVoltage found 108/108/216Voltage leave 108/108/216
Non-Outage | J.E.26.07.06350 | C001874797 | Barrington Brown | St.James | Completed | Load_241445 | Queens Drive - 710 | 2026-08-05 08:45 | 2026-08-05 08:47 | 2026-08-05 11:50 | 2026-08-05 11:51 | 2026-08-05 12:27 | 2026-08-05 12:27 | 2026-08-05 12:27 | 2026-08-05 12:27 |  |  | Fair | No | Checked and found ok
Non-Outage | J.E.26.07.06365 | C001874796 | Barrington Brown | St.James | Completed | Load_251546 | Queens Drive - 710 | 2026-08-05 08:45 | 2026-08-05 08:47 | 2026-08-05 09:42 | 2026-08-05 09:43 | 2026-08-05 10:28 | 2026-08-05 10:31 | 2026-08-05 10:32 | 2026-08-05 10:32 |  |  | Fair | No | Checked and found ok
Non-Outage | J.E.26.07.07294 | C001874795 | Barrington Brown | St.James | Completed | Load_261935 | Queens Drive - 710 | 2026-08-05 08:45 | 2026-08-05 08:47 | 2026-08-05 10:32 | 2026-08-05 10:33 | 2026-08-05 11:25 | 2026-08-05 11:50 | 2026-08-05 11:50 | 2026-08-05 11:50 |  |  | Fair | No | Checked and found ok
Non-Outage | J.E.26.06.26508 | C001874808 | Odeanie Davis | KSAS | Completed | Load_256552 | Greenwich - 510 | 2026-08-05 08:48 | 2026-08-05 08:50 | 2026-08-05 10:43 | 2026-08-05 10:48 | 2026-08-05 10:47 | 2026-08-05 10:56 | 2026-08-05 10:48 | 2026-08-05 10:48 |  |  | Fair | No | Customer stated that they don’t have any power issues
Non-Outage | J.E.26.07.35110 | C001874805 | Odeanie Davis | KSAS | Completed | Load_294227 | Greenwich - 310 | 2026-08-05 08:48 | 2026-08-05 08:50 | 2026-08-05 09:55 | 2026-08-05 11:31 | 2026-08-05 11:31 | 2026-08-05 11:42 | 2026-08-05 11:31 | 2026-08-05 11:31 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.07.37168 | C001874807 | Odeanie Davis | KSAS | Completed | Load_290940 | Greenwich - 410 | 2026-08-05 08:48 | 2026-08-05 08:50 | 2026-08-05 09:27 | 2026-08-05 09:27 | 2026-08-05 09:27 | 2026-08-05 09:32 | 2026-08-05 09:28 | 2026-08-05 09:28 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.07.40168 | C001874806 | Odeanie Davis | KSAS | Completed | Load_242539 | Greenwich - 310 | 2026-08-05 08:48 | 2026-08-05 08:50 | 2026-08-05 09:07 | 2026-08-05 09:07 | 2026-08-05 09:15 | 2026-08-05 09:23 | 2026-08-05 09:24 | 2026-08-05 09:24 |  |  | Fair | No | Defective wire at pothead, customer was advised to contact their electrician
Non-Outage | J.E.26.08.04710 | C001874809 | Odeanie Davis | KSAS | Completed | Load_248285 | Greenwich - 510 | 2026-08-05 08:48 | 2026-08-05 08:50 | 2026-08-05 09:33 | 2026-08-05 14:18 | 2026-08-05 14:17 | 2026-08-05 13:59 | 2026-08-05 14:18 | 2026-08-05 14:18 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.04734 | C001874810 | Odeanie Davis | KSAS | Completed | Load_239966 | Greenwich - 510 | 2026-08-05 08:48 | 2026-08-05 08:50 | 2026-08-05 09:37 | 2026-08-05 14:19 | 2026-08-05 14:18 | 2026-08-05 14:30 | 2026-08-05 14:19 | 2026-08-05 14:19 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.07.25842 | C001874812 | Odeanie Davis | KSAS | Completed | Load_268141 | Greenwich - 710 | 2026-08-05 08:49 | 2026-08-05 08:50 | 2026-08-05 10:07 | 2026-08-05 14:17 | 2026-08-05 14:16 | 2026-08-05 13:31 | 2026-08-05 14:17 | 2026-08-05 14:17 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.04739 | C001874811 | Odeanie Davis | KSAS | Completed | Load_252777 | Greenwich - 510 | 2026-08-05 08:49 | 2026-08-05 08:50 | 2026-08-05 09:46 | 2026-08-05 11:06 | 2026-08-05 11:06 | 2026-08-05 11:19 | 2026-08-05 11:07 | 2026-08-05 11:07 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.06508 | C001874813 | Odeanie Davis | KSAS | Completed | Load_263810 | Greenwich - 710 | 2026-08-05 08:49 | 2026-08-05 08:51 | 2026-08-05 10:17 | 2026-08-05 10:33 | 2026-08-05 10:33 | 2026-08-05 10:37 | 2026-08-05 10:37 | 2026-08-05 10:37 |  |  | Fair | No | 116v/0V at location from rammi box, meter not communicating, customer is left with partial supply, meter needs to be changed, rammi team needed.
Outage | J.E.26.08.07668 | C001874814 | Fitzroy Turner | KSAS | Completed | Load_259337 | Up Park Camp - 510 | 2026-08-05 08:50 | 2026-08-05 08:51 | 2026-08-05 09:25 | 2026-08-05 09:25 | 2026-08-05 09:25 | 2026-08-05 09:25 | 2026-08-05 09:26 | 2026-08-05 09:26 |  |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.08.07656 | C001874824 | Denton Williams | Portland | Completed | Load_349987 | Port Antonio - 410 | 2026-08-05 08:52 | 2026-08-05 08:53 | 2026-08-05 14:04 | 2026-08-05 14:04 | 2026-08-05 15:42 | 2026-08-05 15:44 | 2026-08-05 15:47 | 2026-08-05 15:47 |  |  | Fair | No | #2 csr insulated wire corroded, need 305 feet of 2# wire to change it
Outage | J.E.26.08.07667 | C001874825 | Omar King | St.Ann | Completed | Load_265231 | Roaring River - 210 | 2026-08-05 08:52 | 2026-08-05 08:52 | 2026-08-05 16:05 | 2026-08-05 16:06 | 2026-08-05 17:21 | 2026-08-05 17:23 | 2026-08-05 17:23 | 2026-08-05 17:23 |  |  | Fair | No | Found 30 amp trip saver open cause by defective switch mechanism please refer to maintenance. Temporary work as been carried out to restore customer
Non-Outage | J.E.26.08.06334 | C001874827 | Fitzroy Turner |  | Completed |  |  | 2026-08-05 08:55 | 2026-08-05 08:57 | 2026-08-05 09:21 | 2026-08-05 09:21 | 2026-08-05 09:21 | 2026-08-05 09:21 | 2026-08-05 09:21 | 2026-08-05 09:21 | BangingWires |  | EarthMovement | No | Customer premises found with electricity supply
Outage | J.E.26.08.07486 | C001874828 | Edward Royal | KSAS | Completed | Load_252659 | Rockfort - 410 | 2026-08-05 09:03 | 2026-08-05 09:04 | 2026-08-05 15:39 | 2026-08-05 15:40 | 2026-08-05 15:39 | 2026-08-05 15:40 | 2026-08-05 15:40 | 2026-08-05 15:40 |  |  | Fair | No | Service pothead using 3 single bolt clamp spliced and reconnected service phase
Outage | J.E.26.08.07683 | C001874836 | Fitzroy Turner | KSAS | Completed | Load_253645 | Cane River - 310 | 2026-08-05 09:12 | 2026-08-05 09:23 | 2026-08-05 09:34 | 2026-08-05 09:41 | 2026-08-05 09:41 | 2026-08-05 10:06 | 2026-08-05 10:45 | 2026-08-05 10:45 | Fire |  | Fair | No | Found tree wire open secondary phase and neutral cut down cause by win .use 120ft of #2 aluminum conductor 4 #2 preform and 6 one bolt clamps and one D/iron to carry out repair supply restored to areas
Non-Outage | J.E.26.08.07464 | C001874837 | Milton Charlton |  | Completed |  |  | 2026-08-05 09:16 | 2026-08-05 09:16 | 2026-08-05 10:55 | 2026-08-05 11:39 | 2026-08-05 12:46 | 2026-08-05 12:50 | 2026-08-05 12:47 | 2026-08-05 12:47 | BrokenWire |  | Fair | No | Reconnect customer meter by J.P.S. Escalation.
Outage | J.E.26.08.07689 | C001874838 | Christopher Edwards | KSAN | Completed | Load_254366 | Constant Spring - 210 | 2026-08-05 09:18 | 2026-08-05 09:19 | 2026-08-05 11:30 | 2026-08-05 11:31 | 2026-08-05 11:49 | 2026-08-05 12:51 | 2026-08-05 12:52 | 2026-08-05 12:52 |  |  | Fair | No | Remake burnt phase joint At poleUsing (1) one bolt clamps Voltage:114v (110 meter)
Outage | J.E.26.08.06718 | C001874884 | Fitzroy Turner | KSAS | Completed | Load_266609 | Cane River - 310 | 2026-08-05 09:24 | 2026-08-05 12:34 | 2026-08-05 13:28 | 2026-08-05 13:29 | 2026-08-05 13:39 | 2026-08-05 13:48 | 2026-08-05 13:50 | 2026-08-05 13:50 | BrokenWire |  | Fair | No | Found tree wire service neutral burnt off at pole use one clamp and 3ft service neutral to splice and retention wires service return to customer
Outage | J.E.26.08.07482 | C001874886 | Moses Elliston | St.Catherine | Completed | Load_242257 | Tredegar - 410 | 2026-08-05 09:26 | 2026-08-05 09:28 | 2026-08-05 10:35 | 2026-08-05 10:36 | 2026-08-05 10:35 | 2026-08-05 10:27 | 2026-08-05 10:38 | 2026-08-05 10:38 |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.08.07620 | C001874885 | Christopher West | St.Catherine | Completed | Load_240416 | Tredegar - 210 | 2026-08-05 09:26 | 2026-08-05 09:29 | 2026-08-05 10:12 | 2026-08-05 10:13 | 2026-08-05 10:12 | 2026-08-05 11:00 | 2026-08-05 11:07 | 2026-08-05 11:07 |  |  | Fair | No | 3 wire service had a damaged section, used 6’ #6 triplex 4 clamps & 2 pen unions for repairs, V/R 117v x2 234v, customer now okay.
Outage | J.E.26.08.06841 | C001874887 | Moses Elliston | St.Catherine | Completed | Load_557299 | Tredegar - 410 | 2026-08-05 09:27 | 2026-08-05 09:28 | 2026-08-05 10:39 | 2026-08-05 10:40 | 2026-08-05 10:39 | 2026-08-05 10:41 | 2026-08-05 10:41 | 2026-08-05 10:41 |  |  | Fair | No | Credit added to prepaid account.
Non-Outage | J.E.26.08.03444 | C001874908 | Odaine Johnson |  | Completed |  |  | 2026-08-05 09:29 | 2026-08-05 09:31 | 2026-08-05 10:37 | 2026-08-05 12:23 | 2026-08-05 12:25 | 2026-08-05 12:25 | 2026-08-05 12:26 | 2026-08-05 12:26 |  |  | Fair | No | Unable to locate customer multiple efforts made to contact customer but unsuccessful
Non-Outage | J.E.26.08.03482 | C001874906 | Odaine Johnson | Clarendon | Completed | Load_268788 | Monymusk - 210 | 2026-08-05 09:29 | 2026-08-05 09:30 | 2026-08-05 10:37 | 2026-08-05 14:57 | 2026-08-05 15:01 | 2026-08-05 15:01 | 2026-08-05 15:03 | 2026-08-05 15:03 |  |  | Fair | No | Loose phase connection found at pole and retention voltage reading 110/112/222 volts
Non-Outage | J.E.26.08.03809 | C001874905 | Odaine Johnson | Clarendon | Completed | Load_257855 | Monymusk - 210 | 2026-08-05 09:29 | 2026-08-05 09:30 | 2026-08-05 10:37 | 2026-08-05 12:27 | 2026-08-05 12:29 | 2026-08-05 12:29 | 2026-08-05 12:30 | 2026-08-05 12:30 |  |  | Fair | No | Customer stated they didn’t make any report
Non-Outage | J.E.26.08.05168 | C001874902 | Odaine Johnson |  | Completed |  |  | 2026-08-05 09:29 | 2026-08-05 09:30 | 2026-08-05 10:38 | 2026-08-05 12:30 | 2026-08-05 12:36 | 2026-08-05 12:36 | 2026-08-05 12:38 | 2026-08-05 12:38 | BrokenPole |  | EarthMovement | No | One span of broken secondary neutral found, emergency team needed
Non-Outage | J.E.26.08.06273 | C001874904 | Odaine Johnson | Clarendon | Completed | Load_351198 | Parnassus - 310 | 2026-08-05 09:29 | 2026-08-05 09:30 | 2026-08-05 10:38 | 2026-08-05 15:04 | 2026-08-05 15:20 | 2026-08-05 15:20 | 2026-08-05 15:21 | 2026-08-05 15:21 |  |  | Fair | No | Premises not found multiple efforts made to contact customer but was unsuccessful
Non-Outage | J.E.26.08.06286 | C001874900 | Odaine Johnson | Clarendon | Completed | Load_262700 | Parnassus - 210 | 2026-08-05 09:29 | 2026-08-05 09:30 | 2026-08-05 10:38 | 2026-08-05 11:36 | 2026-08-05 11:41 | 2026-08-05 11:42 | 2026-08-05 11:43 | 2026-08-05 11:43 | BrokenPole |  | Fair | No | Contacted customer and customer stated that the issue was resolved already
Non-Outage | J.E.26.08.06649 | C001874901 | Odaine Johnson | Clarendon | Completed | Load_573392 | Parnassus - 310 | 2026-08-05 09:29 | 2026-08-05 09:30 | 2026-08-05 10:38 | 2026-08-05 12:39 | 2026-08-05 12:55 | 2026-08-05 12:55 | 2026-08-05 12:56 | 2026-08-05 12:56 |  |  | Fair | No | Customer is connected to rami box # HEX00877
Non-Outage | J.E.26.08.07390 | C001874899 | Odaine Johnson | Clarendon | Completed | Load_246213 | Parnassus - 210 | 2026-08-05 09:29 | 2026-08-05 09:30 | 2026-08-05 10:38 | 2026-08-05 15:22 | 2026-08-05 15:36 | 2026-08-05 15:36 | 2026-08-05 15:37 | 2026-08-05 15:37 |  |  | Fair | No | Multiple efforts made to contact customer but was unsuccessful
Non-Outage | J.E.26.08.07632 | C001874898 | Odaine Johnson | Clarendon | Completed | Load_570300 | Parnassus - 310 | 2026-08-05 09:29 | 2026-08-05 09:30 | 2026-08-05 10:38 | 2026-08-05 12:58 | 2026-08-05 12:57 | 2026-08-05 12:58 | 2026-08-05 12:58 | 2026-08-05 12:58 |  |  | Fair | No | Customer contacted to a rami system
Non-Outage | J.E.26.08.07670 | C001874888 | Odaine Johnson | Clarendon | Completed | Load_292535 | Parnassus - 310 | 2026-08-05 09:29 | 2026-08-05 09:30 | 2026-08-05 10:38 | 2026-08-05 11:17 | 2026-08-05 11:29 | 2026-08-05 11:29 | 2026-08-05 11:30 | 2026-08-05 11:30 |  |  | Fair | No | Try to contact customer but no answer and no proper direction was given
Outage | J.E.26.08.06688 | C001874909 | Fitzroy Turner | KSAS | Completed | Load_244328 | Rockfort - 210 | 2026-08-05 09:30 | 2026-08-05 09:31 | 2026-08-05 12:45 | 2026-08-05 12:46 | 2026-08-05 13:08 | 2026-08-05 13:09 | 2026-08-05 13:10 | 2026-08-05 13:10 |  |  | Fair | No | Found tree phase primary one phase found blown replaced one 8 amps fuse.supply restored to customer
Outage | J.E.26.08.07257 | C001874911 | Christopher West | St.Catherine | Completed | Load_241890 | Rhodens Pen - 210 | 2026-08-05 09:32 | 2026-08-05 09:52 | 2026-08-05 11:56 | 2026-08-05 11:56 | 2026-08-05 11:56 | 2026-08-05 12:20 | 2026-08-05 12:33 | 2026-08-05 12:33 |  |  | Fair | No | Broken open secondary lower phase caused from an illegal connection, a 50kva transformer was de-energized, used 4 clamps for repairs, transformer was re-energized, area now ok.
Non-Outage | J.E.26.07.38039 | C001874912 | Christopher West | St.Catherine | Completed | Load_568135 | Rhodens Pen - 210 | 2026-08-05 09:33 | 2026-08-05 09:52 | 2026-08-05 13:24 | 2026-08-05 13:24 | 2026-08-05 13:42 | 2026-08-05 14:13 | 2026-08-05 14:13 | 2026-08-05 14:13 | BrokenPole |  | Fair | No | Kindly refer to streetlight personnel.
Outage | J.E.26.08.06624 | C001874929 | Rusean Allen | KSAS | Completed | Load_252512 | Rockfort - 410 | 2026-08-05 09:38 | 2026-08-06 08:11 | 2026-08-06 08:42 | 2026-08-06 08:42 | 2026-08-06 08:59 | 2026-08-06 09:00 | 2026-08-06 09:01 | 2026-08-06 09:01 |  |  | Fair | No | Premises locked customer phone went unanswered
Outage | J.E.26.08.06661 | C001874926 | Edward Royal | KSAS | Completed | Load_257873 | Rockfort - 210 | 2026-08-05 09:38 | 2026-08-05 09:52 | 2026-08-05 12:15 | 2026-08-05 12:16 | 2026-08-05 12:28 | 2026-08-05 12:37 | 2026-08-05 12:38 | 2026-08-05 12:38 |  |  | Fair | No | Premises found close unable to communicate with customer
Non-Outage | J.E.26.07.38772 | C001874936 | Christopher West | St.Catherine | Completed | Load_556367 | Rhodens Pen - 210 | 2026-08-05 09:47 | 2026-08-05 09:53 | 2026-08-05 12:33 | 2026-08-05 12:34 | 2026-08-05 13:00 | 2026-08-05 13:18 | 2026-08-05 13:24 | 2026-08-05 13:24 |  |  | Fair | No | Customer seems to have an internal issue, V/R 119v x2 238v, customer advised accordingly.
Outage | J.E.26.08.07707 | C001874939 | Fitzroy Turner | KSAS | Completed | Load_575102 | Cane River - 410 | 2026-08-05 09:50 | 2026-08-05 09:52 | 2026-08-05 11:13 | 2026-08-05 11:19 | 2026-08-05 11:46 | 2026-08-05 11:50 | 2026-08-05 11:52 | 2026-08-05 11:52 |  |  | Fair | No | Found two 5amps found blown at bank of three 2 50kva and one 100kva transformer replaced two 5amps fuse supply restored to customer
Non-Outage | J.E.26.08.07703 | C001874942 | Denton Williams | Portland | Completed | Load_572639 | Port Antonio - 410 | 2026-08-05 09:51 | 2026-08-05 09:55 | 2026-08-05 13:25 | 2026-08-05 13:26 | 2026-08-05 13:52 | 2026-08-05 13:58 | 2026-08-05 14:04 | 2026-08-05 14:04 |  |  | Fair | No | Customer states that is election sorted it out
Outage | J.E.26.08.07666 | C001874941 | Radcliffe Coleman | St.Catherine | Completed | Load_237641 | Twickenham - 310 | 2026-08-05 09:51 | 2026-08-05 09:53 | 2026-08-05 10:41 | 2026-08-05 10:42 | 2026-08-05 10:57 | 2026-08-05 11:21 | 2026-08-05 11:22 | 2026-08-05 11:22 |  |  | Fair | No | Location found with two blown fuses at pole# 0104410 bank three 50kva bank checked found okay fuses refuse and closed customer now okay.
Outage | J.E.26.08.07677 | C001874944 | Raymond Carr | St.Ann | Completed | Load_245285 | Upper White River - 110 | 2026-08-05 09:53 | 2026-08-05 09:57 | 2026-08-05 13:45 | 2026-08-05 13:45 | 2026-08-05 14:18 | 2026-08-05 14:16 | 2026-08-05 14:21 | 2026-08-05 14:21 | BrokenWire |  | Fair | No | Supply was reconnected using 100ft#6 triplex, 3 one bolt clamps. Left okay.
Outage | J.E.26.08.07693 | C001874945 | Raymond Carr | St.Ann | Completed | Load_251915 | Upper White River - 110 | 2026-08-05 09:54 | 2026-08-05 09:57 | 2026-08-05 13:20 | 2026-08-05 13:20 | 2026-08-05 13:32 | 2026-08-05 13:34 | 2026-08-05 13:45 | 2026-08-05 13:45 |  |  | Fair | No | Several calls to contact number went unanswered.
Outage | J.E.26.08.07697 | C001874967 | Swon Miller | St.James | Completed | Load_257366 | Queens Drive - 710 | 2026-08-05 10:06 | 2026-08-05 14:53 | 2026-08-05 14:58 | 2026-08-05 18:45 | 2026-08-05 20:05 | 2026-08-05 20:18 | 2026-08-05 20:26 | 2026-08-05 20:26 | BrokenWire |  | Fair | No | Check and found okay voltage found 114/115/231 customer states that problem was resolved voltage left 115/114/231
Outage | J.E.26.08.07705 | C001874968 | Dean- Smith | Hanover | Completed | Load_574027 | Orange Bay - 310 | 2026-08-05 10:07 | 2026-08-05 15:48 | 2026-08-05 20:26 | 2026-08-05 20:26 | 2026-08-05 20:26 | 2026-08-05 20:26 | 2026-08-05 20:29 | 2026-08-05 20:29 |  |  | Fair | No | Area was restored
Outage | J.E.26.08.07706 | C001874969 | Horace Malcolm | St.James | Completed | Load_245028 | Bogue - 610 | 2026-08-05 10:07 | 2026-08-05 10:09 | 2026-08-05 11:55 | 2026-08-05 11:55 | 2026-08-05 13:49 | 2026-08-05 14:40 | 2026-08-05 14:40 | 2026-08-05 14:40 |  |  | Fair | No | Check and found meter disconnected however call center system down for the moment so meter unable to reconnected
Non-Outage | J.E.26.08.07695 | C001874972 | Evan Spaulding |  | Completed |  |  | 2026-08-05 10:08 | 2026-08-05 10:08 | 2026-08-05 10:21 | 2026-08-05 10:22 | 2026-08-05 10:22 | 2026-08-05 10:52 | 2026-08-05 10:54 | 2026-08-05 10:54 |  |  | Fair | No | Use 4-1 bolt clamps on Transformer drop leads,voltage left 116v,117v, 233v.
Outage | J.E.26.08.07690 | C001874983 | Denton Williams | Portland | Completed | Load_248931 | Port Antonio - 410 | 2026-08-05 10:12 | 2026-08-05 10:13 | 2026-08-05 10:49 | 2026-08-05 10:49 | 2026-08-05 12:03 | 2026-08-05 12:28 | 2026-08-05 12:29 | 2026-08-05 12:29 |  |  | Fair | No | Use three clamps to correct broken secondary jumper.
Outage | J.E.26.08.07518 | C001874984 | Tyrese Williams | St.Ann | Completed | Load_266713 | Cardiff Hall - 210 | 2026-08-05 10:13 | 2026-08-05 10:13 | 2026-08-05 10:32 | 2026-08-05 10:46 | 2026-08-05 10:45 | 2026-08-05 11:21 | 2026-08-05 11:21 | 2026-08-05 11:21 |  |  | Fair | No | Remade service joint at pothead use 1 pg clamp voltage left 120/118/238
Non-Outage | J.E.26.08.07672 | C001874994 | Locksley Allen | St.Mary | Completed | Load_245649 | Highgate - 210 | 2026-08-05 10:15 | 2026-08-05 10:17 | 2026-08-05 11:38 | 2026-08-05 12:54 | 2026-08-05 12:54 | 2026-08-05 13:13 | 2026-08-05 13:11 | 2026-08-05 13:11 |  |  | Fair | No | Pothead found corroded,clean up connectors at pothead Voltage at meter socket phase to phase 230v. Phase to neutral 14&116vMeter left working
Non-Outage | J.E.26.08.07716 | C001874993 | Locksley Allen | St.Mary | Completed | Load_264075 | Annotto Bay - 210 | 2026-08-05 10:15 | 2026-08-05 10:17 | 2026-08-05 10:46 | 2026-08-05 11:35 | 2026-08-05 11:35 | 2026-08-05 11:41 | 2026-08-05 11:38 | 2026-08-05 11:38 |  |  | Fair | No | This area is Rami. Voltage at panel phase to phase 0Phase to neutral 113&116. Please check Rami system as soon as possible
Non-Outage | J.E.26.08.05026 | C001874999 | Oraine Minto | St.Ann | Completed | Load_260609 | Ocho Rios - 310 | 2026-08-05 10:17 | 2026-08-05 10:18 | 2026-08-05 13:25 | 2026-08-05 15:21 | 2026-08-05 15:20 | 2026-08-05 15:21 | 2026-08-05 15:22 | 2026-08-05 15:22 |  |  | Fair | No | 234v 117v 117v The only issue I see is a damaged primary neutral over tree
Non-Outage | J.E.26.08.05111 | C001874998 | Oraine Minto | St.Ann | Completed | Load_267230 | Ocho Rios - 410 | 2026-08-05 10:17 | 2026-08-05 10:18 | 2026-08-05 11:03 | 2026-08-05 11:04 | 2026-08-05 11:09 | 2026-08-05 11:09 | 2026-08-05 11:10 | 2026-08-05 11:10 |  |  | Fair | No | Issue was resolved customer states
Non-Outage | J.E.26.08.05232 | C001874996 | Oraine Minto | St.Ann | Completed | Load_267230 | Ocho Rios - 410 | 2026-08-05 10:17 | 2026-08-05 10:18 | 2026-08-05 11:12 | 2026-08-05 11:12 | 2026-08-05 11:12 | 2026-08-05 11:12 | 2026-08-05 11:14 | 2026-08-05 11:14 |  |  | Fair | No | Issue was resolved
Non-Outage | J.E.26.08.04109 | C001875000 | Oraine Minto | St.Ann | Completed | Load_260609 | Ocho Rios - 310 | 2026-08-05 10:18 | 2026-08-05 10:18 | 2026-08-05 13:23 | 2026-08-05 13:24 | 2026-08-05 13:23 | 2026-08-05 15:17 | 2026-08-05 15:20 | 2026-08-05 15:20 |  |  | Fair | No | Refer to maintenance Primary neutral mid spond about 3 strands holding it together above a breadfruit tree
Outage | J.E.26.08.07740 | C001875013 | Fitzroy Turner | KSAS | Completed | Load_243254 | Up Park Camp - 510 | 2026-08-05 10:28 | 2026-08-05 10:29 | 2026-08-05 12:00 | 2026-08-05 12:00 | 2026-08-05 12:21 | 2026-08-05 12:43 | 2026-08-05 12:45 | 2026-08-05 12:45 |  |  | Fair | No | Found tree wire service phase broke off at pole use one clamp to carry out repair supply restored to customer
Non-Outage | J.E.26.07.39522 | C001875022 | Tyrese Williams | St.Ann | Completed | Load_262615 | Cardiff Hall - 310 | 2026-08-05 10:30 | 2026-08-05 10:37 | 2026-08-05 10:44 | 2026-08-05 11:22 | 2026-08-05 13:12 | 2026-08-05 13:15 | 2026-08-05 13:16 | 2026-08-05 13:16 |  |  | Fair | No | Remade service wire neutral joint at pole use1 pg clamp
Outage | J.E.26.08.07185 | C001875030 | Edward Royal | KSAS | Completed | Load_244176 | Hunts Bay - 310 | 2026-08-05 10:37 | 2026-08-05 10:38 | 2026-08-05 10:52 | 2026-08-05 10:52 | 2026-08-05 10:58 | 2026-08-05 11:35 | 2026-08-05 11:36 | 2026-08-05 11:36 |  |  | Fair | No | Primary jumper burn off from switch top reffered to live line crew
Outage | J.E.26.08.07759 | C001875039 | Dwayne Cohen | KSAS | Completed | Load_259209 | Greenwich - 410 | 2026-08-05 10:48 | 2026-08-05 10:57 | 2026-08-05 11:07 | 2026-08-05 11:08 | 2026-08-05 11:21 | 2026-08-05 11:44 | 2026-08-05 11:46 | 2026-08-05 11:46 |  |  | Fair | No | Defective 25KVA Transformer found.
Non-Outage | J.E.26.08.04178 | C001875054 | Orville Lee | St.Catherine | Completed | Load_245048 | Twickenham - 210 | 2026-08-05 10:49 | 2026-08-05 10:50 | 2026-08-05 11:04 | 2026-08-05 11:05 | 2026-08-05 11:04 | 2026-08-05 11:04 | 2026-08-05 11:05 | 2026-08-05 11:05 |  |  | Fair | No | Pothead connection corroded 1 Penn union & 1 one bolt clamp usedVoltage 115V
Non-Outage | J.E.26.08.06388 | C001875053 | Orville Lee | Portmore | Completed | Load_258707 | Naggo Head - 510 | 2026-08-05 10:49 | 2026-08-05 10:50 | 2026-08-05 11:05 | 2026-08-05 12:33 | 2026-08-05 13:07 | 2026-08-05 13:16 | 2026-08-05 13:16 | 2026-08-05 13:16 |  |  | Fair | No | Premise found ok upon arrival. Issue was resolved by a technician Voltage 116V117V234V
Outage | J.E.26.08.07739 | C001875059 | Romaine Roberts | St.Mary | Completed | Load_247430 | Highgate - 210 | 2026-08-05 10:53 | 2026-08-05 15:32 | 2026-08-05 16:20 | 2026-08-05 16:21 | 2026-08-05 18:17 | 2026-08-05 18:31 | 2026-08-05 18:33 | 2026-08-05 18:33 | LeaningPole |  | Fair | No | Pole need to be straightening up pole was plant lean maintenance crew need to visit the area to address issue of pole leaning
Outage | J.E.26.08.07752 | C001875060 | Raymond Carr | St.Ann | Completed | Load_252656 | Upper White River - 110 | 2026-08-05 10:53 | 2026-08-05 10:56 | 2026-08-05 12:13 | 2026-08-05 13:19 | 2026-08-05 13:18 | 2026-08-05 13:00 | 2026-08-05 13:19 | 2026-08-05 13:19 |  |  | Fair | No | Planned outage.
Outage | J.E.26.08.07734 | C001875065 | Radcliffe Coleman | St.Catherine | Completed | Load_248181 | Tredegar - 410 | 2026-08-05 10:55 | 2026-08-05 11:11 | 2026-08-05 13:13 | 2026-08-05 13:14 | 2026-08-05 13:13 | 2026-08-05 13:15 | 2026-08-05 13:15 | 2026-08-05 13:15 | BrokenWire |  | Fair | No | Dispatch to evening crew
Outage | J.E.26.08.07767 | C001875080 | Denton Williams | Portland | Completed | Load_246318 | Port Antonio - 410 | 2026-08-05 11:04 | 2026-08-05 11:06 | 2026-08-05 12:31 | 2026-08-05 12:32 | 2026-08-05 12:31 | 2026-08-05 13:22 | 2026-08-05 13:24 | 2026-08-05 13:24 | BrokenWire |  | Fair | No | Use 20 ft of #6 service wire to repair broken wire and three clamps. 116/113/230 volts
Outage | J.E.26.08.07773 | C001875083 | Barrington Brown | St.James | Completed | Load_249162 | Bogue - 310 | 2026-08-05 11:07 | 2026-08-05 11:07 | 2026-08-05 12:40 | 2026-08-05 12:41 | 2026-08-05 12:49 | 2026-08-05 15:26 | 2026-08-05 15:26 | 2026-08-05 15:26 |  |  | Fair | No | Crew found blown 65amp junction fuse on location caused by clearance breach between primary phase and neutral. Crew tripped recloser and open switches to lower primary neutral. Crew also removed creepers from pole and re energized circuit. All customers restored.
Outage | J.E.26.08.07685 | C001875085 | Dean- Smith | Hanover | Completed | Load_573348 | Orange Bay - 310 | 2026-08-05 11:08 | 2026-08-05 15:47 | 2026-08-05 20:04 | 2026-08-05 20:05 | 2026-08-05 20:04 | 2026-08-05 20:04 | 2026-08-05 20:07 | 2026-08-05 20:07 |  |  | Fair | No | Primary conductor dislodge from insulator, replace 40amp junction fuse at entrance to scheme. Pole number n/a
Outage | J.E.26.08.07712 | C001875091 | Moses Elliston | St.Catherine | Completed | Load_557299 | Tredegar - 410 | 2026-08-05 11:11 | 2026-08-05 11:12 | 2026-08-05 12:21 | 2026-08-05 12:22 | 2026-08-05 12:21 | 2026-08-05 10:58 | 2026-08-05 12:24 | 2026-08-05 12:24 |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.08.07784 | C001875092 | Omar King | St.Ann | Completed | Load_254060 | Ocho Rios - 510 | 2026-08-05 11:13 | 2026-08-05 11:13 | 2026-08-05 13:25 | 2026-08-05 13:25 | 2026-08-05 14:31 | 2026-08-05 14:36 | 2026-08-05 14:37 | 2026-08-05 14:37 | BrokenWire |  | Fair | No | Found secondary pole broken from Melissa hurricane. Secondary line was built with #2 two triplex please refer to maintenance customer is still with supply
Outage | J.E.26.08.07789 | C001875099 | Tyrese Williams | St.Ann | Completed | Load_265457 | Cardiff Hall - 210 | 2026-08-05 11:15 | 2026-08-05 11:16 | 2026-08-05 12:02 | 2026-08-05 13:16 | 2026-08-05 14:31 | 2026-08-05 14:45 | 2026-08-05 15:12 | 2026-08-05 15:12 |  |  | Fair | No | Remade service wire joint at pole use 1 pg clamp 116/118/234
Outage | J.E.26.08.07724 | C001875103 | Dwayne Cohen | KSAS | Completed | Load_575133 | Three Miles - 510 | 2026-08-05 11:17 | 2026-08-05 11:18 | 2026-08-05 11:46 | 2026-08-05 11:47 | 2026-08-05 11:46 | 2026-08-05 11:46 | 2026-08-05 11:48 | 2026-08-05 11:48 |  |  | Fair | No | Change defective Lightning Arrester and refuse blown 3amps link , supply now restore.
Outage | J.E.26.08.07728 | C001875102 | Dwayne Cohen | KSAS | Completed | Load_258271 | Three Miles - 410 | 2026-08-05 11:17 | 2026-08-05 11:18 | 2026-08-05 13:48 | 2026-08-05 13:48 | 2026-08-05 14:06 | 2026-08-05 15:09 | 2026-08-05 15:10 | 2026-08-05 15:10 |  |  | Fair | No | Repair burnt transformer drop lead, supply now restore.
Outage | J.E.26.08.07788 | C001875100 | Dwayne Cohen | KSAN | Completed | Load_253416 | Washington Blvd - 310 | 2026-08-05 11:17 | 2026-08-05 11:18 | 2026-08-05 11:54 | 2026-08-05 11:55 | 2026-08-05 12:17 | 2026-08-05 12:17 | 2026-08-05 12:18 | 2026-08-05 12:18 |  |  | Fair | No | Premises found closed.
Outage | J.E.26.08.07790 | C001875101 | Rusean Allen | KSAS | Completed | Load_248058 | Hunts Bay - 510 | 2026-08-05 11:17 | 2026-08-05 11:18 | 2026-08-05 12:00 | 2026-08-05 12:05 | 2026-08-05 12:05 | 2026-08-05 12:06 | 2026-08-05 12:06 | 2026-08-05 12:06 |  |  | Fair | No | Related to 27 Charles Street
Outage | J.E.26.08.07725 | C001875104 | Moses Elliston | Portmore | Completed | Load_570224 | Naggo Head - 610 | 2026-08-05 11:18 | 2026-08-05 11:19 | 2026-08-05 13:12 | 2026-08-05 13:12 | 2026-08-05 13:12 | 2026-08-05 13:12 | 2026-08-05 13:14 | 2026-08-05 13:14 |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.08.07791 | C001875112 | Edward Royal | KSAS | Completed | Load_300938 | Up Park Camp - 510 | 2026-08-05 11:20 | 2026-08-05 11:21 | 2026-08-05 11:49 | 2026-08-05 11:50 | 2026-08-05 11:49 | 2026-08-05 12:05 | 2026-08-05 12:08 | 2026-08-05 12:08 |  |  | Fair | No | Replaced transformer fuse (5A) no pole#
Outage | J.E.26.08.07760 | C001875113 | Elvis Trowers | KSAN | Completed | Load_253893 | Constant Spring - 210 | 2026-08-05 11:21 | 2026-08-05 11:26 | 2026-08-05 14:14 | 2026-08-05 14:15 | 2026-08-05 14:35 | 2026-08-05 15:12 | 2026-08-05 15:12 | 2026-08-05 15:12 |  |  | Fair | Yes | Happened to be a disconnection, meter found barell lock and not communicating with escalation service, meter was unable to complete checks.
Non-Outage | J.E.26.08.07754 | C001875145 | Delano Gayle |  | Completed |  |  | 2026-08-05 11:44 | 2026-08-05 23:18 | 2026-08-06 03:35 | 2026-08-06 03:35 | 2026-08-06 04:01 | 2026-08-06 04:02 | 2026-08-06 04:02 | 2026-08-06 04:02 | BrokenWire |  | Fair | No | Premises not located in St Catherine
Outage | J.E.26.08.07750 | C001875147 | Tajay Bernard | Hanover | Completed | Load_241034 | Orange Bay - 210 | 2026-08-05 11:46 | 2026-08-05 11:48 | 2026-08-05 12:59 | 2026-08-05 12:59 | 2026-08-05 13:34 | 2026-08-05 13:51 | 2026-08-05 13:52 | 2026-08-05 13:52 |  |  | Fair | No | Refuse 1 pad mount Transformer use 50amp fuse
Outage | J.E.26.08.07654 | C001875162 | Raymond Carr | St.Catherine | Completed | Load_242473 | New Michelton - 410 | 2026-08-05 11:54 | 2026-08-05 11:54 | 2026-08-05 12:02 | 2026-08-05 12:02 | 2026-08-05 12:02 | 2026-08-05 | 2026-08-05 12:08 | 2026-08-05 12:08 |  |  | Fair | No | Supply was restored.
Non-Outage | J.E.26.08.07749 | C001875163 | Nickolas Rodriques |  | Completed |  |  | 2026-08-05 11:55 | 2026-08-05 11:59 | 2026-08-05 15:29 | 2026-08-05 15:30 | 2026-08-05 15:52 | 2026-08-05 16:03 | 2026-08-05 16:10 | 2026-08-05 16:10 |  |  | Fair | No | Unable to locate or communicate with the customer after several attempts.
Non-Outage | J.E.26.08.07811 | C001875164 | Rusean Allen |  | Completed |  |  | 2026-08-05 11:55 | 2026-08-05 11:56 | 2026-08-05 11:59 | 2026-08-05 12:27 | 2026-08-05 12:27 | 2026-08-05 12:29 | 2026-08-05 12:29 | 2026-08-05 12:29 |  |  | Fair | No | Related to 27 Charles Street
Outage | J.E.26.08.07185 | C001875172 | Eric Williams | KSAS | Completed | Load_244176 | Hunts Bay - 310 | 2026-08-05 11:59 | 2026-08-05 15:24 | 2026-08-05 16:29 | 2026-08-05 16:30 | 2026-08-05 17:59 | 2026-08-05 18:03 | 2026-08-05 18:05 | 2026-08-05 18:05 |  |  | Fair | No | Burnt switch top found and repair, also burnt joint on secondary jumper, used 4 onebolt clamps
Outage | J.E.26.08.07653 | C001875181 | Oshane Warren | Westmoreland | Completed | Load_254275 | Paradise - 310 | 2026-08-05 12:07 | 2026-08-05 14:55 | 2026-08-05 15:04 |  | 2026-08-05 15:04 | 2026-08-05 15:09 | 2026-08-05 15:09 | 2026-08-05 15:09 |  |  | Rains | No | Replace 5 amp 50 kva transformer fuse
Outage | J.E.26.08.07249 | C001875191 | Christopher West | St.Catherine | Completed | Load_1000329 | Twickenham - 310 | 2026-08-05 12:11 | 2026-08-05 12:12 | 2026-08-05 15:02 | 2026-08-05 15:03 | 2026-08-05 15:02 | 2026-08-05 15:03 | 2026-08-05 15:03 | 2026-08-05 15:03 |  |  | Fair | No | Assign to evening crew
Outage | J.E.26.08.06265 | C001875205 | Moses Elliston | St.Catherine | Completed | Load_247080 | Twickenham - 310 | 2026-08-05 12:21 | 2026-08-05 12:23 | 2026-08-05 13:15 | 2026-08-05 13:16 | 2026-08-05 13:15 | 2026-08-05 12:31 | 2026-08-05 13:19 | 2026-08-05 13:19 |  |  | Fair | No | Defective collector changed to #31684719 due to non communication
Non-Outage | J.E.26.08.04459 | C001875213 | Clyde Brown | Clarendon | Completed | Load_247306 | Monymusk - 410 | 2026-08-05 12:24 | 2026-08-05 12:26 | 2026-08-05 13:13 | 2026-08-05 19:13 | 2026-08-05 19:17 | 2026-08-05 19:20 | 2026-08-05 19:21 | 2026-08-05 19:21 |  |  | Fair | No | Cannot be located customer has overseas number
Non-Outage | J.E.26.08.02903 | C001875216 | Elvis Trowers | KSAN | Completed | Load_265054 | Washington Blvd - 710 | 2026-08-05 12:25 | 2026-08-05 12:26 | 2026-08-06 13:24 | 2026-08-06 13:25 | 2026-08-06 13:34 | 2026-08-06 16:14 | 2026-08-06 16:15 | 2026-08-06 16:15 |  |  | Fair | Yes | Areas was found having low voltage when checked and a 50 kva transformer was isolated at pole #0025691 to make top change from C to D voltage when checked was left at 120+121=241 volts.and 4 one bolt clamps on neutral joints.
Outage | J.E.26.08.07806 | C001875218 | Moses Elliston | Portmore | Completed | Load_576148 | Naggo Head - 610 | 2026-08-05 12:25 | 2026-08-05 12:26 | 2026-08-05 14:23 | 2026-08-05 14:23 | 2026-08-05 14:23 | 2026-08-05 14:23 | 2026-08-05 14:27 | 2026-08-05 14:27 |  |  | Fair | No | Wrapped joints at 3 wire service pothead.3 linkets used.
Outage | J.E.26.08.07820 | C001875217 | Eric Williams | KSAS | Completed | Load_248058 | Hunts Bay - 510 | 2026-08-05 12:25 | 2026-08-05 15:24 | 2026-08-05 18:23 | 2026-08-05 18:23 | 2026-08-05 19:02 | 2026-08-05 19:15 | 2026-08-05 19:16 | 2026-08-05 19:16 |  |  | Fair | No | Burnt hotline clamps found and replaced
Non-Outage | J.E.26.07.38772 | C001875220 | Moses Elliston | St.Catherine | Completed | Load_556367 | Rhodens Pen - 210 | 2026-08-05 12:26 | 2026-08-05 12:27 | 2026-08-05 16:35 | 2026-08-05 16:36 | 2026-08-05 16:36 | 2026-08-05 16:36 | 2026-08-05 16:37 | 2026-08-05 16:37 |  |  | Fair | No | Supply ok at premises 114-114-228 volts
Non-Outage | J.E.26.08.00110 | C001875219 | Moses Elliston | St.Catherine | Completed | Load_305217 | Rhodens Pen - 210 | 2026-08-05 12:26 | 2026-08-05 12:27 | 2026-08-05 17:05 | 2026-08-05 17:05 | 2026-08-05 17:05 | 2026-08-05 17:05 | 2026-08-05 17:08 | 2026-08-05 17:08 |  |  | Fair | No | Meter changed to # 1365330 due to single phasing condition.
Outage | J.E.26.08.07845 | C001875247 | Derrick Grubb | St.Thomas | Completed | Load_259414 | Good Year - 210 | 2026-08-05 12:58 | 2026-08-05 12:59 | 2026-08-06 11:46 | 2026-08-06 11:46 | 2026-08-06 11:46 | 2026-08-06 11:47 | 2026-08-06 11:47 | 2026-08-06 11:47 |  |  | Fair | No | Contact customer by phone and customer said premises is okay.
Outage | J.E.26.08.07864 | C001875274 | Daniel Francis | St.Ann | Completed | Load_266408 | Cardiff Hall - 210 | 2026-08-05 13:21 | 2026-08-05 15:24 | 2026-08-05 15:54 | 2026-08-05 15:54 | 2026-08-05 17:02 | 2026-08-05 17:03 | 2026-08-05 17:03 | 2026-08-05 17:03 | Fire |  | Fair | No | Found okay
Non-Outage | J.E.26.08.07674 | C001875282 | Rusean Allen | KSAS | Completed | Load_254739 | Up Park Camp - 510 | 2026-08-05 13:31 | 2026-08-06 08:25 | 2026-08-06 08:38 | 2026-08-06 08:39 | 2026-08-06 08:40 | 2026-08-06 08:41 | 2026-08-06 08:41 | 2026-08-06 08:41 | BrokenWire |  | Fair | No | Customer not aware of any problems reported since recent
Outage | J.E.26.08.07801 | C001875283 | Daniel Lobar | Trelawny | Completed | Load_262089 | Martha Brae - 210 | 2026-08-05 13:33 | 2026-08-05 13:35 | 2026-08-05 13:54 | 2026-08-05 13:55 | 2026-08-05 13:54 | 2026-08-05 15:26 | 2026-08-05 15:36 | 2026-08-05 15:36 | BrokenWire |  | Fair | No | Repaired broken no. 6 service wire, six 1-bolt clamp and15” of no: 6 triplex service wire used. A voltage reading of 117v/117v/234v was left
Outage | J.E.26.08.07901 | C001875299 | Marlon Brown | Trelawny | Completed | Load_238287 | Greenwood - 210 | 2026-08-05 13:40 | 2026-08-05 15:41 | 2026-08-05 16:41 | 2026-08-05 17:42 | 2026-08-05 17:41 | 2026-08-05 17:55 | 2026-08-05 17:57 | 2026-08-05 17:57 | BrokenWire |  | Fair | No | Retention service wire
Outage | J.E.26.08.07861 | C001875300 | Wan Carlos Scarlett | Portmore | Completed | Load_255889 | Naggo Head - 610 | 2026-08-05 13:43 | 2026-08-05 14:07 | 2026-08-05 15:40 | 2026-08-05 15:41 | 2026-08-05 16:23 | 2026-08-05 17:24 | 2026-08-05 17:26 | 2026-08-05 17:26 | BrokenWire |  | Fair | No | Found customer 3 wire service at pothead with bout phase and neutral corroded use 3 Penn union at pothead reading 114 115 230
Outage | J.E.26.08.07721 | C001875306 | Raymond Carr | St.Ann | Completed | Load_353250 | Upper White River - 110 | 2026-08-05 13:44 | 2026-08-05 13:45 | 2026-08-05 14:21 | 2026-08-05 14:22 | 2026-08-05 14:26 | 2026-08-05 14:36 | 2026-08-05 14:43 | 2026-08-05 14:43 |  |  | Fair | No | Blown junction fuse found at pole number 0014264, line patrol and found okay,however tree contact was suspected. A 8 amp fuse fuse was used to renew supply was restored.
Outage | J.E.26.08.07859 | C001875307 | Denton Williams | Portland | Completed | Load_265513 | Port Antonio - 410 | 2026-08-05 13:44 | 2026-08-05 13:45 | 2026-08-05 16:02 | 2026-08-05 16:03 | 2026-08-05 16:05 | 2026-08-05 16:06 | 2026-08-05 16:09 | 2026-08-05 16:09 | BrokenPole |  | Fair | No | No driving direction, make several calls to the customer, phone keep ringing without an answer
Non-Outage | J.E.26.08.07863 | C001875312 | Oraine Minto | St.Ann | Completed | Load_238576 | Roaring River - 210 | 2026-08-05 13:46 | 2026-08-05 13:47 | 2026-08-06 13:35 | 2026-08-06 13:36 | 2026-08-06 13:35 | 2026-08-06 13:36 | 2026-08-06 13:37 | 2026-08-06 13:37 |  |  | Rains | No | Refer to maintenance Customer states that light keeps going on and off for five minutes intervals And happens more when the area is windy
Non-Outage | J.E.26.08.07679 | C001875313 | Richard Watson | St.Elizabeth | Completed | Load_257642 | Maggotty - 110 | 2026-08-05 13:47 | 2026-08-05 13:48 | 2026-08-05 14:06 | 2026-08-05 14:06 | 2026-08-05 14:15 | 2026-08-05 14:21 | 2026-08-05 14:25 | 2026-08-05 14:25 |  |  | Fair | No | Voltage found at metering point 108v, 109v, 195v phase and neutral and 217v, 222v, 223v bank of three 50kva transformer, low voltage on primary affecting secondary voltage.
Non-Outage | J.E.26.08.04063 | C001875321 | Edward Royal | KSAS | Completed | Load_258045 | Rockfort - 410 | 2026-08-05 14:03 | 2026-08-05 14:04 | 2026-08-05 21:33 | 2026-08-05 21:34 | 2026-08-05 21:33 | 2026-08-05 21:34 | 2026-08-05 21:34 | 2026-08-05 21:34 | BrokenPole |  | Fair | No | Call related
Outage | J.E.26.08.07850 | C001875325 | Damion Reid | Manchester | Completed | Load_302137 | Spur Tree - 310 | 2026-08-05 14:04 | 2026-08-06 07:26 | 2026-08-06 08:18 | 2026-08-06 08:19 | 2026-08-06 09:10 | 2026-08-06 09:45 | 2026-08-06 09:48 | 2026-08-06 09:48 |  |  | Fair | No | Remade corroded phase at pothead for 3 wire service using one 1 bolt clamp voltage reading at meter socket phase to neutral 110v-109v across phase 222v
Non-Outage | J.E.26.08.07642 | C001875330 | Ryan Richards |  | Completed |  |  | 2026-08-05 14:05 | 2026-08-05 14:06 | 2026-08-05 16:29 | 2026-08-05 16:29 | 2026-08-05 17:53 | 2026-08-05 18:55 | 2026-08-05 18:55 | 2026-08-05 18:55 | LowHangingWires |  | Fair | No | 1 span of broken lower secondary phase found cause by market truck open 25 kva transformer slice and retention using 20ft#2/0 aluminum 1#2/0 preform 3 one bolt clamps and reclose transformer all customers are now with supply
Non-Outage | J.E.26.08.07894 | C001875329 | Barnett Brown |  | Completed |  |  | 2026-08-05 14:05 | 2026-08-06 15:11 | 2026-08-06 15:35 | 2026-08-06 16:01 | 2026-08-06 17:15 | 2026-08-06 18:14 | 2026-08-06 18:18 | 2026-08-06 18:18 | Fire |  | Fair | No | Remove meter for house that was burnt completely. Meter number 2885693
Outage | J.E.26.08.07704 | C001875328 | Damion Reid | Manchester | Completed | Load_1002521 | Kendal - 310 | 2026-08-05 14:05 | 2026-08-06 07:26 | 2026-08-06 10:38 | 2026-08-06 10:39 | 2026-08-06 11:23 | 2026-08-06 11:36 | 2026-08-06 11:37 | 2026-08-06 11:37 |  |  | Fair | No | Premises closed
Outage | J.E.26.08.07835 | C001875326 | Ryan Richards | Manchester | Completed | Load_256612 | Kendal - 310 | 2026-08-05 14:05 | 2026-08-05 14:06 | 2026-08-05 14:38 | 2026-08-05 14:39 | 2026-08-05 15:39 | 2026-08-05 16:29 | 2026-08-05 16:29 | 2026-08-05 16:29 |  |  | Fair | No | Corroded one bolt clamps found at pothead for 3 wire meter remade corroded phase and neutral using 3 penunion voltage 113/116/229 volts
Outage | J.E.26.08.07848 | C001875331 | Richard Grant | St.Catherine | Completed | Load_249743 | New Michelton - 310 | 2026-08-05 14:06 | 2026-08-05 14:07 | 2026-08-05 14:24 | 2026-08-05 14:25 | 2026-08-05 14:24 | 2026-08-05 14:25 | 2026-08-05 14:25 | 2026-08-05 14:25 | Fire |  | Fair | No | Premises found okay
Outage | J.E.26.08.07919 | C001875333 | Antony Levy | KSAN | Completed | Load_265507 | Constant Spring - 210 | 2026-08-05 14:13 | 2026-08-06 08:09 | 2026-08-06 08:21 | 2026-08-06 08:22 | 2026-08-06 08:50 | 2026-08-06 09:13 | 2026-08-06 09:14 | 2026-08-06 09:14 |  |  | Fair | No | Internal problem customer advised.
Outage | J.E.26.08.07911 | C001875341 | Edward Royal | KSAS | Completed | Load_245842 | Rockfort - 210 | 2026-08-05 14:20 | 2026-08-05 14:21 | 2026-08-05 14:47 | 2026-08-05 14:47 | 2026-08-05 14:47 | 2026-08-05 14:47 | 2026-08-05 14:47 | 2026-08-05 14:47 |  |  | Fair | No | Premises found ok related to outage at rifle road
Outage | J.E.26.08.07937 | C001875363 | Denton Williams | Portland | Completed | Load_242857 | Port Antonio - 410 | 2026-08-05 14:34 | 2026-08-05 14:37 | 2026-08-05 15:47 | 2026-08-05 15:47 | 2026-08-05 15:53 | 2026-08-05 15:57 | 2026-08-05 15:59 | 2026-08-05 15:59 |  |  | Fair | No | In proper driving direction, invalid phone number, unable to locate customer
Outage | J.E.26.08.07941 | C001875364 | Denton Williams | Portland | Completed | Load_247771 | Port Antonio - 310 | 2026-08-05 14:34 | 2026-08-05 14:37 | 2026-08-05 17:03 | 2026-08-05 17:03 | 2026-08-05 17:03 | 2026-08-05 17:25 | 2026-08-05 17:26 | 2026-08-05 17:26 |  |  | Fair | No | Use two clamps to correct wrap joints on pole. 115/115/231 volts
Outage | J.E.26.08.07723 | C001875381 | Barrington Brown | St.James | Completed | Load_261458 | Queens Drive - 710 | 2026-08-05 14:53 | 2026-08-06 08:29 | 2026-08-06 09:48 | 2026-08-06 09:48 | 2026-08-06 10:10 | 2026-08-06 10:14 | 2026-08-06 10:14 | 2026-08-06 10:14 |  |  | Fair | No | Checked and found ok
Outage | J.E.26.08.07827 | C001875385 | Swon Miller | St.James | Completed | Load_257022 | Rose Hall - 210 | 2026-08-05 14:53 | 2026-08-05 14:54 | 2026-08-05 17:21 | 2026-08-05 17:23 | 2026-08-05 17:29 | 2026-08-19 17:46 | 2026-08-05 17:46 | 2026-08-05 17:46 |  |  | Fair | No | Check and found area okay customer complained about street light not working
Outage | J.E.26.08.07844 | C001875383 | Barrington Brown | St.James | Completed | Load_258445 | Rose Hall - 110 | 2026-08-05 14:53 | 2026-08-06 08:30 | 2026-08-06 12:01 | 2026-08-06 14:09 | 2026-08-06 14:39 | 2026-08-06 14:44 | 2026-08-06 14:44 | 2026-08-06 14:44 |  |  | Fair | No | Crew found open secondary conductors within reach from ground in customer yard and is unsafe. Conductors need to be raised one pole . Please refer to maintenance department to have work done immediately. Customer says it’s been like that from restoration and she has small children at the house.
Outage | J.E.26.08.07940 | C001875382 | Swon Miller | St.James | Completed | Load_263606 | Queens Drive - 310 | 2026-08-05 14:53 | 2026-08-05 14:54 | 2026-08-05 17:46 | 2026-08-05 17:46 | 2026-08-05 18:21 | 2026-08-05 18:40 | 2026-08-05 18:44 | 2026-08-05 18:44 | Fire |  | Fair | No
Outage | J.E.26.08.07978 | C001875389 | Swon Miller | St.James | Completed | Load_1001843 | Rose Hall - 210 | 2026-08-05 14:55 | 2026-08-05 14:56 | 2026-08-05 15:15 | 2026-08-05 15:16 | 2026-08-05 15:51 | 2026-08-18 04:38 | 2026-08-05 16:42 | 2026-08-05 16:42 |  |  | Fair | No | Found customer service wire burnt off due to slack connection voltage found 115 clean and remake joint use 1pg voltage left 115/114/231
Outage | J.E.26.08.07607 | C001875398 | Wayne Dillion | Manchester | Completed | Load_267967 | Spur Tree - 210 | 2026-08-05 15:01 | 2026-08-05 16:56 | 2026-08-05 18:28 | 2026-08-05 18:28 | 2026-08-05 18:28 | 2026-08-05 18:26 | 2026-08-05 18:29 | 2026-08-05 18:29 |  |  | Fair | No | Customer disconnected due to none payment of bill. But unable to reconnect by customer care due to system down.
Outage | J.E.26.08.07888 | C001875396 | Wayne Dillion | Manchester | Completed | Load_268532 | Spur Tree - 210 | 2026-08-05 15:01 | 2026-08-05 15:36 | 2026-08-05 18:05 | 2026-08-05 18:05 | 2026-08-05 18:05 | 2026-08-05 18:05 | 2026-08-05 18:08 | 2026-08-05 18:08 |  |  | Fair | No | Supply restored to the area.
Outage | J.E.26.08.07954 | C001875395 | Raheem Ricketts | Manchester | Completed | Load_292220 | Spur Tree - 210 | 2026-08-05 15:01 | 2026-08-05 15:03 | 2026-08-05 15:55 | 2026-08-05 21:07 | 2026-08-05 21:07 | 2026-08-05 21:08 | 2026-08-05 21:09 | 2026-08-05 21:09 |  |  | Fair | No | Check and found okay customer says call was made earlier an power has been restored
Outage | J.E.26.08.07960 | C001875397 | Wayne Dillion | Manchester | Completed | Load_266485 | Spur Tree - 210 | 2026-08-05 15:01 | 2026-08-05 15:36 | 2026-08-05 18:02 | 2026-08-05 18:02 | 2026-08-05 18:02 | 2026-08-05 18:02 | 2026-08-05 18:04 | 2026-08-05 18:04 |  |  | Fair | No | Supply restored to the area.
Outage | J.E.26.08.07977 | C001875394 | Raheem Ricketts | Manchester | Completed | Load_265048 | Spur Tree - 210 | 2026-08-05 15:01 | 2026-08-05 15:03 | 2026-08-05 15:55 | 2026-08-05 17:20 | 2026-08-05 17:49 | 2026-08-05 17:49 | 2026-08-05 17:50 | 2026-08-05 17:50 |  |  | Fair | No | Unable to locate customer
Outage | J.E.26.08.07136 | C001875399 | Raheem Ricketts | St.Elizabeth | Completed | Load_259003 | Maggotty - 210 | 2026-08-05 15:02 | 2026-08-05 15:03 | 2026-08-05 15:55 | 2026-08-05 16:05 | 2026-08-05 16:34 | 2026-08-05 16:46 | 2026-08-05 16:46 | 2026-08-05 16:46 |  |  | Fair | No | Check and found okay customer makes report towards changing meter meter burn however voltage is 110,110,220 meter is still working properly a customer says they are not affected
Outage | J.E.26.08.07355 | C001875400 | Jowayne Newmans | St.Elizabeth | Completed | Load_266291 | Maggotty - 210 | 2026-08-05 15:02 | 2026-08-06 12:00 | 2026-08-06 12:14 | 2026-08-06 12:14 | 2026-08-06 13:19 | 2026-08-06 13:49 | 2026-08-06 13:49 | 2026-08-06 13:49 |  |  | Fair | No | Patrol and found customer with low voltage 80v cause by corroded one bolt clamp on secondary conductor. Repair by reconnecting service wire to secondary conductor using 1 one bolt clamp. Voltage reading after repair 109v.
Outage | J.E.26.08.07973 | C001875405 | Edward Royal | KSAS | Completed | Load_250013 | Cane River - 610 | 2026-08-05 15:08 | 2026-08-05 15:21 | 2026-08-05 15:43 | 2026-08-05 15:43 | 2026-08-05 16:13 | 2026-08-05 16:48 | 2026-08-05 16:48 | 2026-08-05 16:48 |  |  | Fair | No | Replaced 2 20A junction fuse 3A transformer fuse
Outage | J.E.26.08.07916 | C001875412 | Marlon Brown | Trelawny | Completed | Load_257683 | Martha Brae - 210 | 2026-08-05 15:16 | 2026-08-05 15:18 | 2026-08-05 15:26 | 2026-08-05 15:26 | 2026-08-05 15:54 | 2026-08-05 17:00 | 2026-08-05 17:00 | 2026-08-05 17:00 |  |  | Fair | No | Reconnect service wire at pothead and pole, use 3 linkers and 3 pg clamps Voltage found noneVoltage leaving at pothead 15/116=231v.
Outage | J.E.26.08.07942 | C001875411 | Marlon Brown | Trelawny | Completed | Load_262089 | Martha Brae - 210 | 2026-08-05 15:16 | 2026-08-05 15:18 | 2026-08-05 16:41 | 2026-08-05 21:00 | 2026-08-05 22:02 | 2026-08-05 22:05 | 2026-08-05 22:05 | 2026-08-05 22:05 |  |  | Fair | No | Found ok Voltage found at meter socket 115/115=230Voltage leaving at meter socket 115/115=230
Outage | J.E.26.08.07490 | C001875413 | Marlon Brown | Trelawny | Completed | Load_259574 | Greenwood - 110 | 2026-08-05 15:18 | 2026-08-05 15:19 | 2026-08-05 16:41 | 2026-08-05 17:58 | 2026-08-05 18:35 | 2026-08-05 18:41 | 2026-08-05 18:41 | 2026-08-05 18:41 |  |  | Fair | No | Reconnect supply at pole use 1pg clamp Voltage found at pothead 105Voltage leaving at pothead 105/107=212v.
Outage | J.E.26.08.07947 | C001875418 | Donald Cunningham | St.Catherine | Completed | Load_262168 | New Michelton - 210 | 2026-08-05 15:19 | 2026-08-05 15:20 | 2026-08-05 15:39 | 2026-08-05 15:39 | 2026-08-05 17:21 | 2026-08-05 18:16 | 2026-08-05 18:19 | 2026-08-05 18:19 |  |  | Fair | No | Blown junction fuse by train line in ewarton replace 65 / 50 amp in main line to time and patience
Outage | J.E.26.08.07950 | C001875419 | Donald Cunningham | St.Catherine | Completed | Load_255656 | New Michelton - 210 | 2026-08-05 15:19 | 2026-08-05 15:20 | 2026-08-05 18:19 | 2026-08-05 18:19 | 2026-08-05 18:54 | 2026-08-05 18:54 | 2026-08-05 18:59 | 2026-08-05 18:59 |  |  | Fair | No | Premises found ok supply restored
Outage | J.E.26.08.07969 | C001875417 | Donald Cunningham | St.Catherine | Completed | Load_262970 | New Michelton - 210 | 2026-08-05 15:19 | 2026-08-05 15:20 | 2026-08-05 19:00 | 2026-08-05 19:00 | 2026-08-05 20:15 | 2026-08-05 20:16 | 2026-08-05 20:24 | 2026-08-05 20:24 |  |  | Fair | No | Supply restored
Outage | J.E.26.08.07948 | C001875421 | Roxroy Needham | St.Ann | Completed | Load_266947 | Roaring River - 210 | 2026-08-05 15:21 | 2026-08-05 22:46 | 2026-08-06 01:21 | 2026-08-06 03:24 | 2026-08-06 03:24 | 2026-08-06 03:20 | 2026-08-06 03:25 | 2026-08-06 03:25 |  |  | Fair | No | Premises found ok call customer and customer say that the light is back
Outage | J.E.26.08.07993 | C001875422 | Omar King | St.Ann | Completed | Load_251697 | Roaring River - 410 | 2026-08-05 15:22 | 2026-08-05 15:23 | 2026-08-05 22:54 | 2026-08-05 22:55 | 2026-08-05 22:54 | 2026-08-05 22:57 | 2026-08-05 22:58 | 2026-08-05 22:58 | BrokenWire |  | Fair | No | Found 15 amp junction fuse blow cause by broken primary conductor cause by falling tree limb cause 35 feet class #4 pole top to broke temporary work as been carried out to restore customer
Outage | J.E.26.08.07249 | C001875426 | Kemark Slue | St.Catherine | Completed | Load_1000329 | Twickenham - 310 | 2026-08-05 15:24 | 2026-08-05 15:25 | 2026-08-05 15:31 | 2026-08-05 15:31 | 2026-08-05 16:42 | 2026-08-05 16:54 | 2026-08-05 16:57 | 2026-08-05 16:57 |  |  | Fair | No | Premises was checked and found okay.
Outage | J.E.26.08.07734 | C001875425 | Kemark Slue | St.Catherine | Completed | Load_248181 | Tredegar - 410 | 2026-08-05 15:24 | 2026-08-05 15:25 | 2026-08-05 18:45 | 2026-08-05 20:07 | 2026-08-05 20:09 | 2026-08-05 20:23 | 2026-08-05 21:41 | 2026-08-05 21:41 | BrokenWire |  | Fair | No | Upon arrival at the location the crew discovered that 20 amps middle and road junction fuse were blown at pole # 045190, further patrol revealed that a flock of birds were the caused, refuse links and re-energized line section.
Outage | J.E.26.08.05194 | C001875429 | Kemark Slue | St.Catherine | Completed | Load_265584 | Tredegar - 510 | 2026-08-05 15:26 | 2026-08-05 15:27 | 2026-08-05 15:45 | 2026-08-05 16:58 | 2026-08-05 18:26 | 2026-08-05 18:00 | 2026-08-05 19:55 | 2026-08-05 19:55 |  |  | Fair | No | Unable to locate premises due to inadequate directions and all calls to number given were unsuccessful however there is supply in the general area at the time of visit.
Outage | J.E.26.08.07831 | C001875428 | Delano Gayle | St.Catherine | Completed | Load_254079 | Rhodens Pen - 210 | 2026-08-05 15:26 | 2026-08-05 23:18 | 2026-08-05 23:24 | 2026-08-05 23:24 | 2026-08-06 00:30 | 2026-08-06 02:31 | 2026-08-06 02:31 | 2026-08-06 02:31 |  |  | Fair | No | Prepaid customer unable to add credit, send call to Moses
Outage | J.E.26.08.07853 | C001875441 | Damion Reid | Manchester | Completed | Load_238320 | Kendal - 210 | 2026-08-05 15:29 | 2026-08-05 15:31 | 2026-08-05 18:03 | 2026-08-05 18:04 | 2026-08-05 18:37 | 2026-08-05 19:29 | 2026-08-05 19:31 | 2026-08-05 19:31 |  |  | Fair | No | Blown 20amp junction fuse found cause by contamination line patrol and replace blown fuse
Outage | J.E.26.08.07876 | C001875440 | Damion Reid | Manchester | Completed | Load_238024 | Kendal - 210 | 2026-08-05 15:29 | 2026-08-05 15:31 | 2026-08-05 17:37 | 2026-08-05 17:38 | 2026-08-05 17:47 | 2026-08-05 17:55 | 2026-08-05 17:56 | 2026-08-05 17:56 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.07986 | C001875439 | Richard Samuda | Manchester | Completed | Load_303120 | Kendal - 210 | 2026-08-05 15:29 | 2026-08-06 15:08 | 2026-08-06 15:45 | 2026-08-06 15:49 | 2026-08-06 17:03 | 2026-08-06 17:25 | 2026-08-06 17:25 | 2026-08-06 17:25 |  |  | Rains | No | Found 15 amp junction blown patrol line found nothing replaced fuse customer back to normal
Non-Outage | J.E.26.08.07221 | C001875445 | Kemark Slue |  | Completed |  |  | 2026-08-05 15:30 | 2026-08-05 15:32 | 2026-08-05 19:48 | 2026-08-05 22:29 | 2026-08-05 22:59 | 2026-08-05 22:59 | 2026-08-05 23:00 | 2026-08-05 23:00 | BrokenWire |  | Fair | No | Premises was checked and found okay.
Outage | J.E.26.08.07805 | C001875443 | Damion Reid | Manchester | Completed | Load_303067 | Kendal - 210 | 2026-08-05 15:30 | 2026-08-05 15:31 | 2026-08-05 19:55 | 2026-08-05 22:18 | 2026-08-05 22:18 | 2026-08-05 22:22 | 2026-08-05 22:25 | 2026-08-05 22:25 |  |  | Fair | No | Remade burnt off phase at pothead and in meter socket for 3 wire service using one 1 bolt clamp voltage reading at meter socket phase to neutral 116v-115v across phase 223v
Non-Outage | J.E.26.08.07077 | C001875446 | Kemark Slue | St.Catherine | Completed | Load_269368 | Tredegar - 210 | 2026-08-05 15:31 | 2026-08-05 15:32 | 2026-08-05 15:45 | 2026-08-05 22:16 | 2026-08-05 22:27 | 2026-08-05 22:27 | 2026-08-05 22:29 | 2026-08-05 22:29 | BrokenWire |  | Fair | No | Upon arrival at the location the crew discovered that one phase from #6 triplex service supplying the customer was broken at JPS pole, terminate conductor and remake joint using one, one bolt clamp.
Non-Outage | J.E.26.08.05386 | C001875452 | Fitzroy Turner | KSAS | Completed | Load_239499 | Rockfort - 410 | 2026-08-05 15:33 | 2026-08-06 12:30 | 2026-08-06 12:40 | 2026-08-06 12:41 | 2026-08-06 13:05 | 2026-08-06 13:06 | 2026-08-06 13:35 | 2026-08-06 13:35 |  |  | Fair | No | Found bank of two 50 kva transformer found one fuse for the power transformer blown replace one 5 amp fuse supply restored to areas
Non-Outage | J.E.26.08.06320 | C001875450 | Nickolas Rodriques | Portmore | Completed | Load_254184 | Naggo Head - 510 | 2026-08-05 15:33 | 2026-08-05 15:34 | 2026-08-05 21:56 | 2026-08-05 21:56 | 2026-08-05 22:15 | 2026-08-05 22:34 | 2026-08-05 22:42 | 2026-08-05 22:42 | LeaningPole |  | Fair | No | Checked and found guy wire which supports a 40 ft concrete main line pole rooted from the ground caused by car accident. Refer to maintenance.
Non-Outage | J.E.26.08.07612 | C001875449 | Rodclif Dawkins | St.Catherine | Completed | Load_264108 | Twickenham - 210 | 2026-08-05 15:33 | 2026-08-06 15:39 | 2026-08-06 16:42 | 2026-08-06 16:52 | 2026-08-06 17:45 | 2026-08-06 17:45 | 2026-08-06 17:51 | 2026-08-06 17:51 | Fire |  | Fair | No | Found 30/6 pole burnt at pole top , pole does not belong to jps. Third party communication pole with communication cables. Customer was advised to contact third party company. Customer service wire is anchored on pole
Outage | J.E.26.08.07990 | C001875460 | Wayne Dillion | Manchester | Completed | Load_245643 | Spur Tree - 210 | 2026-08-05 15:34 | 2026-08-05 15:36 | 2026-08-05 18:19 | 2026-08-05 18:20 | 2026-08-05 18:20 | 2026-08-05 18:24 | 2026-08-05 18:28 | 2026-08-05 18:28 |  |  | Fair | No | Customer disconnected due to none payment of bill. But unable to reconnect by customer care due to system down.
Outage | J.E.26.08.08000 | C001875459 | Wayne Dillion | Manchester | Completed | Load_262620 | Spur Tree - 210 | 2026-08-05 15:34 | 2026-08-05 15:36 | 2026-08-05 16:41 | 2026-08-05 16:42 | 2026-08-05 16:41 | 2026-08-05 17:13 | 2026-08-05 17:15 | 2026-08-05 17:15 |  |  | Fair | No | Patrol and found one blown 20amp junction fuse no pole #. Replace same and supply restored okay.
Outage | J.E.26.08.08003 | C001875457 | Wayne Dillion | Manchester | Completed | Load_302864 | Spur Tree - 210 | 2026-08-05 15:34 | 2026-08-05 15:36 | 2026-08-05 18:43 | 2026-08-05 18:44 | 2026-08-05 18:43 | 2026-08-05 18:46 | 2026-08-05 18:47 | 2026-08-05 18:47 |  |  | Fair | No | Supply check and found customer single phasing. Further checks reveals one side of the meter burnt. Please refer same to the field services department for a meter change.
Outage | J.E.26.08.08004 | C001875458 | Wayne Dillion | Manchester | Completed | Load_247150 | Spur Tree - 210 | 2026-08-05 15:34 | 2026-08-05 15:36 | 2026-08-05 17:15 | 2026-08-05 17:15 | 2026-08-05 17:15 | 2026-08-05 17:46 | 2026-08-05 17:47 | 2026-08-05 17:47 |  |  | Fair | No | Patrol and found 2 chip saver operate size not visible and one blown 10amp junction fuse no pole #. Re-close chip savers and replace 10amp fuse and supply restored to the area.
Non-Outage | J.E.26.08.05168 | C001875462 | Clyde Brown |  | Completed |  |  | 2026-08-05 15:35 | 2026-08-05 15:36 | 2026-08-05 17:34 | 2026-08-05 18:47 | 2026-08-05 19:07 | 2026-08-05 19:07 | 2026-08-05 19:12 | 2026-08-05 19:12 | BrokenPole |  | Fair | No | Broken pole cannot be located
Non-Outage | J.E.26.08.07110 | C001875461 | Clyde Brown |  | Completed |  |  | 2026-08-05 15:35 | 2026-08-05 15:36 | 2026-08-05 17:34 | 2026-08-05 17:35 | 2026-08-05 18:39 | 2026-08-05 18:41 | 2026-08-05 18:45 | 2026-08-05 18:45 | BrokenPole |  | Fair | No | 40c4 T concrete pole break at base and need to be replaced
Non-Outage | J.E.26.08.07239 | C001875468 | Richman Whyte |  | Completed |  |  | 2026-08-05 15:38 | 2026-08-05 15:39 | 2026-08-05 16:45 | 2026-08-05 16:45 | 2026-08-05 16:45 | 2026-08-05 16:46 | 2026-08-05 16:46 | 2026-08-05 16:46 |  |  | Fair | No | Check and found okay
Outage | J.E.26.08.07825 | C001875465 | Richman Whyte | Westmoreland | Completed | Load_267481 | Paradise - 310 | 2026-08-05 15:38 | 2026-08-05 15:39 | 2026-08-05 16:46 | 2026-08-05 16:46 | 2026-08-05 16:46 | 2026-08-05 16:47 | 2026-08-05 16:47 | 2026-08-05 16:47 |  |  | Fair | No | Customer complained about getting light bill an he haven’t got connected back after hurricane
Outage | J.E.26.08.07974 | C001875464 | Richman Whyte | Westmoreland | Completed | Load_257048 | Paradise - 310 | 2026-08-05 15:38 | 2026-08-05 15:39 | 2026-08-05 18:25 | 2026-08-05 18:26 | 2026-08-05 18:25 | 2026-08-05 18:26 | 2026-08-05 18:27 | 2026-08-05 18:27 |  |  | Fair | No | Connect back customer after hurricane use 30ft #6 triplex service wire voltage 112 112 223
Outage | J.E.26.08.07628 | C001875472 | Dean- Smith | Hanover | Completed | Load_249925 | Orange Bay - 310 | 2026-08-05 15:39 | 2026-08-05 15:40 | 2026-08-05 16:38 | 2026-08-05 16:38 | 2026-08-05 17:51 | 2026-08-05 17:51 | 2026-08-05 17:53 | 2026-08-05 17:53 |  |  | Fair | No | Cut and remove vegetation, replace 8amp junction fuse.,pole number n/a
Outage | J.E.26.08.07661 | C001875470 | Dean- Smith | Hanover | Completed | Load_267471 | Orange Bay - 310 | 2026-08-05 15:39 | 2026-08-05 15:40 | 2026-08-05 17:54 | 2026-08-05 17:55 | 2026-08-05 17:55 | 2026-08-05 17:55 | 2026-08-05 17:56 | 2026-08-05 17:56 |  |  | Fair | No | Area restored
Outage | J.E.26.08.07997 | C001875473 | Kemark Slue | St.Catherine | Completed | Load_257738 | Tredegar - 210 | 2026-08-05 15:42 | 2026-08-05 15:43 | 2026-08-05 17:39 | 2026-08-05 21:48 | 2026-08-05 22:11 | 2026-08-05 22:11 | 2026-08-05 22:15 | 2026-08-05 22:15 |  |  | Fair | No | Upon arrival at the location the discovered that the customer has a prepaid account that credit ran out and was successfully top up, the team liaison with the Escalation department who explained that the Itron application is down so the customer’s three wire meter is unable to turn back on, so the customer is still without supply.
Outage | J.E.26.08.08020 | C001875474 | Denton Williams | Portland | Completed | Load_249256 | Port Antonio - 410 | 2026-08-05 15:43 | 2026-08-05 15:48 | 2026-08-05 16:11 | 2026-08-05 16:11 | 2026-08-05 16:11 | 2026-08-05 16:11 | 2026-08-05 16:13 | 2026-08-05 16:13 |  |  | Fair | No | Customer was on disconnection, customer stated that she get back power
Outage | J.E.26.08.07963 | C001875479 | Stephen Taylor | St.Thomas | Completed | Load_252687 | Good Year - 210 | 2026-08-05 15:45 | 2026-08-05 15:47 | 2026-08-05 16:16 | 2026-08-05 16:16 | 2026-08-05 16:40 | 2026-08-05 16:41 | 2026-08-05 16:42 | 2026-08-05 16:42 |  |  | Fair | No | Reset 25 kva transformer customer is now okay
Outage | J.E.26.08.07755 | C001875488 | Romeo Brissett | St.James | Completed | Load_243887 | Bogue - 510 | 2026-08-05 15:49 | 2026-08-05 23:11 | 2026-08-06 00:16 | 2026-08-06 00:17 | 2026-08-06 00:51 | 2026-08-06 04:00 | 2026-08-06 05:10 | 2026-08-06 05:10 |  |  | Fair | No | Customer was connected by escalation
Outage | J.E.26.08.07756 | C001875487 | Derrick Dawkins | St.James | Completed | Load_246135 | Bogue - 610 | 2026-08-05 15:49 | 2026-08-05 15:50 | 2026-08-05 15:59 | 2026-08-05 18:42 | 2026-08-05 18:57 | 2026-08-05 19:03 | 2026-08-05 19:04 | 2026-08-05 19:04 |  |  | Fair | No | Checked and found ok Voltage 109/1110=220
Outage | J.E.26.08.07758 | C001875486 | Derrick Dawkins | St.James | Completed | Load_265417 | Bogue - 610 | 2026-08-05 15:49 | 2026-08-05 15:50 | 2026-08-05 18:35 | 2026-08-05 18:35 | 2026-08-05 18:37 | 2026-08-05 18:41 | 2026-08-05 18:41 | 2026-08-05 18:41 |  |  | Fair | No | Calls to customer went unanswered no location provided can’t locate
Outage | J.E.26.08.07875 | C001875484 | Derrick Dawkins | St.James | Completed | Load_259760 | Bogue - 610 | 2026-08-05 15:49 | 2026-08-05 15:50 | 2026-08-05 17:27 | 2026-08-05 17:28 | 2026-08-05 18:00 | 2026-08-05 18:34 | 2026-08-05 18:34 | 2026-08-05 18:34 |  |  | Fair | No | Found one span secondary phase burned down due to vehicle accident open 25 kva to carry out repairs splice and retention
Outage | J.E.26.08.07938 | C001875481 | Derrick Dawkins | St.James | Completed | Load_292985 | Bogue - 610 | 2026-08-05 15:49 | 2026-08-05 15:50 | 2026-08-05 20:05 | 2026-08-05 20:06 | 2026-08-05 20:14 | 2026-08-05 20:15 | 2026-08-05 20:15 | 2026-08-05 20:15 |  |  | Fair | No | Premises ok
Outage | J.E.26.08.07945 | C001875482 | Derrick Dawkins | St.James | Completed | Load_292389 | Bogue - 610 | 2026-08-05 15:49 | 2026-08-05 15:50 | 2026-08-05 19:11 | 2026-08-05 19:11 | 2026-08-05 19:45 | 2026-08-05 20:03 | 2026-08-05 20:04 | 2026-08-05 20:04 |  |  | Fair | No | Premises found ok 107/106=214
Outage | J.E.26.08.08002 | C001875483 | Derrick Dawkins | St.James | Completed | Load_255304 | Bogue - 310 | 2026-08-05 15:49 | 2026-08-06 08:31 | 2026-08-06 12:22 | 2026-08-06 12:23 | 2026-08-06 12:22 | 2026-08-06 13:20 | 2026-08-06 13:26 | 2026-08-06 13:26 |  |  | Rains | No | Due to the hurricane customers service wire dislocated from the jps pole reconnect customer service wire voltage left 118
Outage | J.E.26.08.07898 | C001875491 | Milton Charlton | KSAN | Completed | Load_239572 | Hope - 310 | 2026-08-05 15:53 | 2026-08-05 15:54 | 2026-08-05 18:08 | 2026-08-05 22:04 | 2026-08-05 22:04 | 2026-08-05 22:15 | 2026-08-05 22:09 | 2026-08-05 22:09 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.07996 | C001875494 | Milton Charlton | KSAN | Completed | Load_247724 | Hope - 310 | 2026-08-05 15:53 | 2026-08-05 15:54 | 2026-08-05 18:08 | 2026-08-05 18:12 | 2026-08-05 19:01 | 2026-08-05 20:05 | 2026-08-05 19:02 | 2026-08-05 19:02 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.08008 | C001875492 | Milton Charlton | KSAN | Completed | Load_245872 | Washington Blvd - 410 | 2026-08-05 15:53 | 2026-08-05 15:54 | 2026-08-05 16:25 | 2026-08-05 16:26 | 2026-08-05 17:26 | 2026-08-05 17:25 | 2026-08-05 17:30 | 2026-08-05 17:30 |  |  | Fair | No | Customer meter # 2935688 not working J.P.S. Escalation is unable to access meter they states system is down unable to reconnect meter. Technician working to get the system back up.
Outage | J.E.26.08.08015 | C001875493 | Milton Charlton | KSAN | Completed | Load_247530 | Washington Blvd - 610 | 2026-08-05 15:53 | 2026-08-05 15:54 | 2026-08-05 17:30 | 2026-08-05 17:31 | 2026-08-05 17:59 | 2026-08-05 18:10 | 2026-08-05 18:08 | 2026-08-05 18:08 | TreeContact |  | Fair | No | Found okay upon arrival. Primary and secondary bushing required.
Outage | J.E.26.08.07984 | C001875500 | Swon Miller | St.James | Completed | Load_250164 | Rose Hall - 210 | 2026-08-05 15:54 | 2026-08-05 15:56 | 2026-08-05 16:43 | 2026-08-05 16:44 | 2026-08-05 16:51 | 2026-08-05 17:20 | 2026-08-05 17:21 | 2026-08-05 17:21 |  |  | Fair | No | Found 1,30 amp pad mount fuse blown cause by contamination replace 1,30 amp fuse no pole
Outage | J.E.26.08.07304 | C001875504 | Kaydon Taylor | KSAS | Completed | Load_251132 | Duhaney - 310 | 2026-08-05 15:55 | 2026-08-05 16:43 | 2026-08-05 16:51 | 2026-08-05 17:30 | 2026-08-05 17:29 | 2026-08-05 17:31 | 2026-08-05 17:31 | 2026-08-05 17:31 |  |  | Fair | No | Internal problem
Outage | J.E.26.08.07904 | C001875503 | Kaydon Taylor | KSAN | Completed | Load_242936 | Washington Blvd - 310 | 2026-08-05 15:55 | 2026-08-05 17:55 | 2026-08-05 18:24 | 2026-08-05 19:33 | 2026-08-05 19:52 | 2026-08-05 20:00 | 2026-08-05 20:00 | 2026-08-05 20:00 | LowHangingWires |  | Fair | No | Telecommunication wire found
Outage | J.E.26.08.07970 | C001875502 | Kaydon Taylor | KSAS | Completed | Load_240238 | Duhaney - 410 | 2026-08-05 15:55 | 2026-08-05 17:55 | 2026-08-05 21:37 | 2026-08-05 22:14 | 2026-08-05 22:14 | 2026-08-05 22:17 | 2026-08-05 22:18 | 2026-08-05 22:18 |  |  | Fair | No | Customer request to come in the daytime
Outage | J.E.26.08.08029 | C001875505 | Dean- Smith | Hanover | Completed | Load_303169 | Orange Bay - 210 | 2026-08-05 15:56 | 2026-08-05 15:57 | 2026-08-05 16:15 | 2026-08-06 00:24 | 2026-08-06 00:24 | 2026-08-06 00:24 | 2026-08-06 00:26 | 2026-08-06 00:26 | Fire |  | Fair | No | Related to the transformer across from negril bus park.
Outage | J.E.26.08.08030 | C001875506 | Dean- Smith | Hanover | Completed | Load_252846 | Orange Bay - 210 | 2026-08-05 15:57 | 2026-08-05 15:57 | 2026-08-05 21:33 | 2026-08-05 21:34 | 2026-08-05 23:01 | 2026-08-06 01:00 | 2026-08-06 00:24 | 2026-08-06 00:24 | BrokenPole |  | Fair | No | Defective 50 kva transformer across from negril bus park, circuit was tied to a 50 kva close to sweet spice restaurant. Please forward to maintenance dept
Non-Outage | J.E.26.08.07995 | C001875522 | Eric Williams | KSAN | Completed | Load_269301 | West Kings House - 410 | 2026-08-05 16:17 | 2026-08-05 16:17 | 2026-08-05 21:21 | 2026-08-05 21:22 | 2026-08-05 21:30 | 2026-08-05 21:31 | 2026-08-05 21:33 | 2026-08-05 21:33 |  |  | Fair | No | Customer not at the location, customer stated the issue happened at 2pm each day, so they ask for a visit tomorrow at 2pm, but as it stand at the moment everything okay
Outage | J.E.26.08.08031 | C001875523 | Eric Williams | KSAS | Completed | Load_579116 | Greenwich - 510 | 2026-08-05 16:18 | 2026-08-05 16:18 | 2026-08-05 19:52 | 2026-08-05 19:53 | 2026-08-05 20:04 | 2026-08-05 21:12 | 2026-08-05 21:13 | 2026-08-05 21:13 |  |  | Fair | No | Found middle junction link open (not blown) cause by defective 100kva transformer, customer left with power supply.
Outage | J.E.26.08.08040 | C001875529 | Swon Miller | St.James | Completed | Load_261336 | Bogue - 310 | 2026-08-05 16:20 | 2026-08-05 16:21 | 2026-08-05 20:26 | 2026-08-05 20:26 | 2026-08-05 21:17 | 2026-08-18 22:20 | 2026-08-05 22:33 | 2026-08-05 22:33 |  |  | Fair | No | Found 50 kva transformer fuse blown cause by vegetation cut and remove vegetation from transformer and replace 5 amp in a 50 kva transformer (customer meter is i disconnected voltage found 0.000 voltage left 114/116/234) also 40 class 6 transformer pole broken at the base and need to be replaced and 30 ft class six pole with 2/o twisted need to straighten at bel field great house .further assessment needed to be carried out by maintenance.
Outage | J.E.26.08.07722 | C001875539 | Marlon Authors | St.Elizabeth | Completed | Load_245347 | Maggotty - 110 | 2026-08-05 16:28 | 2026-08-06 15:37 | 2026-08-06 16:13 | 2026-08-06 16:14 | 2026-08-06 16:56 | 2026-08-06 17:09 | 2026-08-06 17:08 | 2026-08-06 17:08 |  |  | Fair | No | Supply checked and found no service wire. Connect same using 60 feet of #6 triplex service wire two clamps and two linkets. Supply leave working okay rdg 114 volts
Outage | J.E.26.08.07871 | C001875538 | Selvin White | St.Elizabeth | Completed | Load_247131 | Maggotty - 110 | 2026-08-05 16:28 | 2026-08-05 16:29 | 2026-08-05 18:27 | 2026-08-05 18:27 | 2026-08-05 20:14 | 2026-08-05 20:19 | 2026-08-05 20:19 | 2026-08-05 20:19 |  |  | Rains | No | Replace a blown 1.5 amp fuse for a 15 KVA transformer circuit at pole number 0208876 after patrolling secondary circuit with 2 customers . Supply restored. Lightning strike was said to be the cause.
Outage | J.E.26.08.08033 | C001875536 | Selvin White | St.Elizabeth | Completed | Load_255437 | Maggotty - 210 | 2026-08-05 16:28 | 2026-08-05 16:29 | 2026-08-05 18:25 | 2026-08-05 20:53 | 2026-08-05 21:47 | 2026-08-05 22:09 | 2026-08-05 22:12 | 2026-08-05 22:12 |  |  | Rains | No | Defective 10 KVA transformer found at location that cannot be tied in. Please advise Delroy Crew so arrangements can be made for replacement. Very urgent.
Outage | J.E.26.08.08050 | C001875537 | Selvin White | St.Elizabeth | Completed | Load_242431 | Maggotty - 210 | 2026-08-05 16:28 | 2026-08-05 16:29 | 2026-08-05 17:07 | 2026-08-05 17:07 | 2026-08-05 17:50 | 2026-08-05 18:23 | 2026-08-05 18:23 | 2026-08-05 18:23 |  |  | Rains | No | Replace a blown 15 amp junction fuse at the entrance to Greenfield district at pole number 0231147 after patrolling single phase primary line. Supply restored to the affected customers. Lightning strike was said to be the cause. Customer says streetlight on the same switch pole is not working so please refer to the relevant department.
Outage | J.E.26.08.07600 | C001875551 | Eric Williams | KSAS | Completed | Load_290055 | Hunts Bay - 810 | 2026-08-05 16:43 | 2026-08-05 16:50 | 2026-08-05 21:33 | 2026-08-05 21:34 | 2026-08-05 22:07 | 2026-08-05 22:07 | 2026-08-05 22:08 | 2026-08-05 22:08 |  |  | Fair | No | Premises found okay
Non-Outage | J.E.26.08.06439 | C001875563 | Milton Charlton | KSAS | Completed | Load_261656 | Greenwich - 410 | 2026-08-05 16:49 | 2026-08-05 16:52 | 2026-08-05 19:02 | 2026-08-05 19:03 | 2026-08-05 20:16 | 2026-08-05 20:20 | 2026-08-05 20:28 | 2026-08-05 20:28 |  |  | Fair | No | Found one 30 amps junction fuse blown at pole #129297. Refused using one 30 amps fuse and reclosed junction switch. Readings at meter socket 121-122-215 & 243-245-247 volts.
Non-Outage | J.E.26.08.05436 | C001875564 | Eric Williams | KSAS | Completed | Load_244176 | Hunts Bay - 310 | 2026-08-05 16:51 | 2026-08-05 16:52 | 2026-08-05 18:06 | 2026-08-05 18:06 | 2026-08-05 18:13 | 2026-08-05 18:20 | 2026-08-05 18:21 | 2026-08-05 18:21 |  |  | Fair | No | Burnt switch top found and repair, also burnt joint on secondary jumper, used 4 onebolt clamps
Non-Outage | J.E.26.08.06695 | C001875565 | Eric Williams | KSAS | Completed | Load_261859 | Hunts Bay - 210 | 2026-08-05 16:54 | 2026-08-05 16:55 | 2026-08-05 19:16 | 2026-08-05 19:17 | 2026-08-05 19:35 | 2026-08-05 19:52 | 2026-08-05 19:52 | 2026-08-05 19:52 |  |  | Fair | No | 3wire 240 volts meter burnt and defective, send to field service department to have same corrected.
Non-Outage | J.E.26.08.08046 | C001875566 | Neckell Ormsby |  | Completed |  |  | 2026-08-05 16:57 | 2026-08-05 19:50 | 2026-08-05 20:10 | 2026-08-05 20:11 | 2026-08-05 20:49 | 2026-08-05 21:30 | 2026-08-05 21:30 | 2026-08-05 21:30 | Fire |  | Fair | No | Found broken secondary phase open 25kva transformer to splice and retention 2- pole span secondary phase using approximately 30ft #2 AA and 3- one bolt clamps no pole # seen
Outage | J.E.26.08.08047 | C001875567 | Romaine Roberts | St.Mary | Completed | Load_259755 | Annotto Bay - 210 | 2026-08-05 16:57 | 2026-08-05 17:00 | 2026-08-05 18:38 | 2026-08-05 18:38 | 2026-08-05 20:43 | 2026-08-05 21:02 | 2026-08-05 21:03 | 2026-08-05 21:03 |  |  | Fair | No | After carrying out several checks and cleaning up pole and pothead found burn breaker in customer breaker panel advise customer to get electrician
Non-Outage | J.E.26.08.05342 | C001875573 | Daniel Francis | St.Ann | Completed | Load_252030 | Cardiff Hall - 310 | 2026-08-05 17:06 | 2026-08-05 17:07 | 2026-08-05 17:15 | 2026-08-05 17:15 | 2026-08-05 17:48 | 2026-08-05 18:34 | 2026-08-05 18:36 | 2026-08-05 18:36 | BrokenPole |  | Fair | No | Found 30/c6 broken conducter need to be transferred to new secondary only
Outage | J.E.26.08.07516 | C001875576 | Richman Whyte | St.Elizabeth | Completed | Load_557810 | Maggotty - 110 | 2026-08-05 17:07 | 2026-08-05 17:14 | 2026-08-05 20:08 | 2026-08-05 20:09 | 2026-08-05 20:08 | 2026-08-05 20:08 | 2026-08-05 20:09 | 2026-08-05 20:09 |  |  | Fair | No | Customer haven’t finished repairing for connection
Outage | J.E.26.08.07929 | C001875575 | Richman Whyte | St.Elizabeth | Completed | Load_266366 | Maggotty - 110 | 2026-08-05 17:07 | 2026-08-05 17:08 | 2026-08-05 20:07 | 2026-08-05 20:08 | 2026-08-05 20:07 | 2026-08-05 20:08 | 2026-08-05 20:08 | 2026-08-05 20:08 |  |  | Fair | No | Check and found okay
Outage | J.E.26.08.08080 | C001875574 | Richman Whyte | St.Elizabeth | Completed | Load_292490 | Maggotty - 110 | 2026-08-05 17:07 | 2026-08-05 17:08 | 2026-08-05 19:17 | 2026-08-05 19:17 | 2026-08-05 19:17 | 2026-08-05 19:45 | 2026-08-05 19:45 | 2026-08-05 19:45 |  |  | Fair | No | Replace .25, amp junction fuse
Outage | J.E.26.08.07989 | C001875585 | Wayne Dillion | Manchester | Completed | Load_238671 | Spur Tree - 210 | 2026-08-05 17:20 | 2026-08-05 17:20 | 2026-08-05 17:55 | 2026-08-05 17:55 | 2026-08-05 17:55 | 2026-08-05 17:58 | 2026-08-05 18:01 | 2026-08-05 18:01 |  |  | Fair | No | Supply restored to area.
Outage | J.E.26.08.08024 | C001875592 | Marlon Brown | Trelawny | Completed | Load_570268 | Martha Brae - 110 | 2026-08-05 17:30 | 2026-08-05 17:31 | 2026-08-05 18:43 | 2026-08-05 18:44 | 2026-08-05 19:58 | 2026-08-05 20:17 | 2026-08-05 20:17 | 2026-08-05 20:17 | LeaningPole,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Retention service wire, however customer needs to have electrician effect repairs.Voltage found at pothead 115/115=230Voltage leaving at pothead 115/115=230.
Outage | J.E.26.08.08036 | C001875591 | Marlon Brown | Trelawny | Completed | Load_251614 | Martha Brae - 210 | 2026-08-05 17:30 | 2026-08-05 17:31 | 2026-08-05 20:17 | 2026-08-05 20:17 | 2026-08-05 20:34 | 2026-08-05 21:00 | 2026-08-05 21:00 | 2026-08-05 21:00 |  |  | Fair | No | Meter is defective, refer to Field Service Department. Voltage found at meter socket 109//113=222Voltage leaving at meter socket 109/113=222v.
Non-Outage | J.E.26.08.07966 | C001875594 | Denton Williams | Portland | Completed | Load_245592 | Port Antonio - 310 | 2026-08-05 17:36 | 2026-08-05 17:37 | 2026-08-05 19:07 | 2026-08-05 19:07 | 2026-08-05 20:15 | 2026-08-05 20:16 | 2026-08-05 20:18 | 2026-08-05 20:18 | BangingWires |  | Fair | No | The customer was contacted via telephone and they are requesting daytime visit. Follow up is required.
Outage | J.E.26.08.08092 | C001875600 | Stephen Taylor | St.Thomas | Completed | Load_264680 | Good Year - 110 | 2026-08-05 17:53 | 2026-08-05 17:54 | 2026-08-05 18:12 | 2026-08-05 18:12 | 2026-08-05 18:54 | 2026-08-05 18:55 | 2026-08-05 18:56 | 2026-08-05 18:56 | Fire |  | Fair | No | Cut tree off service wire customer is now okay
Outage | J.E.26.08.08095 | C001875601 | Kaydon Taylor | KSAN | Completed | Load_238439 | Washington Blvd - 610 | 2026-08-05 17:54 | 2026-08-05 17:57 | 2026-08-05 18:02 | 2026-08-05 18:23 | 2026-08-05 18:23 | 2026-08-05 18:24 | 2026-08-05 18:24 | 2026-08-05 18:24 |  |  | Fair | No | Internal problem
Outage | J.E.26.08.07963 | C001875604 | Stephen Taylor | St.Thomas | Completed | Load_252687 | Good Year - 210 | 2026-08-05 17:56 | 2026-08-05 17:57 | 2026-08-05 19:14 | 2026-08-05 19:15 | 2026-08-05 19:15 | 2026-08-05 19:15 | 2026-08-05 19:16 | 2026-08-05 19:16 |  |  | Fair | No | Need more information a lot of call to customer no one answered the phone. And also a Jamaican telephone number
Outage | J.E.26.08.08072 | C001875603 | Eric Williams | KSAS | Completed | Load_268210 | Greenwich - 510 | 2026-08-05 17:56 | 2026-08-05 20:49 | 2026-08-05 21:13 | 2026-08-05 21:13 | 2026-08-05 21:13 | 2026-08-05 21:17 | 2026-08-05 21:18 | 2026-08-05 21:18 |  |  | Fair | No | Found bank of three transformer 1 - 167 kva and 2 - 100kva, power transformer 100 kva defective send to ksa maintenance to have same corrected.
Outage | J.E.26.08.07981 | C001875606 | Nickolas Rodriques | Portmore | Completed | Load_263072 | Naggo Head - 510 | 2026-08-05 18:02 | 2026-08-05 18:03 | 2026-08-05 20:12 | 2026-08-05 21:04 | 2026-08-05 21:36 | 2026-08-05 21:45 | 2026-08-05 21:55 | 2026-08-05 21:55 | Fire |  | Fair | No | The area was patrolled and no fire was found. (Unable to reach the customer on the contact number provided).
Non-Outage | J.E.26.08.06441 | C001875612 | Michael Paterson | Westmoreland | Completed | Load_247902 | Paradise - 210 | 2026-08-05 18:06 | 2026-08-05 18:07 | 2026-08-05 19:13 | 2026-08-05 19:13 | 2026-08-05 19:39 | 2026-08-05 20:20 | 2026-08-05 20:21 | 2026-08-05 20:21 |  |  | Fair | No | Customer has internal problem, advise to fix, voltage readings115v, 116v 231v
Non-Outage | J.E.26.08.07727 | C001875610 | Michael Paterson |  | Completed |  |  | 2026-08-05 18:06 | 2026-08-05 18:07 | 2026-08-05 20:25 | 2026-08-05 20:26 | 2026-08-05 20:54 | 2026-08-05 20:55 | 2026-08-05 20:55 | 2026-08-05 20:55 |  |  | Fair | No | Customer mention that he didn’t make any report, confirm via phone call.
Outage | J.E.26.08.07802 | C001875611 | Michael Paterson | Westmoreland | Completed | Load_267763 | Paradise - 210 | 2026-08-05 18:06 | 2026-08-05 18:07 | 2026-08-05 18:19 | 2026-08-05 18:20 | 2026-08-05 18:46 | 2026-08-05 18:57 | 2026-08-05 18:57 | 2026-08-05 18:57 | BrokenPole |  | Fair | No | Unable to connect customer due to broken 30ft pole, also, area is experiencing low voltage, voltage readings 96v, 100v, 196v. 50kva xfmr in area, customer count 70, customer is residing in lane, customer count in lane 40, Please refer to Mr. James Hudson at paradise to address matter speedily.
Non-Outage | J.E.26.08.07207 | C001875613 | Michael Paterson | Westmoreland | Completed | Load_264370 | Paradise - 210 | 2026-08-05 18:07 | 2026-08-05 18:07 | 2026-08-05 20:57 | 2026-08-05 20:58 | 2026-08-05 23:13 | 2026-08-05 23:19 | 2026-08-05 23:20 | 2026-08-05 23:20 | LeaningPole |  | Fair | No | Assessment done at location, voltage reading taken, 100v, 102v, 202v, customer count on entire circuit 80 not include illegal connections, voltage reading at 50kva xfmr, 119v, 119v, 238v, current readings 168amps, 175amps and 40amps in neutral, customer is at of line circuit 9 span from xfmr, please refer to maintenance, Mr James Hudson at paradise.
Non-Outage | J.E.26.08.07822 | C001875621 | Kaydon Taylor | KSAN | Completed | Load_256909 | Constant Spring - 210 | 2026-08-05 18:20 | 2026-08-05 18:23 | 2026-08-05 20:00 | 2026-08-05 20:03 | 2026-08-05 21:14 | 2026-08-05 21:37 | 2026-08-05 21:37 | 2026-08-05 21:37 |  |  | Fair | No | Found okay
Outage | J.E.26.08.08135 | C001875629 | Denton Williams | Portland | Completed | Load_242857 | Port Antonio - 410 | 2026-08-05 18:40 | 2026-08-05 19:43 | 2026-08-05 20:18 | 2026-08-05 20:18 | 2026-08-05 21:27 | 2026-08-05 22:25 | 2026-08-05 22:29 | 2026-08-05 22:29 |  |  | Fair | No | Truck pull down customer service line. Replace approximately 110ft of no.6 three wire service line, 3 one bolt clamp was also used. Voltage leave 118v, 116v & 225v.
Outage | J.E.26.08.07807 | C001876135 | Derrick Dawkins | St.James | Completed | Load_255716 | Bogue - 610 | 2026-08-05 18:52 | 2026-08-05 18:54 | 2026-08-05 20:15 | 2026-08-05 20:16 | 2026-08-05 20:29 | 2026-08-05 20:29 | 2026-08-05 20:30 | 2026-08-05 20:30 |  |  | Fair | No | Calls to customer went unanswered cannot locate
Non-Outage | J.E.26.08.08141 | C001876136 | Derrick Dawkins | St.James | Completed | Load_292881 | Bogue - 610 | 2026-08-05 19:02 | 2026-08-05 19:03 | 2026-08-05 20:30 | 2026-08-05 20:31 | 2026-08-05 21:36 | 2026-08-05 21:58 | 2026-08-05 22:03 | 2026-08-05 22:03 |  |  | Fair | No | Found 50kva transformer fuse blown due to vegetation replace 8amp fuse no pole number numbers available
Outage | J.E.26.08.08169 | C001877136 | Clyde Brown | Clarendon | Completed | Load_246213 | Parnassus - 210 | 2026-08-05 19:15 | 2026-08-05 19:16 | 2026-08-05 19:21 | 2026-08-05 19:22 | 2026-08-05 21:04 | 2026-08-05 20:47 | 2026-08-05 21:07 | 2026-08-05 21:07 |  |  | Fair | No | Pay as you go customer
Outage | J.E.26.08.08177 | C001877137 | Clyde Brown | Clarendon | Completed | Load_259584 | Parnassus - 310 | 2026-08-05 19:16 | 2026-08-05 19:16 | 2026-08-05 19:21 | 2026-08-05 21:11 | 2026-08-05 22:30 | 2026-08-05 22:29 | 2026-08-05 22:36 | 2026-08-05 22:36 |  |  | Fair | No | Corroded clamp at secondary line for 3 wire service phase clamp replaced,voltage left 112/112 and 224V
Outage | J.E.26.08.08132 | C001878484 | Raheem Ricketts | St.Elizabeth | Completed | Load_264052 | Maggotty - 210 | 2026-08-05 19:19 | 2026-08-05 19:23 | 2026-08-05 19:29 | 2026-08-05 19:38 | 2026-08-05 20:02 | 2026-08-05 21:06 | 2026-08-05 21:07 | 2026-08-05 21:07 |  |  | Fair | No | Customer says power has been restored
Outage | J.E.26.08.08143 | C001878639 | Wayne Dillion | Manchester | Completed | Load_1002334 | Spur Tree - 210 | 2026-08-05 19:20 | 2026-08-05 19:35 | 2026-08-05 19:47 | 2026-08-05 19:48 | 2026-08-05 20:27 | 2026-08-05 20:29 | 2026-08-05 20:34 | 2026-08-05 20:34 |  |  | Fair | No | Patrol and found one blown 20amp junction fuse no pole #. Replace same and supply restored okay.
Outage | J.E.26.08.08082 | C001878640 | Raheem Ricketts | St.Elizabeth | Completed | Load_292995 | Maggotty - 210 | 2026-08-05 19:22 | 2026-08-05 19:23 | 2026-08-05 19:29 | 2026-08-05 21:11 | 2026-08-05 21:11 | 2026-08-05 21:41 | 2026-08-05 21:41 | 2026-08-05 21:41 | BrokenWire |  | Fair | No | Check and found okay customer need street light at pole power is at premises
Outage | J.E.26.08.08009 | C001879394 | Wayne Dillion | Manchester | Completed | Load_244726 | Spur Tree - 210 | 2026-08-05 19:34 | 2026-08-05 19:35 | 2026-08-05 20:34 | 2026-08-05 20:34 | 2026-08-05 20:34 | 2026-08-05 20:36 | 2026-08-05 20:36 | 2026-08-05 20:36 | BrokenWire |  | Fair | No | Supply restored okay.
Outage | J.E.26.08.08037 | C001879393 | Wayne Dillion | Manchester | Completed | Load_244043 | Spur Tree - 210 | 2026-08-05 19:34 | 2026-08-05 19:35 | 2026-08-05 20:39 | 2026-08-05 20:39 | 2026-08-05 20:39 | 2026-08-05 20:41 | 2026-08-05 20:41 | 2026-08-05 20:41 |  |  | Fair | No | Supply restored okay.
Outage | J.E.26.08.08068 | C001879395 | Wayne Dillion | Manchester | Completed | Load_302820 | Spur Tree - 210 | 2026-08-05 19:34 | 2026-08-05 19:35 | 2026-08-05 20:36 | 2026-08-05 20:37 | 2026-08-05 20:36 | 2026-08-05 20:38 | 2026-08-05 20:39 | 2026-08-05 20:39 |  |  | Fair | No | Supply restored okay.
Outage | J.E.26.08.08179 | C001879979 | Kemark Slue | St.Catherine | Completed | Load_238712 | Tredegar - 510 | 2026-08-05 19:44 | 2026-08-05 19:45 | 2026-08-05 20:43 | 2026-08-05 21:44 | 2026-08-05 21:44 | 2026-08-05 21:44 | 2026-08-05 21:47 | 2026-08-05 21:47 | BrokenWire |  | Fair | No | Upon arrival at the location the crew discovered that two spans of secondary bottom phase was broken resulting from illegal connections, isolate 25 kva 13.8 kv transformer at pole # 0076432, splice and retention conductor using one #2 splicing sleeve, #2 preform and re-energized circuit.
Outage | J.E.26.08.08181 | C001880809 | Damion Reid | Manchester | Completed | Load_239398 | Kendal - 210 | 2026-08-05 20:20 | 2026-08-05 20:21 | 2026-08-06 07:24 | 2026-08-06 07:25 | 2026-08-06 07:25 | 2026-08-06 07:26 | 2026-08-06 07:31 | 2026-08-06 07:31 | Fire |  | Fair | No | Primary jumper found lodged against pole open 30amp trip saver secure jumper and restore power
Outage | J.E.26.08.08074 | C001880810 | Damion Reid | Manchester | Completed | Load_260436 | Kendal - 310 | 2026-08-05 20:21 | 2026-08-05 20:21 | 2026-08-05 22:26 | 2026-08-05 22:27 | 2026-08-05 23:19 | 2026-08-05 23:21 | 2026-08-05 23:22 | 2026-08-05 23:22 |  |  | Fair | No | Call was assigned to another team
Outage | J.E.26.08.07684 | C001880815 | Derrick Dawkins | St.James | Completed | Load_301723 | Bogue - 310 | 2026-08-05 20:24 | 2026-08-06 08:31 | 2026-08-06 10:56 | 2026-08-06 10:56 | 2026-08-06 10:56 | 2026-09-04 10:13 | 2026-08-06 11:02 | 2026-08-06 11:02 |  |  | EarthMovement | No | Check and found dat customer has been disconnected for non payment of bill advice customer
Outage | J.E.26.08.08203 | C001880816 | Daniel Francis | St.Ann | Completed | Load_264061 | Cardiff Hall - 310 | 2026-08-05 20:27 | 2026-08-05 20:40 | 2026-08-05 20:53 | 2026-08-05 20:53 | 2026-08-05 21:40 | 2026-08-06 00:06 | 2026-08-06 00:51 | 2026-08-06 00:51 | BrokenWire |  | Fair | No | Found wire on the ground live we open 25kva transformer Retention 3 span use 100ft of wire 4 one bolt clamps 4 preform power restored to the area
Outage | J.E.26.08.08205 | C001880818 | Dean- Smith | Hanover | Completed | Load_292847 | Orange Bay - 310 | 2026-08-05 20:29 | 2026-08-05 20:30 | 2026-08-05 21:03 | 2026-08-05 21:03 | 2026-08-05 21:03 | 2026-08-05 21:03 | 2026-08-05 21:09 | 2026-08-05 21:09 | Fire |  | Fair | No | 50kva power transformer Burnt/ leaking oil ( bring Transformer bag). Please forward to maintenance to organize transformer change ASAP. Unable do create open bank because of hot oil spraying from transformer.
Outage | J.E.26.08.08201 | C001880825 | Donald Cunningham | St.Catherine | Completed | Load_240447 | New Michelton - 210 | 2026-08-05 21:14 | 2026-08-05 21:14 | 2026-08-05 21:43 | 2026-08-05 21:44 | 2026-08-05 22:38 | 2026-08-05 22:39 | 2026-08-05 22:46 | 2026-08-05 22:46 |  |  | Fair | No | Need more directions customer customer not reachable
Non-Outage | J.E.26.08.08211 | C001880827 | Rusean Allen |  | Completed |  |  | 2026-08-05 21:18 | 2026-08-05 23:15 | 2026-08-06 02:10 | 2026-08-06 02:10 | 2026-08-06 02:22 | 2026-08-06 02:24 | 2026-08-06 02:24 | 2026-08-06 02:24 | BrokenWire |  | Fair | No | Not found
Outage | J.E.26.08.08199 | C001880828 | Edward Royal | KSAS | Completed | Load_263100 | Cane River - 410 | 2026-08-05 21:18 | 2026-08-05 21:20 | 2026-08-05 22:21 | 2026-08-05 22:21 | 2026-08-05 22:21 | 2026-08-05 22:21 | 2026-08-05 22:21 | 2026-08-05 22:21 |  |  | Fair | No | Call related
Outage | J.E.26.08.08220 | C001880826 | Edward Royal | KSAS | Completed | Load_1002687 | Cane River - 410 | 2026-08-05 21:18 | 2026-08-05 21:20 | 2026-08-05 21:34 | 2026-08-05 21:35 | 2026-08-05 21:55 | 2026-08-05 22:20 | 2026-08-05 22:21 | 2026-08-05 22:21 |  |  | Fair | No | Hexin box not responding box need to be check reffered to field service box#HEX 04375 pole#0137808
Non-Outage | J.E.26.08.08153 | C001880835 | Javid Vernon |  | Completed |  |  | 2026-08-05 21:40 | 2026-08-06 07:28 | 2026-08-06 08:10 | 2026-08-06 08:10 | 2026-08-06 08:10 | 2026-08-06 08:10 | 2026-08-06 08:11 | 2026-08-06 08:11 |  |  | Fair | No | Customer stated that the power was restored
Outage | J.E.26.08.08204 | C001880834 | Javid Vernon | Westmoreland | Completed | Load_265324 | Paradise - 210 | 2026-08-05 21:40 | 2026-08-06 07:28 | 2026-08-06 08:06 | 2026-08-06 08:08 | 2026-08-06 08:08 | 2026-08-06 08:08 | 2026-08-06 08:09 | 2026-08-06 08:09 |  |  | Fair | No | Customer stated that the power was restored from last night
Non-Outage | J.E.26.08.08239 | C001880839 | Hartley Chin |  | Completed |  |  | 2026-08-05 22:03 | 2026-08-06 08:44 | 2026-08-06 08:51 | 2026-08-06 08:53 | 2026-08-06 09:39 | 2026-08-06 09:40 | 2026-08-06 09:50 | 2026-08-06 09:50 | BrokenPole |  | Fair | No | Ref to maintenance: broken 30 ft open secondary NB customer as electricity but needs urgent attention. Pole broken in two and second balancing the pole.
Outage | J.E.26.08.08198 | C001880844 | Delano Gayle | St.Catherine | Completed | Load_290087 | Rhodens Pen - 210 | 2026-08-05 22:29 | 2026-08-05 23:18 | 2026-08-06 04:03 | 2026-08-06 04:03 | 2026-08-06 04:39 | 2026-08-06 04:41 | 2026-08-06 04:41 | 2026-08-06 04:41 |  |  | Fair | No | Premises not found, hexing area patrolled and found okay
Outage | J.E.26.08.08240 | C001880843 | Delano Gayle | St.Catherine | Completed | Load_256288 | Twickenham - 310 | 2026-08-05 22:29 | 2026-08-05 23:18 | 2026-08-06 04:41 | 2026-08-06 04:41 | 2026-08-06 05:31 | 2026-08-06 05:39 | 2026-08-06 05:39 | 2026-08-06 05:39 | Fire |  | Fair | No | Premises not found area patrolled and found okay no fire seen
Outage | J.E.26.08.08245 | C001880855 | Roxroy Needham | St.Ann | Completed | Load_254060 | Ocho Rios - 510 | 2026-08-05 22:45 | 2026-08-05 22:48 | 2026-08-06 00:21 | 2026-08-06 01:22 | 2026-08-06 02:30 | 2026-08-06 02:42 | 2026-08-06 02:44 | 2026-08-06 02:44 | Fire |  | Fair | No | JPS meter found defective need to change
Outage | J.E.26.08.08248 | C001880856 | Roxroy Needham | St.Ann | Completed | Load_266261 | Ocho Rios - 410 | 2026-08-05 22:45 | 2026-08-05 22:48 | 2026-08-05 23:23 | 2026-08-05 23:23 | 2026-08-06 01:13 | 2026-08-06 01:19 | 2026-08-06 01:20 | 2026-08-06 01:20 |  |  | Fair | No | Replace a 25 KVA Tran fuse with a 3 amps at pole
Outage | J.E.26.08.07709 | C001880865 | Romeo Brissett | St.James | Completed | Load_257498 | Bogue - 610 | 2026-08-05 23:01 | 2026-08-05 23:06 | 2026-08-05 23:08 | 2026-08-05 23:09 | 2026-08-06 00:10 | 2026-08-06 00:13 | 2026-08-06 00:16 | 2026-08-06 00:16 | LeaningPole |  | Fair | No | Patrolled and found power in the area. Found (1)40ft concrete pole leaning with twisted secondary, need to be straighten please send to maintenance. Customer stated that they reporting about the pole not an outage.
Outage | J.E.26.08.07923 | C001880864 | Romeo Brissett | St.James | Completed | Load_292204 | Bogue - 610 | 2026-08-05 23:01 | 2026-08-05 23:07 | 2026-08-06 05:10 | 2026-08-06 05:10 | 2026-08-06 05:10 | 2026-08-06 05:00 | 2026-08-06 05:14 | 2026-08-06 05:14 |  |  | Fair | No | Replaced (1)10KVA transformer fuse.
Non-Outage | J.E.26.08.08120 | C001880874 | Daniel Francis |  | Completed |  |  | 2026-08-05 23:11 | 2026-08-06 07:47 | 2026-08-06 11:12 | 2026-08-06 11:13 | 2026-08-06 11:23 | 2026-08-06 11:25 | 2026-08-06 11:25 | 2026-08-06 11:25 |  |  | Fair | No | Customer not answering phone not found
Outage | J.E.26.08.08200 | C001880875 | Rusean Allen | KSAN | Completed | Load_245872 | Washington Blvd - 410 | 2026-08-05 23:13 | 2026-08-05 23:14 | 2026-08-06 00:08 | 2026-08-06 00:08 | 2026-08-06 01:34 | 2026-08-06 01:36 | 2026-08-06 01:36 | 2026-08-06 01:36 |  |  | Fair | No | Customer having prepaid meter issues, refer to field service department.
Outage | J.E.26.08.08235 | C001880878 | Rusean Allen | KSAN | Completed | Load_293764 | Washington Blvd - 710 | 2026-08-05 23:15 | 2026-08-05 23:16 | 2026-08-06 02:52 | 2026-08-06 02:53 | 2026-08-06 03:02 | 2026-08-06 03:03 | 2026-08-06 03:03 | 2026-08-06 03:03 |  |  | Fair | No | Rami failure, customer is the only one without power, refer to field service department.
Non-Outage | J.E.26.08.08250 | C001880888 | Roxroy Needham |  | Completed |  |  | 2026-08-06 | 2026-08-06 00:01 | 2026-08-06 00:12 | 2026-08-06 02:44 | 2026-08-06 03:22 | 2026-08-06 03:22 | 2026-08-06 03:24 | 2026-08-06 03:24 | BrokenWire | Y | Fair | No | Replace a 8 amps junction fuse at pole
Outage | J.E.26.08.08038 | C001880898 | Derrick Dawkins | St.James | Completed | Load_258485 | Bogue - 310 | 2026-08-06 00:45 | 2026-08-06 08:32 | 2026-08-06 08:43 | 2026-08-06 08:44 | 2026-08-06 10:26 | 2026-08-06 09:55 | 2026-08-06 10:55 | 2026-08-06 10:55 |  |  | Fair | No | Customer says that she haven’t made any report
Outage | J.E.26.08.08213 | C001880897 | Romeo Brissett | St.James | Completed | Load_263074 | Rose Hall - 210 | 2026-08-06 00:45 | 2026-08-06 00:47 | 2026-08-06 05:14 | 2026-08-06 05:14 | 2026-08-06 06:09 | 2026-08-06 07:18 | 2026-08-06 07:30 | 2026-08-06 07:30 |  |  | Fair | No | Removed vegetation and replaced (1)20amps junction fuse
Outage | J.E.26.08.08229 | C001880901 | Roxroy Needham | St.Ann | Completed | Load_413038 | Roaring River - 410 | 2026-08-06 00:54 | 2026-08-06 00:54 | 2026-08-06 05:05 | 2026-08-06 05:06 | 2026-08-06 06:31 | 2026-08-06 06:27 | 2026-08-06 06:32 | 2026-08-06 06:32 |  |  | Fair | No | Premises found ok call customer and customer say that the light is ok
Outage | J.E.26.08.08275 | C001880902 | Delano Gayle | St.Catherine | Completed | Load_258463 | Tredegar - 210 | 2026-08-06 01:05 | 2026-08-06 01:05 | 2026-08-06 02:31 | 2026-08-06 02:31 | 2026-08-06 03:14 | 2026-08-06 03:34 | 2026-08-06 03:34 | 2026-08-06 03:34 |  |  | Fair | No | Blown 10kva transformer fuse no pole#, patrolled circuit and found okay for closure replace 2amps, transformer not sending out any voltage, trip mechanism seems to be defective as many attempts were made to reset transformer, send call to maintenance for transformer to be replaced
Outage | J.E.26.08.08274 | C001880918 | Romeo Brissett | St.James | Completed | Load_254071 | Rose Hall - 210 | 2026-08-06 05:14 | 2026-08-06 05:15 | 2026-08-06 07:30 | 2026-08-06 07:30 | 2026-08-06 07:30 | 2026-08-06 07:15 | 2026-08-06 07:30 | 2026-08-06 07:30 |  |  | Fair | No | Check and found ok
Outage | J.E.26.08.08353 | C001880919 | Barrington Brown | St.James | Completed | Load_259498 | Queens Drive - 710 | 2026-08-06 05:15 | 2026-08-06 08:19 | 2026-08-06 10:14 | 2026-08-06 10:14 | 2026-08-06 10:49 | 2026-08-06 10:51 | 2026-08-06 10:52 | 2026-08-06 10:52 |  |  | Fair | No | Crew checked and customer has internal issues. Reading left 112 112 224
Outage | J.E.26.08.07831 | C001880920 | Moses Elliston | St.Catherine | Completed | Load_254079 | Rhodens Pen - 210 | 2026-08-06 05:27 | 2026-08-06 05:28 | 2026-08-06 10:50 | 2026-08-06 10:51 | 2026-08-06 12:04 | 2026-08-06 10:52 | 2026-08-06 12:06 | 2026-08-06 12:06 |  |  | Fair | No | Supply ok at premises
Outage | J.E.26.08.08364 | C001880923 | Daniel Francis | St.Ann | Completed | Load_413084 | Roaring River - 410 | 2026-08-06 06:27 | 2026-08-06 07:47 | 2026-08-06 08:37 | 2026-08-06 08:37 | 2026-08-06 08:56 | 2026-08-06 10:17 | 2026-08-06 10:23 | 2026-08-06 10:23 |  |  | Fair | No | Found switch wire disconnect we replace it at pole 0091747
Outage | J.E.26.08.08401 | C001880971 | Gregory Grossett | Portland | Completed | Load_252130 | Port Antonio - 410 | 2026-08-06 07:20 | 2026-08-06 07:27 | 2026-08-06 07:56 | 2026-08-06 07:57 | 2026-08-06 08:46 | 2026-08-06 09:06 | 2026-08-06 09:06 | 2026-08-06 09:06 |  |  | Fair | No | 25kva transformer fuse blown at pole#557026 patrol line section then restore supply to the area material use 2amps fuse.
Outage | J.E.26.08.08180 | C001880973 | Gregory Grossett | Portland | Completed | Load_244330 | Port Antonio - 310 | 2026-08-06 07:21 | 2026-08-06 07:26 | 2026-08-06 09:06 | 2026-08-06 09:07 | 2026-08-06 10:40 | 2026-08-06 11:04 | 2026-08-06 11:04 | 2026-08-06 11:04 |  |  | Fair | No | 110 service wire corroded at pothead joints repair and ok however we advise customer to get a certified electrician and change defective meter socket voltage reading at meter socket 121v
Outage | J.E.26.08.08312 | C001880972 | Gregory Grossett | Portland | Completed | Load_249857 | Port Antonio - 410 | 2026-08-06 07:21 | 2026-08-06 07:24 | 2026-08-06 07:34 | 2026-08-06 07:34 | 2026-08-06 07:39 | 2026-08-06 07:56 | 2026-08-06 07:56 | 2026-08-06 07:56 |  |  | Fair | No | 50kva transformer fuse blown patrol line section section then restore supply to the area.Material use 3amps fuse.
Outage | J.E.26.08.08074 | C001880974 | Damion Reid | Manchester | Completed | Load_260436 | Kendal - 310 | 2026-08-06 07:22 | 2026-08-06 07:29 | 2026-08-06 11:38 | 2026-08-06 11:39 | 2026-08-06 12:12 | 2026-08-06 13:07 | 2026-08-06 13:08 | 2026-08-06 13:08 |  |  | Fair | No | Remade burnt off phase at secondary pole for 3 wire service using one 1 bolt clamp
Non-Outage | J.E.26.08.08346 | C001880975 | Damion Reid |  | Completed |  |  | 2026-08-06 07:23 | 2026-08-06 07:29 | 2026-08-06 09:49 | 2026-08-06 09:50 | 2026-08-06 10:34 | 2026-08-06 10:36 | 2026-08-06 10:37 | 2026-08-06 10:37 |  |  | Fair | No | Unable to contact or locate customer
Outage | J.E.26.08.08202 | C001881006 | Javid Vernon | Westmoreland | Completed | Load_249422 | Paradise - 210 | 2026-08-06 07:28 | 2026-08-06 07:29 | 2026-08-06 08:06 | 2026-08-06 08:07 | 2026-08-06 08:07 | 2026-08-06 08:07 | 2026-08-06 08:08 | 2026-08-06 08:08 |  |  | Fair | No | Customer stated that the power was restored from last night
Non-Outage | J.E.26.08.08043 | C001881013 | Oshane Warren |  | Completed |  |  | 2026-08-06 07:29 | 2026-08-06 07:34 | 2026-08-06 11:52 | 2026-08-06 11:54 | 2026-08-06 11:54 | 2026-08-06 13:17 | 2026-08-06 13:18 | 2026-08-06 13:18 |  |  | Fair | No | Replace 3 amp 25 kva transformer fuse
Non-Outage | J.E.26.08.08242 | C001881014 | Derrick Grubb |  | Completed |  |  | 2026-08-06 07:30 | 2026-08-06 08:34 | 2026-08-06 10:41 | 2026-08-06 10:41 | 2026-08-06 11:44 | 2026-08-06 11:45 | 2026-08-06 11:46 | 2026-08-06 11:46 | Fire |  | Fair | No | Premises not found. However, power is in the area.
Outage | J.E.26.08.08221 | C001881026 | Oshane Warren | St.Elizabeth | Completed | Load_237739 | Maggotty - 110 | 2026-08-06 07:40 | 2026-08-06 07:42 | 2026-08-06 10:17 | 2026-08-06 10:17 | 2026-08-06 10:51 | 2026-08-06 10:51 | 2026-08-06 10:52 | 2026-08-06 10:52 |  |  | Fair | No | Replace 20 amp junction fuse
Outage | J.E.26.08.08234 | C001881024 | Oshane Warren | St.Elizabeth | Completed | Load_238298 | Maggotty - 110 | 2026-08-06 07:40 | 2026-08-06 07:42 | 2026-08-06 11:52 | 2026-08-06 11:53 | 2026-08-06 11:53 | 2026-08-06 11:53 | 2026-08-06 11:53 | 2026-08-06 11:53 |  |  | Fair | No | Check and found ok
Outage | J.E.26.08.08411 | C001881027 | Daniel Francis | St.Ann | Completed | Load_256334 | Ocho Rios - 310 | 2026-08-06 07:40 | 2026-08-06 07:47 | 2026-08-06 11:25 | 2026-08-06 11:26 | 2026-08-06 12:26 | 2026-08-06 13:19 | 2026-08-06 13:21 | 2026-08-06 13:21 |  |  | Fair | No | Found tree branch resting close to primary conducter
Outage | J.E.26.08.08337 | C001881029 | Neville Spencer | Clarendon | Completed | Load_576786 | Parnassus - 210 | 2026-08-06 07:42 | 2026-08-06 07:43 | 2026-08-06 08:36 | 2026-08-06 08:37 | 2026-08-06 09:33 | 2026-08-06 09:33 | 2026-08-06 09:42 | 2026-08-06 09:42 |  |  | Fair | No | Found ok.
Outage | J.E.26.08.08350 | C001881030 | Neville Spencer | St.Catherine | Completed | Load_263189 | Rhodens Pen - 310 | 2026-08-06 07:42 | 2026-08-06 07:43 | 2026-08-06 10:09 | 2026-08-06 10:10 | 2026-08-06 10:27 | 2026-08-06 12:09 | 2026-08-06 12:12 | 2026-08-06 12:12 | Fire |  | Fair | No | Open 25 kva xmfr remade remade burnt out clamps on phase and neutral drops leads used 3 clamps. Also renew blown 3 amp fuse supply restored.
Outage | J.E.26.08.08415 | C001881031 | Selvin White | St.Elizabeth | Completed | Load_292260 | Maggotty - 110 | 2026-08-06 07:43 | 2026-08-06 15:16 | 2026-08-06 16:07 | 2026-08-06 16:07 | 2026-08-06 17:16 | 2026-08-06 17:35 | 2026-08-06 17:35 | 2026-08-06 17:35 |  |  | Rains | No | Replace a 1 amp fuse with a 2 amp fuse for a 25 KVA transformer circuit in front the Thornton primary school with no pole number found at location.. Supply restored to the affected customers.
Outage | J.E.26.08.08033 | C001881035 | Richard Watson | St.Elizabeth | Completed | Load_255437 | Maggotty - 210 | 2026-08-06 07:44 | 2026-08-06 07:46 | 2026-08-06 10:07 | 2026-08-06 10:07 | 2026-08-06 11:06 | 2026-08-06 13:00 | 2026-08-06 13:22 | 2026-08-06 13:22 |  |  | Fair | No | Replace defective 10kva transformer no pole#, voltage readings 113v, 113v, 226v, and load readings 2amp A phase, 8.6amp B phase and neutral 6amp.
Outage | J.E.26.08.08089 | C001881033 | Selvin White | St.Elizabeth | Completed | Load_254694 | Maggotty - 110 | 2026-08-06 07:44 | 2026-08-06 15:15 | 2026-08-06 17:53 | 2026-08-06 17:54 | 2026-08-06 18:26 | 2026-08-06 19:08 | 2026-08-06 19:12 | 2026-08-06 19:12 |  |  | Fair | No | Install approximately 30 feet of number six triplex service that was damaged and removed after the recent hurricane. Supply restored to the affected customer with voltage readings of 221,111,110 volts.
Outage | J.E.26.08.08304 | C001881039 | Richard Grant | St.Catherine | Completed | Load_249847 | New Michelton - 210 | 2026-08-06 07:44 | 2026-08-06 07:45 | 2026-08-06 12:29 | 2026-08-06 12:29 | 2026-08-06 13:32 | 2026-08-06 14:11 | 2026-08-06 14:11 | 2026-08-06 14:11 |  |  | Fair | No | Broken joint and wrapped on found at pole. 2 onebolt clamps used to correct fault and supply restored. Premises left okay.
Outage | J.E.26.08.08387 | C001881040 | Richard Grant | St.Catherine | Completed | Load_250336 | New Michelton - 210 | 2026-08-06 07:44 | 2026-08-06 07:45 | 2026-08-06 09:51 | 2026-08-06 12:28 | 2026-08-06 12:27 | 2026-08-06 12:28 | 2026-08-06 12:28 | 2026-08-06 12:28 |  |  | Fair | No | 25a fuse found blown at junction pole# 028682 caused by incorrect fuse coordinations. 40a fuse found at junction pole# 028633 and was replaced with 20a fuse. 15d amps & 7d amps fuse also found blown at separate single phase junction poles. No visible cause seen after patrol conducted. 25k amps fuse replaced with same, 15d amps replaced with 15k amps fuse, 7d amps fuse replaced with 8k amps fuse and supply restored. Area left with supply and okay.
Outage | J.E.26.08.08391 | C001881038 | Richard Grant | St.Catherine | Completed | Load_249773 | New Michelton - 210 | 2026-08-06 07:44 | 2026-08-06 07:45 | 2026-08-06 09:50 | 2026-08-06 12:28 | 2026-08-06 12:28 | 2026-08-06 12:28 | 2026-08-06 12:29 | 2026-08-06 12:29 |  |  | Fair | No | 25a fuse found blown at junction pole# 028682 caused by incorrect fuse coordinations. 40a fuse found at junction pole# 028633 and was replaced with 20a fuse. 15d amps & 7d amps fuse also found blown at separate single phase junction poles. No visible cause seen after patrol conducted. 25k amps fuse replaced with same, 15d amps replaced with 15k amps fuse, 7d amps fuse replaced with 8k amps fuse and supply restored. Area left with supply and okay.
Outage | J.E.26.08.08399 | C001881036 | Richard Grant | St.Catherine | Completed | Load_244982 | New Michelton - 210 | 2026-08-06 07:44 | 2026-08-06 07:45 | 2026-08-06 09:50 | 2026-08-06 12:26 | 2026-08-06 12:25 | 2026-08-06 12:26 | 2026-08-06 12:26 | 2026-08-06 12:26 |  |  | Fair | No | 25a fuse found blown at junction pole# 028682 caused by incorrect fuse coordinations. 40a fuse found at junction pole# 028633 and was replaced with 20a fuse. 15d amps & 7d amps fuse also found blown at separate single phase junction poles. No visible cause seen after patrol conducted. 25k amps fuse replaced with same, 15d amps replaced with 15k amps fuse, 7d amps fuse replaced with 8k amps fuse and supply restored. Area left with supply and okay.
Outage | J.E.26.08.08400 | C001881037 | Richard Grant | St.Catherine | Completed | Load_267600 | New Michelton - 210 | 2026-08-06 07:44 | 2026-08-06 07:45 | 2026-08-06 09:50 | 2026-08-06 12:27 | 2026-08-06 12:26 | 2026-08-06 12:27 | 2026-08-06 12:27 | 2026-08-06 12:27 |  |  | Fair | No | 25a fuse found blown at junction pole# 028682 caused by incorrect fuse coordinations. 40a fuse found at junction pole# 028633 and was replaced with 20a fuse. 15d amps & 7d amps fuse also found blown at separate single phase junction poles. No visible cause seen after patrol conducted. 25k amps fuse replaced with same, 15d amps replaced with 15k amps fuse, 7d amps fuse replaced with 8k amps fuse and supply restored. Area left with supply and okay.
Outage | J.E.26.08.08412 | C001881034 | Richard Grant | St.Catherine | Completed | Load_248711 | New Michelton - 210 | 2026-08-06 07:44 | 2026-08-06 07:46 | 2026-08-06 09:50 | 2026-08-06 09:50 | 2026-08-06 10:42 | 2026-08-06 12:24 | 2026-08-06 12:25 | 2026-08-06 12:25 |  |  | Fair | No | 25a fuse found blown at junction pole# 028682 caused by incorrect fuse coordinations. 40a fuse found at junction pole# 028633 and was replaced with 20a fuse. 15d amps & 7d amps fuse also found blown at separate single phase junction poles. No visible cause seen after patrol conducted. 25k amps fuse replaced with same, 15d amps replaced with 15k amps fuse, 7d amps fuse replaced with 8k amps fuse and supply restored. Area left with supply and okay.
Non-Outage | J.E.26.08.08192 | C001881042 | Jowayne Newmans |  | Completed |  |  | 2026-08-06 07:45 | 2026-08-06 07:49 | 2026-08-06 07:53 | 2026-08-06 07:54 | 2026-08-06 07:53 | 2026-08-06 07:54 | 2026-08-06 07:54 | 2026-08-06 07:54 |  |  | Fair | No | Customer stated that light came back last night.
Outage | J.E.26.08.08069 | C001881043 | Jowayne Newmans | Manchester | Completed | Load_302904 | Spur Tree - 210 | 2026-08-06 07:45 | 2026-08-06 07:49 | 2026-08-06 08:00 | 2026-08-06 08:00 | 2026-08-06 08:00 | 2026-08-06 08:01 | 2026-08-06 08:01 | 2026-08-06 08:01 |  |  | Fair | No | Customer stated that they got back electricity from last night.
Outage | J.E.26.08.08073 | C001881044 | Jowayne Newmans | Manchester | Completed | Load_302905 | Spur Tree - 210 | 2026-08-06 07:45 | 2026-08-06 07:49 | 2026-08-06 07:56 | 2026-08-06 07:56 | 2026-08-06 07:56 | 2026-08-06 07:57 | 2026-08-06 07:57 | 2026-08-06 07:57 |  |  | Fair | No | Customer stated that they got back supply from last night.
Outage | J.E.26.08.08121 | C001881041 | Oshane Warren | St.Elizabeth | Completed | Load_238097 | Maggotty - 110 | 2026-08-06 07:45 | 2026-08-06 07:46 | 2026-08-06 11:44 | 2026-08-06 11:45 | 2026-08-06 11:44 | 2026-08-06 11:47 | 2026-08-06 11:49 | 2026-08-06 11:49 |  |  | Fair | No | Reconnection back service wire at secondary line used 3service connector 3 1 bolt clamps 5 ft #6 service wire voltage 120 121 240
Outage | J.E.26.08.08178 | C001881045 | Jowayne Newmans | St.Elizabeth | Completed | Load_262393 | Maggotty - 210 | 2026-08-06 07:46 | 2026-08-06 07:49 | 2026-08-06 08:07 | 2026-08-06 08:07 | 2026-08-06 09:08 | 2026-08-06 09:39 | 2026-08-06 09:42 | 2026-08-06 09:42 |  |  | Fair | No | Patrol and found 10 amp junction fuse blown also 25 kva transformer fuse cause by lightning, repair by replacing 10 and 2 amp fuses. Customers now have electricity.
Outage | J.E.26.08.07297 | C001881053 | Rodclif Dawkins | St.Catherine | Completed | Load_245048 | Twickenham - 210 | 2026-08-06 07:48 | 2026-08-06 15:22 | 2026-08-06 22:42 | 2026-08-06 22:42 | 2026-08-06 22:44 | 2026-08-06 22:44 | 2026-08-06 22:44 | 2026-08-06 22:44 |  |  | Fair | No | Calls to number provided went to voicemail
Outage | J.E.26.08.07710 | C001881051 | Rodclif Dawkins | Portmore | Completed | Load_570098 | Naggo Head - 610 | 2026-08-06 07:48 | 2026-08-06 15:22 | 2026-08-06 17:51 | 2026-08-06 17:51 | 2026-08-06 18:38 | 2026-08-06 18:38 | 2026-08-06 18:43 | 2026-08-06 18:43 |  |  | Fair | No | Customer reporting streetlight .please refer to streetlight department
Outage | J.E.26.08.08032 | C001881052 | Nickolas Rodriques | Portmore | Completed | Load_250964 | Naggo Head - 510 | 2026-08-06 07:48 | 2026-08-06 07:50 | 2026-08-06 08:13 | 2026-08-06 08:16 | 2026-08-06 08:40 | 2026-08-06 08:51 | 2026-08-06 08:52 | 2026-08-06 08:52 |  |  | Fair | No | Customer is reporting a defective streetlight. Refer to streetlight department.
Outage | J.E.26.08.08136 | C001881050 | Nickolas Rodriques | Portmore | Completed | Load_255598 | Naggo Head - 510 | 2026-08-06 07:48 | 2026-08-06 07:50 | 2026-08-06 08:52 | 2026-08-06 08:57 | 2026-08-06 09:33 | 2026-08-06 09:40 | 2026-08-06 09:49 | 2026-08-06 09:49 |  |  | Fair | No | Unable to communicate with the customer after several attempts.
Outage | J.E.26.08.08138 | C001881049 | Nickolas Rodriques | St.Catherine | Completed | Load_576141 | Twickenham - 210 | 2026-08-06 07:48 | 2026-08-06 07:50 | 2026-08-06 12:08 | 2026-08-06 12:09 | 2026-08-06 12:36 | 2026-08-06 12:56 | 2026-08-06 12:58 | 2026-08-06 12:58 |  |  | Fair | No | Found customer with power. She confirmed that the area outage was restored.
Outage | J.E.26.08.08276 | C001881048 | Nickolas Rodriques | Portmore | Completed | Load_241627 | Naggo Head - 510 | 2026-08-06 07:48 | 2026-08-06 07:50 | 2026-08-06 09:53 | 2026-08-06 10:04 | 2026-08-06 10:40 | 2026-08-06 10:56 | 2026-08-06 11:04 | 2026-08-06 11:04 |  |  | Fair | No | Found premises with electricity. The maintenance team stated that there was an internal issue that was already rectified.
Outage | J.E.26.08.08277 | C001881047 | Evan Spaulding | St.Mary | Completed | Load_246199 | Highgate - 210 | 2026-08-06 07:48 | 2026-08-06 07:49 | 2026-08-06 10:01 | 2026-08-06 10:01 | 2026-08-06 11:11 | 2026-08-06 11:27 | 2026-08-06 11:30 | 2026-08-06 11:30 |  |  | Fair | No | Phase was touching neutral on the Transformer drop lead,Reposition jumper,voltage left 118v,117v,235v.
Outage | J.E.26.08.08389 | C001881046 | Evan Spaulding | St.Mary | Completed | Load_263195 | Annotto Bay - 210 | 2026-08-06 07:48 | 2026-08-06 07:49 | 2026-08-06 08:54 | 2026-08-06 08:54 | 2026-08-06 09:34 | 2026-08-06 09:56 | 2026-08-06 09:57 | 2026-08-06 09:57 |  |  | Fair | No | Patrol line section no fault seen,replace 1-15 amps junction fuse at pole number 0207662.
Non-Outage | J.E.26.08.08224 | C001881058 | Romeo Brissett |  | Completed |  |  | 2026-08-06 07:49 | 2026-08-06 08:18 | 2026-08-06 17:55 | 2026-08-06 17:56 | 2026-08-06 17:55 | 2026-08-06 17:53 | 2026-08-06 17:57 | 2026-08-06 17:57 |  |  | Rains | No | Low Voltage due to secondary circuit been tied in. Maintenance is aware.
Non-Outage | J.E.26.08.08233 | C001881056 | Romeo Brissett |  | Completed |  |  | 2026-08-06 07:49 | 2026-08-06 08:18 | 2026-08-06 11:46 | 2026-08-06 11:47 | 2026-08-06 11:46 | 2026-08-06 11:36 | 2026-08-06 11:47 | 2026-08-06 11:47 |  |  | Fair | No | Found (1)10KVA transformer defective please send to maintenance. Related to 08193
Outage | J.E.26.08.08183 | C001881059 | Romeo Brissett | Hanover | Completed | Load_249925 | Orange Bay - 310 | 2026-08-06 07:49 | 2026-08-06 08:18 | 2026-08-06 11:40 | 2026-08-06 11:41 | 2026-08-06 11:44 | 2026-08-06 11:39 | 2026-08-06 11:46 | 2026-08-06 11:46 |  |  | Fair | No | Found (1)10KVA transformer defective please send to maintenance. Related to job #08193.
Outage | J.E.26.08.08193 | C001881057 | Romeo Brissett | Hanover | Completed | Load_267471 | Orange Bay - 310 | 2026-08-06 07:49 | 2026-08-06 08:18 | 2026-08-06 08:22 | 2026-08-06 08:23 | 2026-08-06 10:22 | 2026-08-06 11:00 | 2026-08-06 11:40 | 2026-08-06 11:40 |  |  | Fair | No | Found (1)10KVA transformer defective resulting 21customer without supply. Transformer was found tripped illegal connections removed and drop lead disconnected, removed and transformer still tripping.
Outage | J.E.26.08.08165 | C001881060 | Romeo Brissett | Hanover | Completed | Load_258790 | Orange Bay - 310 | 2026-08-06 07:50 | 2026-08-06 08:18 | 2026-08-06 11:47 | 2026-08-06 11:48 | 2026-08-06 12:56 | 2026-08-06 13:56 | 2026-08-06 14:04 | 2026-08-06 14:04 |  |  | Rains | No | Spliced and retention customer service wire. Used 20ft of #6 and 2 clamps
Non-Outage | J.E.26.08.08420 | C001881061 | Andre Smith |  | Completed |  |  | 2026-08-06 07:51 | 2026-08-06 08:13 | 2026-08-06 08:52 | 2026-08-06 08:52 | 2026-08-06 10:18 | 2026-08-06 11:07 | 2026-08-06 11:10 | 2026-08-06 11:10 | BrokenWire |  | Fair | No | Repair burnt secondary phase using 10ft 2/0 aaa supply restored reset 50kva transformer
Outage | J.E.26.08.08219 | C001881062 | Fitzroy Turner | KSAS | Completed | Load_242023 | Hunts Bay - 410 | 2026-08-06 07:51 | 2026-08-06 08:08 | 2026-08-06 08:49 | 2026-08-06 08:49 | 2026-08-06 08:50 | 2026-08-06 08:57 | 2026-08-06 08:57 | 2026-08-06 08:57 |  |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.08.07970 | C001881063 | Fitzroy Turner | KSAS | Completed | Load_240238 | Duhaney - 410 | 2026-08-06 07:52 | 2026-08-06 08:08 | 2026-08-06 09:48 | 2026-08-06 09:50 | 2026-08-06 11:23 | 2026-08-06 11:32 | 2026-08-06 11:34 | 2026-08-06 11:34 |  |  | Fair | No | Found two wires service neutral burnt mid span use 7ft of service neutral and two one bolt clamps to carry out repair supply restored to customer
Outage | J.E.26.08.08131 | C001881064 | Jowayne Newmans | Manchester | Completed | Load_249866 | Spur Tree - 210 | 2026-08-06 07:52 | 2026-08-06 07:56 | 2026-08-06 11:16 | 2026-08-06 11:17 | 2026-08-06 11:16 | 2026-08-06 11:17 | 2026-08-06 11:17 | 2026-08-06 11:17 | Fire |  | Fair | No | After several attempts to contact customer phone rang without answering and no directions to premises.
Non-Outage | J.E.26.08.08130 | C001881066 | Jowayne Newmans | Manchester | Completed | Load_249866 | Spur Tree - 210 | 2026-08-06 07:53 | 2026-08-06 07:56 | 2026-08-06 11:17 | 2026-08-06 11:18 | 2026-08-06 11:17 | 2026-08-06 11:18 | 2026-08-06 11:18 | 2026-08-06 11:18 |  |  | Fair | No | After several attempts to contact customer phone rang without answering and no directions to premises.
Non-Outage | J.E.26.08.08397 | C001881065 | Jowayne Newmans | Manchester | Completed | Load_248021 | Spur Tree - 210 | 2026-08-06 07:53 | 2026-08-06 07:56 | 2026-08-06 11:00 | 2026-08-06 11:00 | 2026-08-06 11:00 | 2026-08-06 11:01 | 2026-08-06 11:01 | 2026-08-06 11:01 |  |  | Fair | No | After several attempts to contact customer phone rang without answering and no directions to location.
Non-Outage | J.E.26.08.06895 | C001881070 | Error Coore | Manchester | Completed | Load_302011 | Spur Tree - 310 | 2026-08-06 07:58 | 2026-08-06 08:01 | 2026-08-06 09:45 | 2026-08-06 09:46 | 2026-08-06 10:10 | 2026-08-06 11:44 | 2026-08-06 11:46 | 2026-08-06 11:46 |  |  | Fair | No | Found customer with corroded phase and neutral at pothead remade corroded phase and neutral using 3 service sleeve voltage reading 114/115/229 volts
Non-Outage | J.E.26.08.06960 | C001881071 | Error Coore | Manchester | Completed | Load_245784 | Spur Tree - 310 | 2026-08-06 07:58 | 2026-08-06 08:01 | 2026-08-06 16:03 | 2026-08-06 16:03 | 2026-08-06 16:52 | 2026-08-06 16:57 | 2026-08-06 16:58 | 2026-08-06 16:58 |  |  | Fair | No | Premise not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.08.07147 | C001881069 | Error Coore | Manchester | Completed | Load_243155 | Spur Tree - 310 | 2026-08-06 07:58 | 2026-08-06 08:01 | 2026-08-06 09:01 | 2026-08-06 09:04 | 2026-08-06 09:37 | 2026-08-06 09:39 | 2026-08-06 09:41 | 2026-08-06 09:41 |  |  | Fair | No | Unable to carry out repair due to leaning pole refer to a emergency bucket truck crew
Non-Outage | J.E.26.08.07572 | C001881068 | Error Coore | Manchester | Completed | Load_1002534 | Kendal - 310 | 2026-08-06 07:58 | 2026-08-06 08:01 | 2026-08-06 15:30 | 2026-08-06 15:30 | 2026-08-06 15:50 | 2026-08-06 16:01 | 2026-08-06 16:02 | 2026-08-06 16:02 |  |  | Fair | No | Premises found ok voltage reading 117/118/235 volts
Non-Outage | J.E.26.08.07992 | C001881067 | Error Coore | Manchester | Completed | Load_267897 | Spur Tree - 310 | 2026-08-06 07:58 | 2026-08-06 08:01 | 2026-08-07 11:13 | 2026-08-07 11:14 | 2026-08-07 12:00 | 2026-08-07 14:40 | 2026-08-07 14:43 | 2026-08-07 14:43 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.08.05062 | C001881077 | Kenroy Dale | Manchester | Completed | Load_266029 | Kendal - 210 | 2026-08-06 07:59 | 2026-08-06 08:04 | 2026-08-06 08:21 | 2026-08-06 08:26 | 2026-08-06 09:58 | 2026-08-06 10:11 | 2026-08-06 10:12 | 2026-08-06 10:12 |  |  | Fair | No | Supply found okay voltage reading 114/112/226
Non-Outage | J.E.26.08.05935 | C001881076 | Error Coore | Manchester | Completed | Load_292850 | Kendal - 310 | 2026-08-06 07:59 | 2026-08-06 08:01 | 2026-08-06 08:37 | 2026-08-06 08:37 | 2026-08-06 09:01 | 2026-08-06 09:02 | 2026-08-06 09:03 | 2026-08-06 09:03 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.08.06601 | C001881075 | Error Coore | Manchester | Completed | Load_268222 | Spur Tree - 310 | 2026-08-06 07:59 | 2026-08-06 08:01 | 2026-08-06 12:27 | 2026-08-06 12:28 | 2026-08-06 12:56 | 2026-08-06 12:59 | 2026-08-06 13:00 | 2026-08-06 13:00 | LowHangingWires |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.08.06668 | C001881074 | Error Coore | Manchester | Completed | Load_244954 | Spur Tree - 310 | 2026-08-06 07:59 | 2026-08-06 08:01 | 2026-08-07 15:34 | 2026-08-07 15:35 | 2026-08-07 16:06 | 2026-08-07 16:21 | 2026-08-07 16:22 | 2026-08-07 16:22 |  |  | Fair | No | Premises found ok customer said that she did not make any report
Non-Outage | J.E.26.08.06814 | C001881073 | Error Coore | Manchester | Completed | Load_302217 | Spur Tree - 310 | 2026-08-06 07:59 | 2026-08-06 08:01 | 2026-08-07 08:05 | 2026-08-07 08:06 | 2026-08-07 08:43 | 2026-08-07 09:21 | 2026-08-07 09:28 | 2026-08-07 09:28 |  |  | Fair | No | Customer is have having low voltage due to customers or at the end of the circuit also found a primary dislodge and a defective 25 KVA xformer voltage reading nearby the tied in xformer circuit 1116/115/231 volts
Non-Outage | J.E.26.08.06826 | C001881072 | Error Coore | Manchester | Completed | Load_292247 | Spur Tree - 310 | 2026-08-06 07:59 | 2026-08-06 08:01 | 2026-08-06 09:03 | 2026-08-06 13:01 | 2026-08-06 14:26 | 2026-08-06 14:40 | 2026-08-06 14:41 | 2026-08-06 14:41 |  |  | Fair | No | Premises found ok voltage reading 115/114/229 volts
Outage | J.E.26.08.08376 | C001881080 | Elvis Trowers | KSAN | Completed | Load_247180 | Constant Spring - 210 | 2026-08-06 08:08 | 2026-08-06 08:10 | 2026-08-06 09:24 | 2026-08-06 09:25 | 2026-08-06 10:07 | 2026-08-06 10:27 | 2026-08-06 10:27 | 2026-08-06 10:27 |  |  | Fair | Yes | Happened to be internal when checked, voltage when checked was left at 118+118=236 volts, from pole to pat head.
Outage | J.E.26.08.08436 | C001881079 | Jowayne Newmans | Manchester | Completed | Load_242270 | Spur Tree - 210 | 2026-08-06 08:08 | 2026-08-06 08:21 | 2026-08-06 10:57 | 2026-08-06 10:58 | 2026-08-06 10:57 | 2026-08-06 10:58 | 2026-08-06 10:58 | 2026-08-06 10:58 |  |  | Fair | No | Customer stated that they some internal issues however they got it sorted out. Customer has electricity.
Outage | J.E.26.08.08066 | C001881081 | Rusean Allen | KSAS | Completed | Load_239845 | Hunts Bay - 210 | 2026-08-06 08:11 | 2026-08-07 08:16 | 2026-08-07 12:36 | 2026-08-07 12:37 | 2026-08-07 12:38 | 2026-08-07 12:39 | 2026-08-07 12:41 | 2026-08-07 12:41 |  |  | Fair | No | Premises found locked
Non-Outage | J.E.26.08.08432 | C001881090 | Christopher West |  | Completed |  |  | 2026-08-06 08:12 | 2026-08-06 08:14 | 2026-08-06 10:10 | 2026-08-06 10:11 | 2026-08-06 11:21 | 2026-08-06 11:22 | 2026-08-06 11:22 | 2026-08-06 11:22 |  |  | Fair | No | Kindly refer to Mr. Elliston.
Outage | J.E.26.08.07796 | C001881101 | Radcliffe Coleman | KSAS | Completed | Load_405565 | Duhaney - 210 | 2026-08-06 08:14 | 2026-08-06 08:31 | 2026-08-06 09:43 | 2026-08-06 09:44 | 2026-08-06 10:01 | 2026-08-06 10:13 | 2026-08-06 10:14 | 2026-08-06 10:14 | BrokenWire |  | Fair | No | Customer meter and meter socket was found burnt at the time of visit. Customer was advised to do the necessary repairs, then contact JPS so that new meter can be installed.
Non-Outage | J.E.26.08.05355 | C001881102 | Radcliffe Coleman |  | Completed |  |  | 2026-08-06 08:15 | 2026-08-06 08:32 | 2026-08-06 10:14 | 2026-08-06 10:15 | 2026-08-06 10:14 | 2026-08-06 10:15 | 2026-08-06 10:15 | 2026-08-06 10:15 |  |  | Fair | No | Customer meter and meter socket was found burnt at the time of visit. Customer was advised to do the necessary repairs, then contact JPS so that new meter can be installed.
Outage | J.E.26.08.07900 | C001881114 | Derrick Dawkins | Trelawny | Completed | Load_265756 | Greenwood - 210 | 2026-08-06 08:19 | 2026-08-06 12:43 | 2026-08-06 14:52 | 2026-08-06 14:52 | 2026-08-06 14:52 | 2026-08-06 14:57 | 2026-08-06 14:57 | 2026-08-06 14:57 |  |  | Rains | No | Cannot locate customer
Outage | J.E.26.08.08163 | C001881113 | Floyd Taylor | Trelawny | Completed | Load_239746 | Greenwood - 210 | 2026-08-06 08:19 | 2026-08-06 08:21 | 2026-08-06 08:47 | 2026-08-06 08:47 | 2026-08-06 09:29 | 2026-08-06 11:10 | 2026-08-06 12:25 | 2026-08-06 12:25 |  |  | Fair | No | Hex05350 - HX 22655765 suspects 15kva transformer defective also replace 15 amp junction fuse
Outage | J.E.26.08.08262 | C001881115 | Floyd Taylor | Trelawny | Completed | Load_265112 | Greenwood - 210 | 2026-08-06 08:19 | 2026-08-06 08:21 | 2026-08-06 12:25 | 2026-08-06 12:26 | 2026-08-06 12:25 | 2026-08-06 12:26 | 2026-08-06 12:28 | 2026-08-06 12:28 | BrokenWire |  | Fair | No | Disconnected service wire from post , customer pothead fell down customer was advised to get an electrician to fix issue
Outage | J.E.26.08.08438 | C001881116 | Kenroy Dale | Manchester | Completed | Load_246637 | Kendal - 210 | 2026-08-06 08:25 | 2026-08-06 08:30 | 2026-08-06 10:13 | 2026-08-06 10:14 | 2026-08-06 11:38 | 2026-08-06 12:24 | 2026-08-06 12:33 | 2026-08-06 12:33 |  |  | Fair | No | Blown 3 amp transformer fuse found line patrol one span of secondary neutral found broken conductor was splice and retention blown fuse replaced and area now with supply
Outage | J.E.26.08.07892 | C001881117 | Barrington Brown | St.James | Completed | Load_237795 | Queens Drive - 710 | 2026-08-06 08:28 | 2026-08-06 08:29 | 2026-08-06 10:52 | 2026-08-06 10:52 | 2026-08-06 11:20 | 2026-08-06 12:00 | 2026-08-06 12:00 | 2026-08-06 12:00 |  |  | Fair | No | Checked and found ok
Outage | J.E.26.08.07662 | C001881118 | Derrick Dawkins | St.James | Completed | Load_267594 | Bogue - 310 | 2026-08-06 08:30 | 2026-08-06 08:35 | 2026-08-06 11:05 | 2026-08-06 11:05 | 2026-08-06 11:42 | 2026-08-06 11:46 | 2026-08-06 12:02 | 2026-08-06 12:02 | LeaningPole |  | Fair | No | Found jps old retired pole with cable wire only leaning
Outage | J.E.26.08.08430 | C001881119 | Derrick Grubb | St.Thomas | Completed | Load_240437 | Good Year - 210 | 2026-08-06 08:31 | 2026-08-06 08:34 | 2026-08-06 11:52 | 2026-08-06 11:53 | 2026-08-06 12:05 | 2026-08-06 12:08 | 2026-08-06 12:08 | 2026-08-06 12:08 |  |  | Fair | No | Premises found okay.
Non-Outage | J.E.26.08.08216 | C001881120 | Radcliffe Coleman |  | Completed |  |  | 2026-08-06 08:32 | 2026-08-06 08:39 | 2026-08-06 10:15 | 2026-08-06 10:16 | 2026-08-06 10:40 | 2026-08-06 10:42 | 2026-08-06 10:42 | 2026-08-06 10:42 | Fire |  | Fair | No | Premises found closed at the time of visit.
Non-Outage | J.E.26.08.07976 | C001881122 | Antony Levy | KSAN | Completed | Load_256909 | Constant Spring - 210 | 2026-08-06 08:34 | 2026-08-06 08:36 | 2026-08-06 11:02 | 2026-08-06 11:03 | 2026-08-06 11:47 | 2026-08-06 12:41 | 2026-08-06 12:45 | 2026-08-06 12:45 |  |  | Fair | No | Cx stated they have been experiencing power surges of high voltage... transformer extensive check done with meter..... neutral drop lead identified to be burnt on 25kva transformer ...burnt right inside the ampact.... neutral drop lead rebounded to the open neutral via 2 clamps..... readings 120,120,240
Non-Outage | J.E.26.08.07837 | C001881123 | Antony Levy | KSAN | Completed | Load_269032 | Washington Blvd - 610 | 2026-08-06 08:35 | 2026-08-06 08:36 | 2026-08-06 11:47 | 2026-08-06 12:46 | 2026-08-06 13:30 | 2026-08-06 13:48 | 2026-08-06 13:49 | 2026-08-06 13:49 | LowHangingWires |  | Fair | No | Unable to reach customer premises not found.
Non-Outage | J.E.26.08.05846 | C001881126 | Barrington Brown | St.James | Completed | Load_266902 | Rose Hall - 210 | 2026-08-06 08:36 | 2026-08-06 08:37 | 2026-08-06 12:21 | 2026-08-06 12:21 | 2026-08-06 13:04 | 2026-08-06 13:45 | 2026-08-06 13:45 | 2026-08-06 13:45 |  |  | Fair | No | Crew found corroded joint at customer meter pole. Crew used one one bolt clamp to correct joint. Customer supply now restored 115 115 230
Non-Outage | J.E.26.08.07903 | C001881128 | Christopher Edwards | KSAN | Completed | Load_250006 | Constant Spring - 410 | 2026-08-06 08:36 | 2026-08-06 08:38 | 2026-08-06 10:21 | 2026-08-06 13:06 | 2026-08-06 13:35 | 2026-08-06 14:02 | 2026-08-06 14:03 | 2026-08-06 14:03 |  |  | Fair | No | Clear vegetation off open secondary lineThat was causing phase and neutral lines to bang whenever the wind blows
Non-Outage | J.E.26.08.07952 | C001881127 | Christopher Edwards | KSAN | Completed | Load_246237 | Constant Spring - 410 | 2026-08-06 08:36 | 2026-08-06 08:38 | 2026-08-06 08:51 | 2026-08-06 09:24 | 2026-08-06 09:23 | 2026-08-06 10:19 | 2026-08-06 10:21 | 2026-08-06 10:21 |  |  | Fair | No | Customer has their electrician on site rectifying the issue
Non-Outage | J.E.26.08.06541 | C001881131 | Shamour Haughton | St.James | Completed | Load_238660 | Bogue - 610 | 2026-08-06 08:37 | 2026-08-06 08:39 | 2026-08-06 12:04 | 2026-08-06 12:05 | 2026-08-06 14:05 | 2026-08-06 14:14 | 2026-08-06 14:19 | 2026-08-06 14:19 |  |  | Fair | No | Found okay, voltage left 115,117,232
Non-Outage | J.E.26.08.07644 | C001881129 | Shamour Haughton | St.James | Completed | Load_252070 | Bogue - 610 | 2026-08-06 08:37 | 2026-08-06 08:39 | 2026-08-06 08:51 | 2026-08-06 08:51 | 2026-08-06 09:39 | 2026-08-06 09:39 | 2026-08-06 09:41 | 2026-08-06 09:41 |  |  | Fair | No | Found customer service wire burnt off at pole, splice service wire using 1 clamps, voltage left 115,116,231
Non-Outage | J.E.26.08.07747 | C001881132 | Shamour Haughton | St.James | Completed | Load_292389 | Bogue - 610 | 2026-08-06 08:37 | 2026-08-06 08:39 | 2026-08-06 09:42 | 2026-08-06 09:42 | 2026-08-06 12:00 | 2026-08-06 12:00 | 2026-08-06 12:04 | 2026-08-06 12:04 |  |  | Fair | No | Found customer experiencing internal issue, voltage left 107,109,216
Non-Outage | J.E.26.08.08023 | C001881130 | Derrick Dawkins | St.James | Completed | Load_262825 | Bogue - 610 | 2026-08-06 08:37 | 2026-08-06 13:03 | 2026-08-06 14:52 | 2026-08-06 16:04 | 2026-08-06 16:29 | 2026-08-06 15:37 | 2026-08-06 16:37 | 2026-08-06 16:37 |  |  | Rains | No | Cannot locate customer
Non-Outage | J.E.26.08.07325 | C001881133 | Shamour Haughton | St.James | Completed | Load_248306 | Bogue - 510 | 2026-08-06 08:38 | 2026-08-06 08:39 | 2026-08-06 15:33 | 2026-08-06 15:34 | 2026-08-06 16:41 | 2026-08-06 16:42 | 2026-08-06 16:43 | 2026-08-06 16:43 |  |  | Fair | No | Check and found okay, voltage left 119,119,,238
Non-Outage | J.E.26.08.07730 | C001881134 | Christopher Edwards | KSAN | Completed | Load_250229 | Constant Spring - 410 | 2026-08-06 08:38 | 2026-08-06 08:40 | 2026-08-06 11:08 | 2026-08-06 11:08 | 2026-08-06 11:08 | 2026-08-06 12:05 | 2026-08-06 12:06 | 2026-08-06 12:06 |  |  | Fair | No | Corroded neutral joint at poleRemake joint using (1) one bolt clamps Voltage:114,113,230v
Non-Outage | J.E.26.08.07800 | C001881136 | Dwayne Cohen | KSAS | Completed | Load_244364 | Duhaney - 310 | 2026-08-06 08:39 | 2026-08-06 08:42 | 2026-08-06 09:00 | 2026-08-06 10:08 | 2026-08-06 11:34 | 2026-08-06 11:34 | 2026-08-06 11:37 | 2026-08-06 11:37 |  |  | Fair | No | Customer is concern about high consumption , please refer this report to Field Service Department
Non-Outage | J.E.26.08.07824 | C001881135 | Dwayne Cohen | KSAS | Completed | Load_269685 | Duhaney - 310 | 2026-08-06 08:39 | 2026-08-06 08:42 | 2026-08-06 09:01 | 2026-08-06 09:01 | 2026-08-06 10:01 | 2026-08-06 10:01 | 2026-08-06 10:02 | 2026-08-06 10:02 |  |  | Fair | No | Defective meter found, refer this report to Field Service Department.
Outage | J.E.26.08.08449 | C001881137 | Oshane Warren | St.Elizabeth | Completed | Load_237739 | Maggotty - 110 | 2026-08-06 08:43 | 2026-08-06 10:06 | 2026-08-06 10:52 | 2026-08-06 10:53 | 2026-08-06 10:52 | 2026-08-06 10:52 | 2026-08-06 10:53 | 2026-08-06 10:53 |  |  | Fair | No | Replace 20 amp junction fuse
Non-Outage | J.E.26.08.07462 | C001881138 | Antony Levy | KSAN | Completed | Load_252373 | Constant Spring - 210 | 2026-08-06 08:44 | 2026-08-06 08:46 | 2026-08-06 09:14 | 2026-08-06 09:14 | 2026-08-06 10:27 | 2026-08-06 11:01 | 2026-08-06 11:02 | 2026-08-06 11:02 |  |  | Fair | No | Extensive bushing required ..... also needs 150 feet 2/0 AA needed to rerun a phase of open secondary 2 phases and neutral
Non-Outage | J.E.26.08.07852 | C001881140 | Andre Smith | KSAS | Completed | Load_247103 | Greenwich - 310 | 2026-08-06 08:51 | 2026-08-06 08:52 | 2026-08-06 11:10 | 2026-08-06 11:11 | 2026-08-06 11:17 | 2026-08-06 11:28 | 2026-08-06 11:28 | 2026-08-06 11:28 |  |  | Fair | No | Premises found close
Non-Outage | J.E.26.08.08035 | C001881146 | Fitzroy Turner | KSAS | Completed | Load_261859 | Hunts Bay - 210 | 2026-08-06 08:52 | 2026-08-06 08:53 | 2026-08-06 08:58 | 2026-08-06 08:59 | 2026-08-06 09:12 | 2026-08-06 09:44 | 2026-08-06 09:48 | 2026-08-06 09:48 |  |  | Fair | No | Defective customer meter needs to be change meter burnt one side.electrician carry out repair already please send email to field service department to have issue resolved
Non-Outage | J.E.26.08.08244 | C001881144 | Oraine Minto | St.Ann | Completed | Load_266947 | Roaring River - 210 | 2026-08-06 08:52 | 2026-08-06 08:57 | 2026-08-06 11:16 | 2026-08-06 11:17 | 2026-08-06 11:17 | 2026-08-06 11:18 | 2026-08-06 11:18 | 2026-08-06 11:18 |  |  | Fair | No | Power was restored
Non-Outage | J.E.26.08.08452 | C001881141 | Daniel Francis |  | Completed |  |  | 2026-08-06 08:52 | 2026-08-06 08:56 | 2026-08-06 10:23 | 2026-08-06 10:23 | 2026-08-06 11:04 | 2026-08-06 11:08 | 2026-08-06 11:09 | 2026-08-06 11:09 | BrokenWire |  | Fair | No | Pole #574290 remove 100ft of wire from pole house was on fire
Non-Outage | J.E.26.08.07736 | C001881151 | Oraine Minto | St.Ann | Completed | Load_252506 | Ocho Rios - 310 | 2026-08-06 08:53 | 2026-08-06 08:57 | 2026-08-06 10:51 | 2026-08-06 10:52 | 2026-08-06 10:51 | 2026-08-06 10:54 | 2026-08-06 10:54 | 2026-08-06 10:54 |  |  | Fair | No | Refer to maintenance Customer states that when it is windy the power chips on and off
Non-Outage | J.E.26.08.08150 | C001881147 | Oraine Minto | St.Ann | Completed | Load_256871 | Roaring River - 210 | 2026-08-06 08:53 | 2026-08-06 08:57 | 2026-08-06 10:59 | 2026-08-06 11:00 | 2026-08-06 10:59 | 2026-08-06 11:00 | 2026-08-06 11:00 | 2026-08-06 11:00 |  |  | Fair | No | Issue was resolved
Non-Outage | J.E.26.08.07793 | C001881153 | Dwayne Cohen | KSAN | Completed | Load_256453 | Washington Blvd - 710 | 2026-08-06 08:57 | 2026-08-06 08:58 | 2026-08-06 11:37 | 2026-08-06 11:38 | 2026-08-06 12:18 | 2026-08-06 12:19 | 2026-08-06 12:19 | 2026-08-06 12:19 |  |  | Fair | No | Premises close.
Non-Outage | J.E.26.08.07933 | C001881155 | Derrick Dawkins |  | Completed |  |  | 2026-08-06 09:02 | 2026-08-06 09:03 | 2026-08-06 11:02 | 2026-08-06 11:03 | 2026-08-06 11:03 | 2026-08-06 10:38 | 2026-08-06 11:04 | 2026-08-06 11:04 |  |  | Fair | No | Found premises ok
Outage | J.E.26.08.08474 | C001881156 | Jowayne Newmans | St.Elizabeth | Completed | Load_246774 | Maggotty - 210 | 2026-08-06 09:08 | 2026-08-06 09:10 | 2026-08-06 09:47 | 2026-08-06 09:47 | 2026-08-06 09:47 | 2026-08-06 09:49 | 2026-08-06 09:49 | 2026-08-06 09:49 |  |  | Fair | No | Customer Mr Gary White confirmed that he got back electricity telephone number #876-371-4556
Outage | J.E.26.08.07622 | C001881159 | Romeo Brissett | Westmoreland | Completed | Load_243368 | Paradise - 210 | 2026-08-06 09:11 | 2026-08-06 09:30 | 2026-08-06 14:05 | 2026-08-06 14:05 | 2026-08-06 14:46 | 2026-08-06 15:30 | 2026-08-06 16:23 | 2026-08-06 16:23 |  |  | Rains | No | Removed vegetation and replaced (1)25KVA transformer fuse
Outage | J.E.26.08.08470 | C001881158 | Oshane Warren | Westmoreland | Completed | Load_244662 | Paradise - 310 | 2026-08-06 09:11 | 2026-08-06 09:30 | 2026-08-06 13:18 | 2026-08-06 13:21 | 2026-08-06 14:20 | 2026-08-06 14:21 | 2026-08-06 14:21 | 2026-08-06 14:21 |  |  | Fair | No | Replace 3 amp 25 kva transformer fuse
Non-Outage | J.E.26.08.08446 | C001881160 | Jowayne Newmans | Manchester | Completed | Load_238422 | Spur Tree - 210 | 2026-08-06 09:17 | 2026-08-06 09:30 | 2026-08-06 09:56 | 2026-08-06 09:56 | 2026-08-06 10:49 | 2026-08-06 10:54 | 2026-08-06 10:54 | 2026-08-06 10:54 | LeaningPole |  | Fair | No | Patrol and found 35ft T pole leaning and need to be straightened, pole consist of single phase primary conductor and open secondary conductor. Refer call to maintenance for follow up.
Non-Outage | J.E.26.08.08478 | C001881162 | Error Coore | Manchester | Completed | Load_244954 | Spur Tree - 310 | 2026-08-06 09:33 | 2026-08-06 09:41 | 2026-08-06 14:41 | 2026-08-06 14:42 | 2026-08-06 15:13 | 2026-08-06 15:28 | 2026-08-06 15:29 | 2026-08-06 15:29 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Outage | J.E.26.08.07997 | C001881163 | Radcliffe Coleman | St.Catherine | Completed | Load_257738 | Tredegar - 210 | 2026-08-06 09:35 | 2026-08-06 09:36 | 2026-08-06 10:42 | 2026-08-06 10:43 | 2026-08-06 11:14 | 2026-08-06 11:15 | 2026-08-06 11:16 | 2026-08-06 11:16 | Other |  | Fair | No | Premises found okay
Outage | J.E.26.08.08508 | C001881164 | Richard Samuda | Manchester | Completed | Load_263608 | Kendal - 210 | 2026-08-06 09:39 | 2026-08-06 15:08 | 2026-08-06 19:16 | 2026-08-06 20:39 | 2026-08-06 20:39 | 2026-08-06 08:40 | 2026-08-06 20:40 | 2026-08-06 20:40 |  |  | Rains | No | Call to phone no answer premises not found
Non-Outage | J.E.26.08.08467 | C001881166 | Error Coore | Manchester | Completed | Load_1002521 | Kendal - 310 | 2026-08-06 09:45 | 2026-08-06 09:46 | 2026-08-07 16:23 | 2026-08-07 16:23 | 2026-08-07 16:57 | 2026-08-07 17:02 | 2026-08-07 17:03 | 2026-08-07 17:03 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Outage | J.E.26.08.07802 | C001881167 | Javid Vernon | Westmoreland | Completed | Load_267763 | Paradise - 210 | 2026-08-06 09:51 | 2026-08-06 10:04 | 2026-08-06 10:28 | 2026-08-06 10:32 | 2026-08-06 11:00 | 2026-08-06 11:29 | 2026-08-06 11:29 | 2026-08-06 11:29 | BrokenPole |  | Fair | No | Check and found customer meter stantion more than a hundred feet away from the JPS pole customer was advised and meter found defective that needs to be replaced urgently refer to field service
Non-Outage | J.E.26.08.08473 | C001881168 | Edward Royal | KSAS | Completed | Load_252944 | Up Park Camp - 410 | 2026-08-06 10:03 | 2026-08-06 10:05 | 2026-08-06 11:24 | 2026-08-06 11:24 | 2026-08-06 12:40 | 2026-08-06 12:55 | 2026-08-06 13:22 | 2026-08-06 13:22 |  |  | Fair | No | Replaced 3A transformer fuse voltage reading 232 232 231 115 115 202 v
Non-Outage | J.E.26.08.08547 | C001881170 | Kenroy Dale | Manchester | Completed | Load_238024 | Kendal - 210 | 2026-08-06 10:33 | 2026-08-06 12:54 | 2026-08-06 13:19 | 2026-08-06 14:17 | 2026-08-06 14:22 | 2026-08-06 14:35 | 2026-08-06 14:37 | 2026-08-06 14:37 |  |  | Rains | No | Open 25 kva transformer to remade burn off drop lead, connection remade transformer re-closed area now with supply voltage reading 114/116/220
Non-Outage | J.E.26.08.08555 | C001881177 | Javid Vernon |  | Completed |  |  | 2026-08-06 10:56 | 2026-08-06 11:09 | 2026-08-06 13:12 | 2026-08-06 13:13 | 2026-08-06 13:13 | 2026-08-06 13:13 | 2026-08-06 13:13 | 2026-08-06 13:13 |  |  | Fair | No | Related to previous call job#08582
Outage | J.E.26.08.08582 | C001881178 | Javid Vernon | Westmoreland | Completed | Load_259874 | Paradise - 110 | 2026-08-06 11:08 | 2026-08-06 11:09 | 2026-08-06 11:35 | 2026-08-06 11:38 | 2026-08-06 12:30 | 2026-08-06 13:12 | 2026-08-06 13:12 | 2026-08-06 13:12 |  |  | Fair | No | Remove vegetation and refuse one 25kva transformer use 3amp fuse
Outage | J.E.26.08.07656 | C001881180 | Gregory Grossett | Portland | Completed | Load_349987 | Port Antonio - 410 | 2026-08-06 11:19 | 2026-08-06 11:23 | 2026-08-06 11:27 | 2026-08-06 11:28 | 2026-08-06 12:56 | 2026-08-06 15:04 | 2026-08-06 15:05 | 2026-08-06 15:05 |  |  | Fair | No | Secondary top phase conductor defective open 25kva transformer fuse to change cross country wire close transformer fuse to restore normal supply to the area.Material use 300ft of number 2 conductor 2 number 2 preform 4 one bolt clamps voltage reading at customer meter socket 120/118/240 on both phase.
Outage | J.E.26.08.08584 | C001881181 | Evan Spaulding | St.Mary | Completed | Load_249622 | Highgate -110 | 2026-08-06 11:19 | 2026-08-06 11:24 | 2026-08-06 12:09 | 2026-08-06 12:10 | 2026-08-06 12:50 | 2026-08-06 13:19 | 2026-08-06 13:20 | 2026-08-06 13:20 | Fire |  | Rains | No | Replace 50ft #6 Triplex service wire and 6- 1 bolt clamps,116v,115v,231v.
Non-Outage | J.E.26.07.34018 | C001881185 | Tyrese Williams | St.Ann | Completed | Load_247718 | Cardiff Hall - 210 | 2026-08-06 11:39 | 2026-08-06 11:47 | 2026-08-06 12:33 | 2026-08-06 12:43 | 2026-08-06 12:43 | 2026-08-06 12:43 | 2026-08-06 12:43 | 2026-08-06 12:43 |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.07.37847 | C001881184 | Tyrese Williams | St.Ann | Completed | Load_246183 | Cardiff Hall - 210 | 2026-08-06 11:39 | 2026-08-06 11:47 | 2026-08-06 12:03 | 2026-08-06 12:41 | 2026-08-06 12:41 | 2026-08-06 12:41 | 2026-08-06 12:41 | 2026-08-06 12:41 |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.07.37327 | C001881186 | Tyrese Williams | St.Ann | Completed | Load_265301 | Cardiff Hall - 310 | 2026-08-06 11:40 | 2026-08-06 11:47 | 2026-08-06 13:00 | 2026-08-06 13:02 | 2026-08-06 13:02 | 2026-08-06 13:03 | 2026-08-06 13:04 | 2026-08-06 13:04 |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.07.37356 | C001881187 | Tyrese Williams | St.Ann | Completed | Load_238385 | Cardiff Hall - 310 | 2026-08-06 11:40 | 2026-08-06 11:47 | 2026-08-06 12:34 | 2026-08-06 12:44 | 2026-08-06 12:45 | 2026-08-06 12:46 | 2026-08-06 12:46 | 2026-08-06 12:46 |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.08.04427 | C001881188 | Tyrese Williams | St.Ann | Completed | Load_556218 | Cardiff Hall - 210 | 2026-08-06 11:40 | 2026-08-06 11:47 | 2026-08-06 12:01 | 2026-08-06 12:48 | 2026-08-06 12:48 | 2026-08-06 12:48 | 2026-08-06 12:48 | 2026-08-06 12:48 |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.08.08578 | C001881191 | Milton Charlton |  | Completed |  |  | 2026-08-06 11:48 | 2026-08-06 11:51 | 2026-08-06 12:36 | 2026-08-06 12:36 | 2026-08-06 13:21 | 2026-08-06 13:20 | 2026-08-06 13:24 | 2026-08-06 13:24 | BrokenPole |  | Fair | No | Reconnect customer meter that was disconnected. Reconnection was done by JPS escalation.
Outage | J.E.26.08.08565 | C001881192 | Christopher Edwards | KSAN | Completed | Load_265740 | Constant Spring - 410 | 2026-08-06 11:49 | 2026-08-06 11:50 | 2026-08-06 14:04 | 2026-08-06 18:56 | 2026-08-06 19:25 | 2026-08-06 20:01 | 2026-08-06 20:01 | 2026-08-06 20:01 |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Outage | J.E.26.08.08585 | C001881193 | Christopher Edwards | KSAN | Completed | Load_248982 | Constant Spring - 410 | 2026-08-06 11:49 | 2026-08-06 11:50 | 2026-08-06 12:06 | 2026-08-06 14:05 | 2026-08-06 14:42 | 2026-08-06 15:15 | 2026-08-06 15:15 | 2026-08-06 15:15 | TreeContact | Y | Fair | No | Required bucket truck to clear bamboo off #2 twisted wire Supply is at the premises
Outage | J.E.26.08.08566 | C001881196 | Rusean Allen | KSAS | Completed | Load_263100 | Cane River - 410 | 2026-08-06 11:52 | 2026-08-06 11:54 | 2026-08-06 13:11 | 2026-08-06 13:12 | 2026-08-06 13:14 | 2026-08-06 13:16 | 2026-08-06 13:17 | 2026-08-06 13:17 |  |  | Fair | No | Hexing failure, meter having communication issues refer to field service department.
Outage | J.E.26.08.08623 | C001881195 | Fitzroy Turner | KSAS | Completed | Load_268037 | Hunts Bay - 210 | 2026-08-06 11:52 | 2026-08-06 11:54 | 2026-08-06 14:08 | 2026-08-06 14:09 | 2026-08-06 14:08 | 2026-08-06 14:09 | 2026-08-06 14:11 | 2026-08-06 14:11 |  |  | Fair | No | Found too 10amps fuse blown for bank of three 100kva transformer.replace too 10 amps fuse supply restored to the areas
Non-Outage | J.E.26.07.32696 | C001881197 | Daniel Francis | St.Ann | Completed | Load_250381 | Cardiff Hall - 210 | 2026-08-06 11:55 | 2026-08-07 08:09 | 2026-08-07 10:20 | 2026-08-07 10:21 | 2026-08-07 10:47 | 2026-08-07 10:47 | 2026-08-07 10:48 | 2026-08-07 10:48 |  |  | Fair | No | Found okay 116 116 234 in all
Non-Outage | J.E.26.07.32499 | C001881198 | Tyrese Williams | St.Ann | Completed | Load_250530 | Cardiff Hall - 210 | 2026-08-06 11:56 | 2026-08-06 12:00 | 2026-08-06 12:59 | 2026-08-06 13:06 | 2026-08-06 13:05 | 2026-08-06 13:06 | 2026-08-06 13:06 | 2026-08-06 13:06 |  |  | Fair | No | Premises not found not getting customer on phone
Non-Outage | J.E.26.07.32696 | C001881199 | Daniel Francis | St.Ann | Completed | Load_250381 | Cardiff Hall - 210 | 2026-08-06 11:56 | 2026-08-07 08:09 | 2026-08-07 14:14 | 2026-08-07 14:15 | 2026-08-07 14:41 | 2026-08-07 14:42 | 2026-08-07 14:43 | 2026-08-07 14:43 |  |  | Fair | No | Found okay
Non-Outage | J.E.26.07.32946 | C001881200 | Daniel Francis | St.Ann | Completed | Load_239317 | Cardiff Hall - 310 | 2026-08-06 11:56 | 2026-08-07 08:09 | 2026-08-07 10:49 | 2026-08-07 10:49 | 2026-08-07 11:38 | 2026-08-07 13:12 | 2026-08-07 13:18 | 2026-08-07 13:18 |  |  | Fair | No | Found service wire defective replace 100ft voltage 112/112/224
Non-Outage | J.E.26.07.35174 | C001881202 | Tyrese Williams | St.Ann | Completed | Load_245873 | Cardiff Hall - 210 | 2026-08-06 11:58 | 2026-08-06 12:00 | 2026-08-06 12:58 | 2026-08-06 13:33 | 2026-08-06 13:32 | 2026-08-06 14:28 | 2026-08-06 14:28 | 2026-08-06 14:28 |  |  | Fair | No | Remade secondary neutral jumper at pole use 1 pg clamp
Non-Outage | J.E.26.07.37656 | C001881203 | Tyrese Williams | St.Ann | Completed | Load_244555 | Cardiff Hall - 210 | 2026-08-06 11:58 | 2026-08-06 12:00 | 2026-08-06 12:14 | 2026-08-06 12:51 | 2026-08-06 12:51 | 2026-08-06 12:52 | 2026-08-06 12:52 | 2026-08-06 12:52 |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.08.08637 | C001881201 | Tyrese Williams | St.Ann | Completed | Load_574690 | Cardiff Hall - 210 | 2026-08-06 11:58 | 2026-08-06 12:00 | 2026-08-06 12:36 | 2026-08-06 12:49 | 2026-08-06 12:50 | 2026-08-06 12:50 | 2026-08-06 12:51 | 2026-08-06 12:51 |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.07.37324 | C001881204 | Tyrese Williams | St.Ann | Completed | Load_264076 | Cardiff Hall - 210 | 2026-08-06 11:59 | 2026-08-06 12:00 | 2026-08-06 12:07 | 2026-08-06 12:55 | 2026-08-06 12:54 | 2026-08-06 12:55 | 2026-08-06 12:55 | 2026-08-06 12:55 |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.07.37709 | C001881205 | Tyrese Williams | St.Ann | Completed | Load_262356 | Cardiff Hall - 210 | 2026-08-06 11:59 | 2026-08-06 12:00 | 2026-08-06 12:06 | 2026-08-06 12:57 | 2026-08-06 12:56 | 2026-08-06 12:57 | 2026-08-06 12:57 | 2026-08-06 12:57 |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.07.37765 | C001881206 | Tyrese Williams | St.Ann | Completed | Load_238385 | Cardiff Hall - 310 | 2026-08-06 11:59 | 2026-08-06 12:00 | 2026-08-06 12:05 | 2026-08-06 12:57 | 2026-08-06 12:57 | 2026-08-06 12:58 | 2026-08-06 12:58 | 2026-08-06 12:58 |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.08.08626 | C001881210 | Javid Vernon | Westmoreland | Completed | Load_267763 | Paradise - 210 | 2026-08-06 12:12 | 2026-08-06 12:16 | 2026-08-06 13:14 | 2026-08-06 13:15 | 2026-08-06 13:15 | 2026-08-06 13:16 | 2026-08-06 13:16 | 2026-08-06 13:16 | BrokenPole |  | Fair | No | Related to this call job # 07802
Outage | J.E.26.08.08517 | C001881211 | Richard Nicholas | St.Catherine | Completed | Load_242607 | New Michelton - 210 | 2026-08-06 12:13 | 2026-08-06 15:32 | 2026-08-06 19:52 | 2026-08-06 19:53 | 2026-08-06 20:21 | 2026-08-06 21:33 | 2026-08-06 21:37 | 2026-08-06 21:37 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Splice broken secondary phase,transfer secondary phase and neutral from retired pole to newly erected 40ft class 6 pole, and retention same.20ft of #2aac,8 clamp and one preformed was used to complete the repair.
Non-Outage | J.E.26.08.08507 | C001881212 | Derrick Grubb |  | Completed |  |  | 2026-08-06 12:15 | 2026-08-06 12:26 | 2026-08-06 13:15 | 2026-08-06 13:15 | 2026-08-06 13:15 | 2026-08-06 13:17 | 2026-08-06 13:17 | 2026-08-06 13:17 |  |  | Fair | No | Contact customer by phone and customer said premises is okay.
Outage | J.E.26.08.08573 | C001881213 | Barrington Brown | St.James | Completed | Load_302515 | Queens Drive - 310 | 2026-08-06 12:22 | 2026-08-06 12:24 | 2026-08-06 13:45 | 2026-08-06 13:46 | 2026-08-06 14:05 | 2026-08-06 14:09 | 2026-08-06 14:09 | 2026-08-06 14:09 |  |  | Fair | No | Crew found customer meter load side lug and wire burnt on location. Customer was advised to contact electrician to have work done
Non-Outage | J.E.26.08.04974 | C001881214 | Fitzroy Turner | KSAS | Completed | Load_239715 | Hunts Bay - 210 | 2026-08-06 12:24 | 2026-08-06 12:27 | 2026-08-06 13:36 | 2026-08-06 13:37 | 2026-08-06 13:50 | 2026-08-06 14:06 | 2026-08-06 14:08 | 2026-08-06 14:08 |  |  | Fair | No | Found bank of three 100kva transformer too fuse found blown replaced too 10 amps fuse supply restored to the areas
Outage | J.E.26.08.08568 | C001881217 | Floyd Taylor | Trelawny | Completed | Load_265863 | Greenwood - 210 | 2026-08-06 12:42 | 2026-08-06 12:56 | 2026-08-06 18:15 | 2026-08-06 18:16 | 2026-08-06 19:16 | 2026-08-06 20:44 | 2026-08-06 20:46 | 2026-08-06 20:46 |  |  | Rains | No | Replace 1-15 amp junction fuse also 1-50 KVA transformer found defective, refer to maintenance.
Outage | J.E.26.08.08569 | C001881216 | Floyd Taylor | Trelawny | Completed | Load_575541 | Greenwood - 210 | 2026-08-06 12:42 | 2026-08-06 12:56 | 2026-08-06 20:48 | 2026-08-06 20:48 | 2026-08-06 20:48 | 2026-08-06 20:48 | 2026-08-06 20:49 | 2026-08-06 20:49 |  |  | Fair | No | Customer say power was restored
Non-Outage | J.E.26.08.08028 | C001881220 | Richard Watson | St.Elizabeth | Completed | Load_242431 | Maggotty - 210 | 2026-08-06 13:07 | 2026-08-06 13:08 | 2026-08-06 13:25 | 2026-08-06 13:26 | 2026-08-06 13:54 | 2026-08-06 13:56 | 2026-08-06 13:57 | 2026-08-06 13:57 |  |  | Fair | No | Found okay, customer stated that the supply was restored from yesterday.
Non-Outage | J.E.26.08.05683 | C001881223 | Andre Smith | KSAS | Completed | Load_255768 | Hunts Bay - 310 | 2026-08-06 13:23 | 2026-08-06 13:25 | 2026-08-06 13:43 | 2026-08-06 13:43 | 2026-08-06 14:26 | 2026-08-06 15:24 | 2026-08-06 15:24 | 2026-08-06 15:24 |  |  | Fair | No | Replace defective one bolt clamp at pole on phase supply restored
Outage | J.E.26.08.08739 | C001881225 | Tyrese Williams | St.Ann | Completed | Load_264409 | Cardiff Hall - 310 | 2026-08-06 13:30 | 2026-08-06 13:44 | 2026-08-06 14:29 | 2026-08-06 14:30 | 2026-08-06 14:30 | 2026-08-06 14:34 | 2026-08-06 14:34 | 2026-08-06 14:34 |  |  | Fair | No | Premises found ok customer said she didn’t make any report
Non-Outage | J.E.26.08.08717 | C001881226 | Daniel Francis |  | Completed |  |  | 2026-08-06 13:34 | 2026-08-06 13:45 | 2026-08-06 14:28 | 2026-08-06 14:29 | 2026-08-06 14:58 | 2026-08-06 16:30 | 2026-08-06 16:56 | 2026-08-06 16:56 | Fire |  | Fair | No | Replace 50ft service wire it’s 2 customer one needs to replace wire 10mm to meter box we also use 3 one bolt clamps
Outage | J.E.26.08.08687 | C001881228 | Romaine Roberts | St.Mary | Completed | Load_267302 | Highgate -110 | 2026-08-06 13:41 | 2026-08-06 15:12 | 2026-08-06 15:33 | 2026-08-06 15:34 | 2026-08-06 16:52 | 2026-08-06 18:01 | 2026-08-06 18:02 | 2026-08-06 18:02 |  |  | Fair | No | Junction fuse found blown patrol suspect rain and lightning to cause fuse to blow patrol and replace 15 amp power restore
Non-Outage | J.E.26.08.08617 | C001881229 | Raymond Carr | St.Mary | Completed | Load_265475 | Oracabessa - 210 | 2026-08-06 13:48 | 2026-08-06 13:50 | 2026-08-06 13:56 | 2026-08-06 13:56 | 2026-08-06 14:43 | 2026-08-06 14:30 | 2026-08-06 14:44 | 2026-08-06 14:44 |  |  | Fair | No | Several calls to contact number went unanswered.
Non-Outage | J.E.26.08.07638 | C001881230 | Raymond Carr | St.Mary | Completed | Load_352448 | Oracabessa - 210 | 2026-08-06 13:49 | 2026-08-06 13:50 | 2026-08-06 14:45 | 2026-08-06 14:45 | 2026-08-06 15:01 | 2026-08-06 14:59 | 2026-08-06 15:03 | 2026-08-06 15:03 |  |  | Fair | No | Customer couldn’t be contacted.
Outage | J.E.26.08.08777 | C001881233 | Barrington Brown | St.James | Completed | Load_245339 | Queens Drive - 310 | 2026-08-06 14:16 | 2026-08-06 14:20 | 2026-08-06 15:13 | 2026-08-06 15:13 | 2026-08-06 15:13 | 2026-08-06 15:13 | 2026-08-06 15:13 | 2026-08-06 15:13 |  |  | Fair | No | Unable to locate customer. Tried calling no answer
Outage | J.E.26.08.08786 | C001881234 | Barrington Brown | St.James | Completed | Load_293527 | Queens Drive - 310 | 2026-08-06 14:17 | 2026-08-06 14:20 | 2026-08-06 14:44 | 2026-08-06 14:44 | 2026-08-06 15:12 | 2026-08-06 15:12 | 2026-08-06 15:12 | 2026-08-06 15:12 |  |  | Fair | No | Unable to locate customer. Tried calling no answer
Outage | J.E.26.08.08706 | C001881236 | Shamour Haughton | St.James | Completed | Load_1001320 | Bogue - 510 | 2026-08-06 14:18 | 2026-08-06 14:20 | 2026-08-06 17:14 | 2026-08-06 17:14 | 2026-08-06 17:14 | 2026-08-06 17:14 | 2026-08-06 17:14 | 2026-08-06 17:14 |  |  | Fair | No | Related to previous call
Outage | J.E.26.08.08708 | C001881235 | Shamour Haughton | St.James | Completed | Load_260989 | Bogue - 510 | 2026-08-06 14:18 | 2026-08-06 14:20 | 2026-08-06 17:16 | 2026-08-06 17:17 | 2026-08-06 17:16 | 2026-08-06 17:16 | 2026-08-06 17:17 | 2026-08-06 17:17 |  |  | Fair | No | Related to previous report
Outage | J.E.26.08.08951 | C001881256 | Richard Samuda | Manchester | Completed | Load_243336 | Kendal - 210 | 2026-08-06 15:07 | 2026-08-06 15:09 | 2026-08-06 17:25 | 2026-08-06 17:26 | 2026-08-06 17:54 | 2026-08-06 18:10 | 2026-08-06 18:10 | 2026-08-06 18:10 |  |  | Rains | No | Pole number:0172311 found 15 amp junction blown patrol line found nothing replaced fuse customer back to normal
Non-Outage | J.E.26.08.07966 | C001881258 | Denton Williams | Portland | Completed | Load_245592 | Port Antonio - 310 | 2026-08-06 15:10 | 2026-08-06 15:34 | 2026-08-06 17:17 | 2026-08-06 17:17 | 2026-08-06 17:47 | 2026-08-06 17:47 | 2026-08-06 17:48 | 2026-08-06 17:48 | BangingWires |  | Fair | No | Wire not belonging to JPS.
Outage | J.E.26.08.08876 | C001881257 | Denton Williams | Portland | Completed | Load_351947 | Port Antonio - 310 | 2026-08-06 15:10 | 2026-08-06 15:34 | 2026-08-06 16:04 | 2026-08-06 17:10 | 2026-08-06 17:10 | 2026-08-06 17:14 | 2026-08-06 17:16 | 2026-08-06 17:16 |  |  | Fair | No | Use four ft of #6 neutral conductor to correct broken service neutral.116/115/232 volts
Non-Outage | J.E.26.08.06611 | C001881260 | Stephen Taylor | St.Thomas | Completed | Load_327665 | Lysson - 410 | 2026-08-06 15:11 | 2026-08-06 15:12 | 2026-08-06 16:32 | 2026-08-06 16:32 | 2026-08-06 17:23 | 2026-08-06 17:23 | 2026-08-06 17:25 | 2026-08-06 17:25 |  |  | Fair | No | Patrol area and power is in the area but several calls to single customer and no one answering the phone failed to locate customer
Non-Outage | J.E.26.08.07534 | C001881264 | Hopeton Henry | St.Thomas | Completed | Load_266044 | Good Year - 210 | 2026-08-06 15:11 | 2026-08-07 08:04 | 2026-08-07 08:34 | 2026-08-07 12:41 | 2026-08-07 12:40 | 2026-08-07 12:41 | 2026-08-07 12:42 | 2026-08-07 12:42 |  |  | Fair | No | Issue resolved 112-109-220 volts
Non-Outage | J.E.26.08.07603 | C001881262 | Hopeton Henry | St.Thomas | Completed | Load_266044 | Good Year - 210 | 2026-08-06 15:11 | 2026-08-07 08:04 | 2026-08-07 08:34 | 2026-08-07 08:39 | 2026-08-07 10:35 | 2026-08-07 12:32 | 2026-08-07 12:40 | 2026-08-07 12:40 |  |  | Fair | No | Remove tree from secondary and remake jump 112-109-220 volt
Non-Outage | J.E.26.08.08161 | C001881261 | Stephen Taylor | St.Thomas | Completed | Load_246431 | Good Year - 210 | 2026-08-06 15:11 | 2026-08-06 15:12 | 2026-08-06 18:52 | 2026-08-06 18:52 | 2026-08-06 18:52 | 2026-08-06 18:52 | 2026-08-06 18:53 | 2026-08-06 18:53 |  |  | Fair | No | Contact customer and customer say that the best time to visit the premises is tomorrow
Non-Outage | J.E.26.08.08167 | C001881263 | Stephen Taylor | St.Thomas | Completed | Load_246431 | Good Year - 210 | 2026-08-06 15:11 | 2026-08-06 15:12 | 2026-08-06 17:32 | 2026-08-06 17:32 | 2026-08-06 17:32 | 2026-08-06 17:32 | 2026-08-06 17:34 | 2026-08-06 17:34 |  |  | Fair | No | Failed to locate customer several calls and no one answering the phone
Non-Outage | J.E.26.08.08231 | C001881259 | Stephen Taylor | St.Thomas | Completed | Load_577132 | Lysson - 410 | 2026-08-06 15:11 | 2026-08-06 15:12 | 2026-08-06 16:08 | 2026-08-06 16:09 | 2026-08-06 16:30 | 2026-08-06 16:30 | 2026-08-06 16:31 | 2026-08-06 16:31 |  |  | Fair | No | Call to customer and customer said power is back now and okay
Non-Outage | J.E.26.08.06262 | C001881265 | Stephen Taylor | St.Thomas | Completed | Load_238488 | Good Year - 210 | 2026-08-06 15:12 | 2026-08-06 15:12 | 2026-08-06 17:29 | 2026-08-06 17:30 | 2026-08-06 17:29 | 2026-08-06 17:30 | 2026-08-06 17:31 | 2026-08-06 17:31 |  |  | Fair | No | Check with customer and customer said power is back now
Non-Outage | J.E.26.07.34097 | C001881268 | Christopher Edwards | KSAN | Completed | Load_265660 | Constant Spring - 410 | 2026-08-06 15:16 | 2026-08-06 15:18 | 2026-08-06 18:22 | 2026-08-06 18:53 | 2026-08-06 18:52 | 2026-08-06 18:54 | 2026-08-06 18:55 | 2026-08-06 18:55 |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Outage | J.E.26.08.08650 | C001881266 | Selvin White | St.Elizabeth | Completed | Load_246804 | Maggotty - 110 | 2026-08-06 15:16 | 2026-08-06 15:17 | 2026-08-06 19:12 | 2026-08-06 19:14 | 2026-08-06 19:30 | 2026-08-06 20:08 | 2026-08-06 20:08 | 2026-08-06 20:08 |  |  | Rains | No | Replace a blown 1.5 amp fuse for a 15 KVA transformer that supply HEX 01881 box. Supply restored to the affected customers. Dead bird found at location was said to be the cause.
Outage | J.E.26.08.08824 | C001881267 | Selvin White | St.Elizabeth | Completed | Load_262525 | Maggotty - 110 | 2026-08-06 15:16 | 2026-08-06 15:17 | 2026-08-06 20:08 | 2026-08-06 20:38 | 2026-08-06 21:15 | 2026-08-06 21:34 | 2026-08-06 21:38 | 2026-08-06 21:38 |  |  | Fair | No | Replace a blown 1.5 amp fuse for a 25 KVA transformer circuit after patrolling secondary circuit. Supply restored to the line section.
Non-Outage | J.E.26.07.32773 | C001881270 | Christopher Edwards | KSAN | Completed | Load_264247 | Constant Spring - 410 | 2026-08-06 15:17 | 2026-08-06 15:18 | 2026-08-06 15:21 | 2026-08-06 15:22 | 2026-08-06 16:36 | 2026-08-06 17:38 | 2026-08-06 18:22 | 2026-08-06 18:22 |  |  | Fair | No | Removed illegal connections that was causing phase and neutral joint to make contact which each other Voltage:114,113,228v
Outage | J.E.26.08.08867 | C001881272 | Floyd Taylor | Trelawny | Completed | Load_244593 | Greenwood - 110 | 2026-08-06 15:19 | 2026-08-06 15:21 | 2026-08-06 15:53 | 2026-08-06 15:53 | 2026-08-06 17:01 | 2026-08-06 17:29 | 2026-08-06 17:30 | 2026-08-06 17:30 |  |  | Rains | No | Replace 1-30amp junction fuse
Outage | J.E.26.08.08896 | C001881271 | Floyd Taylor | Trelawny | Completed | Load_265272 | Greenwood - 110 | 2026-08-06 15:19 | 2026-08-06 15:21 | 2026-08-06 17:30 | 2026-08-06 17:30 | 2026-08-06 18:12 | 2026-08-06 18:13 | 2026-08-06 18:15 | 2026-08-06 18:15 |  |  | Fair | No | Power was restored
Outage | J.E.26.08.09006 | C001881274 | Neville Spencer | St.Catherine | Completed | Load_263189 | Rhodens Pen - 310 | 2026-08-06 15:19 | 2026-08-06 15:20 | 2026-08-06 15:27 | 2026-08-06 15:27 | 2026-08-06 15:58 | 2026-08-06 16:24 | 2026-08-06 16:24 | 2026-08-06 16:24 |  |  | Fair | No | Retention 2 spans of secondary neutral Conductor used 2 clamps,1, preferred. Also renew blown 3 amp fuse protecting 25 kva xmfr at pole #. 013215 supply restored.
Outage | J.E.26.08.07176 | C001881276 | Rodclif Dawkins | Portmore | Completed | Load_241440 | Naggo Head - 510 | 2026-08-06 15:23 | 2026-08-06 15:24 | 2026-08-06 18:47 | 2026-08-06 20:34 | 2026-08-06 20:46 | 2026-08-06 21:00 | 2026-08-06 21:04 | 2026-08-06 21:04 | LeaningPole |  | Fair | No | Found 40/4 pole with single phase deadend rotten 100% . Pole is equipped with 50kva transformer. Please refer to Kymani Allman and Clement Smih at maintenance.
Outage | J.E.26.08.08868 | C001881275 | Rodclif Dawkins | Portmore | Completed | Load_570083 | Naggo Head - 610 | 2026-08-06 15:23 | 2026-08-06 15:25 | 2026-08-06 16:41 | 2026-08-06 18:44 | 2026-08-06 18:49 | 2026-08-06 19:00 | 2026-08-06 19:06 | 2026-08-06 19:06 |  |  | Fair | No | Found triplex #6 with wrapped joints at pothead. Using 2 penunion joint replaced.
Outage | J.E.26.08.08881 | C001881277 | Milton Charlton | KSAN | Completed | Load_412923 | Hope - 410 | 2026-08-06 15:25 | 2026-08-06 15:26 | 2026-08-06 15:32 | 2026-08-06 15:32 | 2026-08-06 16:23 | 2026-08-06 16:25 | 2026-08-06 16:25 | 2026-08-06 16:25 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Non-Outage | J.E.26.08.08645 | C001881279 | Neville Spencer |  | Completed |  |  | 2026-08-06 15:26 | 2026-08-06 15:27 | 2026-08-06 16:24 | 2026-08-06 16:25 | 2026-08-06 16:51 | 2026-08-06 17:38 | 2026-08-06 17:40 | 2026-08-06 17:40 |  |  | Fair | No | Reconnect 3, wire service at pothead used 3 6/6 sleeves voltage reading 114 117 232 supply restored.
Outage | J.E.26.08.08765 | C001881278 | Clyde Brown | Clarendon | Completed | Load_262895 | May Pen - 110 | 2026-08-06 15:26 | 2026-08-06 15:27 | 2026-08-06 15:44 | 2026-08-06 15:45 | 2026-08-06 17:35 | 2026-08-06 17:25 | 2026-08-06 17:39 | 2026-08-06 17:39 | Fire |  | Fair | No | Cannot be located customer not answering phone
Outage | J.E.26.08.08926 | C001881280 | Richard Nicholas | St.Catherine | Completed | Load_245424 | New Michelton - 310 | 2026-08-06 15:31 | 2026-08-06 15:33 | 2026-08-06 16:16 | 2026-08-06 16:17 | 2026-08-06 18:56 | 2026-08-06 19:50 | 2026-08-06 19:51 | 2026-08-06 19:51 |  |  | Fair | No | Replaced blown 25kva transformer 5amp fuse on pole #0102184.
Non-Outage | J.E.26.08.06502 | C001881284 | Kaydon Taylor |  | Completed |  |  | 2026-08-06 15:33 | 2026-08-06 15:34 | 2026-08-06 20:44 | 2026-08-06 20:51 | 2026-08-06 20:51 | 2026-08-06 20:53 | 2026-08-06 20:53 | 2026-08-06 20:53 | Fire |  | Fair | No | Premises closed
Non-Outage | J.E.26.08.08770 | C001881283 | Kemark Slue |  | Completed |  |  | 2026-08-06 15:33 | 2026-08-06 15:34 | 2026-08-06 16:19 | 2026-08-06 19:11 | 2026-08-06 19:10 | 2026-08-06 17:00 | 2026-08-06 19:16 | 2026-08-06 19:16 | Fire |  | Fair | No | Premises was checked and found okay.
Outage | J.E.26.08.08790 | C001881282 | Kemark Slue | St.Catherine | Completed | Load_256288 | Twickenham - 310 | 2026-08-06 15:33 | 2026-08-06 15:34 | 2026-08-06 16:19 | 2026-08-06 18:09 | 2026-08-06 19:09 | 2026-08-06 16:54 | 2026-08-06 19:10 | 2026-08-06 19:10 | Fire |  | Fair | No | Premises was checked and found okay.
Non-Outage | J.E.26.08.08059 | C001881288 | Kemark Slue | St.Catherine | Completed | Load_1001550 | Tredegar - 510 | 2026-08-06 15:34 | 2026-08-06 15:36 | 2026-08-06 16:42 | 2026-08-06 19:17 | 2026-08-06 19:17 | 2026-08-06 18:00 | 2026-08-06 19:41 | 2026-08-06 19:41 | BrokenPole |  | Fair | No | Upon arrival at the location the crew discovered that a 40 ft cl 4 pole is badly leaning towards the roadway and 100 % rotten, pole consisting of two phase primary, rack open secondary, three 3-wire service and telecommunications also there’s a 30 ft cl 6 secondary pole that 98% rotten in close proximity as well please refer to A. Murray to have a detailed patrol done on the line section and replace defective poles asap.
Non-Outage | J.E.26.08.07617 | C001881289 | Kemark Slue | St.Catherine | Completed | Load_260095 | Twickenham - 310 | 2026-08-06 15:35 | 2026-08-06 15:36 | 2026-08-06 16:03 | 2026-08-06 16:03 | 2026-08-06 18:07 | 2026-08-06 16:00 | 2026-08-06 18:08 | 2026-08-06 18:08 | LeaningPole |  | Fair | No | Unable to locate premises due to inadequate directions and all calls to number given were futile.
Non-Outage | J.E.26.08.02965 | C001881295 | Kaydon Taylor | KSAS | Completed | Load_263200 | Hunts Bay - 310 | 2026-08-06 15:36 | 2026-08-06 15:37 | 2026-08-06 20:41 | 2026-08-06 20:53 | 2026-08-06 20:53 | 2026-08-06 20:55 | 2026-08-06 20:55 | 2026-08-06 20:55 |  |  | Fair | No | Unable to reach customer via telecommunication.
Non-Outage | J.E.26.08.04562 | C001881293 | Kaydon Taylor | KSAS | Completed | Load_269480 | Hunts Bay - 710 | 2026-08-06 15:36 | 2026-08-06 15:37 | 2026-08-06 16:52 | 2026-08-06 16:54 | 2026-08-06 18:31 | 2026-08-06 18:35 | 2026-08-06 18:35 | 2026-08-06 18:35 |  |  | Fair | No | Premises closed
Non-Outage | J.E.26.08.04724 | C001881291 | Kaydon Taylor | KSAS | Completed | Load_269480 | Hunts Bay - 710 | 2026-08-06 15:36 | 2026-08-06 15:37 | 2026-08-06 18:36 | 2026-08-06 18:36 | 2026-08-06 20:39 | 2026-08-06 20:00 | 2026-08-06 20:40 | 2026-08-06 20:40 |  |  | Fair | No | Premises closed
Non-Outage | J.E.26.08.08851 | C001881299 | Rodclif Dawkins | Portmore | Completed | Load_247114 | Naggo Head - 610 | 2026-08-06 15:36 | 2026-08-06 15:40 | 2026-08-06 18:10 | 2026-08-06 19:07 | 2026-08-06 19:36 | 2026-08-06 20:17 | 2026-08-06 20:20 | 2026-08-06 20:20 | BrokenWire |  | Fair | No | Found triplex #6 supplying 2w meter with corroded joint at pothead. Using 2 penunion joint repaired
Non-Outage | J.E.26.08.08984 | C001881298 | Raymond Lewis |  | Completed |  |  | 2026-08-06 15:36 | 2026-08-06 15:45 | 2026-08-06 21:05 | 2026-08-06 21:05 | 2026-08-06 21:05 | 2026-08-06 21:06 | 2026-08-06 21:06 | 2026-08-06 21:06 | BrokenWire |  | Rains | No | Supply restored
Non-Outage | J.E.26.08.09059 | C001881297 | Rodclif Dawkins |  | Completed |  |  | 2026-08-06 15:36 | 2026-08-06 15:41 | 2026-08-06 20:34 | 2026-08-06 21:05 | 2026-08-06 21:16 | 2026-08-06 21:16 | 2026-08-06 21:18 | 2026-08-06 21:18 | LeaningPole |  | Fair | No | Found2 40/6 pole with 3phase T construction leaning. Dig and straighten required. Please refer to maintenance
Outage | J.E.26.08.08776 | C001881290 | Raymond Lewis | St.Ann | Completed | Load_251263 | Cardiff Hall - 310 | 2026-08-06 15:36 | 2026-08-06 15:37 | 2026-08-06 22:00 | 2026-08-06 22:01 | 2026-08-06 22:00 | 2026-08-06 22:15 | 2026-08-06 22:16 | 2026-08-06 22:16 |  |  | Rains | No | Refuse and close 15 A junction fuse
Outage | J.E.26.08.08795 | C001881292 | Daniel Francis | St.Ann | Completed | Load_269163 | Cardiff Hall - 210 | 2026-08-06 15:36 | 2026-08-07 08:08 | 2026-08-07 08:45 | 2026-08-07 08:45 | 2026-08-07 09:56 | 2026-08-07 10:14 | 2026-08-07 10:17 | 2026-08-07 10:17 |  |  | Fair | No | Please refer to field service customer connect in hexing box meter not responding
Outage | J.E.26.08.08805 | C001881294 | Raymond Lewis | St.Ann | Completed | Load_268180 | Cardiff Hall - 310 | 2026-08-06 15:36 | 2026-08-06 15:45 | 2026-08-06 16:33 | 2026-08-06 16:33 | 2026-08-06 19:09 | 2026-08-06 20:57 | 2026-08-06 20:59 | 2026-08-06 20:59 |  |  | Rains | No | Patrol and Remade John crow from primary refuse and close 25 A junction fuse
Outage | J.E.26.08.09013 | C001881300 | Daniel Francis | St.Ann | Completed | Load_573336 | Roaring River - 410 | 2026-08-06 15:36 | 2026-08-06 15:40 | 2026-08-06 16:56 | 2026-08-06 16:56 | 2026-08-06 17:05 | 2026-08-06 17:06 | 2026-08-06 17:06 | 2026-08-06 17:06 |  |  | Fair | No | We call customer and she say light come back
Non-Outage | J.E.26.08.08747 | C001881304 | Romeo Brissett |  | Completed |  |  | 2026-08-06 15:46 | 2026-08-06 15:47 | 2026-08-06 17:52 | 2026-08-06 17:53 | 2026-08-06 17:52 | 2026-08-06 17:54 | 2026-08-06 17:55 | 2026-08-06 17:55 |  |  | Rains | No | Check and found secondary circuit tied in due defective 50kva transformer, resulting low voltage V/R 71-82-163. Please send to maintenance.
Non-Outage | J.E.26.08.08761 | C001881303 | Romeo Brissett | Hanover | Completed | Load_253641 | Orange Bay - 210 | 2026-08-06 15:46 | 2026-08-06 15:47 | 2026-08-06 16:26 | 2026-08-06 16:26 | 2026-08-06 16:53 | 2026-08-06 17:28 | 2026-08-06 17:52 | 2026-08-06 17:52 |  |  | Rains | No | Removed vegetation, replaced (2)10amps junction and (2)25KVA transformer fuse,
Non-Outage | J.E.26.07.31356 | C001881307 | Eric Williams | KSAN | Completed | Load_263165 | Constant Spring - 210 | 2026-08-06 15:47 | 2026-08-06 15:48 | 2026-08-06 20:09 | 2026-08-06 20:10 | 2026-08-06 21:02 | 2026-08-06 21:22 | 2026-08-06 21:23 | 2026-08-06 21:23 |  |  | Fair | No | Calls to customer went unanswered
Non-Outage | J.E.26.08.04431 | C001881308 | Eric Williams | KSAN | Completed | Load_252360 | Constant Spring - 210 | 2026-08-06 15:47 | 2026-08-06 15:48 | 2026-08-06 18:09 | 2026-08-06 18:10 | 2026-08-06 18:47 | 2026-08-06 20:08 | 2026-08-06 20:09 | 2026-08-06 20:09 |  |  | Fair | No | 3 wire service Corroded joints at pole, used 1 onebolt clamp
Non-Outage | J.E.26.07.10976 | C001881314 | Romaine Roberts | St.Mary | Completed | Load_241220 | Highgate - 210 | 2026-08-06 15:50 | 2026-08-06 16:31 | 2026-08-06 18:06 | 2026-08-06 18:07 | 2026-08-06 19:33 | 2026-08-06 19:47 | 2026-08-06 19:48 | 2026-08-06 19:48 |  |  | Fair | No | Open and close 25 kva transformer to splice and retention one span of secondary neutral power restore
Outage | J.E.26.08.08523 | C001881313 | Dean- Smith | Hanover | Completed | Load_1001379 | Orange Bay - 310 | 2026-08-06 15:50 | 2026-08-06 16:00 | 2026-08-06 16:54 | 2026-08-06 16:54 | 2026-08-06 16:54 | 2026-08-06 16:54 | 2026-08-06 16:56 | 2026-08-06 16:56 |  |  | Rains | No | Unable to correct single phasing because of rain. Please have morning team re-visit location.
Outage | J.E.26.08.08567 | C001881312 | Dean- Smith | Hanover | Completed | Load_253221 | Orange Bay - 310 | 2026-08-06 15:50 | 2026-08-06 16:00 | 2026-08-06 17:00 | 2026-08-06 17:00 | 2026-08-06 18:01 | 2026-08-06 18:01 | 2026-08-06 18:03 | 2026-08-06 18:03 |  |  | Rains | No | Check and found ok
Outage | J.E.26.08.08965 | C001881311 | Dean- Smith | Hanover | Completed | Load_249767 | Orange Bay - 310 | 2026-08-06 15:50 | 2026-08-06 16:00 | 2026-08-06 19:10 | 2026-08-06 19:11 | 2026-08-06 19:12 | 2026-08-06 19:14 | 2026-08-06 19:15 | 2026-08-06 19:15 |  |  | Rains | No | Area was restored
Outage | J.E.26.08.09110 | C001881315 | Denton Williams | Portland | Completed | Load_264174 | Port Antonio - 410 | 2026-08-06 15:51 | 2026-08-06 16:30 | 2026-08-06 17:53 | 2026-08-06 17:53 | 2026-08-06 19:48 | 2026-08-06 19:49 | 2026-08-06 19:52 | 2026-08-06 19:52 |  | Y | Fair | No | Close three trip saver after open two15 amp trip saver and remove bamboo from line. All customers restored
Outage | J.E.26.08.09054 | C001881316 | Eric Williams | KSAS | Completed | Load_578970 | Up Park Camp - 310 | 2026-08-06 15:57 | 2026-08-06 15:58 | 2026-08-06 16:17 | 2026-08-06 16:17 | 2026-08-06 18:06 | 2026-08-06 18:07 | 2026-08-06 18:08 | 2026-08-06 18:08 |  | Y | Fair | No | Defective switch and fuse holder and 2 blown 50amps fuse found and replaced, cause by bushing, major bushing done
Outage | J.E.26.08.08979 | C001881321 | Derrick Dawkins | St.James | Completed | Load_301752 | Bogue - 310 | 2026-08-06 16:01 | 2026-08-06 16:02 | 2026-08-06 16:37 | 2026-08-06 16:38 | 2026-08-06 16:52 | 2026-08-06 18:22 | 2026-08-06 18:32 | 2026-08-06 18:32 |  |  | Rains | No | Found 3 (50amp junction fuse due to lightning replace 3 (50amp at pole number 008953
Outage | J.E.26.08.09086 | C001881319 | Clyde Brown | Clarendon | Completed | Load_250271 | May Pen - 110 | 2026-08-06 16:01 | 2026-08-06 16:02 | 2026-08-06 17:40 | 2026-08-06 17:41 | 2026-08-06 21:40 | 2026-08-06 21:30 | 2026-08-06 21:46 | 2026-08-06 21:46 |  |  | Fair | No | Blown 100 amps junction fuse at Danks,line patrolled and no fault seen,blown 65 amps junction fuse replaced
Outage | J.E.26.08.08724 | C001881322 | Shamour Haughton | St.James | Completed | Load_264245 | Bogue - 510 | 2026-08-06 16:02 | 2026-08-06 16:04 | 2026-08-06 17:15 | 2026-08-06 17:16 | 2026-08-06 17:15 | 2026-08-06 17:15 | 2026-08-06 17:16 | 2026-08-06 17:16 |  |  | Fair | No | Related to previous call
Outage | J.E.26.08.08725 | C001881324 | Shamour Haughton | St.James | Completed | Load_254670 | Bogue - 510 | 2026-08-06 16:03 | 2026-08-06 16:04 | 2026-08-06 16:50 | 2026-08-06 16:50 | 2026-08-06 16:50 | 2026-08-06 17:10 | 2026-08-06 17:12 | 2026-08-06 17:12 |  |  | Fair | No | Found 1,50amp junction fuse blown, refuse 50amp junction
Outage | J.E.26.08.08726 | C001881323 | Tajay Bernard | Hanover | Completed | Load_292444 | Orange Bay - 310 | 2026-08-06 16:03 | 2026-08-07 07:29 | 2026-08-07 07:32 | 2026-08-07 07:33 | 2026-08-07 08:03 | 2026-08-07 08:52 | 2026-08-07 08:52 | 2026-08-07 08:52 | BrokenWire |  | Fair | No | Remove vegetation and refuse 1 25kva Transformer and 1 8amp junction fuse use 3amp fuse
Outage | J.E.26.08.09165 | C001881327 | Denton Williams | Portland | Completed | Load_349777 | Port Antonio - 410 | 2026-08-06 16:29 | 2026-08-06 16:30 | 2026-08-06 19:52 | 2026-08-06 19:52 | 2026-08-06 20:06 | 2026-08-06 20:07 | 2026-08-06 20:09 | 2026-08-06 20:09 |  |  | Fair | No | No driving direction, number provided going straight to mail box
Outage | J.E.26.08.09102 | C001881328 | Richman Whyte | Westmoreland | Completed | Load_292720 | Paradise - 310 | 2026-08-06 16:30 | 2026-08-06 16:32 | 2026-08-06 16:46 | 2026-08-06 16:47 | 2026-08-06 17:58 | 2026-08-06 19:07 | 2026-08-06 19:10 | 2026-08-06 19:10 |  |  | Rains | No | Change defective surge arrester off twenty five kva transformer and replace two different three amp twenty five kva transformer fuse and two junction fuse 8&25 amp fuse
Outage | J.E.26.08.09151 | C001881330 | Marlon Authors | Manchester | Completed | Load_292834 | Spur Tree - 210 | 2026-08-06 16:30 | 2026-08-06 16:32 | 2026-08-06 17:15 | 2026-08-06 17:15 | 2026-08-06 19:01 | 2026-08-06 19:33 | 2026-08-06 19:33 | 2026-08-06 19:33 | Fire |  | Fair | No | Supply checked and found working ok. Customer said he doesn’t want supply to be disrupted to do a voltage rdg because he has customers
Outage | J.E.26.08.09174 | C001881329 | Richard Samuda | Manchester | Completed | Load_255147 | Kendal - 210 | 2026-08-06 16:30 | 2026-08-06 16:32 | 2026-08-06 18:11 | 2026-08-06 18:24 | 2026-08-06 18:36 | 2026-08-06 19:06 | 2026-08-06 19:06 | 2026-08-06 19:06 |  |  | Rains | No | Pole number: 0176930 found 20amp junction blown patrol area found nothing replaced fuse customer back to normal
Outage | J.E.26.08.09198 | C001881331 | Richard Nicholas | St.Catherine | Completed | Load_249974 | Rhodens Pen - 210 | 2026-08-06 16:30 | 2026-08-06 16:31 | 2026-08-06 21:38 | 2026-08-06 21:38 | 2026-08-06 22:58 | 2026-08-06 22:58 | 2026-08-06 23:01 | 2026-08-06 23:01 |  |  | EarthMovement | No | 10kva transformer located on pole #0063718 checked and found defective.follow up to replace same required.
Outage | J.E.26.08.09123 | C001881332 | Neckell Ormsby | St.Ann | Completed | Load_247343 | Upper White River - 110 | 2026-08-06 16:31 | 2026-08-06 16:41 | 2026-08-06 16:51 | 2026-08-06 17:03 | 2026-08-06 17:28 | 2026-08-06 17:44 | 2026-08-06 17:44 | 2026-08-06 17:44 |  |  | Rains | No | Unable to locate customer after several calls however called call center and have the supply reconnected
Outage | J.E.26.08.09162 | C001881333 | Romaine Roberts | St.Mary | Completed | Load_267027 | Highgate -110 | 2026-08-06 16:32 | 2026-08-06 16:34 | 2026-08-06 18:02 | 2026-08-06 18:02 | 2026-08-06 18:06 | 2026-08-06 18:06 | 2026-08-06 18:06 | 2026-08-06 18:06 |  |  | Fair | No | Junction fuse found blown patrol suspect rain and lightning to cause fuse to blow patrol and replace 15 amp power restore
Outage | J.E.26.08.09181 | C001881334 | Neckell Ormsby | St.Mary | Completed | Load_239754 | Highgate - 210 | 2026-08-06 16:32 | 2026-08-06 16:41 | 2026-08-06 16:51 | 2026-08-06 16:52 | 2026-08-06 17:01 | 2026-08-06 17:03 | 2026-08-06 17:03 | 2026-08-06 17:03 |  |  | Rains | No | Clarendon call not St Mary
Outage | J.E.26.08.09208 | C001881336 | Milton Charlton | KSAN | Completed | Load_248814 | Hope - 510 | 2026-08-06 16:46 | 2026-08-06 16:46 | 2026-08-06 16:52 | 2026-08-06 16:53 | 2026-08-06 18:47 | 2026-08-06 19:00 | 2026-08-06 19:08 | 2026-08-06 19:08 | Fire |  | Fair | No | Found one 10 amps junction fuse blown at pole # 0073576. Refused using one 10 amps fuse and reclosed junction switch.
Outage | J.E.26.08.09039 | C001881339 | Daniel Francis | St.Ann | Completed | Load_239867 | Cardiff Hall - 310 | 2026-08-06 16:56 | 2026-08-07 08:09 | 2026-08-07 13:44 | 2026-08-07 13:44 | 2026-08-07 14:12 | 2026-08-07 14:13 | 2026-08-07 14:14 | 2026-08-07 14:14 |  |  | Fair | No | We call customer them say light come found okay
Outage | J.E.26.08.09211 | C001881340 | Daniel Francis | St.Ann | Completed | Load_243179 | Ocho Rios - 310 | 2026-08-06 16:57 | 2026-08-06 16:59 | 2026-08-06 18:25 | 2026-08-06 18:26 | 2026-08-06 18:26 | 2026-08-06 18:29 | 2026-08-06 18:29 | 2026-08-06 18:29 |  |  | Fair | No | We call customer and she say light come when I ask what time it come is the same time we were there working so it’s okay now she says
Non-Outage | J.E.26.08.09250 | C001881341 | Raymond Lewis |  | Completed |  |  | 2026-08-06 16:59 | 2026-08-06 17:34 | 2026-08-06 21:02 | 2026-08-06 21:03 | 2026-08-06 21:03 | 2026-08-06 21:03 | 2026-08-06 21:04 | 2026-08-06 21:04 | BrokenWire |  | Rains | No | Supply restored
Outage | J.E.26.08.09275 | C001881348 | Kemark Slue | St.Catherine | Completed | Load_556330 | Rhodens Pen - 210 | 2026-08-06 17:59 | 2026-08-06 18:00 | 2026-08-06 19:09 | 2026-08-06 19:42 | 2026-08-06 20:05 | 2026-08-06 19:14 | 2026-08-06 20:06 | 2026-08-06 20:06 |  |  | Fair | No | Upon arrival at the location the crew discovered that customer’s meter was off, liaison with the Escalation department who ad meter turned on.
Outage | J.E.26.08.08921 | C001881349 | Derrick Dawkins | St.James | Completed | Load_269909 | Bogue - 310 | 2026-08-06 18:21 | 2026-08-06 18:22 | 2026-08-06 18:32 | 2026-08-06 18:52 | 2026-08-06 18:52 | 2026-08-06 19:46 | 2026-08-06 19:55 | 2026-08-06 19:55 |  |  | Rains | No | Found 2 (65amp trip saver brown due to lightning. Close trip saver at pole LAB6-677
Outage | J.E.26.08.08936 | C001881350 | Shamour Haughton | St.James | Completed | Load_257668 | Queens Drive - 710 | 2026-08-06 18:23 | 2026-08-06 18:24 | 2026-08-06 18:58 | 2026-08-06 18:58 | 2026-08-06 20:08 | 2026-08-06 20:08 | 2026-08-06 20:11 | 2026-08-06 20:11 |  |  | Fair | No | Found 1,50amp junction fuse blown, refuse 50amp junction
Outage | J.E.26.08.09255 | C001881354 | Derrick Grubb | St.Thomas | Completed | Load_348616 | Good Year - 210 | 2026-08-06 18:29 | 2026-08-07 07:22 | 2026-08-07 08:14 | 2026-08-07 08:15 | 2026-08-07 09:29 | 2026-08-07 09:34 | 2026-08-07 09:34 | 2026-08-07 09:34 |  |  | Fair | No | Premises found okay.
Outage | J.E.26.08.08953 | C001881358 | Floyd Taylor | Trelawny | Completed | Load_293079 | Greenwood - 210 | 2026-08-06 18:47 | 2026-08-06 18:48 | 2026-08-06 20:46 | 2026-08-06 20:47 | 2026-08-06 20:46 | 2026-08-06 20:47 | 2026-08-06 20:47 | 2026-08-06 20:47 |  |  | Fair | No | Power was restored
Outage | J.E.26.08.09121 | C001881356 | Floyd Taylor | Trelawny | Completed | Load_248423 | Greenwood - 110 | 2026-08-06 18:47 | 2026-08-06 18:48 | 2026-08-06 22:32 | 2026-08-06 22:33 | 2026-08-06 22:32 | 2026-08-06 22:33 | 2026-08-06 22:34 | 2026-08-06 22:34 |  |  | Fair | No | Customer service was restored
Outage | J.E.26.08.09264 | C001881357 | Floyd Taylor | Trelawny | Completed | Load_256332 | Greenwood - 110 | 2026-08-06 18:47 | 2026-08-06 18:48 | 2026-08-06 22:30 | 2026-08-06 22:31 | 2026-08-06 22:30 | 2026-08-06 22:31 | 2026-08-06 22:32 | 2026-08-06 22:32 |  |  | Fair | No | Customer service was restored
Outage | J.E.26.08.08796 | C001881361 | Dean- Smith | Hanover | Completed | Load_242732 | Orange Bay - 310 | 2026-08-06 18:50 | 2026-08-06 18:51 | 2026-08-06 19:15 | 2026-08-06 19:16 | 2026-08-06 20:25 | 2026-08-06 20:25 | 2026-08-06 20:53 | 2026-08-06 20:53 |  |  | Rains | No | Replace 20amp junction fuse at Jericho square. Pole number n/a
Outage | J.E.26.08.09191 | C001881360 | Dean- Smith | Hanover | Completed | Load_257564 | Orange Bay - 310 | 2026-08-06 18:50 | 2026-08-06 18:51 | 2026-08-06 19:14 | 2026-08-06 20:54 | 2026-08-06 20:54 | 2026-08-06 20:54 | 2026-08-06 20:55 | 2026-08-06 20:55 |  |  | Rains | No | Area restored
Outage | J.E.26.08.09296 | C001881359 | Dean- Smith | Hanover | Completed | Load_265980 | Orange Bay - 310 | 2026-08-06 18:50 | 2026-08-06 18:51 | 2026-08-06 20:55 | 2026-08-06 20:55 | 2026-08-06 22:34 | 2026-08-06 22:34 | 2026-08-06 22:35 | 2026-08-06 22:35 | Fire |  | Rains | No | Replace 8amp junction fuse. Pole number n/a
Outage | J.E.26.08.09360 | C001881376 | Floyd Taylor | Trelawny | Completed | Load_258421 | Greenwood - 110 | 2026-08-06 20:14 | 2026-08-06 20:16 | 2026-08-06 22:29 | 2026-08-06 22:29 | 2026-08-06 22:29 | 2026-08-06 22:29 | 2026-08-06 22:30 | 2026-08-06 22:30 |  |  | Fair | No | Customer service was restored
Outage | J.E.26.08.09360 | C001881377 | Floyd Taylor | Trelawny | Completed | Load_258421 | Greenwood - 110 | 2026-08-06 20:15 | 2026-08-06 20:16 | 2026-08-06 20:51 | 2026-08-06 20:51 | 2026-08-06 21:42 | 2026-08-06 21:43 | 2026-08-06 22:29 | 2026-08-06 22:29 |  |  | Rains | No | Reclose 80amp tripsaver and replace a 50 amp junction fuse.
Outage | J.E.26.08.09357 | C001881378 | Selvin White | St.Elizabeth | Completed | Load_262525 | Maggotty - 110 | 2026-08-06 20:21 | 2026-08-06 20:27 | 2026-08-06 21:38 | 2026-08-06 21:41 | 2026-08-06 21:52 | 2026-08-06 22:06 | 2026-08-06 22:06 | 2026-08-06 22:06 |  |  | Rains | No | Replace a defective 2 amp fuse for a 25 KVA transformer with a 1.5 amp fuse after patrolling secondary circuit. Supply restored to the affected customers.
Outage | J.E.26.08.09167 | C001881379 | Marlon Authors | Manchester | Completed | Load_250630 | Spur Tree - 210 | 2026-08-06 20:43 | 2026-08-06 20:46 | 2026-08-06 20:58 | 2026-08-06 20:58 | 2026-08-06 20:58 | 2026-08-06 21:00 | 2026-08-06 21:00 | 2026-08-06 21:00 |  |  | Fair | No | Patrol and found clear. Replace one blown 2 amp fuse that protects 10 kva transformer circuit no pole #. Restored supply ok
Outage | J.E.26.08.09410 | C001881381 | Shamour Haughton | St.James | Completed | Load_264128 | Queens Drive - 710 | 2026-08-06 20:44 | 2026-08-06 20:44 | 2026-08-06 22:03 | 2026-08-06 22:04 | 2026-08-06 22:56 | 2026-08-06 22:57 | 2026-08-06 23:08 | 2026-08-06 23:08 |  |  | Fair | No | Found 1,10amp junction fuse blown, refuse 10amp junction
Non-Outage | J.E.26.08.09510 | C001881382 | Denton Williams |  | Completed |  |  | 2026-08-06 20:55 | 2026-08-06 21:16 | 2026-08-06 22:10 | 2026-08-06 22:10 | 2026-08-06 22:12 | 2026-08-06 22:21 | 2026-08-06 22:27 | 2026-08-06 22:27 |  |  | Fair | No | Customer electrical supply was disconnected yesterday. JPS escalation was contacted and they confirmed customer electrical supply was reconnected. Customer was advised to contact a electrician.
Outage | J.E.26.08.09196 | C001881383 | Shamour Haughton | St.James | Completed | Load_248368 | Queens Drive - 310 | 2026-08-06 20:57 | 2026-08-06 20:58 | 2026-08-06 21:04 | 2026-08-06 21:05 | 2026-08-06 21:33 | 2026-08-06 21:33 | 2026-08-06 21:36 | 2026-08-06 21:36 |  |  | Fair | No | Found 1 switch bottom burn off in the main line
Outage | J.E.26.08.09508 | C001881385 | Rodclif Dawkins | KSAS | Completed | Load_302962 | Duhaney - 210 | 2026-08-06 21:05 | 2026-08-06 21:09 | 2026-08-06 21:18 | 2026-08-06 21:19 | 2026-08-06 21:32 | 2026-08-06 22:00 | 2026-08-06 22:07 | 2026-08-06 22:07 |  |  | Fair | No | At location crew found blown junction fuse from 3phase line section supplying 2 transformer circuit line section patrolled and crew observed blown fuse for 25kva transformer . Bird seen at pole foot. At junction found 15amp replaced 8amp at transformer 3amp found and replaced. Area okay
Outage | J.E.26.08.09520 | C001881386 | Rodclif Dawkins | KSAS | Completed | Load_302324 | Duhaney - 210 | 2026-08-06 21:05 | 2026-08-06 21:10 | 2026-08-06 22:08 | 2026-08-06 22:08 | 2026-08-06 22:09 | 2026-08-06 22:09 | 2026-08-06 22:09 | 2026-08-06 22:09 |  |  | Fair | No | At location crew found blown junction fuse from 3phase line section supplying 2 transformer circuit line section patrolled and crew observed blown fuse for 25kva transformer . Bird seen at pole foot. At junction found 15amp replaced 8amp at transformer 3amp found and replaced. Area okay
Outage | J.E.26.08.09507 | C001881387 | Christopher West | Portmore | Completed | Load_241385 | Naggo Head - 610 | 2026-08-06 21:06 | 2026-08-07 08:56 | 2026-08-07 11:20 | 2026-08-07 11:20 | 2026-08-07 11:29 | 2026-08-07 14:23 | 2026-08-07 14:26 | 2026-08-07 14:26 | Fire |  | Fair | No | Check made revealed a burnt drop lead connection for a 50kva transformer at pole#006055, neutral connection was corroded, transformer was de-energized, a corroded connection was also found in mid span on the lower phase, service line supplying customer had burnt connections, used 12 clamps, 4’ #2AA & 3’ #4 bare copper for repairs, transformer was re-energized, customer now okay.
Outage | J.E.26.08.09521 | C001881389 | Daniel Francis | St.Ann | Completed | Load_264609 | Ocho Rios - 310 | 2026-08-06 21:21 | 2026-08-06 21:23 | 2026-08-06 21:30 | 2026-08-06 21:31 | 2026-08-06 21:32 | 2026-08-06 18:33 | 2026-08-06 21:33 | 2026-08-06 21:33 |  |  | Fair | No | We call customer she say light come 20 minutes ago
Outage | J.E.26.08.09313 | C001881398 | Shamour Haughton | St.James | Completed | Load_252260 | Queens Drive - 810 | 2026-08-06 21:37 | 2026-08-06 21:38 | 2026-08-06 21:40 | 2026-08-06 21:41 | 2026-08-06 22:01 | 2026-08-06 22:02 | 2026-08-06 22:03 | 2026-08-06 22:03 |  |  | Fair | No | Found 1,100kva fuse blown, refuse 100kva use 1,10amp fuse
Non-Outage | J.E.26.08.09550 | C001881404 | Derrick Dawkins | St.James | Completed | Load_263655 | Bogue - 310 | 2026-08-06 21:58 | 2026-08-06 21:58 | 2026-08-06 22:42 | 2026-08-06 22:43 | 2026-08-06 22:43 | 2026-08-06 23:16 | 2026-08-06 23:17 | 2026-08-06 23:17 |  |  | Fair | No | Found 1 50kva transformer in a bank of 3 defective recommend to replace 50 kva to 100kva refer to maintenance
Outage | J.E.26.08.09559 | C001881415 | Edward Royal | KSAS | Completed | Load_245842 | Rockfort - 210 | 2026-08-06 22:43 | 2026-08-06 22:44 | 2026-08-07 01:28 | 2026-08-07 02:01 | 2026-08-07 02:00 | 2026-08-07 02:50 | 2026-08-07 02:50 | 2026-08-07 02:50 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Premises found ok
Outage | J.E.26.08.08874 | C001881421 | Horace Malcolm | St.James | Completed | Load_251119 | Queens Drive - 310 | 2026-08-06 23:15 | 2026-08-06 23:16 | 2026-08-06 23:21 | 2026-08-06 23:22 | 2026-08-06 23:47 | 2026-08-07 00:37 | 2026-08-07 00:37 | 2026-08-07 00:37 |  |  | Fair | No | Reconnect tripsaver switch bottom drop lead used one clamp
Outage | J.E.26.08.09574 | C001881426 | Edward Royal | KSAS | Completed | Load_268137 | Three Miles - 410 | 2026-08-07 00:20 | 2026-08-07 00:21 | 2026-08-07 01:28 | 2026-08-07 01:29 | 2026-08-07 01:28 | 2026-08-07 01:37 | 2026-08-07 01:38 | 2026-08-07 01:38 |  |  | Fair | No | Replaced 5A junction fuse
Outage | J.E.26.08.09630 | C001881427 | Richard Samuda | Manchester | Completed | Load_263073 | Kendal - 310 | 2026-08-07 00:23 | 2026-08-07 00:29 | 2026-08-07 00:35 | 2026-08-07 00:35 | 2026-08-07 00:38 | 2026-08-07 00:47 | 2026-08-07 00:47 | 2026-08-07 00:47 |  |  | Fair | No | Found three phase primary T pole on fire open three phase switch in front of cable and wireless on main st mandevil so fire personnel can put out fire but on able to reclosed line because cross arm on pole almost brunt off and pole top damaged refer call to maintenance pole needs to repair or replaced 30 ft c 2 pole over 25 customer affected
Outage | J.E.26.08.09235 | C001881434 | Horace Malcolm | St.James | Completed | Load_254051 | Rose Hall - 210 | 2026-08-07 01:03 | 2026-08-07 01:05 | 2026-08-07 01:25 | 2026-08-07 01:25 | 2026-08-07 01:48 | 2026-08-07 02:11 | 2026-08-07 02:12 | 2026-08-07 02:12 |  |  | Rains | No | Reset one 25kva transformer
Outage | J.E.26.08.09428 | C001881435 | Horace Malcolm | St.James | Completed | Load_245227 | Bogue - 310 | 2026-08-07 01:15 | 2026-08-07 01:16 | 2026-08-07 02:12 | 2026-08-07 02:12 | 2026-08-07 02:40 | 2026-08-07 03:50 | 2026-08-07 03:50 | 2026-08-07 03:50 | BrokenWire |  | Rains | No | Refused three 25amp junction fuse and replaced two 100kva transformer fuse used (2)10amp fuse pole number 552547
Outage | J.E.26.08.09678 | C001881442 | Richard Samuda | Manchester | Completed | Load_301951 | Spur Tree - 310 | 2026-08-07 07:11 | 2026-08-07 07:12 | 2026-08-07 07:19 | 2026-08-07 09:17 | 2026-08-07 09:45 | 2026-08-07 10:15 | 2026-08-07 10:15 | 2026-08-07 10:15 |  |  | Fair | No | Found 10 amp junction blown patrol area found palm tree branch cut and laying-on primary line use switch stick to remove branch replaced fuse close switch customer back to normal
Non-Outage | J.E.26.08.09675 | C001881443 | Omar King |  | Completed |  |  | 2026-08-07 07:12 | 2026-08-07 07:45 | 2026-08-07 07:56 | 2026-08-07 07:57 | 2026-08-07 08:22 | 2026-08-07 09:51 | 2026-08-07 09:54 | 2026-08-07 09:54 |  |  | Fair | No | Found one defective at transformer drop lead as been replaced customer is now with supply
Non-Outage | J.E.26.08.09445 | C001881445 | Omar King |  | Completed |  |  | 2026-08-07 07:13 | 2026-08-07 07:46 | 2026-08-07 09:55 | 2026-08-07 09:56 | 2026-08-07 10:31 | 2026-08-07 11:10 | 2026-08-07 11:10 | 2026-08-07 11:10 |  |  | Fair | No | Problem as been resolved
Outage | J.E.26.08.09685 | C001881446 | Derrick Grubb | St.Thomas | Completed | Load_262922 | Lysson - 410 | 2026-08-07 07:19 | 2026-08-07 07:21 | 2026-08-07 11:35 | 2026-08-07 11:36 | 2026-08-07 11:49 | 2026-08-07 11:58 | 2026-08-07 11:58 | 2026-08-07 11:58 |  |  | Fair | No | Check and found okay. Customer breaker was off.
Non-Outage | J.E.26.08.07962 | C001881447 | Hopeton Henry | St.Thomas | Completed | Load_257005 | Good Year - 110 | 2026-08-07 07:22 | 2026-08-07 08:05 | 2026-08-07 08:34 | 2026-08-07 12:43 | 2026-08-07 13:40 | 2026-08-07 14:12 | 2026-08-07 14:13 | 2026-08-07 14:13 |  |  | Fair | Yes | Found corrosion at pole 110-110-220 volts
Outage | J.E.26.08.09180 | C001881453 | Tajay Bernard | Hanover | Completed | Load_249257 | Orange Bay - 310 | 2026-08-07 07:24 | 2026-08-07 07:25 | 2026-08-07 11:27 | 2026-08-07 11:28 | 2026-08-07 11:48 | 2026-08-07 11:50 | 2026-08-07 11:50 | 2026-08-07 11:50 |  |  | Fair | No | Customer stated that power was restored
Outage | J.E.26.08.09356 | C001881452 | Tajay Bernard | Hanover | Completed | Load_262248 | Orange Bay - 310 | 2026-08-07 07:24 | 2026-08-07 07:51 | 2026-08-07 11:50 | 2026-08-07 11:51 | 2026-08-07 11:50 | 2026-08-07 11:51 | 2026-08-07 11:51 | 2026-08-07 11:51 |  |  | Fair | No | Customer stated that power was restored
Outage | J.E.26.08.09435 | C001881450 | Tajay Bernard | Hanover | Completed | Load_252846 | Orange Bay - 210 | 2026-08-07 07:24 | 2026-08-07 07:25 | 2026-08-07 11:51 | 2026-08-07 11:51 | 2026-08-07 12:18 | 2026-08-07 12:19 | 2026-08-07 12:19 | 2026-08-07 12:19 |  |  | Fair | No | Customer stated that the issue has been resolved
Outage | J.E.26.08.09629 | C001881451 | Tajay Bernard | Hanover | Completed | Load_302837 | Orange Bay - 310 | 2026-08-07 07:24 | 2026-08-07 07:25 | 2026-08-07 09:02 | 2026-08-07 09:03 | 2026-08-07 10:23 | 2026-08-07 10:43 | 2026-08-07 10:44 | 2026-08-07 10:44 |  |  | Fair | No | Refuse 1 25kva Transformer use 3amp fuse
Outage | J.E.26.08.09724 | C001881449 | Richard Samuda | Manchester | Completed | Load_260536 | Spur Tree - 210 | 2026-08-07 07:24 | 2026-08-07 07:25 | 2026-08-07 07:35 | 2026-08-07 07:36 | 2026-08-07 07:43 | 2026-08-07 09:15 | 2026-08-07 09:16 | 2026-08-07 09:16 |  |  | Fair | No | Pole number:017432 refer call defective 25kva transformer, transformer is burn needs to be replaced over 30 customers affected
Outage | J.E.26.08.08523 | C001881454 | Tajay Bernard | Hanover | Completed | Load_1001379 | Orange Bay - 310 | 2026-08-07 07:25 | 2026-08-07 07:53 | 2026-08-07 10:44 | 2026-08-07 10:45 | 2026-08-07 10:57 | 2026-08-07 11:25 | 2026-08-07 11:26 | 2026-08-07 11:26 |  |  | Fair | No | Clean and remake joint and jps pole use 1 clamps Voltage found 114Voltage left 114/116/230
Outage | J.E.26.08.09587 | C001881457 | Raheem Ricketts | Manchester | Completed | Load_247150 | Spur Tree - 210 | 2026-08-07 07:27 | 2026-08-07 07:28 | 2026-08-07 08:21 | 2026-08-07 08:22 | 2026-08-07 08:21 | 2026-08-07 08:22 | 2026-08-07 08:22 | 2026-08-07 08:22 |  |  | Fair | No | Unable to locate customer cell phone went unanswered after several calls
Outage | J.E.26.08.09716 | C001881455 | Antony Levy | KSAS | Completed | Load_237642 | Duhaney - 310 | 2026-08-07 07:27 | 2026-08-07 07:28 | 2026-08-07 07:45 | 2026-08-07 07:45 | 2026-08-07 08:25 | 2026-08-07 09:38 | 2026-08-07 09:45 | 2026-08-07 09:45 |  |  | Fair | No | Customer stated no supply line patrolled and found blown 30 amp junction fuse at pole #0083855 ....line patrolled and a arrestor bottom found leaking onto primary suspension polymer voltage from a separate phase are stored bottom shifted off of polymer.... line refused using 30amp fuse .... power restored
Non-Outage | J.E.26.08.09595 | C001881463 | Richard Samuda |  | Completed |  |  | 2026-08-07 07:29 | 2026-08-07 07:32 | 2026-08-07 14:09 | 2026-08-07 14:10 | 2026-08-07 14:29 | 2026-08-07 14:30 | 2026-08-07 14:31 | 2026-08-07 14:31 | Fire |  | Fair | No | Call to phone no answer premises not found
Outage | J.E.26.08.09563 | C001881462 | Richard Samuda | Manchester | Completed | Load_258010 | Spur Tree - 310 | 2026-08-07 07:29 | 2026-08-07 07:30 | 2026-08-07 10:21 | 2026-08-07 10:22 | 2026-08-07 10:25 | 2026-08-07 10:25 | 2026-08-07 10:26 | 2026-08-07 10:26 |  |  | Fair | No | Customer said they are a back to normal
Outage | J.E.26.08.09567 | C001881461 | Barnett Brown | Manchester | Completed | Load_238024 | Kendal - 210 | 2026-08-07 07:29 | 2026-08-07 07:30 | 2026-08-07 08:38 | 2026-08-07 08:39 | 2026-08-07 10:53 | 2026-08-07 11:20 | 2026-08-07 11:23 | 2026-08-07 11:23 |  |  | Fair | No | Isolate burnt 25 kva transformer, concentric line.
Outage | J.E.26.08.09691 | C001881469 | Christopher Edwards | KSAN | Completed | Load_263172 | Constant Spring - 410 | 2026-08-07 07:30 | 2026-08-07 07:32 | 2026-08-07 07:40 | 2026-08-07 09:27 | 2026-08-07 09:52 | 2026-08-07 11:33 | 2026-08-07 11:35 | 2026-08-07 11:35 |  |  | Fair | No | Reclose 80 amps trip saver
Outage | J.E.26.08.09699 | C001881467 | Christopher Edwards | KSAN | Completed | Load_242323 | Constant Spring - 410 | 2026-08-07 07:30 | 2026-08-07 07:32 | 2026-08-07 11:36 | 2026-08-07 11:36 | 2026-08-07 11:36 | 2026-08-07 11:36 | 2026-08-07 11:36 | 2026-08-07 11:36 |  |  | Fair | No | Related to previous call that was resolved
Outage | J.E.26.08.09700 | C001881466 | Christopher Edwards | KSAN | Completed | Load_240100 | Constant Spring - 410 | 2026-08-07 07:30 | 2026-08-07 07:32 | 2026-08-07 11:36 | 2026-08-07 11:37 | 2026-08-07 11:36 | 2026-08-07 11:37 | 2026-08-07 11:37 | 2026-08-07 11:37 |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Outage | J.E.26.08.09168 | C001881470 | Andre Williams | Trelawny | Completed | Load_238624 | Greenwood - 210 | 2026-08-07 07:31 | 2026-08-07 08:21 | 2026-08-07 09:31 | 2026-08-07 09:31 | 2026-08-07 09:31 | 2026-08-07 09:32 | 2026-08-07 09:32 | 2026-08-07 09:32 |  |  | Fair | No | Power returned to area since morning confirm by customer
Non-Outage | J.E.26.08.09561 | C001881476 | Odeanie Davis | KSAS | Completed | Load_267274 | Greenwich - 310 | 2026-08-07 07:32 | 2026-08-07 07:36 | 2026-08-07 09:25 | 2026-08-07 16:06 | 2026-08-07 16:05 | 2026-08-07 15:48 | 2026-08-07 16:06 | 2026-08-07 16:06 |  |  | Fair | No | Customer stated that issue was resolved
Outage | J.E.26.08.08791 | C001881473 | Horace Malcolm | Trelawny | Completed | Load_1001689 | Greenwood - 110 | 2026-08-07 07:32 | 2026-08-07 15:35 | 2026-08-07 19:22 | 2026-08-07 19:22 | 2026-08-07 19:56 | 2026-08-07 19:57 | 2026-08-07 19:57 | 2026-08-07 19:57 |  |  | Fair | No | Check and found ok supply restored
Outage | J.E.26.08.09273 | C001881471 | Daniel Lobar | Trelawny | Completed | Load_244451 | Duncans - 210 | 2026-08-07 07:32 | 2026-08-07 08:22 | 2026-08-07 13:50 | 2026-08-07 13:50 | 2026-08-07 14:32 | 2026-08-07 15:06 | 2026-08-07 15:10 | 2026-08-07 15:10 |  |  | Fair | No | 50kva transformer found defective at pole # 586640 at McHill Clark’s Town. There is damage to secondary bushing x1 however customers were given temporary 110v supply on x3, transformer needs to be changed. Please refer to maintenance.
Outage | J.E.26.08.09572 | C001881474 | Andre Williams | Trelawny | Completed | Load_292876 | Greenwood - 210 | 2026-08-07 07:32 | 2026-08-07 08:21 | 2026-08-07 09:32 | 2026-08-07 09:34 | 2026-08-07 09:59 | 2026-08-07 10:01 | 2026-08-07 10:05 | 2026-08-07 10:05 |  |  | Fair | No | Defective 50 kva transformer, primary bushing damage and transformer leaking oil,reffer to maintenance, use customer # for directions
Outage | J.E.26.08.09590 | C001881475 | Andre Williams | Trelawny | Completed | Load_261362 | Greenwood - 210 | 2026-08-07 07:32 | 2026-08-07 08:21 | 2026-08-07 08:32 | 2026-08-07 08:36 | 2026-08-07 09:14 | 2026-08-07 09:24 | 2026-08-07 09:29 | 2026-08-07 09:29 |  |  | Fair | No | Change defective clamp at Jps pole voltage before 37+116=153 voltage after repairs 116+118=234
Non-Outage | J.E.26.08.06722 | C001881483 | Odeanie Davis | KSAS | Completed | Load_262052 | Hunts Bay - 510 | 2026-08-07 07:33 | 2026-08-07 07:36 | 2026-08-07 10:07 | 2026-08-07 16:07 | 2026-08-07 16:07 | 2026-08-07 16:14 | 2026-08-07 16:08 | 2026-08-07 16:08 | Fire |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.06921 | C001881482 | Odeanie Davis | KSAN | Completed | Load_569029 | Washington Blvd - 710 | 2026-08-07 07:33 | 2026-08-07 07:36 | 2026-08-07 14:41 | 2026-08-07 14:42 | 2026-08-07 14:41 | 2026-08-07 14:48 | 2026-08-07 14:45 | 2026-08-07 14:45 |  |  | Fair | No | 401v across phase at location, customer states that this is too low and is causing their AC unit protection to trip, transformer team needed.
Non-Outage | J.E.26.08.07634 | C001881481 | Odeanie Davis | KSAS | Completed | Load_255433 | Three Miles - 410 | 2026-08-07 07:33 | 2026-08-07 07:36 | 2026-08-07 11:04 | 2026-08-07 11:04 | 2026-08-07 11:04 | 2026-08-07 11:10 | 2026-08-07 11:11 | 2026-08-07 11:11 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.07676 | C001881479 | Odeanie Davis | KSAS | Completed | Load_258271 | Three Miles - 410 | 2026-08-07 07:33 | 2026-08-07 07:36 | 2026-08-07 10:47 | 2026-08-07 16:06 | 2026-08-07 16:06 | 2026-08-07 15:59 | 2026-08-07 16:07 | 2026-08-07 16:07 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.07852 | C001881480 | Odeanie Davis | KSAS | Completed | Load_247103 | Greenwich - 310 | 2026-08-07 07:33 | 2026-08-07 07:36 | 2026-08-07 09:42 | 2026-08-07 09:43 | 2026-08-07 09:42 | 2026-08-07 10:04 | 2026-08-07 10:04 | 2026-08-07 10:04 |  |  | Fair | No | 120v/119v & 239v in meter socket, no power issues found on jps end
Non-Outage | J.E.26.08.08963 | C001881478 | Odeanie Davis | KSAS | Completed | Load_250548 | Three Miles - 410 | 2026-08-07 07:33 | 2026-08-07 07:36 | 2026-08-07 11:39 | 2026-08-07 11:39 | 2026-08-07 11:39 | 2026-08-07 12:35 | 2026-08-07 12:37 | 2026-08-07 12:37 |  |  | Fair | No | 108v/119 at arrival, open neutral o customer’s line corrected, 2 penn union & 1 one bolt clamp, 112v/118v & 230v after correction
Non-Outage | J.E.26.08.05282 | C001881495 | Odeanie Davis | KSAN | Completed | Load_249011 | Washington Blvd - 310 | 2026-08-07 07:34 | 2026-08-07 07:36 | 2026-08-07 13:21 | 2026-08-07 13:22 | 2026-08-07 13:23 | 2026-08-07 14:08 | 2026-08-07 14:08 | 2026-08-07 14:08 |  |  | Fair | No | 116v/0V at arrival, open circuit at pothead and secondary corrected, 3 penn union & 2 one bolt clamps, 114v/106v after correction.
Non-Outage | J.E.26.08.05293 | C001881494 | Odeanie Davis | KSAS | Completed | Load_255919 | Hunts Bay - 310 | 2026-08-07 07:34 | 2026-08-07 07:36 | 2026-08-07 10:43 | 2026-08-07 16:10 | 2026-08-07 16:09 | 2026-08-07 16:54 | 2026-08-07 16:10 | 2026-08-07 16:10 |  |  | Fair | No
Non-Outage | J.E.26.08.05420 | C001881496 | Odeanie Davis | KSAS | Completed | Load_263810 | Greenwich - 710 | 2026-08-07 07:34 | 2026-08-07 07:36 | 2026-08-07 16:10 | 2026-08-07 16:11 | 2026-08-07 16:10 | 2026-08-07 17:00 | 2026-08-07 16:14 | 2026-08-07 16:14 |  |  | Fair | No | 116v/0V at location from rammi box, meter not communicating, customer is left with partial supply, meter needs to be change. Rammi team needed
Non-Outage | J.E.26.08.05692 | C001881493 | Odeanie Davis | KSAS | Completed | Load_250009 | Hunts Bay - 310 | 2026-08-07 07:34 | 2026-08-07 07:36 | 2026-08-07 10:39 | 2026-08-07 16:09 | 2026-08-07 16:09 | 2026-08-07 16:41 | 2026-08-07 16:09 | 2026-08-07 16:09 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.05711 | C001881492 | Odeanie Davis | KSAS | Completed | Load_243267 | Hunts Bay - 310 | 2026-08-07 07:34 | 2026-08-07 07:36 | 2026-08-07 10:36 | 2026-08-07 16:08 | 2026-08-07 16:08 | 2026-08-07 16:30 | 2026-08-07 16:08 | 2026-08-07 16:08 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.05908 | C001881491 | Odeanie Davis | KSAN | Completed | Load_265054 | Washington Blvd - 710 | 2026-08-07 07:34 | 2026-08-07 07:36 | 2026-08-07 14:12 | 2026-08-07 14:12 | 2026-08-07 14:24 | 2026-08-07 14:31 | 2026-08-07 14:29 | 2026-08-07 14:29 |  |  | Fair | No
Non-Outage | J.E.26.08.06296 | C001881489 | Odeanie Davis | KSAS | Completed | Load_265991 | Greenwich - 710 | 2026-08-07 07:34 | 2026-08-07 07:36 | 2026-08-07 10:13 | 2026-08-07 10:13 | 2026-08-07 10:17 | 2026-08-07 10:32 | 2026-08-07 10:32 | 2026-08-07 10:32 |  |  | Fair | No | Defective wire at pothead, stanchion where twisted is defective, customer was advised to contact their electrician
Non-Outage | J.E.26.08.06344 | C001881490 | Odeanie Davis | KSAN | Completed | Load_247699 | Washington Blvd - 310 | 2026-08-07 07:34 | 2026-08-07 07:36 | 2026-08-07 14:47 | 2026-08-07 14:48 | 2026-08-07 15:05 | 2026-08-07 15:33 | 2026-08-07 16:05 | 2026-08-07 16:05 |  |  | Fair | No | 88v/89v at location, customer has over 200ft of defective twisted wire wire several joints, customer was advised to contact their electrician to re-run wire to meet the 100ft of twisted wire that is allotted from jps,
Non-Outage | J.E.26.08.08209 | C001881497 | Odeanie Davis | KSAS | Completed | Load_259963 | Three Miles - 410 | 2026-08-07 07:35 | 2026-08-07 07:38 | 2026-08-07 11:16 | 2026-08-07 11:17 | 2026-08-07 11:16 | 2026-08-07 11:18 | 2026-08-07 11:18 | 2026-08-07 11:18 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.09289 | C001881498 | Rusean Allen |  | Completed |  |  | 2026-08-07 07:36 | 2026-08-07 07:39 | 2026-08-07 11:46 | 2026-08-07 11:46 | 2026-08-07 11:48 | 2026-08-07 11:48 | 2026-08-07 11:48 | 2026-08-07 11:48 |  |  | Fair | No | More information needed
Non-Outage | J.E.26.08.09732 | C001881500 | Rusean Allen | KSAS | Completed | Load_244455 | Cane River - 610 | 2026-08-07 07:36 | 2026-08-07 07:39 | 2026-08-07 22:09 | 2026-08-07 22:10 | 2026-08-07 22:14 | 2026-08-07 22:14 | 2026-08-07 22:15 | 2026-08-07 22:15 |  |  | Fair | No | Phone what unanswered
Outage | J.E.26.08.09692 | C001881499 | Rusean Allen | KSAS | Completed | Load_245842 | Rockfort - 210 | 2026-08-07 07:36 | 2026-08-07 07:40 | 2026-08-07 11:29 | 2026-08-07 12:04 | 2026-08-07 12:18 | 2026-08-07 12:21 | 2026-08-07 12:21 | 2026-08-07 12:21 | BrokenWire |  | Fair | No | Reconnected wire at pole
Non-Outage | J.E.26.08.07594 | C001881506 | Rusean Allen |  | Completed |  |  | 2026-08-07 07:37 | 2026-08-07 07:39 | 2026-08-07 14:15 | 2026-08-07 14:15 | 2026-08-07 14:21 | 2026-08-07 14:21 | 2026-08-07 14:21 | 2026-08-07 14:21 | BrokenWire |  | Fair | No | Not found
Non-Outage | J.E.26.08.07783 | C001881507 | Rusean Allen | KSAS | Completed | Load_1002665 | Cane River - 410 | 2026-08-07 07:37 | 2026-08-07 07:39 | 2026-08-07 11:27 | 2026-08-07 11:29 | 2026-08-07 11:45 | 2026-08-07 11:45 | 2026-08-07 11:45 | 2026-08-07 11:45 | LowHangingWires |  | Fair | No | Found okay
Non-Outage | J.E.26.08.07873 | C001881504 | Rusean Allen |  | Completed |  |  | 2026-08-07 07:37 | 2026-08-07 07:39 | 2026-08-07 22:09 | 2026-08-07 22:09 | 2026-08-07 22:09 | 2026-08-07 22:09 | 2026-08-07 22:09 | 2026-08-07 22:09 | LeakingTransformer |  | Fair | No | Not found
Non-Outage | J.E.26.08.09053 | C001881503 | Milton Charlton | KSAN | Completed | Load_260652 | Hope - 510 | 2026-08-07 07:37 | 2026-08-07 07:39 | 2026-08-07 09:43 | 2026-08-07 09:53 | 2026-08-07 10:16 | 2026-08-07 11:30 | 2026-08-07 11:48 | 2026-08-07 11:48 |  |  | Fair | No | Found one 2amps transformer fuse blown at pole #604852. Refused using one 2 amps fuse and reclosed transformer switch
Non-Outage | J.E.26.08.09204 | C001881502 | Milton Charlton | KSAN | Completed | Load_578924 | Hope - 510 | 2026-08-07 07:37 | 2026-08-07 07:39 | 2026-08-07 09:30 | 2026-08-07 09:30 | 2026-08-07 09:40 | 2026-08-07 09:40 | 2026-08-07 09:42 | 2026-08-07 09:42 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.09482 | C001881505 | Milton Charlton | KSAN | Completed | Load_266807 | Hope - 410 | 2026-08-07 07:37 | 2026-08-07 07:39 | 2026-08-07 11:48 | 2026-08-07 11:49 | 2026-08-07 13:15 | 2026-08-07 13:15 | 2026-08-07 13:16 | 2026-08-07 13:16 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Non-Outage | J.E.26.08.09624 | C001881522 | Tajay Bernard |  | Completed |  |  | 2026-08-07 07:50 | 2026-08-07 07:51 | 2026-08-07 08:53 | 2026-08-07 08:53 | 2026-08-07 08:53 | 2026-08-07 08:53 | 2026-08-07 08:53 | 2026-08-07 08:53 |  |  | Fair | No | This call belongs to st James
Outage | J.E.26.08.09165 | C001881524 | Gregory Grossett | Portland | Completed | Load_349777 | Port Antonio - 410 | 2026-08-07 07:50 | 2026-08-07 07:53 | 2026-08-07 07:55 | 2026-08-07 07:56 | 2026-08-07 08:21 | 2026-08-07 08:22 | 2026-08-07 08:23 | 2026-08-07 08:23 |  |  | Fair | No | After making several calls we could not reach out to the customer.
Outage | J.E.26.08.09175 | C001881523 | Tajay Bernard | Hanover | Completed | Load_238936 | Orange Bay - 310 | 2026-08-07 07:50 | 2026-08-07 07:51 | 2026-08-07 08:54 | 2026-08-07 08:54 | 2026-08-07 09:01 | 2026-08-07 09:01 | 2026-08-07 09:01 | 2026-08-07 09:01 |  |  | Fair | No | Customer stated that power was restored
Outage | J.E.26.08.09726 | C001881525 | Evan Spaulding | St.Mary | Completed | Load_239639 | Highgate -110 | 2026-08-07 07:53 | 2026-08-07 07:56 | 2026-08-07 08:18 | 2026-08-07 08:19 | 2026-08-07 08:26 | 2026-08-07 08:26 | 2026-08-07 08:27 | 2026-08-07 08:27 |  |  | Fair | No | Customer says power was restored last night.
Outage | J.E.26.08.09752 | C001881526 | Derrick Grubb | St.Thomas | Completed | Load_248385 | Lysson - 410 | 2026-08-07 07:53 | 2026-08-07 07:58 | 2026-08-07 09:36 | 2026-08-07 09:36 | 2026-08-07 11:09 | 2026-08-07 11:24 | 2026-08-07 11:24 | 2026-08-07 11:24 |  |  | Fair | No | Troubleshoot and found one 15kva hexin transformer defective. Also transformer pole leaning. Please refer to maintenance and field service technician teams. Two customers affected.
Non-Outage | J.E.26.08.09517 | C001881535 | Gregory Grossett | Portland | Completed | Load_261986 | Port Antonio - 310 | 2026-08-07 07:57 | 2026-08-07 09:32 | 2026-08-07 09:36 | 2026-08-07 09:37 | 2026-08-07 10:56 | 2026-08-07 11:02 | 2026-08-07 11:02 | 2026-08-07 11:02 |  |  | Fair | No | 25kva transformer drop leads corroded and 2/0 triplex conductor oxidized open transformer fuse to make repairs then close transformer fuse to restore normal supply to the area.Material use 15 one bolt clamps 5ft of 2/0 conductor.
Non-Outage | J.E.26.08.09745 | C001881534 | Gregory Grossett | Portland | Completed | Load_270184 | Port Antonio - 410 | 2026-08-07 07:57 | 2026-08-08 08:51 | 2026-08-08 08:55 | 2026-08-08 08:55 | 2026-08-08 09:51 | 2026-08-08 10:48 | 2026-08-08 10:48 | 2026-08-08 10:48 |  |  | Fair | No | 25kva transformer casing ground and neutral clamp corroded open transformer fuse link to make repairs then close fuse link to restore normal supply to the area.Material use 4 one bolt clamps voltage readings 116/115/231 on both phase.
Non-Outage | J.E.26.08.09481 | C001881537 | Andrae Clarke | Portland | Completed | Load_261986 | Port Antonio - 310 | 2026-08-07 07:58 | 2026-08-07 08:21 | 2026-08-07 11:32 | 2026-08-07 11:32 | 2026-08-07 11:32 | 2026-08-07 11:10 | 2026-08-07 11:33 | 2026-08-07 11:33 |  |  | Fair | No | Check premises Premises found okay Check voltage 119/117/236
Non-Outage | J.E.26.08.08601 | C001881541 | Royston Montague | St.Catherine | Completed | Load_243457 | Tredegar - 310 | 2026-08-07 08:00 | 2026-08-07 08:02 | 2026-08-07 08:23 | 2026-08-07 15:27 | 2026-08-07 16:12 | 2026-08-07 16:13 | 2026-08-07 16:14 | 2026-08-07 16:14 |  |  | Fair | No | Faulty neutral joint at pothead. Same corrected. Voltage found 230v 127v 103v voltage after job completion are 230v 115v 113v
Non-Outage | J.E.26.08.08611 | C001881540 | Royston Montague | St.Catherine | Completed | Load_270057 | Tredegar - 210 | 2026-08-07 08:00 | 2026-08-07 08:02 | 2026-08-07 08:23 | 2026-08-07 11:34 | 2026-08-07 13:44 | 2026-08-07 14:24 | 2026-08-07 14:24 | 2026-08-07 14:24 |  |  | Fair | No | Faulty neutral joint at customer take off point. Same corrected. Voltage found 224v 124v 100v. Voltage after job completion are 224v 109v 111v
Non-Outage | J.E.26.08.09387 | C001881538 | Royston Montague | St.Catherine | Completed | Load_257339 | Tredegar - 310 | 2026-08-07 08:00 | 2026-08-07 08:02 | 2026-08-07 08:23 | 2026-08-07 14:25 | 2026-08-07 15:25 | 2026-08-07 15:26 | 2026-08-07 15:26 | 2026-08-07 15:26 |  |  | Fair | No | Slack joints at pothead. Same corrected voltage found 110v voltage after 116v
Non-Outage | J.E.26.08.07720 | C001881545 | Royston Montague | St.Catherine | Completed | Load_1000349 | Tredegar - 210 | 2026-08-07 08:01 | 2026-08-07 08:02 | 2026-08-07 08:23 | 2026-08-07 10:43 | 2026-08-07 11:32 | 2026-08-07 11:33 | 2026-08-07 11:33 | 2026-08-07 11:33 |  |  | Fair | No | Burn wire in meter socket. Customer informed to get an electrician to repair same . Voltage 228v 114v 113v
Non-Outage | J.E.26.08.07834 | C001881543 | Royston Montague | St.Catherine | Completed | Load_251765 | Tredegar - 510 | 2026-08-07 08:01 | 2026-08-07 08:02 | 2026-08-07 08:23 | 2026-08-07 16:14 | 2026-08-07 18:38 | 2026-08-07 18:40 | 2026-08-07 18:40 | 2026-08-07 18:40 |  |  | Fair | No | Open phase at customer take off point. Same corrected. Voltage found 111v voltage after job completion are 229v 114v 114v
Non-Outage | J.E.26.08.09698 | C001881546 | Richman Whyte |  | Completed |  |  | 2026-08-07 08:02 | 2026-08-07 08:03 | 2026-08-07 08:08 | 2026-08-07 08:08 | 2026-08-07 09:51 | 2026-08-07 10:05 | 2026-08-07 10:06 | 2026-08-07 10:06 |  |  | Fair | No | Replace two amp twenty five kva transformer fuse voltage 115 113 230
Non-Outage | J.E.26.08.06851 | C001881551 | Hopeton Henry | St.Thomas | Completed | Load_257871 | Good Year - 110 | 2026-08-07 08:04 | 2026-08-07 08:05 | 2026-08-07 08:34 | 2026-08-07 14:14 | 2026-08-07 15:16 | 2026-08-07 15:16 | 2026-08-07 15:18 | 2026-08-07 15:18 |  |  | Fair | No | Reconnect service at pole use 5 connector 114-115-230
Non-Outage | J.E.26.06.19767 | C001881552 | Derrick Grubb | St.Thomas | Completed | Load_264991 | Good Year - 110 | 2026-08-07 08:05 | 2026-08-07 08:06 | 2026-08-07 12:15 | 2026-08-07 12:16 | 2026-08-07 14:10 | 2026-08-07 14:11 | 2026-08-07 14:11 | 2026-08-07 14:11 |  |  | Fair | No | Premises not found. Several calls to customer phone went unanswered.
Non-Outage | J.E.26.08.04313 | C001881555 | Fredrick Hamilton | KSAN | Completed | Load_257446 | Constant Spring - 210 | 2026-08-07 08:05 | 2026-08-07 08:07 | 2026-08-07 08:17 | 2026-08-07 11:32 | 2026-08-07 11:36 | 2026-08-07 11:39 | 2026-08-07 11:39 | 2026-08-07 11:39 |  |  | Fair | No | Premises found locked at time of visit Calls to customer went straight to voicemail
Non-Outage | J.E.26.08.07814 | C001881554 | Fredrick Hamilton | KSAN | Completed | Load_256846 | Constant Spring - 210 | 2026-08-07 08:05 | 2026-08-07 08:07 | 2026-08-07 08:17 | 2026-08-07 11:59 | 2026-08-07 12:23 | 2026-08-07 12:33 | 2026-08-07 12:33 | 2026-08-07 12:33 |  |  | Fair | No | Pole #1080925 Customer experiencing single phase Hexing meter at location Pothead checked and found ok Service wire found ok Please assign to emergency
Non-Outage | J.E.26.08.08785 | C001881553 | Fredrick Hamilton | KSAN | Completed | Load_261829 | Washington Blvd - 810 | 2026-08-07 08:05 | 2026-08-07 08:07 | 2026-08-07 08:17 | 2026-08-07 10:22 | 2026-08-07 10:42 | 2026-08-07 11:26 | 2026-08-07 11:26 | 2026-08-07 11:26 |  |  | Fair | No | Burnt wires detected at pole same was corrected 2 clamps usedPremises is no ok
Non-Outage | J.E.26.07.35990 | C001881558 | Fredrick Hamilton | KSAN | Completed | Load_263454 | Washington Blvd - 610 | 2026-08-07 08:06 | 2026-08-07 08:07 | 2026-08-07 08:17 | 2026-08-07 08:39 | 2026-08-07 08:38 | 2026-08-07 08:42 | 2026-08-07 08:42 | 2026-08-07 08:42 |  |  | Fair | No | Customer contacted and stated that power was restored fully previously Premises is ok
Non-Outage | J.E.26.08.01436 | C001881556 | Fredrick Hamilton |  | Completed |  |  | 2026-08-07 08:06 | 2026-08-07 08:07 | 2026-08-07 08:17 | 2026-08-07 08:27 | 2026-08-07 08:27 | 2026-08-07 08:35 | 2026-08-07 08:35 | 2026-08-07 08:35 |  |  | Fair | No | Customer contacted and stated that premises is inaccessible customer Stated that issue is at pothead Customer advised to make another report when access can be granted
Non-Outage | J.E.26.08.04071 | C001881557 | Fredrick Hamilton | KSAN | Completed | Load_250523 | Constant Spring - 210 | 2026-08-07 08:06 | 2026-08-07 08:07 | 2026-08-07 08:17 | 2026-08-07 11:39 | 2026-08-07 11:41 | 2026-08-07 11:49 | 2026-08-07 11:49 | 2026-08-07 11:49 |  |  | Fair | No | Premises found ok at time of inspection power was restored fully previously 236v/118v/117v obtained
Non-Outage | J.E.26.08.09751 | C001881559 | Roemello Brown | Trelawny | Completed | Load_1001503 | Duncans - 110 | 2026-08-07 08:06 | 2026-08-07 08:08 | 2026-08-07 11:27 | 2026-08-07 12:21 | 2026-08-07 12:20 | 2026-08-07 12:36 | 2026-08-07 12:44 | 2026-08-07 12:44 |  |  | Fair | No | Customer meter burnt needs field service team to have meter change Voltage found 119/120/239Voltage leave 119/120/239
Non-Outage | J.E.26.08.07885 | C001881563 | Daniel Lobar | Trelawny | Completed | Load_268209 | Martha Brae - 210 | 2026-08-07 08:07 | 2026-08-07 08:17 | 2026-08-07 09:11 | 2026-08-07 09:11 | 2026-08-07 09:20 | 2026-08-07 10:53 | 2026-08-07 10:54 | 2026-08-07 10:54 | LowHangingWires |  | Fair | No | Remove, splice and retention 2 #6 service wires
Non-Outage | J.E.26.08.07926 | C001881564 | Roemello Brown | Trelawny | Completed | Load_239199 | Duncans - 210 | 2026-08-07 08:07 | 2026-08-07 08:08 | 2026-08-07 11:00 | 2026-08-07 11:00 | 2026-08-07 11:27 | 2026-08-07 11:27 | 2026-08-07 12:00 | 2026-08-07 12:00 |  |  | Fair | No | Corrosion at pole side have clamps change Voltage found 93 volts Voltage leave 117
Non-Outage | J.E.26.08.08841 | C001881560 | Roemello Brown | Trelawny | Completed | Load_291989 | Duncans - 210 | 2026-08-07 08:07 | 2026-08-07 08:08 | 2026-08-07 10:29 | 2026-08-07 10:29 | 2026-08-07 10:47 | 2026-08-07 10:47 | 2026-08-07 10:55 | 2026-08-07 10:55 |  |  | Fair | No | Transformer drop lead burn off needs emergency team to assist please Voltage found 118/29/147Voltage leave 118/29/147
Non-Outage | J.E.26.08.09143 | C001881562 | Roemello Brown | Trelawny | Completed | Load_261362 | Greenwood - 210 | 2026-08-07 08:07 | 2026-08-07 08:08 | 2026-08-07 12:35 | 2026-08-07 12:44 | 2026-08-07 14:44 | 2026-08-07 14:44 | 2026-08-07 14:49 | 2026-08-07 14:49 |  |  | Fair | No | Premises found working ok Voltage found 118/118/236Voltage leave 118/118/236
Non-Outage | J.E.26.08.09239 | C001881561 | Roemello Brown | Trelawny | Completed | Load_246807 | Duncans - 210 | 2026-08-07 08:07 | 2026-08-07 08:08 | 2026-08-07 09:31 | 2026-08-07 10:07 | 2026-08-07 10:19 | 2026-08-07 10:26 | 2026-08-07 10:29 | 2026-08-07 10:29 |  |  | Fair | No | Transformer drop lead burn off needs emergency team to assist Voltage found 118/29Voltage leave 118/29
Non-Outage | J.E.26.07.12067 | C001881571 | Oraine Minto | St.Ann | Completed | Load_258154 | Roaring River - 410 | 2026-08-07 08:11 | 2026-08-07 08:14 | 2026-08-07 16:12 | 2026-08-07 16:13 | 2026-08-07 16:12 | 2026-08-07 16:13 | 2026-08-07 16:13 | 2026-08-07 16:13 |  |  | Fair | No | Issue was resolved
Non-Outage | J.E.26.07.13250 | C001881572 | Oraine Minto | St.Ann | Completed | Load_256871 | Roaring River - 210 | 2026-08-07 08:11 | 2026-08-07 08:14 | 2026-08-07 16:05 | 2026-08-07 16:05 | 2026-08-07 16:05 | 2026-08-07 16:05 | 2026-08-07 16:05 | 2026-08-07 16:05 |  |  | Fair | No | Issue resolved
Non-Outage | J.E.26.07.13250 | C001881574 | Oraine Minto | St.Ann | Completed | Load_256871 | Roaring River - 210 | 2026-08-07 08:11 | 2026-08-07 08:14 | 2026-08-07 16:06 | 2026-08-07 16:06 | 2026-08-07 16:06 | 2026-08-07 16:06 | 2026-08-07 16:06 | 2026-08-07 16:06 |  |  | Fair | No | Issue was resolved
Non-Outage | J.E.26.07.18632 | C001881576 | Oraine Minto | St.Ann | Completed | Load_248565 | Roaring River - 410 | 2026-08-07 08:12 | 2026-08-07 08:14 | 2026-08-07 16:02 | 2026-08-07 16:02 | 2026-08-07 16:02 | 2026-08-07 16:03 | 2026-08-07 16:03 | 2026-08-07 16:03 |  |  | Fair | No | Unable to reach customer number doesn’t work
Non-Outage | J.E.26.07.33593 | C001881584 | Tyrese Williams | St.Ann | Completed | Load_556003 | Roaring River - 410 | 2026-08-07 08:17 | 2026-08-07 15:45 | 2026-08-07 16:14 | 2026-08-07 16:45 | 2026-08-07 16:45 | 2026-08-07 16:50 | 2026-08-07 16:50 | 2026-08-07 16:50 |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.08.09248 | C001881591 | Orville Lee | Portmore | Completed | Load_557221 | Naggo Head - 610 | 2026-08-07 08:19 | 2026-08-07 08:19 | 2026-08-07 08:55 | 2026-08-07 08:56 | 2026-08-07 09:37 | 2026-08-07 10:07 | 2026-08-07 10:08 | 2026-08-07 10:08 |  |  | Fair | No | Pothead connection found corroded 3 Penn union used Voltage 118V119V237V
Outage | J.E.26.08.09761 | C001881593 | Antony Levy | KSAS | Completed | Load_244693 | Duhaney - 310 | 2026-08-07 08:19 | 2026-08-07 08:22 | 2026-08-07 09:46 | 2026-08-07 09:46 | 2026-08-07 09:47 | 2026-08-07 09:50 | 2026-08-07 09:50 | 2026-08-07 09:50 |  |  | Fair | No
Non-Outage | J.E.26.08.00607 | C001881599 | Odaine Johnson | Clarendon | Completed | Load_263789 | Parnassus - 210 | 2026-08-07 08:20 | 2026-08-07 08:22 | 2026-08-07 12:43 | 2026-08-07 13:38 | 2026-08-07 14:01 | 2026-08-07 14:01 | 2026-08-07 14:01 | 2026-08-07 14:01 |  |  | Fair | No | Emergency team need
Non-Outage | J.E.26.08.03780 | C001881601 | Odaine Johnson | Clarendon | Completed | Load_269281 | Monymusk - 210 | 2026-08-07 08:20 | 2026-08-07 08:22 | 2026-08-07 11:20 | 2026-08-07 11:21 | 2026-08-07 11:26 | 2026-08-07 11:26 | 2026-08-07 11:26 | 2026-08-07 11:26 |  |  | Fair | No | Customer stated that the issue was resolved
Non-Outage | J.E.26.08.08006 | C001881598 | Odaine Johnson | Clarendon | Completed | Load_405463 | Parnassus - 310 | 2026-08-07 08:20 | 2026-08-07 08:22 | 2026-08-07 12:26 | 2026-08-07 13:34 | 2026-08-07 13:37 | 2026-08-07 13:37 | 2026-08-07 13:37 | 2026-08-07 13:37 |  |  | Fair | No | Premises found okay customer stated the issue was resolved
Non-Outage | J.E.26.08.08109 | C001881597 | Odaine Johnson | Clarendon | Completed | Load_246748 | Parnassus - 210 | 2026-08-07 08:20 | 2026-08-07 08:22 | 2026-08-07 10:27 | 2026-08-07 10:28 | 2026-08-07 10:40 | 2026-08-07 10:41 | 2026-08-07 10:42 | 2026-08-07 10:42 |  |  | Fair | No | Meter burn allowing customer to be experiencing single phase voltage reading 114/113/228 volts customer receiving 113 volts only
Non-Outage | J.E.26.08.09552 | C001881594 | Odaine Johnson | Clarendon | Completed | Load_241776 | Monymusk - 210 | 2026-08-07 08:20 | 2026-08-07 08:22 | 2026-08-07 11:24 | 2026-08-07 11:27 | 2026-08-07 11:42 | 2026-08-07 11:51 | 2026-08-07 11:52 | 2026-08-07 11:52 |  |  | Fair | No | Premises found okay voltage reading 110/108/219
Outage | J.E.26.08.09373 | C001881595 | Andre Smith | KSAS | Completed | Load_240238 | Duhaney - 410 | 2026-08-07 08:20 | 2026-08-07 08:36 | 2026-08-07 09:15 | 2026-08-07 09:16 | 2026-08-07 09:42 | 2026-08-07 09:42 | 2026-08-07 09:42 | 2026-08-07 09:42 |  |  | Fair | No | Premises found okay supply restored already
Non-Outage | J.E.26.07.39560 | C001881604 | Odaine Johnson | Clarendon | Completed | Load_252773 | Monymusk - 410 | 2026-08-07 08:21 | 2026-08-07 08:22 | 2026-08-07 12:23 | 2026-08-07 12:26 | 2026-08-07 12:41 | 2026-08-07 12:41 | 2026-08-07 12:42 | 2026-08-07 12:42 |  |  | Fair | No | Customer stated that the issue was resolved already resolved
Non-Outage | J.E.26.07.39731 | C001881605 | Odaine Johnson | Clarendon | Completed | Load_259584 | Parnassus - 310 | 2026-08-07 08:21 | 2026-08-07 08:22 | 2026-08-07 12:18 | 2026-08-07 12:18 | 2026-08-07 12:22 | 2026-08-07 12:22 | 2026-08-07 12:23 | 2026-08-07 12:23 |  |  | Fair | No | Premises was found working ok Voltage Reading is A115 B114 AB229
Non-Outage | J.E.26.07.39802 | C001881602 | Odaine Johnson | Clarendon | Completed | Load_269857 | Parnassus - 310 | 2026-08-07 08:21 | 2026-08-07 08:22 | 2026-08-07 11:54 | 2026-08-07 11:56 | 2026-08-07 12:15 | 2026-08-07 12:16 | 2026-08-07 12:17 | 2026-08-07 12:17 |  |  | Fair | No | Try contact customer but no one answer and follow direction given and still did not find location
Non-Outage | J.E.26.07.39861 | C001881603 | Odaine Johnson | Clarendon | Completed | Load_301185 | Monymusk - 210 | 2026-08-07 08:21 | 2026-08-07 08:22 | 2026-08-07 12:23 | 2026-08-07 12:42 | 2026-08-07 12:43 | 2026-08-07 12:43 | 2026-08-07 12:43 | 2026-08-07 12:43 |  |  | Fair | No | Customer stated that the issue was resolved
Non-Outage | J.E.26.08.08572 | C001881606 | Hartley Chin | Clarendon | Completed | Load_254560 | Parnassus - 310 | 2026-08-07 08:22 | 2026-08-07 08:24 | 2026-08-07 08:33 | 2026-08-07 08:34 | 2026-08-07 09:34 | 2026-08-07 10:38 | 2026-08-07 10:40 | 2026-08-07 10:40 |  |  | Fair | No | Reading 117v 67v found corrosion on one leg change clamps then read 117v 115v 231v
Non-Outage | J.E.26.08.09157 | C001881608 | Clyde Brown | Clarendon | Completed | Load_350768 | May Pen - 110 | 2026-08-07 08:22 | 2026-08-07 10:13 | 2026-08-07 11:41 | 2026-08-07 11:41 | 2026-08-07 11:41 | 2026-08-07 11:42 | 2026-08-07 11:45 | 2026-08-07 11:45 |  |  | Fair | No | Found ok,customer said supply was restored
Non-Outage | J.E.26.08.09326 | C001881609 | Clyde Brown | Clarendon | Completed | Load_241943 | May Pen - 110 | 2026-08-07 08:22 | 2026-08-07 08:24 | 2026-08-07 10:13 | 2026-08-07 10:14 | 2026-08-07 10:14 | 2026-08-07 10:10 | 2026-08-07 10:20 | 2026-08-07 10:20 | LowHangingWires |  | Fair | No | Low service line caused by truck customer advise to get stantion fix,before wire can be retention.
Non-Outage | J.E.26.08.09543 | C001881610 | Hartley Chin | Clarendon | Completed | Load_249064 | May Pen - 110 | 2026-08-07 08:22 | 2026-08-08 07:52 | 2026-08-08 08:14 | 2026-08-08 08:15 | 2026-08-08 08:14 | 2026-08-08 08:21 | 2026-08-08 08:22 | 2026-08-08 08:22 |  |  | Fair | No | Wrong parish st. Ann call
Outage | J.E.26.08.06071 | C001881607 | Rusean Allen | KSAS | Completed | Load_268672 | Rockfort - 410 | 2026-08-07 08:22 | 2026-08-07 08:24 | 2026-08-07 12:41 | 2026-08-07 12:42 | 2026-08-07 13:10 | 2026-08-07 13:15 | 2026-08-07 13:16 | 2026-08-07 13:16 |  |  | Fair | No | Corroded clamp found at pothead, clamps were changed.Voltage: 118v
Non-Outage | J.E.26.08.07699 | C001881611 | Andrae Clarke | Portland | Completed | Load_244330 | Port Antonio - 310 | 2026-08-07 08:23 | 2026-08-07 08:24 | 2026-08-07 08:35 | 2026-08-07 11:35 | 2026-08-07 11:43 | 2026-08-07 11:44 | 2026-08-07 11:44 | 2026-08-07 11:44 |  |  | Fair | No | Premises found okay
Non-Outage | J.E.26.08.09667 | C001881618 | Swon Miller |  | Completed |  |  | 2026-08-07 08:24 | 2026-08-07 08:26 | 2026-08-07 08:30 | 2026-08-07 08:45 | 2026-08-07 08:59 | 2026-08-27 01:18 | 2026-08-07 13:22 | 2026-08-07 13:22 |  |  | Fair | No | Found cross arm with 3 phase primary dislodged from pole 1,80 amp junction fuse blown 100 kva transformer switch bottom lead burnt off fuse blown open 2,80 amp junction fuse to carry out repairs recenter cross bracket and repair 100 kva switch bottom lead and close all 3,80 junction fuse at pole number lab6-648
Non-Outage | J.E.26.07.08774 | C001881626 | Locksley Allen | St.Mary | Completed | Load_248567 | Highgate -110 | 2026-08-07 08:25 | 2026-08-07 08:27 | 2026-08-07 09:49 | 2026-08-07 10:42 | 2026-08-07 10:41 | 2026-08-07 10:47 | 2026-08-07 10:44 | 2026-08-07 10:44 | LeaningPole |  | Fair | No | No problem found at the premises. Voltage at meter socket phase to phase 226v. Phase to neutral 113&114v. Meter left working okay
Non-Outage | J.E.26.07.11647 | C001881625 | Locksley Allen |  | Completed |  |  | 2026-08-07 08:25 | 2026-08-07 08:29 | 2026-08-07 10:45 | 2026-08-07 11:14 | 2026-08-07 11:13 | 2026-08-07 11:20 | 2026-08-07 11:18 | 2026-08-07 11:18 | LeaningPole |  | Fair | No | JPS pole is lean and needs a Guy wire. Please refer to maintainance
Non-Outage | J.E.26.07.23711 | C001881628 | Locksley Allen |  | Completed |  |  | 2026-08-07 08:25 | 2026-08-07 08:29 | 2026-08-07 11:36 | 2026-08-07 11:36 | 2026-08-07 11:36 | 2026-08-07 11:40 | 2026-08-07 11:37 | 2026-08-07 11:37 | LeaningPole |  | Fair | No | Need better direction
Outage | J.E.26.08.09523 | C001881623 | Swon Miller | St.James | Completed | Load_412893 | Bogue - 410 | 2026-08-07 08:25 | 2026-08-07 08:26 | 2026-08-07 08:30 | 2026-08-07 13:23 | 2026-08-07 14:11 | 2026-08-07 14:52 | 2026-08-07 15:08 | 2026-08-07 15:08 |  |  | Fair | No | Check and found area okay voltage found 115/117/233 voltage left 117/115/233
Outage | J.E.26.08.09755 | C001881629 | Raymond Carr | St.Mary | Completed | Load_240442 | Oracabessa - 210 | 2026-08-07 08:25 | 2026-08-07 08:30 | 2026-08-07 08:45 | 2026-08-07 08:45 | 2026-08-07 09:27 | 2026-08-07 09:38 | 2026-08-07 09:42 | 2026-08-07 09:42 |  |  | Fair | No | Blown junction fuse found at pole number 0115796, U R D system. Unable to ascertain, cause of outage. A 10 amp fuse was used to renew supply was restored.
Non-Outage | J.E.26.08.07798 | C001881632 | Romeo Brissett |  | Completed |  |  | 2026-08-07 08:26 | 2026-08-07 08:27 | 2026-08-07 12:56 | 2026-08-07 12:57 | 2026-08-07 13:27 | 2026-08-07 13:30 | 2026-08-07 13:40 | 2026-08-07 13:40 |  |  | Fair | No | Removed illegal connections and Reset (1)10KVA transformer.
Non-Outage | J.E.26.08.08781 | C001881631 | Romeo Brissett |  | Completed |  |  | 2026-08-07 08:26 | 2026-08-07 08:27 | 2026-08-07 08:50 | 2026-08-07 08:50 | 2026-08-07 10:18 | 2026-08-07 11:00 | 2026-08-07 11:21 | 2026-08-07 11:21 |  |  | Fair | No | (1)50kva Transformer fuse was found blown line patrolled and illegal connections was removed, transformer was tested closed and held however no power coming from transformer secondary circuit. 0.093V. Twelve (12) customers is without supply, recommending (1)25KVA , Transformer urgently need to change circuit cannot be tie. Please send to maintenance.
Non-Outage | J.E.26.08.09496 | C001881630 | Romeo Brissett |  | Completed |  |  | 2026-08-07 08:26 | 2026-08-07 08:27 | 2026-08-07 08:49 | 2026-08-07 11:22 | 2026-08-07 11:21 | 2026-08-07 12:50 | 2026-08-07 12:56 | 2026-08-07 12:56 |  |  | Fair | No | Replaced (1)20amp, (1)15amps, (1)8amps junction fuses and (1)15KVA transformer fuse. Found (1)15KVA transformer HEX#04148 Rammy box transformer suspected defective. Please send to maintenance and copy to field service department. Used (1)20amps, (1)15amps, (3)8amps, (2)2amps and (1)1.5amps
Outage | J.E.26.08.06251 | C001881633 | Romeo Brissett | St.James | Completed | Load_245028 | Bogue - 610 | 2026-08-07 08:26 | 2026-08-07 08:27 | 2026-08-07 13:40 | 2026-08-07 13:41 | 2026-08-07 14:53 | 2026-08-07 15:08 | 2026-08-07 15:11 | 2026-08-07 15:11 |  |  | Fair | No | Line patrolled and found power in the area, resident stated power was restored meter is located and found powered.
Non-Outage | J.E.26.08.07818 | C001881644 | Derrick Dawkins | St.James | Completed | Load_261423 | Bogue - 310 | 2026-08-07 08:31 | 2026-08-07 08:46 | 2026-08-07 11:05 | 2026-08-07 11:05 | 2026-08-07 11:05 | 2026-08-07 11:38 | 2026-08-07 11:06 | 2026-08-07 11:06 |  |  | Fair | No | Premises ok
Non-Outage | J.E.26.08.07968 | C001881643 | Derrick Dawkins | St.James | Completed | Load_266571 | Bogue - 310 | 2026-08-07 08:31 | 2026-08-07 08:46 | 2026-08-07 11:02 | 2026-08-07 11:03 | 2026-08-07 11:03 | 2026-08-07 11:16 | 2026-08-07 11:05 | 2026-08-07 11:05 |  |  | Fair | No | Premises ok
Non-Outage | J.E.26.08.08698 | C001881642 | Derrick Dawkins | St.James | Completed | Load_261864 | Bogue - 610 | 2026-08-07 08:31 | 2026-08-07 08:46 | 2026-08-07 12:14 | 2026-08-07 12:15 | 2026-08-07 12:15 | 2026-08-07 12:15 | 2026-08-07 12:16 | 2026-08-07 12:16 |  |  | Fair | No | 5 customer without light in the hexing box refer back to field service kadian
Non-Outage | J.E.26.08.06972 | C001881645 | Derrick Dawkins | St.James | Completed | Load_258319 | Bogue - 310 | 2026-08-07 08:32 | 2026-08-07 08:46 | 2026-08-07 11:07 | 2026-08-07 11:07 | 2026-08-07 11:07 | 2026-08-07 00:56 | 2026-08-07 11:11 | 2026-08-07 11:11 |  |  | Fair | No | Premises ok
Non-Outage | J.E.26.08.07786 | C001881646 | Derrick Dawkins | St.James | Completed | Load_1001936 | Bogue - 310 | 2026-08-07 08:32 | 2026-08-07 08:46 | 2026-08-07 09:03 | 2026-08-07 09:03 | 2026-08-07 10:58 | 2026-08-07 10:33 | 2026-08-07 10:59 | 2026-08-07 10:59 |  |  | Fair | No | Premises ok
Outage | J.E.26.08.09776 | C001881647 | Christopher Edwards | KSAN | Completed | Load_264085 | Constant Spring - 410 | 2026-08-07 08:32 | 2026-08-07 08:38 | 2026-08-07 11:35 | 2026-08-07 11:36 | 2026-08-07 11:35 | 2026-08-07 11:35 | 2026-08-07 11:36 | 2026-08-07 11:36 |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Non-Outage | J.E.26.08.09773 | C001881652 | Richard Watson |  | Completed |  |  | 2026-08-07 08:34 | 2026-08-07 08:36 | 2026-08-07 08:49 | 2026-08-07 08:50 | 2026-08-07 10:57 | 2026-08-07 11:06 | 2026-08-07 11:10 | 2026-08-07 11:10 | BrokenWire |  | Fair | No | Secondary neutral has about 4 broken strands of conductor in midspan, approximately 3strands of wire holding conductor together , bucket truck required to effect repairs.
Outage | J.E.26.08.09649 | C001881651 | Raheem Ricketts | Manchester | Completed | Load_265556 | Spur Tree - 210 | 2026-08-07 08:34 | 2026-08-07 08:36 | 2026-08-07 08:44 | 2026-08-07 09:05 | 2026-08-07 09:25 | 2026-08-07 10:04 | 2026-08-07 10:04 | 2026-08-07 10:04 |  |  | Fair | No | Check an found 10am junction fuse blown refuse junction using one 10amp fuse
Non-Outage | J.E.26.08.06637 | C001881658 | Nicholas Dillon | St.Elizabeth | Completed | Load_292118 | Maggotty - 210 | 2026-08-07 08:38 | 2026-08-07 08:43 | 2026-08-07 12:29 | 2026-08-07 12:30 | 2026-08-07 14:33 | 2026-08-07 14:33 | 2026-08-07 14:36 | 2026-08-07 14:36 |  |  | Fair | No | Check voltage before at meter 113 115 phase to phase 226. Premises found working ok
Non-Outage | J.E.26.08.06905 | C001881654 | Nicholas Dillon | St.Elizabeth | Completed | Load_238091 | Maggotty - 210 | 2026-08-07 08:38 | 2026-08-07 08:43 | 2026-08-07 12:10 | 2026-08-07 12:11 | 2026-08-07 12:22 | 2026-08-07 12:22 | 2026-08-07 12:23 | 2026-08-07 12:23 |  |  | Fair | Yes | Check and found neutral wire corrode at pothead clean joint and use 1 one bolt clamp before I left voltage is 114 111 phase to phase 226
Non-Outage | J.E.26.08.07218 | C001881656 | Nicholas Dillon | St.Elizabeth | Completed | Load_262625 | Maggotty - 210 | 2026-08-07 08:38 | 2026-08-07 08:43 | 2026-08-07 10:28 | 2026-08-07 10:29 | 2026-08-07 10:54 | 2026-08-07 10:54 | 2026-08-07 10:55 | 2026-08-07 10:55 |  |  | Fair | Yes | Check and found at pole clean joint and use 2 one bolt clamp before I left voltage is 117 116 phase to phase 233
Non-Outage | J.E.26.08.07411 | C001881655 | Nicholas Dillon | St.Elizabeth | Completed | Load_248429 | Maggotty - 210 | 2026-08-07 08:38 | 2026-08-07 08:43 | 2026-08-07 11:05 | 2026-08-07 11:06 | 2026-08-07 11:23 | 2026-08-07 11:32 | 2026-08-07 11:33 | 2026-08-07 11:33 |  |  | Fair | No | Check voltage before at meter 107 102 phase to phase 210 . Whole area experiencing low voltage. Transformer need to top up
Non-Outage | J.E.26.08.09146 | C001881666 | Error Coore | Manchester | Completed | Load_238080 | Spur Tree - 310 | 2026-08-07 08:43 | 2026-08-07 08:45 | 2026-08-07 09:32 | 2026-08-07 09:34 | 2026-08-07 09:54 | 2026-08-07 11:09 | 2026-08-07 11:13 | 2026-08-07 11:13 |  |  | Fair | No | Open a 25 KVA xformer to remade a corroded secondary jumper remade corroded jumper using 2 one bolt clamp voltage reading 116/117/233 volts
Non-Outage | J.E.26.08.09780 | C001881665 | Raymond Carr |  | Completed |  |  | 2026-08-07 08:43 | 2026-08-07 08:44 | 2026-08-07 09:42 | 2026-08-07 09:43 | 2026-08-07 09:43 | 2026-08-07 09:27 | 2026-08-07 09:44 | 2026-08-07 09:44 |  |  | Fair | No | Supply was restored. Related to Edge hill outage.
Outage | J.E.26.08.09705 | C001881671 | Radcliffe Coleman | St.Catherine | Completed | Load_239371 | Tredegar - 210 | 2026-08-07 08:46 | 2026-08-07 08:48 | 2026-08-07 09:30 | 2026-08-07 09:31 | 2026-08-07 10:55 | 2026-08-07 11:04 | 2026-08-07 11:04 | 2026-08-07 11:04 |  |  | Fair | No | Customer meter socket found defective, he was advised to contact his electrician to make the necessary repairs.
Outage | J.E.26.08.09771 | C001881673 | Radcliffe Coleman | St.Catherine | Completed | Load_238623 | Twickenham - 310 | 2026-08-07 08:46 | 2026-08-07 08:48 | 2026-08-07 09:50 | 2026-08-07 12:49 | 2026-08-07 13:22 | 2026-08-07 13:25 | 2026-08-07 13:25 | 2026-08-07 13:25 | LeaningPole |  | Fair | No | There is a leaning pole at the location, please refer to the maintenance department for their intervention.
Outage | J.E.26.08.09790 | C001881672 | Radcliffe Coleman | KSAN | Completed | Load_574824 | Washington Blvd - 610 | 2026-08-07 08:46 | 2026-08-07 08:49 | 2026-08-07 11:04 | 2026-08-07 11:05 | 2026-08-07 11:04 | 2026-08-07 11:07 | 2026-08-07 11:07 | 2026-08-07 11:07 |  |  | Fair | No | Please refer to Mosses Eliston for his intervention.
Outage | J.E.26.08.09677 | C001881674 | Radcliffe Coleman | St.Catherine | Completed | Load_260095 | Twickenham - 310 | 2026-08-07 08:48 | 2026-08-07 08:49 | 2026-08-07 10:18 | 2026-08-07 13:26 | 2026-08-07 13:26 | 2026-08-07 13:28 | 2026-08-07 13:28 | 2026-08-07 13:28 | LeaningPole |  | Fair | No | Unable to locate customer due to inadequate direction, also a number of calls were placed to telephone number provided which went to voicemail.
Outage | J.E.26.08.09778 | C001881679 | Clyde Brown | Clarendon | Completed | Load_244375 | May Pen - 110 | 2026-08-07 08:49 | 2026-08-07 08:50 | 2026-08-07 10:21 | 2026-08-07 10:21 | 2026-08-07 11:29 | 2026-08-07 11:35 | 2026-08-07 11:39 | 2026-08-07 11:39 | Fire |  | Fair | No | Secondary phase and neutral entangled open 25 kva transformer and retention secondary neutral and line now cleared.
Outage | J.E.26.08.09582 | C001881681 | Christopher West | Portmore | Completed | Load_244060 | Naggo Head - 610 | 2026-08-07 08:50 | 2026-08-07 08:52 | 2026-08-07 10:21 | 2026-08-07 10:21 | 2026-08-07 10:38 | 2026-08-07 11:10 | 2026-08-07 11:20 | 2026-08-07 11:20 |  |  | Fair | No | 3 wire service supplying 4 customers had a burnt phase, used 3 pen inions for repairs, customer now ok.
Outage | J.E.26.08.09722 | C001881682 | Christopher West | Portmore | Completed | Load_249433 | Naggo Head - 610 | 2026-08-07 08:50 | 2026-08-07 08:52 | 2026-08-07 09:10 | 2026-08-07 09:11 | 2026-08-07 10:18 | 2026-08-07 10:20 | 2026-08-07 10:20 | 2026-08-07 10:20 |  |  | Fair | No | A blown 10A junction fuse was found at Pole#0081353 by maintenance personnel, line section patrolled however, no abnormalities were found, blown fuse renewed, line re-energized, area now ok.
Outage | J.E.26.08.09793 | C001881680 | Moses Elliston | Portmore | Completed | Load_576144 | Naggo Head - 610 | 2026-08-07 08:50 | 2026-08-07 11:19 | 2026-08-07 13:49 | 2026-08-07 13:49 | 2026-08-07 13:49 | 2026-08-07 13:49 | 2026-08-07 13:50 | 2026-08-07 13:50 |  |  | Fair | No | Credit added to prepaid account
Outage | J.E.26.08.07106 | C001881683 | Rodclif Dawkins | Portmore | Completed | Load_268747 | Naggo Head - 510 | 2026-08-07 08:52 | 2026-08-07 15:34 | 2026-08-07 21:03 | 2026-08-07 21:03 | 2026-08-07 21:53 | 2026-08-07 21:53 | 2026-08-07 22:57 | 2026-08-07 22:57 |  |  | Fair | No | Customer found with supply
Outage | J.E.26.08.09798 | C001881688 | Edward Royal | KSAS | Completed | Load_301272 | Hunts Bay - 510 | 2026-08-07 08:55 | 2026-08-07 09:03 | 2026-08-07 10:34 | 2026-08-07 10:35 | 2026-08-07 10:34 | 2026-08-07 11:57 | 2026-08-07 11:57 | 2026-08-07 11:57 | BrokenWire |  | Fair | No | Spliced and reconnected secondary phase using 50ft number 3 conductor and 4 single bolt clamp replaced 15A junction fuse
Non-Outage | J.E.26.08.07958 | C001881693 | Richard Grant | St.Catherine | Completed | Load_252028 | New Michelton - 210 | 2026-08-07 08:56 | 2026-08-07 08:57 | 2026-08-07 16:49 | 2026-08-07 16:51 | 2026-08-07 16:50 | 2026-08-07 16:51 | 2026-08-07 16:51 | 2026-08-07 16:51 |  |  | Fair | No | Premises found okay
Non-Outage | J.E.26.08.08228 | C001881692 | Richard Grant | St.Catherine | Completed | Load_242607 | New Michelton - 210 | 2026-08-07 08:56 | 2026-08-07 08:57 | 2026-08-07 16:49 | 2026-08-07 16:50 | 2026-08-07 16:50 | 2026-08-07 16:50 | 2026-08-07 16:50 | 2026-08-07 16:50 |  |  | Fair | No | Premises found okay
Non-Outage | J.E.26.08.09148 | C001881691 | Richard Grant | St.Catherine | Completed | Load_244637 | New Michelton - 210 | 2026-08-07 08:56 | 2026-08-07 08:57 | 2026-08-07 13:14 | 2026-08-07 16:49 | 2026-08-07 16:49 | 2026-08-07 16:50 | 2026-08-07 16:50 | 2026-08-07 16:50 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.09746 | C001881689 | Richard Grant | St.Catherine | Completed | Load_246207 | New Michelton - 310 | 2026-08-07 08:56 | 2026-08-07 08:57 | 2026-08-07 09:11 | 2026-08-07 09:11 | 2026-08-07 10:22 | 2026-08-07 13:13 | 2026-08-07 13:13 | 2026-08-07 13:13 |  |  | Fair | No | Broken neutral and defective phases found for 2/0 triplex wire caused by truck accident. 25kva transformer also found leaning causing oil to leak. Transformer straightened, 1 2/0 sleeve, 1 2/0 preform, 11 onebolt clamps, approximately 8ft 2/0 insulated copper and approximately 20ft 2/0 triplex used to take out damaged area of wire, retention line and change out defective dropleads. Supply restored and area left okay
Outage | J.E.26.08.09770 | C001881690 | Richard Samuda | Manchester | Completed | Load_230012 | Porus - 310 | 2026-08-07 08:56 | 2026-08-07 08:57 | 2026-08-07 12:42 | 2026-08-07 12:42 | 2026-08-07 14:06 | 2026-08-07 14:08 | 2026-08-07 14:08 | 2026-08-07 14:08 |  |  | Fair | No | Found ok customer has a damaged main breaker advised customer to sort out breaker voltage 113, 114 227
Non-Outage | J.E.26.08.07006 | C001881696 | Ricky Hall | St.Catherine | Completed | Load_260140 | Rhodens Pen - 410 | 2026-08-07 08:57 | 2026-08-07 15:13 | 2026-08-07 17:55 | 2026-08-07 17:55 | 2026-08-07 18:23 | 2026-08-07 19:16 | 2026-08-07 19:17 | 2026-08-07 19:17 |  |  | Fair | No | Splice and reconnect 3 w service mid span use 2 clamps 114/112/226
Non-Outage | J.E.26.08.07498 | C001881695 | Donald Cunningham | St.Catherine | Completed | Load_245730 | Rhodens Pen - 410 | 2026-08-07 08:57 | 2026-08-07 08:59 | 2026-08-07 09:57 | 2026-08-07 09:58 | 2026-08-07 12:29 | 2026-08-07 13:07 | 2026-08-07 13:09 | 2026-08-07 13:09 |  |  | Fair | No | Burnt and corroded phase corrected 5 customer affected voltage readings 114/2/228
Non-Outage | J.E.26.08.08457 | C001881694 | Ricky Hall | St.Catherine | Completed | Load_240129 | Rhodens Pen - 210 | 2026-08-07 08:57 | 2026-08-07 15:13 | 2026-08-07 15:35 | 2026-08-07 15:42 | 2026-08-07 16:38 | 2026-08-07 17:11 | 2026-08-07 17:17 | 2026-08-07 17:17 |  |  | Fair | No | 50 kva xfmr circuit overload due to length of circuit customer quantity and numerous illegal connections customers at D/E getting 100*2/201 reading at xfmr 120*2/240 @normal tap also evidence of leakage seen line section may need extension plz refer to the relevant personnelNB no breakage in circuit
Non-Outage | J.E.26.07.38859 | C001881699 | Donald Cunningham | St.Catherine | Completed | Load_256035 | Rhodens Pen - 410 | 2026-08-07 08:58 | 2026-08-08 08:32 | 2026-08-08 12:33 | 2026-08-08 12:33 | 2026-08-08 14:09 | 2026-08-08 14:36 | 2026-08-08 14:36 | 2026-08-08 14:36 |  |  | Fair | No | Premises found ok issues already resolved
Non-Outage | J.E.26.08.00829 | C001881697 | Donald Cunningham | St.Catherine | Completed | Load_239125 | Rhodens Pen - 410 | 2026-08-07 08:58 | 2026-08-07 08:59 | 2026-08-07 13:10 | 2026-08-07 13:10 | 2026-08-07 14:55 | 2026-08-07 14:56 | 2026-08-07 14:57 | 2026-08-07 14:57 |  |  | Fair | No | Need more directions customer not reachable
Outage | J.E.26.08.09808 | C001881703 | Evan Spaulding | St.Mary | Completed | Load_244370 | Highgate - 210 | 2026-08-07 09:02 | 2026-08-07 09:03 | 2026-08-07 10:47 | 2026-08-07 10:48 | 2026-08-07 11:24 | 2026-08-07 12:40 | 2026-08-07 12:42 | 2026-08-07 12:42 | Fire | Y | Fair | No | Carry out spot bushing,retention one span secondary conductors use 1-1 bolt clamp,Also line section needs bushing,refer to maintenance.
Outage | J.E.26.08.09814 | C001881704 | Rusean Allen | KSAS | Completed | Load_254739 | Cane River - 610 | 2026-08-07 09:03 | 2026-08-07 09:04 | 2026-08-07 09:16 | 2026-08-07 09:36 | 2026-08-07 10:39 | 2026-08-07 10:54 | 2026-08-07 10:54 | 2026-08-07 10:54 | BrokenWire |  | Fair | No | Found a 20 amps fuse Replace a 20 amps fusec
Non-Outage | J.E.26.08.09125 | C001881714 | Andre Williams |  | Completed |  |  | 2026-08-07 09:09 | 2026-08-07 09:10 | 2026-08-07 10:08 | 2026-08-07 10:09 | 2026-08-07 10:23 | 2026-08-07 10:24 | 2026-08-07 10:25 | 2026-08-07 10:25 |  |  | Fair | No | Power was restored to area from lastnight confirm by call
Outage | J.E.26.08.09254 | C001881715 | Tajay Bernard | Hanover | Completed | Load_255660 | Orange Bay - 310 | 2026-08-07 09:10 | 2026-08-07 09:11 | 2026-08-07 12:19 | 2026-08-07 12:20 | 2026-08-07 13:02 | 2026-08-07 13:03 | 2026-08-07 13:03 | 2026-08-07 13:03 |  |  | Fair | No | Area check and found okay unable to locate customer on premises multiple phone calls to customer number went unanswered
Non-Outage | J.E.26.08.04998 | C001881716 | Tyrese Williams | St.Ann | Completed | Load_242953 | Roaring River - 410 | 2026-08-07 09:13 | 2026-08-07 15:45 | 2026-08-07 17:10 | 2026-08-07 17:23 | 2026-08-07 17:51 | 2026-08-07 18:24 | 2026-08-07 18:24 | 2026-08-07 18:24 |  |  | Fair | No | Remade secondary neutral jumper voltage 112/110/222
Non-Outage | J.E.26.07.32388 | C001881726 | Andrae Clarke | Portland | Completed | Load_240419 | Port Antonio - 410 | 2026-08-07 09:15 | 2026-08-07 10:01 | 2026-08-07 11:44 | 2026-08-07 11:45 | 2026-08-07 14:22 | 2026-08-07 14:31 | 2026-08-07 14:25 | 2026-08-07 14:25 |  |  | Fair | No | Premises found okay 119/121/240
Outage | J.E.26.08.09824 | C001881727 | Daniel Lobar | Trelawny | Completed | Load_270209 | Duncans - 210 | 2026-08-07 09:15 | 2026-08-07 09:16 | 2026-08-07 12:54 | 2026-08-07 12:54 | 2026-08-07 13:41 | 2026-08-07 13:54 | 2026-08-07 13:49 | 2026-08-07 13:49 |  |  | Fair | No | Premises checked and found ok, the voltage are 117v/118v/235v: the customer was advised to call an electrician as the problem is an internal issue
Non-Outage | J.E.26.08.09624 | C001881736 | Derrick Dawkins |  | Completed |  |  | 2026-08-07 09:19 | 2026-08-07 16:32 | 2026-08-07 18:58 | 2026-08-07 18:58 | 2026-08-07 18:58 | 2026-08-07 18:15 | 2026-08-07 18:59 | 2026-08-07 18:59 |  |  | Fair | No | Customer complained about street lights premises ok
Non-Outage | J.E.26.08.09759 | C001881737 | Edward Royal | KSAS | Completed | Load_300617 | Hunts Bay - 710 | 2026-08-07 09:19 | 2026-08-07 09:37 | 2026-08-07 12:17 | 2026-08-07 12:17 | 2026-08-07 12:17 | 2026-08-07 13:51 | 2026-08-07 13:52 | 2026-08-07 13:52 |  |  | Fair | No | Spliced and reconnected transformer drop lead to secondary phase and neutral using 3 am pack
Outage | J.E.26.08.09575 | C001881760 | Horace Malcolm | Trelawny | Completed | Load_241701 | Greenwood - 110 | 2026-08-07 09:28 | 2026-08-07 15:35 | 2026-08-07 19:57 | 2026-08-07 19:57 | 2026-08-07 20:13 | 2026-08-07 20:14 | 2026-08-07 20:14 | 2026-08-07 20:14 |  |  | Fair | No | Check and found area ok
Non-Outage | J.E.26.08.08653 | C001881765 | Andre Williams |  | Completed |  |  | 2026-08-07 09:34 | 2026-08-07 09:34 | 2026-08-07 10:05 | 2026-08-07 10:29 | 2026-08-07 11:07 | 2026-08-07 11:08 | 2026-08-07 11:09 | 2026-08-07 11:09 |  |  | Fair | No | Field service team on location
Outage | J.E.26.08.09852 | C001881766 | Andre Smith | KSAN | Completed | Load_259291 | Washington Blvd - 310 | 2026-08-07 09:37 | 2026-08-07 09:38 | 2026-08-07 09:43 | 2026-08-07 09:43 | 2026-08-07 10:08 | 2026-08-07 10:09 | 2026-08-07 10:09 | 2026-08-07 10:09 |  |  | Fair | No | Customer meter not located in ypp box field service department required to replace customer meter
Outage | J.E.26.08.09815 | C001881791 | Ricky Hall | St.Catherine | Completed | Load_250255 | New Michelton - 210 | 2026-08-07 09:49 | 2026-08-08 07:57 | 2026-08-08 10:54 | 2026-08-08 10:54 | 2026-08-08 12:03 | 2026-08-08 12:07 | 2026-08-08 12:07 | 2026-08-08 12:07 | LowHangingWires |  | Fair | No | Low hanging internet wire customer advised
Outage | J.E.26.08.09843 | C001881792 | Richard Grant | St.Catherine | Completed | Load_243844 | New Michelton - 310 | 2026-08-07 09:49 | 2026-08-07 09:50 | 2026-08-07 10:25 | 2026-08-07 13:14 | 2026-08-07 13:13 | 2026-08-07 13:14 | 2026-08-07 13:14 | 2026-08-07 13:14 | LeakingTransformer |  | Fair | No | Broken neutral and defective phases found for 2/0 triplex wire caused by truck accident. 25kva transformer also found leaning causing oil to leak. Transformer straightened, 1 2/0 sleeve, 1 2/0 preform, 11 onebolt clamps, approximately 8ft 2/0 insulated copper and approximately 20ft 2/0 triplex used to take out damaged area of wire, retention line and change out defective dropleads. Supply restored and area left okay
Outage | J.E.26.08.09823 | C001881794 | Radcliffe Coleman | St.Catherine | Completed | Load_568919 | Twickenham - 310 | 2026-08-07 09:50 | 2026-08-07 09:51 | 2026-08-07 11:07 | 2026-08-07 11:08 | 2026-08-07 11:07 | 2026-08-07 11:09 | 2026-08-07 11:10 | 2026-08-07 11:10 |  |  | Fair | No | Please refer to Mosses Eliston for his intervention.
Outage | J.E.26.08.09853 | C001881793 | Ricky Hall | St.Catherine | Completed | Load_243118 | Rhodens Pen - 410 | 2026-08-07 09:50 | 2026-08-07 15:13 | 2026-08-07 17:18 | 2026-08-07 17:18 | 2026-08-07 17:51 | 2026-08-07 17:52 | 2026-08-07 17:52 | 2026-08-07 17:52 | Fire |  | Fair | No | Broken customer pole customer advised
Outage | J.E.26.08.09830 | C001881796 | Rodclif Dawkins | Portmore | Completed | Load_289799 | Naggo Head - 510 | 2026-08-07 09:51 | 2026-08-07 15:34 | 2026-08-07 17:02 | 2026-08-07 17:03 | 2026-08-07 17:02 | 2026-08-07 17:02 | 2026-08-07 17:05 | 2026-08-07 17:05 |  |  | Fair | No | Customer supplied by quad logic. Please refer to the relevant person meter noncomm
Outage | J.E.26.08.09868 | C001881797 | Richard Samuda | Manchester | Completed | Load_302545 | Spur Tree - 210 | 2026-08-07 09:51 | 2026-08-07 09:53 | 2026-08-07 10:26 | 2026-08-07 10:26 | 2026-08-07 10:56 | 2026-08-07 11:35 | 2026-08-07 11:35 | 2026-08-07 11:35 |  |  | Fair | No | Found 30 amps junction blown patrol area found nothing replaced fuse close line customer back to normal
Outage | J.E.26.08.09862 | C001881798 | Rodclif Dawkins | St.Catherine | Completed | Load_259149 | Twickenham - 210 | 2026-08-07 09:52 | 2026-08-07 15:34 | 2026-08-07 22:57 | 2026-08-07 22:57 | 2026-08-07 22:57 | 2026-08-07 22:57 | 2026-08-07 22:58 | 2026-08-07 22:58 |  |  | Fair | No | Customer found okay
Non-Outage | J.E.26.08.09871 | C001881819 | Edward Royal | KSAS | Completed | Load_301272 | Hunts Bay - 510 | 2026-08-07 10:02 | 2026-08-07 10:16 | 2026-08-07 11:58 | 2026-08-07 11:58 | 2026-08-07 11:58 | 2026-08-07 11:59 | 2026-08-07 11:59 | 2026-08-07 11:59 |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.08.09881 | C001881816 | Gregory Grossett | Portland | Completed | Load_261986 | Port Antonio - 310 | 2026-08-07 10:02 | 2026-08-07 10:23 | 2026-08-07 11:03 | 2026-08-07 11:03 | 2026-08-07 11:03 | 2026-08-07 11:04 | 2026-08-07 11:04 | 2026-08-07 11:04 |  |  | Fair | No | 25kva transformer drop leads corroded and 2/0 triplex conductor oxidized open transformer fuse to make repairs then close transformer fuse to restore normal supply to the area.Material use 15 one bolt clamps 5ft of 2/0 conductor.
Non-Outage | J.E.26.08.09847 | C001881837 | Antony Levy | KSAN | Completed | Load_239759 | Constant Spring - 210 | 2026-08-07 10:15 | 2026-08-07 10:28 | 2026-08-07 13:37 | 2026-08-07 13:58 | 2026-08-07 14:16 | 2026-08-07 14:17 | 2026-08-07 14:19 | 2026-08-07 14:19 | LowHangingWires |  | Fair | No | Premises found okay not jps wires .... internet wires flow and digicel
Non-Outage | J.E.26.08.09909 | C001881840 | Gregory Grossett |  | Completed |  |  | 2026-08-07 10:16 | 2026-08-07 10:36 | 2026-08-07 12:43 | 2026-08-07 12:44 | 2026-08-07 14:03 | 2026-08-07 14:41 | 2026-08-07 14:42 | 2026-08-07 14:42 |  |  | Fair | No | Customer was on disconnection for non payment.
Outage | J.E.26.08.09891 | C001881839 | Rusean Allen | KSAS | Completed | Load_1002854 | Rockfort - 210 | 2026-08-07 10:16 | 2026-08-07 10:21 | 2026-08-07 12:21 | 2026-08-07 12:22 | 2026-08-07 12:30 | 2026-08-07 12:32 | 2026-08-07 12:33 | 2026-08-07 12:33 |  |  | Fair | No | Premises is located in snow hill Portland
Outage | J.E.26.08.09849 | C001881842 | Omar King | St.Ann | Completed | Load_269690 | Roaring River - 210 | 2026-08-07 10:18 | 2026-08-07 10:23 | 2026-08-07 11:11 | 2026-08-07 11:11 | 2026-08-07 11:47 | 2026-08-07 12:20 | 2026-08-07 12:20 | 2026-08-07 12:20 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Found 25 KVA transformer fuse blown cause broken secondary conductor repair as been carry out and fuse as been replaced area is now with supply
Outage | J.E.26.08.09866 | C001881843 | Tyrese Williams | St.Ann | Completed | Load_258564 | Roaring River - 410 | 2026-08-07 10:18 | 2026-08-07 15:45 | 2026-08-07 16:50 | 2026-08-07 20:20 | 2026-08-07 20:19 | 2026-08-07 20:20 | 2026-08-07 20:20 | 2026-08-07 20:20 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.09895 | C001881844 | Tyrese Williams | St.Ann | Completed | Load_269625 | Roaring River - 410 | 2026-08-07 10:18 | 2026-08-07 15:45 | 2026-08-07 17:10 | 2026-08-07 18:59 | 2026-08-07 19:34 | 2026-08-07 19:45 | 2026-08-07 20:18 | 2026-08-07 20:18 | BrokenWire |  | Fair | No | Premises not found not getting customer at the time of visit
Outage | J.E.26.08.09922 | C001881859 | Raymond Lewis | St.Ann | Completed | Load_254492 | Ocho Rios - 510 | 2026-08-07 10:20 | 2026-08-07 23:18 | 2026-08-08 00:04 | 2026-08-08 00:04 | 2026-08-08 00:45 | 2026-08-08 12:58 | 2026-08-08 00:59 | 2026-08-08 00:59 | BrokenWire |  | Fair | No | Customer need to cut tree for job to complete
Outage | J.E.26.08.09925 | C001881860 | Rusean Allen | KSAS | Completed | Load_261838 | Hunts Bay - 210 | 2026-08-07 10:22 | 2026-08-07 14:46 | 2026-08-07 15:39 | 2026-08-07 15:39 | 2026-08-07 15:50 | 2026-08-07 15:53 | 2026-08-07 15:53 | 2026-08-07 15:53 |  |  | Fair | No | Area congested
Outage | J.E.26.08.09934 | C001881867 | Denton Williams | Portland | Completed | Load_245066 | Port Antonio - 410 | 2026-08-07 10:27 | 2026-08-07 15:12 | 2026-08-07 15:21 | 2026-08-07 15:22 | 2026-08-07 15:21 | 2026-08-07 15:22 | 2026-08-07 15:27 | 2026-08-07 15:27 |  |  | Fair | No | After reaching out to the customer, they informed me that their main breaker was off and their electrical supply is okay.
Outage | J.E.26.08.09940 | C001881868 | Rusean Allen | KSAS | Completed | Load_248877 | Cane River - 610 | 2026-08-07 10:28 | 2026-08-07 10:30 | 2026-08-07 11:01 | 2026-08-07 11:02 | 2026-08-07 11:18 | 2026-08-07 11:28 | 2026-08-07 11:28 | 2026-08-07 11:28 |  |  | Fair | No | 1x 3amp fuse found 1x 3amp fuse replaced
Outage | J.E.26.08.09949 | C001881891 | Gregory Grossett | Portland | Completed | Load_268491 | Port Antonio - 310 | 2026-08-07 10:35 | 2026-08-07 10:36 | 2026-08-07 11:04 | 2026-08-07 11:05 | 2026-08-07 11:46 | 2026-08-07 12:40 | 2026-08-07 12:40 | 2026-08-07 12:40 |  | Y | Fair | No | 15amp junction fuse blown cause by vegetation on line section cut and removed several vines then restore supply to the area material use 15amp fuse.
Outage | J.E.26.08.09917 | C001881893 | Evan Spaulding | St.Mary | Completed | Load_238645 | Highgate - 210 | 2026-08-07 10:37 | 2026-08-07 10:42 | 2026-08-07 12:48 | 2026-08-07 13:49 | 2026-08-07 14:33 | 2026-08-07 14:37 | 2026-08-07 14:39 | 2026-08-07 14:39 | BangingWires |  | Fair | No | Tree fall on service wire to customer house,customer advised to get tree cut off wire.
Outage | J.E.26.08.09931 | C001881892 | Raymond Carr | St.Ann | Completed | Load_262554 | Upper White River - 110 | 2026-08-07 10:37 | 2026-08-07 10:41 | 2026-08-07 10:53 | 2026-08-07 10:54 | 2026-08-07 11:56 | 2026-08-07 00:16 | 2026-08-07 12:17 | 2026-08-07 12:17 |  |  | Fair | No | Blown 25 kva transformer fuse found, line patrol and found okay, however tree contact was suspected. A 2 amp fuse was used to renew supply was restored.
Outage | J.E.26.08.09963 | C001881894 | Raymond Carr | St.Ann | Completed | Load_251915 | Upper White River - 110 | 2026-08-07 10:38 | 2026-08-07 10:41 | 2026-08-07 12:18 | 2026-08-07 12:19 | 2026-08-07 12:39 | 2026-08-07 13:03 | 2026-08-07 13:12 | 2026-08-07 13:12 |  |  | Fair | No | Customer was advised that account is disconnected.
Non-Outage | J.E.26.08.09858 | C001881914 | Richard Samuda |  | Completed |  |  | 2026-08-07 10:45 | 2026-08-07 10:47 | 2026-08-07 11:35 | 2026-08-07 11:41 | 2026-08-07 11:41 | 2026-08-07 11:48 | 2026-08-07 11:48 | 2026-08-07 11:48 |  |  | Fair | No | Pole number : 0138389 found 15amp junction blown patrol line found nothing replaced fuse close line customer back to normal
Outage | J.E.26.08.09938 | C001881913 | Richard Samuda | Manchester | Completed | Load_270245 | Kendal - 310 | 2026-08-07 10:45 | 2026-08-07 10:47 | 2026-08-07 11:50 | 2026-08-07 11:52 | 2026-08-07 12:38 | 2026-08-07 00:41 | 2026-08-07 12:41 | 2026-08-07 12:41 |  |  | Fair | No | Customer said power was restored
Outage | J.E.26.08.09945 | C001881916 | Radcliffe Coleman | St.Catherine | Completed | Load_557324 | Twickenham - 410 | 2026-08-07 10:47 | 2026-08-07 10:50 | 2026-08-07 11:10 | 2026-08-07 11:10 | 2026-08-07 12:15 | 2026-08-07 12:48 | 2026-08-07 12:49 | 2026-08-07 12:49 |  |  | Fair | No | Area found with two blown junction fuse (2-30A), line section was patrolled and no visible fault found. Line section was re-energize with same value fuse found. Area left with supply.
Outage | J.E.26.08.09990 | C001881933 | Fredrick Hamilton | KSAS | Completed | Load_257773 | Duhaney - 310 | 2026-08-07 10:54 | 2026-08-07 12:29 | 2026-08-07 13:24 | 2026-08-07 13:24 | 2026-08-07 13:35 | 2026-08-07 14:02 | 2026-08-07 14:02 | 2026-08-07 14:02 |  |  | Fair | No | Burnt phase and defective neutral observed at pole same was corrected 2 clamps usedPremises is now ok
Non-Outage | J.E.26.08.09943 | C001881946 | Fredrick Hamilton | KSAN | Completed | Load_261778 | Constant Spring - 310 | 2026-08-07 11:04 | 2026-08-07 11:08 | 2026-08-07 11:29 | 2026-08-07 11:51 | 2026-08-07 11:56 | 2026-08-07 11:58 | 2026-08-07 11:58 | 2026-08-07 11:58 |  |  | Fair | No | Please assign to losses department customer requires a losses inspection No JPS defect at location
Outage | J.E.26.08.09790 | C001881947 | Moses Elliston | KSAN | Completed | Load_574824 | Washington Blvd - 610 | 2026-08-07 11:07 | 2026-08-07 11:08 | 2026-08-08 00:55 | 2026-08-08 00:56 | 2026-08-08 00:55 | 2026-08-07 15:40 | 2026-08-08 00:59 | 2026-08-08 00:59 |  |  | Fair | No | Slack meter 3 wire service meter phase lead tightened.
Outage | J.E.26.08.09823 | C001881948 | Moses Elliston | St.Catherine | Completed | Load_568919 | Twickenham - 310 | 2026-08-07 11:09 | 2026-08-07 11:09 | 2026-08-07 12:11 | 2026-08-07 12:11 | 2026-08-07 12:11 | 2026-08-07 12:12 | 2026-08-07 12:13 | 2026-08-07 12:13 |  |  | Fair | No | Credit added to prepaid account
Outage | J.E.26.08.09969 | C001881960 | Radcliffe Coleman | St.Catherine | Completed | Load_262759 | Twickenham - 310 | 2026-08-07 11:10 | 2026-08-07 11:12 | 2026-08-07 13:29 | 2026-08-07 13:29 | 2026-08-07 14:13 | 2026-08-07 14:14 | 2026-08-07 14:14 | 2026-08-07 14:14 | BrokenPole |  | Fair | No | Customer is reporting a defective street light, please refer to the street light department for their intervention.
Non-Outage | J.E.26.08.09306 | C001881978 | Omar King | St.Ann | Completed | Load_252857 | Roaring River - 210 | 2026-08-07 11:19 | 2026-08-07 11:20 | 2026-08-07 12:20 | 2026-08-07 12:21 | 2026-08-07 12:20 | 2026-08-07 13:15 | 2026-08-07 13:16 | 2026-08-07 13:16 |  |  | Fair | No | Due system low voltage I have to top up transformer to increase voltage level voltage reading before 102-102-204 V after top up 109-108-217 Volts
Non-Outage | J.E.26.08.10017 | C001881979 | Moses Elliston |  | Completed |  |  | 2026-08-07 11:19 | 2026-08-07 11:20 | 2026-08-07 12:53 | 2026-08-07 12:53 | 2026-08-07 12:53 | 2026-08-07 12:50 | 2026-08-07 12:54 | 2026-08-07 12:54 |  |  | Fair | No | Credit added to prepaid account.
Non-Outage | J.E.26.08.10028 | C001881977 | Edward Royal |  | Completed |  |  | 2026-08-07 11:19 | 2026-08-07 12:09 | 2026-08-08 07:55 | 2026-08-08 07:55 | 2026-08-08 07:55 | 2026-08-08 07:55 | 2026-08-08 07:55 | 2026-08-08 07:55 | LowHangingWires |  | Fair | No
Outage | J.E.26.08.10025 | C001881980 | Rusean Allen | KSAS | Completed | Load_259746 | Hunts Bay - 210 | 2026-08-07 11:20 | 2026-08-07 11:23 | 2026-08-07 13:52 | 2026-08-07 13:52 | 2026-08-07 13:52 | 2026-08-07 14:13 | 2026-08-07 14:15 | 2026-08-07 14:15 | BrokenWire |  | Fair | No | 50ft #6 service wire was re installed.
Non-Outage | J.E.26.08.08115 | C001881988 | Richman Whyte | Westmoreland | Completed | Load_256003 | Paradise - 310 | 2026-08-07 11:27 | 2026-08-07 11:28 | 2026-08-07 13:22 | 2026-08-07 13:23 | 2026-08-07 13:22 | 2026-08-07 13:22 | 2026-08-07 13:23 | 2026-08-07 13:23 |  |  | Fair | No | Check and found ok
Non-Outage | J.E.26.08.09957 | C001881987 | Javid Vernon | Westmoreland | Completed | Load_292200 | Paradise - 110 | 2026-08-07 11:27 | 2026-08-07 11:28 | 2026-08-07 11:50 | 2026-08-07 11:53 | 2026-08-07 13:13 | 2026-08-07 14:33 | 2026-08-07 14:36 | 2026-08-07 14:36 |  |  | Fair | No | Check and found customer having low voltage 98/97/195 after checking customer pothead, JPS secondary and joints isolate 100kva transformer to change tap changer from 3 to 4 then reclose transformer voltage left 113/113/226 but #2 triplex service wire is defective needs to be upgraded because the wire is under size for feeding 22 customer on the building refer to field service customers need urgent assistance
Outage | J.E.26.08.09964 | C001881990 | Rodclif Dawkins | Portmore | Completed | Load_1004118 | Naggo Head - 510 | 2026-08-07 11:28 | 2026-08-07 15:34 | 2026-08-07 20:31 | 2026-08-07 20:32 | 2026-08-07 20:50 | 2026-08-07 20:51 | 2026-08-07 21:03 | 2026-08-07 21:03 |  |  | Fair | No | Customer found with supply
Outage | J.E.26.08.09982 | C001881989 | Rodclif Dawkins | KSAS | Completed | Load_254412 | Duhaney - 210 | 2026-08-07 11:28 | 2026-08-07 15:34 | 2026-08-07 16:54 | 2026-08-07 17:06 | 2026-08-07 17:31 | 2026-08-07 18:08 | 2026-08-07 17:51 | 2026-08-07 17:51 |  |  | Fair | No
Outage | J.E.26.08.10029 | C001881996 | Raymond Lewis | St.Ann | Completed | Load_248659 | Upper White River - 210 | 2026-08-07 11:29 | 2026-08-07 23:17 | 2026-08-08 00:59 | 2026-08-08 01:00 | 2026-08-08 01:18 | 2026-08-08 13:20 | 2026-08-08 01:20 | 2026-08-08 01:20 | BrokenWire |  | Fair | No | Phone not answering
Outage | J.E.26.08.10041 | C001882007 | Richard Samuda | Manchester | Completed | Load_254867 | Spur Tree - 210 | 2026-08-07 11:40 | 2026-08-07 11:41 | 2026-08-07 14:31 | 2026-08-07 14:31 | 2026-08-07 14:56 | 2026-08-07 14:57 | 2026-08-07 14:57 | 2026-08-07 14:57 |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.08.10052 | C001882020 | Raymond Carr |  | Completed |  |  | 2026-08-07 11:50 | 2026-08-07 11:54 | 2026-08-07 14:07 | 2026-08-07 14:07 | 2026-08-07 14:54 | 2026-08-07 14:55 | 2026-08-07 14:56 | 2026-08-07 14:56 |  |  | Fair | No | Supply was already restored.
Outage | J.E.26.08.10078 | C001882022 | Raheem Ricketts | Manchester | Completed | Load_264159 | Spur Tree - 210 | 2026-08-07 11:50 | 2026-08-07 11:52 | 2026-08-07 12:17 | 2026-08-07 12:23 | 2026-08-07 12:41 | 2026-08-07 12:54 | 2026-08-07 12:55 | 2026-08-07 12:55 | Fire |  | Fair | No | Check and found 10 amp junction fuse blown refuse junction using 1,10amp fure
Non-Outage | J.E.26.08.09821 | C001882033 | Hartley Chin | Clarendon | Completed | Load_262895 | May Pen - 110 | 2026-08-07 11:55 | 2026-08-08 07:52 | 2026-08-08 14:23 | 2026-08-08 14:23 | 2026-08-08 14:23 | 2026-08-08 14:23 | 2026-08-08 14:28 | 2026-08-08 14:28 |  |  | Fair | No | Customer meter socket defective and service wire was disconnected for customer to repairs done. Customer was informed to call back JPS to be reconnected when repairs are done
Non-Outage | J.E.26.08.09899 | C001882032 | Clyde Brown | Clarendon | Completed | Load_241202 | May Pen - 110 | 2026-08-07 11:55 | 2026-08-07 11:56 | 2026-08-07 12:39 | 2026-08-07 12:39 | 2026-08-07 14:06 | 2026-08-07 14:23 | 2026-08-07 14:30 | 2026-08-07 14:30 |  |  | Fair | No | Defective 3 wire service same spliced and retention with30ft-#6 triplex service wire and three clamp,voltage left 117/117 and 234V
Non-Outage | J.E.26.08.09981 | C001882035 | Evan Spaulding |  | Completed |  |  | 2026-08-07 11:57 | 2026-08-07 12:01 | 2026-08-07 12:48 | 2026-08-07 13:40 | 2026-08-07 13:40 | 2026-08-07 13:40 | 2026-08-07 13:41 | 2026-08-07 13:41 | Fire |  | Fair | No | Associated call.
Non-Outage | J.E.26.08.09817 | C001882036 | Neckell Ormsby | St.Mary | Completed | Load_250540 | Annotto Bay - 310 | 2026-08-07 11:58 | 2026-08-07 16:38 | 2026-08-07 16:44 | 2026-08-07 17:02 | 2026-08-07 18:05 | 2026-08-07 18:32 | 2026-08-07 18:33 | 2026-08-07 18:33 | Fire |  | Fair | No | Found 35class 6 wood pole burnt at the bass by bush fire carrying primary and neutral conductor please refer to maintenance department to have it changed, fire was put out
Non-Outage | J.E.26.08.09975 | C001882043 | Evan Spaulding |  | Completed |  |  | 2026-08-07 11:59 | 2026-08-07 12:01 | 2026-08-07 12:44 | 2026-08-07 12:45 | 2026-08-07 12:48 | 2026-08-07 13:37 | 2026-08-07 13:40 | 2026-08-07 13:40 | Fire |  | Fair | No | Flow strand was touching one of the phase,use 1-1 bolt clamp to repair burnt off ground wire.
Outage | J.E.26.08.10064 | C001882044 | Richard Grant | St.Catherine | Completed | Load_249743 | New Michelton - 310 | 2026-08-07 12:00 | 2026-08-07 12:01 | 2026-08-07 16:48 | 2026-08-07 16:49 | 2026-08-07 16:48 | 2026-08-07 16:49 | 2026-08-07 16:49 | 2026-08-07 16:49 |  |  | Fair | No | Premises found okay
Non-Outage | J.E.26.08.09801 | C001882045 | Raymond Carr | St.Ann | Completed | Load_244965 | Upper White River - 110 | 2026-08-07 12:02 | 2026-08-07 12:14 | 2026-08-07 13:13 | 2026-08-07 13:13 | 2026-08-07 13:59 | 2026-08-07 14:00 | 2026-08-07 14:03 | 2026-08-07 14:03 | LowHangingWires |  | Fair | No | Customer reported supply okay.
Outage | J.E.26.08.10000 | C001882046 | Antony Levy | KSAN | Completed | Load_253684 | Constant Spring - 210 | 2026-08-07 12:02 | 2026-08-07 12:02 | 2026-08-07 12:16 | 2026-08-07 12:17 | 2026-08-07 13:37 | 2026-08-07 13:49 | 2026-08-07 13:56 | 2026-08-07 13:56 |  |  | Fair | No
Outage | J.E.26.08.10097 | C001882053 | Oshane Warren | Westmoreland | Completed | Load_265343 | Paradise - 110 | 2026-08-07 12:07 | 2026-08-07 14:59 | 2026-08-07 15:44 | 2026-08-07 15:44 | 2026-08-07 18:34 | 2026-08-07 20:05 | 2026-08-07 20:11 | 2026-08-07 20:11 |  |  | Fair | No | Vehicle accident mashup meter caused meter to burned up on caused secondary conductor to burned off repair and reconnect back customer at pathead voltage 112 112 224
Non-Outage | J.E.26.08.10034 | C001882054 | Milton Charlton | KSAN | Completed | Load_252148 | Hope - 510 | 2026-08-07 12:08 | 2026-08-07 12:20 | 2026-08-07 13:20 | 2026-08-07 13:21 | 2026-08-07 15:31 | 2026-08-07 15:35 | 2026-08-07 15:37 | 2026-08-07 15:37 |  |  | Fair | No | Isolate bank of transformers 3-50 kva at pole # ( no pole#) and repair broken 190 leg on open wire secondary. Repair using 100ft #2AA conductor, one #2 preform and four 1- bolt clamps. Readings at meter socket 115-116-205 and 233-234-235 volts. Reclosed bank of transformers.
Outage | J.E.26.08.10110 | C001882062 | Romaine Roberts | St.Mary | Completed | Load_261726 | Oracabessa - 110 | 2026-08-07 12:13 | 2026-08-07 16:36 | 2026-08-07 18:29 | 2026-08-07 18:29 | 2026-08-07 19:48 | 2026-08-07 19:50 | 2026-08-07 19:50 | 2026-08-07 19:50 |  |  | Fair | No | Customer 3 wire service phase burn off at pole clean and remake joints voltage 112-112 224
Outage | J.E.26.08.10106 | C001882069 | Edward Royal | KSAS | Completed | Load_1003139 | Hunts Bay - 410 | 2026-08-07 12:15 | 2026-08-07 12:21 | 2026-08-07 14:05 | 2026-08-07 14:06 | 2026-08-07 14:06 | 2026-08-07 14:48 | 2026-08-07 14:48 | 2026-08-07 14:48 |  |  | Fair | No | Replaced 3A transformer fuse
Outage | J.E.26.08.10111 | C001882070 | Rusean Allen | KSAS | Completed | Load_254508 | Hunts Bay - 310 | 2026-08-07 12:15 | 2026-08-07 12:21 | 2026-08-07 13:16 | 2026-08-07 13:16 | 2026-08-07 13:34 | 2026-08-07 13:51 | 2026-08-07 13:52 | 2026-08-07 13:52 |  |  | Fair | No | Found a 5 amps fuse Replace a 5 amps fuse
Outage | J.E.26.08.10119 | C001882077 | Eric Williams | KSAN | Completed | Load_266452 | Constant Spring - 210 | 2026-08-07 12:21 | 2026-08-07 16:46 | 2026-08-07 17:27 | 2026-08-07 17:28 | 2026-08-07 18:16 | 2026-08-07 18:17 | 2026-08-07 18:18 | 2026-08-07 18:18 | Fire |  | Fair | No | Fire set and burn pole, pole not badly damaged, refer to maintenance department
Non-Outage | J.E.26.08.10131 | C001882097 | Rusean Allen |  | Completed |  |  | 2026-08-07 12:38 | 2026-08-07 12:43 | 2026-08-07 14:22 | 2026-08-07 14:22 | 2026-08-07 14:22 | 2026-08-07 14:22 | 2026-08-07 14:23 | 2026-08-07 14:23 |  |  | Fair | No | Phone went unanswered
Outage | J.E.26.08.09891 | C001882106 | Denton Williams | KSAS | Completed | Load_1002854 | Rockfort - 210 | 2026-08-07 12:41 | 2026-08-07 15:12 | 2026-08-07 15:27 | 2026-08-07 15:27 | 2026-08-07 15:27 | 2026-08-07 15:27 | 2026-08-07 15:28 | 2026-08-07 15:28 |  |  | Fair | No | The customer stated that a JPS team visited the area and everything is normal now.
Outage | J.E.26.08.10100 | C001882107 | Derrick Grubb | St.Thomas | Completed | Load_252161 | Good Year - 110 | 2026-08-07 12:43 | 2026-08-07 12:46 | 2026-08-07 14:11 | 2026-08-07 14:12 | 2026-08-07 14:11 | 2026-08-07 14:12 | 2026-08-07 14:12 | 2026-08-07 14:12 |  |  | Fair | No | Premises found okay.
Outage | J.E.26.08.10141 | C001882114 | Denton Williams | Portland | Completed | Load_253854 | Port Antonio - 410 | 2026-08-07 12:44 | 2026-08-07 15:12 | 2026-08-07 15:28 | 2026-08-07 15:29 | 2026-08-07 16:05 | 2026-08-07 16:07 | 2026-08-07 16:09 | 2026-08-07 16:09 | BrokenWire |  | Fair | No | Customer meter socket was defective, upon arrival it was replaced. Reconnect service line using three Penn union sleeves and one 1 bolt clamp.
Non-Outage | J.E.26.08.10099 | C001882115 | Hopeton Henry | St.Thomas | Completed | Load_240330 | Good Year - 210 | 2026-08-07 12:48 | 2026-08-07 12:50 | 2026-08-07 13:43 | 2026-08-07 15:18 | 2026-08-07 15:34 | 2026-08-07 17:34 | 2026-08-07 17:35 | 2026-08-07 17:35 |  |  | Fair | Yes | Change defective service wire 110-112-222 volts
Outage | J.E.26.08.10144 | C001882126 | Antony Levy | KSAS | Completed | Load_268633 | Duhaney - 310 | 2026-08-07 12:50 | 2026-08-07 12:52 | 2026-08-07 14:54 | 2026-08-07 14:55 | 2026-08-07 14:54 | 2026-08-07 14:55 | 2026-08-07 14:55 | 2026-08-07 14:55 |  |  | Fair | No | Internal problem customer has defective breaker.
Outage | J.E.26.08.10151 | C001882127 | Antony Levy | KSAS | Completed | Load_269535 | Duhaney - 310 | 2026-08-07 12:50 | 2026-08-07 12:52 | 2026-08-07 14:19 | 2026-08-07 14:22 | 2026-08-07 14:37 | 2026-08-07 14:47 | 2026-08-07 14:48 | 2026-08-07 14:48 | BrokenWire |  | Fair | No | Internal problem Customer has a defective breaker.
Outage | J.E.26.08.10158 | C001882128 | Rusean Allen | KSAS | Completed | Load_255134 | Cane River - 310 | 2026-08-07 12:53 | 2026-08-07 12:55 | 2026-08-07 15:42 | 2026-08-07 16:28 | 2026-08-07 17:30 | 2026-08-07 18:11 | 2026-08-07 18:11 | 2026-08-07 18:11 |  |  | Fair | No | Transformer found chipped, transformer reset was done.
Outage | J.E.26.08.10161 | C001882129 | Rusean Allen | KSAS | Completed | Load_240840 | Cane River - 310 | 2026-08-07 12:53 | 2026-08-07 12:55 | 2026-08-07 13:10 | 2026-08-07 18:13 | 2026-08-07 18:13 | 2026-08-07 18:14 | 2026-08-07 18:14 | 2026-08-07 18:14 |  |  | Fair | No | Related
Non-Outage | J.E.26.08.09905 | C001882134 | Christopher Edwards | KSAN | Completed | Load_261661 | Constant Spring - 410 | 2026-08-07 12:55 | 2026-08-07 15:24 | 2026-08-07 15:26 | 2026-08-07 15:28 | 2026-08-07 16:11 | 2026-08-07 17:39 | 2026-08-07 17:42 | 2026-08-07 17:42 |  |  | Fair | No | Remake corroded neutral joint Using:(1) one bolt clamps Voltage:113,114,230v
Outage | J.E.26.08.10115 | C001882135 | Neville Spencer | Clarendon | Completed | Load_239897 | May Pen - 110 | 2026-08-07 12:56 | 2026-08-07 15:04 | 2026-08-07 15:35 | 2026-08-07 15:35 | 2026-08-07 16:33 | 2026-08-07 16:53 | 2026-08-07 16:56 | 2026-08-07 16:56 | Fire |  | Fair | No | Found secondary phase and neutral conductor entangled.Cleared bamboo from secondary lines renew blown 3 amp fuse protecting 25 kva xmfr at pole #. 0100915 supply restored.
Outage | J.E.26.08.10096 | C001882137 | Marlon Brown | Trelawny | Completed | Load_240202 | Duncans - 210 | 2026-08-07 12:57 | 2026-08-07 16:15 | 2026-08-07 18:00 | 2026-08-07 18:01 | 2026-08-07 18:36 | 2026-08-07 18:37 | 2026-08-07 18:37 | 2026-08-07 18:37 |  |  | Fair | No | Premises closed l
Outage | J.E.26.08.10147 | C001882136 | Daniel Francis | St.Ann | Completed | Load_268325 | Cardiff Hall - 310 | 2026-08-07 12:57 | 2026-08-07 13:17 | 2026-08-07 14:43 | 2026-08-07 14:43 | 2026-08-07 15:05 | 2026-08-07 15:16 | 2026-08-07 15:17 | 2026-08-07 15:17 |  |  | Fair | No | Found okay 115 114 230 in all internal problems
Outage | J.E.26.08.10039 | C001882146 | Kenroy Dale | Manchester | Completed | Load_251668 | Spur Tree - 310 | 2026-08-07 13:06 | 2026-08-07 15:04 | 2026-08-07 18:41 | 2026-08-07 18:42 | 2026-08-07 19:48 | 2026-08-07 20:56 | 2026-08-07 21:00 | 2026-08-07 21:00 | BrokenWire |  | Fair | No | Open 25 kva transformer to de-bush area in order to splice and retention 2 span of secondary neutral and one span of secondary phase, conductors was splice and retention transformer re-closed and area now with supply
Outage | J.E.26.08.10129 | C001882145 | Kenroy Dale | Manchester | Completed | Load_295289 | Spur Tree - 310 | 2026-08-07 13:06 | 2026-08-07 15:04 | 2026-08-07 15:15 | 2026-08-07 15:27 | 2026-08-07 16:47 | 2026-08-07 17:25 | 2026-08-07 17:26 | 2026-08-07 17:26 | Fire |  | Fair | No | Corroded phase jumper found remade connection using 1 one bolt clamp voltage reading 116/116/232
Outage | J.E.26.08.10154 | C001882147 | Richard Watson | St.Elizabeth | Completed | Load_250259 | Maggotty - 210 | 2026-08-07 13:07 | 2026-08-07 13:08 | 2026-08-07 13:54 | 2026-08-07 13:55 | 2026-08-07 14:21 | 2026-08-07 14:32 | 2026-08-07 14:52 | 2026-08-07 14:52 |  |  | Fair | No | Voltage found inside meter socket 106v,115v, 221v, however meter is single phasing and meter socket defective, customer advised to get electrician to replace meter socket and call back for meter replacement.
Non-Outage | J.E.26.08.10182 | C001882162 | Tyrese Williams |  | Completed |  |  | 2026-08-07 13:20 | 2026-08-07 15:45 | 2026-08-07 17:10 | 2026-08-07 17:10 | 2026-08-07 17:10 | 2026-08-07 17:20 | 2026-08-07 17:22 | 2026-08-07 17:22 | Fire |  | Fair | No | Service wire was disconnected due to customer pothead burnt up customer was advised to get a electrician
Outage | J.E.26.08.10153 | C001882163 | Richard Grant | St.Catherine | Completed | Load_262168 | New Michelton - 210 | 2026-08-07 13:21 | 2026-08-07 13:22 | 2026-08-07 13:28 | 2026-08-07 13:29 | 2026-08-07 14:02 | 2026-08-07 16:47 | 2026-08-07 16:47 | 2026-08-07 16:47 |  |  | Fair | No | Blown 65amps fuse found at junction pole number 0060371 caused by primary phase banging on opened secondary D Iron. 1 pole top lap and 1 post type insulator used to raised and secure phase. 65amps fuse replaced with same and supply restored. Area left okay.
Outage | J.E.26.08.10156 | C001882164 | Richard Grant | St.Catherine | Completed | Load_240447 | New Michelton - 210 | 2026-08-07 13:21 | 2026-08-07 13:22 | 2026-08-07 13:28 | 2026-08-07 16:48 | 2026-08-07 16:47 | 2026-08-07 16:48 | 2026-08-07 16:48 | 2026-08-07 16:48 |  |  | Fair | No | Blown 65amps fuse found at junction pole number 0060371 caused by primary phase banging on opened secondary D Iron. 1 pole top lap and 1 post type insulator used to raised and secure phase. 65amps fuse replaced with same and supply restored. Area left okay.
Outage | J.E.26.08.10080 | C001882165 | Derrick Dawkins | St.James | Completed | Load_260486 | Bogue - 310 | 2026-08-07 13:22 | 2026-08-07 13:25 | 2026-08-07 17:08 | 2026-08-07 17:08 | 2026-08-07 17:36 | 2026-08-07 17:46 | 2026-08-07 17:46 | 2026-08-07 17:46 |  |  | Fair | No | Found junction fuse blown 20 amp replaced 20 amp junction fuse
Outage | J.E.26.08.09876 | C001882168 | Derrick Dawkins | St.James | Completed | Load_555956 | Bogue - 410 | 2026-08-07 13:23 | 2026-08-07 13:25 | 2026-08-07 17:06 | 2026-08-07 17:06 | 2026-08-07 17:06 | 2026-08-07 17:12 | 2026-08-07 17:07 | 2026-08-07 17:07 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.10108 | C001882166 | Horace Malcolm | St.James | Completed | Load_247384 | Queens Drive - 710 | 2026-08-07 13:23 | 2026-08-07 15:35 | 2026-08-07 16:14 | 2026-08-07 16:14 | 2026-08-07 16:49 | 2026-08-07 16:55 | 2026-08-07 16:55 | 2026-08-07 16:55 |  |  | Fair | No | Check and ok supply restored
Outage | J.E.26.08.10159 | C001882167 | Derrick Dawkins | St.James | Completed | Load_555956 | Bogue - 410 | 2026-08-07 13:23 | 2026-08-07 13:25 | 2026-08-07 14:24 | 2026-08-07 14:24 | 2026-08-07 15:56 | 2026-08-07 17:02 | 2026-08-07 17:02 | 2026-08-07 17:02 |  |  | Fair | No | Found 100 kva transformer drop lead burn off due to slack connection open 100/50 kva transformer to carry out repairs clean and remade joint used 6 clamps 2 amp pack 2/0 2/0 voltage left 120/120=208. 240/240=239
Outage | J.E.26.08.10204 | C001882188 | Derrick Dawkins | Hanover | Completed | Load_269526 | Orange Bay - 310 | 2026-08-07 13:47 | 2026-08-07 16:32 | 2026-08-07 18:56 | 2026-08-07 18:57 | 2026-08-07 18:56 | 2026-08-07 19:09 | 2026-08-07 18:57 | 2026-08-07 18:57 |  |  | Fair | No | Premises ok
Non-Outage | J.E.26.08.09811 | C001882205 | Richman Whyte | St.Elizabeth | Completed | Load_245885 | Maggotty - 110 | 2026-08-07 13:54 | 2026-08-07 13:55 | 2026-08-07 14:48 | 2026-08-07 14:48 | 2026-08-07 14:48 | 2026-08-07 14:48 | 2026-08-07 14:49 | 2026-08-07 14:49 |  |  | Fair | No | Open 3 #20 amp junction fuse above underground cable
Outage | J.E.26.08.10224 | C001882211 | Christopher Edwards | KSAN | Completed | Load_301567 | Constant Spring - 310 | 2026-08-07 14:00 | 2026-08-07 14:01 | 2026-08-07 15:19 | 2026-08-07 15:20 | 2026-08-07 15:22 | 2026-08-07 15:24 | 2026-08-07 15:24 | 2026-08-07 15:24 |  | Y | Fair | No | Refuse blown junction Using (1) 20 ampsClear vegetation off primary line
Non-Outage | J.E.26.08.06888 | C001882274 | Rusean Allen | KSAS | Completed | Load_247707 | Hunts Bay - 110 | 2026-08-07 14:49 | 2026-08-07 15:01 | 2026-08-07 15:53 | 2026-08-07 15:54 | 2026-08-07 16:09 | 2026-08-07 16:10 | 2026-08-07 16:10 | 2026-08-07 16:10 |  |  | Fair | No | 1x 10amp fuse found 1x 10amp fuse replaced.
Outage | J.E.26.08.10215 | C001882275 | Hartley Chin | Clarendon | Completed | Load_242818 | Monymusk - 210 | 2026-08-07 14:49 | 2026-08-07 14:51 | 2026-08-07 15:59 | 2026-08-07 15:59 | 2026-08-07 17:32 | 2026-08-07 17:32 | 2026-08-07 17:33 | 2026-08-07 17:33 |  |  | Fair | No | Premises found ok customer lost power due to plan outage.
Outage | J.E.26.08.10050 | C001882288 | Kemark Slue | St.Catherine | Completed | Load_253560 | Tredegar - 310 | 2026-08-07 15:00 | 2026-08-07 15:03 | 2026-08-07 15:20 | 2026-08-07 18:06 | 2026-08-07 18:48 | 2026-08-07 18:00 | 2026-08-07 20:01 | 2026-08-07 20:01 |  |  | Fair | No | Upon arrival at the location the crew discovered that a 25 kva 13.8 kv transformer at pole # 0021482 fuse was blown, further observation revealed that fuse was blown from a surge, refuse link and re-energized circuit.
Outage | J.E.26.08.10232 | C001882289 | Oshane Warren | Westmoreland | Completed | Load_252147 | Paradise - 210 | 2026-08-07 15:00 | 2026-08-07 15:01 | 2026-08-07 20:11 | 2026-08-07 20:11 | 2026-08-07 20:24 | 2026-08-07 20:24 | 2026-08-07 20:25 | 2026-08-07 20:25 |  |  | Fair | No | Unable to locate or contact customer
Non-Outage | J.E.26.08.10265 | C001882291 | Hartley Chin |  | Completed |  |  | 2026-08-07 15:03 | 2026-08-07 15:05 | 2026-08-07 17:33 | 2026-08-07 17:34 | 2026-08-07 18:35 | 2026-08-07 18:36 | 2026-08-07 18:36 | 2026-08-07 18:36 |  |  | Fair | No | Area found ok but exact Prem not found and unable to contact customer number in report.
Outage | J.E.26.08.10283 | C001882290 | Hartley Chin | Clarendon | Completed | Load_242961 | Parnassus - 210 | 2026-08-07 15:03 | 2026-08-07 15:04 | 2026-08-07 18:37 | 2026-08-07 18:37 | 2026-08-07 20:42 | 2026-08-07 21:04 | 2026-08-07 21:05 | 2026-08-07 21:05 |  |  | Fair | No | Unable to contact customer, meter found 113v 112v 225v at meter
Outage | J.E.26.08.10263 | C001882297 | Neville Spencer | Clarendon | Completed | Load_255475 | May Pen - 110 | 2026-08-07 15:04 | 2026-08-07 15:05 | 2026-08-07 16:57 | 2026-08-07 16:57 | 2026-08-07 18:34 | 2026-08-07 19:11 | 2026-08-07 19:14 | 2026-08-07 19:14 | BrokenWire |  | Fair | No | Remove defective 3, wire customer needs to carry out repair advise .
Outage | J.E.26.08.10253 | C001882298 | Kemark Slue | St.Catherine | Completed | Load_568828 | Twickenham - 310 | 2026-08-07 15:06 | 2026-08-07 15:06 | 2026-08-07 18:57 | 2026-08-07 20:02 | 2026-08-07 20:02 | 2026-08-07 18:51 | 2026-08-07 20:03 | 2026-08-07 20:03 | BrokenWire |  | Fair | No | Upon arrival at the location the crew discovered that customer’s is supplied from an enclosure please refer to Moses Elliston to effectively carry out repairs.
Outage | J.E.26.08.10198 | C001882312 | Denton Williams | Portland | Completed | Load_256253 | Port Antonio - 310 | 2026-08-07 15:10 | 2026-08-07 15:11 | 2026-08-07 16:14 | 2026-08-07 16:15 | 2026-08-07 16:15 | 2026-08-07 16:16 | 2026-08-07 16:18 | 2026-08-07 16:18 |  |  | Fair | No | Customer was wrongfully disconnected. JPS escalation team was contacted and customer was reconnected, customer also confirmed that their electrical supply is back.
Outage | J.E.26.08.10292 | C001882311 | Denton Williams | Portland | Completed | Load_265158 | Port Antonio - 310 | 2026-08-07 15:10 | 2026-08-07 15:11 | 2026-08-07 16:18 | 2026-08-07 16:19 | 2026-08-07 16:56 | 2026-08-07 17:35 | 2026-08-07 17:37 | 2026-08-07 17:37 |  |  | Fair | No | Corrosion at 10kva transformer drop leads. Use three one bolt clamp to correct corrosion. Voltage readings leave 120v, 120v and 241v.
Outage | J.E.26.08.10288 | C001882327 | Rusean Allen | KSAS | Completed | Load_259161 | Cane River - 410 | 2026-08-07 15:16 | 2026-08-07 15:17 | 2026-08-07 16:12 | 2026-08-07 16:12 | 2026-08-07 16:24 | 2026-08-07 16:26 | 2026-08-07 16:26 | 2026-08-07 16:26 |  |  | Fair | No | Meter was reconnected by customer service
Non-Outage | J.E.26.08.06921 | C001882337 | Eric Williams | KSAN | Completed | Load_569029 | Washington Blvd - 710 | 2026-08-07 15:21 | 2026-08-07 17:51 | 2026-08-07 19:57 | 2026-08-07 19:58 | 2026-08-07 20:22 | 2026-08-07 20:22 | 2026-08-07 20:27 | 2026-08-07 20:27 |  |  | Fair | No | Voltage check this evening at 4:38pm ( voltage readings 407v,406,406,237,237,236volts) reading check again at 8:20pm (418,417,417,241,240,240volts) follow up checks needed during the day time
Outage | J.E.26.08.09140 | C001882347 | Derrick Dawkins | St.James | Completed | Load_244286 | Bogue - 310 | 2026-08-07 15:32 | 2026-08-07 15:38 | 2026-08-07 17:59 | 2026-08-07 17:59 | 2026-08-07 18:55 | 2026-08-07 18:59 | 2026-08-07 18:56 | 2026-08-07 18:56 |  |  | Fair | No | Can’t locate
Outage | J.E.26.08.10146 | C001882348 | Kenroy Dale | Manchester | Completed | Load_294267 | Spur Tree - 210 | 2026-08-07 15:32 | 2026-08-07 15:36 | 2026-08-07 17:27 | 2026-08-07 17:30 | 2026-08-07 18:12 | 2026-08-07 18:40 | 2026-08-07 18:41 | 2026-08-07 18:41 |  |  | Fair | No | Blown 3 amp fuse found for 25 kva transformer line patrol nothing found blown fuse was replaced and area now with supply
Outage | J.E.26.08.10225 | C001882346 | Derrick Dawkins | St.James | Completed | Load_569876 | Bogue - 310 | 2026-08-07 15:32 | 2026-08-07 15:38 | 2026-08-07 17:52 | 2026-08-07 17:53 | 2026-08-07 17:52 | 2026-08-07 17:58 | 2026-08-07 17:53 | 2026-08-07 17:53 |  |  | Fair | No | Premises ok
Non-Outage | J.E.26.06.34585 | C001882358 | Damion Reid | Manchester | Completed | Load_264563 | Kendal - 210 | 2026-08-07 15:34 | 2026-08-07 15:36 | 2026-08-07 20:13 | 2026-08-07 20:13 | 2026-08-07 20:23 | 2026-08-07 20:53 | 2026-08-07 20:54 | 2026-08-07 20:54 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.09887 | C001882354 | Horace Malcolm | St.James | Completed | Load_241478 | Queens Drive - 810 | 2026-08-07 15:34 | 2026-08-07 15:37 | 2026-08-07 15:49 | 2026-08-07 15:50 | 2026-08-07 15:53 | 2026-08-07 16:13 | 2026-08-07 16:13 | 2026-08-07 16:13 |  |  | Fair | No | Check and found area ok supply restored
Outage | J.E.26.08.10040 | C001882353 | Horace Malcolm | St.James | Completed | Load_293424 | Queens Drive - 310 | 2026-08-07 15:34 | 2026-08-07 15:37 | 2026-08-07 16:56 | 2026-08-07 16:57 | 2026-08-07 17:32 | 2026-08-07 19:22 | 2026-08-07 19:22 | 2026-08-07 19:22 |  |  | Fair | No | Refused 15kva transformer used one 1amp fuse
Outage | J.E.26.08.10118 | C001882355 | Rodclif Dawkins | Portmore | Completed | Load_260070 | Naggo Head - 610 | 2026-08-07 15:34 | 2026-08-07 15:36 | 2026-08-07 17:57 | 2026-08-07 19:37 | 2026-08-07 19:56 | 2026-08-07 19:58 | 2026-08-07 19:58 | 2026-08-07 19:58 |  |  | Fair | No | Directions not clear. Calls to number went to voicemail
Outage | J.E.26.08.10155 | C001882356 | Rodclif Dawkins | Portmore | Completed | Load_576149 | Naggo Head - 610 | 2026-08-07 15:34 | 2026-08-07 15:35 | 2026-08-07 17:57 | 2026-08-07 17:58 | 2026-08-07 18:42 | 2026-08-07 19:32 | 2026-08-07 19:34 | 2026-08-07 19:34 | BrokenWire |  | Fair | No | Found triplex with broken phase, running through tree. Tree limbs around service wire removed. Using 1 penunion service restored
Non-Outage | J.E.26.08.08088 | C001882360 | Damion Reid | Manchester | Completed | Load_242926 | Kendal - 210 | 2026-08-07 15:35 | 2026-08-07 15:36 | 2026-08-07 17:39 | 2026-08-07 17:39 | 2026-08-07 18:12 | 2026-08-07 19:54 | 2026-08-07 20:05 | 2026-08-07 20:05 |  |  | Fair | No | Defective secondary neutral conductor found cause by contamination open 25kva transformer fuse link replace defective conductor using 80ft of #2 aluminum conductor two one bolt clamp and restore power voltage reading at meter socket before correction phase to neutral 143v-97v across phase 235v after correction phase to neutral at meter 117v-116v across phase 235v
Outage | J.E.26.08.06700 | C001882375 | Selvin White | St.Elizabeth | Completed | Load_259624 | Maggotty - 110 | 2026-08-07 15:39 | 2026-08-07 15:42 | 2026-08-07 16:08 | 2026-08-07 16:09 | 2026-08-07 17:09 | 2026-08-07 17:24 | 2026-08-07 17:24 | 2026-08-07 17:24 |  |  | Rains | No | Re- install approximately 50 ft of number six triplex service wire that was damaged and removed after the recent hurricane. Supply restored with voltage readings left inside customer’s meter socket of 232,115,117 volts.
Non-Outage | J.E.26.05.06499 | C001882376 | Selvin White | St.Elizabeth | Completed | Load_267210 | Maggotty - 110 | 2026-08-07 15:40 | 2026-08-07 15:42 | 2026-08-07 17:30 | 2026-08-07 17:31 | 2026-08-07 17:59 | 2026-08-07 18:05 | 2026-08-07 18:06 | 2026-08-07 18:06 |  |  | Fair | No | Customers premises was damaged during the recent hurricane and currently has no power but customer says.bill is still being sent to her. Please advise C Johnson at the field service department as customer premises is being repaired .
Non-Outage | J.E.26.08.10184 | C001882377 | Selvin White |  | Completed |  |  | 2026-08-07 15:40 | 2026-08-07 15:42 | 2026-08-07 20:06 | 2026-08-07 20:07 | 2026-08-07 21:19 | 2026-08-07 21:37 | 2026-08-07 21:37 | 2026-08-07 21:37 |  |  | Fair | No | Customer cannot be contacted or located however the escalation department was contacted and said meter was not assigned so please refer to C.Johnson so arrangements can be made for inspection of customer’s premises to assign meter. RAMI system.
Non-Outage | J.E.26.08.08128 | C001882378 | Selvin White | St.Elizabeth | Completed | Load_259615 | Maggotty - 110 | 2026-08-07 15:41 | 2026-08-07 15:42 | 2026-08-07 18:06 | 2026-08-07 18:07 | 2026-08-07 18:27 | 2026-08-07 19:39 | 2026-08-07 19:40 | 2026-08-07 19:40 |  |  | Rains | No | Voltage readings found at location are 230,225,229,392,401,394 volts . Tap up three 25 KVA transformers from 3 to tap 5. Voltage readings after tap up are 240,239,238,407,417,408 volts. Voltage is low due to damage voltage regulators at West St.
Outage | J.E.26.08.10212 | C001882379 | Daniel Francis | St.Ann | Completed | Load_249221 | Cardiff Hall - 310 | 2026-08-07 15:42 | 2026-08-08 08:02 | 2026-08-08 10:58 | 2026-08-08 10:58 | 2026-08-08 11:37 | 2026-08-08 11:46 | 2026-08-08 11:56 | 2026-08-08 11:56 |  |  | Fair | No | Found okay 114 115 230 in all
Non-Outage | J.E.26.07.05203 | C001882380 | Selvin White | St.Elizabeth | Completed | Load_266017 | Maggotty - 110 | 2026-08-07 15:43 | 2026-08-07 15:44 | 2026-08-07 17:27 | 2026-08-07 19:40 | 2026-08-07 20:00 | 2026-08-07 20:05 | 2026-08-07 20:05 | 2026-08-07 20:05 |  |  | Rains | No | Customer is having low voltage due to some voltage regulators that were damaged at West St.during the recent hurricane that needs to be replaced. The maintenance department is aware of the situation.
Non-Outage | J.E.26.07.33428 | C001882386 | Raheem Ricketts | St.Elizabeth | Completed | Load_250190 | Maggotty - 110 | 2026-08-07 15:45 | 2026-08-07 15:52 | 2026-08-07 15:56 | 2026-08-07 17:06 | 2026-08-07 17:30 | 2026-08-07 17:37 | 2026-08-07 17:37 | 2026-08-07 17:37 |  |  | Fair | No | Check and found okay
Outage | J.E.26.08.10043 | C001882393 | Marlon Brown | Trelawny | Completed | Load_243995 | Greenwood - 110 | 2026-08-07 15:46 | 2026-08-07 16:14 | 2026-08-07 16:28 | 2026-08-07 16:28 | 2026-08-07 17:42 | 2026-08-07 17:59 | 2026-08-07 17:59 | 2026-08-07 17:59 |  |  | Fair | No | Refer to Field Service Department as call center representative is unable to reset due box number 5320 is not added to the application hence unable to communicate.
Non-Outage | J.E.26.06.29772 | C001882397 | Raheem Ricketts | Manchester | Completed | Load_302752 | Spur Tree - 210 | 2026-08-07 15:48 | 2026-08-07 15:51 | 2026-08-07 15:56 | 2026-08-07 20:08 | 2026-08-07 20:47 | 2026-08-07 20:49 | 2026-08-07 20:49 | 2026-08-07 20:49 |  |  | Fair | No | Open 25kva to change transformer neutral clamp at jumper and reclosed 25kva
Non-Outage | J.E.26.06.33888 | C001882398 | Raheem Ricketts | Manchester | Completed | Load_247548 | Spur Tree - 210 | 2026-08-07 15:48 | 2026-08-07 15:51 | 2026-08-07 15:56 | 2026-08-07 16:24 | 2026-08-07 16:42 | 2026-08-07 16:57 | 2026-08-07 16:57 | 2026-08-07 16:57 |  |  | Fair | No | Check and found 1leg of customer service wire burn at pole use one clamp to remake joint at pole
Non-Outage | J.E.26.07.02870 | C001882396 | Raheem Ricketts | Manchester | Completed | Load_302733 | Spur Tree - 210 | 2026-08-07 15:48 | 2026-08-07 15:51 | 2026-08-07 15:56 | 2026-08-07 20:04 | 2026-08-07 20:03 | 2026-08-07 20:04 | 2026-08-07 20:04 | 2026-08-07 20:04 |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.07.31189 | C001882395 | Raheem Ricketts | Manchester | Completed | Load_261304 | Spur Tree - 210 | 2026-08-07 15:48 | 2026-08-07 15:51 | 2026-08-07 15:56 | 2026-08-07 18:24 | 2026-08-07 19:14 | 2026-08-07 20:03 | 2026-08-07 20:03 | 2026-08-07 20:03 |  |  | Fair | No | Check and found customer experiencing 1 leg remake joint at pole using one clamp
Non-Outage | J.E.26.03.02475 | C001882410 | Wayne Dillion | Manchester | Completed | Load_302870 | Spur Tree - 210 | 2026-08-07 15:49 | 2026-08-07 15:51 | 2026-08-07 17:04 | 2026-08-07 17:04 | 2026-08-07 17:32 | 2026-08-07 17:40 | 2026-08-07 17:43 | 2026-08-07 17:43 |  |  | Fair | No | Supply check and found customer experiencing low voltage. Voltage check at transformer is 109v, 109v. Isolate 25kva transformer no pole # to tap to tap 4. Close same and supply leave working okay reading left is 113v, 112v and cross phase 225volts.
Non-Outage | J.E.26.08.09989 | C001882406 | Marlon Brown |  | Completed |  |  | 2026-08-07 15:49 | 2026-08-07 15:59 | 2026-08-07 16:09 | 2026-08-07 16:09 | 2026-08-07 16:18 | 2026-08-07 16:18 | 2026-08-07 16:18 | 2026-08-07 16:18 |  |  | Fair | No | Unable to locate customer via telephone nor direction
Non-Outage | J.E.26.07.06471 | C001882416 | Raheem Ricketts | Manchester | Completed | Load_249470 | Spur Tree - 210 | 2026-08-07 15:52 | 2026-08-07 15:53 | 2026-08-07 15:56 | 2026-08-07 20:50 | 2026-08-07 20:50 | 2026-08-07 20:50 | 2026-08-07 20:51 | 2026-08-07 20:51 |  |  | Fair | No | Unable to locate customer cell phone wrong several times straight voicemail
Non-Outage | J.E.26.07.23993 | C001882415 | Raheem Ricketts | Manchester | Completed | Load_240892 | Spur Tree - 210 | 2026-08-07 15:52 | 2026-08-07 15:53 | 2026-08-07 15:56 | 2026-08-07 20:05 | 2026-08-07 20:04 | 2026-08-07 20:05 | 2026-08-07 20:05 | 2026-08-07 20:05 |  |  | Fair | No | Check and found okay call related
Non-Outage | J.E.26.07.31564 | C001882413 | Raheem Ricketts | Manchester | Completed | Load_302792 | Spur Tree - 210 | 2026-08-07 15:52 | 2026-08-07 15:53 | 2026-08-07 15:56 | 2026-08-07 18:05 | 2026-08-07 18:05 | 2026-08-07 18:05 | 2026-08-07 18:06 | 2026-08-07 18:06 |  |  | Fair | No | Unable to locate customer cell phone went straight voicemail
Non-Outage | J.E.26.07.33058 | C001882414 | Raheem Ricketts | Manchester | Completed | Load_302792 | Spur Tree - 210 | 2026-08-07 15:52 | 2026-08-07 15:53 | 2026-08-07 15:56 | 2026-08-07 18:10 | 2026-08-07 18:10 | 2026-08-07 18:10 | 2026-08-07 18:11 | 2026-08-07 18:11 |  |  | Fair | No
Non-Outage | J.E.26.08.04988 | C001882411 | Raheem Ricketts | Manchester | Completed | Load_251009 | Spur Tree - 210 | 2026-08-07 15:52 | 2026-08-07 15:53 | 2026-08-07 15:56 | 2026-08-07 18:03 | 2026-08-07 18:03 | 2026-08-07 18:03 | 2026-08-07 18:03 | 2026-08-07 18:03 |  |  | Fair | No | Call related to meter call
Non-Outage | J.E.26.08.10234 | C001882412 | Raheem Ricketts | Manchester | Completed | Load_241153 | Spur Tree - 210 | 2026-08-07 15:52 | 2026-08-07 15:53 | 2026-08-07 15:56 | 2026-08-07 17:39 | 2026-08-07 17:59 | 2026-08-07 18:00 | 2026-08-07 18:00 | 2026-08-07 18:00 |  |  | Fair | No | Check and found customer meter burn meter # 2711609
Non-Outage | J.E.26.07.00212 | C001882417 | Raheem Ricketts | Manchester | Completed | Load_256355 | Spur Tree - 210 | 2026-08-07 15:53 | 2026-08-07 15:54 | 2026-08-07 18:00 | 2026-08-07 18:01 | 2026-08-07 18:00 | 2026-08-07 18:01 | 2026-08-07 18:01 | 2026-08-07 18:01 |  |  | Fair | No | Problem has been solved
Non-Outage | J.E.26.08.05377 | C001882427 | Michael Paterson | Westmoreland | Completed | Load_241436 | Paradise - 310 | 2026-08-07 15:59 | 2026-08-07 16:03 |  | 2026-08-07 16:22 | 2026-08-07 16:22 | 2026-08-07 16:23 | 2026-08-07 16:44 | 2026-08-07 16:44 |  |  | Fair | No | Unable to locate customer not responding to phone calls
Outage | J.E.26.08.10350 | C001882442 | Marlon Brown | Trelawny | Completed | Load_247755 | Martha Brae - 210 | 2026-08-07 16:05 | 2026-08-07 16:06 | 2026-08-07 16:18 | 2026-08-07 16:19 | 2026-08-07 16:18 | 2026-08-07 16:26 | 2026-08-07 16:26 | 2026-08-07 16:26 |  |  | Fair | No | Unable to locate customer via telephone nor direction, person doesn’t have this number anymore.
Outage | J.E.26.08.10367 | C001882459 | Kemark Slue | St.Catherine | Completed | Load_253743 | Twickenham - 310 | 2026-08-07 16:21 | 2026-08-07 16:21 | 2026-08-07 19:43 | 2026-08-07 20:04 | 2026-08-07 20:03 | 2026-08-07 19:04 | 2026-08-07 20:10 | 2026-08-07 20:10 |  |  | Fair | No | Upon arrival at the location the crew discovered that the landlady had paid on the wrong account as the premises is consisting of two meters, customer was advised to contact the customer care or use the my JPS app to reversed the payment.
Outage | J.E.26.08.10294 | C001882468 | Dean- Smith | Hanover | Completed | Load_257747 | Orange Bay - 310 | 2026-08-07 16:27 | 2026-08-07 16:31 | 2026-08-07 17:26 | 2026-08-07 17:27 | 2026-08-07 18:10 | 2026-08-07 18:10 | 2026-08-07 18:45 | 2026-08-07 18:45 |  |  | Rains | No | Replace 5amp 50kva transformer fuse. Pole number n/a
Outage | J.E.26.08.10317 | C001882467 | Dean- Smith | Hanover | Completed | Load_266822 | Orange Bay - 310 | 2026-08-07 16:27 | 2026-08-07 16:31 | 2026-08-07 18:45 | 2026-08-07 18:46 | 2026-08-07 20:51 | 2026-08-07 20:55 | 2026-08-07 20:56 | 2026-08-07 20:56 |  |  | Rains | No | Check and found ok
Outage | J.E.26.08.10355 | C001882484 | Stephen Taylor | St.Thomas | Completed | Load_237781 | Good Year - 110 | 2026-08-07 16:34 | 2026-08-07 16:35 | 2026-08-07 18:46 | 2026-08-07 18:47 | 2026-08-07 18:46 | 2026-08-07 18:47 | 2026-08-07 18:47 | 2026-08-07 18:47 |  |  | Fair | No | The jps maintenance team are in the area working
Outage | J.E.26.08.10370 | C001882486 | Stephen Taylor | St.Thomas | Completed | Load_251845 | Lysson - 410 | 2026-08-07 16:34 | 2026-08-07 16:35 | 2026-08-07 16:56 | 2026-08-07 16:56 | 2026-08-07 18:24 | 2026-08-07 18:24 | 2026-08-07 18:27 | 2026-08-07 18:27 |  |  | Fair | No | Splice and retention services wire 45 feet 3 clamps customer is now okay
Outage | J.E.26.08.10208 | C001882487 | Romaine Roberts | St.Mary | Completed | Load_353347 | Oracabessa - 210 | 2026-08-07 16:35 | 2026-08-07 16:36 | 2026-08-07 19:55 | 2026-08-07 19:55 | 2026-08-07 20:26 | 2026-08-07 20:37 | 2026-08-07 20:37 | 2026-08-07 20:37 | BrokenWire |  | Fair | No | Cannot reach customer after several attempts caller phone number not reachable
Outage | J.E.26.08.10318 | C001882489 | Rusean Allen | KSAN | Completed | Load_265123 | Hope - 510 | 2026-08-07 16:35 | 2026-08-07 17:41 | 2026-08-07 18:12 | 2026-08-07 18:15 | 2026-08-07 18:16 | 2026-08-07 18:17 | 2026-08-07 18:17 | 2026-08-07 18:17 |  |  | Fair | No | Related to chipped transformer
Outage | J.E.26.08.10319 | C001882490 | Eric Williams | KSAN | Completed | Load_253684 | Constant Spring - 210 | 2026-08-07 16:36 | 2026-08-07 16:37 | 2026-08-07 18:20 | 2026-08-07 18:21 | 2026-08-07 18:44 | 2026-08-07 19:51 | 2026-08-07 19:57 | 2026-08-07 19:57 |  |  | Fair | No | 3 wire open secondary broken phase cause by tree cutting by contractor, use 70 feet 2/0 AA, 2 2/0 splicing sleeve,
Non-Outage | J.E.26.08.09708 | C001882493 | Roxroy Needham | St.Ann | Completed | Load_304934 | Cardiff Hall - 310 | 2026-08-07 16:47 | 2026-08-07 16:48 | 2026-08-07 17:40 | 2026-08-07 17:41 | 2026-08-07 18:12 | 2026-08-07 18:15 | 2026-08-07 18:17 | 2026-08-07 18:17 |  |  | Fair | No | Premises found ok customer have internal problem meter box defective voltage left at meter 117-118-239
Non-Outage | J.E.26.08.09740 | C001882494 | Roxroy Needham | St.Ann | Completed | Load_262327 | Cardiff Hall - 310 | 2026-08-07 16:47 | 2026-08-07 16:48 | 2026-08-07 19:18 | 2026-08-07 19:25 | 2026-08-07 20:58 | 2026-08-07 21:12 | 2026-08-07 21:12 | 2026-08-07 21:12 |  | Y | Fair | No | Remake joint at pole used 2 pg clamp voltage left at meter 114-113-229
Non-Outage | J.E.26.08.09937 | C001882495 | Roxroy Needham | St.Ann | Completed | Load_251950 | Cardiff Hall - 310 | 2026-08-07 16:48 | 2026-08-07 16:48 | 2026-08-07 18:17 | 2026-08-07 18:18 | 2026-08-07 19:02 | 2026-08-07 19:13 | 2026-08-07 19:14 | 2026-08-07 19:14 |  |  | Fair | No | Remake joint at pole and pothead used 4 pg clamp voltage left at meter 113-112-219
Non-Outage | J.E.26.08.08558 | C001882497 | Omar King | St.Ann | Completed | Load_257680 | Ocho Rios - 310 | 2026-08-07 16:50 | 2026-08-08 08:01 | 2026-08-08 08:21 | 2026-08-08 08:53 | 2026-08-08 09:35 | 2026-08-08 09:38 | 2026-08-08 09:39 | 2026-08-08 09:39 |  |  | Fair | No | On arrival at the location and do a voltage reading I observed that problem as been resolved
Outage | J.E.26.08.10385 | C001882500 | Damion Reid | Manchester | Completed | Load_268999 | Kendal - 210 | 2026-08-07 16:56 | 2026-08-07 16:57 | 2026-08-07 20:55 | 2026-08-07 20:55 | 2026-08-07 21:56 | 2026-08-07 22:45 | 2026-08-07 22:46 | 2026-08-07 22:46 | Fire |  | Fair | No | Area found ok no spark found at location
Outage | J.E.26.08.10401 | C001882506 | Kenroy Dale | Manchester | Completed | Load_269342 | Porus - 310 | 2026-08-07 17:01 | 2026-08-07 17:39 | 2026-08-07 21:01 | 2026-08-07 21:01 | 2026-08-07 21:52 | 2026-08-07 22:34 | 2026-08-07 22:40 | 2026-08-07 22:40 |  |  | Fair | No | Blown 20 amp junction and 3 amp transformer fuse found line patrol 1 span of secondary neutral found broken resident also inform that saw man cut tree on line. Conductor was splice and retention Blown fuses was replaced and area now with supply
Non-Outage | J.E.26.08.10363 | C001882511 | Michael Paterson | Westmoreland | Completed | Load_249240 | Paradise - 210 | 2026-08-07 17:13 | 2026-08-07 17:16 |  | 2026-08-07 17:27 | 2026-08-07 19:23 | 2026-08-07 19:34 | 2026-08-07 19:34 | 2026-08-07 19:34 | BrokenWire |  | Fair | No | Assessment done at location, confirm customer has power, however, meter and test switch box rotten and fall from pole, please refer to Mr. Clinton Johnson at paradise, urgent attention needed.
Outage | J.E.26.08.10396 | C001882519 | Kemark Slue | St.Catherine | Completed | Load_257011 | Tredegar - 210 | 2026-08-07 17:17 | 2026-08-07 18:13 | 2026-08-07 19:52 | 2026-08-07 20:11 | 2026-08-07 21:34 | 2026-08-07 20:00 | 2026-08-07 21:35 | 2026-08-07 21:35 |  |  | Fair | No | Premises was checked and found okay.
Outage | J.E.26.08.09965 | C001882548 | Ricky Hall | St.Catherine | Completed | Load_302341 | New Michelton - 310 | 2026-08-07 18:07 | 2026-08-08 07:57 | 2026-08-08 08:07 | 2026-08-08 08:20 | 2026-08-08 10:06 | 2026-08-08 10:53 | 2026-08-08 10:54 | 2026-08-08 10:54 | BrokenWire |  | Fair | No | Splice and reconnect 2 w service use 10’#6 duplex 2 clamps 117
Outage | J.E.26.08.10478 | C001882554 | Horace Malcolm | St.James | Completed | Load_249760 | Queens Drive - 310 | 2026-08-07 18:24 | 2026-08-07 18:26 | 2026-08-07 20:14 | 2026-08-07 20:14 | 2026-08-07 20:27 | 2026-08-07 20:33 | 2026-08-07 20:33 | 2026-08-07 20:33 |  |  | Fair | No | Refused one 100 kva transformer used one 10amp fuse
Outage | J.E.26.08.09925 | C001882558 | Rusean Allen | KSAS | Completed | Load_261838 | Hunts Bay - 210 | 2026-08-07 18:34 | 2026-08-07 18:35 | 2026-08-07 20:52 | 2026-08-07 20:52 | 2026-08-07 21:14 | 2026-08-07 22:08 | 2026-08-07 22:08 | 2026-08-07 22:08 |  |  | Fair | No | Wires were reconnected at pothead, using one bolt clamps.Voltage: 117 117 210 235 237 239
Outage | J.E.26.08.10392 | C001882560 | Stephen Taylor | St.Thomas | Completed | Load_259414 | Good Year - 210 | 2026-08-07 18:35 | 2026-08-07 18:36 | 2026-08-07 19:30 | 2026-08-07 19:31 | 2026-08-07 20:04 | 2026-08-07 20:05 | 2026-08-07 20:06 | 2026-08-07 20:06 |  |  | Fair | No | Premise found okay customer said breaker was reset and okay now
Outage | J.E.26.08.10479 | C001882559 | Stephen Taylor | St.Thomas | Completed | Load_262336 | Good Year - 110 | 2026-08-07 18:35 | 2026-08-07 18:36 | 2026-08-07 21:12 | 2026-08-07 21:12 | 2026-08-08 10:49 | 2026-08-08 10:50 | 2026-08-08 11:08 | 2026-08-08 11:08 |  |  | Rains | No | See transformer link down no number on pole patrol see nothing a close up back 25 amp transformer all customer is now okay
Outage | J.E.26.08.10353 | C001882568 | Horace Malcolm | St.James | Completed | Load_266140 | Queens Drive - 710 | 2026-08-07 18:49 | 2026-08-07 18:52 | 2026-08-08 07:58 | 2026-08-08 07:59 | 2026-08-08 07:59 | 2026-08-08 08:00 | 2026-08-08 08:00 | 2026-08-08 08:00 |  |  | Fair | No | Check and found ok supply restored
Outage | J.E.26.08.10361 | C001882569 | Horace Malcolm | St.James | Completed | Load_260146 | Queens Drive - 710 | 2026-08-07 18:49 | 2026-08-07 18:52 | 2026-08-08 08:08 | 2026-08-08 08:09 | 2026-08-08 08:08 | 2026-08-08 08:10 | 2026-08-08 08:10 | 2026-08-08 08:10 |  |  | Fair | No | Unable to locate customer or premises no directions given call to customer phone number not in service
Outage | J.E.26.08.10409 | C001882570 | Horace Malcolm | St.James | Completed | Load_570263 | Queens Drive - 810 | 2026-08-07 18:50 | 2026-08-07 18:52 | 2026-08-07 20:33 | 2026-08-07 20:34 | 2026-08-07 20:42 | 2026-08-07 21:08 | 2026-08-07 21:08 | 2026-08-07 21:08 |  |  | Fair | No | Refused one 8amp junction fuse comple have 6 defective junction switch need replacement
Outage | J.E.26.08.10471 | C001882573 | Rodclif Dawkins | Portmore | Completed | Load_248680 | Naggo Head - 510 | 2026-08-07 18:54 | 2026-08-07 18:55 | 2026-08-07 19:59 | 2026-08-07 19:59 | 2026-08-07 20:16 | 2026-08-07 20:16 | 2026-08-07 20:25 | 2026-08-07 20:25 | LeakingTransformer |  | Fair | No | Crew observed 25kva transformer leaking at the lower brim of transformer. Please refer to maintenance. Second right turn in silver stone. Second transformer circuit.
Outage | J.E.26.08.10407 | C001882577 | Denton Williams | Portland | Completed | Load_263058 | Port Antonio - 410 | 2026-08-07 19:13 | 2026-08-07 19:14 | 2026-08-07 20:31 | 2026-08-07 20:31 | 2026-08-07 20:31 | 2026-08-07 20:31 | 2026-08-07 20:36 | 2026-08-07 20:36 |  |  | Fair | No | Digicel customer service stated that power is at the site
Outage | J.E.26.08.10531 | C001882580 | Cliton Henry | St.Mary | Completed | Load_251308 | Oracabessa - 110 | 2026-08-07 19:14 | 2026-08-08 08:40 | 2026-08-08 08:48 | 2026-08-08 08:48 | 2026-08-08 09:37 | 2026-08-08 09:59 | 2026-08-08 10:02 | 2026-08-08 10:02 | Fire |  | Fair | No | A single phase condition found was reconnected using 1- one bolt clamp at pole. Voltages left were 11-113/225 volts.
Outage | J.E.26.08.10557 | C001882591 | Horace Malcolm | St.James | Completed | Load_249281 | Queens Drive - 310 | 2026-08-07 19:53 | 2026-08-07 20:57 | 2026-08-07 21:10 | 2026-08-07 22:18 | 2026-08-07 22:24 | 2026-08-07 22:55 | 2026-08-07 22:55 | 2026-08-07 22:55 |  |  | Fair | No | Reconnect burnt off transformer nuetral drop lead clamp used one clamp voltage 115-117-232
Outage | J.E.26.08.10522 | C001882594 | Kemark Slue | St.Catherine | Completed | Load_260095 | Twickenham - 310 | 2026-08-07 20:02 | 2026-08-07 20:02 | 2026-08-07 21:34 | 2026-08-07 21:36 | 2026-08-07 21:50 | 2026-08-07 21:02 | 2026-08-07 21:53 | 2026-08-07 21:53 | LeaningPole |  | Fair | No | Unable to locate premises due to inadequate directions and all calls to number given were unsuccessful.
Outage | J.E.26.08.10441 | C001882595 | Hartley Chin | Clarendon | Completed | Load_250052 | Parnassus - 210 | 2026-08-07 20:03 | 2026-08-07 20:03 | 2026-08-07 21:05 | 2026-08-07 21:06 | 2026-08-07 22:17 | 2026-08-07 22:42 | 2026-08-07 22:43 | 2026-08-07 22:43 |  |  | Fair | No | Require day light attention premises close meter center inside and pothead unreachable
Outage | J.E.26.08.10554 | C001882600 | Oshane Warren | Westmoreland | Completed | Load_265324 | Paradise - 210 | 2026-08-07 20:37 | 2026-08-07 20:38 | 2026-08-07 20:42 | 2026-08-07 20:43 | 2026-08-07 22:12 | 2026-08-07 22:39 | 2026-08-07 22:39 | 2026-08-07 22:39 |  |  | Fair | No | Replace 3 amp 25 kva transformer fuse
Non-Outage | J.E.26.08.05405 | C001882603 | Dean- Smith | Hanover | Completed | Load_252795 | Orange Bay - 310 | 2026-08-07 20:56 | 2026-08-07 20:58 | 2026-08-07 23:01 | 2026-08-07 23:02 | 2026-08-07 23:01 | 2026-08-07 23:01 | 2026-08-07 23:02 | 2026-08-07 23:02 |  |  | Fair | No | Shift ended
Non-Outage | J.E.26.08.08680 | C001882604 | Dean- Smith | Hanover | Completed | Load_292847 | Orange Bay - 310 | 2026-08-07 20:57 | 2026-08-07 20:58 | 2026-08-07 21:05 | 2026-08-07 21:05 | 2026-08-07 22:56 | 2026-08-07 22:56 | 2026-08-07 23:01 | 2026-08-07 23:01 |  |  | Fair | No | Transformer was on fire; Defective 50kva transformer, same that was replaced recently. Please forward to maintenance dept ,bring 4/0 or 2/0 copper/clamps when going to the location.
Non-Outage | J.E.26.08.10229 | C001882613 | Raymond Lewis |  | Completed |  |  | 2026-08-07 21:34 | 2026-08-07 23:17 | 2026-08-07 23:32 | 2026-08-07 23:33 | 2026-08-07 23:54 | 2026-08-07 23:57 | 2026-08-07 23:58 | 2026-08-07 23:58 | BrokenWire |  | Fair | No | Customer said it was an internal issue
Non-Outage | J.E.26.08.10270 | C001882611 | Raymond Lewis |  | Completed |  |  | 2026-08-07 21:34 | 2026-08-07 23:17 | 2026-08-08 01:20 | 2026-08-08 01:20 | 2026-08-08 02:23 | 2026-08-08 15:27 | 2026-08-08 02:29 | 2026-08-08 02:29 | BrokenWire |  | Fair | No | Supply restored
Non-Outage | J.E.26.08.10275 | C001882610 | Tyrese Williams |  | Completed |  |  | 2026-08-07 21:34 | 2026-08-07 21:35 | 2026-08-07 21:46 | 2026-08-07 21:47 | 2026-08-07 21:47 | 2026-08-07 21:51 | 2026-08-07 21:51 | 2026-08-07 21:51 | BrokenWire |  | Fair | No | Call isn’t for st. Ann team customer is from Kingston
Non-Outage | J.E.26.08.10718 | C001882609 | Horace Malcolm | St.James | Completed | Load_250164 | Rose Hall - 210 | 2026-08-07 21:34 | 2026-08-07 21:35 | 2026-08-07 21:59 | 2026-08-07 22:00 | 2026-08-07 22:00 | 2026-08-07 22:18 | 2026-08-07 22:18 | 2026-08-07 22:18 |  |  | Fair | No | Refused one 40amp junction fuse (not reggae riu it’s the other riu)
Outage | J.E.26.08.10218 | C001882614 | Tyrese Williams | St.Ann | Completed | Load_248004 | Roaring River - 410 | 2026-08-07 21:34 | 2026-08-07 21:35 | 2026-08-07 21:54 | 2026-08-07 21:54 | 2026-08-07 22:30 | 2026-08-07 22:31 | 2026-08-07 22:31 | 2026-08-07 22:31 | Fire |  | Fair | No | Customer has internal problem
Outage | J.E.26.08.10249 | C001882612 | Omar King | St.Ann | Completed | Load_242505 | Ocho Rios - 310 | 2026-08-07 21:34 | 2026-08-08 08:01 | 2026-08-08 09:43 | 2026-08-08 09:43 | 2026-08-08 10:15 | 2026-08-08 11:12 | 2026-08-08 11:12 | 2026-08-08 11:12 |  |  | Fair | No | Customer found with internal issues I advise customer to contact developer of property
Outage | J.E.26.08.10732 | C001882618 | Clyde Brown | Clarendon | Completed | Load_263846 | May Pen - 210 | 2026-08-07 22:25 | 2026-08-08 07:51 | 2026-08-08 08:26 | 2026-08-08 08:27 | 2026-08-08 08:53 | 2026-08-08 10:05 | 2026-08-08 10:18 | 2026-08-08 10:18 | Fire |  | Fair | No | Defective pothead and meter socket caused fire at at pothead one pothead disconnected and other meter now okay customer advised for burnt up pothead.
Outage | J.E.26.08.10863 | C001882636 | Edward Royal | KSAN | Completed | Load_264325 | Washington Blvd - 510 | 2026-08-08 04:58 | 2026-08-08 05:00 | 2026-08-08 06:33 | 2026-08-08 06:34 | 2026-08-08 06:33 | 2026-08-08 06:34 | 2026-08-08 06:34 | 2026-08-08 06:34 |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.08.10860 | C001882637 | Edward Royal | KSAN | Completed | Load_269032 | Washington Blvd - 610 | 2026-08-08 04:59 | 2026-08-08 05:00 | 2026-08-08 06:33 | 2026-08-08 06:33 | 2026-08-08 06:33 | 2026-08-08 06:33 | 2026-08-08 06:33 | 2026-08-08 06:33 |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.08.10878 | C001882638 | Edward Royal | KSAN | Completed | Load_252550 | Washington Blvd - 510 | 2026-08-08 05:00 | 2026-08-08 05:01 | 2026-08-08 06:09 | 2026-08-08 06:10 | 2026-08-08 06:09 | 2026-08-08 06:32 | 2026-08-08 06:33 | 2026-08-08 06:33 |  |  | Fair | No | Replaced 20A junction fuse and 3A transformer fuse
Outage | J.E.26.08.10370 | C001882644 | Stephen Taylor | St.Thomas | Completed | Load_251845 | Lysson - 410 | 2026-08-08 07:31 | 2026-08-08 07:33 | 2026-08-08 10:21 | 2026-08-08 10:22 | 2026-08-08 10:21 | 2026-08-08 10:21 | 2026-08-08 10:23 | 2026-08-08 10:23 |  |  | Fair | No | Splice and retention services wire 30 feet reading 112 customer is now okay
Outage | J.E.26.08.10372 | C001882643 | Stephen Taylor | St.Thomas | Completed | Load_269349 | Lysson - 410 | 2026-08-08 07:31 | 2026-08-08 07:33 | 2026-08-08 10:19 | 2026-08-08 10:20 | 2026-08-08 10:20 | 2026-08-08 10:20 | 2026-08-08 10:21 | 2026-08-08 10:21 |  |  | Fair | No | Premise found okay reading 111,112,223 customer is now okay
Non-Outage | J.E.26.08.10439 | C001882648 | Swon Miller |  | Completed |  |  | 2026-08-08 07:36 | 2026-08-08 23:14 | 2026-08-08 23:20 | 2026-08-09 01:05 | 2026-08-09 02:03 | 2026-08-09 02:22 | 2026-08-09 02:25 | 2026-08-09 02:25 |  |  | Fair | No | Check and found okay voltage found 117/118/236 customer states that a jps personal came and close up the blown fuse on Friday voltage left 118/117/236
Outage | J.E.26.08.10250 | C001882649 | Romeo Brissett | St.James | Completed | Load_259760 | Bogue - 610 | 2026-08-08 07:36 | 2026-08-08 07:38 | 2026-08-08 07:56 | 2026-08-08 07:56 | 2026-08-08 08:36 | 2026-08-08 08:28 | 2026-08-08 08:38 | 2026-08-08 08:38 |  |  | Fair | No | Customer was contacted and he stated he’s busy and is unable to be on the phone and won’t able to give directions.
Outage | J.E.26.08.10659 | C001882650 | Andre Smith | KSAS | Completed | Load_242023 | Hunts Bay - 410 | 2026-08-08 07:36 | 2026-08-08 07:48 | 2026-08-08 10:43 | 2026-08-08 10:43 | 2026-08-08 11:17 | 2026-08-08 11:19 | 2026-08-08 11:19 | 2026-08-08 11:19 |  |  | Fair | No | Premises found okay supply restored already
Outage | J.E.26.08.10670 | C001882651 | Andre Smith | KSAS | Completed | Load_289871 | Hunts Bay - 810 | 2026-08-08 07:36 | 2026-08-08 07:48 | 2026-08-08 08:20 | 2026-08-08 08:20 | 2026-08-08 09:19 | 2026-08-08 09:20 | 2026-08-08 09:20 | 2026-08-08 09:20 |  |  | Fair | No | Premises found okay supply restored already
Non-Outage | J.E.26.08.08992 | C001882654 | Horace Malcolm |  | Completed |  |  | 2026-08-08 07:37 | 2026-08-08 07:42 | 2026-08-08 08:11 | 2026-08-08 09:06 | 2026-08-08 09:06 | 2026-08-08 09:41 | 2026-08-08 09:41 | 2026-08-08 09:41 |  |  | Fair | No | Check and found area ok unable to reach out to person who made report by phone call
Outage | J.E.26.08.10431 | C001882652 | Andre Smith | KSAN | Completed | Load_246286 | Washington Blvd - 310 | 2026-08-08 07:37 | 2026-08-08 07:48 | 2026-08-08 09:20 | 2026-08-08 09:21 | 2026-08-08 10:22 | 2026-08-08 10:43 | 2026-08-08 10:43 | 2026-08-08 10:43 |  |  | Fair | No | Premises found okay supply restored already
Outage | J.E.26.08.10904 | C001882653 | Romeo Brissett | St.James | Completed | Load_250412 | Bogue - 310 | 2026-08-08 07:37 | 2026-08-08 07:38 | 2026-08-08 08:38 | 2026-08-08 08:39 | 2026-08-08 09:21 | 2026-08-08 10:00 | 2026-08-08 10:03 | 2026-08-08 10:03 |  |  | Fair | No | Check and found costumer no power coming service wire, disconnected from rammy box, please send to field service.
Non-Outage | J.E.26.08.10931 | C001882655 | Edward Royal | KSAS | Completed | Load_259609 | Duhaney - 310 | 2026-08-08 07:39 | 2026-08-08 07:41 | 2026-08-08 08:14 | 2026-08-08 08:15 | 2026-08-08 08:20 | 2026-08-08 08:34 | 2026-08-08 08:35 | 2026-08-08 08:35 |  |  | Fair | No | Replaced 2 transformer fuse 10A 5A fuse
Non-Outage | J.E.26.08.10662 | C001882657 | Dwayne Samuels |  | Completed |  |  | 2026-08-08 07:40 | 2026-08-08 07:43 | 2026-08-08 09:43 | 2026-08-08 10:34 | 2026-08-08 10:43 | 2026-08-08 10:43 | 2026-08-08 10:44 | 2026-08-08 10:44 |  |  | Fair | No | Check and found working ok voltage found 109v/113v/222v customer was advised get a electrician to do some internal checks
Non-Outage | J.E.26.08.10672 | C001882656 | Dwayne Samuels |  | Completed |  |  | 2026-08-08 07:40 | 2026-08-08 07:43 | 2026-08-08 09:41 | 2026-08-08 09:42 | 2026-08-08 10:31 | 2026-08-08 10:32 | 2026-08-08 10:33 | 2026-08-08 10:33 |  |  | Fair | No | Check and found working ok voltage found 109v/113v/222v customer was advised get a electrician to do some internal checks
Outage | J.E.26.08.10882 | C001882658 | Dwayne Samuels | Trelawny | Completed | Load_256777 | Greenwood - 110 | 2026-08-08 07:40 | 2026-08-08 07:43 | 2026-08-08 08:26 | 2026-08-08 08:27 | 2026-08-08 09:21 | 2026-08-08 09:39 | 2026-08-08 09:39 | 2026-08-08 09:39 |  |  | Fair | No | 50kva transformer switch top lead burnt off from main 3 phase primary line refer to Fraser and copy to Obrain Ellis about 35 customer without power.
Non-Outage | J.E.26.08.10629 | C001882659 | Edward Royal |  | Completed |  |  | 2026-08-08 07:44 | 2026-08-08 07:46 | 2026-08-08 08:42 | 2026-08-08 08:43 | 2026-08-08 08:42 | 2026-08-08 08:43 | 2026-08-08 08:43 | 2026-08-08 08:43 |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.08.10781 | C001882660 | Edward Royal |  | Completed |  |  | 2026-08-08 07:44 | 2026-08-08 07:46 | 2026-08-08 09:24 | 2026-08-08 09:25 | 2026-08-08 09:24 | 2026-08-08 09:54 | 2026-08-08 09:55 | 2026-08-08 09:55 |  |  | Fair | No | Meter mixed up advice customers to visit ruthven road for more information
Outage | J.E.26.08.10702 | C001882663 | Edward Royal | KSAS | Completed | Load_241437 | Duhaney - 310 | 2026-08-08 07:44 | 2026-08-08 07:46 | 2026-08-08 08:35 | 2026-08-08 08:36 | 2026-08-08 08:37 | 2026-08-08 08:38 | 2026-08-08 08:38 | 2026-08-08 08:38 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.10707 | C001882662 | Edward Royal | KSAN | Completed | Load_256532 | Constant Spring - 210 | 2026-08-08 07:44 | 2026-08-08 07:46 | 2026-08-08 08:38 | 2026-08-08 08:39 | 2026-08-08 08:38 | 2026-08-08 08:39 | 2026-08-08 08:39 | 2026-08-08 08:39 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.10710 | C001882661 | Edward Royal | KSAN | Completed | Load_574002 | Constant Spring - 210 | 2026-08-08 07:44 | 2026-08-08 07:46 | 2026-08-08 10:04 | 2026-08-08 10:04 | 2026-08-08 10:04 | 2026-08-08 10:58 | 2026-08-08 10:58 | 2026-08-08 10:58 |  |  | Fair | No | Premises found close unable to communicate with customer
Outage | J.E.26.08.10910 | C001882664 | Andre Williams | Trelawny | Completed | Load_253461 | Duncans - 210 | 2026-08-08 07:44 | 2026-08-08 15:18 | 2026-08-08 15:47 | 2026-08-08 15:48 | 2026-08-08 15:47 | 2026-08-08 15:50 | 2026-08-08 15:50 | 2026-08-08 15:50 |  |  | Fair | No | Premises found ok power was restored to area confirm by call
Outage | J.E.26.08.09210 | C001882665 | Dwayne Samuels | St.James | Completed | Load_254649 | Bogue - 310 | 2026-08-08 07:45 | 2026-08-08 07:46 | 2026-08-08 10:44 | 2026-08-08 10:45 | 2026-08-08 11:55 | 2026-08-08 12:32 | 2026-08-08 12:32 | 2026-08-08 12:32 |  |  | Fair | No | Check and found area working ok voltage found 113v/1112v/225v
Outage | J.E.26.08.10509 | C001882667 | Javid Vernon | Westmoreland | Completed | Load_252107 | Paradise - 310 | 2026-08-08 07:46 | 2026-08-08 07:47 | 2026-08-08 08:27 | 2026-08-08 08:28 | 2026-08-08 08:27 | 2026-08-08 08:28 | 2026-08-08 08:28 | 2026-08-08 08:28 |  |  | Fair | No | Customer stated that the power was restored to her premises
Outage | J.E.26.08.10692 | C001882666 | Javid Vernon | Westmoreland | Completed | Load_250155 | Paradise - 310 | 2026-08-08 07:46 | 2026-08-08 07:47 | 2026-08-08 08:29 | 2026-08-08 08:29 | 2026-08-08 08:29 | 2026-08-08 08:29 | 2026-08-08 08:29 | 2026-08-08 08:29 |  |  | Fair | No | Customer stated that the power was restored
Outage | J.E.26.08.10689 | C001882668 | Richman Whyte | Westmoreland | Completed | Load_256472 | Paradise - 110 | 2026-08-08 07:47 | 2026-08-08 07:54 | 2026-08-08 09:46 | 2026-08-08 09:47 | 2026-08-08 10:23 | 2026-08-08 10:38 | 2026-08-08 10:49 | 2026-08-08 10:49 |  |  | Fair | No | Replace five amp junction fuse
Outage | J.E.26.08.10801 | C001882669 | Richman Whyte | Westmoreland | Completed | Load_256472 | Paradise - 110 | 2026-08-08 07:47 | 2026-08-08 07:54 | 2026-08-08 10:50 | 2026-08-08 10:50 | 2026-08-08 10:50 | 2026-08-08 10:50 | 2026-08-08 10:51 | 2026-08-08 10:51 |  |  | Rains | No | Replace five amp junction fuse
Outage | J.E.26.08.10835 | C001882671 | Richman Whyte | Westmoreland | Completed | Load_247108 | Paradise - 210 | 2026-08-08 07:47 | 2026-08-08 07:54 | 2026-08-08 11:14 | 2026-08-08 11:14 | 2026-08-08 11:14 | 2026-08-08 11:14 | 2026-08-08 11:15 | 2026-08-08 11:15 |  |  | Fair | No | Customer state she didn’t make any call
Outage | J.E.26.08.10901 | C001882670 | Richman Whyte | Westmoreland | Completed | Load_249422 | Paradise - 210 | 2026-08-08 07:47 | 2026-08-08 07:54 | 2026-08-08 11:16 | 2026-08-08 11:16 | 2026-08-08 11:16 | 2026-08-08 11:16 | 2026-08-08 11:17 | 2026-08-08 11:17 |  |  | Fair | No | Customer state that power was restored to the area from last night
Non-Outage | J.E.26.08.10796 | C001882675 | Clyde Brown |  | Completed |  |  | 2026-08-08 07:48 | 2026-08-08 07:51 | 2026-08-08 11:20 | 2026-08-08 11:26 | 2026-08-08 11:25 | 2026-08-08 11:20 | 2026-08-08 11:28 | 2026-08-08 11:28 | Fire |  | Fair | No | Blown 3 amps fuse for 25kva transformer caused by burnt up fuse holder,line patrolled and fuse holder replaced with 3 amps fuse
Outage | J.E.26.08.10441 | C001882677 | Clyde Brown | Clarendon | Completed | Load_250052 | Parnassus - 210 | 2026-08-08 07:48 | 2026-08-08 07:51 | 2026-08-08 11:31 | 2026-08-08 11:32 | 2026-08-08 12:22 | 2026-08-08 12:22 | 2026-08-08 12:29 | 2026-08-08 12:29 |  |  | Fair | No | Burnt off phase for 3 wire service connection remade with 1- clamp,voltage now 112/112 and 225V
Outage | J.E.26.08.10777 | C001882673 | Romaine Roberts | St.Mary | Completed | Load_241220 | Highgate - 210 | 2026-08-08 07:48 | 2026-08-08 07:48 | 2026-08-08 09:15 | 2026-08-08 09:16 | 2026-08-08 11:38 | 2026-08-08 11:41 | 2026-08-08 11:43 | 2026-08-08 11:43 |  |  | Fair | Yes | Open and close 25 kva transformer to splice and retention conductor and carry out bushing to clear line power restore
Outage | J.E.26.08.10792 | C001882676 | Clyde Brown | Clarendon | Completed | Load_255816 | May Pen - 210 | 2026-08-08 07:48 | 2026-08-08 07:51 | 2026-08-08 10:18 | 2026-08-08 10:19 | 2026-08-08 11:20 | 2026-08-08 11:20 | 2026-08-08 11:25 | 2026-08-08 11:25 |  |  | Fair | No | 25 kva transformer 3 amps fuse blown caused by defective fuse holder ,line patrolled and fuse holder replaced.
Outage | J.E.26.08.10828 | C001882674 | Hartley Chin | Clarendon | Completed | Load_269030 | May Pen - 110 | 2026-08-08 07:48 | 2026-08-08 07:50 | 2026-08-08 10:34 | 2026-08-08 10:35 | 2026-08-08 11:41 | 2026-08-08 12:58 | 2026-08-08 12:59 | 2026-08-08 12:59 | LeaningPole |  | Fair | No | Refer to maintenance. Found 10 amp junction blown due to fallen trees breaking 30ft over head guy and leaning 35ft TA pole single phase primary open secondary remove tree and repair open secondary then refuse junction
Outage | J.E.26.08.10895 | C001882672 | Romaine Roberts | St.Mary | Completed | Load_254745 | Highgate -110 | 2026-08-08 07:48 | 2026-08-08 07:48 | 2026-08-08 14:32 | 2026-08-08 14:33 | 2026-08-08 14:32 | 2026-08-08 14:33 | 2026-08-08 14:33 | 2026-08-08 14:33 |  |  | Fair | No | Bamboo come down on primary line and blow junction fuse patrol and clear line and replace 15 amp junction power restore
Outage | J.E.26.08.09161 | C001882679 | Tajay Bernard | Hanover | Completed | Load_575731 | Orange Bay - 310 | 2026-08-08 07:49 | 2026-08-08 07:52 | 2026-08-08 07:59 | 2026-08-08 09:09 | 2026-08-08 09:09 | 2026-08-08 09:12 | 2026-08-08 09:12 | 2026-08-08 09:12 |  |  | Fair | No | Area check and found okay unable to locate customer on premises, phone number that was given was an international number so we weren’t able to get in contact with the customer
Outage | J.E.26.08.09869 | C001882678 | Tajay Bernard | Hanover | Completed | Load_573350 | Orange Bay - 310 | 2026-08-08 07:49 | 2026-08-08 07:52 | 2026-08-08 08:43 | 2026-08-08 08:44 | 2026-08-08 08:47 | 2026-08-08 09:08 | 2026-08-08 09:09 | 2026-08-08 09:09 |  |  | Fair | No | Refuse 1 25kva Transformer use 3amp fuse
Non-Outage | J.E.26.08.08499 | C001882682 | Tajay Bernard | Hanover | Completed | Load_252846 | Orange Bay - 210 | 2026-08-08 07:50 | 2026-08-08 07:52 | 2026-08-08 13:13 | 2026-08-08 13:14 | 2026-08-08 13:37 | 2026-08-08 13:38 | 2026-08-08 13:38 | 2026-08-08 13:38 |  |  | Fair | No | Customer stated that the issue has been resolved
Non-Outage | J.E.26.08.08581 | C001882681 | Tajay Bernard | Hanover | Completed | Load_252846 | Orange Bay - 210 | 2026-08-08 07:50 | 2026-08-08 07:52 | 2026-08-08 11:43 | 2026-08-08 11:44 | 2026-08-08 11:47 | 2026-08-08 13:10 | 2026-08-08 13:11 | 2026-08-08 13:11 |  |  | Fair | No | Isolate a 50kva and a 25kva Transformer to splice and retention 2 pole span of secondary phase and neutral, 30 ft of #2 conductor was use and 3 #2 preform
Non-Outage | J.E.26.08.08848 | C001882680 | Tajay Bernard | Hanover | Completed | Load_252846 | Orange Bay - 210 | 2026-08-08 07:50 | 2026-08-08 07:52 | 2026-08-08 13:11 | 2026-08-08 13:12 | 2026-08-08 13:12 | 2026-08-08 13:13 | 2026-08-08 13:13 | 2026-08-08 13:13 |  |  | Fair | No | Related to previous call job number 08581
Non-Outage | J.E.26.06.38877 | C001882683 | Tajay Bernard | Hanover | Completed | Load_244399 | Orange Bay - 210 | 2026-08-08 07:51 | 2026-08-08 07:52 | 2026-08-08 10:53 | 2026-08-08 10:54 | 2026-08-08 11:41 | 2026-08-08 11:42 | 2026-08-08 11:43 | 2026-08-08 11:43 |  |  | Fair | No | Premises check and found okay customer has internal problems customer was advised
Non-Outage | J.E.26.07.19525 | C001882684 | Tajay Bernard | Hanover | Completed | Load_242280 | Orange Bay - 310 | 2026-08-08 07:51 | 2026-08-08 07:52 | 2026-08-08 09:12 | 2026-08-08 09:13 | 2026-08-08 10:19 | 2026-08-08 10:52 | 2026-08-08 10:53 | 2026-08-08 10:53 |  |  | Fair | No | Clean and remake joints at jps pole use 2 clamps Voltage found 102/109/211Voltage left 114/115/230
Non-Outage | J.E.26.08.10302 | C001882685 | Hartley Chin | Clarendon | Completed | Load_250685 | May Pen - 110 | 2026-08-08 07:51 | 2026-08-08 07:53 | 2026-08-08 08:22 | 2026-08-08 08:22 | 2026-08-08 10:07 | 2026-08-08 10:32 | 2026-08-08 10:34 | 2026-08-08 10:34 |  |  | Fair | No | Removed chafed wire off neutral and insulated chafed phase
Non-Outage | J.E.26.08.09775 | C001882686 | Hartley Chin | Clarendon | Completed | Load_244375 | May Pen - 110 | 2026-08-08 07:52 | 2026-08-08 07:53 | 2026-08-08 13:00 | 2026-08-08 13:01 | 2026-08-08 13:33 | 2026-08-08 14:22 | 2026-08-08 14:23 | 2026-08-08 14:23 |  |  | Fair | No | Remove banging conductors and reset 15KVA transformer
Outage | J.E.26.08.10917 | C001882688 | Daniel Francis | St.Ann | Completed | Load_243427 | Cardiff Hall - 210 | 2026-08-08 07:54 | 2026-08-08 08:02 | 2026-08-08 10:56 | 2026-08-08 10:57 | 2026-08-08 10:56 | 2026-08-08 10:57 | 2026-08-08 10:58 | 2026-08-08 10:58 |  |  | Fair | No | Found okay
Outage | J.E.26.08.10772 | C001882689 | Barnett Brown | Manchester | Completed | Load_245342 | Spur Tree - 310 | 2026-08-08 07:55 | 2026-08-08 08:00 | 2026-08-08 08:29 | 2026-08-08 08:29 | 2026-08-08 10:29 | 2026-08-08 10:42 | 2026-08-08 10:43 | 2026-08-08 10:43 |  |  | Fair | Yes | Premises found ok
Outage | J.E.26.08.10779 | C001882690 | Barnett Brown | Manchester | Completed | Load_249945 | Spur Tree - 310 | 2026-08-08 07:55 | 2026-08-08 08:00 | 2026-08-08 10:44 | 2026-08-08 10:45 | 2026-08-08 11:32 | 2026-08-08 11:58 | 2026-08-08 12:01 | 2026-08-08 12:01 |  |  | Fair | No | Patrol line, found nothing, replace blown 30 amp junction fuse
Outage | J.E.26.08.10783 | C001882691 | Barnett Brown | Manchester | Completed | Load_248160 | Spur Tree - 310 | 2026-08-08 07:55 | 2026-08-08 08:00 | 2026-08-08 16:08 | 2026-08-08 16:08 | 2026-08-08 16:08 | 2026-08-08 16:43 | 2026-08-08 16:48 | 2026-08-08 16:48 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.10787 | C001882692 | Barnett Brown | Manchester | Completed | Load_247254 | Spur Tree - 310 | 2026-08-08 07:55 | 2026-08-08 08:00 | 2026-08-08 12:06 | 2026-08-08 12:07 | 2026-08-08 12:06 | 2026-08-08 12:06 | 2026-08-08 12:08 | 2026-08-08 12:08 |  |  | Fair | No | Related to previous Bethel st call where 30 amp junction fuse was replaced.
Outage | J.E.26.08.10790 | C001882693 | Barnett Brown | Manchester | Completed | Load_263270 | Spur Tree - 310 | 2026-08-08 07:55 | 2026-08-08 08:00 | 2026-08-08 12:08 | 2026-08-08 12:09 | 2026-08-08 12:10 | 2026-08-08 12:10 | 2026-08-08 12:13 | 2026-08-08 12:13 |  |  | Fair | No | Related to previous Bethel st call where 30 amp fuse was replaced
Outage | J.E.26.08.10836 | C001882695 | Barnett Brown | Manchester | Completed | Load_248160 | Spur Tree - 310 | 2026-08-08 07:55 | 2026-08-08 08:00 | 2026-08-08 13:55 | 2026-08-08 13:56 | 2026-08-08 16:04 | 2026-08-08 16:04 | 2026-08-08 16:07 | 2026-08-08 16:07 |  |  | Fair | No
Outage | J.E.26.08.10853 | C001882694 | Barnett Brown | Manchester | Completed | Load_292951 | Spur Tree - 310 | 2026-08-08 07:55 | 2026-08-08 08:00 | 2026-08-08 12:15 | 2026-08-08 12:16 | 2026-08-08 13:23 | 2026-08-08 13:54 | 2026-08-08 13:55 | 2026-08-08 13:55 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.10879 | C001882698 | Daniel Francis | St.Ann | Completed | Load_244223 | Cardiff Hall - 210 | 2026-08-08 07:58 | 2026-08-08 07:59 | 2026-08-08 08:24 | 2026-08-08 08:24 | 2026-08-08 09:37 | 2026-08-08 10:38 | 2026-08-08 10:43 | 2026-08-08 10:43 |  |  | Fair | No | Repair switch bottom jumper at queen cresent and renew junction 15 amp
Outage | J.E.26.08.10888 | C001882697 | Daniel Francis | St.Ann | Completed | Load_241005 | Cardiff Hall - 210 | 2026-08-08 07:58 | 2026-08-08 07:59 | 2026-08-08 10:46 | 2026-08-08 10:47 | 2026-08-08 10:46 | 2026-08-08 10:26 | 2026-08-08 10:48 | 2026-08-08 10:48 |  |  | Fair | No | Change one 25amp fuse pole #0010400 power restored
Outage | J.E.26.08.10909 | C001882696 | Daniel Francis | St.Ann | Completed | Load_268153 | Cardiff Hall - 210 | 2026-08-08 07:58 | 2026-08-08 07:59 | 2026-08-08 10:49 | 2026-08-08 10:55 | 2026-08-08 10:54 | 2026-08-08 10:56 | 2026-08-08 10:56 | 2026-08-08 10:56 |  |  | Fair | No | Found okay
Non-Outage | J.E.26.08.10467 | C001882739 | Kenroy Dale |  | Completed |  |  | 2026-08-08 08:13 | 2026-08-09 07:31 | 2026-08-09 09:16 | 2026-08-09 09:18 | 2026-08-09 09:27 | 2026-08-09 09:32 | 2026-08-09 09:35 | 2026-08-09 09:35 | BrokenWire |  | Fair | No | Area checked found with supply customer also confirmed that supply was restored
Non-Outage | J.E.26.08.10134 | C001882741 | Delano Gayle | Portmore | Completed | Load_567976 | Naggo Head - 610 | 2026-08-08 08:14 | 2026-08-08 08:27 | 2026-08-08 08:33 | 2026-08-08 08:33 | 2026-08-08 09:07 | 2026-08-08 09:28 | 2026-08-08 09:28 | 2026-08-08 09:28 | Fire |  | Fair | No | Premises found okay, voltage readings on load at pothead 115-116-231
Non-Outage | J.E.26.08.10139 | C001882742 | Delano Gayle | St.Catherine | Completed | Load_247287 | Twickenham - 210 | 2026-08-08 08:14 | 2026-08-08 08:27 | 2026-08-08 13:12 | 2026-08-08 13:13 | 2026-08-08 13:51 | 2026-08-08 14:08 | 2026-08-08 14:08 | 2026-08-08 14:08 | Fire |  | Fair | No | Broken phase at pole repair use 1 clamp voltage readings 115-116-232
Non-Outage | J.E.26.08.10807 | C001882749 | Richard Nicholas | St.Catherine | Completed | Load_568632 | Tredegar - 510 | 2026-08-08 08:26 | 2026-08-08 08:27 | 2026-08-08 10:42 | 2026-08-08 10:42 | 2026-08-08 11:16 | 2026-08-08 11:47 | 2026-08-08 11:48 | 2026-08-08 11:48 |  |  | Fair | No | No broken JPS.co pole seen ,only a leaning private pole with service wire.
Outage | J.E.26.08.10714 | C001882752 | Jowayne Newmans | St.Elizabeth | Completed | Load_262476 | Maggotty - 210 | 2026-08-08 08:27 | 2026-08-08 08:28 | 2026-08-08 08:49 | 2026-08-08 08:50 | 2026-08-08 11:51 | 2026-08-08 11:58 | 2026-08-08 11:58 | 2026-08-08 11:58 |  |  | Fair | No | Patrol and found customer meter burn and is single phasing, meter need to be replaced. Refer call to field service to replace meter. Voltage reading at meter socket 112v, 110v, 222v.
Non-Outage | J.E.26.08.06991 | C001882754 | Donald Cunningham | St.Catherine | Completed | Load_254033 | Rhodens Pen - 310 | 2026-08-08 08:28 | 2026-08-08 08:30 | 2026-08-08 14:36 | 2026-08-08 14:37 | 2026-08-08 15:52 | 2026-08-08 15:53 | 2026-08-08 15:53 | 2026-08-08 15:53 |  |  | Fair | No | Rami system in area refer to mr Ellison
Non-Outage | J.E.26.08.10569 | C001882753 | Donald Cunningham | St.Catherine | Completed | Load_305202 | Rhodens Pen - 310 | 2026-08-08 08:28 | 2026-08-08 08:30 | 2026-08-08 15:55 | 2026-08-08 15:56 | 2026-08-08 16:41 | 2026-08-08 17:02 | 2026-08-08 17:03 | 2026-08-08 17:03 |  |  | Fair | No | Corroded phase and neural by pole corrected also corroded meter socket corrected voltage readings 114/2/230
Non-Outage | J.E.26.07.39104 | C001882756 | Richard Nicholas | St.Catherine | Completed | Load_240154 | Tredegar - 510 | 2026-08-08 08:31 | 2026-08-08 08:32 | 2026-08-08 11:48 | 2026-08-08 11:49 | 2026-08-08 12:21 | 2026-08-08 12:35 | 2026-08-08 12:36 | 2026-08-08 12:36 | Fire |  | Fair | No | Area found ok,no fire seen.
Non-Outage | J.E.26.08.03467 | C001882755 | Richard Nicholas | St.Catherine | Completed | Load_260534 | Tredegar - 510 | 2026-08-08 08:31 | 2026-08-08 08:32 | 2026-08-08 08:49 | 2026-08-08 08:50 | 2026-08-08 10:21 | 2026-08-08 10:41 | 2026-08-08 10:41 | 2026-08-08 10:41 | BrokenPole |  | Fair | No | No broken pole seen
Non-Outage | J.E.26.08.11016 | C001882758 | Rusean Allen |  | Completed |  |  | 2026-08-08 08:45 | 2026-08-08 08:46 | 2026-08-08 11:10 | 2026-08-08 11:10 | 2026-08-08 11:13 | 2026-08-08 11:13 | 2026-08-08 11:13 | 2026-08-08 11:13 | BrokenWire |  | Fair | No | Not found
Outage | J.E.26.08.10955 | C001882760 | Omar King | St.Ann | Completed | Load_312801 | Roaring River - 410 | 2026-08-08 08:55 | 2026-08-08 08:56 | 2026-08-08 11:12 | 2026-08-08 11:13 | 2026-08-08 11:40 | 2026-08-08 12:00 | 2026-08-08 12:00 | 2026-08-08 12:00 |  |  | Fair | No | Found two 25 amp junction blow as been replaced customer is now with supply
Outage | J.E.26.08.11026 | C001882759 | Daniel Francis | St.Ann | Completed | Load_269957 | Roaring River - 210 | 2026-08-08 08:55 | 2026-08-08 15:16 | 2026-08-09 09:49 | 2026-08-09 09:50 | 2026-08-09 10:35 | 2026-08-09 11:11 | 2026-08-09 11:11 | 2026-08-09 11:11 |  |  | Fair | No | Retention two span of secondary neutral and reset 25kva transformer
Non-Outage | J.E.26.08.09993 | C001882761 | Gregory Grossett |  | Completed |  |  | 2026-08-08 08:57 | 2026-08-08 09:12 | 2026-08-08 10:48 | 2026-08-08 10:49 | 2026-08-08 11:09 | 2026-08-08 11:15 | 2026-08-08 11:15 | 2026-08-08 11:15 | LeaningPole |  | Fair | No | 10.5 meter concrete pole leaning badly and need to be straighten also over head wood guy pole broken and in the the road in the same area please refer to maintenance department to have this work done.
Non-Outage | J.E.26.08.10104 | C001882762 | Gregory Grossett | Portland | Completed | Load_237910 | Port Antonio - 410 | 2026-08-08 08:57 | 2026-08-08 09:10 | 2026-08-08 11:58 | 2026-08-08 11:59 | 2026-08-08 12:19 | 2026-08-08 12:42 | 2026-08-08 12:43 | 2026-08-08 12:43 |  |  | Fair | No | Premises found ok voltage readings at pothead 118/118/236 on both phase however meter has locking bond so we cannot get access into the meter socket.
Non-Outage | J.E.26.08.09789 | C001882769 | Delano Gayle | St.Catherine | Completed | Load_264582 | Twickenham - 210 | 2026-08-08 08:58 | 2026-08-08 09:00 | 2026-08-08 09:30 | 2026-08-08 09:30 | 2026-08-08 10:09 | 2026-08-08 10:31 | 2026-08-08 10:31 | 2026-08-08 10:31 |  |  | Fair | No | Broken #6 neutral mid span, splice and retention use 5ft #6 phase 1 linket 1 clamp voltage reading 115-116-231
Non-Outage | J.E.26.08.09837 | C001882768 | Delano Gayle | St.Catherine | Completed | Load_259123 | Twickenham - 210 | 2026-08-08 08:58 | 2026-08-08 09:00 | 2026-08-08 10:32 | 2026-08-08 10:32 | 2026-08-08 10:57 | 2026-08-08 11:14 | 2026-08-08 11:14 | 2026-08-08 11:14 |  |  | Fair | No | Repair corroded neutral at pothead use 1 linket voltage reading 112, customer has internal problems advised customer
Non-Outage | J.E.26.08.10404 | C001882767 | Wan Carlos Scarlett | St.Catherine | Completed | Load_265320 | Twickenham - 210 | 2026-08-08 08:58 | 2026-08-08 15:08 | 2026-08-08 20:42 | 2026-08-08 20:42 | 2026-08-08 21:31 | 2026-08-08 21:53 | 2026-08-08 21:54 | 2026-08-08 21:54 |  |  | Fair | No | Customer not available at this time premises closed customer will reschedule for a next visit
Non-Outage | J.E.26.08.10535 | C001882763 | Gregory Grossett | Portland | Completed | Load_348337 | Port Antonio - 410 | 2026-08-08 08:58 | 2026-08-08 09:10 | 2026-08-08 11:17 | 2026-08-08 11:17 | 2026-08-08 11:56 | 2026-08-08 11:57 | 2026-08-08 11:58 | 2026-08-08 11:58 |  |  | Fair | No | After calling customer he said that everything start to work ok again.
Non-Outage | J.E.26.08.10951 | C001882765 | Wan Carlos Scarlett | St.Catherine | Completed | Load_251822 | Twickenham - 210 | 2026-08-08 08:58 | 2026-08-08 15:08 | 2026-08-08 16:57 | 2026-08-08 16:58 | 2026-08-08 17:26 | 2026-08-08 17:48 | 2026-08-08 17:51 | 2026-08-08 17:51 |  |  | Fair | No | Found customer stanchion broken customer service wire hanging low to the ground isolate 3 wire service at pole advise customer to get a licensed electrician to fix the problem.
Non-Outage | J.E.26.08.07738 | C001882771 | Rusean Allen | KSAS | Completed | Load_556657 | Cane River - 410 | 2026-08-08 09:00 | 2026-08-08 09:02 | 2026-08-08 11:14 | 2026-08-08 11:14 | 2026-08-08 11:30 | 2026-08-08 11:35 | 2026-08-08 11:35 | 2026-08-08 11:35 |  |  | Fair | No | Unable to identify customers pothead, customer was advised to contact electrician to mark pothead.
Non-Outage | J.E.26.08.07764 | C001882770 | Rusean Allen | KSAS | Completed | Load_259209 | Greenwich - 410 | 2026-08-08 09:00 | 2026-08-08 09:01 | 2026-08-08 09:39 | 2026-08-08 10:08 | 2026-08-08 10:58 | 2026-08-08 10:59 | 2026-08-08 10:59 | 2026-08-08 10:59 |  |  | Fair | No | Premises found locked
Non-Outage | J.E.26.08.11036 | C001882772 | Edward Royal | KSAS | Completed | Load_259244 | Duhaney - 310 | 2026-08-08 09:07 | 2026-08-08 09:07 | 2026-08-08 09:16 | 2026-08-08 09:17 | 2026-08-08 09:16 | 2026-08-08 09:17 | 2026-08-08 09:17 | 2026-08-08 09:17 |  |  | Fair | No | Replaced 2 3A transformer fuse
Non-Outage | J.E.26.08.11029 | C001882778 | Javid Vernon |  | Completed |  |  | 2026-08-08 09:23 | 2026-08-08 09:25 | 2026-08-08 09:58 | 2026-08-08 09:58 | 2026-08-08 11:43 | 2026-08-08 11:43 | 2026-08-08 11:44 | 2026-08-08 11:44 |  |  | Fair | No | Customer stated that the power was restored
Outage | J.E.26.08.11031 | C001882777 | Javid Vernon | Westmoreland | Completed | Load_253744 | Paradise - 310 | 2026-08-08 09:23 | 2026-08-08 09:25 | 2026-08-08 11:44 | 2026-08-08 11:44 | 2026-08-08 11:44 | 2026-08-08 11:44 | 2026-08-08 11:45 | 2026-08-08 11:45 |  |  | Fair | No | Customer stated that the power was restored
Outage | J.E.26.08.10975 | C001882780 | Javid Vernon | Westmoreland | Completed | Load_240662 | Paradise - 310 | 2026-08-08 09:26 | 2026-08-08 09:27 | 2026-08-08 11:45 | 2026-08-08 11:45 | 2026-08-08 11:45 | 2026-08-08 11:45 | 2026-08-08 11:45 | 2026-08-08 11:45 |  |  | Fair | No | Customer stated that the power was restored
Outage | J.E.26.08.10990 | C001882781 | Javid Vernon | Westmoreland | Completed | Load_238824 | Paradise - 310 | 2026-08-08 09:26 | 2026-08-08 09:27 | 2026-08-08 11:46 | 2026-08-08 11:46 | 2026-08-08 11:46 | 2026-08-08 11:46 | 2026-08-08 11:46 | 2026-08-08 11:46 |  |  | Fair | No | Customer stated that the power was restored
Non-Outage | J.E.26.08.10953 | C001882782 | Christopher Edwards | KSAN | Completed | Load_264247 | Constant Spring - 410 | 2026-08-08 09:27 | 2026-08-08 09:28 | 2026-08-08 09:32 | 2026-08-08 09:48 | 2026-08-08 10:41 | 2026-08-08 11:23 | 2026-08-08 11:24 | 2026-08-08 11:24 |  |  | Fair | No | Remake neural joint at pole Using (1) one bolt clamps Voltage:112,113,220v
Non-Outage | J.E.26.08.09202 | C001882785 | Shamour Haughton | St.James | Completed | Load_302881 | Bogue - 310 | 2026-08-08 09:33 | 2026-08-08 09:36 | 2026-08-08 11:46 | 2026-08-08 11:46 | 2026-08-08 11:46 | 2026-08-08 11:46 | 2026-08-08 11:46 | 2026-08-08 11:46 |  |  | Fair | No | Customer states that power was restored
Non-Outage | J.E.26.07.22980 | C001882790 | Shamour Haughton | St.James | Completed | Load_245091 | Bogue - 310 | 2026-08-08 09:34 | 2026-08-08 09:36 | 2026-08-08 12:30 | 2026-08-08 12:31 | 2026-08-08 12:30 | 2026-08-08 12:30 | 2026-08-08 12:31 | 2026-08-08 12:31 |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.07.39208 | C001882788 | Shamour Haughton | St.James | Completed | Load_301732 | Bogue - 310 | 2026-08-08 09:34 | 2026-08-08 09:36 | 2026-08-08 10:28 | 2026-08-08 10:28 | 2026-08-08 10:45 | 2026-08-08 11:16 | 2026-08-08 11:39 | 2026-08-08 11:39 |  |  | Fair | No | Found customer single phasing, isolate 50kva to clean and remake joint at pole use 1 clamp, reclose 50kva at pole number 621641
Non-Outage | J.E.26.07.40155 | C001882789 | Shamour Haughton | St.James | Completed | Load_247752 | Bogue - 310 | 2026-08-08 09:34 | 2026-08-08 09:36 | 2026-08-08 12:38 | 2026-08-08 12:39 | 2026-08-08 13:37 | 2026-08-08 13:37 | 2026-08-08 13:39 | 2026-08-08 13:39 |  |  | Fair | No | Check and found okay, voltage left 115,115,230
Non-Outage | J.E.26.08.00068 | C001882787 | Shamour Haughton | St.James | Completed | Load_301802 | Bogue - 310 | 2026-08-08 09:34 | 2026-08-08 09:36 | 2026-08-08 11:48 | 2026-08-08 11:49 | 2026-08-08 11:48 | 2026-08-08 11:48 | 2026-08-08 12:28 | 2026-08-08 12:28 |  |  | Fair | No | Customer states that power was restored
Non-Outage | J.E.26.08.04996 | C001882786 | Shamour Haughton | St.James | Completed | Load_557698 | Bogue - 410 | 2026-08-08 09:34 | 2026-08-08 09:36 | 2026-08-08 14:43 | 2026-08-08 14:43 | 2026-08-08 14:43 | 2026-08-08 14:44 | 2026-08-08 14:47 | 2026-08-08 14:47 |  |  | Fair | No | Check and found okay, voltage left 119,118,210,240,240,241
Non-Outage | J.E.26.08.10070 | C001882791 | Romeo Brissett | St.James | Completed | Load_258893 | Bogue - 610 | 2026-08-08 09:36 | 2026-08-08 09:39 | 2026-08-08 12:19 | 2026-08-08 12:20 | 2026-08-08 13:14 | 2026-08-08 14:09 | 2026-08-08 14:11 | 2026-08-08 14:11 |  |  | Fair | No | Isolated (1)15KVA transformer, removed tree several illegal connections and retention secondary. V/R 108-111-218
Non-Outage | J.E.26.08.10311 | C001882792 | Romeo Brissett | St.James | Completed | Load_258453 | Bogue - 510 | 2026-08-08 09:36 | 2026-08-08 09:39 | 2026-08-08 14:11 | 2026-08-08 14:12 | 2026-08-08 15:03 | 2026-08-08 15:30 | 2026-08-08 15:50 | 2026-08-08 15:50 |  |  | Fair | No | Removed illegal connections and repaired secondary jumper used 2 clamps V/R 107-109-211.
Non-Outage | J.E.26.07.21248 | C001882793 | Romeo Brissett |  | Completed |  |  | 2026-08-08 09:37 | 2026-08-08 09:39 | 2026-08-08 10:04 | 2026-08-08 10:05 | 2026-08-08 11:06 | 2026-08-08 12:18 | 2026-08-08 12:19 | 2026-08-08 12:19 | Fire |  | Fair | No | Isolated (1)15amps junction fuse, cut and cleared tree limbs retention secondary.
Outage | J.E.26.08.11058 | C001882794 | Delano Gayle | Portmore | Completed | Load_1000831 | Naggo Head - 610 | 2026-08-08 09:44 | 2026-08-08 09:45 | 2026-08-08 11:14 | 2026-08-08 11:15 | 2026-08-08 11:43 | 2026-08-08 12:11 | 2026-08-08 12:11 | 2026-08-08 12:11 |  |  | Fair | No | Blown junction in 3 phase line no pole#, blown 25kva transformer fuse no pole number, bird flew in line, replace 25amps at junction and 3amps at transformer fuse
Outage | J.E.26.08.10145 | C001882795 | Shamour Haughton | St.James | Completed | Load_1002115 | Bogue - 310 | 2026-08-08 09:48 | 2026-08-08 09:49 | 2026-08-08 11:42 | 2026-08-08 11:42 | 2026-08-08 11:42 | 2026-08-08 11:44 | 2026-08-08 11:45 | 2026-08-08 11:45 |  |  | Fair | No | Customer states that power was restored
Non-Outage | J.E.26.08.11094 | C001882796 | Rusean Allen | KSAS | Completed | Load_244455 | Cane River - 610 | 2026-08-08 09:54 | 2026-08-08 09:55 | 2026-08-08 17:36 | 2026-08-08 21:00 | 2026-08-08 21:00 | 2026-08-08 21:00 | 2026-08-08 21:01 | 2026-08-08 21:01 |  |  | Fair | No | Customer phone went unanswered
Outage | J.E.26.08.11077 | C001882798 | Milton Charlton | KSAN | Completed | Load_240114 | Hope - 410 | 2026-08-08 10:09 | 2026-08-08 10:11 | 2026-08-08 10:15 | 2026-08-08 10:15 | 2026-08-08 11:00 | 2026-08-08 10:40 | 2026-08-08 11:12 | 2026-08-08 11:12 |  |  | Fair | No | Refused and reclosed 25 kva Hexing transformer at pole#( no pole#). Transformer fuse blown and the pressure fly out of the transformer splashing oil on the ground. 25 kva transformer at the gate of 22 Barbican Road defective.
Outage | J.E.26.08.11082 | C001882799 | Milton Charlton | KSAN | Completed | Load_263854 | Hope - 410 | 2026-08-08 10:09 | 2026-08-08 10:11 | 2026-08-08 11:12 | 2026-08-08 11:12 | 2026-08-08 11:12 | 2026-08-08 10:40 | 2026-08-08 11:21 | 2026-08-08 11:21 |  |  | Fair | No | Refused and reclosed 25 kva Hexing transformer switch at pole#( no pole#). Transformer fuse blow and pressure switch fly out of the transformer splashing oil on the ground.25 kva transformer at the gate of 22 Barbican Road defective.
Outage | J.E.26.08.10961 | C001882800 | Dwayne Samuels | Trelawny | Completed | Load_255143 | Greenwood - 110 | 2026-08-08 10:10 | 2026-08-08 10:12 | 2026-08-08 12:32 | 2026-08-08 12:33 | 2026-08-08 13:32 | 2026-08-08 13:35 | 2026-08-08 13:35 | 2026-08-08 13:35 | BrokenWire |  | Fair | No | Customer stanchion broke down customer was advised to get an electrician to fix before connection…..
Outage | J.E.26.08.11151 | C001882802 | Romaine Roberts | St.Mary | Completed | Load_255715 | Highgate -110 | 2026-08-08 10:31 | 2026-08-08 10:33 | 2026-08-08 11:43 | 2026-08-08 11:44 | 2026-08-08 12:55 | 2026-08-08 14:31 | 2026-08-08 14:32 | 2026-08-08 14:32 |  | Y | Fair | No | Bamboo come down on primary line and blow junction fuse patrol and clear line and replace 15 amp junction power restore
Outage | J.E.26.08.11184 | C001882804 | Gregory Grossett | Portland | Completed | Load_577181 | Port Antonio - 310 | 2026-08-08 10:31 | 2026-08-08 10:33 | 2026-08-08 14:18 | 2026-08-08 14:19 | 2026-08-08 14:18 | 2026-08-08 14:19 | 2026-08-08 14:19 | 2026-08-08 14:19 |  |  | Fair | No | After calling digicel call center Javon brown said that power is at the site.
Outage | J.E.26.08.11186 | C001882805 | Gregory Grossett | Portland | Completed | Load_260046 | Port Antonio - 310 | 2026-08-08 10:31 | 2026-08-08 10:33 | 2026-08-08 14:16 | 2026-08-08 14:17 | 2026-08-08 14:17 | 2026-08-08 14:18 | 2026-08-08 14:18 | 2026-08-08 14:18 |  |  | Fair | No | After calling digicel call center Javon brown said that power is at the site.
Outage | J.E.26.08.11207 | C001882803 | Omar King | St.Ann | Completed | Load_240455 | Upper White River - 210 | 2026-08-08 10:31 | 2026-08-08 10:36 | 2026-08-09 16:39 | 2026-08-09 16:39 | 2026-08-09 17:01 | 2026-08-09 17:01 | 2026-08-09 17:01 | 2026-08-09 17:01 |  |  | Fair | No | Unable to find customer call several times no answer directions not sufficient
Outage | J.E.26.08.11193 | C001882806 | Richard Samuda | Manchester | Completed | Load_259427 | Kendal - 310 | 2026-08-08 10:32 | 2026-08-08 12:33 | 2026-08-08 12:46 | 2026-08-08 12:47 | 2026-08-08 13:06 | 2026-08-08 13:25 | 2026-08-08 13:25 | 2026-08-08 13:25 |  |  | Fair | No | Pole number: 0123849 found 10 amp junction blown patrol line found nothing replaced fuse close line customer back to normal
Non-Outage | J.E.26.08.11112 | C001882807 | Gregory Grossett | Portland | Completed | Load_255671 | Port Antonio - 310 | 2026-08-08 10:42 | 2026-08-08 10:42 | 2026-08-08 12:43 | 2026-08-08 12:43 | 2026-08-08 13:45 | 2026-08-08 14:16 | 2026-08-08 14:16 | 2026-08-08 14:16 |  |  | Fair | No | 220 service phase broke at pole repair and ok material use 1-one bolt clamp voltage readings at meter socket 118/118/236 on both phase.
Non-Outage | J.E.26.08.11273 | C001882815 | Omar King |  | Completed |  |  | 2026-08-08 11:25 | 2026-08-08 11:26 | 2026-08-08 12:18 | 2026-08-08 12:19 | 2026-08-08 13:56 | 2026-08-08 14:42 | 2026-08-08 14:43 | 2026-08-08 14:43 |  |  | Fair | No | Found customer with internal problem I advise customer to use electrician to resolve
Outage | J.E.26.08.11249 | C001882816 | Romaine Roberts | St.Mary | Completed | Load_248864 | Highgate - 210 | 2026-08-08 11:27 | 2026-08-09 15:33 | 2026-08-09 16:16 |  | 2026-08-09 16:16 | 2026-08-09 16:29 | 2026-08-09 16:30 | 2026-08-09 16:30 |  |  | Fair | No | Found ok power was restore
Outage | J.E.26.08.11258 | C001882817 | Romaine Roberts | St.Mary | Completed | Load_574194 | Annotto Bay - 310 | 2026-08-08 11:27 | 2026-08-08 11:28 | 2026-08-08 14:33 | 2026-08-08 14:34 | 2026-08-08 15:43 | 2026-08-08 15:50 | 2026-08-08 15:50 | 2026-08-08 15:50 |  |  | Fair | No | 3 wire service phase oxidize and break in mid air patrol and clean and remake joints power restore
Non-Outage | J.E.26.08.11086 | C001882818 | Delano Gayle |  | Completed |  |  | 2026-08-08 11:36 | 2026-08-08 11:53 | 2026-08-08 12:11 | 2026-08-08 12:12 | 2026-08-08 12:50 | 2026-08-08 13:13 | 2026-08-08 13:12 | 2026-08-08 13:12 | BrokenWire |  | Fair | No | Premises not located no answer from customer phone
Outage | J.E.26.08.11090 | C001882820 | Andre Smith | KSAS | Completed | Load_259700 | Hunts Bay - 510 | 2026-08-08 11:49 | 2026-08-08 11:54 | 2026-08-08 12:12 | 2026-08-08 12:13 | 2026-08-08 12:47 | 2026-08-08 13:29 | 2026-08-08 13:29 | 2026-08-08 13:29 | BrokenWire |  | Fair | No | Repair burnt transformer droplead using one one bolt clamp at supply restored
Outage | J.E.26.08.11209 | C001882822 | Rusean Allen | KSAN | Completed | Load_575386 | Washington Blvd - 710 | 2026-08-08 11:52 | 2026-08-08 15:12 | 2026-08-08 21:00 | 2026-08-08 21:01 | 2026-08-08 21:01 | 2026-08-08 21:02 | 2026-08-08 21:02 | 2026-08-08 21:02 |  |  | Fair | No | Meter was reconnected by customer service
Outage | J.E.26.08.11309 | C001882824 | Andre Smith | KSAS | Completed | Load_247482 | Greenwich - 510 | 2026-08-08 11:54 | 2026-08-08 11:55 | 2026-08-08 13:29 | 2026-08-08 13:30 | 2026-08-08 14:03 | 2026-08-08 14:30 | 2026-08-08 14:30 | 2026-08-08 14:30 | BrokenWire |  | Fair | No | Defective customer pothead customer advised of repairs
Outage | J.E.26.08.11169 | C001882829 | Richard Nicholas | St.Catherine | Completed | Load_557148 | Tredegar - 210 | 2026-08-08 12:08 | 2026-08-08 12:09 | 2026-08-08 12:40 | 2026-08-08 12:40 | 2026-08-08 13:30 | 2026-08-08 14:44 | 2026-08-08 14:46 | 2026-08-08 14:46 |  |  | Fair | No | Replaced blown 25amp junctions fuse on pole #595950 and blown Rammy 15kva x2 transformer 5amp fuse on pole #612691.
Outage | J.E.26.08.11153 | C001882831 | Ricky Hall | St.Catherine | Completed | Load_568263 | New Michelton - 210 | 2026-08-08 12:18 | 2026-08-08 12:19 | 2026-08-08 12:55 | 2026-08-08 12:56 | 2026-08-08 13:43 | 2026-08-08 15:00 | 2026-08-08 15:01 | 2026-08-08 15:01 | BrokenWire |  | Rains | No | Splice and retention broken twisted secondary line use 4 clamps 5’#2/0 aa
Non-Outage | J.E.26.08.11229 | C001882835 | Richard Nicholas |  | Completed |  |  | 2026-08-08 12:19 | 2026-08-08 12:21 | 2026-08-08 14:46 | 2026-08-08 14:47 | 2026-08-08 15:45 | 2026-08-08 16:24 | 2026-08-08 16:29 | 2026-08-08 16:29 | BrokenWire |  | Rains | No | One span of broken 3phase primary neural on the trunk line,T-off to ebony housing scheme.
Non-Outage | J.E.26.08.11231 | C001882834 | Ricky Hall |  | Completed |  |  | 2026-08-08 12:19 | 2026-08-08 12:20 | 2026-08-08 15:02 | 2026-08-08 15:02 | 2026-08-08 15:02 | 2026-08-08 15:03 | 2026-08-08 15:03 | 2026-08-08 15:03 | BrokenWire |  | Rains | No | Call associated with outage #11153
Non-Outage | J.E.26.08.11256 | C001882838 | Horace Malcolm |  | Completed |  |  | 2026-08-08 12:20 | 2026-08-08 12:22 | 2026-08-08 12:34 | 2026-08-08 12:36 | 2026-08-08 12:55 | 2026-08-08 12:57 | 2026-08-08 12:57 | 2026-08-08 12:57 |  |  | Fair | No | Check and found ok supply restored back
Outage | J.E.26.08.11146 | C001882837 | Horace Malcolm | St.James | Completed | Load_302615 | Queens Drive - 310 | 2026-08-08 12:20 | 2026-08-08 12:22 | 2026-08-08 12:58 | 2026-08-08 12:58 | 2026-08-08 12:58 | 2026-08-08 12:59 | 2026-08-08 12:59 | 2026-08-08 12:59 |  |  | Fair | No | Check and found ok supply restored back
Outage | J.E.26.08.11316 | C001882836 | Horace Malcolm | St.James | Completed | Load_250164 | Rose Hall - 210 | 2026-08-08 12:20 | 2026-08-08 12:22 | 2026-08-08 12:27 | 2026-08-08 12:28 | 2026-08-08 12:27 | 2026-08-08 12:29 | 2026-08-08 12:29 | 2026-08-08 12:29 |  |  | Fair | No | Refused one 50amp junction fuse CT and PT needs cleaning
Non-Outage | J.E.26.08.11116 | C001882839 | Horace Malcolm |  | Completed |  |  | 2026-08-08 12:21 | 2026-08-08 12:22 | 2026-08-08 12:57 | 2026-08-08 12:57 | 2026-08-08 12:57 | 2026-08-08 12:58 | 2026-08-08 12:58 | 2026-08-08 12:58 |  |  | Fair | No | Check and found ok supply restored back
Outage | J.E.26.08.11340 | C001882842 | Neville Spencer | Clarendon | Completed | Load_237798 | May Pen - 110 | 2026-08-08 12:35 | 2026-08-08 14:41 | 2026-08-08 15:11 | 2026-08-08 15:11 | 2026-08-08 18:35 | 2026-08-08 18:35 | 2026-08-08 18:51 | 2026-08-08 18:51 |  |  | Fair | No | Renew blown 15 amp j/ fuse at pole # 0155424 area restored.
Outage | J.E.26.08.11300 | C001882843 | Wayne Dillion | St.Elizabeth | Completed | Load_245885 | Maggotty - 110 | 2026-08-08 12:41 | 2026-08-08 12:46 | 2026-08-08 13:13 | 2026-08-08 13:13 | 2026-08-08 13:13 | 2026-08-08 13:15 | 2026-08-08 13:16 | 2026-08-08 13:16 |  |  | Fair | No | Please refer this call to a Westmoreland team.
Outage | J.E.26.08.11306 | C001882844 | Dwayne Samuels | Trelawny | Completed | Load_265112 | Greenwood - 210 | 2026-08-08 12:42 | 2026-08-08 12:46 | 2026-08-08 13:36 | 2026-08-08 13:36 | 2026-08-08 14:22 | 2026-08-08 14:44 | 2026-08-08 14:45 | 2026-08-08 14:45 | BrokenWire |  | Fair | No | Corrosion at pothead is the cause of customer no supply use 1 linket at same for repairs voltage found on arrival 81v/116v voltage left 111v/116v/227v
Outage | J.E.26.08.11156 | C001882846 | Stephen Taylor | St.Thomas | Completed | Load_245249 | Lysson - 410 | 2026-08-08 12:43 | 2026-08-08 12:46 | 2026-08-08 14:04 | 2026-08-08 14:05 | 2026-08-08 15:35 | 2026-08-08 15:35 | 2026-08-08 15:37 | 2026-08-08 15:37 |  |  | Fair | No | See junction link down no number on pole patrol see nothing and close up back junction with a 7 amp fuse customer is now okay
Outage | J.E.26.08.11188 | C001882845 | Stephen Taylor | St.Thomas | Completed | Load_577138 | Lysson - 410 | 2026-08-08 12:43 | 2026-08-08 12:46 | 2026-08-08 15:37 | 2026-08-08 15:38 | 2026-08-08 15:37 | 2026-08-08 15:37 | 2026-08-08 15:39 | 2026-08-08 15:39 |  |  | Fair | No | See junction down no number on pole patrol see nothing and close up back junction with a 10 amp fuse safely customer is now okay
Outage | J.E.26.08.10366 | C001882848 | Stephen Taylor | St.Thomas | Completed | Load_353202 | Good Year - 210 | 2026-08-08 12:45 | 2026-08-08 12:46 | 2026-08-08 15:40 | 2026-08-08 15:40 | 2026-08-08 15:40 | 2026-08-08 15:40 | 2026-08-08 15:41 | 2026-08-08 15:41 |  |  | Fair | No | Need more information a lot of call to customer no one answered the phone
Outage | J.E.26.08.10921 | C001882847 | Stephen Taylor | St.Thomas | Completed | Load_266529 | Good Year - 210 | 2026-08-08 12:45 | 2026-08-08 12:46 | 2026-08-08 13:31 | 2026-08-08 13:32 | 2026-08-08 13:52 | 2026-08-08 13:52 | 2026-08-08 13:59 | 2026-08-08 13:59 | BrokenWire |  | Fair | No | Clean up single phase and use 3 clamps customer is now ok reading 111,112,224 customer is now okay
Outage | J.E.26.08.11326 | C001882849 | Rusean Allen | KSAS | Completed | Load_269528 | Greenwich - 310 | 2026-08-08 12:47 | 2026-08-08 12:48 | 2026-08-08 16:58 | 2026-08-08 16:59 | 2026-08-08 17:16 | 2026-08-08 18:20 | 2026-08-08 18:20 | 2026-08-08 18:20 |  |  | Fair | No | Broken wire found at switch top, wire was reconnected
Outage | J.E.26.08.11388 | C001882853 | Edward Royal | KSAN | Completed | Load_252193 | Hope - 410 | 2026-08-08 13:22 | 2026-08-08 13:29 | 2026-08-08 14:31 | 2026-08-08 14:31 | 2026-08-08 14:31 | 2026-08-08 15:15 | 2026-08-08 15:15 | 2026-08-08 15:15 | LowHangingWires |  | Fair | No | Spliced and reconnected service cable using 2 single bolt clamp
Outage | J.E.26.08.11392 | C001882854 | Christopher Edwards | KSAN | Completed | Load_251185 | Constant Spring - 410 | 2026-08-08 13:26 | 2026-08-08 13:27 | 2026-08-08 13:56 | 2026-08-08 14:23 | 2026-08-08 15:46 | 2026-08-08 17:14 | 2026-08-08 17:14 | 2026-08-08 17:14 |  |  | Fair | No | Broken primary line3 spans of primary line is broken (covered conductor)Pole is severely leaning however a pole was planted beside it with all the primary attachment, wires just need to be spliced and transfer to new pole3 phase line is isolated at free town square
Outage | J.E.26.08.11369 | C001882855 | Daniel Francis | St.Ann | Completed | Load_254492 | Ocho Rios - 510 | 2026-08-08 13:31 | 2026-08-08 16:14 | 2026-08-08 17:52 | 2026-08-08 17:52 | 2026-08-08 18:16 | 2026-08-08 18:24 | 2026-08-08 18:29 | 2026-08-08 18:29 | BrokenWire |  | Fair | No | Found service wire missing requires 80 ft. customer says was broken by truck Not resolved
Outage | J.E.26.08.11389 | C001882858 | Neville Spencer | Clarendon | Completed | Load_350105 | May Pen - 110 | 2026-08-08 13:32 | 2026-08-08 14:41 | 2026-08-08 18:59 | 2026-08-08 18:59 | 2026-08-08 19:23 | 2026-08-08 19:23 | 2026-08-08 21:16 | 2026-08-08 21:16 | Fire |  | Fair | No | Splice and retention broken secondary phase Conductor used 30;ft wire, 2, clamps,1, preferred. Also renew blown 3 amp fuse protecting 25 kva xmfr at pole #0101861 supply restored.
Outage | J.E.26.08.11436 | C001882860 | Andre Smith | KSAS | Completed | Load_245690 | Greenwich - 510 | 2026-08-08 13:40 | 2026-08-08 13:41 | 2026-08-08 14:31 | 2026-08-08 14:31 | 2026-08-08 15:02 | 2026-08-08 15:02 | 2026-08-08 15:02 | 2026-08-08 15:02 | Fire |  | Fair | No | Replace defective hotline clamp supply restored
Outage | J.E.26.08.11357 | C001882863 | Tajay Bernard | Hanover | Completed | Load_252846 | Orange Bay - 210 | 2026-08-08 13:47 | 2026-08-08 13:49 | 2026-08-08 14:34 | 2026-08-08 14:34 | 2026-08-08 14:34 | 2026-08-08 14:50 | 2026-08-08 14:50 | 2026-08-08 14:50 |  |  | Fair | No | Customer stated the issue has been resolved
Outage | J.E.26.08.11430 | C001882866 | Wayne Dillion | St.Elizabeth | Completed | Load_262519 | Maggotty - 110 | 2026-08-08 14:00 | 2026-08-08 14:01 | 2026-08-08 14:53 | 2026-08-08 14:53 | 2026-08-08 14:53 | 2026-08-08 14:53 | 2026-08-08 14:55 | 2026-08-08 14:55 |  |  | Fair | No | Customer said supply was restored.
Outage | J.E.26.08.11431 | C001882867 | Wayne Dillion | St.Elizabeth | Completed | Load_244065 | Maggotty - 110 | 2026-08-08 14:00 | 2026-08-08 14:01 | 2026-08-08 14:55 | 2026-08-08 14:55 | 2026-08-08 14:55 | 2026-08-08 14:57 | 2026-08-08 14:57 | 2026-08-08 14:57 |  |  | Fair | No | Customer said supply was restored.
Outage | J.E.26.08.11432 | C001882868 | Wayne Dillion | St.Elizabeth | Completed | Load_266765 | Maggotty - 110 | 2026-08-08 14:00 | 2026-08-08 14:01 | 2026-08-08 14:57 | 2026-08-08 14:58 | 2026-08-08 14:58 | 2026-08-08 14:59 | 2026-08-08 14:59 | 2026-08-08 14:59 |  |  | Fair | No | Customer said supply was restored.
Outage | J.E.26.08.11325 | C001882869 | Denton Williams | Portland | Completed | Load_574173 | Port Antonio - 410 | 2026-08-08 14:01 | 2026-08-08 15:32 | 2026-08-08 15:39 | 2026-08-08 15:50 | 2026-08-08 15:49 | 2026-08-08 15:50 | 2026-08-08 15:51 | 2026-08-08 15:51 |  |  | Fair | No | Cannot locate any place goes by this name, cell number not assigned.
Outage | J.E.26.08.11390 | C001882870 | Richman Whyte | Westmoreland | Completed | Load_268428 | Paradise - 310 | 2026-08-08 14:02 | 2026-08-08 15:56 | 2026-08-08 18:26 | 2026-08-08 19:20 | 2026-08-08 19:20 | 2026-08-08 19:20 | 2026-08-08 19:20 | 2026-08-08 19:20 |  |  | Rains | No | Check and found okay
Outage | J.E.26.08.11393 | C001882872 | Richman Whyte | Westmoreland | Completed | Load_252107 | Paradise - 310 | 2026-08-08 14:02 | 2026-08-08 15:56 | 2026-08-08 19:40 | 2026-08-08 19:40 | 2026-08-08 20:12 | 2026-08-08 20:15 | 2026-08-08 20:15 | 2026-08-08 20:15 |  |  | Rains | No | Replace three amp twenty five kva transformer fuse
Outage | J.E.26.08.11513 | C001882871 | Javid Vernon | Westmoreland | Completed | Load_259245 | Paradise - 310 | 2026-08-08 14:02 | 2026-08-08 14:04 | 2026-08-08 14:18 | 2026-08-08 14:18 | 2026-08-09 07:00 | 2026-08-09 07:01 | 2026-08-09 07:02 | 2026-08-09 07:02 |  |  | Fair | No | Customer stated that the power was restored
Outage | J.E.26.08.11423 | C001882873 | Cliton Henry | St.Mary | Completed | Load_350137 | Oracabessa - 210 | 2026-08-08 14:09 | 2026-08-08 14:10 | 2026-08-08 14:18 | 2026-08-08 14:36 | 2026-08-08 14:36 | 2026-08-08 14:41 | 2026-08-08 14:42 | 2026-08-08 14:42 |  |  | Fair | No | RAMI infrastructure, the customer found disconnected and was reconnected by the assistance from the escalation team.
Outage | J.E.26.08.11429 | C001882874 | Cliton Henry | St.Mary | Completed | Load_264056 | Oracabessa - 210 | 2026-08-08 14:09 | 2026-08-08 14:10 | 2026-08-08 14:32 | 2026-08-08 14:33 | 2026-08-08 14:32 | 2026-08-08 14:35 | 2026-08-08 14:35 | 2026-08-08 14:35 |  |  | Fair | No | RAMI infrastructure, the customer found disconnected and was reconnected by the help of the escalation team and dispatch
Outage | J.E.26.08.11527 | C001882878 | Wan Carlos Scarlett | St.Catherine | Completed | Load_557334 | Twickenham - 210 | 2026-08-08 14:20 | 2026-08-08 14:44 | 2026-08-08 15:13 | 2026-08-08 15:14 | 2026-08-08 16:02 | 2026-08-08 16:54 | 2026-08-08 16:56 | 2026-08-08 16:56 | BrokenWire |  | Fair | No | Found one span of open secondary line phase jumper burn out from the one bolt clamp use 4 one bolt clamps at pole readings 116-117-234
Outage | J.E.26.08.11433 | C001882882 | Jowayne Newmans | St.Elizabeth | Completed | Load_268577 | Maggotty - 210 | 2026-08-08 14:24 | 2026-08-08 14:33 | 2026-08-08 17:49 | 2026-08-08 17:50 | 2026-08-08 17:50 | 2026-08-08 17:50 | 2026-08-08 17:50 | 2026-08-08 17:50 |  |  | Rains | No | After several attempts to contact customer phone rang without answering and no directions to customer premises.
Outage | J.E.26.08.11438 | C001882881 | Jowayne Newmans | St.Elizabeth | Completed | Load_268577 | Maggotty - 210 | 2026-08-08 14:24 | 2026-08-08 14:33 | 2026-08-08 17:48 | 2026-08-08 17:49 | 2026-08-08 17:48 | 2026-08-08 17:49 | 2026-08-08 17:49 | 2026-08-08 17:49 |  |  | Rains | No | After several attempts to contact customer phone rang without answering and no directions to customer premises.
Outage | J.E.26.08.11499 | C001882880 | Marlon Authors | St.Elizabeth | Completed | Load_258061 | Maggotty - 210 | 2026-08-08 14:24 | 2026-08-08 15:47 | 2026-08-08 16:30 | 2026-08-08 16:31 | 2026-08-08 16:30 | 2026-08-08 16:33 | 2026-08-08 16:33 | 2026-08-08 16:33 |  |  | Fair | No | Customer said supply was restored
Outage | J.E.26.08.11579 | C001882884 | Jowayne Newmans | Manchester | Completed | Load_258651 | Spur Tree - 210 | 2026-08-08 14:31 | 2026-08-08 14:33 | 2026-08-08 19:19 | 2026-08-08 19:20 | 2026-08-08 19:19 | 2026-08-08 19:20 | 2026-08-08 19:20 | 2026-08-08 19:20 |  |  | Fair | No | After several attempts to contact customer phone rang without answering and no directions to premises.
Outage | J.E.26.08.11581 | C001882883 | Jowayne Newmans | Manchester | Completed | Load_249534 | Spur Tree - 210 | 2026-08-08 14:31 | 2026-08-08 14:33 | 2026-08-08 15:01 | 2026-08-08 15:01 | 2026-08-08 15:01 | 2026-08-08 15:01 | 2026-08-08 15:01 | 2026-08-08 15:01 |  |  | Rains | No | Customer stated that they have electricity.
Non-Outage | J.E.26.08.11349 | C001882886 | Romaine Roberts |  | Completed |  |  | 2026-08-08 14:32 | 2026-08-08 14:34 | 2026-08-08 17:09 | 2026-08-08 17:09 | 2026-08-08 18:28 | 2026-08-08 01:00 | 2026-08-08 19:46 | 2026-08-08 19:46 | BrokenWire |  | Fair | No | Corrosion at pole and pothead clean and remake joints voltage 115-114 230
Outage | J.E.26.08.11355 | C001882885 | Romaine Roberts | St.Mary | Completed | Load_270058 | Annotto Bay - 210 | 2026-08-08 14:32 | 2026-08-08 14:34 | 2026-08-08 15:50 | 2026-08-08 15:51 | 2026-08-08 16:26 | 2026-08-08 17:01 | 2026-08-08 17:03 | 2026-08-08 17:03 | BrokenWire |  | Fair | No | Open and close 25 kva transformer to splice and retention 2 span of secondary neutral power restore
Outage | J.E.26.08.11541 | C001882887 | Romaine Roberts | St.Mary | Completed | Load_240813 | Highgate -110 | 2026-08-08 14:33 | 2026-08-08 14:34 | 2026-08-08 19:46 | 2026-08-08 19:47 | 2026-08-08 20:27 | 2026-08-08 21:22 | 2026-08-08 21:22 | 2026-08-08 21:22 |  |  | Fair | No | Junction fuse found blown patrol line and found bamboo on line clear bamboo and replace 15 and power restore
Outage | J.E.26.08.11498 | C001882889 | Omar King | St.Ann | Completed | Load_262903 | Upper White River - 210 | 2026-08-08 14:35 | 2026-08-08 14:36 | 2026-08-08 16:51 | 2026-08-09 15:58 | 2026-08-09 15:58 | 2026-08-09 15:59 | 2026-08-09 15:59 | 2026-08-09 15:59 |  |  | Fair | No | Found a 8 amp junction fuse blow cause by tree limb fuse as been replaced area is now with supply
Outage | J.E.26.08.11530 | C001882888 | Hartley Chin | St.Ann | Completed | Load_247405 | Cardiff Hall - 310 | 2026-08-08 14:35 | 2026-08-09 08:03 | 2026-08-09 08:07 | 2026-08-09 11:21 | 2026-08-09 11:20 | 2026-08-09 14:29 | 2026-08-09 14:30 | 2026-08-09 14:30 | BrokenWire | Y | Fair | No | Found 30 amp junction blown due to tree resting on line remove tree and refuse. NB No broken wire
Outage | J.E.26.08.11562 | C001882891 | Clyde Brown | Clarendon | Completed | Load_242439 | Parnassus - 210 | 2026-08-08 14:39 | 2026-08-08 14:41 | 2026-08-08 14:53 | 2026-08-08 14:54 | 2026-08-08 16:28 | 2026-08-08 16:40 | 2026-08-08 16:49 | 2026-08-08 16:49 |  |  | Rains | No | 25kva 13.8kv transformer burnt caused by lightning same isolated and need to be change as about 30 customers are left without supply also need fuse holder as fuse holder is burnt up.
Outage | J.E.26.08.11426 | C001882892 | Donald Cunningham | St.Catherine | Completed | Load_262179 | Rhodens Pen - 410 | 2026-08-08 14:41 | 2026-08-08 14:43 | 2026-08-08 18:38 | 2026-08-08 18:41 | 2026-08-08 18:43 | 2026-08-08 18:43 | 2026-08-08 18:44 | 2026-08-08 18:44 |  |  | Fair | No | Need more directions customer customer not reachable
Outage | J.E.26.08.11606 | C001882897 | Delano Gayle | St.Catherine | Completed | Load_248047 | New Michelton - 210 | 2026-08-08 14:46 | 2026-08-08 14:48 | 2026-08-08 14:51 | 2026-08-08 14:51 | 2026-08-08 16:34 | 2026-08-08 16:41 | 2026-08-08 16:41 | 2026-08-08 16:41 |  |  | Fair | No | Premises found okay power restored
Outage | J.E.26.08.11359 | C001882901 | Rusean Allen | KSAS | Completed | Load_301275 | Hunts Bay - 510 | 2026-08-08 14:49 | 2026-08-08 20:46 | 2026-08-08 20:51 | 2026-08-08 20:52 | 2026-08-08 20:59 | 2026-08-08 20:59 | 2026-08-08 21:00 | 2026-08-08 21:00 |  |  | Fair | No | Premises locked
Outage | J.E.26.08.11619 | C001882902 | Christopher Edwards | KSAN | Completed | Load_264085 | Constant Spring - 410 | 2026-08-08 14:51 | 2026-08-08 15:20 | 2026-08-08 17:27 | 2026-08-08 17:27 | 2026-08-08 18:18 | 2026-08-08 19:02 | 2026-08-08 19:03 | 2026-08-08 19:03 |  |  | Fair | No | Customer is having an internal issue Customer was advised to get electrician to rectify issue
Outage | J.E.26.08.11623 | C001882907 | Daniel Francis | St.Ann | Completed | Load_269957 | Roaring River - 210 | 2026-08-08 15:04 | 2026-08-08 15:10 | 2026-08-08 21:43 | 2026-08-08 21:44 | 2026-08-08 21:43 | 2026-08-08 23:48 | 2026-08-08 23:50 | 2026-08-08 23:50 |  |  | Fair | No | Hostile residents
Outage | J.E.26.08.11508 | C001882911 | Daniel Francis | St.Ann | Completed | Load_267462 | Upper White River - 210 | 2026-08-08 15:10 | 2026-08-08 15:12 | 2026-08-08 18:38 | 2026-08-08 18:38 | 2026-08-08 19:08 | 2026-08-08 19:25 | 2026-08-08 19:25 | 2026-08-08 19:25 |  |  | Fair | No | Found 25 kva transformer fuse blown at pole 0065966 one 3amp replace
Outage | J.E.26.08.11525 | C001882912 | Daniel Francis | St.Ann | Completed | Load_245180 | Ocho Rios - 410 | 2026-08-08 15:10 | 2026-08-08 15:11 | 2026-08-08 15:58 | 2026-08-08 15:58 | 2026-08-08 17:11 | 2026-08-08 17:47 | 2026-08-08 17:51 | 2026-08-08 17:51 |  |  | Fair | No | Replace fuse and fuse holder at0012671 5amp
Outage | J.E.26.08.11103 | C001882914 | Andre Williams | Trelawny | Completed | Load_266091 | Greenwood - 110 | 2026-08-08 15:13 | 2026-08-08 15:19 | 2026-08-08 15:31 | 2026-08-08 15:32 | 2026-08-08 15:31 | 2026-08-08 15:32 | 2026-08-08 15:33 | 2026-08-08 15:33 |  |  | Fair | No | Call located in Montego Bay side reffer to st James emergency
Outage | J.E.26.08.11425 | C001882913 | Andre Williams | Trelawny | Completed | Load_292887 | Greenwood - 210 | 2026-08-08 15:13 | 2026-08-08 15:19 | 2026-08-08 15:50 | 2026-08-08 15:53 | 2026-08-08 16:01 | 2026-08-08 16:02 | 2026-08-08 16:07 | 2026-08-08 16:07 |  |  | Fair | No | Power restored to premises customer reconnected with the help of meter center
Outage | J.E.26.08.11330 | C001882916 | Daniel Francis | St.Ann | Completed | Load_269957 | Roaring River - 210 | 2026-08-08 15:15 | 2026-08-08 15:17 | 2026-08-08 19:40 | 2026-08-08 19:41 | 2026-08-08 20:56 | 2026-08-08 21:26 | 2026-08-08 21:30 | 2026-08-08 21:30 |  |  | Fair | No | Hostile resident in area treating with violent
Outage | J.E.26.08.11667 | C001882915 | Milton Charlton | KSAS | Completed |  |  | 2026-08-08 15:15 | 2026-08-08 15:15 | 2026-08-08 15:31 | 2026-08-08 15:31 | 2026-08-08 15:31 | 2026-08-08 15:35 | 2026-08-08 15:40 | 2026-08-08 15:40 |  |  | Fair | No | Isolate three phase primary at pole#000080 to assist firemen to put out fire on a crossarm at pole #0001674. Isolator leaking at 3A glenview Terrace .
Outage | J.E.26.08.11259 | C001882917 | Daniel Francis | St.Ann | Completed | Load_262635 | Upper White River - 210 | 2026-08-08 15:16 | 2026-08-08 15:17 | 2026-08-08 19:38 | 2026-08-08 19:39 | 2026-08-08 19:38 | 2026-08-08 19:39 | 2026-08-08 19:40 | 2026-08-08 19:40 |  |  | Fair | No | We call customer and him say light come
Outage | J.E.26.08.11267 | C001882918 | Daniel Francis | St.Ann | Completed | Load_267462 | Upper White River - 210 | 2026-08-08 15:16 | 2026-08-08 15:22 | 2026-08-08 19:34 | 2026-08-08 19:34 | 2026-08-08 19:34 | 2026-08-08 19:36 | 2026-08-08 19:36 | 2026-08-08 19:36 |  |  | Fair | No | Power restored
Outage | J.E.26.08.11620 | C001882920 | Kaydon Taylor | KSAN | Completed | Load_264066 | West Kings House - 410 | 2026-08-08 15:19 | 2026-08-08 15:20 | 2026-08-08 15:31 | 2026-08-08 15:39 | 2026-08-08 16:20 | 2026-08-08 16:33 | 2026-08-08 16:33 | 2026-08-08 16:33 |  |  | Fair | No | Defective 5’ cross arm needs urgent replacement. Conductor is on top of the street light!.
Non-Outage | J.E.26.08.11502 | C001882921 | Donald Cunningham |  | Completed |  |  | 2026-08-08 15:26 | 2026-08-08 15:28 | 2026-08-08 17:03 | 2026-08-08 17:04 | 2026-08-08 18:27 | 2026-08-08 18:28 | 2026-08-08 18:37 | 2026-08-08 18:37 |  |  | Fair | No | Rami system in area need to check customer single phasing
Outage | J.E.26.08.11672 | C001882922 | Rusean Allen | KSAS | Completed | Load_254827 | Hunts Bay - 110 | 2026-08-08 15:27 | 2026-08-08 15:28 | 2026-08-08 18:20 | 2026-08-08 18:21 | 2026-08-08 18:30 | 2026-08-08 18:54 | 2026-08-08 18:54 | 2026-08-08 18:54 |  |  | Fair | No | Fuse barrel adjusted and re energized.
Outage | J.E.26.08.11696 | C001882933 | Richard Nicholas | St.Catherine | Completed | Load_259602 | Tredegar - 210 | 2026-08-08 15:39 | 2026-08-08 17:17 | 2026-08-08 21:37 | 2026-08-08 21:37 | 2026-08-08 21:52 | 2026-08-08 22:55 | 2026-08-08 22:57 | 2026-08-08 22:57 |  |  | Fair | No | Splice and retention 2 span of broken secondary neutral.2 clamp was used.replaced blown 30amp junctions fuse near to pole #0076307 and 50kva transformer 5amp fuse on pole #0079213.
Outage | J.E.26.08.11027 | C001882937 | Horace Malcolm | St.James | Completed | Load_267602 | Bogue - 310 | 2026-08-08 15:44 | 2026-08-08 15:56 | 2026-08-08 17:50 | 2026-08-08 17:50 | 2026-08-08 18:51 | 2026-08-08 19:00 | 2026-08-08 19:01 | 2026-08-08 19:01 |  |  | Fair | No | Check and found premises ok issue resolved voltage 113-116-229
Outage | J.E.26.08.11667 | C001882936 | Eric Williams | KSAS | Completed | Load_252238 | Up Park Camp - 410 | 2026-08-08 15:44 | 2026-08-08 15:45 | 2026-08-08 16:11 | 2026-08-08 16:11 | 2026-08-08 17:53 | 2026-08-08 17:53 | 2026-08-08 17:54 | 2026-08-08 17:54 |  |  | Fair | No | Defective insulator found and replaced
Outage | J.E.26.08.11639 | C001882938 | Romeo Brissett | St.James | Completed | Load_237651 | Bogue - 510 | 2026-08-08 15:45 | 2026-08-08 15:52 | 2026-08-08 16:01 | 2026-08-08 16:02 | 2026-08-08 16:38 | 2026-08-08 17:00 | 2026-08-08 17:21 | 2026-08-08 17:21 |  |  | Rains | No | Line patrolled and found power in the area, no fire found on line, no tree contact found.
Outage | J.E.26.08.11537 | C001882939 | Marlon Authors | St.Elizabeth | Completed | Load_266085 | Maggotty - 110 | 2026-08-08 15:48 | 2026-08-08 15:50 | 2026-08-08 20:50 | 2026-08-08 20:51 | 2026-08-08 21:46 | 2026-08-08 21:53 | 2026-08-08 21:53 | 2026-08-08 21:53 |  |  | Fair | No | Patrol and found clear. Reset trip type transformer circuit no pole #. Restored supply okay
Outage | J.E.26.08.11635 | C001882942 | Jowayne Newmans | St.Elizabeth | Completed | Load_246642 | Maggotty - 210 | 2026-08-08 15:48 | 2026-08-08 15:50 | 2026-08-08 16:17 | 2026-08-08 16:18 | 2026-08-08 16:25 | 2026-08-08 17:40 | 2026-08-08 17:48 | 2026-08-08 17:48 |  |  | Rains | No | Patrol and found 25kva transformer trip cause by service wire shorting out, repair by splicing and retention service wire using 5ft of #6 service wire and 2 one bolt clamps. Customer now have electricity.
Outage | J.E.26.08.11671 | C001882941 | Jowayne Newmans | St.Elizabeth | Completed | Load_240525 | Maggotty - 210 | 2026-08-08 15:48 | 2026-08-08 15:50 | 2026-08-08 17:55 | 2026-08-08 17:55 | 2026-08-08 18:39 | 2026-08-08 18:58 | 2026-08-08 18:58 | 2026-08-08 18:58 | Fire |  | Rains | No | Patrol and found 25 kva transformer fuse blown cause by bad weather, repair by replacing 3 amp fuse. Customers now have electricity.
Outage | J.E.26.08.11697 | C001882940 | Marlon Authors | St.Elizabeth | Completed | Load_250050 | Maggotty - 110 | 2026-08-08 15:48 | 2026-08-08 15:50 | 2026-08-08 17:36 | 2026-08-08 17:36 | 2026-08-08 17:36 | 2026-08-08 20:13 | 2026-08-08 19:14 | 2026-08-08 19:14 |  |  | Fair | No | Patrol and found clear. Replace one blown 10 amp junction fuse at pole #008553 and one 2 amp fuse that protects 25 kva transformer circuit at pole #618541. Further checks revealed that the transformer is burnt . Please refer same to the maintenance department for replacement. Approximately 12 customers are without supply
Outage | J.E.26.08.11494 | C001882943 | Horace Malcolm | St.James | Completed | Load_242308 | Bogue - 310 | 2026-08-08 15:52 | 2026-08-08 15:54 | 2026-08-08 16:26 | 2026-08-08 16:26 | 2026-08-08 16:26 | 2026-08-08 16:27 | 2026-08-08 16:27 | 2026-08-08 16:27 |  |  | Fair | No | Customer got disconnected
Outage | J.E.26.08.11636 | C001882944 | Horace Malcolm | St.James | Completed | Load_301686 | Bogue - 310 | 2026-08-08 15:52 | 2026-08-08 15:54 | 2026-08-08 17:07 | 2026-08-08 17:07 | 2026-08-08 17:45 | 2026-08-08 17:50 | 2026-08-08 17:50 | 2026-08-08 17:50 |  |  | Fair | No | Check and found ok voltage 113-115-228
Outage | J.E.26.08.11692 | C001882945 | Horace Malcolm | St.James | Completed | Load_251499 | Queens Drive - 710 | 2026-08-08 15:52 | 2026-08-08 15:54 | 2026-08-08 16:39 | 2026-08-08 16:39 | 2026-08-08 17:00 | 2026-08-08 17:05 | 2026-08-08 17:05 | 2026-08-08 17:05 |  |  | Fair | No | Unable to locate customer multiple calls to customer unavailable no directions given
Outage | J.E.26.08.11675 | C001882949 | Richman Whyte | Westmoreland | Completed | Load_267689 | Paradise - 310 | 2026-08-08 15:53 | 2026-08-08 15:55 | 2026-08-08 21:59 | 2026-08-08 22:00 | 2026-08-08 22:00 | 2026-08-08 22:00 | 2026-08-08 22:01 | 2026-08-08 22:01 |  |  | Rains | No | Restore with the closing of the twenty five amp junction fuse
Non-Outage | J.E.26.08.10445 | C001882950 | Richman Whyte |  | Completed |  |  | 2026-08-08 15:54 | 2026-08-08 15:57 | 2026-08-08 19:21 | 2026-08-08 19:21 | 2026-08-08 19:33 | 2026-08-08 19:38 | 2026-08-08 19:39 | 2026-08-08 19:39 |  |  | Rains | No | Replace 3 amp 25kva transformer fuse
Outage | J.E.26.08.11607 | C001882951 | Richman Whyte | Westmoreland | Completed | Load_240662 | Paradise - 310 | 2026-08-08 15:56 | 2026-08-08 16:01 | 2026-08-08 17:26 | 2026-08-08 17:27 | 2026-08-08 17:46 | 2026-08-08 18:22 | 2026-08-08 18:23 | 2026-08-08 18:23 |  |  | Rains | No | Replace 15amp junction fuse at farm and two 2amp twenty five kva transformer fuse at McAlpine
Outage | J.E.26.08.11124 | C001882954 | Horace Malcolm | St.James | Completed | Load_260146 | Queens Drive - 710 | 2026-08-08 15:58 | 2026-08-08 16:03 | 2026-08-08 16:27 | 2026-08-08 16:28 | 2026-08-08 16:37 | 2026-08-08 16:38 | 2026-08-08 16:38 | 2026-08-08 16:38 |  |  | Fair | No | Check and found no supply coming from meter rami meter referred to field service
Outage | J.E.26.08.11604 | C001882955 | Barnett Brown | Manchester | Completed | Load_240794 | Spur Tree - 210 | 2026-08-08 15:59 | 2026-08-08 17:51 | 2026-08-08 20:27 | 2026-08-08 20:27 | 2026-08-08 21:39 | 2026-08-08 21:39 | 2026-08-08 21:48 | 2026-08-08 21:48 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.11600 | C001882958 | Jowayne Newmans | Manchester | Completed | Load_266485 | Spur Tree - 210 | 2026-08-08 16:00 | 2026-08-08 17:06 | 2026-08-08 19:24 | 2026-08-08 19:24 | 2026-08-08 19:24 | 2026-08-08 19:24 | 2026-08-08 19:25 | 2026-08-08 19:25 |  |  | Fair | No | Customer stated that they got back electricity.
Outage | J.E.26.08.11601 | C001882957 | Jowayne Newmans | Manchester | Completed | Load_244043 | Spur Tree - 210 | 2026-08-08 16:00 | 2026-08-08 16:02 | 2026-08-08 21:40 | 2026-08-08 21:41 | 2026-08-08 21:41 | 2026-08-08 21:41 | 2026-08-08 21:41 | 2026-08-08 21:41 |  |  | Fair | No | Customer stated that they got back electricity.
Outage | J.E.26.08.11605 | C001882956 | Jowayne Newmans | St.Elizabeth | Completed | Load_292683 | Maggotty - 210 | 2026-08-08 16:00 | 2026-08-08 16:02 | 2026-08-08 19:01 | 2026-08-08 19:02 | 2026-08-08 19:18 | 2026-08-08 19:19 | 2026-08-08 19:19 | 2026-08-08 19:19 |  |  | Fair | No | Patrol and found all customers in the area with supply.
Non-Outage | J.E.26.08.09807 | C001882959 | Richman Whyte | St.Elizabeth | Completed | Load_245885 | Maggotty - 110 | 2026-08-08 16:03 | 2026-08-08 16:04 | 2026-08-08 17:06 | 2026-08-08 17:07 | 2026-08-08 17:25 | 2026-08-08 17:25 | 2026-08-08 17:26 | 2026-08-08 17:26 |  |  | Rains | No | Close back three twenty amp junction fuse
Outage | J.E.26.08.11677 | C001882961 | Barnett Brown | Manchester | Completed | Load_240176 | Porus - 310 | 2026-08-08 16:05 | 2026-08-08 16:07 | 2026-08-08 17:00 | 2026-08-08 17:00 | 2026-08-08 19:46 | 2026-08-08 20:17 | 2026-08-08 20:25 | 2026-08-08 20:25 |  |  | Fair | No | 40 class 4 tde with secondary line, rotten and break at root. Trees need to cut also
Outage | J.E.26.08.11644 | C001882965 | Richard Samuda | Manchester | Completed | Load_253480 | Kendal - 210 | 2026-08-08 16:06 | 2026-08-08 16:08 | 2026-08-08 17:50 | 2026-08-08 17:51 | 2026-08-08 17:50 | 2026-08-08 17:52 | 2026-08-08 17:52 | 2026-08-08 17:52 |  |  | Rains | No | Call to phone no answer premises not found
Outage | J.E.26.08.11649 | C001882963 | Richard Samuda | Manchester | Completed | Load_260724 | Kendal - 210 | 2026-08-08 16:06 | 2026-08-08 16:08 | 2026-08-08 17:25 | 2026-08-08 17:25 | 2026-08-08 17:41 | 2026-08-08 05:44 | 2026-08-08 17:44 | 2026-08-08 17:44 | LeaningPole |  | Rains | No | Leaning primary t pole 40ftconcrete pole , pole needs to be replaced customer concern pole may fall refer call to maintenance
Outage | J.E.26.08.11650 | C001882962 | Richard Samuda | Manchester | Completed | Load_303017 | Kendal - 210 | 2026-08-08 16:06 | 2026-08-08 16:08 | 2026-08-08 16:19 | 2026-08-08 16:20 | 2026-08-08 16:59 | 2026-08-08 17:23 | 2026-08-08 17:23 | 2026-08-08 17:23 |  |  | Rains | No | Found 25 amp junction blown patrol line found nothing replaced fuse close line customer back to normal
Outage | J.E.26.08.11651 | C001882964 | Richard Samuda | Manchester | Completed | Load_303019 | Kendal - 210 | 2026-08-08 16:06 | 2026-08-08 16:08 | 2026-08-08 17:23 | 2026-08-08 17:24 | 2026-08-08 17:23 | 2026-08-08 17:24 | 2026-08-08 17:25 | 2026-08-08 17:25 |  |  | Rains | No | Customer said Power was restored
Outage | J.E.26.08.11729 | C001882966 | Richard Nicholas | St.Catherine | Completed | Load_260382 | Twickenham - 310 | 2026-08-08 16:08 | 2026-08-08 16:10 | 2026-08-08 18:20 | 2026-08-08 18:20 | 2026-08-08 19:54 | 2026-08-08 20:38 | 2026-08-08 20:42 | 2026-08-08 20:42 |  |  | Fair | No | Temporary repair done to dislodged transformer drop out switch due to a burnt off 4ft cross arm.replaced blown 40amp junctions fuse on pole #045009 and blown 8amp junctions fuse on pole #527791.follow up to replaced damaged cross arm is required.
Outage | J.E.26.08.11730 | C001882967 | Richard Nicholas | St.Catherine | Completed | Load_1000937 | Tredegar - 410 | 2026-08-08 16:08 | 2026-08-08 16:10 | 2026-08-08 17:19 | 2026-08-08 17:19 | 2026-08-08 17:44 | 2026-08-08 18:18 | 2026-08-08 18:19 | 2026-08-08 18:19 |  |  | Fair | No | Replaced blown 30amp junctions fuse on pole #008104 and blown 15amp junctions fuse at single phase T-off to 19 march pen road.
Outage | J.E.26.08.11683 | C001882968 | Neville Spencer | Clarendon | Completed | Load_255475 | May Pen - 110 | 2026-08-08 16:11 | 2026-08-08 16:20 | 2026-08-08 21:16 | 2026-08-08 21:40 | 2026-08-08 21:39 | 2026-08-08 22:14 | 2026-08-08 22:19 | 2026-08-08 22:19 | BrokenWire |  | Fair | No | Open 25 kva xmf at pole # 0101856 installed 90 ft #6 triplex, 2 clamps, 3, 6/6 sleeves voltage reading 114 117 232 supply restored.
Outage | J.E.26.08.10929 | C001882969 | Tajay Bernard | Hanover | Completed | Load_292847 | Orange Bay - 310 | 2026-08-08 16:12 | 2026-08-08 16:14 | 2026-08-08 16:17 | 2026-08-08 16:28 | 2026-08-08 16:32 | 2026-08-08 16:34 | 2026-08-08 16:34 | 2026-08-08 16:34 |  |  | Fair | No | Operation department is handling the situation
Outage | J.E.26.08.11742 | C001882970 | Horace Malcolm | St.James | Completed | Load_257603 | Queens Drive - 710 | 2026-08-08 16:15 | 2026-08-08 16:17 | 2026-08-08 20:49 | 2026-08-08 20:50 | 2026-08-08 21:15 | 2026-08-08 21:24 | 2026-08-08 21:24 | 2026-08-08 21:24 |  |  | Fair | No | Unable to locate customer or premises from the direction given
Outage | J.E.26.08.11752 | C001882971 | Milton Charlton | KSAS | Completed | Load_238550 | Up Park Camp - 410 | 2026-08-08 16:22 | 2026-08-08 16:23 | 2026-08-08 16:28 | 2026-08-08 16:29 | 2026-08-08 17:12 | 2026-08-08 17:15 | 2026-08-08 17:14 | 2026-08-08 17:14 |  |  | Fair | No | Reset customer main circuit breaker.
Outage | J.E.26.08.11764 | C001882974 | Richard Nicholas | St.Catherine | Completed | Load_240246 | Tredegar - 310 | 2026-08-08 16:29 | 2026-08-08 16:33 | 2026-08-08 20:44 | 2026-08-08 20:44 | 2026-08-08 21:04 | 2026-08-08 21:33 | 2026-08-08 21:35 | 2026-08-08 21:35 |  |  | Fair | No | Replaced blown 30amp x3 junctions fuse and a fuse holder on pole #0030471 and blown 100kva transformer 10amp x2 fuse at the plaza however transformer and pole covered with vegetation.please refer to the bushing team.
Outage | J.E.26.08.11725 | C001882975 | Christopher Edwards | KSAN | Completed | Load_253873 | Constant Spring - 410 | 2026-08-08 16:30 | 2026-08-08 16:30 | 2026-08-08 17:15 | 2026-08-08 17:15 | 2026-08-08 17:15 | 2026-08-08 17:26 | 2026-08-08 17:27 | 2026-08-08 17:27 |  |  | Fair | No | Reclose 50 amps trip saver
Outage | J.E.26.08.11721 | C001882978 | Hartley Chin | St.Ann | Completed | Load_262654 | Cardiff Hall - 310 | 2026-08-08 16:45 | 2026-08-09 08:17 | 2026-08-09 14:32 | 2026-08-09 14:33 | 2026-08-09 14:32 | 2026-08-09 14:32 | 2026-08-09 14:33 | 2026-08-09 14:33 |  |  | Fair | No | Call related to 11530
Outage | J.E.26.08.11760 | C001882980 | Denton Williams | Portland | Completed | Load_265666 | Port Antonio - 310 | 2026-08-08 16:51 | 2026-08-08 16:51 | 2026-08-08 17:39 | 2026-08-08 17:40 | 2026-08-08 18:14 | 2026-08-08 18:30 | 2026-08-08 18:33 | 2026-08-08 18:33 |  |  | Fair | No | Defective 25kva transformer single bushing. A replacement is needed.
Outage | J.E.26.08.11786 | C001882981 | Kaydon Taylor | KSAN | Completed |  |  | 2026-08-08 16:57 | 2026-08-08 16:58 | 2026-08-08 18:01 | 2026-08-08 18:02 | 2026-08-08 18:01 | 2026-08-08 18:05 | 2026-08-08 18:05 | 2026-08-08 18:05 |  |  | Fair | No | Isolate 25 kva at pole #0057471 to carry out repair. 6 clamps 12’ of # 6 service wire to repair 4 service neutrals .note defective 5’ cross arm needs to replace urgently
Non-Outage | J.E.26.08.11748 | C001882985 | Stephen Taylor |  | Completed |  |  | 2026-08-08 17:00 | 2026-08-08 19:06 | 2026-08-09 13:49 | 2026-08-09 13:50 | 2026-08-09 13:49 | 2026-08-09 13:49 | 2026-08-09 13:51 | 2026-08-09 13:51 |  |  | Fair | No | Call to customer and someone answered and said it the wrong number he have no problem with jps
Outage | J.E.26.08.11025 | C001882983 | Stephen Taylor | St.Thomas | Completed | Load_260689 | Good Year - 110 | 2026-08-08 17:00 | 2026-08-08 17:01 | 2026-08-08 17:25 | 2026-08-08 17:59 | 2026-08-08 18:49 | 2026-08-08 18:50 | 2026-08-08 18:51 | 2026-08-08 18:51 |  |  | Fair | No | Patrol see nothing and close up back 25 amp transformer with a 3 amp fuse all customer is now okay
Outage | J.E.26.08.11245 | C001882984 | Stephen Taylor | St.Thomas | Completed | Load_266440 | Good Year - 210 | 2026-08-08 17:00 | 2026-08-08 17:01 | 2026-08-09 13:53 | 2026-08-09 13:53 | 2026-08-09 13:53 | 2026-08-09 13:53 | 2026-08-09 13:54 | 2026-08-09 13:54 |  |  | Fair | No | Call to customer and customer said power is back now and okay
Outage | J.E.26.08.11731 | C001882982 | Stephen Taylor | St.Thomas | Completed | Load_353202 | Good Year - 210 | 2026-08-08 17:00 | 2026-08-08 17:01 | 2026-08-08 18:52 | 2026-08-08 18:52 | 2026-08-08 19:32 | 2026-08-08 19:32 | 2026-08-08 19:32 | 2026-08-08 19:32 |  |  | Fair | No | Need more information a lot of call to customer no one answered the phone
Outage | J.E.26.08.11773 | C001882986 | Marlon Authors | St.Elizabeth | Completed | Load_568349 | Maggotty - 210 | 2026-08-08 17:05 | 2026-08-08 17:05 | 2026-08-08 20:38 | 2026-08-08 20:38 | 2026-08-08 20:38 | 2026-08-08 20:50 | 2026-08-08 20:50 | 2026-08-08 20:50 |  |  | Fair | No | Patrol and found clear. Replace one blown 10 amp junction fuse at pole #610886. Restored supply ok
Outage | J.E.26.08.11812 | C001882988 | Wan Carlos Scarlett | Portmore | Completed | Load_263898 | Naggo Head - 510 | 2026-08-08 17:22 | 2026-08-08 17:24 | 2026-08-08 17:52 | 2026-08-08 17:53 | 2026-08-08 19:05 | 2026-08-08 19:19 | 2026-08-08 19:22 | 2026-08-08 19:22 |  |  | Fair | No | Found customer 2 wire service at pothead with phase and neutral corroded use 2 Penn union at pothead reading 115
Outage | J.E.26.08.11798 | C001882989 | Tajay Bernard | Hanover | Completed | Load_575056 | Orange Bay - 310 | 2026-08-08 17:30 | 2026-08-08 17:34 | 2026-08-08 17:39 | 2026-08-08 17:40 | 2026-08-08 18:18 | 2026-08-08 19:53 | 2026-08-08 19:56 | 2026-08-08 19:56 |  |  | Fair | No | Customer stated that power was fluctuating from 9am to 5am
Outage | J.E.26.08.11833 | C001882991 | Romeo Brissett | St.James | Completed | Load_237651 | Bogue - 510 | 2026-08-08 17:53 | 2026-08-08 17:54 | 2026-08-08 18:02 | 2026-08-08 18:03 | 2026-08-08 19:37 | 2026-08-08 19:45 | 2026-08-08 19:50 | 2026-08-08 19:50 | Fire |  | Fair | No | Check and found customer meter burned due to defective meter socket. Disconnected customer pothead, unable to reach customer on the phone.
Outage | J.E.26.08.11790 | C001882992 | Richard Nicholas | St.Catherine | Completed | Load_254944 | Twickenham - 310 | 2026-08-08 17:57 | 2026-08-08 18:09 | 2026-08-08 20:43 | 2026-08-08 20:43 | 2026-08-08 20:43 | 2026-08-08 20:43 | 2026-08-08 20:43 | 2026-08-08 20:43 | Fire |  | Fair | No | Found ok
Outage | J.E.26.08.11840 | C001882994 | Neville Spencer | Clarendon | Completed | Load_246673 | May Pen - 110 | 2026-08-08 18:03 | 2026-08-08 18:26 | 2026-08-08 18:52 | 2026-08-08 18:53 | 2026-08-08 18:56 | 2026-08-08 18:56 | 2026-08-08 18:58 | 2026-08-08 18:58 |  |  | Fair | No | Renew blown 15 amp j/ fuse at pole # 0155424 area restored.
Non-Outage | J.E.26.08.11811 | C001882997 | Richman Whyte |  | Completed |  |  | 2026-08-08 18:11 | 2026-08-08 18:45 | 2026-08-08 20:16 | 2026-08-08 20:17 | 2026-08-08 20:17 | 2026-08-08 20:17 | 2026-08-08 20:17 | 2026-08-08 20:17 |  |  | Fair | No | Restore earlier
Outage | J.E.26.08.11805 | C001882998 | Richman Whyte | Westmoreland | Completed | Load_252107 | Paradise - 310 | 2026-08-08 18:11 | 2026-08-08 18:16 | 2026-08-08 20:16 | 2026-08-08 20:16 | 2026-08-08 20:16 | 2026-08-08 20:16 | 2026-08-08 20:16 | 2026-08-08 20:16 |  |  | Rains | No | Replace three amp twenty five kva transformer fuse
Outage | J.E.26.08.11838 | C001882995 | Richman Whyte | Westmoreland | Completed | Load_255234 | Paradise - 310 | 2026-08-08 18:11 | 2026-08-08 18:16 | 2026-08-08 20:22 | 2026-08-08 20:22 | 2026-08-08 21:43 | 2026-08-08 21:52 | 2026-08-08 21:59 | 2026-08-08 21:59 | Fire |  | Fair | No | Replace twenty five amp junction fuse
Outage | J.E.26.08.11842 | C001882996 | Oshane Warren | Westmoreland | Completed | Load_263858 | Paradise - 110 | 2026-08-08 18:11 | 2026-08-08 18:16 | 2026-08-08 20:30 | 2026-08-08 20:31 | 2026-08-08 20:30 | 2026-08-08 20:31 | 2026-08-08 20:31 | 2026-08-08 20:31 |  |  | Rains | No | Replace 25 amp junction fuse
Outage | J.E.26.08.11847 | C001882999 | Oshane Warren | Westmoreland | Completed | Load_248383 | Paradise - 110 | 2026-08-08 18:11 | 2026-08-08 18:16 | 2026-08-08 18:27 | 2026-08-08 18:27 | 2026-08-08 20:28 | 2026-08-08 20:28 | 2026-08-08 20:29 | 2026-08-08 20:29 |  |  | Rains | No | Replace 25 amp junction fuse
Outage | J.E.26.08.11620 | C001883000 | Eric Williams | KSAN | Completed | Load_264066 | West Kings House - 410 | 2026-08-08 18:12 | 2026-08-08 18:15 | 2026-08-08 18:17 | 2026-08-08 18:18 | 2026-08-08 19:19 | 2026-08-08 19:21 | 2026-08-08 19:23 | 2026-08-08 19:23 |  |  | Fair | No | defective insulator found and replaced
Outage | J.E.26.08.11786 | C001883001 | Eric Williams | KSAN | Completed | Load_258637 | Constant Spring - 210 | 2026-08-08 18:12 | 2026-08-08 18:14 | 2026-08-08 19:23 | 2026-08-08 19:24 | 2026-08-08 19:52 | 2026-08-08 21:27 | 2026-08-08 21:27 | 2026-08-08 21:27 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.11777 | C001883002 | Jowayne Newmans | Manchester | Completed | Load_265228 | Spur Tree - 210 | 2026-08-08 18:17 | 2026-08-08 18:50 | 2026-08-08 19:30 | 2026-08-08 19:31 | 2026-08-08 20:53 | 2026-08-08 21:36 | 2026-08-08 21:40 | 2026-08-08 21:40 | Fire |  | Fair | No | Patrol and found customer without supply cause by motor vehicle accident that damaged customer meter pole, meter was damaged and will need to be replaced when customer fix their meter pole. Customer is left without electricity.
Outage | J.E.26.08.11873 | C001883003 | Delano Gayle | St.Catherine | Completed | Load_265577 | Twickenham - 310 | 2026-08-08 18:22 | 2026-08-08 18:25 | 2026-08-08 18:29 | 2026-08-08 18:29 | 2026-08-08 18:55 | 2026-08-08 20:00 | 2026-08-08 20:00 | 2026-08-08 20:00 | Fire |  | Fair | No | Broken secondary phase in 1 span, burnt #6 phase joint, vegetation on line, open 25kva transformer fuse no pole number, remove vegetation, splice and retention phase use 30ft #2aa, 1 #2 preform, 4 clamps, repair burnt #6 phase use 1 clamp, close transformer fuse voltage readings 115-116-231
Outage | J.E.26.08.11852 | C001883005 | Wan Carlos Scarlett | Portmore | Completed | Load_240625 | Naggo Head - 510 | 2026-08-08 18:26 | 2026-08-08 18:38 | 2026-08-08 21:54 | 2026-08-08 21:55 | 2026-08-08 22:21 | 2026-08-08 23:26 | 2026-08-08 23:38 | 2026-08-08 23:38 |  |  | Fair | No | Customer not available at this time premises closed
Outage | J.E.26.08.11856 | C001883004 | Wan Carlos Scarlett | St.Catherine | Completed | Load_243421 | Twickenham - 210 | 2026-08-08 18:26 | 2026-08-08 18:38 | 2026-08-08 19:22 | 2026-08-08 19:23 | 2026-08-08 19:51 | 2026-08-08 20:40 | 2026-08-08 20:41 | 2026-08-08 20:41 |  |  | Fair | No | Found customer with internal problem advised customer to get a licensed electrician to fix the problem.customer meter socket defective
Outage | J.E.26.08.11898 | C001883006 | Clyde Brown | Clarendon | Completed | Load_258999 | Monymusk - 410 | 2026-08-08 18:36 | 2026-08-08 19:02 | 2026-08-08 19:20 | 2026-08-08 19:20 | 2026-08-08 20:32 | 2026-08-08 20:32 | 2026-08-08 20:38 | 2026-08-08 20:38 | Fire |  | Fair | No | Found voltage ok reading 116/109 and 225V
Outage | J.E.26.08.11895 | C001883007 | Rusean Allen | KSAS | Completed | Load_242532 | Cane River - 610 | 2026-08-08 18:37 | 2026-08-08 18:38 | 2026-08-08 20:29 | 2026-08-08 20:30 | 2026-08-08 20:31 | 2026-08-08 20:31 | 2026-08-08 20:32 | 2026-08-08 20:32 |  |  | Fair | No | Related to 12 Florizel avenue
Outage | J.E.26.08.11905 | C001883009 | Rusean Allen | KSAS | Completed | Load_243254 | Cane River - 610 | 2026-08-08 18:46 | 2026-08-08 18:52 | 2026-08-08 19:27 | 2026-08-08 19:28 | 2026-08-08 20:01 | 2026-08-08 20:29 | 2026-08-08 20:29 | 2026-08-08 20:29 |  |  | Fair | No | 1x 40amp fuse found 1x 40amp fuse replaced.
Outage | J.E.26.08.11788 | C001883011 | Jowayne Newmans | St.Elizabeth | Completed | Load_268766 | Maggotty - 210 | 2026-08-08 18:49 | 2026-08-08 18:50 | 2026-08-08 22:08 | 2026-08-08 22:09 | 2026-08-08 22:08 | 2026-08-08 22:09 | 2026-08-08 22:09 | 2026-08-08 22:09 |  |  | Fair | No | After several attempts to contact customer phone went unanswered and no directions to premises.
Outage | J.E.26.08.11851 | C001883013 | Stephen Taylor | St.Thomas | Completed | Load_250441 | Good Year - 110 | 2026-08-08 18:51 | 2026-08-08 18:53 | 2026-08-09 13:42 | 2026-08-09 13:47 | 2026-08-09 13:47 | 2026-08-09 13:00 | 2026-08-09 13:49 | 2026-08-09 13:49 |  |  | Fair | No | Failed to locate customer several calls but no one answering the phone need more information
Outage | J.E.26.08.11869 | C001883012 | Stephen Taylor | St.Thomas | Completed | Load_245650 | Good Year - 210 | 2026-08-08 18:51 | 2026-08-08 18:53 | 2026-08-08 19:40 | 2026-08-08 19:41 | 2026-08-08 19:40 | 2026-08-08 19:41 | 2026-08-08 19:42 | 2026-08-08 19:42 | BrokenWire |  | Fair | No | Patrol the area power is in the area a lot of call to single customer no one answered the phone need a Jamaican phone number also
Outage | J.E.26.08.11914 | C001883014 | Horace Malcolm | St.James | Completed | Load_301686 | Bogue - 310 | 2026-08-08 18:53 | 2026-08-08 18:53 | 2026-08-08 19:32 | 2026-08-08 19:32 | 2026-08-08 20:45 | 2026-08-08 20:47 | 2026-08-08 20:47 | 2026-08-08 20:47 |  |  | Fair | No | Clear banging secondary and nuetral line tie up together and reset one 25kva transformer
Outage | J.E.26.08.11888 | C001883016 | Andre Williams | Trelawny | Completed | Load_262089 | Martha Brae - 210 | 2026-08-08 18:54 | 2026-08-08 18:58 | 2026-08-08 19:05 | 2026-08-08 19:07 | 2026-08-08 19:38 | 2026-08-08 19:40 | 2026-08-08 19:44 | 2026-08-08 19:44 |  |  | Fair | No | Clean coroded joints at pothead on two customer #6 three wire service, voltage at pole 116+114=230
Outage | J.E.26.08.11844 | C001883018 | Romaine Roberts | St.Mary | Completed | Load_255715 | Highgate -110 | 2026-08-08 18:58 | 2026-08-08 19:01 | 2026-08-08 22:40 | 2026-08-08 22:40 | 2026-08-08 22:40 | 2026-08-08 22:40 | 2026-08-08 22:41 | 2026-08-08 22:41 |  |  | Fair | No | Junction fuse found blown patrol line nothing found replace 20 to restore power no pole number
Outage | J.E.26.08.11872 | C001883020 | Cliton Henry | St.Ann | Completed | Load_354886 | Upper White River - 110 | 2026-08-08 18:58 | 2026-08-08 19:00 | 2026-08-08 19:32 | 2026-08-08 19:32 | 2026-08-08 20:16 | 2026-08-08 20:16 | 2026-08-08 20:18 | 2026-08-08 20:18 |  |  | Fair | No | The customer stated that the supply was restored approximately 2 hours ago
Outage | J.E.26.08.11831 | C001883021 | Romaine Roberts | St.Mary | Completed | Load_251228 | Highgate -110 | 2026-08-08 19:01 | 2026-08-08 19:01 | 2026-08-08 21:25 | 2026-08-08 21:26 | 2026-08-08 22:17 | 2026-08-08 22:35 | 2026-08-08 22:37 | 2026-08-08 22:37 | BrokenWire |  | Fair | No | Junction fuse found blown patrol line nothing found replace 20 to restore power no pole number
Outage | J.E.26.08.11917 | C001883022 | Raymond Lewis | St.Ann | Completed | Load_242078 | Cardiff Hall - 310 | 2026-08-08 19:02 | 2026-08-08 23:19 | 2026-08-09 03:10 | 2026-08-09 03:11 | 2026-08-09 03:10 | 2026-08-09 03:26 | 2026-08-09 03:26 | 2026-08-09 03:26 | BrokenWire |  | Fair | No | Phone number not working
Outage | J.E.26.08.11863 | C001883024 | Tajay Bernard | Hanover | Completed | Load_256375 | Orange Bay - 310 | 2026-08-08 19:10 | 2026-08-08 21:07 | 2026-08-08 21:13 | 2026-08-08 21:31 | 2026-08-08 22:02 | 2026-08-08 22:17 | 2026-08-08 22:18 | 2026-08-08 22:18 |  |  | Fair | No | Refuse 1 10amp junction fuse
Outage | J.E.26.08.11947 | C001883025 | Clyde Brown | Clarendon | Completed | Load_258277 | Parnassus - 210 | 2026-08-08 19:12 | 2026-08-08 19:13 | 2026-08-08 20:49 | 2026-08-08 20:50 | 2026-08-08 20:49 | 2026-08-08 20:49 | 2026-08-08 20:54 | 2026-08-08 20:54 | Fire |  | Fair | No | Customer said she did not make call to JPS
Non-Outage | J.E.26.08.11958 | C001883027 | Rusean Allen |  | Completed |  |  | 2026-08-08 19:19 | 2026-08-08 19:21 | 2026-08-08 21:09 | 2026-08-08 21:09 | 2026-08-08 21:27 | 2026-08-09 09:06 | 2026-08-09 09:06 | 2026-08-09 09:06 | Fire |  | Fair | No | Transformer defective needs to change Transformer is single phasing Refer to maintenance department
Outage | J.E.26.08.11760 | C001883028 | Denton Williams | Portland | Completed | Load_265666 | Port Antonio - 310 | 2026-08-08 19:20 | 2026-08-08 19:20 | 2026-08-08 19:35 | 2026-08-08 19:36 | 2026-08-08 20:55 | 2026-08-08 20:56 | 2026-08-08 21:04 | 2026-08-08 21:04 |  |  | Fair | No | Replace defective 25kva transformer. Material used one 3amps fuse and 3 one bolt clamp. Area is now restored. Voltage readings leave 120v, 120v, & 241v. Amps readings 45amps, 66amps.
Outage | J.E.26.08.11938 | C001883029 | Marlon Authors | St.Elizabeth | Completed | Load_253590 | Maggotty - 110 | 2026-08-08 19:21 | 2026-08-08 19:22 | 2026-08-08 19:40 | 2026-08-08 19:41 | 2026-08-08 19:42 | 2026-08-08 20:07 | 2026-08-08 20:07 | 2026-08-08 20:07 |  |  | Fair | No | Patrol and found clear. Replace one blown 20 amp junction fuse no pole #and one blown 2 amp fuse that protects 25 kva transformer no pole #. Restored supply ok
Non-Outage | J.E.26.08.11171 | C001883030 | Milton Charlton | KSAN | Completed | Load_260342 | Washington Blvd - 510 | 2026-08-08 19:30 | 2026-08-09 08:53 | 2026-08-09 09:43 | 2026-08-09 09:43 | 2026-08-09 10:23 | 2026-08-09 10:25 | 2026-08-09 10:24 | 2026-08-09 10:24 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Non-Outage | J.E.26.08.11561 | C001883031 | Kaydon Taylor | KSAN | Completed | Load_248496 | Washington Blvd - 410 | 2026-08-08 19:30 | 2026-08-08 19:31 | 2026-08-08 19:39 | 2026-08-08 19:40 | 2026-08-08 20:25 | 2026-08-08 20:26 | 2026-08-08 20:27 | 2026-08-08 20:27 |  |  | Fair | No | Premises closed
Non-Outage | J.E.26.08.11225 | C001883032 | Christopher Edwards | KSAN | Completed | Load_262077 | Constant Spring - 410 | 2026-08-08 19:32 | 2026-08-08 22:02 | 2026-08-09 09:35 | 2026-08-09 09:38 | 2026-08-09 10:16 | 2026-08-09 11:26 | 2026-08-09 11:26 | 2026-08-09 11:26 |  |  | Fair | No | Leaning cable pole that is resting on open secondary wireCausing wire to bang whenever the wind blows heavy Cable pole needs to be removed
Non-Outage | J.E.26.08.11971 | C001883033 | Roxroy Needham | St.Ann | Completed | Load_244725 | Roaring River - 410 | 2026-08-08 19:33 | 2026-08-08 19:34 | 2026-08-08 20:05 | 2026-08-08 20:05 | 2026-08-08 20:20 | 2026-08-08 20:21 | 2026-08-08 20:24 | 2026-08-08 20:24 |  |  | Fair | No | Unable to reach location dew to heavy traffic
Outage | J.E.26.08.11944 | C001883035 | Romeo Brissett | St.James | Completed | Load_244828 | Bogue - 610 | 2026-08-08 19:36 | 2026-08-08 19:37 | 2026-08-08 19:50 | 2026-08-08 19:51 | 2026-08-08 21:34 | 2026-08-08 22:48 | 2026-08-08 22:49 | 2026-08-08 22:49 | Fire |  | Fair | No | Isolated (1)15 kva transformer, removed several illegal connections, spliced and retention 2 span of secondary.
Outage | J.E.26.08.11926 | C001883036 | Swon Miller | St.James | Completed | Load_556239 | Bogue - 610 | 2026-08-08 19:38 | 2026-08-08 23:00 | 2026-08-08 23:29 | 2026-08-08 23:33 | 2026-08-08 23:52 | 2026-08-12 00:56 | 2026-08-09 00:03 | 2026-08-09 00:03 |  |  | Fair | No | Found customer without supply with the help of customer care agent ordained power supply was restored voltage found 0.000 voltage left 116/116/233
Outage | J.E.26.08.11853 | C001883037 | Raymond Lewis | St.Ann | Completed | Load_247553 | Roaring River - 210 | 2026-08-08 19:43 | 2026-08-08 23:35 | 2026-08-09 03:07 | 2026-08-09 03:07 | 2026-08-09 03:07 | 2026-08-09 03:08 | 2026-08-09 03:08 | 2026-08-09 03:08 | BrokenWire |  | Fair | No | Phone not answering
Outage | J.E.26.08.11992 | C001883038 | Cliton Henry | St.Mary | Completed | Load_242379 | Blackstonedge - 110 | 2026-08-08 19:46 | 2026-08-08 20:04 | 2026-08-08 20:28 | 2026-08-08 20:29 | 2026-08-08 21:39 | 2026-08-08 22:34 | 2026-08-08 22:34 | 2026-08-08 22:34 |  |  | Fair | No | A blown 3 amp fuse found for a 25 kva transformer at pole #0100731 due to broken secondary neutral conductor. Corrective work done to spliced and retention secondary neutral conductor using approximately 15 feet #2 AA conductor, 2-#2 splicing sleeve and 1- one bolt clamp also retention 2 span of secondary conductors. Supply restored using 1 3 amp fuse.
Outage | J.E.26.08.11991 | C001883040 | Kaydon Taylor | KSAN | Completed | Load_258808 | Washington Blvd - 510 | 2026-08-08 19:49 | 2026-08-08 19:50 | 2026-08-08 20:27 | 2026-08-08 20:28 | 2026-08-08 21:28 | 2026-08-08 21:40 | 2026-08-08 21:40 | 2026-08-08 21:40 | Fire |  | Fair | No | No fire seen
Outage | J.E.26.08.12015 | C001883041 | Swon Miller | St.James | Completed | Load_302426 | Bogue - 510 | 2026-08-08 19:54 | 2026-08-08 23:00 | 2026-08-08 23:29 | 2026-08-09 00:04 | 2026-08-09 00:44 | 2026-08-09 01:04 | 2026-08-09 01:04 | 2026-08-09 01:04 |  |  | Fair | No | Check and found okay voltage found 117/116/234 customer have internal problems voltage left 117/116/234
Non-Outage | J.E.26.08.11998 | C001883044 | Romaine Roberts |  | Completed |  |  | 2026-08-08 20:02 | 2026-08-08 20:03 | 2026-08-08 22:38 | 2026-08-08 22:38 | 2026-08-08 22:38 | 2026-08-08 22:39 | 2026-08-08 22:39 | 2026-08-08 22:39 |  |  | Fair | No | Junction fuse found blown patrol line nothing found replace 20 to restore power no pole number
Non-Outage | J.E.26.08.12032 | C001883045 | Roxroy Needham |  | Completed |  |  | 2026-08-08 20:12 | 2026-08-08 20:13 | 2026-08-08 20:25 | 2026-08-08 20:25 | 2026-08-08 20:57 | 2026-08-08 21:00 | 2026-08-08 21:01 | 2026-08-08 21:01 |  |  | Fair | No | Use switch stick to separate phase from neutral and replace 1- 5 amp fuse for a 50 KVA transformer
Outage | J.E.26.08.11881 | C001883046 | Oshane Warren | Westmoreland | Completed | Load_261089 | Paradise - 110 | 2026-08-08 20:19 | 2026-08-08 21:05 | 2026-08-08 21:21 | 2026-08-08 21:21 | 2026-08-08 21:38 | 2026-08-08 21:38 | 2026-08-08 21:39 | 2026-08-08 21:39 |  |  | Rains | No | Replace 20 amp junction fuse
Outage | J.E.26.08.11864 | C001883048 | Richard Samuda | Manchester | Completed | Load_253480 | Kendal - 210 | 2026-08-08 20:25 | 2026-08-08 20:28 | 2026-08-08 21:30 | 2026-08-08 21:31 | 2026-08-08 22:18 | 2026-08-08 22:46 | 2026-08-08 22:46 | 2026-08-08 22:46 |  |  | Rains | No | Found 25 kva transformer blown found nothing replaced fuse close line customer back to normal area is full of illegal connections
Outage | J.E.26.08.12055 | C001883049 | Rusean Allen | KSAS | Completed | Load_238206 | Cane River - 410 | 2026-08-08 20:38 | 2026-08-08 20:40 | 2026-08-08 20:45 | 2026-08-08 20:49 | 2026-08-08 20:50 | 2026-08-08 20:51 | 2026-08-08 20:51 | 2026-08-08 20:51 | BrokenWire |  | Fair | No | Broken pole is of telecommunications company
Outage | J.E.26.08.12059 | C001883051 | Roxroy Needham | St.Ann | Completed | Load_267137 | Cardiff Hall - 210 | 2026-08-08 20:44 | 2026-08-08 20:45 | 2026-08-08 21:02 | 2026-08-08 21:02 | 2026-08-08 21:02 | 2026-08-08 21:02 | 2026-08-08 21:03 | 2026-08-08 21:03 | Fire |  | Fair | No | Customer light was restored
Outage | J.E.26.08.12063 | C001883052 | Andre Smith | KSAS | Completed | Load_257993 | Three Miles - 410 | 2026-08-08 20:44 | 2026-08-09 08:32 | 2026-08-09 09:50 | 2026-08-09 09:51 | 2026-08-09 10:02 | 2026-08-09 10:56 | 2026-08-09 10:56 | 2026-08-09 10:56 | BrokenWire |  | Fair | No | Repair broken phase and neutral 40ft #2aaacause by illegal connections supply restored
Outage | J.E.26.08.12068 | C001883053 | Kaydon Taylor | KSAN | Completed | Load_266172 | Washington Blvd - 610 | 2026-08-08 20:46 | 2026-08-08 20:47 | 2026-08-08 21:41 | 2026-08-08 21:42 | 2026-08-08 22:00 | 2026-08-08 22:02 | 2026-08-08 22:03 | 2026-08-08 22:03 |  |  | Fair | No | Found okay
Outage | J.E.26.08.12077 | C001883054 | Andre Smith | KSAS | Completed | Load_252375 | Three Miles - 410 | 2026-08-08 20:51 | 2026-08-09 08:32 | 2026-08-09 08:53 | 2026-08-09 08:56 | 2026-08-09 09:32 | 2026-08-09 09:50 | 2026-08-09 09:50 | 2026-08-09 09:50 | Fire |  | Fair | No | Repair burnt neutral service wire cause by illegal connections supply restored
Outage | J.E.26.08.12069 | C001883055 | Tajay Bernard | Hanover | Completed | Load_250656 | Orange Bay - 310 | 2026-08-08 21:01 | 2026-08-08 21:05 | 2026-08-08 21:14 | 2026-08-08 21:15 | 2026-08-08 21:14 | 2026-08-08 21:30 | 2026-08-08 21:31 | 2026-08-08 21:31 |  |  | Fair | No | Refuse 1 25kva Transformer use 3amp fuse
Non-Outage | J.E.26.08.12048 | C001883059 | Roxroy Needham |  | Completed |  |  | 2026-08-08 21:27 | 2026-08-08 21:28 | 2026-08-08 21:53 | 2026-08-08 21:54 | 2026-08-08 22:55 | 2026-08-08 22:56 | 2026-08-08 22:56 | 2026-08-08 22:56 | Fire |  | Fair | No | Open 2 100 KVA Tran at pole to retention 2 span of secondary line
Non-Outage | J.E.26.08.12091 | C001883056 | Raymond Lewis |  | Completed |  |  | 2026-08-08 21:27 | 2026-08-08 23:20 | 2026-08-09 02:01 | 2026-08-09 02:02 | 2026-08-09 02:11 | 2026-08-09 03:01 | 2026-08-09 03:02 | 2026-08-09 03:02 |  |  | Fair | No | Open 25 kva x former to splice and retention 2 span secondary
Outage | J.E.26.08.11742 | C001883060 | Horace Malcolm | St.James | Completed | Load_257603 | Queens Drive - 710 | 2026-08-08 21:28 | 2026-08-08 21:29 | 2026-08-08 21:40 | 2026-08-08 21:40 | 2026-08-08 22:12 | 2026-08-08 22:23 | 2026-08-08 22:23 | 2026-08-08 22:23 |  |  | Rains | No | Clean and remake joints used one clamp voltage 110-114-224
Outage | J.E.26.08.11976 | C001883063 | Stephen Taylor | St.Thomas | Completed | Load_245249 | Lysson - 410 | 2026-08-08 21:53 | 2026-08-08 21:55 | 2026-08-09 07:50 | 2026-08-09 07:51 | 2026-08-09 09:19 | 2026-08-09 09:19 | 2026-08-09 09:21 | 2026-08-09 09:21 |  |  | Fair | No | Premises locked with lock and key it’s a goat pen
Non-Outage | J.E.26.08.11819 | C001883065 | Milton Charlton | KSAN | Completed | Load_574897 | Washington Blvd - 610 | 2026-08-08 22:00 | 2026-08-08 22:01 | 2026-08-09 09:11 | 2026-08-09 09:11 | 2026-08-09 09:40 | 2026-08-09 21:30 | 2026-08-09 09:42 | 2026-08-09 09:42 |  |  | Fair | No | Unable to locate customer by telephone and the security at the gate states he can’t let us in the meter room.
Non-Outage | J.E.26.08.11724 | C001883066 | Edward Royal | KSAN | Completed | Load_256846 | Constant Spring - 210 | 2026-08-08 22:01 | 2026-08-08 22:50 | 2026-08-09 03:40 | 2026-08-09 03:40 | 2026-08-09 03:40 | 2026-08-09 03:43 | 2026-08-09 03:43 | 2026-08-09 03:43 |  |  | Fair | No | Called related to outage
Outage | J.E.26.08.12070 | C001883067 | Raymond Carr | St.Mary | Completed | Load_266757 | Highgate -110 | 2026-08-08 22:04 | 2026-08-09 07:37 | 2026-08-09 12:20 | 2026-08-09 12:21 | 2026-08-09 12:52 | 2026-08-09 00:44 | 2026-08-09 12:54 | 2026-08-09 12:54 |  |  | Fair | No | Several calls to contact number went unanswered.
Outage | J.E.26.08.12152 | C001883069 | Christopher Edwards | KSAN | Completed | Load_262126 | Constant Spring - 210 | 2026-08-08 22:48 | 2026-08-09 08:03 | 2026-08-09 08:07 | 2026-08-09 08:10 | 2026-08-09 08:58 | 2026-08-09 09:22 | 2026-08-09 09:22 | 2026-08-09 09:22 |  |  | Fair | No | Refuse blown junction fuseUsing (1) 40 amps
Outage | J.E.26.08.12153 | C001883068 | Edward Royal | KSAN | Completed | Load_270129 | Constant Spring - 210 | 2026-08-08 22:48 | 2026-08-08 22:50 | 2026-08-09 01:35 | 2026-08-09 01:36 | 2026-08-09 01:35 | 2026-08-09 03:39 | 2026-08-09 03:39 | 2026-08-09 03:39 |  |  | Fair | No | Requesting daylight attention unable to patrol line properly because poor visibility and the line also run cross country
Outage | J.E.26.08.11920 | C001883071 | Andre Smith | KSAS | Completed | Load_289871 | Hunts Bay - 810 | 2026-08-08 22:50 | 2026-08-09 08:32 | 2026-08-09 10:56 | 2026-08-09 10:57 | 2026-08-09 11:51 | 2026-08-09 12:43 | 2026-08-09 12:43 | 2026-08-09 12:43 |  |  | Fair | No | Replace blown transformer fuse 5A cause by kite tails supply restored
Non-Outage | J.E.26.08.09139 | C001883072 | Swon Miller |  | Completed |  |  | 2026-08-08 22:57 | 2026-08-08 22:59 | 2026-08-09 00:03 | 2026-08-09 02:25 | 2026-08-09 02:41 | 2026-08-09 03:11 | 2026-08-09 03:14 | 2026-08-09 03:14 |  |  | Fair | No | Unable to locate customer phone calls to customer number went unanswered
Outage | J.E.26.08.12133 | C001883074 | Nickolas Rodriques | St.Catherine | Completed | Load_264610 | Tredegar - 210 | 2026-08-08 23:10 | 2026-08-08 23:13 | 2026-08-08 23:23 | 2026-08-08 23:58 | 2026-08-09 01:05 | 2026-08-09 01:46 | 2026-08-09 01:48 | 2026-08-09 01:48 |  |  | Fair | No | Found customer with power. He confirmed that the area outage was restored.
Outage | J.E.26.08.12166 | C001883078 | Edward Royal | KSAS | Completed | Load_253497 | Up Park Camp - 310 | 2026-08-08 23:22 | 2026-08-08 23:24 | 2026-08-09 00:08 | 2026-08-09 00:09 | 2026-08-09 00:17 | 2026-08-09 00:33 | 2026-08-09 00:34 | 2026-08-09 00:34 |  |  | Fair | No | Replaced 80A junction fuse
Outage | J.E.26.08.12186 | C001883083 | Swon Miller | St.James | Completed | Load_573541 | Bogue - 610 | 2026-08-09 02:28 | 2026-08-09 05:05 | 2026-08-09 05:53 | 2026-08-09 06:22 | 2026-08-09 06:34 | 2026-08-12 06:56 | 2026-08-09 06:58 | 2026-08-09 06:58 |  |  | Fair | No | Unable to locate customer phone calls to customer number went unanswered
Non-Outage | J.E.26.08.11952 | C001883095 | Lancelot Brown |  | Completed |  |  | 2026-08-09 07:07 | 2026-08-09 07:10 | 2026-08-09 07:22 | 2026-08-09 08:06 | 2026-08-09 08:06 | 2026-08-09 08:07 | 2026-08-09 08:07 | 2026-08-09 08:07 |  |  | Rains | No | This call related to 10kva trip caused by vegetation supply restore
Outage | J.E.26.08.11863 | C001883094 | Lancelot Brown | Hanover | Completed | Load_256375 | Orange Bay - 310 | 2026-08-09 07:07 | 2026-08-09 07:10 | 2026-08-09 07:22 | 2026-08-09 07:24 | 2026-08-09 07:46 | 2026-08-09 08:04 | 2026-08-09 08:06 | 2026-08-09 08:06 |  |  | Rains | No | Found 10kva trip patroll found vegetation on secondary line cut and remove vegetation from secondary reset 10kva supply restore also primary line need bushing please pass on to maintenance department in Hanover mr Richards
Outage | J.E.26.08.12163 | C001883096 | Denton Williams | Portland | Completed | Load_348940 | Port Antonio - 410 | 2026-08-09 07:07 | 2026-08-09 07:10 | 2026-08-09 07:24 | 2026-08-09 07:25 | 2026-08-09 09:44 | 2026-08-09 10:34 | 2026-08-09 10:35 | 2026-08-09 10:35 | TreeContact |  | Fair | No | Remove fallen tree from line and replace one 10 amp junction fuse. All customers restored
Outage | J.E.26.08.12292 | C001883093 | Lancelot Brown | Hanover | Completed | Load_265148 | Orange Bay - 310 | 2026-08-09 07:07 | 2026-08-09 07:10 | 2026-08-09 07:22 | 2026-08-09 16:31 | 2026-08-09 16:30 | 2026-08-09 16:25 | 2026-08-09 16:32 | 2026-08-09 16:32 |  |  | EarthMovement | No | Cannot locate customer no answer from contact number need proper direction
Non-Outage | J.E.26.08.11878 | C001883097 | Lancelot Brown | Hanover | Completed | Load_256665 | Orange Bay - 310 | 2026-08-09 07:10 | 2026-08-09 07:12 | 2026-08-09 07:22 | 2026-08-09 08:19 | 2026-08-09 08:18 | 2026-08-09 08:20 | 2026-08-09 08:20 | 2026-08-09 08:20 |  |  | Fair | No | Check and found ok customer said this call was from hurricane melisa supply restore
Non-Outage | J.E.26.07.34584 | C001883101 | Lancelot Brown |  | Completed |  |  | 2026-08-09 07:11 | 2026-08-09 07:14 | 2026-08-09 07:22 | 2026-08-09 08:55 | 2026-08-09 09:27 | 2026-08-09 09:39 | 2026-08-09 09:42 | 2026-08-09 09:42 |  |  | Fair | No | Disconnected temporary 220 supply from pole service line and meter still at location
Non-Outage | J.E.26.08.00837 | C001883100 | Lancelot Brown | Hanover | Completed | Load_573736 | Orange Bay - 210 | 2026-08-09 07:11 | 2026-08-09 07:12 | 2026-08-09 07:22 | 2026-08-09 14:33 | 2026-08-09 14:33 | 2026-08-09 14:34 | 2026-08-09 14:34 | 2026-08-09 14:34 |  |  | Fair | No | Check and found ok customer said there was a diffective transformer and it was replaced two days ago supply restore
Non-Outage | J.E.26.08.08218 | C001883099 | Lancelot Brown | Hanover | Completed | Load_263889 | Orange Bay - 210 | 2026-08-09 07:11 | 2026-08-09 07:12 | 2026-08-09 07:22 | 2026-08-09 12:10 | 2026-08-09 13:25 | 2026-08-09 14:02 | 2026-08-09 14:03 | 2026-08-09 14:03 |  |  | Fair | No | Customer complained of low voltage understand primary voltage is coming in low other customers having same problem on different circuit vl at secondary line 112-104-216
Non-Outage | J.E.26.08.11781 | C001883098 | Lancelot Brown | Hanover | Completed | Load_264233 | Orange Bay - 310 | 2026-08-09 07:11 | 2026-08-09 07:12 | 2026-08-09 07:22 | 2026-08-09 09:42 | 2026-08-09 11:17 | 2026-08-09 12:09 | 2026-08-09 12:09 | 2026-08-09 12:09 |  |  | Fair | No | Triplex service line feed two customers one custome have internal trouble disconnected advise customer to carry out repair and call back vl at mrs smith pothead 112-114-227 supply restore
Outage | J.E.26.08.12084 | C001883103 | Marlon Brown | Trelawny | Completed | Load_294519 | Duncans - 110 | 2026-08-09 07:13 | 2026-08-09 07:15 | 2026-08-09 08:10 | 2026-08-09 08:10 | 2026-08-09 08:40 | 2026-08-09 08:40 | 2026-08-09 08:40 | 2026-08-09 08:40 |  |  | Fair | No | Unable to locate customer via telephone nor direction
Outage | J.E.26.08.12128 | C001883102 | Marlon Brown | Trelawny | Completed | Load_292238 | Greenwood - 210 | 2026-08-09 07:13 | 2026-08-09 07:14 | 2026-08-09 07:25 | 2026-08-09 07:26 | 2026-08-09 07:46 | 2026-08-09 08:09 | 2026-08-09 08:09 | 2026-08-09 08:09 | Fire |  | Fair | No | Needs 150ft #4/0 twisted to effect repairs, refer to E. Richards.
Outage | J.E.26.08.12193 | C001883104 | Wayne Dillion | St.Elizabeth | Completed | Load_266497 | Maggotty - 110 | 2026-08-09 07:15 | 2026-08-09 07:17 | 2026-08-09 11:30 | 2026-08-09 11:31 | 2026-08-09 11:30 | 2026-08-09 11:30 | 2026-08-09 11:31 | 2026-08-09 11:31 |  |  | Fair | No | Supply was restored to the area
Outage | J.E.26.08.12308 | C001883105 | Wayne Dillion | St.Elizabeth | Completed | Load_249837 | Maggotty - 110 | 2026-08-09 07:15 | 2026-08-09 07:17 | 2026-08-09 08:22 | 2026-08-09 08:22 | 2026-08-09 08:22 | 2026-08-09 10:00 | 2026-08-09 10:07 | 2026-08-09 10:07 | BrokenWire |  | Fair | No | Supply check and found working okay. Further checks reveals a tree laying on the secondary conductors. Isolate 15kva transformer circuit pole # 004409 to cut and remove same. Recluse transformer circuit and supply leave working okay.
Outage | J.E.26.08.12075 | C001883107 | Wayne Dillion | St.Elizabeth | Completed | Load_270212 | Maggotty - 110 | 2026-08-09 07:16 | 2026-08-09 07:17 | 2026-08-09 12:25 | 2026-08-09 12:34 | 2026-08-09 13:41 | 2026-08-09 14:00 | 2026-08-09 14:01 | 2026-08-09 14:01 |  |  | Fair | No | Supply check and found customer has illegal connection on pot head that causes phase to break. Remove illegal connection and re-made pot head using 3 linkets. Supply leave working okay reading 112v, 111v and cross phase 223volts.
Outage | J.E.26.08.12185 | C001883106 | Wayne Dillion | St.Elizabeth | Completed | Load_258532 | Maggotty - 110 | 2026-08-09 07:16 | 2026-08-09 07:17 | 2026-08-09 10:09 | 2026-08-09 10:10 | 2026-08-09 10:54 | 2026-08-09 11:00 | 2026-08-09 11:30 | 2026-08-09 11:30 |  |  | Fair | No | Patrol and found one blown 30amp junction fuse no pole #. Replace same and supply restored okay.
Outage | J.E.26.08.12170 | C001883109 | Raheem Ricketts | St.Elizabeth | Completed | Load_260249 | Maggotty - 210 | 2026-08-09 07:17 | 2026-08-09 07:19 | 2026-08-09 08:14 | 2026-08-09 08:15 | 2026-08-09 08:15 | 2026-08-09 08:15 | 2026-08-09 08:16 | 2026-08-09 08:16 |  |  | Fair | No | Unable to locate customer customer cell number out of service
Outage | J.E.26.08.12319 | C001883108 | Raheem Ricketts | St.Elizabeth | Completed | Load_268766 | Maggotty - 210 | 2026-08-09 07:17 | 2026-08-09 07:19 | 2026-08-09 08:07 | 2026-08-09 08:21 | 2026-08-09 08:20 | 2026-08-09 08:21 | 2026-08-09 08:21 | 2026-08-09 08:21 |  |  | Fair | No | Unable to locate customer cell number went straight voicemail after several calls
Outage | J.E.26.08.11294 | C001883110 | Raheem Ricketts | Manchester | Completed | Load_252413 | Spur Tree - 210 | 2026-08-09 07:18 | 2026-08-09 07:19 | 2026-08-09 08:29 | 2026-08-09 08:30 | 2026-08-09 08:37 | 2026-08-09 08:43 | 2026-08-09 08:43 | 2026-08-09 08:43 | LeaningPole |  | Fair | No | Check and found 35,ft pole class 6,dead end open secondary pole leaning pole needs replacing or replanting however no one is affected light is still in the area
Outage | J.E.26.08.11706 | C001883111 | Raheem Ricketts | St.Elizabeth | Completed | Load_254651 | Maggotty - 210 | 2026-08-09 07:18 | 2026-08-09 07:19 | 2026-08-09 08:25 | 2026-08-09 08:27 | 2026-08-09 08:27 | 2026-08-09 08:28 | 2026-08-09 08:28 | 2026-08-09 08:28 |  |  | Fair | No | Customer 2,phone number went voicemail
Non-Outage | J.E.26.08.11518 | C001883112 | Wayne Dillion |  | Completed |  |  | 2026-08-09 07:22 | 2026-08-09 07:23 | 2026-08-09 12:30 | 2026-08-09 12:31 | 2026-08-09 12:30 | 2026-08-09 12:32 | 2026-08-09 12:32 | 2026-08-09 12:32 |  |  | Fair | No | Customer said supply was restored yesterday.
Non-Outage | J.E.26.08.11687 | C001883113 | Wayne Dillion |  | Completed |  |  | 2026-08-09 07:22 | 2026-08-09 07:23 | 2026-08-09 12:01 | 2026-08-09 12:01 | 2026-08-09 12:01 | 2026-08-09 12:03 | 2026-08-09 12:03 | 2026-08-09 12:03 |  |  | Fair | No | Call is related to a defective transformer.
Non-Outage | J.E.26.08.11717 | C001883114 | Wayne Dillion |  | Completed |  |  | 2026-08-09 07:22 | 2026-08-09 07:23 | 2026-08-09 11:54 | 2026-08-09 11:54 | 2026-08-09 11:54 | 2026-08-09 11:55 | 2026-08-09 11:55 | 2026-08-09 11:55 |  |  | Fair | No | Customer said supply was restored okay.
Outage | J.E.26.08.12096 | C001883115 | Raheem Ricketts | St.Elizabeth | Completed | Load_257287 | Maggotty - 210 | 2026-08-09 07:22 | 2026-08-09 08:48 | 2026-08-09 11:42 | 2026-08-09 11:43 | 2026-08-09 11:43 | 2026-08-09 11:43 | 2026-08-09 11:43 | 2026-08-09 11:43 |  |  | Fair | No | Check and found okay call related
Non-Outage | J.E.26.08.12051 | C001883117 | Javid Vernon |  | Completed |  |  | 2026-08-09 07:28 | 2026-08-09 07:29 | 2026-08-09 12:26 | 2026-08-09 12:26 | 2026-08-09 12:26 | 2026-08-09 12:27 | 2026-08-09 12:27 | 2026-08-09 12:27 |  |  | Fair | No | Related to previous call job number 123700
Outage | J.E.26.08.12159 | C001883116 | Javid Vernon | Westmoreland | Completed | Load_292387 | Paradise - 210 | 2026-08-09 07:28 | 2026-08-09 07:29 | 2026-08-09 08:30 | 2026-08-09 08:30 | 2026-08-09 08:47 | 2026-08-09 09:26 | 2026-08-09 09:27 | 2026-08-09 09:27 |  |  | Fair | No | Clean and remake joints at JPS pole use 1 clamps Voltage found 115/103/218Voltage left 116/109/224
Outage | J.E.26.08.12227 | C001883118 | Raymond Carr | St.Mary | Completed | Load_251228 | Highgate -110 | 2026-08-09 07:29 | 2026-08-09 07:31 | 2026-08-09 08:47 | 2026-08-09 08:47 | 2026-08-09 10:55 | 2026-08-09 | 2026-08-09 12:07 | 2026-08-09 12:07 | BrokenWire |  | Fair | No | Spliced and retention secondary conductors using 110ft#2aa, 1#2 splicing sleeve. Supply was restored.
Outage | J.E.26.08.11323 | C001883119 | Daniel Francis | St.Mary | Completed | Load_248562 | Oracabessa - 210 | 2026-08-09 07:30 | 2026-08-09 07:31 | 2026-08-09 09:33 | 2026-08-09 09:33 | 2026-08-09 09:33 | 2026-08-09 09:34 | 2026-08-09 09:37 | 2026-08-09 09:37 |  |  | Fair | No | Power restored from yesterday evening
Outage | J.E.26.08.11599 | C001883120 | Kenroy Dale | Manchester | Completed | Load_260536 | Spur Tree - 210 | 2026-08-09 07:30 | 2026-08-09 07:32 | 2026-08-09 09:37 | 2026-08-09 09:38 | 2026-08-09 11:03 | 2026-08-09 11:39 | 2026-08-09 11:40 | 2026-08-09 11:40 |  |  | Fair | No | Blown 3 amp transformer fuse found for 25 kva transformer line patrol nothing found blown fuse was replaced and area now with supply
Outage | J.E.26.08.12183 | C001883121 | Stephen Taylor | St.Thomas | Completed | Load_268599 | Good Year - 110 | 2026-08-09 07:35 | 2026-08-09 07:36 | 2026-08-09 13:37 | 2026-08-09 13:37 | 2026-08-09 13:37 | 2026-08-09 13:37 | 2026-08-09 13:38 | 2026-08-09 13:38 |  |  | Fair | No | Patrol clear line and close up chip saver 20 amp customer is now okay
Outage | J.E.26.08.12335 | C001883124 | Stephen Taylor | St.Thomas | Completed | Load_260235 | Good Year - 110 | 2026-08-09 07:35 | 2026-08-09 07:36 | 2026-08-09 09:21 | 2026-08-09 09:22 | 2026-08-09 11:14 | 2026-08-09 13:22 | 2026-08-09 13:35 | 2026-08-09 13:35 |  |  | Fair | No | Trees fall on line in Stanton rd repair secondary line and close up back 20 amp chip saver safely 80% off customer is still with out supply needs assistance from the jps maintenance team to carry out bushings before power can restore 20 amp chip saver isolated no # and pole
Outage | J.E.26.08.12167 | C001883127 | Ryan Richards | Manchester | Completed | Load_253480 | Kendal - 210 | 2026-08-09 07:58 | 2026-08-09 08:02 | 2026-08-09 08:33 | 2026-08-09 08:33 | 2026-08-09 10:35 | 2026-08-09 11:56 | 2026-08-09 11:56 | 2026-08-09 11:56 |  |  | Fair | No | Area found ok customer that made report was unable to locate multiple efforts made to locate customer but unsuccessful
Non-Outage | J.E.26.08.11532 | C001883128 | Javid Vernon | Westmoreland | Completed | Load_265343 | Paradise - 110 | 2026-08-09 08:00 | 2026-08-09 08:01 | 2026-08-09 12:28 | 2026-08-09 12:28 | 2026-08-09 13:12 | 2026-08-09 13:28 | 2026-08-09 13:29 | 2026-08-09 13:29 | BrokenWire |  | Fair | No | Area check and found okay no broken swire was found unable to locate customer on premises multiple phone call to customer number went unanswered
Non-Outage | J.E.26.08.12149 | C001883130 | Christopher Edwards |  | Completed |  |  | 2026-08-09 08:01 | 2026-08-09 08:04 | 2026-08-09 09:23 | 2026-08-09 09:24 | 2026-08-09 09:23 | 2026-08-09 09:24 | 2026-08-09 09:24 | 2026-08-09 09:24 |  |  | Fair | No | Related to previous call that was rectify
Outage | J.E.26.08.12153 | C001883129 | Christopher Edwards | KSAN | Completed | Load_270129 | Constant Spring - 210 | 2026-08-09 08:01 | 2026-08-09 08:02 | 2026-08-09 08:06 | 2026-08-09 09:23 | 2026-08-09 09:22 | 2026-08-09 09:23 | 2026-08-09 09:23 | 2026-08-09 09:23 |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Non-Outage | J.E.26.08.12257 | C001883131 | Hartley Chin |  | Completed |  |  | 2026-08-09 08:02 | 2026-08-09 08:04 | 2026-08-09 08:07 | 2026-08-09 14:31 | 2026-08-09 14:31 | 2026-08-09 14:31 | 2026-08-09 14:32 | 2026-08-09 14:32 | BrokenWire |  | Fair | No | Call related to 11530
Non-Outage | J.E.26.08.07207 | C001883132 | Javid Vernon | Westmoreland | Completed | Load_264370 | Paradise - 210 | 2026-08-09 08:03 | 2026-08-09 08:04 | 2026-08-09 13:29 | 2026-08-09 13:30 | 2026-08-09 14:16 | 2026-08-09 14:36 | 2026-08-09 14:36 | 2026-08-09 14:36 | LeaningPole |  | Fair | No | Check and found one 35ft class 6 pole three phase primary and secondary leaning it is slightly putting tension on customer service wire voltage reading 112/114/226 refer to maintenance
Outage | J.E.26.08.11695 | C001883133 | Ricky Hall | St.Catherine | Completed |  |  | 2026-08-09 08:06 | 2026-08-09 08:07 | 2026-08-09 09:08 | 2026-08-09 09:11 | 2026-08-09 09:53 | 2026-08-09 09:58 | 2026-08-09 09:58 | 2026-08-09 09:58 | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | No fire seen issue was resolved on previous shift
Non-Outage | J.E.26.08.11545 | C001883136 | Ricky Hall |  | Completed |  |  | 2026-08-09 08:07 | 2026-08-09 08:11 | 2026-08-09 09:59 | 2026-08-09 10:00 | 2026-08-09 10:13 | 2026-08-09 10:47 | 2026-08-09 10:48 | 2026-08-09 10:48 | BrokenWire |  | Fair | No | Rerouted splice and reconnect 3W service use 70#6 triplex 2 clamps 118/118/236
Non-Outage | J.E.26.08.11909 | C001883135 | Ricky Hall |  | Completed |  |  | 2026-08-09 08:07 | 2026-08-09 08:11 | 2026-08-09 08:37 | 2026-08-09 08:38 | 2026-08-09 09:07 | 2026-08-09 09:08 | 2026-08-09 09:11 | 2026-08-09 09:11 | BrokenWire |  | Fair | No | Call located in guys hill not Spanish Town
Outage | J.E.26.08.11533 | C001883137 | Ricky Hall | St.Catherine | Completed | Load_266264 | Twickenham - 310 | 2026-08-09 08:07 | 2026-08-09 08:11 | 2026-08-09 11:12 | 2026-08-09 11:13 | 2026-08-09 11:33 | 2026-08-09 12:11 | 2026-08-09 12:11 | 2026-08-09 12:11 | BrokenPole |  | Fair | No | Premises not located insufficient information customer unreachable
Outage | J.E.26.08.11546 | C001883134 | Ricky Hall | St.Catherine | Completed | Load_244398 | Tredegar - 510 | 2026-08-09 08:07 | 2026-08-09 08:11 | 2026-08-09 09:58 | 2026-08-09 10:49 | 2026-08-09 10:49 | 2026-08-09 10:49 | 2026-08-09 10:49 | 2026-08-09 10:49 | BrokenWire |  | Fair | No | Call associated with outage #11546
Outage | J.E.26.08.12342 | C001883138 | Nickolas Rodriques | St.Catherine | Completed | Load_258027 | New Michelton - 210 | 2026-08-09 08:08 | 2026-08-09 08:11 | 2026-08-09 09:51 | 2026-08-09 10:00 | 2026-08-09 11:41 | 2026-08-09 12:58 | 2026-08-09 13:11 | 2026-08-09 13:11 |  |  | Fair | No | Checked and found two junction fuses blown from same line (20 amp and 8 amp). Patrol and found nothing on line. Repaired by replacing the fuses after completing patrol.
Outage | J.E.26.08.12359 | C001883139 | Ricky Hall | St.Catherine | Completed | Load_1000933 | Tredegar - 410 | 2026-08-09 08:14 | 2026-08-09 08:16 | 2026-08-09 09:07 | 2026-08-09 10:50 | 2026-08-09 10:59 | 2026-08-09 11:10 | 2026-08-09 11:11 | 2026-08-09 11:11 | BrokenWire |  | Fair | No | Premises not located no broken wire seen
Outage | J.E.26.08.12375 | C001883140 | Nickolas Rodriques | St.Catherine | Completed | Load_268326 | New Michelton - 210 | 2026-08-09 08:14 | 2026-08-09 08:16 | 2026-08-09 13:12 | 2026-08-09 13:13 | 2026-08-09 13:22 | 2026-08-09 13:34 | 2026-08-09 13:35 | 2026-08-09 13:35 |  |  | Fair | No | Power restored. Call relates to the 20 amp and 8 amp junction fuses that were replaced.
Outage | J.E.26.08.12219 | C001883142 | Omar King | St.Ann | Completed | Load_240455 | Upper White River - 210 | 2026-08-09 08:23 | 2026-08-09 15:24 | 2026-08-09 15:59 | 2026-08-09 16:00 | 2026-08-09 16:35 | 2026-08-09 16:36 | 2026-08-09 16:36 | 2026-08-09 16:36 |  |  | Fair | No | Problem as been resolved
Non-Outage | J.E.26.08.12109 | C001883143 | Raymond Carr |  | Completed |  |  | 2026-08-09 08:29 | 2026-08-09 08:32 | 2026-08-09 12:17 | 2026-08-09 12:17 | 2026-08-09 12:17 | 2026-08-09 | 2026-08-09 12:18 | 2026-08-09 12:18 |  |  | Fair | No | Call is not for St Mary.
Outage | J.E.26.08.12340 | C001883144 | Raymond Lewis | St.Ann | Completed | Load_268325 | Cardiff Hall - 310 | 2026-08-09 08:30 | 2026-08-09 08:32 | 2026-08-09 09:06 | 2026-08-09 09:07 | 2026-08-09 10:10 | 2026-08-09 10:13 | 2026-08-09 10:13 | 2026-08-09 10:13 |  |  | Fair | No | Internal fault
Non-Outage | J.E.26.08.10323 | C001883145 | Daniel Francis | St.Ann | Completed | Load_256455 | Roaring River - 210 | 2026-08-09 08:32 | 2026-08-09 08:36 | 2026-08-09 11:14 | 2026-08-09 11:15 | 2026-08-09 12:26 | 2026-08-09 12:26 | 2026-08-09 12:27 | 2026-08-09 12:27 | BrokenPole |  | Fair | No | Not found customer not answering phone
Non-Outage | J.E.26.08.10417 | C001883149 | Cliton Henry | St.Mary | Completed | Load_260379 | Oracabessa - 110 | 2026-08-09 08:33 | 2026-08-09 08:37 | 2026-08-09 10:40 | 2026-08-09 10:40 | 2026-08-09 10:56 | 2026-08-09 14:58 | 2026-08-09 15:06 | 2026-08-09 15:06 |  |  | Fair | No | A 25 kva transformer was de energized at pole # 005125 to carryout repairs. Defective joint found along the secondary circuit were reconnected using 6 one bolt clamps, remove illegal connections. Voltages left 102-109/211 volts. Kindly refer to St. Mary Operations for a secondary rehabilitation.
Non-Outage | J.E.26.08.11269 | C001883148 | Cliton Henry | St.Mary | Completed | Load_254936 | Oracabessa - 210 | 2026-08-09 08:33 | 2026-08-09 08:37 | 2026-08-09 15:07 | 2026-08-09 15:08 | 2026-08-09 15:47 | 2026-08-09 15:55 | 2026-08-09 15:58 | 2026-08-09 15:58 |  |  | Fair | No | A corroded neutral conductor found at pothead was reconnected using 1 one bolt clamp. Voltages left 118-120/238 volts.
Non-Outage | J.E.26.08.12041 | C001883151 | Cliton Henry | St.Mary | Completed | Load_258327 | Oracabessa - 110 | 2026-08-09 08:33 | 2026-08-09 08:37 | 2026-08-09 10:00 | 2026-08-09 10:01 | 2026-08-09 10:23 | 2026-08-09 10:34 | 2026-08-09 10:39 | 2026-08-09 10:39 |  |  | Fair | No | The voltages found at the customer pothead were 118-119/237 volts. A defective meter socket found and customer was advised to get a licensed electrician it replaced.
Non-Outage | J.E.26.08.11775 | C001883153 | Denton Williams |  | Completed |  |  | 2026-08-09 08:34 | 2026-08-09 08:37 | 2026-08-09 10:39 | 2026-08-09 10:39 | 2026-08-09 13:43 | 2026-08-09 13:44 | 2026-08-09 13:47 | 2026-08-09 13:47 | BrokenPole |  | Fair | No | Customer cannot found.
Outage | J.E.26.08.12147 | C001883155 | Neville Spencer | Clarendon | Completed | Load_557132 | May Pen - 210 | 2026-08-09 08:36 | 2026-08-09 08:42 | 2026-08-09 08:51 | 2026-08-09 08:52 | 2026-08-09 09:29 | 2026-08-09 09:29 | 2026-08-09 09:29 | 2026-08-09 09:29 |  |  | Fair | No | Unable to locate customer.
Outage | J.E.26.08.12337 | C001883156 | Neville Spencer | Clarendon | Completed | Load_247892 | Monymusk - 410 | 2026-08-09 08:36 | 2026-08-09 08:42 | 2026-08-09 09:30 | 2026-08-09 09:30 | 2026-08-09 11:55 | 2026-08-09 11:55 | 2026-08-09 12:04 | 2026-08-09 12:04 |  |  | Fair | No | Found supply disconnect supply reconnect voltage reading 113 114 229;supply restored.
Non-Outage | J.E.26.08.10886 | C001883159 | Roxroy Needham | St.Ann | Completed | Load_255068 | Cardiff Hall - 310 | 2026-08-09 08:37 | 2026-08-09 15:36 | 2026-08-09 16:35 | 2026-08-09 16:35 | 2026-08-09 16:35 | 2026-08-09 16:31 | 2026-08-09 16:36 | 2026-08-09 16:36 |  |  | Fair | No | Premises found ok call customer and customer say that JPS team come before
Non-Outage | J.E.26.08.12203 | C001883157 | Roxroy Needham | St.Ann | Completed | Load_244118 | Cardiff Hall - 310 | 2026-08-09 08:37 | 2026-08-09 15:34 | 2026-08-09 16:17 | 2026-08-09 16:18 | 2026-08-09 16:33 | 2026-08-09 16:28 | 2026-08-09 16:34 | 2026-08-09 16:34 |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.08.12399 | C001883161 | Raheem Ricketts | St.Elizabeth | Completed | Load_257287 | Maggotty - 210 | 2026-08-09 08:46 | 2026-08-09 08:47 | 2026-08-09 08:58 | 2026-08-09 08:59 | 2026-08-09 11:30 | 2026-08-09 11:31 | 2026-08-09 11:32 | 2026-08-09 11:32 |  |  | Fair | No | Check and found 25kva fuse blown refuse 25kva
Outage | J.E.26.08.12395 | C001883162 | Raheem Ricketts | Manchester | Completed | Load_251930 | Spur Tree - 210 | 2026-08-09 08:47 | 2026-08-09 08:47 | 2026-08-09 11:38 | 2026-08-09 11:39 | 2026-08-09 11:38 | 2026-08-09 11:40 | 2026-08-09 11:40 | 2026-08-09 11:40 |  |  | Fair | No | Unable to locate customer cell number went straight voicemail after several calls
Outage | J.E.26.08.11915 | C001883163 | Raheem Ricketts | St.Elizabeth | Completed | Load_237785 | Maggotty - 210 | 2026-08-09 08:48 | 2026-08-09 08:49 | 2026-08-09 11:36 | 2026-08-09 11:37 | 2026-08-09 11:37 | 2026-08-09 11:38 | 2026-08-09 11:38 | 2026-08-09 11:38 |  |  | Fair | No | Unable to locate customer cell number went unanswered
Outage | J.E.26.08.12383 | C001883164 | Richman Whyte | Westmoreland | Completed | Load_252107 | Paradise - 310 | 2026-08-09 08:52 | 2026-08-09 09:03 | 2026-08-09 11:31 | 2026-08-09 11:32 | 2026-08-09 11:31 | 2026-08-09 11:36 | 2026-08-09 11:37 | 2026-08-09 11:37 |  |  | Fair | No | Clair vegetation from line and replace three amp twenty five kva transformer fuse
Non-Outage | J.E.26.08.12122 | C001883166 | Raymond Lewis |  | Completed |  |  | 2026-08-09 08:54 | 2026-08-09 08:56 | 2026-08-09 11:36 | 2026-08-09 11:37 | 2026-08-09 11:37 | 2026-08-09 11:39 | 2026-08-09 11:38 | 2026-08-09 11:38 |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.08.12407 | C001883165 | Denton Williams |  | Completed |  |  | 2026-08-09 08:54 | 2026-08-09 08:56 | 2026-08-09 10:36 | 2026-08-09 10:36 | 2026-08-09 10:36 | 2026-08-09 10:36 | 2026-08-09 10:37 | 2026-08-09 10:37 | BrokenWire | Y | Fair | No | Remove fallen tree from line and replace one 10 amp junction fuse. All customers restored. Area need bushing, refer to Portland maintenance
Outage | J.E.26.08.11623 | C001883167 | Daniel Francis | St.Ann | Completed | Load_269957 | Roaring River - 210 | 2026-08-09 08:55 | 2026-08-09 08:56 | 2026-08-09 12:27 | 2026-08-09 12:28 | 2026-08-09 12:28 | 2026-08-09 11:57 | 2026-08-09 12:29 | 2026-08-09 12:29 |  |  | Fair | No | Found okay 115 114 230 in alll
Non-Outage | J.E.26.08.12352 | C001883168 | Christopher Edwards | KSAN | Completed | Load_261006 | Constant Spring - 410 | 2026-08-09 08:58 | 2026-08-09 09:10 | 2026-08-09 09:24 | 2026-08-09 09:25 | 2026-08-09 09:25 | 2026-08-09 09:33 | 2026-08-09 09:35 | 2026-08-09 09:35 |  |  | Fair | No | Related to previous call that has been resolved
Outage | J.E.26.08.12402 | C001883169 | Kenroy Dale | Manchester | Completed | Load_268212 | Spur Tree - 310 | 2026-08-09 08:59 | 2026-08-09 09:00 | 2026-08-09 11:40 | 2026-08-09 11:42 | 2026-08-09 13:13 | 2026-08-09 13:43 | 2026-08-09 13:45 | 2026-08-09 13:45 | BrokenWire |  | Fair | No | Defective service wire found, service wires was splice and retention using 1 one bolt clamp and 2 service sleeve voltage reading 114/113/227
Outage | J.E.26.08.12409 | C001883170 | Kenroy Dale | Manchester | Completed | Load_292816 | Spur Tree - 310 | 2026-08-09 08:59 | 2026-08-09 09:00 | 2026-08-09 13:45 | 2026-08-09 13:46 | 2026-08-09 14:58 | 2026-08-09 15:27 | 2026-08-09 15:28 | 2026-08-09 15:28 |  |  | Fair | No | Burn off phase found at pole remade connection using 1 one bolt clamp voltage reading 116
Non-Outage | J.E.26.08.12381 | C001883171 | Richman Whyte |  | Completed |  |  | 2026-08-09 09:01 | 2026-08-09 09:02 | 2026-08-09 10:49 | 2026-08-09 11:37 | 2026-08-09 12:23 | 2026-08-09 12:43 | 2026-08-09 12:43 | 2026-08-09 12:43 |  |  | Fair | No | Replace 3 amp 25 kva transformer fuse
Outage | J.E.26.08.12370 | C001883172 | Javid Vernon | Westmoreland | Completed | Load_270068 | Paradise - 110 | 2026-08-09 09:01 | 2026-08-09 09:02 | 2026-08-09 09:31 | 2026-08-09 09:32 | 2026-08-09 11:43 | 2026-08-09 12:23 | 2026-08-09 12:25 | 2026-08-09 12:25 |  |  | Fair | No | Remove vegetation and refuse 1 25kva transformer use 2amp fuse
Outage | J.E.26.08.12422 | C001883173 | Gregory Grossett | Portland | Completed | Load_577181 | Port Antonio - 310 | 2026-08-09 09:42 | 2026-08-09 16:09 | 2026-08-09 16:25 | 2026-08-09 16:36 | 2026-08-09 18:38 | 2026-08-09 18:45 | 2026-08-09 18:53 | 2026-08-09 18:53 |  |  | Fair | No | 100 kva transformer fuse blown , cause by bird , restore and okay, material used 1-8 amps fuse.
Outage | J.E.26.08.12419 | C001883174 | Daniel Francis | St.Ann | Completed | Load_572156 | Roaring River - 410 | 2026-08-09 09:43 | 2026-08-09 10:00 | 2026-08-09 14:44 | 2026-08-09 14:45 | 2026-08-09 14:55 | 2026-08-09 15:19 | 2026-08-09 15:19 | 2026-08-09 15:19 |  |  | Fair | No | Change 2 fuse one 8amp and one 7am also found junction out pole #0111472 at that pole we change one 30amp fuse power restored
Non-Outage | J.E.26.08.10573 | C001883175 | Elvis Trowers | KSAS | Completed | Load_254965 | Duhaney - 310 | 2026-08-09 10:00 | 2026-08-09 10:03 | 2026-08-09 14:26 | 2026-08-09 14:27 | 2026-08-09 15:02 | 2026-08-09 15:05 | 2026-08-09 15:05 | 2026-08-09 15:05 |  |  | Fair | Yes | Premises checked and found ok.
Non-Outage | J.E.26.08.10575 | C001883176 | Elvis Trowers | KSAS | Completed | Load_247472 | Duhaney - 310 | 2026-08-09 10:00 | 2026-08-09 10:03 | 2026-08-09 13:05 | 2026-08-09 13:06 | 2026-08-09 13:32 | 2026-08-09 13:36 | 2026-08-09 13:36 | 2026-08-09 13:36 |  |  | Fair | Yes | Premises checked and found ok upon arrival, customer was also spoken with.
Non-Outage | J.E.26.08.10581 | C001883178 | Elvis Trowers | KSAS | Completed | Load_265476 | Duhaney - 310 | 2026-08-09 10:00 | 2026-08-09 10:03 | 2026-08-09 12:25 | 2026-08-09 12:25 | 2026-08-09 13:01 | 2026-08-09 13:04 | 2026-08-09 13:04 | 2026-08-09 13:04 |  |  | Fair | Yes | Premises checked and found ok upon arrival, customer was also spoken with however she said that the situation was resolved.
Non-Outage | J.E.26.08.10687 | C001883177 | Elvis Trowers | KSAS | Completed | Load_269320 | Duhaney - 310 | 2026-08-09 10:00 | 2026-08-09 10:03 | 2026-08-09 10:37 | 2026-08-09 10:37 | 2026-08-09 12:15 | 2026-08-09 12:18 | 2026-08-09 12:18 | 2026-08-09 12:18 |  |  | Fair | Yes | Customer was found having fluctuating voltage when checked and corroded joints was found at pat head where 2 one bolt clamps was used, voltage was left at 118+117=235 volts.
Non-Outage | J.E.26.08.10850 | C001883179 | Elvis Trowers | KSAS | Completed | Load_245998 | Duhaney - 310 | 2026-08-09 10:00 | 2026-08-09 10:03 | 2026-08-09 14:23 | 2026-08-09 14:24 | 2026-08-09 14:24 | 2026-08-09 14:26 | 2026-08-09 14:26 | 2026-08-09 14:26 |  |  | Fair | Yes | Premises found without electricity supply and 2 blown 5 amps transformer fuses was found during patrol and was replaced at pole #0101677.
Non-Outage | J.E.26.08.11168 | C001883180 | Elvis Trowers | KSAS | Completed | Load_567648 | Duhaney - 310 | 2026-08-09 10:00 | 2026-08-09 10:03 | 2026-08-09 13:38 | 2026-08-09 13:38 | 2026-08-09 13:56 | 2026-08-09 14:22 | 2026-08-09 14:22 | 2026-08-09 14:22 |  |  | Fair | Yes | Premises found without electricity supply when checked and 2 blown 5 amps transformer fuses was found and replaced after patrol was completed at pole #0101677
Non-Outage | J.E.26.08.10267 | C001883182 | Christopher Edwards | KSAN | Completed | Load_261778 | Constant Spring - 310 | 2026-08-09 10:01 | 2026-08-09 10:03 | 2026-08-09 12:54 | 2026-08-09 13:25 | 2026-08-09 13:24 | 2026-08-09 14:34 | 2026-08-09 14:34 | 2026-08-09 14:34 |  |  | Fair | No | Customer suspected that their neighbor is tampering with their meterCustomer requested meter to be barrel lockVoltage:117,116,233v
Non-Outage | J.E.26.08.11387 | C001883181 | Christopher Edwards | KSAN | Completed | Load_264247 | Constant Spring - 410 | 2026-08-09 10:01 | 2026-08-09 10:03 | 2026-08-10 08:06 | 2026-08-10 12:45 | 2026-08-10 12:56 | 2026-08-10 13:45 | 2026-08-10 13:46 | 2026-08-10 13:46 |  |  | Fair | No | Remake burnt phase joint on 2/0 twisted wire Using (1) one bolt clamps Voltage:114,113,230v
Outage | J.E.26.08.12460 | C001883186 | Delano Gayle | St.Catherine | Completed | Load_240658 | New Michelton - 210 | 2026-08-09 10:21 | 2026-08-09 15:51 | 2026-08-09 15:58 | 2026-08-09 15:59 | 2026-08-09 17:38 | 2026-08-09 18:04 | 2026-08-09 18:05 | 2026-08-09 18:05 |  |  | Fair | No | Defective customer equipment advised customer, burnt wire leading down in building, burnt phase disconnected
Non-Outage | J.E.26.08.12473 | C001883190 | Neville Spencer |  | Completed |  |  | 2026-08-09 10:26 | 2026-08-09 10:28 | 2026-08-09 12:04 | 2026-08-09 12:05 | 2026-08-09 13:09 | 2026-08-09 13:09 | 2026-08-09 13:10 | 2026-08-09 13:10 |  |  | Fair | No | Planned outage in area.
Outage | J.E.26.08.12447 | C001883193 | Andre Smith | KSAS | Completed | Load_255412 | Hunts Bay - 210 | 2026-08-09 10:39 | 2026-08-09 13:58 | 2026-08-10 09:38 | 2026-08-10 09:39 | 2026-08-10 09:55 | 2026-08-10 10:18 | 2026-08-10 10:18 | 2026-08-10 10:18 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.12480 | C001883195 | Kenroy Dale | Manchester | Completed | Load_266835 | Porus - 310 | 2026-08-09 10:40 | 2026-08-09 10:41 | 2026-08-09 20:40 | 2026-08-09 20:41 | 2026-08-09 21:10 | 2026-08-09 21:38 | 2026-08-09 21:42 | 2026-08-09 21:42 | LowHangingWires |  | Fair | No | Was unable to locate customer area patrol and found with supply
Outage | J.E.26.08.12503 | C001883197 | Milton Charlton | KSAN | Completed | Load_264271 | Washington Blvd - 610 | 2026-08-09 10:56 | 2026-08-09 10:57 | 2026-08-09 13:32 | 2026-08-09 13:32 | 2026-08-09 16:13 | 2026-08-09 16:10 | 2026-08-09 16:14 | 2026-08-09 16:14 |  |  | Fair | No | Reconnect customer meter 2369755 by J.P.S. Escalation.
Outage | J.E.26.08.12519 | C001883198 | Milton Charlton | KSAN | Completed | Load_239828 | Hope - 510 | 2026-08-09 10:56 | 2026-08-09 10:57 | 2026-08-09 12:12 | 2026-08-09 12:13 | 2026-08-09 13:30 | 2026-08-09 13:30 | 2026-08-09 13:32 | 2026-08-09 13:32 |  |  | Fair | No | J.P.S crew on site working. Scheduled outage.
Outage | J.E.26.08.12548 | C001883203 | Ryan Richards | Manchester | Completed | Load_253480 | Kendal - 210 | 2026-08-09 11:18 | 2026-08-09 11:19 | 2026-08-09 12:00 | 2026-08-09 13:28 | 2026-08-09 14:37 | 2026-08-09 16:01 | 2026-08-09 16:01 | 2026-08-09 16:01 |  |  | Fair | No | 1 span of broken secondary neutral and burn phase and neutral drop lead found cause by banging phase and neutral conductor open 25 kva transformer replaced drop lead using 9ft#2/0 copper and two#2/0 ampac splice and retention broken neutral using 20ft#2 aluminum 2 one bolt clamps and reclose transformer area was rechecked all customers are now with supply
Non-Outage | J.E.26.08.11883 | C001883211 | Roemello Brown | Trelawny | Completed | Load_262089 | Martha Brae - 210 | 2026-08-09 11:53 | 2026-08-10 08:11 | 2026-08-10 08:24 | 2026-08-10 13:21 | 2026-08-10 13:42 | 2026-08-10 13:42 | 2026-08-10 13:50 | 2026-08-10 13:50 |  |  | Fair | No | Premises found working okayVoltage found 117/116/233Voltage leave 117/116/233
Non-Outage | J.E.26.08.12547 | C001883210 | Roemello Brown | Trelawny | Completed | Load_292238 | Greenwood - 210 | 2026-08-09 11:53 | 2026-08-10 08:12 | 2026-08-10 11:14 | 2026-08-10 11:15 | 2026-08-10 12:01 | 2026-08-10 12:01 | 2026-08-10 12:26 | 2026-08-10 12:26 |  |  | Fair | No | Secondary twisted two north burn up needs maintenance team to assist 146 feet of wire need to be change change Voltage found 107/29
Non-Outage | J.E.26.08.06545 | C001883216 | Roemello Brown | Trelawny | Completed | Load_245108 | Greenwood - 210 | 2026-08-09 11:54 | 2026-08-10 08:11 | 2026-08-10 12:30 | 2026-08-10 12:31 | 2026-08-10 12:46 | 2026-08-10 12:46 | 2026-08-10 13:20 | 2026-08-10 13:20 |  |  | Fair | No | Corrosion at the pothead have clamps change Voltage found 101/102/203Voltage leave 104/104/209
Non-Outage | J.E.26.08.06581 | C001883215 | Marlon Brown | Trelawny | Completed | Load_262457 | Greenwood - 110 | 2026-08-09 11:54 | 2026-08-09 11:57 | 2026-08-09 14:18 | 2026-08-09 14:18 | 2026-08-09 14:34 | 2026-08-09 14:55 | 2026-08-09 14:55 | 2026-08-09 14:55 |  |  | Fair | No | Check and found ok Voltage found at pothead 120/123/204=223/222/220vVoltage leaving at pothead 120/123/204=223/222/220v.
Non-Outage | J.E.26.08.07307 | C001883214 | Roemello Brown | Trelawny | Completed | Load_292911 | Greenwood - 110 | 2026-08-09 11:54 | 2026-08-10 08:11 | 2026-08-10 09:35 | 2026-08-10 10:13 | 2026-08-10 10:13 | 2026-08-10 10:13 | 2026-08-10 11:12 | 2026-08-10 11:12 |  |  | Fair | No | Corrosion at the pothead an at the pole side have clamps change Voltage found 118/118/236Voltage leave 118/119/237
Non-Outage | J.E.26.08.07858 | C001883213 | Marlon Brown | Trelawny | Completed | Load_263192 | Martha Brae - 110 | 2026-08-09 11:54 | 2026-08-09 11:57 | 2026-08-09 13:03 | 2026-08-09 13:03 | 2026-08-09 13:21 | 2026-08-09 14:14 | 2026-08-09 14:15 | 2026-08-09 14:15 |  |  | Fair | No | Illegal connections causing area to have low voltage, Voltage found at meter socket 98/112=202vVoltage leaving at meter socket 112/98=202v Refer to losses department.
Outage | J.E.26.08.12571 | C001883218 | Nickolas Rodriques | St.Catherine | Completed | Load_253990 | New Michelton - 310 | 2026-08-09 11:59 | 2026-08-09 12:01 | 2026-08-09 13:37 | 2026-08-09 13:39 | 2026-08-09 14:21 | 2026-08-09 15:21 | 2026-08-09 15:23 | 2026-08-09 15:23 |  |  | Fair | No | Checked and found a 3 amp transformer fuse blown. Patrol and found nothing on line. Repaired by replacing the fuse after completing patrol.
Non-Outage | J.E.26.07.38674 | C001883220 | Daniel Francis | St.Ann | Completed | Load_240751 | Roaring River - 210 | 2026-08-09 12:02 | 2026-08-09 12:03 | 2026-08-09 12:29 | 2026-08-09 12:30 | 2026-08-09 13:45 | 2026-08-09 14:35 | 2026-08-09 14:44 | 2026-08-09 14:44 |  |  | Fair | No | Retention and change 2 one bolt clamp we get 109 on one side and 97 on one offer do that we trend transformer from 3 to 5 and we get 110 111 221 in all
Non-Outage | J.E.26.08.11237 | C001883222 | Shamour Haughton | St.James | Completed | Load_255029 | Bogue - 310 | 2026-08-09 12:06 | 2026-08-09 16:23 | 2026-08-09 16:39 | 2026-08-09 16:40 | 2026-08-09 17:04 | 2026-08-09 17:04 | 2026-08-09 17:07 | 2026-08-09 17:07 | Fire |  | Fair | No | Found customer service wire corroded at pole, clean and remake joint at pole, voltage left 113,113,226
Non-Outage | J.E.26.08.11614 | C001883231 | Swon Miller | St.James | Completed | Load_253031 | Queens Drive - 310 | 2026-08-09 12:08 | 2026-08-09 12:09 | 2026-08-09 12:20 | 2026-08-09 13:16 | 2026-08-09 13:25 | 2026-08-25 01:47 | 2026-08-09 14:00 | 2026-08-09 14:00 |  |  | Fair | No | Found 50 kva transformer fuse blown cause by contamination replace 5 amp in a 50 kva transformer at pole number 562613
Non-Outage | J.E.26.08.12103 | C001883230 | Swon Miller | St.James | Completed | Load_256990 | Queens Drive - 710 | 2026-08-09 12:08 | 2026-08-09 12:09 | 2026-08-09 12:20 | 2026-08-09 14:01 | 2026-08-09 14:28 | 2026-08-20 15:50 | 2026-08-09 16:03 | 2026-08-09 16:03 |  |  | Fair | No | Check and found number 6 jumper clamp burnt cause by slack connection clean and remake joints use 2 pg voltage found 112/99/211 voltage left 111/112/224
Outage | J.E.26.08.12588 | C001883227 | Raymond Lewis | St.Ann | Completed | Load_263745 | Cardiff Hall - 310 | 2026-08-09 12:08 | 2026-08-09 12:47 | 2026-08-09 13:06 | 2026-08-09 13:06 | 2026-08-09 13:37 | 2026-08-09 13:38 | 2026-08-09 13:39 | 2026-08-09 13:39 |  |  | Fair | No | Phone not answering
Non-Outage | J.E.26.08.08995 | C001883236 | Derrick Dawkins | St.James | Completed | Load_267952 | Rose Hall - 210 | 2026-08-09 12:09 | 2026-08-09 12:10 | 2026-08-09 12:22 | 2026-08-09 12:22 | 2026-08-09 13:07 | 2026-08-09 13:10 | 2026-08-09 13:11 | 2026-08-09 13:11 | Fire |  | Fair | No | Found premises ok
Non-Outage | J.E.26.08.09402 | C001883234 | Romeo Brissett | St.James | Completed | Load_302071 | Queens Drive - 810 | 2026-08-09 12:09 | 2026-08-10 12:42 | 2026-08-10 13:16 | 2026-08-10 13:54 | 2026-08-10 14:17 | 2026-08-10 15:00 | 2026-08-10 15:06 | 2026-08-10 15:06 |  |  | Fair | No | Check and found V/R 103.4-103.6-179.8/207.1-207.4-207.6. Please send SMD.
Non-Outage | J.E.26.08.09534 | C001883235 | Derrick Dawkins | St.James | Completed | Load_260605 | Queens Drive - 710 | 2026-08-09 12:09 | 2026-08-09 12:10 | 2026-08-09 12:29 | 2026-08-09 13:11 | 2026-08-09 13:42 | 2026-08-09 14:26 | 2026-08-09 14:34 | 2026-08-09 14:34 |  |  | Fair | No | Found customer service wire neutral burn off due to banging secondary wire splice and retention customer service wire used 20ft #6 triplex 2pg clamp voltage left 119/117/23
Non-Outage | J.E.26.08.12414 | C001883239 | Gregory Grossett |  | Completed |  |  | 2026-08-09 12:16 | 2026-08-09 18:55 | 2026-08-09 19:10 | 2026-08-09 19:10 | 2026-08-09 19:10 | 2026-08-09 19:10 | 2026-08-09 19:11 | 2026-08-09 19:11 | BrokenWire |  | Fair | No | Call is related to previous call for Rollandsfield
Outage | J.E.26.08.12363 | C001883237 | Stephen Taylor | St.Thomas | Completed | Load_266529 | Good Year - 210 | 2026-08-09 12:16 | 2026-08-09 12:17 | 2026-08-09 15:00 | 2026-08-09 15:00 | 2026-08-09 16:27 | 2026-08-09 16:27 | 2026-08-09 16:29 | 2026-08-09 16:29 | Fire |  | Fair | No | Replace 100 ft a service wire 3 clamps and 3 p/union Rdg 114–116 226
Outage | J.E.26.08.12607 | C001883245 | Romaine Roberts | St.Ann | Completed | Load_261553 | Upper White River - 110 | 2026-08-09 12:52 | 2026-08-09 15:31 | 2026-08-09 16:55 | 2026-08-09 16:56 | 2026-08-09 18:31 | 2026-08-09 18:32 | 2026-08-09 18:41 | 2026-08-09 18:41 | Fire |  | Fair | No | Leaning pole causing causing tree to make Contact with primary line pole need to be straighten up also tree lim née to b clear
Non-Outage | J.E.26.08.11277 | C001883248 | Cliton Henry | St.Mary | Completed | Load_351007 | Oracabessa - 210 | 2026-08-09 13:00 | 2026-08-09 15:49 | 2026-08-09 15:58 | 2026-08-09 15:58 | 2026-08-09 16:12 | 2026-08-09 16:18 | 2026-08-09 16:18 | 2026-08-09 16:18 |  |  | Fair | No | The voltages found at the metering point were 115-118/233 volts. The customer was advised to get a licensed electrician to check internally.
Non-Outage | J.E.26.08.12584 | C001883249 | Milton Charlton | KSAN | Completed | Load_258037 | Washington Blvd - 510 | 2026-08-09 13:02 | 2026-08-09 18:23 | 2026-08-09 19:47 | 2026-08-09 19:47 | 2026-08-09 20:55 | 2026-08-09 20:55 | 2026-08-09 21:00 | 2026-08-09 21:00 |  |  | Fair | No | Premises closed.unable to connect burnt off #6 triplex phase because of feed back coming from the premises.
Outage | J.E.26.08.12611 | C001883254 | Neville Spencer | Clarendon | Completed | Load_267083 | Monymusk - 210 | 2026-08-09 13:19 | 2026-08-09 13:23 | 2026-08-09 16:03 | 2026-08-09 16:03 | 2026-08-09 17:56 | 2026-08-09 17:56 | 2026-08-09 17:57 | 2026-08-09 17:57 |  |  | Fair | No | Customer did not make any report.
Outage | J.E.26.08.12626 | C001883253 | Clyde Brown | Clarendon | Completed | Load_240712 | May Pen - 110 | 2026-08-09 13:19 | 2026-08-10 07:26 | 2026-08-10 09:23 | 2026-08-10 09:23 | 2026-08-10 09:47 | 2026-08-10 09:40 | 2026-08-10 09:50 | 2026-08-10 09:50 |  |  | Fair | No | Found ok
Outage | J.E.26.08.12632 | C001883252 | Neville Spencer | Clarendon | Completed | Load_258999 | Monymusk - 410 | 2026-08-09 13:19 | 2026-08-09 13:23 | 2026-08-09 14:16 | 2026-08-09 14:17 | 2026-08-09 15:06 | 2026-08-09 15:06 | 2026-08-09 16:03 | 2026-08-09 16:03 |  |  | Fair | No | Remade corrded phase and neutral joints at pothead on 3, wire service used 3, 2/6 sleeves voltage reading 113 116 231 supply restored.
Outage | J.E.26.08.12535 | C001883255 | Hartley Chin | Clarendon | Completed | Load_260474 | Monymusk - 410 | 2026-08-09 13:23 | 2026-08-10 07:24 | 2026-08-10 11:59 | 2026-08-10 12:00 | 2026-08-10 12:00 | 2026-08-10 12:00 | 2026-08-10 12:02 | 2026-08-10 12:02 |  |  | Fair | No | Call related to job # 11530
Outage | J.E.26.08.12677 | C001883260 | Wayne Dillion | St.Elizabeth | Completed | Load_249683 | Maggotty - 110 | 2026-08-09 13:43 | 2026-08-09 13:44 | 2026-08-09 14:09 | 2026-08-09 14:10 | 2026-08-09 14:09 | 2026-08-09 14:10 | 2026-08-09 14:11 | 2026-08-09 14:11 |  |  | Fair | No | Customer said supply was restored to the area.
Outage | J.E.26.08.12446 | C001883263 | Rusean Allen | KSAS | Completed | Load_246905 | Cane River - 410 | 2026-08-09 13:56 | 2026-08-09 13:57 | 2026-08-09 14:32 | 2026-08-09 15:02 | 2026-08-09 17:49 | 2026-08-09 19:00 | 2026-08-09 19:00 | 2026-08-09 19:00 |  |  | Fair | No | Transformer defective 50 kva refer to maintenance department
Outage | J.E.26.08.12689 | C001883276 | Kenroy Dale | Manchester | Completed | Load_245342 | Spur Tree - 310 | 2026-08-09 14:23 | 2026-08-09 14:24 | 2026-08-09 15:29 | 2026-08-09 15:43 | 2026-08-09 17:07 | 2026-08-09 17:59 | 2026-08-09 18:08 | 2026-08-09 18:08 |  |  | Fair | No | Blown 2 amp transformer fuse found drop lead was also corrected remade connection using 2 one bolt transformer re-closed and area now with supply voltage reading 113/113/226
Outage | J.E.26.08.12693 | C001883277 | Kenroy Dale | Manchester | Completed | Load_266835 | Porus - 310 | 2026-08-09 14:23 | 2026-08-09 14:24 | 2026-08-09 19:54 | 2026-08-09 20:17 | 2026-08-09 20:38 | 2026-08-09 20:39 | 2026-08-09 20:40 | 2026-08-09 20:40 | BrokenWire |  | Fair | No | Customer made reports for the wrong parish
Outage | J.E.26.08.12714 | C001883285 | Javid Vernon | Westmoreland | Completed | Load_263128 | Paradise - 110 | 2026-08-09 14:46 | 2026-08-09 14:46 | 2026-08-09 16:51 | 2026-08-09 16:54 | 2026-08-09 17:09 | 2026-08-09 17:38 | 2026-08-09 17:38 | 2026-08-09 17:38 | TreeContact |  | Fair | No | Remove vegetation an clean and remake joints at JPS pole voltage found 97/84/181 voltage left 114/115/229
Outage | J.E.26.08.12646 | C001883294 | Romeo Brissett | St.James | Completed | Load_268384 | Bogue - 610 | 2026-08-09 14:54 | 2026-08-09 14:55 | 2026-08-09 15:05 | 2026-08-09 15:05 | 2026-08-09 15:53 | 2026-08-09 16:28 | 2026-08-09 16:32 | 2026-08-09 16:32 | BrokenWire |  | Fair | No | Removed tree limbs, replaced (1)10amps junction fuse.
Outage | J.E.26.08.12660 | C001883295 | Romeo Brissett | St.James | Completed | Load_302426 | Bogue - 510 | 2026-08-09 14:54 | 2026-08-09 21:30 | 2026-08-09 21:52 | 2026-08-09 21:53 | 2026-08-09 21:57 | 2026-08-09 22:44 | 2026-08-09 22:47 | 2026-08-09 22:47 |  |  | Fair | No | Check and found internal fault customer was advised to get an electrician.
Outage | J.E.26.08.12577 | C001883296 | Fitzroy Turner | KSAN | Completed | Load_267231 | Washington Blvd - 710 | 2026-08-09 14:58 | 2026-08-09 15:36 | 2026-08-09 16:54 | 2026-08-09 16:55 | 2026-08-09 16:54 | 2026-08-09 17:16 | 2026-08-09 17:18 | 2026-08-09 17:18 | BrokenWire |  | Fair | No | Found tree wire open secondary neutral cut down cause by illegal connections.use 30ft of 2# aluminum wire and two preform and 4one bolt clamps to carry out repair supply restored to the areas
Outage | J.E.26.08.12578 | C001883298 | Fitzroy Turner | KSAN | Completed | Load_253322 | Washington Blvd - 310 | 2026-08-09 14:58 | 2026-08-09 15:37 | 2026-08-09 17:30 | 2026-08-09 18:04 | 2026-08-09 18:28 | 2026-08-09 19:23 | 2026-08-09 19:24 | 2026-08-09 19:24 |  |  | Fair | No | Found two wires service phase burnt off in YPP box have service reconnected in box supply restored to customer
Outage | J.E.26.08.12617 | C001883297 | Rusean Allen | KSAS | Completed | Load_573563 | Cane River - 410 | 2026-08-09 14:58 | 2026-08-09 15:14 | 2026-08-09 19:00 | 2026-08-09 19:01 | 2026-08-09 19:29 | 2026-08-09 19:54 | 2026-08-09 19:54 | 2026-08-09 19:54 |  |  | Fair | No | No communication from meter refer to field service
Outage | J.E.26.08.12656 | C001883299 | Rusean Allen | KSAS | Completed | Load_301275 | Hunts Bay - 510 | 2026-08-09 14:58 | 2026-08-10 07:54 | 2026-08-10 13:51 | 2026-08-10 13:52 | 2026-08-10 14:52 | 2026-08-10 14:53 | 2026-08-10 14:53 | 2026-08-10 14:53 |  |  | Fair | No | Area congested, unable to access Poe to conduct repairs.
Non-Outage | J.E.26.06.12915 | C001883311 | Ryan Richards | Manchester | Completed | Load_262533 | Kendal - 210 | 2026-08-09 15:05 | 2026-08-09 15:06 | 2026-08-09 18:42 | 2026-08-09 18:42 | 2026-08-09 19:51 | 2026-08-09 20:56 | 2026-08-09 20:58 | 2026-08-09 20:58 |  |  | Fair | No | Broken service wire found splice and retention using 20ft#6 triplex 3 one bolt clamps voltage 117/119/237 volt
Non-Outage | J.E.26.06.39342 | C001883308 | Ryan Richards | Manchester | Completed | Load_261906 | Kendal - 210 | 2026-08-09 15:05 | 2026-08-09 15:06 | 2026-08-09 19:38 | 2026-08-09 20:59 | 2026-08-09 23:28 | 2026-08-09 23:29 | 2026-08-09 23:29 | 2026-08-09 23:29 |  |  | Fair | No | Premises found ok customer was disconnected for bill issues customer was advised to visit office
Non-Outage | J.E.26.07.10529 | C001883306 | Ryan Richards | Manchester | Completed | Load_252632 | Kendal - 210 | 2026-08-09 15:05 | 2026-08-09 15:06 | 2026-08-09 16:04 | 2026-08-09 16:05 | 2026-08-09 17:36 | 2026-08-09 18:41 | 2026-08-09 18:41 | 2026-08-09 18:41 |  |  | Fair | No | Corroded phase and neutral found at pole remade corroded phase and neutral using 2 one bolt clamps voltage 112/114/227 Volts
Non-Outage | J.E.26.08.12729 | C001883315 | Floyd Taylor |  | Completed |  |  | 2026-08-09 15:10 | 2026-08-09 15:13 | 2026-08-09 20:32 | 2026-08-09 20:32 | 2026-08-09 20:37 | 2026-08-09 20:37 | 2026-08-09 20:38 | 2026-08-09 20:38 |  |  | Fair | No | Customer power was restored
Outage | J.E.26.08.12523 | C001883316 | Floyd Taylor | Trelawny | Completed | Load_292482 | Greenwood - 210 | 2026-08-09 15:10 | 2026-08-09 15:13 | 2026-08-09 15:28 | 2026-08-09 15:29 | 2026-08-09 16:18 | 2026-08-09 17:37 | 2026-08-09 17:37 | 2026-08-09 17:37 | BrokenPole,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Clean and remake joints at pole using 3pg -clamp also 30ft secondary pole rotten at the base and leaning towards the customer premises needs to be replaced. Voltage readings left 114,115,231
Outage | J.E.26.08.12627 | C001883317 | Floyd Taylor | Trelawny | Completed | Load_268469 | Duncans - 210 | 2026-08-09 15:10 | 2026-08-09 15:13 | 2026-08-09 17:42 | 2026-08-09 17:42 | 2026-08-09 19:52 | 2026-08-09 20:30 | 2026-08-09 20:31 | 2026-08-09 20:31 |  |  | Fair | No | Cut vines from line and replace 1-15 amp junction fuse.
Non-Outage | J.E.26.05.05227 | C001883324 | Javid Vernon | Westmoreland | Completed | Load_292200 | Paradise - 110 | 2026-08-09 15:14 | 2026-08-09 15:16 | 2026-08-09 15:44 | 2026-08-09 15:45 | 2026-08-09 16:06 | 2026-08-09 16:46 | 2026-08-09 16:46 | 2026-08-09 16:46 |  |  | Fair | No | Check and found customer service wire under size for supplying 22 customer #2 triplex wire needs to be upgraded wire is defective a previous report was made and was refer to field service job #09957
Non-Outage | J.E.26.06.38173 | C001883322 | Javid Vernon | Westmoreland | Completed | Load_260985 | Paradise - 110 | 2026-08-09 15:14 | 2026-08-09 15:16 | 2026-08-09 21:01 | 2026-08-09 21:01 | 2026-08-09 21:54 | 2026-08-09 22:18 | 2026-08-09 22:18 | 2026-08-09 22:18 |  |  | Fair | No | Area check and found okay unable to locate customer on premises multiple phone calls to customer number went unanswered
Non-Outage | J.E.26.07.00457 | C001883321 | Javid Vernon | Westmoreland | Completed | Load_248383 | Orange Bay - 310 | 2026-08-09 15:14 | 2026-08-09 15:16 | 2026-08-09 18:51 | 2026-08-09 18:51 | 2026-08-09 19:12 | 2026-08-09 19:36 | 2026-08-09 19:36 | 2026-08-09 19:36 |  |  | Fair | No | Reconnect customer service neutral use one clamp voltage left 107/111/218
Non-Outage | J.E.26.08.04596 | C001883323 | Javid Vernon | Westmoreland | Completed | Load_242624 | Paradise - 110 | 2026-08-09 15:14 | 2026-08-09 15:16 | 2026-08-09 17:55 | 2026-08-09 17:56 | 2026-08-09 18:08 | 2026-08-09 18:34 | 2026-08-09 18:35 | 2026-08-09 18:35 |  |  | Fair | No | Clean and remake joints at JPS pole use two clamp voltage found 100/91/191 voltage left 108/105/213
Non-Outage | J.E.26.08.07445 | C001883320 | Javid Vernon | Westmoreland | Completed | Load_262801 | Paradise - 110 | 2026-08-09 15:14 | 2026-08-09 15:16 | 2026-08-09 18:37 | 2026-08-09 19:37 | 2026-08-09 20:33 | 2026-08-09 20:56 | 2026-08-09 21:00 | 2026-08-09 21:00 |  |  | Fair | No | Connect customer service neutral use one clamp voltage found 216 voltage left 106/110/216
Non-Outage | J.E.26.08.10305 | C001883319 | Javid Vernon | Westmoreland | Completed | Load_263040 | Paradise - 110 | 2026-08-09 15:14 | 2026-08-09 15:16 | 2026-08-09 16:52 | 2026-08-09 16:53 | 2026-08-09 16:52 | 2026-08-09 16:53 | 2026-08-09 16:54 | 2026-08-09 16:54 |  |  | Fair | No | Customer stated that the power was restored
Outage | J.E.26.08.11937 | C001883327 | Shamour Haughton | St.James | Completed | Load_555837 | Bogue - 310 | 2026-08-09 15:15 | 2026-08-09 15:23 | 2026-08-09 16:00 | 2026-08-09 16:00 | 2026-08-09 16:35 | 2026-08-09 16:35 | 2026-08-09 16:37 | 2026-08-09 16:37 | LeaningPole |  | Fair | No | Customer reporting about streetlight
Outage | J.E.26.08.12687 | C001883326 | Shamour Haughton | St.James | Completed | Load_292555 | Bogue - 310 | 2026-08-09 15:15 | 2026-08-09 15:23 | 2026-08-09 17:07 | 2026-08-09 17:07 | 2026-08-09 17:07 | 2026-08-09 17:07 | 2026-08-09 17:08 | 2026-08-09 17:08 |  |  | Fair | No | Customer states that power was restored
Non-Outage | J.E.26.08.11887 | C001883328 | Oshane Warren | Westmoreland | Completed | Load_249420 | Paradise - 310 | 2026-08-09 15:18 | 2026-08-09 15:28 | 2026-08-09 15:40 | 2026-08-09 15:41 | 2026-08-09 15:40 | 2026-08-09 15:41 | 2026-08-09 15:41 | 2026-08-09 15:41 |  |  | Rains | No | Unable to locate or contact customer need direction
Outage | J.E.26.08.12739 | C001883331 | Milton Charlton | KSAN | Completed | Load_248814 | Hope - 510 | 2026-08-09 15:19 | 2026-08-09 15:23 | 2026-08-09 16:14 | 2026-08-09 16:15 | 2026-08-09 17:02 | 2026-08-09 17:10 | 2026-08-09 17:04 | 2026-08-09 17:04 | Fire |  | Fair | No | Found one 15 junction fuse blown at pole# 0073576. Refuse using one 15 amps fuse and reclosed junction switch.
Non-Outage | J.E.26.06.36832 | C001883332 | Marlon Authors | Manchester | Completed | Load_1002334 | Spur Tree - 210 | 2026-08-09 15:20 | 2026-08-09 15:22 | 2026-08-09 18:16 | 2026-08-09 18:17 | 2026-08-09 18:58 | 2026-08-09 19:33 | 2026-08-09 19:33 | 2026-08-09 19:33 |  |  | Fair | No | Unable to locate and the customer not answering the phone
Non-Outage | J.E.26.07.00351 | C001883339 | Marlon Authors | Manchester | Completed | Load_302835 | Spur Tree - 210 | 2026-08-09 15:21 | 2026-08-09 15:22 | 2026-08-09 19:40 | 2026-08-09 19:40 | 2026-08-09 19:40 | 2026-08-09 19:43 | 2026-08-09 19:43 | 2026-08-09 19:43 |  |  | Fair | No | Unable to locate and the customer not answering the phone
Non-Outage | J.E.26.07.03315 | C001883338 | Marlon Authors | Manchester | Completed | Load_302821 | Spur Tree - 210 | 2026-08-09 15:21 | 2026-08-09 15:22 | 2026-08-09 19:52 | 2026-08-09 19:52 | 2026-08-09 19:52 | 2026-08-09 19:54 | 2026-08-09 19:54 | 2026-08-09 19:54 |  |  | Fair | No | Customer said supply is okay
Non-Outage | J.E.26.07.04864 | C001883337 | Marlon Authors | Manchester | Completed | Load_238812 | Spur Tree - 210 | 2026-08-09 15:21 | 2026-08-09 15:22 | 2026-08-09 19:59 | 2026-08-09 20:00 | 2026-08-09 20:00 | 2026-08-09 20:01 | 2026-08-09 20:01 | 2026-08-09 20:01 |  |  | Fair | No | Unable to locate and the customer not answering the phone
Non-Outage | J.E.26.08.05430 | C001883334 | Marlon Authors | Manchester | Completed | Load_255067 | Spur Tree - 210 | 2026-08-09 15:21 | 2026-08-09 15:22 | 2026-08-09 21:26 | 2026-08-09 21:26 | 2026-08-09 21:26 | 2026-08-09 21:28 | 2026-08-09 21:28 | 2026-08-09 21:28 |  |  | Fair | No | Unable to locate and the customer not answering the phone
Non-Outage | J.E.26.08.06032 | C001883335 | Marlon Authors | Manchester | Completed | Load_556608 | Spur Tree - 210 | 2026-08-09 15:21 | 2026-08-09 15:22 | 2026-08-09 20:03 | 2026-08-09 20:03 | 2026-08-09 20:03 | 2026-08-09 20:09 | 2026-08-09 20:09 | 2026-08-09 20:09 |  |  | Fair | No | Supply seen in the area, unable to locate premises customer not answering the phone
Non-Outage | J.E.26.08.10449 | C001883336 | Marlon Authors | Manchester | Completed | Load_248021 | Spur Tree - 210 | 2026-08-09 15:21 | 2026-08-09 15:22 | 2026-08-09 20:44 | 2026-08-09 20:45 | 2026-08-09 20:44 | 2026-08-09 20:45 | 2026-08-09 20:45 | 2026-08-09 20:45 |  |  | Fair | No | Supply restored to premises
Non-Outage | J.E.26.08.10451 | C001883333 | Marlon Authors | Manchester | Completed | Load_248021 | Spur Tree - 210 | 2026-08-09 15:21 | 2026-08-09 15:22 | 2026-08-09 20:15 | 2026-08-09 20:15 | 2026-08-09 20:26 | 2026-08-09 20:40 | 2026-08-09 20:40 | 2026-08-09 20:40 |  |  | Fair | No | Supply checked and found service wire neutral broken. Splice and retention same using five feet of #6 triplex service wire and two clamps. Supply leave working ok rdg 112v,114v and cross phased 227 volts
Non-Outage | J.E.26.03.06495 | C001883352 | Raheem Ricketts | St.Elizabeth | Completed | Load_261671 | Maggotty - 210 | 2026-08-09 15:25 | 2026-08-09 15:27 | 2026-08-09 15:41 | 2026-08-09 16:06 | 2026-08-09 16:06 | 2026-08-09 16:07 | 2026-08-09 16:07 | 2026-08-09 16:07 |  |  | Fair | No | Customer experiencing an internal problem
Non-Outage | J.E.26.03.18287 | C001883351 | Raheem Ricketts | St.Elizabeth | Completed | Load_238091 | Maggotty - 210 | 2026-08-09 15:25 | 2026-08-09 15:27 | 2026-08-09 15:41 | 2026-08-09 15:58 | 2026-08-09 15:58 | 2026-08-09 15:58 | 2026-08-09 15:58 | 2026-08-09 15:58 |  |  | Fair | No | Unable to communicate with customer cel number went straight voicemail
Non-Outage | J.E.26.03.27748 | C001883350 | Raheem Ricketts | St.Elizabeth | Completed | Load_267239 | Maggotty - 210 | 2026-08-09 15:25 | 2026-08-09 15:27 | 2026-08-09 15:41 | 2026-08-09 17:05 | 2026-08-09 17:04 | 2026-08-09 17:05 | 2026-08-09 17:05 | 2026-08-09 17:05 |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.03.44047 | C001883349 | Raheem Ricketts | St.Elizabeth | Completed | Load_250172 | Maggotty - 210 | 2026-08-09 15:25 | 2026-08-09 15:27 | 2026-08-09 15:41 | 2026-08-09 15:56 | 2026-08-09 15:56 | 2026-08-09 15:56 | 2026-08-09 15:57 | 2026-08-09 15:57 |  |  | Fair | No | Customer cell phone number is out of service
Non-Outage | J.E.26.05.15875 | C001883348 | Raheem Ricketts | St.Elizabeth | Completed | Load_242212 | Maggotty - 210 | 2026-08-09 15:25 | 2026-08-09 15:27 | 2026-08-09 15:41 | 2026-08-09 15:53 | 2026-08-09 15:53 | 2026-08-09 15:54 | 2026-08-09 15:54 | 2026-08-09 15:54 |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.05.24212 | C001883347 | Raheem Ricketts | St.Elizabeth | Completed | Load_1002215 | Maggotty - 210 | 2026-08-09 15:25 | 2026-08-09 15:27 | 2026-08-09 15:41 | 2026-08-09 17:21 | 2026-08-09 17:21 | 2026-08-09 17:21 | 2026-08-09 17:21 | 2026-08-09 17:21 |  |  | Fair | No | Customer cell number went straight voicemail after several calls
Non-Outage | J.E.26.06.07957 | C001883344 | Raheem Ricketts | St.Elizabeth | Completed | Load_261671 | Spur Tree - 210 | 2026-08-09 15:25 | 2026-08-09 15:27 | 2026-08-09 15:41 | 2026-08-09 15:46 | 2026-08-09 15:46 | 2026-08-09 15:46 | 2026-08-09 15:46 | 2026-08-09 15:46 |  |  | Fair | No | Unable to locate customer cell phone went straight voicemail after several calls
Non-Outage | J.E.26.06.18745 | C001883346 | Raheem Ricketts | St.Elizabeth | Completed | Load_257851 | Spur Tree - 210 | 2026-08-09 15:25 | 2026-08-09 15:27 | 2026-08-09 15:41 | 2026-08-09 15:50 | 2026-08-09 15:50 | 2026-08-09 15:50 | 2026-08-09 15:50 | 2026-08-09 15:50 |  |  | Fair | No | Customer 2 phone number went straight voicemail
Non-Outage | J.E.26.07.01847 | C001883345 | Raheem Ricketts | St.Elizabeth | Completed | Load_303240 | Spur Tree - 210 | 2026-08-09 15:25 | 2026-08-09 15:27 | 2026-08-09 15:41 | 2026-08-09 17:08 | 2026-08-09 17:07 | 2026-08-09 17:08 | 2026-08-09 17:08 | 2026-08-09 17:08 |  |  | Fair | No | Customer cell number went voicemail after several calls
Non-Outage | J.E.26.07.17348 | C001883343 | Raheem Ricketts | St.Elizabeth | Completed | Load_292586 | Spur Tree - 210 | 2026-08-09 15:25 | 2026-08-09 15:27 | 2026-08-09 15:41 | 2026-08-09 16:08 | 2026-08-09 16:31 | 2026-08-09 17:04 | 2026-08-09 17:04 | 2026-08-09 17:04 |  |  | Fair | No | Check and found one leg of customer service wire burn at pole remake joint using one clamp
Outage | J.E.26.08.11515 | C001883354 | Ricky Hall | St.Catherine | Completed | Load_256300 | Tredegar - 210 | 2026-08-09 15:26 | 2026-08-09 15:50 | 2026-08-09 17:53 | 2026-08-09 17:54 | 2026-08-09 19:01 | 2026-08-09 19:11 | 2026-08-09 19:12 | 2026-08-09 19:12 |  |  | Fair | No | Customer found disconnected unable to reach escalation team for a reset
Outage | J.E.26.08.11676 | C001883356 | Ricky Hall | St.Catherine | Completed | Load_256392 | Tredegar - 410 | 2026-08-09 15:26 | 2026-08-09 15:50 | 2026-08-09 17:09 | 2026-08-09 19:44 | 2026-08-09 20:09 | 2026-08-09 20:09 | 2026-08-09 20:10 | 2026-08-09 20:10 |  |  | Fair | No | Customer found with supply
Outage | J.E.26.08.12158 | C001883357 | Ricky Hall | St.Catherine | Completed | Load_265213 | Tredegar - 510 | 2026-08-09 15:26 | 2026-08-09 15:50 | 2026-08-09 17:08 | 2026-08-09 17:18 | 2026-08-09 17:42 | 2026-08-09 17:52 | 2026-08-09 17:52 | 2026-08-09 17:52 |  |  | Fair | No | Premises closed
Outage | J.E.26.08.12420 | C001883353 | Richard Nicholas | St.Catherine | Completed | Load_568174 | Rhodens Pen - 410 | 2026-08-09 15:26 | 2026-08-09 15:42 | 2026-08-09 16:07 | 2026-08-09 16:08 | 2026-08-09 18:17 | 2026-08-09 18:55 | 2026-08-09 18:56 | 2026-08-09 18:56 |  |  | EarthMovement | No | Premises can not locate and customer telephone number unreachable.directions needed.
Outage | J.E.26.08.12691 | C001883355 | Ricky Hall | St.Catherine | Completed | Load_254315 | Tredegar - 310 | 2026-08-09 15:26 | 2026-08-09 15:50 | 2026-08-09 20:10 | 2026-08-09 20:11 | 2026-08-09 20:34 | 2026-08-09 20:40 | 2026-08-09 20:41 | 2026-08-09 20:41 |  |  | Fair | No | Issue resolved by electrician 117 at pothead
Non-Outage | J.E.26.08.11971 | C001883359 | Roxroy Needham | St.Ann | Completed | Load_244725 | Roaring River - 410 | 2026-08-09 15:31 | 2026-08-09 15:32 | 2026-08-09 16:37 | 2026-08-09 16:38 | 2026-08-09 16:37 | 2026-08-09 16:38 | 2026-08-09 16:39 | 2026-08-09 16:39 |  |  | Flood | No | Premises found ok call customer and customer say that JPS team com yesterday and the pump is ok
Non-Outage | J.E.26.08.12212 | C001883362 | Omar King | St.Ann | Completed | Load_254060 | Ocho Rios - 510 | 2026-08-09 15:34 | 2026-08-09 15:35 | 2026-08-09 19:24 | 2026-08-09 19:25 | 2026-08-09 20:11 | 2026-08-09 20:14 | 2026-08-09 20:15 | 2026-08-09 20:15 |  |  | Fair | No | Unable to find customer
Outage | J.E.26.08.12398 | C001883363 | Rusean Allen | KSAS | Completed | Load_269201 | Hunts Bay - 310 | 2026-08-09 15:34 | 2026-08-09 15:35 | 2026-08-09 22:20 | 2026-08-09 22:20 | 2026-08-10 08:30 | 2026-08-10 10:39 | 2026-08-10 10:40 | 2026-08-10 10:40 |  |  | Fair | No | No communication from meter
Outage | J.E.26.08.12463 | C001883366 | Rusean Allen | KSAS | Completed | Load_248008 | Rockfort - 410 | 2026-08-09 15:34 | 2026-08-09 15:35 | 2026-08-09 19:54 | 2026-08-09 19:55 | 2026-08-09 19:56 | 2026-08-09 19:58 | 2026-08-09 19:58 | 2026-08-09 19:58 |  |  | Fair | No | Customer cell phone rill with out answer
Outage | J.E.26.08.12182 | C001883368 | Fitzroy Turner | KSAN | Completed | Load_575386 | Washington Blvd - 710 | 2026-08-09 15:37 | 2026-08-09 15:38 | 2026-08-09 15:59 | 2026-08-09 16:09 | 2026-08-09 16:53 | 2026-08-09 16:53 | 2026-08-09 16:54 | 2026-08-09 16:54 |  |  | EarthMovement | No | Customer supply restored with the help of the call center
Outage | J.E.26.08.12551 | C001883373 | Donald Cunningham | St.Catherine | Completed | Load_251822 | Twickenham - 210 | 2026-08-09 15:39 | 2026-08-09 15:42 | 2026-08-09 15:54 | 2026-08-09 15:55 | 2026-08-09 17:03 | 2026-08-09 17:29 | 2026-08-09 17:31 | 2026-08-09 17:31 |  |  | Fair | No | Reconnect broken 3 wire service after repair 3 clamps use voltage readings 115/2/230
Outage | J.E.26.08.12746 | C001883370 | Donald Cunningham | St.Catherine | Completed | Load_260246 | Twickenham - 210 | 2026-08-09 15:39 | 2026-08-09 15:42 | 2026-08-09 17:32 | 2026-08-09 17:32 | 2026-08-09 18:25 | 2026-08-09 18:25 | 2026-08-09 18:55 | 2026-08-09 18:55 |  |  | Fair | No | Corroded phase and neural by pole corrected 2 clamps use voltage readings by meter socket 110
Outage | J.E.26.08.03961 | C001883374 | Romeo Brissett | St.James | Completed | Load_292067 | Bogue - 610 | 2026-08-09 15:43 | 2026-08-09 15:44 | 2026-08-09 16:45 | 2026-08-09 16:46 | 2026-08-09 16:45 | 2026-08-09 16:45 | 2026-08-09 16:49 | 2026-08-09 16:49 |  |  | Fair | No | Customer meter is relocated to almost 200ft and need service wire, Customer was advised to relocate meter point within the hundred feet and report back to JPS whenever they’re finish.
Outage | J.E.26.07.23690 | C001883377 | Romeo Brissett | St.James | Completed | Load_249633 | Bogue - 610 | 2026-08-09 15:46 | 2026-08-09 15:47 | 2026-08-09 16:54 | 2026-08-09 16:55 | 2026-08-09 18:39 | 2026-08-09 19:40 | 2026-08-09 19:47 | 2026-08-09 19:47 |  |  | Fair | No | Isolated (1)25kva transformer, removed illegal connections, repaired secondary jumper.
Outage | J.E.26.08.12721 | C001883382 | Dwayne Cohen | KSAN | Completed | Load_261080 | Constant Spring - 210 | 2026-08-09 15:52 | 2026-08-09 15:54 | 2026-08-09 16:21 | 2026-08-09 16:48 | 2026-08-09 18:30 | 2026-08-09 18:31 | 2026-08-09 18:32 | 2026-08-09 18:32 |  |  | Fair | No | Premises can’t be located, several calls to phone when unanswered.
Outage | J.E.26.08.12722 | C001883385 | Dwayne Cohen | KSAS | Completed | Load_567648 | Duhaney - 310 | 2026-08-09 15:53 | 2026-08-09 15:54 | 2026-08-09 16:04 | 2026-08-09 16:05 | 2026-08-09 16:21 | 2026-08-09 16:42 | 2026-08-09 16:48 | 2026-08-09 16:48 |  |  | Fair | No | Refuse blown 20amps junction, supply now restore.
Non-Outage | J.E.26.08.12436 | C001883389 | Donald Cunningham |  | Completed |  |  | 2026-08-09 15:59 | 2026-08-09 17:39 | 2026-08-09 20:15 | 2026-08-09 20:16 | 2026-08-09 20:39 | 2026-08-09 20:44 | 2026-08-09 20:44 | 2026-08-09 20:44 | LowHangingWires |  | Fair | No | Premises not found contact not reachable
Outage | J.E.26.08.12784 | C001883392 | Lancelot Brown | Hanover | Completed | Load_265980 | Orange Bay - 310 | 2026-08-09 16:04 | 2026-08-09 16:06 | 2026-08-09 16:34 | 2026-08-09 16:35 | 2026-08-09 17:40 | 2026-08-09 17:59 | 2026-08-09 18:00 | 2026-08-09 18:00 |  |  | Rains | No | Found junction fuse blown patroll also found 25kva fuse blown replace 1-15amps junction fuse no pole number also replace 1-2amps fuse at 25kva no pole number supply restore
Outage | J.E.26.08.12241 | C001883395 | Stephen Taylor | St.Thomas | Completed | Load_255249 | Good Year - 110 | 2026-08-09 16:08 | 2026-08-09 16:09 | 2026-08-09 16:34 | 2026-08-09 16:35 | 2026-08-09 17:40 | 2026-08-09 17:40 | 2026-08-09 17:41 | 2026-08-09 17:41 |  |  | Fair | No | Premeses found okay Rdg 112–113–226
Outage | J.E.26.08.12711 | C001883394 | Stephen Taylor | St.Thomas | Completed | Load_577193 | Good Year - 110 | 2026-08-09 16:08 | 2026-08-09 16:09 | 2026-08-09 16:31 | 2026-08-09 16:31 | 2026-08-09 16:31 | 2026-08-09 16:31 | 2026-08-09 16:33 | 2026-08-09 16:33 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Failed to locate customer several calls and no one answering the phone
Outage | J.E.26.08.12734 | C001883393 | Stephen Taylor | St.Thomas | Completed | Load_262795 | Good Year - 110 | 2026-08-09 16:08 | 2026-08-09 16:09 | 2026-08-09 16:33 | 2026-08-09 16:33 | 2026-08-09 16:33 | 2026-08-09 16:33 | 2026-08-09 16:34 | 2026-08-09 16:34 | BrokenWire |  | Fair | No | Failed to locate customer several calls and no one answering the phone
Non-Outage | J.E.26.07.23560 | C001883401 | Raheem Ricketts | St.Elizabeth | Completed | Load_253758 | Maggotty - 210 | 2026-08-09 16:18 | 2026-08-09 16:20 | 2026-08-09 17:23 | 2026-08-09 17:23 | 2026-08-09 17:23 | 2026-08-09 17:24 | 2026-08-09 17:25 | 2026-08-09 17:25 |  |  | Fair | No | Unable to locate customer cell number not working
Non-Outage | J.E.26.05.31095 | C001883405 | Raheem Ricketts | St.Elizabeth | Completed | Load_258483 | Maggotty - 210 | 2026-08-09 16:19 | 2026-08-09 16:20 | 2026-08-09 17:13 | 2026-08-09 17:13 | 2026-08-09 17:13 | 2026-08-09 17:14 | 2026-08-09 17:14 | 2026-08-09 17:14 | LowHangingWires |  | Fair | No | Check and found okay customer says she didn’t make any report and power is at her house
Non-Outage | J.E.26.05.31922 | C001883404 | Raheem Ricketts | St.Elizabeth | Completed | Load_262476 | Maggotty - 210 | 2026-08-09 16:19 | 2026-08-09 16:20 | 2026-08-09 17:25 | 2026-08-09 17:25 | 2026-08-09 17:25 | 2026-08-09 17:25 | 2026-08-09 17:26 | 2026-08-09 17:26 |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.05.31927 | C001883403 | Raheem Ricketts | St.Elizabeth | Completed | Load_262476 | Maggotty - 210 | 2026-08-09 16:19 | 2026-08-09 16:20 | 2026-08-09 17:10 | 2026-08-09 17:11 | 2026-08-09 17:10 | 2026-08-09 17:11 | 2026-08-09 17:11 | 2026-08-09 17:11 |  |  | Fair | No | Check and found okay customer says she didn’t make any report and power is at her property
Non-Outage | J.E.26.05.32142 | C001883406 | Raheem Ricketts | St.Elizabeth | Completed | Load_266702 | Maggotty - 210 | 2026-08-09 16:19 | 2026-08-09 16:20 | 2026-08-09 17:17 | 2026-08-09 17:18 | 2026-08-09 17:17 | 2026-08-09 17:18 | 2026-08-09 17:18 | 2026-08-09 17:18 |  |  | Fair | No | Unable to communicate with customer cell number went voicemail
Non-Outage | J.E.26.06.15011 | C001883407 | Raheem Ricketts | St.Elizabeth | Completed | Load_238622 | Maggotty - 210 | 2026-08-09 16:19 | 2026-08-09 16:20 | 2026-08-09 17:27 | 2026-08-09 17:27 | 2026-08-09 17:27 | 2026-08-09 17:28 | 2026-08-09 17:28 | 2026-08-09 17:28 |  |  | Fair | No | Customer say he didn’t make any report power is at his property
Non-Outage | J.E.26.07.05380 | C001883402 | Raheem Ricketts | St.Elizabeth | Completed | Load_265503 | Maggotty - 210 | 2026-08-09 16:19 | 2026-08-09 16:20 | 2026-08-09 17:06 | 2026-08-09 17:06 | 2026-08-09 17:06 | 2026-08-09 17:06 | 2026-08-09 17:06 | 2026-08-09 17:06 |  |  | Fair | No | Check and found okay customer says problem has been solved
Outage | J.E.26.08.12572 | C001883408 | Ricky Hall | St.Catherine | Completed | Load_262759 | Twickenham - 310 | 2026-08-09 16:20 | 2026-08-09 16:21 | 2026-08-09 19:13 | 2026-08-09 19:13 | 2026-08-09 19:31 | 2026-08-09 19:32 | 2026-08-09 19:32 | 2026-08-09 19:32 |  |  | Fair | No | Premises closed
Outage | J.E.26.08.12573 | C001883410 | Delano Gayle | St.Catherine | Completed | Load_568247 | New Michelton - 210 | 2026-08-09 16:21 | 2026-08-09 16:31 | 2026-08-09 18:06 | 2026-08-09 18:06 | 2026-08-09 19:00 | 2026-08-09 19:06 | 2026-08-09 19:50 | 2026-08-09 19:50 |  |  | Fair | No | Blown junction on main no pole#, patrolled line section and found okay for closure replace 20amps
Outage | J.E.26.08.12807 | C001883411 | Neville Spencer | Clarendon | Completed | Load_557160 | May Pen - 210 | 2026-08-09 16:21 | 2026-08-09 16:23 | 2026-08-09 17:58 | 2026-08-09 17:59 | 2026-08-09 18:16 | 2026-08-09 18:16 | 2026-08-09 18:18 | 2026-08-09 18:18 |  |  | Fair | No | Found supply in area
Non-Outage | J.E.26.08.06921 | C001883413 | Fitzroy Turner | KSAN | Completed | Load_569029 | Washington Blvd - 710 | 2026-08-09 16:22 | 2026-08-09 16:46 | 2026-08-09 17:19 | 2026-08-09 17:19 | 2026-08-09 17:29 | 2026-08-09 17:29 | 2026-08-09 17:30 | 2026-08-09 17:30 |  |  | Fair | No | Customer premises found with electricity supply
Non-Outage | J.E.26.08.12804 | C001883412 | Rusean Allen |  | Completed |  |  | 2026-08-09 16:22 | 2026-08-10 07:54 | 2026-08-10 10:40 | 2026-08-10 10:40 | 2026-08-10 12:45 | 2026-08-10 13:19 | 2026-08-10 13:20 | 2026-08-10 13:20 | Fire |  | Fair | No | Corroded wires found at pothead, wires were disconnected and reconnected with one bolt clamps
Outage | J.E.26.08.12795 | C001883416 | Omar King | St.Ann | Completed | Load_237943 | Roaring River - 210 | 2026-08-09 16:25 | 2026-08-09 16:26 | 2026-08-09 17:02 | 2026-08-09 17:02 | 2026-08-09 18:52 | 2026-08-09 18:59 | 2026-08-09 18:59 | 2026-08-09 18:59 |  |  | Fair | No | Customer meter was turned off,system fault.the customer is back with supply.
Non-Outage | J.E.26.02.25600 | C001883418 | Horace Malcolm |  | Completed |  |  | 2026-08-09 16:27 | 2026-08-09 16:28 | 2026-08-09 16:39 | 2026-08-09 16:40 | 2026-08-09 17:15 | 2026-08-09 17:18 | 2026-08-09 17:18 | 2026-08-09 17:18 | Fire |  | Fair | No | Check and found no fire on wire
Non-Outage | J.E.26.02.36421 | C001883417 | Horace Malcolm | St.James | Completed | Load_241438 | Queens Drive - 710 | 2026-08-09 16:27 | 2026-08-09 16:28 | 2026-08-09 17:18 | 2026-08-09 17:18 | 2026-08-09 17:47 | 2026-08-09 17:58 | 2026-08-09 17:58 | 2026-08-09 17:58 | Fire |  | Fair | No | Check and found no sparks at pole
Non-Outage | J.E.26.08.12814 | C001883419 | Milton Charlton |  | Completed |  |  | 2026-08-09 16:27 | 2026-08-09 16:59 | 2026-08-09 17:05 | 2026-08-09 17:05 | 2026-08-09 17:35 | 2026-08-09 17:40 | 2026-08-09 17:38 | 2026-08-09 17:38 | BrokenPole |  | Fair | No | Reconnect customer meter that was disconnected. Reconnection was done by JPS escalation.
Non-Outage | J.E.26.03.01057 | C001883425 | Horace Malcolm |  | Completed |  |  | 2026-08-09 16:29 | 2026-08-09 16:32 | 2026-08-09 21:28 | 2026-08-09 21:29 | 2026-08-09 22:14 | 2026-08-09 22:17 | 2026-08-09 22:17 | 2026-08-09 22:17 | LeaningPole |  | Fair | No | Check and found one 25ft dead end pole leaning down with open span secondary line
Non-Outage | J.E.26.08.08126 | C001883424 | Horace Malcolm | St.James | Completed | Load_261029 | Rose Hall - 210 | 2026-08-09 16:29 | 2026-08-09 16:32 | 2026-08-09 19:50 | 2026-08-09 19:51 | 2026-08-09 20:12 | 2026-08-09 20:27 | 2026-08-09 20:27 | 2026-08-09 20:27 | LowHangingWires |  | Fair | No | Check found open span secondary and primary line near to customer fence wall
Non-Outage | J.E.26.08.12771 | C001883426 | Donald Cunningham |  | Completed |  |  | 2026-08-09 16:32 | 2026-08-09 16:46 | 2026-08-09 18:56 | 2026-08-09 18:56 | 2026-08-09 19:59 | 2026-08-09 20:00 | 2026-08-09 20:09 | 2026-08-09 20:09 | BrokenWire |  | Fair | No | Customer unable to add credit refer to mr Ellison
Non-Outage | J.E.26.08.12811 | C001883430 | Roxroy Needham |  | Completed |  |  | 2026-08-09 16:35 | 2026-08-09 16:36 | 2026-08-09 17:37 | 2026-08-09 17:38 | 2026-08-09 17:37 | 2026-08-09 18:06 | 2026-08-09 18:06 | 2026-08-09 18:06 | BrokenWire |  | Fair | No | Isolate 25 KVA transformer splice and retention 1 span of secondary phase use 1 splicing sleeve and reclose 25 KVA transformer
Outage | J.E.26.08.12806 | C001883431 | Lancelot Brown | Hanover | Completed | Load_302837 | Orange Bay - 310 | 2026-08-09 16:38 | 2026-08-09 16:41 | 2026-08-09 18:02 | 2026-08-09 18:03 | 2026-08-09 18:02 | 2026-08-09 18:04 | 2026-08-09 18:04 | 2026-08-09 18:04 |  |  | Rains | No | This call related to 15amps junction fuse also 3amps fuse at 25kva supply restore
Outage | J.E.26.08.12818 | C001883432 | Fitzroy Turner | KSAN | Completed | Load_252296 | Washington Blvd - 310 | 2026-08-09 16:39 | 2026-08-09 16:41 | 2026-08-09 17:30 | 2026-08-09 17:49 | 2026-08-09 17:49 | 2026-08-09 18:02 | 2026-08-09 18:03 | 2026-08-09 18:03 | BrokenWire |  | Fair | No | Found 50kva transformer fuse blown replace one 5 amp fuse supply restored to the areas
Non-Outage | J.E.26.08.12824 | C001883439 | Delano Gayle |  | Completed |  |  | 2026-08-09 16:57 | 2026-08-09 17:00 | 2026-08-09 19:50 | 2026-08-09 19:51 | 2026-08-09 20:37 | 2026-08-09 21:54 | 2026-08-09 21:55 | 2026-08-09 21:55 | BrokenWire |  | Fair | No | Blown junction on main no pole#, tree fell on line, heavy heavy heavy spot bushing to remove tree, replace 25amps fuse at junction
Outage | J.E.26.08.12841 | C001883443 | Neville Spencer | Clarendon | Completed | Load_260709 | May Pen - 210 | 2026-08-09 17:00 | 2026-08-09 17:01 | 2026-08-09 18:19 | 2026-08-09 18:19 | 2026-08-09 18:52 | 2026-08-09 18:52 | 2026-08-09 18:53 | 2026-08-09 18:53 |  |  | Fair | No | Found supply in area .
Non-Outage | J.E.26.07.36906 | C001883447 | Omar King | St.Ann | Completed | Load_266296 | Ocho Rios - 310 | 2026-08-09 17:06 | 2026-08-09 17:08 | 2026-08-09 20:10 | 2026-08-09 20:16 | 2026-08-09 21:28 | 2026-08-09 21:29 | 2026-08-09 21:29 | 2026-08-09 21:29 |  |  | Fair | No | Unable to find customer call several times no answer directions not sufficient
Non-Outage | J.E.26.07.37673 | C001883446 | Omar King | St.Ann | Completed | Load_240435 | Cardiff Hall - 210 | 2026-08-09 17:06 | 2026-08-09 17:09 | 2026-08-09 19:11 | 2026-08-09 19:11 | 2026-08-09 19:19 | 2026-08-09 19:23 | 2026-08-09 19:23 | 2026-08-09 19:23 |  |  | Fair | No | Unable to find customer
Non-Outage | J.E.26.08.03032 | C001883448 | Omar King | St.Ann | Completed | Load_265652 | Roaring River - 410 | 2026-08-09 17:06 | 2026-08-09 17:09 | 2026-08-09 19:03 | 2026-08-09 19:03 | 2026-08-09 19:07 | 2026-08-09 19:10 | 2026-08-09 19:10 | 2026-08-09 19:10 |  |  | Fair | No | Customer is with supply
Outage | J.E.26.08.12829 | C001883450 | Oshane Warren | Westmoreland | Completed | Load_295444 | Paradise - 310 | 2026-08-09 17:10 | 2026-08-09 17:11 | 2026-08-09 17:42 | 2026-08-09 17:43 | 2026-08-09 18:38 | 2026-08-09 18:39 | 2026-08-09 18:39 | 2026-08-09 18:39 |  |  | Rains | No | Replace 2 amp 25 kva transformer fuse
Outage | J.E.26.08.11961 | C001883451 | Ricky Hall | St.Catherine | Completed | Load_260095 | Twickenham - 310 | 2026-08-09 17:21 | 2026-08-09 17:22 | 2026-08-09 19:32 | 2026-08-09 19:33 | 2026-08-09 19:43 | 2026-08-09 19:43 | 2026-08-09 19:43 | 2026-08-09 19:43 | LeaningPole,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Premises not located
Outage | J.E.26.08.05913 | C001883453 | Horace Malcolm | St.James | Completed | Load_258936 | Queens Drive - 710 | 2026-08-09 17:44 | 2026-08-09 17:45 | 2026-08-09 18:04 | 2026-08-09 18:05 | 2026-08-09 18:25 | 2026-08-09 18:51 | 2026-08-09 18:51 | 2026-08-09 18:51 | BrokenWire |  | Fair | No | Unable to locate premises the direction wen call to customer give unable to reach out back to customer
Non-Outage | J.E.26.08.03829 | C001883455 | Dwayne Cohen |  | Completed |  |  | 2026-08-09 18:09 | 2026-08-09 18:12 | 2026-08-09 18:32 | 2026-08-09 18:33 | 2026-08-09 19:13 | 2026-08-09 19:14 | 2026-08-09 19:14 | 2026-08-09 19:14 | LeaningPole |  | Fair | No | Premises found okay
Outage | J.E.26.08.12837 | C001883456 | Omar King | St.Ann | Completed | Load_574451 | Roaring River - 210 | 2026-08-09 18:13 | 2026-08-09 18:13 | 2026-08-09 19:00 | 2026-08-09 19:00 | 2026-08-09 19:00 | 2026-08-09 19:02 | 2026-08-09 19:02 | 2026-08-09 19:02 |  |  | Fair | No | Customer meter was turned off,system fault.the customer is back with supply.
Outage | J.E.26.08.12885 | C001883459 | Raheem Ricketts | St.Elizabeth | Completed | Load_239122 | Maggotty - 210 | 2026-08-09 18:20 | 2026-08-09 18:21 | 2026-08-09 18:32 | 2026-08-09 18:42 | 2026-08-09 19:35 | 2026-08-09 22:35 | 2026-08-09 22:35 | 2026-08-09 22:35 | BrokenWire |  | Fair | No | Check and found two pole span of secondary both neutral an bottom phase broken splice and retention both 2pole span of neutral an bottom phase cut on remove tree from line and reclosed 25,kva
Outage | J.E.26.08.12836 | C001883461 | Raymond Carr | St.Mary | Completed | Load_250719 | Annotto Bay - 210 | 2026-08-09 18:24 | 2026-08-09 18:25 | 2026-08-09 19:30 | 2026-08-09 19:30 | 2026-08-09 19:47 | 2026-08-09 07:30 | 2026-08-09 19:48 | 2026-08-09 19:48 |  |  | Fair | No | Customer reported supply okay.
Non-Outage | J.E.26.08.12857 | C001883462 | Oshane Warren |  | Completed |  |  | 2026-08-09 18:25 | 2026-08-09 18:26 | 2026-08-09 18:42 | 2026-08-09 18:42 | 2026-08-09 20:26 | 2026-08-09 20:26 | 2026-08-09 22:05 | 2026-08-09 22:05 |  |  | Rains | No | Replace 3 amp 25 kva transformer fuse
Outage | J.E.26.08.12895 | C001883464 | Richard Nicholas | St.Catherine | Completed | Load_251630 | Rhodens Pen - 410 | 2026-08-09 18:35 | 2026-08-09 18:36 | 2026-08-09 18:57 | 2026-08-09 18:57 | 2026-08-09 19:59 | 2026-08-09 20:37 | 2026-08-09 20:42 | 2026-08-09 20:42 |  |  | Fair | No | Splice and retention 1 span of broken secondary phase,1 splicing sleeve,5ft 2/0aac and 1 clamp was used.please refer to the maintenance department to have leaning secondary pole dig and straighten.because of the leaning pole some customer stanchion and pothead broken and service wire become stiff and low hanging across the main road.
Non-Outage | J.E.26.03.32889 | C001883465 | Horace Malcolm |  | Completed |  |  | 2026-08-09 18:39 | 2026-08-09 18:47 | 2026-08-09 20:28 | 2026-08-09 20:28 | 2026-08-09 21:02 | 2026-08-09 21:03 | 2026-08-09 21:03 | 2026-08-09 21:03 | LeaningPole |  | Fair | No | Customer says no report was made an no leaning pole
Non-Outage | J.E.26.07.32371 | C001883466 | Horace Malcolm |  | Completed |  |  | 2026-08-09 18:44 | 2026-08-09 18:47 | 2026-08-09 21:03 | 2026-08-09 21:04 | 2026-08-09 21:27 | 2026-08-09 21:28 | 2026-08-09 21:28 | 2026-08-09 21:28 | Fire |  | Fair | No | Customer reports about street light not working
Non-Outage | J.E.26.07.11937 | C001883467 | Horace Malcolm | St.James | Completed | Load_243259 | Queens Drive - 710 | 2026-08-09 18:46 | 2026-08-09 18:47 | 2026-08-09 22:17 | 2026-08-09 22:18 | 2026-08-09 22:39 | 2026-08-09 22:51 | 2026-08-09 22:52 | 2026-08-09 22:52 | LeaningPole |  | Fair | No | Unable to locate no directions given
Outage | J.E.26.08.12919 | C001883473 | Lancelot Brown | Hanover | Completed | Load_573350 | Orange Bay - 310 | 2026-08-09 19:05 | 2026-08-09 19:12 | 2026-08-09 20:23 | 2026-08-09 20:24 | 2026-08-09 20:24 | 2026-08-09 20:37 | 2026-08-09 20:38 | 2026-08-09 20:38 |  |  | Fair | No | Found bank of 3-25kva 2-25kva fuse blown carry out checks found 1-25kva leaking oil lots of oil spilt on the ground please pass on to maintenance department in Hanover mr Richards need ergent attention
Outage | J.E.26.08.12930 | C001883474 | Rusean Allen | KSAS | Completed | Load_261030 | Rockfort - 410 | 2026-08-09 19:12 | 2026-08-09 19:16 | 2026-08-09 20:52 | 2026-08-09 20:53 | 2026-08-09 20:52 | 2026-08-09 22:19 | 2026-08-09 22:19 | 2026-08-09 22:19 |  |  | Fair | No | Reconnected switch bottom at pole
Outage | J.E.26.08.12923 | C001883476 | Neville Spencer | Clarendon | Completed | Load_269299 | Parnassus - 210 | 2026-08-09 19:16 | 2026-08-09 19:19 | 2026-08-09 19:32 | 2026-08-09 19:32 | 2026-08-09 20:23 | 2026-08-09 21:02 | 2026-08-09 21:05 | 2026-08-09 21:05 |  |  | Fair | No | Cleared bird from xmfr pole renew blown 3 amp fuse protecting 25 kva xmfr at pole # 0112850 supply restored.
Non-Outage | J.E.26.08.12906 | C001883478 | Richard Nicholas | St.Catherine | Completed | Load_568174 | Rhodens Pen - 410 | 2026-08-09 19:24 | 2026-08-09 19:34 | 2026-08-09 21:31 | 2026-08-09 21:32 | 2026-08-09 22:18 | 2026-08-09 22:45 | 2026-08-09 22:47 | 2026-08-09 22:47 | BrokenPole |  | Fair | No | No broken JPS.co pole seen however a broken private pole seen on private property therefore customer was advised during a telephone conversation.
Outage | J.E.26.08.12942 | C001883479 | Roxroy Needham | St.Ann | Completed | Load_244118 | Cardiff Hall - 310 | 2026-08-09 19:35 | 2026-08-09 19:36 | 2026-08-09 21:09 | 2026-08-09 21:09 | 2026-08-09 21:32 | 2026-08-09 21:33 | 2026-08-09 21:34 | 2026-08-09 21:34 | BrokenWire |  | Fair | No | Clean and remake joint at pole use 1- 1bolt clamp
Outage | J.E.26.08.12960 | C001883482 | Donald Cunningham | St.Catherine | Completed | Load_254666 | Twickenham - 210 | 2026-08-09 20:05 | 2026-08-09 20:07 | 2026-08-09 20:47 | 2026-08-09 20:48 | 2026-08-09 21:59 | 2026-08-09 22:00 | 2026-08-09 22:11 | 2026-08-09 22:11 | BrokenWire |  | Fair | No | Broken down stanchion need to be repair customer advised cause by vehicle accident
Outage | J.E.26.08.12957 | C001883483 | Dwayne Cohen | KSAS | Completed | Load_268591 | Duhaney - 310 | 2026-08-09 20:14 | 2026-08-09 20:15 | 2026-08-09 20:30 | 2026-08-09 20:30 | 2026-08-09 20:52 | 2026-08-09 21:19 | 2026-08-09 21:22 | 2026-08-09 21:22 | Fire |  | Fair | No | Refuse blown 3amps transformer link , supply now restore.
Outage | J.E.26.08.12956 | C001883484 | Romeo Brissett | St.James | Completed | Load_256725 | Bogue - 610 | 2026-08-09 20:15 | 2026-08-09 21:29 | 2026-08-09 21:52 |  | 2026-08-09 21:52 | 2026-08-09 21:48 | 2026-08-09 21:57 | 2026-08-09 21:57 |  |  | Fair | No | Replaced (1)25 kva transformer fuse
Non-Outage | J.E.26.08.12500 | C001883487 | Gregory Grossett | Portland | Completed | Load_354844 | Port Antonio - 410 | 2026-08-09 20:28 | 2026-08-09 20:29 | 2026-08-09 21:38 | 2026-08-09 21:38 | 2026-08-09 22:15 | 2026-08-09 22:16 | 2026-08-09 22:18 | 2026-08-09 22:18 |  |  | Fair | No | Need daylight attention to properly check service lines as multiple service wires are at the location
Outage | J.E.26.08.12954 | C001883488 | Roxroy Needham | St.Ann | Completed | Load_238052 | Cardiff Hall - 310 | 2026-08-09 20:30 | 2026-08-09 20:31 | 2026-08-09 21:34 | 2026-08-09 21:35 | 2026-08-09 22:22 | 2026-08-09 22:25 | 2026-08-09 22:25 | 2026-08-09 22:25 |  |  | Fair | No | Remove vine from pole and replace 1- 8 amp junction fuse
Outage | J.E.26.08.12946 | C001883490 | Richard Nicholas | St.Catherine | Completed | Load_237792 | Rhodens Pen - 410 | 2026-08-09 20:31 | 2026-08-09 20:32 | 2026-08-09 20:43 | 2026-08-09 20:43 | 2026-08-09 20:59 | 2026-08-09 21:30 | 2026-08-09 21:31 | 2026-08-09 21:31 |  |  | Fair | No | Replaced blown 50kva transformer 5amp fuse on pole #0116505.
Non-Outage | J.E.26.07.12651 | C001883493 | Vivian Gordon |  | Completed |  |  | 2026-08-09 20:37 | 2026-08-09 20:38 | 2026-08-10 09:04 | 2026-08-10 09:05 | 2026-08-10 09:04 | 2026-08-07 16:07 | 2026-08-10 09:06 | 2026-08-10 09:06 |  |  | Fair | No | Single phase corrected
Outage | J.E.26.08.12994 | C001883503 | Delano Gayle | St.Catherine | Completed | Load_246128 | Twickenham - 310 | 2026-08-09 21:27 | 2026-08-09 21:30 | 2026-08-09 21:55 | 2026-08-09 21:56 | 2026-08-09 22:13 | 2026-08-09 22:14 | 2026-08-09 22:14 | 2026-08-09 22:14 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Premises found okay related to call where 25amps junction fuse was replaced
Outage | J.E.26.08.13019 | C001883504 | Rodclif Dawkins | St.Catherine | Completed | Load_265213 | Tredegar - 510 | 2026-08-09 21:28 | 2026-08-10 07:30 | 2026-08-10 13:12 | 2026-08-10 13:13 | 2026-08-10 13:23 | 2026-08-10 14:34 | 2026-08-10 14:49 | 2026-08-10 14:49 |  |  | Fair | No | At location crew along with customer care was able to connect customer.
Outage | J.E.26.08.13008 | C001883505 | Lancelot Brown | Hanover | Completed | Load_263889 | Orange Bay - 210 | 2026-08-09 21:31 | 2026-08-09 21:32 | 2026-08-10 09:53 | 2026-08-10 09:55 | 2026-08-10 10:38 | 2026-08-10 11:21 | 2026-08-10 11:21 | 2026-08-10 11:21 |  |  | Fair | No | Carry out checks found customer meter socket diffective advise customer to carry out vl at meter socket 110 -109-219
Outage | J.E.26.08.13012 | C001883506 | Roxroy Needham | St.Ann | Completed | Load_250482 | Cardiff Hall - 310 | 2026-08-09 21:35 | 2026-08-09 21:36 | 2026-08-10 00:05 | 2026-08-10 00:06 | 2026-08-10 00:33 | 2026-08-10 00:26 | 2026-08-10 00:34 | 2026-08-10 00:34 |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.08.13021 | C001883507 | Roxroy Needham | St.Ann | Completed | Load_263745 | Cardiff Hall - 310 | 2026-08-09 21:36 | 2026-08-09 21:37 | 2026-08-09 22:50 | 2026-08-09 22:51 | 2026-08-09 23:33 | 2026-08-10 00:03 | 2026-08-10 00:05 | 2026-08-10 00:05 |  |  | Fair | No | Open a 25 KVA transformer at pole to repair transformer leed used 2 pg clamp
Non-Outage | J.E.26.08.12771 | C001883508 | Moses Elliston |  | Completed |  |  | 2026-08-09 21:37 | 2026-08-09 21:38 | 2026-08-10 14:36 | 2026-08-10 14:37 | 2026-08-10 14:36 | 2026-08-10 13:15 | 2026-08-10 14:38 | 2026-08-10 14:38 |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.08.13013 | C001883510 | Neville Spencer | Clarendon | Completed | Load_254560 | Parnassus - 310 | 2026-08-09 21:39 | 2026-08-09 21:40 | 2026-08-09 21:45 | 2026-08-09 21:45 | 2026-08-09 22:07 | 2026-08-09 22:07 | 2026-08-09 22:45 | 2026-08-09 22:45 | Fire |  | Fair | No | Remade burnt out clamp on 3 , service at pothead feeding 4 , customers used 1, clamp voltage reading 114 117 231 supply restored.
Outage | J.E.26.08.13054 | C001883517 | Dwayne Samuels | Trelawny | Completed | Load_292930 | Duncans - 210 | 2026-08-09 22:22 | 2026-08-10 08:03 | 2026-08-10 13:34 | 2026-08-10 15:12 | 2026-08-10 15:12 | 2026-08-10 15:03 | 2026-08-10 15:14 | 2026-08-10 15:14 | BrokenWire |  | Fair | No | Call is related to broken system neural and disconnected service wire that was repaired earlier today
Outage | J.E.26.08.13066 | C001883521 | Nickolas Rodriques | St.Catherine | Completed | Load_246200 | New Michelton - 310 | 2026-08-09 22:58 | 2026-08-09 22:59 | 2026-08-10 00:56 | 2026-08-10 01:41 | 2026-08-10 02:53 | 2026-08-10 04:00 | 2026-08-10 04:02 | 2026-08-10 04:02 |  |  | Fair | No | Checked and found a 30 amp junction fuse blown. Patrol and found nothing on line. Repaired by replacing the fuse after completing patrol.
Outage | J.E.26.08.13067 | C001883522 | Nickolas Rodriques | St.Catherine | Completed | Load_251641 | New Michelton - 310 | 2026-08-09 22:58 | 2026-08-09 22:59 | 2026-08-10 04:02 | 2026-08-10 04:35 | 2026-08-10 07:01 | 2026-08-10 06:38 | 2026-08-10 07:04 | 2026-08-10 07:04 |  |  | Fair | No | Power restored. Call relates to the 30 amp junction fuse that was replaced.
Non-Outage | J.E.26.08.13106 | C001883582 | Denton Williams |  | Completed |  |  | 2026-08-10 07:11 | 2026-08-10 07:15 | 2026-08-10 09:43 | 2026-08-10 09:44 | 2026-08-10 09:43 | 2026-08-10 09:44 | 2026-08-10 09:44 | 2026-08-10 09:44 | BrokenWire |  | Fair | No | 25kva transformer trip cause by tree fall on secondary conductors and burst down neutral wire splice and retention conductor then restored supply to the area.Material use 2 one bolt clamps 5ft of number 2 aluminum conductor.
Outage | J.E.26.08.13089 | C001883581 | Denton Williams | Portland | Completed | Load_349280 | Port Antonio - 410 | 2026-08-10 07:11 | 2026-08-10 07:15 | 2026-08-10 09:48 | 2026-08-10 09:48 | 2026-08-10 10:11 | 2026-08-10 10:23 | 2026-08-10 10:28 | 2026-08-10 10:28 |  | Y | Fair | No | Patrol line and replace one 10 amp junction fuse. All customers restored, line need bushing, refer to Portland maintenance.
Outage | J.E.26.08.13117 | C001883583 | Denton Williams | Portland | Completed | Load_255277 | Port Antonio - 410 | 2026-08-10 07:11 | 2026-08-10 07:15 | 2026-08-10 08:07 | 2026-08-10 08:08 | 2026-08-10 08:59 | 2026-08-10 09:43 | 2026-08-10 09:43 | 2026-08-10 09:43 |  | Y | Fair | No | 25kva transformer trip cause by tree fall on secondary conductors and burst down neutral wire splice and retention conductor then restored supply to the area.Material use 2 one bolt clamps 5ft of number 2 aluminum conductor.
Outage | J.E.26.08.12853 | C001883593 | Wayne Dillion | Manchester | Completed | Load_1002301 | Kendal - 210 | 2026-08-10 07:23 | 2026-08-10 07:39 | 2026-08-10 08:57 | 2026-08-10 08:58 | 2026-08-10 08:57 | 2026-08-10 08:59 | 2026-08-10 08:59 | 2026-08-10 08:59 |  |  | Fair | No | Customer said supply ok
Outage | J.E.26.08.13126 | C001883588 | Cliton Henry | St.Mary | Completed | Load_242891 | Oracabessa - 210 | 2026-08-10 07:23 | 2026-08-10 07:26 | 2026-08-10 08:42 | 2026-08-10 08:43 | 2026-08-10 09:17 | 2026-08-10 09:32 | 2026-08-10 09:35 | 2026-08-10 09:35 |  |  | Fair | No | A blown 10 amp junction fuse found at Hunter’s Piece rd. at pole # 0013654 due to vines made contact with the primary phase conductor. The vine was removed and supply restored 1-10 amp fuse.
Outage | J.E.26.08.13152 | C001883590 | Cliton Henry | St.Mary | Completed | Load_263482 | Oracabessa - 210 | 2026-08-10 07:23 | 2026-08-10 07:26 | 2026-08-10 09:36 | 2026-08-10 09:37 | 2026-08-10 09:55 | 2026-08-10 10:00 | 2026-08-10 10:03 | 2026-08-10 10:03 |  |  | Rains | No | The voltages found at the customer pothead were 116-120/236. The neutral at the pothead on the customer side found disconnected and the meter fallen off the pole. The customer was advised to carryout repairs.
Outage | J.E.26.08.13157 | C001883592 | Ryan Richards | Manchester | Completed | Load_246637 | Kendal - 210 | 2026-08-10 07:23 | 2026-08-10 07:25 | 2026-08-10 08:26 | 2026-08-10 08:26 | 2026-08-10 09:16 | 2026-08-10 10:16 | 2026-08-10 10:17 | 2026-08-10 10:17 |  |  | Fair | No | Blown 30 amp junction fuse found line patrol nothing found blown fuse was replaced all customers are now with supply
Outage | J.E.26.08.13171 | C001883589 | Cliton Henry | St.Mary | Completed | Load_249215 | Blackstonedge - 110 | 2026-08-10 07:23 | 2026-08-10 07:26 | 2026-08-10 10:36 | 2026-08-10 10:37 | 2026-08-10 10:37 | 2026-08-10 10:38 | 2026-08-10 10:38 | 2026-08-10 10:38 |  |  | Fair | No | The customer stated that he discover that the problem is internal.
Outage | J.E.26.08.13172 | C001883596 | Hartley Chin | Clarendon | Completed | Load_258981 | Parnassus - 210 | 2026-08-10 07:23 | 2026-08-10 07:25 | 2026-08-10 08:18 | 2026-08-10 08:18 | 2026-08-10 11:07 | 2026-08-10 11:53 | 2026-08-10 11:56 | 2026-08-10 11:56 |  |  | Fair | No | Found a burnt 5 amp fuse holder @ 055981 reason unknown, replace fuse and fuse hold. No network to call in.
Non-Outage | J.E.26.08.10006 | C001883604 | Odaine Johnson | Clarendon | Completed | Load_257855 | Monymusk - 210 | 2026-08-10 07:24 | 2026-08-10 09:00 | 2026-08-10 09:59 | 2026-08-10 10:00 | 2026-08-10 10:11 | 2026-08-10 10:13 | 2026-08-10 10:14 | 2026-08-10 10:14 |  |  | Fair | No | Customer experiencing single phase coming from rami box, box # 06926
Non-Outage | J.E.26.08.13193 | C001883599 | Hartley Chin | Clarendon | Completed | Load_260924 | May Pen - 210 | 2026-08-10 07:24 | 2026-08-10 07:26 | 2026-08-10 16:23 | 2026-08-10 16:24 | 2026-08-10 16:58 | 2026-08-10 16:59 | 2026-08-10 17:09 | 2026-08-10 17:09 |  |  | Fair | No | Found corroded one bolt clamp on service wire , replaced clamp.Voltage reading (v113)
Outage | J.E.26.08.12809 | C001883600 | Selvin White | St.Elizabeth | Completed | Load_238193 | Maggotty - 210 | 2026-08-10 07:24 | 2026-08-10 07:27 | 2026-08-10 07:57 | 2026-08-10 07:58 | 2026-08-10 09:40 | 2026-08-10 10:05 | 2026-08-10 10:16 | 2026-08-10 10:16 |  |  | Fair | No | Replace a blown 20 amp junction fuse at pole number 604741 after patrolling 3 phase primary line that also supply the NIC pump and Agro Grace.
Outage | J.E.26.08.12833 | C001883601 | Selvin White | St.Elizabeth | Completed | Load_1002241 | Maggotty - 210 | 2026-08-10 07:24 | 2026-08-10 07:26 | 2026-08-10 07:45 | 2026-08-10 10:17 | 2026-08-10 10:59 | 2026-08-10 11:40 | 2026-08-10 11:40 | 2026-08-10 11:40 |  |  | SevereWind | No | Replace approximately 90 ft of number six triplex service wire for for Church of Godto which customer is in charge of. Meter number 3009074; two wire service. Wire was found burnt . Supply restored with voltage readings of 109 volts.
Outage | J.E.26.08.13048 | C001883603 | Wayne Dillion | St.Elizabeth | Completed | Load_269016 | Maggotty - 110 | 2026-08-10 07:24 | 2026-08-10 12:36 | 2026-08-10 13:38 | 2026-08-10 13:38 | 2026-08-10 14:31 | 2026-08-10 14:52 | 2026-08-10 14:53 | 2026-08-10 14:53 |  |  | Rains | No | Patrol and found tree laying on secondary conductors. Remove same and replace one blown 2amp fuse that protects 25kva transformer circuit no pole#. Supply restored okay.
Outage | J.E.26.08.13154 | C001883602 | Wayne Dillion | St.Elizabeth | Completed | Load_256628 | Maggotty - 210 | 2026-08-10 07:24 | 2026-08-10 07:40 | 2026-08-10 13:08 | 2026-08-10 13:09 | 2026-08-10 13:08 | 2026-08-10 13:11 | 2026-08-10 13:12 | 2026-08-10 13:12 | Fire |  | Fair | No | Unable to locate and customer not answering the phone.
Non-Outage | J.E.26.08.11155 | C001883606 | Neville Spencer | Clarendon | Completed | Load_568439 | May Pen - 110 | 2026-08-10 07:26 | 2026-08-11 07:24 | 2026-08-11 09:09 | 2026-08-11 09:15 | 2026-08-11 11:13 | 2026-08-11 11:13 | 2026-08-11 11:16 | 2026-08-11 11:16 |  |  | Fair | No | Call resolved yesterday.
Non-Outage | J.E.26.08.12591 | C001883611 | Cliton Henry | St.Ann | Completed | Load_261553 | Upper White River - 110 | 2026-08-10 07:28 | 2026-08-10 07:31 | 2026-08-10 10:04 | 2026-08-10 10:05 | 2026-08-10 10:23 | 2026-08-10 10:24 | 2026-08-10 10:24 | 2026-08-10 10:24 | Fire |  | Fair | No | Line patrol revealed no fire seen on line
Non-Outage | J.E.26.08.13169 | C001883610 | Cliton Henry | St.Mary | Completed | Load_245479 | Blackstonedge - 110 | 2026-08-10 07:28 | 2026-08-10 07:31 | 2026-08-10 10:42 | 2026-08-10 10:43 | 2026-08-10 10:43 | 2026-08-10 10:45 | 2026-08-10 10:47 | 2026-08-10 10:47 | BrokenPole |  | Fair | No | .A broken 30-c6 over head guy pole found, kindly refer to St.Mary Operations for replacement.
Outage | J.E.26.08.13077 | C001883612 | Moses Elliston | St.Catherine | Completed | Load_267575 | Tredegar - 510 | 2026-08-10 07:29 | 2026-08-10 07:36 | 2026-08-11 14:31 | 2026-08-11 14:32 | 2026-08-11 14:32 | 2026-08-11 14:32 | 2026-08-11 14:33 | 2026-08-11 14:33 |  |  | Fair | No | Credit added to prepaid account
Outage | J.E.26.08.13202 | C001883618 | Wayne Dillion | St.Elizabeth | Completed | Load_261202 | Maggotty - 210 | 2026-08-10 07:43 | 2026-08-10 07:44 | 2026-08-10 10:13 | 2026-08-10 10:13 | 2026-08-10 11:17 | 2026-08-10 11:48 | 2026-08-10 11:55 | 2026-08-10 11:55 |  |  | Rains | No | Supply check and found single phasing at pole. Affix same using 1 clamp. Supply leave working okay reading 111v, 112v and cross phase 223volts.
Non-Outage | J.E.26.08.11311 | C001883621 | Stephen Taylor | St.Thomas | Completed | Load_239634 | Lysson - 410 | 2026-08-10 07:44 | 2026-08-10 07:50 | 2026-08-10 11:42 | 2026-08-10 11:42 | 2026-08-10 12:34 | 2026-08-10 12:34 | 2026-08-10 13:10 | 2026-08-10 13:10 | Fire |  | SevereWind | No | Clean up single phase on transformer drop lead use 3 clamps reading 112,113,225 all customer is now okay
Non-Outage | J.E.26.08.12462 | C001883620 | Stephen Taylor | St.Thomas | Completed | Load_239634 | Lysson - 410 | 2026-08-10 07:44 | 2026-08-10 07:50 | 2026-08-10 13:11 | 2026-08-10 13:12 | 2026-08-10 13:11 | 2026-08-10 13:11 | 2026-08-10 13:17 | 2026-08-10 13:17 | Fire |  | SevereWind | No | Splice and retention secondary wires and close up back 25 kva transformer safety with a 3 amp fuse
Non-Outage | J.E.26.08.12867 | C001883619 | Derrick Grubb | St.Thomas | Completed | Load_239668 | Good Year - 110 | 2026-08-10 07:44 | 2026-08-10 14:48 | 2026-08-10 21:49 | 2026-08-10 21:55 | 2026-08-10 21:54 | 2026-08-10 22:16 | 2026-08-10 22:16 | 2026-08-10 22:16 | Fire |  | Fair | No | Secondary circuit needs bushing refer to maintenance,
Outage | J.E.26.08.13049 | C001883626 | Derrick Grubb | St.Thomas | Completed | Load_353202 | Good Year - 210 | 2026-08-10 07:50 | 2026-08-10 14:48 | 2026-08-10 19:48 | 2026-08-10 20:32 | 2026-08-10 20:32 | 2026-08-10 20:32 | 2026-08-10 20:33 | 2026-08-10 20:33 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.13076 | C001883625 | Stephen Taylor | St.Thomas | Completed | Load_265904 | Lysson - 410 | 2026-08-10 07:50 | 2026-08-10 07:51 | 2026-08-10 11:12 | 2026-08-10 11:12 | 2026-08-10 11:37 | 2026-08-10 11:37 | 2026-08-10 11:38 | 2026-08-10 11:38 |  |  | Fair | No | Clean up single phase reading 111,112,224 customer is now okay
Outage | J.E.26.08.13090 | C001883624 | Stephen Taylor | St.Thomas | Completed | Load_243122 | Lysson - 410 | 2026-08-10 07:50 | 2026-08-10 07:51 | 2026-08-10 09:05 | 2026-08-10 10:02 | 2026-08-10 10:34 | 2026-08-10 10:34 | 2026-08-10 11:01 | 2026-08-10 11:01 |  |  | Fair | No | See junction link down patrol and see two primary pole broken need assistance for the jps maintenance team to restore power to the community isolated at pole # 0004854 the road is still block
Outage | J.E.26.08.13055 | C001883627 | Edward Royal | KSAS | Completed | Load_244500 | Greenwich - 410 | 2026-08-10 07:52 | 2026-08-10 07:53 | 2026-08-10 14:17 | 2026-08-10 14:18 | 2026-08-10 14:18 | 2026-08-10 14:18 | 2026-08-10 14:18 | 2026-08-10 14:18 |  |  | Fair | No | Premises found close
Non-Outage | J.E.26.08.12433 | C001883629 | Royston Montague |  | Completed |  |  | 2026-08-10 07:56 | 2026-08-10 08:01 | 2026-08-10 08:27 | 2026-08-10 13:41 | 2026-08-10 13:41 | 2026-08-10 13:42 | 2026-08-10 13:42 | 2026-08-10 13:42 | Fire |  | Fair | No | Not locating this premises, multiple calls to customer phone go without answer.
Non-Outage | J.E.26.08.13212 | C001883628 | Wan Carlos Scarlett |  | Completed |  |  | 2026-08-10 07:56 | 2026-08-10 07:57 | 2026-08-10 08:48 | 2026-08-10 08:49 | 2026-08-10 09:10 | 2026-08-10 10:47 | 2026-08-10 10:52 | 2026-08-10 10:52 | Fire |  | Fair | No | Found fire on transmission pole transmission team is on site 3 pole broken crew is arranging how tow resolved issue
Non-Outage | J.E.26.08.12498 | C001883631 | Kemark Slue | St.Catherine | Completed | Load_263428 | New Michelton - 210 | 2026-08-10 07:57 | 2026-08-10 07:59 | 2026-08-10 08:25 | 2026-08-10 08:26 | 2026-08-10 10:36 | 2026-08-10 09:00 | 2026-08-10 11:45 | 2026-08-10 11:45 |  |  | Rains | No | Upon arrival at the location the crew discovered that 25 kva 13.8 kv transformer lighting transformer from bank of two was blown resulting from a surge, refuse link and re-energized bank.
Non-Outage | J.E.26.08.12768 | C001883632 | Richard Nicholas | St.Catherine | Completed | Load_254999 | Rhodens Pen - 410 | 2026-08-10 07:57 | 2026-08-10 07:59 | 2026-08-10 10:47 | 2026-08-10 10:49 | 2026-08-10 12:37 | 2026-08-10 12:53 | 2026-08-10 12:54 | 2026-08-10 12:54 |  |  | Fair | No | Supply checked at meter,same found ok.voltage reading 116x2 and 232v.
Non-Outage | J.E.26.08.09404 | C001883641 | Orville Lee | Portmore | Completed | Load_264712 | Naggo Head - 510 | 2026-08-10 07:58 | 2026-08-10 08:01 | 2026-08-10 10:21 | 2026-08-11 15:22 | 2026-08-11 15:51 | 2026-08-11 16:15 | 2026-08-11 16:17 | 2026-08-11 16:17 |  |  | Fair | No | Customer was reporting spark at pole Upon arrival no spark or burning sign seen
Non-Outage | J.E.26.08.11428 | C001883639 | Orville Lee | Portmore | Completed | Load_268319 | Naggo Head - 610 | 2026-08-10 07:58 | 2026-08-10 08:01 | 2026-08-10 10:21 | 2026-08-11 09:10 | 2026-08-11 09:25 | 2026-08-11 09:51 | 2026-08-11 09:56 | 2026-08-11 09:56 |  |  | Fair | No | Checks made and found pot head connections corroded Voltage119v120v240v
Non-Outage | J.E.26.08.11933 | C001883637 | Orville Lee | St.Catherine | Completed | Load_247916 | Twickenham - 210 | 2026-08-10 07:58 | 2026-08-10 08:01 | 2026-08-10 10:21 | 2026-08-10 13:44 | 2026-08-10 13:57 | 2026-08-10 15:02 | 2026-08-10 15:04 | 2026-08-10 15:04 |  |  | Fair | No | Checks made and found service wire defective 80ft wire three pen union and three one bolt clampsVoltage118v118v237v
Non-Outage | J.E.26.08.12014 | C001883638 | Orville Lee | Portmore | Completed | Load_576099 | Naggo Head - 510 | 2026-08-10 07:58 | 2026-08-10 08:01 | 2026-08-10 10:21 | 2026-08-11 11:30 | 2026-08-11 11:44 | 2026-08-11 12:09 | 2026-08-11 12:12 | 2026-08-11 12:12 |  |  | Fair | No | Customer meter socket defective Premises found ok upon Arrival Voltage118v118v237v
Non-Outage | J.E.26.08.12082 | C001883636 | Orville Lee | Portmore | Completed | Load_245935 | Naggo Head - 610 | 2026-08-10 07:58 | 2026-08-10 08:01 | 2026-08-10 08:27 | 2026-08-10 08:28 | 2026-08-10 09:18 | 2026-08-10 09:43 | 2026-08-10 09:47 | 2026-08-10 09:47 |  |  | Fair | No | Checks made and found pothead corroded Six pen union usedVoltage 120v120v240v
Non-Outage | J.E.26.08.12864 | C001883635 | Orville Lee | St.Catherine | Completed | Load_256398 | Twickenham - 210 | 2026-08-10 07:58 | 2026-08-10 08:01 | 2026-08-10 10:21 | 2026-08-10 12:17 | 2026-08-10 12:28 | 2026-08-10 13:37 | 2026-08-10 13:39 | 2026-08-10 13:39 |  |  | Fair | No | Checks made and found neutral disconnected Voltage 115v115v230v
Non-Outage | J.E.26.08.05584 | C001883647 | Odeanie Davis | KSAS | Completed | Load_239845 | Rockfort - 410 | 2026-08-10 07:59 | 2026-08-10 08:00 | 2026-08-10 12:09 | 2026-08-10 12:09 | 2026-08-10 12:09 | 2026-08-10 12:18 | 2026-08-10 12:13 | 2026-08-10 12:13 |  |  | Fair | No | 103v/126v & 230v from secondary line, no neutral from transformer, transformer team needed
Non-Outage | J.E.26.08.06499 | C001883644 | Odeanie Davis | KSAS | Completed | Load_241668 | Rockfort - 210 | 2026-08-10 07:59 | 2026-08-10 08:00 | 2026-08-10 11:30 | 2026-08-10 13:12 | 2026-08-10 13:11 | 2026-08-10 14:03 | 2026-08-10 13:12 | 2026-08-10 13:12 |  |  | Fair | No | Customer stated that issue was resolved
Outage | J.E.26.08.13056 | C001883646 | Dwayne Samuels | Trelawny | Completed | Load_251870 | Greenwood - 110 | 2026-08-10 07:59 | 2026-08-10 08:02 | 2026-08-10 08:24 | 2026-08-10 08:25 | 2026-08-10 09:03 | 2026-08-10 10:44 | 2026-08-10 10:44 | 2026-08-10 10:44 |  |  | Fair | No | Patrol secondary to find 1 phase of customer service wire burnt off from jps pole and 1 pole span of broken system neutral open 1 8amp junction to splice and retention system neutral using about 40ft of copper wire and reconnect customer phase voltage left 119v/119v/238v
Non-Outage | J.E.26.08.05041 | C001883648 | Odeanie Davis | KSAS | Completed | Load_240151 | Rockfort - 410 | 2026-08-10 08:00 | 2026-08-10 08:00 | 2026-08-10 11:36 | 2026-08-10 11:37 | 2026-08-10 11:38 | 2026-08-10 11:46 | 2026-08-10 11:40 | 2026-08-10 11:40 |  |  | Fair | No | Customer stated that issue was resolved by their electrician
Non-Outage | J.E.26.08.05271 | C001883649 | Odeanie Davis | KSAS | Completed | Load_253177 | Rockfort - 410 | 2026-08-10 08:00 | 2026-08-10 08:00 | 2026-08-10 10:01 | 2026-08-10 10:16 | 2026-08-10 10:16 | 2026-08-10 10:53 | 2026-08-10 10:53 | 2026-08-10 10:53 |  |  | Fair | No | 130v/108v & 239v at location, 130v/108v & 239v from secondary line, secondary line is located on sirgarny dr, bucket truck needed.
Non-Outage | J.E.26.08.10726 | C001883653 | Royston Montague | St.Catherine | Completed | Load_294016 | Rhodens Pen - 310 | 2026-08-10 08:00 | 2026-08-10 08:02 | 2026-08-10 08:27 | 2026-08-10 08:44 | 2026-08-10 08:44 | 2026-08-10 08:48 | 2026-08-10 08:49 | 2026-08-10 08:49 |  |  | Fair | No | Rami system in area, customer having partial supply. Please assign to the relevant team thanks.
Non-Outage | J.E.26.08.11179 | C001883654 | Royston Montague | St.Catherine | Completed | Load_568263 | New Michelton - 210 | 2026-08-10 08:00 | 2026-08-10 08:02 | 2026-08-10 08:27 | 2026-08-11 09:33 | 2026-08-11 09:32 | 2026-08-11 09:33 | 2026-08-11 09:33 | 2026-08-11 09:33 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.08.11367 | C001883650 | Royston Montague | St.Catherine | Completed | Load_261629 | Tredegar - 410 | 2026-08-10 08:00 | 2026-08-10 08:02 | 2026-08-10 08:27 | 2026-08-10 13:00 | 2026-08-10 13:21 | 2026-08-10 13:32 | 2026-08-10 13:33 | 2026-08-10 13:33 |  |  | Fair | No | Burn meter. Customer only getting one leg, same needs to change, please inform field service department thank. Voltage at location 226v 112v 112
Non-Outage | J.E.26.08.11733 | C001883651 | Royston Montague | St.Catherine | Completed | Load_1000389 | Rhodens Pen - 410 | 2026-08-10 08:00 | 2026-08-10 08:02 | 2026-08-10 08:27 | 2026-08-10 08:55 | 2026-08-10 10:14 | 2026-08-10 10:26 | 2026-08-10 10:26 | 2026-08-10 10:26 |  |  | Fair | No | Premises found ok. Voltage 226v 112v 112v , joints in good condition. Likewise meter socket and service wire. Customers in area complained of regular outage in area at least twice a week.
Non-Outage | J.E.26.08.11871 | C001883657 | Royston Montague | St.Catherine | Completed | Load_252913 | New Michelton - 210 | 2026-08-10 08:00 | 2026-08-10 08:02 | 2026-08-10 08:27 | 2026-08-11 09:18 | 2026-08-11 09:31 | 2026-08-11 09:32 | 2026-08-11 09:32 | 2026-08-11 09:32 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.08.11875 | C001883652 | Royston Montague | St.Catherine | Completed | Load_264610 | Tredegar - 210 | 2026-08-10 08:00 | 2026-08-10 08:02 | 2026-08-10 08:27 | 2026-08-10 11:21 | 2026-08-10 11:48 | 2026-08-10 11:52 | 2026-08-10 11:54 | 2026-08-10 11:54 |  |  | Fair | No | Full voltage found at customer take off point. 114v unable to check pothead and meter socket. Multiple calls to customer phone go without answer.
Non-Outage | J.E.26.08.11946 | C001883656 | Royston Montague | St.Catherine | Completed | Load_264500 | New Michelton - 210 | 2026-08-10 08:00 | 2026-08-10 08:02 | 2026-08-10 08:27 | 2026-08-11 08:13 | 2026-08-11 09:16 | 2026-08-11 09:16 | 2026-08-11 09:17 | 2026-08-11 09:17 |  |  | Fair | No | Customer confirmed issue resolved. Please update thanks.
Non-Outage | J.E.26.08.12124 | C001883655 | Royston Montague | St.Catherine | Completed | Load_568284 | New Michelton - 310 | 2026-08-10 08:00 | 2026-08-10 08:02 | 2026-08-10 08:27 | 2026-08-11 09:33 | 2026-08-11 09:45 | 2026-08-11 09:45 | 2026-08-11 09:45 | 2026-08-11 09:45 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.08.11142 | C001883661 | Odaine Johnson | Clarendon | Completed | Load_257284 | Parnassus - 310 | 2026-08-10 08:03 | 2026-08-10 08:37 | 2026-08-10 09:59 | 2026-08-10 11:00 | 2026-08-10 11:12 | 2026-08-10 11:12 | 2026-08-10 11:13 | 2026-08-10 11:13 |  |  | Fair | No | Premises found okay customer was advised to get an electrician to check the premises voltage reading 110/109/220 volts
Non-Outage | J.E.26.08.12428 | C001883662 | Odaine Johnson | Clarendon | Completed | Load_256590 | Parnassus - 310 | 2026-08-10 08:03 | 2026-08-10 08:37 | 2026-08-10 09:59 | 2026-08-10 10:15 | 2026-08-10 10:58 | 2026-08-10 10:58 | 2026-08-10 10:59 | 2026-08-10 10:59 |  |  | Fair | No | Corroded neutral found at pole remade connection using 1 one bolt clamp voltage reading 117/115/232
Non-Outage | J.E.26.08.12638 | C001883660 | Odaine Johnson | Clarendon | Completed | Load_258999 | Monymusk - 410 | 2026-08-10 08:03 | 2026-08-10 08:37 | 2026-08-10 09:59 | 2026-08-10 12:07 | 2026-08-10 12:24 | 2026-08-10 12:24 | 2026-08-10 12:25 | 2026-08-10 12:25 |  |  | Fair | No | Premises found okay customer stated that the issue was resolved from yesterday
Non-Outage | J.E.26.08.12773 | C001883658 | Christopher Edwards | KSAN | Completed | Load_267645 | Constant Spring - 410 | 2026-08-10 08:03 | 2026-08-10 08:04 | 2026-08-10 08:07 | 2026-08-10 08:32 | 2026-08-10 09:43 | 2026-08-10 10:48 | 2026-08-10 10:49 | 2026-08-10 10:49 |  |  | Fair | No | Defective meter Customer is currently experiencing single phasing as a result of burnt meter
Non-Outage | J.E.26.08.10453 | C001883663 | Odaine Johnson | Clarendon | Completed | Load_250052 | Parnassus - 210 | 2026-08-10 08:04 | 2026-08-10 08:37 | 2026-08-10 09:59 | 2026-08-11 13:43 | 2026-08-11 14:24 | 2026-08-11 14:25 | 2026-08-11 14:25 | 2026-08-11 14:25 |  |  | Fair | No | Premises found okay customer stated that the issue was resolved
Non-Outage | J.E.26.08.10515 | C001883664 | Odaine Johnson | Clarendon | Completed | Load_257457 | Monymusk - 410 | 2026-08-10 08:04 | 2026-08-10 08:37 | 2026-08-10 09:59 | 2026-08-10 13:11 | 2026-08-10 13:16 | 2026-08-10 13:16 | 2026-08-10 13:17 | 2026-08-10 13:17 |  |  | Fair | No | Corroded phase found at pothead remade connection using 1 pen union
Outage | J.E.26.08.13143 | C001883666 | Romeo Brissett | St.James | Completed | Load_259728 | Queens Drive - 710 | 2026-08-10 08:05 | 2026-08-10 08:07 | 2026-08-10 10:55 | 2026-08-10 10:55 | 2026-08-10 10:55 | 2026-08-10 10:48 | 2026-08-10 10:56 | 2026-08-10 10:56 |  |  | Fair | No | Check and found ok, related to job#13179
Outage | J.E.26.08.13173 | C001883667 | Shamour Haughton | St.James | Completed | Load_250412 | Bogue - 310 | 2026-08-10 08:05 | 2026-08-10 08:08 | 2026-08-10 09:12 | 2026-08-10 09:13 | 2026-08-10 09:40 | 2026-08-10 09:41 | 2026-08-10 09:50 | 2026-08-10 09:50 |  |  | Fair | No | Contact call center, the meter is showing connected but customer is still without power, please refer to field service, box number is EN 04491
Outage | J.E.26.08.13179 | C001883665 | Romeo Brissett | St.James | Completed | Load_259728 | Queens Drive - 710 | 2026-08-10 08:05 | 2026-08-10 08:07 | 2026-08-10 08:14 | 2026-08-10 08:15 | 2026-08-10 09:24 | 2026-08-10 10:38 | 2026-08-10 10:54 | 2026-08-10 10:54 |  |  | Fair | No | Isolated (1)50kva transformer, removed illegal connections, spliced and retention 2 span of secondary, used 50ft of #2, 20ft of 2/0,
Non-Outage | J.E.26.08.12915 | C001883673 | Roemello Brown | Trelawny | Completed | Load_302479 | Duncans - 210 | 2026-08-10 08:12 | 2026-08-10 08:13 | 2026-08-10 09:29 | 2026-08-10 14:01 | 2026-08-10 15:36 | 2026-08-10 15:36 | 2026-08-10 15:46 | 2026-08-10 15:46 |  |  | Fair | No | Premises found working okayVoltage found 114/115/229Voltage leave 114/115/229
Non-Outage | J.E.26.07.36880 | C001883677 | Edward Royal | KSAS | Completed | Load_245440 | Up Park Camp - 310 | 2026-08-10 08:13 | 2026-08-10 08:14 | 2026-08-10 12:34 | 2026-08-10 12:34 | 2026-08-10 12:34 | 2026-08-10 12:35 | 2026-08-10 12:36 | 2026-08-10 12:36 |  |  | Fair | No | Premises found close unable to communicate with customer
Non-Outage | J.E.26.08.04567 | C001883676 | Edward Royal | KSAS | Completed | Load_239090 | Up Park Camp - 310 | 2026-08-10 08:13 | 2026-08-10 08:14 | 2026-08-10 09:08 | 2026-08-10 09:09 | 2026-08-10 09:08 | 2026-08-10 09:09 | 2026-08-10 09:09 | 2026-08-10 09:09 |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.08.11247 | C001883675 | Edward Royal | KSAS | Completed | Load_268260 | Greenwich - 310 | 2026-08-10 08:13 | 2026-08-10 08:14 | 2026-08-10 09:06 | 2026-08-10 09:07 | 2026-08-10 09:06 | 2026-08-10 09:07 | 2026-08-10 09:07 | 2026-08-10 09:07 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.13227 | C001883678 | Richard Nicholas | St.Catherine | Completed | Load_568174 | Rhodens Pen - 410 | 2026-08-10 08:14 | 2026-08-10 08:16 | 2026-08-10 08:46 | 2026-08-10 08:46 | 2026-08-10 10:24 | 2026-09-01 10:46 | 2026-08-10 10:47 | 2026-08-10 10:47 |  |  | Fair | No | Replaced blown 15amp junctions fuse at 3phase T-off to colbeck castle.
Non-Outage | J.E.26.08.05184 | C001883680 | Rochaine Hussey | KSAN | Completed | Load_249915 | Constant Spring - 410 | 2026-08-10 08:17 | 2026-08-10 08:26 | 2026-08-10 10:49 | 2026-08-10 10:51 | 2026-08-10 10:50 | 2026-08-10 10:53 | 2026-08-10 10:53 | 2026-08-10 10:53 |  |  | Fair | No | On the open secondary line there is some joint that is corroded which is causing the voltage to fluctuate bucket truck is needed to fix issue not only one customer affected Customer is say it’s damaging there equipments
Non-Outage | J.E.26.08.13187 | C001883679 | Denton Williams | Portland | Completed | Load_354844 | Port Antonio - 410 | 2026-08-10 08:17 | 2026-08-10 08:26 | 2026-08-10 09:49 | 2026-08-10 10:28 | 2026-08-10 11:19 | 2026-08-10 12:36 | 2026-08-10 12:36 | 2026-08-10 12:36 |  |  | Fair | No | Electrician advised customer to do an upgrade
Non-Outage | J.E.26.08.03419 | C001883688 | Rayon Foster | Hanover | Completed | Load_268987 | Orange Bay - 310 | 2026-08-10 08:20 | 2026-08-10 08:22 | 2026-08-10 08:55 | 2026-08-10 09:05 | 2026-08-10 11:20 | 2026-08-10 11:48 | 2026-08-10 12:09 | 2026-08-10 12:09 |  |  | Rains | No | Corrosion on customer pathead and jps pole was the cause of low voltage issues remake joints using three clamps voltage before 98/101 voltage after repair 110/109AB 219 volts
Non-Outage | J.E.26.08.04191 | C001883689 | Rayon Foster | Hanover | Completed | Load_1001382 | Orange Bay - 310 | 2026-08-10 08:20 | 2026-08-10 08:22 | 2026-08-10 08:57 | 2026-08-10 12:32 | 2026-08-10 12:35 | 2026-08-10 12:48 | 2026-08-10 12:48 | 2026-08-10 12:48 |  |  | Rains | No | Customer had internal issues which was resolved by there electrician
Non-Outage | J.E.26.07.19277 | C001883690 | Rayon Foster | Hanover | Completed | Load_244774 | Orange Bay - 310 | 2026-08-10 08:21 | 2026-08-10 08:22 | 2026-08-10 08:56 | 2026-08-10 12:15 | 2026-08-10 12:15 | 2026-08-10 12:31 | 2026-08-10 12:31 | 2026-08-10 12:31 |  |  | Rains | No | Call customer, customer said that issue was resolved
Non-Outage | J.E.26.07.33846 | C001883691 | Rayon Foster | Hanover | Completed | Load_268077 | Orange Bay - 310 | 2026-08-10 08:21 | 2026-08-10 08:22 | 2026-08-10 12:48 | 2026-08-10 12:49 | 2026-08-10 12:56 | 2026-08-10 13:54 | 2026-08-10 13:54 | 2026-08-10 13:54 |  |  | Rains | No | Customer said Issue was resolved by a JPS team few weeks ago
Outage | J.E.26.08.13230 | C001883694 | Hartley Chin | Clarendon | Completed | Load_257013 | Parnassus - 210 | 2026-08-10 08:22 | 2026-08-10 08:24 | 2026-08-10 11:57 | 2026-08-10 11:57 | 2026-08-10 11:57 | 2026-08-10 11:57 | 2026-08-10 11:58 | 2026-08-10 11:58 |  |  | Fair | No | Call related to job #13172
Non-Outage | J.E.26.08.13041 | C001883700 | Andrae Dawkins | St.James | Completed | Load_263658 | Bogue - 610 | 2026-08-10 08:23 | 2026-08-10 08:25 | 2026-08-10 15:39 | 2026-08-10 15:40 | 2026-08-10 15:40 | 2026-08-10 15:41 | 2026-08-10 15:43 | 2026-08-10 15:43 |  |  | Fair | No | Cannot locate customer unable to reach customer mobile phone
Non-Outage | J.E.26.08.13060 | C001883699 | Andrae Dawkins | St.James | Completed | Load_267529 | Bogue - 610 | 2026-08-10 08:23 | 2026-08-10 08:25 | 2026-08-10 13:47 | 2026-08-10 13:59 | 2026-08-10 14:11 | 2026-08-10 14:29 | 2026-08-10 14:32 | 2026-08-10 14:32 |  |  | Fair | No | Found customer meter socket defective advised customer to get an electrician to carry oust repairs voltage found 120/120/240
Non-Outage | J.E.26.08.13177 | C001883698 | Andrae Dawkins | St.James | Completed | Load_259728 | Queens Drive - 710 | 2026-08-10 08:23 | 2026-08-10 08:25 | 2026-08-10 09:24 | 2026-08-10 11:05 | 2026-08-10 11:05 | 2026-08-10 09:16 | 2026-08-10 11:06 | 2026-08-10 11:06 |  |  | Fair | No | Check and found ok problem was already resolved
Non-Outage | J.E.26.08.12366 | C001883704 | Andrae Dawkins | St.James | Completed | Load_258893 | Bogue - 610 | 2026-08-10 08:24 | 2026-08-10 08:25 | 2026-08-10 13:04 | 2026-08-10 13:04 | 2026-08-10 13:04 | 2026-08-10 13:45 | 2026-08-10 13:46 | 2026-08-10 13:46 |  |  | Fair | No | Found multiple customers 7 poles span from transformer experiencing low voltage voltage found at pothead 103/107/210 voltage found at transformer 113/114/228 refer back to emergency
Non-Outage | J.E.26.08.12967 | C001883703 | Andrae Dawkins | St.James | Completed | Load_412841 | Bogue - 610 | 2026-08-10 08:24 | 2026-08-10 08:25 | 2026-08-10 15:34 | 2026-08-10 15:35 | 2026-08-10 15:35 | 2026-08-10 14:41 | 2026-08-10 15:39 | 2026-08-10 15:39 |  |  | Fair | No | Cannot locate customer unable to reach customer’s mobile phone
Non-Outage | J.E.26.08.13032 | C001883702 | Andrae Dawkins | St.James | Completed | Load_254682 | Bogue - 310 | 2026-08-10 08:24 | 2026-08-10 08:25 | 2026-08-10 11:38 | 2026-08-10 11:38 | 2026-08-10 11:38 | 2026-08-10 09:46 | 2026-08-10 11:42 | 2026-08-10 11:42 |  |  | Fair | No | Check and found okay customer aid that they didn’t make any report
Non-Outage | J.E.26.08.13037 | C001883701 | Andrae Dawkins | St.James | Completed | Load_248155 | Queens Drive - 710 | 2026-08-10 08:24 | 2026-08-10 08:25 | 2026-08-10 09:30 | 2026-08-10 14:33 | 2026-08-10 14:33 | 2026-08-10 15:31 | 2026-08-10 15:32 | 2026-08-10 15:32 |  |  | Fair | No | Cannot locate customer unable to reach customers mobile phone
Outage | J.E.26.08.13244 | C001883706 | Hartley Chin | Clarendon | Completed | Load_246032 | Monymusk - 410 | 2026-08-10 08:24 | 2026-08-10 08:28 | 2026-08-10 14:10 | 2026-08-10 14:10 | 2026-08-10 14:10 | 2026-08-10 14:10 | 2026-08-10 14:11 | 2026-08-10 14:11 |  |  | SevereWind | No | Call related to job 13282
Non-Outage | J.E.26.08.08171 | C001883707 | Odaine Johnson | St.Catherine | Completed | Load_567904 | Rhodens Pen - 310 | 2026-08-10 08:25 | 2026-08-10 08:30 | 2026-08-10 09:59 | 2026-08-10 13:03 | 2026-08-10 13:07 | 2026-08-10 13:08 | 2026-08-10 13:09 | 2026-08-10 13:09 |  |  | Fair | No | Premises not found multiple efforts made to contact customer but was unsuccessful
Non-Outage | J.E.26.08.03493 | C001883718 | Fredrick Hamilton | KSAN | Completed | Load_265054 | Washington Blvd - 710 | 2026-08-10 08:28 | 2026-08-10 08:29 | 2026-08-10 08:34 | 2026-08-10 13:57 | 2026-08-10 14:21 | 2026-08-10 14:28 | 2026-08-10 14:28 | 2026-08-10 14:28 |  |  | Fair | No | 210v/101v/105v obtained low voltage detected Please have emergency inspect secondary jumper Multiple customers being affected
Non-Outage | J.E.26.08.03708 | C001883717 | Fredrick Hamilton | KSAN | Completed | Load_265054 | Washington Blvd - 710 | 2026-08-10 08:28 | 2026-08-10 08:29 | 2026-08-10 08:34 | 2026-08-10 14:29 | 2026-08-10 14:30 | 2026-08-10 14:33 | 2026-08-10 14:33 | 2026-08-10 14:33 |  |  | Fair | No | 207v/99v/105v please have emergency inspect secondary jumper Low voltage affecting multiple customers
Non-Outage | J.E.26.08.03817 | C001883716 | Fredrick Hamilton | KSAN | Completed | Load_293564 | Washington Blvd - 710 | 2026-08-10 08:28 | 2026-08-10 08:29 | 2026-08-10 08:34 | 2026-08-10 08:45 | 2026-08-10 08:45 | 2026-08-10 08:47 | 2026-08-10 08:47 | 2026-08-10 08:47 |  |  | Fair | No | Customer contacted and stated that report was made last year and power was restored fully previously Premises is ok
Non-Outage | J.E.26.08.04531 | C001883710 | Fredrick Hamilton | KSAN | Completed | Load_293397 | Washington Blvd - 710 | 2026-08-10 08:28 | 2026-08-10 08:29 | 2026-08-10 08:34 | 2026-08-10 14:34 | 2026-08-10 14:35 | 2026-08-10 14:35 | 2026-08-10 14:36 | 2026-08-10 14:36 |  |  | Fair | No | Multiple calls to customer went unanswered
Non-Outage | J.E.26.08.07019 | C001883709 | Fredrick Hamilton | KSAN | Completed | Load_243339 | Washington Blvd - 710 | 2026-08-10 08:28 | 2026-08-10 08:29 | 2026-08-10 08:34 | 2026-08-10 08:53 | 2026-08-10 08:53 | 2026-08-10 08:54 | 2026-08-10 08:54 | 2026-08-10 08:54 |  |  | Fair | No | Customer contacted and stated that power was restored fully previously PremisesPremises is ok
Non-Outage | J.E.26.08.10057 | C001883708 | Fredrick Hamilton | KSAN | Completed | Load_256453 | Washington Blvd - 710 | 2026-08-10 08:28 | 2026-08-10 08:29 | 2026-08-10 08:34 | 2026-08-10 08:59 | 2026-08-10 08:59 | 2026-08-10 09:00 | 2026-08-10 09:00 | 2026-08-10 09:00 |  |  | Fair | No | Customer contacted and stated that power was restored fully previously Premises is ok
Non-Outage | J.E.26.08.10127 | C001883720 | Dwain Samuels | Westmoreland | Completed | Load_569997 | Paradise - 210 | 2026-08-10 08:29 | 2026-08-10 08:30 | 2026-08-10 08:36 | 2026-08-10 12:18 | 2026-08-10 12:17 | 2026-08-10 12:17 | 2026-08-10 12:18 | 2026-08-10 12:18 |  |  | Fair | No | Meter found burnt. Voltage check 115-116-231
Non-Outage | J.E.26.08.11281 | C001883721 | Dwain Samuels | Westmoreland | Completed | Load_292540 | Paradise - 210 | 2026-08-10 08:29 | 2026-08-10 08:30 | 2026-08-10 08:36 | 2026-08-10 11:35 | 2026-08-10 11:34 | 2026-08-10 11:51 | 2026-08-10 11:52 | 2026-08-10 11:52 |  |  | Fair | No | Meter found burnt. Voltage check 112-113-225
Non-Outage | J.E.26.08.13199 | C001883719 | Dwain Samuels | Westmoreland | Completed | Load_247476 | Paradise - 110 | 2026-08-10 08:29 | 2026-08-10 08:30 | 2026-08-10 08:36 | 2026-08-10 09:15 | 2026-08-10 09:51 | 2026-08-10 10:40 | 2026-08-10 10:41 | 2026-08-10 10:41 |  |  | Fair | No | Corrosion found at 3 wire pole. Voltage check 107-115-123. Corrosion clear use 2 one bolt clamp. Voltage check 114-116-230
Non-Outage | J.E.26.07.32757 | C001883735 | Error Coore | Manchester | Completed | Load_237731 | Spur Tree - 310 | 2026-08-10 08:31 | 2026-08-10 08:33 | 2026-08-10 12:48 | 2026-08-10 12:49 | 2026-08-10 13:43 | 2026-08-10 13:58 | 2026-08-10 13:59 | 2026-08-10 13:59 |  |  | Rains | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.33012 | C001883734 | Error Coore | Manchester | Completed | Load_250435 | Spur Tree - 310 | 2026-08-10 08:31 | 2026-08-10 08:33 | 2026-08-10 08:53 | 2026-08-10 08:54 | 2026-08-10 09:37 | 2026-08-10 09:51 | 2026-08-10 09:53 | 2026-08-10 09:53 |  |  | Fair | No | Unable to carry out repair due to customer meter pole badly rotten at base
Non-Outage | J.E.26.08.10381 | C001883727 | Hopeton Henry | St.Thomas | Completed | Load_353202 | Good Year - 210 | 2026-08-10 08:31 | 2026-08-10 08:32 | 2026-08-10 08:45 | 2026-08-10 12:44 | 2026-08-10 13:43 | 2026-08-10 13:43 | 2026-08-10 13:44 | 2026-08-10 13:44 |  |  | Fair | No | Found ok issue resolved
Non-Outage | J.E.26.08.11511 | C001883732 | Error Coore | Manchester | Completed | Load_1002521 | Kendal - 310 | 2026-08-10 08:31 | 2026-08-10 08:33 | 2026-08-10 16:12 | 2026-08-10 16:12 | 2026-08-10 16:36 | 2026-08-10 16:42 | 2026-08-10 16:45 | 2026-08-10 16:45 |  |  | Rains | No | Premise not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.08.12238 | C001883724 | Hopeton Henry | St.Thomas | Completed | Load_353202 | Good Year - 210 | 2026-08-10 08:31 | 2026-08-10 08:32 | 2026-08-10 08:45 | 2026-08-10 12:42 | 2026-08-10 12:42 | 2026-08-10 12:42 | 2026-08-10 12:43 | 2026-08-10 12:43 |  |  | Fair | No | Issue resolved reconnect drop lead at transformer
Non-Outage | J.E.26.08.12377 | C001883733 | Error Coore | Manchester | Completed | Load_266835 | Porus - 310 | 2026-08-10 08:31 | 2026-08-10 08:33 | 2026-08-10 11:14 | 2026-08-10 11:15 | 2026-08-10 12:18 | 2026-08-10 12:46 | 2026-08-10 12:48 | 2026-08-10 12:48 |  |  | Rains | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.08.12894 | C001883731 | Error Coore | Manchester | Completed | Load_248276 | Spur Tree - 310 | 2026-08-10 08:31 | 2026-08-10 08:33 | 2026-08-10 15:23 | 2026-08-10 15:24 | 2026-08-10 15:58 | 2026-08-10 16:10 | 2026-08-10 16:12 | 2026-08-10 16:12 |  |  | Rains | No | Premise not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.08.12976 | C001883729 | Error Coore | Manchester | Completed | Load_266457 | Kendal - 310 | 2026-08-10 08:31 | 2026-08-10 08:33 | 2026-08-10 09:59 | 2026-08-10 10:01 | 2026-08-10 10:27 | 2026-08-10 11:11 | 2026-08-10 11:12 | 2026-08-10 11:12 |  |  | Rains | No | Premises found ok voltage reading 115/114/229 volts
Non-Outage | J.E.26.07.32675 | C001883736 | Error Coore | Manchester | Completed | Load_243202 | Spur Tree - 310 | 2026-08-10 08:32 | 2026-08-10 08:33 | 2026-08-10 13:59 | 2026-08-10 14:00 | 2026-08-10 15:05 | 2026-08-10 15:21 | 2026-08-10 15:23 | 2026-08-10 15:23 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.05.29684 | C001883739 | Nicholas Dillon | St.Elizabeth | Completed | Load_248332 | Maggotty - 210 | 2026-08-10 08:34 | 2026-08-10 08:36 | 2026-08-10 08:58 | 2026-08-10 11:24 | 2026-08-10 11:24 | 2026-08-10 11:24 | 2026-08-10 11:25 | 2026-08-10 11:25 |  |  | Fair | No | Check voltage before at meter 113 112 phase to phase 226 . Premises found working ok
Non-Outage | J.E.26.05.30348 | C001883741 | Nicholas Dillon | St.Elizabeth | Completed | Load_267466 | Maggotty - 210 | 2026-08-10 08:34 | 2026-08-10 08:36 | 2026-08-10 08:58 | 2026-08-10 10:47 | 2026-08-10 10:50 | 2026-08-10 10:53 | 2026-08-10 10:54 | 2026-08-10 10:54 |  |  | Fair | No | Check voltage before at meter 116 118 phase to phase 234. Premises found working ok
Non-Outage | J.E.26.05.30541 | C001883740 | Nicholas Dillon | St.Elizabeth | Completed | Load_292364 | Maggotty - 210 | 2026-08-10 08:34 | 2026-08-10 08:36 | 2026-08-10 08:58 | 2026-08-10 10:36 | 2026-08-10 10:40 | 2026-08-10 10:40 | 2026-08-10 10:45 | 2026-08-10 10:45 |  |  | Fair | Yes | Check and found corrosion at pole clean joint and use 2 one bolt clamp before I left voltage is 113 116 phase to phase 229
Non-Outage | J.E.26.05.31143 | C001883743 | Nicholas Dillon | St.Elizabeth | Completed | Load_260221 | Maggotty - 210 | 2026-08-10 08:34 | 2026-08-10 08:36 | 2026-08-10 08:58 | 2026-08-10 11:02 | 2026-08-10 11:02 | 2026-08-10 11:07 | 2026-08-10 11:10 | 2026-08-10 11:10 |  |  | Fair | No | Check voltage at meter 116 115 phase to phase 231. Premises found working ok
Non-Outage | J.E.26.05.31715 | C001883744 | Nicholas Dillon | St.Elizabeth | Completed | Load_242009 | Maggotty - 210 | 2026-08-10 08:34 | 2026-08-10 08:36 | 2026-08-10 08:58 | 2026-08-10 13:31 | 2026-08-10 13:30 | 2026-08-10 13:31 | 2026-08-10 13:32 | 2026-08-10 13:32 |  |  | Fair | No | Check voltage before at meter 116 115 phase to phase 231 . Premises found working ok
Non-Outage | J.E.26.05.32857 | C001883745 | Nicholas Dillon | St.Elizabeth | Completed | Load_239222 | Maggotty - 210 | 2026-08-10 08:35 | 2026-08-10 08:36 | 2026-08-10 08:58 | 2026-08-10 13:34 | 2026-08-10 13:38 | 2026-08-10 13:38 | 2026-08-10 13:40 | 2026-08-10 13:40 |  |  | Fair | No | Check voltage before at meter 111 113 phase to phase 225 . Premises found working ok
Non-Outage | J.E.26.05.34557 | C001883746 | Nicholas Dillon | St.Elizabeth | Completed | Load_242590 | Maggotty - 210 | 2026-08-10 08:35 | 2026-08-10 08:36 | 2026-08-10 08:58 | 2026-08-10 10:25 | 2026-08-10 10:25 | 2026-08-10 10:27 | 2026-08-10 10:28 | 2026-08-10 10:28 |  |  | Fair | Yes | Check voltage before at meter 115 114 phase to phase 230. Premises found working ok
Non-Outage | J.E.26.05.35547 | C001883748 | Nicholas Dillon | St.Elizabeth | Completed | Load_249737 | Maggotty - 210 | 2026-08-10 08:35 | 2026-08-10 08:36 | 2026-08-10 08:58 | 2026-08-10 13:57 | 2026-08-11 10:26 | 2026-08-11 10:26 | 2026-08-11 10:27 | 2026-08-11 10:27 |  |  | Fair | No | Check voltage before at meter 113 115 phase to phase 229 . Premises found working ok
Non-Outage | J.E.26.05.37084 | C001883747 | Nicholas Dillon | St.Elizabeth | Completed | Load_1002233 | Spur Tree - 210 | 2026-08-10 08:35 | 2026-08-10 08:36 | 2026-08-10 08:58 | 2026-08-10 11:51 | 2026-08-10 11:51 | 2026-08-10 11:55 | 2026-08-10 11:57 | 2026-08-10 11:57 |  |  | Fair | Yes | Check and found one leg of the service wire burn of at pole clean joint and connect back 3w pole before I left voltage is 112 113 phase to phase 226
Outage | J.E.26.08.13254 | C001883749 | Hartley Chin | Clarendon | Completed | Load_262889 | Parnassus - 310 | 2026-08-10 08:35 | 2026-08-10 08:38 | 2026-08-10 15:17 | 2026-08-10 15:18 | 2026-08-10 15:54 | 2026-08-10 15:55 | 2026-08-10 15:55 | 2026-08-10 15:55 |  |  | Fair | No | Customer as internal issues 113v 114v 228v
Non-Outage | J.E.26.08.13234 | C001883750 | Lancelot Brown |  | Completed |  |  | 2026-08-10 08:36 | 2026-08-10 09:05 | 2026-08-10 09:53 | 2026-08-10 14:00 | 2026-08-10 14:00 | 2026-08-10 14:50 | 2026-08-10 14:50 | 2026-08-10 14:50 |  |  | Rains | No | Found one span secondary neutral cut down isolate 25kva splice and retention one span of secondary neutral used thirty feet #2 conductor one #2 preform two pg clamps energise 25kva no pole number supply restore vl at secondary 114-114-228
Non-Outage | J.E.26.08.11404 | C001883751 | Wan Carlos Scarlett | St.Catherine | Completed | Load_241679 | Twickenham - 210 | 2026-08-10 08:37 | 2026-08-10 08:39 | 2026-08-10 11:21 | 2026-08-10 11:50 | 2026-08-10 11:59 | 2026-08-10 12:38 | 2026-08-10 12:51 | 2026-08-10 12:51 |  |  | Fair | No | Found customer meter socket defective advised customer to get a licensed electrician to fix the problem
Non-Outage | J.E.26.08.13246 | C001883752 | Rusean Allen |  | Completed |  |  | 2026-08-10 08:40 | 2026-08-10 08:41 | 2026-08-10 13:47 | 2026-08-10 13:48 | 2026-08-10 13:50 | 2026-08-10 13:51 | 2026-08-10 13:51 | 2026-08-10 13:51 | Fire |  | Fair | No | Premises okay
Outage | J.E.26.08.13255 | C001883756 | Andre Smith | KSAS | Completed | Load_1002929 | Hunts Bay - 810 | 2026-08-10 08:49 | 2026-08-10 09:01 | 2026-08-10 12:13 | 2026-08-10 12:14 | 2026-08-10 12:29 | 2026-08-10 13:59 | 2026-08-10 13:59 | 2026-08-10 13:59 |  |  | Fair | No | Replace burnt transformer droplead 4ft 4/0 copper supply restored
Non-Outage | J.E.26.08.10967 | C001883758 | Edward Royal | KSAS | Completed | Load_242463 | Greenwich - 310 | 2026-08-10 08:50 | 2026-08-10 08:51 | 2026-08-10 09:13 | 2026-08-10 09:14 | 2026-08-10 09:13 | 2026-08-10 09:14 | 2026-08-10 09:14 | 2026-08-10 09:14 |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.08.11133 | C001883757 | Edward Royal | KSAS | Completed | Load_255695 | Greenwich - 310 | 2026-08-10 08:50 | 2026-08-10 08:51 | 2026-08-10 09:11 | 2026-08-10 09:11 | 2026-08-10 09:11 | 2026-08-10 09:12 | 2026-08-10 09:12 | 2026-08-10 09:12 |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.08.13259 | C001883759 | Clyde Brown | Clarendon | Completed | Load_1003561 | May Pen - 110 | 2026-08-10 08:51 | 2026-08-10 08:55 | 2026-08-10 09:52 | 2026-08-10 09:52 | 2026-08-10 10:31 | 2026-08-10 11:25 | 2026-08-10 11:38 | 2026-08-10 11:38 | BrokenWire |  | Fair | No | Broken secondary neutral open 25 kva transformer and repaired with 8ft-#2,2- clamp and 1-preform.
Outage | J.E.26.08.13261 | C001883760 | Cliton Henry | St.Mary | Completed | Load_252639 | Oracabessa - 110 | 2026-08-10 08:56 | 2026-08-10 08:58 | 2026-08-10 12:00 | 2026-08-10 14:19 | 2026-08-10 14:42 | 2026-08-11 09:44 | 2026-08-11 09:45 | 2026-08-11 09:45 | Fire |  | Fair | No | Supply found ok, voltages at the customer pothead were 118-119/237 volts.
Non-Outage | J.E.26.08.13274 | C001883761 | Andre Smith |  | Completed |  |  | 2026-08-10 09:01 | 2026-08-10 09:01 | 2026-08-10 10:28 | 2026-08-10 10:29 | 2026-08-10 11:09 | 2026-08-10 11:39 | 2026-08-10 11:39 | 2026-08-10 11:39 | BrokenWire |  | Fair | No | Supply restored with the assistance of field service department
Outage | J.E.26.08.13268 | C001883762 | Lancelot Brown | Hanover | Completed | Load_261941 | Orange Bay - 210 | 2026-08-10 09:01 | 2026-08-10 09:03 | 2026-08-10 09:53 | 2026-08-10 11:23 | 2026-08-10 11:29 | 2026-08-10 11:45 | 2026-08-10 11:45 | 2026-08-10 11:45 |  |  | Rains | No | Energise bank of 3-50kva no pole number restore supply to charging system vl at pothead 240-238-238 -414-415-414 supply restore
Outage | J.E.26.08.13281 | C001883769 | Hartley Chin | Clarendon | Completed | Load_257457 | Monymusk - 410 | 2026-08-10 09:04 | 2026-08-10 09:16 | 2026-08-10 12:03 | 2026-08-10 12:03 | 2026-08-10 13:01 | 2026-08-10 14:08 | 2026-08-10 14:09 | 2026-08-10 14:09 |  |  | SevereWind | No | Found broken #2 triplex repair with approximately 40 ft #2
Non-Outage | J.E.26.08.13272 | C001883775 | Richard Nicholas | St.Catherine | Completed | Load_269089 | Rhodens Pen - 410 | 2026-08-10 09:14 | 2026-08-10 09:17 | 2026-08-10 12:55 | 2026-08-10 12:55 | 2026-08-10 13:58 | 2026-08-10 15:29 | 2026-08-10 15:31 | 2026-08-10 15:31 |  |  | Rains | No | Remade slack 2w service phase and neutral joint at pole and pothead.2 clamp and 1 penunion was used.voltage reading 114v.
Outage | J.E.26.08.13283 | C001883777 | Cliton Henry | St.Ann | Completed | Load_268810 | Upper White River - 210 | 2026-08-10 09:18 | 2026-08-10 09:39 | 2026-08-10 11:32 | 2026-08-10 11:32 | 2026-08-10 11:43 | 2026-08-10 11:44 | 2026-08-10 11:45 | 2026-08-10 11:45 |  |  | Fair | No | Unable to locate customer, the customer contact number provided went unanswered. This report need a direction to premises.
Non-Outage | J.E.26.08.13303 | C001883778 | Elvis Trowers |  | Completed |  |  | 2026-08-10 09:21 | 2026-08-10 09:22 | 2026-08-10 14:01 | 2026-08-10 14:01 | 2026-08-10 14:23 | 2026-08-10 14:41 | 2026-08-10 14:42 | 2026-08-10 14:42 | Fire |  | Fair | Yes | Areas checked and found ok during patrol, no sparks or fire was seen even though customer could not be contacted by telephone either.
Outage | J.E.26.08.13313 | C001883783 | Elvis Trowers | KSAN | Completed | Load_243712 | Washington Blvd - 410 | 2026-08-10 09:25 | 2026-08-10 09:26 | 2026-08-10 12:41 | 2026-08-10 12:41 | 2026-08-10 13:30 | 2026-08-10 13:57 | 2026-08-10 13:57 | 2026-08-10 13:57 |  |  | Fair | Yes | Happened to be internal when checked defective 4 wire meter socket found burnt out and needs to be changed, meter #2515421.
Outage | J.E.26.08.13319 | C001883784 | Daniel Francis | St.Ann | Completed | Load_247013 | Cardiff Hall - 310 | 2026-08-10 09:27 | 2026-08-10 19:28 | 2026-08-10 20:40 | 2026-08-10 20:41 | 2026-08-10 20:57 | 2026-08-10 21:45 | 2026-08-10 21:47 | 2026-08-10 21:47 |  |  | Fair | No | Meter socket defective advise customer voltage 108/108/217
Outage | J.E.26.08.13308 | C001883799 | Oshane Warren | Westmoreland | Completed | Load_263820 | Paradise - 110 | 2026-08-10 09:29 | 2026-08-10 09:31 | 2026-08-10 11:09 | 2026-08-10 11:10 | 2026-08-10 15:15 | 2026-08-10 15:17 | 2026-08-10 15:17 | 2026-08-10 15:17 |  |  | Rains | No | Clean corrosion from line section used 2 pg clamps
Outage | J.E.26.08.13315 | C001883800 | Michael Paterson | Westmoreland | Completed | Load_292449 | Paradise - 310 | 2026-08-10 09:29 | 2026-08-10 09:31 | 2026-08-10 10:00 | 2026-08-10 10:00 | 2026-08-10 10:02 | 2026-08-10 11:40 | 2026-08-10 11:40 | 2026-08-10 11:40 |  |  | Fair | No | Found junction fuse blown, no pole # additional checks done, no additional fault found, replace 8amps fuse, supply restored, customer confirm ok.
Non-Outage | J.E.26.08.13356 | C001883838 | Wan Carlos Scarlett |  | Completed |  |  | 2026-08-10 09:53 | 2026-08-10 10:01 | 2026-08-10 11:16 | 2026-08-10 11:17 | 2026-08-10 11:32 | 2026-08-10 11:48 | 2026-08-10 11:50 | 2026-08-10 11:50 | BrokenWire |  | Fair | No | Found customer with internal problem customer stansion and pothead defective advised customer to contact a licensed electrician to fix the problem
Outage | J.E.26.08.13357 | C001883828 | Tyrese Williams | St.Ann | Completed | Load_263745 | Cardiff Hall - 310 | 2026-08-10 09:53 | 2026-08-10 09:55 | 2026-08-10 10:05 | 2026-08-10 10:54 | 2026-08-10 11:24 | 2026-08-10 10:36 | 2026-08-10 11:57 | 2026-08-10 11:57 |  |  | Fair | No | Meter found burnt need to be change
Outage | J.E.26.08.13349 | C001883840 | Hartley Chin | Clarendon | Completed | Load_267083 | Monymusk - 210 | 2026-08-10 09:54 | 2026-08-10 10:01 | 2026-08-10 14:41 | 2026-08-10 14:41 | 2026-08-10 14:58 | 2026-08-10 14:58 | 2026-08-10 15:05 | 2026-08-10 15:05 |  |  | Fair | No | Premisis not found. Customer made a report for someone in Fraser’s field. Area patrolled and found four (4) hexing boxes with power. Unable to contact customer in Fraser’s field
Outage | J.E.26.08.13305 | C001883871 | Cliton Henry | St.Mary | Completed | Load_263482 | Oracabessa - 210 | 2026-08-10 10:04 | 2026-08-10 10:08 | 2026-08-10 10:52 | 2026-08-10 10:52 | 2026-08-10 11:07 | 2026-08-10 11:26 | 2026-08-10 11:31 | 2026-08-10 11:31 | Fire |  | Fair | No | The voltages found at the customer’s pothead were 116-117/233 volts. The customer was advised to get licensed electrician to carryout repairs
Outage | J.E.26.08.13354 | C001883873 | Cliton Henry | St.Mary | Completed | Load_250654 | Oracabessa - 210 | 2026-08-10 10:05 | 2026-08-10 10:08 | 2026-08-10 11:45 | 2026-08-10 12:01 | 2026-08-10 12:00 | 2026-08-10 12:42 | 2026-08-10 12:44 | 2026-08-10 12:44 |  |  | Fair | No | A defective #2 triplex service wire was replaced with 50 feet #6 triplex service wire. Voltages left were 111-114/225 volts.
Non-Outage | J.E.26.08.13379 | C001883876 | Denton Williams | Portland | Completed | Load_266805 | Port Antonio - 410 | 2026-08-10 10:07 | 2026-08-10 10:11 | 2026-08-10 14:59 | 2026-08-10 15:00 | 2026-08-10 15:00 | 2026-08-10 15:01 | 2026-08-10 15:01 | 2026-08-10 15:01 |  |  | Fair | No | Supply has been restored to the area.
Non-Outage | J.E.26.08.13366 | C001883884 | Royston Montague | St.Catherine | Completed | Load_246133 | Tredegar - 510 | 2026-08-10 10:08 | 2026-08-10 10:20 | 2026-08-10 10:26 | 2026-08-10 16:10 | 2026-08-10 16:59 | 2026-08-10 17:00 | 2026-08-10 17:00 | 2026-08-10 17:00 |  |  | Fair | No | Issue is on customer load side. Same inform to get an electrician. Voltage at premises 228v 113v 114v
Non-Outage | J.E.26.08.13385 | C001883885 | Odaine Johnson | Clarendon | Completed | Load_241776 | Monymusk - 210 | 2026-08-10 10:10 | 2026-08-10 10:19 | 2026-08-10 11:36 | 2026-08-10 11:36 | 2026-08-10 12:03 | 2026-08-10 12:03 | 2026-08-10 12:05 | 2026-08-10 12:05 |  |  | Fair | No | Premises found okay voltage reading 110/111/221 volts
Non-Outage | J.E.26.08.08086 | C001883891 | Orville Lee | Portmore | Completed | Load_243791 | Naggo Head - 510 | 2026-08-10 10:11 | 2026-08-10 10:23 | 2026-08-11 16:18 | 2026-08-11 16:19 | 2026-08-11 16:21 | 2026-08-11 16:24 | 2026-08-11 16:32 | 2026-08-11 16:32 |  |  | Fair | No | Premises found ok upon arrival Customer issues was resolved by a technician Voltage 117v118v237v
Non-Outage | J.E.26.08.08173 | C001883892 | Orville Lee | Portmore | Completed | Load_262745 | Naggo Head - 610 | 2026-08-10 10:11 | 2026-08-10 10:23 | 2026-08-11 09:58 | 2026-08-11 09:59 | 2026-08-11 10:22 | 2026-08-11 10:35 | 2026-08-11 10:35 | 2026-08-11 10:35 |  |  | Fair | No | Premises found ok upon arrival 121v121v242
Non-Outage | J.E.26.08.08237 | C001883889 | Orville Lee | Portmore | Completed | Load_244060 | Naggo Head - 610 | 2026-08-10 10:11 | 2026-08-10 10:23 | 2026-08-11 08:02 | 2026-08-11 08:02 | 2026-08-11 09:01 | 2026-08-11 09:06 | 2026-08-11 09:07 | 2026-08-11 09:07 |  |  | Fair | No | Premises found ok upon arrival Customer had the issue resolved by a technician Voltage 116v117v
Outage | J.E.26.08.13403 | C001883906 | Daniel Francis | St.Ann | Completed | Load_339987 | Roaring River - 410 | 2026-08-10 10:15 | 2026-08-10 10:16 | 2026-08-10 10:25 | 2026-08-10 10:26 | 2026-08-10 11:38 | 2026-08-10 10:30 | 2026-08-10 11:42 | 2026-08-10 11:42 |  |  | Fair | No | Not found
Non-Outage | J.E.26.08.12879 | C001883907 | Daniel Francis | St.Ann | Completed | Load_258977 | Ocho Rios - 310 | 2026-08-10 10:17 | 2026-08-10 10:19 | 2026-08-10 11:45 | 2026-08-10 11:45 | 2026-08-10 13:40 | 2026-08-10 14:26 | 2026-08-10 14:28 | 2026-08-10 14:28 |  |  | Fair | No | Found okay 117 118 234 internal problems
Outage | J.E.26.08.13173 | C001883921 | Vivian Gordon | St.James | Completed | Load_250412 | Bogue - 310 | 2026-08-10 10:21 | 2026-08-10 10:22 | 2026-08-10 14:42 | 2026-08-10 14:42 | 2026-08-10 14:42 | 2026-08-10 14:42 | 2026-08-10 14:50 | 2026-08-10 14:50 |  |  | Fair | No | Meter Mix up, This meter is serving customer account #487113 491191name Ancel Christie however it shows on the system otherwise, please update same. This customer Lelith Smith meter number is 1854470
Outage | J.E.26.08.13418 | C001883922 | Swon Miller | St.James | Completed | Load_259760 | Bogue - 610 | 2026-08-10 10:22 | 2026-08-10 10:23 | 2026-08-10 10:34 | 2026-08-10 10:35 | 2026-08-10 11:07 | 2026-08-10 12:28 | 2026-08-10 12:30 | 2026-08-10 12:30 | BrokenWire |  | Rains | No | Found service wire disconnected from pothead and jps main due to pothead wires burnt.voltage found 0.000 customer replace pothead wires cut and remove tree from secondary lines and reconnect customer service wire voltage left 114/115/231
Outage | J.E.26.08.13309 | C001883925 | Romeo Brissett | St.James | Completed | Load_248155 | Queens Drive - 710 | 2026-08-10 10:23 | 2026-08-10 10:24 | 2026-08-10 12:32 | 2026-08-10 12:32 | 2026-08-10 13:01 | 2026-08-10 13:12 | 2026-08-10 13:16 | 2026-08-10 13:16 |  |  | Fair | No | Line patrolled and found ok, no fire found, resident stated it’s an old reported report.
Outage | J.E.26.08.13312 | C001883926 | Romeo Brissett | St.James | Completed | Load_247836 | Queens Drive - 710 | 2026-08-10 10:23 | 2026-08-10 10:24 | 2026-08-10 11:01 | 2026-08-10 11:01 | 2026-08-10 11:19 | 2026-08-10 12:00 | 2026-08-10 12:07 | 2026-08-10 12:07 |  |  | Fair | No | Spliced and retention customer service wire, used 20ft of #6and 3 clamps V/R 107-110-217
Outage | J.E.26.08.13317 | C001883927 | Romeo Brissett | St.James | Completed | Load_292181 | Queens Drive - 310 | 2026-08-10 10:23 | 2026-08-10 10:24 | 2026-08-10 12:07 | 2026-08-10 12:08 | 2026-08-10 12:21 | 2026-08-10 12:28 | 2026-08-10 12:31 | 2026-08-10 12:31 |  |  | Fair | No | Premises was visited and found power. Security stated a team came by yesterday.
Outage | J.E.26.08.13412 | C001883928 | Edward Royal | KSAS | Completed | Load_579116 | Greenwich - 510 | 2026-08-10 10:25 | 2026-08-10 10:33 | 2026-08-10 10:52 | 2026-08-10 10:53 | 2026-08-10 10:52 | 2026-08-10 12:22 | 2026-08-10 12:23 | 2026-08-10 12:23 |  |  | Fair | No | Defective 100kva transformer need to be change it the power transformer out of a bank of 3 transformer reffered to maintenance replaced 2 junction fuse 40A defective transformer feed general accident and there with out supply
Non-Outage | J.E.26.08.13371 | C001883930 | Dwayne Samuels |  | Completed |  |  | 2026-08-10 10:26 | 2026-08-10 10:47 | 2026-08-10 12:18 | 2026-08-10 12:18 | 2026-08-10 13:13 | 2026-08-10 13:28 | 2026-08-10 13:32 | 2026-08-10 13:32 |  |  | Fair | No | Customer meter is burnt on the left side load and line side refer to field service team voltage found 114v/114v/228v
Outage | J.E.26.08.13420 | C001883929 | Rusean Allen | KSAS | Completed | Load_241864 | Rockfort - 210 | 2026-08-10 10:26 | 2026-08-10 10:28 | 2026-08-10 13:20 | 2026-08-10 13:21 | 2026-08-10 13:41 | 2026-08-10 13:47 | 2026-08-10 13:47 | 2026-08-10 13:47 | BrokenWire |  | Fair | No | 1 span broken secondary wire found, wire was spliced retention and reconnected
Outage | J.E.26.08.13373 | C001883931 | Michael Paterson | Westmoreland | Completed | Load_254517 | Paradise - 310 | 2026-08-10 10:27 | 2026-08-10 10:28 | 2026-08-10 11:41 | 2026-08-10 11:41 | 2026-08-10 11:41 | 2026-08-10 11:42 | 2026-08-10 11:44 | 2026-08-10 11:44 |  |  | Fair | No | Found junction fuse blown, no pole #, no additional fault found, replace 8amps fuse, supply restored.
Outage | J.E.26.08.13397 | C001883932 | Oshane Warren | Westmoreland | Completed | Load_270220 | Paradise - 110 | 2026-08-10 10:27 | 2026-08-10 10:28 | 2026-08-10 11:04 | 2026-08-10 11:05 | 2026-08-10 11:04 | 2026-08-10 11:05 | 2026-08-10 11:09 | 2026-08-10 11:09 |  |  | Fair | No | Customer got disconnected for none payment of bill however customer cleared up the bill and need connection
Outage | J.E.26.08.13350 | C001883935 | Damion Reid | Manchester | Completed | Load_238264 | Kendal - 210 | 2026-08-10 10:28 | 2026-08-10 18:10 | 2026-08-10 21:10 | 2026-08-10 21:11 | 2026-08-10 21:43 | 2026-08-10 22:27 | 2026-08-10 22:31 | 2026-08-10 22:31 |  |  | Rains | No | Blown 10amp junction fuse found cause by lightning line patrol and replace blown fuse
Outage | J.E.26.08.13406 | C001883941 | Derrick Grubb | St.Thomas | Completed | Load_262795 | Good Year - 110 | 2026-08-10 10:28 | 2026-08-10 14:48 | 2026-08-10 16:20 | 2026-08-10 16:21 | 2026-08-10 18:18 | 2026-08-10 19:39 | 2026-08-10 19:42 | 2026-08-10 19:42 | BrokenWire |  | Fair | No | Splice and retention two span open secondary neutral, reset 10 kva transformer at pole number 037250
Outage | J.E.26.08.13410 | C001883942 | Derrick Grubb | St.Thomas | Completed | Load_577193 | Good Year - 110 | 2026-08-10 10:28 | 2026-08-10 14:48 | 2026-08-10 19:42 | 2026-08-10 19:43 | 2026-08-10 19:42 | 2026-08-10 19:43 | 2026-08-10 19:43 | 2026-08-10 19:43 | BrokenWire |  | Fair | No | Splice and retention two span open secondary neutral, reset 10 kva transformer at pole number 037250
Outage | J.E.26.08.13421 | C001883934 | Richard Samuda | Manchester | Completed | Load_249921 | Kendal - 310 | 2026-08-10 10:28 | 2026-08-10 10:29 | 2026-08-10 10:41 | 2026-08-10 10:43 | 2026-08-10 11:14 | 2026-08-10 11:16 | 2026-08-10 11:16 | 2026-08-10 11:16 |  |  | Rains | No | Found customer has a damaged meter and meter socket advised customer to repair meter refer call to field service voltage: 113, 116 229
Outage | J.E.26.08.13339 | C001883943 | Stephen Taylor | St.Thomas | Completed | Load_243122 | Lysson - 410 | 2026-08-10 10:29 | 2026-08-10 10:38 | 2026-08-10 11:39 | 2026-08-10 11:40 | 2026-08-10 11:40 | 2026-08-10 11:40 | 2026-08-10 11:40 | 2026-08-10 11:40 | BrokenWire |  | Fair | No | See junction link down patrol and see two primary pole broken need assistance for the jps maintenance team to restore power to the community isolated at pole # 0004854 the road is still block
Outage | J.E.26.08.13352 | C001883944 | Milton Charlton | KSAN | Completed | Load_243463 | Hope - 510 | 2026-08-10 10:31 | 2026-08-10 10:34 | 2026-08-10 13:40 | 2026-08-10 13:41 | 2026-08-10 14:28 | 2026-08-10 14:25 | 2026-08-10 14:32 | 2026-08-10 14:32 |  |  | Fair | No | Reconnect customer meter that was disconnected. Reconnection was done by JPS escalation.
Outage | J.E.26.08.13386 | C001883945 | Milton Charlton | KSAN | Completed | Load_567800 | Hope - 510 | 2026-08-10 10:32 | 2026-08-10 10:34 | 2026-08-10 10:45 | 2026-08-10 10:45 | 2026-08-10 11:35 | 2026-08-10 12:20 | 2026-08-10 12:29 | 2026-08-10 12:29 |  |  | Fair | No | Customer service wire #6 triplex burnoff at pole. Repair using one 1- bolt clamp. Readings at meter socket 116-117-234 volts.
Outage | J.E.26.08.13359 | C001883946 | Edward Royal | KSAS | Completed | Load_268210 | Greenwich - 510 | 2026-08-10 10:33 | 2026-08-10 10:34 | 2026-08-10 12:24 | 2026-08-10 12:25 | 2026-08-10 12:24 | 2026-08-10 12:25 | 2026-08-10 12:25 | 2026-08-10 12:25 |  |  | Fair | No | Call related
Non-Outage | J.E.26.08.13414 | C001883955 | Edward Royal |  | Completed |  |  | 2026-08-10 10:34 | 2026-08-10 10:38 | 2026-08-10 12:23 | 2026-08-10 12:24 | 2026-08-10 12:23 | 2026-08-10 12:24 | 2026-08-10 12:24 | 2026-08-10 12:24 | LeakingTransformer |  | Fair | No | Related to defective transformer
Non-Outage | J.E.26.08.13431 | C001883954 | Milton Charlton |  | Completed |  |  | 2026-08-10 10:34 | 2026-08-10 10:35 | 2026-08-10 12:29 | 2026-08-10 12:30 | 2026-08-10 13:38 | 2026-08-10 13:40 | 2026-08-10 13:40 | 2026-08-10 13:40 | BrokenWire |  | Fair | No | Customer service wire #6 triplex neutral burn off in mid span. Splice and retention using 6ft #6 triplex neutral and two 1- bolt clamps. Readings at meter socket 114-115-230 volts.
Outage | J.E.26.08.13398 | C001883953 | Denton Williams | Portland | Completed | Load_250156 | Port Antonio - 410 | 2026-08-10 10:34 | 2026-08-10 10:37 | 2026-08-10 12:39 | 2026-08-10 12:39 | 2026-08-10 12:46 | 2026-08-10 12:58 | 2026-08-10 13:40 | 2026-08-10 13:40 | TreeContact | Y | Fair | No | 15amps junction fuse blown cause by tree limb touches primary conductor cut and remove limb then restored supply to the area.
Outage | J.E.26.08.13441 | C001883952 | Daniel Francis | St.Ann | Completed | Load_264096 | Roaring River - 410 | 2026-08-10 10:34 | 2026-08-10 10:37 | 2026-08-10 11:42 | 2026-08-10 11:43 | 2026-08-10 11:42 | 2026-08-10 11:18 | 2026-08-10 11:44 | 2026-08-10 11:44 | BrokenWire |  | Fair | No | Change one clump 114 114 228 in all
Outage | J.E.26.08.13383 | C001883956 | Elvis Trowers | KSAN | Completed | Load_257446 | Constant Spring - 210 | 2026-08-10 10:37 | 2026-08-10 10:38 | 2026-08-10 12:39 | 2026-08-10 12:39 | 2026-08-10 12:39 | 2026-08-10 12:40 | 2026-08-10 12:40 | 2026-08-10 12:40 |  |  | Fair | Yes | Call related.
Outage | J.E.26.08.13392 | C001883957 | Elvis Trowers | KSAN | Completed | Load_244804 | Constant Spring - 210 | 2026-08-10 10:37 | 2026-08-10 10:38 | 2026-08-10 12:38 | 2026-08-10 12:38 | 2026-08-10 12:38 | 2026-08-10 12:39 | 2026-08-10 12:39 | 2026-08-10 12:39 |  |  | Fair | Yes | CALL related, found ok.
Non-Outage | J.E.26.08.13444 | C001883965 | Oshane Warren |  | Completed |  |  | 2026-08-10 10:42 | 2026-08-10 10:44 | 2026-08-10 10:47 | 2026-08-10 10:54 | 2026-08-10 10:54 | 2026-08-10 10:54 | 2026-08-10 10:56 | 2026-08-10 10:56 |  |  | Rains | No | 25 kva transformer Defective need to change refer to maintenance 12 customer is with power
Outage | J.E.26.08.13481 | C001883970 | Tyrese Williams | St.Ann | Completed | Load_258465 | Cardiff Hall - 210 | 2026-08-10 10:44 | 2026-08-10 11:57 | 2026-08-10 12:04 | 2026-08-10 12:05 | 2026-08-10 12:21 | 2026-08-10 14:27 | 2026-08-10 14:29 | 2026-08-10 14:29 | BrokenWire | Y | Rains | No | Cut tree from secondary line, Splice and retention 4 span of secondary phase and neutral use 80ft of #2AA, 4 pg clamp and 1 splicing sleeve and replace a 25 kva transformer fuse at pole
Non-Outage | J.E.26.08.13335 | C001883973 | Rochaine Hussey | KSAN | Completed | Load_263666 | Constant Spring - 410 | 2026-08-10 10:47 | 2026-08-10 10:48 | 2026-08-10 11:56 | 2026-08-10 11:57 | 2026-08-10 11:56 | 2026-08-10 13:04 | 2026-08-10 13:05 | 2026-08-10 13:05 |  |  | Fair | No | The voltage at the transformer is found okay 115/116/2321v 2 pole away from the transformer the voltage drop to 107/105 v I’m unable to fix the issue due to the pole located on a banking so ladder is unable to reach bucket truck needed also at the customer Premesis the voltage is 105/99vPole number 0037571/0037817Bucket truck needed
Non-Outage | J.E.26.08.13485 | C001883972 | Rochaine Hussey | KSAN | Completed | Load_269403 | Constant Spring - 410 | 2026-08-10 10:47 | 2026-08-10 10:48 | 2026-08-10 11:49 | 2026-08-10 11:49 | 2026-08-10 11:49 | 2026-08-10 11:55 | 2026-08-10 11:56 | 2026-08-10 11:56 |  |  | Fair | No | Customer was called multiple times no answer Unable to locate
Non-Outage | J.E.26.08.13279 | C001883980 | Shamour Haughton | St.James | Completed | Load_556946 | Bogue - 310 | 2026-08-10 10:49 | 2026-08-10 10:50 | 2026-08-10 11:28 | 2026-08-10 11:28 | 2026-08-10 11:53 | 2026-08-10 11:53 | 2026-08-10 11:58 | 2026-08-10 11:58 | LowHangingWires |  | Fair | No | Found 1,40ft pole leaning, HEX02977 service wires are hanging low across the road, please refer to maintenance
Outage | J.E.26.08.13479 | C001883981 | Swon Miller | St.James | Completed | Load_239119 | Bogue - 610 | 2026-08-10 10:52 | 2026-08-10 10:54 | 2026-08-10 12:31 | 2026-08-10 12:31 | 2026-08-10 13:47 | 2026-08-18 02:30 | 2026-08-10 14:48 | 2026-08-10 14:48 |  |  | Fair | No | Found customer without supply cause by hurricane M unable to reconnect customer due to pothead and meter socket damage advice customer to carry out repairs before power can be restored customer states that repairs will be carried out this week
Outage | J.E.26.08.13282 | C001884001 | Andre Williams | Trelawny | Completed | Load_268209 | Martha Brae - 210 | 2026-08-10 11:18 | 2026-08-10 15:27 | 2026-08-10 15:40 | 2026-08-10 20:34 | 2026-08-10 20:49 | 2026-08-10 20:52 | 2026-08-10 20:53 | 2026-08-10 20:53 |  |  | Fair | No | Premises not found, customer number not in service , need more directions
Outage | J.E.26.08.13294 | C001884000 | Andre Williams | Trelawny | Completed | Load_260941 | Duncans - 210 | 2026-08-10 11:18 | 2026-08-10 15:27 | 2026-08-10 17:17 | 2026-08-10 17:19 | 2026-08-10 18:11 | 2026-08-10 18:25 | 2026-08-10 18:25 | 2026-08-10 18:25 | BrokenWire |  | Fair | No | Patrol line section re fuse and close blown 12 amp junction on single phase line
Outage | J.E.26.08.13364 | C001884002 | Dwayne Samuels | Trelawny | Completed | Load_247755 | Martha Brae - 210 | 2026-08-10 11:18 | 2026-08-10 11:18 | 2026-08-10 13:33 | 2026-08-10 13:33 | 2026-08-10 14:21 | 2026-08-10 14:56 | 2026-08-10 15:11 | 2026-08-10 15:11 |  |  | Fair | No | Check and found working ok voltage found at pole and pothead 121v/123v/244v customer was advised to get an electrician to do some internal checks
Non-Outage | J.E.26.08.13548 | C001884012 | Kemark Slue |  | Completed |  |  | 2026-08-10 11:25 | 2026-08-10 11:27 | 2026-08-10 11:54 | 2026-08-10 13:57 | 2026-08-10 13:58 | 2026-08-10 13:59 | 2026-08-10 13:59 | 2026-08-10 13:59 |  |  | Rains | No | Upon arrival at the location the crew discovered that 8 amps junction fuse was blown, further observation and patrol revealed that lightning was the caused, refuse link and re-energized line section.
Outage | J.E.26.08.13519 | C001884013 | Moses Elliston | St.Catherine | Completed | Load_568572 | Tredegar - 510 | 2026-08-10 11:25 | 2026-08-10 11:27 | 2026-08-11 15:10 | 2026-08-11 15:11 | 2026-08-11 15:11 | 2026-08-11 15:11 | 2026-08-11 15:12 | 2026-08-11 15:12 |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.08.13552 | C001884010 | Denton Williams | Portland | Completed | Load_242981 | Port Antonio - 410 | 2026-08-10 11:25 | 2026-08-10 11:27 | 2026-08-10 12:36 | 2026-08-10 12:37 | 2026-08-10 12:37 | 2026-08-10 12:38 | 2026-08-10 12:38 | 2026-08-10 12:38 | BrokenWire |  | Fair | No | After making several calls we could not reach out to the customer.
Outage | J.E.26.08.13557 | C001884011 | Kemark Slue | St.Catherine | Completed | Load_253135 | New Michelton - 310 | 2026-08-10 11:25 | 2026-08-10 11:27 | 2026-08-10 11:54 | 2026-08-10 11:54 | 2026-08-10 13:10 | 2026-08-10 13:44 | 2026-08-10 13:56 | 2026-08-10 13:56 |  |  | Rains | No | Upon arrival at the location the crew discovered that 8 amps junction fuse was blown, further observation and patrol revealed that lightning was the caused, refuse link and re-energized line section.
Outage | J.E.26.08.13549 | C001884014 | Moses Elliston | St.Catherine | Completed | Load_1000940 | Tredegar - 410 | 2026-08-10 11:26 | 2026-08-10 11:27 | 2026-08-11 12:47 | 2026-08-11 12:47 | 2026-08-11 12:47 | 2026-08-11 12:47 | 2026-08-11 12:48 | 2026-08-11 12:48 |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.08.13574 | C001884015 | Rodclif Dawkins | St.Catherine | Completed | Load_1000408 | Tredegar - 510 | 2026-08-10 11:26 | 2026-08-11 11:41 | 2026-08-11 12:22 | 2026-08-11 12:59 | 2026-08-11 13:13 | 2026-08-11 13:52 | 2026-08-11 13:55 | 2026-08-11 13:55 | LowHangingWires |  | Fair | No | Customer stanchion broken, customer was advised to have electrician and carpenter effect repairs
Outage | J.E.26.08.13507 | C001884025 | Gregory Grossett | Portland | Completed | Load_268491 | Port Antonio - 310 | 2026-08-10 11:33 | 2026-08-10 15:11 | 2026-08-10 15:48 | 2026-08-10 15:48 | 2026-08-10 17:55 | 2026-08-10 18:25 | 2026-08-10 18:30 | 2026-08-10 18:30 |  |  | Fair | No | 15 amps junction fuse blown at pole number 0014570 , cause by sagging conductor, repair and restore line section, material used 1 silicone disc , 1-15 amps fuse.
Outage | J.E.26.08.13575 | C001884033 | Richard Samuda | Manchester | Completed | Load_241236 | Spur Tree - 310 | 2026-08-10 11:41 | 2026-08-10 11:44 | 2026-08-10 11:54 | 2026-08-10 12:16 | 2026-08-10 12:52 | 2026-08-10 02:29 | 2026-08-10 14:30 | 2026-08-10 14:30 |  |  | Rains | No | Meter number: 2973957, 2973956, 2382634 splice reconnected customer service wire that was broken by customer truck using 40ft of number 6 service wire and 3 1 bolt customer back to normal voltage 116,117 233
Outage | J.E.26.08.13600 | C001884035 | Hartley Chin | Clarendon | Completed | Load_265787 | Monymusk - 210 | 2026-08-10 11:45 | 2026-08-10 11:52 | 2026-08-10 14:39 | 2026-08-10 14:40 | 2026-08-10 14:40 | 2026-08-10 14:40 | 2026-08-10 14:40 | 2026-08-10 14:40 | BrokenWire |  | Fair | No | Call related to job 13599
Non-Outage | J.E.26.08.13599 | C001884036 | Hartley Chin | Clarendon | Completed | Load_265787 | Monymusk - 210 | 2026-08-10 11:46 | 2026-08-10 11:52 | 2026-08-10 14:12 | 2026-08-10 14:13 | 2026-08-10 14:36 | 2026-08-10 14:36 | 2026-08-10 14:39 | 2026-08-10 14:39 | BrokenWire |  | SevereWind | No | Repair broken joint customer was single phasing 113v114v228v
Outage | J.E.26.08.13576 | C001884038 | Horace Malcolm | St.James | Completed | Load_238926 | Bogue - 610 | 2026-08-10 11:47 | 2026-08-10 15:15 | 2026-08-10 15:43 | 2026-08-10 15:44 | 2026-08-10 16:57 | 2026-08-10 19:35 | 2026-08-10 19:36 | 2026-08-10 19:36 |  |  | Fair | No | Isolate one 25kva transformer to splice and retention two pole span secondary phase and nuetral used 50ft #2 conductor four #2- preforms and 3clamps
Outage | J.E.26.08.13588 | C001884037 | Marlon Authors | St.Elizabeth | Completed | Load_250102 | Maggotty - 210 | 2026-08-10 11:47 | 2026-08-10 15:44 | 2026-08-10 17:34 | 2026-08-10 17:35 | 2026-08-10 18:40 | 2026-08-10 19:29 | 2026-08-10 19:29 | 2026-08-10 19:29 | BrokenWire |  | Fair | No | Patrol and found one pole span of secondary lower phase broken caused by vehicle accident. Isolate and close 50 kva transformer circuit no pole #, to splice and retention same using five feet of 2/0 conductor and four clamps. Restored supply okay
Non-Outage | J.E.26.08.13437 | C001884045 | Royston Montague | St.Catherine | Completed | Load_1001432 | Tredegar - 210 | 2026-08-10 11:55 | 2026-08-10 12:03 | 2026-08-10 13:50 | 2026-08-11 15:40 | 2026-08-11 18:27 | 2026-08-11 18:28 | 2026-08-11 18:28 | 2026-08-11 18:28 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.08.13530 | C001884047 | Royston Montague | St.Catherine | Completed | Load_249048 | Tredegar - 410 | 2026-08-10 11:55 | 2026-08-10 12:03 | 2026-08-10 13:50 | 2026-08-11 09:46 | 2026-08-11 10:26 | 2026-08-11 10:26 | 2026-08-11 10:26 | 2026-08-11 10:26 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.08.13544 | C001884044 | Kemark Slue | St.Catherine | Completed | Load_240658 | New Michelton - 210 | 2026-08-10 11:55 | 2026-08-11 08:36 | 2026-08-11 11:45 | 2026-08-11 12:05 | 2026-08-11 12:05 | 2026-08-11 09:16 | 2026-08-11 12:07 | 2026-08-11 12:07 |  |  | Fair | No | Upon arrival at the location the crew was told that the request is no longer required.
Non-Outage | J.E.26.08.13590 | C001884049 | Radcliffe Coleman | St.Catherine | Completed | Load_253597 | Tredegar - 210 | 2026-08-10 11:55 | 2026-08-10 18:07 | 2026-08-10 19:28 | 2026-08-10 19:29 | 2026-08-10 21:50 | 2026-08-10 22:03 | 2026-08-10 22:03 | 2026-08-10 22:03 |  |  | Fair | No | There is an issue at the location that requires daylight attention.
Non-Outage | J.E.26.08.13616 | C001884048 | Royston Montague | St.Catherine | Completed | Load_255939 | Tredegar - 510 | 2026-08-10 11:55 | 2026-08-10 12:03 | 2026-08-10 13:50 | 2026-08-10 13:51 | 2026-08-10 15:46 | 2026-08-10 16:09 | 2026-08-10 16:09 | 2026-08-10 16:09 |  |  | Fair | No | Slack meter in meter socket. Same corrected. Voltage 217v 108v 107v
Non-Outage | J.E.26.08.13517 | C001884054 | Odaine Johnson | Clarendon | Completed | Load_249266 | May Pen - 110 | 2026-08-10 12:03 | 2026-08-10 12:34 | 2026-08-11 08:38 | 2026-08-11 13:39 | 2026-08-11 13:42 | 2026-08-11 13:42 | 2026-08-11 13:42 | 2026-08-11 13:42 |  |  | Fair | No | Emergency team needed, area experiencing low voltage
Outage | J.E.26.08.13648 | C001884076 | Wan Carlos Scarlett | St.Catherine | Completed | Load_248660 | Twickenham - 410 | 2026-08-10 12:26 | 2026-08-10 13:34 | 2026-08-10 14:11 | 2026-08-10 14:12 | 2026-08-10 14:11 | 2026-08-10 14:52 | 2026-08-10 14:56 | 2026-08-10 14:56 |  |  | Fair | No | Found customer with internal problem customer meter socket defective advised customer to contact a licensed electrician to fix the issue reading 115 116 232
Outage | J.E.26.08.13662 | C001884090 | Neckell Ormsby | St.Ann | Completed | Load_352050 | Upper White River - 110 | 2026-08-10 12:34 | 2026-08-11 09:26 | 2026-08-11 09:34 | 2026-08-11 09:34 | 2026-08-11 11:04 | 2026-08-11 11:48 | 2026-08-11 12:01 | 2026-08-11 12:01 | BrokenWire |  | SevereWind | No | Found junction fuse blown at pole #0014130 patrol and found no permanent fault however line section needs bushing replace 1-15 amp junction fuse
Outage | J.E.26.08.13635 | C001884093 | Richard Samuda | Manchester | Completed | Load_246031 | Spur Tree - 310 | 2026-08-10 12:39 | 2026-08-10 12:40 | 2026-08-10 14:52 | 2026-08-10 14:53 | 2026-08-10 14:54 | 2026-08-10 02:54 | 2026-08-10 14:55 | 2026-08-10 14:55 |  |  | Rains | No | Customer said power was restored
Outage | J.E.26.08.13675 | C001884094 | Richard Samuda | Manchester | Completed | Load_256785 | Spur Tree - 310 | 2026-08-10 12:39 | 2026-08-10 12:40 | 2026-08-10 14:30 | 2026-08-10 14:30 | 2026-08-10 14:40 | 2026-08-10 14:52 | 2026-08-10 14:52 | 2026-08-10 14:52 | Fire |  | Rains | No | Found 15amp junction blown patrol line found nothing replaced fuse close line customer back to normal
Outage | J.E.26.08.13622 | C001884095 | Cliton Henry | St.Mary | Completed | Load_245909 | Oracabessa - 110 | 2026-08-10 12:42 | 2026-08-10 12:43 | 2026-08-10 13:49 | 2026-08-10 13:50 | 2026-08-10 14:05 | 2026-08-10 14:18 | 2026-08-10 14:18 | 2026-08-10 14:18 | Fire |  | Fair | No | A 25 kva transformer found tripped due to entangled secondary conductors caused by a truck. The transformer was further de energized for a physical disconnect. The conductors were cleared and supply restored to reset and energized the 25 kva transformer.
Non-Outage | J.E.26.08.13573 | C001884107 | Daniel Francis | St.Ann | Completed | Load_328142 | Roaring River - 210 | 2026-08-10 12:45 | 2026-08-10 12:47 | 2026-08-10 16:59 | 2026-08-10 16:59 | 2026-08-10 18:42 | 2026-08-10 20:28 | 2026-08-10 20:35 | 2026-08-10 20:35 |  |  | Fair | No | Renew 1bolt clamp at secondary' jumper also retention 1span of secondary phase voltage left 107/106/215
Non-Outage | J.E.26.08.13704 | C001884106 | Daniel Francis | St.Ann | Completed | Load_248191 | Roaring River - 210 | 2026-08-10 12:45 | 2026-08-10 12:47 | 2026-08-10 16:09 | 2026-08-10 16:10 | 2026-08-10 16:48 | 2026-08-10 16:52 | 2026-08-10 16:59 | 2026-08-10 16:59 | BrokenPole |  | Fair | No | Pole #574435 found 30ft pole with service wire and street light 100% defective need to be change now it’s not in a safe position
Non-Outage | J.E.26.08.13742 | C001884131 | Edward Royal |  | Completed |  |  | 2026-08-10 12:56 | 2026-08-10 12:57 | 2026-08-10 14:16 | 2026-08-10 14:17 | 2026-08-10 14:16 | 2026-08-10 14:17 | 2026-08-10 14:17 | 2026-08-10 14:17 |  |  | Fair | No | Call related to outage
Outage | J.E.26.08.13740 | C001884132 | Edward Royal | KSAN | Completed | Load_557466 | Washington Blvd - 410 | 2026-08-10 12:56 | 2026-08-10 12:57 | 2026-08-10 13:43 | 2026-08-10 13:44 | 2026-08-10 13:43 | 2026-08-10 14:14 | 2026-08-10 14:14 | 2026-08-10 14:14 |  |  | Fair | No | Greenwich feeder trip and now restore
Non-Outage | J.E.26.08.13737 | C001884133 | Andre Smith |  | Completed |  |  | 2026-08-10 12:58 | 2026-08-10 12:59 | 2026-08-10 14:00 | 2026-08-10 14:00 | 2026-08-10 14:43 | 2026-08-10 14:44 | 2026-08-10 14:44 | 2026-08-10 14:44 |  |  | Fair | No | Supply restored feeder restored
Outage | J.E.26.08.13723 | C001884139 | Christopher Edwards | KSAN | Completed | Load_256208 | Constant Spring - 410 | 2026-08-10 13:01 | 2026-08-10 13:01 | 2026-08-10 13:46 | 2026-08-10 13:47 | 2026-08-10 14:46 | 2026-08-10 15:30 | 2026-08-10 15:32 | 2026-08-10 15:32 |  |  | Fair | No | Required small bucket truck to check 2/0 twisted connections Approximately 4 customers are getting single phasing Unable to reach connections to check the joints
Non-Outage | J.E.26.08.13401 | C001884147 | Cliton Henry |  | Completed |  |  | 2026-08-10 13:07 | 2026-08-10 13:08 | 2026-08-10 13:12 | 2026-08-10 13:12 | 2026-08-10 13:40 | 2026-08-10 13:48 | 2026-08-10 13:49 | 2026-08-10 13:49 |  |  | Fair | No | A blown 8 amp junction fuse found at pole #0013435 due vines. The vine was removed and supply restored using 1-8 amp fuse
Outage | J.E.26.08.13724 | C001884146 | Daniel Francis | St.Ann | Completed | Load_269408 | Ocho Rios - 310 | 2026-08-10 13:07 | 2026-08-10 13:08 | 2026-08-10 15:39 | 2026-08-10 15:40 | 2026-08-10 15:39 | 2026-08-10 16:04 | 2026-08-10 16:09 | 2026-08-10 16:09 |  |  | Fair | No | Change 2 fuse one 3amp and one 2amp pole #0098830
Non-Outage | J.E.26.08.13613 | C001884156 | Moses Elliston |  | Completed |  |  | 2026-08-10 13:09 | 2026-08-10 14:21 | 2026-08-10 15:30 | 2026-08-10 15:31 | 2026-08-10 15:30 | 2026-08-10 15:15 | 2026-08-10 15:32 | 2026-08-10 15:32 |  |  | Fair | No | Supply ok at premises,112-112-224 volts at pothead
Outage | J.E.26.08.13419 | C001884157 | Denton Williams | Portland | Completed | Load_266805 | Port Antonio - 410 | 2026-08-10 13:10 | 2026-08-10 13:12 | 2026-08-10 13:45 | 2026-08-10 13:46 | 2026-08-10 13:57 | 2026-08-10 14:55 | 2026-08-10 14:59 | 2026-08-10 14:59 |  |  | Fair | No | 100kva transformer top phase drop lead burn out open transformer fuse link to make repairs then close fuse link to restore normal supply to the area.Material use 5ft of 2/0 copper 3 one bolt clamps.
Outage | J.E.26.08.13847 | C001884158 | Andre Williams | Trelawny | Completed | Load_239537 | Duncans - 210 | 2026-08-10 13:11 | 2026-08-10 15:27 | 2026-08-10 15:48 | 2026-08-10 15:49 | 2026-08-10 16:29 | 2026-08-10 17:01 | 2026-08-10 17:01 | 2026-08-10 17:01 | Fire |  | Fair | No | Open 100kva transformer remake joint that was burning and touching telephone wires on 2naut twisted voltage on line 115+117=232
Outage | J.E.26.08.13567 | C001884199 | Stephen Taylor | St.Thomas | Completed | Load_239634 | Lysson - 410 | 2026-08-10 13:29 | 2026-08-10 13:29 | 2026-08-10 13:53 | 2026-08-10 13:54 | 2026-08-10 14:24 | 2026-08-10 14:24 | 2026-08-10 14:24 | 2026-08-10 14:24 |  |  | Fair | No | Splice and retention secondary wires and close up back 25 kva transformer safety with a 3 amp fuse
Outage | J.E.26.08.13983 | C001884204 | Daniel Francis | St.Ann | Completed | Load_312665 | Roaring River - 410 | 2026-08-10 13:33 | 2026-08-10 13:41 | 2026-08-10 22:29 | 2026-08-10 22:29 | 2026-08-10 22:31 | 2026-08-10 22:32 | 2026-08-10 22:32 | 2026-08-10 22:32 |  |  | Fair | No | Not found customer not answering phone
Non-Outage | J.E.26.07.30244 | C001884237 | Moses Elliston | St.Catherine | Completed | Load_556848 | Naggo Head - 610 | 2026-08-10 14:10 | 2026-08-10 14:11 | 2026-08-10 16:06 | 2026-08-10 16:07 | 2026-08-10 16:06 | 2026-08-10 16:07 | 2026-08-10 16:09 | 2026-08-10 16:09 |  |  | Fair | No | Burnt 3 wire service phase and neutral repaired with 2 linkets,and 2 clamps.112-112.-224 volts on service line.
Outage | J.E.26.08.14036 | C001884247 | Richard Nicholas | St.Catherine | Completed | Load_242365 | Rhodens Pen - 210 | 2026-08-10 14:25 | 2026-08-11 08:33 | 2026-08-11 09:15 | 2026-08-11 09:16 | 2026-08-11 10:25 | 2026-08-11 10:53 | 2026-08-11 10:55 | 2026-08-11 10:55 |  |  | Fair | No | 3w meter checked,same found defective.one side of meter relay found open however please refer to the field service department to have meter replace.voltage reading 117x2 and 234v.
Non-Outage | J.E.26.08.13946 | C001884313 | Roxroy Needham |  | Completed |  |  | 2026-08-10 15:05 | 2026-08-10 15:16 | 2026-08-10 16:06 | 2026-08-10 17:42 | 2026-08-10 18:33 | 2026-08-10 19:18 | 2026-08-10 19:19 | 2026-08-10 19:19 |  |  | Fair | No | Replace 1- 8 amp junction fuse at pole
Outage | J.E.26.08.13471 | C001884312 | Gregory Grossett | Portland | Completed | Load_240782 | Port Antonio - 310 | 2026-08-10 15:05 | 2026-08-10 15:12 | 2026-08-10 18:32 | 2026-08-10 18:32 | 2026-08-10 18:50 | 2026-08-10 18:50 | 2026-08-10 18:52 | 2026-08-10 18:52 |  |  | Fair | No | Jps meter is defective and need to be replaced, please refer to field service
Outage | J.E.26.08.13540 | C001884306 | Christopher Edwards | KSAN | Completed | Load_292076 | Constant Spring - 310 | 2026-08-10 15:05 | 2026-08-11 11:24 | 2026-08-11 13:17 | 2026-08-11 13:18 | 2026-08-11 14:12 | 2026-08-11 14:53 | 2026-08-11 14:55 | 2026-08-11 14:55 |  |  | Fair | No | Customer meter socket is wired 220 but customer has a 110 meterCustomer was advised to get electrician to correct the wiring Also customer meter is burnt Customer was advised to file report as soon as electrician correct the fault
Outage | J.E.26.08.13709 | C001884311 | Gregory Grossett | Portland | Completed | Load_239329 | Port Antonio - 310 | 2026-08-10 15:05 | 2026-08-10 15:11 | 2026-08-10 18:30 | 2026-08-10 18:31 | 2026-08-10 18:30 | 2026-08-10 18:24 | 2026-08-10 18:32 | 2026-08-10 18:32 |  |  | Fair | No | 15 amps junction fuse blown at pole number 0014570 , cause by sagging conductor, repair and restore line section, material used 1 silicone disc , 1-15 amps fuse.
Outage | J.E.26.08.13730 | C001884308 | Dwayne Cohen | KSAN | Completed | Load_258336 | Washington Blvd - 810 | 2026-08-10 15:05 | 2026-08-10 15:41 | 2026-08-10 16:25 | 2026-08-10 16:26 | 2026-08-10 16:49 | 2026-08-10 16:54 | 2026-08-10 16:55 | 2026-08-10 16:55 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.13738 | C001884310 | Gregory Grossett | Portland | Completed | Load_265513 | Port Antonio - 410 | 2026-08-10 15:05 | 2026-08-10 15:10 | 2026-08-10 19:58 | 2026-08-10 19:59 | 2026-08-10 20:58 | 2026-08-10 21:00 | 2026-08-10 21:08 | 2026-08-10 21:08 |  |  | Fair | No | Broken 30ft wooden pole DE construction. Approximately 200ft of no.2 conductor is needed and 120ft of no.6 service wire. Two customer stated that the pole had been broken from July 2026 and they have been without power supply since. Please refer to Portland Maintenance Team.
Outage | J.E.26.08.14098 | C001884309 | Gregory Grossett | Portland | Completed | Load_255677 | Port Antonio - 410 | 2026-08-10 15:05 | 2026-08-10 15:09 | 2026-08-10 21:08 | 2026-08-10 21:09 | 2026-08-10 21:32 | 2026-08-10 21:32 | 2026-08-10 21:33 | 2026-08-10 21:33 |  |  | Fair | No | After reaching out to customer they stated that their power supply is back. Customer okay.
Outage | J.E.26.08.14147 | C001884314 | Roxroy Needham | St.Ann | Completed | Load_241195 | Cardiff Hall - 310 | 2026-08-10 15:05 | 2026-08-10 15:20 | 2026-08-10 16:03 | 2026-08-10 16:04 | 2026-08-10 17:12 | 2026-08-10 17:39 | 2026-08-10 17:40 | 2026-08-10 17:40 |  |  | Fair | No | Replace 1-25 amp junction fuse after line was patrol
Outage | J.E.26.08.14233 | C001884307 | Horace Malcolm | St.James | Completed | Load_249383 | Bogue - 610 | 2026-08-10 15:05 | 2026-08-10 15:07 | 2026-08-10 19:36 | 2026-08-10 19:36 | 2026-08-10 20:30 | 2026-08-10 20:56 | 2026-08-10 20:56 | 2026-08-10 20:56 |  |  | Fair | No | Check and found customer have no service wire at premises customer needs 90ft #6 triplex wire
Non-Outage | J.E.26.08.13116 | C001884325 | Evan Spaulding |  | Completed |  |  | 2026-08-10 15:11 | 2026-08-10 15:55 | 2026-08-10 19:11 | 2026-08-10 19:11 | 2026-08-10 19:50 | 2026-08-10 20:02 | 2026-08-10 20:03 | 2026-08-10 20:03 |  |  | Fair | No | Burnt off wire in meter socket, customer advised to get Electrician correct the issue.
Outage | J.E.26.08.12033 | C001884327 | Nickolas Rodriques | St.Catherine | Completed | Load_264194 | Twickenham - 210 | 2026-08-10 15:13 | 2026-08-10 15:14 | 2026-08-10 17:19 | 2026-08-10 17:29 | 2026-08-10 18:17 | 2026-08-10 18:41 | 2026-08-10 18:44 | 2026-08-10 18:44 |  |  | Fair | No | Unable to locate or communicate with the specific customer. However, the area was patrolled and no noticeable outage was found.
Outage | J.E.26.08.14212 | C001884332 | Romeo Brissett | St.James | Completed | Load_242456 | Bogue - 310 | 2026-08-10 15:13 | 2026-08-10 15:17 | 2026-08-10 16:11 | 2026-08-10 16:11 | 2026-08-10 17:07 | 2026-08-10 17:30 | 2026-08-10 17:34 | 2026-08-10 17:34 |  |  | Fair | No | Isolated (1)25KVA transformer, Removed illegal connections, repaired transformer drop lead and retention secondary
Outage | J.E.26.08.14253 | C001884326 | Nickolas Rodriques | KSAS | Completed | Load_254412 | Duhaney - 210 | 2026-08-10 15:13 | 2026-08-10 15:15 | 2026-08-10 15:36 | 2026-08-10 16:23 | 2026-08-10 16:49 | 2026-08-10 17:08 | 2026-08-10 17:18 | 2026-08-10 17:18 |  |  | Fair | No | Checked and found a 10 KVA transformer tripped. Patrol and found nothing on line Repaired by replacing the fuse and energized after completing patrol.
Outage | J.E.26.08.13660 | C001884335 | Neville Spencer | Clarendon | Completed | Load_249796 | May Pen - 110 | 2026-08-10 15:15 | 2026-08-10 15:16 | 2026-08-10 18:55 | 2026-08-10 18:56 | 2026-08-10 19:00 | 2026-08-10 19:14 | 2026-08-10 19:16 | 2026-08-10 19:16 |  |  | Fair | No | Reset trip 25 kva xmfr remade supply restored.
Outage | J.E.26.08.13710 | C001884334 | Neville Spencer | Clarendon | Completed | Load_255025 | May Pen - 110 | 2026-08-10 15:15 | 2026-08-10 15:16 | 2026-08-10 15:26 | 2026-08-10 15:27 | 2026-08-10 17:28 | 2026-08-10 17:28 | 2026-08-10 18:55 | 2026-08-10 18:55 |  |  | Fair | No | Renew blown 25 amp j/ fuse at pole #0159101 . Also renew blown 30 , amp j/ fuse at pole # 0165992 area restored.
Outage | J.E.26.08.13728 | C001884339 | Damion Reid | Manchester | Completed | Load_268909 | Kendal - 210 | 2026-08-10 15:20 | 2026-08-10 15:37 | 2026-08-10 17:50 | 2026-08-10 17:51 | 2026-08-10 19:07 | 2026-08-10 19:16 | 2026-08-10 19:18 | 2026-08-10 19:18 | BrokenWire |  | Rains | No | Unable to contact or locate customer meter was pinged by the dispatcher and found on line
Non-Outage | J.E.26.07.27039 | C001884346 | Hartley Chin | Clarendon | Completed | Load_254926 | Parnassus - 310 | 2026-08-10 15:21 | 2026-08-10 15:22 | 2026-08-10 17:16 | 2026-08-10 17:17 | 2026-08-10 17:16 | 2026-08-10 17:17 | 2026-08-10 17:18 | 2026-08-10 17:18 |  |  | Fair | No | Premisis found ok.
Non-Outage | J.E.26.07.27054 | C001884345 | Hartley Chin | Clarendon | Completed | Load_247615 | Parnassus - 310 | 2026-08-10 15:21 | 2026-08-10 15:22 | 2026-08-10 17:18 | 2026-08-10 17:18 | 2026-08-10 17:18 | 2026-08-10 17:19 | 2026-08-10 17:20 | 2026-08-10 17:20 |  |  | Fair | No | Premisis found ok
Non-Outage | J.E.26.07.27232 | C001884344 | Hartley Chin | Clarendon | Completed | Load_263080 | Parnassus - 310 | 2026-08-10 15:21 | 2026-08-10 15:22 | 2026-08-10 17:20 | 2026-08-10 17:21 | 2026-08-10 17:20 | 2026-08-10 17:21 | 2026-08-10 17:22 | 2026-08-10 17:22 |  |  | Fair | No | Premisis found ok.
Non-Outage | J.E.26.07.29424 | C001884342 | Hartley Chin | Clarendon | Completed | Load_246828 | Parnassus - 310 | 2026-08-10 15:21 | 2026-08-10 15:22 | 2026-08-10 17:26 | 2026-08-10 17:26 | 2026-08-10 17:26 | 2026-08-10 17:26 | 2026-08-10 17:27 | 2026-08-10 17:27 |  |  | Fair | No | Premisis found ok.
Non-Outage | J.E.26.07.29647 | C001884343 | Hartley Chin | Clarendon | Completed | Load_262352 | Parnassus - 310 | 2026-08-10 15:21 | 2026-08-10 15:22 | 2026-08-10 17:22 | 2026-08-10 17:23 | 2026-08-10 17:23 | 2026-08-10 17:24 | 2026-08-10 17:25 | 2026-08-10 17:25 |  |  | Fair | No | Premisis found ok.
Non-Outage | J.E.26.07.30230 | C001884341 | Hartley Chin | Clarendon | Completed | Load_262352 | Parnassus - 310 | 2026-08-10 15:21 | 2026-08-10 15:22 | 2026-08-10 17:27 | 2026-08-10 17:28 | 2026-08-10 17:27 | 2026-08-10 17:28 | 2026-08-10 17:28 | 2026-08-10 17:28 |  |  | Fair | No | Premisis found ok.
Non-Outage | J.E.26.07.39318 | C001884340 | Hartley Chin | Clarendon | Completed | Load_259584 | Parnassus - 310 | 2026-08-10 15:21 | 2026-08-10 15:22 | 2026-08-10 17:28 | 2026-08-10 17:29 | 2026-08-10 17:29 | 2026-08-10 17:29 | 2026-08-10 17:30 | 2026-08-10 17:30 |  |  | Fair | No | Premisis found ok.
Non-Outage | J.E.26.07.29318 | C001884347 | Hartley Chin | Clarendon | Completed | Load_261816 | Parnassus - 310 | 2026-08-10 15:22 | 2026-08-10 15:23 | 2026-08-10 17:15 | 2026-08-10 17:15 | 2026-08-10 17:15 | 2026-08-10 17:15 | 2026-08-10 17:16 | 2026-08-10 17:16 |  |  | Fair | No | Premisis found ok.
Non-Outage | J.E.26.08.12733 | C001884354 | Odeanie Davis | KSAS | Completed | Load_244455 | Cane River - 610 | 2026-08-10 15:23 | 2026-08-11 09:59 | 2026-08-11 11:51 | 2026-08-11 14:45 | 2026-08-11 14:50 | 2026-08-11 15:38 | 2026-08-11 15:39 | 2026-08-11 15:39 |  |  | Fair | No | 102v/123v at arrival, open circuit at secondary corrected, 4 one bolt clamps, 1 penn union & 10ft twisted, 110v/115v & 225v ,
Outage | J.E.26.08.13731 | C001884348 | Kemark Slue | St.Catherine | Completed | Load_245363 | New Michelton - 310 | 2026-08-10 15:23 | 2026-08-11 08:29 | 2026-08-11 08:33 | 2026-08-11 08:33 | 2026-08-11 10:16 | 2026-08-11 08:32 | 2026-08-11 11:59 | 2026-08-11 11:59 |  |  | Fair | No | Unable to locate customer’s premises due to inadequate directions and all calls to number given were unanswered.
Outage | J.E.26.08.13618 | C001884357 | Radcliffe Coleman | St.Catherine | Completed | Load_255048 | Tredegar - 410 | 2026-08-10 15:24 | 2026-08-10 15:26 | 2026-08-10 15:44 | 2026-08-10 15:47 | 2026-08-10 16:36 | 2026-08-10 18:27 | 2026-08-10 18:27 | 2026-08-10 18:27 |  |  | Fair | No | Location found with a bank of three transformer (3-100kva) with one of the drop leads burnt. Repairs were done with aid of one ampact and approximately four feet of #4 copper. The bank was isolated before repairs were done. Location now back to normal.
Outage | J.E.26.08.14239 | C001884356 | Moses Elliston | St.Catherine | Completed | Load_1001076 | Tredegar - 210 | 2026-08-10 15:24 | 2026-08-10 15:25 | 2026-08-11 09:49 | 2026-08-11 09:50 | 2026-08-11 09:49 | 2026-08-11 09:49 | 2026-08-11 09:54 | 2026-08-11 09:54 |  |  | Fair | No | Supply ok at premises
Outage | J.E.26.08.13729 | C001884358 | Romaine Roberts | St.Mary | Completed | Load_260682 | Highgate - 210 | 2026-08-10 15:25 | 2026-08-10 15:31 | 2026-08-10 17:18 | 2026-08-10 17:19 | 2026-08-10 17:39 | 2026-08-10 18:07 | 2026-08-10 18:07 | 2026-08-10 18:07 |  |  | Fair | No | After carrying out checks found customer breaker defective advise customer to get electrician to carryout repairs
Outage | J.E.26.08.13269 | C001884359 | Romaine Roberts | St.Mary | Completed | Load_263079 | Highgate - 210 | 2026-08-10 15:26 | 2026-08-10 15:30 | 2026-08-10 18:39 | 2026-08-10 18:40 | 2026-08-10 19:58 | 2026-08-10 20:16 | 2026-08-10 20:22 | 2026-08-10 20:22 | Fire |  | Fair | No | Truck burnt down customer 3 wire service replace 100 foot number 6 triplex also wire burn up in customer meter panel and pipes advise customer to get electrician to carryout repairs
Outage | J.E.26.08.14085 | C001884360 | Radcliffe Coleman | St.Catherine | Completed | Load_248018 | Tredegar - 410 | 2026-08-10 15:26 | 2026-08-10 15:28 | 2026-08-10 15:45 | 2026-08-10 18:27 | 2026-08-10 18:27 | 2026-08-10 18:28 | 2026-08-10 18:28 | 2026-08-10 18:28 |  |  | Fair | No | Location found with a bank of three transformer (3-100kva) with one of the drop leads burnt. Repairs were done with aid of one ampact and approximately four feet of #4 copper. The bank was isolated before repairs were done. Location now back to normal.
Outage | J.E.26.08.14185 | C001884361 | Radcliffe Coleman | St.Catherine | Completed | Load_255048 | Tredegar - 410 | 2026-08-10 15:26 | 2026-08-10 15:28 | 2026-08-10 15:45 | 2026-08-10 18:29 | 2026-08-10 18:28 | 2026-08-10 18:29 | 2026-08-10 18:29 | 2026-08-10 18:29 |  |  | Fair | No | Location found with a bank of three transformer (3-100kva) with one of the drop leads burnt. Repairs were done with aid of one ampact and approximately four feet of #4 copper. The bank was isolated before repairs were done. Location now back to normal.
Outage | J.E.26.08.14252 | C001884362 | Radcliffe Coleman | St.Catherine | Completed | Load_260753 | Tredegar - 410 | 2026-08-10 15:26 | 2026-08-10 15:28 | 2026-08-10 15:45 | 2026-08-10 18:29 | 2026-08-10 18:29 | 2026-08-10 18:30 | 2026-08-10 18:30 | 2026-08-10 18:30 |  |  | Fair | No | Location found with a bank of three transformer (3-100kva) with one of the drop leads burnt. Repairs were done with aid of one ampact and approximately four feet of #4 copper. The bank was isolated before repairs were done. Location now back to normal.
Outage | J.E.26.08.14230 | C001884364 | Romaine Roberts | St.Mary | Completed | Load_247631 | Highgate - 210 | 2026-08-10 15:27 | 2026-08-10 15:31 | 2026-08-10 18:07 | 2026-08-10 18:08 | 2026-08-10 18:38 | 2026-08-10 18:39 | 2026-08-10 18:39 | 2026-08-10 18:39 |  |  | Fair | No | Found ok
Non-Outage | J.E.26.08.13002 | C001884375 | Neville Spencer | Clarendon | Completed | Load_245015 | May Pen - 110 | 2026-08-10 15:28 | 2026-08-10 15:29 | 2026-08-10 19:18 | 2026-08-10 19:19 | 2026-08-10 21:06 | 2026-08-10 21:08 | 2026-08-10 21:09 | 2026-08-10 21:09 |  |  | Fair | No | Customer not located.
Outage | J.E.26.08.13988 | C001884377 | Romaine Roberts | St.Mary | Completed | Load_267806 | Highgate - 210 | 2026-08-10 15:28 | 2026-08-10 15:31 | 2026-08-10 20:22 | 2026-08-10 20:22 | 2026-08-10 22:49 | 2026-08-10 22:51 | 2026-08-10 22:52 | 2026-08-10 22:52 |  |  | Fair | No | Junction fuse found blown patrol line clear vegetation from primary line and replace 10 amp power restore no pole number at location
Outage | J.E.26.08.14078 | C001884374 | Romaine Roberts | St.Mary | Completed | Load_265076 | Highgate - 210 | 2026-08-10 15:28 | 2026-08-10 15:29 | 2026-08-10 15:40 | 2026-08-10 15:41 | 2026-08-10 16:53 | 2026-08-10 17:01 | 2026-08-10 17:03 | 2026-08-10 17:03 |  |  | Fair | No | Found customer meter defective and need to be change meter pole burnt off meter number 2640721
Outage | J.E.26.08.14086 | C001884376 | Evan Spaulding | St.Mary | Completed | Load_354721 | Oracabessa - 210 | 2026-08-10 15:28 | 2026-08-10 15:29 | 2026-08-10 18:52 | 2026-08-10 18:53 | 2026-08-10 18:52 | 2026-08-10 18:53 | 2026-08-10 18:54 | 2026-08-10 18:54 |  |  | Fair | No | Meter was Reconnected and customer is ok now.
Outage | J.E.26.08.13284 | C001884380 | Radcliffe Coleman | St.Catherine | Completed | Load_1000406 | Twickenham - 410 | 2026-08-10 15:30 | 2026-08-10 15:31 | 2026-08-10 18:32 | 2026-08-10 18:32 | 2026-08-10 19:23 | 2026-08-10 19:28 | 2026-08-10 19:28 | 2026-08-10 19:28 |  |  | Fair | No | The area was visited, however, we were unable to locate the customer. A number of calls were placed to the telephone number provided which went to voicemail.
Outage | J.E.26.08.14158 | C001884379 | Moses Elliston | St.Catherine | Completed | Load_1000329 | Tredegar - 410 | 2026-08-10 15:30 | 2026-08-10 15:30 | 2026-08-11 17:16 | 2026-08-11 17:16 | 2026-08-11 17:16 | 2026-08-11 17:16 | 2026-08-11 17:17 | 2026-08-11 17:17 |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.08.14037 | C001884381 | Christopher West | St.Catherine | Completed | Load_268319 | Twickenham - 410 | 2026-08-10 15:31 | 2026-08-10 15:33 | 2026-08-10 17:00 | 2026-08-10 17:00 | 2026-08-10 17:41 | 2026-08-10 17:53 | 2026-08-10 17:53 | 2026-08-10 17:53 |  |  | Fair | No | Premises found closed at time of visit.
Outage | J.E.26.08.12606 | C001884382 | Christopher West | St.Catherine | Completed | Load_251619 | Naggo Head - 610 | 2026-08-10 15:32 | 2026-08-10 15:33 | 2026-08-10 17:54 | 2026-08-10 17:54 | 2026-08-10 17:54 | 2026-08-10 19:20 | 2026-08-10 19:23 | 2026-08-10 19:23 |  |  | Fair | No | 50kva transformer at pole#624625 had burnt & corroded connections, transformer was de-energized, used two 2/0 -2/0 and one 2/0-#2 ampact for repairs, transformer was re-energized, area now okay.
Outage | J.E.26.08.13206 | C001884386 | Richard Watson | St.Elizabeth | Completed | Load_247893 | Maggotty - 210 | 2026-08-10 15:32 | 2026-08-10 15:33 | 2026-08-10 17:23 | 2026-08-10 17:24 | 2026-08-10 17:37 | 2026-08-10 17:45 | 2026-08-10 17:49 | 2026-08-10 17:49 |  |  | Fair | No | Found ok, meter found displaying voltage found in meter socket 110v, 111v, 221v, customer not at premises at time of visit.
Outage | J.E.26.08.14041 | C001884384 | Christopher West | St.Catherine | Completed | Load_260827 | Twickenham - 210 | 2026-08-10 15:32 | 2026-08-10 15:33 | 2026-08-10 15:45 | 2026-08-10 16:08 | 2026-08-10 16:38 | 2026-08-10 16:53 | 2026-08-10 16:54 | 2026-08-10 16:54 |  |  | Fair | No | Premises found closed at time of visit however kwh meter is energized and registering.
Outage | J.E.26.08.14109 | C001884385 | Richard Watson | St.Elizabeth | Completed | Load_249737 | Maggotty - 210 | 2026-08-10 15:32 | 2026-08-10 15:33 | 2026-08-10 17:59 | 2026-08-10 18:00 | 2026-08-10 18:25 | 2026-08-10 18:28 | 2026-08-10 18:28 | 2026-08-10 18:28 |  |  | Fair | No | Found okay, supply found at premises.
Outage | J.E.26.08.13789 | C001884394 | Barnett Brown | Manchester | Completed | Load_268774 | Kendal - 210 | 2026-08-10 15:34 | 2026-08-10 18:16 | 2026-08-10 18:58 | 2026-08-10 18:59 | 2026-08-10 19:17 | 2026-08-10 19:17 | 2026-08-10 19:20 | 2026-08-10 19:20 |  |  | Fair | No
Outage | J.E.26.08.13659 | C001884395 | Fitzroy Turner | KSAS | Completed | Load_260446 | Hunts Bay - 310 | 2026-08-10 15:35 | 2026-08-10 15:42 | 2026-08-10 19:38 | 2026-08-10 20:07 | 2026-08-10 20:43 | 2026-08-10 21:52 | 2026-08-10 21:52 | 2026-08-10 21:52 |  |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.08.14169 | C001884396 | Romeo Brissett | Trelawny | Completed | Load_245327 | Duncans - 210 | 2026-08-10 15:35 | 2026-08-10 15:35 | 2026-08-10 17:34 | 2026-08-10 17:34 | 2026-08-10 17:50 | 2026-08-10 18:50 | 2026-08-10 18:54 | 2026-08-10 18:54 |  |  | Fair | No | Removed bird and replaced (1)8amps junction and (1)10KVA transformer fuse
Outage | J.E.26.08.14193 | C001884397 | Radcliffe Coleman | St.Catherine | Completed | Load_569944 | Twickenham - 410 | 2026-08-10 15:36 | 2026-08-10 15:36 | 2026-08-10 15:45 | 2026-08-10 18:31 | 2026-08-10 18:31 | 2026-08-10 18:31 | 2026-08-10 18:31 | 2026-08-10 18:31 |  |  | Fair | No | Location found with a bank of three transformer (3-100kva) with one of the drop leads burnt. Repairs were done with aid of one ampact and approximately four feet of #4 copper. The bank was isolated before repairs were done. Location now back to normal.
Outage | J.E.26.08.13779 | C001884398 | Barnett Brown | Manchester | Completed | Load_240486 | Kendal - 210 | 2026-08-10 15:37 | 2026-08-10 15:37 | 2026-08-10 17:40 | 2026-08-10 17:40 | 2026-08-10 18:32 | 2026-08-10 18:48 | 2026-08-10 18:49 | 2026-08-10 18:49 |  |  | Rains | No
Outage | J.E.26.08.13871 | C001884409 | Damion Reid | Manchester | Completed | Load_238024 | Kendal - 210 | 2026-08-10 15:39 | 2026-08-10 15:39 | 2026-08-10 16:34 | 2026-08-10 16:35 | 2026-08-10 17:16 | 2026-08-10 17:47 | 2026-08-10 17:50 | 2026-08-10 17:50 |  |  | Rains | No | Blown 50Amp junction fuse found cause by lightning line patrol and replace blown fuse
Outage | J.E.26.08.14149 | C001884412 | Dwayne Cohen | KSAN | Completed | Load_251645 | Washington Blvd - 710 | 2026-08-10 15:39 | 2026-08-10 15:40 | 2026-08-10 15:53 | 2026-08-10 15:54 | 2026-08-10 16:23 | 2026-08-10 16:23 | 2026-08-10 16:25 | 2026-08-10 16:25 | TreeContact |  | Fair | No | Over grown mango tree , secondary vegetation needed ASAP . Please this report to the relevant department.
Outage | J.E.26.08.14215 | C001884411 | Milton Charlton | KSAS | Completed | Load_255821 | Up Park Camp - 410 | 2026-08-10 15:39 | 2026-08-10 16:07 | 2026-08-10 16:57 | 2026-08-10 16:58 | 2026-08-10 17:46 | 2026-08-10 17:35 | 2026-08-10 17:48 | 2026-08-10 17:48 |  |  | Fair | No | Found okay upon arrival. Readings at meter socket 118-118-236 volts. Customer has an internal problem.
Outage | J.E.26.08.14219 | C001884413 | Milton Charlton | KSAN | Completed | Load_239828 | Hope - 510 | 2026-08-10 15:39 | 2026-08-10 16:06 | 2026-08-10 19:12 | 2026-08-10 19:12 | 2026-08-10 19:46 | 2026-08-10 19:40 | 2026-08-10 19:47 | 2026-08-10 19:47 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.14240 | C001884414 | Barnett Brown | Manchester | Completed | Load_246031 | Spur Tree - 310 | 2026-08-10 15:40 | 2026-08-10 15:41 | 2026-08-10 15:50 | 2026-08-10 15:50 | 2026-08-10 17:16 | 2026-08-10 17:38 | 2026-08-10 17:39 | 2026-08-10 17:39 |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.08.13651 | C001884418 | Fitzroy Turner |  | Completed |  |  | 2026-08-10 15:41 | 2026-08-10 15:42 | 2026-08-10 18:59 | 2026-08-10 18:59 | 2026-08-10 19:00 | 2026-08-10 19:01 | 2026-08-10 19:02 | 2026-08-10 19:02 |  |  | Fair | No | Found tree wire service neutral wire burnt of at pole use two one bolt clamps to carry out repair supply restored to customer
Non-Outage | J.E.26.08.13707 | C001884415 | Fitzroy Turner |  | Completed |  |  | 2026-08-10 15:41 | 2026-08-10 15:42 | 2026-08-10 21:53 | 2026-08-10 21:53 | 2026-08-10 21:53 | 2026-08-10 21:53 | 2026-08-10 21:54 | 2026-08-10 21:54 |  |  | Fair | No | Found 5 kva transformer drop leads burnt off at transformer pole use two one bolt clamps to carry out repair supply restored to customer
Outage | J.E.26.08.14197 | C001884417 | Fitzroy Turner | KSAS | Completed | Load_248716 | Up Park Camp - 510 | 2026-08-10 15:41 | 2026-08-10 15:42 | 2026-08-10 19:08 | 2026-08-10 19:09 | 2026-08-10 19:33 | 2026-08-10 19:34 | 2026-08-10 19:35 | 2026-08-10 19:35 |  |  | Fair | No | Found 25kva transformer trip have transformer reset supply restored to the areas
Outage | J.E.26.08.14265 | C001884416 | Fitzroy Turner | KSAS | Completed | Load_251380 | Up Park Camp - 510 | 2026-08-10 15:41 | 2026-08-10 15:42 | 2026-08-10 19:36 | 2026-08-10 19:36 | 2026-08-10 20:05 | 2026-08-10 20:06 | 2026-08-10 20:06 | 2026-08-10 20:06 |  |  | Fair | No | Customer premises found with electricity supply
Non-Outage | J.E.26.08.13534 | C001884420 | Barnett Brown | Manchester | Completed | Load_257171 | Spur Tree - 310 | 2026-08-10 15:42 | 2026-08-10 15:43 | 2026-08-10 20:41 | 2026-08-10 20:41 | 2026-08-10 22:15 | 2026-08-10 22:15 | 2026-08-10 22:17 | 2026-08-10 22:17 |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.08.04891 | C001884422 | Edward Royal | KSAS | Completed | Load_300789 | Greenwich - 510 | 2026-08-10 15:43 | 2026-08-10 15:46 | 2026-08-11 09:24 | 2026-08-11 09:25 | 2026-08-11 09:25 | 2026-08-11 09:25 | 2026-08-11 09:25 | 2026-08-11 09:25 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.14226 | C001884429 | Marlon Authors | Manchester | Completed | Load_292938 | Spur Tree - 210 | 2026-08-10 15:43 | 2026-08-10 15:44 | 2026-08-10 22:14 | 2026-08-10 22:15 | 2026-08-10 22:21 | 2026-08-10 22:22 | 2026-08-10 22:22 | 2026-08-10 22:22 |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.08.13604 | C001884430 | Roxroy Needham | St.Ann | Completed | Load_241183 | Cardiff Hall - 210 | 2026-08-10 15:44 | 2026-08-10 15:45 | 2026-08-10 21:50 | 2026-08-10 21:51 | 2026-08-10 22:41 | 2026-08-10 22:41 | 2026-08-10 22:45 | 2026-08-10 22:45 | BrokenWire |  | Fair | No | Premises found ok customer say that JPS team come before
Outage | J.E.26.08.14101 | C001884431 | Javid Vernon | Westmoreland | Completed | Load_265015 | Paradise - 210 | 2026-08-10 15:44 | 2026-08-10 15:45 | 2026-08-10 17:36 | 2026-08-10 17:36 | 2026-08-10 17:36 | 2026-08-10 17:37 | 2026-08-10 17:37 | 2026-08-10 17:37 |  |  | Fair | No | Related to previous call job # 14144
Outage | J.E.26.08.14144 | C001884432 | Javid Vernon | Westmoreland | Completed | Load_253691 | Paradise - 210 | 2026-08-10 15:44 | 2026-08-10 15:45 | 2026-08-10 16:39 | 2026-08-10 16:40 | 2026-08-10 17:14 | 2026-08-10 17:35 | 2026-08-10 17:35 | 2026-08-10 17:35 |  |  | Fair | No | Refuse one 8amp junction fuse
Non-Outage | J.E.26.07.39593 | C001884448 | Roxroy Needham | St.Ann | Completed | Load_1003802 | Cardiff Hall - 210 | 2026-08-10 15:45 | 2026-08-10 15:46 | 2026-08-10 19:20 | 2026-08-10 19:20 | 2026-08-10 19:56 | 2026-08-10 19:58 | 2026-08-10 19:59 | 2026-08-10 19:59 |  |  | Fair | No | Customer state that, the call is In Kingston
Non-Outage | J.E.26.07.40112 | C001884442 | Edward Royal | KSAN | Completed | Load_265054 | Washington Blvd - 710 | 2026-08-10 15:45 | 2026-08-10 15:46 | 2026-08-10 16:36 | 2026-08-10 16:36 | 2026-08-10 16:36 | 2026-08-10 18:20 | 2026-08-10 18:22 | 2026-08-10 18:22 |  |  | Fair | No | Spliced and reconnected drop lead to secondary line using 3 am pack before reading at the drop lead 228 115 114 and at the end of the line 204 101 106 after repaired voltage reading 240 120 120 v at the end of the line 107 108 215 v
Non-Outage | J.E.26.08.00042 | C001884441 | Edward Royal | KSAN | Completed | Load_265054 | Washington Blvd - 710 | 2026-08-10 15:45 | 2026-08-10 15:46 | 2026-08-10 18:23 | 2026-08-10 18:23 | 2026-08-10 18:23 | 2026-08-10 18:23 | 2026-08-10 18:23 | 2026-08-10 18:23 |  |  | Fair | No | Premises found ok related to outage
Non-Outage | J.E.26.08.03493 | C001884440 | Edward Royal | KSAN | Completed | Load_265054 | Washington Blvd - 710 | 2026-08-10 15:45 | 2026-08-10 15:46 | 2026-08-10 18:23 | 2026-08-10 18:24 | 2026-08-10 18:23 | 2026-08-10 18:24 | 2026-08-10 18:24 | 2026-08-10 18:24 |  |  | Fair | No | Premises found ok related to outage
Non-Outage | J.E.26.08.03708 | C001884438 | Edward Royal | KSAN | Completed | Load_265054 | Washington Blvd - 710 | 2026-08-10 15:45 | 2026-08-10 15:46 | 2026-08-10 18:25 | 2026-08-10 18:25 | 2026-08-10 18:25 | 2026-08-10 18:25 | 2026-08-10 18:25 | 2026-08-10 18:25 |  |  | Fair | No | Call related
Non-Outage | J.E.26.08.05908 | C001884437 | Edward Royal | KSAN | Completed | Load_265054 | Washington Blvd - 710 | 2026-08-10 15:45 | 2026-08-10 15:46 | 2026-08-10 18:25 | 2026-08-10 18:26 | 2026-08-10 18:25 | 2026-08-10 18:26 | 2026-08-10 18:26 | 2026-08-10 18:26 |  |  | Fair | No | Premises found ok related to outage
Non-Outage | J.E.26.08.11244 | C001884436 | Oraine Minto | St.Ann | Completed | Load_1007080 | Cardiff Hall - 210 | 2026-08-10 15:45 | 2026-08-11 08:12 | 2026-08-11 11:24 | 2026-08-11 11:25 | 2026-08-11 11:24 | 2026-08-11 11:25 | 2026-08-11 11:26 | 2026-08-11 11:26 |  |  | Fair | No | Customer states that a team came by and from that the issue was fixed
Non-Outage | J.E.26.08.13595 | C001884433 | Roxroy Needham | St.Ann | Completed | Load_258465 | Cardiff Hall - 210 | 2026-08-10 15:45 | 2026-08-10 15:45 | 2026-08-10 22:45 | 2026-08-10 22:49 | 2026-08-10 22:49 | 2026-08-10 22:49 | 2026-08-10 22:51 | 2026-08-10 22:51 | Fire |  | Fair | No | Pre Found ok customer say that JPS team come before
Outage | J.E.26.08.13606 | C001884435 | Javid Vernon | Westmoreland | Completed | Load_264370 | Paradise - 210 | 2026-08-10 15:45 | 2026-08-10 15:45 | 2026-08-10 15:51 | 2026-08-10 15:52 | 2026-08-10 16:11 | 2026-08-10 16:39 | 2026-08-10 16:39 | 2026-08-10 16:39 |  |  | Fair | No | Clean and remake joints at customer pothead voltage found 110/74/184 voltage left 114/112/226
Outage | J.E.26.08.13993 | C001884434 | Javid Vernon | Westmoreland | Completed | Load_240446 | Paradise - 310 | 2026-08-10 15:45 | 2026-08-10 15:45 | 2026-08-10 18:13 | 2026-08-10 18:14 | 2026-08-10 18:13 | 2026-08-10 18:13 | 2026-08-10 18:14 | 2026-08-10 18:14 |  |  | Fair | No | Customer stated that the power was restored
Outage | J.E.26.08.14291 | C001884444 | Oshane Warren | Westmoreland | Completed | Load_253762 | Paradise - 310 | 2026-08-10 15:45 | 2026-08-10 15:46 | 2026-08-10 17:32 | 2026-08-10 17:33 | 2026-08-10 18:13 | 2026-08-10 18:14 | 2026-08-10 18:17 | 2026-08-10 18:17 |  |  | Rains | No | Need 100 ft of number 6twisted to carry out reconnection
Non-Outage | J.E.26.04.01803 | C001884449 | Romeo Brissett |  | Completed |  |  | 2026-08-10 15:46 | 2026-08-10 15:48 | 2026-08-10 20:34 | 2026-08-10 20:35 | 2026-08-10 21:49 | 2026-08-10 22:20 | 2026-08-10 22:40 | 2026-08-10 22:40 | LeaningPole |  | Fair | No | Found (1)35ft pole leaning with single phase primary and twisted service wires.
Non-Outage | J.E.26.04.08605 | C001884450 | Romeo Brissett | St.James | Completed | Load_557032 | Bogue - 310 | 2026-08-10 15:46 | 2026-08-10 15:48 | 2026-08-10 20:02 | 2026-08-10 20:03 | 2026-08-10 20:02 | 2026-08-10 20:28 | 2026-08-10 20:34 | 2026-08-10 20:34 | LeaningPole |  | Fair | No | Spliced and retention customer service, used 30ft of #2 and 1 clamp V/R 113-113-227
Non-Outage | J.E.26.04.30709 | C001884451 | Romeo Brissett | St.James | Completed | Load_256318 | Bogue - 310 | 2026-08-10 15:47 | 2026-08-10 15:48 | 2026-08-11 01:24 | 2026-08-11 01:24 | 2026-08-11 05:32 | 2026-08-11 06:16 | 2026-08-11 06:18 | 2026-08-11 06:18 | LeaningPole |  | Fair | No | Found (1)35ft pole leaning with single phase Primary and down guy and one T pole leaning. Urgently need to be straighten. Please send to maintenance
Non-Outage | J.E.26.08.13639 | C001884454 | Richard Watson | St.Elizabeth | Completed | Load_569165 | Maggotty - 210 | 2026-08-10 15:48 | 2026-08-10 15:49 | 2026-08-10 16:06 | 2026-08-10 16:07 | 2026-08-10 16:55 | 2026-08-10 17:16 | 2026-08-10 17:20 | 2026-08-10 17:20 |  |  | Fair | No | Voltage found at metering point 227v, 230v, 231v, phase to neutral and 395v, 396v, 403v, suspected cause primary line experiencing low voltage.
Non-Outage | J.E.26.08.14083 | C001884455 | Richard Watson | St.Elizabeth | Completed | Load_252693 | Maggotty - 210 | 2026-08-10 15:48 | 2026-08-10 15:49 | 2026-08-10 18:28 | 2026-08-10 18:28 | 2026-08-10 19:06 | 2026-08-10 19:17 | 2026-08-10 19:22 | 2026-08-10 19:22 |  |  | Fair | No | Meter socket terminal burnt on loadside due to defective meter socket, which is already replaced, please refer to Field service department to have meter replaced, (200amp 3wire 240v meter).
Outage | J.E.26.08.14204 | C001884456 | Richard Nicholas | St.Catherine | Completed | Load_243118 | Rhodens Pen - 410 | 2026-08-10 15:50 | 2026-08-11 08:37 | 2026-08-11 10:56 | 2026-08-11 10:56 | 2026-08-11 11:14 | 2026-08-11 11:33 | 2026-08-11 11:34 | 2026-08-11 11:34 |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.06.34731 | C001884457 | Romeo Brissett |  | Completed |  |  | 2026-08-10 15:51 | 2026-08-10 15:54 | 2026-08-10 18:54 | 2026-08-10 18:55 | 2026-08-10 19:44 | 2026-08-10 19:40 | 2026-08-10 20:02 | 2026-08-10 20:02 | BrokenPole |  | Fair | No | Line patrolled no broken pole found resident stated pole has been changed.
Non-Outage | J.E.26.03.13769 | C001884458 | Romeo Brissett | St.James | Completed | Load_261720 | Queens Drive - 710 | 2026-08-10 15:59 | 2026-08-10 16:00 | 2026-08-10 23:12 | 2026-08-10 23:12 | 2026-08-11 | 2026-08-11 23:43 | 2026-08-11 00:38 | 2026-08-11 00:38 |  |  | Fair | No | Customer stated he’s only getting 110-220, Found 2/0 quad however only one transformer on pole supplying secondary, found (1)25 kva transformer need another transformer to supply 3 phases circuit, please send to maintenance.
Non-Outage | J.E.26.08.07017 | C001884460 | Barrington Brown | St.James | Completed | Load_253376 | Bogue - 310 | 2026-08-10 16:03 | 2026-08-10 16:04 | 2026-08-10 18:34 | 2026-08-10 20:45 | 2026-08-10 21:39 | 2026-08-10 21:39 | 2026-08-10 21:39 | 2026-08-10 21:39 |  |  | Fair | No | Checked and found ok
Non-Outage | J.E.26.08.14307 | C001884461 | Dwayne Cohen |  | Completed |  |  | 2026-08-10 16:03 | 2026-08-10 16:04 | 2026-08-10 16:55 | 2026-08-10 16:55 | 2026-08-10 17:34 | 2026-08-10 17:34 | 2026-08-10 17:36 | 2026-08-10 17:36 | BrokenPole |  | Fair | No | Customer Hexing meter reconnect by call center representative, supply now restore.
Non-Outage | J.E.26.07.23969 | C001884463 | Vivian Gordon | St.James | Completed | Load_556943 | Bogue - 310 | 2026-08-10 16:05 | 2026-08-10 16:07 | 2026-08-11 14:48 | 2026-08-11 14:49 | 2026-08-11 14:49 | 2026-08-11 14:49 | 2026-08-11 14:51 | 2026-08-11 14:51 |  |  | Fair | No | Several calls to customer went unanswered, premises visited and supply found ok
Non-Outage | J.E.26.07.15680 | C001884464 | Vivian Gordon | St.James | Completed | Load_249504 | Bogue - 310 | 2026-08-10 16:06 | 2026-08-10 16:07 | 2026-08-11 14:14 | 2026-08-11 14:14 | 2026-08-11 14:14 | 2026-08-11 13:40 | 2026-08-11 14:17 | 2026-08-11 14:17 |  |  | Fair | No | Customer was contacted and customer reply everything ok and a technician visited the premises before already
Non-Outage | J.E.26.08.13416 | C001884465 | Milton Charlton | KSAN | Completed | Load_261011 | Hope - 510 | 2026-08-10 16:09 | 2026-08-10 16:10 | 2026-08-10 17:49 | 2026-08-10 17:50 | 2026-08-10 19:09 | 2026-08-10 19:10 | 2026-08-10 19:12 | 2026-08-10 19:12 |  |  | Fair | No | Customer service wire #6 triplex neutral corroded at pole repair using two 1- bolt clamps. Readings at meter socket 115-116-234 volts.
Non-Outage | J.E.26.08.14206 | C001884466 | Milton Charlton | KSAN | Completed | Load_239828 | Hope - 510 | 2026-08-10 16:09 | 2026-08-10 16:09 | 2026-08-10 19:47 | 2026-08-10 19:47 | 2026-08-10 20:06 | 2026-08-10 20:05 | 2026-08-10 20:08 | 2026-08-10 20:08 |  |  | Fair | No | Call duplicated.
Non-Outage | J.E.26.08.14214 | C001884495 | Derrick Grubb |  | Completed |  |  | 2026-08-10 16:18 | 2026-08-10 16:19 | 2026-08-10 19:46 | 2026-08-10 19:46 | 2026-08-10 19:46 | 2026-08-10 19:47 | 2026-08-10 19:47 | 2026-08-10 19:47 | Fire |  | Fair | No | Splice and retention two span open secondary neutral, reset 10 kva transformer at pole number 037250
Outage | J.E.26.08.13339 | C001884479 | Derrick Grubb | St.Thomas | Completed | Load_243122 | Lysson - 410 | 2026-08-10 16:18 | 2026-08-10 16:19 | 2026-08-10 22:53 | 2026-08-10 22:54 | 2026-08-10 22:53 | 2026-08-10 22:54 | 2026-08-10 22:54 | 2026-08-10 22:54 | BrokenWire |  | Fair | No | Fallen pole refer to the maintenance team
Outage | J.E.26.08.14341 | C001884480 | Derrick Grubb | St.Thomas | Completed | Load_243122 | Lysson - 410 | 2026-08-10 16:18 | 2026-08-10 16:19 | 2026-08-10 22:16 | 2026-08-10 22:17 | 2026-08-10 22:52 | 2026-08-10 22:52 | 2026-08-10 22:53 | 2026-08-10 22:53 |  |  | Fair | No | Fallen pole refer to the maintenance team
Outage | J.E.26.08.14336 | C001884516 | Horace Malcolm | St.James | Completed | Load_254670 | Bogue - 510 | 2026-08-10 16:33 | 2026-08-10 16:40 | 2026-08-10 20:56 | 2026-08-10 20:57 | 2026-08-10 21:36 | 2026-08-10 21:49 | 2026-08-10 21:49 | 2026-08-10 21:49 |  |  | Fair | No | Customer go disconnected however customer pay bill and need to get connected call to call center customer got physically disconnected locking band on meter field service required to reconnect customer
Non-Outage | J.E.26.08.14345 | C001884533 | Andre Williams |  | Completed |  |  | 2026-08-10 16:41 | 2026-08-10 16:42 | 2026-08-10 20:10 | 2026-08-10 20:13 | 2026-08-10 20:14 | 2026-08-10 20:32 | 2026-08-10 20:32 | 2026-08-10 20:32 |  |  | Fair | No | Customer reconnected with the help of meter center
Outage | J.E.26.08.14250 | C001884541 | Gregory Grossett | Portland | Completed | Load_574173 | Port Antonio - 410 | 2026-08-10 16:55 | 2026-08-10 17:12 | 2026-08-10 18:52 | 2026-08-10 18:53 | 2026-08-10 19:53 | 2026-08-10 19:51 | 2026-08-10 19:58 | 2026-08-10 19:58 |  |  | Fair | No | 3 phase supply was disconnected in meter socket, remove seals and reconnect customer supply, voltage left 120-120-210,240,240,242 volts
Outage | J.E.26.08.14358 | C001884551 | Milton Charlton | KSAN | Completed | Load_301568 | Constant Spring - 310 | 2026-08-10 17:09 | 2026-08-10 17:11 | 2026-08-10 20:10 | 2026-08-10 20:10 | 2026-08-10 21:12 | 2026-08-10 20:50 | 2026-08-10 21:14 | 2026-08-10 21:14 |  |  | Fair | No | Unable to locate customer by telephone. Number on the report going straight to voicemail.
Outage | J.E.26.08.14365 | C001884550 | Dwayne Cohen | KSAN | Completed | Load_244504 | Washington Blvd - 610 | 2026-08-10 17:09 | 2026-08-10 17:11 | 2026-08-10 17:37 | 2026-08-10 17:37 | 2026-08-10 18:15 | 2026-08-10 18:30 | 2026-08-10 18:30 | 2026-08-10 18:30 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.14404 | C001884549 | Dwayne Cohen | KSAN | Completed | Load_406051 | Constant Spring - 410 | 2026-08-10 17:09 | 2026-08-10 17:10 | 2026-08-10 18:31 | 2026-08-10 18:32 | 2026-08-10 19:46 | 2026-08-10 19:59 | 2026-08-10 19:59 | 2026-08-10 19:59 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.14379 | C001884552 | Oshane Warren | Westmoreland | Completed | Load_240446 | Paradise - 310 | 2026-08-10 17:28 | 2026-08-10 17:29 | 2026-08-10 18:23 | 2026-08-10 18:23 | 2026-08-10 18:46 | 2026-08-10 19:06 | 2026-08-10 19:45 | 2026-08-10 19:45 | BrokenWire |  | Rains | No | Truck hitch 2/0 conductor and damage one pole span 2/0 conductor isolated one pole span 2/0 conductor and reset 25 kva transformer no customer was left with out power
Outage | J.E.26.08.14304 | C001884555 | Barnett Brown | Manchester | Completed | Load_248836 | Spur Tree - 310 | 2026-08-10 17:29 | 2026-08-10 17:30 | 2026-08-10 19:20 | 2026-08-10 19:21 | 2026-08-10 19:47 | 2026-08-10 20:35 | 2026-08-10 20:39 | 2026-08-10 20:39 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Balance 2 span secondary neutral
Outage | J.E.26.08.14434 | C001884560 | Derrick Grubb | St.Thomas | Completed | Load_245249 | Lysson - 410 | 2026-08-10 17:39 | 2026-08-10 17:42 | 2026-08-10 20:57 | 2026-08-10 20:57 | 2026-08-10 21:24 | 2026-08-10 21:24 | 2026-08-10 21:25 | 2026-08-10 21:25 |  |  | Fair | No | Meter turn on with the assistance of the call center
Outage | J.E.26.08.14343 | C001884568 | Wan Carlos Scarlett | St.Catherine | Completed | Load_269220 | Twickenham - 410 | 2026-08-10 17:55 | 2026-08-11 07:45 | 2026-08-11 08:06 | 2026-08-11 08:06 | 2026-08-11 08:58 | 2026-08-11 10:29 | 2026-08-11 10:34 | 2026-08-11 10:34 |  |  | Fair | No | Found a set of bank of 3 transformer with 1 of the 100 KVA transformer defective no pole # was found transformers were isolated
Outage | J.E.26.08.14406 | C001884571 | Roxroy Needham | St.Ann | Completed | Load_239026 | Roaring River - 210 | 2026-08-10 18:12 | 2026-08-11 08:46 | 2026-08-11 09:37 | 2026-08-11 09:37 | 2026-08-11 10:50 | 2026-08-11 10:52 | 2026-08-11 10:52 | 2026-08-11 10:52 |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.08.14452 | C001884573 | Edward Royal | KSAN | Completed | Load_248819 | Washington Blvd - 310 | 2026-08-10 18:16 | 2026-08-10 18:20 | 2026-08-10 20:22 | 2026-08-10 20:22 | 2026-08-10 20:22 | 2026-08-10 20:23 | 2026-08-10 20:23 | 2026-08-10 20:23 |  |  | Fair | No | Premises found ok related to outage
Non-Outage | J.E.26.08.14395 | C001884578 | Andre Williams | Trelawny | Completed | Load_255254 | Duncans - 110 | 2026-08-10 18:17 | 2026-08-10 18:18 | 2026-08-10 18:25 | 2026-08-10 18:26 | 2026-08-10 19:03 | 2026-08-10 19:49 | 2026-08-10 19:50 | 2026-08-10 19:50 |  |  | Fair | No | No visible fault seen on 2naut twisted voltage at transformer 120+120=240 after 3 pole span, voltage fluctuating between 125 and 127 on one phase and other phase dropping to 90 and back to 118, potheads on line sections check out, reffer daylight attention to check customer meters ( call incomplete)
Outage | J.E.26.08.14355 | C001884577 | Edward Royal | KSAN | Completed | Load_268534 | Washington Blvd - 310 | 2026-08-10 18:17 | 2026-08-10 18:20 | 2026-08-10 18:27 | 2026-08-10 18:28 | 2026-08-10 18:28 | 2026-08-10 18:28 | 2026-08-10 18:28 | 2026-08-10 18:28 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.14405 | C001884576 | Edward Royal | KSAN | Completed | Load_249587 | Washington Blvd - 310 | 2026-08-10 18:17 | 2026-08-10 18:20 | 2026-08-10 18:49 | 2026-08-10 18:50 | 2026-08-10 18:49 | 2026-08-10 20:16 | 2026-08-10 20:21 | 2026-08-10 20:21 |  |  | Fair | No | Spliced and reconnected primary jumper using 1 single bolt clamp
Outage | J.E.26.08.14487 | C001884575 | Edward Royal | KSAN | Completed | Load_266260 | Washington Blvd - 310 | 2026-08-10 18:17 | 2026-08-10 18:20 | 2026-08-10 20:21 | 2026-08-10 20:22 | 2026-08-10 20:21 | 2026-08-10 20:22 | 2026-08-10 20:22 | 2026-08-10 20:22 |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.08.14133 | C001884584 | Richard Watson | St.Elizabeth | Completed | Load_262973 | Maggotty - 110 | 2026-08-10 18:34 | 2026-08-10 18:35 | 2026-08-10 21:42 | 2026-08-10 21:43 | 2026-08-10 22:07 | 2026-08-10 22:15 | 2026-08-10 22:15 | 2026-08-10 22:15 |  |  | Fair | No | Unable to reach customer by phone or locate customer premises.
Non-Outage | J.E.26.08.14354 | C001884585 | Marlon Authors |  | Completed |  |  | 2026-08-10 18:35 | 2026-08-10 18:37 | 2026-08-10 19:37 | 2026-08-10 19:38 | 2026-08-10 20:24 | 2026-08-10 20:48 | 2026-08-10 20:48 | 2026-08-10 20:48 |  |  | Fair | No | Supply checked and found low voltage rdg 105v,106v and cross phased 211 volts. Isolate and close 25 kva transformer circuit no pole # to tap up transformer to tap 5. Supply leave working ok rdg 111v,111v and cross phased 222 volts
Outage | J.E.26.08.14332 | C001884602 | Hartley Chin | Clarendon | Completed | Load_252936 | Parnassus - 310 | 2026-08-10 18:42 | 2026-08-10 18:43 | 2026-08-10 20:54 | 2026-08-10 20:55 | 2026-08-10 21:49 | 2026-08-10 21:49 | 2026-08-10 21:51 | 2026-08-10 21:48 | LeaningPole |  | Fair | No | Ref to maintenance found 3 leaning 35ft pole along rose well rd. Did not get customer but found 3 35ft pole leaning.
Outage | J.E.26.08.14459 | C001884604 | Hartley Chin | Clarendon | Completed | Load_244642 | May Pen - 210 | 2026-08-10 18:42 | 2026-08-10 18:43 | 2026-08-10 18:51 | 2026-08-10 18:51 | 2026-08-10 19:16 | 2026-08-10 19:25 | 2026-08-10 19:26 | 2026-08-10 19:26 | BrokenWire |  | Fair | No | Repair broken joint on service wire 116v 115v 230v
Outage | J.E.26.08.14525 | C001884603 | Hartley Chin | Clarendon | Completed | Load_242545 | Parnassus - 210 | 2026-08-10 18:42 | 2026-08-10 18:43 | 2026-08-10 19:26 | 2026-08-10 19:26 | 2026-08-10 20:50 | 2026-08-10 20:51 | 2026-08-10 20:54 | 2026-08-10 20:54 |  |  | Fair | No | Un able to contact customer Unable to find meter or polePatrolled second and third hill and still unable to find meter pole for connection.
Outage | J.E.26.08.14113 | C001884606 | Richard Watson | St.Elizabeth | Completed | Load_253396 | Maggotty - 110 | 2026-08-10 18:45 | 2026-08-10 18:46 | 2026-08-10 19:30 | 2026-08-10 19:31 | 2026-08-10 21:00 | 2026-08-10 21:15 | 2026-08-10 21:17 | 2026-08-10 21:17 |  |  | Fair | No | Found okay, premises found okay.
Outage | J.E.26.08.14357 | C001884607 | Damion Reid | Manchester | Completed | Load_242522 | Kendal - 210 | 2026-08-10 18:50 | 2026-08-10 18:50 | 2026-08-10 19:19 | 2026-08-10 19:19 | 2026-08-10 19:43 | 2026-08-10 20:02 | 2026-08-10 20:04 | 2026-08-10 20:04 |  |  | Rains | No | Blown 10amp junction found cause by lightning line patrol and replace blown fuse
Outage | J.E.26.08.14174 | C001884611 | Damion Reid | Manchester | Completed | Load_239382 | Kendal - 210 | 2026-08-10 18:53 | 2026-08-10 18:54 | 2026-08-10 20:06 | 2026-08-10 20:07 | 2026-08-10 20:35 | 2026-08-10 21:09 | 2026-08-10 21:09 | 2026-08-10 21:09 |  |  | Rains | No | Area found ok
Outage | J.E.26.08.14529 | C001884612 | Derrick Grubb | St.Thomas | Completed | Load_269082 | Lysson - 410 | 2026-08-10 18:55 | 2026-08-10 18:56 | 2026-08-10 21:28 | 2026-08-10 21:29 | 2026-08-10 21:47 | 2026-08-10 21:48 | 2026-08-10 21:48 | 2026-08-10 21:48 | LeaningPole |  | Fair | No | Premises not located and several calls to customer went unanswered
Outage | J.E.26.08.14546 | C001884617 | Fitzroy Turner | KSAN | Completed | Load_237915 | West Kings House - 410 | 2026-08-10 19:12 | 2026-08-10 21:15 | 2026-08-10 21:58 | 2026-08-10 21:58 | 2026-08-10 22:24 | 2026-08-10 22:24 | 2026-08-10 22:25 | 2026-08-10 22:25 |  |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.08.14549 | C001884624 | Tyrese Williams | St.Ann | Completed | Load_241195 | Cardiff Hall - 310 | 2026-08-10 19:26 | 2026-08-11 10:17 | 2026-08-11 10:35 | 2026-08-11 11:32 | 2026-08-11 11:32 | 2026-08-11 11:33 | 2026-08-11 11:34 | 2026-08-11 11:34 |  |  | Fair | No | Replace a 25 kva transformer fuse with a 3 amp at pole
Outage | J.E.26.08.14618 | C001884627 | Barrington Brown | St.James | Completed | Load_293503 | Queens Drive - 310 | 2026-08-10 19:29 | 2026-08-10 19:32 | 2026-08-10 20:42 | 2026-08-10 20:43 | 2026-08-10 20:42 | 2026-08-10 20:44 | 2026-08-10 20:44 | 2026-08-10 20:44 |  |  | Fair | No | Crew found two corroded joints at customer pothead. Crew corrected joints using 2 one bolt clamps. Customer full supply restored 119 119 239
Non-Outage | J.E.26.08.07650 | C001884628 | Roxroy Needham | St.Ann | Completed | Load_268918 | Cardiff Hall - 210 | 2026-08-10 19:30 | 2026-08-10 19:31 | 2026-08-10 20:50 | 2026-08-10 20:51 | 2026-08-10 21:31 | 2026-08-10 21:50 | 2026-08-10 21:50 | 2026-08-10 21:50 |  |  | Fair | No | Remake joint at pole and pothead used 4 pg clamp voltage left at meter
Non-Outage | J.E.26.08.07866 | C001884629 | Daniel Francis | St.Ann | Completed | Load_264096 | Roaring River - 410 | 2026-08-10 19:30 | 2026-08-10 19:32 | 2026-08-10 22:06 | 2026-08-10 22:07 | 2026-08-10 22:26 | 2026-08-10 22:26 | 2026-08-10 22:27 | 2026-08-10 22:27 |  |  | Fair | No | Not Found customer not answering phone
Non-Outage | J.E.26.08.14183 | C001884633 | Evan Spaulding |  | Completed |  |  | 2026-08-10 20:03 | 2026-08-10 20:05 | 2026-08-10 20:59 | 2026-08-10 20:59 | 2026-08-10 21:51 | 2026-08-10 22:04 | 2026-08-10 22:06 | 2026-08-10 22:06 |  |  | Fair | No | Customer was getting 130v,126v,Tap down 10kva Transformer from position 5 to position 3, voltage left 120v,120v,240v.
Outage | J.E.26.08.14398 | C001884634 | Evan Spaulding | St.Mary | Completed | Load_354661 | Oracabessa - 110 | 2026-08-10 20:03 | 2026-08-10 20:04 | 2026-08-10 20:17 | 2026-08-10 20:17 | 2026-08-10 20:22 | 2026-08-10 20:55 | 2026-08-10 20:56 | 2026-08-10 20:56 |  |  | Fair | No | Patrol line section not fault seen,replace 1-20 amps junction fuse at pole number 005180.
Outage | J.E.26.08.14541 | C001884635 | Evan Spaulding | St.Mary | Completed | Load_254009 | Oracabessa - 210 | 2026-08-10 20:03 | 2026-08-10 20:04 | 2026-08-10 20:15 | 2026-08-10 20:15 | 2026-08-10 20:15 | 2026-08-10 20:15 | 2026-08-10 20:16 | 2026-08-10 20:16 |  |  | Fair | No | Customer says she didn’t make any report to JPS.
Outage | J.E.26.08.14052 | C001884636 | Neckell Ormsby | St.Mary | Completed | Load_568327 | Blackstonedge - 110 | 2026-08-10 20:05 | 2026-08-11 09:48 | 2026-08-11 12:01 | 2026-08-11 12:02 | 2026-08-11 12:01 | 2026-08-11 12:03 | 2026-08-11 12:04 | 2026-08-11 12:04 |  |  | SevereWind | No | Found junction fuse blown at pole #0014130 patrol and found no permanent fault however line section needs bushing replace 1-15 amp junction fuse
Outage | J.E.26.08.14929 | C001884638 | Radcliffe Coleman | St.Catherine | Completed | Load_250553 | Tredegar - 410 | 2026-08-10 20:31 | 2026-08-10 20:33 | 2026-08-10 22:06 | 2026-08-10 22:06 | 2026-08-10 22:18 | 2026-08-10 22:22 | 2026-08-10 22:23 | 2026-08-10 22:23 | Fire |  | Fair | No | No fire seen in the area when the team visited.
Outage | J.E.26.08.14939 | C001884639 | Delano Gayle | St.Catherine | Completed | Load_267523 | Tredegar - 410 | 2026-08-10 20:31 | 2026-08-10 23:02 | 2026-08-10 23:07 | 2026-08-10 23:07 | 2026-08-11 00:01 | 2026-08-11 01:02 | 2026-08-11 01:02 | 2026-08-11 01:02 |  |  | Fair | No | Blown 40amps junction in 3phase line no pole number on Hanover street, replace 40amps, blown 30amps junction in 3phase line located on kings street no pole# replace 30amps, blown 15amps junction in 3 phase line at Nugent street no pole number replace 15amps, blown 10amp junction on single phase Line no pole#, tree fell on line, replace 10amps
Outage | J.E.26.08.14914 | C001884640 | Christopher West | KSAS | Completed | Load_259363 | Duhaney - 210 | 2026-08-10 20:40 | 2026-08-10 20:42 | 2026-08-10 20:54 | 2026-08-10 20:54 | 2026-08-10 21:47 | 2026-08-10 22:40 | 2026-08-10 22:45 | 2026-08-10 22:45 |  |  | Fair | No | Multiple blown fuses were found different locations, the intersection of Portmore Villa Blvd & Cherrie Lee Dr, blown 40A, at pole# 055516 a blown 30A, at the intersection of Portmore Villa & Las Palmas Ave a blown 20A and at the T off to Espanol Dr a blown 10A, line section was patrolled however, no abnormalities were found, crew was told that someone was doing some welding when the blown fuses occurred, no visible fault was seen, blown fuses were renewed, lines re-energized, area now ok.
Outage | J.E.26.08.15037 | C001884643 | Andre Williams | Trelawny | Completed | Load_256332 | Greenwood - 110 | 2026-08-10 21:11 | 2026-08-10 21:13 | 2026-08-10 21:27 | 2026-08-10 21:28 | 2026-08-10 22:21 | 2026-08-10 22:29 | 2026-08-10 22:30 | 2026-08-10 22:30 |  |  | Fair | No | Patrol line section re fuse and close blown 50 amp main junction on 3 phase line no visible fault seen
Outage | J.E.26.08.14835 | C001884645 | Rusean Allen | KSAN | Completed | Load_261222 | Washington Blvd - 510 | 2026-08-10 21:15 | 2026-08-10 23:04 | 2026-08-10 23:59 | 2026-08-10 23:59 | 2026-08-11 00:51 | 2026-08-11 00:53 | 2026-08-11 00:53 | 2026-08-11 00:53 |  |  | Fair | No | Burnt fuse barrel found, fuse barrel was replaced.1x 10amp fuse found 1x 10amp fuse replaced.
Non-Outage | J.E.26.08.14607 | C001884649 | Christopher Edwards |  | Completed |  |  | 2026-08-10 21:31 | 2026-08-11 07:43 | 2026-08-11 11:25 | 2026-08-11 11:31 | 2026-08-11 11:31 | 2026-08-11 11:41 | 2026-08-11 11:42 | 2026-08-11 11:42 | BrokenWire |  | Fair | No | Isolate 25 kva transformer To splice and retention broken open secondary wireUsing:40 ft #2 AA conductor (2) #2 preforms4 one bolt clamps
Outage | J.E.26.08.14920 | C001884651 | Daniel Francis | St.Ann | Completed | Load_328142 | Roaring River - 210 | 2026-08-10 22:00 | 2026-08-10 22:03 | 2026-08-10 22:27 | 2026-08-10 22:28 | 2026-08-10 22:27 | 2026-08-10 22:28 | 2026-08-10 22:29 | 2026-08-10 22:29 |  |  | Fair | No | We call customer and she say light come she is ok for now
Outage | J.E.26.08.15294 | C001884652 | Lancelot Brown | Hanover | Completed | Load_573351 | Orange Bay - 310 | 2026-08-10 22:08 | 2026-08-10 22:09 | 2026-08-10 22:25 | 2026-08-10 22:25 | 2026-08-10 22:54 | 2026-08-10 23:07 | 2026-08-10 23:08 | 2026-08-10 23:08 | Fire |  | Fair | No | Found bank of 3-25kva that was replaced by maintenance incorrectly wired on the secondary side. Please pass on to maintenance department in Montego Bay to have same corrected, Mr. Gibbs for urgent attention
Outage | J.E.26.08.15018 | C001884657 | Delano Gayle | St.Catherine | Completed | Load_264508 | Rhodens Pen - 410 | 2026-08-10 23:02 | 2026-08-10 23:03 | 2026-08-10 23:06 | 2026-08-11 02:04 | 2026-08-11 02:58 | 2026-08-11 03:34 | 2026-08-11 03:34 | 2026-08-11 03:34 |  |  | Fair | No | Blown 25kva transformer fuse no pole number, patrolled and found okay for closure replace 3amps
Outage | J.E.26.08.15090 | C001884658 | Delano Gayle | St.Catherine | Completed | Load_261126 | Rhodens Pen - 210 | 2026-08-10 23:02 | 2026-08-10 23:03 | 2026-08-11 01:02 | 2026-08-11 01:03 | 2026-08-11 01:55 | 2026-08-11 02:03 | 2026-08-11 02:03 | 2026-08-11 02:03 |  |  | Fair | No | Blown 50kva transformer fuse no pole number replace 5amps
Outage | J.E.26.08.15459 | C001884660 | Romeo Brissett | St.James | Completed | Load_250861 | Queens Drive - 710 | 2026-08-11 00:09 | 2026-08-11 00:10 | 2026-08-11 00:38 | 2026-08-11 00:38 | 2026-08-11 00:38 | 2026-08-11 01:20 | 2026-08-11 01:24 | 2026-08-11 01:24 |  |  | Fair | No | Found (1)50kva transformer defective which supplied, 28 customers, urgently need to change because circuit cannot be tied, secondary dead end pole need D iron. Please send to maintenance.
Outage | J.E.26.08.15478 | C001884662 | Delano Gayle | St.Catherine | Completed | Load_238241 | Tredegar - 310 | 2026-08-11 01:59 | 2026-08-11 02:00 | 2026-08-11 03:34 | 2026-08-11 04:21 | 2026-08-11 04:46 | 2026-08-11 04:59 | 2026-08-11 05:00 | 2026-08-11 05:00 |  |  | Fair | No | Blown junction on main in 2 phase line no pole number, patrolled and found okay for closure replace 25amps
Outage | J.E.26.08.15506 | C001884664 | Roxroy Needham | KSAS | Completed | Load_259630 | Cane River - 410 | 2026-08-11 02:38 | 2026-08-11 08:36 | 2026-08-11 08:42 | 2026-08-11 08:43 | 2026-08-11 08:42 | 2026-08-11 08:43 | 2026-08-11 08:44 | 2026-08-11 08:44 |  |  | Fair | No | Call is not for st ann call customer and customer say she is not from st ann
Outage | J.E.26.08.15505 | C001884671 | Rusean Allen | KSAS | Completed | Load_269980 | Cane River - 410 | 2026-08-11 05:35 | 2026-08-11 14:50 | 2026-08-11 15:07 | 2026-08-11 15:08 | 2026-08-11 15:07 | 2026-08-11 15:09 | 2026-08-11 15:09 | 2026-08-11 15:09 |  |  | Fair | No | Defective 50KVA transformer needs to be changed, refer to maintenance department.
Outage | J.E.26.08.14505 | C001884698 | Stephen Taylor | St.Thomas | Completed | Load_577133 | Lysson - 410 | 2026-08-11 06:59 | 2026-08-11 07:17 | 2026-08-11 08:39 | 2026-08-11 08:40 | 2026-08-11 09:02 | 2026-08-11 09:03 | 2026-08-11 09:04 | 2026-08-11 09:04 |  |  | Fair | No | Clean up single phase use 2 clamps customer is now okay reading 111,112,224
Outage | J.E.26.08.14979 | C001884699 | Stephen Taylor | St.Thomas | Completed | Load_265499 | Good Year - 210 | 2026-08-11 06:59 | 2026-08-11 07:17 | 2026-08-11 10:07 | 2026-08-11 10:08 | 2026-08-11 10:07 | 2026-08-11 10:07 | 2026-08-11 10:08 | 2026-08-11 10:08 |  |  | Fair | No | Call to customer and customer say that power was restored 10:00 last night
Outage | J.E.26.08.14441 | C001884701 | Collin Robinson | Portland | Completed | Load_260238 | Port Antonio - 410 | 2026-08-11 07:09 | 2026-08-11 07:11 | 2026-08-11 08:10 | 2026-08-11 08:11 | 2026-08-11 10:00 | 2026-08-11 10:27 | 2026-08-11 10:27 | 2026-08-11 10:27 |  |  | Fair | No | Repair broken natural conductor at pole and check voltage Voltage reading 117v 118v 235v
Non-Outage | J.E.26.08.14161 | C001884703 | Neville Spencer | Clarendon | Completed | Load_579438 | May Pen - 110 | 2026-08-11 07:20 | 2026-08-11 13:23 | 2026-08-11 13:26 | 2026-08-11 13:27 | 2026-08-11 15:07 | 2026-08-11 15:07 | 2026-08-11 15:54 | 2026-08-11 15:54 |  |  | Fair | No | Found defective 3, wire service .Installed 95 ft #6 triplex, 3, 6/6 sleeves , 2, clamps voltage reading 110 112 223 supply restored.
Non-Outage | J.E.26.08.13987 | C001884706 | Eric Williams | KSAS | Completed | Load_263370 | Washington Blvd - 710 | 2026-08-11 07:24 | 2026-08-11 07:39 | 2026-08-11 08:27 | 2026-08-11 08:27 | 2026-08-11 09:26 | 2026-08-11 09:27 | 2026-08-11 09:27 | 2026-08-11 09:27 |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.08.15399 | C001884704 | Eric Williams | KSAN | Completed | Load_242229 | Constant Spring - 210 | 2026-08-11 07:24 | 2026-08-11 07:48 | 2026-08-11 09:28 | 2026-08-11 09:28 | 2026-08-11 09:32 | 2026-08-11 09:36 | 2026-08-11 09:37 | 2026-08-11 09:37 | BrokenPole |  | Fair | No | 40 ft cl 4 pole broken in main line by vehicle accident sent to maintenance to have same corrected. Pole carrying 3 phase primary conductor, open secondary and third party cables.
Non-Outage | J.E.26.08.15543 | C001884708 | Roemello Brown | Trelawny | Completed | Load_294649 | Greenwood - 110 | 2026-08-11 07:29 | 2026-08-11 08:21 | 2026-08-11 11:27 | 2026-08-11 11:46 | 2026-08-11 13:08 | 2026-08-11 13:08 | 2026-08-11 13:16 | 2026-08-11 13:16 | LowHangingWires |  | Fair | No | Premises found working okayVoltage found 107/107/214Voltage leave 107/107/214
Outage | J.E.26.08.15425 | C001884711 | Rusean Allen | KSAS | Completed | Load_266562 | Hunts Bay - 310 | 2026-08-11 07:30 | 2026-08-11 08:12 | 2026-08-11 09:34 | 2026-08-11 09:34 | 2026-08-11 11:18 | 2026-08-11 11:24 | 2026-08-11 11:25 | 2026-08-11 11:25 | BrokenWire |  | Fair | No | Excessive illegal connections needs to be removed, refer to RPD to remove illegal connections.
Outage | J.E.26.08.15081 | C001884712 | Marlon Brown | Trelawny | Completed | Load_292095 | Duncans - 210 | 2026-08-11 07:34 | 2026-08-11 07:38 | 2026-08-11 07:53 | 2026-08-11 07:54 | 2026-08-11 07:53 | 2026-08-11 07:54 | 2026-08-11 07:54 | 2026-08-11 07:54 |  |  | Fair | No | St Catherine call however customer says the electricity has been restored.
Non-Outage | J.E.26.08.14701 | C001884723 | Marlon Brown | Trelawny | Completed | Load_269069 | Duncans - 210 | 2026-08-11 07:40 | 2026-08-11 07:44 | 2026-08-11 09:24 | 2026-08-11 09:24 | 2026-08-11 10:07 | 2026-08-11 10:08 | 2026-08-11 10:08 | 2026-08-11 10:08 | Fire |  | Fair | No | Unable to locate customer via telephone nor direction.
Outage | J.E.26.08.14463 | C001884727 | Edward Royal | KSAS | Completed | Load_300789 | Greenwich - 510 | 2026-08-11 07:40 | 2026-08-11 08:00 | 2026-08-11 09:26 | 2026-08-11 09:26 | 2026-08-11 09:26 | 2026-08-11 09:26 | 2026-08-11 09:26 | 2026-08-11 09:26 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.14500 | C001884726 | Rusean Allen | KSAS | Completed | Load_262530 | Rockfort - 410 | 2026-08-11 07:40 | 2026-08-11 08:00 | 2026-08-11 11:29 | 2026-08-11 11:35 | 2026-08-11 11:47 | 2026-08-11 11:48 | 2026-08-11 11:48 | 2026-08-11 11:48 |  |  | Fair | No | Premises found locked
Outage | J.E.26.08.14666 | C001884725 | Rusean Allen | KSAS | Completed | Load_267551 | Cane River - 410 | 2026-08-11 07:40 | 2026-08-11 08:01 | 2026-08-11 13:11 | 2026-08-11 13:42 | 2026-08-11 14:48 | 2026-08-11 14:49 | 2026-08-11 14:49 | 2026-08-11 14:49 | Fire |  | Fair | No | Found okay
Outage | J.E.26.08.14772 | C001884724 | Rusean Allen | KSAS | Completed | Load_241686 | Rockfort - 410 | 2026-08-11 07:40 | 2026-08-11 08:00 | 2026-08-11 11:29 | 2026-08-11 11:49 | 2026-08-11 12:53 | 2026-08-11 12:54 | 2026-08-11 12:54 | 2026-08-11 12:54 |  |  | Fair | No | Power was already restored
Outage | J.E.26.08.15383 | C001884722 | Edward Royal | KSAN | Completed | Load_243339 | Washington Blvd - 710 | 2026-08-11 07:40 | 2026-08-11 08:02 | 2026-08-11 12:22 | 2026-08-11 12:23 | 2026-08-11 12:22 | 2026-08-11 12:23 | 2026-08-11 12:23 | 2026-08-11 12:23 |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.08.15519 | C001884715 | Edward Royal | KSAS | Completed | Load_244500 | Greenwich - 410 | 2026-08-11 07:40 | 2026-08-11 08:02 | 2026-08-11 20:46 | 2026-08-11 20:46 | 2026-08-11 20:46 | 2026-08-11 20:46 | 2026-08-11 20:46 | 2026-08-11 20:46 |  |  | Fair | No | Premises found close
Outage | J.E.26.08.13538 | C001884731 | Edward Royal | KSAN | Completed | Load_575405 | Washington Blvd - 710 | 2026-08-11 07:41 | 2026-08-11 08:00 | 2026-08-11 09:12 | 2026-08-11 09:12 | 2026-08-11 09:12 | 2026-08-11 09:12 | 2026-08-11 09:12 | 2026-08-11 09:12 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.14328 | C001884730 | Edward Royal | KSAS | Completed | Load_241557 | Up Park Camp - 310 | 2026-08-11 07:41 | 2026-08-11 08:00 | 2026-08-11 17:27 | 2026-08-11 17:28 | 2026-08-11 17:27 | 2026-08-11 17:28 | 2026-08-11 17:29 | 2026-08-11 17:29 | BrokenPole |  | Fair | No | Premises found ok customer was referring about private pole
Outage | J.E.26.08.14450 | C001884728 | Edward Royal | KSAS | Completed | Load_248285 | Greenwich - 510 | 2026-08-11 07:41 | 2026-08-11 08:00 | 2026-08-11 09:09 | 2026-08-11 09:09 | 2026-08-11 09:09 | 2026-08-11 09:09 | 2026-08-11 09:10 | 2026-08-11 09:10 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.15053 | C001884734 | Wayne Dillion | St.Elizabeth | Completed | Load_252841 | Maggotty - 110 | 2026-08-11 07:42 | 2026-08-11 07:51 | 2026-08-11 08:39 | 2026-08-11 08:40 | 2026-08-11 09:38 | 2026-08-11 22:07 | 2026-08-11 10:08 | 2026-08-11 10:08 |  |  | Fair | No | Patrol and found one blown 15amp junction fuse no pole # caused by burnt out fuse holder. Replace fuse holder and fuse and supply leave working okay.
Outage | J.E.26.08.15559 | C001884733 | Rodclif Dawkins | St.Catherine | Completed | Load_244358 | Tredegar - 410 | 2026-08-11 07:42 | 2026-08-11 08:32 | 2026-08-11 11:24 | 2026-08-11 11:25 | 2026-08-11 12:00 | 2026-08-11 12:00 | 2026-08-11 12:22 | 2026-08-11 12:22 | BrokenWire |  | Fair | No | Customer found okay at time of visit
Non-Outage | J.E.26.08.14423 | C001884736 | Marlon Brown | Trelawny | Completed | Load_1001498 | Duncans - 110 | 2026-08-11 07:44 | 2026-08-11 07:45 | 2026-08-11 07:56 | 2026-08-11 07:57 | 2026-08-11 08:44 | 2026-08-11 09:16 | 2026-08-11 09:16 | 2026-08-11 09:16 |  |  | Fair | No | Clear vegetation from riser pole and replaced 15amps junction fuse.
Outage | J.E.26.08.13723 | C001884738 | Elvis Trowers | KSAN | Completed | Load_256208 | Constant Spring - 410 | 2026-08-11 07:46 | 2026-08-11 07:47 | 2026-08-11 09:32 | 2026-08-11 09:32 | 2026-08-11 10:20 | 2026-08-11 12:42 | 2026-08-11 12:42 | 2026-08-11 12:42 |  |  | Fair | Yes | Customers was found having single phasing when checked, during trouble shooting burnt twisted secondary phase was found, about 4’ feet of #2 triplex and 2 one bolt clamps was used for splicing broken wire, voltage when checked was left at 118+117=235 volts.
Non-Outage | J.E.26.08.14427 | C001884744 | Roemello Brown | Trelawny | Completed | Load_292238 | Greenwood - 210 | 2026-08-11 07:50 | 2026-08-11 07:52 | 2026-08-12 13:32 | 2026-08-12 13:33 | 2026-08-12 13:59 | 2026-08-12 14:00 | 2026-08-12 14:05 | 2026-08-12 14:05 |  |  | Fair | No | Secondary twisted burnt up please send maintenance team to change wire a section of the community have this issue some person are without power about 146 feet of number two north needs to be changed only getting 107 volts please assist as soon as possible please
Non-Outage | J.E.26.08.14954 | C001884743 | Roemello Brown | Trelawny | Completed | Load_292238 | Greenwood - 210 | 2026-08-11 07:50 | 2026-08-11 07:52 | 2026-08-12 12:50 | 2026-08-12 12:51 | 2026-08-12 12:53 | 2026-08-12 12:53 | 2026-08-12 12:58 | 2026-08-12 12:58 |  |  | Fair | No | Secondary twisted burnt up please send maintenance team to change wire a section of the community have this issue some persons are without power about 146 feet of number two north needs to be changed only getting 107volts please assist soon as possible please
Non-Outage | J.E.26.08.15435 | C001884742 | Roemello Brown | Trelawny | Completed | Load_248970 | Martha Brae - 110 | 2026-08-11 07:50 | 2026-08-11 07:52 | 2026-08-11 09:06 | 2026-08-11 09:07 | 2026-08-11 09:43 | 2026-08-11 09:44 | 2026-08-11 09:48 | 2026-08-11 09:48 |  |  | Fair | No | Customer stated that i have the wrong number and she doesn’t know the person also complainants need to update proper address to the premises please an phone number
Non-Outage | J.E.26.08.00070 | C001884746 | Roemello Brown | Trelawny | Completed | Load_259574 | Greenwood - 110 | 2026-08-11 07:51 | 2026-08-11 07:52 | 2026-08-11 09:08 | 2026-08-11 10:07 | 2026-08-11 11:38 | 2026-08-11 11:39 | 2026-08-11 11:45 | 2026-08-11 11:45 |  |  | Fair | No | Premises found working okayVoltage found 116/115/231Voltage leave 116/115/231
Non-Outage | J.E.26.08.13293 | C001884745 | Roemello Brown | Trelawny | Completed | Load_239556 | Duncans - 210 | 2026-08-11 07:51 | 2026-08-11 07:52 | 2026-08-12 10:34 | 2026-08-12 10:35 | 2026-08-12 11:57 | 2026-08-12 11:57 | 2026-08-12 12:02 | 2026-08-12 12:02 |  |  | Fair | No | Neutral wire broke off at pole side have it reclamp Voltage found 118/118/236Voltage leave 118/118/236
Non-Outage | J.E.26.08.13394 | C001884748 | Roemello Brown | Trelawny | Completed | Load_247755 | Martha Brae - 210 | 2026-08-11 07:52 | 2026-08-11 07:54 | 2026-08-11 09:11 | 2026-08-11 14:02 | 2026-08-11 15:04 | 2026-08-12 08:30 | 2026-08-12 08:36 | 2026-08-12 08:36 |  |  | Fair | No | Customer meter socket defective inform customer to get an private electrician to have meter socket change Voltage found 122/123/246Voltage leave 122/123/246
Non-Outage | J.E.26.08.14493 | C001884749 | Roemello Brown | Trelawny | Completed | Load_292238 | Greenwood - 210 | 2026-08-11 07:52 | 2026-08-11 07:54 | 2026-08-12 14:05 | 2026-08-12 14:06 | 2026-08-12 14:14 | 2026-08-12 14:14 | 2026-08-12 14:21 | 2026-08-12 14:21 |  |  | Fair | No | Secondary twisted burnt up please send maintenance team to change wire a section of the community have this issue some people are without power about 146 feet of number two north needs to be changed only getting 107 volts please assist as soon as possible please
Non-Outage | J.E.26.08.15363 | C001884747 | Roemello Brown | Trelawny | Completed | Load_575578 | Greenwood - 210 | 2026-08-11 07:52 | 2026-08-11 07:54 | 2026-08-11 09:10 | 2026-08-11 09:49 | 2026-08-11 09:52 | 2026-08-11 09:52 | 2026-08-11 10:06 | 2026-08-11 10:06 | LeaningPole |  | Fair | No | Customer reporting an leaning transformer pole that needs to be straighten please send maintenance team to assist please
Non-Outage | J.E.26.08.08106 | C001884750 | Roemello Brown | Trelawny | Completed | Load_248867 | Greenwood - 210 | 2026-08-11 07:53 | 2026-08-11 07:54 | 2026-08-11 13:20 | 2026-08-11 13:21 | 2026-08-11 13:21 | 2026-08-11 13:21 | 2026-08-11 13:23 | 2026-08-11 13:23 |  |  | Fair | No | This call is for st.James team please transfer to them please
Non-Outage | J.E.26.08.14499 | C001884758 | Damion Reid |  | Completed |  |  | 2026-08-11 07:59 | 2026-08-11 08:05 | 2026-08-11 09:32 | 2026-08-11 09:32 | 2026-08-11 10:38 | 2026-08-11 12:27 | 2026-08-11 12:29 | 2026-08-11 12:29 | BrokenWire |  | Fair | No | Two span of broken secondary phase an neutral conductor found cause by trees open 25kva transformer fuse link splice an retention conductor using 40ft of #2 aluminum conductor two #2 preform 4 one bolt clamp and restore power
Outage | J.E.26.08.15570 | C001884759 | Edward Royal | KSAN | Completed | Load_243339 | Washington Blvd - 710 | 2026-08-11 07:59 | 2026-08-11 08:04 | 2026-08-11 11:15 | 2026-08-11 11:16 | 2026-08-11 11:31 | 2026-08-11 12:15 | 2026-08-11 12:15 | 2026-08-11 12:15 | BrokenWire |  | Fair | No | Spliced and reconnected 2 span of secondary phase using 80ft 2 north conductor and 3 single bolt clamp
Non-Outage | J.E.26.08.13307 | C001884763 | Andrae Clarke | Portland | Completed | Load_240782 | Port Antonio - 310 | 2026-08-11 08:03 | 2026-08-12 08:57 | 2026-08-12 09:05 | 2026-08-12 10:09 | 2026-08-12 10:27 | 2026-08-12 10:19 | 2026-08-12 10:43 | 2026-08-12 10:43 |  |  | Fair | No | Premises found okay Check voltage 117/119/236
Non-Outage | J.E.26.08.14373 | C001884762 | Andrae Clarke | Portland | Completed | Load_265666 | Port Antonio - 310 | 2026-08-11 08:03 | 2026-08-11 08:10 | 2026-08-11 08:14 | 2026-08-11 08:15 | 2026-08-11 09:20 | 2026-08-11 09:20 | 2026-08-11 09:21 | 2026-08-11 09:21 |  |  | Fair | No | Repair broken wires used two one bolt clamp Check voltage 17/116/234
Outage | J.E.26.08.12656 | C001884764 | Elvis Trowers | KSAS | Completed | Load_301275 | Hunts Bay - 510 | 2026-08-11 08:04 | 2026-08-12 08:09 | 2026-08-12 09:14 | 2026-08-12 09:15 | 2026-08-12 10:51 | 2026-08-12 10:53 | 2026-08-12 10:53 | 2026-08-12 10:53 |  |  | Fair | No | Customer service wire #6 triplex phase burn off at pole. Repair using one 1- bolt clamp. Reading at meter socket 117-118-236 volts.
Outage | J.E.26.08.15194 | C001884767 | Rodclif Dawkins | St.Catherine | Completed | Load_1001432 | Tredegar - 210 | 2026-08-11 08:05 | 2026-08-11 09:44 | 2026-08-11 10:24 | 2026-08-11 10:24 | 2026-08-11 11:02 | 2026-08-11 11:02 | 2026-08-11 11:24 | 2026-08-11 11:24 |  |  | Fair | No | Customer found okay
Non-Outage | J.E.26.08.13390 | C001884772 | Andrae Clarke | Portland | Completed | Load_250156 | Port Antonio - 410 | 2026-08-11 08:06 | 2026-08-11 08:08 | 2026-08-11 09:29 | 2026-08-11 09:29 | 2026-08-11 10:11 | 2026-08-11 10:25 | 2026-08-11 10:26 | 2026-08-11 10:26 |  |  | Fair | No | Premises found okay 119/123/241
Non-Outage | J.E.26.08.13433 | C001884771 | Andrae Clarke |  | Completed |  |  | 2026-08-11 08:06 | 2026-08-11 08:08 | 2026-08-11 10:26 | 2026-08-11 10:26 | 2026-08-11 10:45 | 2026-08-11 11:27 | 2026-08-11 11:43 | 2026-08-11 11:43 |  |  | Fair | No | Made several calls to the customer and got no response On reaching premises Premises locked
Outage | J.E.26.08.15384 | C001884770 | Michael Paterson | Westmoreland | Completed | Load_265015 | Paradise - 210 | 2026-08-11 08:06 | 2026-08-11 08:07 | 2026-08-11 10:50 | 2026-08-11 10:50 | 2026-08-11 11:34 | 2026-08-11 11:36 | 2026-08-11 11:45 | 2026-08-11 11:45 |  |  | Fair | No | Contact customer via phone call customer service crew that supply has been restored
Outage | J.E.26.08.15531 | C001884769 | Michael Paterson | Westmoreland | Completed | Load_265015 | Paradise - 210 | 2026-08-11 08:06 | 2026-08-11 08:07 | 2026-08-11 11:34 | 2026-08-11 11:45 | 2026-08-11 12:36 | 2026-08-11 12:39 | 2026-08-11 12:39 | 2026-08-11 12:39 |  |  | Fair | No | Contact customer via phone she advise crew that supply restored was restored early this morning
Outage | J.E.26.08.15575 | C001884768 | Raheem Ricketts | St.Elizabeth | Completed | Load_257774 | Maggotty - 210 | 2026-08-11 08:06 | 2026-08-11 08:07 | 2026-08-11 08:18 | 2026-08-11 08:19 | 2026-08-11 08:19 | 2026-08-11 08:20 | 2026-08-11 08:20 | 2026-08-11 08:20 |  |  | Fair | No | Check found okay customer says problem was and his end
Non-Outage | J.E.26.08.15162 | C001884775 | Rusean Allen |  | Completed |  |  | 2026-08-11 08:08 | 2026-08-12 07:42 | 2026-08-12 11:52 | 2026-08-12 11:53 | 2026-08-12 12:43 | 2026-08-12 12:43 | 2026-08-12 12:44 | 2026-08-12 12:44 |  |  | Fair | No | More information required
Outage | J.E.26.08.14466 | C001884774 | Damion Reid | Manchester | Completed | Load_270012 | Porus - 310 | 2026-08-11 08:08 | 2026-08-11 08:09 | 2026-08-11 14:11 | 2026-08-11 14:12 | 2026-08-11 14:50 | 2026-08-11 16:39 | 2026-08-11 16:41 | 2026-08-11 16:41 | BrokenPole |  | Fair | No | Blown 20amp junction fuse found cause by contamination line patrol and replace blown fuse (also found defective 35ft cv construction pole about 90% of pole foot decay pole need to rectify soon
Non-Outage | J.E.26.08.04652 | C001884776 | Odeanie Davis | KSAS | Completed | Load_251064 | Rockfort - 210 | 2026-08-11 08:09 | 2026-08-11 08:11 | 2026-08-11 11:51 | 2026-08-11 14:16 | 2026-08-11 14:16 | 2026-08-11 14:27 | 2026-08-11 14:27 | 2026-08-11 14:27 |  |  | Fair | No | Customer defective wiring at pothead, customer was advised to contact their electrician
Non-Outage | J.E.26.08.05802 | C001884778 | Odeanie Davis | KSAS | Completed | Load_245738 | Rockfort - 210 | 2026-08-11 08:09 | 2026-08-11 08:11 | 2026-08-11 11:51 | 2026-08-11 13:01 | 2026-08-11 13:01 | 2026-08-11 13:10 | 2026-08-11 13:05 | 2026-08-11 13:05 |  |  | Fair | No | 105v/125v at arrival, open neutral at secondary corrected, 3 one bolt clamps, 115v/115v & 231v after correction.
Non-Outage | J.E.26.08.06444 | C001884779 | Odeanie Davis | KSAS | Completed | Load_246732 | Rockfort - 210 | 2026-08-11 08:09 | 2026-08-11 08:11 | 2026-08-11 11:51 | 2026-08-11 13:39 | 2026-08-11 13:38 | 2026-08-11 14:09 | 2026-08-11 14:09 | 2026-08-11 14:09 |  |  | Fair | No | 99v/109v on secondary line, secondary line & transformer needs to be checked and rectify
Non-Outage | J.E.26.08.06453 | C001884777 | Odeanie Davis | KSAS | Completed | Load_240821 | Rockfort - 210 | 2026-08-11 08:09 | 2026-08-11 08:11 | 2026-08-11 09:31 | 2026-08-11 12:29 | 2026-08-11 12:28 | 2026-08-11 12:46 | 2026-08-11 12:29 | 2026-08-11 12:29 |  |  | Fair | No
Non-Outage | J.E.26.07.09376 | C001884784 | Odeanie Davis | KSAS | Completed | Load_251973 | Rockfort - 410 | 2026-08-11 08:10 | 2026-08-11 08:11 | 2026-08-11 08:33 | 2026-08-11 08:33 | 2026-08-11 08:33 | 2026-08-11 09:17 | 2026-08-11 09:17 | 2026-08-11 09:17 |  |  | Fair | No | 111v/114v at arrival, open circuit at secondary corrected, 3 one bolt clamps, 111v/119v 230v after correction
Non-Outage | J.E.26.08.01267 | C001884783 | Odeanie Davis | KSAS | Completed | Load_266084 | Rockfort - 410 | 2026-08-11 08:10 | 2026-08-11 08:11 | 2026-08-11 09:38 | 2026-08-11 12:27 | 2026-08-11 12:27 | 2026-08-11 12:35 | 2026-08-11 12:28 | 2026-08-11 12:28 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.13609 | C001884782 | Odeanie Davis | KSAS | Completed | Load_245738 | Rockfort - 210 | 2026-08-11 08:10 | 2026-08-11 08:11 | 2026-08-11 11:51 | 2026-08-11 13:06 | 2026-08-11 13:10 | 2026-08-11 13:22 | 2026-08-11 13:13 | 2026-08-11 13:13 |  |  | Fair | No | 105v/ 125v at arrival, open neutral at secondary corrected, 3 one bolt clamps, 115v/115v & 231v after correction
Non-Outage | J.E.26.08.14455 | C001884780 | Odeanie Davis | KSAS | Completed | Load_257291 | Rockfort - 210 | 2026-08-11 08:10 | 2026-08-11 08:11 | 2026-08-11 11:51 | 2026-08-11 13:24 | 2026-08-11 13:23 | 2026-08-11 13:45 | 2026-08-11 13:34 | 2026-08-11 13:34 |  |  | Fair | No | Secondary twisted burnt by fire and need to replaced, trees needs de-bushing, secondary twisted is hanging low and needs to be anchored to pole properly
Outage | J.E.26.08.15554 | C001884781 | Barrington Brown | St.James | Completed | Load_303201 | Bogue - 310 | 2026-08-11 08:10 | 2026-08-11 15:30 | 2026-08-11 19:34 | 2026-08-11 19:35 | 2026-08-11 21:31 | 2026-08-11 21:38 | 2026-08-11 21:38 | 2026-08-11 21:38 |  |  | Fair | No | Checked and found ok. 115v/115v/231v
Outage | J.E.26.08.15557 | C001884795 | Rodclif Dawkins | St.Catherine | Completed | Load_265040 | Twickenham - 310 | 2026-08-11 08:10 | 2026-08-11 08:32 | 2026-08-11 12:23 | 2026-08-11 12:23 | 2026-08-11 12:58 | 2026-08-11 12:58 | 2026-08-11 12:59 | 2026-08-11 12:59 |  |  | Fair | No | Customer found okay
Outage | J.E.26.08.14533 | C001884797 | Clyde Brown | Clarendon | Completed | Load_243213 | Monymusk - 210 | 2026-08-11 08:11 | 2026-08-11 08:11 | 2026-08-11 10:43 | 2026-08-11 10:44 | 2026-08-11 11:59 | 2026-08-11 12:02 | 2026-08-11 12:05 | 2026-08-11 12:05 |  |  | Fair | No | All customers from Exim box # 21753741 are without supply and field service need to check box.
Non-Outage | J.E.26.07.32051 | C001884801 | Oraine Minto | St.Ann | Completed | Load_264076 | Cardiff Hall - 210 | 2026-08-11 08:12 | 2026-08-11 08:13 | 2026-08-11 11:28 | 2026-08-11 11:29 | 2026-08-11 11:29 | 2026-08-11 11:29 | 2026-08-11 11:30 | 2026-08-11 11:30 |  |  | Fair | No | 237v 118v 116v
Non-Outage | J.E.26.07.38823 | C001884803 | Oraine Minto | St.Ann | Completed | Load_246617 | Cardiff Hall - 210 | 2026-08-11 08:12 | 2026-08-11 08:14 | 2026-08-11 11:13 | 2026-08-11 11:14 | 2026-08-11 11:14 | 2026-08-11 11:15 | 2026-08-11 11:15 | 2026-08-11 11:15 |  |  | Fair | No | Customer states that the issue has been resolved
Non-Outage | J.E.26.08.02616 | C001884802 | Oraine Minto | St.Ann | Completed | Load_262356 | Cardiff Hall - 210 | 2026-08-11 08:12 | 2026-08-11 08:15 | 2026-08-11 11:16 | 2026-08-11 11:19 | 2026-08-11 11:18 | 2026-08-11 11:19 | 2026-08-11 11:20 | 2026-08-11 11:20 |  |  | Fair | No | Customer states that issue is ok now but sometimes goes of an on
Non-Outage | J.E.26.08.04608 | C001884800 | Oraine Minto | St.Ann | Completed | Load_265383 | Cardiff Hall - 210 | 2026-08-11 08:12 | 2026-08-11 08:16 | 2026-08-11 11:20 | 2026-08-11 11:21 | 2026-08-11 11:21 | 2026-08-11 11:22 | 2026-08-11 11:22 | 2026-08-11 11:22 |  |  | Fair | No | Premises ok 234v 117v 116v
Non-Outage | J.E.26.08.15457 | C001884798 | Rodclif Dawkins | St.Catherine | Completed | Load_246045 | Tredegar - 510 | 2026-08-11 08:12 | 2026-08-11 08:32 | 2026-08-11 09:10 | 2026-08-11 09:11 | 2026-08-11 09:41 | 2026-08-11 10:17 | 2026-08-11 10:15 | 2026-08-11 10:15 |  |  | Fair | No | Found defective dropout switch on location supplying single phase T-off. Using grip stick line section isolated and switch changed. Line section energized and area okay
Non-Outage | J.E.26.08.13440 | C001884807 | Andrae Dawkins | St.James | Completed | Load_253389 | Bogue - 310 | 2026-08-11 08:13 | 2026-08-11 08:15 | 2026-08-11 14:10 | 2026-08-11 14:10 | 2026-08-11 14:14 | 2026-08-11 14:33 | 2026-08-11 14:35 | 2026-08-11 14:35 |  |  | Fair | No | Found customer single phasing due to slack connection at pole clean and remade joints voltage left 113/107/221
Non-Outage | J.E.26.08.13556 | C001884806 | Andrae Dawkins | St.James | Completed | Load_303191 | Bogue - 310 | 2026-08-11 08:13 | 2026-08-11 08:15 | 2026-08-11 14:35 | 2026-08-11 14:44 | 2026-08-11 16:38 | 2026-08-11 14:50 | 2026-08-11 16:40 | 2026-08-11 16:40 |  |  | Fair | No | Cannot locate customer unable to reach customer’s mobile phone
Non-Outage | J.E.26.08.14022 | C001884805 | Andrae Dawkins | St.James | Completed | Load_246427 | Bogue - 310 | 2026-08-11 08:13 | 2026-08-11 08:15 | 2026-08-11 08:49 | 2026-08-11 10:43 | 2026-08-11 10:43 | 2026-08-11 10:57 | 2026-08-11 10:57 | 2026-08-11 10:57 |  |  | Fair | No | Found multiple customers experiencing low voltage due to 100 kva transformer fuse blown urgent attention required refer back to emergency crew
Non-Outage | J.E.26.08.14324 | C001884804 | Andrae Dawkins | St.James | Completed | Load_239765 | Bogue - 310 | 2026-08-11 08:13 | 2026-08-11 08:15 | 2026-08-11 08:49 | 2026-08-11 11:01 | 2026-08-11 11:29 | 2026-08-11 11:35 | 2026-08-11 11:36 | 2026-08-11 11:36 |  |  | Fair | No | Found customer singlephasing from EG box 00570 voltage found 119/46/126 refer back to field service
Non-Outage | J.E.26.08.09397 | C001884808 | Andrae Dawkins | St.James | Completed | Load_1001861 | Bogue - 310 | 2026-08-11 08:14 | 2026-08-11 08:15 | 2026-08-11 11:36 | 2026-08-11 11:36 | 2026-08-11 14:05 | 2026-08-11 11:32 | 2026-08-11 14:09 | 2026-08-11 14:09 |  |  | Fair | No | Cannot locate customer unable to reach customer’s mobile phone
Non-Outage | J.E.26.08.15569 | C001884809 | Hopeton Henry | St.Thomas | Completed | Load_266044 | Good Year - 210 | 2026-08-11 08:14 | 2026-08-11 08:16 | 2026-08-11 10:52 | 2026-08-12 13:14 | 2026-08-12 13:13 | 2026-08-12 13:26 | 2026-08-12 13:27 | 2026-08-12 13:27 |  |  | Fair | No | Reconnect broken service wire
Non-Outage | J.E.26.08.13498 | C001884816 | Hopeton Henry | St.Thomas | Completed | Load_249913 | Good Year - 110 | 2026-08-11 08:15 | 2026-08-11 08:16 | 2026-08-11 10:52 | 2026-08-11 12:06 | 2026-08-11 12:43 | 2026-08-11 13:15 | 2026-08-11 13:18 | 2026-08-11 13:18 |  |  | Fair | No | Found ok , customer states the issue was resolved
Non-Outage | J.E.26.08.14309 | C001884814 | Hopeton Henry | St.Thomas | Completed | Load_268649 | Lysson - 410 | 2026-08-11 08:15 | 2026-08-11 08:16 | 2026-08-11 10:52 | 2026-08-11 13:19 | 2026-08-11 13:39 | 2026-08-11 13:43 | 2026-08-11 13:43 | 2026-08-11 13:43 | Fire |  | Fair | No | Use 1 clamp at pole 113-115-228 volts
Non-Outage | J.E.26.08.14721 | C001884812 | Hopeton Henry | St.Thomas | Completed | Load_252203 | Good Year - 210 | 2026-08-11 08:15 | 2026-08-11 08:16 | 2026-08-11 10:52 | 2026-08-11 11:22 | 2026-08-11 11:28 | 2026-08-11 12:02 | 2026-08-11 12:04 | 2026-08-11 12:04 |  |  | Fair | Yes | Found corrosion at pole and pothead 112-117-229 volts
Non-Outage | J.E.26.08.15106 | C001884818 | Edward Royal |  | Completed |  |  | 2026-08-11 08:16 | 2026-08-11 08:17 | 2026-08-11 09:19 | 2026-08-11 09:19 | 2026-08-11 09:19 | 2026-08-11 09:19 | 2026-08-11 09:20 | 2026-08-11 09:20 |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.08.13837 | C001884821 | Dean- Smith | Hanover | Completed | Load_253913 | Orange Bay - 310 | 2026-08-11 08:18 | 2026-08-11 08:20 | 2026-08-11 11:24 | 2026-08-11 11:25 | 2026-08-11 15:21 | 2026-08-11 15:22 | 2026-08-11 15:22 | 2026-08-11 15:22 |  |  | Rains | No | Unable to complete because of rain
Non-Outage | J.E.26.08.14552 | C001884820 | Dean- Smith | Hanover | Completed | Load_264368 | Orange Bay - 310 | 2026-08-11 08:18 | 2026-08-11 08:20 | 2026-08-11 09:19 | 2026-08-11 09:20 | 2026-08-11 09:39 | 2026-08-11 09:39 | 2026-08-11 11:23 | 2026-08-11 11:23 |  |  | Fair | No | Low voltage in the area , voltage found 105v,106v, 211v ..50kva transformer found at top”4” . Same was top out to top “5” . Voltage left 110v,111v,221v.
Non-Outage | J.E.26.08.09499 | C001884823 | Dean- Smith | Hanover | Completed | Load_242732 | Orange Bay - 310 | 2026-08-11 08:19 | 2026-08-11 08:20 | 2026-08-11 15:23 | 2026-08-11 15:24 | 2026-08-11 15:23 | 2026-08-11 15:23 | 2026-08-11 15:24 | 2026-08-11 15:24 |  |  | Rains | No | Unable to complete because of rain
Non-Outage | J.E.26.08.09860 | C001884824 | Cliton Henry | St.Mary | Completed | Load_260379 | Oracabessa - 110 | 2026-08-11 08:19 | 2026-08-11 11:56 | 2026-08-11 13:31 | 2026-08-11 13:32 | 2026-08-11 13:36 | 2026-08-11 14:09 | 2026-08-11 14:10 | 2026-08-11 14:10 |  |  | Fair | No | The voltages found at the customer’s pothead were 102-109/211 volts. A rehabilitation of the secondary lines is recommended due multiple spliced seen. Kindly refer to St. Mary Operations for execution.
Non-Outage | J.E.26.08.10596 | C001884822 | Dean- Smith | Hanover | Completed | Load_261657 | Orange Bay - 310 | 2026-08-11 08:19 | 2026-08-11 08:20 | 2026-08-11 15:24 | 2026-08-11 15:24 | 2026-08-11 15:24 | 2026-08-11 15:24 | 2026-08-11 15:25 | 2026-08-11 15:25 |  |  | Rains | No | Unable to complete because of rain
Non-Outage | J.E.26.08.13017 | C001884828 | Locksley Allen | St.Mary | Completed | Load_243245 | Oracabessa - 210 | 2026-08-11 08:20 | 2026-08-11 08:23 | 2026-08-11 12:24 | 2026-08-11 12:41 | 2026-08-11 12:41 | 2026-08-11 13:46 | 2026-08-11 13:42 | 2026-08-11 13:42 |  |  | Fair | No | No low voltage problem found at premises. Pothead found corroded Change 3 clamps at pothead and clean up connectors at pole Voltage at meter socket phase to phase 242v. Phase to neutral 119&121vMeter left working okay
Non-Outage | J.E.26.08.13216 | C001884829 | Cliton Henry | St.Mary | Completed | Load_259506 | Oracabessa - 210 | 2026-08-11 08:20 | 2026-08-11 08:21 | 2026-08-11 10:23 | 2026-08-11 11:20 | 2026-08-11 11:42 | 2026-08-11 11:52 | 2026-08-11 11:52 | 2026-08-11 11:52 | BrokenWire |  | Fair | No | A broken secondary phase conductor found. A 25 kva transformer was de energized at pole #0013727 to carryout repairs. Corrective work done to spliced and retention secondary phase conductor using approximately 1 foot #2 AA conductor and 2- one bolt clamps. Supply restored to energized the 25 kva transformer at pole #0013727
Non-Outage | J.E.26.08.14190 | C001884831 | Locksley Allen | St.Mary | Completed | Load_254665 | Oracabessa - 210 | 2026-08-11 08:21 | 2026-08-11 08:24 | 2026-08-11 11:01 | 2026-08-11 11:42 | 2026-08-11 11:42 | 2026-08-11 11:52 | 2026-08-11 11:50 | 2026-08-11 11:50 | BrokenPole |  | Fair | No | JPS concrete pole is cracked near the base of the pole,a car crashed into it Customer doesn’t have a current p
Outage | J.E.26.08.15063 | C001884830 | Michael Paterson | Westmoreland | Completed | Load_292188 | Paradise - 210 | 2026-08-11 08:21 | 2026-08-12 07:45 | 2026-08-12 10:33 | 2026-08-12 10:34 | 2026-08-12 10:33 | 2026-08-12 10:37 | 2026-08-12 10:37 | 2026-08-12 10:37 |  |  | Fair | No | Unable to connect customer as customer has internal problem, advise to fix.
Non-Outage | J.E.26.08.13950 | C001884834 | Horace Malcolm | St.James | Completed | Load_269658 | Queens Drive - 810 | 2026-08-11 08:23 | 2026-08-11 08:25 | 2026-08-11 14:23 | 2026-08-11 14:24 | 2026-08-11 14:25 | 2026-08-11 14:26 | 2026-08-11 14:26 | 2026-08-11 14:26 |  |  | Fair | No | Check and found ok related to previous call job number 14237
Non-Outage | J.E.26.08.14237 | C001884833 | Horace Malcolm | St.James | Completed | Load_269658 | Queens Drive - 810 | 2026-08-11 08:23 | 2026-08-11 08:25 | 2026-08-11 09:55 | 2026-08-11 09:56 | 2026-08-11 11:11 | 2026-08-11 14:21 | 2026-08-11 14:21 | 2026-08-11 14:21 |  |  | Fair | No | Isolate one 50kva transformer to repair one nuetral jumper used 2ft #2 conductor 2clamps and three phase jumper used 8ft #2 twisted wire 6clamps voltage 114-112-226
Non-Outage | J.E.26.08.09973 | C001884838 | Horace Malcolm | St.James | Completed | Load_243182 | Queens Drive - 710 | 2026-08-11 08:24 | 2026-08-11 08:25 | 2026-08-11 14:42 | 2026-08-11 14:43 | 2026-08-11 15:13 | 2026-08-11 15:15 | 2026-08-11 15:15 | 2026-08-11 15:15 |  |  | Fair | No | Check and found area ok tangled wire found voltage 115-118-232
Non-Outage | J.E.26.08.13250 | C001884837 | Horace Malcolm | St.James | Completed | Load_239097 | Queens Drive - 710 | 2026-08-11 08:24 | 2026-08-11 15:03 | 2026-08-11 15:24 | 2026-08-11 15:24 | 2026-08-11 15:49 | 2026-08-11 15:50 | 2026-08-11 15:50 | 2026-08-11 15:50 |  |  | Fair | No | Check and found premises ok issue resolved voltage 113-115-228
Non-Outage | J.E.26.08.13252 | C001884835 | Swon Miller | St.James | Completed | Load_259728 | Queens Drive - 710 | 2026-08-11 08:24 | 2026-08-12 07:50 | 2026-08-12 07:53 | 2026-08-12 08:13 | 2026-08-12 08:30 | 2026-08-04 08:40 | 2026-08-12 08:47 | 2026-08-12 08:47 |  |  | Fair | No | Check and found areas okay voltage found 115/114/231 customer states that power supply was restored two days ago voltage left 114/115/231
Outage | J.E.26.08.15588 | C001884836 | Cliton Henry | St.Mary | Completed | Load_412803 | Oracabessa - 210 | 2026-08-11 08:24 | 2026-08-11 08:25 | 2026-08-11 09:50 | 2026-08-11 09:50 | 2026-08-11 10:28 | 2026-08-11 11:09 | 2026-08-11 11:17 | 2026-08-11 11:17 |  |  | Fair | No | A blown 10 junction fuse found at Hillside close at pole # 232112 due to a clearance breach as a result of a conductor sag. Corrective work done to retention 1- span of primary conductor. Supply restored using 1-10 amp fuse.
Outage | J.E.26.08.15553 | C001884844 | Selvin White | St.Elizabeth | Completed | Load_256628 | Maggotty - 210 | 2026-08-11 08:26 | 2026-08-11 10:41 | 2026-08-11 11:20 | 2026-08-11 11:28 | 2026-08-11 12:12 | 2026-08-11 13:33 | 2026-08-11 13:33 | 2026-08-11 13:33 |  |  | SevereWind | No | Replace a blown 10 amp junction fuse at pole number 563706 after patrolling 2 phase primary line. Supply restored to the three customers that were affected. Customer says power went out after a lightning strike.
Outage | J.E.26.08.15592 | C001884845 | Edward Royal | KSAN | Completed | Load_257472 | Washington Blvd - 710 | 2026-08-11 08:26 | 2026-08-11 08:27 | 2026-08-11 09:21 | 2026-08-11 09:21 | 2026-08-11 09:21 | 2026-08-11 09:21 | 2026-08-11 09:22 | 2026-08-11 09:22 |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.08.15566 | C001884847 | Hopeton Henry | St.Thomas | Completed | Load_266529 | Good Year - 210 | 2026-08-11 08:27 | 2026-08-11 08:33 | 2026-08-11 10:52 | 2026-08-11 10:55 | 2026-08-11 11:06 | 2026-08-11 11:20 | 2026-08-11 11:20 | 2026-08-11 11:20 |  |  | Fair | No | Found ok 118-119- 237 volts
Outage | J.E.26.08.14391 | C001884848 | Barnett Brown | Manchester | Completed | Load_302137 | Spur Tree - 310 | 2026-08-11 08:28 | 2026-08-12 15:04 | 2026-08-12 15:24 | 2026-08-12 15:25 | 2026-08-12 16:11 | 2026-08-12 16:54 | 2026-08-12 17:13 | 2026-08-12 17:13 | Fire |  | Fair | No | Balance 2 span secondary line
Outage | J.E.26.08.14403 | C001884849 | Barnett Brown | Manchester | Completed | Load_252972 | Kendal - 310 | 2026-08-11 08:28 | 2026-08-11 08:33 | 2026-08-11 11:16 | 2026-08-11 12:50 | 2026-08-11 13:43 | 2026-08-11 16:09 | 2026-08-11 16:11 | 2026-08-11 16:11 |  |  | Fair | No | Customer out of service since last hurricane. There’s a transformer pole down
Outage | J.E.26.08.15157 | C001884850 | Barnett Brown | Manchester | Completed | Load_248836 | Spur Tree - 310 | 2026-08-11 08:28 | 2026-08-11 08:33 | 2026-08-11 09:16 | 2026-08-11 09:17 | 2026-08-11 10:29 | 2026-08-11 11:00 | 2026-08-11 11:02 | 2026-08-11 11:02 | BrokenWire |  | Fair | No | Splice and retention service wire
Outage | J.E.26.08.14917 | C001884855 | Kemark Slue | St.Catherine | Completed | Load_253711 | New Michelton - 310 | 2026-08-11 08:31 | 2026-08-11 08:32 | 2026-08-11 11:16 | 2026-08-11 12:07 | 2026-08-11 12:07 | 2026-08-11 11:45 | 2026-08-11 14:02 | 2026-08-11 14:02 |  |  | Fair | No | Upon arrival at the location the crew discovered that a 25 kva 13.8 kv transformer fuse was blown at pole # 581301 resulting from creepers that had made contact with the switch bottom, remove creepers, refuse link and re-energized circuit.
Outage | J.E.26.08.15595 | C001884856 | Horace Malcolm | St.James | Completed | Load_256451 | Rose Hall - 210 | 2026-08-11 08:31 | 2026-08-11 15:03 | 2026-08-11 19:31 | 2026-08-11 19:31 | 2026-08-11 19:52 | 2026-08-11 19:55 | 2026-08-11 19:55 | 2026-08-11 19:55 |  |  | Fair | No | Check and found area ok unable to customer multiple calls to customer unavailable
Outage | J.E.26.08.15600 | C001884857 | Dean- Smith | Hanover | Completed | Load_573350 | Orange Bay - 310 | 2026-08-11 08:32 | 2026-08-11 08:33 | 2026-08-11 15:22 | 2026-08-11 15:23 | 2026-08-11 15:22 | 2026-08-11 15:22 | 2026-08-11 15:23 | 2026-08-11 15:23 |  |  | Rains | No | Unable to complete because of rain
Non-Outage | J.E.26.08.14247 | C001884863 | Fredrick Hamilton | KSAN | Completed | Load_266150 | West Kings House - 410 | 2026-08-11 08:33 | 2026-08-11 08:36 | 2026-08-11 08:43 | 2026-08-11 10:22 | 2026-08-11 10:28 | 2026-08-11 10:38 | 2026-08-11 10:40 | 2026-08-11 10:40 | Fire |  | Fair | No | Phase and neutral found dangling same was corrected Premises now ok
Non-Outage | J.E.26.08.14313 | C001884864 | Fredrick Hamilton | KSAS | Completed | Load_579134 | Washington Blvd - 710 | 2026-08-11 08:33 | 2026-08-11 08:36 | 2026-08-11 08:43 | 2026-08-11 13:34 | 2026-08-11 13:47 | 2026-08-11 14:04 | 2026-08-11 14:04 | 2026-08-11 14:04 |  |  | Fair | No | 222v/107v/113v obtained corrosion detected at pothead same was corrected 3 penunion used
Non-Outage | J.E.26.08.14507 | C001884865 | Fredrick Hamilton | KSAN | Completed | Load_258037 | Washington Blvd - 510 | 2026-08-11 08:33 | 2026-08-11 08:36 | 2026-08-11 08:43 | 2026-08-11 12:02 | 2026-08-11 12:09 | 2026-08-11 12:13 | 2026-08-11 12:13 | 2026-08-11 12:13 |  |  | Fair | No | Premises locked calls to customer went to voicemail
Non-Outage | J.E.26.08.15396 | C001884861 | Fredrick Hamilton | KSAN | Completed | Load_267896 | Constant Spring - 310 | 2026-08-11 08:33 | 2026-08-11 08:36 | 2026-08-11 08:43 | 2026-08-11 12:16 | 2026-08-11 12:26 | 2026-08-11 12:48 | 2026-08-11 12:49 | 2026-08-11 12:49 |  |  | Fair | No | 250v/124v/124v obtained high voltage detected affecting multiple customers please assign to emergency
Outage | J.E.26.08.14468 | C001884860 | Rodclif Dawkins | St.Catherine | Completed | Load_557877 | Tredegar - 310 | 2026-08-11 08:33 | 2026-08-11 08:34 | 2026-08-11 10:16 | 2026-08-11 10:18 | 2026-08-11 10:23 | 2026-08-11 10:23 | 2026-08-11 10:23 | 2026-08-11 10:23 |  |  | Fair | No | Found defective dropout switch on location supplying single phase T-off. Using grip stick line section isolated and switch changed. Line section energized and area okay
Outage | J.E.26.08.14735 | C001884862 | Tyrese Williams | St.Ann | Completed | Load_242574 | Cardiff Hall - 310 | 2026-08-11 08:33 | 2026-08-11 08:34 | 2026-08-11 08:51 | 2026-08-11 10:38 | 2026-08-11 11:25 | 2026-08-11 11:31 | 2026-08-11 11:31 | 2026-08-11 11:31 |  |  | Fair | No | Replace a 25 kva transformer fuse with a 3 amp at pole
Outage | J.E.26.08.15135 | C001884859 | Tyrese Williams | St.Ann | Completed | Load_250391 | Cardiff Hall - 310 | 2026-08-11 08:33 | 2026-08-11 08:36 | 2026-08-11 08:51 | 2026-08-11 08:51 | 2026-08-11 10:34 | 2026-08-11 10:37 | 2026-08-11 10:37 | 2026-08-11 10:37 |  |  | Fair | No | Replace a 5 amp junction fuse at pole
Non-Outage | J.E.26.07.40166 | C001884876 | Rochaine Hussey | KSAN | Completed | Load_265225 | Constant Spring - 210 | 2026-08-11 08:34 | 2026-08-11 08:36 | 2026-08-11 16:07 | 2026-08-11 16:08 | 2026-08-11 16:07 | 2026-08-11 16:09 | 2026-08-11 16:10 | 2026-08-11 16:10 |  |  | Fair | No | Unable to locate Customer was called multiple times no answer
Non-Outage | J.E.26.08.12043 | C001884873 | Rochaine Hussey | KSAN | Completed | Load_264247 | Constant Spring - 410 | 2026-08-11 08:34 | 2026-08-11 08:36 | 2026-08-12 14:09 | 2026-08-12 14:09 | 2026-08-12 14:09 | 2026-08-12 14:11 | 2026-08-12 14:11 | 2026-08-12 14:11 |  |  | Fair | No | Number on the system is incorrect Unable to locate
Non-Outage | J.E.26.08.12043 | C001884875 | Rochaine Hussey | KSAN | Completed | Load_264247 | Constant Spring - 410 | 2026-08-11 08:34 | 2026-08-11 08:36 | 2026-08-12 14:11 | 2026-08-12 14:12 | 2026-08-12 14:12 | 2026-08-12 14:14 | 2026-08-12 14:14 | 2026-08-12 14:14 |  |  | Fair | No | Number on the system is incorrect Unable to locate
Non-Outage | J.E.26.08.13291 | C001884874 | Rochaine Hussey | KSAN | Completed | Load_240400 | Constant Spring - 210 | 2026-08-11 08:34 | 2026-08-11 08:36 | 2026-08-11 13:55 | 2026-08-11 13:56 | 2026-08-11 13:55 | 2026-08-11 15:15 | 2026-08-11 15:17 | 2026-08-11 15:17 |  |  | Fair | No | 25kv transformer was isolated Clamps were called Issue resolved 118/118/236v
Non-Outage | J.E.26.08.13426 | C001884870 | Fredrick Hamilton | KSAS | Completed | Load_257825 | Duhaney - 310 | 2026-08-11 08:34 | 2026-08-11 08:36 | 2026-08-11 08:43 | 2026-08-11 12:54 | 2026-08-11 12:54 | 2026-08-11 12:54 | 2026-08-11 12:55 | 2026-08-11 12:55 |  |  | Fair | No | Please assign to field service
Non-Outage | J.E.26.08.13584 | C001884871 | Fredrick Hamilton | KSAN | Completed | Load_261467 | Washington Blvd - 410 | 2026-08-11 08:34 | 2026-08-11 08:37 | 2026-08-11 08:43 | 2026-08-11 09:32 | 2026-08-11 09:52 | 2026-08-11 10:12 | 2026-08-11 10:12 | 2026-08-11 10:12 | Unable to safely erect ladder |  | Fair | No | 95v119v/197vLow voltage detected on 3 phase connection Bucket truck required unable to use ladder to carry out repairs at pothead
Non-Outage | J.E.26.08.13668 | C001884869 | Fredrick Hamilton | KSAN | Completed | Load_251797 | Constant Spring - 410 | 2026-08-11 08:34 | 2026-08-11 08:36 | 2026-08-11 08:43 | 2026-08-11 11:40 | 2026-08-11 11:43 | 2026-08-11 11:58 | 2026-08-11 11:58 | 2026-08-11 11:58 |  |  | Fair | No | Open secondary at pole emergency required fuse link require to be open to carry out repairs
Non-Outage | J.E.26.08.13697 | C001884867 | Fredrick Hamilton | KSAN | Completed | Load_574835 | Washington Blvd - 610 | 2026-08-11 08:34 | 2026-08-11 08:36 | 2026-08-11 08:43 | 2026-08-11 11:33 | 2026-08-11 11:37 | 2026-08-11 11:38 | 2026-08-11 11:39 | 2026-08-11 11:39 |  |  | Fair | No | Multiple calls to customer went to voicemail
Non-Outage | J.E.26.08.13834 | C001884866 | Fredrick Hamilton | KSAN | Completed | Load_253397 | Washington Blvd - 810 | 2026-08-11 08:34 | 2026-08-11 08:36 | 2026-08-11 08:43 | 2026-08-11 13:01 | 2026-08-11 13:03 | 2026-08-11 13:18 | 2026-08-11 13:18 | 2026-08-11 13:18 |  | Y | Fair | No | 241.8v/120.9v/120.0v obtained Bushing required Banging wires at location Emergency required Customer stated that premises visited by technicians 6 times
Outage | J.E.26.08.15178 | C001884872 | Barnett Brown | Manchester | Completed | Load_251310 | Kendal - 310 | 2026-08-11 08:34 | 2026-08-11 08:37 | 2026-08-11 11:27 | 2026-08-11 11:28 | 2026-08-11 12:29 | 2026-08-11 12:46 | 2026-08-11 12:48 | 2026-08-11 12:48 | Fire |  | Fair | No | Clear service neutral from cable neutral. There was a potential difference.
Outage | J.E.26.08.15270 | C001884868 | Richard Nicholas | St.Catherine | Completed | Load_568138 | Rhodens Pen - 210 | 2026-08-11 08:34 | 2026-08-11 08:35 | 2026-08-11 11:34 | 2026-08-11 11:35 | 2026-08-11 11:53 | 2026-08-11 12:16 | 2026-08-11 12:17 | 2026-08-11 12:17 |  |  | Fair | No | Area found ok.supply was restored last night.
Non-Outage | J.E.26.08.10095 | C001884882 | Edward Royal | KSAN | Completed | Load_256467 | Washington Blvd - 310 | 2026-08-11 08:38 | 2026-08-11 08:39 | 2026-08-11 18:33 | 2026-08-11 18:34 | 2026-08-11 18:34 | 2026-08-11 18:34 | 2026-08-11 18:34 | 2026-08-11 18:34 |  |  | Fair | No | Premises found close
Outage | J.E.26.08.14435 | C001884879 | Kenroy Dale | Manchester | Completed | Load_255527 | Kendal - 210 | 2026-08-11 08:38 | 2026-08-11 15:23 | 2026-08-11 22:23 | 2026-08-11 22:23 | 2026-08-11 23:23 | 2026-08-12 07:33 | 2026-08-12 07:35 | 2026-08-12 07:35 |  |  | Fair | No | Burned off neutral jumper found, connection was remade and area now with supply voltage reading 114/115/229
Outage | J.E.26.08.15033 | C001884880 | Damion Reid | Manchester | Completed | Load_240891 | Kendal - 210 | 2026-08-11 08:38 | 2026-08-11 08:40 | 2026-08-11 12:47 | 2026-08-11 13:45 | 2026-08-11 13:58 | 2026-08-11 14:09 | 2026-08-11 14:11 | 2026-08-11 14:11 |  |  | Fair | No | Remade corroded phase an neutral at secondary pole and in meter socket after correction voltage reading at meter socket phase to neutral 113v-114v across phase 229v
Outage | J.E.26.08.15601 | C001884881 | Kenroy Dale | Manchester | Completed | Load_265474 | Kendal - 210 | 2026-08-11 08:38 | 2026-08-11 15:23 | 2026-08-11 16:12 | 2026-08-11 16:12 | 2026-08-11 17:12 | 2026-08-11 18:42 | 2026-08-11 18:48 | 2026-08-11 18:48 | Fire |  | Fair | No | Open banker 2 transformer to de-bush and retention 2 span of secondary phase, conductor was retention transformer re-closed area now with supply
Outage | J.E.26.08.15608 | C001884896 | Christopher Edwards | KSAN | Completed | Load_266569 | Constant Spring - 410 | 2026-08-11 08:40 | 2026-08-11 08:43 | 2026-08-11 11:43 | 2026-08-11 11:43 | 2026-08-11 12:37 | 2026-08-11 13:16 | 2026-08-11 13:17 | 2026-08-11 13:17 |  |  | Fair | No | Remake phase joint at pothead using (1) one bolt clamps Voltage:114,115,230v
Outage | J.E.26.08.14433 | C001884897 | Wan Carlos Scarlett | Portmore | Completed | Load_266515 | Twickenham - 410 | 2026-08-11 08:41 | 2026-08-11 08:41 | 2026-08-11 11:24 | 2026-08-11 12:23 | 2026-08-11 13:00 | 2026-08-11 13:24 | 2026-08-11 13:25 | 2026-08-11 13:25 |  |  | Fair | No | Customer got reconnected by escalation department power supply has been restored
Outage | J.E.26.08.15603 | C001884898 | Richard Nicholas | St.Catherine | Completed | Load_249334 | Tredegar - 210 | 2026-08-11 08:41 | 2026-08-11 08:42 | 2026-08-11 12:17 | 2026-08-11 12:18 | 2026-08-11 12:58 | 2026-08-11 13:01 | 2026-08-11 13:02 | 2026-08-11 13:02 | LowHangingWires |  | Fair | No | Premises found locked.
Outage | J.E.26.08.15609 | C001884905 | Clyde Brown | Clarendon | Completed | Load_253931 | Monymusk - 410 | 2026-08-11 08:46 | 2026-08-11 08:46 | 2026-08-11 08:58 | 2026-08-11 08:59 | 2026-08-11 10:38 | 2026-08-11 10:38 | 2026-08-11 10:43 | 2026-08-11 10:43 |  |  | Fair | No | Found ok,voltage reading 109/117 and 226 across phases
Outage | J.E.26.08.15068 | C001884912 | Rodclif Dawkins | St.Catherine | Completed | Load_253243 | Tredegar - 310 | 2026-08-11 08:51 | 2026-08-11 08:53 | 2026-08-11 14:23 | 2026-08-11 14:23 | 2026-08-11 14:23 | 2026-08-11 14:23 | 2026-08-11 14:24 | 2026-08-11 14:24 |  |  | Fair | No | Customer found okay
Outage | J.E.26.08.15616 | C001884914 | Marlon Brown | Trelawny | Completed | Load_242706 | Martha Brae - 110 | 2026-08-11 08:54 | 2026-08-11 08:55 | 2026-08-11 10:59 | 2026-08-11 10:59 | 2026-08-11 11:28 | 2026-08-11 11:29 | 2026-08-11 11:29 | 2026-08-11 11:29 |  |  | Fair | No | Same as call number 15621.
Outage | J.E.26.08.15621 | C001884913 | Marlon Brown | Trelawny | Completed | Load_1001463 | Martha Brae - 110 | 2026-08-11 08:54 | 2026-08-11 08:55 | 2026-08-11 10:08 | 2026-08-11 10:10 | 2026-08-11 10:55 | 2026-08-11 10:59 | 2026-08-11 10:59 | 2026-08-11 10:59 |  |  | Fair | No | Check and found ok Voltage found 112/111=223v@ meter socket. Voltage leaving 112/111=223 @ meter socket.
Non-Outage | J.E.26.08.14621 | C001884922 | Selvin White |  | Completed |  |  | 2026-08-11 08:59 | 2026-08-11 10:41 | 2026-08-11 10:55 | 2026-08-11 10:56 | 2026-08-11 11:18 | 2026-08-11 11:20 | 2026-08-11 11:20 | 2026-08-11 11:20 |  |  | Fair | No | Customer was contacted and said supply was restored from yesterday evening.
Outage | J.E.26.08.13480 | C001884926 | Wayne Dillion | St.Elizabeth | Completed | Load_568323 | Maggotty - 110 | 2026-08-11 08:59 | 2026-08-11 09:00 | 2026-08-11 12:29 | 2026-08-11 12:29 | 2026-08-11 12:29 | 2026-08-11 12:31 | 2026-08-11 12:31 | 2026-08-11 12:31 |  |  | Fair | No | Unable to locate and customer not answering the phone.
Outage | J.E.26.08.13614 | C001884925 | Selvin White | St.Elizabeth | Completed | Load_267768 | Maggotty - 110 | 2026-08-11 08:59 | 2026-08-12 07:52 | 2026-08-12 08:40 | 2026-08-12 08:40 | 2026-08-12 08:59 | 2026-08-12 09:03 | 2026-08-12 09:03 | 2026-08-12 09:03 |  |  | Fair | No | Please refer to Jesse Morales at the field service department so the field service department can make arrangements to check premises.
Outage | J.E.26.08.14396 | C001884927 | Moses Elliston | St.Catherine | Completed | Load_262911 | Tredegar - 510 | 2026-08-11 08:59 | 2026-08-11 09:00 | 2026-08-11 09:42 | 2026-08-11 09:43 | 2026-08-11 09:42 | 2026-08-11 09:42 | 2026-08-11 09:43 | 2026-08-11 09:43 |  |  | Fair | No | Supply ok at premises.
Outage | J.E.26.08.14401 | C001884924 | Wayne Dillion | Manchester | Completed | Load_239279 | Spur Tree - 210 | 2026-08-11 08:59 | 2026-08-11 09:00 | 2026-08-11 13:24 | 2026-08-11 13:25 | 2026-08-11 13:24 | 2026-08-11 13:26 | 2026-08-11 13:26 | 2026-08-11 13:26 |  |  | Fair | No | Please refer call to field hexing box in area customer meter is on but still no supply
Outage | J.E.26.08.14402 | C001884923 | Wayne Dillion | St.Elizabeth | Completed | Load_256896 | Maggotty - 110 | 2026-08-11 08:59 | 2026-08-11 09:00 | 2026-08-11 10:17 | 2026-08-11 10:17 | 2026-08-11 10:17 | 2026-08-11 10:20 | 2026-08-11 10:20 | 2026-08-11 10:20 |  |  | Fair | No | Customer said supply was restored to the area.
Non-Outage | J.E.26.08.14449 | C001884943 | Dwain Samuels | Westmoreland | Completed | Load_292703 | Paradise - 210 | 2026-08-11 09:03 | 2026-08-11 09:05 | 2026-08-11 09:50 | 2026-08-11 10:12 | 2026-08-11 11:10 | 2026-08-11 11:46 | 2026-08-11 11:49 | 2026-08-11 11:49 |  |  | Fair | No | Corrosion found at 3 wire pot head . Voltage check 103-102-205. Corrosion clear use 2 pen union and 1 one bolt clamp. Voltage check 113-114-227
Non-Outage | J.E.26.08.14688 | C001884942 | Dwain Samuels | Westmoreland | Completed | Load_247636 | Paradise - 210 | 2026-08-11 09:03 | 2026-08-11 09:05 | 2026-08-11 09:50 | 2026-08-11 12:35 | 2026-08-11 12:34 | 2026-08-11 12:35 | 2026-08-11 12:35 | 2026-08-11 12:35 |  |  | Fair | No | Called customer said supply was restored
Non-Outage | J.E.26.08.14937 | C001884941 | Dwain Samuels | Westmoreland | Completed | Load_249078 | Paradise - 210 | 2026-08-11 09:03 | 2026-08-11 09:05 | 2026-08-11 09:50 | 2026-08-11 12:27 | 2026-08-11 12:27 | 2026-08-11 12:27 | 2026-08-11 12:28 | 2026-08-11 12:28 |  |  | Fair | No | Called customer said supply was restored
Non-Outage | J.E.26.08.15341 | C001884940 | Dwain Samuels | Westmoreland | Completed | Load_253691 | Paradise - 210 | 2026-08-11 09:03 | 2026-08-11 09:05 | 2026-08-11 09:50 | 2026-08-11 11:50 | 2026-08-11 11:50 | 2026-08-11 12:18 | 2026-08-11 12:19 | 2026-08-11 12:19 |  |  | Fair | No | Area affected by low voltage.transformer feeding too far
Outage | J.E.26.08.14926 | C001884944 | Moses Elliston | St.Catherine | Completed | Load_406252 | Rhodens Pen - 210 | 2026-08-11 09:04 | 2026-08-11 09:05 | 2026-08-12 13:37 | 2026-08-12 13:37 | 2026-08-12 13:37 | 2026-08-12 13:44 | 2026-08-12 13:50 | 2026-08-12 13:50 |  |  | Rains | No | Broken 3 wire service neutral repaired with one clamp.
Non-Outage | J.E.26.08.14340 | C001884953 | Richman Whyte | Westmoreland | Completed | Load_249420 | Paradise - 310 | 2026-08-11 09:15 | 2026-08-11 15:38 | 2026-08-11 17:51 | 2026-08-11 17:51 | 2026-08-11 17:51 | 2026-08-11 17:51 | 2026-08-11 17:52 | 2026-08-11 17:52 |  |  | Fair | No | Internal problem advise to fix voltage 114 114 226
Non-Outage | J.E.26.03.25014 | C001884956 | Nicholas Dillon | St.Elizabeth | Completed | Load_265222 | Maggotty - 210 | 2026-08-11 09:18 | 2026-08-11 09:19 | 2026-08-12 14:28 | 2026-08-12 14:29 | 2026-08-12 14:28 | 2026-08-12 14:30 | 2026-08-12 14:32 | 2026-08-12 14:32 |  |  | Fair | Yes | Check and found corrosion at pothead clean joint and use 2 pen union before I left voltage is 116 115 phase to phase 232
Non-Outage | J.E.26.08.04791 | C001884961 | Wan Carlos Scarlett | Portmore | Completed | Load_243335 | Naggo Head - 610 | 2026-08-11 09:18 | 2026-08-11 09:19 | 2026-08-11 10:34 | 2026-08-11 10:35 | 2026-08-11 10:52 | 2026-08-11 11:19 | 2026-08-11 11:24 | 2026-08-11 11:24 |  |  | Fair | No | Found customer with internal problem customer load side service wire defective advised customer to contact licensed electrician to fix problem
Non-Outage | J.E.26.08.15638 | C001884966 | Royston Montague | St.Catherine | Completed | Load_246112 | Rhodens Pen - 410 | 2026-08-11 09:19 | 2026-08-11 09:20 | 2026-08-11 10:24 | 2026-08-11 10:27 | 2026-08-11 12:14 | 2026-08-11 13:03 | 2026-08-11 13:04 | 2026-08-11 13:04 |  |  | Fair | No | Faulty neutral at customer take off point. Same corrected, voltage found 216v 100v 115v voltage after job completion are 216v 106v 106v
Non-Outage | J.E.26.08.13298 | C001884976 | Error Coore | Manchester | Completed | Load_266835 | Porus - 310 | 2026-08-11 09:21 | 2026-08-11 09:23 | 2026-08-12 15:27 | 2026-08-12 15:28 | 2026-08-12 16:05 | 2026-08-12 16:17 | 2026-08-12 16:19 | 2026-08-12 16:19 |  |  | Fair | No | Premises found ok voltage reading 118/117/235 volts
Non-Outage | J.E.26.08.14155 | C001884975 | Error Coore | Manchester | Completed | Load_266835 | Porus - 310 | 2026-08-11 09:21 | 2026-08-11 09:23 | 2026-08-12 13:21 | 2026-08-12 13:22 | 2026-08-12 14:12 | 2026-08-12 14:35 | 2026-08-12 14:37 | 2026-08-12 14:37 |  |  | Fair | No | Premises found ok voltage reading 114/114/228 volts
Non-Outage | J.E.26.08.14258 | C001884974 | Error Coore | Manchester | Completed | Load_257520 | Porus - 210 | 2026-08-11 09:21 | 2026-08-11 09:23 | 2026-08-12 16:19 | 2026-08-12 16:20 | 2026-08-12 16:38 | 2026-08-12 16:54 | 2026-08-12 16:56 | 2026-08-12 16:56 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.08.15615 | C001884973 | Error Coore | Manchester | Completed | Load_292371 | Spur Tree - 310 | 2026-08-11 09:21 | 2026-08-11 09:23 | 2026-08-11 13:34 | 2026-08-11 13:35 | 2026-08-11 14:01 | 2026-08-11 14:30 | 2026-08-11 14:31 | 2026-08-11 14:31 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.26517 | C001884982 | Error Coore | Manchester | Completed | Load_254646 | Spur Tree - 310 | 2026-08-11 09:22 | 2026-08-11 09:23 | 2026-08-11 11:53 | 2026-08-11 11:54 | 2026-08-11 12:35 | 2026-08-11 13:32 | 2026-08-11 13:34 | 2026-08-11 13:34 |  |  | Fair | No | Found customer with wrap connection at pothead remade wrap connection using 3 service sleeve voltage reading 116/115/231 volts
Non-Outage | J.E.26.07.33065 | C001884981 | Error Coore | Manchester | Completed | Load_244764 | Kendal - 310 | 2026-08-11 09:22 | 2026-08-11 09:23 | 2026-08-11 15:44 | 2026-08-11 15:45 | 2026-08-11 16:30 | 2026-08-11 16:44 | 2026-08-11 16:45 | 2026-08-11 16:45 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.34516 | C001884978 | Error Coore | Manchester | Completed | Load_270245 | Kendal - 310 | 2026-08-11 09:22 | 2026-08-11 09:23 | 2026-08-11 10:17 | 2026-08-11 10:17 | 2026-08-11 10:35 | 2026-08-11 10:47 | 2026-08-11 10:48 | 2026-08-11 10:48 |  |  | Fair | No | Premises found ok voltage reading 115 volts
Non-Outage | J.E.26.07.36760 | C001884979 | Error Coore | Manchester | Completed | Load_1002521 | Kendal - 310 | 2026-08-11 09:22 | 2026-08-11 09:23 | 2026-08-11 14:33 | 2026-08-11 14:34 | 2026-08-11 15:12 | 2026-08-11 15:41 | 2026-08-11 15:43 | 2026-08-11 15:43 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.08.13266 | C001884980 | Error Coore | Manchester | Completed | Load_237916 | Spur Tree - 310 | 2026-08-11 09:22 | 2026-08-11 09:23 | 2026-08-11 10:49 | 2026-08-11 10:49 | 2026-08-11 11:32 | 2026-08-11 11:51 | 2026-08-11 11:53 | 2026-08-11 11:53 |  |  | Fair | No | Premises found ok voltage reading 117/116/233 volts
Non-Outage | J.E.26.07.30455 | C001884985 | Wan Carlos Scarlett | Portmore | Completed | Load_255537 | Naggo Head - 610 | 2026-08-11 09:25 | 2026-08-11 09:26 | 2026-08-11 11:18 | 2026-08-11 11:25 | 2026-08-11 11:39 | 2026-08-11 12:21 | 2026-08-11 12:22 | 2026-08-11 12:22 |  |  | Fair | No | Found customer 3 wire service at pothead with phase and neutral corroded use 3 Penn union at service wire phase and neutral readings 115-114-230
Outage | J.E.26.08.15653 | C001884990 | Moses Elliston | St.Catherine | Completed | Load_248235 | Tredegar - 410 | 2026-08-11 09:37 | 2026-08-11 09:38 | 2026-08-11 10:37 | 2026-08-11 10:37 | 2026-08-11 10:37 | 2026-08-11 10:37 | 2026-08-11 10:38 | 2026-08-11 10:38 |  |  | Fair | No | Not located,no answer from cell
Outage | J.E.26.08.15655 | C001884991 | Edward Royal | KSAN | Completed | Load_267241 | Washington Blvd - 310 | 2026-08-11 09:40 | 2026-08-11 09:50 | 2026-08-11 17:25 | 2026-08-11 17:26 | 2026-08-11 17:25 | 2026-08-11 17:25 | 2026-08-11 17:27 | 2026-08-11 17:27 |  |  | Fair | No | Meter not responding meter need to be check reffered to field
Non-Outage | J.E.26.08.13590 | C001884999 | Richard Nicholas | St.Catherine | Completed | Load_253597 | Tredegar - 210 | 2026-08-11 09:45 | 2026-08-11 09:45 | 2026-08-11 13:02 | 2026-08-11 13:03 | 2026-08-11 13:52 | 2026-08-11 14:45 | 2026-08-11 14:52 | 2026-08-11 14:52 |  |  | Fair | No | Supply checked at meter at 4w meter socket,meter socket lug found with corrosion and customer private service wire that runs from meter to building also damaged at mid span,phase and neutral burnt out.voltage reading taking at line side at pothead,117,118,235 and the high leg is 108 due to one of the power transformer fuse found open however customer is not using the 3phase supply currently therefore same was left as found.customer presently using single phase 220v.all the findings was pointed out to a gentleman that doing welding at the premises.
Outage | J.E.26.08.15664 | C001885018 | Kenroy Dale | Manchester | Completed | Load_263978 | Kendal - 210 | 2026-08-11 09:52 | 2026-08-11 15:23 | 2026-08-11 18:58 | 2026-08-11 18:59 | 2026-08-11 20:04 | 2026-08-11 20:30 | 2026-08-11 20:33 | 2026-08-11 20:33 | BrokenWire |  | Fair | No | Blown 3 amp transformer fuse found line patrol 1 span of secondary neutral found broken cause from vehicle accident, conductor was splice and retention blown fuse replaced and area now with supply
Outage | J.E.26.08.15606 | C001885031 | Ryan Richards | Manchester | Completed | Load_1002521 | Kendal - 310 | 2026-08-11 09:59 | 2026-08-11 15:25 | 2026-08-11 20:11 | 2026-08-11 20:12 | 2026-08-11 21:38 | 2026-08-11 22:10 | 2026-08-11 22:10 | 2026-08-11 22:10 |  |  | Fair | No | Premises found with supply customer seems to disconnect for non payment of bill
Outage | J.E.26.08.14334 | C001885048 | Richman Whyte | Westmoreland | Completed | Load_238003 | Paradise - 310 | 2026-08-11 10:01 | 2026-08-11 10:02 | 2026-08-11 13:05 | 2026-08-11 13:05 | 2026-08-11 13:05 | 2026-08-11 13:06 | 2026-08-11 13:06 | 2026-08-11 13:06 |  |  | Fair | No | Run an connected 60ft #6 triplex service wire voltage 113 113 226 use 3# service connectors #3 clamps
Outage | J.E.26.08.15694 | C001885050 | Edward Royal | KSAS | Completed | Load_261811 | Hunts Bay - 810 | 2026-08-11 10:04 | 2026-08-11 10:33 | 2026-08-11 12:20 | 2026-08-11 12:20 | 2026-08-11 12:20 | 2026-08-11 12:21 | 2026-08-11 12:21 | 2026-08-11 12:21 |  |  | Fair | No | When contacted customer said that no one is at home until Thursday
Non-Outage | J.E.26.08.15648 | C001885067 | Odaine Johnson | Clarendon | Completed | Load_246809 | May Pen - 210 | 2026-08-11 10:05 | 2026-08-11 10:06 | 2026-08-11 10:13 | 2026-08-11 11:23 | 2026-08-11 11:47 | 2026-08-11 11:47 | 2026-08-11 11:49 | 2026-08-11 11:49 |  |  | Fair | No | Premises found okay voltage reading 119/119/238 volts
Non-Outage | J.E.26.08.14752 | C001885068 | Clyde Brown | Clarendon | Completed | Load_238199 | Parnassus - 310 | 2026-08-11 10:06 | 2026-08-11 10:07 | 2026-08-11 10:43 | 2026-08-11 13:23 | 2026-08-11 13:46 | 2026-08-11 13:45 | 2026-08-11 13:49 | 2026-08-11 13:49 |  |  | Fair | No | Premises closed
Non-Outage | J.E.26.08.15545 | C001885069 | Clyde Brown | Clarendon | Completed | Load_260474 | Monymusk - 410 | 2026-08-11 10:07 | 2026-08-11 10:07 | 2026-08-11 10:43 | 2026-08-11 12:09 | 2026-08-11 12:31 | 2026-08-11 12:29 | 2026-08-11 12:40 | 2026-08-11 12:40 |  |  | Fair | No | Cannot be located customer not answering phone
Non-Outage | J.E.26.08.15605 | C001885070 | Odaine Johnson | Clarendon | Completed | Load_351851 | May Pen - 210 | 2026-08-11 10:07 | 2026-08-11 10:08 | 2026-08-11 10:13 | 2026-08-11 10:36 | 2026-08-11 11:14 | 2026-08-11 11:14 | 2026-08-11 11:15 | 2026-08-11 11:15 |  |  | Fair | No | Burn off phase found at pole remade connection using 1 one bolt clamp voltage reading 119/119/239 volts
Outage | J.E.26.08.15697 | C001885082 | Tyrese Williams | St.Ann | Completed | Load_268597 | Cardiff Hall - 310 | 2026-08-11 10:14 | 2026-08-11 10:16 | 2026-08-11 11:59 | 2026-08-11 13:21 | 2026-08-11 13:50 | 2026-08-11 14:18 | 2026-08-11 14:18 | 2026-08-11 14:18 |  |  | Fair | No | Customer meter found burnt need to change
Outage | J.E.26.08.15644 | C001885084 | Tyrese Williams | St.Ann | Completed | Load_256510 | Cardiff Hall - 210 | 2026-08-11 10:15 | 2026-08-11 10:16 | 2026-08-11 12:31 | 2026-08-11 12:52 | 2026-08-11 13:12 | 2026-08-11 13:20 | 2026-08-11 13:21 | 2026-08-11 13:21 | BrokenPole |  | Fair | No | Premises found ok voltage check 110/111/221
Outage | J.E.26.08.15689 | C001885083 | Roxroy Needham | St.Ann | Completed | Load_261173 | Roaring River - 210 | 2026-08-11 10:15 | 2026-08-11 10:15 | 2026-08-11 10:52 | 2026-08-11 10:53 | 2026-08-11 12:12 | 2026-08-11 12:18 | 2026-08-11 12:19 | 2026-08-11 12:19 |  | Y | Fair | No | Replace a 8 amps junction fuse at pole
Outage | J.E.26.08.14964 | C001885098 | Moses Elliston | St.Catherine | Completed | Load_247419 | New Michelton - 310 | 2026-08-11 10:20 | 2026-08-11 10:20 | 2026-08-11 11:20 | 2026-08-11 11:20 | 2026-08-11 11:20 | 2026-08-11 11:00 | 2026-08-11 11:22 | 2026-08-11 11:22 |  |  | Fair | No | Supply ok .Outage was in area.
Outage | J.E.26.08.15701 | C001885127 | Clyde Brown | Clarendon | Completed | Load_246357 | Parnassus - 210 | 2026-08-11 10:26 | 2026-08-11 10:26 | 2026-08-11 10:43 | 2026-08-11 12:41 | 2026-08-11 12:57 | 2026-08-11 13:07 | 2026-08-11 13:19 | 2026-08-11 13:19 |  |  | Fair | No | Blown 3 amps fuse for bank of 3x25 kva transformer line patrolled and no fault seen,blown fuse replaced
Outage | J.E.26.08.15744 | C001885149 | Wayne Dillion | St.Elizabeth | Completed | Load_292638 | Maggotty - 110 | 2026-08-11 10:37 | 2026-08-11 10:43 | 2026-08-11 10:58 | 2026-08-11 10:59 | 2026-08-11 12:02 | 2026-08-11 12:20 | 2026-08-11 12:22 | 2026-08-11 12:22 | Fire |  | Fair | No | Supply check and found service wire neutral burnt off. Repair same using 1 clamp and 3 linkets. Supply leave working okay reading 109v, 110v and cross phase 219volts.
Outage | J.E.26.08.15744 | C001885152 | Wayne Dillion | St.Elizabeth | Completed | Load_292638 | Maggotty - 110 | 2026-08-11 10:42 | 2026-08-11 12:32 | 2026-08-11 13:10 | 2026-08-11 13:10 | 2026-08-11 13:10 | 2026-08-11 13:11 | 2026-08-11 13:11 | 2026-08-11 13:11 | Fire |  | Fair | No | Call related to the same call that was just sent. The problem was resolved.
Non-Outage | J.E.26.08.00094 | C001885155 | Rusean Allen | KSAS | Completed | Load_239845 | Rockfort - 410 | 2026-08-11 10:43 | 2026-08-11 10:50 | 2026-08-11 11:49 | 2026-08-11 12:55 | 2026-08-11 13:12 | 2026-08-11 13:42 | 2026-08-11 13:42 | 2026-08-11 13:42 |  |  | Fair | No | Corroded clamp found at secondary jumper, clamp was changed.Voltage: 116 116 232
Outage | J.E.26.08.15770 | C001885156 | Raymond Lewis | St.Ann | Completed | Load_254095 | Ocho Rios - 310 | 2026-08-11 10:44 | 2026-08-12 07:53 | 2026-08-12 11:33 | 2026-08-12 11:33 | 2026-08-12 11:33 | 2026-08-12 11:34 | 2026-08-12 11:34 | 2026-08-12 11:34 |  |  | Fair | No | Customer meter burn up
Non-Outage | J.E.26.07.17498 | C001885165 | Moses Elliston | St.Catherine | Completed | Load_1001612 | Tredegar - 310 | 2026-08-11 10:45 | 2026-08-11 10:46 | 2026-08-11 11:25 | 2026-08-11 11:26 | 2026-08-11 11:25 | 2026-08-11 11:25 | 2026-08-11 11:26 | 2026-08-11 11:26 |  |  | Fair | No | For next crew
Outage | J.E.26.08.15765 | C001885157 | Cliton Henry | St.Mary | Completed | Load_254009 | Oracabessa - 210 | 2026-08-11 10:45 | 2026-08-11 10:46 | 2026-08-11 12:03 | 2026-08-11 12:03 | 2026-08-11 12:08 | 2026-08-11 12:08 | 2026-08-11 12:15 | 2026-08-11 12:15 |  |  | Fair | No | RAMI infrastructure, the customer found disconnected. Supply restored with the assistance from the escalation team. Kindly refer to Franklyn Coach to correct problems too much error disconnection taking place in this Hexing enclosed.
Non-Outage | J.E.26.08.05450 | C001885176 | Kemark Slue | St.Catherine | Completed | Load_243610 | New Michelton - 210 | 2026-08-11 10:52 | 2026-08-11 10:52 | 2026-08-11 11:45 | 2026-08-11 14:03 | 2026-08-11 14:02 | 2026-08-11 14:03 | 2026-08-11 14:10 | 2026-08-11 14:10 |  |  | Fair | No | Upon arrival at the location the crew discovered that 25 kva 13.8 kv transformer drop lead for lower phase was burnt off, isolate said transformer, terminate conductor and remake joint.
Non-Outage | J.E.26.08.15597 | C001885179 | Edward Royal | KSAN | Completed | Load_257472 | Washington Blvd - 710 | 2026-08-11 10:53 | 2026-08-11 10:55 | 2026-08-11 12:28 | 2026-08-11 12:28 | 2026-08-11 12:38 | 2026-08-11 12:56 | 2026-08-11 13:00 | 2026-08-11 13:00 | BrokenWire |  | Fair | No | Number 2 quad need to be change approximately 200ft of number 2 quad is needed
Non-Outage | J.E.26.08.15787 | C001885180 | Odeanie Davis | KSAS | Completed | Load_266562 | Hunts Bay - 310 | 2026-08-11 10:53 | 2026-08-11 10:55 | 2026-08-11 11:51 | 2026-08-11 12:14 | 2026-08-11 12:14 | 2026-08-11 12:23 | 2026-08-11 12:24 | 2026-08-11 12:24 |  |  | Fair | No | Phase and neutral burnt off from secondary, secondary wire needs to be replaced,
Outage | J.E.26.08.15843 | C001885197 | Stephen Taylor | St.Thomas | Completed | Load_243122 | Lysson - 410 | 2026-08-11 11:00 | 2026-08-11 11:01 | 2026-08-11 11:59 | 2026-08-11 12:00 | 2026-08-11 11:59 | 2026-08-11 12:03 | 2026-08-11 12:03 | 2026-08-11 12:03 |  |  | Fair | No | Jps maintenance team are working in the area
Non-Outage | J.E.26.08.15764 | C001885206 | Gregory Grossett | Portland | Completed | Load_240735 | Port Antonio - 410 | 2026-08-11 11:07 | 2026-08-12 15:41 | 2026-08-12 16:03 | 2026-08-12 16:04 | 2026-08-12 16:44 | 2026-08-12 16:44 | 2026-08-12 16:45 | 2026-08-12 16:45 | LeaningPole |  | Fair | No | Customer meter pole is defective, we advise the customer to get certified electrician and repair.
Outage | J.E.26.08.14773 | C001885221 | Moses Elliston | St.Catherine | Completed | Load_1001550 | Tredegar - 510 | 2026-08-11 11:17 | 2026-08-11 11:18 | 2026-08-11 13:23 | 2026-08-11 13:24 | 2026-08-11 13:23 | 2026-08-11 13:50 | 2026-08-11 13:52 | 2026-08-11 13:52 |  |  | Fair | No | Broken 3 wire service replaced with 60 ‘ 3 clamps ,3 linkets
Non-Outage | J.E.26.08.15853 | C001885222 | Odaine Johnson | St.Catherine | Completed | Load_243516 | Rhodens Pen - 310 | 2026-08-11 11:18 | 2026-08-11 11:18 | 2026-08-11 11:52 | 2026-08-11 11:53 | 2026-08-11 11:54 | 2026-08-11 11:54 | 2026-08-11 11:55 | 2026-08-11 11:55 |  |  | Fair | No | Unable to locate premises multiple efforts made to contact customer but was unsuccessful
Outage | J.E.26.08.15702 | C001885224 | Orville Lee | Portmore | Completed | Load_570096 | Naggo Head - 610 | 2026-08-11 11:20 | 2026-08-11 12:38 | 2026-08-11 12:43 | 2026-08-11 12:43 | 2026-08-11 13:06 | 2026-08-11 13:16 | 2026-08-11 13:21 | 2026-08-11 13:21 |  |  | Fair | No | Upon arrival unauthorized work is being carried out by the developer Unable to energize
Outage | J.E.26.08.15857 | C001885231 | Edward Royal | KSAN | Completed | Load_268663 | Washington Blvd - 710 | 2026-08-11 11:25 | 2026-08-11 11:42 | 2026-08-11 12:16 | 2026-08-11 12:16 | 2026-08-11 12:16 | 2026-08-11 12:16 | 2026-08-11 12:16 | 2026-08-11 12:16 |  |  | Fair | No | Premises found ok related to outage
Non-Outage | J.E.26.07.37016 | C001885245 | Roxroy Needham | St.Ann | Completed | Load_240222 | Ocho Rios - 310 | 2026-08-11 11:27 | 2026-08-11 11:28 | 2026-08-11 12:21 | 2026-08-11 12:21 | 2026-08-11 13:15 | 2026-08-11 13:54 | 2026-08-11 13:57 | 2026-08-11 13:57 |  | Y | Fair | No | Open a 25 KVA transformer at pole to repair transformer leed used 2 pg clamp
Outage | J.E.26.08.15886 | C001885257 | Collin Robinson | Portland | Completed | Load_265583 | Port Antonio - 410 | 2026-08-11 11:33 | 2026-08-11 11:34 | 2026-08-11 12:42 | 2026-08-11 12:43 | 2026-08-11 13:06 | 2026-08-11 13:11 | 2026-08-11 13:11 | 2026-08-11 13:11 |  |  | Fair | No | Premises found with supply Meter socket voltage reading 120v 119v 239v
Outage | J.E.26.08.15888 | C001885258 | Omar King | St.Ann | Completed | Load_252888 | Upper White River - 210 | 2026-08-11 11:34 | 2026-08-11 19:58 | 2026-08-11 21:59 | 2026-08-11 21:59 | 2026-08-11 23:30 | 2026-08-11 23:32 | 2026-08-11 23:32 | 2026-08-11 23:32 |  |  | Fair | No | Unable to find customer call several times no answer directions not sufficient
Outage | J.E.26.08.15856 | C001885260 | Omar King | St.Ann | Completed | Load_239474 | Ocho Rios - 410 | 2026-08-11 11:35 | 2026-08-11 19:58 | 2026-08-11 21:33 | 2026-08-11 21:34 | 2026-08-11 21:57 | 2026-08-11 21:58 | 2026-08-11 21:58 | 2026-08-11 21:58 |  |  | Fair | No | Unable to find customer call several times no answer directions not sufficient
Outage | J.E.26.08.15894 | C001885273 | Moses Elliston | St.Catherine | Completed | Load_262925 | Tredegar - 410 | 2026-08-11 11:39 | 2026-08-11 11:40 | 2026-08-12 10:11 | 2026-08-12 10:11 | 2026-08-12 10:11 | 2026-08-12 10:11 | 2026-08-12 10:11 | 2026-08-12 10:11 |  |  | Fair | No | Supply ok at premises
Non-Outage | J.E.26.08.14444 | C001885284 | Neville Spencer |  | Completed |  |  | 2026-08-11 11:45 | 2026-08-11 11:46 | 2026-08-11 13:23 | 2026-08-11 13:23 | 2026-08-11 13:23 | 2026-08-11 13:23 | 2026-08-11 13:24 | 2026-08-11 13:24 |  |  | Fair | No | Found supply in area call resolved yesterday.
Non-Outage | J.E.26.08.12500 | C001885308 | Collin Robinson | Portland | Completed | Load_354844 | Port Antonio - 410 | 2026-08-11 11:56 | 2026-08-11 11:57 | 2026-08-11 13:18 | 2026-08-11 13:19 | 2026-08-11 13:22 | 2026-08-11 13:29 | 2026-08-11 13:29 | 2026-08-11 13:29 |  |  | Fair | No | Unable to locate customer
Outage | J.E.26.08.15906 | C001885314 | Stephen Taylor | St.Thomas | Completed | Load_268683 | Lysson - 410 | 2026-08-11 12:01 | 2026-08-11 12:02 | 2026-08-11 14:04 | 2026-08-11 15:59 | 2026-08-11 15:59 | 2026-08-11 16:02 | 2026-08-11 16:02 | 2026-08-11 16:02 |  |  | Fair | No | See trip saver down no number on pole patrol see nothing and close up back 65 amp trip saver safely all customer is now okay
Outage | J.E.26.08.15949 | C001885320 | Moses Elliston | St.Catherine | Completed | Load_254079 | Rhodens Pen - 210 | 2026-08-11 12:06 | 2026-08-11 12:17 | 2026-08-11 12:42 | 2026-08-11 12:42 | 2026-08-11 12:42 | 2026-08-11 12:30 | 2026-08-11 12:44 | 2026-08-11 12:44 |  |  | Fair | No | Credit added to prepaid account
Outage | J.E.26.08.15923 | C001885321 | Gregory Grossett | Portland | Completed | Load_267378 | Port Antonio - 310 | 2026-08-11 12:08 | 2026-08-11 15:04 | 2026-08-11 18:44 | 2026-08-11 18:44 | 2026-08-11 20:13 | 2026-08-11 20:15 | 2026-08-11 20:15 | 2026-08-11 20:15 |  |  | Fair | No | 220 service phase broken at pole repair and ok material use 1-one bolt clamp.
Outage | J.E.26.08.15930 | C001885322 | Gregory Grossett | Portland | Completed | Load_262308 | Port Antonio - 310 | 2026-08-11 12:08 | 2026-08-11 15:04 | 2026-08-11 15:18 | 2026-08-11 15:19 | 2026-08-11 16:07 | 2026-08-11 16:09 | 2026-08-11 16:09 | 2026-08-11 16:09 | Fire |  | Fair | No | After making several calls we could not locate the customer.
Non-Outage | J.E.26.08.15959 | C001885323 | Rodclif Dawkins | St.Catherine | Completed | Load_238492 | Tredegar - 310 | 2026-08-11 12:10 | 2026-08-11 12:13 | 2026-08-11 13:55 | 2026-08-11 13:55 | 2026-08-11 14:21 | 2026-08-11 14:21 | 2026-08-11 14:23 | 2026-08-11 14:23 | BangingWires |  | Fair | No | Low hanging wires customer refers to are third party communication wires. Customer was advised to contact relevant company
Outage | J.E.26.08.15945 | C001885329 | Ryan Richards | Manchester | Completed | Load_242175 | Spur Tree - 310 | 2026-08-11 12:11 | 2026-08-11 15:25 | 2026-08-11 17:53 | 2026-08-11 17:54 | 2026-08-11 18:46 | 2026-08-11 20:10 | 2026-08-11 20:11 | 2026-08-11 20:11 |  |  | Fair | No | 4 blown junction fuse found two 20&two 10 amp junction fuses line patrol tree limb found broken and the primary conductor chap tree limb from line further checks made nothing else found blown 10&20 amp junction fuse was replaced
Non-Outage | J.E.26.08.15968 | C001885342 | Odaine Johnson | St.Catherine | Completed | Load_243516 | Rhodens Pen - 310 | 2026-08-11 12:18 | 2026-08-11 12:19 | 2026-08-11 13:03 | 2026-08-11 13:04 | 2026-08-11 13:36 | 2026-08-11 13:36 | 2026-08-11 13:39 | 2026-08-11 13:39 |  |  | Fair | No | Corroded neutral found at pole remade connection using 1 one bolt clamp voltage reading 112/113/225 volts
Outage | J.E.26.08.15979 | C001885354 | Odaine Johnson | Clarendon | Completed | Load_255181 | Monymusk - 410 | 2026-08-11 12:21 | 2026-08-11 12:45 | 2026-08-11 14:25 | 2026-08-11 14:26 | 2026-08-11 14:37 | 2026-08-11 14:38 | 2026-08-11 14:39 | 2026-08-11 14:39 |  |  | Fair | No | Corroded phase and neutral found at pothead remade connection using 2 pen union voltage reading 116 volts
Non-Outage | J.E.26.08.15985 | C001885372 | Royston Montague | St.Catherine | Completed | Load_242349 | Rhodens Pen - 410 | 2026-08-11 12:32 | 2026-08-11 12:33 | 2026-08-11 13:04 | 2026-08-11 13:13 | 2026-08-11 13:13 | 2026-08-11 14:02 | 2026-08-11 14:03 | 2026-08-11 14:03 |  |  | Fair | No | Slack connection at pothead. Same corrected. Voltage 216v 105v 109V
Outage | J.E.26.08.15963 | C001885371 | Neckell Ormsby | St.Mary | Completed | Load_251602 | Highgate - 210 | 2026-08-11 12:32 | 2026-08-11 12:32 | 2026-08-11 13:30 | 2026-08-11 13:31 | 2026-08-11 14:21 | 2026-08-11 14:32 | 2026-08-11 14:32 | 2026-08-11 14:32 |  |  | Fair | No | Found broken secondary neutral isolate by opening 25kva transformer at pole 031055 please refer to other team due to shft ended
Non-Outage | J.E.26.08.15933 | C001885374 | Clyde Brown |  | Completed |  |  | 2026-08-11 12:33 | 2026-08-11 12:34 | 2026-08-11 13:22 | 2026-08-11 14:38 | 2026-08-11 14:58 | 2026-08-11 14:58 | 2026-08-11 15:06 | 2026-08-11 15:06 | BrokenPole |  | Fair | No | Tw/R 30c6 pole broken and need to be change urgently secondary line on pole .
Outage | J.E.26.08.15996 | C001885375 | Edward Royal | KSAN | Completed | Load_261386 | Washington Blvd - 710 | 2026-08-11 12:33 | 2026-08-11 12:34 | 2026-08-11 13:02 | 2026-08-11 13:02 | 2026-08-11 13:20 | 2026-08-11 14:23 | 2026-08-11 14:24 | 2026-08-11 14:24 | BrokenWire |  | Fair | No | Spliced and reconnected service cable using 2 single bolt clamp
Outage | J.E.26.08.16004 | C001885378 | Wan Carlos Scarlett | Portmore | Completed | Load_245206 | Naggo Head - 610 | 2026-08-11 12:35 | 2026-08-11 12:36 | 2026-08-11 12:47 | 2026-08-11 13:26 | 2026-08-11 14:08 | 2026-08-11 14:09 | 2026-08-11 14:13 | 2026-08-11 14:13 |  |  | Fair | No | Found customer 3 wire service at pole with 1 of the phase wire broken off use 1 one bolt clamps at pole readings 116 116 232
Outage | J.E.26.08.16005 | C001885380 | Richman Whyte | Westmoreland | Completed | Load_243785 | Paradise - 310 | 2026-08-11 12:35 | 2026-08-11 12:36 | 2026-08-11 15:42 | 2026-08-11 15:43 | 2026-08-11 15:42 | 2026-08-11 15:43 | 2026-08-11 15:43 | 2026-08-11 15:43 |  |  | Fair | No | Unable to locate or contact customer on the phone
Outage | J.E.26.08.16015 | C001885388 | Edward Royal | KSAS | Completed | Load_244976 | Duhaney - 410 | 2026-08-11 12:38 | 2026-08-11 12:38 | 2026-08-11 16:00 | 2026-08-11 16:01 | 2026-08-11 16:19 | 2026-08-11 16:27 | 2026-08-11 16:27 | 2026-08-11 16:27 | BrokenPole |  | Fair | No | Transmission pole brake and buss primary and concrete pole need to be change referred to maintenance class 4 40ft pole
Non-Outage | J.E.26.08.15820 | C001885389 | Neville Spencer | Clarendon | Completed | Load_258682 | May Pen - 110 | 2026-08-11 12:39 | 2026-08-11 12:40 | 2026-08-11 15:54 | 2026-08-11 15:56 | 2026-08-11 15:55 | 2026-08-11 17:15 | 2026-08-11 17:15 | 2026-08-11 17:15 |  |  | Fair | No | Open 25 kva xmfr at pole #0106068 cleared bamboo from secondary lines .Also remade burnt off phase drop lead used 2 clamps voltage reading 114 117 232 supply restored.
Outage | J.E.26.08.16017 | C001885396 | Wan Carlos Scarlett | Portmore | Completed | Load_412901 | Naggo Head - 510 | 2026-08-11 12:41 | 2026-08-11 12:42 | 2026-08-11 14:13 | 2026-08-11 14:14 | 2026-08-11 14:48 | 2026-08-11 15:45 | 2026-08-11 15:48 | 2026-08-11 15:48 |  |  | Fair | No | Refuse 40amp junction pole # 016275 clear bird from off primary line
Non-Outage | J.E.26.08.15983 | C001885399 | Orville Lee | St.Catherine | Completed | Load_247011 | Twickenham - 210 | 2026-08-11 12:44 | 2026-08-11 12:45 | 2026-08-12 10:53 | 2026-08-12 12:04 | 2026-08-12 12:29 | 2026-08-12 12:59 | 2026-08-12 13:00 | 2026-08-12 13:00 |  |  | Fair | No | Checks made and found pothead and secondary connections corroded Two pen union and one 1 bolt clamp115v
Non-Outage | J.E.26.08.16051 | C001885398 | Gregory Grossett |  | Completed |  |  | 2026-08-11 12:44 | 2026-08-11 15:09 | 2026-08-11 21:00 | 2026-08-11 21:01 | 2026-08-11 21:19 | 2026-08-11 21:21 | 2026-08-11 21:21 | 2026-08-11 21:21 |  |  | Fair | No | After calling customer she said she would rather a daylight visit because her premises already locked up.
Outage | J.E.26.08.16035 | C001885397 | Collin Robinson | Portland | Completed | Load_249141 | Port Antonio - 310 | 2026-08-11 12:44 | 2026-08-11 12:44 | 2026-08-11 13:30 | 2026-08-11 13:30 | 2026-08-11 14:17 | 2026-08-11 14:30 | 2026-08-11 14:30 | 2026-08-11 14:30 | BrokenWire |  | Fair | No | Change two corroded one bolt clamp at pole Voltage reading 118v 118v 236v
Outage | J.E.26.08.16063 | C001885413 | Royston Montague | St.Catherine | Completed | Load_261455 | Rhodens Pen - 410 | 2026-08-11 12:51 | 2026-08-11 14:03 | 2026-08-11 14:07 | 2026-08-11 14:07 | 2026-08-11 15:13 | 2026-08-11 15:14 | 2026-08-11 15:14 | 2026-08-11 15:14 |  |  | Fair | No | Not locating this premises, need proper directions and a valid phone number thanks.
Non-Outage | J.E.26.08.15751 | C001885445 | Horace Malcolm |  | Completed |  |  | 2026-08-11 13:12 | 2026-08-11 16:31 | 2026-08-11 18:41 | 2026-08-11 18:42 | 2026-08-11 19:20 | 2026-08-11 19:31 | 2026-08-11 19:31 | 2026-08-11 19:31 | BrokenWire |  | Fair | No | Cut down service wire not using that is blocking customer gateway
Non-Outage | J.E.26.07.03031 | C001885451 | Royston Montague | St.Catherine | Completed | Load_254033 | Rhodens Pen - 310 | 2026-08-11 13:18 | 2026-08-11 13:19 | 2026-08-11 14:03 | 2026-08-11 15:15 | 2026-08-11 15:37 | 2026-08-11 15:38 | 2026-08-11 15:38 | 2026-08-11 15:38 |  |  | Fair | No | Rami system in area. Please assign to the relevant team thanks.
Outage | J.E.26.08.16112 | C001885452 | Horace Malcolm | St.James | Completed | Load_293364 | Queens Drive - 310 | 2026-08-11 13:20 | 2026-08-11 15:03 | 2026-08-11 17:35 | 2026-08-11 17:36 | 2026-08-11 18:10 | 2026-08-11 18:41 | 2026-08-11 18:41 | 2026-08-11 18:41 | Fire |  | Fair | No | Check and found customer got disconnected for non payment
Non-Outage | J.E.26.08.15435 | C001885465 | Roemello Brown | Trelawny | Completed | Load_248970 | Martha Brae - 110 | 2026-08-11 13:30 | 2026-08-11 13:30 | 2026-08-12 08:40 | 2026-08-12 08:41 | 2026-08-12 08:52 | 2026-08-12 08:52 | 2026-08-12 09:35 | 2026-08-12 09:35 |  |  | Fair | No | Corrosion at the pole side and at the pothead have both clamps change Voltage found 108/117/225Voltage leave 117/116/234
Non-Outage | J.E.26.08.10088 | C001885479 | Fredrick Hamilton | KSAN | Completed | Load_253322 | Washington Blvd - 310 | 2026-08-11 13:32 | 2026-08-11 13:46 | 2026-08-11 14:15 | 2026-08-11 14:30 | 2026-08-11 14:31 | 2026-08-11 14:37 | 2026-08-11 14:37 | 2026-08-11 14:37 |  |  | Fair | No | Pole#083156Emergency Response required Rami customer Pothead ok
Outage | J.E.26.08.16164 | C001885490 | Moses Elliston | Portmore | Completed | Load_576152 | Naggo Head - 610 | 2026-08-11 13:41 | 2026-08-11 13:41 | 2026-08-11 16:11 | 2026-08-11 16:12 | 2026-08-11 16:11 | 2026-08-11 16:11 | 2026-08-11 16:14 | 2026-08-11 16:14 |  |  | Fair | No | Customer complaining of high consumption on pay as you go usage.
Outage | J.E.26.08.16151 | C001885503 | Edward Royal | KSAN | Completed | Load_244466 | Washington Blvd - 710 | 2026-08-11 13:48 | 2026-08-11 13:49 | 2026-08-11 14:24 | 2026-08-11 14:25 | 2026-08-11 14:31 | 2026-08-11 15:39 | 2026-08-11 15:59 | 2026-08-11 15:59 | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Spliced and reconnected secondary phase using 60ft 2 north conductor perform 4 single bolt clamp
Outage | J.E.26.08.16185 | C001885504 | Clyde Brown | Clarendon | Completed | Load_244410 | Parnassus - 310 | 2026-08-11 13:49 | 2026-08-11 13:50 | 2026-08-11 13:57 | 2026-08-11 13:58 | 2026-08-11 14:31 | 2026-08-11 14:32 | 2026-08-11 14:37 | 2026-08-11 14:37 | BrokenPole |  | Fair | No | TA-40c4 pole with transformer rotten with secondary back to back.broken pole not seen
Non-Outage | J.E.26.08.16183 | C001885514 | Donald Cunningham |  | Completed |  |  | 2026-08-11 13:51 | 2026-08-11 15:58 | 2026-08-11 16:15 | 2026-08-11 16:15 | 2026-08-11 17:28 | 2026-08-11 17:37 | 2026-08-11 17:39 | 2026-08-11 17:39 | BrokenWire |  | Fair | No | Broken stanchion repair not completed advised customer on same
Outage | J.E.26.08.15858 | C001885525 | Barrington Brown | St.James | Completed | Load_263053 | Bogue - 310 | 2026-08-11 14:02 | 2026-08-11 15:31 | 2026-08-11 18:48 | 2026-08-11 18:48 | 2026-08-11 19:32 | 2026-08-11 19:34 | 2026-08-11 19:34 | 2026-08-11 19:34 | BrokenWire |  | Fair | No | Please refer to field service department to have customer reconnected.
Outage | J.E.26.08.16105 | C001885526 | Dean- Smith | Hanover | Completed | Load_253533 | Orange Bay - 210 | 2026-08-11 14:03 | 2026-08-11 14:03 | 2026-08-11 15:25 | 2026-08-11 15:25 | 2026-08-11 15:25 | 2026-08-11 15:25 | 2026-08-11 15:25 | 2026-08-11 15:25 | BrokenWire |  | Rains | No | Unable to complete because of rain
Non-Outage | J.E.26.08.14065 | C001885569 | Fredrick Hamilton | KSAN | Completed | Load_266737 | Washington Blvd - 310 | 2026-08-11 14:31 | 2026-08-11 14:33 | 2026-08-11 14:38 | 2026-08-11 14:38 | 2026-08-11 14:43 | 2026-08-11 14:56 | 2026-08-11 14:56 | 2026-08-11 14:56 |  |  | Fair | No | 216v/107v/107v obtained Low voltage affecting multiple customers at location Emergency required Please check for corrosion at transformer
Outage | J.E.26.08.16328 | C001885589 | Clyde Brown | Clarendon | Completed | Load_239411 | Parnassus - 310 | 2026-08-11 14:42 | 2026-08-11 14:43 | 2026-08-11 15:14 | 2026-08-11 17:14 | 2026-08-11 17:14 | 2026-08-11 17:03 | 2026-08-11 17:17 | 2026-08-11 17:17 |  |  | Fair | No | Blown 2-40amps junction fuse at MacCorner caused by telephone line thrown on primary 3 phase line same removed and blown fuse replaced.
Outage | J.E.26.08.16344 | C001885609 | Christopher Edwards | KSAN | Completed | Load_264073 | Constant Spring - 210 | 2026-08-11 14:51 | 2026-08-12 07:44 | 2026-08-12 07:47 | 2026-08-12 08:08 | 2026-08-12 08:08 | 2026-08-12 08:15 | 2026-08-12 08:15 | 2026-08-12 08:15 |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Outage | J.E.26.08.16136 | C001885616 | Raymond Lewis | St.Ann | Completed | Load_241157 | Cardiff Hall - 310 | 2026-08-11 14:55 | 2026-08-11 15:15 | 2026-08-11 19:58 | 2026-08-11 19:58 | 2026-08-11 21:00 | 2026-08-11 21:01 | 2026-08-11 21:01 | 2026-08-11 21:01 |  |  | Fair | No | Phone number not working
Outage | J.E.26.08.16163 | C001885614 | Omar King | St.Ann | Completed | Load_250748 | Ocho Rios - 310 | 2026-08-11 14:55 | 2026-08-11 15:15 | 2026-08-11 16:38 | 2026-08-11 16:39 | 2026-08-11 17:20 | 2026-08-11 18:45 | 2026-08-11 18:45 | 2026-08-11 18:45 |  |  | Fair | No | Found customer service wire defective as been replaced customer is now with supply
Outage | J.E.26.08.16318 | C001885615 | Omar King | St.Ann | Completed | Load_240455 | Upper White River - 210 | 2026-08-11 14:55 | 2026-08-11 15:15 | 2026-08-11 15:38 | 2026-08-11 15:39 | 2026-08-11 16:36 | 2026-08-11 16:37 | 2026-08-11 16:38 | 2026-08-11 16:38 |  |  | Fair | No | Found customer three (3) wire meter defective please refer to field service
Non-Outage | J.E.26.08.16274 | C001885618 | Horace Malcolm |  | Completed |  |  | 2026-08-11 14:59 | 2026-08-11 15:03 | 2026-08-11 17:27 | 2026-08-11 17:27 | 2026-08-11 17:28 | 2026-08-11 17:29 | 2026-08-11 17:29 | 2026-08-11 17:29 | BrokenWire |  | Fair | No | Related to previous call job number 12685
Outage | J.E.26.08.16285 | C001885617 | Horace Malcolm | St.James | Completed | Load_292475 | Queens Drive - 310 | 2026-08-11 14:59 | 2026-08-11 15:03 | 2026-08-11 15:53 | 2026-08-11 15:54 | 2026-08-11 16:20 | 2026-08-11 17:25 | 2026-08-11 17:25 | 2026-08-11 17:25 |  |  | Fair | No | After all check on transformer suspect transformer defective one 10kva transformer with EG box on it box number EG02376 referred to field service or maintenance clinic is out of supply due to the defective transformer
Outage | J.E.26.08.16347 | C001885619 | Clyde Brown | Clarendon | Completed | Load_259178 | Parnassus - 310 | 2026-08-11 15:00 | 2026-08-11 15:01 | 2026-08-11 15:14 | 2026-08-11 15:14 | 2026-08-11 16:28 | 2026-08-11 17:03 | 2026-08-11 17:09 | 2026-08-11 17:09 |  |  | Fair | No | Found 2 -40amps junction fuse at Mac Corner and removed telephone wire off primary line,blown fuse replaced
Outage | J.E.26.08.15978 | C001885627 | Gregory Grossett | Portland | Completed | Load_242632 | Port Antonio - 410 | 2026-08-11 15:03 | 2026-08-11 15:09 | 2026-08-11 17:17 | 2026-08-11 17:17 | 2026-08-11 17:17 | 2026-08-11 17:18 | 2026-08-11 17:18 | 2026-08-11 17:18 |  |  | Fair | No | Customer breaker inside her house was turn off.
Outage | J.E.26.08.16074 | C001885628 | Gregory Grossett | Portland | Completed | Load_238403 | Port Antonio - 410 | 2026-08-11 15:03 | 2026-08-11 15:08 | 2026-08-11 21:21 | 2026-08-11 21:21 | 2026-08-11 21:21 | 2026-08-11 21:38 | 2026-08-11 21:39 | 2026-08-11 21:39 |  |  | Fair | No | Premises found ok voltage reading at meter socket 117/118/235 on both phase.
Outage | J.E.26.08.16319 | C001885626 | Gregory Grossett | Portland | Completed | Load_242632 | Port Antonio - 410 | 2026-08-11 15:03 | 2026-08-11 15:08 | 2026-08-11 16:10 | 2026-08-11 16:10 | 2026-08-11 16:58 | 2026-08-11 17:16 | 2026-08-11 17:17 | 2026-08-11 17:17 |  |  | Fair | No | Customer breaker inside her house was turn off.
Outage | J.E.26.08.16329 | C001885640 | Clyde Brown | Clarendon | Completed | Load_254336 | Parnassus - 310 | 2026-08-11 15:11 | 2026-08-11 15:14 | 2026-08-11 17:09 | 2026-08-11 17:10 | 2026-08-11 17:09 | 2026-08-11 17:03 | 2026-08-11 17:13 | 2026-08-11 17:13 |  |  | Fair | No | Blown 2-40 amps junction fuse at MacCorner caused by telephone line thrown on primary line same removed and blown fuse replaced.
Outage | J.E.26.08.15893 | C001885656 | Selvin White | St.Elizabeth | Completed | Load_267928 | Maggotty - 110 | 2026-08-11 15:16 | 2026-08-12 07:43 | 2026-08-12 12:41 | 2026-08-12 12:42 | 2026-08-12 13:43 | 2026-08-12 13:54 | 2026-08-12 13:54 | 2026-08-12 13:54 |  |  | Fair | No | Please refer to the field service department so the technician can visit the location as problem is hurricane related.
Outage | J.E.26.08.16286 | C001885654 | Richard Watson | St.Elizabeth | Completed | Load_292077 | Maggotty - 210 | 2026-08-11 15:16 | 2026-08-11 15:17 | 2026-08-11 17:11 | 2026-08-11 17:11 | 2026-08-11 17:35 | 2026-08-11 17:42 | 2026-08-11 17:47 | 2026-08-11 17:47 |  |  | Fair | No | Found okay, supply found at metering point, voltage found 105v, 105v, 210v.
Outage | J.E.26.08.16353 | C001885655 | Richard Watson | St.Elizabeth | Completed | Load_292549 | Maggotty - 210 | 2026-08-11 15:16 | 2026-08-11 15:17 | 2026-08-11 17:56 | 2026-08-11 17:56 | 2026-08-11 18:33 | 2026-08-11 19:00 | 2026-08-11 19:07 | 2026-08-11 19:07 |  |  | Fair | No | Check customer service wire coming out of Hexing box and found that no supply is coming from box, please refer to field service department for follow up check.
Outage | J.E.26.08.16363 | C001885653 | Richard Watson | St.Elizabeth | Completed | Load_248902 | Maggotty - 210 | 2026-08-11 15:16 | 2026-08-11 15:17 | 2026-08-11 15:57 | 2026-08-11 15:57 | 2026-08-11 16:24 | 2026-08-11 17:00 | 2026-08-11 17:05 | 2026-08-11 17:05 |  |  | Fair | No | Customer reconnected at secondary pole after carrying out inspection, voltage left inside meter socket 105v, 115v, 220v, customer connected closed to dead end, also numerous illegal connections are on circuit.
Non-Outage | J.E.26.02.36210 | C001885664 | Raheem Ricketts | Manchester | Completed | Load_292725 | Spur Tree - 210 | 2026-08-11 15:19 | 2026-08-11 15:20 | 2026-08-11 17:08 | 2026-08-11 17:39 | 2026-08-11 17:49 | 2026-08-11 17:51 | 2026-08-11 17:51 | 2026-08-11 17:51 |  |  | Fair | No | Unable to communicate with customer however check and found 25kva jumper clamp burn out isolate 25kva to remake joint
Non-Outage | J.E.26.04.11721 | C001885665 | Raheem Ricketts | Manchester | Completed | Load_239027 | Spur Tree - 210 | 2026-08-11 15:19 | 2026-08-11 15:20 | 2026-08-11 17:13 | 2026-08-11 17:13 | 2026-08-11 17:28 | 2026-08-11 17:29 | 2026-08-11 17:30 | 2026-08-11 17:30 |  |  | Fair | No | Check and found customer experiencing internal problem 110,110,220
Non-Outage | J.E.26.05.00294 | C001885663 | Raheem Ricketts | Manchester | Completed | Load_246385 | Spur Tree - 210 | 2026-08-11 15:19 | 2026-08-11 15:20 | 2026-08-11 17:06 | 2026-08-11 17:06 | 2026-08-11 17:06 | 2026-08-11 17:07 | 2026-08-11 17:07 | 2026-08-11 17:07 |  |  | Fair | No | Unable to communicate with customer cell phone out of service
Non-Outage | J.E.26.05.32089 | C001885662 | Raheem Ricketts | Manchester | Completed | Load_266073 | Spur Tree - 210 | 2026-08-11 15:19 | 2026-08-11 15:20 | 2026-08-11 17:01 | 2026-08-11 17:01 | 2026-08-11 17:01 | 2026-08-11 17:01 | 2026-08-11 17:01 | 2026-08-11 17:01 |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.07.02794 | C001885661 | Raheem Ricketts | Manchester | Completed | Load_265389 | Spur Tree - 210 | 2026-08-11 15:19 | 2026-08-11 15:20 | 2026-08-11 16:55 | 2026-08-11 16:56 | 2026-08-11 16:55 | 2026-08-11 16:57 | 2026-08-11 16:57 | 2026-08-11 16:57 |  |  | Fair | No | Unable to locate customer cell number went straight voicemail
Non-Outage | J.E.26.07.10377 | C001885659 | Raheem Ricketts | Manchester | Completed | Load_245516 | Spur Tree - 210 | 2026-08-11 15:19 | 2026-08-11 15:20 | 2026-08-11 16:53 | 2026-08-11 16:54 | 2026-08-11 16:53 | 2026-08-11 16:54 | 2026-08-11 16:54 | 2026-08-11 16:54 |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.07.24667 | C001885660 | Raheem Ricketts | Manchester | Completed | Load_265389 | Spur Tree - 210 | 2026-08-11 15:19 | 2026-08-11 15:20 | 2026-08-11 16:58 | 2026-08-11 16:58 | 2026-08-11 16:58 | 2026-08-11 16:59 | 2026-08-11 16:59 | 2026-08-11 16:59 |  |  | Fair | No | Customer says she didn’t make any report
Non-Outage | J.E.26.07.31481 | C001885657 | Raheem Ricketts | Manchester | Completed | Load_245516 | Spur Tree - 210 | 2026-08-11 15:19 | 2026-08-11 15:20 | 2026-08-11 15:32 | 2026-08-11 17:37 | 2026-08-11 17:36 | 2026-08-11 17:38 | 2026-08-11 17:38 | 2026-08-11 17:38 |  |  | Fair | No | Check and found okay problem has been solved
Non-Outage | J.E.26.07.34725 | C001885658 | Raheem Ricketts | Manchester | Completed | Load_257368 | Spur Tree - 210 | 2026-08-11 15:19 | 2026-08-11 15:20 | 2026-08-11 15:51 | 2026-08-11 15:52 | 2026-08-11 16:32 | 2026-08-11 16:52 | 2026-08-11 16:52 | 2026-08-11 16:52 |  |  | Fair | No | Check and found okay voltage left 110,110,220
Outage | J.E.26.08.15673 | C001885667 | Raheem Ricketts | Manchester | Completed | Load_237647 | Spur Tree - 210 | 2026-08-11 15:20 | 2026-08-11 15:21 | 2026-08-11 17:09 | 2026-08-11 17:10 | 2026-08-11 17:10 | 2026-08-11 17:10 | 2026-08-11 17:10 | 2026-08-11 17:10 | LeaningPole |  | Fair | No | Check and found okay
Outage | J.E.26.08.15834 | C001885666 | Raheem Ricketts | Manchester | Completed | Load_240847 | Spur Tree - 210 | 2026-08-11 15:20 | 2026-08-11 15:21 | 2026-08-11 17:52 | 2026-08-11 18:42 | 2026-08-11 18:42 | 2026-08-11 18:43 | 2026-08-11 18:43 | 2026-08-11 18:43 |  |  | Fair | No | Check and found okay
Outage | J.E.26.08.14044 | C001885676 | Kenroy Dale | Manchester | Completed | Load_263608 | Kendal - 210 | 2026-08-11 15:22 | 2026-08-11 15:23 | 2026-08-11 20:46 | 2026-08-11 20:47 | 2026-08-11 21:52 | 2026-08-11 22:21 | 2026-08-11 22:23 | 2026-08-11 22:23 |  |  | Fair | No | Customer meter missing, field service required
Outage | J.E.26.08.16077 | C001885677 | Hartley Chin | Clarendon | Completed | Load_348441 | May Pen - 110 | 2026-08-11 15:22 | 2026-08-11 15:23 | 2026-08-11 17:30 | 2026-08-11 17:31 | 2026-08-11 17:30 | 2026-08-11 17:32 | 2026-08-11 17:34 | 2026-08-11 17:34 |  |  | Fair | No | Wrong parish….St Catherine
Outage | J.E.26.08.15860 | C001885679 | Ryan Richards | Manchester | Completed | Load_257506 | Spur Tree - 310 | 2026-08-11 15:23 | 2026-08-11 15:25 | 2026-08-11 22:11 | 2026-08-11 22:11 | 2026-08-12 07:29 | 2026-08-12 07:29 | 2026-08-12 07:30 | 2026-08-12 07:30 |  |  | Fair | No | Premises found ok area has supply
Outage | J.E.26.08.16371 | C001885680 | Ryan Richards | Manchester | Completed | Load_259181 | Spur Tree - 310 | 2026-08-11 15:23 | 2026-08-11 15:25 | 2026-08-11 16:24 | 2026-08-11 16:24 | 2026-08-11 17:17 | 2026-08-11 17:53 | 2026-08-11 17:53 | 2026-08-11 17:53 |  |  | Fair | No | Burn off phase found at pole remade burn off phase used 1 one bolt clamps voltage 115 volts
Non-Outage | J.E.26.08.15913 | C001885692 | Edward Royal |  | Completed |  |  | 2026-08-11 15:29 | 2026-08-11 15:31 | 2026-08-11 17:07 | 2026-08-11 17:08 | 2026-08-11 17:14 | 2026-08-11 17:24 | 2026-08-11 17:25 | 2026-08-11 17:25 | BrokenWire |  | Fair | No | Premises found ok broken wire was already repaired 234 118 117 v
Outage | J.E.26.08.16144 | C001885690 | Fitzroy Turner | KSAS | Completed | Load_261669 | Hunts Bay - 310 | 2026-08-11 15:29 | 2026-08-11 15:47 | 2026-08-11 16:24 | 2026-08-11 16:25 | 2026-08-11 16:52 | 2026-08-11 18:16 | 2026-08-11 18:21 | 2026-08-11 18:21 |  |  | Fair | No | Found loads busters open LAB-6/7 at the top off orange st .have now clue how switch .switch needs to lock .please send email to text to have switches locks
Outage | J.E.26.08.16376 | C001885691 | Fitzroy Turner | KSAS | Completed | Load_242317 | Hunts Bay - 310 | 2026-08-11 15:29 | 2026-08-11 15:47 | 2026-08-11 19:48 | 2026-08-11 19:48 | 2026-08-11 22:34 | 2026-08-11 22:34 | 2026-08-11 22:35 | 2026-08-11 22:35 |  |  | Fair | No | Customer premises found with electricity supply after load busters closed
Outage | J.E.26.08.16380 | C001885693 | Fitzroy Turner | KSAS | Completed | Load_574891 | Hunts Bay - 310 | 2026-08-11 15:29 | 2026-08-11 15:47 | 2026-08-11 22:35 | 2026-08-11 22:36 | 2026-08-11 22:35 | 2026-08-11 22:36 | 2026-08-11 22:36 | 2026-08-11 22:36 |  |  | Fair | No | Customer premises found with electricity supply
Non-Outage | J.E.26.08.15675 | C001885694 | Edward Royal |  | Completed |  |  | 2026-08-11 15:30 | 2026-08-11 15:31 | 2026-08-11 16:59 | 2026-08-11 16:59 | 2026-08-11 16:59 | 2026-08-11 17:05 | 2026-08-11 17:05 | 2026-08-11 17:05 | BrokenWire |  | Fair | No | Premises found close unable to communicate with customer
Outage | J.E.26.08.15377 | C001885695 | Fitzroy Turner | KSAS | Completed | Load_254241 | Cane River - 310 | 2026-08-11 15:30 | 2026-08-11 15:47 | 2026-08-11 18:21 | 2026-08-11 18:21 | 2026-08-11 18:37 | 2026-08-11 18:39 | 2026-08-11 18:40 | 2026-08-11 18:40 |  |  | Fair | No | Found 50 kva transformer fuse blown no fault found replaced one 7amp fuse supply restored to the areas
Outage | J.E.26.08.14224 | C001885711 | Radcliffe Coleman | St.Catherine | Completed | Load_557189 | Tredegar - 410 | 2026-08-11 15:31 | 2026-08-11 15:34 | 2026-08-11 16:02 | 2026-08-11 16:03 | 2026-08-11 18:37 | 2026-08-11 18:40 | 2026-08-11 18:41 | 2026-08-11 18:41 | TreeContact |  | Fair | No | There is a tree at the location that needs to be cut, please refer to the maintenance department for there intervention.
Outage | J.E.26.08.16266 | C001885710 | Radcliffe Coleman | St.Catherine | Completed | Load_567663 | Tredegar - 310 | 2026-08-11 15:31 | 2026-08-11 15:34 | 2026-08-11 18:42 | 2026-08-11 18:42 | 2026-08-11 18:42 | 2026-08-11 18:48 | 2026-08-11 18:48 | 2026-08-11 18:48 | LeaningPole |  | Fair | No | There are a number of customer who’s service wire needs to be transferred to a new pole that was set. Please refer this situation to the field service department for their intervention.
Outage | J.E.26.08.16105 | C001885714 | Tajay Bernard | Hanover | Completed | Load_253533 | Orange Bay - 210 | 2026-08-11 15:32 | 2026-08-11 21:03 | 2026-08-11 21:29 | 2026-08-11 21:29 | 2026-08-11 21:29 | 2026-08-11 21:29 | 2026-08-11 21:30 | 2026-08-11 21:30 | BrokenWire |  | Fair | No | Customer stated that the issue has been resolved
Non-Outage | J.E.26.08.11328 | C001885715 | Evan Spaulding | St.Mary | Completed | Load_256175 | Highgate -110 | 2026-08-11 15:34 | 2026-08-11 16:38 | 2026-08-11 20:22 | 2026-08-11 20:23 | 2026-08-11 20:22 | 2026-08-11 21:47 | 2026-08-11 21:48 | 2026-08-11 21:48 |  |  | Fair | No | Retention secondary conductors using 1-2/0 preform,3-1 bolt clamps,voltage left 115v,115v,230v.
Non-Outage | J.E.26.08.13570 | C001885718 | Romaine Roberts | St.Mary | Completed | Load_238360 | Highgate - 210 | 2026-08-11 15:35 | 2026-08-11 16:37 | 2026-08-11 20:14 | 2026-08-11 20:15 | 2026-08-11 21:18 | 2026-08-11 21:31 | 2026-08-11 21:32 | 2026-08-11 21:32 |  |  | Fair | No | 3 wire service corrosion at pole and pothead clean and remake joints 6 clamps voltage 115-115-232
Non-Outage | J.E.26.08.13842 | C001885719 | Romaine Roberts | St.Mary | Completed | Load_238645 | Highgate - 210 | 2026-08-11 15:35 | 2026-08-11 16:37 | 2026-08-11 22:25 | 2026-08-11 22:25 | 2026-08-11 22:38 | 2026-08-11 22:57 | 2026-08-11 22:57 | 2026-08-11 22:57 | LowHangingWires |  | Fair | No | Tree fall on several service wire however all customer is still with supply a day time attention is needed to open 25 kva to clear tree off wire a power saw is needed
Non-Outage | J.E.26.08.14187 | C001885716 | Romaine Roberts | St.Mary | Completed | Load_265076 | Highgate - 210 | 2026-08-11 15:35 | 2026-08-11 16:37 | 2026-08-11 21:33 | 2026-08-11 21:34 | 2026-08-11 22:19 | 2026-08-11 22:21 | 2026-08-11 22:24 | 2026-08-11 22:24 |  |  | Fair | No | Customer meter was burnt and however meter has been change and customer is now restore and ok
Non-Outage | J.E.26.08.15440 | C001885730 | Evan Spaulding | St.Mary | Completed | Load_250014 | Annotto Bay - 310 | 2026-08-11 15:37 | 2026-08-11 16:38 | 2026-08-11 16:54 | 2026-08-11 16:55 | 2026-08-11 17:36 | 2026-08-11 18:47 | 2026-08-11 18:49 | 2026-08-11 18:49 |  |  | Fair | No | Retention one span secondary conductor,use 13ft 2/0 PVC copper,3-2/0 to 2/0 ampacts,voltage left 120v,120v,240v.
Non-Outage | J.E.26.08.15672 | C001885733 | Richman Whyte | Westmoreland | Completed | Load_268428 | Paradise - 310 | 2026-08-11 15:37 | 2026-08-11 15:38 | 2026-08-11 18:35 | 2026-08-11 18:35 | 2026-08-11 18:35 | 2026-08-11 18:35 | 2026-08-11 18:36 | 2026-08-11 18:36 |  |  | Fair | No | Clean corrosion on service wire at pothead use 3pg clamps voltage #113 113 #226
Outage | J.E.26.08.16257 | C001885732 | Richman Whyte | Westmoreland | Completed | Load_268226 | Paradise - 310 | 2026-08-11 15:37 | 2026-08-11 15:38 | 2026-08-11 20:20 | 2026-08-11 20:20 | 2026-08-11 20:20 | 2026-08-11 20:20 | 2026-08-11 20:20 | 2026-08-11 20:20 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Unable to locate or contact customer on the phone number given
Outage | J.E.26.08.16370 | C001885734 | Floyd Taylor | Trelawny | Completed | Load_242087 | Greenwood - 110 | 2026-08-11 15:37 | 2026-08-11 15:39 | 2026-08-11 19:32 | 2026-08-11 19:32 | 2026-08-11 20:41 | 2026-08-11 20:50 | 2026-08-11 20:51 | 2026-08-11 20:51 |  |  | Fair | No | Breaker of in meter room voltage readings left 118,119,236
Outage | J.E.26.08.16186 | C001885735 | Dwayne Samuels | Trelawny | Completed | Load_261243 | Greenwood - 110 | 2026-08-11 15:38 | 2026-08-12 07:36 | 2026-08-12 12:00 | 2026-08-12 12:09 | 2026-08-12 12:56 | 2026-08-12 12:59 | 2026-08-12 12:59 | 2026-08-12 12:59 |  |  | Fair | No | Customer has a internal issue and was advised to get a electrician to do some internal checks
Outage | J.E.26.08.16317 | C001885736 | Floyd Taylor | Trelawny | Completed | Load_254512 | Martha Brae - 110 | 2026-08-11 15:38 | 2026-08-11 15:39 | 2026-08-11 16:08 | 2026-08-11 16:09 | 2026-08-11 16:33 | 2026-08-11 17:27 | 2026-08-11 17:29 | 2026-08-11 17:29 | Fire |  | Fair | No | Clean and remake joint at pole using 2pg clamps, voltage reading left, 117,116,234
Non-Outage | J.E.26.06.38611 | C001885743 | Oshane Warren | Westmoreland | Completed | Load_237775 | Paradise - 210 | 2026-08-11 15:40 | 2026-08-11 15:42 | 2026-08-11 20:13 | 2026-08-11 20:13 | 2026-08-11 20:13 | 2026-08-11 20:14 | 2026-08-11 20:32 | 2026-08-11 20:32 |  |  | Fair | No | Unable to locate or contact customer need direction
Non-Outage | J.E.26.07.01067 | C001885744 | Oshane Warren | Westmoreland | Completed | Load_248205 | Paradise - 210 | 2026-08-11 15:40 | 2026-08-11 15:42 | 2026-08-11 18:42 | 2026-08-11 18:42 | 2026-08-11 19:55 | 2026-08-11 19:58 | 2026-08-11 20:00 | 2026-08-11 20:00 |  |  | Fair | No | Change defective clamps at pathead voltage 117 112 238
Outage | J.E.26.08.15753 | C001885742 | Swon Miller | Trelawny | Completed | Load_246089 | Greenwood - 110 | 2026-08-11 15:40 | 2026-08-11 15:41 | 2026-08-11 15:52 | 2026-08-11 15:53 | 2026-08-11 16:21 | 2026-08-11 16:34 | 2026-08-11 16:39 | 2026-08-11 16:39 |  |  | Fair | No
Non-Outage | J.E.26.05.13074 | C001885745 | Oshane Warren | Westmoreland | Completed | Load_249880 | Paradise - 210 | 2026-08-11 15:41 | 2026-08-11 15:42 | 2026-08-11 18:34 | 2026-08-11 18:35 | 2026-08-11 18:34 | 2026-08-11 18:41 | 2026-08-11 18:41 | 2026-08-11 18:41 |  |  | Fair | No | Customer promises is lock crow should visit in the morning
Non-Outage | J.E.26.06.38173 | C001885747 | Oshane Warren | Westmoreland | Completed | Load_260985 | Paradise - 110 | 2026-08-11 15:41 | 2026-08-11 15:42 | 2026-08-11 16:46 | 2026-08-11 16:47 | 2026-08-11 18:28 | 2026-08-11 18:29 | 2026-08-11 18:30 | 2026-08-11 18:30 |  |  | Fair | No | Check and found ok customer stated that she didn’t make any report
Non-Outage | J.E.26.08.15079 | C001885746 | Oshane Warren | Westmoreland | Completed | Load_245791 | Paradise - 110 | 2026-08-11 15:41 | 2026-08-11 15:42 | 2026-08-11 20:07 | 2026-08-11 20:08 | 2026-08-11 20:08 | 2026-08-11 20:08 | 2026-08-11 20:08 | 2026-08-11 20:08 |  |  | Fair | No | Check and found okay
Outage | J.E.26.08.16288 | C001885749 | Swon Miller | St.James | Completed | Load_237811 | Bogue - 610 | 2026-08-11 15:42 | 2026-08-11 15:59 | 2026-08-11 17:32 | 2026-08-11 17:32 | 2026-08-11 18:44 | 2026-08-19 07:05 | 2026-08-11 19:06 | 2026-08-11 19:06 |  |  | Fair | No | Check and found okay voltage found 113/112/226 voltage left 113/112/226
Outage | J.E.26.08.15869 | C001885753 | Swon Miller | St.James | Completed | Load_265669 | Bogue - 610 | 2026-08-11 15:43 | 2026-08-11 16:00 | 2026-08-11 20:43 | 2026-08-11 20:43 | 2026-08-11 21:24 | 2026-08-18 09:44 | 2026-08-11 21:32 | 2026-08-11 21:32 | LeaningPole |  | Fair | No | Check and found okay
Outage | J.E.26.08.16131 | C001885752 | Swon Miller | St.James | Completed | Load_264882 | Bogue - 610 | 2026-08-11 15:43 | 2026-08-11 15:59 | 2026-08-11 16:39 | 2026-08-11 16:40 | 2026-08-11 17:10 | 2026-08-11 05:23 | 2026-08-11 17:29 | 2026-08-11 17:29 |  |  | EarthMovement | No | Found 1,8 amp junction fuse causes by contamination replace 1, 8 amp junction fuse no pole number available voltage found 0.000 voltage left 115/114/230
Outage | J.E.26.08.15600 | C001885754 | Tajay Bernard | Hanover | Completed | Load_573350 | Orange Bay - 310 | 2026-08-11 15:44 | 2026-08-11 15:52 | 2026-08-11 19:37 | 2026-08-11 20:26 | 2026-08-11 20:52 | 2026-08-11 21:19 | 2026-08-11 21:27 | 2026-08-11 21:27 |  |  | Fair | No | Premises check and found okay voltage found 120/120/206
Outage | J.E.26.08.14233 | C001885758 | Swon Miller | St.James | Completed | Load_249383 | Bogue - 610 | 2026-08-11 15:47 | 2026-08-11 15:51 | 2026-08-11 19:44 | 2026-08-11 19:45 | 2026-08-11 20:20 | 2026-08-11 08:42 | 2026-08-11 20:42 | 2026-08-11 20:42 |  |  | Fair | No | Found customer without supply cause by hurricane M need 100ft #6 triplex to carry out repairs voltage found 0.000 voltage left 0.000
Non-Outage | J.E.26.08.15675 | C001885760 | Fitzroy Turner |  | Completed |  |  | 2026-08-11 15:48 | 2026-08-11 15:49 | 2026-08-11 18:41 | 2026-08-11 18:42 | 2026-08-11 19:06 | 2026-08-11 19:41 | 2026-08-11 19:42 | 2026-08-11 19:42 | BrokenWire |  | Fair | No | Found third party cables hanging low advise customer to call cable provided
Non-Outage | J.E.26.08.15713 | C001885759 | Fitzroy Turner |  | Completed |  |  | 2026-08-11 15:48 | 2026-08-11 15:49 | 2026-08-11 19:42 | 2026-08-11 19:43 | 2026-08-11 19:43 | 2026-08-11 19:44 | 2026-08-11 19:45 | 2026-08-11 19:45 |  |  | Fair | No | Found customer main breaker trip have customer breaker reset supply restored to customer
Outage | J.E.26.08.15813 | C001885761 | Richman Whyte | St.Elizabeth | Completed | Load_243757 | Maggotty - 110 | 2026-08-11 15:49 | 2026-08-11 15:50 | 2026-08-11 18:39 | 2026-08-11 18:40 | 2026-08-11 18:40 | 2026-08-11 18:40 | 2026-08-11 18:41 | 2026-08-11 18:41 |  |  | Fair | No | Customer stated that the premises is not ready for connection
Outage | J.E.26.08.16083 | C001885774 | Donald Cunningham | Portmore | Completed | Load_260602 | Naggo Head - 510 | 2026-08-11 15:59 | 2026-08-11 16:00 | 2026-08-11 19:08 | 2026-08-11 19:09 | 2026-08-11 21:36 | 2026-08-11 21:37 | 2026-08-11 21:39 | 2026-08-11 21:39 |  |  | Fair | No | Corroded phase and neural by transformer corrected using 6 clamps also bushing done in area also burnt secondary jumper corrected
Outage | J.E.26.08.15703 | C001885780 | Donald Cunningham | St.Catherine | Completed | Load_251980 | Twickenham - 210 | 2026-08-11 16:00 | 2026-08-11 16:01 | 2026-08-11 18:21 | 2026-08-11 18:21 | 2026-08-11 19:06 | 2026-08-11 19:07 | 2026-08-11 19:07 | 2026-08-11 19:07 |  |  | Fair | No | Supply restored
Outage | J.E.26.08.16142 | C001885776 | Nickolas Rodriques | Portmore | Completed | Load_255303 | Naggo Head - 610 | 2026-08-11 16:00 | 2026-08-12 07:21 | 2026-08-12 13:19 | 2026-08-12 13:31 | 2026-08-12 13:47 | 2026-08-12 14:16 | 2026-08-12 14:17 | 2026-08-12 14:17 |  |  | Fair | No | Found premises locked. Efforts to reach the customer on the contact number provided were unsuccessful.
Outage | J.E.26.08.16416 | C001885781 | Donald Cunningham | St.Catherine | Completed | Load_250245 | Twickenham - 210 | 2026-08-11 16:00 | 2026-08-11 16:01 | 2026-08-11 17:39 | 2026-08-11 17:40 | 2026-08-11 18:17 | 2026-08-11 18:18 | 2026-08-11 18:20 | 2026-08-11 18:20 |  |  | Fair | No | Premises closed
Outage | J.E.26.08.16447 | C001885790 | Shawn Medley | St.James | Completed | Load_268413 | Bogue - 310 | 2026-08-11 16:14 | 2026-08-12 08:20 | 2026-08-12 08:35 | 2026-08-12 08:40 | 2026-08-12 09:33 | 2026-08-12 09:34 | 2026-08-12 09:36 | 2026-08-12 09:36 |  |  | Fair | No | Customer not ready to accommodate Jps, I advise customer to get electrician to carryout relevant repairs, then make another report.
Outage | J.E.26.08.16440 | C001885792 | Horace Malcolm | St.James | Completed | Load_249698 | Queens Drive - 710 | 2026-08-11 16:15 | 2026-08-11 16:20 | 2026-08-11 21:29 | 2026-08-11 21:30 | 2026-08-11 21:47 | 2026-08-11 21:53 | 2026-08-11 21:53 | 2026-08-11 21:53 |  |  | Fair | No | Unable to locate customer or premises multiple calls to customer unavailable no directions given
Outage | J.E.26.08.16419 | C001885796 | Horace Malcolm | St.James | Completed | Load_293554 | Queens Drive - 310 | 2026-08-11 16:17 | 2026-08-11 16:20 | 2026-08-11 19:57 | 2026-08-11 19:57 | 2026-08-11 20:29 | 2026-08-11 20:30 | 2026-08-11 20:30 | 2026-08-11 20:30 |  |  | Fair | No | Customer got disconnected
Outage | J.E.26.08.16453 | C001885820 | Floyd Taylor | Trelawny | Completed | Load_1001528 | Duncans - 110 | 2026-08-11 16:40 | 2026-08-11 16:44 | 2026-08-11 17:36 | 2026-08-11 17:36 | 2026-08-11 17:59 | 2026-08-11 18:08 | 2026-08-11 18:08 | 2026-08-11 18:08 |  |  | Fair | No | No power coming from HEX06342 Hx27121770 Voltage reading, 0.35, 0.50, 000Refer to field service
Outage | J.E.26.08.16463 | C001885819 | Floyd Taylor | Trelawny | Completed | Load_249842 | Duncans - 210 | 2026-08-11 16:40 | 2026-08-11 16:44 | 2026-08-11 18:15 | 2026-08-11 18:16 | 2026-08-11 18:46 | 2026-08-11 19:29 | 2026-08-11 19:32 | 2026-08-11 19:32 |  |  | Fair | No | Clean and remake joint at pole using 2 clamp, voltage reading left, 118,119,238 and also tape up transformer drop lead
Non-Outage | J.E.26.08.16405 | C001885834 | Clyde Brown |  | Completed |  |  | 2026-08-11 16:50 | 2026-08-11 17:01 | 2026-08-11 17:09 | 2026-08-11 17:19 | 2026-08-11 19:12 | 2026-08-11 19:47 | 2026-08-11 20:16 | 2026-08-11 20:16 |  |  | Fair | No | Defective 3 wire servicespliced and retention with 8ft-#6 triplex service wire,voltage left 119/119 238v
Non-Outage | J.E.26.08.16501 | C001885841 | Neckell Ormsby |  | Completed |  |  | 2026-08-11 16:57 | 2026-08-12 07:17 | 2026-08-12 08:25 | 2026-08-12 08:25 | 2026-08-12 08:25 | 2026-08-12 08:26 | 2026-08-12 08:26 | 2026-08-12 08:26 |  |  | Fair | No | Found 1- junction fuse blown out of 3 patrol and found bird entangled on transformer, clear with switch stick and replace 1- 50amp no pole # seen
Outage | J.E.26.08.16506 | C001885842 | Neckell Ormsby | St.Mary | Completed | Load_251602 | Highgate - 210 | 2026-08-11 16:57 | 2026-08-12 07:08 | 2026-08-12 08:27 | 2026-08-12 08:27 | 2026-08-12 09:45 | 2026-08-12 10:04 | 2026-08-12 10:04 | 2026-08-12 10:04 |  |  | Fair | No | Splice and retention 2- pole span secondary neutral using approximately 40ft #2 AA, 3-one bolt clamps and reclose 25kva transformer pole 031055
Outage | J.E.26.08.16535 | C001885852 | Romaine Roberts | St.Mary | Completed | Load_239058 | Blackstonedge - 110 | 2026-08-11 17:12 | 2026-08-11 17:13 | 2026-08-11 17:24 | 2026-08-11 17:25 | 2026-08-11 20:03 | 2026-08-11 20:12 | 2026-08-11 20:12 | 2026-08-11 20:12 |  |  | Fair | No | Premises close customer leave premises said he never remembers to we where coming said to come in the morning
Outage | J.E.26.08.16554 | C001885857 | Neville Spencer | Clarendon | Completed | Load_245051 | Parnassus - 310 | 2026-08-11 17:35 | 2026-08-12 07:12 | 2026-08-12 09:26 | 2026-08-12 09:26 | 2026-08-12 09:30 | 2026-08-12 09:32 | 2026-08-12 09:32 | 2026-08-12 09:32 |  |  | Fair | No | Found ok call resolved yesterday.
Outage | J.E.26.08.16564 | C001885861 | Radcliffe Coleman | St.Catherine | Completed | Load_243687 | Twickenham - 310 | 2026-08-11 17:41 | 2026-08-11 17:44 | 2026-08-11 18:34 | 2026-08-11 18:49 | 2026-08-11 20:20 | 2026-08-11 21:05 | 2026-08-11 21:06 | 2026-08-11 21:06 | BrokenWire |  | Fair | No | Area found with one span of open secondary phase dislodge from pole. This was a result of a defective preform, repair were done with the aid of one 2/0 preform and three one bolt clamp. A 10kva transformer was open at pole 0105095 before repairs were done. Area left okay.
Outage | J.E.26.08.16418 | C001885863 | Richard Watson | St.Elizabeth | Completed | Load_269445 | Maggotty - 210 | 2026-08-11 17:57 | 2026-08-11 18:01 | 2026-08-11 19:21 | 2026-08-11 19:22 | 2026-08-11 20:42 | 2026-08-11 20:52 | 2026-08-11 20:54 | 2026-08-11 20:54 |  |  | Fair | No | Customer loadside was mistakenly connected to a meter that is currently disconnected for outstanding balance (meter#2970945), after truck accidentally tore down service wires, customer advised to get electrician to make correction.
Outage | J.E.26.08.16586 | C001885866 | Donald Cunningham | Portmore | Completed | Load_260602 | Naggo Head - 510 | 2026-08-11 18:00 | 2026-08-11 18:32 | 2026-08-11 22:01 | 2026-08-11 22:02 | 2026-08-11 22:29 | 2026-08-11 22:29 | 2026-08-11 22:30 | 2026-08-11 22:30 |  |  | Fair | No | Supply restored
Outage | J.E.26.08.16549 | C001885869 | Swon Miller | St.James | Completed | Load_240373 | Queens Drive - 710 | 2026-08-11 18:01 | 2026-08-12 07:44 | 2026-08-12 07:51 | 2026-08-12 08:48 | 2026-08-12 09:38 | 2026-08-12 09:57 | 2026-08-12 10:12 | 2026-08-12 10:12 |  |  | Fair | No | Found customer no supply due pothead clamps burnt voltage found 0.000 clean and remake joints use 2pg voltage left 117/116/234
Outage | J.E.26.08.16576 | C001885870 | Barrington Brown | St.James | Completed | Load_301723 | Bogue - 310 | 2026-08-11 18:01 | 2026-08-11 18:10 | 2026-08-11 22:03 | 2026-08-11 22:04 | 2026-08-11 22:56 | 2026-08-11 22:59 | 2026-08-11 22:59 | 2026-08-11 22:59 | BrokenWire |  | Fair | No | Bushing requires to reconnect customer and bucket truck needed due the pole being on a hill side and tree limbs needing to be cut
Outage | J.E.26.08.16581 | C001885868 | Swon Miller | St.James | Completed | Load_263560 | Bogue - 610 | 2026-08-11 18:01 | 2026-08-11 18:09 | 2026-08-11 19:07 | 2026-08-11 19:07 | 2026-08-11 19:28 | 2026-09-02 07:42 | 2026-08-11 19:44 | 2026-08-11 19:44 |  |  | Fair | No | Check and found okay voltage found 115/114/230 voltage left 115/114/230
Outage | J.E.26.08.16394 | C001885875 | Edward Royal | KSAN | Completed | Load_269185 | Washington Blvd - 710 | 2026-08-11 18:16 | 2026-08-11 18:17 | 2026-08-11 18:36 | 2026-08-11 18:37 | 2026-08-11 18:36 | 2026-08-11 18:37 | 2026-08-11 18:37 | 2026-08-11 18:37 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.16438 | C001885874 | Edward Royal | KSAS | Completed | Load_246560 | Greenwich - 310 | 2026-08-11 18:16 | 2026-08-11 18:17 | 2026-08-11 18:50 | 2026-08-11 18:50 | 2026-08-11 18:50 | 2026-08-11 20:40 | 2026-08-11 20:41 | 2026-08-11 20:41 |  |  | Fair | No | Primary jumper burnt off from dot reffered to main line crew
Outage | J.E.26.08.16550 | C001885873 | Edward Royal | KSAN | Completed | Load_267179 | Washington Blvd - 710 | 2026-08-11 18:16 | 2026-08-11 18:17 | 2026-08-11 20:43 | 2026-08-11 20:43 | 2026-08-11 20:43 | 2026-08-11 20:45 | 2026-08-11 20:45 | 2026-08-11 20:45 | LeaningPole |  | Fair | No | Class 6 30ft rotten pole on it open secondary 3rd party cable reffered to maintenance pole #059479
Outage | J.E.26.08.16589 | C001885872 | Edward Royal | KSAN | Completed | Load_267571 | Washington Blvd - 710 | 2026-08-11 18:16 | 2026-08-11 18:17 | 2026-08-11 20:41 | 2026-08-11 20:41 | 2026-08-11 20:41 | 2026-08-11 20:42 | 2026-08-11 20:42 | 2026-08-11 20:42 |  |  | Fair | No | When contacted customer said that power was restored
Non-Outage | J.E.26.08.12531 | C001885879 | Raheem Ricketts | Manchester | Completed | Load_252998 | Spur Tree - 210 | 2026-08-11 18:26 | 2026-08-11 18:28 | 2026-08-11 18:40 | 2026-08-11 18:41 | 2026-08-11 18:40 | 2026-08-11 18:42 | 2026-08-11 18:42 | 2026-08-11 18:42 |  |  | Fair | No | Customer cell number went straight voi After several calls
Non-Outage | J.E.26.07.22276 | C001885883 | Raheem Ricketts | St.Elizabeth | Completed | Load_237839 | Spur Tree - 210 | 2026-08-11 18:27 | 2026-08-11 18:28 | 2026-08-11 18:52 | 2026-08-11 18:57 | 2026-08-11 19:22 | 2026-08-11 21:55 | 2026-08-11 21:55 | 2026-08-11 21:55 |  |  | Fair | No | Reconnect 100ft of service wire using 6 clamps isolated 25kva to splice an retention secondary neutral
Non-Outage | J.E.26.08.11611 | C001885881 | Raheem Ricketts | St.Elizabeth | Completed | Load_256104 | Maggotty - 210 | 2026-08-11 18:27 | 2026-08-11 18:28 | 2026-08-11 18:48 | 2026-08-11 18:48 | 2026-08-11 18:52 | 2026-08-11 18:53 | 2026-08-11 18:53 | 2026-08-11 18:53 |  |  | Fair | No | Unable to locate customer cell phone is out of service
Non-Outage | J.E.26.08.12525 | C001885882 | Raheem Ricketts | Manchester | Completed | Load_252998 | Spur Tree - 210 | 2026-08-11 18:27 | 2026-08-11 18:28 | 2026-08-11 18:55 | 2026-08-11 18:55 | 2026-08-11 18:55 | 2026-08-11 18:55 | 2026-08-11 18:56 | 2026-08-11 18:56 |  |  | Fair | No
Outage | J.E.26.08.16632 | C001885887 | Richard Grant | St.Catherine | Completed | Load_239495 | Tredegar - 410 | 2026-08-11 18:39 | 2026-08-11 18:41 | 2026-08-11 18:53 | 2026-08-11 18:54 | 2026-08-11 20:22 | 2026-08-11 21:17 | 2026-08-11 21:17 | 2026-08-11 21:17 |  | Y | Fair | No | 50amps, 8k, 10k, 10k amps fuses all found blown at 3phase junction pole and for 3 separate 100kva transformers, respectively, caused by wisp growing onto one of the 100kva transformers switch droplead. Wisp removed, all 100kva transformers switch fuses replaced with 10d amps fuse, 50amps fuse replaced with same and supply restored. Kindly send email to A Murray to have line section bushed and de-wisp. Area left okay
Non-Outage | J.E.26.08.16631 | C001885888 | Clyde Brown |  | Completed |  |  | 2026-08-11 18:43 | 2026-08-11 18:45 | 2026-08-11 20:17 | 2026-08-11 20:17 | 2026-08-11 21:32 | 2026-08-10 22:08 | 2026-08-11 22:11 | 2026-08-11 22:11 |  |  | Fair | No | Found pump ok reading phase to neutral 244/248/241 and phase to phase 424/426/422
Outage | J.E.26.08.16653 | C001885889 | Neville Spencer | Clarendon | Completed | Load_241995 | Parnassus - 210 | 2026-08-11 18:45 | 2026-08-12 07:12 | 2026-08-12 09:33 | 2026-08-12 09:33 | 2026-08-12 11:29 | 2026-08-12 11:30 | 2026-08-12 11:33 | 2026-08-12 11:33 |  |  | Fair | No | Customer not located.
Outage | J.E.26.08.15986 | C001885893 | Omar King | St.Ann | Completed | Load_248125 | Ocho Rios - 310 | 2026-08-11 18:57 | 2026-08-11 18:57 | 2026-08-11 19:39 | 2026-08-11 19:39 | 2026-08-11 19:39 | 2026-08-11 21:33 | 2026-08-11 21:33 | 2026-08-11 21:33 |  |  | Fair | No | Customer found with internal issues I advise customer to use electrician to resolve issues
Outage | J.E.26.08.16671 | C001885900 | Hartley Chin | Clarendon | Completed | Load_264315 | May Pen - 110 | 2026-08-11 19:17 | 2026-08-11 19:18 | 2026-08-11 19:23 | 2026-08-11 19:29 | 2026-08-11 20:52 | 2026-08-11 21:00 | 2026-08-11 21:01 | 2026-08-11 21:01 |  |  | Fair | No | Customer has internal issue . Needs new meter socket.
Outage | J.E.26.08.16652 | C001885901 | Horace Malcolm | St.James | Completed | Load_1002304 | Queens Drive - 310 | 2026-08-11 19:18 | 2026-08-11 19:21 | 2026-08-11 20:32 | 2026-08-11 20:32 | 2026-08-11 21:27 | 2026-08-11 21:28 | 2026-08-11 21:28 | 2026-08-11 21:28 |  |  | Fair | No | Check and found customer got disconnected
Outage | J.E.26.08.16670 | C001885902 | Neville Spencer | Clarendon | Completed | Load_260333 | Parnassus - 310 | 2026-08-11 19:20 | 2026-08-12 07:12 | 2026-08-12 07:37 | 2026-08-12 07:38 | 2026-08-12 09:24 | 2026-08-12 09:25 | 2026-08-12 09:25 | 2026-08-12 09:25 |  |  | Fair | No | Unable to locate customer.
Non-Outage | J.E.26.08.16708 | C001885905 | Hartley Chin |  | Completed |  |  | 2026-08-11 19:33 | 2026-08-11 19:34 | 2026-08-11 21:01 | 2026-08-11 21:02 | 2026-08-11 21:01 | 2026-08-11 21:35 | 2026-08-11 21:36 | 2026-08-11 21:36 |  |  | Fair | No | Isolate 50 KVA transformer to remove banging wires the close transformer
Outage | J.E.26.08.16716 | C001885908 | Donald Cunningham | Portmore | Completed | Load_258762 | Naggo Head - 510 | 2026-08-11 19:39 | 2026-08-11 19:40 | 2026-08-11 21:39 | 2026-08-11 21:40 | 2026-08-11 21:57 | 2026-08-11 21:58 | 2026-08-11 22:00 | 2026-08-11 22:00 |  |  | Fair | No | Supply restored
Outage | J.E.26.08.16532 | C001885910 | Javid Vernon | Westmoreland | Completed | Load_253644 | Paradise - 310 | 2026-08-11 19:40 | 2026-08-12 07:46 | 2026-08-12 08:07 | 2026-08-12 08:08 | 2026-08-12 09:51 | 2026-08-12 10:16 | 2026-08-12 10:16 | 2026-08-12 10:16 |  |  | Fair | No | Customer got disconnected for none payment but was reconnect after paying bill voltage reading 110/111/221
Outage | J.E.26.08.16677 | C001885912 | Javid Vernon | Westmoreland | Completed | Load_248237 | Paradise - 310 | 2026-08-11 19:40 | 2026-08-12 07:48 | 2026-08-12 14:25 | 2026-08-12 14:26 | 2026-08-12 14:42 | 2026-08-12 14:52 | 2026-08-12 14:52 | 2026-08-12 14:52 |  |  | Fair | No | Area check and found okay unable to locate customer and premises phone calls to customer number went unanswered and no directions were given
Outage | J.E.26.08.16711 | C001885913 | Javid Vernon | Westmoreland | Completed | Load_253406 | Paradise - 310 | 2026-08-11 19:40 | 2026-08-12 07:47 | 2026-08-12 10:16 | 2026-08-12 10:17 | 2026-08-12 11:31 | 2026-08-12 11:45 | 2026-08-12 11:45 | 2026-08-12 11:45 |  |  | Fair | No | Customer got disconnected for none payment voltage left at premises 116/117/233
Non-Outage | J.E.26.08.14264 | C001885922 | Tajay Bernard |  | Completed |  |  | 2026-08-11 19:52 | 2026-08-11 20:08 | 2026-08-11 20:16 | 2026-08-11 20:17 | 2026-08-11 20:17 | 2026-08-11 20:25 | 2026-08-11 20:26 | 2026-08-11 20:26 |  |  | Fair | No | Customer stated that she’s without electricity for a 1 week now, and also stated that her neighbors are also experiencing the same issues in the hexing box.Refer to field service, the matter needs to be resolved urgently
Outage | J.E.26.08.16706 | C001885927 | Milton Charlton | KSAN | Completed | Load_261829 | Washington Blvd - 810 | 2026-08-11 19:59 | 2026-08-11 20:54 | 2026-08-11 22:07 | 2026-08-11 22:08 | 2026-08-11 22:57 | 2026-08-11 22:25 | 2026-08-11 23:01 | 2026-08-11 23:01 |  |  | Fair | No | Customer meter disconnected for debt.
Outage | J.E.26.08.16722 | C001885926 | Evan Spaulding | St.Mary | Completed | Load_266701 | Highgate - 210 | 2026-08-11 19:59 | 2026-08-11 20:06 | 2026-08-11 21:51 | 2026-08-11 21:51 | 2026-08-11 22:23 | 2026-08-11 23:01 | 2026-08-11 23:02 | 2026-08-11 23:02 |  |  | Fair | No | Remove creepers from Transformer pole and replace 1-8 amps junction fuse at pole number 0010745.
Non-Outage | J.E.26.08.16456 | C001885930 | Milton Charlton | KSAS | Completed | Load_245057 | Duhaney - 310 | 2026-08-11 20:00 | 2026-08-11 20:54 | 2026-08-11 21:07 | 2026-08-11 21:08 | 2026-08-11 22:02 | 2026-08-11 22:10 | 2026-08-11 22:06 | 2026-08-11 22:06 |  |  | Fair | No | Customer service wire #6 triplex readings at pothead 123-123-247 volts. Transformer on 40ft concrete pole. Need bucket truck to tap change transformer.
Non-Outage | J.E.26.08.16176 | C001885933 | Milton Charlton | KSAN | Completed | Load_265649 | Hope - 510 | 2026-08-11 20:01 | 2026-08-11 20:01 | 2026-08-11 20:35 | 2026-08-11 20:36 | 2026-08-11 21:02 | 2026-08-11 20:40 | 2026-08-11 21:06 | 2026-08-11 21:06 |  |  | Fair | No | Unable to locate customer by telephone. No one answering call on report.
Outage | J.E.26.08.16174 | C001885935 | Derrick Grubb | St.Thomas | Completed | Load_238108 | Lysson - 410 | 2026-08-11 20:08 | 2026-08-11 20:09 | 2026-08-11 20:18 | 2026-08-11 20:18 | 2026-08-11 21:08 | 2026-08-11 21:40 | 2026-08-11 21:40 | 2026-08-11 21:40 | Fire |  | Fair | No | Clear banging wires and refuse 15 amp junction at pole number 005030
Outage | J.E.26.08.15966 | C001885936 | Stephen Taylor | St.Thomas | Completed | Load_266044 | Good Year - 210 | 2026-08-11 20:09 | 2026-08-12 07:33 | 2026-08-12 08:35 | 2026-08-12 08:36 | 2026-08-12 11:09 | 2026-08-12 11:09 | 2026-08-12 11:12 | 2026-08-12 11:12 |  |  | Fair | No | Clean up single phase use 2 clamps customer is now okay reading 111,112,224
Outage | J.E.26.08.16279 | C001885938 | Derrick Grubb | St.Thomas | Completed | Load_238431 | Good Year - 110 | 2026-08-11 20:09 | 2026-08-11 20:09 | 2026-08-11 21:43 | 2026-08-11 22:38 | 2026-08-11 22:37 | 2026-08-11 22:46 | 2026-08-11 22:47 | 2026-08-11 22:47 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.16292 | C001885937 | Derrick Grubb | St.Thomas | Completed | Load_258429 | Lysson - 410 | 2026-08-11 20:09 | 2026-08-11 20:09 | 2026-08-11 21:42 | 2026-08-11 21:42 | 2026-08-11 21:42 | 2026-08-11 21:43 | 2026-08-11 21:43 | 2026-08-11 21:43 |  |  | Fair | No | Premises found ok, customer was contacted by phone
Outage | J.E.26.08.16305 | C001885939 | Derrick Grubb | St.Thomas | Completed | Load_242808 | Lysson - 410 | 2026-08-11 20:09 | 2026-08-11 20:09 | 2026-08-11 21:40 | 2026-08-11 21:41 | 2026-08-11 21:40 | 2026-08-11 21:41 | 2026-08-11 21:42 | 2026-08-11 21:42 |  |  | Fair | No | Premises found okay, customer was contacted by cellphone
Outage | J.E.26.08.16598 | C001885945 | Andre Williams | Trelawny | Completed | Load_257453 | Duncans - 210 | 2026-08-11 20:15 | 2026-08-12 15:18 | 2026-08-12 15:25 | 2026-08-12 15:31 | 2026-08-12 16:11 | 2026-08-12 16:21 | 2026-08-12 16:21 | 2026-08-12 16:21 |  |  | Fair | No | Retention low hanging neutral that was touching lower phase ,reset 50 kva trip type transformer area now with supply.
Outage | J.E.26.08.16577 | C001885946 | Andre Williams | Trelawny | Completed | Load_245994 | Duncans - 210 | 2026-08-11 20:16 | 2026-08-12 15:18 | 2026-08-12 15:24 | 2026-08-12 16:27 | 2026-08-12 17:01 | 2026-08-12 17:27 | 2026-08-12 17:26 | 2026-08-12 17:26 |  |  | Fair | No | Open 25 kva transformer remake burnt off transformer lead , retention low hanging top phase on open secondary that was touching neutral, area now with full supply.
Outage | J.E.26.08.16702 | C001885950 | Swon Miller | St.James | Completed | Load_256751 | Bogue - 610 | 2026-08-11 20:21 | 2026-08-11 20:24 | 2026-08-11 21:33 | 2026-08-11 21:34 | 2026-08-11 22:28 | 2026-08-11 23:15 | 2026-08-11 23:16 | 2026-08-11 23:16 |  |  | Fair | No | Found 10 kva transformer trip due to illegal connections remove illegal connections from secondary lines and reset 10 kva transformer
Outage | J.E.26.08.16761 | C001885952 | Horace Malcolm | St.James | Completed | Load_267656 | Queens Drive - 710 | 2026-08-11 20:21 | 2026-08-11 20:24 | 2026-08-11 21:53 | 2026-08-11 21:54 | 2026-08-11 22:18 | 2026-08-11 22:22 | 2026-08-11 22:22 | 2026-08-11 22:22 |  |  | Fair | No | Customer got disconnected for non payment
Outage | J.E.26.08.16733 | C001885953 | Ricky Hall | Portmore | Completed | Load_269534 | Naggo Head - 510 | 2026-08-11 20:23 | 2026-08-11 23:29 | 2026-08-12 00:55 | 2026-08-12 00:55 | 2026-08-12 01:10 | 2026-08-12 01:17 | 2026-08-12 01:17 | 2026-08-12 01:17 | Fire |  | Fair | No | No fire seen
Outage | J.E.26.08.16764 | C001885954 | Tajay Bernard | Hanover | Completed | Load_253839 | Orange Bay - 310 | 2026-08-11 20:24 | 2026-08-11 20:26 | 2026-08-11 21:13 | 2026-08-11 21:28 | 2026-08-11 21:28 | 2026-08-11 21:29 | 2026-08-11 21:29 | 2026-08-11 21:29 |  |  | Fair | No | Customer is reporting a defective street light
Outage | J.E.26.08.16816 | C001885969 | Raymond Lewis | St.Ann | Completed | Load_249157 | Ocho Rios - 410 | 2026-08-11 22:09 | 2026-08-12 07:52 | 2026-08-12 10:51 | 2026-08-12 10:52 | 2026-08-12 11:26 | 2026-08-12 11:27 | 2026-08-12 11:27 | 2026-08-12 11:27 |  |  | Fair | No | Premises disconnected
Outage | J.E.26.08.16634 | C001885971 | Christopher Edwards | KSAS | Completed | Load_241156 | Rockfort - 410 | 2026-08-11 22:14 | 2026-08-11 23:09 | 2026-08-12 00:43 | 2026-08-12 00:48 | 2026-08-12 01:06 | 2026-08-12 07:18 | 2026-08-12 07:18 | 2026-08-12 07:18 | Fire |  | Fair | No | Splice and retention broken open secondary wireUsing:40ft #2 AA conductor 2 #2 preform 4 one bolt clamps Refuse blown 25 kva transformer Using :(1) 3 ampsRefuse blown junction fuse Using (1) 15 amps
Outage | J.E.26.08.16637 | C001885972 | Rusean Allen | KSAS | Completed | Load_259025 | Rockfort - 410 | 2026-08-11 22:14 | 2026-08-12 07:41 | 2026-08-12 09:12 | 2026-08-12 09:12 | 2026-08-12 10:29 | 2026-08-12 10:46 | 2026-08-12 10:47 | 2026-08-12 10:47 |  |  | Fair | No | Customer phone went unanswered
Outage | J.E.26.08.16792 | C001885973 | Rusean Allen | KSAS | Completed | Load_267237 | Up Park Camp - 510 | 2026-08-11 22:14 | 2026-08-12 07:40 | 2026-08-12 10:53 | 2026-08-12 10:54 | 2026-08-12 11:14 | 2026-08-12 11:17 | 2026-08-12 11:18 | 2026-08-12 11:18 | BrokenWire |  | Fair | No | Broken secondary jumper found, wire was reconnected
Non-Outage | J.E.26.08.16848 | C001885977 | Shamour Haughton |  | Completed |  |  | 2026-08-11 22:41 | 2026-08-11 22:42 | 2026-08-12 00:59 | 2026-08-12 01:00 | 2026-08-12 01:00 | 2026-08-12 01:00 | 2026-08-12 01:02 | 2026-08-12 01:02 | BrokenPole |  | Fair | No | No broken pole seen, customer is saying that the area is dark and she needs back the street light
Outage | J.E.26.08.16758 | C001885980 | Christopher Edwards | KSAS | Completed | Load_261030 | Rockfort - 410 | 2026-08-11 23:08 | 2026-08-11 23:10 | 2026-08-12 00:47 | 2026-08-12 07:18 | 2026-08-12 07:18 | 2026-08-12 07:18 | 2026-08-12 07:18 | 2026-08-12 07:18 |  |  | Fair | No | Related to previous call that was resolved
Outage | J.E.26.08.16787 | C001885982 | Ricky Hall | Portmore | Completed | Load_253066 | Naggo Head - 610 | 2026-08-11 23:11 | 2026-08-11 23:26 | 2026-08-11 23:47 | 2026-08-11 23:53 | 2026-08-12 00:44 | 2026-08-12 00:54 | 2026-08-12 00:55 | 2026-08-12 00:55 |  |  | Fair | No | Area found with supply
Outage | J.E.26.08.16880 | C001885989 | Raymond Lewis | St.Ann | Completed | Load_266261 | Ocho Rios - 410 | 2026-08-12 00:35 | 2026-08-12 07:52 | 2026-08-12 09:15 | 2026-08-12 09:16 | 2026-08-12 09:59 | 2026-08-12 22:07 | 2026-08-12 10:07 | 2026-08-12 10:07 |  |  | Fair | No | Refuse and close 25kva x former pole number 622461
Non-Outage | J.E.26.08.16522 | C001885992 | Shamour Haughton | St.James | Completed | Load_239431 | Bogue - 610 | 2026-08-12 01:09 | 2026-08-12 01:55 | 2026-08-12 02:14 | 2026-08-12 02:15 | 2026-08-12 02:14 | 2026-08-12 02:14 | 2026-08-12 02:15 | 2026-08-12 02:15 | BrokenWire |  | Fair | No | Westmoreland call
Non-Outage | J.E.26.08.15599 | C001885993 | Shamour Haughton | St.James | Completed | Load_239765 | Bogue - 310 | 2026-08-12 01:14 | 2026-08-12 01:55 | 2026-08-12 02:15 | 2026-08-12 02:15 | 2026-08-12 02:15 | 2026-08-12 02:15 | 2026-08-12 02:16 | 2026-08-12 02:16 | BrokenWire |  | Fair | No | Unable to locate customer , needs better directions, customer number keeps going voicemail
Outage | J.E.26.08.16917 | C001885994 | Ricky Hall | Portmore | Completed | Load_253066 | Naggo Head - 610 | 2026-08-12 01:54 | 2026-08-12 01:55 | 2026-08-12 02:00 | 2026-08-12 02:00 | 2026-08-12 02:00 | 2026-08-12 03:09 | 2026-08-12 03:10 | 2026-08-12 03:10 |  |  | Fair | No | Isolate 50 kva xfmr to change defective secondary drop lead use 5’#2/0 pvc copper 2 clamps
Non-Outage | J.E.26.08.16949 | C001886004 | Tyrese Williams |  | Completed |  |  | 2026-08-12 06:12 | 2026-08-12 07:22 | 2026-08-12 07:45 | 2026-08-12 13:37 | 2026-08-12 13:36 | 2026-08-12 13:53 | 2026-08-12 14:10 | 2026-08-12 14:10 | Fire |  | Fair | No | Premises found ok call related to 25kva
Non-Outage | J.E.26.08.16051 | C001886041 | Denton Williams |  | Completed |  |  | 2026-08-12 07:06 | 2026-08-12 07:07 | 2026-08-12 07:19 | 2026-08-12 07:20 | 2026-08-12 09:36 | 2026-08-12 09:37 | 2026-08-12 09:40 | 2026-08-12 09:40 |  |  | Fair | No | Customer supply found okay. Voltage readings found 114v, 115v & 230v, same readings leave. However, the glass covering on the meter is falling off. A meter change is required. Please refer to Carl Grant field service.
Outage | J.E.26.08.16969 | C001886042 | Neckell Ormsby | St.Mary | Completed | Load_260682 | Highgate - 210 | 2026-08-12 07:07 | 2026-08-12 07:08 | 2026-08-12 07:16 | 2026-08-12 07:17 | 2026-08-12 07:36 | 2026-08-12 08:24 | 2026-08-12 08:24 | 2026-08-12 08:24 |  |  | Rains | No | Found 1- junction fuse blown out of 3 patrol and found bird entangled on transformer, clear with switch stick and replace 1- 50amp no pole # seen
Non-Outage | J.E.26.08.16560 | C001886044 | Ryan Richards |  | Completed |  |  | 2026-08-12 07:08 | 2026-08-12 07:10 | 2026-08-12 10:34 | 2026-08-12 10:34 | 2026-08-12 11:03 | 2026-08-12 11:48 | 2026-08-12 11:48 | 2026-08-12 11:48 |  |  | Fair | No | Blown 3 amp fuse found for 25 kva transformer line patrol nothing found blown fuse was replaced all customers are now with supply
Outage | J.E.26.08.16962 | C001886043 | Stephen Taylor | St.Thomas | Completed | Load_249841 | Good Year - 210 | 2026-08-12 07:08 | 2026-08-12 07:34 | 2026-08-12 11:12 | 2026-08-12 11:12 | 2026-08-12 13:40 | 2026-08-12 13:41 | 2026-08-12 13:51 | 2026-08-12 13:51 |  |  | Fair | No | Clean up single phase use 1 clamp reading 111,112,224 customer is now okay
Outage | J.E.26.08.16439 | C001886045 | Richard Samuda | Manchester | Completed | Load_263292 | Kendal - 210 | 2026-08-12 07:09 | 2026-08-12 18:00 | 2026-08-12 18:06 | 2026-08-12 18:08 | 2026-08-12 18:22 | 2026-08-12 18:23 | 2026-08-12 18:23 | 2026-08-12 18:23 |  |  | Fair | No | Customer said she is back to normal from yesterday
Non-Outage | J.E.26.08.15633 | C001886050 | Ryan Richards |  | Completed |  |  | 2026-08-12 07:13 | 2026-08-12 07:14 | 2026-08-12 08:03 | 2026-08-12 08:04 | 2026-08-12 10:06 | 2026-08-12 10:32 | 2026-08-12 10:33 | 2026-08-12 10:33 | BrokenWire |  | Fair | Yes | 2 broken service wire found replace 60ft#6 triplex. 6 penunion 5 one bolt clamps voltage 113/115/229 volts
Non-Outage | J.E.26.08.16946 | C001886054 | Tyrese Williams | St.Ann | Completed | Load_238008 | Cardiff Hall - 310 | 2026-08-12 07:20 | 2026-08-12 07:22 | 2026-08-12 07:45 | 2026-08-12 10:10 | 2026-08-12 12:44 | 2026-08-12 13:19 | 2026-08-12 13:36 | 2026-08-12 13:36 | Fire |  | Fair | No | Open a 25kva transformer and splice and retention 2 span of secondary #6 service wire twisted use 80 ft off #6 service wire and 3 pg clamp
Outage | J.E.26.08.16760 | C001886052 | Nickolas Rodriques | Portmore | Completed | Load_576246 | Naggo Head - 510 | 2026-08-12 07:20 | 2026-08-12 07:21 | 2026-08-12 09:17 | 2026-08-12 09:33 | 2026-08-12 09:55 | 2026-08-12 10:34 | 2026-08-12 10:40 | 2026-08-12 10:40 |  |  | Fair | No | Checked and found customer without electricity caused by broken connector wire from switch to transformer. Isolate 100 KVA transformer for safety to repair. Repaired by connecting lead and replaced the fuse after completing patrol.
Outage | J.E.26.08.16766 | C001886053 | Nickolas Rodriques | Portmore | Completed | Load_244609 | Naggo Head - 510 | 2026-08-12 07:20 | 2026-08-12 07:32 | 2026-08-12 07:53 | 2026-08-12 08:32 | 2026-08-12 09:00 | 2026-08-12 09:06 | 2026-08-12 09:13 | 2026-08-12 09:13 |  |  | Fair | No | Checked and found hotline clamp burnt off that supplies a 50 amp trip saver at three phase line.
Outage | J.E.26.08.16770 | C001886055 | Nickolas Rodriques | Portmore | Completed | Load_257809 | Naggo Head - 610 | 2026-08-12 07:20 | 2026-08-12 07:21 | 2026-08-12 10:47 | 2026-08-12 10:53 | 2026-08-12 11:02 | 2026-08-12 11:22 | 2026-08-12 11:25 | 2026-08-12 11:25 |  |  | Fair | No | Unable to locate or communicate with the customer after several attempts.
Outage | J.E.26.08.16922 | C001886057 | Nickolas Rodriques |  | Completed | Load_269422 | Naggo Head - 510 | 2026-08-12 07:20 | 2026-08-12 07:21 | 2026-08-12 14:18 | 2026-08-12 14:18 | 2026-08-12 14:39 | 2026-08-12 14:53 | 2026-08-12 15:00 | 2026-08-12 15:00 |  |  | Rains | No | Found premises with electricity. Call relates to the hotline clamp which supplies the 50 amp trip-saver that was repaired earlier.
Outage | J.E.26.08.16791 | C001886062 | Marlon Authors | Manchester | Completed | Load_257705 | Spur Tree - 210 | 2026-08-12 07:23 | 2026-08-12 07:25 | 2026-08-12 11:03 | 2026-08-12 11:04 | 2026-08-12 11:03 | 2026-08-12 11:04 | 2026-08-12 11:04 | 2026-08-12 11:04 |  |  | Fair | No | Customer said supply was restored
Outage | J.E.26.08.16811 | C001886059 | Raheem Ricketts | St.Elizabeth | Completed | Load_257801 | Maggotty - 210 | 2026-08-12 07:23 | 2026-08-12 15:58 | 2026-08-12 16:02 | 2026-08-12 16:20 | 2026-08-12 16:20 | 2026-08-12 16:21 | 2026-08-12 16:21 | 2026-08-12 16:21 | BrokenWire |  | Fair | No | Unable to locate customer cell number went straight voicemail after several calls
Outage | J.E.26.08.16840 | C001886061 | Marlon Authors | Manchester | Completed | Load_261757 | Spur Tree - 210 | 2026-08-12 07:23 | 2026-08-12 07:25 | 2026-08-12 10:12 | 2026-08-12 10:12 | 2026-08-12 10:58 | 2026-08-12 11:00 | 2026-08-12 11:01 | 2026-08-12 11:01 |  |  | Fair | No | Customer said supply was disconnected for none payment
Outage | J.E.26.08.16868 | C001886060 | Marlon Authors | Manchester | Completed | Load_249870 | Spur Tree - 210 | 2026-08-12 07:23 | 2026-08-12 07:25 | 2026-08-12 11:04 | 2026-08-12 11:05 | 2026-08-12 11:32 | 2026-08-12 11:43 | 2026-08-12 11:43 | 2026-08-12 11:43 |  |  | Fair | No | Supply checked and found defective meter,rdg 119 volts. Please refer same to the field services department for replacement
Outage | J.E.26.08.16641 | C001886063 | Marlon Authors | Manchester | Completed | Load_243742 | Spur Tree - 210 | 2026-08-12 07:24 | 2026-08-12 07:25 | 2026-08-12 08:47 | 2026-08-12 08:48 | 2026-08-12 09:03 | 2026-08-12 09:36 | 2026-08-12 09:36 | 2026-08-12 09:36 |  |  | Fair | No | Supply checked and found single phasing caused by corrosion at pole. Repair same using two clamps, supply leave working okay rdg 109v,110v and cross phased 219 volts
Non-Outage | J.E.26.08.15880 | C001886066 | Kenroy Dale |  | Completed |  |  | 2026-08-12 07:26 | 2026-08-12 07:38 | 2026-08-12 10:37 | 2026-08-12 11:14 | 2026-08-12 12:06 | 2026-08-12 12:32 | 2026-08-12 12:35 | 2026-08-12 12:35 | BrokenPole |  | Fair | No | Customer requesting abandoned pole to be removed from premises
Outage | J.E.26.08.15998 | C001886070 | Michael Paterson | Westmoreland | Completed | Load_246442 | Paradise - 110 | 2026-08-12 07:28 | 2026-08-12 07:45 | 2026-08-12 11:04 | 2026-08-12 11:04 | 2026-08-12 11:04 | 2026-08-12 11:05 | 2026-08-12 11:05 | 2026-08-12 11:05 |  |  | Fair | No | Customer confirm ok via phone call
Outage | J.E.26.08.16894 | C001886068 | Michael Paterson | Westmoreland | Completed | Load_250896 | Paradise - 210 | 2026-08-12 07:28 | 2026-08-12 07:45 | 2026-08-12 07:57 | 2026-08-12 07:58 | 2026-08-12 09:13 | 2026-08-12 10:13 | 2026-08-12 10:18 | 2026-08-12 10:18 |  |  | Fair | No | Assessment done in area, found two junction fuse blown, no pole #, also found 25kva xfmr fuse blown, no fault found on line section, replaced 15amp fuse at main junction, 8amps fuse at second junction, 2amps fuse at xfmr,supply restored, voltage readings at xfmr 119v, 119v, 238v, current reading, 165amps, 110amps and 60amps in neutral, several illegal connections in area, team suggesting remove open secondary and replace with 2/0 triplex, customer count 20. Please refer to Mr, Eglan Richard’s.
Outage | J.E.26.08.16907 | C001886069 | Michael Paterson | Westmoreland | Completed | Load_269379 | Paradise - 210 | 2026-08-12 07:28 | 2026-08-12 07:45 | 2026-08-12 11:09 | 2026-08-12 11:10 | 2026-08-12 11:10 | 2026-08-12 11:10 | 2026-08-12 11:10 | 2026-08-12 11:10 |  |  | Fair | Yes | Customer confirm ok via phone call.
Outage | J.E.26.08.16077 | C001886077 | Donald Cunningham | Clarendon | Completed | Load_348441 | May Pen - 110 | 2026-08-12 07:32 | 2026-08-12 07:33 | 2026-08-12 08:11 | 2026-08-12 08:12 | 2026-08-12 11:14 | 2026-08-12 11:14 | 2026-08-12 11:15 | 2026-08-12 11:15 |  |  | Fair | No | Need more directions customer not reachable
Outage | J.E.26.08.16817 | C001886076 | Hartley Chin | Clarendon | Completed | Load_263360 | May Pen - 110 | 2026-08-12 07:32 | 2026-08-12 07:33 | 2026-08-12 07:45 | 2026-08-12 08:13 | 2026-08-12 10:05 | 2026-08-12 10:36 | 2026-08-12 10:37 | 2026-08-12 10:37 | BrokenWire |  | Fair | No | Approximately 90ft service wire required job in complete
Outage | J.E.26.08.16633 | C001886078 | Michael Paterson | Westmoreland | Completed | Load_570273 | Paradise - 110 | 2026-08-12 07:34 | 2026-08-12 07:45 | 2026-08-12 11:11 | 2026-08-12 11:12 | 2026-08-12 14:10 | 2026-08-12 14:10 | 2026-08-12 14:10 | 2026-08-12 14:10 |  |  | Fair | No | Check and found ok, supply in area supply at premises.
Outage | J.E.26.08.16963 | C001886080 | Dwayne Samuels | Trelawny | Completed | Load_1001528 | Duncans - 110 | 2026-08-12 07:35 | 2026-08-12 08:38 | 2026-08-12 12:00 | 2026-08-12 13:00 | 2026-08-12 13:53 | 2026-08-12 13:55 | 2026-08-12 13:55 | 2026-08-12 13:55 |  |  | Fair | No | Customer meter is in locking band refer to field service to have further checked completed urgently.
Outage | J.E.26.08.16996 | C001886079 | Neckell Ormsby | St.Mary | Completed | Load_329776 | Highgate - 210 | 2026-08-12 07:35 | 2026-08-12 07:36 | 2026-08-12 08:24 | 2026-08-12 08:24 | 2026-08-12 08:24 | 2026-08-12 08:25 | 2026-08-12 08:25 | 2026-08-12 08:25 |  |  | Fair | No | Found 1- junction fuse blown out of 3 patrol and found bird entangled on transformer, clear with switch stick and replace 1- 50amp no pole # seen
Non-Outage | J.E.26.08.15620 | C001886081 | Rusean Allen |  | Completed |  |  | 2026-08-12 07:36 | 2026-08-12 07:40 | 2026-08-12 12:44 | 2026-08-12 12:44 | 2026-08-12 13:41 | 2026-08-12 13:43 | 2026-08-12 13:43 | 2026-08-12 13:43 |  |  | Fair | No | More information needed
Outage | J.E.26.08.16729 | C001886082 | Rusean Allen | KSAS | Completed | Load_241866 | Cane River - 310 | 2026-08-12 07:37 | 2026-08-12 07:41 | 2026-08-12 11:35 | 2026-08-12 11:36 | 2026-08-12 11:48 | 2026-08-12 11:49 | 2026-08-12 11:49 | 2026-08-12 11:49 |  |  | Fair | No | Power was was restored
Outage | J.E.26.08.16090 | C001886084 | Edward Royal | KSAS | Completed | Load_267606 | Duhaney - 410 | 2026-08-12 07:38 | 2026-08-12 07:42 | 2026-08-12 09:18 | 2026-08-12 13:18 | 2026-08-12 14:01 | 2026-08-12 14:31 | 2026-08-12 14:33 | 2026-08-12 14:33 | LowHangingWires |  | Fair | No | Customer have internal problems customer have defective wire holder advise customer to get electrician to fix the problem customer was disconnected
Outage | J.E.26.08.16762 | C001886083 | Rusean Allen | KSAS | Completed | Load_265849 | Rockfort - 210 | 2026-08-12 07:38 | 2026-08-12 07:41 | 2026-08-12 11:18 | 2026-08-12 11:19 | 2026-08-12 11:32 | 2026-08-12 11:33 | 2026-08-12 11:33 | 2026-08-12 11:33 |  |  | Fair | No | Found okay
Non-Outage | J.E.26.08.06824 | C001886088 | Ryan Richards | Manchester | Completed | Load_302217 | Spur Tree - 310 | 2026-08-12 07:39 | 2026-08-12 07:41 | 2026-08-12 12:03 | 2026-08-12 12:03 | 2026-08-12 13:24 | 2026-08-12 14:15 | 2026-08-12 14:16 | 2026-08-12 14:16 | LeaningPole |  | Fair | No | Corroded neutral jumper found almost at the end of the line causing customer to experience low voltage remade corroded neutral jumper using 1 one bolt clamps voltage 114/110/215 volts
Non-Outage | J.E.26.08.13348 | C001886085 | Kenroy Dale | Manchester | Completed | Load_249834 | Kendal - 210 | 2026-08-12 07:39 | 2026-08-12 07:41 | 2026-08-12 10:07 | 2026-08-12 10:08 | 2026-08-12 10:19 | 2026-08-12 10:19 | 2026-08-12 10:35 | 2026-08-12 10:35 | LeaningPole |  | Fair | No | 35 class 4 concrete T pole found badly leaning and causing strange on customer service wire
Outage | J.E.26.08.16487 | C001886090 | Elvis Trowers | KSAS | Completed | Load_266530 | Hunts Bay - 310 | 2026-08-12 07:41 | 2026-08-12 08:09 | 2026-08-12 08:32 | 2026-08-12 08:41 | 2026-08-12 09:09 | 2026-08-12 08:50 | 2026-08-12 09:13 | 2026-08-12 09:13 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.16545 | C001886089 | Edward Royal | KSAN | Completed | Load_264813 | Washington Blvd - 710 | 2026-08-12 07:41 | 2026-08-12 07:46 | 2026-08-12 09:18 | 2026-08-12 13:11 | 2026-08-12 13:17 | 2026-08-12 13:17 | 2026-08-12 13:18 | 2026-08-12 13:18 |  |  | Fair | No | Premises found close unable to communicate with customer
Outage | J.E.26.08.16654 | C001886091 | Selvin White | St.Elizabeth | Completed | Load_253149 | Maggotty - 110 | 2026-08-12 07:41 | 2026-08-12 07:44 | 2026-08-12 10:39 | 2026-08-12 10:40 | 2026-08-12 11:25 | 2026-08-12 12:30 | 2026-08-12 12:38 | 2026-08-12 12:38 |  |  | Fair | No | Reset a trip 10 KVA circuit after troubleshooting and removing a 120 volts, 2 wire meter due to defect inside customer’s premises . No one seen at the time of visit however message was left to advise the customer to get an electrician to correct the defect before supply can be restored. Meter number is 3005666. Supply was restored to all other customers.
Outage | J.E.26.08.16763 | C001886092 | Selvin White | St.Elizabeth | Completed | Load_238875 | Maggotty - 110 | 2026-08-12 07:42 | 2026-08-12 07:44 | 2026-08-12 09:04 | 2026-08-12 09:04 | 2026-08-12 10:13 | 2026-08-12 10:36 | 2026-08-12 10:36 | 2026-08-12 10:36 |  |  | Fair | No | Isolate a 25 KVA transformer circuit at pole number 0211580 in order to clear entangled secondary phase and neutral conductors caused by cable company that was carrying out work in the area at the time of the outage. Supply restored to the affected customers.
Outage | J.E.26.08.16951 | C001886094 | Eric Williams | KSAS | Completed | Load_267829 | Duhaney - 310 | 2026-08-12 07:44 | 2026-08-12 07:46 | 2026-08-12 08:50 | 2026-08-12 08:50 | 2026-08-12 09:46 | 2026-08-12 09:54 | 2026-08-12 09:54 | 2026-08-12 09:54 |  |  | Fair | No | Premises close, calls to customer went unanswered, power in the area
Outage | J.E.26.08.16812 | C001886095 | Javid Vernon | Westmoreland | Completed | Load_248686 | Paradise - 310 | 2026-08-12 07:45 | 2026-08-12 07:46 | 2026-08-12 11:45 | 2026-08-12 11:46 | 2026-08-12 11:46 | 2026-08-12 11:48 | 2026-08-12 11:48 | 2026-08-12 11:48 |  |  | Fair | No | Related to previous call job #16711
Non-Outage | J.E.26.08.16298 | C001886096 | Swon Miller | St.James | Completed | Load_251501 | Queens Drive - 710 | 2026-08-12 07:46 | 2026-08-12 07:46 | 2026-08-12 07:51 | 2026-08-12 13:57 | 2026-08-12 14:33 | 2026-08-12 14:52 | 2026-08-12 14:57 | 2026-08-12 14:57 |  |  | Fair | No | Unable to locate customer phone calls to customer number went unanswered
Non-Outage | J.E.26.08.16960 | C001886097 | Javid Vernon |  | Completed |  |  | 2026-08-12 07:47 | 2026-08-12 07:48 | 2026-08-12 19:32 | 2026-08-12 19:33 | 2026-08-12 20:12 | 2026-08-12 20:38 | 2026-08-12 20:42 | 2026-08-12 20:42 |  |  | Fair | No | Check found customer meter burnt needs to be replaced urgently refer to field service voltage left 111/112/223
Non-Outage | J.E.26.08.16727 | C001886098 | Oshane Warren |  | Completed |  |  | 2026-08-12 07:49 | 2026-08-13 07:37 | 2026-08-13 08:25 | 2026-08-13 08:26 | 2026-08-13 08:26 | 2026-08-13 08:26 | 2026-08-13 08:27 | 2026-08-13 08:27 |  |  | Fair | No | Hexing metering system refer to field service
Outage | J.E.26.08.16904 | C001886100 | Romeo Brissett | St.James | Completed | Load_239431 | Bogue - 610 | 2026-08-12 07:52 | 2026-08-12 07:52 | 2026-08-12 08:04 | 2026-08-12 08:04 | 2026-08-12 09:18 | 2026-08-12 09:33 | 2026-08-12 10:02 | 2026-08-12 10:02 |  |  | Fair | No | Line patrolled found power in the area resident was ask and stated, Blue fields Belmont is Westmoreland. Please send to Westmoreland team.
Non-Outage | J.E.26.08.15718 | C001886104 | Romeo Brissett | St.James | Completed | Load_239941 | Bogue - 610 | 2026-08-12 07:53 | 2026-08-12 07:54 | 2026-08-12 19:19 | 2026-08-12 19:20 | 2026-08-12 20:32 | 2026-08-12 20:28 | 2026-08-12 20:36 | 2026-08-12 20:36 |  |  | Fair | No | Unable to locate customer
Non-Outage | J.E.26.08.15822 | C001886105 | Romeo Brissett | St.James | Completed | Load_256374 | Bogue - 610 | 2026-08-12 07:53 | 2026-08-12 07:54 | 2026-08-12 10:03 | 2026-08-12 10:03 | 2026-08-12 10:03 | 2026-08-12 10:14 | 2026-08-12 10:30 | 2026-08-12 10:30 |  |  | Fair | No | Check and found customer relocated there meter over 600ft from JPS, customer was advised to get an electrician. V/R 106–109-211
Non-Outage | J.E.26.08.16020 | C001886107 | Romeo Brissett | St.James | Completed | Load_255363 | Bogue - 610 | 2026-08-12 07:53 | 2026-08-12 07:54 | 2026-08-12 10:32 | 2026-08-12 10:32 | 2026-08-12 10:47 | 2026-08-12 11:00 | 2026-08-12 11:36 | 2026-08-12 11:36 | BrokenWire |  | Fair | No | Check and found telephone line not related to JPS, customer was advised.
Non-Outage | J.E.26.08.16882 | C001886103 | Raymond Lewis |  | Completed |  |  | 2026-08-12 07:53 | 2026-08-12 07:53 | 2026-08-12 08:36 | 2026-08-12 08:37 | 2026-08-12 08:36 | 2026-08-12 08:38 | 2026-08-12 08:38 | 2026-08-12 08:38 |  |  | Fair | No | Phone turn off
Outage | J.E.26.08.17014 | C001886102 | Raymond Lewis | St.Ann | Completed | Load_260937 | Roaring River - 210 | 2026-08-12 07:53 | 2026-08-12 07:53 | 2026-08-12 12:30 | 2026-08-12 12:31 | 2026-08-12 15:45 | 2026-08-12 15:46 | 2026-08-12 15:47 | 2026-08-12 15:47 |  |  | Fair | No | Phone not answering
Outage | J.E.26.08.16997 | C001886110 | Andre Williams | Trelawny | Completed | Load_262583 | Duncans - 210 | 2026-08-12 07:59 | 2026-08-12 15:18 | 2026-08-12 15:25 | 2026-08-12 16:22 | 2026-08-12 16:22 | 2026-08-12 16:22 | 2026-08-12 16:23 | 2026-08-12 16:23 |  |  | Fair | No | Retention low hanging neutral that was touching lower phase ,reset 50 kva trip type transformer area now with supply.
Non-Outage | J.E.26.07.34886 | C001886117 | Error Coore |  | Completed |  |  | 2026-08-12 08:03 | 2026-08-12 08:05 | 2026-08-12 11:10 | 2026-08-12 11:11 | 2026-08-12 11:32 | 2026-08-12 11:46 | 2026-08-12 11:47 | 2026-08-12 11:47 |  |  | Fair | No | Premises found ok customer have internal problem voltage reading 115/114/229 volts
Non-Outage | J.E.26.08.15660 | C001886116 | Error Coore | Manchester | Completed | Load_266835 | Porus - 310 | 2026-08-12 08:03 | 2026-08-12 08:05 | 2026-08-12 14:37 | 2026-08-12 14:38 | 2026-08-12 15:00 | 2026-08-12 15:26 | 2026-08-12 15:27 | 2026-08-12 15:27 |  |  | Fair | No | Premises found ok voltage reading 114/115/229 volts
Non-Outage | J.E.26.08.16110 | C001886115 | Error Coore | Manchester | Completed | Load_254918 | Porus - 310 | 2026-08-12 08:03 | 2026-08-12 08:05 | 2026-08-12 08:58 | 2026-08-12 11:48 | 2026-08-12 12:30 | 2026-08-12 13:17 | 2026-08-12 13:21 | 2026-08-12 13:21 |  |  | Fair | No | Premises found. Voltage reading 116/117/233 volts
Non-Outage | J.E.26.08.16925 | C001886114 | Error Coore | Manchester | Completed | Load_240559 | Porus - 310 | 2026-08-12 08:03 | 2026-08-12 08:05 | 2026-08-12 09:01 | 2026-08-12 09:02 | 2026-08-12 09:51 | 2026-08-12 11:01 | 2026-08-12 11:05 | 2026-08-12 11:05 |  |  | Fair | No | Found one span of secondary neutral dislodge open a 10 KVA xformer to splice and retention secondary neutral using 10 ft of #6 service wire neutral and 4 one bolt clamp voltage reading 115/116/231 volts
Non-Outage | J.E.26.08.14455 | C001886123 | Rusean Allen | KSAS | Completed | Load_257291 | Rockfort - 210 | 2026-08-12 08:08 | 2026-08-12 08:09 | 2026-08-12 10:54 | 2026-08-12 11:49 | 2026-08-12 11:51 | 2026-08-12 11:52 | 2026-08-12 11:52 | 2026-08-12 11:52 | BangingWires |  | Fair | No | Not found
Non-Outage | J.E.26.08.16958 | C001886124 | Marlon Authors |  | Completed |  |  | 2026-08-12 08:09 | 2026-08-12 08:10 | 2026-08-12 13:01 | 2026-08-12 13:01 | 2026-08-12 14:49 | 2026-08-12 16:24 | 2026-08-12 16:25 | 2026-08-12 16:25 | BrokenWire |  | Fair | No | Patrol and found defective customer service wire. Disconnect same and supply leave working ok rdg 111v,110v and cross phased 221 volts
Non-Outage | J.E.26.08.16739 | C001886134 | Rodclif Dawkins |  | Completed |  |  | 2026-08-12 08:13 | 2026-08-12 08:15 | 2026-08-12 08:53 | 2026-08-12 08:54 | 2026-08-12 09:21 | 2026-08-12 09:25 | 2026-08-12 09:26 | 2026-08-12 09:26 | LeaningPole |  | Fair | No | Customer was found with supply, however what customer was reporting is non-functional street light.
Non-Outage | J.E.26.08.17012 | C001886133 | Nickolas Rodriques |  | Completed |  |  | 2026-08-12 08:13 | 2026-08-12 08:15 | 2026-08-12 11:25 | 2026-08-12 11:52 | 2026-08-12 12:21 | 2026-08-12 13:00 | 2026-08-12 13:02 | 2026-08-12 13:02 | BrokenWire |  | Fair | No | Checked and found customer service wire broken caused by slack connection. Repaired by splice and retention wire using two clamps and two service sleeves, current reading is (118). Customer confirmed that all is well now.
Outage | J.E.26.08.17023 | C001886136 | Romeo Brissett | St.James | Completed | Load_243432 | Bogue - 610 | 2026-08-12 08:18 | 2026-08-12 08:19 | 2026-08-12 11:37 | 2026-08-12 11:37 | 2026-08-12 12:18 | 2026-08-12 15:00 | 2026-08-12 15:22 | 2026-08-12 15:22 | BrokenWire |  | Fair | No | Found 2 pole span of secondary broken due vehicle accident resulting leaning pole, isolated (1)10KVA transformer, spliced and retention 2 span of used 20ft of #2, (2)2/0 preformed and 4 clamps. (1)40ft TA construction pole with (1)10KVA Transformer single phase Primary and open secondary urgently need to be straighten along with (1)40ft T pole with single phase primary and open secondary one span from transformer pole leaning due to vehicle accident. Urgent attention needed. Please send to maintenance.
Non-Outage | J.E.26.08.02818 | C001886139 | Royston Montague | St.Catherine | Completed | Load_256101 | New Michelton - 410 | 2026-08-12 08:19 | 2026-08-12 08:21 | 2026-08-12 08:26 | 2026-08-13 08:46 | 2026-08-13 08:52 | 2026-08-13 08:52 | 2026-08-13 08:52 | 2026-08-13 08:52 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.08.02874 | C001886138 | Royston Montague | St.Catherine | Completed | Load_254399 | Tredegar - 310 | 2026-08-12 08:19 | 2026-08-12 08:21 | 2026-08-12 08:26 | 2026-08-12 12:16 | 2026-08-12 13:50 | 2026-08-12 13:50 | 2026-08-12 13:50 | 2026-08-12 13:50 |  |  | Rains | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.08.05417 | C001886137 | Royston Montague | St.Catherine | Completed | Load_568160 | Twickenham - 310 | 2026-08-12 08:19 | 2026-08-12 08:21 | 2026-08-12 08:26 | 2026-08-12 15:59 | 2026-08-12 15:59 | 2026-08-12 15:59 | 2026-08-12 15:59 | 2026-08-12 15:59 |  |  | Rains | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.07.39292 | C001886143 | Royston Montague | St.Catherine | Completed | Load_247630 | Tredegar - 510 | 2026-08-12 08:20 | 2026-08-12 08:21 | 2026-08-12 08:26 | 2026-08-12 10:24 | 2026-08-12 10:46 | 2026-08-12 12:15 | 2026-08-12 12:15 | 2026-08-12 12:15 |  |  | Fair | No | Corrosion at pothead same corrected, voltage found 209v 107v 99v voltage after job completion are 222v 111v 108v
Non-Outage | J.E.26.07.39982 | C001886140 | Royston Montague | St.Catherine | Completed | Load_269015 | Twickenham - 310 | 2026-08-12 08:20 | 2026-08-12 08:21 | 2026-08-12 08:26 | 2026-08-12 13:51 | 2026-08-12 15:27 | 2026-08-12 15:43 | 2026-08-12 15:44 | 2026-08-12 15:44 |  |  | Rains | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.07.40109 | C001886141 | Royston Montague | St.Catherine | Completed | Load_243412 | Tredegar - 310 | 2026-08-12 08:20 | 2026-08-12 08:21 | 2026-08-12 08:26 | 2026-08-12 08:43 | 2026-08-12 09:17 | 2026-08-12 09:18 | 2026-08-12 09:18 | 2026-08-12 09:18 |  |  | Fair | No | Faulty meter socket. Customer asked to get an electrician. Voltage 229v 114v 115v
Non-Outage | J.E.26.08.03352 | C001886142 | Royston Montague | St.Catherine | Completed | Load_248402 | Twickenham - 310 | 2026-08-12 08:20 | 2026-08-12 08:21 | 2026-08-12 08:26 | 2026-08-12 09:19 | 2026-08-12 09:22 | 2026-08-12 09:42 | 2026-08-12 09:42 | 2026-08-12 09:42 |  |  | Fair | No | Customer said they didn’t report an issue.
Outage | J.E.26.08.17046 | C001886165 | Edward Royal | KSAN | Completed | Load_241915 | Washington Blvd - 710 | 2026-08-12 08:30 | 2026-08-12 08:35 | 2026-08-12 09:18 | 2026-08-12 12:25 | 2026-08-12 12:25 | 2026-08-12 12:26 | 2026-08-12 12:28 | 2026-08-12 12:28 |  |  | Fair | No | When contacted customer by phone customer said that no one is at home
Outage | J.E.26.08.17040 | C001886167 | Edward Royal | KSAS | Completed | Load_290946 | Hunts Bay - 810 | 2026-08-12 08:31 | 2026-08-12 08:32 | 2026-08-12 09:18 | 2026-08-12 10:04 | 2026-08-12 10:15 | 2026-08-12 11:02 | 2026-08-12 11:03 | 2026-08-12 11:03 |  |  | Fair | No | Replaced 30A junction fuse
Non-Outage | J.E.26.08.16073 | C001886179 | Dean- Smith | Hanover | Completed | Load_250447 | Orange Bay - 310 | 2026-08-12 08:43 | 2026-08-12 08:45 | 2026-08-13 10:49 | 2026-08-13 10:50 | 2026-08-13 12:15 | 2026-08-13 12:15 | 2026-08-13 13:12 | 2026-08-13 13:12 |  |  | Rains | No | Splice and retention (2) span of secondary phase conductor , cause by leaning secondary 30/6 pole. Voltage left 111v,11v,222v.......secondary 30/6 DE pole decay/ leaning, please forward to maintenance dept to get pole replace.
Non-Outage | J.E.26.08.17036 | C001886181 | Dean- Smith | Hanover | Completed | Load_252494 | Orange Bay - 310 | 2026-08-12 08:43 | 2026-08-12 08:45 | 2026-08-13 08:01 | 2026-08-13 08:02 | 2026-08-13 10:45 | 2026-08-13 10:47 | 2026-08-13 10:48 | 2026-08-13 10:48 |  |  | EarthMovement | No | Unable to locate
Outage | J.E.26.08.17045 | C001886190 | Tyrese Williams | St.Ann | Completed | Load_238497 | Cardiff Hall - 210 | 2026-08-12 08:45 | 2026-08-12 08:47 | 2026-08-12 14:10 | 2026-08-12 14:11 | 2026-08-12 15:25 | 2026-08-12 15:28 | 2026-08-12 15:28 | 2026-08-12 15:28 |  |  | Fair | No | Customer was advised to go in the office
Non-Outage | J.E.26.07.39281 | C001886198 | Odaine Johnson | Clarendon | Completed | Load_267245 | Parnassus - 210 | 2026-08-12 08:47 | 2026-08-12 08:49 | 2026-08-12 10:50 | 2026-08-13 13:20 | 2026-08-13 13:19 | 2026-08-13 13:19 | 2026-08-13 13:20 | 2026-08-13 13:20 |  |  | Fair | No | Premises not found multiple efforts made to contact customer but was unsuccessful
Non-Outage | J.E.26.07.39315 | C001886199 | Odaine Johnson | Clarendon | Completed | Load_252773 | Monymusk - 410 | 2026-08-12 08:47 | 2026-08-12 08:49 | 2026-08-12 10:51 | 2026-08-12 11:06 | 2026-08-12 11:13 | 2026-08-12 11:13 | 2026-08-12 11:14 | 2026-08-12 11:14 |  |  | Fair | No | Premises found okay customer stated that the issue was resolved already
Non-Outage | J.E.26.07.39449 | C001886196 | Odaine Johnson | Clarendon | Completed | Load_263155 | Monymusk - 210 | 2026-08-12 08:47 | 2026-08-12 08:49 | 2026-08-12 10:50 | 2026-08-12 11:35 | 2026-08-12 11:41 | 2026-08-12 01:00 | 2026-08-12 11:42 | 2026-08-12 11:42 |  |  | Fair | No | Customer experiencing low voltage coming from rami box number HEX06922
Non-Outage | J.E.26.07.39538 | C001886197 | Odaine Johnson | Clarendon | Completed | Load_257855 | Monymusk - 210 | 2026-08-12 08:47 | 2026-08-12 08:49 | 2026-08-12 10:50 | 2026-08-12 11:15 | 2026-08-12 11:33 | 2026-08-12 11:33 | 2026-08-12 11:33 | 2026-08-12 11:33 |  |  | Fair | No | Premises found okay customer stated that the issue was resolved
Non-Outage | J.E.26.07.40009 | C001886195 | Odaine Johnson | Clarendon | Completed | Load_265906 | May Pen - 210 | 2026-08-12 08:47 | 2026-08-12 08:49 | 2026-08-12 10:50 | 2026-08-12 13:04 | 2026-08-12 13:22 | 2026-08-12 13:23 | 2026-08-12 13:24 | 2026-08-12 13:24 |  |  | Fair | No | Meter burn allowing customer to experiencing single phase, meter need replaced
Non-Outage | J.E.26.08.15992 | C001886192 | Odaine Johnson | Clarendon | Completed | Load_246068 | May Pen - 210 | 2026-08-12 08:47 | 2026-08-12 08:49 | 2026-08-12 10:49 | 2026-08-12 12:20 | 2026-08-12 12:25 | 2026-08-12 12:46 | 2026-08-12 12:48 | 2026-08-12 12:48 |  |  | Fair | No | Premises found okay voltage reading 112/115/228 volts, meter blank and not displaying need replaced
Non-Outage | J.E.26.08.16399 | C001886193 | Odaine Johnson | Clarendon | Completed | Load_258821 | Parnassus - 310 | 2026-08-12 08:47 | 2026-08-12 08:49 | 2026-08-12 10:50 | 2026-08-12 11:43 | 2026-08-12 11:48 | 2026-08-12 11:48 | 2026-08-12 11:48 | 2026-08-12 11:48 |  |  | Fair | No | Area experiencing on and off supply emergency team needed
Non-Outage | J.E.26.08.16855 | C001886194 | Odaine Johnson | Clarendon | Completed | Load_265690 | May Pen - 210 | 2026-08-12 08:47 | 2026-08-12 08:49 | 2026-08-12 10:50 | 2026-08-12 12:09 | 2026-08-12 12:10 | 2026-08-12 12:18 | 2026-08-12 12:19 | 2026-08-12 12:19 | LowHangingWires |  | Fair | No | Burn off neutral leads to service wire hanging retention and connected using 1 one bolt clamp voltage reading 115/114/230 volts
Non-Outage | J.E.26.07.39068 | C001886200 | Odaine Johnson | Clarendon | Completed | Load_269757 | Monymusk - 210 | 2026-08-12 08:48 | 2026-08-12 08:49 | 2026-08-12 10:51 | 2026-08-12 13:25 | 2026-08-13 08:04 | 2026-08-13 08:04 | 2026-08-13 08:05 | 2026-08-13 08:05 |  |  | Fair | No | Premises was found working ok voltage reading is A115 B116 AB231
Non-Outage | J.E.26.08.16990 | C001886201 | Odaine Johnson | Clarendon | Completed | Load_579463 | Parnassus - 310 | 2026-08-12 08:48 | 2026-08-12 08:49 | 2026-08-12 10:51 | 2026-08-12 11:49 | 2026-08-12 12:01 | 2026-08-12 12:06 | 2026-08-12 12:08 | 2026-08-12 12:08 |  |  | Fair | No | Meter burn allowin customer to be experiencing single phase
Non-Outage | J.E.26.07.25185 | C001886202 | Rochaine Hussey | KSAN | Completed | Load_255669 | Constant Spring - 310 | 2026-08-12 08:49 | 2026-08-12 08:50 | 2026-08-12 11:02 | 2026-08-12 13:42 | 2026-08-12 13:42 | 2026-08-12 13:43 | 2026-08-12 13:43 | 2026-08-12 13:43 |  |  | Fair | No | Customer said issue was already resolved
Non-Outage | J.E.26.07.39887 | C001886205 | Rochaine Hussey | KSAN | Completed | Load_265225 | Constant Spring - 210 | 2026-08-12 08:49 | 2026-08-12 08:50 | 2026-08-12 09:23 | 2026-08-13 11:40 | 2026-08-13 11:39 | 2026-08-13 12:55 | 2026-08-13 12:55 | 2026-08-13 12:55 |  |  | Fair | No | Customer say the issue was resolved and Premesis is now okay
Non-Outage | J.E.26.08.16094 | C001886206 | Rochaine Hussey | KSAN | Completed | Load_253056 | Constant Spring - 410 | 2026-08-12 08:49 | 2026-08-12 08:53 | 2026-08-12 11:08 | 2026-08-12 11:08 | 2026-08-12 11:10 | 2026-08-12 11:19 | 2026-08-12 11:19 | 2026-08-12 11:19 |  |  | Fair | No | Customer meter burnt which causes customer to be getting single Reffering to field service 113/116/29v
Non-Outage | J.E.26.08.16324 | C001886203 | Rochaine Hussey | KSAN | Completed | Load_574518 | Constant Spring - 210 | 2026-08-12 08:49 | 2026-08-12 08:50 | 2026-08-12 13:12 | 2026-08-12 13:13 | 2026-08-12 13:13 | 2026-08-12 13:40 | 2026-08-12 13:41 | 2026-08-12 13:41 |  |  | Fair | No | Meter in hexing box needs to be checked due to low voltage coming from box Hex 04067 101/140v Referring to field service Custom is unable to use appliances
Non-Outage | J.E.26.08.10291 | C001886216 | Fredrick Hamilton | KSAN | Completed | Load_257856 | Washington Blvd - 410 | 2026-08-12 08:51 | 2026-08-13 09:54 | 2026-08-13 10:06 | 2026-08-13 12:29 | 2026-08-13 12:41 | 2026-08-13 13:27 | 2026-08-13 13:27 | 2026-08-13 13:27 |  |  | Fair | No | 205v/113v/55v obtained Low voltage detected on secondary line Requesting emergency to check lineMultiple customers affected
Non-Outage | J.E.26.08.13668 | C001886215 | Fredrick Hamilton | KSAN | Completed | Load_251797 | Constant Spring - 410 | 2026-08-12 08:51 | 2026-08-13 09:54 | 2026-08-13 10:06 | 2026-08-13 10:11 | 2026-08-13 10:10 | 2026-08-13 10:13 | 2026-08-13 10:13 | 2026-08-13 10:13 |  |  | Fair | No | Emergency crew required to open line to lesson load in order to do repairs Customers experiencing low voltage on 1 phase
Non-Outage | J.E.26.08.13834 | C001886217 | Eric Williams | KSAN | Completed | Load_253397 | Washington Blvd - 810 | 2026-08-12 08:51 | 2026-08-12 10:01 | 2026-08-12 11:34 | 2026-08-12 11:35 | 2026-08-12 14:00 | 2026-08-12 14:18 | 2026-08-12 14:38 | 2026-08-12 14:38 | BangingWires,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards | Y | Fair | No | Tree over grown open secondary conductors causing open secondary phase and neutral to come in contact.
Non-Outage | J.E.26.08.16146 | C001886218 | Locksley Allen | St.Mary | Completed | Load_254261 | Blackstonedge - 110 | 2026-08-12 08:53 | 2026-08-12 08:55 | 2026-08-12 11:36 | 2026-08-12 11:49 | 2026-08-12 11:48 | 2026-08-12 11:57 | 2026-08-12 11:57 | 2026-08-12 11:57 | Fire |  | Fair | No | The secondary line is slack and hanging low. Some trees are entangle in the line. Two strands of wire in the top conductor is burst. Please refer to emergency. Customer doesn’t live near the problem
Non-Outage | J.E.26.08.10395 | C001886223 | Locksley Allen | St.Ann | Completed | Load_262554 | Upper White River - 110 | 2026-08-12 08:54 | 2026-08-12 08:55 | 2026-08-12 12:04 | 2026-08-12 12:04 | 2026-08-12 12:04 | 2026-08-12 12:09 | 2026-08-12 12:07 | 2026-08-12 12:07 |  |  | Fair | No | Need better direction and customer not answering the
Non-Outage | J.E.26.08.12357 | C001886219 | Locksley Allen | St.Mary | Completed | Load_262614 | Blackstonedge - 110 | 2026-08-12 08:54 | 2026-08-12 08:55 | 2026-08-12 10:10 | 2026-08-12 11:26 | 2026-08-12 11:26 | 2026-08-12 11:31 | 2026-08-12 11:27 | 2026-08-12 11:27 |  |  | Fair | No | No single phase problem found at premises.Voltage at meter socket phase to phase 233v. Phase to neutral 116&117vMeter left working okay
Non-Outage | J.E.26.08.12648 | C001886222 | Hopeton Henry | St.Thomas | Completed | Load_577193 | Good Year - 110 | 2026-08-12 08:54 | 2026-08-12 08:55 | 2026-08-12 09:49 | 2026-08-12 11:20 | 2026-08-12 11:20 | 2026-08-12 11:21 | 2026-08-12 11:21 | 2026-08-12 11:21 |  |  | Fair | No | Customer not located customer not located
Non-Outage | J.E.26.08.16651 | C001886220 | Hopeton Henry | St.Thomas | Completed | Load_577252 | Good Year - 110 | 2026-08-12 08:54 | 2026-08-12 08:55 | 2026-08-12 09:49 | 2026-08-12 11:55 | 2026-08-12 12:34 | 2026-08-12 13:09 | 2026-08-12 13:12 | 2026-08-12 13:12 |  |  | Fair | No | Correct corrosion problem at pole and pot head 114–116-230 volts
Non-Outage | J.E.26.08.17005 | C001886237 | Andrae Clarke | Portland | Completed | Load_257633 | Port Antonio - 310 | 2026-08-12 08:55 | 2026-08-12 08:58 | 2026-08-12 10:43 | 2026-08-12 10:44 | 2026-08-12 10:51 | 2026-08-12 10:55 | 2026-08-12 10:58 | 2026-08-12 10:58 |  |  | Fair | No | Check voltage 120/119/239 Meter defective meter burn delivering only one legReferring to field service to change meter
Non-Outage | J.E.26.08.13842 | C001886245 | Neckell Ormsby | St.Mary | Completed | Load_238645 | Highgate - 210 | 2026-08-12 09:06 | 2026-08-12 09:10 | 2026-08-12 10:04 | 2026-08-12 10:05 | 2026-08-12 10:41 | 2026-08-12 10:51 | 2026-08-12 10:51 | 2026-08-12 10:51 | LowHangingWires |  | Fair | No | Customer made report on behalf of Mr Riley however unable to get to Mr Riley after several calls also unable to locate low hanging wire
Non-Outage | J.E.26.08.15846 | C001886246 | Elvis Trowers | KSAS | Completed | Load_241155 | Hunts Bay - 110 | 2026-08-12 09:10 | 2026-08-12 09:11 | 2026-08-12 10:53 | 2026-08-12 10:53 | 2026-08-12 11:53 | 2026-08-12 11:55 | 2026-08-12 12:03 | 2026-08-12 12:03 |  |  | Fair | No | Isolate bank of 3-100 kva at pole #0052341 and repair twisted #2/0 quad crystallized burnt and broken. Repaired using four 1- bolt clamps. And reclose bank of transformers.
Non-Outage | J.E.26.08.15662 | C001886251 | Fredrick Hamilton | KSAS | Completed | Load_261554 | Duhaney - 310 | 2026-08-12 09:11 | 2026-08-12 09:12 | 2026-08-12 09:20 | 2026-08-12 10:16 | 2026-08-12 10:31 | 2026-08-12 11:32 | 2026-08-12 11:32 | 2026-08-12 11:32 |  |  | Fair | No | Corrosion detected at pothead same was connected 3 penunion used235v/118v/117v obtained
Non-Outage | J.E.26.08.16088 | C001886250 | Rochaine Hussey | KSAS | Completed | Load_243423 | Duhaney - 310 | 2026-08-12 09:11 | 2026-08-12 09:12 | 2026-08-12 11:39 | 2026-08-12 11:39 | 2026-08-12 11:39 | 2026-08-12 12:39 | 2026-08-12 12:39 | 2026-08-12 12:39 |  |  | Fair | No | Corrosion on pole1clamp usedIssue resolved 108/110/218v
Non-Outage | J.E.26.08.16339 | C001886249 | Fredrick Hamilton | KSAS | Completed | Load_266131 | Duhaney - 310 | 2026-08-12 09:11 | 2026-08-12 09:12 | 2026-08-12 09:20 | 2026-08-12 11:34 | 2026-08-12 11:48 | 2026-08-12 11:52 | 2026-08-12 11:52 | 2026-08-12 11:52 |  |  | Fair | No | Multiple calls to customer went to voicemail Premises locked
Outage | J.E.26.08.16766 | C001886253 | Kemark Slue | Portmore | Completed | Load_244609 | Naggo Head - 510 | 2026-08-12 09:13 | 2026-08-12 09:13 | 2026-08-12 09:35 | 2026-08-12 09:36 | 2026-08-12 10:17 | 2026-08-12 10:19 | 2026-08-12 11:08 | 2026-08-12 11:08 |  |  | Fair | No | Upon arrival at the location the crew discovered that bush phase trip saver hotline clamp was burnt off from main, isolate trip saver and used live line techniques to replace stirrup and hotline clamp and re-energized line section.
Non-Outage | J.E.26.08.17065 | C001886254 | Romeo Brissett | St.James | Completed | Load_266714 | Bogue - 610 | 2026-08-12 09:15 | 2026-08-12 09:16 | 2026-08-12 17:18 | 2026-08-12 17:19 | 2026-08-12 17:54 | 2026-08-12 19:00 | 2026-08-12 19:19 | 2026-08-12 19:19 | BrokenWire |  | Fair | No | Spliced and retention customer service wire, used 30ft of #6 3 clamps
Non-Outage | J.E.26.08.00883 | C001886258 | Andrae Dawkins | St.James | Completed | Load_576009 | Bogue - 310 | 2026-08-12 09:16 | 2026-08-12 09:18 | 2026-08-12 09:37 | 2026-08-12 13:11 | 2026-08-12 13:37 | 2026-08-12 12:24 | 2026-08-12 13:43 | 2026-08-12 13:43 |  |  | Fair | No | Check and found okay voltage found 116/118/234 Customer said that she experienced low voltage mostly during the night refer back to field service EN 07114
Non-Outage | J.E.26.08.16861 | C001886257 | Andrae Dawkins | St.James | Completed | Load_254682 | Bogue - 310 | 2026-08-12 09:16 | 2026-08-12 09:18 | 2026-08-12 09:37 | 2026-08-12 09:37 | 2026-08-12 12:04 | 2026-08-12 10:09 | 2026-08-12 12:12 | 2026-08-12 12:12 |  |  | Fair | No | Found customer single phasing from EG box 01668 voltage found 118/57/236 refer back to field service
Non-Outage | J.E.26.08.17068 | C001886256 | Andrae Dawkins | St.James | Completed | Load_264759 | Bogue - 310 | 2026-08-12 09:16 | 2026-08-12 09:18 | 2026-08-12 09:37 | 2026-08-12 12:42 | 2026-08-12 12:42 | 2026-08-12 11:46 | 2026-08-12 13:10 | 2026-08-12 13:10 |  |  | Fair | No | Found customer single phasing due to slack connection at pole clean and remade joints voltage left 113/110/223
Outage | J.E.26.08.17062 | C001886259 | Cliton Henry | St.Mary | Completed | Load_253901 | Oracabessa - 110 | 2026-08-12 09:19 | 2026-08-12 09:22 | 2026-08-12 09:54 | 2026-08-12 09:54 | 2026-08-12 10:14 | 2026-08-12 10:52 | 2026-08-12 10:54 | 2026-08-12 10:54 | TreeContact |  | Fair | No | Unable to access tree from public roadway. Customer premises lock need a re visit.
Outage | J.E.26.08.17083 | C001886260 | Hopeton Henry | St.Thomas | Completed | Load_577232 | Good Year - 210 | 2026-08-12 09:20 | 2026-08-12 09:20 | 2026-08-12 09:45 | 2026-08-12 09:45 | 2026-08-12 09:45 | 2026-08-12 09:46 | 2026-08-12 09:48 | 2026-08-12 09:48 |  |  | Fair | No | Refuse junction and 25 kva transformer 5 amp , 3 amp fuse used
Non-Outage | J.E.26.08.17030 | C001886264 | Swon Miller | St.James | Completed | Load_248155 | Queens Drive - 710 | 2026-08-12 09:21 | 2026-08-12 09:22 | 2026-08-12 12:42 | 2026-08-12 12:42 | 2026-08-12 13:01 | 2026-08-12 13:24 | 2026-08-12 13:28 | 2026-08-12 13:28 |  |  | Fair | No | Check and found areas okay
Non-Outage | J.E.26.08.17032 | C001886263 | Swon Miller | St.James | Completed | Load_256990 | Queens Drive - 710 | 2026-08-12 09:21 | 2026-08-12 09:22 | 2026-08-12 10:12 | 2026-08-12 10:13 | 2026-08-12 10:32 | 2026-08-18 00:30 | 2026-08-12 12:40 | 2026-08-12 12:40 |  |  | Fair | No | Found customers voltage fluctuating voltage found 103/111due to 2/o hampack without tongue no connection to neutral open 25 kva transformer to carry out repairs clean and remake joints use 2pg voltage left 113/112/226
Outage | J.E.26.08.17085 | C001886265 | Elvis Trowers | KSAS | Completed | Load_239260 | Hunts Bay - 210 | 2026-08-12 09:21 | 2026-08-12 09:25 | 2026-08-12 12:05 | 2026-08-12 12:05 | 2026-08-12 12:22 | 2026-08-12 00:25 | 2026-08-12 12:23 | 2026-08-12 12:23 | BrokenPole |  | Fair | No | Broken pole belongs to telephone company
Non-Outage | J.E.26.08.00942 | C001886269 | Odeanie Davis | KSAS | Completed | Load_253227 | Cane River - 610 | 2026-08-12 09:22 | 2026-08-12 09:24 | 2026-08-12 10:32 | 2026-08-12 10:34 | 2026-08-12 10:38 | 2026-08-12 10:59 | 2026-08-12 10:59 | 2026-08-12 10:59 |  |  | Fair | No
Non-Outage | J.E.26.08.06259 | C001886266 | Odeanie Davis | KSAS | Completed | Load_242999 | Cane River - 410 | 2026-08-12 09:22 | 2026-08-12 09:24 | 2026-08-12 10:17 | 2026-08-12 10:17 | 2026-08-12 10:30 | 2026-08-12 10:40 | 2026-08-12 10:32 | 2026-08-12 10:32 |  |  | Fair | No | 114v&115v & 230v at location, no power issues found.
Non-Outage | J.E.26.08.06395 | C001886268 | Odeanie Davis | KSAS | Completed | Load_258722 | Cane River - 410 | 2026-08-12 09:22 | 2026-08-12 09:24 | 2026-08-12 10:10 | 2026-08-12 10:10 | 2026-08-12 10:10 | 2026-08-12 10:23 | 2026-08-12 10:16 | 2026-08-12 10:16 |  |  | Fair | No | Customer stated that issue was resolved
Outage | J.E.26.08.17086 | C001886267 | Denton Williams | Portland | Completed | Load_250156 | Port Antonio - 410 | 2026-08-12 09:22 | 2026-08-12 09:27 | 2026-08-12 09:40 | 2026-08-12 09:41 | 2026-08-12 10:49 | 2026-08-12 11:00 | 2026-08-12 11:05 | 2026-08-12 11:05 | LeakingTransformer | Y | Fair | No | Use one 20 amp to connect blown fuse, all customers restored
Non-Outage | J.E.26.07.09434 | C001886271 | Odeanie Davis | KSAS | Completed | Load_263506 | Cane River - 310 | 2026-08-12 09:23 | 2026-08-12 09:24 | 2026-08-12 10:07 | 2026-08-12 13:38 | 2026-08-12 13:38 | 2026-08-12 13:47 | 2026-08-12 13:38 | 2026-08-12 13:38 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.16247 | C001886270 | Elvis Trowers | KSAS | Completed | Load_241982 | Greenwich - 310 | 2026-08-12 09:23 | 2026-08-12 09:25 | 2026-08-12 09:58 | 2026-08-12 13:25 | 2026-08-12 14:43 | 2026-08-12 14:50 | 2026-08-12 14:53 | 2026-08-12 14:53 |  |  | Rains | No | Found okay upon arrival. Customer has an internal problem. Readings at meter socket 114-115-205 and 233-232-231 volts.
Outage | J.E.26.08.14291 | C001886273 | Javid Vernon | Westmoreland | Completed | Load_253762 | Paradise - 310 | 2026-08-12 09:24 | 2026-08-12 09:25 | 2026-08-12 11:51 | 2026-08-12 11:52 | 2026-08-12 12:47 | 2026-08-12 13:05 | 2026-08-12 13:06 | 2026-08-12 13:06 |  |  | Fair | No | Replace 70ft #6 triplex wire and use 4 clamps voltage reading 112/112/224
Non-Outage | J.E.26.08.03800 | C001886277 | Raymond Lewis | St.Ann | Completed | Load_240309 | Ocho Rios - 310 | 2026-08-12 09:25 | 2026-08-12 09:26 | 2026-08-12 10:18 | 2026-08-12 10:19 | 2026-08-12 10:48 | 2026-08-12 10:50 | 2026-08-12 10:50 | 2026-08-12 10:50 |  |  | Fair | No | Remade joint at pole 3 wire service
Non-Outage | J.E.26.08.14986 | C001886280 | Michael Paterson |  | Completed |  |  | 2026-08-12 09:29 | 2026-08-13 07:37 | 2026-08-13 08:13 | 2026-08-13 08:14 | 2026-08-13 10:36 | 2026-08-13 10:42 | 2026-08-13 10:42 | 2026-08-13 10:42 |  |  | Fair | No | Contact customer via phone call she advise crew that supply was restored
Outage | J.E.26.08.17118 | C001886291 | Cliton Henry | St.Ann | Completed | Load_268139 | Upper White River - 110 | 2026-08-12 09:40 | 2026-08-12 09:41 | 2026-08-12 10:51 | 2026-08-12 10:55 | 2026-08-12 11:59 | 2026-08-12 12:43 | 2026-08-12 12:47 | 2026-08-12 12:47 |  |  | Fair | No | A 10 amp trip saver found tripped at Claude Stewart way entrance at pole #108407 due to bamboo trees fell on single phase primary line. Corrective work done to cut and remove bamboo trees and other branches that is in close proximity to the primary line. Supply restored to energized the 10 kva transformer at pole 108407.
Outage | J.E.26.08.17112 | C001886293 | Elvis Trowers | KSAS | Completed | Load_269025 | Hunts Bay - 210 | 2026-08-12 09:45 | 2026-08-12 09:46 | 2026-08-12 12:24 | 2026-08-12 12:24 | 2026-08-12 12:27 | 2026-08-12 12:30 | 2026-08-12 12:35 | 2026-08-12 12:35 |  |  | Fair | No | Drop out switch at pole # 0063382 one of the switch top burn off at hotline clamp and styrup in main line . The bush leg burn off . Need bucket truck to repair in main line. Pole is at the intersection of tower street and Johns lane.
Outage | J.E.26.08.17121 | C001886292 | Edward Royal | KSAN | Completed | Load_256453 | Washington Blvd - 710 | 2026-08-12 09:45 | 2026-08-12 09:46 | 2026-08-12 12:47 | 2026-08-12 12:48 | 2026-08-12 12:47 | 2026-08-12 13:10 | 2026-08-12 13:10 | 2026-08-12 13:10 |  |  | Fair | No | Customer has a meter mixed up advise customers to visit ruthven road for more information
Outage | J.E.26.08.17128 | C001886306 | Eric Williams | KSAN | Completed | Load_259570 | Constant Spring - 210 | 2026-08-12 09:53 | 2026-08-12 09:54 | 2026-08-12 09:59 | 2026-08-12 10:00 | 2026-08-12 10:05 | 2026-08-12 11:32 | 2026-08-12 11:34 | 2026-08-12 11:34 |  |  | Fair | No | Blown 65amps fuse found and replaced cause by defective arrester
Outage | J.E.26.08.17098 | C001886310 | Marlon Authors | Manchester | Completed | Load_255704 | Spur Tree - 210 | 2026-08-12 09:56 | 2026-08-12 11:29 | 2026-08-12 11:48 | 2026-08-12 11:49 | 2026-08-12 12:16 | 2026-08-12 12:49 | 2026-08-12 12:49 | 2026-08-12 12:49 | Fire |  | Fair | No | Supply checked and found one drop lead burnt off from the transformer lug . Isolate and close 50 kva transformers in bankers 3, to remaid same. Supply leave working okay rdg 235v,233v and 235 volts
Outage | J.E.26.08.17113 | C001886311 | Kenroy Dale | Manchester | Completed | Load_241306 | Porus - 310 | 2026-08-12 09:58 | 2026-08-13 07:19 | 2026-08-13 08:21 | 2026-08-13 08:39 | 2026-08-13 09:13 | 2026-08-13 09:21 | 2026-08-13 09:22 | 2026-08-13 09:22 |  |  | Fair | No | Area found with supply customer also confirmed that supply was restored
Outage | J.E.26.08.17135 | C001886317 | Stephen Taylor | St.Thomas | Completed | Load_258020 | Good Year - 110 | 2026-08-12 10:01 | 2026-08-12 10:21 | 2026-08-12 14:28 | 2026-08-12 14:29 | 2026-08-12 14:28 | 2026-08-12 14:28 | 2026-08-12 14:29 | 2026-08-12 14:29 |  |  | Fair | No | Transformer switch defective and need to be changed
Outage | J.E.26.08.17168 | C001886369 | Edward Royal | KSAN | Completed | Load_268663 | Washington Blvd - 710 | 2026-08-12 10:30 | 2026-08-12 10:31 | 2026-08-12 11:09 | 2026-08-12 11:10 | 2026-08-12 11:09 | 2026-08-12 12:21 | 2026-08-12 12:21 | 2026-08-12 12:21 | BrokenWire |  | Fair | No | Debush tree from secondary line spliced and reconnected secondary phase using 50ft umber 2 conductor 3 single bolt clamp
Outage | J.E.26.08.17114 | C001886385 | Rodclif Dawkins | St.Catherine | Completed | Load_237792 | Rhodens Pen - 410 | 2026-08-12 10:31 | 2026-08-12 10:33 | 2026-08-12 11:35 | 2026-08-12 11:35 | 2026-08-12 11:35 | 2026-08-12 02:47 | 2026-08-12 14:47 | 2026-08-12 14:47 |  |  | Fair | No | Found lower phase of open secondary broken/burnt. 50kva transformer was de-energized. Using 150ft of aa2/0 conductor and 1,2/0 tension sleeve repairs were done . 50kva transformer energized
Outage | J.E.26.08.17122 | C001886384 | Rodclif Dawkins | St.Catherine | Completed | Load_238407 | Rhodens Pen - 210 | 2026-08-12 10:31 | 2026-08-12 10:33 | 2026-08-12 10:46 | 2026-08-12 10:47 | 2026-08-12 11:33 | 2026-08-12 11:33 | 2026-08-12 11:35 | 2026-08-12 11:35 |  |  | Fair | No | Customer meter turned by customer care
Outage | J.E.26.08.17137 | C001886383 | Kemark Slue | St.Catherine | Completed | Load_243531 | Tredegar - 310 | 2026-08-12 10:31 | 2026-08-12 10:33 | 2026-08-12 11:13 | 2026-08-12 11:13 | 2026-08-12 11:29 | 2026-08-12 11:34 | 2026-08-12 11:34 | 2026-08-12 11:34 |  |  | Fair | No | Upon arrival at the location the crew discovered that customer’s CIU isn’t working please refer to Moses Elliston.
Non-Outage | J.E.26.08.17073 | C001886387 | Neville Spencer |  | Completed |  |  | 2026-08-12 10:33 | 2026-08-12 10:36 | 2026-08-12 11:33 | 2026-08-12 11:34 | 2026-08-12 12:39 | 2026-08-12 13:47 | 2026-08-12 13:54 | 2026-08-12 13:54 | BrokenWire |  | Fair | No | Open 25 kva xmfr r at pole # 0162628 splice and retention broken secondary phase Conductor used 20 ft wire, 2 clamps,1, preform, 1, 2/0 splicing sleeve supply restored.
Outage | J.E.26.08.17194 | C001886412 | Moses Elliston | St.Catherine | Completed | Load_243404 | Twickenham - 310 | 2026-08-12 10:36 | 2026-08-12 10:37 | 2026-08-13 17:47 | 2026-08-13 17:47 | 2026-08-13 17:47 | 2026-08-13 17:48 | 2026-08-13 17:48 | 2026-08-13 17:48 |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.08.17178 | C001886413 | Christopher Edwards | KSAN | Completed | Load_246942 | Constant Spring - 410 | 2026-08-12 10:37 | 2026-08-12 10:56 | 2026-08-12 11:43 | 2026-08-12 11:45 | 2026-08-12 12:13 | 2026-08-12 13:00 | 2026-08-12 13:05 | 2026-08-12 13:05 | BrokenPole |  | Fair | No | Customer is requesting for guy to be removed from their property Customer is expanding and want guy to be removed Supply is at the premises
Outage | J.E.26.08.17195 | C001886414 | Denton Williams | Portland | Completed | Load_266103 | Port Antonio - 410 | 2026-08-12 10:38 | 2026-08-12 10:42 | 2026-08-12 11:06 | 2026-08-12 11:06 | 2026-08-12 11:21 | 2026-08-12 11:21 | 2026-08-12 11:23 | 2026-08-12 11:23 | Fire |  | Fair | No | Customer was on disconnection. Power is now restored.
Outage | J.E.26.08.17185 | C001886429 | Wayne Dillion | St.Elizabeth | Completed | Load_249601 | Maggotty - 110 | 2026-08-12 10:43 | 2026-08-13 07:12 | 2026-08-13 10:36 | 2026-08-13 12:25 | 2026-08-13 12:25 | 2026-08-13 12:30 | 2026-08-13 12:30 | 2026-08-13 12:30 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Reconnect Customer using 120ft of #6 triplex service wire, 3 clamps and 3 linkets. Supply leave working okay reading 110v, 110v and cross phase 221volts.
Outage | J.E.26.08.17210 | C001886439 | Milton Charlton | KSAN | Completed | Load_569913 | West Kings House - 310 | 2026-08-12 10:49 | 2026-08-12 10:51 | 2026-08-12 10:57 | 2026-08-12 10:57 | 2026-08-12 12:40 | 2026-08-12 11:35 | 2026-08-12 12:43 | 2026-08-12 12:43 |  |  | Fair | No | Found okay upon arrival. Customer was doing maintenance on internal electrical system.
Outage | J.E.26.08.17159 | C001886455 | Shawn Medley | St.James | Completed | Load_556790 | Bogue - 310 | 2026-08-12 10:53 | 2026-08-12 10:53 | 2026-08-12 11:44 | 2026-08-12 11:45 | 2026-08-12 12:02 | 2026-08-12 12:19 | 2026-08-12 12:19 | 2026-08-12 12:19 | BrokenWire |  | Fair | No | Found broken #6 service wire ,I isolated broken wire. Customer without supply refer to field service technician to carryout repair. EG box connection.
Non-Outage | J.E.26.08.17217 | C001886463 | Edward Royal |  | Completed |  |  | 2026-08-12 10:57 | 2026-08-12 11:00 | 2026-08-12 12:34 | 2026-08-12 12:34 | 2026-08-12 12:34 | 2026-08-12 12:35 | 2026-08-12 12:35 | 2026-08-12 12:35 | Fire |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.08.17228 | C001886479 | Cliton Henry | St.Mary | Completed | Load_257364 | Oracabessa - 210 | 2026-08-12 11:03 | 2026-08-12 11:06 | 2026-08-12 15:20 | 2026-08-12 15:20 | 2026-08-12 15:20 | 2026-08-12 15:35 | 2026-08-12 15:35 | 2026-08-12 15:35 |  |  | Fair | No | Two (2) blown 10 amp fuse found at a bank of 3 transformer pole #0041444. Supply restored using two (2) 10 amp fuse.
Outage | J.E.26.08.17235 | C001886480 | Raymond Lewis | St.Ann | Completed | Load_248659 | Upper White River - 210 | 2026-08-12 11:04 | 2026-08-12 11:06 | 2026-08-12 12:28 | 2026-08-12 12:29 | 2026-08-12 12:28 | 2026-08-12 12:30 | 2026-08-12 12:30 | 2026-08-12 12:30 | BrokenWire |  | Fair | No | Remade joints at pole 3 wire service
Outage | J.E.26.08.17247 | C001886491 | Swon Miller | St.James | Completed | Load_256990 | Queens Drive - 710 | 2026-08-12 11:09 | 2026-08-12 11:10 | 2026-08-12 13:29 | 2026-08-12 13:29 | 2026-08-12 13:45 | 2026-08-12 13:56 | 2026-08-12 13:55 | 2026-08-12 13:55 |  |  | Fair | No | Check and found areas okay voltage found 115/117/233 customer states that power supply has been restored
Non-Outage | J.E.26.08.16434 | C001886501 | Daniel Lobar | Trelawny | Completed | Load_267441 | Greenwood - 210 | 2026-08-12 11:11 | 2026-08-12 11:12 | 2026-08-12 15:35 | 2026-08-12 15:35 | 2026-08-12 16:59 | 2026-08-12 17:07 | 2026-08-12 17:07 | 2026-08-12 17:07 |  |  | Fair | No | Premises not found. Customer was unable to locate, after several attempts were made to contact the customer. The phone remains unanswered.
Outage | J.E.26.08.17226 | C001886502 | Michael Paterson | Westmoreland | Completed | Load_291994 | Paradise - 110 | 2026-08-12 11:12 | 2026-08-12 11:16 | 2026-08-12 14:25 | 2026-08-12 14:25 | 2026-08-12 14:25 | 2026-08-12 14:29 | 2026-08-12 14:29 | 2026-08-12 14:29 | BrokenWire |  | Fair | No | Customer service wire was cut down but field service agent, customer mentioned that agent was driving a white wish, please refer to Clainton Johnson at paradise to investigate matter, customer is very disgruntled, he further mentioned that his bills were paid in full.
Non-Outage | J.E.26.08.17262 | C001886510 | Roemello Brown | Trelawny | Completed | Load_1001670 | Greenwood - 210 | 2026-08-12 11:16 | 2026-08-12 15:36 | 2026-08-13 08:44 | 2026-08-13 09:13 | 2026-08-13 09:37 | 2026-08-13 09:38 | 2026-08-13 10:09 | 2026-08-13 10:09 |  |  | Fair | No | Corrosion at the pole side have clamps change Voltage found 114/26/113Voltage leave 114/115/229
Outage | J.E.26.08.17103 | C001886517 | Moses Elliston | St.Catherine | Completed | Load_249334 | Tredegar - 210 | 2026-08-12 11:27 | 2026-08-13 07:27 | 2026-08-13 08:49 | 2026-08-13 08:49 | 2026-08-13 08:50 | 2026-08-13 08:50 | 2026-08-13 08:50 | 2026-08-13 08:50 | LowHangingWires |  | Fair | No | For next Crew
Outage | J.E.26.08.17066 | C001886518 | Nickolas Rodriques | Portmore | Completed | Load_240031 | Naggo Head - 610 | 2026-08-12 11:28 | 2026-08-12 11:29 | 2026-08-12 13:02 | 2026-08-12 13:05 | 2026-08-12 13:15 | 2026-08-12 13:16 | 2026-08-12 13:19 | 2026-08-12 13:19 | BrokenWire |  | Fair | No | Call relates to the broken service wire that was repaired earlier.
Outage | J.E.26.08.17267 | C001886519 | Christopher Edwards | KSAN | Completed | Load_244973 | Constant Spring - 410 | 2026-08-12 11:28 | 2026-08-12 11:29 | 2026-08-12 14:03 | 2026-08-12 14:03 | 2026-08-12 14:47 | 2026-08-12 15:07 | 2026-08-12 15:07 | 2026-08-12 15:07 | BrokenWire |  | Fair | No | Remake burnt off phase joint Using (1) one bolt clamps Voltage:115,114,230v
Non-Outage | J.E.26.08.17214 | C001886528 | Elvis Trowers | KSAS | Completed | Load_269480 | Hunts Bay - 710 | 2026-08-12 11:32 | 2026-08-12 11:32 | 2026-08-12 12:42 | 2026-08-12 12:43 | 2026-08-12 13:22 | 2026-08-12 13:25 | 2026-08-12 13:24 | 2026-08-12 13:24 |  |  | Fair | No | Found one 3 amps transformer fuse blown at pole # 0100085. Refused using one 3 amps fuse and reclosed transformer switch.
Outage | J.E.26.08.17000 | C001886529 | Neville Spencer | Clarendon | Completed | Load_241995 | Parnassus - 210 | 2026-08-12 11:32 | 2026-08-12 11:34 | 2026-08-12 14:23 | 2026-08-12 14:23 | 2026-08-12 14:30 | 2026-08-12 14:30 | 2026-08-12 14:33 | 2026-08-12 14:33 |  |  | Fair | No | Cleared bird from xmfr pole renew blown 3 amp fuse protecting 25/kva xmf at pole # 0107933 supply restored.
Outage | J.E.26.08.17276 | C001886530 | Christopher Edwards | KSAN | Completed | Load_244510 | Constant Spring - 410 | 2026-08-12 11:33 | 2026-08-12 11:34 | 2026-08-12 13:05 | 2026-08-12 13:06 | 2026-08-12 13:30 | 2026-08-12 14:02 | 2026-08-12 14:02 | 2026-08-12 14:02 |  |  | Fair | No | Remake dislodge neutral joint at pot head Using (1) one bolt clamps Voltage:112,113,226v
Outage | J.E.26.08.17137 | C001886531 | Moses Elliston | St.Catherine | Completed | Load_243531 | Tredegar - 310 | 2026-08-12 11:34 | 2026-08-12 11:38 | 2026-08-13 06:28 | 2026-08-13 06:29 | 2026-08-13 06:29 | 2026-08-12 20:20 | 2026-08-13 06:31 | 2026-08-13 06:31 |  |  | Rains | No | Credit added to prepaid account.
Outage | J.E.26.08.17220 | C001886540 | Kemark Slue | St.Catherine | Completed | Load_268971 | Tredegar - 210 | 2026-08-12 11:37 | 2026-08-12 11:39 | 2026-08-12 11:47 | 2026-08-12 12:26 | 2026-08-12 12:53 | 2026-08-12 13:00 | 2026-08-12 13:01 | 2026-08-12 13:01 |  |  | Rains | No | Upon arrival at the location the crew discovered that one side of three-wire meter bearing number 2863831 supply customer was burnt resulting from a defective meter socket which was already replaced upon arrival, replace defective meter with new three-wire meter bearing number 302357.
Outage | J.E.26.08.17209 | C001886541 | Kemark Slue | St.Catherine | Completed | Load_266657 | Tredegar - 210 | 2026-08-12 11:38 | 2026-08-12 11:39 | 2026-08-12 11:46 | 2026-08-12 11:47 | 2026-08-12 12:23 | 2026-08-12 12:24 | 2026-08-12 12:25 | 2026-08-12 12:25 |  |  | Rains | No | Upon arrival at the location the crew discovered that prepaid customer is unable to top up as CIU Box needs to be programmed please refer to Moses Elliston.
Outage | J.E.26.08.17293 | C001886547 | Javid Vernon | St.Elizabeth | Completed | Load_568701 | Maggotty - 110 | 2026-08-12 11:44 | 2026-08-12 11:46 | 2026-08-12 13:07 | 2026-08-12 13:11 | 2026-08-12 14:14 | 2026-08-12 14:24 | 2026-08-12 14:25 | 2026-08-12 14:25 |  |  | Fair | No | Area check and found Customer got disconnected for none payment
Outage | J.E.26.08.17303 | C001886548 | Daniel Lobar | Trelawny | Completed | Load_264372 | Greenwood - 110 | 2026-08-12 11:44 | 2026-08-12 11:45 | 2026-08-12 12:01 | 2026-08-12 12:02 | 2026-08-12 14:01 | 2026-08-12 15:12 | 2026-08-12 15:12 | 2026-08-12 15:12 |  |  | Fair | No | Replace 2/0 copper drop lead and clean and remake corroded joints on bank of 3 transformer system.
Outage | J.E.26.08.17100 | C001886550 | Marlon Authors | Manchester | Completed | Load_264159 | Spur Tree - 210 | 2026-08-12 11:45 | 2026-08-12 11:46 | 2026-08-12 12:51 | 2026-08-12 12:52 | 2026-08-12 12:51 | 2026-08-12 12:54 | 2026-08-12 12:55 | 2026-08-12 12:55 | Fire |  | Fair | No | Remaid drop lead at transformer lug supply leave working okay
Outage | J.E.26.08.17306 | C001886549 | Selvin White | St.Elizabeth | Completed | Load_244659 | Maggotty - 110 | 2026-08-12 11:45 | 2026-08-12 11:46 | 2026-08-12 13:19 | 2026-08-12 13:55 | 2026-08-12 14:46 | 2026-08-12 14:52 | 2026-08-12 14:52 | 2026-08-12 14:52 |  |  | Fair | No | Customer premises was found to be damaged and not in use. Customer says premises was damaged during the hurricane and is currently under construction.
Outage | J.E.26.08.17305 | C001886557 | Shawn Medley | St.James | Completed | Load_1001938 | Bogue - 310 | 2026-08-12 11:46 | 2026-08-12 11:47 | 2026-08-12 12:37 | 2026-08-12 12:38 | 2026-08-12 13:02 | 2026-08-12 01:00 | 2026-08-12 13:07 | 2026-08-12 13:07 |  |  | Fair | No | Unable to locate customer and premises; patrol revealed area has supply
Outage | J.E.26.08.17294 | C001886558 | Shawn Medley | St.James | Completed | Load_265224 | Bogue - 410 | 2026-08-12 11:47 | 2026-08-12 11:48 | 2026-08-12 13:22 | 2026-08-12 13:22 | 2026-08-12 13:35 | 2026-08-12 01:00 | 2026-08-12 13:36 | 2026-08-12 13:36 |  |  | Fair | No | Premises checked and found ok
Outage | J.E.26.08.17320 | C001886574 | Raheem Ricketts | Manchester | Completed | Load_239389 | Spur Tree - 210 | 2026-08-12 11:56 | 2026-08-12 15:58 | 2026-08-12 16:02 | 2026-08-12 16:22 | 2026-08-12 16:24 | 2026-08-12 16:25 | 2026-08-12 16:25 | 2026-08-12 16:25 |  |  | Fair | No | Check and found okay power has been restored
Non-Outage | J.E.26.08.17212 | C001886582 | Locksley Allen | St.Mary | Completed | Load_265841 | Oracabessa - 210 | 2026-08-12 12:00 | 2026-08-12 12:03 | 2026-08-12 12:08 | 2026-08-12 14:11 | 2026-08-12 14:11 | 2026-08-12 14:34 | 2026-08-12 14:31 | 2026-08-12 14:31 |  |  | Fair | No | Pothead found corroded. Change 1 clamp and clean up connectors.Voltage at meter socket phase to phase 238v. Phase to neutral 119&119vMeter left working okay
Non-Outage | J.E.26.08.16146 | C001886588 | Cliton Henry | St.Mary | Completed | Load_254261 | Blackstonedge - 110 | 2026-08-12 12:03 | 2026-08-12 12:04 | 2026-08-12 13:43 | 2026-08-12 13:43 | 2026-08-12 13:43 | 2026-08-12 14:04 | 2026-08-12 14:04 | 2026-08-12 14:04 | Fire |  | Fair | No | No fire seen along the roadway. The patrol revealed the primary and secondary conductors found sagging, poles leaning need to be straightened, kindly refer to St. Mary Operations for for maintenance.
Outage | J.E.26.08.17348 | C001886597 | Neckell Ormsby | St.Mary | Completed | Load_252211 | Highgate -110 | 2026-08-12 12:07 | 2026-08-12 12:08 | 2026-08-12 12:19 | 2026-08-12 12:20 | 2026-08-12 13:08 | 2026-08-12 14:13 | 2026-08-12 14:13 | 2026-08-12 14:13 |  |  | Fair | No | Found junction fuse blown at pole #535928 patrol and found transformer fuse blown no pole number seen clear vines from transformer pole with switch stick and replace 1-3amp and replace 1-30 amp at junction
Outage | J.E.26.08.17362 | C001886629 | Romeo Brissett | St.James | Completed | Load_242038 | Bogue - 610 | 2026-08-12 12:26 | 2026-08-12 12:27 | 2026-08-12 15:23 | 2026-08-12 15:23 | 2026-08-12 15:39 | 2026-08-12 17:00 | 2026-08-12 17:18 | 2026-08-12 17:18 |  |  | Fair | No | Found junction fuse and transformer fuse blown due to vegetation, cut and removed vegetation and replaced (1)8amps junction and (1)25KVA transformer fuse. V/R 112-114-227
Non-Outage | J.E.26.08.17418 | C001886663 | Fredrick Hamilton | KSAN | Completed | Load_267241 | Washington Blvd - 310 | 2026-08-12 12:47 | 2026-08-12 12:55 | 2026-08-12 13:08 | 2026-08-12 13:12 | 2026-08-12 13:15 | 2026-08-12 13:23 | 2026-08-12 13:23 | 2026-08-12 13:23 |  |  | Fair | No | Rami customer please assign to emergency low voltage affecting customer 205v/119v/50v obtained Pothead is okLow voltage happened after power cut stated by customer
Outage | J.E.26.08.17434 | C001886669 | Stephen Taylor | St.Thomas | Completed | Load_260882 | Good Year - 210 | 2026-08-12 12:55 | 2026-08-12 12:57 | 2026-08-12 14:32 | 2026-08-12 14:32 | 2026-08-12 14:35 | 2026-08-12 14:35 | 2026-08-12 14:36 | 2026-08-12 14:36 |  |  | Fair | No | Need more information a lot of call to customer no one answered the phone Patrol the area power is in the area
Outage | J.E.26.08.17435 | C001886675 | Wayne Dillion | St.Elizabeth | Completed | Load_265377 | Maggotty - 110 | 2026-08-12 13:01 | 2026-08-13 07:13 | 2026-08-13 11:26 | 2026-08-13 11:31 | 2026-08-13 11:30 | 2026-08-13 11:34 | 2026-08-13 11:35 | 2026-08-13 11:35 |  |  | Fair | No | Customer error. Customer wired house in 220 however customer has a 110 meter. Customer was advised to get an upgrade for 220 supply.
Outage | J.E.26.08.17461 | C001886680 | Edward Royal | KSAS | Completed | Load_250058 | Greenwich - 510 | 2026-08-12 13:07 | 2026-08-12 13:13 | 2026-08-12 14:39 | 2026-08-12 14:40 | 2026-08-12 15:07 | 2026-08-12 15:13 | 2026-08-12 15:14 | 2026-08-12 15:14 |  |  | Fair | No | Defective meter need to be change reffered to field service
Outage | J.E.26.08.17460 | C001886684 | Raheem Ricketts | St.Elizabeth | Completed | Load_242373 | Maggotty - 210 | 2026-08-12 13:15 | 2026-08-12 15:56 | 2026-08-12 16:02 | 2026-08-12 16:26 | 2026-08-12 16:25 | 2026-08-12 16:27 | 2026-08-12 16:33 | 2026-08-12 16:33 |  |  | Fair | No | Customer says she’s not home she will make back a report tomorrow
Outage | J.E.26.08.17452 | C001886697 | Denton Williams | Portland | Completed | Load_244571 | Port Antonio - 310 | 2026-08-12 13:32 | 2026-08-12 13:33 | 2026-08-12 14:03 | 2026-08-12 14:04 | 2026-08-12 14:35 | 2026-08-12 15:10 | 2026-08-12 15:13 | 2026-08-12 15:13 |  | Y | Fair | No | 10amps junction fuse found blown as a result of tree contact. Cut and clear two tree from line and replace 10amp junction fuse to restore power supply to area.
Outage | J.E.26.08.17209 | C001886708 | Moses Elliston | St.Catherine | Completed | Load_266657 | Tredegar - 210 | 2026-08-12 13:41 | 2026-08-12 13:44 | 2026-08-13 11:12 | 2026-08-13 11:12 | 2026-08-13 11:12 | 2026-08-13 11:12 | 2026-08-13 11:14 | 2026-08-13 11:14 |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.08.17366 | C001886709 | Hartley Chin | Clarendon | Completed | Load_245674 | Parnassus - 210 | 2026-08-12 13:43 | 2026-08-13 08:13 | 2026-08-13 11:47 | 2026-08-13 11:56 | 2026-08-13 11:56 | 2026-08-13 11:57 | 2026-08-13 11:57 | 2026-08-13 11:57 |  |  | Fair | No | Premisis found ok.
Outage | J.E.26.08.17378 | C001886710 | Neville Spencer | Clarendon | Completed | Load_260333 | Parnassus - 310 | 2026-08-12 13:43 | 2026-08-12 13:44 | 2026-08-12 18:00 | 2026-08-12 18:00 | 2026-08-12 18:04 | 2026-08-12 18:06 | 2026-08-12 18:06 | 2026-08-12 18:06 |  |  | Fair | No | Renew blown 40 amp j/ fuse at pole #. 115558 area restored.
Outage | J.E.26.08.17379 | C001886713 | Clyde Brown | Clarendon | Completed | Load_253286 | Parnassus - 310 | 2026-08-12 13:43 | 2026-08-13 18:03 | 2026-08-13 18:14 | 2026-08-13 18:15 | 2026-08-13 18:15 | 2026-08-13 18:15 | 2026-08-13 18:16 | 2026-08-13 18:16 |  |  | Fair | No | Prepaid account
Outage | J.E.26.08.17450 | C001886711 | Neville Spencer | Clarendon | Completed | Load_254698 | Parnassus - 310 | 2026-08-12 13:43 | 2026-08-12 13:44 | 2026-08-12 14:34 | 2026-08-12 14:34 | 2026-08-12 15:46 | 2026-08-12 15:46 | 2026-08-12 16:00 | 2026-08-12 16:00 |  |  | Fair | No | Renew blown 15 amp j/ fuse area restored.
Outage | J.E.26.08.17497 | C001886712 | Neville Spencer | Clarendon | Completed | Load_261659 | Parnassus - 310 | 2026-08-12 13:43 | 2026-08-12 13:44 | 2026-08-12 16:02 | 2026-08-12 16:03 | 2026-08-12 16:28 | 2026-08-12 16:28 | 2026-08-12 17:09 | 2026-08-12 17:09 |  |  | Rains | No | Renew blown 20 amp j/ fuse .Also renew blown 3 amp fuse protecting 25 kva xmfr at pole # 0125585 area restored.
Outage | J.E.26.08.17508 | C001886735 | Ryan Richards | Manchester | Completed | Load_238945 | Spur Tree - 310 | 2026-08-12 13:58 | 2026-08-12 13:59 | 2026-08-12 14:18 | 2026-08-12 14:19 | 2026-08-12 15:59 | 2026-08-13 06:36 | 2026-08-13 06:36 | 2026-08-13 06:36 | BrokenWire |  | Fair | No | Blown 2 amp fuse found for 10 kva transformer line patrol 2. Span of broken secondary phase an neural found cause by truck splice and retention using 50ft#2 aluminum 4 one bolt clamps and reclose fuse area area are now with supply
Non-Outage | J.E.26.08.14431 | C001886745 | Raymond Lewis |  | Completed |  |  | 2026-08-12 14:05 | 2026-08-12 14:06 | 2026-08-12 19:32 | 2026-08-12 19:32 | 2026-08-12 20:12 | 2026-08-12 20:16 | 2026-08-12 20:16 | 2026-08-12 20:16 | BrokenWire |  | Fair | No | Cut and remove tree from line and spray and retention number 2 secondary service wire
Outage | J.E.26.08.17588 | C001886760 | Milton Charlton | KSAN | Completed | Load_249713 | Washington Blvd - 410 | 2026-08-12 14:25 | 2026-08-12 14:28 | 2026-08-12 14:37 | 2026-08-12 14:37 | 2026-08-12 15:09 | 2026-08-12 14:55 | 2026-08-12 15:13 | 2026-08-12 15:13 |  |  | Rains | No | Customer service wire #6 triplex disconnected at pothead, meter socket cover off and no meter was seen at the premises. Refer to field service.
Outage | J.E.26.08.17592 | C001886769 | Andre Williams | Trelawny | Completed | Load_292567 | Duncans - 210 | 2026-08-12 14:31 | 2026-08-12 15:18 | 2026-08-12 17:26 | 2026-08-12 17:32 | 2026-08-12 18:36 | 2026-08-12 19:28 | 2026-08-12 19:29 | 2026-08-12 19:29 | Fire |  | Fair | No | Open 25 kva transformer splice and retention 3 span broken neutral, area now ok
Non-Outage | J.E.26.08.16842 | C001886771 | Javid Vernon | Westmoreland | Completed | Load_254289 | Paradise - 210 | 2026-08-12 14:33 | 2026-08-12 14:34 | 2026-08-12 17:38 | 2026-08-12 19:26 | 2026-08-12 19:29 | 2026-08-12 19:31 | 2026-08-12 19:32 | 2026-08-12 19:32 |  |  | Fair | No | Premises check and found okay voltage left at premises 230/255/235/419/399/435
Non-Outage | J.E.26.08.17564 | C001886772 | Javid Vernon | Westmoreland | Completed | Load_244663 | Paradise - 110 | 2026-08-12 14:34 | 2026-08-12 14:34 | 2026-08-12 14:53 | 2026-08-12 14:53 | 2026-08-12 15:44 | 2026-08-12 16:00 | 2026-08-12 16:00 | 2026-08-12 16:00 |  |  | Fair | No | Premises check and found okay voltage reading left at premises 228/237/230/400/408/397
Non-Outage | J.E.26.08.17341 | C001886809 | Javid Vernon |  | Completed |  |  | 2026-08-12 14:57 | 2026-08-12 19:37 | 2026-08-12 21:35 | 2026-08-12 21:36 | 2026-08-12 21:57 | 2026-08-12 22:15 | 2026-08-12 22:15 | 2026-08-12 22:15 |  |  | Fair | No | Check and found customer premises closed meter and stancion on the premises unable to access customer pothead voltage found on JPS pole 110/108/218 customer stated he will not be there until tomorrow
Outage | J.E.26.08.17524 | C001886808 | Javid Vernon | Westmoreland | Completed | Load_259745 | Paradise - 210 | 2026-08-12 14:57 | 2026-08-12 14:58 | 2026-08-12 16:01 | 2026-08-12 16:01 | 2026-08-12 17:03 | 2026-08-12 17:38 | 2026-08-12 17:38 | 2026-08-12 17:38 |  |  | Fair | No | Reconnect customer service wire use two clamps voltage reading 115/117/232
Outage | J.E.26.08.17525 | C001886810 | Richman Whyte | Westmoreland | Completed | Load_264630 | Paradise - 310 | 2026-08-12 14:58 | 2026-08-12 15:27 | 2026-08-12 18:03 | 2026-08-12 18:03 | 2026-08-12 18:03 | 2026-08-12 19:36 | 2026-08-12 19:36 | 2026-08-12 19:36 |  |  | Fair | No | Customer has internal problem advice to fix
Outage | J.E.26.08.17510 | C001886811 | Richard Samuda | Manchester | Completed | Load_302216 | Spur Tree - 310 | 2026-08-12 15:00 | 2026-08-12 19:35 | 2026-08-12 20:23 | 2026-08-12 20:34 | 2026-08-12 20:50 | 2026-08-12 21:29 | 2026-08-12 21:29 | 2026-08-12 21:29 |  |  | Fair | No | Remake joint at customer that was corroded causing customer have no voltage using one 1bolt clamp pothead voltage: 114
Outage | J.E.26.08.17550 | C001886816 | Richard Samuda | Manchester | Completed | Load_263434 | Kendal - 210 | 2026-08-12 15:00 | 2026-08-12 15:01 | 2026-08-12 15:55 | 2026-08-12 15:55 | 2026-08-12 16:41 | 2026-08-12 17:09 | 2026-08-12 17:10 | 2026-08-12 17:10 |  |  | Fair | No | Found ok Customer has a damaged meter socket advised customer to repair meter socket voltage 114
Outage | J.E.26.08.17573 | C001886812 | Richard Samuda | Manchester | Completed | Load_245621 | Kendal - 310 | 2026-08-12 15:00 | 2026-08-12 15:01 | 2026-08-12 15:13 | 2026-08-12 15:13 | 2026-08-12 15:54 | 2026-08-12 03:54 | 2026-08-12 15:55 | 2026-08-12 15:55 |  |  | Fair | No | Call to phone no answer premises not located
Outage | J.E.26.08.17502 | C001886825 | Richard Samuda | Manchester | Completed | Load_1002483 | Kendal - 210 | 2026-08-12 15:02 | 2026-08-12 18:00 | 2026-08-12 18:23 | 2026-08-12 18:23 | 2026-08-12 19:00 | 2026-08-12 19:01 | 2026-08-12 19:01 | 2026-08-12 19:01 |  |  | Fair | No | Refer call to field service customer has a damaged meter voltage: 118,118 236
Outage | J.E.26.08.17112 | C001886857 | Fitzroy Turner | KSAS | Completed | Load_269025 | Hunts Bay - 210 | 2026-08-12 15:12 | 2026-08-12 15:15 | 2026-08-12 17:11 | 2026-08-12 17:12 | 2026-08-12 17:11 | 2026-08-12 17:12 | 2026-08-12 17:13 | 2026-08-12 17:13 |  |  | Rains | No | Found tree phase primary switches top burnt off.use one hot line clamps to carry out repair supply restored to areas
Outage | J.E.26.08.17327 | C001886860 | Elvis Trowers | KSAN | Completed | Load_269184 | Constant Spring - 410 | 2026-08-12 15:14 | 2026-08-12 15:15 | 2026-08-12 16:23 | 2026-08-12 16:24 | 2026-08-12 16:46 | 2026-08-12 16:50 | 2026-08-12 16:48 | 2026-08-12 16:48 |  |  | Fair | No | Found okay
Outage | J.E.26.08.17330 | C001886859 | Elvis Trowers | KSAN | Completed | Load_251989 | Constant Spring - 410 | 2026-08-12 15:14 | 2026-08-12 15:15 | 2026-08-12 20:59 | 2026-08-12 20:59 | 2026-08-12 21:39 | 2026-08-12 21:30 | 2026-08-12 21:40 | 2026-08-12 21:40 |  |  | Fair | No | Found okay upon arrival.
Outage | J.E.26.08.17331 | C001886858 | Elvis Trowers | KSAN | Completed | Load_251430 | Constant Spring - 410 | 2026-08-12 15:14 | 2026-08-12 15:15 | 2026-08-12 22:00 | 2026-08-12 22:00 | 2026-08-12 22:21 | 2026-08-12 22:25 | 2026-08-12 22:22 | 2026-08-12 22:22 |  |  | Fair | No | Found okay .
Outage | J.E.26.08.17604 | C001886868 | Marlon Brown | Trelawny | Completed | Load_254738 | Greenwood - 110 | 2026-08-12 15:16 | 2026-08-13 11:12 | 2026-08-13 11:19 | 2026-08-13 11:20 | 2026-08-13 11:55 | 2026-08-13 12:28 | 2026-08-13 12:28 | 2026-08-13 12:28 |  |  | Fair | No | Check and found ok Voltage found at meter socket 118/119=237vVoltage leaving at meter socket 118/119=237v Joints @ pothead were cleaned and remade. Internal issues, customer advised to have electrician resolved issues.
Outage | J.E.26.08.17622 | C001886869 | Neville Spencer | Clarendon | Completed | Load_406147 | Parnassus - 310 | 2026-08-12 15:18 | 2026-08-12 15:30 | 2026-08-12 17:10 | 2026-08-12 17:11 | 2026-08-12 17:12 | 2026-08-12 17:12 | 2026-08-12 17:13 | 2026-08-12 17:13 |  |  | Rains | No | Renew blown 20 amp J/ fuse supply restored.
Non-Outage | J.E.26.08.17346 | C001886871 | Evan Spaulding |  | Completed |  |  | 2026-08-12 15:19 | 2026-08-12 15:24 | 2026-08-12 19:17 | 2026-08-12 19:18 | 2026-08-12 19:28 | 2026-08-12 19:35 | 2026-08-12 19:36 | 2026-08-12 19:36 |  |  | Fair | No | Burnt meter jaw ,refer to field service to have meter change.
Outage | J.E.26.08.17455 | C001886870 | Evan Spaulding | St.Mary | Completed | Load_255504 | Highgate - 210 | 2026-08-12 15:19 | 2026-08-12 15:24 | 2026-08-12 16:35 | 2026-08-12 16:35 | 2026-08-12 17:08 | 2026-08-12 17:23 | 2026-08-12 17:24 | 2026-08-12 17:24 |  |  | Fair | No | Patrol line section no fault seen,replace 1-20amps junction fuse at pole number 0010997.
Outage | J.E.26.08.17283 | C001886883 | Raymond Lewis | St.Ann | Completed | Load_252938 | Roaring River - 210 | 2026-08-12 15:23 | 2026-08-12 15:24 | 2026-08-12 16:56 | 2026-08-12 16:57 | 2026-08-12 16:57 | 2026-08-12 16:58 | 2026-08-12 16:59 | 2026-08-12 16:59 |  |  | Fair | No | Remade joints at pole 3 wire service
Non-Outage | J.E.26.08.17314 | C001886887 | Omar King | St.Ann | Completed | Load_261488 | Cardiff Hall - 310 | 2026-08-12 15:24 | 2026-08-12 15:26 | 2026-08-12 19:09 | 2026-08-12 19:10 | 2026-08-12 20:35 | 2026-08-12 20:34 | 2026-08-12 20:37 | 2026-08-12 20:37 | BrokenWire |  | Fair | No | Found secondary conductor broken two span as been repaired customer is now with supply
Non-Outage | J.E.26.08.17702 | C001886886 | Barrington Brown |  | Completed |  |  | 2026-08-12 15:24 | 2026-08-12 15:26 | 2026-08-12 17:44 | 2026-08-12 17:44 | 2026-08-12 18:33 | 2026-08-12 20:28 | 2026-08-12 20:28 | 2026-08-12 20:28 |  |  | Fair | No | Crew found defective service wire on location crew used 100ft of #6 triplex 6 one bolt clamps to make repairs. Customer supply now fully restored. Voltage found 126 102 228 left 115 116 232 However there is a 30ft secondary pole on location rotten and falling on customer premises. Please refer to maintenance department to have pole changed.
Outage | J.E.26.08.17511 | C001886885 | Barrington Brown | St.James | Completed | Load_253123 | Queens Drive - 710 | 2026-08-12 15:24 | 2026-08-12 15:26 | 2026-08-12 20:28 | 2026-08-12 20:28 | 2026-08-12 21:59 | 2026-08-12 22:00 | 2026-08-12 22:00 | 2026-08-12 22:00 |  |  | Fair | No | Checked and found ok
Outage | J.E.26.08.17596 | C001886884 | Barrington Brown | St.James | Completed | Load_254331 | Queens Drive - 310 | 2026-08-12 15:24 | 2026-08-12 15:26 | 2026-08-12 15:37 | 2026-08-12 15:38 | 2026-08-12 17:15 | 2026-08-12 17:41 | 2026-08-12 17:41 | 2026-08-12 17:41 |  |  | Fair | No | Crew found defective 10 kva EG transformer on location. Please refer to st James field service department and maintenance department to have transformer changed. Customer has been out since yesterday.
Non-Outage | J.E.26.08.15585 | C001886890 | Omar King |  | Completed |  |  | 2026-08-12 15:25 | 2026-08-12 15:26 | 2026-08-12 20:37 | 2026-08-12 20:38 | 2026-08-12 22:04 | 2026-08-12 22:47 | 2026-08-12 22:47 | 2026-08-12 22:47 | BrokenWire |  | Fair | No | Found three (3) span of secondary phase and neutral broken as been repaired customer is now with supply
Outage | J.E.26.08.15590 | C001886891 | Fitzroy Turner | KSAS | Completed | Load_258334 | Rockfort - 410 | 2026-08-12 15:25 | 2026-08-12 15:27 | 2026-08-12 20:44 | 2026-08-12 20:45 | 2026-08-12 21:30 | 2026-08-12 21:33 | 2026-08-12 21:34 | 2026-08-12 21:34 |  |  | Fair | No | Customer premises close at this time
Outage | J.E.26.08.17027 | C001886889 | Fitzroy Turner | KSAS | Completed | Load_266562 | Hunts Bay - 310 | 2026-08-12 15:25 | 2026-08-12 15:27 | 2026-08-12 18:38 | 2026-08-12 18:38 | 2026-08-12 19:13 | 2026-08-12 19:41 | 2026-08-12 19:43 | 2026-08-12 19:43 | BrokenWire |  | Rains | No | Found 2/0 triplex burnt up need about 100ft of 2/0 triplex to replace defective wire
Outage | J.E.26.08.17490 | C001886899 | Clyde Brown | Clarendon | Completed | Load_247364 | May Pen - 110 | 2026-08-12 15:25 | 2026-08-12 15:31 | 2026-08-13 08:38 | 2026-08-13 08:38 | 2026-08-13 10:13 | 2026-08-13 10:24 | 2026-08-13 10:28 | 2026-08-13 10:28 |  |  | Fair | No | Blown 3 amps fuse for 25 kva transformer,line patrolled and no fault seen,blown fuse replaced.
Outage | J.E.26.08.17598 | C001886896 | Fitzroy Turner | KSAS | Completed | Load_267604 | Rockfort - 410 | 2026-08-12 15:25 | 2026-08-12 15:27 | 2026-08-12 19:44 | 2026-08-12 19:45 | 2026-08-12 19:56 | 2026-08-12 20:15 | 2026-08-12 20:20 | 2026-08-12 20:20 |  |  | Rains | No | Found 2. 15 amps junction fuse blown at the intersection of paradise st and Rae st cause kites replaced too 15amp and too 10amps supply restored to the area
Outage | J.E.26.08.17617 | C001886897 | Fitzroy Turner | KSAS | Completed | Load_241156 | Rockfort - 410 | 2026-08-12 15:25 | 2026-08-12 15:27 | 2026-08-12 20:20 | 2026-08-12 20:20 | 2026-08-12 20:30 | 2026-08-12 20:34 | 2026-08-12 20:36 | 2026-08-12 20:36 |  |  | Fair | No | Found two 10amps fuses blown cause by kite replaced two 10amps fuses supply restored to the areas
Outage | J.E.26.08.17625 | C001886900 | Edward Royal | KSAS | Completed | Load_1003091 | Hunts Bay - 310 | 2026-08-12 15:25 | 2026-08-12 15:30 | 2026-08-13 11:54 | 2026-08-13 11:54 | 2026-08-13 11:54 | 2026-08-13 11:54 | 2026-08-13 11:54 | 2026-08-13 11:54 | Fire |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.17692 | C001886901 | Edward Royal | KSAS | Completed | Load_259189 | Rockfort - 410 | 2026-08-12 15:25 | 2026-08-12 15:30 | 2026-08-13 08:56 | 2026-08-13 08:56 | 2026-08-13 08:56 | 2026-08-13 08:57 | 2026-08-13 08:57 | 2026-08-13 08:57 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.17475 | C001886903 | Shamour Haughton | St.James | Completed | Load_573468 | Bogue - 310 | 2026-08-12 15:26 | 2026-08-12 15:27 | 2026-08-12 15:38 | 2026-08-12 15:39 | 2026-08-12 16:11 | 2026-08-12 16:35 | 2026-08-12 16:38 | 2026-08-12 16:38 | LowHangingWires |  | Fair | No | Retention customer service wire at pothead
Non-Outage | J.E.26.08.16511 | C001886904 | Evan Spaulding |  | Completed |  |  | 2026-08-12 15:27 | 2026-08-12 17:42 | 2026-08-12 20:59 | 2026-08-12 21:00 | 2026-08-12 20:59 | 2026-08-12 21:00 | 2026-08-12 21:00 | 2026-08-12 21:00 |  |  | Fair | No | Premises found lock.
Outage | J.E.26.08.17649 | C001886905 | Edward Royal | KSAS | Completed | Load_262511 | Three Miles - 410 | 2026-08-12 15:27 | 2026-08-12 15:29 | 2026-08-12 17:47 | 2026-08-12 17:47 | 2026-08-12 17:47 | 2026-08-12 18:15 | 2026-08-12 18:17 | 2026-08-12 18:17 |  |  | Fair | No | Replaced 3 junction fuse 65A 30A pole #0108191
Outage | J.E.26.08.17677 | C001886906 | Edward Royal | KSAN | Completed | Load_567705 | Washington Blvd - 310 | 2026-08-12 15:27 | 2026-08-12 15:29 | 2026-08-12 18:21 | 2026-08-12 18:21 | 2026-08-12 18:35 | 2026-08-12 18:41 | 2026-08-12 18:43 | 2026-08-12 18:43 |  |  | Fair | No | Replaced 10A junction fuse
Outage | J.E.26.08.17725 | C001886908 | Edward Royal | KSAS | Completed | Load_406024 | Three Miles - 410 | 2026-08-12 15:27 | 2026-08-12 15:29 | 2026-08-12 18:18 | 2026-08-12 18:19 | 2026-08-12 18:19 | 2026-08-12 18:20 | 2026-08-12 18:20 | 2026-08-12 18:20 |  |  | Fair | No | Premises found ok related to outage
Non-Outage | J.E.26.08.04967 | C001886911 | Raymond Lewis | St.Ann | Completed | Load_256645 | Ocho Rios - 310 | 2026-08-12 15:28 | 2026-08-12 15:30 | 2026-08-12 18:15 | 2026-08-12 18:15 | 2026-08-12 18:56 | 2026-08-12 19:21 | 2026-08-12 19:21 | 2026-08-12 19:21 |  |  | Fair | No | Remade joints at pole 3 wire service
Outage | J.E.26.08.17644 | C001886910 | Dwayne Cohen | KSAN | Completed | Load_255286 | Constant Spring - 210 | 2026-08-12 15:28 | 2026-08-12 15:29 | 2026-08-12 16:46 | 2026-08-12 16:48 | 2026-08-12 18:13 | 2026-08-12 18:14 | 2026-08-12 18:14 | 2026-08-12 18:14 |  |  | Fair | No | Premises not found, multiple calls to customer went unanswered.
Outage | J.E.26.08.17647 | C001886909 | Dwayne Cohen | KSAN | Completed | Load_256019 | Washington Blvd - 610 | 2026-08-12 15:28 | 2026-08-12 15:29 | 2026-08-12 15:53 | 2026-08-12 15:53 | 2026-08-12 16:25 | 2026-08-12 16:45 | 2026-08-12 16:46 | 2026-08-12 16:46 |  |  | Rains | No | Refuse 40amps junction by pole#556475, supply now restore.
Outage | J.E.26.08.17736 | C001886912 | Raymond Lewis | St.Ann | Completed | Load_264401 | Roaring River - 410 | 2026-08-12 15:30 | 2026-08-12 15:31 | 2026-08-12 17:00 | 2026-08-12 17:00 | 2026-08-12 18:13 | 2026-08-12 18:14 | 2026-08-12 18:14 | 2026-08-12 18:14 |  |  | Fair | No | Supply restored
Outage | J.E.26.08.17535 | C001886920 | Richman Whyte | St.Elizabeth | Completed | Load_557832 | Maggotty - 110 | 2026-08-12 15:34 | 2026-08-12 16:15 | 2026-08-12 22:27 | 2026-08-12 22:28 | 2026-08-12 22:28 | 2026-08-12 22:30 | 2026-08-12 22:31 | 2026-08-12 22:31 |  |  | Fair | No | Need daylight attention
Outage | J.E.26.08.17581 | C001886919 | Richard Watson | St.Elizabeth | Completed | Load_264057 | Maggotty - 110 | 2026-08-12 15:34 | 2026-08-12 15:37 | 2026-08-12 16:17 | 2026-08-12 16:18 | 2026-08-12 16:28 | 2026-08-12 16:35 | 2026-08-12 16:40 | 2026-08-12 16:40 |  |  | Rains | No | Reset trip 25kva transformer no pole#, after completing patrol no visible fault found, suspected cause lightning, supply restored to area.
Outage | J.E.26.08.17713 | C001886922 | Richard Watson | St.Elizabeth | Completed | Load_255506 | Maggotty - 210 | 2026-08-12 15:34 | 2026-08-12 15:38 | 2026-08-12 16:47 | 2026-08-12 16:48 | 2026-08-12 17:13 | 2026-08-12 17:55 | 2026-08-12 18:04 | 2026-08-12 18:04 |  |  | Fair | No | Replace blown 20amp junction fuse no pole#, also found blown 1amp fuse for 10kva transformer no pole#, check and found 10kva transformer to be defective and leaking oil from secondary bushings, please refer to Mr Delroy Crew for replacement, approximately 9 customers are affected.
Outage | J.E.26.08.17720 | C001886921 | Richard Watson | St.Elizabeth | Completed | Load_251505 | Maggotty - 110 | 2026-08-12 15:34 | 2026-08-12 15:38 | 2026-08-12 19:29 | 2026-08-12 19:30 | 2026-08-12 20:06 | 2026-08-12 20:11 | 2026-08-12 20:11 | 2026-08-12 20:11 |  |  | Rains | No | Customer is without supply since the passage of hurricane Melissa, please refer to field service department for reconnection.
Outage | J.E.26.08.17465 | C001886924 | Richard Watson | St.Elizabeth | Completed | Load_265227 | Maggotty - 110 | 2026-08-12 15:35 | 2026-08-12 15:36 | 2026-08-12 18:22 | 2026-08-12 18:23 | 2026-08-12 18:44 | 2026-08-12 18:56 | 2026-08-12 19:00 | 2026-08-12 19:00 |  |  | Rains | No | Replace blown 2amp fuse for 25kva transformer no pole#, after completing patrol, suspected cause lightning, supply restored to area.
Outage | J.E.26.08.17135 | C001886933 | Derrick Grubb | St.Thomas | Completed | Load_258020 | Good Year - 110 | 2026-08-12 15:36 | 2026-08-12 15:40 | 2026-08-12 17:49 | 2026-08-12 17:49 | 2026-08-12 20:29 | 2026-08-12 21:21 | 2026-08-12 21:23 | 2026-08-12 21:23 |  |  | Fair | No | Change drop out switch and close 25 kva transformer at pole number 0004312
Outage | J.E.26.08.17246 | C001886934 | Derrick Grubb | St.Thomas | Completed | Load_250144 | Good Year - 110 | 2026-08-12 15:36 | 2026-08-12 15:40 | 2026-08-12 21:56 | 2026-08-12 21:57 | 2026-08-12 22:56 | 2026-08-12 22:56 | 2026-08-12 22:56 | 2026-08-12 22:56 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.17429 | C001886938 | Derrick Grubb | St.Thomas | Completed | Load_244001 | Good Year - 110 | 2026-08-12 15:36 | 2026-08-12 15:40 | 2026-08-12 16:06 | 2026-08-12 16:07 | 2026-08-12 17:41 | 2026-08-12 17:45 | 2026-08-12 17:45 | 2026-08-12 17:45 |  |  | Fair | No | Customer meter isolated due to faulty service wire beyond the meter center
Outage | J.E.26.08.17642 | C001886937 | Derrick Grubb | St.Thomas | Completed | Load_244001 | Good Year - 110 | 2026-08-12 15:36 | 2026-08-12 15:40 | 2026-08-12 17:45 | 2026-08-12 17:46 | 2026-08-12 17:45 | 2026-08-12 17:46 | 2026-08-12 17:49 | 2026-08-12 17:49 |  |  | Fair | No | Clear fault at pothead by isolating another customer , multiple customers being supplied by one service wire
Outage | J.E.26.08.17676 | C001886936 | Derrick Grubb | St.Thomas | Completed | Load_250144 | Good Year - 110 | 2026-08-12 15:36 | 2026-08-12 15:40 | 2026-08-12 21:23 | 2026-08-12 21:24 | 2026-08-12 21:55 | 2026-08-12 21:55 | 2026-08-12 21:56 | 2026-08-12 21:56 | BrokenWire |  | Fair | No | Premises found ok
Outage | J.E.26.08.17748 | C001886935 | Richard Watson | St.Elizabeth | Completed | Load_292913 | Maggotty - 210 | 2026-08-12 15:36 | 2026-08-12 15:36 | 2026-08-12 18:10 | 2026-08-12 18:11 | 2026-08-12 18:17 | 2026-08-12 18:22 | 2026-08-12 18:22 | 2026-08-12 18:22 |  |  | Rains | No | Replace blown 20amp junction fuse, after completing patrol no visible fault found, suspected cause lightning, supply restored to area.
Outage | J.E.26.08.17758 | C001886946 | Andre Williams | Trelawny | Completed | Load_294254 | Duncans - 110 | 2026-08-12 15:40 | 2026-08-12 15:41 | 2026-08-12 19:36 | 2026-08-12 19:37 | 2026-08-12 20:54 | 2026-08-12 20:55 | 2026-08-12 20:55 | 2026-08-12 20:55 |  |  | Fair | No | Customer reconnected with the help of meter center, premises now with supply
Outage | J.E.26.08.17559 | C001886947 | Lancelot Brown | Hanover | Completed | Load_240939 | Orange Bay - 210 | 2026-08-12 15:42 | 2026-08-12 15:42 | 2026-08-12 15:55 | 2026-08-12 16:36 | 2026-08-12 17:44 | 2026-08-12 18:05 | 2026-08-12 18:05 | 2026-08-12 18:05 |  |  | Fair | No | Customer meter diffective need to replace contact customer care was trying to reconnect meter,meter is not reconnecting bridge meter socket supply restore replace meter please pass on to field service department in westmoreland customer need supply on premises need ergent attention
Outage | J.E.26.08.17723 | C001886948 | Evan Spaulding | St.Mary | Completed | Load_249551 | Annotto Bay - 310 | 2026-08-12 15:42 | 2026-08-12 15:44 | 2026-08-12 17:24 | 2026-08-12 17:24 | 2026-08-12 17:57 | 2026-08-12 18:20 | 2026-08-12 18:21 | 2026-08-12 18:21 |  |  | Fair | No | Replace 1-7 amps junction,no pole number.
Outage | J.E.26.08.17503 | C001886955 | Neville Spencer | St.Catherine | Completed | Load_294448 | Rhodens Pen - 310 | 2026-08-12 15:45 | 2026-08-12 15:56 | 2026-08-12 19:40 | 2026-08-12 19:41 | 2026-08-12 19:44 | 2026-08-12 19:44 | 2026-08-12 19:45 | 2026-08-12 19:45 |  |  | Fair | No | Found ok.
Outage | J.E.26.08.17562 | C001886954 | Neville Spencer | St.Catherine | Completed | Load_248929 | Rhodens Pen - 310 | 2026-08-12 15:45 | 2026-08-12 15:56 | 2026-08-12 18:35 | 2026-08-12 18:36 | 2026-08-12 19:17 | 2026-08-12 19:17 | 2026-08-12 19:37 | 2026-08-12 19:37 |  |  | Fair | No | Renew blown 8 amp j/ fuse. Also renew blown 5 amp fuse protecting 50 kva xmfr at pole #+0113112 area restored.
Outage | J.E.26.08.17496 | C001886959 | Christopher West | St.Catherine | Completed | Load_250392 | Tredegar - 310 | 2026-08-12 15:47 | 2026-08-12 15:55 | 2026-08-12 17:30 | 2026-08-12 17:31 | 2026-08-12 17:55 | 2026-08-12 21:00 | 2026-08-12 21:08 | 2026-08-12 21:08 | BrokenPole |  | Fair | No | Old pole at customer’s gate to be retired fell on said gate causing some damage, pole was removed and placed on ground and arrangements have been made to remove pole from location.
Outage | J.E.26.08.17681 | C001886957 | Moses Elliston |  | Completed | Load_247481 | Tredegar - 210 | 2026-08-12 15:47 | 2026-08-13 07:28 | 2026-08-13 10:39 | 2026-08-13 10:40 | 2026-08-13 10:39 | 2026-08-13 10:40 | 2026-08-13 10:43 | 2026-08-13 10:43 |  |  | Fair | No | Credit added to prepaid account
Outage | J.E.26.08.17768 | C001886956 | Delano Gayle | St.Catherine | Completed | Load_248418 | Tredegar - 310 | 2026-08-12 15:47 | 2026-08-13 | 2026-08-13 00:04 | 2026-08-13 00:05 | 2026-08-13 01:27 | 2026-08-13 01:54 | 2026-08-13 01:54 | 2026-08-13 01:54 |  |  | Fair | No | Blown junction on main no pole number, patrolled line section and found okay for closure replace 15amps
Outage | J.E.26.08.17227 | C001886962 | Christopher West | St.Catherine | Completed | Load_266057 | Tredegar - 310 | 2026-08-12 15:48 | 2026-08-12 15:55 | 2026-08-12 17:22 | 2026-08-12 17:23 | 2026-08-12 17:24 | 2026-08-12 17:25 | 2026-08-12 17:30 | 2026-08-12 17:30 |  |  | Fair | No | Found ok.
Outage | J.E.26.08.17411 | C001886961 | Delano Gayle | St.Catherine | Completed | Load_259602 | Tredegar - 210 | 2026-08-12 15:48 | 2026-08-13 00:03 | 2026-08-13 01:59 | 2026-08-13 01:59 | 2026-08-13 02:18 | 2026-08-13 02:27 | 2026-08-13 02:27 | 2026-08-13 02:27 |  |  | Fair | No | Blown 50kva transformer fuse no pole number patrolled and found okay for closure replace 5amps
Outage | J.E.26.08.17776 | C001886960 | Fitzroy Turner | KSAS | Completed | Load_256024 | Hunts Bay - 210 | 2026-08-12 15:48 | 2026-08-12 15:49 | 2026-08-12 17:13 | 2026-08-12 17:14 | 2026-08-12 18:14 | 2026-08-12 18:14 | 2026-08-12 18:37 | 2026-08-12 18:37 |  |  | Fair | No | Found underground cables burnt off cables need to rreterminate please send email to peart to carry out repair
Non-Outage | J.E.26.08.17416 | C001886963 | Richard Nicholas |  | Completed |  |  | 2026-08-12 15:49 | 2026-08-12 17:25 | 2026-08-12 19:14 | 2026-08-12 19:14 | 2026-08-12 19:14 | 2026-08-12 20:20 | 2026-08-12 20:23 | 2026-08-12 20:23 |  |  | Fair | No | Remade burnt off secondary jumper and splice broken system neutral at mid span.4ft of #2 insulated,1ft of #4 bare copper and 4 clamp.voltage reading 120x2 and 240v.
Outage | J.E.26.08.17132 | C001886964 | Christopher West | St.Catherine | Completed | Load_237888 | Tredegar - 310 | 2026-08-12 15:49 | 2026-08-12 15:59 | 2026-08-12 16:20 | 2026-08-12 16:21 | 2026-08-12 17:21 | 2026-08-12 17:22 | 2026-08-12 17:22 | 2026-08-12 17:22 |  |  | Fair | No | Premises found ok.
Outage | J.E.26.08.16372 | C001886978 | Hartley Chin | St.Catherine | Completed | Load_260335 | Rhodens Pen - 310 | 2026-08-12 15:50 | 2026-08-13 15:58 | 2026-08-13 17:39 | 2026-08-13 17:51 | 2026-08-13 17:51 | 2026-08-13 17:52 | 2026-08-13 17:53 | 2026-08-13 17:53 |  |  | Fair | No | Premisis found ok.
Non-Outage | J.E.26.08.17208 | C001886994 | Radcliffe Coleman | Portmore | Completed | Load_576114 | Naggo Head - 510 | 2026-08-12 16:03 | 2026-08-12 16:04 | 2026-08-12 20:31 | 2026-08-12 20:35 | 2026-08-12 22:05 | 2026-08-12 22:09 | 2026-08-12 22:09 | 2026-08-12 22:09 |  |  | Fair | No | Premises found okay at the time of visit.
Outage | J.E.26.08.17700 | C001886997 | Radcliffe Coleman | KSAS | Completed | Load_294474 | Duhaney - 210 | 2026-08-12 16:04 | 2026-08-12 16:08 | 2026-08-12 16:37 | 2026-08-12 16:37 | 2026-08-12 18:13 | 2026-08-12 20:24 | 2026-08-12 20:26 | 2026-08-12 20:26 |  |  | Rains | No | Area found with two blown junction fuse (50A) and a dislodge switch. This was a result of lightning. Isolation was done at pole 0041049 before repairs were done. The same value fuse found was replaced, area now back to normal.
Outage | J.E.26.08.17763 | C001886995 | Radcliffe Coleman | KSAS | Completed | Load_302333 | Duhaney - 210 | 2026-08-12 16:04 | 2026-08-12 16:08 | 2026-08-12 19:42 | 2026-08-12 20:30 | 2026-08-12 20:31 | 2026-08-12 20:34 | 2026-08-12 20:35 | 2026-08-12 20:35 |  |  | Fair | No | Area found with two blown junction fuse (2-65A), line section was patrolled and no visible fault found. The same value fuse found were replaced, are left okay.
Outage | J.E.26.08.17798 | C001886998 | Radcliffe Coleman | KSAS | Completed | Load_305364 | Duhaney - 210 | 2026-08-12 16:04 | 2026-08-12 16:08 | 2026-08-12 19:34 | 2026-08-12 20:27 | 2026-08-12 20:26 | 2026-08-12 20:28 | 2026-08-12 20:28 | 2026-08-12 20:28 |  |  | Fair | No | Area found with two blown junction fuse (50A) and a dislodge switch. This was a result of lightning. Isolation was done at pole 0041049 before repairs were done. The same value fuse found was replaced, area now back to normal.
Outage | J.E.26.08.17506 | C001887006 | Rodclif Dawkins | Portmore | Completed | Load_574021 | Naggo Head - 510 | 2026-08-12 16:05 | 2026-08-13 08:20 | 2026-08-13 11:59 | 2026-08-13 12:00 | 2026-08-13 12:00 | 2026-08-13 12:00 | 2026-08-13 12:01 | 2026-08-13 12:01 |  |  | Fair | No | Customer found okay.
Outage | J.E.26.08.17809 | C001887007 | Radcliffe Coleman | KSAS | Completed | Load_288332 | Duhaney - 210 | 2026-08-12 16:05 | 2026-08-12 16:08 | 2026-08-12 19:35 | 2026-08-12 20:29 | 2026-08-12 20:28 | 2026-08-12 20:29 | 2026-08-12 20:29 | 2026-08-12 20:29 |  |  | Fair | No | Area found with two blown junction fuse (50A) and a dislodge switch. This was a result of lightning. Isolation was done at pole 0041049 before repairs were done. The same value fuse found was replaced, area now back to normal.
Outage | J.E.26.08.17785 | C001887022 | Kenroy Dale | Manchester | Completed | Load_257939 | Porus - 310 | 2026-08-12 16:18 | 2026-08-13 07:51 | 2026-08-13 09:23 | 2026-08-13 09:27 | 2026-08-13 10:09 | 2026-08-13 12:53 | 2026-08-13 13:05 | 2026-08-13 13:05 |  |  | Fair | No | Blown 3 transformer fuse found line patrol 2 span of secondary both phase and neutral found broken, 35 class 6 T pole also found badly leaning and need urgent attention. Conductor was splice and retention blown fuse was replaced and area now with supply
Outage | J.E.26.08.17855 | C001887026 | Neville Spencer | Clarendon | Completed | Load_257023 | Parnassus - 310 | 2026-08-12 16:22 | 2026-08-12 16:28 | 2026-08-12 17:15 | 2026-08-12 17:16 | 2026-08-12 17:25 | 2026-08-12 17:57 | 2026-08-12 17:57 | 2026-08-12 17:57 |  |  | Rains | No | Renew blown 40 amp j/ fuse at pole # 115558 area restored.
Outage | J.E.26.08.17789 | C001887028 | Neville Spencer | Clarendon | Completed | Load_245641 | Parnassus - 210 | 2026-08-12 16:24 | 2026-08-12 16:28 | 2026-08-12 20:13 | 2026-08-12 20:13 | 2026-08-12 20:16 | 2026-08-12 20:16 | 2026-08-12 20:16 | 2026-08-12 20:16 |  |  | Fair | No | Unable to locate customer.
Outage | J.E.26.08.17816 | C001887033 | Neville Spencer | Clarendon | Completed | Load_245051 | Parnassus - 310 | 2026-08-12 16:25 | 2026-08-12 16:28 | 2026-08-12 18:06 | 2026-08-12 18:07 | 2026-08-12 18:22 | 2026-08-12 18:22 | 2026-08-12 18:34 | 2026-08-12 18:34 |  |  | Fair | No | Found supply at location voltage reading 115 117 205 238 239 241 .
Outage | J.E.26.08.17870 | C001887035 | Neville Spencer | Clarendon | Completed | Load_572086 | Parnassus - 310 | 2026-08-12 16:26 | 2026-08-12 16:29 | 2026-08-12 21:09 | 2026-08-12 21:09 | 2026-08-12 21:17 | 2026-08-12 21:34 | 2026-08-12 21:36 | 2026-08-12 21:36 |  |  | EarthMovement | No | Renew blown 30 amp J / fuse at pole # 0183780 area restored.
Outage | J.E.26.08.17879 | C001887040 | Milton Charlton | KSAN | Completed | Load_266033 | Hope - 410 | 2026-08-12 16:31 | 2026-08-13 07:44 | 2026-08-13 10:04 | 2026-08-13 10:05 | 2026-08-13 10:50 | 2026-08-13 10:35 | 2026-08-13 10:55 | 2026-08-13 10:55 |  |  | Fair | No | Refused and reclosed 10 amps junction atpole#0102185 and one 3 amps transformer switch at pole #0110259 using one 10 amps and one 3 amps fuses.
Outage | J.E.26.08.17520 | C001887043 | Raheem Ricketts | St.Elizabeth | Completed | Load_292317 | Maggotty - 210 | 2026-08-12 16:33 | 2026-08-12 16:34 | 2026-08-12 16:45 | 2026-08-12 17:42 | 2026-08-12 18:25 | 2026-08-12 18:26 | 2026-08-12 18:27 | 2026-08-12 18:27 |  |  | Fair | No | Check and found customer problem is not on the jps side voltage 110,110,220
Outage | J.E.26.08.17835 | C001887044 | Raheem Ricketts | St.Elizabeth | Completed | Load_291987 | Maggotty - 210 | 2026-08-12 16:33 | 2026-08-12 16:35 | 2026-08-12 16:45 | 2026-08-13 15:51 | 2026-08-13 15:51 | 2026-08-13 15:51 | 2026-08-13 15:51 | 2026-08-13 15:51 |  |  | Fair | No | Check and found okay
Outage | J.E.26.08.17896 | C001887048 | Milton Charlton | KSAN | Completed | Load_253447 | Hope - 510 | 2026-08-12 16:36 | 2026-08-12 16:37 | 2026-08-12 17:05 | 2026-08-12 17:05 | 2026-08-12 17:08 | 2026-08-12 17:05 | 2026-08-12 17:14 | 2026-08-12 17:14 |  |  | Rains | No | 50kva transformer at pole #025918 secondary bushing burn out . Isolate bank of transformers (2- 50& 1-100 kva). 50 kva transformer at pole #025918 defective.
Non-Outage | J.E.26.08.17899 | C001887067 | Rusean Allen |  | Completed |  |  | 2026-08-12 17:00 | 2026-08-12 23:48 | 2026-08-13 03:08 | 2026-08-13 03:09 | 2026-08-13 03:25 | 2026-08-13 03:26 | 2026-08-13 03:26 | 2026-08-13 03:26 | Fire |  | Fair | No | Found okay
Outage | J.E.26.08.17943 | C001887068 | Daniel Francis | St.Ann | Completed | Load_265231 | Roaring River - 210 | 2026-08-12 17:00 | 2026-08-12 23:16 | 2026-08-12 23:31 | 2026-08-12 23:32 | 2026-08-13 00:40 | 2026-08-13 02:41 | 2026-08-13 02:41 | 2026-08-13 02:41 | BrokenWire |  | Fair | No | Found secondary phase broken splice and retention 2span of 1wire also antangle1 span 3wire
Outage | J.E.26.08.17680 | C001887072 | Dwayne Cohen | KSAN | Completed | Load_265860 | Constant Spring - 210 | 2026-08-12 17:10 | 2026-08-12 17:11 | 2026-08-12 18:14 | 2026-08-12 18:15 | 2026-08-12 19:11 | 2026-08-12 19:12 | 2026-08-12 19:21 | 2026-08-12 19:21 |  |  | Fair | No | Refuse two blown 20amps junction by pole#041908
Outage | J.E.26.08.17778 | C001887083 | Elvis Trowers | KSAN | Completed | Load_251201 | Washington Blvd - 610 | 2026-08-12 17:11 | 2026-08-12 17:27 | 2026-08-12 18:12 | 2026-08-12 18:40 | 2026-08-12 19:01 | 2026-08-12 19:05 | 2026-08-12 19:06 | 2026-08-12 19:06 |  |  | Fair | No | Found one 20 amps junction fuse blown at pole #( no pole #) . Refused using one 20 amps fuse and reclosed junction switch.
Outage | J.E.26.08.17788 | C001887082 | Elvis Trowers | KSAN | Completed | Load_412879 | Washington Blvd - 610 | 2026-08-12 17:11 | 2026-08-12 17:27 | 2026-08-12 21:40 | 2026-08-12 21:40 | 2026-08-12 21:58 | 2026-08-12 22:00 | 2026-08-12 21:59 | 2026-08-12 21:59 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.17820 | C001887084 | Elvis Trowers | KSAN | Completed | Load_240530 | Constant Spring - 210 | 2026-08-12 17:11 | 2026-08-12 17:27 | 2026-08-12 19:53 | 2026-08-12 19:53 | 2026-08-12 20:58 | 2026-08-12 20:30 | 2026-08-12 20:59 | 2026-08-12 20:59 |  |  | Fair | No | Found okay upon arrival.
Outage | J.E.26.08.17568 | C001887096 | Elvis Trowers | KSAN | Completed | Load_556039 | Constant Spring - 310 | 2026-08-12 17:27 | 2026-08-12 17:30 | 2026-08-12 19:18 | 2026-08-12 19:18 | 2026-08-12 19:45 | 2026-08-12 19:45 | 2026-08-12 19:50 | 2026-08-12 19:50 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.17995 | C001887097 | Raheem Ricketts | St.Elizabeth | Completed | Load_305162 | Maggotty - 210 | 2026-08-12 17:30 | 2026-08-12 17:31 | 2026-08-13 15:48 | 2026-08-13 15:48 | 2026-08-13 15:48 | 2026-08-13 15:48 | 2026-08-13 15:48 | 2026-08-13 15:48 |  |  | Fair | No | Problem has been solved
Outage | J.E.26.08.17926 | C001887098 | Oshane Warren | St.Elizabeth | Completed | Load_243757 | Maggotty - 110 | 2026-08-12 17:32 | 2026-08-13 10:34 | 2026-08-13 13:47 | 2026-08-13 13:48 | 2026-08-13 15:01 | 2026-08-13 15:02 | 2026-08-13 15:04 | 2026-08-13 15:04 |  |  | Fair | No | Vehicle struck main pole in the line section and caused 8 amp junction fuse to blow replace 8 amp junction fuse
Non-Outage | J.E.26.08.17977 | C001887099 | Locksley Allen | St.Mary | Completed | Load_269779 | Blackstonedge - 110 | 2026-08-12 17:39 | 2026-08-13 08:27 | 2026-08-13 15:25 | 2026-08-13 15:52 | 2026-08-13 15:51 | 2026-08-13 16:04 | 2026-08-13 16:01 | 2026-08-13 16:01 | LeaningPole |  | Fair | No | Guy pole(rotten) ,broke down and is lying on the road and it is blocking part of the road.Please refer to maintainance
Non-Outage | J.E.26.07.33412 | C001887100 | Romaine Roberts | St.Mary | Completed | Load_350817 | Oracabessa - 110 | 2026-08-12 17:40 | 2026-08-12 17:41 | 2026-08-12 18:03 | 2026-08-12 19:03 | 2026-08-12 19:34 | 2026-08-12 19:59 | 2026-08-12 19:59 | 2026-08-12 19:59 |  |  | Fair | No | Day light attention needed to carry out repairs customer wait it’s too late to visit premises also bucket truck needed
Non-Outage | J.E.26.08.18036 | C001887101 | Evan Spaulding |  | Completed |  |  | 2026-08-12 17:42 | 2026-08-12 17:46 | 2026-08-12 18:27 | 2026-08-12 18:27 | 2026-08-12 19:01 | 2026-08-12 19:01 | 2026-08-12 19:01 | 2026-08-12 19:01 |  |  | Fair | No | Premises not found,customer not answering phone calls to give directions to premises.
Non-Outage | J.E.26.08.17376 | C001887110 | Lancelot Brown | Hanover | Completed | Load_253839 | Orange Bay - 310 | 2026-08-12 18:18 | 2026-08-12 18:19 | 2026-08-12 18:39 | 2026-08-12 18:42 | 2026-08-12 19:35 | 2026-08-12 20:29 | 2026-08-12 20:29 | 2026-08-12 20:29 |  |  | Rains | No | Remake corroded joint at pothead and pole used three connectors two pg clamps vl at pothead 113-115-228 supply restore
Non-Outage | J.E.26.08.17199 | C001887112 | Lancelot Brown | Hanover | Completed | Load_242732 | Orange Bay - 310 | 2026-08-12 18:20 | 2026-08-12 18:21 | 2026-08-12 18:39 | 2026-08-12 22:21 | 2026-08-12 22:55 | 2026-08-12 23:01 | 2026-08-12 23:01 | 2026-08-12 23:01 | BrokenPole |  | Fair | No | 35 feet wooden pole T construction with overhead guy pole rotten need to replace please pass on to maintenance department in Hanover mr Richards need ergent attention please put it on the dashboard
Outage | J.E.26.08.18229 | C001887115 | Romaine Roberts | St.Mary | Completed | Load_239531 | Oracabessa - 210 | 2026-08-12 18:34 | 2026-08-12 18:35 | 2026-08-12 20:00 | 2026-08-12 20:01 | 2026-08-12 21:44 | 2026-08-13 08:09 | 2026-08-13 08:12 | 2026-08-13 08:12 |  |  | Fair | No | Call was made to customer but premises was close a morning visit was requested
Outage | J.E.26.08.17883 | C001887119 | Richard Watson | St.Elizabeth | Completed | Load_251505 | Maggotty - 110 | 2026-08-12 18:35 | 2026-08-12 19:24 | 2026-08-12 20:18 | 2026-08-12 20:19 | 2026-08-12 20:25 | 2026-08-12 20:28 | 2026-08-12 20:28 | 2026-08-12 20:28 |  |  | Rains | No | Area found with supply, a few customers were contacted and they stated that they currently have supply and they didn’t lose any electricity today.
Outage | J.E.26.08.18234 | C001887122 | Neville Spencer | Clarendon | Completed | Load_245579 | Parnassus - 310 | 2026-08-12 18:40 | 2026-08-12 19:10 | 2026-08-12 20:17 | 2026-08-12 20:17 | 2026-08-12 21:05 | 2026-08-12 21:05 | 2026-08-12 21:08 | 2026-08-12 21:08 |  |  | Fair | No | Renew blown 8 amp J / fuse supply restored.
Outage | J.E.26.08.18131 | C001887123 | Raheem Ricketts | St.Elizabeth | Completed | Load_292198 | Maggotty - 210 | 2026-08-12 18:41 | 2026-08-12 18:42 | 2026-08-13 15:49 | 2026-08-13 15:51 | 2026-08-13 15:50 | 2026-08-13 15:51 | 2026-08-13 15:51 | 2026-08-13 15:51 |  |  | Fair | No | Problem has been solved from yesterday
Outage | J.E.26.08.18059 | C001887129 | Javid Vernon | Westmoreland | Completed | Load_238122 | Paradise - 210 | 2026-08-12 18:43 | 2026-08-12 18:44 | 2026-08-12 18:47 | 2026-08-12 18:48 | 2026-08-12 19:18 | 2026-08-12 19:24 | 2026-08-12 19:25 | 2026-08-12 19:25 |  |  | Fair | No | Power was restored to customers after LCB6-725 was reclosed
Outage | J.E.26.08.18153 | C001887130 | Javid Vernon | Westmoreland | Completed | Load_251611 | Paradise - 310 | 2026-08-12 18:44 | 2026-08-12 19:37 | 2026-08-12 22:16 | 2026-08-12 22:16 | 2026-08-12 22:51 | 2026-08-12 22:59 | 2026-08-12 23:00 | 2026-08-12 23:00 |  |  | Fair | No | Area check and found okay unable to locate customer and premises phone calls to customer number went unanswered and no directions was given
Outage | J.E.26.08.17906 | C001887131 | Edward Royal | KSAN | Completed | Load_268534 | Washington Blvd - 310 | 2026-08-12 18:45 | 2026-08-12 18:45 | 2026-08-12 18:56 | 2026-08-12 18:56 | 2026-08-12 19:16 | 2026-08-12 20:10 | 2026-08-12 20:11 | 2026-08-12 20:11 |  |  | Fair | No | Remove tree spliced and reconnected secondary phase using 2 single bolt clamp
Outage | J.E.26.08.18222 | C001887132 | Edward Royal | KSAN | Completed | Load_269564 | Washington Blvd - 310 | 2026-08-12 18:45 | 2026-08-12 18:45 | 2026-08-12 18:53 | 2026-08-12 18:54 | 2026-08-12 18:53 | 2026-08-12 18:55 | 2026-08-12 18:55 | 2026-08-12 18:55 |  |  | Fair | No | Replaced 20A junction fuse
Outage | J.E.26.08.17873 | C001887135 | Neville Spencer | Clarendon | Completed | Load_254041 | Parnassus - 310 | 2026-08-12 18:46 | 2026-08-12 18:47 | 2026-08-12 22:02 | 2026-08-12 22:03 | 2026-08-12 22:29 | 2026-08-12 23:28 | 2026-08-12 23:28 | 2026-08-12 23:28 | BrokenPole |  | Fair | No | Found 35 c6 wooden pole head and cross arm burnt off .ConstructionT D A with 3 phase primary line. Line isolate at FERN CRESCENT primary and secondary lines. Renew 2 blown 15, amp J/ fuse at pole # 0118900 supply restored , one xmfr circuit out pole need to replace.
Outage | J.E.26.08.18247 | C001887134 | Neville Spencer | Clarendon | Completed | Load_254832 | Parnassus - 310 | 2026-08-12 18:46 | 2026-08-12 18:47 | 2026-08-12 21:38 | 2026-08-12 21:39 | 2026-08-12 22:00 | 2026-08-12 22:00 | 2026-08-12 22:02 | 2026-08-12 22:02 |  |  | Fair | No | Renew blown 30 amp j/fuse at pole00183780, area restored.
Outage | J.E.26.08.18262 | C001887152 | Jamainea Fuller | KSAS | Completed | Load_291179 | Greenwich - 510 | 2026-08-12 19:17 | 2026-08-12 19:19 | 2026-08-12 21:37 | 2026-08-12 21:37 | 2026-08-12 21:50 | 2026-08-12 22:37 | 2026-08-12 22:39 | 2026-08-12 22:39 |  |  | Rains | No | 40 amp found blown and was refused. Pole #611635.
Outage | J.E.26.08.18287 | C001887151 | Jamainea Fuller | KSAS | Completed | Load_239554 | Rockfort - 410 | 2026-08-12 19:17 | 2026-08-12 19:19 | 2026-08-12 19:27 | 2026-08-12 21:07 | 2026-08-12 21:06 | 2026-08-12 21:07 | 2026-08-12 21:09 | 2026-08-12 21:09 |  |  | Rains | No | Area inaccessible vehicles parked along roadway.
Outage | J.E.26.08.17874 | C001887154 | Jamainea Fuller | KSAS | Completed | Load_239308 | Rockfort - 410 | 2026-08-12 19:18 | 2026-08-12 19:19 | 2026-08-12 19:46 | 2026-08-12 19:49 | 2026-08-12 20:06 | 2026-08-12 20:57 | 2026-08-12 20:59 | 2026-08-12 20:59 |  |  | Rains | No | Old piece of tie wire came into contact with cross arm, wire was removed.25amp fuse that was blown was replaced. Customers restored.
Outage | J.E.26.08.18260 | C001887153 | Jamainea Fuller | KSAS | Completed | Load_250688 | Hunts Bay - 310 | 2026-08-12 19:18 | 2026-08-12 19:19 | 2026-08-12 21:09 | 2026-08-12 21:09 | 2026-08-12 21:33 | 2026-08-12 21:34 | 2026-08-12 21:34 | 2026-08-12 21:34 |  |  | Rains | No | Related call, customer restored.
Outage | J.E.26.08.17984 | C001887156 | Delano Gayle | St.Catherine | Completed | Load_243531 | Tredegar - 310 | 2026-08-12 19:22 | 2026-08-13 00:05 | 2026-08-13 01:56 | 2026-08-13 01:56 | 2026-08-13 01:58 | 2026-08-13 01:58 | 2026-08-13 01:59 | 2026-08-13 01:59 |  |  | Fair | No | Premises found okay power restored to premises
Outage | J.E.26.08.18325 | C001887158 | Lancelot Brown | Hanover | Completed | Load_238848 | Orange Bay - 310 | 2026-08-12 19:22 | 2026-08-12 19:23 | 2026-08-12 21:21 | 2026-08-12 21:21 | 2026-08-12 22:18 | 2026-08-12 22:19 | 2026-08-12 22:19 | 2026-08-12 22:19 | BrokenWire |  | Rains | No | Please carry forward for daylight attention
Outage | J.E.26.08.18339 | C001887157 | Lancelot Brown | Hanover | Completed | Load_249257 | Orange Bay - 310 | 2026-08-12 19:22 | 2026-08-12 19:23 | 2026-08-12 20:31 | 2026-08-12 20:31 | 2026-08-12 21:16 | 2026-08-12 21:19 | 2026-08-12 21:20 | 2026-08-12 21:20 |  |  | Rains | No | Check and found customer meter not connecting meter need to replace please pass on to field service department in montegobay bay west Hanover customer without supply need ergent attention
Outage | J.E.26.08.17968 | C001887159 | Neville Spencer | St.Catherine | Completed | Load_241036 | Rhodens Pen - 310 | 2026-08-12 19:23 | 2026-08-12 19:32 | 2026-08-12 19:46 | 2026-08-12 19:46 | 2026-08-12 19:56 | 2026-08-12 20:10 | 2026-08-12 20:12 | 2026-08-12 20:12 |  |  | Fair | No | Renew blown 15 amp J/ fuse at pole # 0092796 area restored.
Outage | J.E.26.08.18157 | C001887161 | Delano Gayle | St.Catherine | Completed | Load_574324 | Rhodens Pen - 410 | 2026-08-12 19:24 | 2026-08-13 07:19 | 2026-08-13 10:50 | 2026-08-13 10:50 | 2026-08-13 11:03 | 2026-08-13 11:04 | 2026-08-13 11:04 | 2026-08-13 11:04 |  |  | Fair | No | Premises found okay related to call where 8amps fuse was replaced at blown junction
Outage | J.E.26.08.18288 | C001887160 | Hartley Chin | St.Catherine | Completed | Load_240139 | Rhodens Pen - 310 | 2026-08-12 19:24 | 2026-08-13 16:12 | 2026-08-13 17:44 | 2026-08-13 17:53 | 2026-08-13 17:53 | 2026-08-13 17:54 | 2026-08-13 17:54 | 2026-08-13 17:54 |  |  | Fair | No | Premisis found ok.
Outage | J.E.26.08.17841 | C001887165 | Delano Gayle | St.Catherine | Completed | Load_230025 | Rhodens Pen - 210 | 2026-08-12 19:25 | 2026-08-13 07:19 | 2026-08-13 12:45 | 2026-08-13 12:46 | 2026-08-13 13:42 | 2026-08-13 13:42 | 2026-08-13 13:42 | 2026-08-13 13:42 |  |  | Fair | No | Premises found okay power was restored
Outage | J.E.26.08.18275 | C001887164 | Richard Watson | St.Elizabeth | Completed | Load_238726 | Maggotty - 110 | 2026-08-12 19:25 | 2026-08-12 20:17 | 2026-08-12 20:28 | 2026-08-12 20:29 | 2026-08-12 20:37 | 2026-08-12 20:55 | 2026-08-12 20:59 | 2026-08-12 20:59 |  |  | Rains | No | Replace blown 15amp junction fuse no pole#, after completing patrol, no visible fault found suspected cause lightning, supply restored to affected customers.
Outage | J.E.26.08.17828 | C001887166 | Delano Gayle | St.Catherine | Completed | Load_266876 | Rhodens Pen - 410 | 2026-08-12 19:26 | 2026-08-13 07:19 | 2026-08-13 13:42 | 2026-08-13 13:43 | 2026-08-13 14:21 | 2026-08-13 14:27 | 2026-08-13 14:27 | 2026-08-13 14:27 |  |  | Fair | No | Premises not found
Outage | J.E.26.08.17611 | C001887167 | Edward Royal | KSAS | Completed | Load_261030 | Rockfort - 410 | 2026-08-12 19:28 | 2026-08-12 19:29 | 2026-08-12 20:13 | 2026-08-12 20:14 | 2026-08-12 20:13 | 2026-08-12 20:14 | 2026-08-12 20:14 | 2026-08-12 20:14 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.17653 | C001887168 | Edward Royal | KSAS | Completed | Load_239845 | Rockfort - 410 | 2026-08-12 19:28 | 2026-08-12 19:29 | 2026-08-13 08:58 | 2026-08-13 08:58 | 2026-08-13 08:58 | 2026-08-13 08:58 | 2026-08-13 08:58 | 2026-08-13 08:58 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.17821 | C001887169 | Edward Royal | KSAS | Completed | Load_243736 | Cane River - 310 | 2026-08-12 19:28 | 2026-08-12 19:29 | 2026-08-12 20:59 | 2026-08-12 20:59 | 2026-08-12 20:59 | 2026-08-12 21:41 | 2026-08-12 21:41 | 2026-08-12 21:41 |  |  | Fair | No | Spliced and reconnected drop lead to secondary line using 4 single bolt clamp
Outage | J.E.26.08.18143 | C001887170 | Richard Samuda | Manchester | Completed | Load_253491 | Porus - 310 | 2026-08-12 19:29 | 2026-08-12 19:34 | 2026-08-12 19:41 | 2026-08-12 19:41 | 2026-08-12 20:21 | 2026-08-12 08:22 | 2026-08-12 20:23 | 2026-08-12 20:23 | BrokenWire |  | Fair | No | Found ok customer concerned about street light
Outage | J.E.26.08.18360 | C001887171 | Raymond Lewis | St.Ann | Completed | Load_572667 | Roaring River - 410 | 2026-08-12 19:30 | 2026-08-13 07:28 | 2026-08-13 08:18 | 2026-08-13 08:19 | 2026-08-13 09:37 | 2026-08-13 09:39 | 2026-08-13 09:39 | 2026-08-13 09:39 |  |  | Fair | No | Supply restored
Outage | J.E.26.08.12128 | C001887178 | Andre Williams | Trelawny | Completed | Load_292370 | Greenwood - 210 | 2026-08-12 19:50 | 2026-08-12 19:51 | 2026-08-12 20:59 | 2026-08-12 21:00 | 2026-08-12 21:52 | 2026-08-12 23:37 | 2026-08-12 23:37 | 2026-08-12 23:37 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Open 100 kva transformer splice and repair 120 ft defects 2 naut conductpr area now with full supply
Outage | J.E.26.08.18396 | C001887183 | Romeo Brissett | St.James | Completed | Load_292851 | Bogue - 610 | 2026-08-12 20:20 | 2026-08-12 20:22 | 2026-08-12 20:37 | 2026-08-12 20:37 | 2026-08-12 21:52 | 2026-08-12 22:38 | 2026-08-12 22:39 | 2026-08-12 22:39 |  |  | Fair | No | Removed tree limbs and replaced (1)15amps junction fuse
Outage | J.E.26.08.18384 | C001887185 | Javid Vernon | Westmoreland | Completed | Load_239066 | Paradise - 210 | 2026-08-12 20:21 | 2026-08-12 20:22 | 2026-08-12 20:47 | 2026-08-12 20:48 | 2026-08-12 21:28 | 2026-08-12 21:35 | 2026-08-12 21:35 | 2026-08-12 21:35 |  |  | Fair | No | Premises check and found okay customer stated that the power was restored
Outage | J.E.26.08.17653 | C001887190 | Jamainea Fuller | KSAS | Completed | Load_239845 | Rockfort - 410 | 2026-08-12 20:53 | 2026-08-12 20:54 | 2026-08-12 21:00 | 2026-08-12 21:02 | 2026-08-12 21:02 | 2026-08-12 21:02 | 2026-08-12 21:03 | 2026-08-12 21:03 |  |  | Rains | No | Related call customer restored.
Outage | J.E.26.08.17692 | C001887191 | Jamainea Fuller | KSAS | Completed | Load_259189 | Rockfort - 410 | 2026-08-12 20:53 | 2026-08-12 20:54 | 2026-08-12 21:04 | 2026-08-12 21:05 | 2026-08-12 21:04 | 2026-08-12 21:05 | 2026-08-12 21:06 | 2026-08-12 21:06 |  |  | Rains | No | Related calls. Customer restored.
Outage | J.E.26.08.18399 | C001887192 | Richard Watson | St.Elizabeth | Completed | Load_257801 | Maggotty - 210 | 2026-08-12 20:59 | 2026-08-12 21:00 | 2026-08-12 21:10 | 2026-08-12 21:11 | 2026-08-12 21:38 | 2026-08-12 22:27 | 2026-08-12 22:34 | 2026-08-12 22:34 | BrokenWire |  | Rains | No | Found broken service wire neutral and burnt off service wire phase at secondary pole, drop, splice and retention service wire, use approximately 10ft of #6 triplex service wire and two 1bolt clamps, cause by service wire making contact with secondary phase during severe wind, corrected using diron and spool, voltage left 106v, 115v 221v
Outage | J.E.26.08.18458 | C001887194 | Derrick Dawkins | St.James | Completed | Load_258936 | Queens Drive - 710 | 2026-08-12 21:03 | 2026-08-13 00:20 | 2026-08-13 00:50 | 2026-08-13 12:01 | 2026-08-13 12:00 | 2026-08-13 12:01 | 2026-08-13 12:05 | 2026-08-13 12:05 | BrokenWire |  | Fair | No | Found customer service wire defective. Replaced 37ft #6 triplex voltage left 119/119/238
Non-Outage | J.E.26.08.18447 | C001887195 | Cliton Henry |  | Completed |  |  | 2026-08-12 21:07 | 2026-08-13 07:19 | 2026-08-13 08:13 | 2026-08-13 08:14 | 2026-08-13 08:19 | 2026-08-13 08:19 | 2026-08-13 08:20 | 2026-08-13 08:20 | BrokenWire |  | Fair | No | The customer stated that the repairs was completed
Outage | J.E.26.08.17891 | C001887197 | Fitzroy Turner | KSAS | Completed | Load_244817 | Greenwich - 410 | 2026-08-12 21:11 | 2026-08-12 21:12 | 2026-08-12 21:32 | 2026-08-12 21:34 | 2026-08-12 22:23 | 2026-08-12 22:24 | 2026-08-12 22:24 | 2026-08-12 22:24 |  |  | EarthMovement | No | Customer premises found with electricity supply
Outage | J.E.26.08.17998 | C001887199 | Rusean Allen | KSAS | Completed | Load_253542 | Rockfort - 410 | 2026-08-12 21:11 | 2026-08-13 07:19 | 2026-08-13 11:09 | 2026-08-13 11:10 | 2026-08-13 11:21 | 2026-08-13 11:27 | 2026-08-13 11:27 | 2026-08-13 11:27 |  |  | Fair | No | Meter number #2161203 not found at premises
Outage | J.E.26.08.16737 | C001887202 | Stephen Taylor | St.Thomas | Completed | Load_253268 | Lysson - 410 | 2026-08-12 21:29 | 2026-08-13 07:14 | 2026-08-13 07:29 | 2026-08-13 07:29 | 2026-08-13 08:32 | 2026-08-13 08:32 | 2026-08-13 08:55 | 2026-08-13 08:55 | Fire |  | Fair | No | Retention service wire 3 clamps Rdg 113–114–226
Non-Outage | J.E.26.08.17390 | C001887203 | Stephen Taylor |  | Completed |  |  | 2026-08-12 21:30 | 2026-08-13 07:14 | 2026-08-13 10:17 | 2026-08-13 10:18 | 2026-08-13 11:49 | 2026-08-13 11:51 | 2026-08-13 11:52 | 2026-08-13 11:52 |  |  | Fair | No | Call to customer and customer said power is back from last night and okay
Non-Outage | J.E.26.08.18159 | C001887204 | Michael Paterson |  | Completed |  |  | 2026-08-12 21:51 | 2026-08-13 07:33 | 2026-08-13 11:44 | 2026-08-13 11:44 | 2026-08-13 13:25 | 2026-08-13 13:26 | 2026-08-13 13:27 | 2026-08-13 13:27 |  |  | Fair | No | Check and found area ok, premise no found, invalid contact information.
Outage | J.E.26.08.18410 | C001887206 | Hartley Chin | Clarendon | Completed | Load_256014 | Parnassus - 210 | 2026-08-12 21:55 | 2026-08-13 07:51 | 2026-08-13 11:47 | 2026-08-13 11:55 | 2026-08-13 11:55 | 2026-08-13 11:55 | 2026-08-13 11:56 | 2026-08-13 11:56 |  |  | Fair | No | Premisis found ok.
Outage | J.E.26.08.18478 | C001887221 | Rusean Allen | KSAS | Completed | Load_239308 | Rockfort - 410 | 2026-08-12 23:42 | 2026-08-12 23:48 | 2026-08-13 00:01 | 2026-08-13 00:02 | 2026-08-13 03:07 | 2026-08-13 03:08 | 2026-08-13 03:08 | 2026-08-13 03:08 | BrokenWire |  | Fair | No | Reconnected service wire at pole
Outage | J.E.26.08.18539 | C001887237 | Rusean Allen | KSAS | Completed | Load_1003929 | Rockfort - 410 | 2026-08-13 04:18 | 2026-08-13 04:20 | 2026-08-13 04:37 | 2026-08-13 05:32 | 2026-08-13 05:31 | 2026-08-13 05:32 | 2026-08-13 05:33 | 2026-08-13 05:33 |  |  | Fair | No | 1x 30amp fuse found 1x 30amp fuse replaced.
Non-Outage | J.E.26.08.18670 | C001887239 | Delano Gayle |  | Completed |  |  | 2026-08-13 05:37 | 2026-08-13 05:38 | 2026-08-13 05:47 | 2026-08-13 06:07 | 2026-08-13 07:47 | 2026-08-13 08:22 | 2026-08-13 08:23 | 2026-08-13 08:23 | BrokenWire |  | Fair | No | Broken #6 triplex at pole, tree fell on line, repair use 3 clamps voltage readings 112-113-226, disconnect other defective #6 triplex at pole as no meter was found connected to wire
Outage | J.E.26.08.18663 | C001887240 | Derrick Dawkins | St.James | Completed | Load_256318 | Bogue - 310 | 2026-08-13 06:01 | 2026-08-13 06:02 | 2026-08-13 08:38 | 2026-08-13 08:39 | 2026-08-13 08:39 | 2026-08-13 08:40 | 2026-08-13 08:58 | 2026-08-13 08:58 | TreeContact,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Found 2 span of primary conductor cut down and 35ft class 6 pole broken also need to replace isolat jumper at salters hill entrance to minimize outage refer to maintenance
Outage | J.E.26.08.17535 | C001887280 | Wayne Dillion | St.Elizabeth | Completed | Load_557832 | Maggotty - 110 | 2026-08-13 07:11 | 2026-08-13 07:12 | 2026-08-13 07:49 | 2026-08-13 07:50 | 2026-08-13 07:49 | 2026-08-13 07:50 | 2026-08-13 07:50 | 2026-08-13 07:50 |  |  | Fair | No | Please refer this call to the Westmoreland team
Outage | J.E.26.08.17517 | C001887281 | Oshane Warren | St.Elizabeth | Completed | Load_243757 | Maggotty - 110 | 2026-08-13 07:13 | 2026-08-13 10:33 | 2026-08-13 15:06 | 2026-08-13 15:07 | 2026-08-13 15:06 | 2026-08-13 15:07 | 2026-08-13 15:07 | 2026-08-13 15:07 |  |  | Fair | No | Replace 8 amp junction fuse
Outage | J.E.26.08.18644 | C001887282 | Milton Charlton | KSAN | Completed | Load_256169 | Hope - 510 | 2026-08-13 07:14 | 2026-08-13 07:16 | 2026-08-13 10:58 | 2026-08-13 10:59 | 2026-08-13 11:33 | 2026-08-13 11:35 | 2026-08-13 11:41 | 2026-08-13 11:41 |  |  | Fair | No | 35 ft wooden pole with two wire single phase primary on 5ft crossarm. Crossarm rotten and both conductors dislodged. One resting on top of transformer and blow junction fuse. Need to replace crossarm in order to reclosed junction switch. 5ft crossarm defective.
Outage | J.E.26.08.17558 | C001887285 | Christopher Edwards | KSAN | Completed | Load_246783 | Constant Spring - 410 | 2026-08-13 07:15 | 2026-08-13 07:16 | 2026-08-13 07:30 | 2026-08-13 11:08 | 2026-08-13 12:10 | 2026-08-13 13:22 | 2026-08-13 13:22 | 2026-08-13 13:22 |  |  | Fair | No | Remake corroded phase joint UsingUsing (1) one bolt clamps Voltage:114,115,230v
Outage | J.E.26.08.18624 | C001887284 | Christopher Edwards | KSAN | Completed | Load_256358 | Constant Spring - 410 | 2026-08-13 07:15 | 2026-08-13 07:16 | 2026-08-13 08:35 | 2026-08-13 08:35 | 2026-08-13 10:11 | 2026-08-13 11:03 | 2026-08-13 11:04 | 2026-08-13 11:04 |  |  | Fair | No | Customer made a report for the sue river nwc pumpVisit location and supply is at the premises
Outage | J.E.26.08.18378 | C001887287 | Rusean Allen | KSAS | Completed | Load_266014 | Rockfort - 410 | 2026-08-13 07:17 | 2026-08-13 07:19 | 2026-08-13 10:23 | 2026-08-13 10:25 | 2026-08-13 10:31 | 2026-08-13 10:32 | 2026-08-13 10:33 | 2026-08-13 10:33 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.18484 | C001887286 | Rusean Allen | KSAS | Completed | Load_259334 | Cane River - 610 | 2026-08-13 07:17 | 2026-08-13 07:19 | 2026-08-13 11:32 | 2026-08-13 11:33 | 2026-08-13 12:55 | 2026-08-13 13:06 | 2026-08-13 13:06 | 2026-08-13 13:06 |  |  | Fair | No | 1x 15amp fuse found 1x 15amp fuse replaced.
Outage | J.E.26.08.17971 | C001887288 | Rusean Allen | KSAS | Completed | Load_261603 | Rockfort - 410 | 2026-08-13 07:18 | 2026-08-13 07:19 | 2026-08-13 11:27 | 2026-08-13 11:28 | 2026-08-13 11:31 | 2026-08-13 11:32 | 2026-08-13 11:32 | 2026-08-13 11:32 |  |  | Fair | No | Rami failure, refer to field service department.
Non-Outage | J.E.26.08.18019 | C001887289 | Rusean Allen |  | Completed |  |  | 2026-08-13 07:20 | 2026-08-13 07:23 | 2026-08-13 10:23 | 2026-08-13 10:34 | 2026-08-13 10:33 | 2026-08-13 10:34 | 2026-08-13 10:34 | 2026-08-13 10:34 |  |  | Fair | No | Okay
Outage | J.E.26.08.17589 | C001887290 | Stephen Taylor | St.Thomas | Completed | Load_242945 | Lysson - 410 | 2026-08-13 07:21 | 2026-08-13 07:31 | 2026-08-13 08:59 | 2026-08-13 09:00 | 2026-08-13 09:22 | 2026-08-13 09:23 | 2026-08-13 09:26 | 2026-08-13 09:26 | TreeContact |  | Fair | No | Mango tree needs to cut from secondary line urgent
Outage | J.E.26.08.17827 | C001887291 | Delano Gayle | St.Catherine | Completed | Load_556132 | Rhodens Pen - 210 | 2026-08-13 07:21 | 2026-08-13 07:22 | 2026-08-13 11:05 | 2026-08-13 11:05 | 2026-08-13 11:41 | 2026-08-13 11:50 | 2026-08-13 11:50 | 2026-08-13 11:50 |  |  | Fair | No | Premises found okay power restored
Outage | J.E.26.08.18415 | C001887292 | Delano Gayle | St.Catherine | Completed | Load_574324 | Rhodens Pen - 410 | 2026-08-13 07:21 | 2026-08-13 07:22 | 2026-08-13 10:07 | 2026-08-13 10:08 | 2026-08-13 10:26 | 2026-08-13 10:49 | 2026-08-13 10:49 | 2026-08-13 10:49 |  |  | Fair | No | Burnt 25kva transformer drop lead, blown junction no pole#, repair burnt lead at 25kva and replace 8amps at junction
Non-Outage | J.E.26.08.18213 | C001887293 | Delano Gayle |  | Completed |  |  | 2026-08-13 07:23 | 2026-08-13 07:24 | 2026-08-13 08:23 | 2026-08-13 08:24 | 2026-08-13 08:54 | 2026-08-13 09:03 | 2026-08-13 09:04 | 2026-08-13 09:04 |  |  | Fair | No | Premises found okay
Non-Outage | J.E.26.08.17698 | C001887294 | Milton Charlton | KSAN | Completed | Load_267367 | Hope - 510 | 2026-08-13 07:24 | 2026-08-13 07:27 | 2026-08-13 07:49 | 2026-08-13 07:50 | 2026-08-13 09:51 | 2026-08-13 09:55 | 2026-08-13 10:02 | 2026-08-13 10:02 | Fire |  | Fair | No | 40ft wooden pole #0038858 with three phase primary conductors on double 8ft alley crossarms. Conductor is close to pole top causing fire on pole. Need to cut pole top or remove conductor away from pole top. Need immediate attention because whenever it rains the pole caught fire.
Non-Outage | J.E.26.08.17149 | C001887303 | Eric Williams | KSAS | Completed | Load_267072 | Duhaney - 310 | 2026-08-13 07:26 | 2026-08-13 08:33 | 2026-08-13 11:11 | 2026-08-13 11:18 | 2026-08-13 11:18 | 2026-08-13 11:36 | 2026-08-13 11:36 | 2026-08-13 11:36 |  |  | Fair | No | Found loose joint in meter socket on load side, voltage readings 116/116/232volts, customer advise and left ok.
Non-Outage | J.E.26.08.17674 | C001887302 | Fredrick Hamilton | KSAN | Completed | Load_266150 | West Kings House - 410 | 2026-08-13 07:26 | 2026-08-13 07:27 | 2026-08-13 08:06 | 2026-08-13 08:23 | 2026-08-13 08:22 | 2026-08-13 08:25 | 2026-08-13 08:25 | 2026-08-13 08:25 |  |  | Fair | No | Issue was resolved on the 11/8/2026 customer is ok Phase and neutral got tangled up which same was corrected Premises is ok
Non-Outage | J.E.26.08.17684 | C001887301 | Fredrick Hamilton | KSAN | Completed | Load_256909 | Constant Spring - 210 | 2026-08-13 07:26 | 2026-08-13 07:27 | 2026-08-13 08:06 | 2026-08-13 13:29 | 2026-08-13 13:32 | 2026-08-13 13:40 | 2026-08-13 13:40 | 2026-08-13 13:40 |  |  | Fair | No | Premises found locked no occupant seen at time of visit
Non-Outage | J.E.26.08.18042 | C001887300 | Fredrick Hamilton | KSAS | Completed | Load_262705 | Duhaney - 310 | 2026-08-13 07:26 | 2026-08-13 07:27 | 2026-08-13 08:06 | 2026-08-13 08:15 | 2026-08-13 08:15 | 2026-08-13 08:16 | 2026-08-13 08:16 | 2026-08-13 08:16 |  |  | Fair | No | Customer contacted and stated that power was restored fully at location Premises is ok
Non-Outage | J.E.26.08.18516 | C001887299 | Fredrick Hamilton | KSAS | Completed | Load_243162 | Duhaney - 310 | 2026-08-13 07:26 | 2026-08-13 07:27 | 2026-08-13 08:06 | 2026-08-13 13:43 | 2026-08-13 13:54 | 2026-08-13 13:58 | 2026-08-13 13:58 | 2026-08-13 13:58 |  |  | Fair | No | Premises found locked multiple calls to customer went to voicemail No occupant seen
Non-Outage | J.E.26.08.17467 | C001887304 | Christopher Edwards | KSAN | Completed | Load_264247 | Constant Spring - 410 | 2026-08-13 07:27 | 2026-08-13 07:28 | 2026-08-13 13:22 | 2026-08-13 13:23 | 2026-08-13 14:09 | 2026-08-13 03:15 | 2026-08-13 17:23 | 2026-08-13 17:23 |  |  | Fair | No | Isolate 25 kva transformer To remake burnt phase joint Using:113,112,218v
Non-Outage | J.E.26.08.18386 | C001887306 | Eric Williams | KSAS | Completed | Load_567648 | Duhaney - 310 | 2026-08-13 07:28 | 2026-08-13 07:29 | 2026-08-13 10:07 | 2026-08-13 10:08 | 2026-08-13 10:08 | 2026-08-13 10:08 | 2026-08-13 10:11 | 2026-08-13 10:11 |  |  | Fair | No | Blown 20amps junction fuse found and replaced
Outage | J.E.26.08.18699 | C001887308 | Eric Williams | KSAS | Completed | Load_567648 | Duhaney - 310 | 2026-08-13 07:28 | 2026-08-13 07:29 | 2026-08-13 08:27 | 2026-08-13 08:27 | 2026-08-13 08:30 | 2026-08-13 10:06 | 2026-08-13 10:07 | 2026-08-13 10:07 |  |  | Fair | No | Blown 20amps junction fuse found and replaced
Non-Outage | J.E.26.08.18311 | C001887316 | Elvis Trowers |  | Completed |  |  | 2026-08-13 07:29 | 2026-08-13 07:31 | 2026-08-13 09:49 | 2026-08-13 09:50 | 2026-08-13 10:23 | 2026-08-13 10:30 | 2026-08-13 10:24 | 2026-08-13 10:24 |  |  | Fair | No | Found okay upon arrival. Reset customer circuit breaker.
Outage | J.E.26.08.17792 | C001887311 | Elvis Trowers | KSAN | Completed | Load_254557 | Constant Spring - 310 | 2026-08-13 07:29 | 2026-08-13 07:31 | 2026-08-13 08:08 | 2026-08-13 08:09 | 2026-08-13 09:07 | 2026-08-13 08:40 | 2026-08-13 09:09 | 2026-08-13 09:09 |  |  | Fair | No | Customer service wire #6 triplex phase burn off at pole. Repair using one 1- bolt clamp. Reading at meter socket 118-119-238 volts.
Outage | J.E.26.08.18012 | C001887313 | Clyde Brown | Clarendon | Completed | Load_260045 | May Pen - 110 | 2026-08-13 07:29 | 2026-08-13 07:32 | 2026-08-13 07:43 | 2026-08-13 07:44 | 2026-08-13 08:12 | 2026-08-13 08:30 | 2026-08-13 08:37 | 2026-08-13 08:37 |  |  | Fair | No | Corroded phase at secondary line for 3 wire service ,connection remade with 1 - clamp.voltage left 112/113 and 225V
Outage | J.E.26.08.18383 | C001887309 | Donald Cunningham | St.Catherine | Completed | Load_238037 | Tredegar - 510 | 2026-08-13 07:29 | 2026-08-13 07:32 | 2026-08-13 07:46 | 2026-08-13 07:47 | 2026-08-13 08:57 | 2026-08-13 08:59 | 2026-08-13 09:00 | 2026-08-13 09:00 |  |  | Fair | No | Premises found ok supply restored
Outage | J.E.26.08.18438 | C001887310 | Marlon Authors | St.Elizabeth | Completed | Load_263084 | Maggotty - 210 | 2026-08-13 07:29 | 2026-08-14 09:47 | 2026-08-14 13:00 | 2026-08-14 13:00 | 2026-08-14 13:49 | 2026-08-14 13:38 | 2026-08-14 13:50 | 2026-08-14 13:50 | BrokenWire |  | Fair | No | Customer said supply was restored
Outage | J.E.26.08.18494 | C001887312 | Clyde Brown | Clarendon | Completed | Load_266019 | May Pen - 110 | 2026-08-13 07:29 | 2026-08-13 07:32 | 2026-08-13 12:19 | 2026-08-13 12:51 | 2026-08-13 14:11 | 2026-08-13 14:23 | 2026-08-13 14:27 | 2026-08-13 14:27 | BrokenWire |  | Fair | No | Broken 2 wire service spliced and retention with 15ft-#6 duplex service wire and now ok.
Outage | J.E.26.08.18595 | C001887315 | Clyde Brown | Clarendon | Completed | Load_266797 | May Pen - 110 | 2026-08-13 07:29 | 2026-08-13 07:32 | 2026-08-13 10:29 | 2026-08-13 10:30 | 2026-08-13 12:41 | 2026-08-13 12:43 | 2026-08-13 12:50 | 2026-08-13 12:50 |  | Y | Fair | No | Blown 20 amps junction fuse at Douglas Castle caused by trees near the Baptist Church in the gully need vegetation crew to attend to blown fuse replaced
Outage | J.E.26.08.18700 | C001887314 | Selvin White | St.Elizabeth | Completed | Load_292267 | Maggotty - 210 | 2026-08-13 07:29 | 2026-08-13 07:30 | 2026-08-13 09:11 | 2026-08-13 09:12 | 2026-08-13 09:39 | 2026-08-13 09:42 | 2026-08-13 09:42 | 2026-08-13 09:42 |  |  | Fair | No | The escalation department was contacted and all customers that were affected were restored remotely..
Non-Outage | J.E.26.08.17105 | C001887321 | Elvis Trowers |  | Completed |  |  | 2026-08-13 07:30 | 2026-08-13 07:31 | 2026-08-13 10:24 | 2026-08-13 10:25 | 2026-08-13 10:35 | 2026-08-13 10:40 | 2026-08-13 10:36 | 2026-08-13 10:36 | Fire |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.17850 | C001887318 | Donald Cunningham | St.Catherine | Completed | Load_257696 | Tredegar - 510 | 2026-08-13 07:30 | 2026-08-13 07:32 | 2026-08-13 12:49 | 2026-08-13 12:50 | 2026-08-13 13:20 | 2026-08-13 13:21 | 2026-08-13 13:40 | 2026-08-13 13:40 |  |  | Fair | No | Supply restored
Outage | J.E.26.08.18375 | C001887324 | Ricky Hall | St.Catherine | Completed | Load_241531 | Tredegar - 210 | 2026-08-13 07:30 | 2026-08-14 07:44 | 2026-08-14 10:20 | 2026-08-14 10:21 | 2026-08-14 11:25 | 2026-08-14 11:26 | 2026-08-14 11:34 | 2026-08-14 11:34 | LeaningPole |  | EarthMovement | No | Private pole customer advised
Outage | J.E.26.08.18462 | C001887323 | Donald Cunningham | St.Catherine | Completed | Load_254133 | Tredegar - 310 | 2026-08-13 07:30 | 2026-08-13 07:32 | 2026-08-13 09:01 | 2026-08-13 09:01 | 2026-08-13 09:37 | 2026-08-13 09:37 | 2026-08-13 09:41 | 2026-08-13 09:41 |  |  | Fair | No | Premises found ok supply restored
Outage | J.E.26.08.18589 | C001887317 | Selvin White | St.Elizabeth | Completed | Load_247358 | Maggotty - 110 | 2026-08-13 07:30 | 2026-08-13 07:31 | 2026-08-13 08:13 | 2026-08-13 08:13 | 2026-08-13 08:49 | 2026-08-13 08:57 | 2026-08-13 09:11 | 2026-08-13 09:11 |  |  | Fair | No | Premises found okay however premises was said to be currently unoccupied since the storm.
Outage | J.E.26.08.17983 | C001887325 | Donald Cunningham | St.Catherine | Completed | Load_262367 | Tredegar - 210 | 2026-08-13 07:31 | 2026-08-13 07:32 | 2026-08-13 11:32 | 2026-08-13 11:32 | 2026-08-13 12:33 | 2026-08-13 12:48 | 2026-08-13 12:48 | 2026-08-13 12:48 |  |  | Fair | No | Premises found with supply
Non-Outage | J.E.26.08.18069 | C001887326 | Michael Paterson |  | Completed |  |  | 2026-08-13 07:32 | 2026-08-13 07:33 | 2026-08-13 10:44 | 2026-08-13 10:45 | 2026-08-13 11:41 | 2026-08-13 11:43 | 2026-08-13 11:43 | 2026-08-13 11:43 |  |  | Fair | No | Patrol areas found areas ok contact customer she advise crew that supply restored was was restored
Outage | J.E.26.08.17951 | C001887330 | Edward Royal | KSAS | Completed | Load_255777 | Hunts Bay - 810 | 2026-08-13 07:32 | 2026-08-13 07:33 | 2026-08-13 09:09 | 2026-08-13 09:10 | 2026-08-13 09:09 | 2026-08-13 09:12 | 2026-08-13 09:12 | 2026-08-13 09:12 |  |  | Fair | No | When contacted customer said the power was restored
Outage | J.E.26.08.17999 | C001887328 | Edward Royal | KSAS | Completed | Load_291900 | Hunts Bay - 810 | 2026-08-13 07:32 | 2026-08-13 07:33 | 2026-08-13 09:01 | 2026-08-13 09:01 | 2026-08-13 09:01 | 2026-08-13 09:01 | 2026-08-13 09:01 | 2026-08-13 09:01 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.18200 | C001887327 | Edward Royal | KSAS | Completed | Load_290764 | Hunts Bay - 810 | 2026-08-13 07:32 | 2026-08-13 07:33 | 2026-08-13 09:00 | 2026-08-13 09:00 | 2026-08-13 09:00 | 2026-08-13 09:00 | 2026-08-13 09:01 | 2026-08-13 09:01 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.18211 | C001887329 | Edward Royal | KSAS | Completed | Load_291568 | Hunts Bay - 810 | 2026-08-13 07:32 | 2026-08-13 07:33 | 2026-08-13 09:06 | 2026-08-13 09:07 | 2026-08-13 09:06 | 2026-08-13 09:07 | 2026-08-13 09:09 | 2026-08-13 09:09 |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.08.17774 | C001887332 | Odeanie Davis | KSAS | Completed | Load_240987 | Greenwich - 310 | 2026-08-13 07:34 | 2026-08-13 07:38 | 2026-08-13 10:44 | 2026-08-13 10:44 | 2026-08-13 10:51 | 2026-08-13 11:05 | 2026-08-13 10:59 | 2026-08-13 10:59 | BrokenWire |  | Fair | No | Customer stated that they saw smoke coming from pad mounted transformer after a shower of rain, this was not observed by technician at the time of visit.
Non-Outage | J.E.26.08.03224 | C001887334 | Odeanie Davis | KSAS | Completed | Load_252001 | Duhaney - 410 | 2026-08-13 07:36 | 2026-08-13 07:38 | 2026-08-13 09:19 | 2026-08-13 16:59 | 2026-08-13 16:58 | 2026-08-13 14:07 | 2026-08-13 16:59 | 2026-08-13 16:59 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.03514 | C001887335 | Odeanie Davis | KSAS | Completed | Load_268171 | Rockfort - 210 | 2026-08-13 07:36 | 2026-08-13 07:38 | 2026-08-13 11:25 | 2026-08-13 11:25 | 2026-08-13 11:25 | 2026-08-13 11:35 | 2026-08-13 11:40 | 2026-08-13 11:40 | LowHangingWires |  | Fair | No | 116v/116v & 232v at location, customer stated that when rain fall or work is being done on new apartment building it causes the fuse to open, customer stated that this happens often, customer also stated that they hear sparking sounds from transformer, technician request for transformer to be checked
Non-Outage | J.E.26.08.04493 | C001887336 | Odeanie Davis | KSAS | Completed | Load_301920 | Hunts Bay - 810 | 2026-08-13 07:36 | 2026-08-13 07:38 | 2026-08-13 11:04 | 2026-08-13 17:00 | 2026-08-13 16:59 | 2026-08-13 14:22 | 2026-08-13 17:00 | 2026-08-13 17:00 |  |  | Fair | No
Outage | J.E.26.08.17946 | C001887333 | Hartley Chin | Clarendon | Completed | Load_240881 | Parnassus - 210 | 2026-08-13 07:36 | 2026-08-13 07:46 | 2026-08-13 12:13 | 2026-08-13 12:13 | 2026-08-13 12:15 | 2026-08-13 12:39 | 2026-08-13 12:42 | 2026-08-13 12:42 |  |  | Fair | No | Found blown 10 amp junction . Line patrolled and refused.
Non-Outage | J.E.26.08.04760 | C001887337 | Odeanie Davis | KSAS | Completed | Load_240307 | Greenwich - 510 | 2026-08-13 07:37 | 2026-08-13 07:38 | 2026-08-13 10:14 | 2026-08-13 10:15 | 2026-08-13 10:38 | 2026-08-13 10:43 | 2026-08-13 10:44 | 2026-08-13 10:44 |  |  | Fair | No | 119v/120v & 239v across phases, 209v on 190 phase. Customer and other customers on the same secondary line stated that they are having frequent power outages that interrupts daily production., technician request for transformer to be checked
Outage | J.E.26.08.17535 | C001887338 | Oshane Warren | St.Elizabeth | Completed | Load_557832 | Maggotty - 110 | 2026-08-13 07:37 | 2026-08-13 10:33 | 2026-08-13 15:24 | 2026-08-13 15:25 | 2026-08-13 15:25 | 2026-08-13 15:25 | 2026-08-13 15:27 | 2026-08-13 15:27 |  |  | Fair | No | Hexing metering system refer to field service hexing #07117
Non-Outage | J.E.26.08.18471 | C001887341 | Marlon Brown |  | Completed |  |  | 2026-08-13 07:38 | 2026-08-13 07:44 | 2026-08-13 07:54 | 2026-08-13 07:55 | 2026-08-13 07:54 | 2026-08-13 07:55 | 2026-08-13 07:55 | 2026-08-13 07:55 |  |  | Fair | No | St James call
Outage | J.E.26.08.18235 | C001887343 | Moses Elliston | St.Catherine | Completed | Load_242257 | Tredegar - 410 | 2026-08-13 07:38 | 2026-08-13 07:39 | 2026-08-13 10:18 | 2026-08-13 10:19 | 2026-08-13 10:18 | 2026-08-13 10:19 | 2026-08-13 10:20 | 2026-08-13 10:20 |  |  | Fair | No | Supply ok at Premises.
Outage | J.E.26.08.18572 | C001887342 | Marlon Brown | Trelawny | Completed | Load_292058 | Greenwood - 110 | 2026-08-13 07:38 | 2026-08-13 07:44 | 2026-08-13 07:55 | 2026-08-13 07:56 | 2026-08-13 07:55 | 2026-08-13 07:56 | 2026-08-13 07:56 | 2026-08-13 07:56 |  |  | Fair | No | St James call
Outage | J.E.26.08.18574 | C001887344 | Eric Williams | KSAS | Completed | Load_269807 | Duhaney - 310 | 2026-08-13 07:38 | 2026-08-14 08:32 | 2026-08-14 08:37 | 2026-08-14 08:38 | 2026-08-14 08:52 | 2026-08-14 09:14 | 2026-08-14 09:17 | 2026-08-14 09:17 |  |  | Fair | No | Burnt joints in meter socket, meter disconnected, electrician carrying out repairs
Outage | J.E.26.08.18654 | C001887340 | Marlon Brown | Trelawny | Completed | Load_267437 | Greenwood - 110 | 2026-08-13 07:38 | 2026-08-13 07:44 | 2026-08-13 08:01 | 2026-08-13 08:02 | 2026-08-13 09:05 | 2026-08-13 09:59 | 2026-08-13 09:59 | 2026-08-13 09:59 |  |  | Fair | No | Clean and remake joint at pothead, use 2 linkers Voltage found at meter socket 110vVoltage leaving at meter socket 110/110=220v. Corroded joints.
Non-Outage | J.E.26.08.17754 | C001887345 | Antony Levy | KSAN | Completed | Load_267043 | Washington Blvd - 410 | 2026-08-13 07:40 | 2026-08-13 15:27 | 2026-08-13 22:00 | 2026-08-13 22:01 | 2026-08-13 22:06 | 2026-08-13 22:10 | 2026-08-13 22:10 | 2026-08-13 22:10 |  |  | EarthMovement | No | Premises locked
Non-Outage | J.E.26.08.18023 | C001887346 | Christopher Edwards |  | Completed |  |  | 2026-08-13 07:42 | 2026-08-13 07:43 | 2026-08-14 11:03 | 2026-08-14 15:57 | 2026-08-14 15:57 | 2026-08-14 16:25 | 2026-08-14 16:26 | 2026-08-14 16:26 |  |  | Fair | No | Premises not located Unable to reach customer by phone
Outage | J.E.26.08.17969 | C001887347 | Elvis Trowers | KSAN | Completed | Load_1004249 | Washington Blvd - 810 | 2026-08-13 07:43 | 2026-08-13 07:44 | 2026-08-13 09:09 | 2026-08-13 09:32 | 2026-08-13 09:39 | 2026-08-13 09:50 | 2026-08-13 09:49 | 2026-08-13 09:49 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Non-Outage | J.E.26.08.17301 | C001887349 | Dwain Samuels | Westmoreland | Completed | Load_252248 | Paradise - 110 | 2026-08-13 07:44 | 2026-08-13 07:45 | 2026-08-13 08:14 | 2026-08-13 09:32 | 2026-08-13 09:55 | 2026-08-13 09:57 | 2026-08-13 09:58 | 2026-08-13 09:58 |  |  | Fair | No | Called customer said supply was restored
Non-Outage | J.E.26.08.18355 | C001887348 | Dwain Samuels | Westmoreland | Completed | Load_245695 | Paradise - 210 | 2026-08-13 07:44 | 2026-08-13 07:45 | 2026-08-13 08:14 | 2026-08-13 11:32 | 2026-08-13 11:46 | 2026-08-13 12:03 | 2026-08-13 12:05 | 2026-08-13 12:05 |  |  | Fair | No | Found working okay. Voltage check 116-116-232
Non-Outage | J.E.26.08.17256 | C001887350 | Dwain Samuels | Westmoreland | Completed | Load_268696 | Paradise - 210 | 2026-08-13 07:45 | 2026-08-13 07:46 | 2026-08-13 08:14 | 2026-08-13 10:59 | 2026-08-13 11:04 | 2026-08-13 11:21 | 2026-08-13 11:23 | 2026-08-13 11:23 |  |  | Fair | No | Two pole spand of secondary neutral burnt out. Needs urgent repair and tensioning
Outage | J.E.26.08.18217 | C001887351 | Delano Gayle | St.Catherine | Completed | Load_249216 | Rhodens Pen - 310 | 2026-08-13 07:45 | 2026-08-13 07:46 | 2026-08-13 11:50 | 2026-08-13 11:51 | 2026-08-13 12:21 | 2026-08-13 12:45 | 2026-08-13 12:45 | 2026-08-13 12:45 |  |  | Fair | No | Premises found okay at pothead, voltage readings 115-116-231, advised customer to check breaker when home
Non-Outage | J.E.26.07.39958 | C001887355 | Kemark Slue | St.Catherine | Completed | Load_246331 | New Michelton - 210 | 2026-08-13 07:46 | 2026-08-13 07:47 | 2026-08-13 10:20 | 2026-08-13 10:22 | 2026-08-13 11:12 | 2026-08-13 11:36 | 2026-08-13 11:37 | 2026-08-13 11:37 |  |  | Fair | No | Premises was checked and found ok and left pump running.
Non-Outage | J.E.26.08.18675 | C001887354 | Kemark Slue | St.Catherine | Completed | Load_266641 | Tredegar - 510 | 2026-08-13 07:46 | 2026-08-13 07:47 | 2026-08-13 09:17 | 2026-08-13 09:18 | 2026-08-13 10:13 | 2026-08-13 09:00 | 2026-08-13 10:20 | 2026-08-13 10:20 |  |  | Fair | No | Premises was checked and found leaving a off load voltage reading of 240, 240, 240, 420,420,420V.
Outage | J.E.26.08.18507 | C001887352 | Tyrese Williams | St.Ann | Completed | Load_256141 | Cardiff Hall - 310 | 2026-08-13 07:46 | 2026-08-13 07:47 | 2026-08-13 07:53 | 2026-08-13 07:54 | 2026-08-13 08:00 | 2026-08-13 08:00 | 2026-08-13 08:00 | 2026-08-13 08:00 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.18591 | C001887359 | Ryan Richards | Manchester | Completed | Load_239032 | Spur Tree - 310 | 2026-08-13 07:49 | 2026-08-13 09:05 | 2026-08-13 09:50 | 2026-08-13 09:50 | 2026-08-13 11:14 | 2026-08-13 11:41 | 2026-08-13 11:42 | 2026-08-13 11:42 |  |  | Fair | No | Blown 10 amp fuse found for 100 kva transformer line was checked nothing was found blown 10 amp fuse was replaced
Non-Outage | J.E.26.07.39375 | C001887371 | Royston Montague | St.Catherine | Completed | Load_269368 | Tredegar - 210 | 2026-08-13 07:51 | 2026-08-13 07:53 | 2026-08-13 08:23 | 2026-08-13 11:07 | 2026-08-13 11:23 | 2026-08-13 11:24 | 2026-08-13 11:25 | 2026-08-13 11:25 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.07.39672 | C001887370 | Royston Montague | St.Catherine | Completed | Load_262367 | Tredegar - 210 | 2026-08-13 07:51 | 2026-08-13 07:53 | 2026-08-13 08:23 | 2026-08-13 12:52 | 2026-08-13 13:17 | 2026-08-13 13:21 | 2026-08-13 13:22 | 2026-08-13 13:22 |  |  | Fair | No | Customer confirmed issue resolved resolved.
Non-Outage | J.E.26.07.40232 | C001887369 | Royston Montague | St.Catherine | Completed | Load_261448 | Tredegar - 210 | 2026-08-13 07:51 | 2026-08-13 07:53 | 2026-08-13 08:23 | 2026-08-13 10:32 | 2026-08-13 10:38 | 2026-08-13 10:47 | 2026-08-13 10:48 | 2026-08-13 10:48 |  |  | Fair | No | Full voltage found, not seeing anyone at premises. Voltage at meter socket 225v 111v 112v . Valid phone number required.
Non-Outage | J.E.26.07.40237 | C001887368 | Royston Montague | St.Catherine | Completed | Load_261448 | Tredegar - 210 | 2026-08-13 07:51 | 2026-08-13 07:53 | 2026-08-13 08:23 | 2026-08-13 10:48 | 2026-08-13 10:48 | 2026-08-13 10:49 | 2026-08-13 10:49 | 2026-08-13 10:49 |  |  | Fair | No | Full voltage found at meter socket. 225v 111v 112v , not seeing anyone at home. Valid phone number required.
Non-Outage | J.E.26.08.00889 | C001887367 | Royston Montague | St.Catherine | Completed | Load_255950 | Tredegar - 210 | 2026-08-13 07:51 | 2026-08-13 07:53 | 2026-08-13 08:23 | 2026-08-13 10:52 | 2026-08-13 11:05 | 2026-08-13 11:06 | 2026-08-13 11:06 | 2026-08-13 11:06 |  |  | Fair | No | Service wire was the culprit , same change few weeks ago. Please update thanks.
Non-Outage | J.E.26.08.02285 | C001887366 | Royston Montague | St.Catherine | Completed | Load_242770 | Tredegar - 210 | 2026-08-13 07:51 | 2026-08-13 07:53 | 2026-08-13 08:23 | 2026-08-13 13:23 | 2026-08-13 14:34 | 2026-08-13 14:35 | 2026-08-13 14:35 | 2026-08-13 14:35 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.08.15262 | C001887362 | Royston Montague | St.Catherine | Completed | Load_250677 | Tredegar - 210 | 2026-08-13 07:51 | 2026-08-13 07:53 | 2026-08-13 08:23 | 2026-08-13 08:54 | 2026-08-13 10:24 | 2026-08-13 10:28 | 2026-08-13 10:29 | 2026-08-13 10:29 |  |  | Fair | No | Customer issue is with a faulty street light near premises. Pole number 0063964.
Non-Outage | J.E.26.08.17080 | C001887363 | Royston Montague | St.Catherine | Completed | Load_249979 | Tredegar - 210 | 2026-08-13 07:51 | 2026-08-13 07:53 | 2026-08-13 08:23 | 2026-08-13 12:08 | 2026-08-13 12:14 | 2026-08-13 12:22 | 2026-08-13 12:22 | 2026-08-13 12:22 |  |  | Fair | No | Faulty meter socket. Customer informed to get an electrician to repair same. Voltage 232v 115v 115v
Non-Outage | J.E.26.06.23292 | C001887379 | Royston Montague | St.Catherine | Completed | Load_1001441 | Tredegar - 210 | 2026-08-13 07:52 | 2026-08-13 07:53 | 2026-08-13 08:23 | 2026-08-13 14:36 | 2026-08-13 14:37 | 2026-08-13 14:39 | 2026-08-13 14:39 | 2026-08-13 14:39 |  |  | Fair | No | Rami system, customer said box not working. Please assign to sir Moses thanks
Non-Outage | J.E.26.06.23634 | C001887378 | Royston Montague | St.Catherine | Completed | Load_268733 | Tredegar - 210 | 2026-08-13 07:52 | 2026-08-13 07:53 | 2026-08-13 08:23 | 2026-08-13 15:07 | 2026-08-13 15:09 | 2026-08-14 08:15 | 2026-08-14 08:15 | 2026-08-14 08:15 |  |  | Fair | No | Customer confirmed issue resolved. Please update thanks.
Non-Outage | J.E.26.07.10903 | C001887376 | Royston Montague | St.Catherine | Completed | Load_241531 | Tredegar - 210 | 2026-08-13 07:52 | 2026-08-13 07:53 | 2026-08-13 08:23 | 2026-08-13 12:24 | 2026-08-13 12:42 | 2026-08-13 12:51 | 2026-08-13 12:51 | 2026-08-13 12:51 |  |  | Fair | No | Rami system at premises. Please assign this job to the relevant team thanks.
Non-Outage | J.E.26.07.21585 | C001887374 | Royston Montague | St.Catherine | Completed | Load_574680 | Tredegar - 210 | 2026-08-13 07:52 | 2026-08-13 07:53 | 2026-08-13 08:23 | 2026-08-14 12:42 | 2026-08-14 12:55 | 2026-08-14 12:56 | 2026-08-14 12:56 | 2026-08-14 12:56 |  |  | Fair | No | Customer confirmed a team visited,
Outage | J.E.26.08.18163 | C001887380 | Hartley Chin | Clarendon | Completed | Load_245674 | Parnassus - 210 | 2026-08-13 07:52 | 2026-08-13 07:53 | 2026-08-13 11:45 | 2026-08-13 11:54 | 2026-08-13 11:53 | 2026-08-13 11:54 | 2026-08-13 11:55 | 2026-08-13 11:55 |  |  | Fair | No | Premisis found ok.
Non-Outage | J.E.26.08.06855 | C001887381 | Rodclif Dawkins | Portmore | Completed | Load_265725 | Naggo Head - 510 | 2026-08-13 07:55 | 2026-08-13 08:19 | 2026-08-13 13:15 | 2026-08-13 13:16 | 2026-08-13 13:33 | 2026-08-13 13:33 | 2026-08-13 13:34 | 2026-08-13 13:34 |  |  | Fair | No | Customer found okay
Non-Outage | J.E.26.08.16108 | C001887389 | Rodclif Dawkins | Portmore | Completed | Load_265725 | Naggo Head - 510 | 2026-08-13 07:55 | 2026-08-13 08:19 | 2026-08-13 11:50 | 2026-08-13 12:02 | 2026-08-13 12:46 | 2026-08-13 13:14 | 2026-08-13 13:15 | 2026-08-13 13:15 |  |  | Fair | No | Prem found okay
Non-Outage | J.E.26.08.18587 | C001887392 | Andrae Clarke | Portland | Completed | Load_258738 | Port Antonio - 410 | 2026-08-13 07:57 | 2026-08-13 08:00 | 2026-08-13 08:05 | 2026-08-13 11:14 | 2026-08-13 11:14 | 2026-08-13 11:09 | 2026-08-13 11:35 | 2026-08-13 11:35 |  |  | Fair | No | Check voltage 114/115/229Premises okay
Outage | J.E.26.08.18524 | C001887391 | Hartley Chin | Clarendon | Completed | Load_246105 | Parnassus - 210 | 2026-08-13 07:57 | 2026-08-13 07:58 | 2026-08-13 09:58 | 2026-08-13 09:59 | 2026-08-13 11:34 | 2026-08-13 11:52 | 2026-08-13 11:53 | 2026-08-13 11:53 |  |  | Fair | No | Premisis found ok.
Non-Outage | J.E.26.07.00318 | C001887406 | Orville Lee | Portmore | Completed | Load_252837 | Naggo Head - 510 | 2026-08-13 07:58 | 2026-08-13 08:00 | 2026-08-13 09:24 | 2026-08-13 10:29 | 2026-08-13 10:41 | 2026-08-13 11:18 | 2026-08-13 11:20 | 2026-08-13 11:20 |  |  | Fair | No | Premises found ok upon arrival Issue was resolved by a technician Voltage 115v116v231v
Non-Outage | J.E.26.07.00320 | C001887405 | Orville Lee | Portmore | Completed | Load_243774 | Naggo Head - 510 | 2026-08-13 07:58 | 2026-08-13 08:00 | 2026-08-13 09:24 | 2026-08-13 12:06 | 2026-08-13 12:06 | 2026-08-13 12:06 | 2026-08-13 12:08 | 2026-08-13 12:08 |  |  | Fair | No | Premises found ok upon arrival Issue was solved by a technician Voltage115v116v231v
Non-Outage | J.E.26.07.00527 | C001887404 | Orville Lee | Portmore | Completed | Load_252837 | Naggo Head - 510 | 2026-08-13 07:58 | 2026-08-13 08:00 | 2026-08-13 09:24 | 2026-08-13 09:27 | 2026-08-13 09:42 | 2026-08-13 09:53 | 2026-08-13 09:53 | 2026-08-13 09:53 |  |  | Fair | No | Premise found ok upon arrival. Issue was resolved by a technician Voltage 117V116V234V
Non-Outage | J.E.26.07.05868 | C001887401 | Orville Lee | Portmore | Completed | Load_246278 | Naggo Head - 510 | 2026-08-13 07:58 | 2026-08-13 08:00 | 2026-08-13 09:24 | 2026-08-13 14:24 | 2026-08-13 14:29 | 2026-08-13 14:36 | 2026-08-13 14:38 | 2026-08-13 14:38 |  |  | Fair | No | Premises found ok upon arrival. Customer was reporting outage in the area
Non-Outage | J.E.26.07.09209 | C001887400 | Orville Lee | Portmore | Completed | Load_576172 | Naggo Head - 510 | 2026-08-13 07:58 | 2026-08-13 08:00 | 2026-08-13 09:24 | 2026-08-13 14:41 | 2026-08-13 15:32 | 2026-08-13 16:00 | 2026-08-13 16:02 | 2026-08-13 16:02 |  |  | Fair | No | Corroded clamps at pothead and secondary line changed 3 Penn union and 3 one bolt clamps used Voltage 120V121V242V
Non-Outage | J.E.26.07.11469 | C001887399 | Orville Lee | Portmore | Completed | Load_269534 | Naggo Head - 510 | 2026-08-13 07:58 | 2026-08-13 08:00 | 2026-08-13 09:24 | 2026-08-13 13:31 | 2026-08-13 13:30 | 2026-08-13 13:31 | 2026-08-13 13:32 | 2026-08-13 13:32 |  |  | Fair | No | Checks made and found secondary line corroded Three oneThree one bolt clamp usedVoltage 119v120v239v
Non-Outage | J.E.26.07.11685 | C001887397 | Orville Lee | Portmore | Completed | Load_259464 | Naggo Head - 510 | 2026-08-13 07:58 | 2026-08-13 08:00 | 2026-08-13 09:24 | 2026-08-13 14:02 | 2026-08-13 14:04 | 2026-08-13 14:18 | 2026-08-13 14:20 | 2026-08-13 14:20 |  |  | Fair | No | Premises found ok upon arrival Issue was resolved by a technician Voltage 116v117v234v
Non-Outage | J.E.26.07.11890 | C001887395 | Orville Lee | Portmore | Completed | Load_255528 | Naggo Head - 510 | 2026-08-13 07:58 | 2026-08-13 08:00 | 2026-08-13 09:24 | 2026-08-13 13:53 | 2026-08-13 13:55 | 2026-08-13 13:58 | 2026-08-13 14:00 | 2026-08-13 14:00 |  |  | Fair | No | Customer mentioned that his report was about a defective street light not showing any light
Non-Outage | J.E.26.07.12036 | C001887394 | Orville Lee | Portmore | Completed | Load_269534 | Naggo Head - 510 | 2026-08-13 07:58 | 2026-08-13 08:00 | 2026-08-13 09:24 | 2026-08-13 12:57 | 2026-08-13 12:57 | 2026-08-13 13:29 | 2026-08-13 13:29 | 2026-08-13 13:29 |  |  | Fair | No | Checks made and found secondary line corroded Three one bolt clamp usedVoltage 119v120v240v
Non-Outage | J.E.26.08.15797 | C001887407 | Error Coore | Manchester | Completed | Load_292371 | Spur Tree - 310 | 2026-08-13 07:58 | 2026-08-13 08:00 | 2026-08-14 12:22 | 2026-08-14 12:23 | 2026-08-14 13:06 | 2026-08-14 14:13 | 2026-08-14 14:18 | 2026-08-14 14:18 |  |  | Fair | No | Premises not found no getting customer on phone
Non-Outage | J.E.26.08.16472 | C001887393 | Error Coore | Manchester | Completed | Load_251668 | Spur Tree - 310 | 2026-08-13 07:58 | 2026-08-13 07:58 | 2026-08-13 08:05 | 2026-08-13 08:15 | 2026-08-13 08:55 | 2026-08-13 09:10 | 2026-08-13 09:12 | 2026-08-13 09:12 |  |  | Fair | No | Premises found ok customer have internal problem voltage reading 120/117/237 volts
Outage | J.E.26.08.18705 | C001887396 | Hartley Chin | Clarendon | Completed | Load_258199 | Parnassus - 210 | 2026-08-13 07:58 | 2026-08-13 07:59 | 2026-08-13 12:01 | 2026-08-13 12:03 | 2026-08-13 12:02 | 2026-08-13 12:04 | 2026-08-13 12:07 | 2026-08-13 12:07 |  |  | Fair | No | Call related to job # 18691
Non-Outage | J.E.26.08.18611 | C001887411 | Swon Miller |  | Completed |  |  | 2026-08-13 07:59 | 2026-08-13 08:00 | 2026-08-13 10:10 | 2026-08-13 10:11 | 2026-08-13 10:33 | 2026-08-11 10:48 | 2026-08-13 10:49 | 2026-08-13 10:49 |  |  | Fair | No | Check and found okay customer states that power supply was restored voltage found 115/114/230 voltage 115/114/230
Non-Outage | J.E.26.08.18734 | C001887409 | Swon Miller |  | Completed |  |  | 2026-08-13 07:59 | 2026-08-13 08:00 | 2026-08-13 08:12 | 2026-08-13 08:13 | 2026-08-13 09:00 | 2026-08-11 09:50 | 2026-08-13 09:51 | 2026-08-13 09:51 | BrokenPole |  | Fair | No | No broken pole found
Outage | J.E.26.08.18594 | C001887412 | Swon Miller | St.James | Completed | Load_252132 | Bogue - 510 | 2026-08-13 07:59 | 2026-08-13 08:00 | 2026-08-13 10:11 | 2026-08-13 10:50 | 2026-08-13 11:02 | 2026-08-25 11:18 | 2026-08-13 11:20 | 2026-08-13 11:20 |  |  | Fair | No | Check and found okay customer states that power supply was restored voltage found 115/115/231 voltage left 115/115/231
Outage | J.E.26.08.18666 | C001887410 | Swon Miller | St.James | Completed | Load_302338 | Queens Drive - 710 | 2026-08-13 07:59 | 2026-08-13 08:00 | 2026-08-13 09:51 | 2026-08-13 09:52 | 2026-08-13 09:51 | 2026-08-19 10:05 | 2026-08-13 10:05 | 2026-08-13 10:05 |  |  | Fair | No | Found customer single phasing cause by burnt hampack open 25 kva transformer to carry out repairs clean and remake joints use 2 pg voltage found 115/22 voltage left 116/115/232
Outage | J.E.26.08.18691 | C001887408 | Hartley Chin | Clarendon | Completed | Load_405730 | Parnassus - 210 | 2026-08-13 07:59 | 2026-08-13 08:00 | 2026-08-13 08:08 | 2026-08-13 08:08 | 2026-08-13 08:48 | 2026-08-13 09:35 | 2026-08-13 09:37 | 2026-08-13 09:37 |  | Y | Fair | No | Found 20 amp Tripsaver open @0094968 due tree contact. Remove tree and close Tripsaver
Non-Outage | J.E.26.08.04197 | C001887420 | Orville Lee | Portmore | Completed | Load_269534 | Naggo Head - 510 | 2026-08-13 08:00 | 2026-08-13 08:01 | 2026-08-13 09:24 | 2026-08-13 13:32 | 2026-08-13 13:34 | 2026-08-13 13:43 | 2026-08-13 13:43 | 2026-08-13 13:43 | Fire |  | Fair | No | Premises found ok upon arrival Customer was reporting seeing sparks above transformer Upon arrival no sparks seen Voltage 117v118v237v
Outage | J.E.26.08.18728 | C001887421 | Shawn Medley | St.James | Completed | Load_238867 | Bogue - 610 | 2026-08-13 08:00 | 2026-08-13 08:02 | 2026-08-13 10:29 | 2026-08-13 10:30 | 2026-08-13 11:45 | 2026-08-13 12:01 | 2026-08-13 12:11 | 2026-08-13 12:11 |  |  | Fair | No | Premises found okay meter is on and advancing 110v 110v 240v
Outage | J.E.26.08.18633 | C001887422 | Horace Malcolm | St.James | Completed | Load_247062 | Bogue - 310 | 2026-08-13 08:03 | 2026-08-13 08:04 | 2026-08-13 08:10 | 2026-08-13 08:10 | 2026-08-13 10:13 | 2026-08-13 10:36 | 2026-08-13 10:36 | 2026-08-13 10:36 |  |  | Fair | No | Check and found premises ok voltage 114-116-230 area check and found ok supply restored
Non-Outage | J.E.26.08.18471 | C001887424 | Swon Miller |  | Completed |  |  | 2026-08-13 08:04 | 2026-08-13 08:16 | 2026-08-13 10:21 | 2026-08-13 16:39 | 2026-08-13 17:20 | 2026-08-19 07:17 | 2026-08-13 19:21 | 2026-08-13 19:21 |  |  | Fair | No | Check and found area okay voltage found 116/117/234 customer states that power supply has been restored voltage left 116/117/234
Outage | J.E.26.08.18572 | C001887425 | Swon Miller | Trelawny | Completed | Load_292058 | Greenwood - 110 | 2026-08-13 08:04 | 2026-08-13 08:16 | 2026-08-13 10:13 | 2026-08-13 11:21 | 2026-08-13 11:44 | 2026-08-13 00:10 | 2026-08-13 12:14 | 2026-08-13 12:14 |  |  | Fair | No | Check and found okay voltage found 117/117/234 customer states that the power supply was restored this morning voltage left 117/117/234
Non-Outage | J.E.26.07.37722 | C001887427 | Oraine Minto | St.Ann | Completed | Load_249971 | Cardiff Hall - 310 | 2026-08-13 08:08 | 2026-08-13 08:09 | 2026-08-13 09:21 | 2026-08-13 11:02 | 2026-08-13 11:02 | 2026-08-13 11:03 | 2026-08-13 11:06 | 2026-08-13 11:06 |  |  | Fair | No | Power restored
Non-Outage | J.E.26.07.37754 | C001887428 | Oraine Minto | St.Ann | Completed | Load_246982 | Cardiff Hall - 310 | 2026-08-13 08:08 | 2026-08-13 08:09 | 2026-08-13 14:00 | 2026-08-13 14:00 | 2026-08-13 14:00 | 2026-08-13 14:00 | 2026-08-13 14:01 | 2026-08-13 14:01 |  |  | Fair | No | Power was restored
Non-Outage | J.E.26.07.37803 | C001887429 | Oraine Minto | St.Ann | Completed | Load_255700 | Cardiff Hall - 310 | 2026-08-13 08:09 | 2026-08-13 08:09 | 2026-08-13 11:07 | 2026-08-13 12:37 | 2026-08-13 12:37 | 2026-08-13 12:37 | 2026-08-13 12:37 | 2026-08-13 12:37 |  |  | Fair | No | Issue resolved
Non-Outage | J.E.26.08.12938 | C001887430 | Oraine Minto | St.Ann | Completed | Load_244118 | Cardiff Hall - 310 | 2026-08-13 08:10 | 2026-08-13 08:11 | 2026-08-13 14:19 | 2026-08-13 14:19 | 2026-08-13 14:23 | 2026-08-13 14:23 | 2026-08-13 14:24 | 2026-08-13 14:24 |  |  | EarthMovement | No | 1 one bolt clamp was used 234v 117v 117v
Non-Outage | J.E.26.08.13010 | C001887431 | Oraine Minto | St.Ann | Completed | Load_245322 | Cardiff Hall - 310 | 2026-08-13 08:10 | 2026-08-13 08:11 | 2026-08-14 08:15 | 2026-08-14 11:33 | 2026-08-14 11:33 | 2026-08-14 11:33 | 2026-08-14 11:36 | 2026-08-14 11:36 |  |  | Fair | No | Refer to emergency Transformer output is 210v 105v 105v
Non-Outage | J.E.26.08.13242 | C001887435 | Oraine Minto | St.Ann | Completed | Load_247013 | Cardiff Hall - 310 | 2026-08-13 08:10 | 2026-08-13 08:11 | 2026-08-14 08:15 | 2026-08-14 11:59 | 2026-08-14 11:59 | 2026-08-14 12:00 | 2026-08-14 12:01 | 2026-08-14 12:01 |  |  | Fair | No | Issue resolved
Outage | J.E.26.08.18229 | C001887436 | Cliton Henry | St.Mary | Completed | Load_239531 | Oracabessa - 210 | 2026-08-13 08:11 | 2026-08-13 08:13 | 2026-08-13 08:22 | 2026-08-13 09:07 | 2026-08-13 09:07 | 2026-08-13 09:08 | 2026-08-13 09:09 | 2026-08-13 09:09 |  |  | Fair | No | Unable to locate customer, this report need a local contact and proper a direction
Non-Outage | J.E.26.08.17153 | C001887437 | Hartley Chin | Clarendon | Completed | Load_405727 | Parnassus - 210 | 2026-08-13 08:12 | 2026-08-13 08:12 | 2026-08-13 12:42 | 2026-08-13 12:43 | 2026-08-13 13:23 | 2026-08-13 13:24 | 2026-08-13 13:26 | 2026-08-13 13:26 | BangingWires |  | Fair | No | Found leaning 40 foot pole with bank of three 100 KVA transformer. Refer to maintenance
Outage | J.E.26.08.17713 | C001887442 | Selvin White | St.Elizabeth | Completed | Load_255506 | Maggotty - 210 | 2026-08-13 08:16 | 2026-08-13 08:17 | 2026-08-13 09:42 | 2026-08-13 09:43 | 2026-08-13 11:36 | 2026-08-13 13:44 | 2026-08-13 13:44 | 2026-08-13 13:44 |  |  | Fair | No | Replace a defective 10 KVA transformer with a 15 KVA transformer at Haughton Housing Scheme at pole number 0180325. Voltage readings left at secondary are 120,120,240 volts . Load readings left at transformer drop leads are 5.3 and 4.9 amps on phases and 1.0 amp in the neutral drop lead. Supply restored to the affected customers.
Outage | J.E.26.08.18325 | C001887441 | Dean- Smith | Hanover | Completed | Load_238848 | Orange Bay - 310 | 2026-08-13 08:16 | 2026-08-13 08:17 | 2026-08-14 09:13 | 2026-08-14 13:36 | 2026-08-14 14:54 | 2026-08-14 14:54 | 2026-08-14 14:55 | 2026-08-14 14:55 | BrokenWire |  | Fair | No | Customer broken meter pole, advised to fix
Outage | J.E.26.08.18171 | C001887444 | Rodclif Dawkins | Portmore | Completed | Load_242652 | Naggo Head - 510 | 2026-08-13 08:19 | 2026-08-13 08:20 | 2026-08-13 09:00 | 2026-08-13 09:00 | 2026-08-13 09:35 | 2026-08-13 11:40 | 2026-08-13 11:47 | 2026-08-13 11:47 |  |  | Fair | No | On location crew found blown fuse from 3phase line section. On close observation 3 dropout switches were defective. Line section was isolated by opening (3) 50amp trip savers and applying short and ground. Using 3 dropout switches and 6ft of #4 copper. Repairs were done. Short and ground removed and line section energized.
Non-Outage | J.E.26.08.17396 | C001887451 | Roemello Brown | Trelawny | Completed | Load_260728 | Martha Brae - 110 | 2026-08-13 08:20 | 2026-08-13 08:21 | 2026-08-14 12:20 | 2026-08-14 12:26 | 2026-08-14 13:01 | 2026-08-14 13:01 | 2026-08-14 13:18 | 2026-08-14 13:18 |  |  | Fair | No | Went to the area ask around the area no one knows the person also customer needs to up date proper directions an landmark please also phone number ring an went to voicemail call the number about 4 times
Non-Outage | J.E.26.08.17537 | C001887450 | Roemello Brown | Trelawny | Completed | Load_292370 | Greenwood - 210 | 2026-08-13 08:20 | 2026-08-13 08:21 | 2026-08-14 09:07 | 2026-08-14 15:22 | 2026-08-14 15:21 | 2026-08-14 15:21 | 2026-08-14 15:22 | 2026-08-14 15:22 |  |  | Fair | No | Premises found working okayVoltage found 110Voltage leave 110
Non-Outage | J.E.26.08.18227 | C001887449 | Roemello Brown | Trelawny | Completed | Load_302817 | Duncans - 110 | 2026-08-13 08:20 | 2026-08-13 08:21 | 2026-08-13 12:05 | 2026-08-13 12:05 | 2026-08-13 14:10 | 2026-08-13 14:10 | 2026-08-13 14:32 | 2026-08-13 14:32 |  |  | Fair | No | Customer meter burn up needs field service team to have meter change Voltage found 113/114/227Voltage leave 113/114/227
Non-Outage | J.E.26.08.18412 | C001887448 | Roemello Brown | Trelawny | Completed | Load_240148 | Greenwood - 210 | 2026-08-13 08:20 | 2026-08-13 08:21 | 2026-08-13 10:16 | 2026-08-13 10:16 | 2026-08-13 10:49 | 2026-08-13 10:49 | 2026-08-13 11:20 | 2026-08-13 11:20 |  |  | Fair | No | Corrosion at the pothead have 3 linkets installed Voltage found 119/118/237Voltage leave 118/118/236
Non-Outage | J.E.26.08.18715 | C001887447 | Roemello Brown | Trelawny | Completed | Load_293023 | Greenwood - 210 | 2026-08-13 08:20 | 2026-08-13 08:21 | 2026-08-14 09:07 | 2026-08-14 14:15 | 2026-08-14 14:28 | 2026-08-14 14:30 | 2026-08-14 14:32 | 2026-08-14 14:32 |  |  | Fair | No | Premises found working okayVoltage found 107/110/217Voltage leave 107/110/217
Non-Outage | J.E.26.08.17077 | C001887454 | Roemello Brown | Trelawny | Completed | Load_255254 | Duncans - 110 | 2026-08-13 08:21 | 2026-08-13 08:26 | 2026-08-14 09:11 | 2026-08-14 10:45 | 2026-08-14 11:13 | 2026-08-14 11:23 | 2026-08-14 11:27 | 2026-08-14 11:27 |  | Y | Fair | No | Premises found working ok Voltage found 120/117/237Voltage leave 120/117/237
Non-Outage | J.E.26.08.17224 | C001887453 | Roemello Brown | Trelawny | Completed | Load_246819 | Duncans - 210 | 2026-08-13 08:21 | 2026-08-13 08:21 | 2026-08-14 10:05 | 2026-08-14 10:06 | 2026-08-14 10:29 | 2026-08-14 10:36 | 2026-08-14 10:39 | 2026-08-14 10:39 | LeaningPole |  | Fair | No | Customer reporting leaning pole please send maintenance team to have pole rectify pole foot rotten out Voltage found 116/115/231Voltage leave 16/115/231
Non-Outage | J.E.26.08.17061 | C001887461 | Junior Scarlett | St.James | Completed | Load_240704 | Rose Hall - 110 | 2026-08-13 08:24 | 2026-08-13 08:25 | 2026-08-13 08:34 | 2026-08-14 09:10 | 2026-08-14 10:09 | 2026-08-14 10:20 | 2026-08-14 10:21 | 2026-08-14 10:21 |  |  | Fair | No | Refer to field service Defective meter Meter burnVoltage found 114v 114v 228vVoltage leave 114v 114v 228vMeter socket defective
Non-Outage | J.E.26.08.17540 | C001887462 | Junior Scarlett | St.James | Completed | Load_241675 | Bogue - 310 | 2026-08-13 08:24 | 2026-08-13 08:25 | 2026-08-13 08:34 | 2026-08-13 13:09 | 2026-08-13 13:22 | 2026-08-13 13:54 | 2026-08-13 13:58 | 2026-08-13 13:58 |  |  | Fair | No | Refer to field service EG systemNo number on box Box near by number 0426Voltage from transformer 115v 114v 229v
Non-Outage | J.E.26.08.17956 | C001887460 | Junior Scarlett | St.James | Completed | Load_247062 | Bogue - 310 | 2026-08-13 08:24 | 2026-08-13 08:25 | 2026-08-13 08:34 | 2026-08-13 12:12 | 2026-08-13 12:53 | 2026-08-13 13:07 | 2026-08-13 13:07 | 2026-08-13 13:07 |  |  | Fair | No | Check and found okVoltage found 115v 115v 230v
Non-Outage | J.E.26.08.18366 | C001887459 | Junior Scarlett | St.James | Completed | Load_259998 | Queens Drive - 710 | 2026-08-13 08:24 | 2026-08-13 08:25 | 2026-08-13 08:34 | 2026-08-13 09:24 | 2026-08-13 10:03 | 2026-08-13 10:50 | 2026-08-13 10:55 | 2026-08-13 10:55 |  |  | Fair | No | Broken neutral Corrosion at pole and potheadReattach wire clean corrosionInstall 4 clamp and two pen unionVoltage found 86v 104v 200vVoltage leave 108v 108v 216v
Non-Outage | J.E.26.08.18407 | C001887458 | Junior Scarlett | St.James | Completed | Load_248155 | Queens Drive - 710 | 2026-08-13 08:24 | 2026-08-13 08:25 | 2026-08-13 08:34 | 2026-08-13 15:40 | 2026-08-13 15:40 | 2026-08-13 03:57 | 2026-08-13 15:56 | 2026-08-13 15:56 |  |  | Fair | No | Unable to locate Voltage from transformer 115v 115v 230v
Non-Outage | J.E.26.08.18665 | C001887457 | Swon Miller | St.James | Completed | Load_302338 | Queens Drive - 710 | 2026-08-13 08:24 | 2026-08-13 09:33 | 2026-08-13 10:07 | 2026-08-13 10:08 | 2026-08-13 10:08 | 2026-08-12 10:10 | 2026-08-13 10:10 | 2026-08-13 10:10 |  |  | Fair | No | Call related to previous
Non-Outage | J.E.26.08.18727 | C001887456 | Junior Scarlett | St.James | Completed | Load_246347 | Queens Drive - 710 | 2026-08-13 08:24 | 2026-08-13 08:25 | 2026-08-13 08:34 | 2026-08-13 10:58 | 2026-08-13 11:27 | 2026-08-13 11:53 | 2026-08-13 11:53 | 2026-08-13 11:53 |  |  | Fair | No | Premesis found Unable to locate Voltage found 110v 111v 221v
Outage | J.E.26.08.18690 | C001887465 | Hartley Chin | Clarendon | Completed | Load_266577 | Parnassus - 210 | 2026-08-13 08:26 | 2026-08-13 08:27 | 2026-08-13 11:58 | 2026-08-13 12:07 | 2026-08-13 12:07 | 2026-08-13 12:07 | 2026-08-13 12:08 | 2026-08-13 12:08 |  |  | Fair | No | Call related to job # 18691
Non-Outage | J.E.26.08.17853 | C001887467 | Fitzroy Turner |  | Completed |  |  | 2026-08-13 08:30 | 2026-08-13 15:38 | 2026-08-13 21:31 | 2026-08-13 21:32 | 2026-08-13 21:31 | 2026-08-13 21:32 | 2026-08-13 21:33 | 2026-08-13 21:33 |  |  | Fair | No | Customer supply restored after replace defective drop switch and one 10 amps fuse
Non-Outage | J.E.26.08.18295 | C001887472 | Rayon Foster | Hanover | Completed | Load_238086 | Orange Bay - 310 | 2026-08-13 08:31 | 2026-08-13 08:33 | 2026-08-13 08:40 | 2026-08-13 08:57 | 2026-08-13 10:17 | 2026-08-13 10:37 | 2026-08-13 10:37 | 2026-08-13 10:37 |  |  | Fair | No | Voltage check on arrival in meter socket 114/113AB227volts customer meter burn on the right side causing single phasing refer to field service to have meter change
Non-Outage | J.E.26.08.18433 | C001887471 | Rayon Foster | Hanover | Completed | Load_242280 | Orange Bay - 310 | 2026-08-13 08:31 | 2026-08-13 08:33 | 2026-08-13 08:40 | 2026-08-13 10:43 | 2026-08-13 11:08 | 2026-08-13 12:12 | 2026-08-13 12:12 | 2026-08-13 12:12 |  |  | Fair | No | Corrosion on customer pathead and jps light poles repair with two linkets and two one bolt clamps voltage check at meter 110/111AB221volts
Non-Outage | J.E.26.08.18738 | C001887470 | Delano Gayle | St.Catherine | Completed | Load_412847 | Rhodens Pen - 410 | 2026-08-13 08:31 | 2026-08-13 08:31 | 2026-08-13 09:04 | 2026-08-13 09:04 | 2026-08-13 09:31 | 2026-08-13 10:07 | 2026-08-13 10:07 | 2026-08-13 10:07 |  |  | Fair | No | Blown 25amps junction on main no pole#, replace 25amps
Outage | J.E.26.08.18724 | C001887469 | Rusean Allen | KSAS | Completed | Load_247260 | Hunts Bay - 210 | 2026-08-13 08:31 | 2026-08-13 08:31 | 2026-08-13 09:47 | 2026-08-13 09:48 | 2026-08-13 10:15 | 2026-08-13 10:19 | 2026-08-13 10:19 | 2026-08-13 10:19 |  |  | Fair | No | 2x defective extra tall fuse barrel found and needs to be changed
Non-Outage | J.E.26.08.18767 | C001887474 | Andrae Clarke | Portland | Completed | Load_268491 | Port Antonio - 310 | 2026-08-13 08:32 | 2026-08-13 08:34 | 2026-08-13 12:03 | 2026-08-13 12:49 | 2026-08-13 13:21 | 2026-08-13 13:35 | 2026-08-13 13:26 | 2026-08-13 13:26 | LeaningPole |  | Fair | No | Premises not found made several phone calls to the number and not getting any response
Non-Outage | J.E.26.08.17189 | C001887488 | Odaine Johnson | Clarendon | Completed | Load_264346 | Parnassus - 210 | 2026-08-13 08:39 | 2026-08-13 08:40 | 2026-08-13 10:26 | 2026-08-13 14:50 | 2026-08-13 15:23 | 2026-08-13 15:35 | 2026-08-13 15:38 | 2026-08-13 15:38 |  |  | Fair | No | Premises found okay voltage reading A115 B109 AB224
Non-Outage | J.E.26.08.17237 | C001887487 | Odaine Johnson | Clarendon | Completed | Load_242828 | May Pen - 110 | 2026-08-13 08:39 | 2026-08-13 08:40 | 2026-08-13 10:26 | 2026-08-13 15:38 | 2026-08-13 15:38 | 2026-08-13 15:39 | 2026-08-13 15:39 | 2026-08-13 15:39 |  |  | EarthMovement | No | Try contact customer but no one answer and no proper direction was given
Non-Outage | J.E.26.08.17369 | C001887489 | Odaine Johnson | Clarendon | Completed | Load_246105 | Parnassus - 210 | 2026-08-13 08:39 | 2026-08-13 08:40 | 2026-08-13 10:26 | 2026-08-14 11:48 | 2026-08-14 15:08 | 2026-08-14 01:00 | 2026-08-14 15:09 | 2026-08-14 15:09 |  |  | Fair | No | Corrosion found at pole remade connection using 1 one bolt clamp voltage reading 114/116/230 volts
Non-Outage | J.E.26.08.17421 | C001887491 | Odaine Johnson | Clarendon | Completed | Load_354585 | May Pen - 110 | 2026-08-13 08:39 | 2026-08-13 08:40 | 2026-08-13 10:26 | 2026-08-13 13:17 | 2026-08-13 13:16 | 2026-08-13 13:17 | 2026-08-13 13:17 | 2026-08-13 13:17 |  |  | Fair | No | Location not found in Clarendon
Non-Outage | J.E.26.08.17423 | C001887493 | Odaine Johnson | Clarendon | Completed | Load_351882 | May Pen - 110 | 2026-08-13 08:39 | 2026-08-13 08:40 | 2026-08-13 10:26 | 2026-08-13 11:25 | 2026-08-13 12:24 | 2026-08-13 12:32 | 2026-08-13 12:33 | 2026-08-13 12:33 |  |  | Fair | No | Premises found okay voltage reading 110 volts
Non-Outage | J.E.26.08.17858 | C001887492 | Odaine Johnson | Clarendon | Completed | Load_257023 | Parnassus - 310 | 2026-08-13 08:39 | 2026-08-13 08:40 | 2026-08-13 10:26 | 2026-08-14 11:00 | 2026-08-14 11:01 | 2026-08-14 11:02 | 2026-08-14 11:02 | 2026-08-14 11:02 |  |  | Fair | No | Customer stated that the issue was resolved
Non-Outage | J.E.26.08.18032 | C001887490 | Odaine Johnson | Clarendon | Completed | Load_247989 | May Pen - 110 | 2026-08-13 08:39 | 2026-08-13 08:40 | 2026-08-13 10:26 | 2026-08-13 12:34 | 2026-08-13 13:02 | 2026-08-13 13:14 | 2026-08-13 13:16 | 2026-08-13 13:16 |  |  | Fair | No | Transformer drop lead burn causing area to experiencing low transformer pole number 0106485 voltage reading 115/90/205 volts
Non-Outage | J.E.26.08.17547 | C001887502 | Hopeton Henry | St.Thomas | Completed | Load_250144 | Good Year - 110 | 2026-08-13 08:40 | 2026-08-13 08:54 | 2026-08-13 10:12 | 2026-08-13 11:25 | 2026-08-13 12:34 | 2026-08-13 12:42 | 2026-08-13 12:42 | 2026-08-13 12:42 |  |  | Fair | No | Found ok,
Non-Outage | J.E.26.07.33412 | C001887519 | Cliton Henry | St.Mary | Completed | Load_350817 | Oracabessa - 110 | 2026-08-13 08:53 | 2026-08-13 08:55 | 2026-08-13 09:24 | 2026-08-13 09:24 | 2026-08-13 09:43 | 2026-08-13 09:59 | 2026-08-13 09:59 | 2026-08-13 09:59 |  |  | Fair | No | A wrapped joint found at pole and disconnected service wire phase conductor found at the customer’s pothead. Both joints were reconnected using two one bolt clamps. Voltages left 115-116/232 volts
Non-Outage | J.E.26.07.07997 | C001887527 | Locksley Allen | St.Ann | Completed | Load_270005 | Blackstonedge - 110 | 2026-08-13 08:58 | 2026-08-13 08:59 | 2026-08-13 11:21 | 2026-08-13 13:43 | 2026-08-13 13:42 | 2026-08-13 13:53 | 2026-08-13 13:51 | 2026-08-13 13:51 |  |  | Fair | No | Meter 2539046 not found. Meter seen 3022342Voltage at meter socket phase to phase 238v. Phase to neutral 117&118vMeter left working okay
Outage | J.E.26.08.17103 | C001887528 | Donald Cunningham | St.Catherine | Completed | Load_249334 | Tredegar - 210 | 2026-08-13 09:00 | 2026-08-13 09:00 | 2026-08-13 09:48 | 2026-08-13 09:48 | 2026-08-13 11:01 | 2026-08-13 11:30 | 2026-08-13 11:31 | 2026-08-13 11:31 | LowHangingWires |  | Fair | No | Broken service neural splice and retention using 3 clamps and 4 feet of service neural for repair voltage readings 114/2/228
Outage | J.E.26.08.18796 | C001887536 | Raymond Lewis | St.Ann | Completed | Load_269625 | Roaring River - 410 | 2026-08-13 09:03 | 2026-08-13 09:04 | 2026-08-13 09:41 | 2026-08-13 09:42 | 2026-08-13 09:55 | 2026-08-13 09:57 | 2026-08-13 09:57 | 2026-08-13 09:57 | BangingWires |  | Fair | No | Premises close
Outage | J.E.26.08.18781 | C001887556 | Neckell Ormsby | St.Mary | Completed | Load_238169 | Annotto Bay - 210 | 2026-08-13 09:12 | 2026-08-13 09:14 | 2026-08-13 09:24 | 2026-08-13 09:25 | 2026-08-13 10:11 | 2026-08-13 10:17 | 2026-08-13 10:17 | 2026-08-13 10:17 |  |  | Fair | No | Found X ing box at location customer said a team went in the box yesterday and no supply since, others affected as well please refer to field service
Outage | J.E.26.08.18784 | C001887569 | Hartley Chin | Clarendon | Completed | Load_252945 | Parnassus - 210 | 2026-08-13 09:17 | 2026-08-13 09:18 | 2026-08-13 12:01 | 2026-08-13 12:09 | 2026-08-13 12:08 | 2026-08-13 12:09 | 2026-08-13 12:10 | 2026-08-13 12:10 | BrokenWire |  | Fair | No | Call related to job #18691
Non-Outage | J.E.26.08.18795 | C001887590 | Rusean Allen |  | Completed |  |  | 2026-08-13 09:25 | 2026-08-13 09:29 | 2026-08-13 09:41 | 2026-08-13 10:34 | 2026-08-13 10:54 | 2026-08-13 11:08 | 2026-08-13 11:09 | 2026-08-13 11:09 |  |  | Fair | No | 1x 30amp fuse found 1x 30amp fuse replaced
Outage | J.E.26.08.18770 | C001887591 | Ryan Richards | Manchester | Completed | Load_240606 | Spur Tree - 310 | 2026-08-13 09:26 | 2026-08-13 09:38 | 2026-08-13 11:47 | 2026-08-13 12:05 | 2026-08-13 12:30 | 2026-08-13 12:33 | 2026-08-13 12:33 | 2026-08-13 12:33 | Fire |  | Fair | No | Burn main service entry found at premises customer charged over switch transfer switch found customer was advised to carry out repair then contact are visit office
Outage | J.E.26.08.18815 | C001887594 | Edward Royal | KSAN | Completed | Load_267241 | Washington Blvd - 310 | 2026-08-13 09:29 | 2026-08-13 09:52 | 2026-08-13 11:51 | 2026-08-13 11:51 | 2026-08-13 11:51 | 2026-08-13 11:52 | 2026-08-13 11:54 | 2026-08-13 11:54 |  |  | Fair | No | Meter not responding meter need to be check reffered to field service
Outage | J.E.26.08.18816 | C001887592 | Denton Williams | Portland | Completed | Load_244251 | Port Antonio - 310 | 2026-08-13 09:29 | 2026-08-13 09:30 | 2026-08-13 09:44 | 2026-08-13 09:44 | 2026-08-13 11:41 | 2026-08-13 12:47 | 2026-08-13 12:50 | 2026-08-13 12:50 | BrokenWire |  | Fair | No | Broken service neutral. Splice and reconnect using two one bolt. Voltage readings leave 114v, 117v & 232v.
Outage | J.E.26.08.18820 | C001887593 | Swon Miller | St.James | Completed | Load_240140 | Queens Drive - 310 | 2026-08-13 09:29 | 2026-08-13 09:33 | 2026-08-13 12:14 | 2026-08-13 12:14 | 2026-08-13 12:40 | 2026-08-18 01:25 | 2026-08-13 13:25 | 2026-08-13 13:25 |  |  | Fair | No | Found customer single phasing due to service wire defective voltage found 113/ splice and retention customer service wire use about 15ft#6 triplex 2linket red to red to carry out repairs voltage left 115/113/229
Outage | J.E.26.08.17806 | C001887618 | Edward Royal | KSAS | Completed | Load_241577 | Three Miles - 410 | 2026-08-13 09:49 | 2026-08-13 09:52 | 2026-08-13 11:48 | 2026-08-13 11:49 | 2026-08-13 11:48 | 2026-08-13 11:50 | 2026-08-13 11:51 | 2026-08-13 11:51 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.17815 | C001887619 | Edward Royal | KSAN | Completed | Load_269564 | Washington Blvd - 310 | 2026-08-13 09:49 | 2026-08-13 09:52 | 2026-08-13 10:22 | 2026-08-13 10:22 | 2026-08-13 10:22 | 2026-08-13 10:22 | 2026-08-13 10:22 | 2026-08-13 10:22 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.18850 | C001887617 | Eric Williams | KSAS | Completed | Load_238539 | Duhaney - 310 | 2026-08-13 09:49 | 2026-08-13 09:52 | 2026-08-13 10:37 | 2026-08-13 10:37 | 2026-08-13 10:38 | 2026-08-13 11:09 | 2026-08-13 11:10 | 2026-08-13 11:10 | Fire |  | Fair | No | 3 wire service corroded joint at pothead, used 1 onebolt clamp
Outage | J.E.26.08.18861 | C001887644 | Ryan Richards | Manchester | Completed | Load_247423 | Spur Tree - 310 | 2026-08-13 10:06 | 2026-08-13 10:07 | 2026-08-13 14:37 | 2026-08-13 14:37 | 2026-08-13 15:25 | 2026-08-13 15:27 | 2026-08-13 15:27 | 2026-08-13 15:27 |  |  | Fair | No | Premises found ok customer was disconnected for non payment customer said she pay bill an the wrong account customer was advised to visit office
Non-Outage | J.E.26.08.18818 | C001887651 | Michael Paterson |  | Completed |  |  | 2026-08-13 10:14 | 2026-08-13 14:21 | 2026-08-13 15:22 | 2026-08-13 15:22 | 2026-08-13 15:22 | 2026-08-13 15:22 | 2026-08-13 15:23 | 2026-08-13 15:23 |  |  | Fair | No | Customer not responding to phone call, area found with supply.
Outage | J.E.26.08.18865 | C001887650 | Oshane Warren | Westmoreland | Completed | Load_263206 | Paradise - 310 | 2026-08-13 10:14 | 2026-08-13 10:35 | 2026-08-13 11:31 | 2026-08-13 11:31 | 2026-08-13 13:37 | 2026-08-13 13:40 | 2026-08-13 13:43 | 2026-08-13 13:43 |  |  | Fair | No | Customer meter is disconnected customer balance is good need to reconnect
Non-Outage | J.E.26.08.08631 | C001887661 | Wayne Dillion | St.Elizabeth | Completed | Load_260670 | Maggotty - 110 | 2026-08-13 10:16 | 2026-08-13 10:17 | 2026-08-13 10:24 | 2026-08-13 10:24 | 2026-08-13 10:24 | 2026-08-13 10:34 | 2026-08-13 10:35 | 2026-08-13 10:35 |  |  | Fair | No | Supply check and found customer experiencing low voltage reading 99v and 102v at the end of the line. Voltage check at the transformer reading 112v, 112v. Isolate 25kva transformer circuit no pole # to tap transformer from 4 to 5. Re-close transformer and voltage reading at transformer is 116v, 116v and cross phase 232volts. Voltage leave at customer premises is 112v, 112v and cross 225volts.
Non-Outage | J.E.26.08.18910 | C001887662 | Andrae Clarke | Portland | Completed | Load_253986 | Port Antonio - 410 | 2026-08-13 10:18 | 2026-08-13 10:28 | 2026-08-13 11:35 | 2026-08-13 11:36 | 2026-08-13 11:59 | 2026-08-13 11:59 | 2026-08-13 12:02 | 2026-08-13 12:02 | Fire | Y | Fair | No | Secondary open and on the ground Transformer drop lead burnSwitch open Refer to Emergency Services
Outage | J.E.26.08.18730 | C001887663 | Richard Watson | St.Elizabeth | Completed | Load_253590 | Maggotty - 110 | 2026-08-13 10:19 | 2026-08-13 15:30 | 2026-08-13 16:13 | 2026-08-13 16:13 | 2026-08-13 17:23 | 2026-08-13 17:30 | 2026-08-13 17:35 | 2026-08-13 17:35 |  |  | Fair | No | Found okay on JPS side, customer breaker trip reset by customer supply restored.
Outage | J.E.26.08.18768 | C001887664 | Richard Watson | St.Elizabeth | Completed | Load_244659 | Maggotty - 110 | 2026-08-13 10:19 | 2026-08-13 15:30 | 2026-08-13 18:49 | 2026-08-13 18:50 | 2026-08-13 19:00 | 2026-08-13 19:06 | 2026-08-13 19:06 | 2026-08-13 19:06 |  |  | Fair | No | Replace blown 20amp junction fuse at pole#0141451, after completing patrol no visible fault found supply restored to area.
Outage | J.E.26.08.18897 | C001887665 | Wayne Dillion | St.Elizabeth | Completed | Load_243624 | Maggotty - 110 | 2026-08-13 10:19 | 2026-08-13 10:20 | 2026-08-13 13:03 | 2026-08-13 13:03 | 2026-08-13 13:55 | 2026-08-13 15:24 | 2026-08-13 16:45 | 2026-08-13 16:45 |  |  | Fair | No | Supply check and found low voltage in area. Further checks reveals customer meter socket and wires are burnt. Disconnect at pot head and customer was advised to have an electrician carry out further checks. Voltage left in area is 118v, 119v and cross phase 237volts.
Outage | J.E.26.08.18958 | C001887697 | Collin Robinson | Portland | Completed | Load_248103 | Port Antonio - 410 | 2026-08-13 10:42 | 2026-08-13 17:27 | 2026-08-13 17:34 | 2026-08-13 17:35 | 2026-08-13 18:05 | 2026-08-13 18:27 | 2026-08-13 18:27 | 2026-08-13 18:27 | BrokenWire |  | Fair | No | Replace 60 ft damage #6 twisted wire and 6 one bolt clamp Voltage reading 119v 120v 239v
Outage | J.E.26.08.18984 | C001887714 | Neckell Ormsby | St.Mary | Completed | Load_249215 | Blackstonedge - 110 | 2026-08-13 10:55 | 2026-08-13 10:57 | 2026-08-13 11:07 | 2026-08-13 11:08 | 2026-08-13 13:23 | 2026-08-13 14:37 | 2026-08-13 14:38 | 2026-08-13 14:38 |  |  | Fair | No | Found broken secondary open 25 kva transformer to splice and retention 2- pole span phase and neutral using approximately 100ft #2 AA, 4- one bolt clamps 1-#2 preform, reclose transformer no pole # seen
Non-Outage | J.E.26.07.33012 | C001887715 | Ryan Richards | Manchester | Completed | Load_250435 | Spur Tree - 310 | 2026-08-13 10:58 | 2026-08-13 11:01 | 2026-08-13 13:16 | 2026-08-13 13:16 | 2026-08-13 13:42 | 2026-08-13 14:36 | 2026-08-13 14:36 | 2026-08-13 14:36 |  |  | Fair | Yes | Defective service wire found replace 70ft#6 triplex 3 penunion 3 one bolt clamps voltage 114/116/231 volts
Outage | J.E.26.08.18885 | C001887718 | Marlon Brown | Trelawny | Completed | Load_292384 | Martha Brae - 110 | 2026-08-13 10:59 | 2026-08-13 11:04 | 2026-08-13 13:22 | 2026-08-13 13:23 | 2026-08-13 13:22 | 2026-08-13 14:16 | 2026-08-13 14:16 | 2026-08-13 14:16 | TreeContact |  | Fair | No | Check and found ok Voltage found at pothead 116/116=232vVoltage leaving at pothead 116/116=232vClear tree limb from secondary line
Outage | J.E.26.08.18972 | C001887724 | Dean- Smith | Hanover | Completed | Load_242378 | Orange Bay - 310 | 2026-08-13 11:03 | 2026-08-13 11:04 | 2026-08-13 13:17 | 2026-08-13 13:18 | 2026-08-13 13:58 | 2026-08-13 13:59 | 2026-08-13 14:10 | 2026-08-13 14:10 | Fire |  | Rains | No | Customer complained of neighbor stealing electricity. No illegal connection was seen at the time of visit
Outage | J.E.26.08.18724 | C001887726 | Edward Royal | KSAS | Completed | Load_247260 | Hunts Bay - 210 | 2026-08-13 11:04 | 2026-08-13 12:00 | 2026-08-13 14:00 | 2026-08-13 14:01 | 2026-08-13 14:00 | 2026-08-13 14:01 | 2026-08-13 14:02 | 2026-08-13 14:02 |  |  | Fair | No | Defective switch need to be changed reffered to live line crew replaced 10A transformer fuse
Outage | J.E.26.08.18923 | C001887725 | Neville Spencer | Clarendon | Completed | Load_248676 | May Pen - 110 | 2026-08-13 11:04 | 2026-08-13 18:05 | 2026-08-13 20:24 | 2026-08-13 20:25 | 2026-08-13 22:18 | 2026-08-13 22:44 | 2026-08-13 22:50 | 2026-08-13 22:50 | BrokenWire |  | Fair | No | Found 120 ft 2/0 triplex defective feeding approximately 20 customers open jumper NEED 120 ft 2/0 triplex to carry out repair.
Outage | J.E.26.08.19001 | C001887736 | Milton Charlton | KSAS | Completed | Load_261156 | Up Park Camp - 410 | 2026-08-13 11:05 | 2026-08-13 11:10 | 2026-08-13 11:33 | 2026-08-13 11:41 | 2026-08-13 13:02 | 2026-08-13 12:25 | 2026-08-13 13:10 | 2026-08-13 13:10 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.19010 | C001887735 | Raymond Lewis | St.Ann | Completed | Load_252506 | Ocho Rios - 310 | 2026-08-13 11:05 | 2026-08-13 11:09 | 2026-08-13 11:17 | 2026-08-13 11:17 | 2026-08-13 12:36 | 2026-08-13 13:27 | 2026-08-13 13:27 | 2026-08-13 13:27 | Fire |  | SevereWind | No | Splice and retention 2 span neutral remade x former neutral,refuse and close 10 A junction fuse
Outage | J.E.26.08.18748 | C001887738 | Hartley Chin | Clarendon | Completed | Load_253922 | May Pen - 210 | 2026-08-13 11:08 | 2026-08-13 11:09 | 2026-08-13 13:27 | 2026-08-13 13:27 | 2026-08-13 13:48 | 2026-08-13 13:49 | 2026-08-13 13:49 | 2026-08-13 13:49 |  |  | Fair | No | Premisis found ok.
Non-Outage | J.E.26.08.19021 | C001887746 | Rusean Allen |  | Completed |  |  | 2026-08-13 11:10 | 2026-08-13 11:11 | 2026-08-13 13:12 | 2026-08-13 13:12 | 2026-08-13 13:23 | 2026-08-13 13:24 | 2026-08-13 13:24 | 2026-08-13 13:24 | Fire |  | Fair | No | Not found , more information needed
Outage | J.E.26.08.18751 | C001887739 | Hartley Chin | Clarendon | Completed | Load_256239 | May Pen - 210 | 2026-08-13 11:10 | 2026-08-13 11:10 | 2026-08-13 11:58 | 2026-08-13 12:10 | 2026-08-13 12:10 | 2026-08-13 12:10 | 2026-08-13 12:11 | 2026-08-13 12:11 |  |  | Fair | No | Call related to job # 18691
Non-Outage | J.E.26.08.19012 | C001887753 | Antony Levy |  | Completed |  |  | 2026-08-13 11:15 | 2026-08-13 15:27 | 2026-08-13 22:11 | 2026-08-13 22:11 | 2026-08-13 22:51 | 2026-08-14 00:01 | 2026-08-14 00:03 | 2026-08-14 00:03 | BrokenWire |  | Fair | No | Cx stated fluctuations in voltage ....line patrolled broken neutral of open secondary 2 phase and neutral found... neutral spliced and retention using 2 1 bolt clamps and a number 2 preform along with 5 ft of #2 AAA conductor... line closed power restored
Outage | J.E.26.08.19043 | C001887757 | Cliton Henry | St.Mary | Completed | Load_243968 | Blackstonedge - 110 | 2026-08-13 11:20 | 2026-08-13 11:21 | 2026-08-13 11:33 | 2026-08-13 11:34 | 2026-08-13 13:10 | 2026-08-13 14:40 | 2026-08-13 14:40 | 2026-08-13 14:40 | Fire |  | Fair | No | A broken secondary neutral conductor found on the ground. A 50 kva transformer was de energized at pole #0100514 to carryout repairs. Corrective work done to spliced and retention secondary neutral conductor using approximately 70 feet #2 AA conductor, 1- s2 preform, 1 d iron and spool and 6 one bolt clamps. Supply restored to energized the 50 kva transformer.
Non-Outage | J.E.26.08.19083 | C001887775 | Donald Cunningham |  | Completed |  |  | 2026-08-13 11:29 | 2026-08-13 11:30 | 2026-08-13 13:41 | 2026-08-13 13:41 | 2026-08-13 14:23 | 2026-08-13 14:23 | 2026-08-13 14:46 | 2026-08-13 14:46 | BrokenWire |  | Fair | No | Broken secondary phase preform corrected using 1 2/0 preform for repair
Outage | J.E.26.08.19093 | C001887791 | Richman Whyte | St.Elizabeth | Completed | Load_243757 | Maggotty - 110 | 2026-08-13 11:38 | 2026-08-13 15:43 | 2026-08-13 19:06 | 2026-08-13 19:06 | 2026-08-13 19:06 | 2026-08-13 19:06 | 2026-08-13 19:07 | 2026-08-13 19:07 |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.08.16412 | C001887798 | Rodclif Dawkins | Portmore | Completed | Load_242652 | Naggo Head - 510 | 2026-08-13 11:40 | 2026-08-13 11:41 | 2026-08-13 11:49 | 2026-08-13 11:49 | 2026-08-13 11:49 | 2026-08-13 11:49 | 2026-08-13 11:50 | 2026-08-13 11:50 |  |  | Fair | No | On location crew found blown fuse from 3phase line section. On close observation 3 dropout switches were defective. Line section was isolated by opening (3) 50amp trip savers and applying short and ground. Using 3 dropout switches and 6ft of #4 copper. Repairs were done. Short and ground removed and line section energized.
Non-Outage | J.E.26.08.19091 | C001887808 | Rusean Allen | KSAS | Completed | Load_300873 | Cane River - 410 | 2026-08-13 11:52 | 2026-08-13 11:55 | 2026-08-13 13:26 | 2026-08-13 13:26 | 2026-08-13 13:46 | 2026-08-13 14:34 | 2026-08-13 14:34 | 2026-08-13 14:34 |  |  | Fair | No | Defective 5KVA transformer found, transformer needs to be changed.Refer to maintenance department.
Outage | J.E.26.08.19095 | C001887813 | Elvis Trowers | KSAN | Completed | Load_255393 | Constant Spring - 210 | 2026-08-13 12:00 | 2026-08-13 17:01 | 2026-08-13 17:09 | 2026-08-13 17:09 | 2026-08-13 18:49 | 2026-08-13 18:50 | 2026-08-13 19:00 | 2026-08-13 19:00 |  |  | Fair | No | Customer service wire #6 triplex burn off in mid span lower splice and retention using 6ft #6 triplex phase and three 1- bolt clamps. Readings at meter socket 114-114-229 volts.repa
Outage | J.E.26.08.19112 | C001887821 | Milton Charlton | KSAS | Completed | Load_245092 | Up Park Camp - 410 | 2026-08-13 12:00 | 2026-08-13 12:01 | 2026-08-13 13:10 | 2026-08-13 13:12 | 2026-08-13 13:37 | 2026-08-13 15:25 | 2026-08-13 15:25 | 2026-08-13 15:25 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.19088 | C001887834 | Collin Robinson | Portland | Completed | Load_349214 | Port Antonio - 410 | 2026-08-13 12:11 | 2026-08-13 15:01 | 2026-08-13 15:06 | 2026-08-13 15:06 | 2026-08-13 15:39 | 2026-08-13 16:34 | 2026-08-13 16:35 | 2026-08-13 16:35 | Fire |  | Fair | No | Splice and retention 2 pole span of broken open secondary conductor and replace 5 amps fuse
Outage | J.E.26.08.19109 | C001887835 | Denton Williams | Portland | Completed | Load_262752 | Port Antonio - 410 | 2026-08-13 12:11 | 2026-08-13 12:12 | 2026-08-13 13:02 | 2026-08-13 13:02 | 2026-08-13 14:14 | 2026-08-13 14:47 | 2026-08-13 14:49 | 2026-08-13 14:49 | Fire |  | Fair | No | Coconut tree limb fell on line and caused a 10 amp junction fuse to operate. Remove limb and replace fuse, all customers restored.
Outage | J.E.26.08.19131 | C001887842 | Ryan Richards | Manchester | Completed | Load_302329 | Spur Tree - 310 | 2026-08-13 12:16 | 2026-08-13 12:18 | 2026-08-13 15:27 | 2026-08-13 15:28 | 2026-08-13 15:59 | 2026-08-13 18:10 | 2026-08-13 18:10 | 2026-08-13 18:10 |  |  | Fair | No | Blown 20 amp junction fuse found line patrol nothing found lighting suspected to be the cause blown fuse was replaced and all customers are now with supply
Outage | J.E.26.08.19162 | C001887841 | Richard Samuda | Manchester | Completed | Load_243246 | Spur Tree - 310 | 2026-08-13 12:16 | 2026-08-14 07:05 | 2026-08-14 09:55 | 2026-08-14 09:56 | 2026-08-14 10:41 | 2026-08-14 10:45 | 2026-08-14 10:46 | 2026-08-14 10:46 | TreeContact |  | Fair | No | Found ok customer was concerned tree may touch line but clearance for line ok
Non-Outage | J.E.26.08.19164 | C001887850 | Horace Malcolm | St.James | Completed | Load_250893 | Bogue - 310 | 2026-08-13 12:23 | 2026-08-13 12:25 | 2026-08-13 13:27 | 2026-08-13 13:27 | 2026-08-13 13:28 | 2026-08-13 13:33 | 2026-08-13 13:33 | 2026-08-13 13:33 |  |  | Fair | No | Refused one 50kva transformer used one 5amp fuse
Outage | J.E.26.08.19132 | C001887855 | Tyrese Williams | St.Ann | Completed | Load_243600 | Cardiff Hall - 310 | 2026-08-13 12:26 | 2026-08-13 12:27 | 2026-08-13 12:36 | 2026-08-13 12:36 | 2026-08-13 14:20 | 2026-08-13 14:26 | 2026-08-13 14:26 | 2026-08-13 14:26 |  |  | Fair | No | Remade service wire joint at pole use 1 pg clamp
Non-Outage | J.E.26.08.00748 | C001887871 | Moses Elliston | Portmore | Completed | Load_253794 | Naggo Head - 510 | 2026-08-13 12:43 | 2026-08-13 12:53 | 2026-08-13 16:58 | 2026-08-13 16:58 | 2026-08-13 16:58 | 2026-08-13 15:56 | 2026-08-13 17:01 | 2026-08-13 17:01 |  |  | Fair | No | Corroaded 3 wire service phase and neutral repaired with 5 linkets,and 1 clamp 118-117 -235 volts at pothead
Outage | J.E.26.08.19213 | C001887884 | Swon Miller | St.James | Completed | Load_245286 | Queens Drive - 710 | 2026-08-13 12:55 | 2026-08-13 12:56 | 2026-08-13 13:26 | 2026-08-13 13:28 | 2026-08-13 14:07 | 2026-08-18 03:14 | 2026-08-13 15:14 | 2026-08-13 15:14 |  |  | Fair | No | Found 1,20 amp junction fuse and 8 amp junction fuse blown cause by defective primary arrester remove arrester and replace 1,20 amp junction fuse and replace 8 amp junction fuse
Outage | J.E.26.08.19239 | C001887885 | Horace Malcolm | St.James | Completed | Load_1001938 | Bogue - 310 | 2026-08-13 12:55 | 2026-08-13 12:57 | 2026-08-13 22:10 | 2026-08-13 22:10 | 2026-08-13 22:18 | 2026-08-13 22:21 | 2026-08-13 22:21 | 2026-08-13 22:21 |  |  | Fair | No | Check and found customer have rami issue hexing meter not communicating zero voltage reading referred to field service
Non-Outage | J.E.26.08.19140 | C001887886 | Roemello Brown | Trelawny | Completed | Load_255801 | Martha Brae - 210 | 2026-08-13 12:57 | 2026-08-13 12:58 | 2026-08-13 14:37 | 2026-08-13 14:37 | 2026-08-13 15:45 | 2026-08-13 15:46 | 2026-08-13 16:06 | 2026-08-13 16:06 |  |  | Fair | No | Secondary line low lots of illegal connections in the area needs losses team to assist Voltage found 109/102/211Voltage leave 109/102/211
Non-Outage | J.E.26.08.19078 | C001887889 | Junior Scarlett | St.James | Completed | Load_263658 | Bogue - 610 | 2026-08-13 12:59 | 2026-08-13 13:00 | 2026-08-13 16:02 | 2026-08-14 10:52 | 2026-08-14 11:36 | 2026-08-14 00:13 | 2026-08-14 12:13 | 2026-08-14 12:13 |  |  | Fair | No | Refer to field service Voltage found 118 v 119v 240v
Outage | J.E.26.08.19264 | C001887898 | Roxroy Needham | St.Ann | Completed | Load_412973 | Cardiff Hall - 210 | 2026-08-13 13:12 | 2026-08-13 15:31 | 2026-08-13 18:22 | 2026-08-13 18:23 | 2026-08-13 19:30 | 2026-08-13 19:32 | 2026-08-13 19:32 | 2026-08-13 19:32 | Fire |  | Fair | No | Found switch leaking need maintenance to carry out repair
Non-Outage | J.E.26.08.19258 | C001887904 | Kenroy Dale |  | Completed |  |  | 2026-08-13 13:23 | 2026-08-13 13:24 | 2026-08-13 13:53 | 2026-08-13 14:02 | 2026-08-13 14:40 | 2026-08-13 15:53 | 2026-08-13 15:56 | 2026-08-13 15:56 | LeakingTransformer |  | Fair | No | Blown 2 amp transformer fuse found line patrol 2 span of secondary neutral found broken, conductor was splice and retention blown fuse replace and area now with supply
Outage | J.E.26.08.18968 | C001887914 | Richman Whyte | Westmoreland | Completed | Load_257936 | Paradise - 310 | 2026-08-13 13:25 | 2026-08-13 15:26 | 2026-08-13 17:55 | 2026-08-13 17:55 | 2026-08-13 18:13 | 2026-08-13 18:13 | 2026-08-13 18:17 | 2026-08-13 18:17 |  |  | Fair | No | Mix up meter customer meter is in the wrong socket the one that is in her socket is disconnect meter number 2729108
Outage | J.E.26.08.19087 | C001887915 | Richman Whyte | Westmoreland | Completed | Load_261360 | Paradise - 310 | 2026-08-13 13:25 | 2026-08-13 15:26 | 2026-08-13 16:38 | 2026-08-13 16:38 | 2026-08-13 17:00 | 2026-08-13 17:13 | 2026-08-13 17:22 | 2026-08-13 17:22 |  |  | Fair | No | Connect back customer after hurricane use 50ft #6 triplex service wire voltage 120 120 240
Outage | J.E.26.08.19291 | C001887916 | Richman Whyte | Westmoreland | Completed | Load_238447 | Paradise - 310 | 2026-08-13 13:25 | 2026-08-13 15:26 | 2026-08-13 17:22 | 2026-08-13 17:23 | 2026-08-13 17:36 | 2026-08-13 17:50 | 2026-08-13 17:51 | 2026-08-13 17:51 |  |  | Fair | No | Clean corrosion on service wire at pothead use three one bolt clamps voltage 109 110 220
Non-Outage | J.E.26.08.19073 | C001887919 | Daniel Francis | St.Ann | Completed | Load_261932 | Ocho Rios - 510 | 2026-08-13 13:29 | 2026-08-13 18:22 | 2026-08-13 21:44 | 2026-08-13 21:45 | 2026-08-13 21:46 | 2026-08-13 21:48 | 2026-08-13 21:48 | 2026-08-13 21:48 |  |  | Fair | No | Meter need to be change 117 116 233 in all
Outage | J.E.26.08.19270 | C001887925 | Shawn Medley | St.James | Completed | Load_242778 | Bogue - 510 | 2026-08-13 13:31 | 2026-08-13 13:35 | 2026-08-13 13:42 | 2026-08-13 13:43 | 2026-08-13 14:10 | 2026-08-13 14:15 | 2026-08-13 14:17 | 2026-08-13 14:17 |  |  | Fair | No | Premises was disconnected due to late payment contacted call customer and supply restored
Non-Outage | J.E.26.08.18910 | C001887938 | Andrae Clarke | Portland | Completed | Load_253986 | Port Antonio - 410 | 2026-08-13 13:40 | 2026-08-13 13:41 | 2026-08-13 13:44 | 2026-08-13 13:45 | 2026-08-13 13:44 | 2026-08-13 10:36 | 2026-08-13 13:47 | 2026-08-13 13:47 | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards | Y | Fair | No | Secondary line burst wire lining on the ground Refer to emergency crew Phuseopen
Outage | J.E.26.08.19297 | C001887952 | Clyde Brown | Clarendon | Completed | Load_250405 | May Pen - 110 | 2026-08-13 13:56 | 2026-08-13 13:59 | 2026-08-13 14:27 | 2026-08-13 14:28 | 2026-08-13 14:55 | 2026-08-13 15:00 | 2026-08-13 15:04 | 2026-08-13 15:04 | LowHangingWires |  | Fair | No | Low primary conductor and primary neutral very low caused by T-off pole lean and need to be straighten this need urgent attention although conductor is covered.
Outage | J.E.26.08.19279 | C001887959 | Hartley Chin | Clarendon | Completed | Load_248737 | Parnassus - 210 | 2026-08-13 14:03 | 2026-08-13 14:04 | 2026-08-13 20:14 | 2026-08-13 20:14 | 2026-08-13 20:14 | 2026-08-13 20:14 | 2026-08-13 20:15 | 2026-08-13 20:15 |  |  | Fair | No | Premisis found ok. Call related to job # 17153
Outage | J.E.26.08.19117 | C001887972 | Derrick Grubb | St.Thomas | Completed | Load_240979 | Good Year - 110 | 2026-08-13 14:16 | 2026-08-13 15:58 | 2026-08-13 18:45 | 2026-08-13 20:00 | 2026-08-13 19:59 | 2026-08-13 21:01 | 2026-08-13 21:02 | 2026-08-13 21:02 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.19336 | C001887973 | Stephen Taylor | St.Thomas | Completed | Load_264837 | Good Year - 110 | 2026-08-13 14:16 | 2026-08-14 07:42 | 2026-08-14 09:38 | 2026-08-14 09:38 | 2026-08-14 10:50 | 2026-08-14 10:50 | 2026-08-14 10:51 | 2026-08-14 10:51 |  |  | Fair | No | Customer was disconnected for nun payment of bill
Non-Outage | J.E.26.08.19378 | C001887974 | Michael Paterson | Westmoreland | Completed | Load_251917 | Paradise - 210 | 2026-08-13 14:19 | 2026-08-13 14:20 | 2026-08-13 14:33 | 2026-08-13 14:33 | 2026-08-13 14:53 | 2026-08-13 15:16 | 2026-08-13 15:17 | 2026-08-13 15:17 |  |  | Fair | No | Assessment done at location, voltage reading taken, 124v, 124v, 248v, had to isolate xfmr to adjust xfmr tap changer from tap 3 to tap 1, voltage readings 117v, 117v, 234v.
Non-Outage | J.E.26.08.19397 | C001887983 | Horace Malcolm | St.James | Completed | Load_250893 | Bogue - 310 | 2026-08-13 14:21 | 2026-08-13 14:22 | 2026-08-13 18:11 | 2026-08-13 18:11 | 2026-08-13 18:11 | 2026-08-13 18:13 | 2026-08-13 18:13 | 2026-08-13 18:13 |  |  | Fair | No | Disconnect defective primary arrester and refuse one 50kva transformer used one 5amp fuse
Outage | J.E.26.08.19395 | C001887984 | Oshane Warren | Westmoreland | Completed | Load_263477 | Paradise - 310 | 2026-08-13 14:22 | 2026-08-13 14:22 | 2026-08-13 15:05 | 2026-08-13 15:05 | 2026-08-13 15:05 | 2026-08-13 15:05 | 2026-08-13 15:05 | 2026-08-13 15:05 |  |  | Fair | No | Replace 8 amp junction fuse
Outage | J.E.26.08.19230 | C001887997 | Christopher Edwards | KSAN | Completed | Load_238744 | Constant Spring - 410 | 2026-08-13 14:30 | 2026-08-13 14:31 | 2026-08-13 17:23 | 2026-08-13 17:23 | 2026-08-13 18:29 | 2026-08-13 19:28 | 2026-08-13 19:29 | 2026-08-13 19:29 |  |  | Fair | No | Required 150ft #6Service wire to carry out repairs Service wire is damaged and needs to be replaced
Outage | J.E.26.08.19350 | C001887996 | Christopher Edwards | KSAN | Completed | Load_242888 | Constant Spring - 410 | 2026-08-13 14:30 | 2026-08-13 14:31 | 2026-08-13 20:56 | 2026-08-13 20:57 | 2026-08-13 20:57 | 2026-08-13 10:42 | 2026-08-14 00:25 | 2026-08-14 00:25 |  |  | Fair | No
Non-Outage | J.E.26.08.18786 | C001888012 | Swon Miller | St.James | Completed | Load_256715 | Queens Drive - 310 | 2026-08-13 14:45 | 2026-08-13 14:46 | 2026-08-13 15:15 | 2026-08-13 15:15 | 2026-08-13 15:38 | 2026-08-10 04:38 | 2026-08-13 16:38 | 2026-08-13 16:38 |  |  | Fair | No | Found clamp burnt at transformer cause by contamination voltage found 238/240/222 clean and remake joint use 1pg voltage left 238/238/240/415/415/416/
Non-Outage | J.E.26.08.19108 | C001888011 | Christopher Edwards | KSAN | Completed | Load_246942 | Constant Spring - 410 | 2026-08-13 14:45 | 2026-08-13 14:46 | 2026-08-13 19:29 | 2026-08-13 19:30 | 2026-08-13 20:08 | 2026-08-13 20:55 | 2026-08-13 20:56 | 2026-08-13 20:56 | BrokenPole |  | Fair | No | Customer is requesting guy to be relocated from off their premises Customer was advised to go to office to make that request
Outage | J.E.26.08.19400 | C001888013 | Clyde Brown | St.Catherine | Completed | Load_240139 | Rhodens Pen - 310 | 2026-08-13 14:47 | 2026-08-13 14:52 | 2026-08-13 15:42 | 2026-08-13 15:43 | 2026-08-13 17:34 | 2026-08-13 17:41 | 2026-08-13 17:45 | 2026-08-13 17:45 |  |  | Fair | No | 1-CT metering meter burnt up and open 25 kva transformer and isolate burnt meter,voltage 113/113 and 228V
Non-Outage | J.E.26.08.19222 | C001888018 | Hartley Chin | St.Catherine | Completed | Load_261748 | Rhodens Pen - 310 | 2026-08-13 14:51 | 2026-08-13 14:51 | 2026-08-13 15:35 | 2026-08-13 15:35 | 2026-08-13 16:40 | 2026-08-13 16:41 | 2026-08-13 16:45 | 2026-08-13 16:45 |  |  | Fair | No | Reset transformer. voltage reading v228 - v230 -v231
Outage | J.E.26.08.19333 | C001888020 | Horace Malcolm | St.James | Completed | Load_250893 | Bogue - 310 | 2026-08-13 14:56 | 2026-08-13 14:57 | 2026-08-13 18:14 | 2026-08-13 18:14 | 2026-08-13 18:14 | 2026-08-13 18:15 | 2026-08-13 18:15 | 2026-08-13 18:15 |  |  | Fair | No | Related to previous call job number 19397 check and found ok
Outage | J.E.26.08.19458 | C001888022 | Collin Robinson | Portland | Completed | Load_245066 | Port Antonio - 410 | 2026-08-13 14:57 | 2026-08-13 15:02 | 2026-08-13 16:42 | 2026-08-13 16:43 | 2026-08-13 17:13 | 2026-08-13 17:21 | 2026-08-13 17:21 | 2026-08-13 17:21 |  |  | Fair | No | Remove bamboo from 1 phase of primary conductor and close 50 Amp trip saver
Outage | J.E.26.08.17722 | C001888042 | Rusean Allen | KSAS | Completed | Load_268072 | Rockfort - 410 | 2026-08-13 15:17 | 2026-08-14 08:28 | 2026-08-14 11:56 | 2026-08-14 11:57 | 2026-08-14 12:03 | 2026-08-14 12:15 | 2026-08-14 12:15 | 2026-08-14 12:15 |  |  | Fair | No | Corroded clamps found at pothead, clamps were changed.Voltage 115 115 231
Outage | J.E.26.08.19185 | C001888043 | Fitzroy Turner | KSAS | Completed | Load_268171 | Rockfort - 210 | 2026-08-13 15:17 | 2026-08-13 15:20 | 2026-08-13 20:04 | 2026-08-13 20:05 | 2026-08-13 20:19 | 2026-08-13 20:34 | 2026-08-13 20:35 | 2026-08-13 20:35 |  |  | Fair | No | Found bank of three 50kva transformer fuse blown replace 3 7amps fuses supply restored to customer
Outage | J.E.26.08.19236 | C001888044 | Fitzroy Turner | KSAS | Completed | Load_253177 | Rockfort - 410 | 2026-08-13 15:17 | 2026-08-13 15:20 | 2026-08-13 19:50 | 2026-08-13 19:51 | 2026-08-13 19:51 | 2026-08-13 19:51 | 2026-08-13 19:57 | 2026-08-13 19:57 |  |  | Fair | No | Found 25 kva transformer drops leads neutral use two one bolt clamps and 2ft of #2 aluminum to carry out repair supply restored to the areas
Outage | J.E.26.08.19094 | C001888045 | Fitzroy Turner | KSAS | Completed | Load_1003929 | Rockfort - 410 | 2026-08-13 15:19 | 2026-08-13 15:23 | 2026-08-13 18:24 | 2026-08-13 19:41 | 2026-08-13 19:41 | 2026-08-13 19:43 | 2026-08-13 19:46 | 2026-08-13 19:46 |  |  | Fair | No | Found defective 50 kva transformer NOT JPS transformer
Outage | J.E.26.08.19092 | C001888052 | Fitzroy Turner | KSAS | Completed | Load_245002 | Rockfort - 410 | 2026-08-13 15:20 | 2026-08-13 15:21 | 2026-08-13 16:00 | 2026-08-13 16:01 | 2026-08-13 17:29 | 2026-08-13 17:36 | 2026-08-13 17:40 | 2026-08-13 17:40 |  |  | Fair | No | Found bank of three 167kva transformer found one fuse blown .replace one 15amp fuse supply restored to areas
Outage | J.E.26.08.19366 | C001888054 | Evan Spaulding | St.Mary | Completed | Load_238360 | Highgate - 210 | 2026-08-13 15:22 | 2026-08-13 15:34 | 2026-08-13 16:17 | 2026-08-13 16:18 | 2026-08-13 16:28 | 2026-08-13 17:11 | 2026-08-13 17:12 | 2026-08-13 17:12 |  |  | Fair | No | Use 6-1 bolt clamps at location, voltage left 112v,106v,218v.
Outage | J.E.26.08.19399 | C001888053 | Evan Spaulding | St.Mary | Completed | Load_255504 | Highgate - 210 | 2026-08-13 15:22 | 2026-08-13 15:33 | 2026-08-13 17:13 | 2026-08-13 17:13 | 2026-08-13 17:34 | 2026-08-13 18:36 | 2026-08-13 18:37 | 2026-08-13 18:37 |  | Y | Fair | No | Carry out spot bushing and replace 1-20 amps junction fuse at pole number 0010997.
Outage | J.E.26.08.19450 | C001888055 | Evan Spaulding | St.Mary | Completed | Load_260173 | Annotto Bay - 310 | 2026-08-13 15:22 | 2026-08-13 15:33 | 2026-08-13 18:54 | 2026-08-13 18:55 | 2026-08-13 18:54 | 2026-08-13 18:54 | 2026-08-13 18:55 | 2026-08-13 18:55 |  |  | Fair | No | Customer says he didn’t make any report to jps
Outage | J.E.26.08.19404 | C001888056 | Roxroy Needham | St.Ann | Completed | Load_556106 | Cardiff Hall - 210 | 2026-08-13 15:23 | 2026-08-13 15:24 | 2026-08-13 15:59 | 2026-08-13 16:00 | 2026-08-13 16:12 | 2026-08-13 16:33 | 2026-08-13 16:37 | 2026-08-13 16:37 |  |  | Fair | No | Remove kite from line and replace a 30 amps junction fuse at pole #616430
Outage | J.E.26.08.18933 | C001888060 | Christopher Edwards | KSAN | Completed | Load_242776 | Constant Spring - 310 | 2026-08-13 15:28 | 2026-08-14 07:21 | 2026-08-14 10:58 | 2026-08-14 10:59 | 2026-08-14 10:58 | 2026-08-14 09:26 | 2026-08-14 11:01 | 2026-08-14 11:01 | TreeContact |  | Fair | No
Outage | J.E.26.08.19360 | C001888058 | Daniel Francis | St.Ann | Completed | Load_239077 | Ocho Rios - 310 | 2026-08-13 15:28 | 2026-08-13 15:29 | 2026-08-13 17:32 | 2026-08-13 17:33 | 2026-08-13 18:42 | 2026-08-13 20:49 | 2026-08-13 20:53 | 2026-08-13 20:53 | Fire |  | Fair | No | Retention 3span of3wire secondary which was sag uneven causing fire when wind brow
Outage | J.E.26.08.19526 | C001888059 | Elvis Trowers | KSAN | Completed | Load_259599 | Washington Blvd - 410 | 2026-08-13 15:28 | 2026-08-13 17:18 | 2026-08-13 20:41 | 2026-08-13 20:41 | 2026-08-13 21:52 | 2026-08-13 22:15 | 2026-08-13 22:08 | 2026-08-13 22:08 |  |  | Fair | No | Premises closed. Premises has light security stated premises has light.
Outage | J.E.26.08.19571 | C001888057 | Daniel Francis | St.Ann | Completed | Load_265231 | Roaring River - 210 | 2026-08-13 15:28 | 2026-08-13 15:29 | 2026-08-13 15:36 | 2026-08-13 15:37 | 2026-08-13 17:08 | 2026-08-13 17:12 | 2026-08-13 17:13 | 2026-08-13 17:13 |  |  | Fair | No | Found defective one bolt clamps at pole replace
Outage | J.E.26.08.19181 | C001888062 | Elvis Trowers | KSAN | Completed | Load_265188 | Constant Spring - 210 | 2026-08-13 15:29 | 2026-08-13 17:01 | 2026-08-13 19:21 | 2026-08-13 19:22 | 2026-08-13 20:38 | 2026-08-13 20:40 | 2026-08-13 20:40 | 2026-08-13 20:40 |  |  | Fair | No | Found one 15 amps junction fuse blown at pole #0011419 and one 5 amps transformer fuse blown at pole #( no pole #). Refused using one 15 amps fuse and one 5 amps fuse and reclosed junction and transformer switches.
Outage | J.E.26.08.19272 | C001888061 | Elvis Trowers | KSAN | Completed | Load_239618 | Constant Spring - 210 | 2026-08-13 15:29 | 2026-08-13 17:01 | 2026-08-13 19:02 | 2026-08-13 19:03 | 2026-08-13 19:20 | 2026-08-13 19:25 | 2026-08-13 19:21 | 2026-08-13 19:21 |  |  | Fair | No | Unable to locate customer by telephone. Number on the report going straight to voicemail.
Outage | J.E.26.08.18644 | C001888067 | Antony Levy | KSAN | Completed | Load_256169 | Hope - 510 | 2026-08-13 15:30 | 2026-08-13 15:30 | 2026-08-13 18:21 | 2026-08-13 18:22 | 2026-08-13 19:22 | 2026-08-13 21:15 | 2026-08-13 21:15 | 2026-08-13 21:15 |  |  | Fair | No | Report stated broken crossarm.... broken cross arm found for 2 phase t primary... after securing work are old wooden cross arm removed and replaced with 1 fiber glass arm ... then old porcelain insulator changed to polymer .... line closed power restored
Non-Outage | J.E.26.08.19042 | C001888075 | Raymond Carr | St.Mary | Completed | Load_243968 | Blackstonedge - 110 | 2026-08-13 15:35 | 2026-08-13 15:36 | 2026-08-13 17:12 | 2026-08-13 17:13 | 2026-08-13 17:55 | 2026-08-13 17:46 | 2026-08-13 17:57 | 2026-08-13 17:57 |  |  | Fair | No | Customer couldn’t be contacted.
Non-Outage | J.E.26.08.19226 | C001888074 | Raymond Carr | St.Mary | Completed | Load_256378 | Oracabessa - 210 | 2026-08-13 15:35 | 2026-08-13 15:36 | 2026-08-13 15:48 | 2026-08-13 15:49 | 2026-08-13 16:08 | 2026-08-13 16:19 | 2026-08-13 17:12 | 2026-08-13 17:12 |  |  | Fair | No | Defective clamps replaced at JPS pole. Voltage readings 105/105/210.
Outage | J.E.26.08.19424 | C001888073 | Raheem Ricketts | Manchester | Completed | Load_264605 | Spur Tree - 210 | 2026-08-13 15:35 | 2026-08-13 15:36 | 2026-08-13 15:49 | 2026-08-13 15:50 | 2026-08-13 15:49 | 2026-08-13 15:50 | 2026-08-13 15:50 | 2026-08-13 15:50 |  |  | Fair | No | Customer cell phone outbof service
Outage | J.E.26.08.18530 | C001888078 | Richard Samuda | Manchester | Completed | Load_270122 | Kendal - 210 | 2026-08-13 15:36 | 2026-08-13 15:38 | 2026-08-13 15:58 | 2026-08-13 15:59 | 2026-08-13 16:34 | 2026-08-13 04:34 | 2026-08-13 16:34 | 2026-08-13 16:34 |  |  | Fair | No | Found ok customer said they are back to normal
Outage | J.E.26.08.19401 | C001888076 | Richard Samuda | Manchester | Completed | Load_262762 | Kendal - 210 | 2026-08-13 15:36 | 2026-08-13 15:38 | 2026-08-13 16:35 | 2026-08-13 16:35 | 2026-08-13 17:06 | 2026-08-13 17:17 | 2026-08-13 17:17 | 2026-08-13 17:17 |  |  | Fair | No | Customer meter was falling out of socket fit back meter into socket customer back to normal 114/116/230
Outage | J.E.26.08.19423 | C001888077 | Richard Samuda | Manchester | Completed | Load_259811 | Kendal - 210 | 2026-08-13 15:36 | 2026-08-13 15:38 | 2026-08-13 17:26 | 2026-08-13 17:26 | 2026-08-13 17:50 | 2026-08-13 17:51 | 2026-08-13 17:51 | 2026-08-13 17:51 |  |  | Fair | No | Customer stated that he didn’t make a call
Non-Outage | J.E.26.07.15111 | C001888082 | Raymond Carr | St.Ann | Completed | Load_269325 | Upper White River - 110 | 2026-08-13 15:37 | 2026-08-13 17:47 | 2026-08-13 17:57 | 2026-08-13 17:57 | 2026-08-13 17:57 | 2026-08-13 18:00 | 2026-08-13 17:58 | 2026-08-13 17:58 |  |  | Fair | No | Refer to St Ann.
Outage | J.E.26.08.19341 | C001888088 | Richard Grant | St.Catherine | Completed | Load_262332 | New Michelton - 310 | 2026-08-13 15:41 | 2026-08-13 15:44 | 2026-08-13 16:06 | 2026-08-13 16:07 | 2026-08-13 18:38 | 2026-08-13 18:52 | 2026-08-13 18:52 | 2026-08-13 18:52 |  |  | Fair | No | Checks revealed customer has defective meter socket and burnt meter. Customer was advised.
Non-Outage | J.E.26.08.18806 | C001888089 | Roxroy Needham | St.Ann | Completed | Load_238745 | Cardiff Hall - 210 | 2026-08-13 15:42 | 2026-08-13 15:43 | 2026-08-13 16:37 | 2026-08-13 17:50 | 2026-08-13 17:50 | 2026-08-13 18:17 | 2026-08-13 18:20 | 2026-08-13 18:20 |  |  | Fair | No | Premises found locked not getting customer on phone
Outage | J.E.26.08.19195 | C001888090 | Richard Grant | St.Catherine | Completed | Load_405664 | New Michelton - 310 | 2026-08-13 15:42 | 2026-08-13 15:44 | 2026-08-13 18:52 | 2026-08-13 18:52 | 2026-08-13 20:35 | 2026-08-13 20:36 | 2026-08-13 20:36 | 2026-08-13 20:36 |  |  | Fair | No | Checks revealed customer has internal issues. Customer advise. 118. 118 236 voltages left at premises
Outage | J.E.26.08.18854 | C001888095 | Ricky Hall | St.Catherine | Completed | Load_265584 | Tredegar - 510 | 2026-08-13 15:45 | 2026-08-13 15:46 | 2026-08-13 16:04 | 2026-08-13 16:05 | 2026-08-13 16:48 | 2026-08-13 16:54 | 2026-08-13 16:55 | 2026-08-13 16:55 | TreeContact |  | Fair | No | Tree fell on customer side of service line internal issue customer advised
Outage | J.E.26.08.18724 | C001888099 | Fitzroy Turner | KSAS | Completed | Load_247260 | Hunts Bay - 210 | 2026-08-13 15:47 | 2026-08-13 15:50 | 2026-08-13 20:39 | 2026-08-13 20:40 | 2026-08-13 21:23 | 2026-08-13 21:23 | 2026-08-13 21:27 | 2026-08-13 21:27 |  |  | Fair | No | Found bank of three 100kva transformer found one defective drop switch cause by defective arrester.remove arrester and replaced one drop switch and one 10 amps fuse supply restored to customer
Outage | J.E.26.08.18870 | C001888098 | Ricky Hall | St.Catherine | Completed | Load_568136 | Rhodens Pen - 210 | 2026-08-13 15:47 | 2026-08-13 15:49 | 2026-08-13 18:11 | 2026-08-13 18:12 | 2026-08-13 18:43 | 2026-08-13 18:49 | 2026-08-13 18:50 | 2026-08-13 18:50 |  |  | Rains | No | Replaced blown 30 amps junction fuse
Outage | J.E.26.08.18902 | C001888097 | Ricky Hall | St.Catherine | Completed | Load_269928 | Rhodens Pen - 210 | 2026-08-13 15:47 | 2026-08-13 15:49 | 2026-08-13 16:57 | 2026-08-13 16:58 | 2026-08-13 17:30 | 2026-08-13 18:10 | 2026-08-13 18:11 | 2026-08-13 18:11 | BrokenWire |  | SevereWind | No | Splice and retention broken secondary lines use 1 clamp 1 automatic splice
Outage | J.E.26.08.18288 | C001888106 | Clyde Brown | St.Catherine | Completed | Load_240139 | Rhodens Pen - 310 | 2026-08-13 15:50 | 2026-08-13 17:27 | 2026-08-13 18:04 | 2026-08-13 18:04 | 2026-08-13 18:04 | 2026-08-13 17:43 | 2026-08-13 18:07 | 2026-08-13 18:07 |  |  | Fair | No | CT metering burnt up,open 25 kva transformer and isolate ct-meter,voltage left 113/113 and 228V
Outage | J.E.26.08.18864 | C001888102 | Clyde Brown | St.Catherine | Completed | Load_240139 | Rhodens Pen - 310 | 2026-08-13 15:50 | 2026-08-13 17:42 | 2026-08-13 17:46 | 2026-08-13 17:46 | 2026-08-13 17:46 | 2026-08-13 17:44 | 2026-08-13 17:49 | 2026-08-13 17:49 |  |  | Fair | No | 1-ct meter burnt up on transformer pole open 25 kva transformer and isolate 1- ct meter voltage now 113/113 and 228V
Outage | J.E.26.08.19249 | C001888101 | Hartley Chin | St.Catherine | Completed | Load_250595 | Rhodens Pen - 310 | 2026-08-13 15:50 | 2026-08-13 15:54 | 2026-08-13 17:31 | 2026-08-13 17:56 | 2026-08-13 17:56 | 2026-08-13 17:57 | 2026-08-13 18:01 | 2026-08-13 18:01 | TreeContact |  | Fair | No | Refer to maintenance . Line requires medium bushing
Outage | J.E.26.08.19400 | C001888118 | Clyde Brown | St.Catherine | Completed | Load_240139 | Rhodens Pen - 310 | 2026-08-13 15:55 | 2026-08-13 17:26 | 2026-08-13 17:58 | 2026-08-13 18:00 | 2026-08-13 18:00 | 2026-08-13 17:43 | 2026-08-13 18:03 | 2026-08-13 18:03 |  |  | Fair | No | CT meter burnt up on pole open 25 kva transformer and isolate ct meter ,voltage
Outage | J.E.26.08.19517 | C001888108 | Horace Malcolm | St.James | Completed | Load_266770 | Bogue - 310 | 2026-08-13 15:55 | 2026-08-13 15:56 | 2026-08-13 18:18 | 2026-08-13 18:19 | 2026-08-13 18:42 | 2026-08-13 18:43 | 2026-08-13 18:44 | 2026-08-13 18:44 |  | Y | Rains | No | Remove bamboos from primary line and reclosed one 65amp junction fuse
Outage | J.E.26.08.19535 | C001888109 | Horace Malcolm | St.James | Completed | Load_292555 | Bogue - 310 | 2026-08-13 15:55 | 2026-08-13 15:56 | 2026-08-13 18:46 | 2026-08-13 18:46 | 2026-08-13 18:46 | 2026-08-13 18:47 | 2026-08-13 18:47 | 2026-08-13 18:47 |  |  | Fair | No | Related to previous call job number 19517
Outage | J.E.26.08.19597 | C001888116 | Horace Malcolm | St.James | Completed | Load_269909 | Bogue - 310 | 2026-08-13 15:55 | 2026-08-13 15:56 | 2026-08-13 18:45 | 2026-08-13 18:45 | 2026-08-13 18:45 | 2026-08-13 18:46 | 2026-08-13 18:46 | 2026-08-13 18:46 |  |  | Fair | No | Related to previous call job number 19517
Outage | J.E.26.08.19600 | C001888117 | Horace Malcolm | St.James | Completed | Load_261708 | Bogue - 310 | 2026-08-13 15:55 | 2026-08-13 15:56 | 2026-08-13 18:44 | 2026-08-13 18:44 | 2026-08-13 18:44 | 2026-08-13 18:44 | 2026-08-13 18:44 | 2026-08-13 18:44 |  |  | Fair | No | Related to previous call job number 19517
Outage | J.E.26.08.18423 | C001888129 | Christopher West | St.Catherine | Completed | Load_556881 | Twickenham - 210 | 2026-08-13 16:04 | 2026-08-13 16:08 | 2026-08-13 17:23 | 2026-08-13 17:24 | 2026-08-13 18:00 | 2026-08-13 18:01 | 2026-08-13 18:01 | 2026-08-13 18:01 |  |  | Fair | No | Premises found closed at time of visit.
Outage | J.E.26.08.18653 | C001888128 | Christopher West | KSAS | Completed | Load_294474 | Duhaney - 210 | 2026-08-13 16:04 | 2026-08-13 16:08 | 2026-08-13 18:01 | 2026-08-13 18:02 | 2026-08-13 19:12 | 2026-08-13 19:13 | 2026-08-13 19:13 | 2026-08-13 19:13 |  |  | Fair | No | Not located, calls made to number provided went to voicemail.
Outage | J.E.26.08.19393 | C001888126 | Christopher West | Portmore | Completed | Load_242652 | Naggo Head - 510 | 2026-08-13 16:04 | 2026-08-13 16:08 | 2026-08-13 22:18 | 2026-08-13 22:19 | 2026-08-13 22:18 | 2026-08-13 20:46 | 2026-08-13 22:19 | 2026-08-13 22:19 |  |  | Fair | No | Found ok.
Outage | J.E.26.08.19461 | C001888127 | Christopher West | Portmore | Completed | Load_576117 | Naggo Head - 510 | 2026-08-13 16:04 | 2026-08-13 16:08 | 2026-08-13 22:19 | 2026-08-13 22:20 | 2026-08-13 22:19 | 2026-08-13 20:45 | 2026-08-13 22:20 | 2026-08-13 22:20 |  |  | Fair | No | Not located.
Non-Outage | J.E.26.08.15539 | C001888141 | Christopher West |  | Completed |  |  | 2026-08-13 16:05 | 2026-08-13 16:08 | 2026-08-13 22:12 | 2026-08-13 22:13 | 2026-08-13 22:12 | 2026-08-13 21:40 | 2026-08-13 22:13 | 2026-08-13 22:13 |  |  | Fair | No | Premises found closed at time of visit.
Outage | J.E.26.08.17277 | C001888139 | Christopher West | Portmore | Completed | Load_247676 | Naggo Head - 510 | 2026-08-13 16:05 | 2026-08-13 16:08 | 2026-08-13 22:17 | 2026-08-13 22:17 | 2026-08-13 22:17 | 2026-08-13 20:40 | 2026-08-13 22:18 | 2026-08-13 22:18 |  |  | Fair | No | Premises found okay.
Outage | J.E.26.08.17507 | C001888138 | Christopher West | St.Catherine | Completed | Load_254666 | Twickenham - 210 | 2026-08-13 16:05 | 2026-08-13 16:08 | 2026-08-13 19:13 | 2026-08-13 19:14 | 2026-08-13 20:02 | 2026-08-13 20:30 | 2026-08-13 20:56 | 2026-08-13 20:56 | BrokenWire |  | Fair | No | Used 100’ #6 triplex, 3 clamps & 3 pen to effect repairs after truck caused damage to customer’s stanchion, V/R 117v x2 234v, customer now okay.
Outage | J.E.26.08.17966 | C001888137 | Rodclif Dawkins | Portmore | Completed | Load_267791 | Naggo Head - 610 | 2026-08-13 16:05 | 2026-08-14 07:21 | 2026-08-14 10:30 | 2026-08-14 13:35 | 2026-08-14 14:30 | 2026-08-14 14:30 | 2026-08-14 14:30 | 2026-08-14 14:30 |  |  | Fair | No | Customer found okay
Outage | J.E.26.08.18372 | C001888130 | Christopher West | St.Catherine | Completed | Load_270130 | Twickenham - 210 | 2026-08-13 16:05 | 2026-08-13 16:08 | 2026-08-13 22:13 | 2026-08-13 22:14 | 2026-08-13 22:13 | 2026-08-13 21:35 | 2026-08-13 22:16 | 2026-08-13 22:16 | BrokenPole |  | Fair | No | 2 phase T off to Cumberland Meadows had a burnt off switch top jumper from the trip saver, trip saver was de-energized, used one clamp to effect repairs, trip saver was re-energized, area now okay.
Outage | J.E.26.08.19134 | C001888143 | Christopher West | St.Catherine | Completed | Load_264412 | Twickenham - 210 | 2026-08-13 16:06 | 2026-08-13 16:08 | 2026-08-13 16:29 | 2026-08-13 16:35 | 2026-08-13 17:10 | 2026-08-13 17:23 | 2026-08-13 17:23 | 2026-08-13 17:23 |  |  | Fair | No | V/R 117v x2 234v, in meter socket, customer was advised to check breakers.
Non-Outage | J.E.26.08.19412 | C001888144 | Christopher West | Portmore | Completed | Load_257228 | Naggo Head - 510 | 2026-08-13 16:10 | 2026-08-13 16:11 | 2026-08-13 23:08 | 2026-08-13 23:08 | 2026-08-13 23:08 | 2026-08-13 23:09 | 2026-08-13 23:09 | 2026-08-13 23:09 |  |  | Fair | No | Burnt phase at pothead, used 2 clamps for repairs, customer now ok.
Outage | J.E.26.08.16817 | C001888163 | Neville Spencer | Clarendon | Completed | Load_263360 | May Pen - 110 | 2026-08-13 16:16 | 2026-08-13 17:49 | 2026-08-13 18:42 | 2026-08-13 18:42 | 2026-08-13 19:06 | 2026-08-13 19:06 | 2026-08-13 19:43 | 2026-08-13 19:43 | BrokenWire |  | Fair | No | Install 50 ft #6 triplex, 3, clamps, 3 ,6/6 sleeves voltage reading 115 118 234 supply restored.
Non-Outage | J.E.26.08.19091 | C001888165 | Andre Smith | KSAS | Completed | Load_300873 | Cane River - 410 | 2026-08-13 16:18 | 2026-08-13 16:19 | 2026-08-13 18:59 | 2026-08-13 18:59 | 2026-08-13 20:28 | 2026-08-13 21:50 | 2026-08-13 21:50 | 2026-08-13 21:50 |  |  | Fair | No | Replace defective 15kva transformer supply restored
Non-Outage | J.E.26.08.19502 | C001888172 | Floyd Taylor |  | Completed |  |  | 2026-08-13 16:21 | 2026-08-13 16:22 | 2026-08-13 17:09 | 2026-08-13 17:10 | 2026-08-13 18:18 | 2026-08-13 20:11 | 2026-08-13 20:12 | 2026-08-13 20:12 | Fire |  | Fair | No | Cut vine from lie and splice and retention two span of secondary neutral using 30ft #2 aac and 4pg clamps voltage readings left 114,116,231
Outage | J.E.26.08.19340 | C001888173 | Dwayne Samuels | Trelawny | Completed | Load_253379 | Greenwood - 210 | 2026-08-13 16:21 | 2026-08-14 07:30 | 2026-08-14 11:40 | 2026-08-14 12:37 | 2026-08-14 12:57 | 2026-08-14 13:11 | 2026-08-14 13:12 | 2026-08-14 13:12 | BrokenWire |  | Fair | No | Check and found customer voltage ok, 115v 116v 231v. Customer was told to relocate meter from house to gate which she’s already started so that service wire can go higher as she’s requesting.
Outage | J.E.26.08.19471 | C001888169 | Floyd Taylor | Trelawny | Completed | Load_292529 | Duncans - 210 | 2026-08-13 16:21 | 2026-08-13 16:22 | 2026-08-13 20:12 | 2026-08-13 20:12 | 2026-08-13 20:51 | 2026-08-13 20:52 | 2026-08-13 20:55 | 2026-08-13 20:55 | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Found ok however customer has internal issues voltage readings left, 114,116, 232
Outage | J.E.26.08.19640 | C001888174 | Dwayne Samuels | Trelawny | Completed | Load_292482 | Greenwood - 210 | 2026-08-13 16:21 | 2026-08-14 07:30 | 2026-08-14 12:07 | 2026-08-14 13:12 | 2026-08-14 13:32 | 2026-08-14 13:39 | 2026-08-14 13:39 | 2026-08-14 13:39 |  |  | Fair | No | Illegal connection caused customer service wire to burn off used 1 once at same voltage left is 114v 116v 230v
Outage | J.E.26.08.19656 | C001888171 | Andre Williams | Trelawny | Completed | Load_267437 | Greenwood - 110 | 2026-08-13 16:21 | 2026-08-14 16:19 | 2026-08-14 17:35 | 2026-08-14 17:40 | 2026-08-14 18:32 | 2026-08-14 18:33 | 2026-08-14 18:33 | 2026-08-14 18:33 |  |  | Fair | No | Lean coroded joint at transformer pole 112+114=226
Outage | J.E.26.08.19666 | C001888176 | Hartley Chin | St.Catherine | Completed | Load_261748 | Rhodens Pen - 310 | 2026-08-13 16:21 | 2026-08-13 16:29 | 2026-08-13 17:32 | 2026-08-13 17:36 | 2026-08-13 17:36 | 2026-08-13 17:36 | 2026-08-13 17:37 | 2026-08-13 17:37 |  |  | Fair | No | Premisis found ok.
Outage | J.E.26.08.19394 | C001888179 | Ricky Hall | St.Catherine | Completed | Load_251595 | Tredegar - 210 | 2026-08-13 16:22 | 2026-08-14 07:45 | 2026-08-14 09:32 | 2026-08-14 09:33 | 2026-08-14 09:41 | 2026-08-14 09:42 | 2026-08-14 09:42 | 2026-08-14 09:42 |  |  | Fair | No | Issue was resolved on previous shift
Outage | J.E.26.08.19479 | C001888178 | Radcliffe Coleman | St.Catherine | Completed | Load_568888 | Twickenham - 310 | 2026-08-13 16:22 | 2026-08-13 16:30 | 2026-08-13 17:03 | 2026-08-13 17:07 | 2026-08-13 18:08 | 2026-08-13 18:10 | 2026-08-13 18:11 | 2026-08-13 18:11 |  |  | EarthMovement | No | Customer has an internal issue he was advised to contact his electrician to make the necessary repairs.
Outage | J.E.26.08.19610 | C001888177 | Ricky Hall | St.Catherine | Completed | Load_248250 | Tredegar - 210 | 2026-08-13 16:22 | 2026-08-14 07:45 | 2026-08-14 09:19 | 2026-08-14 09:20 | 2026-08-14 09:30 | 2026-08-14 09:32 | 2026-08-14 09:32 | 2026-08-14 09:32 |  |  | Fair | No | Issue was resolved on previous shift
Outage | J.E.26.08.19240 | C001888182 | Radcliffe Coleman | St.Catherine | Completed | Load_255497 | Twickenham - 410 | 2026-08-13 16:23 | 2026-08-13 16:31 | 2026-08-13 17:12 | 2026-08-13 18:18 | 2026-08-13 18:33 | 2026-08-13 19:45 | 2026-08-13 19:45 | 2026-08-13 19:45 |  |  | Fair | No | Area found with two blown junction fuse at different locations (25A and 15A) . Line section was patrolled and no visible fault found. The same value fuses found were replaced. Area now has supply.
Outage | J.E.26.08.19288 | C001888181 | Radcliffe Coleman | St.Catherine | Completed | Load_267832 | Twickenham - 410 | 2026-08-13 16:23 | 2026-08-13 16:31 | 2026-08-13 17:12 | 2026-08-13 18:11 | 2026-08-13 18:11 | 2026-08-13 18:17 | 2026-08-13 18:17 | 2026-08-13 18:17 | BrokenPole |  | Fair | No | Area found with a 30-C6 pole broken, with open secondary conductor attached. Customer states that when the time gets windy spark can be seen. Please refer this situation to the maintenance department for their intervention.
Outage | J.E.26.08.19315 | C001888180 | Wan Carlos Scarlett | St.Catherine | Completed | Load_258335 | Tredegar - 310 | 2026-08-13 16:23 | 2026-08-14 02:34 | 2026-08-14 04:13 | 2026-08-14 04:13 | 2026-08-14 04:15 | 2026-08-14 04:16 | 2026-08-14 04:18 | 2026-08-14 04:18 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Customer confirm that power supply has been restored
Outage | J.E.26.08.19119 | C001888183 | Ricky Hall | St.Catherine | Completed | Load_259230 | Tredegar - 410 | 2026-08-13 16:24 | 2026-08-14 07:45 | 2026-08-14 09:43 | 2026-08-14 09:44 | 2026-08-14 10:09 | 2026-08-14 10:13 | 2026-08-14 10:18 | 2026-08-14 10:18 |  |  | Fair | No | Unable to connect remotely plz refer to the relevant team
Non-Outage | J.E.26.08.18830 | C001888190 | Ricky Hall |  | Completed |  |  | 2026-08-13 16:31 | 2026-08-13 16:34 | 2026-08-13 18:52 | 2026-08-13 21:30 | 2026-08-13 22:25 | 2026-08-13 22:26 | 2026-08-13 22:26 | 2026-08-13 22:26 |  |  | Fair | No | Customer located in remote area daylight attention required
Non-Outage | J.E.26.08.19103 | C001888191 | Ricky Hall |  | Completed |  |  | 2026-08-13 16:31 | 2026-08-13 16:34 | 2026-08-13 18:11 | 2026-08-13 18:51 | 2026-08-13 18:50 | 2026-08-13 18:50 | 2026-08-13 18:51 | 2026-08-13 18:51 |  |  | Fair | No | Call associated with outage #18870
Outage | J.E.26.08.19618 | C001888193 | Tajay Bernard | Hanover | Completed | Load_255167 | Orange Bay - 310 | 2026-08-13 16:34 | 2026-08-13 16:42 | 2026-08-13 17:54 | 2026-08-13 17:55 | 2026-08-13 18:30 | 2026-08-13 18:42 | 2026-08-13 18:42 | 2026-08-13 18:42 |  |  | Fair | No | Area check and found unable to locate customer on premises multiple phone call to customer number went unanswered
Outage | J.E.26.08.19668 | C001888192 | Tajay Bernard | Hanover | Completed | Load_252795 | Orange Bay - 310 | 2026-08-13 16:34 | 2026-08-13 16:42 | 2026-08-13 16:59 | 2026-08-13 18:43 | 2026-08-13 18:43 | 2026-08-13 19:16 | 2026-08-13 19:17 | 2026-08-13 19:17 |  |  | Fair | No | Reset 1 25kva transformer Line needs to be patrol, requires daylight attention to do so, suspect illegal connections refer to maintenance
Outage | J.E.26.08.18325 | C001888197 | Tajay Bernard | Hanover | Completed | Load_238848 | Orange Bay - 310 | 2026-08-13 16:44 | 2026-08-13 16:45 | 2026-08-13 16:59 | 2026-08-13 17:00 | 2026-08-13 17:11 | 2026-08-13 17:53 | 2026-08-13 17:54 | 2026-08-13 17:54 | BrokenWire |  | Fair | No | Premises check and found, customer has internal problems. No work can be done until the customer resolved the issue, customer was advised
Non-Outage | J.E.26.08.17929 | C001888201 | Neville Spencer |  | Completed |  |  | 2026-08-13 16:53 | 2026-08-13 16:58 | 2026-08-13 22:50 | 2026-08-13 22:51 | 2026-08-13 22:50 | 2026-08-13 22:50 | 2026-08-13 22:53 | 2026-08-13 22:53 | BrokenWire |  | Fair | No | Found defective 2/0 triplex feeding approximately 20 customers line isolate need 120 ft 2/0 triplex to carry out repair.
Non-Outage | J.E.26.08.17483 | C001888207 | Clyde Brown |  | Completed |  |  | 2026-08-13 16:55 | 2026-08-13 18:07 | 2026-08-13 18:18 | 2026-08-13 18:18 | 2026-08-13 18:18 | 2026-08-13 18:35 | 2026-08-13 18:40 | 2026-08-13 18:40 | LowHangingWires |  | Fair | No | Customer said he did not make call to JPS
Outage | J.E.26.08.18494 | C001888202 | Neville Spencer | Clarendon | Completed | Load_266019 | May Pen - 110 | 2026-08-13 16:55 | 2026-08-13 16:58 | 2026-08-13 17:54 | 2026-08-13 17:55 | 2026-08-13 17:55 | 2026-08-13 17:55 | 2026-08-13 17:56 | 2026-08-13 17:56 |  |  | Fair | No | Found supply at location voltage voltage reading 113. in meter socket.
Outage | J.E.26.08.19707 | C001888209 | Milton Charlton | KSAN | Completed | Load_412987 | West Kings House - 410 | 2026-08-13 17:01 | 2026-08-13 17:02 | 2026-08-13 17:18 | 2026-08-13 17:19 | 2026-08-13 18:51 | 2026-08-13 18:20 | 2026-08-13 18:54 | 2026-08-13 18:54 |  |  | Fair | No | Reconnect customer meter that was disconnected. Reconnection was done by JPS escalation.
Outage | J.E.26.08.19110 | C001888210 | Rusean Allen | KSAS | Completed | Load_267402 | Hunts Bay - 310 | 2026-08-13 17:05 | 2026-08-14 08:28 | 2026-08-14 11:45 | 2026-08-14 11:45 | 2026-08-14 11:51 | 2026-08-14 11:54 | 2026-08-14 11:54 | 2026-08-14 11:54 |  |  | Fair | No | Line side of pothead found okay, customer was advised to contact electrician.
Outage | J.E.26.08.19223 | C001888212 | Fitzroy Turner | KSAS | Completed | Load_240083 | Hunts Bay - 510 | 2026-08-13 17:05 | 2026-08-13 17:06 | 2026-08-13 21:36 | 2026-08-13 21:37 | 2026-08-13 22:20 | 2026-08-13 22:21 | 2026-08-13 22:21 | 2026-08-13 22:21 |  |  | Fair | No | Customer supply restored after switch change and fuse replace
Outage | J.E.26.08.19398 | C001888213 | Fitzroy Turner | KSAS | Completed | Load_251504 | Hunts Bay - 510 | 2026-08-13 17:05 | 2026-08-13 17:06 | 2026-08-13 17:40 | 2026-08-13 19:39 | 2026-08-13 19:39 | 2026-08-13 19:39 | 2026-08-13 19:40 | 2026-08-13 19:40 |  |  | Fair | No | Customer have internal problems customer advised to get electrician
Outage | J.E.26.08.19681 | C001888211 | Rusean Allen | KSAS | Completed | Load_254508 | Hunts Bay - 310 | 2026-08-13 17:05 | 2026-08-14 08:28 | 2026-08-14 11:16 | 2026-08-14 11:17 | 2026-08-14 11:41 | 2026-08-14 11:44 | 2026-08-14 11:44 | 2026-08-14 11:44 |  |  | Fair | No | Broken service wire found at meter pole, wire was reconnected.
Outage | J.E.26.08.19271 | C001888220 | Hartley Chin | Clarendon | Completed | Load_263691 | Parnassus - 210 | 2026-08-13 17:12 | 2026-08-13 17:13 | 2026-08-13 20:18 | 2026-08-13 20:18 | 2026-08-13 20:18 | 2026-08-13 20:18 | 2026-08-13 20:18 | 2026-08-13 20:18 |  |  | Fair | No | Call related to 17153
Outage | J.E.26.08.19197 | C001888224 | Richard Watson | St.Elizabeth | Completed | Load_258532 | Maggotty - 110 | 2026-08-13 17:17 | 2026-08-13 17:24 | 2026-08-13 19:07 | 2026-08-13 19:07 | 2026-08-13 19:38 | 2026-08-13 19:43 | 2026-08-13 19:44 | 2026-08-13 19:44 |  |  | Fair | No | Found okay area found with electricity.
Outage | J.E.26.08.19375 | C001888226 | Raheem Ricketts | St.Elizabeth | Completed | Load_239430 | Maggotty - 210 | 2026-08-13 17:18 | 2026-08-13 17:23 | 2026-08-13 17:34 | 2026-08-13 17:44 | 2026-08-13 17:49 | 2026-08-13 01:00 | 2026-08-13 17:54 | 2026-08-13 17:54 |  |  | Fair | No | Customer says she did not make any report powere is at her house
Outage | J.E.26.08.19478 | C001888225 | Raheem Ricketts | St.Elizabeth | Completed | Load_256650 | Maggotty - 210 | 2026-08-13 17:18 | 2026-08-13 17:23 | 2026-08-13 17:34 | 2026-08-13 18:21 | 2026-08-13 19:25 | 2026-08-13 20:06 | 2026-08-13 20:06 | 2026-08-13 20:06 |  |  | Fair | No | Splice and retention 100ft of service wire remake joint at pole using 3,clamps retention secondary neutral an refuse 25 ,kva an reclosed
Outage | J.E.26.08.18537 | C001888229 | Raheem Ricketts | St.Elizabeth | Completed | Load_292706 | Maggotty - 210 | 2026-08-13 17:19 | 2026-08-13 17:23 | 2026-08-13 17:34 | 2026-08-13 17:58 | 2026-08-13 17:57 | 2026-08-13 17:58 | 2026-08-13 17:58 | 2026-08-13 17:58 |  |  | Fair | No | Unable to locate customer cell number went straight voicemail
Outage | J.E.26.08.18725 | C001888228 | Raheem Ricketts | St.Elizabeth | Completed | Load_292060 | Maggotty - 210 | 2026-08-13 17:19 | 2026-08-13 17:23 | 2026-08-13 17:34 | 2026-08-13 18:00 | 2026-08-13 18:00 | 2026-08-13 18:01 | 2026-08-13 18:01 | 2026-08-13 18:01 |  |  | Fair | No | Not my call
Outage | J.E.26.08.18822 | C001888227 | Raheem Ricketts | St.Elizabeth | Completed | Load_292190 | Maggotty - 210 | 2026-08-13 17:19 | 2026-08-13 17:23 | 2026-08-13 17:34 | 2026-08-13 17:55 | 2026-08-13 17:54 | 2026-08-13 17:55 | 2026-08-13 17:55 | 2026-08-13 17:55 |  |  | Fair | No | Check and found okay customer says jps team solved problem earlier
Outage | J.E.26.08.19476 | C001888234 | Richard Watson | St.Elizabeth | Completed | Load_244659 | Maggotty - 110 | 2026-08-13 17:24 | 2026-08-13 17:27 | 2026-08-13 17:54 | 2026-08-13 17:54 | 2026-08-13 18:20 | 2026-08-13 18:41 | 2026-08-13 18:49 | 2026-08-13 18:49 |  |  | Fair | No | Replace blown 20amp junction fuse at pole#0141451, after completing patrol no visible fault found supply restored to area.
Outage | J.E.26.08.19528 | C001888232 | Richard Watson | St.Elizabeth | Completed | Load_267768 | Maggotty - 110 | 2026-08-13 17:24 | 2026-08-13 17:27 | 2026-08-13 20:09 | 2026-08-13 20:10 | 2026-08-13 21:59 | 2026-08-13 22:29 | 2026-08-13 22:54 | 2026-08-13 22:54 |  |  | Fair | No | Found three Hexing Box with all customers out of supply namely;HX29171431, HX29171256 and HX26552497 also one customer out of supply from Sunday in hexing box HX26552260, Please refer to Field Service department bucket truck required.
Outage | J.E.26.08.19617 | C001888233 | Selvin White | St.Elizabeth | Completed | Load_256394 | Maggotty - 110 | 2026-08-13 17:24 | 2026-08-14 07:21 | 2026-08-14 10:40 | 2026-08-14 10:54 | 2026-08-14 11:19 | 2026-08-14 11:26 | 2026-08-14 11:27 | 2026-08-14 11:27 |  |  | Fair | No | Approximately 120 ft. of number six triplex service wire will be required along with a 3 wire 240 volt meter in order for customer supply to be restored as meter at location was said to be damaged during the recent hurricane. Please advise C.Johnson and Jesse Morales at the field service department
Non-Outage | J.E.26.08.18875 | C001888239 | Neville Spencer | Clarendon | Completed | Load_238054 | May Pen - 110 | 2026-08-13 17:29 | 2026-08-13 17:36 | 2026-08-13 17:58 | 2026-08-13 17:58 | 2026-08-13 18:39 | 2026-08-13 18:40 | 2026-08-13 18:41 | 2026-08-13 18:41 | BrokenPole |  | Fair | No | Unable to locate customer.
Outage | J.E.26.08.18490 | C001888240 | Clyde Brown | St.Catherine | Completed | Load_240139 | Rhodens Pen - 310 | 2026-08-13 17:29 | 2026-08-13 17:36 | 2026-08-13 17:52 | 2026-08-13 17:53 | 2026-08-13 17:52 | 2026-08-13 17:43 | 2026-08-13 17:58 | 2026-08-13 17:58 |  |  | Fair | No | CT metering burnt up at Inverness open 25 kva transformer and isolate CT meter .voltage now reading 113/113 and 228V.
Outage | J.E.26.08.19773 | C001888242 | Hartley Chin | Clarendon | Completed | Load_250549 | May Pen - 110 | 2026-08-13 17:34 | 2026-08-14 07:14 | 2026-08-14 09:25 | 2026-08-14 09:28 | 2026-08-14 10:17 | 2026-08-14 10:18 | 2026-08-14 10:19 | 2026-08-14 10:19 | Fire |  | Fair | No | Removed banging wires
Non-Outage | J.E.26.08.19674 | C001888245 | Evan Spaulding | St.Mary | Completed | Load_244370 | Highgate - 210 | 2026-08-13 17:48 | 2026-08-13 17:49 | 2026-08-13 19:28 | 2026-08-13 19:29 | 2026-08-13 19:37 | 2026-08-13 20:03 | 2026-08-13 20:04 | 2026-08-13 20:04 |  |  | Fair | No | Voltage found on left 113v,114v,227v.
Outage | J.E.26.08.19777 | C001888246 | Derrick Grubb | St.Thomas | Completed | Load_262471 | Good Year - 110 | 2026-08-13 17:49 | 2026-08-13 17:50 | 2026-08-13 17:55 | 2026-08-13 17:55 | 2026-08-13 19:39 | 2026-08-13 19:59 | 2026-08-13 19:59 | 2026-08-13 19:59 |  |  | Fair | No | Patrol and refuse 25 kva transformer
Outage | J.E.26.08.19636 | C001888249 | Richman Whyte | Westmoreland | Completed | Load_264630 | Paradise - 310 | 2026-08-13 18:04 | 2026-08-13 18:10 | 2026-08-13 20:00 | 2026-08-13 20:01 | 2026-08-13 20:00 | 2026-08-13 20:00 | 2026-08-13 20:02 | 2026-08-13 20:02 | BrokenPole |  | Fair | No | Concrete pole fell in customer yard she need it to move out sand referral to maintenance department
Outage | J.E.26.08.19745 | C001888250 | Richard Samuda | Manchester | Completed | Load_263978 | Kendal - 210 | 2026-08-13 18:04 | 2026-08-13 18:10 | 2026-08-13 18:23 | 2026-08-13 18:24 | 2026-08-13 19:10 | 2026-08-13 07:49 | 2026-08-13 19:49 | 2026-08-13 19:49 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Pole number:0105150 found 25amp junction blown patrol line found nothing replaced fuse close line customer back to normal
Outage | J.E.26.08.19760 | C001888253 | Javid Vernon | Westmoreland | Completed | Load_269379 | Paradise - 210 | 2026-08-13 18:06 | 2026-08-13 18:10 | 2026-08-13 18:20 | 2026-08-13 20:36 | 2026-08-13 20:35 | 2026-08-13 20:36 | 2026-08-13 20:36 | 2026-08-13 20:36 |  |  | Fair | No | Related to previous call job #19701
Non-Outage | J.E.26.08.19701 | C001888260 | Javid Vernon |  | Completed |  |  | 2026-08-13 18:19 | 2026-08-13 18:20 | 2026-08-13 18:24 | 2026-08-13 18:26 | 2026-08-13 19:37 | 2026-08-13 20:35 | 2026-08-13 20:35 | 2026-08-13 20:35 | BrokenWire |  | EarthMovement | No | Isolate 25kva transformer to remove vegetation an splice and retention one pole span of secondary neutral use 20ft #2 conductor and two clamps after reclosing transformer voltage left 116/113/229
Outage | J.E.26.08.19825 | C001888259 | Roxroy Needham | St.Ann | Completed | Load_252857 | Roaring River - 210 | 2026-08-13 18:19 | 2026-08-13 22:38 | 2026-08-13 23:15 | 2026-08-13 23:15 | 2026-08-13 23:15 | 2026-08-13 23:15 | 2026-08-13 23:16 | 2026-08-13 23:16 |  |  | Fair | No | Not getting customer on the phone
Outage | J.E.26.08.19824 | C001888261 | Roxroy Needham | St.Ann | Completed | Load_244071 | Cardiff Hall - 210 | 2026-08-13 18:20 | 2026-08-13 18:21 | 2026-08-13 21:06 | 2026-08-13 21:07 | 2026-08-13 21:59 | 2026-08-13 22:00 | 2026-08-13 22:00 | 2026-08-13 22:00 |  |  | Rains | No | Replace 8 amp junction fuse
Outage | J.E.26.08.19775 | C001888262 | Rodclif Dawkins | Portmore | Completed | Load_269674 | Naggo Head - 610 | 2026-08-13 18:24 | 2026-08-14 07:21 | 2026-08-14 10:28 | 2026-08-14 13:29 | 2026-08-14 13:29 | 2026-08-14 13:29 | 2026-08-14 13:32 | 2026-08-14 13:32 |  |  | Fair | No | Customer found okay
Outage | J.E.26.08.19832 | C001888264 | Roxroy Needham | St.Ann | Completed | Load_304950 | Cardiff Hall - 310 | 2026-08-13 18:26 | 2026-08-13 18:30 | 2026-08-13 19:57 | 2026-08-13 19:58 | 2026-08-13 21:04 | 2026-08-13 21:06 | 2026-08-13 21:06 | 2026-08-13 21:06 |  |  | Fair | No | Replace amp fuse for 25 KVA transformer
Outage | J.E.26.08.19668 | C001888265 | Tajay Bernard | Hanover | Completed | Load_252795 | Orange Bay - 310 | 2026-08-13 18:35 | 2026-08-13 18:36 | 2026-08-13 19:17 | 2026-08-13 19:18 | 2026-08-13 19:17 | 2026-08-13 19:25 | 2026-08-13 19:25 | 2026-08-13 19:25 |  |  | Fair | No | Related to previous call Job number 19668
Non-Outage | J.E.26.08.19850 | C001888266 | Hartley Chin |  | Completed |  |  | 2026-08-13 18:36 | 2026-08-13 18:38 | 2026-08-13 20:16 | 2026-08-13 20:17 | 2026-08-13 20:16 | 2026-08-13 20:16 | 2026-08-13 20:17 | 2026-08-13 20:17 | BrokenWire |  | Fair | No | Wrong parish. Manchester call
Outage | J.E.26.08.19861 | C001888267 | Collin Robinson | Portland | Completed | Load_260238 | Port Antonio - 410 | 2026-08-13 18:44 | 2026-08-13 18:48 | 2026-08-13 19:21 | 2026-08-13 19:22 | 2026-08-13 20:06 | 2026-08-13 20:18 | 2026-08-13 20:19 | 2026-08-13 20:19 | TreeContact |  | Rains | No | Remove palm tree limb from primary and secondary conductor and replace 20 amps junction fuse
Outage | J.E.26.08.19742 | C001888270 | Milton Charlton | KSAN | Completed | Load_293683 | Washington Blvd - 710 | 2026-08-13 18:56 | 2026-08-13 18:58 | 2026-08-13 19:08 | 2026-08-13 19:08 | 2026-08-13 19:29 | 2026-08-13 19:35 | 2026-08-13 19:39 | 2026-08-13 19:39 | Fire |  | Fair | No | Found okay upon arrival. No fire seen and customers were okay.
Outage | J.E.26.08.19856 | C001888271 | Milton Charlton | KSAN | Completed | Load_256666 | Washington Blvd - 710 | 2026-08-13 18:56 | 2026-08-13 18:58 | 2026-08-13 21:15 | 2026-08-13 21:20 | 2026-08-13 21:23 | 2026-08-13 21:10 | 2026-08-13 21:26 | 2026-08-13 21:26 | BrokenWire |  | Fair | No | Isolate 100 kva transformer at pole #0020671 and repair broken open wire secondary neutral using 50ft #2AA conductor, one #2 preform and three 1- bolt clamps and reclosed transformer switch.
Outage | J.E.26.08.18907 | C001888272 | Elvis Trowers | KSAN | Completed | Load_241915 | Washington Blvd - 710 | 2026-08-13 18:57 | 2026-08-14 07:16 | 2026-08-14 11:45 | 2026-08-14 11:46 | 2026-08-14 12:23 | 2026-08-14 12:25 | 2026-08-14 12:28 | 2026-08-14 12:28 |  |  | Fair | No | Customer service wire #6 triplex phase and neutral burn off at pothead. Repair using three 1- bolt clamps. Readings at meter socket 110-111-222 volts.
Outage | J.E.26.08.19836 | C001888273 | Rusean Allen | KSAS | Completed | Load_258334 | Rockfort - 410 | 2026-08-13 18:57 | 2026-08-14 08:50 | 2026-08-14 10:08 | 2026-08-14 10:09 | 2026-08-14 11:05 | 2026-08-14 11:16 | 2026-08-14 11:16 | 2026-08-14 11:16 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Power was restored
Non-Outage | J.E.26.08.19956 | C001888274 | Radcliffe Coleman |  | Completed |  |  | 2026-08-13 19:01 | 2026-08-13 19:04 | 2026-08-13 19:46 | 2026-08-13 19:48 | 2026-08-13 20:29 | 2026-08-13 22:26 | 2026-08-13 22:26 | 2026-08-13 22:26 | Fire |  | Fair | No | Area found with three span of open secondary neutral burnt and laying on the ground. Repairs were done with the aid of eight onebolt clamp, one #2 preform and approximately 300ft of #2 aaa conductor. A 25kva transformer was open at pole 0030435 before repairs were done. Area left okay.
Non-Outage | J.E.26.08.19976 | C001888276 | Fitzroy Turner |  | Completed |  |  | 2026-08-13 19:08 | 2026-08-13 19:08 | 2026-08-13 20:35 | 2026-08-13 20:36 | 2026-08-13 20:35 | 2026-08-13 20:35 | 2026-08-13 20:38 | 2026-08-13 20:38 | BrokenWire |  | Fair | No | Found 4wires open secondary burnt down cause by tree banging wires causing fire two span of open secondary needs to replace.2/0 conductors needed
Outage | J.E.26.08.19111 | C001888278 | Milton Charlton | KSAN | Completed | Load_257472 | Washington Blvd - 710 | 2026-08-13 19:10 | 2026-08-13 19:11 | 2026-08-13 19:39 | 2026-08-13 19:39 | 2026-08-13 21:16 | 2026-08-13 19:55 | 2026-08-13 21:19 | 2026-08-13 21:19 | Fire |  | Fair | No | Found okay upon arrival.
Outage | J.E.26.08.19736 | C001888281 | Horace Malcolm | St.James | Completed | Load_269279 | Bogue - 310 | 2026-08-13 19:36 | 2026-08-13 19:40 | 2026-08-13 21:27 | 2026-08-13 21:28 | 2026-08-13 21:50 | 2026-08-13 21:58 | 2026-08-13 21:58 | 2026-08-13 21:58 | BrokenWire |  | Fair | No | Check and found premises closed no occupant multiple calls to customer unavailable
Outage | J.E.26.08.20032 | C001888282 | Collin Robinson | Portland | Completed | Load_256366 | Port Antonio - 410 | 2026-08-13 19:38 | 2026-08-13 19:39 | 2026-08-13 20:19 | 2026-08-13 20:19 | 2026-08-13 21:12 | 2026-08-13 21:16 | 2026-08-13 21:16 | 2026-08-13 21:16 |  |  | Fair | No | Repair broken neutral joint at pothead use 1 one bolt clamp atVoltage reading 118v two service
Outage | J.E.26.08.19609 | C001888283 | Horace Malcolm | St.James | Completed | Load_242510 | Bogue - 310 | 2026-08-13 19:39 | 2026-08-14 07:32 | 2026-08-14 08:32 | 2026-08-14 08:54 | 2026-08-14 08:54 | 2026-08-14 08:57 | 2026-08-14 08:57 | 2026-08-14 08:57 |  |  | Fair | No | Check and found customer having no supply from EG box meter call center getting no communication to meter referred to field service
Outage | J.E.26.08.19815 | C001888285 | Swon Miller | St.James | Completed | Load_256840 | Queens Drive - 710 | 2026-08-13 19:39 | 2026-08-13 19:40 | 2026-08-13 21:19 | 2026-08-13 21:19 | 2026-08-13 21:58 | 2026-08-13 21:21 | 2026-08-13 22:26 | 2026-08-13 22:26 |  |  | Fair | No | Found customer with low voltage found 108/101 plz refer to field service
Outage | J.E.26.08.20026 | C001888284 | Horace Malcolm | St.James | Completed | Load_293373 | Queens Drive - 310 | 2026-08-13 19:39 | 2026-08-14 07:32 | 2026-08-14 08:57 | 2026-08-14 08:58 | 2026-08-14 09:12 | 2026-08-14 09:21 | 2026-08-14 09:21 | 2026-08-14 09:21 |  |  | Fair | No | Splice customer service nuetral wire used 10ft #6 triplex wire and 1clamp voltage 113-115-228
Outage | J.E.26.08.18855 | C001888289 | Horace Malcolm | St.James | Completed | Load_242717 | Bogue - 310 | 2026-08-13 19:40 | 2026-08-13 19:41 | 2026-08-13 22:37 | 2026-08-13 22:38 | 2026-08-13 22:51 | 2026-08-13 22:54 | 2026-08-13 22:54 | 2026-08-13 22:54 |  |  | Fair | No | Check and found premises ok supply restored voltage 113-111-224
Outage | J.E.26.08.19296 | C001888287 | Horace Malcolm | St.James | Completed | Load_301828 | Bogue - 310 | 2026-08-13 19:40 | 2026-08-13 19:41 | 2026-08-13 21:58 | 2026-08-13 22:22 | 2026-08-13 22:34 | 2026-08-13 22:37 | 2026-08-13 22:37 | 2026-08-13 22:37 | LowHangingWires |  | Fair | No | Check and found no hanging wires in area unable to reach out to customer
Outage | J.E.26.08.19358 | C001888290 | Horace Malcolm | St.James | Completed | Load_252838 | Bogue - 610 | 2026-08-13 19:40 | 2026-08-13 19:41 | 2026-08-13 20:41 | 2026-08-13 20:42 | 2026-08-13 21:12 | 2026-08-13 21:26 | 2026-08-13 21:26 | 2026-08-13 21:26 |  |  | Rains | No | Clean and remake joints at pole used 2clamps voltage 113-115-228
Outage | J.E.26.08.19621 | C001888288 | Horace Malcolm | St.James | Completed | Load_261969 | Bogue - 310 | 2026-08-13 19:40 | 2026-08-13 19:41 | 2026-08-13 20:10 | 2026-08-13 20:10 | 2026-08-13 20:39 | 2026-08-13 20:40 | 2026-08-13 20:40 | 2026-08-13 20:40 |  |  | Fair | No | Check and found premises ok customer received back supply
Outage | J.E.26.08.20005 | C001888292 | Hartley Chin | Clarendon | Completed | Load_258223 | Parnassus - 210 | 2026-08-13 19:45 | 2026-08-13 19:48 | 2026-08-13 20:35 | 2026-08-13 20:36 | 2026-08-13 20:37 | 2026-08-13 21:59 | 2026-08-13 22:01 | 2026-08-13 22:01 |  |  | Fair | No | Found 25 KVA transformer trip due to broken neutral, isolate transformer to repair 4span of neutral close transformer switch then reset transformer
Outage | J.E.26.08.20075 | C001888296 | Daniel Francis | St.Ann | Completed | Load_412921 | Ocho Rios - 510 | 2026-08-13 20:08 | 2026-08-13 20:10 | 2026-08-13 20:54 | 2026-08-13 20:59 | 2026-08-13 21:22 | 2026-08-13 21:35 | 2026-08-13 21:37 | 2026-08-13 21:37 |  |  | Fair | No | Found ok voltage 250/250/250/435/432/436
Outage | J.E.26.08.19988 | C001888303 | Ricky Hall | St.Catherine | Completed | Load_266209 | Rhodens Pen - 410 | 2026-08-13 20:10 | 2026-08-13 20:14 | 2026-08-13 20:29 | 2026-08-13 20:30 | 2026-08-13 21:22 | 2026-08-13 21:29 | 2026-08-13 21:30 | 2026-08-13 21:30 |  |  | Fair | No | Customer found with supply
Outage | J.E.26.08.19989 | C001888301 | Richard Nicholas | St.Catherine | Completed | Load_568187 | Rhodens Pen - 410 | 2026-08-13 20:10 | 2026-08-14 07:34 | 2026-08-14 10:23 | 2026-08-14 10:24 | 2026-08-14 10:44 | 2026-08-14 11:00 | 2026-08-14 11:01 | 2026-08-14 11:01 |  |  | Fair | No | Area found ok
Outage | J.E.26.08.20000 | C001888302 | Richard Nicholas | St.Catherine | Completed | Load_257485 | Rhodens Pen - 410 | 2026-08-13 20:10 | 2026-08-14 07:34 | 2026-08-14 13:33 | 2026-08-14 13:34 | 2026-08-14 14:04 | 2026-08-14 14:15 | 2026-08-14 14:16 | 2026-08-14 14:16 |  |  | Fair | No | Premises found locked however supply four ok in the area,supply was restored from last night.
Outage | J.E.26.08.20001 | C001888299 | Richard Nicholas | St.Catherine | Completed | Load_1000360 | Rhodens Pen - 410 | 2026-08-13 20:10 | 2026-08-14 07:34 | 2026-08-14 08:24 | 2026-08-14 08:24 | 2026-08-14 09:48 | 2026-08-14 10:09 | 2026-08-14 10:11 | 2026-08-14 10:11 |  |  | Fair | No | Premises found locked however slack 3w service phase connections observed at pothead.follow up to correct same,required.
Outage | J.E.26.08.20033 | C001888307 | Elvis Trowers | KSAN | Completed | Load_253996 | Washington Blvd - 710 | 2026-08-13 20:16 | 2026-08-14 07:15 | 2026-08-14 07:56 | 2026-08-14 09:51 | 2026-08-14 10:17 | 2026-08-14 09:40 | 2026-08-14 10:35 | 2026-08-14 10:35 |  |  | Fair | No | Isolate 15 kva transformer whit Y.P. Box that caught on fire at pole #0064837. Y.P. Box feeds about 15 customers which is now whit out supply. Box need to be change. Refer to field service.
Outage | J.E.26.08.19816 | C001888311 | Hartley Chin | Clarendon | Completed | Load_349049 | May Pen - 110 | 2026-08-13 20:23 | 2026-08-14 07:14 | 2026-08-14 10:27 | 2026-08-14 10:27 | 2026-08-14 12:05 | 2026-08-14 12:18 | 2026-08-14 12:23 | 2026-08-14 12:23 |  |  | Fair | No | Unable to contact customer . Meter found . Voltage reading v113- v116-v 230 . Neighbor said supply was restored last night.
Outage | J.E.26.08.19847 | C001888316 | Christopher West | St.Catherine | Completed | Load_270130 | Twickenham - 210 | 2026-08-13 20:26 | 2026-08-13 20:29 | 2026-08-13 22:09 | 2026-08-13 22:09 | 2026-08-13 22:09 | 2026-08-13 21:35 | 2026-08-13 22:09 | 2026-08-13 22:09 |  |  | Fair | No | 2 phase T off to Cumberland Meadows had a burnt off switch top jumper from the trip saver, trip saver was de-energized, used one clamp to effect repairs, trip saver was re-energized, area now okay.
Outage | J.E.26.08.19851 | C001888314 | Christopher West | St.Catherine | Completed | Load_267495 | Twickenham - 210 | 2026-08-13 20:26 | 2026-08-13 20:29 | 2026-08-13 22:10 | 2026-08-13 22:10 | 2026-08-13 22:10 | 2026-08-13 21:35 | 2026-08-13 22:11 | 2026-08-13 22:11 |  |  | Fair | No | 2 phase T off to Cumberland Meadows had a burnt off switch top jumper from the trip saver, trip saver was de-energized, used one clamp to effect repairs, trip saver was re-energized, area now okay.
Outage | J.E.26.08.19854 | C001888315 | Christopher West | St.Catherine | Completed | Load_245048 | Twickenham - 210 | 2026-08-13 20:26 | 2026-08-13 20:29 | 2026-08-13 20:57 | 2026-08-13 20:57 | 2026-08-13 21:13 | 2026-08-13 21:35 | 2026-08-13 22:08 | 2026-08-13 22:08 |  |  | Fair | No | 2 phase T off to Cumberland Meadows had a burnt off switch top jumper from the trip saver, trip saver was de-energized, used one clamp to effect repairs, trip saver was re-energized, area now okay.
Outage | J.E.26.08.19987 | C001888313 | Christopher West | St.Catherine | Completed | Load_241645 | Twickenham - 210 | 2026-08-13 20:26 | 2026-08-13 20:29 | 2026-08-13 22:11 | 2026-08-13 22:12 | 2026-08-13 22:11 | 2026-08-13 21:35 | 2026-08-13 22:12 | 2026-08-13 22:12 |  |  | Fair | No | 2 phase T off to Cumberland Meadows had a burnt off switch top jumper from the trip saver, trip saver was de-energized, used one clamp to effect repairs, trip saver was re-energized, area now okay.
Outage | J.E.26.08.20037 | C001888319 | Derrick Grubb | St.Thomas | Completed | Load_260408 | Good Year - 110 | 2026-08-13 20:36 | 2026-08-13 20:36 | 2026-08-13 21:02 | 2026-08-13 21:03 | 2026-08-13 21:50 | 2026-08-13 22:22 | 2026-08-13 22:22 | 2026-08-13 22:22 |  |  | Fair | Yes | Patrol remove illegal connections and reset 15 kva transformer
Outage | J.E.26.08.19770 | C001888323 | Antony Levy | KSAN | Completed | Load_264437 | Constant Spring - 410 | 2026-08-13 20:37 | 2026-08-13 20:40 | 2026-08-13 21:16 | 2026-08-13 21:16 | 2026-08-13 21:50 | 2026-08-13 21:58 | 2026-08-13 21:58 | 2026-08-13 21:58 |  |  | Fair | No
Outage | J.E.26.08.20073 | C001888324 | Eric Williams | KSAN | Completed | Load_257246 | Constant Spring - 410 | 2026-08-13 20:39 | 2026-08-14 07:53 | 2026-08-14 10:42 | 2026-08-14 10:42 | 2026-08-14 10:58 | 2026-08-14 11:47 | 2026-08-14 11:48 | 2026-08-14 11:48 |  |  | Fair | No | 2 blown 30amps, 2 blown 15amps and 10amps transformer fuse found and replaced cause by banging wire
Outage | J.E.26.08.20074 | C001888325 | Antony Levy | KSAN | Completed | Load_250407 | Constant Spring - 410 | 2026-08-13 20:39 | 2026-08-13 20:40 | 2026-08-14 17:06 | 2026-08-14 17:06 | 2026-08-14 18:19 | 2026-08-14 18:19 | 2026-08-14 18:20 | 2026-08-14 18:20 |  |  | Fair | No | Premises found okay with power
Outage | J.E.26.08.19735 | C001888329 | Tajay Bernard | Hanover | Completed | Load_262588 | Orange Bay - 210 | 2026-08-13 20:42 | 2026-08-13 20:44 | 2026-08-13 20:50 | 2026-08-13 20:53 | 2026-08-13 21:18 | 2026-08-13 21:50 | 2026-08-13 21:51 | 2026-08-13 21:51 |  |  | Fair | No | Refuse 1 50amp junction fuse
Outage | J.E.26.08.20039 | C001888330 | Christopher Edwards | KSAN | Completed | Load_301568 | Constant Spring - 310 | 2026-08-13 20:45 | 2026-08-13 20:46 | 2026-08-14 09:08 | 2026-08-14 10:57 | 2026-08-14 10:56 | 2026-08-14 09:17 | 2026-08-14 10:57 | 2026-08-14 10:57 |  |  | Fair | No | Customer was contacted and stated that they required meter to be resealed
Outage | J.E.26.08.20119 | C001888331 | Christopher West | St.Catherine | Completed | Load_258914 | Twickenham - 210 | 2026-08-13 20:48 | 2026-08-13 21:06 | 2026-08-13 22:20 | 2026-08-13 22:21 | 2026-08-13 22:20 | 2026-08-13 22:50 | 2026-08-13 23:08 | 2026-08-13 23:08 | BrokenWire |  | Fair | No | Broken open secondary neutral caused from a burnt off preform at the D/E point, a 50kva transformer was de-energized, used 80’ #2AA and 2 clamps to splice & retention said neutral, the burnt off preform was cleared and made safe however, requesting a memo be sent to Mr. Roy Brown to have a permanent solution effected for the location, transformer was re-energized, area now ok.
Outage | J.E.26.08.19724 | C001888346 | Javid Vernon | Westmoreland | Completed | Load_292536 | Paradise - 310 | 2026-08-13 21:19 | 2026-08-14 07:30 | 2026-08-14 07:52 | 2026-08-14 07:52 | 2026-08-14 08:21 | 2026-08-14 08:49 | 2026-08-14 08:50 | 2026-08-14 08:50 |  |  | Fair | No | Customer got disconnected for none payment but was reconnected after paying the bill voltage reading 111/113/224
Non-Outage | J.E.26.08.20053 | C001888349 | Dwayne Samuels |  | Completed |  |  | 2026-08-13 21:20 | 2026-08-14 07:30 | 2026-08-14 09:27 | 2026-08-14 09:29 | 2026-08-14 09:29 | 2026-08-14 09:29 | 2026-08-14 09:29 | 2026-08-14 09:29 | Fire |  | Fair | No | Westmoreland call
Non-Outage | J.E.26.08.19704 | C001888353 | Dwayne Samuels |  | Completed |  |  | 2026-08-13 21:24 | 2026-08-14 07:30 | 2026-08-14 09:27 | 2026-08-14 09:28 | 2026-08-14 09:28 | 2026-08-14 09:28 | 2026-08-14 09:28 | 2026-08-14 09:28 | BrokenWire |  | Fair | No | Westmoreland call
Outage | J.E.26.08.20066 | C001888352 | Andre Williams | Trelawny | Completed | Load_266224 | Martha Brae - 110 | 2026-08-13 21:24 | 2026-08-14 16:18 | 2026-08-14 17:33 | 2026-08-14 17:34 | 2026-08-14 17:33 | 2026-08-14 17:35 | 2026-08-14 17:35 | 2026-08-14 17:35 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Call related to job #20344
Outage | J.E.26.08.20121 | C001888355 | Christopher Edwards | KSAN | Completed | Load_267672 | Constant Spring - 210 | 2026-08-13 21:27 | 2026-08-14 07:19 | 2026-08-14 07:42 | 2026-08-14 08:21 | 2026-08-14 08:21 | 2026-08-14 09:08 | 2026-08-14 09:08 | 2026-08-14 09:08 |  |  | Fair | No | Customer meter socket is damaged customer was advised to get electrician to replace meter socket
Outage | J.E.26.08.20087 | C001888362 | Clyde Brown | Clarendon | Completed | Load_250524 | Parnassus - 310 | 2026-08-13 21:46 | 2026-08-14 07:13 | 2026-08-14 09:08 | 2026-08-14 09:09 | 2026-08-14 10:23 | 2026-08-14 11:32 | 2026-08-14 11:36 | 2026-08-14 11:36 | Fire |  | Fair | No | Burnt off 25 kva transformer phase lead open transformer and change 2/0 pvc 5ft-2/0 PVC phase lead,voltage 11/4/113 and 227V
Outage | J.E.26.08.20144 | C001888398 | Wan Carlos Scarlett | Portmore | Completed | Load_576246 | Naggo Head - 510 | 2026-08-13 23:13 | 2026-08-13 23:18 | 2026-08-14 01:17 | 2026-08-14 01:18 | 2026-08-14 01:18 | 2026-08-14 04:11 | 2026-08-14 04:13 | 2026-08-14 04:13 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Reset 25KVA transformer pole # 014032 nothing was found on the secondary
Outage | J.E.26.08.20194 | C001888400 | Edward Royal | KSAS | Completed | Load_253645 | Cane River - 310 | 2026-08-13 23:32 | 2026-08-13 23:33 | 2026-08-14 00:08 | 2026-08-14 00:08 | 2026-08-14 00:08 | 2026-08-14 00:10 | 2026-08-14 00:11 | 2026-08-14 00:11 | BrokenPole |  | Fair | No | Class 4 40ft broken pole need to be change on it 3 phase primary line 2 north tripe x 3 party cable reffered to maintenance pole #0119330 pole rest on customer wall
Outage | J.E.26.08.20214 | C001888402 | Elvis Trowers | KSAN | Completed | Load_256666 | Washington Blvd - 710 | 2026-08-13 23:45 | 2026-08-14 07:10 | 2026-08-14 11:02 | 2026-08-14 11:44 | 2026-08-14 11:44 | 2026-08-14 11:50 | 2026-08-14 11:44 | 2026-08-14 11:44 |  |  | Fair | No | Call related to call at 27 worrell crescent.
Outage | J.E.26.08.20249 | C001888408 | Edward Royal | KSAS | Completed | Load_266562 | Hunts Bay - 310 | 2026-08-14 01:57 | 2026-08-14 02:14 | 2026-08-14 09:06 | 2026-08-14 09:07 | 2026-08-14 09:06 | 2026-08-14 09:08 | 2026-08-14 09:17 | 2026-08-14 09:17 |  |  | Fair | No | Contact customer by phone customer said the problem was resolved
Outage | J.E.26.08.20215 | C001888435 | Elvis Trowers | KSAN | Completed | Load_261822 | Washington Blvd - 310 | 2026-08-14 07:04 | 2026-08-14 07:07 | 2026-08-14 08:25 | 2026-08-14 08:26 | 2026-08-14 09:44 | 2026-08-14 09:50 | 2026-08-14 09:50 | 2026-08-14 09:50 |  |  | Fair | No | Isolate 100 kva transformer at pole #( no pole #) and repair broken open wire secondary phase. Repair using 6ft #2 AA conductor, one #2 preform and three 1- bolt clamps. And reclose transformer switch.
Outage | J.E.26.08.20260 | C001888434 | Richard Samuda | Manchester | Completed | Load_254948 | Spur Tree - 310 | 2026-08-14 07:04 | 2026-08-14 07:06 | 2026-08-14 07:13 | 2026-08-14 07:14 | 2026-08-14 07:28 | 2026-08-14 07:58 | 2026-08-14 07:58 | 2026-08-14 07:58 |  |  | Fair | No | Refer call bucket truck required to carry out three phase line coming from main line in spur tree switch top burnt off leading into hope-ton garden refer call to maintenance over 50 customers affected
Outage | J.E.26.08.20177 | C001888442 | Richard Samuda | Manchester | Completed | Load_262087 | Kendal - 310 | 2026-08-14 07:07 | 2026-08-14 07:07 | 2026-08-14 12:32 | 2026-08-14 14:25 | 2026-08-14 14:25 | 2026-08-14 02:26 | 2026-08-14 14:26 | 2026-08-14 14:26 |  |  | Fair | No | Call to phone no answer premises not located
Outage | J.E.26.08.20210 | C001888443 | Elvis Trowers | KSAN | Completed | Load_267231 | Washington Blvd - 710 | 2026-08-14 07:09 | 2026-08-14 07:12 | 2026-08-14 11:02 | 2026-08-14 11:03 | 2026-08-14 11:34 | 2026-08-14 11:45 | 2026-08-14 11:43 | 2026-08-14 11:43 |  |  | Fair | No | Isolate 100 kva transformer at pole # . And repair open wire secondary neutral using 25 ft #2 AA conductor, one #2 preform and four 1- bolt clamps. And reclose transformer switch.
Non-Outage | J.E.26.08.20308 | C001888447 | Clyde Brown |  | Completed |  |  | 2026-08-14 07:13 | 2026-08-14 07:14 | 2026-08-14 07:40 | 2026-08-14 07:41 | 2026-08-14 08:56 | 2026-08-14 09:00 | 2026-08-14 09:08 | 2026-08-14 09:08 | BrokenWire |  | Fair | No
Non-Outage | J.E.26.08.18032 | C001888449 | Hartley Chin | Clarendon | Completed | Load_247989 | May Pen - 110 | 2026-08-14 07:15 | 2026-08-14 07:16 | 2026-08-14 13:24 | 2026-08-14 13:25 | 2026-08-14 13:59 | 2026-08-14 13:59 | 2026-08-14 14:00 | 2026-08-14 14:00 |  |  | Fair | No | Customer state problem was corrected
Non-Outage | J.E.26.08.18878 | C001888450 | Hartley Chin | Clarendon | Completed | Load_1003291 | May Pen - 110 | 2026-08-14 07:15 | 2026-08-14 07:16 | 2026-08-14 12:24 | 2026-08-14 12:24 | 2026-08-14 13:02 | 2026-08-14 13:24 | 2026-08-14 13:24 | 2026-08-14 13:24 |  |  | Fair | No | Found customer neutral clamp in street light. Clamp had corrosion. Changed clamp and separate neutrals. Reading before 113-115-227 and reading after 114-115-227
Non-Outage | J.E.26.08.20190 | C001888448 | Elvis Trowers |  | Completed |  |  | 2026-08-14 07:15 | 2026-08-14 07:16 | 2026-08-14 09:50 | 2026-08-14 12:28 | 2026-08-14 13:27 | 2026-08-14 13:00 | 2026-08-14 13:27 | 2026-08-14 13:27 |  |  | Fair | No | Duplicate call.
Non-Outage | J.E.26.08.19220 | C001888453 | Odaine Johnson | Clarendon | Completed | Load_405463 | Parnassus - 310 | 2026-08-14 07:16 | 2026-08-14 07:18 | 2026-08-14 08:02 | 2026-08-14 11:03 | 2026-08-14 11:14 | 2026-08-14 11:31 | 2026-08-14 11:32 | 2026-08-14 11:32 |  |  | Fair | No | Corroded phases and neutral found at pothead remade connection using three pen union voltage reading 116/116/232 volts
Non-Outage | J.E.26.08.19322 | C001888452 | Odaine Johnson | Clarendon | Completed | Load_260666 | Parnassus - 310 | 2026-08-14 07:16 | 2026-08-14 07:18 | 2026-08-14 08:02 | 2026-08-14 10:12 | 2026-08-14 10:54 | 2026-08-14 10:55 | 2026-08-14 10:56 | 2026-08-14 10:56 |  |  | Fair | No | Corroded neutral found at pothead remade connection using one pen union voltage reading 111/111/223 volts
Outage | J.E.26.08.19467 | C001888455 | Selvin White | St.Elizabeth | Completed | Load_291987 | Maggotty - 210 | 2026-08-14 07:18 | 2026-08-14 07:20 | 2026-08-14 09:26 | 2026-08-14 09:28 | 2026-08-14 10:06 | 2026-08-14 10:09 | 2026-08-14 10:09 | 2026-08-14 10:09 |  |  | Fair | No | Customer says supply was restored earlier this morning.
Outage | J.E.26.08.20080 | C001888456 | Selvin White | St.Elizabeth | Completed | Load_266241 | Maggotty - 110 | 2026-08-14 07:18 | 2026-08-14 07:20 | 2026-08-14 08:19 | 2026-08-14 08:19 | 2026-08-14 08:54 | 2026-08-14 08:57 | 2026-08-14 08:57 | 2026-08-14 08:57 |  |  | Fair | No | Customer cannot be contacted or located as number is an overseas one.
Outage | J.E.26.08.19277 | C001888457 | Selvin White | St.Elizabeth | Completed | Load_292795 | Maggotty - 110 | 2026-08-14 07:19 | 2026-08-14 07:21 | 2026-08-14 08:57 | 2026-08-14 08:58 | 2026-08-14 09:19 | 2026-08-14 09:25 | 2026-08-14 09:26 | 2026-08-14 09:26 |  |  | Fair | No | Customer was found to be disconnected for nonpayment of bills. Customer was advised.
Outage | J.E.26.08.20072 | C001888460 | Rodclif Dawkins | Portmore | Completed | Load_260244 | Naggo Head - 510 | 2026-08-14 07:21 | 2026-08-14 07:22 | 2026-08-14 10:12 | 2026-08-14 10:18 | 2026-08-14 10:19 | 2026-08-14 10:20 | 2026-08-14 10:21 | 2026-08-14 10:21 |  |  | Fair | No | Call number provided went t voicemail, at location doors open. No answer at gate.
Outage | J.E.26.08.20329 | C001888462 | Rodclif Dawkins | Portmore | Completed | Load_242652 | Naggo Head - 510 | 2026-08-14 07:21 | 2026-08-14 07:22 | 2026-08-14 08:48 | 2026-08-14 08:48 | 2026-08-14 09:21 | 2026-08-14 10:00 | 2026-08-14 10:09 | 2026-08-14 10:09 |  |  | Fair | No | Customer breaker was found tripped. Customer advised
Outage | J.E.26.08.19115 | C001888464 | Selvin White | St.Elizabeth | Completed | Load_250309 | Maggotty - 110 | 2026-08-14 07:23 | 2026-08-14 07:29 | 2026-08-14 10:26 | 2026-08-14 10:26 | 2026-08-14 10:45 | 2026-08-14 10:53 | 2026-08-14 10:53 | 2026-08-14 10:53 |  |  | Fair | No | Customer was contacted and said no one is currently at the premises so they would call back whenever they are at location.
Outage | J.E.26.08.20199 | C001888463 | Marlon Authors | St.Elizabeth | Completed | Load_292706 | Maggotty - 210 | 2026-08-14 07:23 | 2026-08-14 07:29 | 2026-08-14 08:16 | 2026-08-14 08:17 | 2026-08-14 08:16 | 2026-08-14 08:19 | 2026-08-14 08:19 | 2026-08-14 08:19 |  |  | Fair | No | Supply checked and found customers load side service wire damaged. Customer was advised about same, supply was disconnected at pothead
Outage | J.E.26.08.20271 | C001888465 | Selvin White | St.Elizabeth | Completed | Load_302924 | Maggotty - 110 | 2026-08-14 07:23 | 2026-08-14 07:29 | 2026-08-14 08:00 | 2026-08-14 11:28 | 2026-08-14 12:01 | 2026-08-14 12:03 | 2026-08-14 12:03 | 2026-08-14 12:03 |  |  | Fair | No | Customer was contacted and said supply was restored from yesterday.
Outage | J.E.26.08.11369 | C001888473 | Raymond Lewis | St.Ann | Completed | Load_254492 | Ocho Rios - 510 | 2026-08-14 07:27 | 2026-08-14 09:38 | 2026-08-14 12:21 | 2026-08-14 12:21 | 2026-08-14 12:30 | 2026-08-14 12:32 | 2026-08-14 12:32 | 2026-08-14 12:32 | BrokenWire |  | Fair | No | Customer say that supply has returned
Outage | J.E.26.08.20274 | C001888474 | Neckell Ormsby | St.Mary | Completed | Load_246199 | Highgate - 210 | 2026-08-14 07:27 | 2026-08-14 07:30 | 2026-08-14 07:42 | 2026-08-14 07:43 | 2026-08-14 08:39 | 2026-08-14 08:51 | 2026-08-14 08:51 | 2026-08-14 08:51 |  |  | Rains | No | Found supply ok at Site no junction fuse blown or transformer also meter ok
Outage | J.E.26.08.20302 | C001888475 | Michael Paterson | Westmoreland | Completed | Load_250896 | Paradise - 210 | 2026-08-14 07:27 | 2026-08-14 07:28 | 2026-08-14 08:07 | 2026-08-14 08:08 | 2026-08-14 09:42 | 2026-08-14 10:03 | 2026-08-14 10:15 | 2026-08-14 10:15 |  |  | Fair | No | Patrol done, found 25kva xfmr fuse blown, replace 2amps fuse, supply restored, voltage readings at xfmr 119v, 119v, 238v, Current readings 165A, 105amps, and 50amp in neutral, however, several illegal connections in area, meter count on circuit 20, crew suggesting removal of open secondary, replace with 2/0 triplex. Please refer to James Hudson at paradise, urgent attention needed.
Non-Outage | J.E.26.08.20343 | C001888478 | Elvis Trowers |  | Completed |  |  | 2026-08-14 07:28 | 2026-08-14 07:29 | 2026-08-14 10:26 | 2026-08-14 10:36 | 2026-08-14 10:38 | 2026-08-14 11:00 | 2026-08-14 11:00 | 2026-08-14 11:00 | BrokenPole |  | Fair | No | 40ft wooden pole damage in motor vehicle accident and broken in deferent three pieces. Apart of the pole is now hanging in the air held up by wires. Pole construction is T.A whit 3-phase primary and system neutral. Need immediate attention. Refer to Maintenance.
Outage | J.E.26.08.20270 | C001888476 | Oshane Warren | Westmoreland | Completed | Load_269379 | Paradise - 210 | 2026-08-14 07:28 | 2026-08-14 15:22 | 2026-08-14 18:04 | 2026-08-14 18:04 | 2026-08-14 18:04 | 2026-08-14 18:04 | 2026-08-14 18:04 | 2026-08-14 18:04 |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.08.20311 | C001888479 | Royston Montague | St.Catherine | Completed | Load_248181 | Tredegar - 410 | 2026-08-14 07:29 | 2026-08-14 07:31 | 2026-08-14 08:15 | 2026-08-14 08:47 | 2026-08-14 09:49 | 2026-08-14 10:09 | 2026-08-14 10:12 | 2026-08-14 10:12 |  |  | Fair | No | Faulty neutral joint at pothead, same corrected. Voltage found 232v 128v 102v voltage after job completion are 232v 116v 115v
Non-Outage | J.E.26.08.19420 | C001888483 | Royston Montague | St.Catherine | Completed | Load_265928 | Tredegar - 510 | 2026-08-14 07:30 | 2026-08-14 07:31 | 2026-08-14 08:15 | 2026-08-14 10:13 | 2026-08-14 11:17 | 2026-08-14 12:36 | 2026-08-14 12:36 | 2026-08-14 12:36 | LowHangingWires |  | Fair | No | Location found ok. Tree removed.
Non-Outage | J.E.26.08.19646 | C001888480 | Royston Montague | St.Catherine | Completed | Load_238168 | Twickenham - 310 | 2026-08-14 07:30 | 2026-08-14 07:31 | 2026-08-14 08:15 | 2026-08-14 14:17 | 2026-08-14 15:29 | 2026-08-14 16:20 | 2026-08-14 16:20 | 2026-08-14 16:20 |  |  | Fair | No | Faulty meter socket, customer asked to get an electrician to repair same. Voltage 227v 112v 113v
Non-Outage | J.E.26.08.20103 | C001888482 | Royston Montague | St.Catherine | Completed | Load_251765 | Tredegar - 510 | 2026-08-14 07:30 | 2026-08-14 07:31 | 2026-08-14 08:15 | 2026-08-14 12:57 | 2026-08-14 13:09 | 2026-08-14 14:15 | 2026-08-14 14:16 | 2026-08-14 14:16 |  |  | Fair | No | Slack meter in socket, same corrected. Voltage 229v 114v 115v
Outage | J.E.26.08.19985 | C001888487 | Damion Reid | Manchester | Completed | Load_257939 | Porus - 310 | 2026-08-14 07:33 | 2026-08-14 16:19 | 2026-08-14 16:47 | 2026-08-14 16:48 | 2026-08-14 17:21 | 2026-08-14 17:28 | 2026-08-14 17:29 | 2026-08-14 17:29 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.20071 | C001888488 | Damion Reid | Manchester | Completed | Load_269864 | Kendal - 210 | 2026-08-14 07:33 | 2026-08-14 16:19 | 2026-08-14 17:29 | 2026-08-14 17:30 | 2026-08-14 18:58 | 2026-08-14 19:25 | 2026-08-14 19:26 | 2026-08-14 19:26 |  |  | Fair | No | Customer was disconnected for outstanding light bill
Outage | J.E.26.08.20151 | C001888486 | Ryan Richards | Manchester | Completed | Load_263292 | Kendal - 210 | 2026-08-14 07:33 | 2026-08-14 07:35 | 2026-08-14 07:53 | 2026-08-14 09:20 | 2026-08-14 09:46 | 2026-08-14 10:46 | 2026-08-14 10:47 | 2026-08-14 10:47 |  |  | Fair | No | Corroded phase and neutral drop lead found for 25kva transformer open transformer and remade drop lead using 3 one bolt clamps and reclose transformer voltage 119/120/240 volts
Outage | J.E.26.08.20154 | C001888489 | Richard Nicholas | St.Catherine | Completed | Load_241272 | Rhodens Pen - 410 | 2026-08-14 07:34 | 2026-08-14 07:36 | 2026-08-14 11:39 | 2026-08-14 11:40 | 2026-08-14 13:01 | 2026-08-14 13:32 | 2026-08-14 13:33 | 2026-08-14 13:33 |  |  | Fair | No | This premises is located in bog walk and not point hill,please refer to the crew that is working in that area.
Outage | J.E.26.08.19835 | C001888492 | Ricky Hall | St.Catherine | Completed | Load_251791 | Tredegar - 310 | 2026-08-14 07:35 | 2026-08-14 07:36 | 2026-08-14 08:05 | 2026-08-14 08:05 | 2026-08-14 08:47 | 2026-08-14 08:56 | 2026-08-14 08:57 | 2026-08-14 08:57 |  |  | Fair | No | Premises closed
Outage | J.E.26.08.20301 | C001888490 | Ricky Hall | St.Catherine | Completed | Load_243154 | Tredegar - 410 | 2026-08-14 07:35 | 2026-08-14 07:36 | 2026-08-14 08:57 | 2026-08-14 08:58 | 2026-08-14 09:15 | 2026-08-14 09:18 | 2026-08-14 09:19 | 2026-08-14 09:19 |  |  | Fair | No | Site found with supply
Outage | J.E.26.08.20355 | C001888491 | Edward Royal | KSAS | Completed |  |  | 2026-08-14 07:35 | 2026-08-14 07:36 | 2026-08-14 07:40 | 2026-08-14 07:40 | 2026-08-14 07:40 | 2026-08-14 08:01 | 2026-08-14 08:02 | 2026-08-14 08:02 |  |  | Fair | No | Total meter burnt and new to be replaced reffered to field service
Non-Outage | J.E.26.08.19040 | C001888495 | Dwayne Samuels | Trelawny | Completed | Load_265112 | Greenwood - 210 | 2026-08-14 07:38 | 2026-08-14 07:39 | 2026-08-14 11:31 | 2026-08-14 11:32 | 2026-08-14 12:07 | 2026-08-14 12:27 | 2026-08-14 12:28 | 2026-08-14 12:28 |  |  | Fair | No | Corrosion at pothead was the cause of customer low voltage use 1 linket at same for repairs voltage left 116v/116v/232v
Non-Outage | J.E.26.08.19592 | C001888493 | Dwayne Samuels | Trelawny | Completed | Load_292361 | Greenwood - 210 | 2026-08-14 07:38 | 2026-08-14 07:39 | 2026-08-14 10:12 | 2026-08-14 10:12 | 2026-08-14 10:34 | 2026-08-14 11:06 | 2026-08-14 11:30 | 2026-08-14 11:30 |  |  | Fair | No | Illegal connections is the cause of customer low voltage, voltage found arrival on line 107v/100v/207 refer to the losses team
Non-Outage | J.E.26.08.19615 | C001888494 | Dwayne Samuels | Trelawny | Completed | Load_260885 | Greenwood - 110 | 2026-08-14 07:38 | 2026-08-14 07:39 | 2026-08-14 09:31 | 2026-08-14 09:32 | 2026-08-14 09:47 | 2026-08-14 10:03 | 2026-08-14 10:05 | 2026-08-14 10:05 |  |  | Fair | No | Check and found area working ok voltage found at pot head 120v/120v/240v customer stanchion is defective
Non-Outage | J.E.26.08.20138 | C001888496 | Horace Malcolm | St.James | Completed | Load_574885 | Rose Hall - 210 | 2026-08-14 07:39 | 2026-08-14 07:39 | 2026-08-14 08:22 | 2026-08-14 08:22 | 2026-08-14 08:22 | 2026-08-14 08:23 | 2026-08-14 08:23 | 2026-08-14 08:23 |  |  | Fair | No | Isolate three junction fuses
Outage | J.E.26.08.20328 | C001888499 | Derrick Grubb | St.Thomas | Completed | Load_243194 | Good Year - 210 | 2026-08-14 07:41 | 2026-08-14 12:23 | 2026-08-14 15:12 | 2026-08-14 15:13 | 2026-08-14 15:12 | 2026-08-14 15:13 | 2026-08-14 15:13 | 2026-08-14 15:13 |  |  | Fair | No | Patrol and refuse one 25 amp switch in easington
Outage | J.E.26.08.20351 | C001888497 | Derrick Grubb | St.Thomas | Completed | Load_238855 | Good Year - 210 | 2026-08-14 07:41 | 2026-08-14 12:23 | 2026-08-14 15:13 | 2026-08-14 15:14 | 2026-08-14 15:13 | 2026-08-14 15:14 | 2026-08-14 15:14 | 2026-08-14 15:14 |  |  | Fair | No | Patrol and refuse one 25 amp switch in easington
Outage | J.E.26.08.20357 | C001888498 | Derrick Grubb | St.Thomas | Completed | Load_577235 | Good Year - 210 | 2026-08-14 07:41 | 2026-08-14 12:23 | 2026-08-14 15:45 | 2026-08-14 15:45 | 2026-08-14 15:45 | 2026-08-14 15:45 | 2026-08-14 15:46 | 2026-08-14 15:46 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.20359 | C001888514 | Tyrese Williams | St.Ann | Completed | Load_255760 | Cardiff Hall - 310 | 2026-08-14 07:46 | 2026-08-14 07:49 | 2026-08-14 08:03 | 2026-08-14 08:12 | 2026-08-14 08:45 | 2026-08-14 10:09 | 2026-08-14 10:09 | 2026-08-14 10:09 |  |  | Fair | No | Premises not found
Outage | J.E.26.08.19755 | C001888516 | Milton Charlton | KSAN | Completed | Load_263443 | Hope - 510 | 2026-08-14 07:49 | 2026-08-14 07:52 | 2026-08-14 10:44 | 2026-08-14 10:45 | 2026-08-14 12:27 | 2026-08-14 12:50 | 2026-08-14 14:27 | 2026-08-14 14:27 | Fire |  | Fair | No | Refused and reclosed one 3 amps transformer switch at pole #0112974 using one 3 amps fuse.
Outage | J.E.26.08.19834 | C001888519 | Milton Charlton | KSAS | Completed | Load_261156 | Up Park Camp - 410 | 2026-08-14 07:49 | 2026-08-14 07:51 | 2026-08-14 10:41 | 2026-08-14 10:41 | 2026-08-14 10:41 | 2026-08-14 10:45 | 2026-08-14 10:42 | 2026-08-14 10:42 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.20146 | C001888517 | Eric Williams | KSAN | Completed | Load_243409 | Constant Spring - 410 | 2026-08-14 07:49 | 2026-08-14 07:53 | 2026-08-14 11:49 | 2026-08-14 11:49 | 2026-08-14 12:09 | 2026-08-14 12:10 | 2026-08-14 12:10 | 2026-08-14 12:10 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.20217 | C001888518 | Eric Williams | KSAN | Completed | Load_1006939 | Washington Blvd - 610 | 2026-08-14 07:49 | 2026-08-14 07:54 | 2026-08-14 12:10 | 2026-08-14 12:11 | 2026-08-14 12:56 | 2026-08-14 12:57 | 2026-08-14 12:57 | 2026-08-14 12:57 |  |  | Fair | No | Premises found okay customer break was off
Outage | J.E.26.08.20327 | C001888515 | Milton Charlton | KSAS | Completed | Load_261156 | Up Park Camp - 410 | 2026-08-14 07:49 | 2026-08-14 07:50 | 2026-08-14 09:56 | 2026-08-14 09:57 | 2026-08-14 10:34 | 2026-08-14 10:35 | 2026-08-14 10:38 | 2026-08-14 10:38 |  |  | Fair | No | Refused and reclosed 5amps transformer switch at pole #0007418 or 563625 using one 5 amps transformer fuse.
Outage | J.E.26.08.19030 | C001888520 | Eric Williams | KSAS | Completed | Load_579129 | Duhaney - 310 | 2026-08-14 07:50 | 2026-08-14 07:56 | 2026-08-14 09:17 | 2026-08-14 09:18 | 2026-08-14 09:25 | 2026-08-14 09:27 | 2026-08-14 09:28 | 2026-08-14 09:28 | TreeContact | Y | Fair | No | 3 wire open secondary, major bushing required, back yard, refer to maintenance department
Non-Outage | J.E.26.08.17382 | C001888524 | Kemark Slue | St.Catherine | Completed | Load_250536 | New Michelton - 310 | 2026-08-14 07:54 | 2026-08-14 07:56 | 2026-08-14 08:52 | 2026-08-14 08:52 | 2026-08-14 10:46 | 2026-08-14 08:50 | 2026-08-14 10:47 | 2026-08-14 10:47 |  |  | Fair | No | Premises was checked and found okay.
Non-Outage | J.E.26.08.19620 | C001888523 | Kemark Slue | St.Catherine | Completed | Load_258753 | New Michelton - 210 | 2026-08-14 07:54 | 2026-08-14 07:56 | 2026-08-14 10:47 | 2026-08-14 10:48 | 2026-08-14 11:00 | 2026-08-14 09:19 | 2026-08-14 11:10 | 2026-08-14 11:10 |  |  | Fair | No | Upon arrival at the location the crew discovered that customer is been fed from and enclosure and is allegedly without supply from the 11th of July 2026 please refer to Moses Elliston to effectively carry out repairs.
Non-Outage | J.E.26.08.16385 | C001888525 | Kemark Slue | St.Catherine | Completed | Load_244952 | New Michelton - 210 | 2026-08-14 07:55 | 2026-08-14 07:56 | 2026-08-14 11:10 | 2026-08-14 11:11 | 2026-08-14 12:09 | 2026-08-14 11:00 | 2026-08-14 12:43 | 2026-08-14 12:43 |  |  | Fair | No | Upon arrival at the location the crew discovered that a section of the neutral from triplex service supplying customer was wrapped and corroded, terminate conductor splice and retention service using approximately 3ft of service neutral and two one bolt clamps.
Non-Outage | J.E.26.08.19417 | C001888526 | Andrae Clarke | Portland | Completed | Load_245066 | Port Antonio - 410 | 2026-08-14 07:57 | 2026-08-14 07:59 | 2026-08-14 08:03 | 2026-08-14 08:19 | 2026-08-14 08:56 | 2026-08-14 09:17 | 2026-08-14 09:10 | 2026-08-14 09:10 |  |  | Fair | No | Premises found okay Check voltage 117/119/236
Non-Outage | J.E.26.08.04783 | C001888531 | Oraine Minto | St.Ann | Completed | Load_241843 | Roaring River - 210 | 2026-08-14 08:02 | 2026-08-14 08:29 | 2026-08-14 10:52 | 2026-08-14 12:06 | 2026-08-14 12:06 | 2026-08-14 12:25 | 2026-08-14 12:25 | 2026-08-14 12:25 |  |  | Fair | No | Power was restored
Non-Outage | J.E.26.07.37669 | C001888537 | Raymond Lewis | St.Ann | Completed | Load_574360 | Cardiff Hall - 210 | 2026-08-14 08:04 | 2026-08-14 08:05 | 2026-08-14 08:34 | 2026-08-14 08:35 | 2026-08-14 08:37 | 2026-08-14 08:42 | 2026-08-14 08:42 | 2026-08-14 08:42 |  |  | Fair | No | Several call was made to customer and no answer
Non-Outage | J.E.26.07.39618 | C001888538 | Raymond Lewis | St.Ann | Completed | Load_574271 | Roaring River - 210 | 2026-08-14 08:04 | 2026-08-14 08:05 | 2026-08-14 08:30 | 2026-08-14 08:31 | 2026-08-14 08:30 | 2026-08-14 08:32 | 2026-08-14 08:32 | 2026-08-14 08:32 |  |  | Fair | No | Supply restored
Outage | J.E.26.08.20387 | C001888563 | Eric Williams | KSAS | Completed | Load_244470 | Duhaney - 310 | 2026-08-14 08:18 | 2026-08-14 08:19 | 2026-08-14 09:28 | 2026-08-14 09:29 | 2026-08-14 10:06 | 2026-08-14 10:40 | 2026-08-14 10:40 | 2026-08-14 10:40 |  |  | Fair | No | Blown 3amps transformer fuse found and replace
Outage | J.E.26.08.20392 | C001888571 | Milton Charlton | KSAN | Completed | Load_269307 | Hope - 510 | 2026-08-14 08:22 | 2026-08-14 08:25 | 2026-08-14 14:29 | 2026-08-14 14:29 | 2026-08-14 15:09 | 2026-08-14 15:10 | 2026-08-14 15:15 | 2026-08-14 15:15 |  |  | Fair | No | Found okay upon arrival. Customer did not report a problem.
Non-Outage | J.E.26.08.20398 | C001888595 | Edward Royal | KSAS | Completed | Load_264521 | Duhaney - 310 | 2026-08-14 08:26 | 2026-08-14 08:27 | 2026-08-14 11:48 | 2026-08-14 11:48 | 2026-08-14 11:48 | 2026-08-14 12:53 | 2026-08-14 12:54 | 2026-08-14 12:54 |  |  | Fair | No | Number 6 service cable need to step up to number 2 tripe x approximately 100ft needed
Non-Outage | J.E.26.08.18833 | C001888596 | Dwain Samuels | Westmoreland | Completed | Load_263858 | Paradise - 110 | 2026-08-14 08:28 | 2026-08-14 08:30 | 2026-08-14 08:47 | 2026-08-14 09:15 | 2026-08-14 09:39 | 2026-08-14 09:59 | 2026-08-14 10:24 | 2026-08-14 10:24 |  |  | Fair | No | Corrosion found at 3 wire pot head . Voltage check 103-105-208. Corrosion clear use 3 pen union clamp. Voltage check 114-115-229
Non-Outage | J.E.26.08.19137 | C001888597 | Oshane Warren | Westmoreland | Completed | Load_268696 | Paradise - 210 | 2026-08-14 08:28 | 2026-08-14 15:22 | 2026-08-14 18:02 | 2026-08-14 18:02 | 2026-08-14 18:02 | 2026-08-14 18:02 | 2026-08-14 18:02 | 2026-08-14 18:02 | Fire |  | Fair | No | Unable to locate or contact customer
Outage | J.E.26.08.20153 | C001888599 | Derrick Dawkins | St.James | Completed | Load_567820 | Bogue - 610 | 2026-08-14 08:29 | 2026-08-15 09:18 | 2026-08-15 09:47 | 2026-08-15 09:48 | 2026-08-15 09:49 | 2026-08-15 09:51 | 2026-08-15 09:52 | 2026-08-15 09:52 |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.07.34804 | C001888605 | Raymond Lewis | St.Ann | Completed | Load_248710 | Ocho Rios - 310 | 2026-08-14 08:30 | 2026-08-14 08:32 | 2026-08-14 08:43 | 2026-08-14 08:44 | 2026-08-14 09:49 | 2026-08-14 09:52 | 2026-08-14 09:53 | 2026-08-14 09:53 |  |  | Fair | No | Found water pump running,225/234/238//408/403/405
Outage | J.E.26.08.20273 | C001888604 | Richard Samuda | Manchester | Completed | Load_292487 | Spur Tree - 310 | 2026-08-14 08:30 | 2026-08-14 09:59 | 2026-08-14 10:46 | 2026-08-14 10:46 | 2026-08-14 11:14 | 2026-08-14 11:38 | 2026-08-14 11:38 | 2026-08-14 11:38 |  |  | Fair | No | Found ok voltage 118, 120 238
Non-Outage | J.E.26.08.20093 | C001888621 | Locksley Allen | St.Mary | Completed | Load_256596 | Blackstonedge - 110 | 2026-08-14 08:38 | 2026-08-14 08:40 | 2026-08-14 09:45 | 2026-08-14 10:25 | 2026-08-14 10:25 | 2026-08-14 10:32 | 2026-08-14 10:29 | 2026-08-14 10:29 |  |  | Fair | No | The neutral and lower conductor is lying on the ground in the Change Hill area,after you pass the Carron Hall Health center
Non-Outage | J.E.26.08.20292 | C001888620 | Locksley Allen | St.Mary | Completed | Load_268253 | Blackstonedge - 110 | 2026-08-14 08:38 | 2026-08-14 08:40 | 2026-08-14 11:27 | 2026-08-14 11:30 | 2026-08-14 11:29 | 2026-08-14 11:36 | 2026-08-14 11:33 | 2026-08-14 11:33 |  |  | Fair | No | The neutral burst and is lying on the ground. Duplicate
Non-Outage | J.E.26.08.20336 | C001888619 | Cliton Henry | St.Mary | Completed | Load_264056 | Oracabessa - 210 | 2026-08-14 08:38 | 2026-08-14 09:44 | 2026-08-14 11:32 | 2026-08-14 11:33 | 2026-08-14 11:32 | 2026-08-14 11:33 | 2026-08-14 11:34 | 2026-08-14 11:34 |  |  | Fair | No | Supply restored, related to outage # 20347
Non-Outage | J.E.26.08.20347 | C001888618 | Cliton Henry | St.Mary | Completed | Load_264056 | Oracabessa - 210 | 2026-08-14 08:38 | 2026-08-14 09:44 | 2026-08-14 10:47 | 2026-08-14 10:47 | 2026-08-14 10:47 | 2026-08-14 11:27 | 2026-08-14 11:31 | 2026-08-14 11:31 |  |  | Fair | No | A burnt off transformer drop lead found for a 50 kva transformer at pole # 0013440. The 50 kva transformer was de energized to carryout repairs. Corrective work done to reconnected the transformer drop leads using 4 one bolt clamps. Voltages left 119-119/238 volts
Non-Outage | J.E.26.08.20374 | C001888608 | Locksley Allen | St.Mary | Completed | Load_268253 | Blackstonedge - 110 | 2026-08-14 08:38 | 2026-08-14 08:40 | 2026-08-14 10:30 | 2026-08-14 11:23 | 2026-08-14 11:22 | 2026-08-14 11:30 | 2026-08-14 11:27 | 2026-08-14 11:27 |  |  | Fair | No | The neutral burst and is lying on the ground
Outage | J.E.26.08.20344 | C001888637 | Andre Williams | Trelawny | Completed | Load_266224 | Martha Brae - 110 | 2026-08-14 08:42 | 2026-08-14 16:18 | 2026-08-14 16:26 | 2026-08-14 16:36 | 2026-08-14 17:09 | 2026-08-14 17:31 | 2026-08-14 17:33 | 2026-08-14 17:33 | BrokenWire |  | Fair | No | Replace 20 ft defective #6 from Jps pole to pothead one customer disconnected meter burn meter also barrel lock reffer to field service to remove so customer can carry out repairs voltage 117+117=234 volts
Non-Outage | J.E.26.08.20430 | C001888649 | Tyrese Williams | St.Ann | Completed | Load_240850 | Cardiff Hall - 310 | 2026-08-14 08:52 | 2026-08-14 08:53 | 2026-08-14 08:58 | 2026-08-14 10:10 | 2026-08-14 11:37 | 2026-08-14 12:43 | 2026-08-14 12:43 | 2026-08-14 12:43 |  |  | Fair | No | Recommend service wire from transformer to meter to be change recommend 120ft off #2 triple x service wire
Non-Outage | J.E.26.08.20432 | C001888650 | Edward Royal |  | Completed |  |  | 2026-08-14 08:53 | 2026-08-14 08:54 | 2026-08-14 13:27 | 2026-08-14 13:28 | 2026-08-14 13:27 | 2026-08-14 13:32 | 2026-08-14 13:32 | 2026-08-14 13:32 |  |  | Fair | No | Meter is not yet install to rami system reffered to field service
Non-Outage | J.E.26.08.17485 | C001888668 | Fredrick Hamilton | KSAN | Completed | Load_240009 | Hope - 410 | 2026-08-14 08:58 | 2026-08-14 09:03 | 2026-08-14 09:09 | 2026-08-14 13:51 | 2026-08-14 13:52 | 2026-08-14 13:53 | 2026-08-14 13:53 | 2026-08-14 13:53 | LeaningPole |  | Fair | No | Please assign to emergency Leaning pole
Non-Outage | J.E.26.08.17614 | C001888669 | Fredrick Hamilton | KSAN | Completed | Load_240009 | Hope - 410 | 2026-08-14 08:58 | 2026-08-14 09:03 | 2026-08-14 09:09 | 2026-08-14 13:43 | 2026-08-14 13:42 | 2026-08-14 13:43 | 2026-08-14 13:44 | 2026-08-14 13:44 | LeaningPole |  | Fair | No | Please assign to emergency Leaning pole
Non-Outage | J.E.26.08.19493 | C001888666 | Richard Samuda | Manchester | Completed | Load_241376 | Spur Tree - 310 | 2026-08-14 08:58 | 2026-08-14 08:59 | 2026-08-14 09:32 | 2026-08-14 09:33 | 2026-08-14 09:40 | 2026-08-14 09:43 | 2026-08-14 09:43 | 2026-08-14 09:43 | Fire |  | Fair | No | There was a bush fire in area that damaged pole pole needs to be replaced but a referral was already written
Non-Outage | J.E.26.08.20378 | C001888670 | Fredrick Hamilton | KSAN | Completed | Load_555972 | Hope - 510 | 2026-08-14 08:58 | 2026-08-14 09:02 | 2026-08-14 09:07 | 2026-08-14 13:26 | 2026-08-14 13:26 | 2026-08-14 13:27 | 2026-08-14 13:27 | 2026-08-14 13:27 |  |  | Fair | No | Customer defect detected Customer advised
Non-Outage | J.E.26.08.20380 | C001888671 | Fredrick Hamilton | KSAN | Completed | Load_555972 | Hope - 510 | 2026-08-14 08:58 | 2026-08-14 08:59 | 2026-08-14 09:07 | 2026-08-14 12:34 | 2026-08-14 12:51 | 2026-08-14 13:26 | 2026-08-14 13:26 | 2026-08-14 13:26 |  |  | Fair | No | Customer defect observed on pothead Customer was advised
Outage | J.E.26.08.20424 | C001888667 | Dean- Smith | Hanover | Completed | Load_240829 | Orange Bay - 310 | 2026-08-14 08:58 | 2026-08-14 08:59 | 2026-08-14 10:57 | 2026-08-14 10:59 | 2026-08-14 12:05 | 2026-08-14 12:05 | 2026-08-14 13:35 | 2026-08-14 13:35 | LowHangingWires |  | Fair | No | Retention secondary conductors phase and neutral. To correct low hanging sec conductors across road way.... area need bushing.
Outage | J.E.26.08.20433 | C001888665 | Dean- Smith | Hanover | Completed | Load_248013 | Orange Bay - 310 | 2026-08-14 08:58 | 2026-08-14 08:59 | 2026-08-14 14:55 | 2026-08-14 14:55 | 2026-08-14 14:55 | 2026-08-14 14:55 | 2026-08-14 14:55 | 2026-08-14 14:55 |  |  | Fair | No | Shift ended
Non-Outage | J.E.26.08.17249 | C001888690 | Fredrick Hamilton | KSAS | Completed | Load_255821 | Up Park Camp - 410 | 2026-08-14 09:04 | 2026-08-14 09:05 | 2026-08-14 09:09 | 2026-08-14 11:46 | 2026-08-14 11:45 | 2026-08-14 12:30 | 2026-08-14 12:31 | 2026-08-14 12:31 |  |  | Fair | No | 234.8v/232.6v/235.3v117.2v/117.0v/201.7v obtained No issues detected at time of visit
Non-Outage | J.E.26.08.18990 | C001888691 | Fredrick Hamilton | KSAS | Completed | Load_261156 | Up Park Camp - 410 | 2026-08-14 09:04 | 2026-08-14 09:07 | 2026-08-14 09:10 | 2026-08-14 11:33 | 2026-08-14 11:34 | 2026-08-14 11:35 | 2026-08-14 11:35 | 2026-08-14 11:35 |  |  | Fair | No | Premises found locked multiple calls to customer went to voicemail
Non-Outage | J.E.26.08.20439 | C001888692 | Fredrick Hamilton | KSAS | Completed | Load_261156 | Up Park Camp - 410 | 2026-08-14 09:04 | 2026-08-14 09:08 | 2026-08-14 09:12 | 2026-08-14 10:40 | 2026-08-14 10:46 | 2026-08-14 11:25 | 2026-08-14 11:25 | 2026-08-14 11:25 |  |  | Fair | No | 244.8v/231.5v/245.1vCustomer defect detected and customer was advised No defect on JPS supply
Outage | J.E.26.08.20176 | C001888700 | Marlon Authors | St.Elizabeth | Completed | Load_239430 | Maggotty - 210 | 2026-08-14 09:05 | 2026-08-14 09:06 | 2026-08-14 11:38 | 2026-08-14 11:38 | 2026-08-14 11:39 | 2026-08-14 12:14 | 2026-08-14 12:14 | 2026-08-14 12:14 |  |  | SevereWind | No | Patrol and found tree putting the secondary upper phase and neutral together whenever the wind blows. Cut and remove same and reset 25 kva transformer circuit at pole #034110. Restored supply ok
Non-Outage | J.E.26.08.18322 | C001888704 | Rochaine Hussey | KSAN | Completed | Load_259808 | Washington Blvd - 510 | 2026-08-14 09:08 | 2026-08-14 09:11 | 2026-08-14 10:09 | 2026-08-14 14:24 | 2026-08-14 14:24 | 2026-08-14 14:26 | 2026-08-14 14:26 | 2026-08-14 14:26 |  |  | Fair | No | Customer said issue was already resolved
Non-Outage | J.E.26.08.18880 | C001888702 | Rochaine Hussey | KSAN | Completed | Load_267043 | Washington Blvd - 410 | 2026-08-14 09:08 | 2026-08-14 09:10 | 2026-08-14 09:22 | 2026-08-14 13:33 | 2026-08-14 13:32 | 2026-08-14 13:33 | 2026-08-14 13:33 | 2026-08-14 13:33 |  |  | Fair | No | Customer said issue was already resolved
Non-Outage | J.E.26.08.19172 | C001888703 | Rochaine Hussey | KSAN | Completed | Load_248496 | Washington Blvd - 410 | 2026-08-14 09:08 | 2026-08-14 09:11 | 2026-08-14 11:17 | 2026-08-14 11:18 | 2026-08-14 12:12 | 2026-08-14 12:13 | 2026-08-14 12:13 | 2026-08-14 12:13 |  |  | Fair | No | Customer was called multiple times Unable to locate
Outage | J.E.26.08.20420 | C001888715 | Michael Paterson | Westmoreland | Completed | Load_262337 | Paradise - 210 | 2026-08-14 09:13 | 2026-08-14 09:14 | 2026-08-14 10:31 | 2026-08-14 10:31 | 2026-08-14 10:47 | 2026-08-14 10:55 | 2026-08-14 10:56 | 2026-08-14 10:56 |  |  | Fair | No | Customer meter is burnt, however customer is getting single phase, please refer to Mr, Chessane Beckford paradise to address matter speedily.
Non-Outage | J.E.26.08.18867 | C001888717 | Rochaine Hussey | KSAS | Completed | Load_247943 | Duhaney - 310 | 2026-08-14 09:14 | 2026-08-14 09:17 | 2026-08-14 10:37 | 2026-08-14 10:37 | 2026-08-14 10:50 | 2026-08-14 11:16 | 2026-08-14 11:16 | 2026-08-14 11:16 |  |  | Fair | No | Low voltage coming from the transformer due to the amount of cable wires and etc I’m unable to fix the issue Bucket trucker truck needed 103/102/210v more than 1 customer is affected
Outage | J.E.26.08.20155 | C001888716 | Oshane Warren | Westmoreland | Completed | Load_269379 | Paradise - 210 | 2026-08-14 09:14 | 2026-08-14 15:22 | 2026-08-14 18:02 | 2026-08-14 18:03 | 2026-08-14 18:03 | 2026-08-14 18:03 | 2026-08-14 18:03 | 2026-08-14 18:03 |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.08.20464 | C001888725 | Cliton Henry | St.Mary | Completed | Load_259797 | Oracabessa - 210 | 2026-08-14 09:16 | 2026-08-14 09:44 | 2026-08-14 12:00 | 2026-08-14 12:00 | 2026-08-14 12:00 | 2026-08-14 12:31 | 2026-08-14 12:32 | 2026-08-14 12:32 |  |  | Fair | No | A single phase condition found coming from the RAMI infrastructure enclosure HEX 06689 HX27121969. Kindly refer to Field Service Department for a corrective action. Voltage found 0-116/116 volts
Non-Outage | J.E.26.08.19673 | C001888734 | Odeanie Davis | KSAS | Completed | Load_269065 | Three Miles - 410 | 2026-08-14 09:18 | 2026-08-14 09:23 | 2026-08-14 09:50 | 2026-08-14 09:51 | 2026-08-14 10:03 | 2026-08-14 10:40 | 2026-08-14 10:36 | 2026-08-14 10:36 |  |  | Fair | No | 151v/87v at arrival, open neutral at secondary corrected, 1 one bolt clamp, 118v/118v & 237v after correction.
Non-Outage | J.E.26.08.19822 | C001888732 | Odeanie Davis | KSAN | Completed | Load_254822 | Washington Blvd - 310 | 2026-08-14 09:18 | 2026-08-14 09:22 | 2026-08-14 11:42 | 2026-08-14 11:44 | 2026-08-14 11:48 | 2026-08-14 12:12 | 2026-08-14 12:09 | 2026-08-14 12:09 |  |  | Fair | No | 95v/121v at arrival, open neutral at pothead corrected, 1 one bolt clamp,108v/108v & 217v after correction,
Non-Outage | J.E.26.08.20083 | C001888733 | Odeanie Davis | KSAS | Completed | Load_237770 | Rockfort - 410 | 2026-08-14 09:18 | 2026-08-14 09:21 | 2026-08-14 14:19 | 2026-08-14 14:20 | 2026-08-14 14:19 | 2026-08-14 13:59 | 2026-08-14 14:20 | 2026-08-14 14:20 | Fire |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.20159 | C001888731 | Odeanie Davis | KSAS | Completed | Load_1002654 | Cane River - 310 | 2026-08-14 09:18 | 2026-08-14 09:21 | 2026-08-14 14:20 | 2026-08-14 14:21 | 2026-08-14 14:20 | 2026-08-14 14:27 | 2026-08-14 14:27 | 2026-08-14 14:27 |  |  | Fair | No | Customer defective meter socket at location, customer electrician fixed issue, however meter is damaged on load side and needs to be replaced, meter was ping and communicating fine.
Non-Outage | J.E.26.08.20204 | C001888729 | Odeanie Davis | KSAN | Completed | Load_253996 | Washington Blvd - 710 | 2026-08-14 09:18 | 2026-08-14 09:21 | 2026-08-14 10:37 | 2026-08-14 10:37 | 2026-08-14 10:56 | 2026-08-14 11:09 | 2026-08-14 11:11 | 2026-08-14 11:11 | Fire |  | Fair | No | Post # 0064837120 Olympic WAY Kingston 11Customer stated that rammi box catch fire on the 13 of aug in the night. we observed the rammi box lock with burn mark and the fuse open above it. No electricity in that area that the rammi box service currently
Non-Outage | J.E.26.08.20241 | C001888728 | Odeanie Davis | KSAN | Completed | Load_256666 | Washington Blvd - 710 | 2026-08-14 09:18 | 2026-08-14 09:20 | 2026-08-14 11:17 | 2026-08-14 11:18 | 2026-08-14 11:17 | 2026-08-14 11:40 | 2026-08-14 11:41 | 2026-08-14 11:41 |  |  | Fair | No | 108v/104v & 212v at location, open neutral on secondary line was resolved by Jps
Outage | J.E.26.08.19651 | C001888777 | Marlon Authors | St.Elizabeth | Completed | Load_258483 | Maggotty - 210 | 2026-08-14 09:40 | 2026-08-14 11:33 | 2026-08-14 18:09 | 2026-08-14 18:09 | 2026-08-14 18:28 | 2026-08-14 18:33 | 2026-08-14 18:33 | 2026-08-14 18:33 |  |  | Fair | No | Customer said he reset his breaker and the supply was restored
Outage | J.E.26.08.20502 | C001888779 | Romeo Brissett | St.James | Completed | Load_256227 | Bogue - 310 | 2026-08-14 09:40 | 2026-08-14 09:41 | 2026-08-14 14:45 | 2026-08-14 14:45 | 2026-08-14 14:45 | 2026-08-14 14:43 | 2026-08-14 14:46 | 2026-08-14 14:46 |  |  | Fair | No | Check and found ok, (1)65amps tripsaver was energize at Johns Hall
Outage | J.E.26.08.20504 | C001888778 | Romeo Brissett | St.James | Completed | Load_243460 | Bogue - 310 | 2026-08-14 09:40 | 2026-08-14 09:41 | 2026-08-14 14:47 | 2026-08-14 14:47 | 2026-08-14 14:47 | 2026-08-14 14:41 | 2026-08-14 14:47 | 2026-08-14 14:47 |  |  | Fair | No | Check and found ok
Outage | J.E.26.08.20473 | C001888783 | Horace Malcolm | St.James | Completed | Load_250893 | Bogue - 310 | 2026-08-14 09:41 | 2026-08-14 09:43 | 2026-08-14 09:51 | 2026-08-14 09:52 | 2026-08-14 09:52 | 2026-08-14 11:53 | 2026-08-14 11:53 | 2026-08-14 11:53 |  |  | Fair | No | Disconnect defective lightening arrester and refuse one 50kva transformer used 5amp fuse
Outage | J.E.26.08.20483 | C001888782 | Romeo Brissett | St.James | Completed | Load_245164 | Bogue - 310 | 2026-08-14 09:41 | 2026-08-14 09:41 | 2026-08-14 10:08 | 2026-08-14 10:09 | 2026-08-14 14:27 | 2026-08-14 14:25 | 2026-08-14 14:38 | 2026-08-14 14:38 |  |  | Fair | No | Line patrolled and found clear and safe to energize reclosed (1)65amps
Outage | J.E.26.08.20497 | C001888781 | Romeo Brissett | St.James | Completed | Load_269909 | Bogue - 310 | 2026-08-14 09:41 | 2026-08-14 09:41 | 2026-08-14 14:46 | 2026-08-14 14:46 | 2026-08-14 14:46 | 2026-08-14 14:35 | 2026-08-14 14:46 | 2026-08-14 14:46 |  |  | Fair | No | Check and found ok
Outage | J.E.26.08.20499 | C001888780 | Romeo Brissett | St.James | Completed | Load_244217 | Bogue - 310 | 2026-08-14 09:41 | 2026-08-14 09:41 | 2026-08-14 10:08 | 2026-08-14 14:49 | 2026-08-14 14:49 | 2026-08-14 14:40 | 2026-08-14 14:50 | 2026-08-14 14:50 |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.08.20472 | C001888784 | Cliton Henry | St.Mary | Completed | Load_264056 | Oracabessa - 210 | 2026-08-14 09:44 | 2026-08-14 09:45 | 2026-08-14 11:36 | 2026-08-14 11:36 | 2026-08-14 11:36 | 2026-08-14 11:36 | 2026-08-14 11:37 | 2026-08-14 11:37 |  |  | Fair | No | Supply restored, related to outage #20347
Outage | J.E.26.08.20482 | C001888786 | Cliton Henry | St.Mary | Completed | Load_352793 | Oracabessa - 210 | 2026-08-14 09:45 | 2026-08-14 09:47 | 2026-08-14 11:48 | 2026-08-14 11:48 | 2026-08-14 11:48 | 2026-08-14 11:48 | 2026-08-14 11:50 | 2026-08-14 11:50 |  |  | Fair | No | The customer meter found disconnected and was reconnected with the assistance from dispatch and the escalation team.
Outage | J.E.26.08.20534 | C001888788 | Neckell Ormsby | St.Mary | Completed | Load_242507 | Highgate - 210 | 2026-08-14 09:49 | 2026-08-14 09:50 | 2026-08-14 09:55 | 2026-08-14 09:55 | 2026-08-14 10:51 | 2026-08-14 11:11 | 2026-08-14 11:11 | 2026-08-14 11:11 | Fire |  | Fair | No | Leaning concrete with 50 kva transformer needs straighten customer pothead holding up pole please refer to maintenance department no pole number seen
Non-Outage | J.E.26.08.20368 | C001888791 | Odaine Johnson | Clarendon | Completed | Load_264303 | Parnassus - 310 | 2026-08-14 09:52 | 2026-08-14 09:53 | 2026-08-14 10:56 | 2026-08-14 10:57 | 2026-08-14 10:59 | 2026-08-14 10:59 | 2026-08-14 10:59 | 2026-08-14 10:59 |  |  | Fair | No | Premises found okay customer stated that the issue was resolved
Non-Outage | J.E.26.08.20446 | C001888792 | Odaine Johnson | Clarendon | Completed | Load_261027 | Parnassus - 310 | 2026-08-14 09:52 | 2026-08-14 09:53 | 2026-08-14 11:33 | 2026-08-14 11:34 | 2026-08-14 11:42 | 2026-08-14 11:45 | 2026-08-14 11:45 | 2026-08-14 11:45 |  |  | Fair | No | Wire coming from primary to switch top burn off at bank of three pole number 0108590 emergency team needed
Outage | J.E.26.08.20530 | C001888794 | Ricky Hall | St.Catherine | Completed | Load_269928 | Rhodens Pen - 210 | 2026-08-14 09:53 | 2026-08-14 09:55 | 2026-08-14 11:34 | 2026-08-14 11:34 | 2026-08-14 12:35 | 2026-08-14 14:42 | 2026-08-14 14:45 | 2026-08-14 14:45 | LowHangingWires |  | Fair | No | Retention banging secondary lines remake burnt off secondary phase jumper replaced burnt out fuse holder and 10 a mp fuse
Outage | J.E.26.08.20564 | C001888807 | Ryan Richards | Manchester | Completed | Load_248339 | Kendal - 210 | 2026-08-14 10:02 | 2026-08-14 10:02 | 2026-08-14 13:01 | 2026-08-14 13:02 | 2026-08-14 14:58 | 2026-08-14 16:40 | 2026-08-14 16:42 | 2026-08-14 16:42 |  |  | Fair | Yes | Corroded phase an neural found for 4 wire service remade corroded phase and neutral at pothead and pole using 8 one bolt clamps voltage 119/117/237/204 volt
Outage | J.E.26.08.20436 | C001888814 | Tyrese Williams | St.Ann | Completed | Load_260720 | Cardiff Hall - 210 | 2026-08-14 10:05 | 2026-08-14 10:10 | 2026-08-14 10:48 | 2026-08-14 13:10 | 2026-08-14 14:34 | 2026-08-14 14:55 | 2026-08-14 14:58 | 2026-08-14 14:58 |  | Y | Fair | No | Cut tree from line and Replace a 15 amp junction fuse at pole
Outage | J.E.26.08.20421 | C001888815 | Richard Watson | St.Elizabeth | Completed | Load_253154 | Maggotty - 210 | 2026-08-14 10:06 | 2026-08-14 18:09 | 2026-08-14 18:22 | 2026-08-14 18:22 | 2026-08-14 18:42 | 2026-08-14 19:19 | 2026-08-14 19:19 | 2026-08-14 19:19 |  |  | Fair | No | Customer not ready for re-connection, meter socket defective and it’s not wired. Unable to reach customer by phone message left with resident in the area.
Outage | J.E.26.08.20513 | C001888817 | Raymond Lewis | St.Ann | Completed | Load_556127 | Roaring River - 410 | 2026-08-14 10:07 | 2026-08-14 10:12 | 2026-08-14 12:33 | 2026-08-14 12:34 | 2026-08-14 12:58 | 2026-08-14 12:59 | 2026-08-14 12:59 | 2026-08-14 12:59 | Fire |  | Fair | No | Jps team members at work
Outage | J.E.26.08.20567 | C001888818 | Raymond Lewis | St.Ann | Completed | Load_242953 | Roaring River - 410 | 2026-08-14 10:07 | 2026-08-14 10:12 | 2026-08-14 12:59 | 2026-08-14 13:00 | 2026-08-14 15:47 | 2026-08-14 15:53 | 2026-08-14 15:53 | 2026-08-14 15:53 |  |  | Fair | No | The area have low voltage secondary jumper need to ampack
Outage | J.E.26.08.20516 | C001888831 | Rodclif Dawkins | Portmore | Completed | Load_255246 | Naggo Head - 510 | 2026-08-14 10:11 | 2026-08-14 10:12 | 2026-08-14 10:27 | 2026-08-14 10:27 | 2026-08-14 10:57 | 2026-08-14 10:57 | 2026-08-14 11:26 | 2026-08-14 11:26 |  |  | Fair | No | Customer found okay
Outage | J.E.26.08.19993 | C001888844 | Richard Nicholas | St.Catherine | Completed | Load_241575 | Rhodens Pen - 410 | 2026-08-14 10:15 | 2026-08-14 10:16 | 2026-08-14 11:01 | 2026-08-14 11:02 | 2026-08-14 11:23 | 2026-08-14 11:38 | 2026-08-14 11:39 | 2026-08-14 11:39 |  |  | Fair | No | Area found ok
Outage | J.E.26.08.20003 | C001888843 | Richard Nicholas | St.Catherine | Completed | Load_1000361 | Rhodens Pen - 410 | 2026-08-14 10:15 | 2026-08-14 10:16 | 2026-08-14 14:17 | 2026-08-14 14:17 | 2026-08-14 15:04 | 2026-08-14 15:04 | 2026-08-14 15:04 | 2026-08-14 15:04 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.20565 | C001888848 | Hartley Chin | Clarendon | Completed | Load_579450 | May Pen - 110 | 2026-08-14 10:20 | 2026-08-14 10:20 | 2026-08-15 07:42 | 2026-08-15 07:42 | 2026-08-15 07:42 | 2026-08-15 07:42 | 2026-08-15 07:43 | 2026-08-15 07:43 | Fire |  | Fair | No | Found ok. Matter was dealt with yesterday
Outage | J.E.26.08.20655 | C001888871 | Richard Samuda | Manchester | Completed | Load_256623 | Kendal - 310 | 2026-08-14 10:42 | 2026-08-14 10:43 | 2026-08-14 11:39 | 2026-08-14 11:39 | 2026-08-14 12:16 | 2026-08-14 12:17 | 2026-08-14 12:17 | 2026-08-14 12:17 |  |  | Fair | No | Found ok customer said they didn’t make a call
Outage | J.E.26.08.20582 | C001888873 | Richard Watson | St.Elizabeth | Completed | Load_241223 | Maggotty - 210 | 2026-08-14 10:46 | 2026-08-14 18:08 | 2026-08-14 19:20 | 2026-08-14 19:20 | 2026-08-14 19:46 | 2026-08-14 20:42 | 2026-08-14 20:48 | 2026-08-14 20:48 |  |  | Fair | No | Replace approximately 70ft of #6 triplex service wire, also use three 1bolt clamps and three #6-#6 service sleeves, voltages left inside meter socket 113v, 117v, 230v, customer was without supply since hurricane Melissa.
Outage | J.E.26.08.20653 | C001888874 | Roxroy Needham | St.Ann | Completed | Load_339987 | Roaring River - 410 | 2026-08-14 10:46 | 2026-08-14 23:10 | 2026-08-14 23:18 | 2026-08-14 23:18 | 2026-08-14 23:45 | 2026-08-14 23:47 | 2026-08-14 23:46 | 2026-08-14 23:46 |  |  | Fair | No | Premises found ok call customer and customer say that JPS team come before
Non-Outage | J.E.26.08.20053 | C001888876 | Michael Paterson |  | Completed |  |  | 2026-08-14 10:53 | 2026-08-14 10:54 | 2026-08-14 11:34 | 2026-08-14 11:34 | 2026-08-14 12:11 | 2026-08-14 16:19 | 2026-08-14 16:19 | 2026-08-14 16:19 | Fire |  | Fair | No | Assessment done in area, found 2/0 triplex Burnt, had to replace approximately 80ft 2/0 triplex, remade joints using six clamps, supply restored was restored, voltage readings 117v, 117v, 234v
Outage | J.E.26.08.20649 | C001888878 | Clyde Brown | Clarendon | Completed | Load_241995 | Parnassus - 210 | 2026-08-14 10:58 | 2026-08-14 11:02 | 2026-08-14 13:06 | 2026-08-14 13:06 | 2026-08-14 13:06 | 2026-08-14 13:03 | 2026-08-14 13:09 | 2026-08-14 13:09 |  |  | Fair | No | Cannot be located customer not answering phone
Outage | J.E.26.08.20601 | C001888885 | Rusean Allen | KSAS | Completed | Load_253645 | Cane River - 310 | 2026-08-14 11:12 | 2026-08-14 11:27 | 2026-08-14 12:40 | 2026-08-14 12:41 | 2026-08-14 13:06 | 2026-08-14 13:11 | 2026-08-14 13:11 | 2026-08-14 13:11 | BrokenPole |  | Fair | No | Broken 35ft pole containing; single phase primary and #2 trplx wires found.Pole needs to be changed asap, refer to maintenance department.
Outage | J.E.26.08.20631 | C001888884 | Rusean Allen | KSAS | Completed | Load_250421 | Cane River - 410 | 2026-08-14 11:12 | 2026-08-14 13:21 | 2026-08-14 17:26 | 2026-08-14 17:31 | 2026-08-14 18:23 | 2026-08-14 18:54 | 2026-08-14 18:54 | 2026-08-14 18:54 |  |  | Fair | No | Wire at H2 bushing on transformer found dislodged , wire was reconnected.
Outage | J.E.26.08.20705 | C001888883 | Milton Charlton | KSAS | Completed | Load_251380 | Up Park Camp - 510 | 2026-08-14 11:12 | 2026-08-14 13:20 | 2026-08-14 16:24 | 2026-08-14 16:43 | 2026-08-14 18:03 | 2026-08-14 18:55 | 2026-08-14 18:33 | 2026-08-14 18:33 | Fire |  | Fair | No | Found okay upon arrival. Customer has an internal problem.
Non-Outage | J.E.26.08.20299 | C001888887 | Christopher Edwards | KSAN | Completed | Load_239920 | Constant Spring - 410 | 2026-08-14 11:13 | 2026-08-14 11:18 | 2026-08-14 12:13 | 2026-08-14 12:14 | 2026-08-14 12:57 | 2026-08-14 14:16 | 2026-08-14 14:17 | 2026-08-14 14:17 |  |  | Fair | No | Isolate 50 kva transformer to Splice and retention broken open secondary wire Using:40ft #2 AA conductor 1 #2 preform 2 one bolt clamps
Non-Outage | J.E.26.08.20652 | C001888886 | Christopher Edwards | KSAN | Completed | Load_267505 | Constant Spring - 310 | 2026-08-14 11:13 | 2026-08-14 11:18 | 2026-08-14 11:28 | 2026-08-14 11:47 | 2026-08-14 12:06 | 2026-08-14 12:12 | 2026-08-14 12:13 | 2026-08-14 12:13 |  |  | Fair | No | Customer was contacted and stated that they would rather a night visit Any time after 9:00pm
Outage | J.E.26.08.20708 | C001888888 | Neckell Ormsby | St.Mary | Completed | Load_256596 | Blackstonedge - 110 | 2026-08-14 11:17 | 2026-08-14 11:19 | 2026-08-14 11:34 | 2026-08-14 11:35 | 2026-08-14 12:45 | 2026-08-14 13:55 | 2026-08-14 13:56 | 2026-08-14 13:56 | BrokenWire |  | Fair | No | Found broken secondary open 25 kva transformer to splice and retention 3- pole span secondary using approximately 50ft #2AA,6- one bolt clamps and 1- #2 preform reclose transformer no pole number seen
Non-Outage | J.E.26.08.20374 | C001888890 | Neckell Ormsby | St.Mary | Completed | Load_268253 | Blackstonedge - 110 | 2026-08-14 11:26 | 2026-08-14 11:27 | 2026-08-14 13:56 | 2026-08-14 13:57 | 2026-08-14 14:51 | 2026-08-14 15:26 | 2026-08-14 15:27 | 2026-08-14 15:27 |  |  | Fair | No | Found broken secondary neutral open 50kva transformer to splice and retention neutral using approximately 15 ft #2 AA, and2- one bolt clamps and reclose transformer no pole # seen
Outage | J.E.26.08.20713 | C001888891 | Denton Williams | St.Mary | Completed | Load_269660 | Annotto Bay - 210 | 2026-08-14 11:30 | 2026-08-14 11:31 | 2026-08-14 11:41 | 2026-08-14 11:41 | 2026-08-14 12:16 | 2026-08-14 12:16 | 2026-08-14 12:19 | 2026-08-14 12:19 | Fire | Y | Fair | No | Open 25 kva transformer and cut mango tree limb from line, close up after completion.
Outage | J.E.26.08.20722 | C001888892 | Clyde Brown | Clarendon | Completed | Load_248888 | Monymusk - 410 | 2026-08-14 11:37 | 2026-08-14 11:38 | 2026-08-14 11:53 | 2026-08-14 11:54 | 2026-08-14 12:49 | 2026-08-14 12:52 | 2026-08-14 13:05 | 2026-08-14 13:05 |  |  | SevereWind | No | Blown 30 amps junction fuse at Clifton ,line patrolled and only heavy winds in area,blown fuse replaced.
Outage | J.E.26.08.20739 | C001888893 | Rusean Allen | KSAS | Completed | Load_240083 | Hunts Bay - 510 | 2026-08-14 11:38 | 2026-08-14 11:39 | 2026-08-14 12:15 | 2026-08-14 12:16 | 2026-08-14 12:29 | 2026-08-14 12:35 | 2026-08-14 12:38 | 2026-08-14 12:38 |  |  | Fair | No | Hexing failure Hex00790. Customer service having issues reconnecting meter, refer to field service department.
Outage | J.E.26.08.19688 | C001888895 | Marlon Authors | St.Elizabeth | Completed | Load_252693 | Maggotty - 210 | 2026-08-14 11:46 | 2026-08-14 11:47 | 2026-08-14 12:19 | 2026-08-14 12:20 | 2026-08-14 12:52 | 2026-08-14 12:58 | 2026-08-14 12:58 | 2026-08-14 12:58 | LeaningPole |  | Fair | No | Patrol and found customer meter pole leaning on another customer’s fence. Not JPS pole
Outage | J.E.26.08.20481 | C001888898 | Derrick Grubb | St.Thomas | Completed | Load_238855 | Good Year - 210 | 2026-08-14 11:50 | 2026-08-14 12:23 | 2026-08-14 15:11 | 2026-08-14 15:11 | 2026-08-14 15:11 | 2026-08-14 15:11 | 2026-08-14 15:12 | 2026-08-14 15:12 |  |  | Fair | No | Patrol and refuse one 25 amp switch in easington
Outage | J.E.26.08.20732 | C001888899 | Derrick Grubb | St.Thomas | Completed | Load_243194 | Good Year - 210 | 2026-08-14 11:51 | 2026-08-14 12:23 | 2026-08-14 15:09 | 2026-08-14 15:09 | 2026-08-14 15:09 | 2026-08-14 15:10 | 2026-08-14 15:11 | 2026-08-14 15:11 |  |  | Fair | No | Patrol and refuse one 25 amp switch in easington
Outage | J.E.26.08.20747 | C001888901 | Oshane Warren | Westmoreland | Completed | Load_269379 | Paradise - 210 | 2026-08-14 11:53 | 2026-08-14 15:22 | 2026-08-14 15:46 | 2026-08-14 15:46 | 2026-08-14 17:47 | 2026-08-14 17:55 | 2026-08-14 17:56 | 2026-08-14 17:56 |  |  | Fair | No | Replace 2amp 25 kva transformer fuse
Outage | J.E.26.08.20760 | C001888900 | Javid Vernon | Westmoreland | Completed | Load_245455 | Paradise - 310 | 2026-08-14 11:53 | 2026-08-14 11:53 | 2026-08-14 12:07 | 2026-08-14 12:08 | 2026-08-14 13:14 | 2026-08-14 13:47 | 2026-08-14 13:49 | 2026-08-14 13:49 |  |  | Fair | No | Splice and retention customer service wire use 40ft #6 triplex wire and 2 clamps voltage left at premises 114
Outage | J.E.26.08.20833 | C001888993 | Richard Watson | St.Elizabeth | Completed | Load_291985 | Maggotty - 210 | 2026-08-14 12:10 | 2026-08-14 18:08 | 2026-08-14 20:49 | 2026-08-14 20:50 | 2026-08-14 21:00 | 2026-08-14 21:06 | 2026-08-14 21:06 | 2026-08-14 21:06 |  |  | Fair | No | Customer contacted by phone and stated that he did not make any report to JPS.
Non-Outage | J.E.26.08.20734 | C001889000 | Locksley Allen |  | Completed |  |  | 2026-08-14 12:18 | 2026-08-14 12:19 | 2026-08-14 12:29 | 2026-08-14 14:10 | 2026-08-14 14:10 | 2026-08-14 14:18 | 2026-08-14 14:15 | 2026-08-14 14:15 | BrokenWire |  | Fair | No | Tree drop on the line and pull down the JPS pole(concrete) that is at the end of the line. Pole blocking the road
Outage | J.E.26.08.20792 | C001889001 | Christopher Edwards | KSAN | Completed | Load_239618 | Constant Spring - 210 | 2026-08-14 12:20 | 2026-08-14 12:28 | 2026-08-14 14:18 | 2026-08-14 14:18 | 2026-08-14 15:19 | 2026-08-14 15:33 | 2026-08-14 15:57 | 2026-08-14 15:57 |  |  | Fair | No | Remake burnt phase joints at pole Using (2) one bolt clamps Voltage:112,113,218
Outage | J.E.26.08.20873 | C001889044 | Cliton Henry | St.Mary | Completed | Load_257332 | Highgate - 210 | 2026-08-14 12:28 | 2026-08-14 12:36 | 2026-08-14 12:41 | 2026-08-14 12:42 | 2026-08-14 13:38 | 2026-08-14 13:56 | 2026-08-14 13:56 | 2026-08-14 13:56 | Fire |  | Fair | No | The secondary conductors found banging when the wind blown. A 25 kva transformer was de energized to carryout repairs. Corrective work done to retention the secondary phase conductor using 2#2 preform. The supply was restored to energized to 25 kva transformer.
Outage | J.E.26.08.18725 | C001889045 | Selvin White | St.Elizabeth | Completed | Load_292060 | Maggotty - 210 | 2026-08-14 12:29 | 2026-08-14 13:00 | 2026-08-14 13:41 | 2026-08-14 13:41 | 2026-08-14 14:13 | 2026-08-14 14:15 | 2026-08-14 14:16 | 2026-08-14 14:16 |  |  | Fair | No | Customer says supply was restored from yesterday in the morning.
Outage | J.E.26.08.20877 | C001889053 | Tyrese Williams | St.Ann | Completed | Load_255760 | Cardiff Hall - 310 | 2026-08-14 12:31 | 2026-08-14 12:33 | 2026-08-14 12:44 | 2026-08-14 12:44 | 2026-08-14 12:55 | 2026-08-14 13:00 | 2026-08-14 13:10 | 2026-08-14 13:10 |  |  | Fair | No | Meter found burnt recommend meter to be change
Outage | J.E.26.08.20860 | C001889059 | Marlon Authors | Manchester | Completed | Load_238761 | Spur Tree - 210 | 2026-08-14 12:38 | 2026-08-14 12:40 | 2026-08-14 14:27 | 2026-08-14 14:27 | 2026-08-14 16:03 | 2026-08-14 16:39 | 2026-08-14 16:39 | 2026-08-14 16:39 | Fire |  | SevereWind | Yes | Patrol and found trees putting the secondary conductors together whenever the wind blows. Cut and remove same, retention one pole span of secondary upper phase and replace one blown 1.5 amp fuse that protect 25 kva transformer circuit no pole #. Restored supply okay
Outage | J.E.26.08.20688 | C001889069 | Richard Samuda | Manchester | Completed | Load_262087 | Kendal - 310 | 2026-08-14 12:44 | 2026-08-14 12:45 | 2026-08-14 13:04 | 2026-08-14 13:16 | 2026-08-14 13:15 | 2026-08-14 01:50 | 2026-08-14 13:50 | 2026-08-14 13:50 |  |  | SevereWind | No | Found 50 kva transformer blown patrol line found nothing replaced fuse customer back to normal
Outage | J.E.26.08.20881 | C001889070 | Richard Samuda | Manchester | Completed | Load_255372 | Kendal - 310 | 2026-08-14 12:45 | 2026-08-14 12:45 | 2026-08-14 14:03 | 2026-08-14 14:03 | 2026-08-14 14:24 | 2026-08-14 02:24 | 2026-08-14 14:25 | 2026-08-14 14:25 |  |  | Fair | No | Call to phone no answer premises not located
Outage | J.E.26.08.20900 | C001889075 | Milton Charlton | KSAS | Completed | Load_261156 | Up Park Camp - 410 | 2026-08-14 12:50 | 2026-08-14 12:51 | 2026-08-14 15:15 | 2026-08-14 15:16 | 2026-08-14 15:54 | 2026-08-14 15:10 | 2026-08-14 16:26 | 2026-08-14 16:26 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.20866 | C001889099 | Romeo Brissett | St.James | Completed | Load_259607 | Bogue - 510 | 2026-08-14 13:06 | 2026-08-14 13:07 | 2026-08-14 14:48 | 2026-08-14 14:48 | 2026-08-14 14:48 | 2026-08-14 14:45 | 2026-08-14 14:48 | 2026-08-14 14:48 | BrokenWire |  | Fair | No | Hanover call
Outage | J.E.26.08.20783 | C001889109 | Elvis Trowers | KSAN | Completed | Load_259801 | Washington Blvd - 710 | 2026-08-14 13:12 | 2026-08-14 13:14 | 2026-08-14 13:28 | 2026-08-14 13:28 | 2026-08-14 14:07 | 2026-08-14 14:00 | 2026-08-14 14:09 | 2026-08-14 14:09 |  |  | Fair | No | Customer complaining about street light at pole #0020410 not working.
Outage | J.E.26.08.20755 | C001889117 | Rusean Allen | KSAS | Completed | Load_269392 | Cane River - 410 | 2026-08-14 13:19 | 2026-08-14 13:20 | 2026-08-14 17:26 | 2026-08-14 19:38 | 2026-08-14 19:37 | 2026-08-14 19:40 | 2026-08-14 19:40 | 2026-08-14 19:40 | BrokenWire |  | Fair | No | Broken service wire found, wire was spliced retention and reconnected.
Outage | J.E.26.08.21011 | C001889121 | Javid Vernon | Westmoreland | Completed | Load_267353 | Paradise - 310 | 2026-08-14 13:23 | 2026-08-14 13:24 | 2026-08-14 13:52 | 2026-08-14 13:52 | 2026-08-14 13:52 | 2026-08-14 13:52 | 2026-08-14 13:53 | 2026-08-14 13:53 |  |  | Fair | No | This call belongs to st James
Non-Outage | J.E.26.08.20762 | C001889125 | Delano Gayle |  | Completed |  |  | 2026-08-14 13:27 | 2026-08-14 16:13 | 2026-08-14 20:46 | 2026-08-14 20:46 | 2026-08-14 21:32 | 2026-08-14 21:58 | 2026-08-14 21:58 | 2026-08-14 21:58 | BrokenWire |  | Fair | No | Broken secondary neutral mid span, burnt phase at pole, repair all use 2 linkets, 3 clamps 4ft #6 neutral, voltage readings 113-114-227
Outage | J.E.26.08.21014 | C001889128 | Eric Williams | KSAN | Completed | Load_264325 | Constant Spring - 410 | 2026-08-14 13:29 | 2026-08-14 13:31 | 2026-08-14 13:41 | 2026-08-14 13:42 | 2026-08-14 14:12 | 2026-08-14 14:46 | 2026-08-14 14:49 | 2026-08-14 14:49 |  | Y | SevereWind | No | 1 blown 30amps and 15amps junction fuse and 1 3amps transformer fuse found and replaced cause by tree contact major bushing done
Outage | J.E.26.08.20717 | C001889135 | Dwayne Samuels | Trelawny | Completed | Load_259574 | Greenwood - 110 | 2026-08-14 13:31 | 2026-08-14 13:32 | 2026-08-14 13:40 | 2026-08-14 13:40 | 2026-08-14 14:52 | 2026-08-14 15:01 | 2026-08-14 15:04 | 2026-08-14 15:04 |  |  | Fair | No | Patrol primary line to find 1 blown 30amp junction fuse complete line patrol before replacing one 30amp junction at same and close
Non-Outage | J.E.26.08.20446 | C001889138 | Clyde Brown | Clarendon | Completed | Load_261027 | Parnassus - 310 | 2026-08-14 13:33 | 2026-08-14 13:34 | 2026-08-14 13:44 | 2026-08-14 13:45 | 2026-08-14 14:33 | 2026-08-14 14:21 | 2026-08-14 14:42 | 2026-08-14 14:42 |  |  | Fair | No | Switch top burnt off bank of 2x50kva and 1-100kva switch top burnt off on paisley Ave main road,Report to maintenance dept to repair.
Outage | J.E.26.08.20154 | C001889141 | Kemark Slue | St.Catherine | Completed | Load_241272 | Rhodens Pen - 410 | 2026-08-14 13:37 | 2026-08-14 13:40 | 2026-08-14 14:02 | 2026-08-14 14:02 | 2026-08-14 14:02 | 2026-08-14 14:02 | 2026-08-14 14:03 | 2026-08-14 14:03 |  |  | Fair | No | Small vehicle required please refer to Roy Brown to make the necessary arrangements.
Non-Outage | J.E.26.08.21047 | C001889181 | Locksley Allen | St.Mary | Completed | Load_260764 | Oracabessa - 110 | 2026-08-14 14:13 | 2026-08-14 14:14 | 2026-08-14 14:18 | 2026-08-14 15:20 | 2026-08-14 15:20 | 2026-08-14 15:27 | 2026-08-14 15:26 | 2026-08-14 15:26 |  |  | Fair | No | Connectors at pole found corroded.clean up connectors at pole Voltage at meter socket phase to phase 237v. Phase to neutral 117&118vSecondary line needs to bush and the lines are slack
Outage | J.E.26.08.21138 | C001889204 | Marlon Authors | St.Elizabeth | Completed | Load_242590 | Maggotty - 210 | 2026-08-14 14:27 | 2026-08-15 07:26 | 2026-08-15 11:14 | 2026-08-15 11:14 | 2026-08-15 11:30 | 2026-08-15 11:33 | 2026-08-15 11:33 | 2026-08-15 11:33 |  |  | Fair | No | Unable to locate and the customer not answering the phone
Non-Outage | J.E.26.08.18755 | C001889205 | Marlon Authors | St.Elizabeth | Completed | Load_292577 | Maggotty - 210 | 2026-08-14 14:29 | 2026-08-14 14:29 | 2026-08-14 17:10 | 2026-08-14 17:11 | 2026-08-14 17:11 | 2026-08-14 18:03 | 2026-08-14 18:03 | 2026-08-14 18:03 |  |  | Fair | No | Supply checked and found low voltage rdg 105v,106v and cross phased 212 volts. Isolate and close transformer circuit at pole #038724 to tap up transformer to tap 5. Supply leave working okay rdg 113v,113v and cross phased 226 volts
Outage | J.E.26.08.21064 | C001889213 | Horace Malcolm | St.James | Completed | Load_250893 | Bogue - 310 | 2026-08-14 14:38 | 2026-08-14 14:38 | 2026-08-14 14:43 | 2026-08-14 14:44 | 2026-08-14 14:43 | 2026-08-14 14:49 | 2026-08-14 14:49 | 2026-08-14 14:49 |  |  | Fair | No | Check and found one 50kva transformer defective amp reading defective transformer amp reading (x1) 16.79 (x3) 379 voltage reading 46-203 asap transformer need replacement maintenance required
Outage | J.E.26.08.21071 | C001889223 | Elvis Trowers | KSAN | Completed | Load_243440 | Washington Blvd - 310 | 2026-08-14 14:42 | 2026-08-14 14:43 | 2026-08-14 14:59 | 2026-08-14 15:00 | 2026-08-14 15:48 | 2026-08-14 15:50 | 2026-08-14 15:50 | 2026-08-14 15:50 | BrokenWire |  | Fair | No | Customer service wire #6 triplex damaged in motor vehicle accident. Repair using 60ft of #6 triplex wire and three 1- bolt clamps. Readings at pothead 118-117-236 volts.
Outage | J.E.26.08.20874 | C001889249 | Wan Carlos Scarlett | KSAS | Completed | Load_254412 | Duhaney - 210 | 2026-08-14 15:04 | 2026-08-14 15:50 | 2026-08-14 18:16 | 2026-08-14 18:17 | 2026-08-14 18:16 | 2026-08-14 18:17 | 2026-08-14 18:19 | 2026-08-14 18:19 | BrokenWire |  | Fair | No | Reset 25KVA transformer no pole # was found nothing was found on the secondary line
Outage | J.E.26.08.21151 | C001889261 | Gregory Grossett | Portland | Completed | Load_250082 | Port Antonio - 410 | 2026-08-14 15:12 | 2026-08-14 15:18 | 2026-08-14 15:28 | 2026-08-14 15:28 | 2026-08-14 16:21 | 2026-08-14 17:29 | 2026-08-14 17:30 | 2026-08-14 17:30 |  |  | Fair | No | 10kva transformer trip cause by 220 service phase and neutral banging clear then reset transformer area is now ok.
Non-Outage | J.E.26.08.21178 | C001889268 | Lancelot Brown |  | Completed |  |  | 2026-08-14 15:17 | 2026-08-14 15:19 | 2026-08-14 15:42 | 2026-08-14 17:23 | 2026-08-14 18:42 | 2026-08-14 18:43 | 2026-08-14 18:43 | 2026-08-14 18:43 |  |  | Fair | No | Remake corroded joint at pothead and pole used three connectors two pg clamps vl at pothead 115-115-230 supply restore
Non-Outage | J.E.26.08.21155 | C001889269 | Lancelot Brown |  | Completed |  |  | 2026-08-14 15:18 | 2026-08-14 15:19 | 2026-08-14 15:42 | 2026-08-14 18:44 | 2026-08-14 19:37 | 2026-08-14 20:34 | 2026-08-14 20:35 | 2026-08-14 20:35 | BrokenWire |  | Fair | No | Found 25kva fuse blown patroll found person cut tree and tree fall on secondary line caused phase and neural banging also caused lower phase contact with street light bracket removed lower phase from street light bracket retention one span secondary phase used one 2/0 preform one pg clamp also replace 1-3amps fuse at 25kva no pole number supply restore vl at 25kva location 115-114-230
Outage | J.E.26.08.21033 | C001889270 | Lancelot Brown | Hanover | Completed | Load_258386 | Orange Bay - 210 | 2026-08-14 15:18 | 2026-08-14 15:19 | 2026-08-14 15:42 | 2026-08-14 17:19 | 2026-08-14 17:19 | 2026-08-14 17:22 | 2026-08-14 17:22 | 2026-08-14 17:22 |  |  | Fair | No | Check and found customer breaker trip reset customer breaker supply restore vl at customer breaker 115-114-205 230-234-232
Outage | J.E.26.08.20812 | C001889271 | Neville Spencer | Clarendon | Completed | Load_352838 | May Pen - 110 | 2026-08-14 15:19 | 2026-08-14 15:20 | 2026-08-14 16:11 | 2026-08-14 16:11 | 2026-08-14 17:01 | 2026-08-14 17:11 | 2026-08-14 17:21 | 2026-08-14 17:21 |  | Y | Fair | No | Cleared creeper from xmfr pole reset trip 25 kva xmfr at pole #. 0100914 supply restored.
Outage | J.E.26.08.20830 | C001889279 | Delano Gayle |  | Completed | Load_569915 | Twickenham - 410 | 2026-08-14 15:22 | 2026-08-14 16:16 | 2026-08-14 18:52 | 2026-08-14 18:53 | 2026-08-14 19:15 | 2026-08-14 19:25 | 2026-08-14 19:25 | 2026-08-14 19:25 |  |  | Fair | No | Prepaid customer unable to add credit send call to Moses
Non-Outage | J.E.26.08.21164 | C001889280 | Delano Gayle |  | Completed |  |  | 2026-08-14 15:23 | 2026-08-14 16:09 | 2026-08-14 16:16 | 2026-08-14 16:17 | 2026-08-14 17:33 | 2026-08-14 17:51 | 2026-08-14 17:51 | 2026-08-14 17:51 | BrokenWire |  | Fair | No | Broken #6 neutral mid span, splice and repair use 3ft #6 neutral 2 linkets voltage readings 113-114-227
Outage | J.E.26.08.20002 | C001889282 | Christopher West | St.Catherine | Completed | Load_243538 | Rhodens Pen - 410 | 2026-08-14 15:23 | 2026-08-14 16:15 | 2026-08-14 21:01 | 2026-08-14 21:01 | 2026-08-14 22:15 | 2026-08-14 22:35 | 2026-08-14 22:35 | 2026-08-14 22:35 |  |  | Fair | No | Premises found ok.
Outage | J.E.26.08.21075 | C001889281 | Radcliffe Coleman | St.Catherine | Completed | Load_252034 | New Michelton - 210 | 2026-08-14 15:23 | 2026-08-14 19:10 | 2026-08-14 20:14 | 2026-08-14 20:14 | 2026-08-14 20:44 | 2026-08-14 21:10 | 2026-08-14 21:10 | 2026-08-14 21:10 | LowHangingWires |  | Fair | No | Low hanging service wire found caused by truck incident. 2 onebolt clamp and 3ft #6 neutral used to retention wire. Supply found and left in area and premises. Area left secure.
Outage | J.E.26.08.20716 | C001889286 | Clyde Brown | Clarendon | Completed | Load_249059 | Parnassus - 210 | 2026-08-14 15:25 | 2026-08-14 15:27 | 2026-08-14 15:34 | 2026-08-14 15:35 | 2026-08-14 15:57 | 2026-08-14 16:21 | 2026-08-14 16:25 | 2026-08-14 16:25 |  |  | Fair | No | Corroded joint at secondary line for 3 wire service ,connection remade with 1- clamp voltage left 114/114 and 228V
Outage | J.E.26.08.20759 | C001889295 | Clyde Brown | Clarendon | Completed | Load_264199 | Parnassus - 210 | 2026-08-14 15:26 | 2026-08-14 15:27 | 2026-08-14 16:27 | 2026-08-14 16:28 | 2026-08-14 17:45 | 2026-08-14 18:08 | 2026-08-14 18:17 | 2026-08-14 18:17 |  | Y | SevereWind | No | Blown 20 amps junction fuse near Pump house caused by tree fell across primary line,line cleared and blown fuse replaced
Outage | J.E.26.08.21235 | C001889296 | Clyde Brown | Clarendon | Completed | Load_405421 | Parnassus - 210 | 2026-08-14 15:26 | 2026-08-14 15:27 | 2026-08-14 18:18 | 2026-08-14 18:18 | 2026-08-14 19:59 | 2026-08-14 19:58 | 2026-08-14 20:04 | 2026-08-14 20:04 | BrokenWire |  | Fair | No | Broken 3 wire service across Scott’s Pass main road with 100ft-#6 triplex service wire.
Outage | J.E.26.08.20894 | C001889299 | Daniel Francis | St.Ann | Completed | Load_245610 | Roaring River - 210 | 2026-08-14 15:28 | 2026-08-14 15:29 | 2026-08-14 19:59 | 2026-08-14 19:59 | 2026-08-14 20:11 | 2026-08-14 20:21 | 2026-08-14 20:25 | 2026-08-14 20:25 |  |  | Fair | No | Customer says did not make report
Outage | J.E.26.08.21041 | C001889298 | Daniel Francis | St.Ann | Completed | Load_413080 | Roaring River - 410 | 2026-08-14 15:28 | 2026-08-14 15:29 | 2026-08-14 20:25 | 2026-08-14 20:26 | 2026-08-14 21:36 | 2026-08-14 21:35 | 2026-08-14 21:37 | 2026-08-14 21:37 |  |  | Fair | No | Not found customer not answering phone
Outage | J.E.26.08.21185 | C001889297 | Daniel Francis | St.Ann | Completed | Load_294668 | Roaring River - 210 | 2026-08-14 15:28 | 2026-08-14 15:29 | 2026-08-14 16:48 | 2026-08-14 16:49 | 2026-08-14 17:37 | 2026-08-14 17:27 | 2026-08-14 18:02 | 2026-08-14 18:02 |  |  | Fair | No | Not found customer not answering phone
Outage | J.E.26.08.21282 | C001889300 | Daniel Francis | St.Ann | Completed | Load_267559 | Roaring River - 410 | 2026-08-14 15:29 | 2026-08-14 15:29 | 2026-08-14 16:07 | 2026-08-14 16:08 | 2026-08-14 16:14 | 2026-08-14 16:39 | 2026-08-14 16:43 | 2026-08-14 16:43 |  |  | Fair | No | Found joint discharge we use one clump to replace it power restored 110 in all
Outage | J.E.26.08.21321 | C001889301 | Daniel Francis | St.Ann | Completed | Load_574344 | Roaring River - 210 | 2026-08-14 15:29 | 2026-08-14 15:29 | 2026-08-14 18:40 | 2026-08-14 18:41 | 2026-08-14 19:48 | 2026-08-14 19:49 | 2026-08-14 19:51 | 2026-08-14 19:51 | TreeContact |  | Fair | No | not found
Outage | J.E.26.08.20888 | C001889305 | Richard Watson | Manchester | Completed | Load_556606 | Spur Tree - 210 | 2026-08-14 15:30 | 2026-08-14 15:32 | 2026-08-14 17:30 | 2026-08-14 17:30 | 2026-08-14 17:39 | 2026-08-14 17:42 | 2026-08-14 17:42 | 2026-08-14 17:42 |  |  | Fair | No | Replace blown 30amp junction fuse at pole#0112419, after completing patrol no visible fault found, supply restored to area.
Outage | J.E.26.08.20896 | C001889303 | Richard Watson | Manchester | Completed | Load_1002209 | Spur Tree - 210 | 2026-08-14 15:30 | 2026-08-14 15:32 | 2026-08-14 15:48 | 2026-08-14 15:49 | 2026-08-14 17:04 | 2026-08-14 17:26 | 2026-08-14 17:29 | 2026-08-14 17:29 |  |  | Fair | No | Replace blown 30amp junction fuse at pole#0112419, after completing patrol no visible fault found, supply restored to area.
Outage | J.E.26.08.21057 | C001889302 | Richard Watson | Manchester | Completed | Load_264364 | Spur Tree - 210 | 2026-08-14 15:30 | 2026-08-14 15:32 | 2026-08-14 17:42 | 2026-08-14 17:43 | 2026-08-14 18:02 | 2026-08-14 18:08 | 2026-08-14 18:09 | 2026-08-14 18:09 |  |  | Fair | No | Escalation Department contacted and it was discovered that the customer is currently disconnected for outstanding balance, customer advised.
Outage | J.E.26.08.21307 | C001889310 | Clyde Brown | Clarendon | Completed | Load_240721 | May Pen - 210 | 2026-08-14 15:31 | 2026-08-14 15:32 | 2026-08-14 20:38 | 2026-08-14 20:38 | 2026-08-14 20:38 | 2026-08-14 20:38 | 2026-08-14 20:43 | 2026-08-14 20:43 |  |  | Fair | No | Found ok
Outage | J.E.26.08.20872 | C001889312 | Neville Spencer | Clarendon | Completed | Load_248676 | May Pen - 110 | 2026-08-14 15:32 | 2026-08-14 15:33 | 2026-08-14 19:23 | 2026-08-14 19:24 | 2026-08-14 20:14 | 2026-08-14 21:56 | 2026-08-14 22:00 | 2026-08-14 22:00 | BrokenWire |  | Fair | No | Install 110 ft. 2/0 triplex ,6 clamps, 2, preform voltage reading n 114 116/ 231 supply restored.
Outage | J.E.26.08.20997 | C001889320 | Daniel Francis | St.Ann | Completed | Load_247901 | Ocho Rios - 410 | 2026-08-14 15:36 | 2026-08-14 16:52 | 2026-08-14 21:37 | 2026-08-14 21:38 | 2026-08-14 21:38 | 2026-08-14 21:39 | 2026-08-14 21:40 | 2026-08-14 21:40 |  |  | Fair | No | Same thing happened customer not answering phone don’t know why we call about 9 times no answer
Outage | J.E.26.08.18773 | C001889330 | Romeo Brissett | St.James | Completed | Load_265607 | Bogue - 310 | 2026-08-14 15:40 | 2026-08-14 15:41 | 2026-08-14 17:54 | 2026-08-14 19:52 | 2026-08-14 19:52 | 2026-08-14 20:10 | 2026-08-14 20:19 | 2026-08-14 20:19 |  |  | Fair | No | Replaced (1)15KVA transformer fuse.
Outage | J.E.26.08.19080 | C001889328 | Romeo Brissett | St.James | Completed | Load_239765 | Bogue - 310 | 2026-08-14 15:40 | 2026-08-14 15:41 | 2026-08-14 18:47 | 2026-08-14 18:47 | 2026-08-14 19:43 | 2026-08-14 19:20 | 2026-08-14 19:52 | 2026-08-14 19:52 | BrokenWire |  | Fair | No | Spliced and retention customer service wire, used 1 clamp, V/R 117-119-236
Outage | J.E.26.08.21160 | C001889324 | Romeo Brissett | St.James | Completed | Load_268449 | Bogue - 310 | 2026-08-14 15:40 | 2026-08-14 15:41 | 2026-08-14 15:48 | 2026-08-14 15:48 | 2026-08-14 16:33 | 2026-08-14 17:30 | 2026-08-14 17:50 | 2026-08-14 17:50 |  |  | Fair | No | Found clearance breach, single phase Primary hanging low and shorting with customer service wire, Isolated (1)50 kva transformer, installed one insulator on a pole with open secondary, customer service wire and one streetlight, attached primary single phase line to insulator and replaced (1)50amps junction fuse, however line Need an intermediate pole to attach primary to, primary line has only one(1) foot clearance from secondary top phase one the pole, Please send to maintenance. Urgent.
Outage | J.E.26.08.21335 | C001889321 | Romeo Brissett | St.James | Completed | Load_575159 | Bogue - 310 | 2026-08-14 15:40 | 2026-08-14 15:41 | 2026-08-15 03:07 | 2026-08-15 03:08 | 2026-08-15 03:22 | 2026-08-15 03:54 | 2026-08-15 03:58 | 2026-08-15 03:58 |  |  | Fair | No | Line was patrolled and found clear and safe to energize. Replaced (1)20amps junction fuse.
Non-Outage | J.E.26.06.33408 | C001889334 | Andre Smith | KSAS | Completed | Load_245749 | Rockfort - 210 | 2026-08-14 15:42 | 2026-08-14 15:44 | 2026-08-14 16:13 | 2026-08-14 16:14 | 2026-08-14 16:58 | 2026-08-14 18:37 | 2026-08-14 18:37 | 2026-08-14 18:37 |  |  | Fair | No | Repair burnt service wire phase at pole and neutral mid span using 2onebolt clamps supply restored cause by illegal connections 112/116/228V
Outage | J.E.26.08.21249 | C001889335 | Horace Malcolm | St.James | Completed | Load_247589 | Queens Drive - 710 | 2026-08-14 15:44 | 2026-08-14 15:45 | 2026-08-14 15:54 | 2026-08-14 15:54 | 2026-08-14 18:22 | 2026-08-14 18:26 | 2026-08-14 18:26 | 2026-08-14 18:26 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Isolate one 25kva transformer to splice and retention 2pole span secondary phase and nuetral used 50ft #2 conductor 2clamps two #2preforms
Outage | J.E.26.08.21000 | C001889337 | Derrick Grubb | St.Thomas | Completed | Load_327665 | Lysson - 410 | 2026-08-14 15:45 | 2026-08-14 15:47 | 2026-08-14 18:45 | 2026-08-14 18:46 | 2026-08-14 19:56 | 2026-08-14 20:04 | 2026-08-14 20:05 | 2026-08-14 20:05 |  |  | Fair | No | Clear corrosion at pole, voltage readings 118 117 235 volts
Outage | J.E.26.08.21339 | C001889336 | Clyde Brown | Clarendon | Completed | Load_249122 | Parnassus - 210 | 2026-08-14 15:45 | 2026-08-14 16:19 | 2026-08-14 20:43 | 2026-08-14 20:44 | 2026-08-14 21:06 | 2026-08-14 21:05 | 2026-08-14 21:16 | 2026-08-14 21:16 |  |  | Fair | No | Junction switch top burnt off at hot line clamp and stirrup connection one transformer left circuit without supply.
Outage | J.E.26.08.20978 | C001889342 | Derrick Grubb | St.Thomas | Completed | Load_253956 | Good Year - 210 | 2026-08-14 15:46 | 2026-08-14 15:47 | 2026-08-14 17:25 | 2026-08-14 17:26 | 2026-08-14 18:44 | 2026-08-14 18:44 | 2026-08-14 18:45 | 2026-08-14 18:45 | BrokenWire |  | Fair | No | Broken 30 class six wooden pole, refer to maintenance
Outage | J.E.26.08.21025 | C001889345 | Wan Carlos Scarlett | Portmore | Completed | Load_248605 | Naggo Head - 610 | 2026-08-14 15:51 | 2026-08-14 16:12 | 2026-08-14 18:42 | 2026-08-14 18:42 | 2026-08-14 18:57 | 2026-08-14 19:06 | 2026-08-14 19:06 | 2026-08-14 19:06 |  |  | Fair | No | Customer was reconnected from escalation department power supply has been restored
Outage | J.E.26.08.20866 | C001889359 | Lancelot Brown | St.James | Completed | Load_259607 | Bogue - 510 | 2026-08-14 16:01 | 2026-08-14 16:02 | 2026-08-14 17:22 | 2026-08-14 20:36 | 2026-08-14 20:35 | 2026-08-14 20:36 | 2026-08-14 20:37 | 2026-08-14 20:37 | BrokenWire |  | Fair | No | This call related to person cut and tree fall on secondary line repair carry out supply restore
Outage | J.E.26.08.20685 | C001889363 | Wan Carlos Scarlett | Portmore | Completed | Load_574326 | Naggo Head - 610 | 2026-08-14 16:03 | 2026-08-14 19:06 | 2026-08-14 21:15 | 2026-08-14 21:16 | 2026-08-14 22:21 | 2026-08-15 07:04 | 2026-08-15 07:05 | 2026-08-15 07:05 |  |  | Fair | No | Customer confirm that power supply has been restored
Outage | J.E.26.08.20913 | C001889361 | Wan Carlos Scarlett | St.Catherine | Completed | Load_557329 | Twickenham - 210 | 2026-08-14 16:03 | 2026-08-14 16:12 | 2026-08-14 18:20 | 2026-08-14 18:38 | 2026-08-14 18:38 | 2026-08-14 18:21 | 2026-08-14 18:38 | 2026-08-14 18:38 |  |  | Fair | No | Found customer 3 wire service at pothead with phase and neutral corroded use 2 Penn union at service wire phase and neutral readings 114-113-229
Outage | J.E.26.08.21113 | C001889376 | Christopher West | St.Catherine | Completed | Load_266244 | Rhodens Pen - 410 | 2026-08-14 16:06 | 2026-08-14 16:17 | 2026-08-14 16:59 | 2026-08-14 17:00 | 2026-08-14 19:29 | 2026-08-14 21:01 | 2026-08-14 21:01 | 2026-08-14 21:01 |  |  | Fair | No | A blown 65A junction fuse was at pole#595982, the T off to ginger piece, line section was patrolled however, no abnormalities were found, blown fuse was renewed, line re-energized, area now okay.
Outage | J.E.26.08.20979 | C001889382 | Horace Malcolm | St.James | Completed | Load_258749 | Queens Drive - 810 | 2026-08-14 16:08 | 2026-08-14 16:09 | 2026-08-14 19:23 | 2026-08-14 19:24 | 2026-08-14 20:07 | 2026-08-14 21:14 | 2026-08-14 21:14 | 2026-08-14 21:14 |  |  | Fair | No | Refused one 40amp and one 30amp junction fuse (one 40amp junction fuse and one 100kva fuse stil out due to vicheles park under pole cannot locate owners of vicheles
Outage | J.E.26.08.21224 | C001889383 | Horace Malcolm | St.James | Completed | Load_258942 | Bogue - 310 | 2026-08-14 16:08 | 2026-08-14 16:09 | 2026-08-14 18:29 | 2026-08-14 18:29 | 2026-08-14 18:35 | 2026-08-14 19:19 | 2026-08-14 19:20 | 2026-08-14 19:20 |  |  | Fair | No | Refused one 40amp junction fuse pole number 212962
Outage | J.E.26.08.21256 | C001889384 | Horace Malcolm | St.James | Completed | Load_244803 | Queens Drive - 710 | 2026-08-14 16:08 | 2026-08-14 16:09 | 2026-08-14 19:20 | 2026-08-14 19:20 | 2026-08-14 19:20 | 2026-08-14 19:21 | 2026-08-14 19:21 | 2026-08-14 19:21 |  |  | Fair | No | Related to previous call job number 21224
Outage | J.E.26.08.21332 | C001889385 | Romeo Brissett | St.James | Completed | Load_238546 | Queens Drive - 710 | 2026-08-14 16:08 | 2026-08-15 00:16 | 2026-08-15 01:01 | 2026-08-15 01:01 | 2026-08-15 01:21 | 2026-08-15 02:50 | 2026-08-15 03:07 | 2026-08-15 03:07 | Fire |  | Fair | No | Isolated (1)100kvq transformer, removed Illegal connections, spliced and retention 2 span of secondary, repaired secondary jumper. Used 50ft of #2 and 6 clamps. V/R 116-118-232
Outage | J.E.26.08.20914 | C001889388 | Evan Spaulding | St.Mary | Completed | Load_238782 | Highgate -110 | 2026-08-14 16:10 | 2026-08-14 16:15 | 2026-08-14 16:19 | 2026-08-14 16:19 | 2026-08-14 17:25 | 2026-08-14 18:54 | 2026-08-14 18:55 | 2026-08-14 18:55 |  | Y | Fair | No | Remove fallen Bamboo from line section and replace 1-15 junction fuse at pole number 0010645
Outage | J.E.26.08.21058 | C001889387 | Evan Spaulding | St.Mary | Completed | Load_248092 | Highgate -110 | 2026-08-14 16:10 | 2026-08-14 16:15 | 2026-08-14 18:55 | 2026-08-14 18:56 | 2026-08-14 18:55 | 2026-08-14 18:56 | 2026-08-14 18:56 | 2026-08-14 18:56 |  |  | Fair | No | Associated call
Outage | J.E.26.08.21341 | C001889386 | Evan Spaulding | St.Mary | Completed | Load_262362 | Highgate -110 | 2026-08-14 16:10 | 2026-08-14 16:15 | 2026-08-14 18:56 | 2026-08-14 18:56 | 2026-08-14 19:48 | 2026-08-14 20:07 | 2026-08-14 20:09 | 2026-08-14 20:09 |  |  | Fair | No | Use 2-1 bolt clamps at pole, voltage left 119v,118v,237v
Outage | J.E.26.08.20731 | C001889390 | Delano Gayle | St.Catherine | Completed | Load_556565 | Tredegar - 310 | 2026-08-14 16:14 | 2026-08-14 16:17 | 2026-08-14 17:51 | 2026-08-14 17:52 | 2026-08-14 18:30 | 2026-08-14 18:52 | 2026-08-14 18:52 | 2026-08-14 18:52 |  |  | Fair | No | Premises found okay power was restored
Outage | J.E.26.08.21043 | C001889394 | Raymond Carr | St.Mary | Completed | Load_240179 | Blackstonedge - 110 | 2026-08-14 16:16 | 2026-08-14 16:30 | 2026-08-14 17:02 | 2026-08-14 17:02 | 2026-08-14 18:14 | 2026-08-13 19:22 | 2026-08-14 19:26 | 2026-08-14 19:26 | BrokenPole |  | Fair | No | Spliced and retention two spans of broken secondary conductors, caused by a motor truck. Using 50ft#2aa, 4#2 splicing sleeves, 2 clamps, 2#2 preforms. Supply was restored.
Outage | J.E.26.08.21062 | C001889396 | Delano Gayle | St.Catherine | Completed | Load_267832 | Twickenham - 410 | 2026-08-14 16:18 | 2026-08-14 16:18 | 2026-08-14 19:26 | 2026-08-14 19:26 | 2026-08-14 20:02 | 2026-08-14 20:46 | 2026-08-14 20:46 | 2026-08-14 20:46 | BrokenPole |  | Fair | No | Premises not found, area found okay
Outage | J.E.26.08.21376 | C001889399 | Neville Spencer | Clarendon | Completed | Load_250549 | May Pen - 110 | 2026-08-14 16:18 | 2026-08-14 16:20 | 2026-08-14 17:22 | 2026-08-14 17:22 | 2026-08-14 19:16 | 2026-08-14 19:16 | 2026-08-14 19:23 | 2026-08-14 19:23 | Fire |  | Fair | No | Found supply at location need daylight visit to check DE pole unable to reach pole no road.
Outage | J.E.26.08.20678 | C001889401 | Kenroy Dale | Manchester | Completed | Load_250940 | Spur Tree - 310 | 2026-08-14 16:19 | 2026-08-14 16:19 | 2026-08-14 19:35 | 2026-08-14 19:36 | 2026-08-14 21:17 | 2026-08-14 21:39 | 2026-08-14 21:40 | 2026-08-14 21:40 |  |  | Fair | No | Customer was disconnected for nonpayment, customer paid bill on wrong account. Customer was advised to visit office
Outage | J.E.26.08.21052 | C001889402 | Kenroy Dale | Manchester | Completed | Load_1002550 | Kendal - 310 | 2026-08-14 16:19 | 2026-08-14 16:19 | 2026-08-14 17:57 | 2026-08-14 17:58 | 2026-08-14 19:14 | 2026-08-14 19:33 | 2026-08-14 19:35 | 2026-08-14 19:35 |  |  | Fair | No | Customer make report to the wrong company, customer stated that they where experiencing a internet issue
Outage | J.E.26.08.21156 | C001889404 | Kenroy Dale | Manchester | Completed | Load_268212 | Spur Tree - 310 | 2026-08-14 16:19 | 2026-08-14 16:19 | 2026-08-14 21:56 | 2026-08-14 22:08 | 2026-08-15 01:41 | 2026-08-15 01:41 | 2026-08-15 01:42 | 2026-08-15 01:42 | BrokenWire |  | Fair | No | Corrosion found at pole remade connection using 3 one bolt clamp
Outage | J.E.26.08.21352 | C001889403 | Clyde Brown | Clarendon | Completed | Load_257341 | May Pen - 210 | 2026-08-14 16:19 | 2026-08-14 16:20 | 2026-08-14 20:05 | 2026-08-14 20:05 | 2026-08-14 20:30 | 2026-08-14 20:31 | 2026-08-14 20:35 | 2026-08-14 20:35 |  |  | Fair | No | Cannot be located customer not answering phone
Outage | J.E.26.08.20522 | C001889415 | Rusean Allen | KSAS | Completed | Load_575822 | Rockfort - 210 | 2026-08-14 16:27 | 2026-08-14 16:30 | 2026-08-14 16:40 | 2026-08-14 16:41 | 2026-08-14 17:28 | 2026-08-14 17:30 | 2026-08-14 17:30 | 2026-08-14 17:30 |  |  | Fair | No | 1x 10amp fuse found 1x 10amp fuse replaced.
Outage | J.E.26.08.21077 | C001889419 | Andre Smith | KSAS | Completed | Load_575567 | Duhaney - 410 | 2026-08-14 16:32 | 2026-08-14 16:33 | 2026-08-14 21:49 | 2026-08-14 21:49 | 2026-08-14 22:06 | 2026-08-14 22:09 | 2026-08-14 22:25 | 2026-08-14 22:25 |  |  | Fair | No | Broken primary pole found maintenance department required
Outage | J.E.26.08.21088 | C001889420 | Edward Royal | KSAS | Completed | Load_569191 | Duhaney - 410 | 2026-08-14 16:32 | 2026-08-14 23:39 | 2026-08-15 03:58 | 2026-08-15 03:59 | 2026-08-15 03:58 | 2026-08-15 03:59 | 2026-08-15 04:00 | 2026-08-15 04:00 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.21225 | C001889423 | Andre Smith | KSAS | Completed | Load_258196 | Up Park Camp - 410 | 2026-08-14 16:34 | 2026-08-14 16:36 | 2026-08-14 18:42 | 2026-08-14 18:43 | 2026-08-14 19:29 | 2026-08-14 19:37 | 2026-08-14 19:37 | 2026-08-14 19:37 |  |  | Fair | No | Premises found okay supply restored already
Outage | J.E.26.08.21353 | C001889421 | Christopher Edwards | KSAN | Completed | Load_263547 | Constant Spring - 410 | 2026-08-14 16:34 | 2026-08-14 16:35 | 2026-08-14 17:27 | 2026-08-14 17:45 | 2026-08-14 17:45 | 2026-08-14 18:23 | 2026-08-14 18:24 | 2026-08-14 18:24 |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Outage | J.E.26.08.21372 | C001889422 | Derrick Grubb | St.Thomas | Completed | Load_243194 | Good Year - 210 | 2026-08-14 16:34 | 2026-08-14 16:35 | 2026-08-14 17:01 | 2026-08-14 17:02 | 2026-08-14 17:24 | 2026-08-14 17:25 | 2026-08-14 17:25 | 2026-08-14 17:25 |  |  | Fair | No | Patrol and refuse a 25 amp switch in easington
Non-Outage | J.E.26.07.36384 | C001889424 | Radcliffe Coleman | St.Catherine | Completed | Load_252376 | New Michelton - 410 | 2026-08-14 16:35 | 2026-08-14 16:36 | 2026-08-14 18:08 | 2026-08-14 18:09 | 2026-08-14 18:14 | 2026-08-14 20:13 | 2026-08-14 20:13 | 2026-08-14 20:13 |  |  | Fair | No | Corroded and defective joints found at 50kva Transformer. Three 403 ampact used to change out defective joints. Supply restored, 116 116 232 voltages left in area. Area left okay
Outage | J.E.26.08.21078 | C001889430 | Rusean Allen | KSAS | Completed | Load_252961 | Cane River - 310 | 2026-08-14 16:39 | 2026-08-14 16:41 | 2026-08-14 18:54 | 2026-08-14 18:55 | 2026-08-14 19:11 | 2026-08-14 19:27 | 2026-08-14 19:27 | 2026-08-14 19:27 |  |  | Fair | No | 1x 3amp fuse found 1x 3amp fuse replaced
Non-Outage | J.E.26.08.21368 | C001889431 | Edward Royal |  | Completed |  |  | 2026-08-14 16:41 | 2026-08-14 23:40 | 2026-08-15 04:33 | 2026-08-15 04:33 | 2026-08-15 04:33 | 2026-08-15 04:33 | 2026-08-15 04:33 | 2026-08-15 04:33 | BrokenWire |  | Fair | No | Premises not found unable to communicate with customer
Non-Outage | J.E.26.08.20427 | C001889439 | Daniel Francis | St.Ann | Completed | Load_265231 | Roaring River - 210 | 2026-08-14 16:47 | 2026-08-14 16:48 | 2026-08-14 18:02 | 2026-08-14 18:03 | 2026-08-14 18:02 | 2026-08-14 18:02 | 2026-08-14 18:04 | 2026-08-14 18:04 |  |  | Fair | No | Banking wire we work on it also charge one 2amp fuse
Outage | J.E.26.08.21027 | C001889435 | Milton Charlton | KSAN | Completed | Load_269032 | Washington Blvd - 610 | 2026-08-14 16:47 | 2026-08-14 16:49 | 2026-08-14 18:33 | 2026-08-14 20:42 | 2026-08-14 21:39 | 2026-08-14 21:10 | 2026-08-14 21:41 | 2026-08-14 21:41 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.21034 | C001889434 | Elvis Trowers | KSAN | Completed | Load_574809 | Washington Blvd - 610 | 2026-08-14 16:47 | 2026-08-15 08:10 | 2026-08-15 11:52 | 2026-08-15 13:38 | 2026-08-15 13:50 | 2026-08-15 13:50 | 2026-08-15 13:51 | 2026-08-15 13:51 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.21070 | C001889436 | Milton Charlton | KSAN | Completed | Load_557450 | West Kings House - 310 | 2026-08-14 16:47 | 2026-08-14 16:49 | 2026-08-14 18:33 | 2026-08-14 20:28 | 2026-08-14 20:39 | 2026-08-14 20:35 | 2026-08-14 20:41 | 2026-08-14 20:41 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.21095 | C001889437 | Milton Charlton | KSAN | Completed | Load_255054 | Constant Spring - 410 | 2026-08-14 16:47 | 2026-08-14 16:49 | 2026-08-14 18:41 | 2026-08-14 19:44 | 2026-08-14 20:25 | 2026-08-14 19:55 | 2026-08-14 20:27 | 2026-08-14 20:27 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.21277 | C001889438 | Milton Charlton | KSAN | Completed | Load_264325 | Constant Spring - 410 | 2026-08-14 16:47 | 2026-08-14 16:49 | 2026-08-14 18:41 | 2026-08-14 18:42 | 2026-08-14 18:50 | 2026-08-14 19:20 | 2026-08-14 19:42 | 2026-08-14 19:42 |  |  | Fair | No | Reconnect customers meter that was disconnected. Reconnection was done by JPS escalation.
Outage | J.E.26.08.19355 | C001889445 | Andre Smith | KSAS | Completed | Load_575567 | Duhaney - 410 | 2026-08-14 16:54 | 2026-08-14 16:56 | 2026-08-14 22:43 | 2026-08-14 22:44 | 2026-08-14 22:44 | 2026-08-14 22:45 | 2026-08-14 22:45 | 2026-08-14 22:45 |  |  | Fair | No | Broken pole found maintenance department required
Outage | J.E.26.08.20736 | C001889443 | Edward Royal | KSAS | Completed | Load_244976 | Duhaney - 410 | 2026-08-14 16:54 | 2026-08-14 23:39 | 2026-08-15 03:56 | 2026-08-15 03:57 | 2026-08-15 03:56 | 2026-08-15 03:57 | 2026-08-15 03:57 | 2026-08-15 03:57 | BrokenPole |  | Fair | No | Related to broken concrete pole at riverton
Non-Outage | J.E.26.08.20996 | C001889446 | Antony Levy |  | Completed |  |  | 2026-08-14 16:57 | 2026-08-14 16:58 | 2026-08-14 21:31 | 2026-08-14 21:31 | 2026-08-14 21:31 | 2026-08-14 21:32 | 2026-08-14 21:33 | 2026-08-14 21:33 |  |  | Fair | No | Multiple illegal connections causing issues...refer to revenue protection.
Outage | J.E.26.08.20718 | C001889447 | Antony Levy | KSAS | Completed | Load_579255 | Duhaney - 310 | 2026-08-14 16:57 | 2026-08-14 16:58 | 2026-08-14 20:29 | 2026-08-14 21:33 | 2026-08-14 21:53 | 2026-08-14 21:53 | 2026-08-14 21:54 | 2026-08-14 21:54 |  |  | Fair | No | Illegal connections causing issues refer to revenue protection.
Non-Outage | J.E.26.08.21069 | C001889451 | Elvis Trowers |  | Completed |  |  | 2026-08-14 17:04 | 2026-08-14 17:06 | 2026-08-14 18:16 | 2026-08-14 18:17 | 2026-08-14 18:53 | 2026-08-14 18:50 | 2026-08-14 18:55 | 2026-08-14 18:55 | BrokenPole |  | Fair | No | Found okay upon arrival. Customer complaining about street light not working at 1 Cresta avenue.
Outage | J.E.26.08.18873 | C001889452 | Elvis Trowers | KSAS | Completed | Load_254338 | Greenwich - 410 | 2026-08-14 17:04 | 2026-08-14 17:06 | 2026-08-14 17:31 | 2026-08-14 17:31 | 2026-08-14 18:08 | 2026-08-14 18:15 | 2026-08-14 18:16 | 2026-08-14 18:16 |  |  | Fair | No | Found one 3 amps transformer fuse blown at pole # 0181062. Refused using one 3 amps fuse and reclosed transformer switch.
Outage | J.E.26.08.21399 | C001889450 | Antony Levy | KSAN | Completed | Load_256666 | Washington Blvd - 710 | 2026-08-14 17:04 | 2026-08-14 17:05 | 2026-08-14 19:36 | 2026-08-14 19:36 | 2026-08-14 20:29 | 2026-08-14 21:10 | 2026-08-14 21:14 | 2026-08-14 21:14 |  |  | Fair | No | Numerous illegal connections causing issue in community...refer to revenue protection.
Outage | J.E.26.08.19403 | C001889455 | Rusean Allen | KSAS | Completed | Load_253227 | Cane River - 610 | 2026-08-14 17:06 | 2026-08-14 17:07 | 2026-08-14 17:27 | 2026-08-14 19:41 | 2026-08-14 20:00 | 2026-08-14 20:16 | 2026-08-14 20:17 | 2026-08-14 20:17 |  |  | Fair | No | Corroded clamps found at pothead, clamps were changed.
Outage | J.E.26.08.20845 | C001889456 | Edward Royal | KSAS | Completed | Load_246463 | Hunts Bay - 310 | 2026-08-14 17:06 | 2026-08-14 23:40 | 2026-08-15 03:55 | 2026-08-15 03:56 | 2026-08-15 03:55 | 2026-08-15 03:55 | 2026-08-15 03:56 | 2026-08-15 03:56 |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.08.21170 | C001889457 | Andre Smith |  | Completed |  |  | 2026-08-14 17:07 | 2026-08-14 17:08 | 2026-08-14 19:37 | 2026-08-14 19:37 | 2026-08-14 21:04 | 2026-08-14 21:42 | 2026-08-14 21:42 | 2026-08-14 21:42 | BrokenPole |  | Fair | No | Broken primary pole found maintenance department required
Outage | J.E.26.08.21020 | C001889461 | Tyrese Williams | St.Ann | Completed | Load_241258 | Cardiff Hall - 310 | 2026-08-14 17:14 | 2026-08-14 17:15 | 2026-08-14 17:24 | 2026-08-14 22:42 | 2026-08-14 23:03 | 2026-08-14 23:04 | 2026-08-14 23:04 | 2026-08-14 23:04 |  |  | Fair | No | Replace a 25 amp junction fuse at pole
Outage | J.E.26.08.21333 | C001889462 | Roxroy Needham | St.Ann | Completed | Load_241505 | Cardiff Hall - 310 | 2026-08-14 17:14 | 2026-08-14 23:10 | 2026-08-14 23:47 | 2026-08-14 23:47 | 2026-08-15 00:50 | 2026-08-15 01:24 | 2026-08-15 01:25 | 2026-08-15 01:25 |  |  | Fair | No | Replace a 50 KVA transformer fuse with a 5 amps at pole
Outage | J.E.26.08.21361 | C001889463 | Tyrese Williams | St.Ann | Completed | Load_256899 | Cardiff Hall - 310 | 2026-08-14 17:14 | 2026-08-14 17:15 | 2026-08-14 17:37 | 2026-08-14 17:42 | 2026-08-14 21:49 | 2026-08-14 22:00 | 2026-08-14 21:59 | 2026-08-14 21:59 |  |  | Fair | No | Replace a 25 kva transformer fuse with a 3amp fuse and a 10 amp junction fuse at pole
Outage | J.E.26.08.21423 | C001889464 | Tyrese Williams | St.Ann | Completed | Load_261967 | Cardiff Hall - 310 | 2026-08-14 17:15 | 2026-08-14 17:15 | 2026-08-14 17:39 | 2026-08-14 22:00 | 2026-08-14 22:32 | 2026-08-14 22:32 | 2026-08-14 22:32 | 2026-08-14 22:32 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.21438 | C001889466 | Wan Carlos Scarlett | Portmore | Completed | Load_570079 | Naggo Head - 610 | 2026-08-14 17:19 | 2026-08-14 17:20 | 2026-08-14 18:53 | 2026-08-14 19:26 | 2026-08-14 20:37 | 2026-08-14 21:14 | 2026-08-14 21:15 | 2026-08-14 21:15 | BrokenPole |  | Fair | No | Customer report streetlight not working
Outage | J.E.26.08.21389 | C001889475 | Gregory Grossett | Portland | Completed | Load_260891 | Port Antonio - 310 | 2026-08-14 17:32 | 2026-08-14 17:33 | 2026-08-14 19:21 | 2026-08-14 19:21 | 2026-08-14 19:27 | 2026-08-14 20:31 | 2026-08-14 20:32 | 2026-08-14 20:32 |  |  | Fair | No | After calling the customer he said that the power has being restored.
Outage | J.E.26.08.21429 | C001889474 | Gregory Grossett | Portland | Completed | Load_260631 | Port Antonio - 410 | 2026-08-14 17:32 | 2026-08-14 17:33 | 2026-08-14 18:16 | 2026-08-14 18:17 | 2026-08-14 19:19 | 2026-08-14 19:20 | 2026-08-14 19:21 | 2026-08-14 19:21 |  |  | Fair | No | After making multiple calls we could not reach out to the customer.
Non-Outage | J.E.26.08.21510 | C001889478 | Neville Spencer |  | Completed |  |  | 2026-08-14 17:40 | 2026-08-14 17:47 | 2026-08-14 22:04 | 2026-08-14 22:04 | 2026-08-14 22:39 | 2026-08-15 01:00 | 2026-08-15 00:01 | 2026-08-15 00:01 |  |  | Fair | No | Open 25 kva xmfr remade secondary neutral jumper used 2/, clamps voltage reading 112 117 228 supply restored.
Outage | J.E.26.08.17621 | C001889484 | Floyd Taylor | Trelawny | Completed | Load_243994 | Duncans - 210 | 2026-08-14 17:44 | 2026-08-15 09:01 | 2026-08-15 16:14 | 2026-08-15 16:15 | 2026-08-15 17:33 | 2026-08-15 18:27 | 2026-08-15 18:27 | 2026-08-15 18:27 |  |  | Fair | No | Clean and remake joint at pole using 2pg clamps voltage readings left 116,118,234
Outage | J.E.26.08.20065 | C001889483 | Andre Williams | Trelawny | Completed | Load_292567 | Duncans - 210 | 2026-08-14 17:44 | 2026-08-14 17:45 | 2026-08-14 18:41 | 2026-08-14 18:41 | 2026-08-14 20:23 | 2026-08-14 20:40 | 2026-08-14 20:40 | 2026-08-14 20:40 | BrokenWire |  | Fair | No | No low voltage or single phase from Jps side voltage at pothead 115+115=230
Outage | J.E.26.08.21132 | C001889486 | Neville Spencer | St.Catherine | Completed | Load_255855 | Rhodens Pen - 310 | 2026-08-14 17:52 | 2026-08-15 08:42 | 2026-08-15 11:56 | 2026-08-15 11:57 | 2026-08-15 12:22 | 2026-08-15 13:10 | 2026-08-15 13:14 | 2026-08-15 13:14 |  |  | Fair | No | Remade corrded phase and neutral joints at pothead and secondary used 3, 6/6 sleeves and 2 clamps voltage reading 114 118; 232 supply restored.
Outage | J.E.26.08.21512 | C001889490 | Elvis Trowers | KSAS | Completed | Load_256788 | Rockfort - 410 | 2026-08-14 17:59 | 2026-08-14 20:09 | 2026-08-14 20:32 | 2026-08-14 20:33 | 2026-08-14 21:05 | 2026-08-14 21:05 | 2026-08-14 21:10 | 2026-08-14 21:10 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.21519 | C001889489 | Rusean Allen | KSAS | Completed | Load_261556 | Rockfort - 410 | 2026-08-14 17:59 | 2026-08-14 18:01 | 2026-08-14 20:17 | 2026-08-14 20:18 | 2026-08-14 20:36 | 2026-08-14 21:03 | 2026-08-14 21:04 | 2026-08-14 21:04 | BrokenWire |  | Fair | No | 1x 40amp fuse found 1x 40amp fuse replaced
Outage | J.E.26.08.21471 | C001889494 | Marlon Authors | Manchester | Completed | Load_238920 | Spur Tree - 210 | 2026-08-14 18:04 | 2026-08-14 18:10 | 2026-08-14 21:25 | 2026-08-14 21:25 | 2026-08-14 21:25 | 2026-08-14 21:26 | 2026-08-14 21:26 | 2026-08-14 21:26 |  |  | SevereWind | No | Supply restored to the area
Outage | J.E.26.08.21518 | C001889496 | Marlon Authors | Manchester | Completed | Load_302589 | Spur Tree - 210 | 2026-08-14 18:04 | 2026-08-14 18:10 | 2026-08-14 18:40 | 2026-08-14 18:40 | 2026-08-14 19:39 | 2026-08-14 20:08 | 2026-08-14 20:08 | 2026-08-14 20:08 | Fire |  | Fair | No | Supply checked and found wires in meter socket and meter burnt. Disconnect supply at pothead, customer was advised to have socket repaired
Outage | J.E.26.08.21559 | C001889495 | Marlon Authors | Manchester | Completed | Load_259417 | Spur Tree - 210 | 2026-08-14 18:04 | 2026-08-14 18:10 | 2026-08-14 20:11 | 2026-08-14 20:12 | 2026-08-14 21:02 | 2026-08-14 21:22 | 2026-08-14 21:22 | 2026-08-14 21:22 |  |  | SevereWind | No | Patrol and found illegal connection putting the secondary conductors together, severe winds in the area. Remove same and reset 10 kva trip type transformer at pole #531019. Restored supply ok
Outage | J.E.26.08.21487 | C001889514 | Evan Spaulding | St.Mary | Completed | Load_238891 | Annotto Bay - 310 | 2026-08-14 18:45 | 2026-08-14 18:45 | 2026-08-14 20:13 | 2026-08-14 20:13 | 2026-08-14 20:43 | 2026-08-14 20:44 | 2026-08-14 20:46 | 2026-08-14 20:46 |  |  | Fair | No | Revisit in the morning,daylight attention needed.
Non-Outage | J.E.26.08.21515 | C001889518 | Milton Charlton |  | Completed |  |  | 2026-08-14 18:48 | 2026-08-15 07:59 | 2026-08-15 17:10 | 2026-08-15 17:10 | 2026-08-15 18:00 | 2026-08-15 18:05 | 2026-08-15 18:02 | 2026-08-15 18:02 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.21550 | C001889517 | Elvis Trowers | KSAN | Completed | Load_264305 | Constant Spring - 410 | 2026-08-14 18:48 | 2026-08-15 07:57 | 2026-08-15 08:20 | 2026-08-15 11:18 | 2026-08-15 11:47 | 2026-08-15 11:45 | 2026-08-15 11:52 | 2026-08-15 11:52 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.21654 | C001889528 | Delano Gayle | St.Catherine | Completed | Load_250263 | Tredegar - 510 | 2026-08-14 19:12 | 2026-08-14 19:14 | 2026-08-14 21:58 | 2026-08-14 21:59 | 2026-08-14 23:05 | 2026-08-14 23:07 | 2026-08-14 23:09 | 2026-08-14 23:09 |  |  | Fair | No | Premises not found no answer from customer phone
Non-Outage | J.E.26.08.20610 | C001889536 | Evan Spaulding |  | Completed |  |  | 2026-08-14 19:21 | 2026-08-14 19:23 | 2026-08-14 21:46 | 2026-08-14 21:46 | 2026-08-14 21:46 | 2026-08-14 21:46 | 2026-08-14 21:47 | 2026-08-14 21:47 |  |  | Fair | No | Refer to field service hexin box.
Outage | J.E.26.08.20672 | C001889535 | Evan Spaulding | St.Mary | Completed | Load_237984 | Annotto Bay - 210 | 2026-08-14 19:21 | 2026-08-14 19:23 | 2026-08-14 20:46 | 2026-08-14 20:46 | 2026-08-14 21:20 | 2026-08-14 21:42 | 2026-08-14 21:43 | 2026-08-14 21:43 |  |  | Fair | No | Voltage found 116v,115v,231v.
Outage | J.E.26.08.21401 | C001889542 | Horace Malcolm | St.James | Completed | Load_267952 | Rose Hall - 210 | 2026-08-14 19:42 | 2026-08-14 19:44 | 2026-08-14 21:18 | 2026-08-14 21:18 | 2026-08-14 22:21 | 2026-08-14 22:42 | 2026-08-14 22:42 | 2026-08-14 22:42 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Isolate one 50kva transformer to splice and retention one pole span secondary phase used 20ft #2 conductor 1clamp and one #2 preform
Outage | J.E.26.08.20990 | C001889544 | Horace Malcolm | St.James | Completed | Load_266914 | Rose Hall - 110 | 2026-08-14 19:53 | 2026-08-15 07:20 | 2026-08-15 08:59 | 2026-08-15 08:59 | 2026-08-15 09:19 | 2026-08-15 09:20 | 2026-08-15 09:20 | 2026-08-15 09:20 | Fire |  | Fair | No | Check and found no sparking of fire in area
Outage | J.E.26.08.21697 | C001889545 | Edward Royal | KSAN | Completed | Load_242894 | Hope - 410 | 2026-08-14 19:54 | 2026-08-14 23:48 | 2026-08-15 04:14 | 2026-08-15 04:14 | 2026-08-15 04:14 | 2026-08-15 04:14 | 2026-08-15 04:14 | 2026-08-15 04:14 | BrokenWire |  | Fair | No | Customer requested daylight visit
Outage | J.E.26.08.21572 | C001889547 | Derrick Grubb | St.Thomas | Completed | Load_238855 | Good Year - 210 | 2026-08-14 19:56 | 2026-08-14 19:57 | 2026-08-14 22:13 | 2026-08-14 22:14 | 2026-08-14 22:13 | 2026-08-14 22:41 | 2026-08-14 22:41 | 2026-08-14 22:41 |  |  | Fair | No | Patrol and replace drop out switch with 30 amp trip saver
Outage | J.E.26.08.21630 | C001889549 | Edward Royal | KSAS | Completed | Load_237946 | Cane River - 310 | 2026-08-14 20:03 | 2026-08-14 23:38 | 2026-08-15 04:09 | 2026-08-15 04:10 | 2026-08-15 04:09 | 2026-08-15 04:10 | 2026-08-15 04:10 | 2026-08-15 04:10 | BrokenWire |  | Fair | No | Customer requesting daylight visit
Outage | J.E.26.08.21507 | C001889550 | Elvis Trowers | KSAS | Completed | Load_261556 | Rockfort - 410 | 2026-08-14 20:07 | 2026-08-14 20:07 | 2026-08-14 21:10 | 2026-08-14 21:11 | 2026-08-14 21:11 | 2026-08-14 21:15 | 2026-08-14 21:12 | 2026-08-14 21:12 | BrokenWire |  | Fair | No | Matter was resolved.
Outage | J.E.26.08.21096 | C001889552 | Edward Royal | KSAS | Completed | Load_1002691 | Cane River - 410 | 2026-08-14 20:20 | 2026-08-14 23:40 | 2026-08-15 04:06 | 2026-08-15 04:07 | 2026-08-15 04:06 | 2026-08-15 04:07 | 2026-08-15 04:08 | 2026-08-15 04:08 |  |  | Fair | No | Premises found close
Outage | J.E.26.08.21615 | C001889553 | Edward Royal | KSAS | Completed | Load_237680 | Cane River - 410 | 2026-08-14 20:21 | 2026-08-14 23:40 | 2026-08-15 04:04 | 2026-08-15 04:04 | 2026-08-15 04:04 | 2026-08-15 04:05 | 2026-08-15 04:05 | 2026-08-15 04:05 |  |  | Fair | No | Premises found close unable to communicate with customer via phone
Non-Outage | J.E.26.08.19704 | C001889557 | Oshane Warren |  | Completed |  |  | 2026-08-14 20:34 | 2026-08-14 20:35 | 2026-08-14 20:41 | 2026-08-14 20:42 | 2026-08-14 20:43 | 2026-08-14 20:44 | 2026-08-14 20:44 | 2026-08-14 20:44 |  |  | Fair | No | Check and found okay
Outage | J.E.26.08.21352 | C001889561 | Clyde Brown | Clarendon | Completed | Load_257341 | May Pen - 210 | 2026-08-14 20:43 | 2026-08-14 20:44 | 2026-08-14 21:16 | 2026-08-14 21:17 | 2026-08-15 00:23 | 2026-08-15 23:40 | 2026-08-15 00:31 | 2026-08-15 00:31 |  |  | SevereWind | No | Broken secondary phase and neutral caused by heavy wind,open 25 kva transformer and repaired with 6ft-#2 conductor,2-splicing sleeve 1-preform and 1- clamp .
Outage | J.E.26.08.21595 | C001889564 | Richard Watson | St.Elizabeth | Completed | Load_252931 | Maggotty - 210 | 2026-08-14 20:51 | 2026-08-14 20:51 | 2026-08-14 21:07 | 2026-08-14 21:07 | 2026-08-14 21:41 | 2026-08-14 22:05 | 2026-08-14 22:06 | 2026-08-14 22:06 |  |  | SevereWind | No | Replace blown 8amp fuse for 100kva transformer cause by banging conductor phase and neutral, clear and retention one span of secondary neutral, supply restored to area.
Outage | J.E.26.08.21626 | C001889563 | Marlon Authors | St.Elizabeth | Completed | Load_256959 | Maggotty - 210 | 2026-08-14 20:51 | 2026-08-15 07:26 | 2026-08-15 11:11 | 2026-08-15 11:11 | 2026-08-15 11:11 | 2026-08-15 11:12 | 2026-08-15 11:12 | 2026-08-15 11:12 | BrokenWire |  | Fair | No | Unable to locate and the customer not answering the phone
Outage | J.E.26.08.21797 | C001889567 | Andre Williams | Trelawny | Completed | Load_241035 | Greenwood - 210 | 2026-08-14 21:00 | 2026-08-14 21:01 | 2026-08-14 21:06 | 2026-08-14 21:07 | 2026-08-14 22:50 | 2026-08-14 22:51 | 2026-08-14 22:52 | 2026-08-14 22:52 | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Open 25 kva transformer splice and retention two span broken secondary phase and one span low hanging neutral that was touching telephone wire causing sparking
Outage | J.E.26.08.20979 | C001889576 | Horace Malcolm | St.James | Completed | Load_258749 | Queens Drive - 810 | 2026-08-14 21:31 | 2026-08-14 21:31 | 2026-08-14 22:42 | 2026-08-14 22:42 | 2026-08-14 23:03 | 2026-08-14 23:05 | 2026-08-14 23:05 | 2026-08-14 23:05 |  |  | Fair | No | Refused one 40amp junction fuse and one 100kva transformer used one 8amp fuse
Outage | J.E.26.08.21571 | C001889578 | Evan Spaulding | St.Mary | Completed | Load_262607 | Annotto Bay - 310 | 2026-08-14 21:36 | 2026-08-14 21:36 | 2026-08-14 21:57 | 2026-08-14 21:57 | 2026-08-14 21:57 | 2026-08-14 22:17 | 2026-08-14 22:18 | 2026-08-14 22:18 |  |  | Fair | No | Replace 1-50 junction fuse at pole number 0099070
Outage | J.E.26.08.21446 | C001889579 | Romeo Brissett | St.James | Completed | Load_242384 | Bogue - 310 | 2026-08-14 21:37 | 2026-08-15 00:15 | 2026-08-15 03:58 | 2026-08-15 03:59 | 2026-08-15 04:32 | 2026-08-15 05:18 | 2026-08-15 05:20 | 2026-08-15 05:20 |  |  | Fair | No | Removed vegetation and replaced (1)50kva transformer fuse.
Outage | J.E.26.08.21898 | C001889582 | Barrington Brown | St.James | Completed | Load_263681 | Bogue - 310 | 2026-08-14 22:14 | 2026-08-14 22:15 | 2026-08-14 22:39 | 2026-08-14 22:40 | 2026-08-14 22:41 | 2026-08-14 23:08 | 2026-08-14 23:08 | 2026-08-14 23:08 |  |  | Fair | No | Crew found blow 30k junction fuse at pole number 215405. Crew conducted patrol and re energized circuit. All customers restored
Outage | J.E.26.08.21950 | C001889586 | Gregory Grossett | Portland | Completed | Load_245297 | Port Antonio - 410 | 2026-08-14 22:41 | 2026-08-14 22:42 | 2026-08-14 22:46 | 2026-08-14 22:47 | 2026-08-14 22:50 | 2026-08-14 22:53 | 2026-08-14 22:53 | 2026-08-14 22:53 | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | SevereWind | No | Customer stated High wind blowing trees towards conductors causing spark on wire conductors customer supply is ok.
Outage | J.E.26.08.20422 | C001889591 | Roxroy Needham | St.Ann | Completed | Load_258590 | Cardiff Hall - 210 | 2026-08-14 23:09 | 2026-08-14 23:10 | 2026-08-15 01:25 | 2026-08-15 01:25 | 2026-08-15 02:22 | 2026-08-15 02:28 | 2026-08-15 02:29 | 2026-08-15 02:29 |  |  | Fair | No | Premises found locked not getting customer on phone
Outage | J.E.26.08.21904 | C001889594 | Romeo Brissett | St.James | Completed | Load_261013 | Bogue - 310 | 2026-08-14 23:15 | 2026-08-14 23:18 | 2026-08-15 00:59 | 2026-08-15 01:00 | 2026-08-15 00:59 | 2026-08-15 00:40 | 2026-08-15 01:00 | 2026-08-15 01:00 |  |  | Fair | No | Check and found ok
Outage | J.E.26.08.21639 | C001889597 | Horace Malcolm | St.James | Completed | Load_247589 | Queens Drive - 710 | 2026-08-14 23:17 | 2026-08-15 07:19 | 2026-08-15 09:26 | 2026-08-15 09:27 | 2026-08-15 10:02 | 2026-08-15 10:13 | 2026-08-15 10:13 | 2026-08-15 10:13 | Fire |  | Fair | No | Check and found no fire on pole area check and found ok
Outage | J.E.26.08.21418 | C001889599 | Horace Malcolm | St.James | Completed | Load_293298 | Queens Drive - 310 | 2026-08-14 23:23 | 2026-08-15 07:17 | 2026-08-15 08:26 | 2026-08-15 08:26 | 2026-08-15 08:26 | 2026-08-15 08:27 | 2026-08-15 08:27 | 2026-08-15 08:27 |  |  | Fair | No | Check and found area ok supply restored
Outage | J.E.26.08.21416 | C001889600 | Horace Malcolm | St.James | Completed | Load_292475 | Queens Drive - 310 | 2026-08-14 23:24 | 2026-08-15 07:17 | 2026-08-15 08:25 | 2026-08-15 08:25 | 2026-08-15 08:25 | 2026-08-15 08:26 | 2026-08-15 08:26 | 2026-08-15 08:26 |  |  | Fair | No | Check and found area ok supply restored
Non-Outage | J.E.26.08.21074 | C001889603 | Edward Royal |  | Completed |  |  | 2026-08-14 23:46 | 2026-08-14 23:47 | 2026-08-15 04:01 | 2026-08-15 04:01 | 2026-08-15 04:01 | 2026-08-15 04:01 | 2026-08-15 04:02 | 2026-08-15 04:02 | Fire |  | Fair | No | Premises not found unable to communicate with customers via phone
Outage | J.E.26.08.22001 | C001889604 | Nickolas Rodriques | St.Catherine | Completed | Load_251876 | New Michelton - 310 | 2026-08-14 23:49 | 2026-08-14 23:50 | 2026-08-15 00:42 | 2026-08-15 00:46 | 2026-08-15 02:26 | 2026-08-15 03:33 | 2026-08-15 03:36 | 2026-08-15 03:36 |  |  | Fair | No | Unable to communicate with this specific customer. However, the area was patrolled and no outage was found.
Outage | J.E.26.08.22012 | C001889608 | Romeo Brissett | St.James | Completed | Load_267637 | Bogue - 610 | 2026-08-15 00:16 | 2026-08-15 00:17 | 2026-08-15 05:20 | 2026-08-15 05:21 | 2026-08-15 05:55 | 2026-08-15 06:48 | 2026-08-15 08:12 | 2026-08-15 08:12 |  |  | Fair | No | Isolated (1)50kva transformer, removed illegal connections and repaired transformer drop lead, used 6 clamps V/R 118-118-236
Outage | J.E.26.08.22056 | C001889613 | Edward Royal | KSAS | Completed | Load_261556 | Rockfort - 410 | 2026-08-15 01:16 | 2026-08-15 01:17 | 2026-08-15 03:19 | 2026-08-15 03:20 | 2026-08-15 03:19 | 2026-08-15 03:20 | 2026-08-15 03:21 | 2026-08-15 03:21 | Fire |  | Fair | No | Call related to outage
Non-Outage | J.E.26.08.21554 | C001889614 | Edward Royal |  | Completed |  |  | 2026-08-15 01:20 | 2026-08-15 01:21 | 2026-08-15 03:13 | 2026-08-15 03:14 | 2026-08-15 03:14 | 2026-08-15 01:00 | 2026-08-15 03:19 | 2026-08-15 03:19 |  |  | Fair | No | Reconnected primary jumper to switch top
Outage | J.E.26.08.22077 | C001889615 | Ricky Hall | St.Catherine | Completed | Load_261976 | Tredegar - 310 | 2026-08-15 02:40 | 2026-08-15 08:42 | 2026-08-15 09:31 | 2026-08-15 09:31 | 2026-08-15 09:40 | 2026-08-15 09:42 | 2026-08-15 09:43 | 2026-08-15 09:43 |  |  | Fair | No | Prepaid customer unable to add credit plz refer to the relevant team
Outage | J.E.26.08.21316 | C001889619 | Horace Malcolm | St.James | Completed | Load_302515 | Queens Drive - 310 | 2026-08-15 04:11 | 2026-08-15 07:19 | 2026-08-15 08:28 | 2026-08-15 08:29 | 2026-08-15 08:45 | 2026-08-15 08:58 | 2026-08-15 08:58 | 2026-08-15 08:58 |  |  | Fair | No | Check and found load side wires burnt in customer meter socket advised customer to rectify issue line side voltage 115-113-227-208
Outage | J.E.26.08.21415 | C001889620 | Horace Malcolm | St.James | Completed | Load_302533 | Queens Drive - 310 | 2026-08-15 04:11 | 2026-08-15 07:21 | 2026-08-15 08:22 | 2026-08-15 08:23 | 2026-08-15 08:22 | 2026-08-15 08:23 | 2026-08-15 08:23 | 2026-08-15 08:23 |  |  | Fair | No | Check and found area ok issue resolved supply restored
Outage | J.E.26.08.22131 | C001889642 | Nickolas Rodriques | St.Catherine | Completed | Load_238241 | Tredegar - 310 | 2026-08-15 06:41 | 2026-08-15 06:42 | 2026-08-15 07:06 | 2026-08-15 07:07 | 2026-08-15 07:06 | 2026-08-15 07:15 | 2026-08-15 07:17 | 2026-08-15 07:17 |  |  | Fair | No | Checked and found a 30 amp junction fuse blown. Patrol and found nothing on line. Repaired by replacing the fuse after completing patrol.
Outage | J.E.26.08.22167 | C001889644 | Omar King | St.Ann | Completed | Load_267440 | Ocho Rios - 510 | 2026-08-15 07:05 | 2026-08-15 07:08 | 2026-08-15 07:50 | 2026-08-15 07:51 | 2026-08-15 09:00 | 2026-08-15 09:05 | 2026-08-15 09:05 | 2026-08-15 09:05 |  |  | Fair | No | Found a 20 amp junction fuse blow cause by tree contact fuse as been replaced area is now with supply
Outage | J.E.26.08.21417 | C001889668 | Horace Malcolm | St.James | Completed | Load_293470 | Queens Drive - 310 | 2026-08-15 07:15 | 2026-08-15 07:16 | 2026-08-15 07:45 | 2026-08-15 07:46 | 2026-08-15 08:12 | 2026-08-15 08:20 | 2026-08-15 08:20 | 2026-08-15 08:20 |  |  | Fair | No | Check and found area ok issue resolved supply restored
Outage | J.E.26.08.21330 | C001889672 | Neville Spencer | Clarendon | Completed | Load_260333 | Parnassus - 310 | 2026-08-15 07:22 | 2026-08-15 07:24 | 2026-08-15 11:41 | 2026-08-15 11:42 | 2026-08-15 11:41 | 2026-08-15 11:41 | 2026-08-15 11:43 | 2026-08-15 11:43 | BrokenWire |  | Fair | No | Found ok customer got back light yesterday.
Outage | J.E.26.08.21339 | C001889673 | Neville Spencer | Clarendon | Completed | Load_249122 | Parnassus - 210 | 2026-08-15 07:22 | 2026-08-15 07:24 | 2026-08-15 07:35 | 2026-08-15 07:36 | 2026-08-15 09:21 | 2026-08-15 09:21 | 2026-08-15 09:24 | 2026-08-15 09:24 |  |  | Fair | No | Found 15 amp j/ switch in main line connection burnt off hot line clamp REF TO Maintenance.
Outage | J.E.26.08.21609 | C001889674 | Wan Carlos Scarlett | Portmore | Completed | Load_268300 | Naggo Head - 610 | 2026-08-15 07:25 | 2026-08-15 07:26 | 2026-08-15 08:15 | 2026-08-15 08:15 | 2026-08-15 08:54 | 2026-08-15 09:49 | 2026-08-15 09:54 | 2026-08-15 09:54 | Fire |  | Fair | No | Found 50kVA transformer drop lead wire to open secondary line phase and neutral corroded use 6 one bolt clamps at pole and found one span of open secondary line phase jumper burn out from the one bolt clamp use 4 one bolt clamps pole at secondary line readings 116-117-234
Outage | J.E.26.08.21945 | C001889675 | Marlon Authors | St.Elizabeth | Completed | Load_292060 | Maggotty - 210 | 2026-08-15 07:25 | 2026-08-15 07:28 | 2026-08-15 11:33 | 2026-08-15 11:34 | 2026-08-15 12:07 | 2026-08-15 12:20 | 2026-08-15 12:20 | 2026-08-15 12:20 |  |  | Fair | No | Patrol and found clear. Replace one blown 1.5 amp fuse that protects 15 kva transformer circuit no pole #. Restored supply ok
Outage | J.E.26.08.21312 | C001889679 | Neville Spencer | Clarendon | Completed | Load_253922 | May Pen - 210 | 2026-08-15 07:27 | 2026-08-15 07:38 | 2026-08-15 16:59 | 2026-08-15 17:00 | 2026-08-15 18:13 | 2026-08-15 18:13 | 2026-08-15 18:15 | 2026-08-15 18:15 |  |  | Fair | No | Cleared creeper from switch pole renew blown 8 amp j/ fuse supply restored.
Outage | J.E.26.08.21495 | C001889680 | Neville Spencer | Clarendon | Completed | Load_261816 | Parnassus - 310 | 2026-08-15 07:27 | 2026-08-15 07:38 | 2026-08-15 13:33 | 2026-08-15 13:33 | 2026-08-15 14:35 | 2026-08-15 14:35 | 2026-08-15 15:32 | 2026-08-15 15:32 |  |  | Fair | No | Remade wrap joints at pothead on 3, wire service used 3, 6/6 sleeves .Also remade burnt out clamp on netural drop lead used 1, clamp voltage reading 113 117 231+supply restored.
Outage | J.E.26.08.21565 | C001889681 | Neville Spencer | Clarendon | Completed | Load_260333 | Parnassus - 310 | 2026-08-15 07:27 | 2026-08-15 07:38 | 2026-08-15 11:34 | 2026-08-15 11:35 | 2026-08-15 11:35 | 2026-08-15 11:35 | 2026-08-15 11:37 | 2026-08-15 11:37 |  |  | Fair | No | Found customers private lines damaged disconnect, disconnect 2, 3 wire service customer advised.
Outage | J.E.26.08.21979 | C001889678 | Raheem Ricketts | St.Elizabeth | Completed | Load_258382 | Maggotty - 210 | 2026-08-15 07:27 | 2026-08-15 07:28 | 2026-08-15 07:42 | 2026-08-15 12:59 | 2026-08-15 12:59 | 2026-08-15 12:59 | 2026-08-15 12:59 | 2026-08-15 12:59 | Fire |  | Fair | No | Call related
Outage | J.E.26.08.21987 | C001889677 | Raheem Ricketts | St.Elizabeth | Completed | Load_258382 | Maggotty - 210 | 2026-08-15 07:27 | 2026-08-15 07:28 | 2026-08-15 07:42 | 2026-08-15 08:03 | 2026-08-15 09:01 | 2026-08-15 10:40 | 2026-08-15 10:40 | 2026-08-15 10:40 | BrokenWire |  | Fair | No | Splice and retention 1pole span of secondary neutral using 80ft of number 2,2,#2 preform 1 number two sleeve 2,clamps retention 2 pole span of secondary top phase also connected 100 ft of customer service wire using 4 clamps two link
Non-Outage | J.E.26.08.20671 | C001889684 | Marlon Authors |  | Completed |  |  | 2026-08-15 07:28 | 2026-08-16 14:55 | 2026-08-16 17:36 | 2026-08-16 17:36 | 2026-08-16 17:56 | 2026-08-16 18:01 | 2026-08-16 18:01 | 2026-08-16 18:01 |  |  | Fair | No | Customer states that she has two meters at the premises,however she only has one account so she is requesting a jps technician to come and rectify this issue. Please refer same to the field services department for further assistance
Outage | J.E.26.08.21872 | C001889682 | Neville Spencer | Clarendon | Completed | Load_260333 | Parnassus - 310 | 2026-08-15 07:28 | 2026-08-15 07:38 | 2026-08-15 11:46 | 2026-08-15 11:47 | 2026-08-15 11:47 | 2026-08-15 11:47 | 2026-08-15 11:47 | 2026-08-15 11:47 |  |  | Fair | No | Customer not located.
Outage | J.E.26.08.22018 | C001889683 | Neville Spencer | Clarendon | Completed | Load_260333 | Parnassus - 310 | 2026-08-15 07:28 | 2026-08-15 07:38 | 2026-08-15 09:32 | 2026-08-15 09:33 | 2026-08-15 10:35 | 2026-08-15 10:35 | 2026-08-15 11:34 | 2026-08-15 11:34 | Fire |  | Fair | No | Found customer private line damaged disconnect 2, 3 wire service customer advised.
Non-Outage | J.E.26.08.21777 | C001889685 | Raymond Lewis |  | Completed |  |  | 2026-08-15 07:30 | 2026-08-15 07:38 | 2026-08-15 09:42 | 2026-08-15 09:43 | 2026-08-15 09:42 | 2026-08-15 09:44 | 2026-08-15 09:44 | 2026-08-15 09:44 |  |  | Fair | No | Supply restored
Outage | J.E.26.08.20944 | C001889686 | Raheem Ricketts | St.Elizabeth | Completed | Load_1002215 | Maggotty - 210 | 2026-08-15 07:31 | 2026-08-15 07:32 | 2026-08-15 07:42 | 2026-08-15 11:04 | 2026-08-15 11:04 | 2026-08-15 11:33 | 2026-08-15 11:34 | 2026-08-15 11:34 | LowHangingWires |  | Fair | No | Check and found customer experiencing 1 leg remake joint at pole using 1 clamp voltage left 110,110,220
Outage | J.E.26.08.20742 | C001889687 | Derrick Dawkins | St.James | Completed | Load_238337 | Bogue - 610 | 2026-08-15 07:32 | 2026-08-15 07:34 | 2026-08-15 10:09 | 2026-08-15 10:10 | 2026-08-15 11:28 | 2026-08-15 11:39 | 2026-08-15 11:40 | 2026-08-15 11:40 |  |  | Fair | No | Customer pothead head torn down need to be fixed customer advised
Non-Outage | J.E.26.08.21741 | C001889688 | Raymond Lewis |  | Completed |  |  | 2026-08-15 07:33 | 2026-08-15 07:38 | 2026-08-15 10:23 | 2026-08-15 10:23 | 2026-08-15 10:45 | 2026-08-15 10:46 | 2026-08-15 10:46 | 2026-08-15 10:46 |  |  | Fair | No | Supply restored
Non-Outage | J.E.26.08.21730 | C001889689 | Raymond Lewis |  | Completed |  |  | 2026-08-15 07:34 | 2026-08-15 07:38 | 2026-08-15 09:47 | 2026-08-15 09:48 | 2026-08-15 09:47 | 2026-08-15 09:48 | 2026-08-15 09:49 | 2026-08-15 09:49 | BrokenWire |  | Fair | No | Supply restored
Non-Outage | J.E.26.08.21265 | C001889694 | Raymond Lewis |  | Completed |  |  | 2026-08-15 07:35 | 2026-08-15 07:38 | 2026-08-15 08:32 | 2026-08-15 08:33 | 2026-08-15 08:32 | 2026-08-15 08:33 | 2026-08-15 08:33 | 2026-08-15 08:33 | Fire |  | Fair | No | Supply restored
Non-Outage | J.E.26.08.21310 | C001889693 | Raymond Lewis |  | Completed |  |  | 2026-08-15 07:35 | 2026-08-15 07:38 | 2026-08-15 08:27 | 2026-08-15 08:27 | 2026-08-15 08:27 | 2026-08-15 08:28 | 2026-08-15 08:28 | 2026-08-15 08:28 |  |  | Fair | No | Supply restored
Non-Outage | J.E.26.08.21464 | C001889692 | Raymond Lewis |  | Completed |  |  | 2026-08-15 07:35 | 2026-08-15 07:38 | 2026-08-15 08:29 | 2026-08-15 08:30 | 2026-08-15 08:29 | 2026-08-15 08:30 | 2026-08-15 08:30 | 2026-08-15 08:30 | Fire |  | Fair | No | Supply restored
Non-Outage | J.E.26.08.21722 | C001889690 | Raymond Lewis |  | Completed |  |  | 2026-08-15 07:35 | 2026-08-15 07:38 | 2026-08-15 08:41 | 2026-08-15 08:41 | 2026-08-15 08:41 | 2026-08-15 08:41 | 2026-08-15 08:42 | 2026-08-15 08:42 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.22129 | C001889695 | Raymond Lewis | St.Ann | Completed | Load_253779 | Cardiff Hall - 310 | 2026-08-15 07:37 | 2026-08-15 07:40 | 2026-08-15 08:38 | 2026-08-15 08:38 | 2026-08-15 08:38 | 2026-08-15 08:39 | 2026-08-15 08:39 | 2026-08-15 08:39 |  |  | Fair | No | Supply restored
Non-Outage | J.E.26.08.21788 | C001889697 | Hartley Chin |  | Completed |  |  | 2026-08-15 07:40 | 2026-08-15 07:43 | 2026-08-15 08:04 | 2026-08-15 08:05 | 2026-08-15 10:11 | 2026-08-15 10:11 | 2026-08-15 10:12 | 2026-08-15 10:12 |  |  | Fair | No | Found ok unable to contact customer area patrolled and found ok
Non-Outage | J.E.26.08.21791 | C001889696 | Hartley Chin |  | Completed |  |  | 2026-08-15 07:40 | 2026-08-15 07:43 | 2026-08-15 08:54 | 2026-08-15 10:18 | 2026-08-15 10:18 | 2026-08-15 10:18 | 2026-08-15 10:18 | 2026-08-15 10:18 |  |  | Fair | No
Outage | J.E.26.08.21775 | C001889699 | Collin Robinson | Portland | Completed | Load_349991 | Port Antonio - 310 | 2026-08-15 07:40 | 2026-08-15 07:41 | 2026-08-15 08:26 | 2026-08-15 08:26 | 2026-08-15 08:30 | 2026-08-15 08:32 | 2026-08-15 08:32 | 2026-08-15 08:32 |  |  | Fair | No | Unable to locate customer
Non-Outage | J.E.26.08.21821 | C001889701 | Stephen Taylor |  | Completed |  |  | 2026-08-15 07:44 | 2026-08-15 07:46 | 2026-08-15 18:31 | 2026-08-15 18:31 | 2026-08-15 18:31 | 2026-08-15 18:31 | 2026-08-15 18:32 | 2026-08-15 18:32 |  |  | Fair | No | Check with customer and customer said power is back now and okay
Outage | J.E.26.08.21370 | C001889700 | Hartley Chin | Clarendon | Completed | Load_569758 | Parnassus - 210 | 2026-08-15 07:44 | 2026-08-16 07:33 | 2026-08-16 14:30 | 2026-08-16 14:31 | 2026-08-16 16:07 | 2026-08-16 16:08 | 2026-08-16 16:13 | 2026-08-16 16:13 | BrokenWire |  | Fair | No | Found slack neutral jumper on line . Replaced with one bolt clamp. No broken wire.
Outage | J.E.26.08.21803 | C001889702 | Stephen Taylor | St.Thomas | Completed | Load_243194 | Good Year - 210 | 2026-08-15 07:44 | 2026-08-15 07:46 | 2026-08-15 10:13 | 2026-08-15 10:13 | 2026-08-15 10:13 | 2026-08-15 10:13 | 2026-08-15 10:14 | 2026-08-15 10:14 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Call to customer and customer said power is back from yesterday and okay
Outage | J.E.26.08.21038 | C001889709 | Kenroy Dale | Manchester | Completed | Load_254233 | Kendal - 210 | 2026-08-15 07:48 | 2026-08-15 07:49 | 2026-08-15 11:52 | 2026-08-15 12:10 | 2026-08-15 13:15 | 2026-08-15 13:43 | 2026-08-15 13:51 | 2026-08-15 13:51 |  |  | Fair | No | Customer meter socket wire incorrect, customer was advised to get an electrician to rectify problem
Outage | J.E.26.08.22146 | C001889708 | Kenroy Dale | Manchester | Completed | Load_268498 | Kendal - 210 | 2026-08-15 07:48 | 2026-08-15 07:49 | 2026-08-15 09:43 | 2026-08-15 09:44 | 2026-08-15 11:00 | 2026-08-15 11:45 | 2026-08-15 11:52 | 2026-08-15 11:52 |  |  | Fair | No | Blown 3 amp transformer fuse found line patrol 3 span of secondary phase and neutral found broken (suspected cause severe wind) Conductor was splice and retention blown fuse replaced and area now with supply
Outage | J.E.26.08.21470 | C001889710 | Barnett Brown | Manchester | Completed | Load_241844 | Spur Tree - 310 | 2026-08-15 07:49 | 2026-08-15 07:50 | 2026-08-15 11:57 | 2026-08-15 11:57 | 2026-08-15 12:29 | 2026-08-15 12:39 | 2026-08-15 12:41 | 2026-08-15 12:41 |  |  | Fair | No | Customer has internal fault, voltage 117 117 234
Outage | J.E.26.08.22079 | C001889712 | Elvis Trowers | KSAS | Completed | Load_579134 | Duhaney - 310 | 2026-08-15 07:49 | 2026-08-15 07:55 | 2026-08-15 10:47 | 2026-08-15 10:53 | 2026-08-15 11:16 | 2026-08-15 11:10 | 2026-08-15 11:17 | 2026-08-15 11:17 |  |  | Fair | No | Customer service wire #6 triplex phase burn off at pole. Repair using one 1- bolt clamp. Readings at pothead 114 volts.
Outage | J.E.26.08.22220 | C001889711 | Elvis Trowers | KSAN | Completed | Load_264325 | Washington Blvd - 510 | 2026-08-15 07:49 | 2026-08-15 07:55 | 2026-08-15 08:21 | 2026-08-15 13:52 | 2026-08-15 13:52 | 2026-08-15 14:10 | 2026-08-15 13:53 | 2026-08-15 13:53 |  |  | Fair | No | Found okay.
Outage | J.E.26.08.21552 | C001889718 | Christopher Edwards | KSAN | Completed | Load_264959 | Constant Spring - 410 | 2026-08-15 07:50 | 2026-08-15 07:54 | 2026-08-15 13:29 | 2026-08-15 13:29 | 2026-08-15 13:29 | 2026-08-15 15:07 | 2026-08-15 15:07 | 2026-08-15 15:07 |  |  | Fair | No | Remake burnt phase joint at pole Using (2) one bolt clamps Voltage:112,113,218v
Outage | J.E.26.08.21611 | C001889717 | Christopher Edwards | KSAN | Completed | Load_259437 | Constant Spring - 210 | 2026-08-15 07:50 | 2026-08-15 07:54 | 2026-08-15 08:06 | 2026-08-15 09:09 | 2026-08-15 09:35 | 2026-08-15 09:52 | 2026-08-15 09:55 | 2026-08-15 09:55 |  |  | Fair | Yes | Unable to locate premises
Outage | J.E.26.08.21747 | C001889716 | Elvis Trowers | KSAN | Completed | Load_557742 | Washington Blvd - 610 | 2026-08-15 07:50 | 2026-08-15 07:55 | 2026-08-15 11:44 | 2026-08-15 13:07 | 2026-08-15 13:10 | 2026-08-15 13:15 | 2026-08-15 13:11 | 2026-08-15 13:11 |  |  | Fair | No | Found okay upon arrival. Customer has an internal problem.
Outage | J.E.26.08.21761 | C001889714 | Elvis Trowers | KSAN | Completed | Load_247868 | Washington Blvd - 810 | 2026-08-15 07:50 | 2026-08-15 07:55 | 2026-08-15 11:52 | 2026-08-15 11:52 | 2026-08-15 13:05 | 2026-08-15 12:30 | 2026-08-15 13:07 | 2026-08-15 13:07 |  |  | Fair | No | Customer service wire #6 triplex phase corroded at pothead repair using two 1- bolt clamps. Readings at pothead and meter socket 114-113-228 volts.
Outage | J.E.26.08.21779 | C001889713 | Elvis Trowers | KSAN | Completed | Load_265878 | Washington Blvd - 410 | 2026-08-15 07:50 | 2026-08-15 07:55 | 2026-08-15 13:11 | 2026-08-15 13:12 | 2026-08-15 13:37 | 2026-08-15 13:30 | 2026-08-15 13:37 | 2026-08-15 13:37 |  |  | Fair | No | Found okay upon arrival. Customer has an internal problem.
Outage | J.E.26.08.22228 | C001889715 | Wayne Dillion | St.Elizabeth | Completed | Load_248025 | Maggotty - 110 | 2026-08-15 07:50 | 2026-08-15 15:28 | 2026-08-15 16:33 | 2026-08-15 16:33 | 2026-08-15 16:33 | 2026-08-15 16:34 | 2026-08-15 16:34 | 2026-08-15 16:34 |  |  | Fair | No | Customer is inquiring about bill and said they want a disconnection
Non-Outage | J.E.26.08.21591 | C001889720 | Javid Vernon | Westmoreland | Completed | Load_264370 | Paradise - 210 | 2026-08-15 07:51 | 2026-08-15 07:52 | 2026-08-15 09:00 | 2026-08-15 09:01 | 2026-08-15 09:52 | 2026-08-15 10:15 | 2026-08-15 10:15 | 2026-08-15 10:15 |  |  | Fair | No | Remove illegal connections and reconnect customer service wire use one clamp voltage reading 105/107/212
Non-Outage | J.E.26.08.21877 | C001889721 | Javid Vernon | Westmoreland | Completed | Load_248847 | Paradise - 210 | 2026-08-15 07:51 | 2026-08-15 07:52 | 2026-08-15 10:15 | 2026-08-15 10:16 | 2026-08-15 10:47 | 2026-08-15 11:11 | 2026-08-15 11:11 | 2026-08-15 11:11 |  |  | Fair | No | Premises check and found okay voltage found and left at premises 113/113/197/235/226/233
Non-Outage | J.E.26.08.22086 | C001889722 | Javid Vernon | Westmoreland | Completed | Load_246361 | Paradise - 110 | 2026-08-15 07:51 | 2026-08-15 07:52 | 2026-08-15 08:55 | 2026-08-15 08:58 | 2026-08-15 08:58 | 2026-08-15 08:58 | 2026-08-15 08:58 | 2026-08-15 08:58 |  |  | Fair | No | Customer stated that the power was restored to her premises
Outage | J.E.26.08.21814 | C001889723 | Elvis Trowers |  | Completed | Load_568735 | Washington Blvd - 510 | 2026-08-15 07:51 | 2026-08-15 07:58 | 2026-08-15 12:32 | 2026-08-15 13:52 | 2026-08-15 13:51 | 2026-08-15 13:55 | 2026-08-15 13:52 | 2026-08-15 13:52 |  |  | Fair | No | Found okay upon arrival.
Outage | J.E.26.08.22120 | C001889719 | Eric Williams | KSAN | Completed | Load_251677 | Constant Spring - 310 | 2026-08-15 07:51 | 2026-08-15 08:39 | 2026-08-15 13:42 | 2026-08-15 13:43 | 2026-08-15 13:43 | 2026-08-15 13:43 | 2026-08-15 13:55 | 2026-08-15 13:55 |  |  | Fair | No | Blown 2amps transformer fuse found and replaced cause by tree contact, major bushing done, refer to maintenance at additional bushing required
Outage | J.E.26.08.21697 | C001889725 | Antony Levy | KSAN | Completed | Load_242894 | Hope - 410 | 2026-08-15 08:00 | 2026-08-15 15:00 | 2026-08-15 15:31 | 2026-08-15 15:31 | 2026-08-15 16:53 | 2026-08-15 16:58 | 2026-08-15 16:59 | 2026-08-15 16:59 | BrokenWire |  | Fair | No
Non-Outage | J.E.26.08.17256 | C001889728 | Javid Vernon | Westmoreland | Completed | Load_268696 | Paradise - 210 | 2026-08-15 08:01 | 2026-08-15 08:02 | 2026-08-15 11:11 | 2026-08-15 11:12 | 2026-08-15 11:11 | 2026-08-15 11:11 | 2026-08-15 11:12 | 2026-08-15 11:12 |  |  | Fair | No | Customer stated that the issue has been resolved
Non-Outage | J.E.26.08.22235 | C001889726 | Oshane Warren |  | Completed |  |  | 2026-08-15 08:01 | 2026-08-15 08:02 | 2026-08-15 09:28 | 2026-08-15 09:28 | 2026-08-15 10:00 | 2026-08-15 10:00 | 2026-08-15 10:01 | 2026-08-15 10:01 |  |  | Fair | No | Unable to locate or contact customer need direction
Outage | J.E.26.08.21149 | C001889727 | Elvis Trowers | KSAS | Completed | Load_579135 | Duhaney - 310 | 2026-08-15 08:01 | 2026-08-15 08:03 | 2026-08-15 10:40 | 2026-08-15 10:41 | 2026-08-15 10:51 | 2026-08-15 10:55 | 2026-08-15 10:53 | 2026-08-15 10:53 | TreeContact |  | Fair | No | Primary bushing required urgently. Tree touching primary three phase line causing sparks.
Outage | J.E.26.08.21843 | C001889729 | Hartley Chin | Clarendon | Completed | Load_352838 | May Pen - 110 | 2026-08-15 08:02 | 2026-08-15 08:08 | 2026-08-15 08:53 | 2026-08-15 10:17 | 2026-08-15 10:17 | 2026-08-15 10:17 | 2026-08-15 10:17 | 2026-08-15 10:17 |  |  | Fair | No | Found ok
Outage | J.E.26.08.22198 | C001889730 | Elvis Trowers | KSAS | Completed | Load_266592 | Greenwich - 710 | 2026-08-15 08:03 | 2026-08-15 08:04 | 2026-08-15 08:57 | 2026-08-15 08:58 | 2026-08-15 09:43 | 2026-08-15 09:30 | 2026-08-15 09:44 | 2026-08-15 09:44 |  |  | Fair | No | Schedule outage in the area.
Outage | J.E.26.08.22232 | C001889732 | Elvis Trowers | KSAS | Completed | Load_579255 | Duhaney - 310 | 2026-08-15 08:05 | 2026-08-15 08:07 | 2026-08-15 09:47 | 2026-08-15 09:47 | 2026-08-15 10:38 | 2026-08-15 09:55 | 2026-08-15 10:40 | 2026-08-15 10:40 |  |  | Fair | No | Customer fed from hexing box and getting no supply from the box no communication coming from the box state J.P.S. Escalation. Refer to field service.
Outage | J.E.26.08.22243 | C001889734 | Tajay Bernard | Hanover | Completed | Load_265332 | Orange Bay - 310 | 2026-08-15 08:07 | 2026-08-15 08:10 | 2026-08-15 08:15 | 2026-08-15 08:16 | 2026-08-15 09:21 | 2026-08-15 09:36 | 2026-08-15 09:38 | 2026-08-15 09:38 |  |  | Fair | No | Remove vegetation and refuse 1 25kva Transformer, 3amp fuse was used
Outage | J.E.26.08.21724 | C001889737 | Neville Spencer | Clarendon | Completed | Load_244812 | Parnassus - 310 | 2026-08-15 08:08 | 2026-08-15 08:09 | 2026-08-15 16:11 | 2026-08-15 16:12 | 2026-08-15 16:18 | 2026-08-15 16:18 | 2026-08-15 16:58 | 2026-08-15 16:58 |  |  | Fair | No | Remade corrded netural joint at pothead on 2 wire service used 1,clamp voltage reading 114 .
Outage | J.E.26.08.21977 | C001889735 | Hartley Chin | Clarendon | Completed | Load_237724 | May Pen - 110 | 2026-08-15 08:08 | 2026-08-15 08:09 | 2026-08-15 08:53 | 2026-08-15 10:17 | 2026-08-15 10:17 | 2026-08-15 10:17 | 2026-08-15 10:17 | 2026-08-15 10:17 |  |  | Fair | No | Found ok
Outage | J.E.26.08.22202 | C001889736 | Richard Nicholas | St.Catherine | Completed | Load_261448 | Tredegar - 210 | 2026-08-15 08:08 | 2026-08-15 08:09 | 2026-08-15 08:15 | 2026-08-15 08:16 | 2026-08-15 09:35 | 2026-08-15 10:37 | 2026-08-15 10:42 | 2026-08-15 10:42 | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Remade slack 3w service phase and neutral joint at pothead,3 linket was used.voltage reading 114x2 and 228v.
Outage | J.E.26.08.22251 | C001889738 | Christopher Edwards | KSAN | Completed | Load_247780 | Constant Spring - 410 | 2026-08-15 08:12 | 2026-08-15 08:13 | 2026-08-15 09:56 | 2026-08-15 09:57 | 2026-08-15 10:30 | 2026-08-15 11:25 | 2026-08-15 11:26 | 2026-08-15 11:26 |  |  | Fair | Yes | Refuse blown junction fuse Using (1) 30 amps
Non-Outage | J.E.26.08.21233 | C001889741 | Rusean Allen |  | Completed |  |  | 2026-08-15 08:13 | 2026-08-15 08:17 | 2026-08-15 12:08 | 2026-08-15 12:08 | 2026-08-15 12:08 | 2026-08-15 12:09 | 2026-08-15 12:09 | 2026-08-15 12:09 |  |  | Fair | No | Okay
Non-Outage | J.E.26.08.21940 | C001889740 | Rusean Allen |  | Completed |  |  | 2026-08-15 08:13 | 2026-08-15 08:17 | 2026-08-15 10:43 | 2026-08-15 12:29 | 2026-08-15 13:37 | 2026-08-15 13:38 | 2026-08-15 13:38 | 2026-08-15 13:38 |  |  | Fair | No | More information needed
Outage | J.E.26.08.21148 | C001889744 | Rusean Allen | KSAS | Completed | Load_257857 | Rockfort - 210 | 2026-08-15 08:13 | 2026-08-15 08:17 | 2026-08-15 10:43 | 2026-08-15 12:10 | 2026-08-15 12:28 | 2026-08-15 12:28 | 2026-08-15 12:29 | 2026-08-15 12:29 |  |  | Fair | No | Customer reported streetlight not working.
Outage | J.E.26.08.21855 | C001889745 | Rusean Allen | KSAS | Completed | Load_261397 | Hunts Bay - 310 | 2026-08-15 08:13 | 2026-08-15 08:17 | 2026-08-15 11:43 | 2026-08-15 11:43 | 2026-08-15 12:02 | 2026-08-15 12:08 | 2026-08-15 12:08 | 2026-08-15 12:08 | BrokenWire |  | Fair | No | Found okay
Outage | J.E.26.08.22171 | C001889743 | Rusean Allen | KSAS | Completed | Load_256320 | Rockfort - 410 | 2026-08-15 08:13 | 2026-08-15 08:17 | 2026-08-15 08:55 | 2026-08-15 08:56 | 2026-08-15 10:24 | 2026-08-15 10:24 | 2026-08-15 10:25 | 2026-08-15 10:25 |  |  | Fair | No | Premises okay
Outage | J.E.26.08.22206 | C001889742 | Rusean Allen | KSAS | Completed | Load_239004 | Rockfort - 410 | 2026-08-15 08:13 | 2026-08-15 08:17 | 2026-08-15 10:41 | 2026-08-15 10:41 | 2026-08-15 11:37 | 2026-08-15 11:42 | 2026-08-15 11:42 | 2026-08-15 11:42 |  |  | Fair | No | Power was already restored
Outage | J.E.26.08.21999 | C001889746 | Wan Carlos Scarlett | St.Catherine | Completed | Load_576209 | Twickenham - 210 | 2026-08-15 08:17 | 2026-08-15 08:19 | 2026-08-15 10:33 | 2026-08-15 11:32 | 2026-08-15 12:46 | 2026-08-15 13:12 | 2026-08-15 13:12 | 2026-08-15 13:12 |  |  | Fair | No | Customer was reconnected from escalation department power supply has been restored
Non-Outage | J.E.26.08.16002 | C001889747 | Wan Carlos Scarlett |  | Completed |  |  | 2026-08-15 08:19 | 2026-08-15 08:20 | 2026-08-15 11:13 | 2026-08-15 17:13 | 2026-08-15 18:06 | 2026-08-15 18:31 | 2026-08-15 18:32 | 2026-08-15 18:32 |  |  | Fair | No | Customer not available at this time premises closed
Outage | J.E.26.08.20251 | C001889748 | Wan Carlos Scarlett | St.Catherine | Completed | Load_249635 | Twickenham - 210 | 2026-08-15 08:19 | 2026-08-15 08:20 | 2026-08-15 12:01 | 2026-08-15 15:09 | 2026-08-15 15:42 | 2026-08-15 16:07 | 2026-08-15 16:08 | 2026-08-15 16:08 |  |  | Fair | No | Customer confirm that power supply has been restored
Outage | J.E.26.08.20425 | C001889749 | Wan Carlos Scarlett | Portmore | Completed | Load_255168 | Naggo Head - 610 | 2026-08-15 08:19 | 2026-08-15 08:20 | 2026-08-15 09:54 | 2026-08-15 09:55 | 2026-08-15 10:13 | 2026-08-15 10:25 | 2026-08-15 10:28 | 2026-08-15 10:28 |  |  | Fair | No | Found customer 3 wire service at pothead with one of the phase corroded use 3 Penn union at service wire phase and neutral readings 113-114-229
Non-Outage | J.E.26.08.17808 | C001889752 | Neville Spencer |  | Completed |  |  | 2026-08-15 08:23 | 2026-08-15 08:25 | 2026-08-15 11:51 | 2026-08-15 11:52 | 2026-08-15 11:51 | 2026-08-15 11:51 | 2026-08-15 11:52 | 2026-08-15 11:52 |  |  | Fair | No | Not located.
Outage | J.E.26.08.22151 | C001889753 | Romaine Roberts | St.Mary | Completed | Load_259600 | Oracabessa - 210 | 2026-08-15 08:24 | 2026-08-15 09:00 | 2026-08-15 12:12 | 2026-08-15 12:12 | 2026-08-15 13:18 | 2026-08-15 13:51 | 2026-08-15 13:51 | 2026-08-15 13:51 | BrokenWire |  | Fair | No | Found junction fuse blown also 50 kva transformer fuse blown patrol line nothing found replace 5 amp and 15 amp junction power restore
Outage | J.E.26.08.22172 | C001889754 | Raymond Carr | St.Mary | Completed | Load_239531 | Oracabessa - 210 | 2026-08-15 08:25 | 2026-08-16 09:46 | 2026-08-16 12:14 | 2026-08-16 12:14 | 2026-08-16 13:00 | 2026-08-16 13:00 | 2026-08-16 13:03 | 2026-08-16 13:03 |  |  | SevereWind | No | Customer couldn’t be contacted.
Non-Outage | J.E.26.08.21437 | C001889755 | Wan Carlos Scarlett |  | Completed |  |  | 2026-08-15 08:29 | 2026-08-15 08:30 | 2026-08-15 10:32 | 2026-08-15 16:08 | 2026-08-15 16:59 | 2026-08-15 17:09 | 2026-08-15 17:13 | 2026-08-15 17:13 | LowHangingWires |  | Fair | No | Found cable and wireless wire hanging low to the ground advised customer to contact cable provider for assistance
Outage | J.E.26.08.20835 | C001889757 | Ricky Hall | Portmore | Completed | Load_254681 | Naggo Head - 510 | 2026-08-15 08:31 | 2026-08-15 08:33 | 2026-08-15 08:58 | 2026-08-15 08:58 | 2026-08-15 09:22 | 2026-08-15 09:30 | 2026-08-15 09:30 | 2026-08-15 09:30 |  |  | Fair | No | Issue was resolved on previous shift
Outage | J.E.26.08.22272 | C001889758 | Collin Robinson | Portland | Completed | Load_250350 | Port Antonio - 410 | 2026-08-15 08:32 | 2026-08-15 08:37 | 2026-08-15 08:53 | 2026-08-15 08:54 | 2026-08-15 10:34 | 2026-08-15 11:17 | 2026-08-15 11:18 | 2026-08-15 11:18 |  |  | Fair | No | Patrol single phase primary line and found tree branch brushing primary conductor cut and clear branch from line and replace 20 amps junction fuse
Outage | J.E.26.08.22275 | C001889759 | Eric Williams | KSAS | Completed | Load_262439 | Hunts Bay - 310 | 2026-08-15 08:34 | 2026-08-15 08:35 | 2026-08-15 08:51 | 2026-08-15 08:57 | 2026-08-15 09:14 | 2026-08-15 10:31 | 2026-08-15 10:32 | 2026-08-15 10:32 |  |  | Fair | No | Open 3 dropout fuse, for SMD to carry out repairs
Outage | J.E.26.08.22273 | C001889760 | Eric Williams | KSAN | Completed | Load_261919 | Constant Spring - 310 | 2026-08-15 08:35 | 2026-08-15 08:38 | 2026-08-15 11:37 | 2026-08-15 11:37 | 2026-08-15 12:11 | 2026-08-15 13:22 | 2026-08-15 13:42 | 2026-08-15 13:42 |  | Y | Fair | No | Blown 2amps transformer fuse found and replaced cause by tree contact, major bushing done, refer to maintenance at additional bushing required
Outage | J.E.26.08.22264 | C001889762 | Barnett Brown | Manchester | Completed | Load_261375 | Spur Tree - 310 | 2026-08-15 08:36 | 2026-08-15 08:37 | 2026-08-15 10:30 | 2026-08-15 10:31 | 2026-08-15 11:32 | 2026-08-15 11:49 | 2026-08-15 11:51 | 2026-08-15 11:51 | BrokenWire |  | Fair | No | No broken wire observed, area has light, no one knows customer
Outage | J.E.26.08.21629 | C001889764 | Floyd Taylor | Trelawny | Completed | Load_268005 | Greenwood - 110 | 2026-08-15 08:37 | 2026-08-15 08:38 | 2026-08-15 09:13 | 2026-08-15 10:12 | 2026-08-15 10:11 | 2026-08-15 11:42 | 2026-08-15 11:43 | 2026-08-15 11:43 | Fire |  | Fair | No | Remove illegal connection from line, voltage reading 111,112, 226
Outage | J.E.26.08.21952 | C001889766 | Andre Williams | Trelawny | Completed | Load_239166 | Duncans - 110 | 2026-08-15 08:37 | 2026-08-16 07:07 | 2026-08-16 07:31 | 2026-08-16 07:33 | 2026-08-16 08:27 | 2026-08-16 08:30 | 2026-08-16 08:30 | 2026-08-16 08:30 | Fire |  | Fair | No | Customer advice to get electrician 400 ft of wire leading to premises line is private
Outage | J.E.26.08.21705 | C001889767 | Romaine Roberts | St.Mary | Completed | Load_239680 | Highgate -110 | 2026-08-15 08:40 | 2026-08-15 08:42 | 2026-08-15 09:22 | 2026-08-15 09:22 | 2026-08-15 11:46 | 2026-08-15 12:11 | 2026-08-15 12:12 | 2026-08-15 12:12 |  |  | Fair | No | 25 kva transformer fuse found blown patrol line nothing found replace 3 amp power restore
Outage | J.E.26.08.21637 | C001889768 | Romaine Roberts | St.Mary | Completed | Load_260173 | Annotto Bay - 310 | 2026-08-15 08:41 | 2026-08-15 08:42 | 2026-08-15 18:40 | 2026-08-15 18:41 | 2026-08-15 19:30 | 2026-08-15 20:33 | 2026-08-15 21:21 | 2026-08-15 21:21 |  |  | Fair | No | Customer is with out supply 5 days now call was made to call center but communication to meter was unable to reach box number hex 03333 also 03343 these are two different box please refer to field service
Outage | J.E.26.08.21920 | C001889769 | Romaine Roberts | St.Mary | Completed | Load_351347 | Blackstonedge - 110 | 2026-08-15 08:41 | 2026-08-15 08:42 | 2026-08-15 15:20 | 2026-08-15 15:21 | 2026-08-15 16:57 | 2026-08-15 17:24 | 2026-08-15 17:31 | 2026-08-15 17:31 |  |  | Fair | No | Open and close 25 kva transformer to clean and remake jumper and drop lead at transformer point voltage 119-118-237
Outage | J.E.26.08.22216 | C001889771 | Romaine Roberts | St.Mary | Completed | Load_245290 | Blackstonedge - 110 | 2026-08-15 08:41 | 2026-08-15 08:42 | 2026-08-15 17:32 | 2026-08-15 17:33 | 2026-08-15 17:33 | 2026-08-15 17:34 | 2026-08-15 17:35 | 2026-08-15 17:35 |  |  | Fair | No | Power restore earlier
Outage | J.E.26.08.22279 | C001889772 | Neville Spencer | Clarendon | Completed | Load_256703 | May Pen - 110 | 2026-08-15 08:47 | 2026-08-16 15:43 | 2026-08-16 17:58 | 2026-08-16 17:59 | 2026-08-16 18:23 | 2026-08-16 18:23 | 2026-08-16 18:25 | 2026-08-16 18:25 |  |  | Fair | No | Found supply at location voltage reading 116
Outage | J.E.26.08.22305 | C001889776 | Horace Malcolm | St.James | Completed | Load_252260 | Queens Drive - 810 | 2026-08-15 09:11 | 2026-08-15 09:15 | 2026-08-15 10:13 | 2026-08-15 10:14 | 2026-08-15 10:32 | 2026-08-15 11:22 | 2026-08-15 11:22 | 2026-08-15 11:22 |  |  | Fair | No | Isolate two 30amp junction fuse to reattached primary back in insulator an fuse one 30amp junction fuse
Outage | J.E.26.08.22309 | C001889777 | Raymond Lewis | St.Ann | Completed | Load_261967 | Cardiff Hall - 310 | 2026-08-15 09:18 | 2026-08-15 09:55 | 2026-08-15 10:46 | 2026-08-15 10:47 | 2026-08-15 12:21 | 2026-08-15 12:35 | 2026-08-15 12:35 | 2026-08-15 12:35 |  |  | Fair | No | Remade joint at pole 3 wire service
Outage | J.E.26.08.22317 | C001889778 | Swon Miller | St.James | Completed | Load_268413 | Bogue - 310 | 2026-08-15 09:24 | 2026-08-15 18:28 | 2026-08-15 18:50 | 2026-08-15 20:49 | 2026-08-15 20:48 | 2026-08-20 08:33 | 2026-08-15 20:57 | 2026-08-15 20:57 |  |  | Fair | No | Check and found area okay customer states that power supply was restored voltage found 115/114/230 voltage left 115/114/230
Non-Outage | J.E.26.08.22263 | C001889780 | Stephen Taylor |  | Completed |  |  | 2026-08-15 09:30 | 2026-08-15 09:34 | 2026-08-15 10:14 | 2026-08-15 10:14 | 2026-08-15 13:27 | 2026-08-15 13:28 | 2026-08-15 13:56 | 2026-08-15 13:56 |  |  | Fair | No | Patrol clear line and close up 30ams tripsaver Rdg—237–243–239–418–417–410
Outage | J.E.26.08.22333 | C001889779 | Horace Malcolm | St.James | Completed | Load_263410 | Queens Drive - 710 | 2026-08-15 09:30 | 2026-08-15 09:32 | 2026-08-15 11:24 | 2026-08-15 11:25 | 2026-08-15 12:57 | 2026-08-15 12:59 | 2026-08-15 12:59 | 2026-08-15 12:59 | LeakingTransformer |  | Fair | No | Check and found one 50kva transformer leaking area is with supply
Non-Outage | J.E.26.08.22260 | C001889782 | Horace Malcolm |  | Completed |  |  | 2026-08-15 09:32 | 2026-08-15 09:33 | 2026-08-15 13:00 | 2026-08-15 13:01 | 2026-08-15 13:28 | 2026-08-15 13:55 | 2026-08-15 13:55 | 2026-08-15 13:55 |  |  | Fair | No | Check and found customer was disconnected got back customer reconnected
Outage | J.E.26.08.22302 | C001889786 | Milton Charlton | KSAN | Completed | Load_258776 | Hope - 510 | 2026-08-15 09:38 | 2026-08-15 09:41 | 2026-08-15 14:28 | 2026-08-15 14:29 | 2026-08-15 14:40 | 2026-08-15 14:25 | 2026-08-15 14:57 | 2026-08-15 14:57 |  |  | Fair | No | Open out going isolators at pole#0119051 and D.A. Switch # LCB6-281 and install main short and groundatpole#0119051 and Auxillary short ground at pole #041370 and repair burnt off primary jumper at pole #041370. Remove main short ground and auxiliary short and ground and at2:10cancelled permit to work at 2.2.05 pm and reclosed out going isolators and DA switch # LCB 6-281.
Outage | J.E.26.08.22315 | C001889784 | Christopher Edwards | KSAN | Completed | Load_266203 | Constant Spring - 410 | 2026-08-15 09:38 | 2026-08-15 09:43 | 2026-08-15 11:26 | 2026-08-15 11:27 | 2026-08-15 12:33 | 2026-08-15 13:29 | 2026-08-15 13:29 | 2026-08-15 13:29 | Fire | Y | Fair | No | Separate open secondary neutral that was twisted together with open secondary phaseCut bamboo that cause wire to bang
Outage | J.E.26.08.22304 | C001889787 | Oshane Warren | Westmoreland | Completed | Load_570031 | Paradise - 310 | 2026-08-15 09:42 | 2026-08-15 09:43 | 2026-08-15 11:47 | 2026-08-15 11:47 | 2026-08-15 12:20 | 2026-08-15 12:25 | 2026-08-15 12:27 | 2026-08-15 12:27 |  |  | Fair | No | Replace 15 amp junction fuse
Outage | J.E.26.08.22311 | C001889789 | Donald Cunningham | St.Catherine | Completed | Load_244563 | Tredegar - 410 | 2026-08-15 09:46 | 2026-08-15 09:48 | 2026-08-15 10:07 | 2026-08-15 10:08 | 2026-08-15 10:45 | 2026-08-15 10:58 | 2026-08-15 11:01 | 2026-08-15 11:01 |  |  | Fair | No | Rami system box need to check customer operate a restaurant urgent assistance needed
Outage | J.E.26.08.22337 | C001889788 | Hartley Chin | Clarendon | Completed | Load_258492 | May Pen - 110 | 2026-08-15 09:46 | 2026-08-15 09:47 | 2026-08-15 10:19 | 2026-08-15 10:19 | 2026-08-15 11:46 | 2026-08-15 14:27 | 2026-08-15 14:27 | 2026-08-15 14:27 | BrokenWire |  | Fair | No | Found 25 KVA transformer broken phase and neutral cross country . Repaired broken wire .
Non-Outage | J.E.26.08.22271 | C001889790 | Antony Levy | KSAN | Completed | Load_252805 | Hope - 310 | 2026-08-15 09:52 | 2026-08-15 15:00 | 2026-08-15 17:55 | 2026-08-15 17:55 | 2026-08-15 18:08 | 2026-08-15 18:37 | 2026-08-15 18:37 | 2026-08-15 18:37 |  |  | Fair | No | Premises closed.
Non-Outage | J.E.26.08.21889 | C001889791 | Barnett Brown | Manchester | Completed | Load_240485 | Spur Tree - 310 | 2026-08-15 09:55 | 2026-08-15 09:57 | 2026-08-15 14:29 | 2026-08-15 14:30 | 2026-08-15 15:59 | 2026-08-15 16:19 | 2026-08-15 16:21 | 2026-08-15 16:21 |  |  | Fair | No | Balance one span secondary line
Non-Outage | J.E.26.08.21445 | C001889793 | Barnett Brown | Manchester | Completed | Load_238080 | Spur Tree - 310 | 2026-08-15 09:56 | 2026-08-15 09:57 | 2026-08-15 12:46 | 2026-08-15 12:46 | 2026-08-15 12:53 | 2026-08-15 14:19 | 2026-08-15 14:29 | 2026-08-15 14:29 |  |  | Fair | No | Balance one span secondary line, bushing requires
Non-Outage | J.E.26.08.22297 | C001889795 | Kenroy Dale | Manchester | Completed | Load_250031 | Kendal - 210 | 2026-08-15 09:57 | 2026-08-15 09:59 | 2026-08-15 19:10 | 2026-08-15 19:11 | 2026-08-15 20:36 | 2026-08-15 21:12 | 2026-08-15 21:21 | 2026-08-15 21:21 | BangingWires |  | Fair | No | Abandoned service wire found touching secondary phase and causing fire whenever there is a wind, service wire was removed and area now safe
Non-Outage | J.E.26.08.22355 | C001889796 | Kenroy Dale | Manchester | Completed | Load_244824 | Kendal - 210 | 2026-08-15 09:57 | 2026-08-15 09:59 | 2026-08-15 14:07 | 2026-08-15 14:08 | 2026-08-15 15:09 | 2026-08-15 16:36 | 2026-08-15 16:43 | 2026-08-15 16:43 |  |  | Fair | No | Open 25 kva transformer to remade corroded drop lead, 3 one bolt clamp used voltage reading 116/116/232
Outage | J.E.26.08.22388 | C001889797 | Floyd Taylor | Trelawny | Completed | Load_267431 | Duncans - 210 | 2026-08-15 10:07 | 2026-08-15 10:11 | 2026-08-15 11:44 | 2026-08-15 11:44 | 2026-08-15 12:55 | 2026-08-15 16:06 | 2026-08-15 16:06 | 2026-08-15 16:06 |  |  | Fair | No | Remove Illegal connection from line and reset 25kva transformer, voltage reading 113,112, 226
Outage | J.E.26.08.22370 | C001889799 | Wan Carlos Scarlett | Portmore | Completed | Load_268300 | Naggo Head - 610 | 2026-08-15 10:19 | 2026-08-15 10:24 | 2026-08-15 10:30 | 2026-08-15 10:30 | 2026-08-15 11:13 | 2026-08-15 01:00 | 2026-08-15 11:30 | 2026-08-15 11:30 |  |  | Fair | No | Customer confirm that power supply has been restored
Non-Outage | J.E.26.08.22368 | C001889802 | Edward Royal |  | Completed |  |  | 2026-08-15 10:31 | 2026-08-15 10:34 | 2026-08-15 13:32 | 2026-08-15 13:32 | 2026-08-15 13:32 | 2026-08-15 15:49 | 2026-08-15 15:50 | 2026-08-15 15:50 | BrokenWire |  | Fair | No | Spliced and reconnected secondary phase and neutral using 60ft number 2tripe x cable and 6 single bolt clamp spliced and reconnected drop lead to secondary line
Outage | J.E.26.08.22387 | C001889803 | Antony Levy | KSAN | Completed | Load_257166 | Hope - 510 | 2026-08-15 10:32 | 2026-08-15 15:00 | 2026-08-15 22:26 | 2026-08-15 22:27 | 2026-08-15 22:39 | 2026-08-15 22:39 | 2026-08-15 22:42 | 2026-08-15 22:42 |  |  | Fair | No | Unable to reach customer,premises not found...
Non-Outage | J.E.26.08.22485 | C001889806 | Eric Williams |  | Completed |  |  | 2026-08-15 11:12 | 2026-08-15 11:12 | 2026-08-15 11:17 | 2026-08-15 11:18 | 2026-08-15 11:34 | 2026-08-15 11:35 | 2026-08-15 11:36 | 2026-08-15 11:36 |  |  | Fair | No | Work completed and team pack up and leave the area
Outage | J.E.26.08.22427 | C001889807 | Collin Robinson | Portland | Completed | Load_245297 | Port Antonio - 410 | 2026-08-15 11:14 | 2026-08-15 11:15 | 2026-08-15 12:09 | 2026-08-15 12:10 | 2026-08-15 12:39 | 2026-08-15 12:48 | 2026-08-15 12:48 | 2026-08-15 12:48 | Fire |  | Fair | No | Entangle and retention open secondary conductor and reset 10 KVA transformer
Outage | J.E.26.08.20567 | C001889810 | Omar King | St.Ann | Completed | Load_242953 | Roaring River - 410 | 2026-08-15 11:18 | 2026-08-15 11:22 | 2026-08-15 11:57 | 2026-08-15 11:57 | 2026-08-15 13:14 | 2026-08-15 13:26 | 2026-08-15 13:26 | 2026-08-15 13:26 |  |  | Fair | No | Unable to find customer customer call several times no answer directions not sufficient
Outage | J.E.26.08.22459 | C001889811 | Clyde Brown | Clarendon | Completed | Load_352838 | May Pen - 110 | 2026-08-15 11:22 | 2026-08-15 19:00 | 2026-08-15 19:25 | 2026-08-16 11:21 | 2026-08-16 11:20 | 2026-08-16 11:21 | 2026-08-16 11:22 | 2026-08-16 11:22 |  |  | Fair | No | Found ok,customer said supply was restored this morning
Outage | J.E.26.08.22507 | C001889813 | Collin Robinson | Portland | Completed | Load_262710 | Port Antonio - 410 | 2026-08-15 11:23 | 2026-08-15 11:24 | 2026-08-15 12:52 | 2026-08-15 12:53 | 2026-08-15 13:07 | 2026-08-15 13:20 | 2026-08-15 13:20 | 2026-08-15 13:20 |  |  | Fair | No | Change one corroded one bolt clamp at pothead Voltage reading 115v two wire service
Non-Outage | J.E.26.08.22422 | C001889814 | Romeo Brissett | St.James | Completed | Load_574885 | Rose Hall - 210 | 2026-08-15 11:39 | 2026-08-15 20:07 | 2026-08-16 07:59 | 2026-08-16 08:00 | 2026-08-16 07:59 | 2026-08-15 23:00 | 2026-08-16 08:01 | 2026-08-16 08:01 |  |  | Fair | No | Found three junction fuse isolated, closed three junction fuse.
Outage | J.E.26.08.22530 | C001889816 | Wan Carlos Scarlett | Portmore | Completed | Load_260827 | Naggo Head - 510 | 2026-08-15 11:52 | 2026-08-15 11:54 | 2026-08-15 13:13 | 2026-08-15 13:13 | 2026-08-15 14:03 | 2026-08-15 15:05 | 2026-08-15 15:09 | 2026-08-15 15:09 |  |  | Fair | No | Found one span of open secondary line phase touching on secondary line neutral tension one of open secondary line top phase use 2 one bolt clamps refuse 50KVA transformer with a 5amp fuse no pole # was found
Outage | J.E.26.08.22501 | C001889817 | Hartley Chin | Clarendon | Completed | Load_249122 | Parnassus - 210 | 2026-08-15 11:54 | 2026-08-16 07:33 | 2026-08-16 14:18 | 2026-08-16 14:18 | 2026-08-16 14:23 | 2026-08-16 14:24 | 2026-08-16 14:25 | 2026-08-16 14:25 |  |  | Fair | No | Premisis found ok. customer stated the supply was restored.
Outage | J.E.26.08.22552 | C001889818 | Neville Spencer | Clarendon | Completed | Load_258269 | Parnassus - 310 | 2026-08-15 11:54 | 2026-08-15 11:55 | 2026-08-15 15:39 | 2026-08-15 15:40 | 2026-08-15 15:47 | 2026-08-15 15:47 | 2026-08-15 16:11 | 2026-08-15 16:11 |  |  | Fair | No | Remade broken off phase joint at secondary on 3, wire service used 2 clamps voltage reading 112 117/231 supply restored.
Outage | J.E.26.08.22403 | C001889821 | Marlon Authors | Manchester | Completed | Load_264605 | Spur Tree - 210 | 2026-08-15 12:06 | 2026-08-15 12:09 | 2026-08-15 12:26 | 2026-08-15 12:26 | 2026-08-15 13:49 | 2026-08-15 14:07 | 2026-08-15 14:07 | 2026-08-15 14:07 |  |  | Fair | No | Supply checked and found working ok,rdg 108v,108v and cross phased 217 volts
Outage | J.E.26.08.22561 | C001889823 | Collin Robinson | Portland | Completed | Load_265014 | Port Antonio - 410 | 2026-08-15 12:11 | 2026-08-15 12:16 | 2026-08-15 13:22 | 2026-08-15 13:23 | 2026-08-15 15:08 | 2026-08-15 15:50 | 2026-08-15 15:50 | 2026-08-15 15:50 | BrokenWire |  | Fair | No | Patrol secondary line station and found two pole span of broken open secondary conductors.isolate 25 KVA transformer to splice and retention conductors use six one bolt clamp 15 ft #2 conductor 25 ft of 2/0 conductor
Outage | J.E.26.08.22529 | C001889824 | Omar King | St.Ann | Completed | Load_265554 | Ocho Rios - 310 | 2026-08-15 12:12 | 2026-08-15 12:15 | 2026-08-15 13:28 | 2026-08-15 13:29 | 2026-08-15 14:35 | 2026-08-15 14:35 | 2026-08-15 14:35 | 2026-08-15 14:35 |  |  | Fair | No | Unable to find customer call several times no answer directions not sufficient
Outage | J.E.26.08.22576 | C001889830 | Donald Cunningham | St.Catherine | Completed | Load_259639 | New Michelton - 210 | 2026-08-15 12:27 | 2026-08-15 12:29 | 2026-08-15 17:35 | 2026-08-15 17:36 | 2026-08-15 18:44 | 2026-08-15 18:45 | 2026-08-15 18:46 | 2026-08-15 18:46 |  |  | Fair | No | Premises found ok supply restored
Outage | J.E.26.08.22579 | C001889829 | Donald Cunningham | St.Catherine | Completed | Load_244259 | New Michelton - 210 | 2026-08-15 12:27 | 2026-08-15 12:29 | 2026-08-15 12:53 | 2026-08-15 12:53 | 2026-08-15 15:16 | 2026-08-15 16:00 | 2026-08-15 16:01 | 2026-08-15 16:01 |  |  | Fair | No | Blown junction fuse found and replace with 30 amp fuse
Outage | J.E.26.08.22582 | C001889831 | Donald Cunningham | St.Catherine | Completed | Load_240393 | New Michelton - 210 | 2026-08-15 12:27 | 2026-08-15 12:29 | 2026-08-15 16:01 | 2026-08-15 16:02 | 2026-08-15 16:13 | 2026-08-15 16:21 | 2026-08-15 16:22 | 2026-08-15 16:22 |  |  | Fair | No | Supply restored
Outage | J.E.26.08.22585 | C001889833 | Javid Vernon | Westmoreland | Completed | Load_247022 | Paradise - 210 | 2026-08-15 12:32 | 2026-08-15 12:34 | 2026-08-15 12:55 | 2026-08-15 12:55 | 2026-08-15 13:55 | 2026-08-15 14:22 | 2026-08-15 14:22 | 2026-08-15 14:22 |  |  | Fair | No | Clear banging wires and refuse one 25kva transformer use 3amp fuse
Outage | J.E.26.08.22518 | C001889843 | Antony Levy | KSAN | Completed | Load_249646 | Hope - 310 | 2026-08-15 13:09 | 2026-08-15 18:23 | 2026-08-15 19:17 | 2026-08-15 19:18 | 2026-08-15 19:47 | 2026-08-15 21:20 | 2026-08-15 21:29 | 2026-08-15 21:29 | Fire |  | Fair | No | Cx stated fire on wire on house top.... service wire seen to be burned and defective.... service wire cut and spliced using # 6 thripplex ... and re anchored to pot head ....power restored
Outage | J.E.26.08.22577 | C001889845 | Collin Robinson | Portland | Completed | Load_352776 | Port Antonio - 410 | 2026-08-15 13:09 | 2026-08-15 13:11 | 2026-08-15 16:55 | 2026-08-15 16:55 | 2026-08-15 17:55 | 2026-08-15 19:24 | 2026-08-15 19:30 | 2026-08-15 19:30 |  |  | Fair | No | De - bush one pole span of open secondary conductor splice and retention broken neutral conductor and replace 8 amps fuse
Outage | J.E.26.08.22584 | C001889844 | Milton Charlton | KSAN | Completed | Load_266398 | Hope - 510 | 2026-08-15 13:09 | 2026-08-15 13:12 | 2026-08-15 15:57 | 2026-08-15 15:57 | 2026-08-15 17:06 | 2026-08-15 16:50 | 2026-08-15 17:09 | 2026-08-15 17:09 |  |  | Fair | No | Refused and reclosed 30amps junction at pole #098123 using one 30 amps fuse.
Outage | J.E.26.08.22550 | C001889847 | Romaine Roberts | St.Mary | Completed | Load_247324 | Blackstonedge - 110 | 2026-08-15 13:15 | 2026-08-15 13:18 | 2026-08-15 13:52 | 2026-08-15 13:53 | 2026-08-15 15:09 | 2026-08-15 15:19 | 2026-08-15 15:20 | 2026-08-15 15:20 |  | Y | Fair | No | 25 kva transformer found trip patrol line and found bamboo that causing line to bang clear bamboo from line and reset transformer power restore
Outage | J.E.26.08.22607 | C001889848 | Derrick Dawkins | St.James | Completed | Load_254478 | Bogue - 610 | 2026-08-15 13:29 | 2026-08-15 13:30 | 2026-08-15 13:39 | 2026-08-15 15:00 | 2026-08-15 15:28 | 2026-08-15 16:14 | 2026-08-15 16:15 | 2026-08-15 16:15 |  |  | Fair | No | Found junction fuse blown due to vegetation 15 amp replace 15 amp junction fuse
Outage | J.E.26.08.22600 | C001889854 | Kenroy Dale | Manchester | Completed | Load_248339 | Kendal - 210 | 2026-08-15 13:47 | 2026-08-15 13:48 | 2026-08-15 16:43 | 2026-08-15 16:44 | 2026-08-15 18:19 | 2026-08-15 19:09 | 2026-08-15 19:10 | 2026-08-15 19:10 |  |  | Fair | No | Corroded neutral junction found remade connection using 2 one bolt clamp voltage reading 116/116/232
Outage | J.E.26.08.22673 | C001889855 | Tajay Bernard | Hanover | Completed | Load_259699 | Orange Bay - 310 | 2026-08-15 13:56 | 2026-08-15 13:57 | 2026-08-15 14:04 | 2026-08-15 14:05 | 2026-08-15 15:32 | 2026-08-15 15:48 | 2026-08-15 15:49 | 2026-08-15 15:49 |  |  | Fair | No | Reset 1 25kva transformer
Outage | J.E.26.08.22623 | C001889857 | Clyde Brown | Clarendon | Completed | Load_254884 | May Pen - 110 | 2026-08-15 13:57 | 2026-08-15 19:00 | 2026-08-15 19:25 | 2026-08-16 11:23 | 2026-08-16 12:57 | 2026-08-16 13:04 | 2026-08-16 13:08 | 2026-08-16 13:08 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Find ok customer made mistakes in making report.
Outage | J.E.26.08.22677 | C001889856 | Clyde Brown | Clarendon | Completed | Load_256703 | May Pen - 110 | 2026-08-15 13:57 | 2026-08-15 19:00 | 2026-08-15 19:25 | 2026-08-16 11:17 | 2026-08-16 11:16 | 2026-08-16 11:15 | 2026-08-16 11:18 | 2026-08-16 11:18 |  |  | Fair | No | Found ok
Outage | J.E.26.08.22599 | C001889860 | Antony Levy | KSAN | Completed | Load_557445 | West Kings House - 310 | 2026-08-15 14:01 | 2026-08-15 15:00 | 2026-08-15 17:54 | 2026-08-15 18:51 | 2026-08-15 18:51 | 2026-08-15 18:51 | 2026-08-15 19:17 | 2026-08-15 19:17 | Fire |  | Fair | No | Cx stated no power .... blown 25 kva transformer fuse found ... secondary patrolled and line refused using 3 amp fuse... power restored
Outage | J.E.26.08.22636 | C001889861 | Collin Robinson | Portland | Completed | Load_261580 | Port Antonio - 410 | 2026-08-15 14:06 | 2026-08-15 14:09 | 2026-08-15 15:51 | 2026-08-15 15:51 | 2026-08-15 16:26 | 2026-08-15 16:54 | 2026-08-15 16:54 | 2026-08-15 16:54 | BrokenWire |  | Fair | No | Patrol secondary line section and found one phase of broken secondary conductor. isolate 25 KVA transformer to Splice and retention 1 phase of broken open secondary conductor
Outage | J.E.26.08.22687 | C001889863 | Clyde Brown | St.Ann | Completed | Load_260792 | Cardiff Hall - 310 | 2026-08-15 14:10 | 2026-08-15 15:28 | 2026-08-15 18:04 | 2026-08-15 18:05 | 2026-08-15 18:04 | 2026-08-15 17:51 | 2026-08-15 18:08 | 2026-08-15 18:08 |  |  | SevereWind | No | 2-30amps Tripsaver tripped at Cave Valley ,line patrolled and no fault seen,heavy winds in area and tripsaver reset.
Outage | J.E.26.08.22689 | C001889865 | Clyde Brown | St.Ann | Completed | Load_248569 | Cardiff Hall - 310 | 2026-08-15 14:10 | 2026-08-15 15:29 | 2026-08-15 15:51 | 2026-08-15 15:52 | 2026-08-15 17:07 | 2026-08-15 17:51 | 2026-08-15 18:00 | 2026-08-15 18:00 |  |  | SevereWind | No | 2-30amps tripsaver tripped at Cave Valley line patrolled and heavy winds in area,tripsaver reset.
Outage | J.E.26.08.22720 | C001889869 | Raheem Ricketts | St.Elizabeth | Completed | Load_261883 | Maggotty - 210 | 2026-08-15 14:13 | 2026-08-15 14:14 | 2026-08-15 16:12 | 2026-08-15 16:12 | 2026-08-15 16:22 | 2026-08-15 17:00 | 2026-08-15 17:01 | 2026-08-15 17:01 | Fire |  | Fair | No | Check and found customer service wire burn splice an retention 40ft of service wire using 3clamps 3link
Outage | J.E.26.08.22737 | C001889873 | Richard Nicholas | St.Catherine | Completed | Load_267832 | Twickenham - 410 | 2026-08-15 14:17 | 2026-08-15 14:18 | 2026-08-15 14:33 | 2026-08-15 14:33 | 2026-08-15 15:21 | 2026-08-15 15:21 | 2026-08-15 15:25 | 2026-08-15 15:25 | BrokenPole |  | Fair | No | Leaning concrete 40ft pole seen.pole is not using and already stripped of all equipment.pole is leaning towards the main road and is posing danger to motor vehicle and pedestrian.follow up to remove same required.
Outage | J.E.26.08.21506 | C001889879 | Horace Malcolm | St.James | Completed | Load_301730 | Bogue - 310 | 2026-08-15 14:37 | 2026-08-16 08:07 | 2026-08-16 12:04 | 2026-08-16 12:04 | 2026-08-16 13:45 | 2026-08-16 13:54 | 2026-08-16 13:54 | 2026-08-16 13:54 |  |  | Fair | No | Customer having no supply from rami box referred to field service
Outage | J.E.26.08.22402 | C001889880 | Swon Miller | St.James | Completed | Load_237918 | Bogue - 310 | 2026-08-15 14:37 | 2026-08-15 14:38 | 2026-08-15 14:48 | 2026-08-15 15:04 | 2026-08-15 16:05 | 2026-08-03 16:44 | 2026-08-15 16:44 | 2026-08-15 16:44 |  |  | Fair | No | Found 8 amp junction fuse blown cause by tree limbs cut and remove tree limbs from primary conductor and replace 8 amp junction fuse no pole number available
Outage | J.E.26.08.22741 | C001889881 | Horace Malcolm | St.James | Completed | Load_241536 | Bogue - 310 | 2026-08-15 14:37 | 2026-08-16 08:07 | 2026-08-16 14:04 | 2026-08-16 14:05 | 2026-08-16 14:18 | 2026-08-16 14:30 | 2026-08-16 14:30 | 2026-08-16 14:30 |  |  | Fair | No | Check an found customer have prepaid service premises closed no occupant check voltage reading 115-113-228
Outage | J.E.26.08.22742 | C001889882 | Swon Miller | St.James | Completed | Load_556782 | Bogue - 310 | 2026-08-15 14:37 | 2026-08-15 14:38 | 2026-08-15 14:48 | 2026-08-15 21:58 | 2026-08-15 22:38 | 2026-08-26 10:55 | 2026-08-15 23:01 | 2026-08-15 23:01 |  |  | Fair | No | Found customer service wire defective need about 200 ft# 6 triplex to carry out repairs isolate customer service wire box number hex 06554
Outage | J.E.26.08.22740 | C001889883 | Stephen Taylor | St.Thomas | Completed | Load_238970 | Lysson - 410 | 2026-08-15 14:42 | 2026-08-15 14:43 | 2026-08-15 15:57 | 2026-08-15 15:57 | 2026-08-15 15:57 | 2026-08-15 15:57 | 2026-08-15 16:11 | 2026-08-15 16:11 |  |  | Fair | No | Patrol clear line and close up junction with 10ams fuse
Outage | J.E.26.08.22776 | C001889886 | Tajay Bernard | Hanover | Completed | Load_230038 | Orange Bay - 310 | 2026-08-15 15:03 | 2026-08-15 15:04 | 2026-08-15 15:50 | 2026-08-15 15:51 | 2026-08-15 15:50 | 2026-08-15 15:51 | 2026-08-15 15:51 | 2026-08-15 15:51 |  |  | Fair | No | Customer stated that power was restored
Outage | J.E.26.08.22709 | C001889887 | Wayne Dillion | St.Elizabeth | Completed | Load_256959 | Maggotty - 210 | 2026-08-15 15:08 | 2026-08-15 17:17 | 2026-08-15 17:44 | 2026-08-15 17:45 | 2026-08-15 18:09 | 2026-08-15 18:45 | 2026-08-15 18:45 | 2026-08-15 18:45 | BrokenWire |  | Fair | No | Reconnect customer using 60 feet of number six triplex 3 linket 3 one bolt clamp voltage reading 114 v 114v 228 v supply leave working ok
Outage | J.E.26.08.22265 | C001889888 | Elvis Trowers | KSAN | Completed | Load_250570 | Constant Spring - 210 | 2026-08-15 15:10 | 2026-08-15 15:13 | 2026-08-15 16:16 | 2026-08-15 16:19 | 2026-08-15 17:02 | 2026-08-15 17:25 | 2026-08-15 17:31 | 2026-08-15 17:31 |  |  | Fair | No | Found one 25 amps junction fuse blown at pole # 01162 and one 3 amps transformer fuse blown at pole#( no pole #). Refused using one 25 amps fuse and one 3 amps fuse and reclosed junction and transformer switches.
Outage | J.E.26.08.22671 | C001889893 | Milton Charlton | KSAN | Completed | Load_578893 | Hope - 510 | 2026-08-15 15:14 | 2026-08-15 15:15 | 2026-08-15 20:23 | 2026-08-15 20:23 | 2026-08-15 21:41 | 2026-08-15 21:20 | 2026-08-15 21:46 | 2026-08-15 21:46 |  |  | Fair | No | Customer meter disconnected and escalation is unable to connect meter.Refer to field service.
Non-Outage | J.E.26.08.21563 | C001889894 | Milton Charlton | KSAN | Completed | Load_258625 | Hope - 510 | 2026-08-15 15:16 | 2026-08-15 15:16 | 2026-08-15 18:02 | 2026-08-15 18:03 | 2026-08-15 20:21 | 2026-08-15 20:20 | 2026-08-15 20:23 | 2026-08-15 20:23 |  |  | Fair | No | Found okay upon arrival. Customer has an internal problem.
Outage | J.E.26.08.22806 | C001889895 | Antony Levy | KSAN | Completed | Load_575611 | Washington Blvd - 610 | 2026-08-15 15:21 | 2026-08-15 15:22 | 2026-08-15 17:01 | 2026-08-15 17:27 | 2026-08-15 17:26 | 2026-08-15 17:54 | 2026-08-15 17:54 | 2026-08-15 17:54 | LowHangingWires |  | Fair | No | Not jps wire
Outage | J.E.26.08.22634 | C001889898 | Richman Whyte | St.Elizabeth | Completed | Load_240484 | Maggotty - 110 | 2026-08-15 15:27 | 2026-08-15 15:33 | 2026-08-15 16:03 | 2026-08-15 16:03 | 2026-08-15 16:03 | 2026-08-15 16:03 | 2026-08-15 16:04 | 2026-08-15 16:04 |  |  | Fair | No | Customer is complaining about getting a bill without having a meter or any connection from hurricane
Non-Outage | J.E.26.08.22555 | C001889899 | Raheem Ricketts | Manchester | Completed | Load_268421 | Spur Tree - 210 | 2026-08-15 15:35 | 2026-08-15 15:37 | 2026-08-15 17:22 | 2026-08-15 17:23 | 2026-08-15 17:51 | 2026-08-15 17:52 | 2026-08-15 17:52 | 2026-08-15 17:52 | BrokenWire |  | Fair | No | Retention customer service wire and remake joint at pole using two clamps
Non-Outage | J.E.26.08.22627 | C001889900 | Barnett Brown | Manchester | Completed | Load_249466 | Spur Tree - 310 | 2026-08-15 15:37 | 2026-08-15 15:49 | 2026-08-15 16:30 | 2026-08-15 16:31 | 2026-08-15 17:44 | 2026-08-15 19:02 | 2026-08-15 19:11 | 2026-08-15 19:11 |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.08.22831 | C001889902 | Rusean Allen |  | Completed |  |  | 2026-08-15 15:39 | 2026-08-15 15:40 | 2026-08-15 15:50 | 2026-08-15 15:51 | 2026-08-15 18:27 | 2026-08-15 19:11 | 2026-08-15 19:11 | 2026-08-15 19:11 |  |  | Fair | No | Broken drop lead wire found at transformer pole, wire was reconnected
Outage | J.E.26.08.22823 | C001889903 | Romeo Brissett | St.James | Completed | Load_574634 | Bogue - 310 | 2026-08-15 15:40 | 2026-08-15 15:44 | 2026-08-15 18:18 | 2026-08-15 18:19 | 2026-08-15 18:18 | 2026-08-16 19:23 | 2026-08-16 07:47 | 2026-08-16 07:47 |  |  | Fair | No | Found (1)100kva transformer defective, there’s was an closed delta and circuit was rewired to closed delta with (1)100, and (1)50kva transformer.
Non-Outage | J.E.26.08.22224 | C001889908 | Swon Miller | St.James | Completed | Load_244750 | Queens Drive - 310 | 2026-08-15 15:41 | 2026-08-16 15:23 | 2026-08-16 15:30 | 2026-08-16 15:31 | 2026-08-16 15:46 | 2026-08-25 04:46 | 2026-08-16 17:00 | 2026-08-16 17:00 |  |  | Fair | No | Check and found customer single phasing cause by contamination at pole clean and remake joints use 2 pg voltage found 115 voltage left 116/115/232
Outage | J.E.26.08.22739 | C001889912 | Andre Smith | KSAS | Completed | Load_579116 | Greenwich - 510 | 2026-08-15 15:45 | 2026-08-15 15:47 | 2026-08-15 16:41 | 2026-08-15 16:42 | 2026-08-15 17:29 | 2026-08-15 17:30 | 2026-08-15 17:31 | 2026-08-15 17:31 |  |  | Fair | No | Reconnection done supply restored
Non-Outage | J.E.26.07.07549 | C001889921 | Omar King | St.Ann | Completed | Load_246075 | Roaring River - 410 | 2026-08-15 15:46 | 2026-08-15 15:47 | 2026-08-15 16:11 | 2026-08-15 16:12 | 2026-08-15 16:29 | 2026-08-15 16:30 | 2026-08-15 16:30 | 2026-08-15 16:30 |  |  | Fair | No | Problem as been resolved
Non-Outage | J.E.26.07.10870 | C001889919 | Omar King | St.Ann | Completed | Load_237638 | Roaring River - 410 | 2026-08-15 15:46 | 2026-08-15 15:47 | 2026-08-15 17:16 | 2026-08-15 17:17 | 2026-08-15 17:45 | 2026-08-15 17:46 | 2026-08-15 17:46 | 2026-08-15 17:46 |  |  | Fair | No | Problem as been resolved
Non-Outage | J.E.26.07.11800 | C001889918 | Omar King | St.Ann | Completed | Load_237638 | Roaring River - 410 | 2026-08-15 15:46 | 2026-08-15 15:47 | 2026-08-15 16:30 | 2026-08-15 16:31 | 2026-08-15 17:14 | 2026-08-15 17:16 | 2026-08-15 17:16 | 2026-08-15 17:16 |  |  | Fair | No | Problem as been resolved
Non-Outage | J.E.26.07.37278 | C001889915 | Omar King | St.Ann | Completed | Load_237638 | Cardiff Hall - 210 | 2026-08-15 15:46 | 2026-08-15 15:47 | 2026-08-15 19:46 | 2026-08-15 19:46 | 2026-08-15 20:34 | 2026-08-15 20:34 | 2026-08-15 20:34 | 2026-08-15 20:34 |  |  | Fair | No | Problem as been resolved
Outage | J.E.26.08.22780 | C001889924 | Clyde Brown | Clarendon | Completed | Load_1003304 | May Pen - 110 | 2026-08-15 15:53 | 2026-08-15 15:55 | 2026-08-15 19:25 | 2026-08-15 19:26 | 2026-08-15 19:25 | 2026-08-15 22:37 | 2026-08-15 22:45 | 2026-08-15 22:45 |  | Y | SevereWind | No | 25 kva transformer tripped caused by tree contact,line cleared and transformer reset.
Non-Outage | J.E.26.08.20313 | C001889934 | Roxroy Needham | St.Ann | Completed | Load_240260 | Cardiff Hall - 210 | 2026-08-15 15:54 | 2026-08-15 15:55 | 2026-08-15 16:16 | 2026-08-15 17:49 | 2026-08-15 17:50 | 2026-08-15 17:50 | 2026-08-15 17:52 | 2026-08-15 17:52 |  |  | Fair | No | Premises found ok call customer and customer say that the light is ok
Non-Outage | J.E.26.08.20318 | C001889932 | Roxroy Needham | St.Ann | Completed | Load_240260 | Cardiff Hall - 210 | 2026-08-15 15:54 | 2026-08-15 15:55 | 2026-08-15 16:16 | 2026-08-15 17:53 | 2026-08-15 17:53 | 2026-08-15 18:08 | 2026-08-15 18:09 | 2026-08-15 18:09 |  |  | Fair | No | Premises found ok call customer and customer say that the light is ok
Non-Outage | J.E.26.08.20321 | C001889931 | Roxroy Needham | St.Ann | Completed | Load_240260 | Cardiff Hall - 210 | 2026-08-15 15:54 | 2026-08-15 15:55 | 2026-08-15 16:16 | 2026-08-15 16:17 | 2026-08-15 16:50 | 2026-08-15 17:46 | 2026-08-15 17:47 | 2026-08-15 17:47 |  | Y | Fair | No | Open a 50 KVA transformer at pole to repair jumper used 2 pg clamp
Non-Outage | J.E.26.08.20370 | C001889930 | Roxroy Needham | St.Ann | Completed | Load_240260 | Cardiff Hall - 210 | 2026-08-15 15:54 | 2026-08-15 15:55 | 2026-08-15 16:16 | 2026-08-15 17:48 | 2026-08-15 17:47 | 2026-08-15 17:47 | 2026-08-15 17:49 | 2026-08-15 17:49 |  |  | Fair | No | Premises found ok call customer and customer say that the light is ok
Non-Outage | J.E.26.08.21704 | C001889928 | Roxroy Needham | St.Ann | Completed | Load_1003802 | Cardiff Hall - 210 | 2026-08-15 15:54 | 2026-08-15 15:55 | 2026-08-15 18:09 | 2026-08-15 18:10 | 2026-08-15 18:38 | 2026-08-15 18:49 | 2026-08-15 18:58 | 2026-08-15 18:58 |  |  | Fair | No | Premises not found security say that no report has make at gate
Non-Outage | J.E.26.08.21728 | C001889927 | Roxroy Needham | St.Ann | Completed | Load_1007113 | Cardiff Hall - 210 | 2026-08-15 15:54 | 2026-08-15 15:55 | 2026-08-15 18:59 | 2026-08-15 19:00 | 2026-08-15 21:06 | 2026-08-15 20:48 | 2026-08-15 21:07 | 2026-08-15 21:07 |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.08.22608 | C001889935 | Donald Cunningham | St.Catherine | Completed | Load_257901 | New Michelton - 310 | 2026-08-15 15:58 | 2026-08-15 16:04 | 2026-08-15 16:22 | 2026-08-15 16:23 | 2026-08-15 16:45 | 2026-08-15 16:45 | 2026-08-15 16:46 | 2026-08-15 16:46 |  |  | Fair | No | Supply restored
Outage | J.E.26.08.22683 | C001889936 | Donald Cunningham | St.Catherine | Completed | Load_266216 | New Michelton - 210 | 2026-08-15 15:58 | 2026-08-15 16:04 | 2026-08-15 16:46 | 2026-08-15 16:47 | 2026-08-15 17:25 | 2026-08-15 17:35 | 2026-08-15 17:35 | 2026-08-15 17:35 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.22471 | C001889944 | Floyd Taylor | Trelawny | Completed | Load_255673 | Greenwood - 210 | 2026-08-15 16:08 | 2026-08-15 16:10 | 2026-08-15 20:10 | 2026-08-15 20:10 | 2026-08-15 20:57 | 2026-08-15 21:05 | 2026-08-15 21:39 | 2026-08-15 21:39 | BrokenWire |  | Fair | No | Replace 100ft of number 6 using 3 penunion and 3pg clamps, voltage reading 114,115,230
Outage | J.E.26.08.22492 | C001889943 | Andre Williams | Trelawny | Completed | Load_256354 | Duncans - 210 | 2026-08-15 16:08 | 2026-08-16 07:07 | 2026-08-16 07:19 | 2026-08-16 07:21 | 2026-08-16 07:21 | 2026-08-16 07:22 | 2026-08-16 07:22 | 2026-08-16 07:22 |  |  | Fair | No | Premises ok and with supply , confirm by call
Outage | J.E.26.08.22542 | C001889942 | Marlon Brown | Trelawny | Completed | Load_257082 | Duncans - 110 | 2026-08-15 16:08 | 2026-08-16 15:05 | 2026-08-16 16:41 | 2026-08-16 16:42 | 2026-08-16 16:41 | 2026-08-16 16:42 | 2026-08-16 16:42 | 2026-08-16 16:42 |  |  | Fair | No | Unable to locate customer via telephone nor direction
Outage | J.E.26.08.22783 | C001889941 | Andre Williams | Trelawny | Completed | Load_294473 | Duncans - 110 | 2026-08-15 16:08 | 2026-08-16 07:07 | 2026-08-16 08:40 | 2026-08-16 08:40 | 2026-08-16 09:13 | 2026-08-16 09:14 | 2026-08-16 09:14 | 2026-08-16 09:14 |  |  | Fair | No | Premises not found need more precise directions to locate customer
Non-Outage | J.E.26.08.21668 | C001889945 | Andre Smith | KSAS | Completed | Load_257291 | Rockfort - 210 | 2026-08-15 16:11 | 2026-08-15 16:14 | 2026-08-15 17:31 | 2026-08-15 17:31 | 2026-08-15 17:55 | 2026-08-15 19:22 | 2026-08-15 19:22 | 2026-08-15 19:22 |  |  | Fair | No | Repair burnt #2triplex using 12ft conductor 4onebolt clamps cause by illegal connections supply restored 116//114/230
Outage | J.E.26.08.22868 | C001889946 | Roxroy Needham | St.Ann | Completed | Load_238147 | Cardiff Hall - 310 | 2026-08-15 16:15 | 2026-08-15 16:15 | 2026-08-15 21:07 | 2026-08-15 21:08 | 2026-08-15 22:23 | 2026-08-15 22:23 | 2026-08-15 22:25 | 2026-08-15 22:25 |  |  | Fair | No | Remake joint at pole used 2 pg clamp
Outage | J.E.26.08.22867 | C001889947 | Wayne Dillion | St.Elizabeth | Completed | Load_247900 | Maggotty - 110 | 2026-08-15 16:17 | 2026-08-15 16:19 | 2026-08-15 16:31 | 2026-08-15 16:31 | 2026-08-15 16:31 | 2026-08-15 16:32 | 2026-08-15 16:32 | 2026-08-15 16:32 |  |  | Fair | No | Premises not found and customer phone not working
Non-Outage | J.E.26.08.22727 | C001889953 | Clyde Brown |  | Completed |  |  | 2026-08-15 16:44 | 2026-08-15 16:45 | 2026-08-15 18:00 | 2026-08-15 18:01 | 2026-08-15 18:00 | 2026-08-15 17:51 | 2026-08-15 18:03 | 2026-08-15 18:03 |  |  | SevereWind | No | 2-30amps Tripsaver tripped at Cave Valley,line patrolled and only heavy winds in area,tripsaver reset.
Non-Outage | J.E.26.08.22834 | C001889954 | Clyde Brown |  | Completed |  |  | 2026-08-15 16:44 | 2026-08-15 16:45 | 2026-08-15 19:25 | 2026-08-15 22:52 | 2026-08-16 09:05 | 2026-08-16 09:19 | 2026-08-16 09:29 | 2026-08-16 09:29 |  | Y | Fair | No | 25kva transformer tripped caused by heavy bushing in girls home bushing done and transformer reset.secondary line in girls home need heavy bushing vegetation crew to be notified.
Outage | J.E.26.08.22879 | C001889952 | Clyde Brown | Clarendon | Completed | Load_256703 | May Pen - 110 | 2026-08-15 16:44 | 2026-08-15 16:45 | 2026-08-15 19:25 | 2026-08-15 22:48 | 2026-08-15 22:48 | 2026-08-15 22:37 | 2026-08-15 22:50 | 2026-08-15 22:50 |  | Y | SevereWind | No | 25 kva transformer tripped caused by tree contact,line patrolled and tree contact seen on line ,line cleared and transformer reset
Outage | J.E.26.08.22570 | C001889955 | Clyde Brown | Clarendon | Completed | Load_258492 | May Pen - 110 | 2026-08-15 16:45 | 2026-08-16 07:41 | 2026-08-16 13:26 | 2026-08-16 13:27 | 2026-08-16 14:23 | 2026-08-16 14:22 | 2026-08-16 14:25 | 2026-08-16 14:25 |  |  | Fair | No | Customer said they are at church so we have to come back
Outage | J.E.26.08.22749 | C001889957 | Nickolas Rodriques | KSAS | Completed | Load_254412 | Duhaney - 210 | 2026-08-15 16:45 | 2026-08-16 11:02 | 2026-08-16 13:02 | 2026-08-16 13:05 | 2026-08-16 13:35 | 2026-08-16 14:21 | 2026-08-16 14:36 | 2026-08-16 14:36 |  |  | Fair | No | Checked and found a 10 KVA transformer tripped. Patrol and found nothing on line. The transformer was reset after completing patrol.
Non-Outage | J.E.26.08.15827 | C001889960 | Richard Samuda |  | Completed |  |  | 2026-08-15 16:49 | 2026-08-16 07:23 | 2026-08-16 16:14 | 2026-08-16 16:15 | 2026-08-16 16:49 | 2026-08-16 04:49 | 2026-08-16 16:50 | 2026-08-16 16:50 |  |  | Fair | No | Found ok customer said power was restored
Non-Outage | J.E.26.08.22872 | C001889961 | Tajay Bernard |  | Completed |  |  | 2026-08-15 16:51 | 2026-08-15 16:52 | 2026-08-15 17:07 | 2026-08-15 19:26 | 2026-08-15 19:26 | 2026-08-15 19:27 | 2026-08-15 19:27 | 2026-08-15 19:27 | BrokenWire |  | Fair | No | Related to previous call job number 22883
Outage | J.E.26.08.22883 | C001889962 | Tajay Bernard | Hanover | Completed | Load_262344 | Orange Bay - 310 | 2026-08-15 16:51 | 2026-08-15 16:52 | 2026-08-15 17:10 | 2026-08-15 17:11 | 2026-08-15 17:40 | 2026-08-15 19:23 | 2026-08-15 19:25 | 2026-08-15 19:25 |  |  | Fair | No | Isolate 1 50kva Transformer to splice and retention 2 pole span of secondary phase and neutral, 2 preform was used
Non-Outage | J.E.26.08.20757 | C001889964 | Collin Robinson | Portland | Completed | Load_242858 | Port Antonio - 310 | 2026-08-15 16:53 | 2026-08-15 16:54 | 2026-08-15 21:45 | 2026-08-15 21:47 | 2026-08-15 22:22 | 2026-08-15 22:34 | 2026-08-15 22:34 | 2026-08-15 22:34 |  |  | Rains | No | Unable to locate call customer several times for better direction phone ring with out answer
Non-Outage | J.E.26.08.22804 | C001889965 | Collin Robinson | Portland | Completed | Load_240878 | Port Antonio - 310 | 2026-08-15 16:53 | 2026-08-15 16:54 | 2026-08-15 20:42 | 2026-08-15 20:42 | 2026-08-15 21:37 | 2026-08-15 21:45 | 2026-08-15 21:45 | 2026-08-15 21:45 |  |  | Rains | No | Unable to locate customer
Non-Outage | J.E.26.08.20415 | C001889966 | Stephen Taylor |  | Completed |  |  | 2026-08-15 17:17 | 2026-08-15 17:18 | 2026-08-15 18:34 | 2026-08-15 18:34 | 2026-08-15 18:34 | 2026-08-15 18:34 | 2026-08-15 18:37 | 2026-08-15 18:37 | BrokenPole |  | Fair | No | Jps over head guide pole lean and need to be straightened
Non-Outage | J.E.26.08.22926 | C001889967 | Stephen Taylor | St.Thomas | Completed | Load_270128 | Good Year - 110 | 2026-08-15 17:17 | 2026-08-15 17:18 | 2026-08-15 19:58 | 2026-08-15 19:58 | 2026-08-15 20:39 | 2026-08-15 20:40 | 2026-08-15 20:40 | 2026-08-15 20:40 | Fire |  | Fair | No | Retention service wire customer is now okay
Outage | J.E.26.08.22903 | C001889970 | Stephen Taylor | St.Thomas | Completed | Load_270128 | Good Year - 110 | 2026-08-15 17:22 | 2026-08-15 17:29 | 2026-08-16 14:21 | 2026-08-16 14:22 | 2026-08-16 14:35 | 2026-08-16 14:52 | 2026-08-16 14:58 | 2026-08-16 14:58 | Fire |  | Fair | No | Splice and retention secondary wire 95% of customers have supplied bushings team was advised to do bushings to restore another 5% customer close 25kva with 3ams fuse
Outage | J.E.26.08.22929 | C001889971 | Antony Levy | KSAS | Completed | Load_412909 | Up Park Camp - 410 | 2026-08-15 17:34 | 2026-08-15 17:35 | 2026-08-15 18:37 | 2026-08-15 21:30 | 2026-08-15 21:39 | 2026-08-15 22:17 | 2026-08-15 22:19 | 2026-08-15 22:19 | BrokenWire |  | Fair | No | Broken cable wire fell across rd...customer advised.
Non-Outage | J.E.26.08.22953 | C001889974 | Romeo Brissett | St.James | Completed | Load_253128 | Bogue - 310 | 2026-08-15 17:43 | 2026-08-15 17:44 | 2026-08-16 07:55 | 2026-08-16 07:55 | 2026-08-16 07:55 | 2026-08-15 21:12 | 2026-08-16 07:57 | 2026-08-16 07:57 |  |  | Fair | No | Found no clamp on customer neutral on pole, Used one clamp on pole V/R 105-106-210
Outage | J.E.26.08.22901 | C001889976 | Andre Smith | KSAS | Completed | Load_289627 | Greenwich - 710 | 2026-08-15 17:50 | 2026-08-15 17:51 | 2026-08-15 19:23 | 2026-08-15 19:23 | 2026-08-15 20:25 | 2026-08-15 21:06 | 2026-08-15 21:06 | 2026-08-15 21:06 | BrokenWire |  | Fair | No | Unable to access box daylight attention required
Outage | J.E.26.08.22961 | C001889977 | Elvis Trowers | KSAN | Completed | Load_253684 | Constant Spring - 210 | 2026-08-15 17:50 | 2026-08-15 17:51 | 2026-08-15 17:55 | 2026-08-15 17:55 | 2026-08-15 18:53 | 2026-08-15 18:55 | 2026-08-15 19:14 | 2026-08-15 19:14 |  |  | Fair | No | Found one 20 amps junction fuse blown at pole #0011438 and one 5 amps transformer fuse blown at pole #0011440. Refused using one 20 amps fuse and one 3 amps fuse and reclosed junction and transformer switches.
Outage | J.E.26.08.22962 | C001889978 | Elvis Trowers | KSAN | Completed | Load_257197 | Constant Spring - 210 | 2026-08-15 17:50 | 2026-08-15 17:51 | 2026-08-15 19:18 | 2026-08-15 19:19 | 2026-08-15 19:18 | 2026-08-15 19:20 | 2026-08-15 19:20 | 2026-08-15 19:20 |  |  | Fair | No | Call related to call at #42 blue mountain road.
Outage | J.E.26.08.22959 | C001889979 | Elvis Trowers | KSAN | Completed | Load_252373 | Constant Spring - 210 | 2026-08-15 17:51 | 2026-08-15 17:51 | 2026-08-15 19:14 | 2026-08-15 19:15 | 2026-08-15 19:14 | 2026-08-15 19:16 | 2026-08-15 19:17 | 2026-08-15 19:17 |  |  | Fair | No | Call related to call at #42 blue mountain road .
Outage | J.E.26.08.22920 | C001889980 | Rusean Allen | KSAS | Completed | Load_237917 | Hunts Bay - 410 | 2026-08-15 17:52 | 2026-08-15 17:55 | 2026-08-15 19:12 | 2026-08-15 19:12 | 2026-08-15 20:08 | 2026-08-15 22:33 | 2026-08-15 22:33 | 2026-08-15 22:33 |  |  | Fair | No | Found a 30 amps fuse Replaced a 30 amps fuse Found a 15 kva transformer defective Refer to maintenance department
Non-Outage | J.E.26.08.20051 | C001889983 | Derrick Dawkins | St.James | Completed | Load_252042 | Bogue - 510 | 2026-08-15 17:53 | 2026-08-15 17:56 | 2026-08-15 19:27 | 2026-08-15 19:38 | 2026-08-15 20:08 | 2026-08-15 20:16 | 2026-08-15 20:27 | 2026-08-15 20:27 |  |  | Fair | No | Check and found customer has internal problems advise customer to get an electrician voltage left 110/109/219
Non-Outage | J.E.26.08.21584 | C001889984 | Tajay Bernard | St.James | Completed | Load_259607 | Bogue - 510 | 2026-08-15 17:53 | 2026-08-15 21:15 | 2026-08-15 22:07 | 2026-08-15 22:08 | 2026-08-15 22:26 | 2026-08-15 22:43 | 2026-08-15 22:43 | 2026-08-15 22:43 |  |  | Fair | No | Clean and remake joints at customer pot head use 1 clamp Voltage found 103/111/214Voltage left 109/111/220
Non-Outage | J.E.26.08.22862 | C001889985 | Derrick Dawkins | St.James | Completed | Load_267637 | Bogue - 610 | 2026-08-15 17:53 | 2026-08-15 17:56 | 2026-08-15 18:50 | 2026-08-15 19:17 | 2026-08-15 19:19 | 2026-08-15 19:20 | 2026-08-15 19:20 | 2026-08-15 19:20 |  |  | Fair | No | Found premises ok
Non-Outage | J.E.26.08.21500 | C001889987 | Derrick Dawkins | St.James | Completed | Load_267637 | Bogue - 610 | 2026-08-15 17:54 | 2026-08-15 17:56 | 2026-08-15 18:47 | 2026-08-15 19:21 | 2026-08-15 19:24 | 2026-08-15 19:26 | 2026-08-15 19:27 | 2026-08-15 19:27 |  |  | Fair | No | Found premises ok
Non-Outage | J.E.26.08.22384 | C001889986 | Derrick Dawkins | St.James | Completed | Load_260918 | Bogue - 610 | 2026-08-15 17:54 | 2026-08-15 17:56 | 2026-08-15 19:27 | 2026-08-15 19:28 | 2026-08-15 19:32 | 2026-08-15 19:37 | 2026-08-15 19:38 | 2026-08-15 19:38 |  |  | Fair | No | Cannot locate customer
Non-Outage | J.E.26.08.21974 | C001889988 | Derrick Dawkins | St.James | Completed | Load_267637 | Bogue - 610 | 2026-08-15 17:55 | 2026-08-15 17:56 | 2026-08-15 18:02 | 2026-08-15 18:02 | 2026-08-15 19:06 | 2026-08-15 19:15 | 2026-08-15 19:16 | 2026-08-15 19:16 |  |  | Fair | No | Found premises ok
Outage | J.E.26.08.22955 | C001889991 | Wayne Dillion | St.Elizabeth | Completed | Load_255849 | Maggotty - 110 | 2026-08-15 17:59 | 2026-08-15 18:01 | 2026-08-15 19:19 | 2026-08-15 19:20 | 2026-08-15 19:20 | 2026-08-15 19:21 | 2026-08-15 19:21 | 2026-08-15 19:21 |  |  | Fair | No | Customer said supply restored to the area.
Outage | J.E.26.08.22957 | C001889990 | Raheem Ricketts | Manchester | Completed | Load_302854 | Spur Tree - 210 | 2026-08-15 17:59 | 2026-08-15 18:01 | 2026-08-15 18:31 | 2026-08-15 18:32 | 2026-08-15 18:32 | 2026-08-15 18:33 | 2026-08-15 18:33 | 2026-08-15 18:33 |  |  | Fair | No | Check and found okay power has been restored
Outage | J.E.26.08.22977 | C001889989 | Raheem Ricketts | Manchester | Completed | Load_262211 | Spur Tree - 210 | 2026-08-15 17:59 | 2026-08-15 18:01 | 2026-08-15 18:21 | 2026-08-15 18:21 | 2026-08-15 18:31 | 2026-08-15 18:31 | 2026-08-15 18:31 | 2026-08-15 18:31 |  |  | Fair | No | Check and found customer experiencing an internal problem
Outage | J.E.26.08.22936 | C001889992 | Barnett Brown | Manchester | Completed | Load_261375 | Spur Tree - 310 | 2026-08-15 18:00 | 2026-08-15 18:01 | 2026-08-15 19:11 | 2026-08-15 19:11 | 2026-08-15 20:18 | 2026-08-15 21:34 | 2026-08-15 21:42 | 2026-08-15 21:42 | BrokenWire |  | Fair | No | Change burnt service wire
Outage | J.E.26.08.22965 | C001889993 | Romeo Brissett | St.James | Completed | Load_293364 | Queens Drive - 310 | 2026-08-15 18:00 | 2026-08-15 18:01 | 2026-08-15 18:11 | 2026-08-16 07:54 | 2026-08-16 07:53 | 2026-08-16 19:50 | 2026-08-16 07:55 | 2026-08-16 07:55 | Fire |  | Fair | No | Replaced (1)30amps junction fuse.
Outage | J.E.26.08.22988 | C001889997 | Richman Whyte | Westmoreland | Completed | Load_262006 | Paradise - 310 | 2026-08-15 18:23 | 2026-08-15 18:24 | 2026-08-15 19:59 | 2026-08-15 19:59 | 2026-08-15 19:59 | 2026-08-15 20:02 | 2026-08-15 20:03 | 2026-08-15 20:03 |  |  | Rains | No | Replace 15 amp junction fuse
Outage | J.E.26.08.23020 | C001890000 | Wayne Dillion | St.Elizabeth | Completed | Load_248974 | Maggotty - 110 | 2026-08-15 18:40 | 2026-08-15 18:41 | 2026-08-15 19:21 | 2026-08-15 19:22 | 2026-08-15 20:21 | 2026-08-15 20:50 | 2026-08-15 20:51 | 2026-08-15 20:51 |  |  | Fair | No | Patrol and found one blown 1.5amp fuse that protects 25kva transformer circuit no pole #. Replace same and supply restored okay.
Outage | J.E.26.08.22991 | C001890001 | Tajay Bernard | Hanover | Completed | Load_238061 | Orange Bay - 310 | 2026-08-15 18:46 | 2026-08-15 18:47 | 2026-08-15 19:30 | 2026-08-15 19:31 | 2026-08-15 20:01 | 2026-08-15 20:30 | 2026-08-15 20:31 | 2026-08-15 20:31 | Fire |  | Fair | No | Remove tree limb and refuse 1 25kva Transformer use 3amp fuse
Outage | J.E.26.08.23021 | C001890002 | Tajay Bernard | Hanover | Completed | Load_258609 | Orange Bay - 210 | 2026-08-15 18:46 | 2026-08-15 18:47 | 2026-08-15 20:32 | 2026-08-15 20:32 | 2026-08-15 20:32 | 2026-08-15 20:33 | 2026-08-15 20:33 | 2026-08-15 20:33 |  |  | Fair | No | Customer stated that the issue has been resolved
Outage | J.E.26.08.22973 | C001890007 | Clyde Brown | Clarendon | Completed | Load_1003304 | May Pen - 110 | 2026-08-15 18:57 | 2026-08-15 18:58 | 2026-08-15 19:25 | 2026-08-15 22:46 | 2026-08-15 22:45 | 2026-08-15 22:37 | 2026-08-15 22:48 | 2026-08-15 22:48 | BrokenWire | Y | SevereWind | No | 25 kva transformer tripped caused by tree contact and no broken wire seen,line cleared and transformer reset.
Outage | J.E.26.08.23017 | C001890005 | Clyde Brown | Clarendon | Completed | Load_258698 | May Pen - 110 | 2026-08-15 18:57 | 2026-08-15 18:58 | 2026-08-15 19:25 | 2026-08-16 10:06 | 2026-08-16 11:00 | 2026-08-16 10:59 | 2026-08-16 11:07 | 2026-08-16 11:07 |  |  | Fair | No | Blown 10 amps junction fuse at Coxwein line patrolled and no fault seen blown fuse replaced
Non-Outage | J.E.26.08.22987 | C001890009 | Elvis Trowers | KSAN | Completed | Load_268356 | Constant Spring - 210 | 2026-08-15 19:14 | 2026-08-15 19:15 | 2026-08-15 19:18 | 2026-08-15 19:20 | 2026-08-15 19:53 | 2026-08-15 20:00 | 2026-08-15 20:08 | 2026-08-15 20:08 |  |  | Fair | No | Found two 20 amps junction fuse at pole #0011746 feed bank of 3-167 transformer blown. Refused using two 20 amps fuse and reclosed junction switches. One of the transformers in the bank is leaking oil from the pressure valve. Transformer need to be checked.
Outage | J.E.26.08.23060 | C001890010 | Wayne Dillion | St.Elizabeth | Completed | Load_249674 | Maggotty - 110 | 2026-08-15 19:36 | 2026-08-15 19:38 | 2026-08-15 21:01 | 2026-08-15 21:01 | 2026-08-15 21:01 | 2026-08-15 21:02 | 2026-08-15 21:03 | 2026-08-15 21:03 |  |  | Fair | No | Customer said supply is okay.
Outage | J.E.26.08.23072 | C001890013 | Kenroy Dale | Manchester | Completed | Load_240757 | Porus - 210 | 2026-08-15 19:38 | 2026-08-15 20:26 | 2026-08-15 21:21 | 2026-08-15 21:39 | 2026-08-15 22:31 | 2026-08-15 22:58 | 2026-08-15 23:02 | 2026-08-15 23:02 | Fire |  | Fair | No | Open 25 kva transformer to retention 1 span of secondary phase that was touching neutral whenever there is a wind, conductor was retention transformer re-closed and area now with supply
Outage | J.E.26.08.23062 | C001890014 | Romaine Roberts | St.Mary | Completed | Load_258392 | Highgate - 210 | 2026-08-15 19:41 | 2026-08-15 19:42 | 2026-08-15 21:21 | 2026-08-15 21:22 | 2026-08-15 22:56 | 2026-08-15 23:02 | 2026-08-15 23:02 | 2026-08-15 23:02 | BrokenPole |  | Fair | No | One 35 wood pole broke and fall down maintenance work needed isolate junction and clear reload pole construction dvpriary and neutral andou 10 customer is with out supply one transformer circuit is out no pole number
Outage | J.E.26.08.23085 | C001890016 | Richman Whyte | Westmoreland | Completed | Load_245098 | Paradise - 310 | 2026-08-15 19:51 | 2026-08-15 19:52 | 2026-08-15 20:59 | 2026-08-15 21:00 | 2026-08-15 20:59 | 2026-08-15 21:00 | 2026-08-15 21:00 | 2026-08-15 21:00 | Fire |  | Rains | No | Unable to locate or contact customer on the phone
Outage | J.E.26.08.23047 | C001890018 | Donald Cunningham | St.Catherine | Completed | Load_259378 | New Michelton - 210 | 2026-08-15 20:04 | 2026-08-15 20:05 | 2026-08-15 21:52 | 2026-08-15 21:53 | 2026-08-15 21:52 | 2026-08-15 22:35 | 2026-08-15 22:41 | 2026-08-15 22:41 | BrokenWire |  | Fair | No | Broken secondary phase splice and retention using 80 feet of #2 aa 1 automatic splice and 1 clamp for repair also reset trip10 kva transformer
Outage | J.E.26.08.23050 | C001890019 | Hartley Chin | Clarendon | Completed | Load_259723 | Monymusk - 410 | 2026-08-15 20:04 | 2026-08-16 07:33 | 2026-08-16 08:11 | 2026-08-16 08:12 | 2026-08-16 11:07 | 2026-08-16 12:23 | 2026-08-16 12:23 | 2026-08-16 12:23 |  |  | SevereWind | No | Found 3 junction blown and a 15 KVA due to banging secondary. Tension secondary refuse transformer 8 amp junction 15 amp and 25 amp junction no pole number
Non-Outage | J.E.26.08.23028 | C001890021 | Raheem Ricketts | St.Elizabeth | Completed | Load_1002276 | Maggotty - 210 | 2026-08-15 20:07 | 2026-08-15 20:48 | 2026-08-15 21:01 | 2026-08-15 21:03 | 2026-08-15 21:03 | 2026-08-15 21:03 | 2026-08-15 21:04 | 2026-08-15 21:04 | Fire |  | Fair | No | Check and found okay
Outage | J.E.26.08.23111 | C001890024 | Nickolas Rodriques | St.Catherine | Completed | Load_260579 | Tredegar - 310 | 2026-08-15 20:29 | 2026-08-15 20:30 | 2026-08-15 21:00 | 2026-08-15 21:01 | 2026-08-15 21:53 | 2026-08-15 22:23 | 2026-08-15 22:30 | 2026-08-15 22:30 | BrokenWire |  | Fair | No | Found premises locked. The customer was contacted and stated that no one is currently at the premises to accommodate the team and she is requesting a team anytime throughout the day tomorrow August 16, 2026.
Outage | J.E.26.08.23116 | C001890027 | Elvis Trowers | KSAS | Completed | Load_239090 | Up Park Camp - 310 | 2026-08-15 20:48 | 2026-08-15 20:53 | 2026-08-15 20:56 | 2026-08-15 21:04 | 2026-08-15 21:39 | 2026-08-15 22:00 | 2026-08-15 21:58 | 2026-08-15 21:58 |  |  | Fair | No | Isolate bank of transformers 1-100 and 2-50 kva at pole #( no pole #). And repair open wire secondary phase jumper burned off. Repair using 6ft #2/0 conductor and four 1- bolt clamps. And reclosed transformers switches.
Outage | J.E.26.08.23117 | C001890029 | Delano Gayle | St.Catherine | Completed | Load_261126 | Rhodens Pen - 210 | 2026-08-15 21:08 | 2026-08-15 21:27 | 2026-08-15 22:07 | 2026-08-15 22:07 | 2026-08-16 00:02 | 2026-08-16 00:17 | 2026-08-16 00:17 | 2026-08-16 00:17 | Fire |  | SevereWind | No | Blown 50kva transformer fuse no pole number replace 5amps
Non-Outage | J.E.26.08.21689 | C001890033 | Tajay Bernard | Hanover | Completed | Load_262897 | Orange Bay - 310 | 2026-08-15 21:14 | 2026-08-15 21:15 | 2026-08-15 21:52 | 2026-08-15 21:53 | 2026-08-15 22:01 | 2026-08-15 22:06 | 2026-08-15 22:06 | 2026-08-15 22:06 |  |  | Fair | No | Area check and found okay unable to locate customer on premises multiple phone calls to customer number went unanswered
Outage | J.E.26.08.23184 | C001890051 | Delano Gayle | St.Catherine | Completed | Load_251630 | Rhodens Pen - 410 | 2026-08-15 22:46 | 2026-08-15 22:47 | 2026-08-16 00:19 | 2026-08-16 00:20 | 2026-08-16 00:49 | 2026-08-16 00:51 | 2026-08-16 00:51 | 2026-08-16 00:51 | BrokenWire |  | SevereWind | No | Defective customer equipment which needs repair before customer can be reconnected
Non-Outage | J.E.26.08.22621 | C001890058 | Christopher Edwards |  | Completed |  |  | 2026-08-15 23:00 | 2026-08-15 23:06 | 2026-08-15 23:54 | 2026-08-15 23:55 | 2026-08-16 00:16 | 2026-08-16 00:20 | 2026-08-16 00:21 | 2026-08-16 00:21 | BrokenWire |  | Fair | No | Check and found ok Supply is in the areaBroken wire is cable wire
Outage | J.E.26.08.22682 | C001890056 | Christopher Edwards | KSAS | Completed | Load_253774 | Up Park Camp - 410 | 2026-08-15 23:00 | 2026-08-15 23:06 | 2026-08-16 00:54 | 2026-08-16 00:54 | 2026-08-16 01:22 | 2026-08-16 01:45 | 2026-08-16 01:48 | 2026-08-16 01:48 |  |  | Fair | No | Unable to gain access to premises Observed supply is on the premises
Outage | J.E.26.08.22881 | C001890055 | Christopher Edwards | KSAN | Completed | Load_250924 | Washington Blvd - 510 | 2026-08-15 23:00 | 2026-08-15 23:06 | 2026-08-15 23:17 | 2026-08-16 01:48 | 2026-08-16 01:48 | 2026-08-16 02:13 | 2026-08-16 02:33 | 2026-08-16 02:33 |  |  | Fair | No | Check and found okSupply is in the area
Outage | J.E.26.08.22612 | C001890059 | Christopher Edwards | KSAN | Completed | Load_255554 | Washington Blvd - 610 | 2026-08-15 23:01 | 2026-08-15 23:06 | 2026-08-16 00:17 | 2026-08-16 00:22 | 2026-08-16 00:38 | 2026-08-16 00:53 | 2026-08-16 00:54 | 2026-08-16 00:54 |  |  | Fair | No | Check and found okSupply is in the area
Outage | J.E.26.08.22890 | C001890062 | Daniel Francis | St.Ann | Completed | Load_574235 | Roaring River - 410 | 2026-08-15 23:16 | 2026-08-15 23:17 | 2026-08-16 01:34 | 2026-08-16 01:34 | 2026-08-16 01:34 | 2026-08-16 01:34 | 2026-08-16 01:36 | 2026-08-16 01:36 |  |  | Fair | No | Reset circuit breaker at meter center center
Outage | J.E.26.08.22916 | C001890064 | Daniel Francis | St.Ann | Completed | Load_413084 | Roaring River - 410 | 2026-08-15 23:16 | 2026-08-15 23:17 | 2026-08-15 23:52 | 2026-08-15 23:52 | 2026-08-16 00:09 | 2026-08-16 01:29 | 2026-08-16 01:31 | 2026-08-16 01:31 |  |  | Fair | No | Found main circuit breaker at meter center trip reset
Outage | J.E.26.08.23022 | C001890063 | Daniel Francis | St.Ann | Completed | Load_253998 | Cardiff Hall - 210 | 2026-08-15 23:16 | 2026-08-15 23:17 | 2026-08-16 01:41 | 2026-08-16 01:41 | 2026-08-16 01:41 | 2026-08-16 01:44 | 2026-08-16 01:45 | 2026-08-16 01:45 |  |  | Fair | No | Day time attention needed for that location
Outage | J.E.26.08.23174 | C001890066 | Delano Gayle | St.Catherine | Completed | Load_239534 | Twickenham - 210 | 2026-08-15 23:17 | 2026-08-15 23:18 | 2026-08-16 00:51 | 2026-08-16 00:52 | 2026-08-16 01:52 | 2026-08-16 02:12 | 2026-08-16 02:12 | 2026-08-16 02:12 |  |  | Fair | No | Blown junction on main at pole#601791, patrolled line section and found okay for closure replace 25amps
Outage | J.E.26.08.23177 | C001890067 | Nickolas Rodriques | St.Catherine | Completed | Load_244063 | Twickenham - 210 | 2026-08-15 23:17 | 2026-08-16 07:30 | 2026-08-16 08:31 | 2026-08-16 08:34 | 2026-08-16 09:07 | 2026-08-16 09:28 | 2026-08-16 09:33 | 2026-08-16 09:33 |  |  | Fair | No | Found area with electricity. The area outage was restored.
Outage | J.E.26.08.23194 | C001890065 | Delano Gayle | St.Catherine | Completed | Load_262197 | Twickenham - 210 | 2026-08-15 23:17 | 2026-08-15 23:18 | 2026-08-16 02:13 | 2026-08-16 02:13 | 2026-08-16 02:18 | 2026-08-16 02:19 | 2026-08-16 02:19 | 2026-08-16 02:19 |  |  | Fair | No | Premises found okay power restored related to call where 25amps junction fuse was replaced
Non-Outage | J.E.26.08.23469 | C001890076 | Delano Gayle |  | Completed |  |  | 2026-08-16 04:04 | 2026-08-16 04:08 | 2026-08-16 05:33 | 2026-08-16 05:34 | 2026-08-16 05:45 | 2026-08-16 05:46 | 2026-08-16 05:46 | 2026-08-16 05:46 | Fire |  | Fair | No | Premises found okay power restored related to call where 65 amps fuse was replaced
Outage | J.E.26.08.23445 | C001890075 | Delano Gayle | St.Catherine | Completed | Load_247083 | Twickenham - 210 | 2026-08-16 04:04 | 2026-08-16 04:08 | 2026-08-16 05:46 | 2026-08-16 05:47 | 2026-08-16 05:54 | 2026-08-16 05:55 | 2026-08-16 05:55 | 2026-08-16 05:55 |  |  | Fair | No | Premises found okay power was restored
Outage | J.E.26.08.23272 | C001890077 | Nickolas Rodriques | St.Catherine | Completed | Load_258830 | Twickenham - 210 | 2026-08-16 04:07 | 2026-08-16 07:30 | 2026-08-16 07:40 | 2026-08-16 07:45 | 2026-08-16 08:18 | 2026-08-16 08:25 | 2026-08-16 08:28 | 2026-08-16 08:28 |  |  | Fair | No | Found customer with electricity. The customer confirmed that the area outage was restored.
Outage | J.E.26.08.23324 | C001890078 | Delano Gayle | St.Catherine | Completed | Load_256303 | Twickenham - 210 | 2026-08-16 04:07 | 2026-08-16 04:08 | 2026-08-16 04:15 | 2026-08-16 04:16 | 2026-08-16 04:46 | 2026-08-16 05:31 | 2026-08-16 05:31 | 2026-08-16 05:31 |  |  | Fair | No | Blown junction on main no pole#, replace 65amps
Outage | J.E.26.08.23352 | C001890079 | Delano Gayle | St.Catherine | Completed | Load_264593 | Twickenham - 210 | 2026-08-16 04:07 | 2026-08-16 04:08 | 2026-08-16 05:55 | 2026-08-16 05:56 | 2026-08-16 06:27 | 2026-08-16 06:34 | 2026-08-16 06:34 | 2026-08-16 06:34 | Fire |  | Fair | No | Premises found okay power was restored
Outage | J.E.26.08.23199 | C001890084 | Swon Miller | St.James | Completed | Load_249364 | Rose Hall - 210 | 2026-08-16 07:08 | 2026-08-16 07:09 | 2026-08-16 08:27 | 2026-08-16 08:27 | 2026-08-16 08:27 | 2026-08-16 08:28 | 2026-08-16 08:28 | 2026-08-16 08:28 |  |  | Fair | No | This call is related to the previous
Outage | J.E.26.08.23202 | C001890083 | Swon Miller | St.James | Completed | Load_263074 | Rose Hall - 210 | 2026-08-16 07:08 | 2026-08-16 07:09 | 2026-08-16 07:13 | 2026-08-16 07:14 | 2026-08-16 07:31 | 2026-08-16 08:19 | 2026-08-16 08:20 | 2026-08-16 08:20 |  |  | Fair | No | Found 15 amp junction fuse blown cause by tree limb cut and remove tree limb from primary conductor and replace 15 amp junction fuse no pole number available
Outage | J.E.26.08.23239 | C001890081 | Swon Miller | St.James | Completed | Load_254071 | Rose Hall - 210 | 2026-08-16 07:08 | 2026-08-16 07:09 | 2026-08-16 08:24 | 2026-08-16 08:25 | 2026-08-16 08:25 | 2026-08-16 08:25 | 2026-08-16 08:25 | 2026-08-16 08:25 |  |  | Fair | No | This call is related to the previous
Outage | J.E.26.08.23395 | C001890082 | Swon Miller | St.James | Completed | Load_263074 | Rose Hall - 210 | 2026-08-16 07:08 | 2026-08-16 07:09 | 2026-08-16 08:25 | 2026-08-16 08:26 | 2026-08-16 08:26 | 2026-08-16 08:26 | 2026-08-16 08:26 | 2026-08-16 08:26 |  |  | Fair | No | This call is related to the previous
Outage | J.E.26.08.23435 | C001890080 | Swon Miller | St.James | Completed | Load_254071 | Rose Hall - 210 | 2026-08-16 07:08 | 2026-08-16 07:09 | 2026-08-16 08:23 | 2026-08-16 08:23 | 2026-08-16 08:23 | 2026-08-16 08:23 | 2026-08-16 08:24 | 2026-08-16 08:24 |  |  | Fair | No | Found 15 amp junction fuse blown cause by tree limb cut and remove tree limb from primary conductor and replace 15 amp junction fuse no pole number available
Outage | J.E.26.08.23556 | C001890085 | Omar King | St.Ann | Completed | Load_246908 | Ocho Rios - 510 | 2026-08-16 07:12 | 2026-08-16 07:13 | 2026-08-16 08:32 | 2026-08-16 08:33 | 2026-08-16 08:34 | 2026-08-16 09:20 | 2026-08-16 09:22 | 2026-08-16 09:22 |  |  | Fair | No | Found 10 amp junction fuse blow fuse as been replaced area is now with supply
Outage | J.E.26.08.23379 | C001890086 | Collin Robinson | Portland | Completed | Load_251148 | Port Antonio - 310 | 2026-08-16 07:16 | 2026-08-16 07:17 | 2026-08-16 12:06 | 2026-08-16 12:07 | 2026-08-16 13:27 | 2026-08-16 13:46 | 2026-08-16 13:48 | 2026-08-16 13:48 |  |  | Rains | No | Clear tree branch from one phase of primary conductor and replace 20 amps junction fuse
Outage | J.E.26.08.23018 | C001890090 | Horace Malcolm | St.James | Completed | Load_250024 | Bogue - 310 | 2026-08-16 07:18 | 2026-08-16 07:19 | 2026-08-16 14:30 | 2026-08-16 14:30 | 2026-08-16 14:58 | 2026-08-16 15:24 | 2026-08-16 15:24 | 2026-08-16 15:24 |  |  | Fair | No | Unable to locate customer or premises from directions given
Outage | J.E.26.08.23527 | C001890093 | Collin Robinson | Portland | Completed | Load_240841 | Port Antonio - 410 | 2026-08-16 07:21 | 2026-08-16 07:21 | 2026-08-16 08:47 | 2026-08-16 08:47 | 2026-08-16 09:41 | 2026-08-16 11:21 | 2026-08-16 11:21 | 2026-08-16 11:21 |  |  | Fair | No | Remove fallen tree from two phase of primary conductor and close two 50 amps trip saver
Outage | J.E.26.08.23407 | C001890095 | Richard Samuda | Manchester | Completed | Load_242746 | Kendal - 310 | 2026-08-16 07:22 | 2026-08-16 07:23 | 2026-08-16 07:40 | 2026-08-16 07:41 | 2026-08-16 08:15 | 2026-08-16 08:26 | 2026-08-16 08:26 | 2026-08-16 08:26 |  |  | Fair | No | Found 25vkva transformer chipped patrol line found nothing restart transformer customer back
Outage | J.E.26.08.23532 | C001890094 | Richard Samuda | Manchester | Completed | Load_242746 | Kendal - 310 | 2026-08-16 07:22 | 2026-08-16 07:23 | 2026-08-16 08:27 | 2026-08-16 08:27 | 2026-08-16 08:27 | 2026-08-16 08:28 | 2026-08-16 08:28 | 2026-08-16 08:28 |  |  | Fair | No | Customer said they are back to normal
Outage | J.E.26.08.23228 | C001890096 | Richard Samuda | Manchester | Completed | Load_292487 | Spur Tree - 310 | 2026-08-16 07:23 | 2026-08-16 07:23 | 2026-08-16 08:51 | 2026-08-16 08:52 | 2026-08-16 09:20 | 2026-08-16 09:20 | 2026-08-16 09:20 | 2026-08-16 09:20 |  |  | Fair | No | Found ok
Outage | J.E.26.08.23494 | C001890099 | Nickolas Rodriques | St.Catherine | Completed | Load_256303 | Twickenham - 210 | 2026-08-16 07:30 | 2026-08-16 07:32 | 2026-08-16 09:33 | 2026-08-16 09:43 | 2026-08-16 10:11 | 2026-08-16 10:21 | 2026-08-16 10:23 | 2026-08-16 10:23 |  |  | Fair | No | Found area with electricity. Customer confirmed that the area outage was later restored.
Outage | J.E.26.08.23506 | C001890098 | Damion Reid | Manchester | Completed | Load_303105 | Kendal - 210 | 2026-08-16 07:30 | 2026-08-16 07:31 | 2026-08-16 09:15 | 2026-08-16 09:16 | 2026-08-16 10:36 | 2026-08-16 11:53 | 2026-08-16 11:56 | 2026-08-16 11:56 |  |  | Rains | No | Blown 10amp junction fuse found cause by broken 35ft TA construction pole line section is isolated two transformer circuit is out
Outage | J.E.26.08.22420 | C001890101 | Donald Cunningham | Portmore | Completed | Load_238905 | Naggo Head - 510 | 2026-08-16 07:31 | 2026-08-16 11:09 | 2026-08-16 12:17 | 2026-08-16 12:18 | 2026-08-16 13:39 | 2026-08-16 13:40 | 2026-08-16 13:48 | 2026-08-16 13:48 | TreeContact |  | Fair | No | Bushing required in area
Outage | J.E.26.08.23250 | C001890100 | Nickolas Rodriques | St.Catherine | Completed | Load_569977 | Twickenham - 210 | 2026-08-16 07:31 | 2026-08-16 07:32 | 2026-08-16 10:24 | 2026-08-16 10:33 | 2026-08-16 10:57 | 2026-08-16 11:24 | 2026-08-16 11:32 | 2026-08-16 11:32 |  |  | Fair | No | Customer was located and stated that the power was later restored.
Outage | J.E.26.08.23165 | C001890102 | Richard Nicholas | St.Catherine | Completed | Load_568138 | Rhodens Pen - 210 | 2026-08-16 07:34 | 2026-08-16 07:37 | 2026-08-16 08:03 | 2026-08-16 08:04 | 2026-08-16 09:44 | 2026-08-16 10:34 | 2026-08-16 10:35 | 2026-08-16 10:35 |  |  | Fair | No | Area found ok
Outage | J.E.26.08.23605 | C001890103 | Richard Nicholas | St.Catherine | Completed | Load_1001432 | Tredegar - 210 | 2026-08-16 07:34 | 2026-08-16 07:37 | 2026-08-16 10:36 | 2026-08-16 10:36 | 2026-08-16 11:25 | 2026-08-16 11:46 | 2026-08-16 11:48 | 2026-08-16 11:48 |  |  | Fair | No | Planned outage in the area.
Non-Outage | J.E.26.08.23107 | C001890106 | Damion Reid | Manchester | Completed | Load_239382 | Kendal - 210 | 2026-08-16 07:37 | 2026-08-16 07:38 | 2026-08-16 08:02 | 2026-08-16 08:03 | 2026-08-16 09:03 | 2026-08-16 09:10 | 2026-08-16 09:11 | 2026-08-16 09:11 |  |  | Fair | No | Unable to contact or locate customer
Non-Outage | J.E.26.08.23490 | C001890107 | Richard Samuda | Manchester | Completed | Load_249466 | Spur Tree - 310 | 2026-08-16 07:37 | 2026-08-16 07:39 | 2026-08-16 09:21 | 2026-08-16 09:21 | 2026-08-16 09:21 | 2026-08-16 11:08 | 2026-08-16 11:08 | 2026-08-16 11:08 |  |  | Fair | No | Splice and reconnected two span of secondary neutral wire that was brunt off causing customer to experience low / hi voltage using 10 ft of #2 aluminum wire and one #2 splicing sleeve and one 1bolt clamp customer back to normal
Non-Outage | J.E.26.08.21279 | C001890111 | Richard Samuda | Manchester | Completed | Load_260536 | Spur Tree - 210 | 2026-08-16 07:38 | 2026-08-16 15:38 | 2026-08-16 20:51 | 2026-08-16 20:51 | 2026-08-16 21:41 | 2026-08-16 10:00 | 2026-08-16 22:01 | 2026-08-16 22:01 | BangingWires |  | Fair | No | Balance secondary neutral that was banging out with lower phase of line
Outage | J.E.26.08.23098 | C001890109 | Clyde Brown | Clarendon | Completed | Load_261658 | May Pen - 110 | 2026-08-16 07:38 | 2026-08-16 07:40 | 2026-08-16 11:13 | 2026-08-16 11:14 | 2026-08-16 11:13 | 2026-08-16 10:59 | 2026-08-16 11:16 | 2026-08-16 11:16 |  |  | Fair | No | Blown 10 amps junction fuse at Coxwein,line patrolled and no fault seen blown fuse replaced
Outage | J.E.26.08.23552 | C001890110 | Romeo Brissett | St.James | Completed | Load_250995 | Bogue - 610 | 2026-08-16 07:38 | 2026-08-16 07:39 | 2026-08-16 08:02 | 2026-08-16 08:02 | 2026-08-16 08:07 | 2026-08-16 08:08 | 2026-08-16 08:23 | 2026-08-16 08:23 |  |  | Fair | No | Westmoreland call
Outage | J.E.26.08.23244 | C001890112 | Horace Malcolm | St.James | Completed | Load_254869 | Bogue - 310 | 2026-08-16 07:39 | 2026-08-16 07:40 | 2026-08-16 07:47 | 2026-08-16 07:47 | 2026-08-16 09:54 | 2026-08-16 11:42 | 2026-08-16 11:42 | 2026-08-16 11:42 |  |  | Fair | No | Remove defective primary lightening arrester and Refused one 10amp junction fuse
Outage | J.E.26.08.23551 | C001890116 | Raymond Carr | St.Mary | Completed | Load_351803 | Oracabessa - 110 | 2026-08-16 07:40 | 2026-08-16 07:42 | 2026-08-16 10:40 | 2026-08-16 10:40 | 2026-08-16 10:47 | 2026-08-16 10:56 | 2026-08-16 10:58 | 2026-08-16 10:58 |  |  | SevereWind | No | Blown junction fuse found, line patrol and found okay, however tree contact was suspected. A 10 amp fuse was used to renew supply was restored .
Outage | J.E.26.08.23587 | C001890115 | Raymond Carr | St.Mary | Completed | Load_351191 | Oracabessa - 210 | 2026-08-16 07:40 | 2026-08-16 07:42 | 2026-08-16 09:52 | 2026-08-16 09:53 | 2026-08-16 09:52 | 2026-08-16 10:00 | 2026-08-16 10:06 | 2026-08-16 10:06 |  |  | Fair | No | Supply was restored.
Outage | J.E.26.08.23600 | C001890113 | Raymond Carr | St.Mary | Completed | Load_351007 | Oracabessa - 210 | 2026-08-16 07:40 | 2026-08-16 07:42 | 2026-08-16 08:07 | 2026-08-16 08:08 | 2026-08-16 09:32 | 2026-08-16 09:41 | 2026-08-16 09:51 | 2026-08-16 09:51 |  |  | SevereWind | No | Blown junction fuse found at pole number 005047, line patrol and found okay, however tree contact was suspected. A 20 amp fuse was used to renew supply was restored.
Outage | J.E.26.08.23606 | C001890114 | Raymond Carr | St.Mary | Completed | Load_249759 | Oracabessa - 210 | 2026-08-16 07:40 | 2026-08-16 07:42 | 2026-08-16 10:06 | 2026-08-16 10:06 | 2026-08-16 10:18 | 2026-08-16 10:00 | 2026-08-16 10:22 | 2026-08-16 10:22 |  |  | Fair | No | Supply was restored.
Outage | J.E.26.08.23353 | C001890117 | Raymond Carr | St.Ann | Completed | Load_247813 | Upper White River - 110 | 2026-08-16 07:41 | 2026-08-16 07:42 | 2026-08-16 10:59 | 2026-08-16 10:59 | 2026-08-16 12:13 | 2026-08-16 | 2026-08-16 12:13 | 2026-08-16 12:13 |  |  | Fair | No | Several calls to contact number went straight to voicemail.
Outage | J.E.26.08.22963 | C001890123 | Stephen Taylor | St.Thomas | Completed | Load_256235 | Lysson - 410 | 2026-08-16 07:50 | 2026-08-16 07:53 | 2026-08-16 14:59 | 2026-08-16 14:59 | 2026-08-16 16:32 | 2026-08-16 16:59 | 2026-08-16 16:59 | 2026-08-16 16:59 | LowHangingWires,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Splice and retention services wire and use 30 foot a service wire
Outage | J.E.26.08.23405 | C001890122 | Stephen Taylor | St.Thomas | Completed | Load_269057 | Lysson - 410 | 2026-08-16 07:50 | 2026-08-16 07:53 | 2026-08-16 08:34 | 2026-08-16 08:34 | 2026-08-16 11:21 | 2026-08-16 11:21 | 2026-08-16 11:23 | 2026-08-16 11:23 |  |  | Fair | No | Patrol clear line and reset 15 kva transformer customer is now okay
Outage | J.E.26.08.23504 | C001890121 | Stephen Taylor | St.Thomas | Completed | Load_243004 | Good Year - 110 | 2026-08-16 07:50 | 2026-08-16 07:53 | 2026-08-16 11:27 | 2026-08-16 11:27 | 2026-08-16 13:33 | 2026-08-16 14:18 | 2026-08-16 14:19 | 2026-08-16 14:19 |  |  | SevereWind | No | Patrol clear line with switch stick and close up junction with 30ams fuse
Outage | J.E.26.08.23515 | C001890120 | Stephen Taylor | St.Thomas | Completed | Load_238970 | Lysson - 410 | 2026-08-16 07:50 | 2026-08-16 07:53 | 2026-08-16 11:23 | 2026-08-16 11:24 | 2026-08-16 11:24 | 2026-08-16 11:24 | 2026-08-16 11:26 | 2026-08-16 11:26 |  |  | Fair | No | Patrol and cut bush off line and close up back 25 kva transformer safely customer is now okay
Non-Outage | J.E.26.08.17542 | C001890124 | Wayne Dillion |  | Completed |  |  | 2026-08-16 07:57 | 2026-08-16 14:54 | 2026-08-16 21:14 | 2026-08-16 21:15 | 2026-08-16 21:15 | 2026-08-16 21:18 | 2026-08-16 21:19 | 2026-08-16 21:19 | BrokenPole |  | Fair | No | Patrol and found one broken 30ft wooden pole. Customer tied it with rope. Please refer same to the maintenance department for replacement
Non-Outage | J.E.26.08.19035 | C001890126 | Oshane Warren | St.Elizabeth | Completed | Load_237739 | Maggotty - 110 | 2026-08-16 07:58 | 2026-08-16 08:00 | 2026-08-16 10:27 | 2026-08-16 10:28 | 2026-08-16 10:31 | 2026-08-16 10:32 | 2026-08-16 10:41 | 2026-08-16 10:41 | BrokenPole |  | Fair | No | Customer is getting billed and her power is not yet connected to the grid…Customer is currently carrying out repairs to their building was advised to visit the office
Non-Outage | J.E.26.08.19887 | C001890125 | Marlon Authors | St.Elizabeth | Completed | Load_247252 | Maggotty - 110 | 2026-08-16 07:58 | 2026-08-16 08:00 | 2026-08-16 13:51 | 2026-08-16 13:52 | 2026-08-16 14:05 | 2026-08-16 14:07 | 2026-08-16 14:07 | 2026-08-16 14:07 |  |  | Fair | No | Unable to locate and the customer not answering the phone
Non-Outage | J.E.26.08.16906 | C001890127 | Marlon Authors | St.Elizabeth | Completed | Load_305113 | Maggotty - 110 | 2026-08-16 07:59 | 2026-08-16 08:00 | 2026-08-16 12:47 | 2026-08-16 12:47 | 2026-08-16 13:39 | 2026-08-16 13:46 | 2026-08-16 13:46 | 2026-08-16 13:46 |  |  | Fair | No | Supply checked and found working ok rdg 111v,111v and cross phased 222 volts
Non-Outage | J.E.26.08.17254 | C001890128 | Wayne Dillion | St.Elizabeth | Completed | Load_568323 | Maggotty - 110 | 2026-08-16 07:59 | 2026-08-16 14:54 | 2026-08-16 18:48 | 2026-08-16 18:49 | 2026-08-16 18:48 | 2026-08-16 18:54 | 2026-08-16 18:54 | 2026-08-16 18:54 |  |  | Fair | No | Patrol and found one defective 25kva transformer and two missing meter from the hurricane leaving two customer without supply. Recommended 10 or 15 kva to replace 25kva transformer that supply two customers. Please refer to the maintenance department to replace transformer and to the field services department for the replacement of two meters.
Non-Outage | J.E.26.08.17373 | C001890129 | Oshane Warren | St.Elizabeth | Completed | Load_243662 | Maggotty - 110 | 2026-08-16 07:59 | 2026-08-16 08:00 | 2026-08-16 14:01 | 2026-08-16 14:02 | 2026-08-16 14:02 | 2026-08-16 14:02 | 2026-08-16 14:03 | 2026-08-16 14:03 |  |  | Fair | No | Advice customer to visit the office to carry out name change
Outage | J.E.26.08.23210 | C001890132 | Romaine Roberts | St.Mary | Completed | Load_250773 | Highgate - 210 | 2026-08-16 08:00 | 2026-08-16 08:02 | 2026-08-16 11:09 | 2026-08-16 11:10 | 2026-08-16 11:10 | 2026-08-16 11:11 | 2026-08-16 11:12 | 2026-08-16 11:12 |  |  | Fair | No | High wind and vegetation blow 25 kva transformer fuse patrol and clear bushing from line and replace 3 amp power restore
Outage | J.E.26.08.23621 | C001890131 | Romaine Roberts | St.Mary | Completed | Load_250540 | Annotto Bay - 310 | 2026-08-16 08:00 | 2026-08-16 08:02 | 2026-08-16 12:53 | 2026-08-16 12:54 | 2026-08-16 12:53 | 2026-08-16 12:54 | 2026-08-16 12:54 | 2026-08-16 12:54 |  |  | Fair | No | Found junction fuse blown patrol line nothing found replace 50 amp to restore supply no pole number
Outage | J.E.26.08.23022 | C001890134 | Roxroy Needham | St.Ann | Completed | Load_253998 | Cardiff Hall - 210 | 2026-08-16 08:04 | 2026-08-16 08:05 | 2026-08-16 08:16 | 2026-08-16 08:16 | 2026-08-16 09:46 | 2026-08-16 10:10 | 2026-08-16 10:13 | 2026-08-16 10:13 |  |  | Fair | No | Replace a 8 amps junction fuse at pole
Outage | J.E.26.08.23416 | C001890135 | Tyrese Williams | St.Ann | Completed | Load_260616 | Cardiff Hall - 210 | 2026-08-16 08:04 | 2026-08-16 15:33 | 2026-08-16 15:38 | 2026-08-16 17:29 | 2026-08-16 17:29 | 2026-08-16 17:32 | 2026-08-16 17:32 | 2026-08-16 17:32 |  |  | Fair | No | Premises found ok customer said power was restored
Non-Outage | J.E.26.08.23632 | C001890137 | Romaine Roberts |  | Completed |  |  | 2026-08-16 08:08 | 2026-08-16 08:09 | 2026-08-16 08:40 | 2026-08-16 08:40 | 2026-08-16 10:21 | 2026-08-16 11:06 | 2026-08-16 11:09 | 2026-08-16 11:09 |  |  | Fair | No | High wind and vegetation blow 25 kva transformer fuse patrol and clear bushing from line and replace 3 amp power restore
Outage | J.E.26.08.23143 | C001890136 | Horace Malcolm | St.James | Completed | Load_301640 | Bogue - 310 | 2026-08-16 08:08 | 2026-08-16 08:09 | 2026-08-16 11:45 | 2026-08-16 11:45 | 2026-08-16 12:02 | 2026-08-16 12:03 | 2026-08-16 12:03 | 2026-08-16 12:03 |  |  | Fair | No | Check and found premises ok voltage 110-112-222
Outage | J.E.26.08.17015 | C001890138 | Swon Miller | St.James | Completed | Load_246358 | Rose Hall - 210 | 2026-08-16 08:11 | 2026-08-16 08:13 | 2026-08-16 08:22 | 2026-08-16 08:22 | 2026-08-16 08:22 | 2026-08-16 08:22 | 2026-08-16 08:23 | 2026-08-16 08:23 |  |  | Fair | No | This call belongs to trelawny
Outage | J.E.26.08.22992 | C001890139 | Swon Miller | St.James | Completed | Load_256619 | Rose Hall - 210 | 2026-08-16 08:11 | 2026-08-16 08:13 | 2026-08-16 08:39 | 2026-08-16 08:40 | 2026-08-16 09:01 | 2026-08-16 09:47 | 2026-08-16 10:00 | 2026-08-16 10:00 |  |  | Fair | No | Found customer meter burnt voltage found 117/116/234 disconnect customer from jps main voltage left 0.000
Non-Outage | J.E.26.08.23620 | C001890141 | Damion Reid |  | Completed |  |  | 2026-08-16 08:16 | 2026-08-16 08:17 | 2026-08-16 11:56 | 2026-08-16 11:56 | 2026-08-16 12:03 | 2026-08-16 12:10 | 2026-08-16 12:11 | 2026-08-16 12:11 | BrokenPole |  | Rains | No | Call related to one done at pike earlier
Outage | J.E.26.08.23094 | C001890143 | Collin Robinson | Portland | Completed | Load_572611 | Port Antonio - 310 | 2026-08-16 08:24 | 2026-08-16 08:25 | 2026-08-16 13:49 | 2026-08-16 13:50 | 2026-08-16 14:02 | 2026-08-16 14:27 | 2026-08-16 14:27 | 2026-08-16 14:27 |  |  | Rains | No | Repair broken #6 twisted and connect pothead Voltage reading 120v 120v 240v
Outage | J.E.26.08.23649 | C001890147 | Raymond Carr | St.Ann | Completed | Load_260661 | Upper White River - 110 | 2026-08-16 08:33 | 2026-08-16 08:33 | 2026-08-16 13:03 | 2026-08-16 13:03 | 2026-08-16 14:14 | 2026-08-16 02:07 | 2026-08-16 14:15 | 2026-08-16 14:15 |  |  | Fair | No | Several calls to contact number went unanswered.
Outage | J.E.26.08.23205 | C001890149 | Fitzroy Turner | KSAN | Completed | Load_256666 | Washington Blvd - 710 | 2026-08-16 08:44 | 2026-08-16 09:11 | 2026-08-16 11:41 | 2026-08-16 12:32 | 2026-08-16 12:45 | 2026-08-16 13:14 | 2026-08-16 13:16 | 2026-08-16 13:16 | BangingWires |  | Fair | No | Areas found without electricity supply.team carry work before
Outage | J.E.26.08.23567 | C001890148 | Rusean Allen | KSAS | Completed | Load_266429 | Up Park Camp - 510 | 2026-08-16 08:44 | 2026-08-16 09:07 | 2026-08-16 09:41 | 2026-08-16 09:41 | 2026-08-16 10:13 | 2026-08-16 10:28 | 2026-08-16 10:34 | 2026-08-16 10:34 | Fire |  | Fair | No | Found a 20 amps fuse Replace a 20 amps fuse
Outage | J.E.26.08.22999 | C001890150 | Edward Royal | KSAS | Completed | Load_267274 | Greenwich - 310 | 2026-08-16 08:45 | 2026-08-16 09:09 | 2026-08-16 11:21 | 2026-08-16 11:21 | 2026-08-16 11:21 | 2026-08-16 15:58 | 2026-08-16 15:58 | 2026-08-16 15:58 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Spliced and reconnected 3 pole span secondary phase using 250 ft 2 north conductor 3 perform 8 single bolt clamp
Outage | J.E.26.08.22571 | C001890154 | Edward Royal | KSAS | Completed | Load_262317 | Greenwich - 310 | 2026-08-16 08:46 | 2026-08-16 09:33 | 2026-08-16 17:34 | 2026-08-16 17:48 | 2026-08-16 17:48 | 2026-08-16 17:49 | 2026-08-16 17:49 | 2026-08-16 17:49 | TreeContact |  | Fair | No | Requesting secondary bushing crew with buckets truck required
Outage | J.E.26.08.22885 | C001890153 | Rusean Allen | KSAS | Completed | Load_243330 | Rockfort - 410 | 2026-08-16 08:46 | 2026-08-16 09:13 | 2026-08-16 10:55 | 2026-08-16 10:55 | 2026-08-16 11:39 | 2026-08-16 11:49 | 2026-08-16 11:49 | 2026-08-16 11:49 |  |  | Fair | No | Broken wire found at pole and pothead, wires were reconnected.
Outage | J.E.26.08.22997 | C001890151 | Fitzroy Turner | KSAS | Completed | Load_261811 | Hunts Bay - 810 | 2026-08-16 08:46 | 2026-08-16 09:35 | 2026-08-16 09:53 | 2026-08-16 11:31 | 2026-08-16 11:31 | 2026-08-16 11:31 | 2026-08-16 11:38 | 2026-08-16 11:38 |  |  | Fair | No | Found tree wire open secondary one phase cut down at the 100kva transformer pole use 70ft of 2/0 aluminum wire and one preform two one bolt clamps and one 4/0 to 2/0 ampact to carry out repair supply restored to the areas
Outage | J.E.26.08.22373 | C001890156 | Edward Royal | KSAN | Completed | Load_567701 | Washington Blvd - 310 | 2026-08-16 08:47 | 2026-08-16 09:31 | 2026-08-16 10:47 | 2026-08-16 10:47 | 2026-08-16 10:47 | 2026-08-16 11:08 | 2026-08-16 11:09 | 2026-08-16 11:09 |  |  | Fair | No | Spliced and reconnected secondary neutral using 2 single bolt clamp
Outage | J.E.26.08.21521 | C001890160 | Rusean Allen | KSAS | Completed | Load_238247 | Cane River - 310 | 2026-08-16 08:51 | 2026-08-16 08:58 | 2026-08-16 13:18 | 2026-08-16 13:19 | 2026-08-16 13:18 | 2026-08-16 13:18 | 2026-08-16 13:19 | 2026-08-16 13:19 |  |  | Fair | No | Premises okay
Outage | J.E.26.08.21630 | C001890159 | Rusean Allen | KSAS | Completed | Load_237946 | Cane River - 310 | 2026-08-16 08:51 | 2026-08-16 08:58 | 2026-08-16 11:49 | 2026-08-16 11:50 | 2026-08-16 12:24 | 2026-08-16 12:31 | 2026-08-16 12:32 | 2026-08-16 12:32 | BrokenWire |  | Fair | No | Broken service wire found at pole, wire was reconnected.
Outage | J.E.26.08.22406 | C001890161 | Edward Royal | KSAS | Completed | Load_239554 | Rockfort - 410 | 2026-08-16 08:55 | 2026-08-16 09:10 | 2026-08-16 15:58 | 2026-08-16 15:59 | 2026-08-16 15:58 | 2026-08-16 15:59 | 2026-08-16 15:59 | 2026-08-16 15:59 | BrokenWire |  | Fair | No | Premises found close unable to communicate with customer
Outage | J.E.26.08.23702 | C001890168 | Oshane Warren | St.Elizabeth | Completed | Load_266160 | Maggotty - 110 | 2026-08-16 09:06 | 2026-08-16 09:08 | 2026-08-16 10:49 | 2026-08-16 11:46 | 2026-08-16 13:55 | 2026-08-16 13:56 | 2026-08-16 14:01 | 2026-08-16 14:01 |  |  | Fair | No | Replace 15 amp junction fuse
Outage | J.E.26.08.22526 | C001890169 | Rusean Allen | KSAS | Completed | Load_250069 | Up Park Camp - 510 | 2026-08-16 09:13 | 2026-08-16 09:15 | 2026-08-16 10:35 | 2026-08-16 10:36 | 2026-08-16 10:53 | 2026-08-16 10:55 | 2026-08-16 10:55 | 2026-08-16 10:55 | BrokenWire |  | Fair | No | Remove service wire from premises To make area safe
Outage | J.E.26.08.23667 | C001890173 | Collin Robinson | Portland | Completed | Load_252368 | Port Antonio - 310 | 2026-08-16 09:24 | 2026-08-16 09:52 | 2026-08-16 19:11 | 2026-08-16 19:11 | 2026-08-16 20:26 | 2026-08-16 20:36 | 2026-08-16 20:36 | 2026-08-16 20:36 | BrokenWire |  | Rains | No | Information received from customer wen reach location that issue was resolved earlier today
Outage | J.E.26.08.22769 | C001890174 | Edward Royal | KSAS | Completed | Load_254544 | Hunts Bay - 310 | 2026-08-16 09:27 | 2026-08-16 09:30 | 2026-08-16 15:59 | 2026-08-16 16:00 | 2026-08-16 15:59 | 2026-08-16 16:01 | 2026-08-16 16:02 | 2026-08-16 16:02 |  |  | Fair | No | Meter not responding meter need to be check reffered field service box #EN 05704 pole#0019223
Outage | J.E.26.08.23715 | C001890175 | Damion Reid | Manchester | Completed | Load_239382 | Kendal - 210 | 2026-08-16 09:28 | 2026-08-16 09:33 | 2026-08-16 12:11 | 2026-08-16 12:11 | 2026-08-16 13:30 | 2026-08-16 14:14 | 2026-08-16 14:15 | 2026-08-16 14:15 |  |  | Fair | No | Remade burnt off phase jumper at secondary pole
Outage | J.E.26.08.23728 | C001890176 | Kenroy Dale | Manchester | Completed | Load_292889 | Spur Tree - 310 | 2026-08-16 09:28 | 2026-08-17 07:43 | 2026-08-17 10:22 | 2026-08-17 10:33 | 2026-08-17 11:29 | 2026-08-17 12:14 | 2026-08-17 12:16 | 2026-08-17 12:16 |  |  | Fair | No | Defective service wire found, service wire was replaced with approximately 60 feet of #6 triplex and 3 one bolt clamp voltage reading 114/115/229
Outage | J.E.26.08.23720 | C001890177 | Omar King | St.Ann | Completed | Load_264945 | Roaring River - 210 | 2026-08-16 09:29 | 2026-08-16 09:32 | 2026-08-16 11:24 | 2026-08-16 11:25 | 2026-08-16 12:19 | 2026-08-16 12:46 | 2026-08-16 12:46 | 2026-08-16 12:46 |  |  | Fair | No | Found 25 amp junction fuse blow cause by wind fuse has been replaced and customer now with supply.
Non-Outage | J.E.26.08.22511 | C001890179 | Edward Royal |  | Completed |  |  | 2026-08-16 09:31 | 2026-08-16 09:32 | 2026-08-16 16:10 | 2026-08-16 16:11 | 2026-08-16 16:11 | 2026-08-16 16:17 | 2026-08-16 16:19 | 2026-08-16 16:19 |  |  | Fair | No | New apartment with hexin meter need to be installed at premises reffered field service
Outage | J.E.26.08.23091 | C001890181 | Marlon Brown | Trelawny | Completed | Load_259864 | Greenwood - 210 | 2026-08-16 09:31 | 2026-08-16 15:05 | 2026-08-16 21:09 | 2026-08-16 21:10 | 2026-08-16 21:34 | 2026-08-16 21:45 | 2026-08-16 21:45 | 2026-08-16 21:45 |  |  | Fair | No | Found electricity in the area.
Outage | J.E.26.08.23223 | C001890180 | Andre Williams | Trelawny | Completed | Load_1001714 | Greenwood - 210 | 2026-08-16 09:31 | 2026-08-16 09:32 | 2026-08-16 12:46 | 2026-08-16 12:46 | 2026-08-16 13:51 | 2026-08-16 14:10 | 2026-08-16 14:10 | 2026-08-16 14:10 |  |  | Fair | No | Remake burnt off joint at Jps pole on #6 wire voltage 117+118=235
Outage | J.E.26.08.23708 | C001890178 | Andre Williams | Trelawny | Completed | Load_267431 | Duncans - 210 | 2026-08-16 09:31 | 2026-08-16 09:32 | 2026-08-16 10:45 | 2026-08-16 10:47 | 2026-08-16 12:09 | 2026-08-16 12:43 | 2026-08-16 12:43 | 2026-08-16 12:43 |  |  | Fair | No | Run 50 #6 twisted from Poe to pothead on customer 3 wire service voltage 116+116=232 premier now with supply
Outage | J.E.26.08.23738 | C001890182 | Omar King | St.Ann | Completed | Load_248606 | Roaring River - 210 | 2026-08-16 09:34 | 2026-08-16 09:35 | 2026-08-16 11:42 | 2026-08-16 12:47 | 2026-08-16 13:48 | 2026-08-16 13:49 | 2026-08-16 13:49 | 2026-08-16 13:49 |  |  | Fair | No | Found 25 KVA transformer fuse as been replaced customer is now with supply
Outage | J.E.26.08.22901 | C001890184 | Fitzroy Turner | KSAS | Completed | Load_289627 | Greenwich - 710 | 2026-08-16 09:36 | 2026-08-16 09:37 | 2026-08-16 11:41 | 2026-08-16 12:30 | 2026-08-16 12:30 | 2026-08-16 12:30 | 2026-08-16 12:31 | 2026-08-16 12:31 | BrokenWire |  | Fair | No | Please send email to field service department have issues resolved
Outage | J.E.26.08.23678 | C001890183 | Raymond Carr | St.Mary | Completed | Load_350076 | Oracabessa - 210 | 2026-08-16 09:36 | 2026-08-16 09:46 | 2026-08-16 10:27 | 2026-08-16 10:28 | 2026-08-16 10:34 | 2026-08-16 10:30 | 2026-08-16 10:38 | 2026-08-16 10:38 |  |  | Fair | No | No access to rammy system.
Non-Outage | J.E.26.08.23080 | C001890186 | Fitzroy Turner |  | Completed |  |  | 2026-08-16 09:37 | 2026-08-16 09:47 | 2026-08-16 11:41 | 2026-08-16 11:41 | 2026-08-16 11:41 | 2026-08-16 11:41 | 2026-08-16 11:50 | 2026-08-16 11:50 | Fire |  | Fair | No | Found tree wire open secondary phase cut down cause by illegal connections use 70ft 2/0 aluminum wire and and two one bolt clamps supply restored areas
Outage | J.E.26.08.23734 | C001890187 | Milton Charlton | KSAN | Completed | Load_257523 | Hope - 510 | 2026-08-16 09:37 | 2026-08-16 09:42 | 2026-08-16 10:08 | 2026-08-16 10:12 | 2026-08-16 11:28 | 2026-08-16 11:25 | 2026-08-16 11:34 | 2026-08-16 11:34 |  |  | Fair | No | Refused and reclosed 3 amps transformer switch atpole #0112952 using one 3 amps fuse.
Outage | J.E.26.08.23741 | C001890185 | Richard Samuda | Manchester | Completed | Load_243242 | Porus - 310 | 2026-08-16 09:37 | 2026-08-16 09:43 | 2026-08-16 11:08 | 2026-08-16 11:44 | 2026-08-16 12:03 | 2026-08-16 00:24 | 2026-08-16 12:24 | 2026-08-16 12:24 | Fire |  | Fair | No | Balance secondary neutral that was banging out with lower phase and carry out spot bushing refer call area needs extensive debushing
Outage | J.E.26.08.23385 | C001890189 | Dwayne Cohen | KSAS | Completed | Load_264109 | Duhaney - 310 | 2026-08-16 09:38 | 2026-08-16 09:43 | 2026-08-16 09:55 | 2026-08-16 09:55 | 2026-08-16 10:21 | 2026-08-16 10:22 | 2026-08-16 10:22 | 2026-08-16 10:22 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.23547 | C001890188 | Dwayne Cohen | KSAS | Completed | Load_258431 | Duhaney - 310 | 2026-08-16 09:38 | 2026-08-16 09:43 | 2026-08-16 10:22 | 2026-08-16 10:23 | 2026-08-16 10:52 | 2026-08-16 11:03 | 2026-08-16 11:04 | 2026-08-16 11:04 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.23397 | C001890190 | Elvis Trowers | KSAN | Completed | Load_242528 | West Kings House - 310 | 2026-08-16 09:39 | 2026-08-16 09:44 | 2026-08-16 10:00 | 2026-08-16 10:01 | 2026-08-16 10:20 | 2026-08-16 10:20 | 2026-08-16 10:24 | 2026-08-16 10:24 |  |  | Fair | No | Reset customer circuit breaker found tripped. Readings at meter socket 117-118-236 volts.
Outage | J.E.26.08.23560 | C001890191 | Elvis Trowers | KSAS | Completed | Load_557433 | Up Park Camp - 410 | 2026-08-16 09:39 | 2026-08-16 09:44 | 2026-08-16 10:35 | 2026-08-16 10:36 | 2026-08-16 10:48 | 2026-08-16 10:55 | 2026-08-16 10:54 | 2026-08-16 10:54 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.22665 | C001890192 | Elvis Trowers | KSAN | Completed | Load_254729 | Washington Blvd - 610 | 2026-08-16 09:41 | 2026-08-16 09:45 | 2026-08-16 10:24 | 2026-08-16 10:25 | 2026-08-16 10:28 | 2026-08-16 10:35 | 2026-08-16 10:35 | 2026-08-16 10:35 |  |  | Fair | No | Unable to locate customer by telephone. Number on the report going straight to voicemail.
Outage | J.E.26.08.23023 | C001890193 | Milton Charlton | KSAN | Completed | Load_266979 | Hope - 510 | 2026-08-16 09:41 | 2026-08-16 09:49 | 2026-08-16 13:34 | 2026-08-16 13:35 | 2026-08-16 13:38 | 2026-08-16 13:40 | 2026-08-16 13:39 | 2026-08-16 13:39 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.23743 | C001890194 | Romaine Roberts | St.Mary | Completed | Load_249551 | Annotto Bay - 310 | 2026-08-16 09:43 | 2026-08-16 09:45 | 2026-08-16 12:41 | 2026-08-16 12:41 | 2026-08-16 12:41 | 2026-08-16 12:50 | 2026-08-16 12:52 | 2026-08-16 12:52 |  |  | Fair | No | Found junction fuse blown patrol line nothing found replace 50 amp to restore supply no pole number
Outage | J.E.26.08.23685 | C001890196 | Donald Cunningham | St.Catherine | Completed | Load_247630 | Tredegar - 510 | 2026-08-16 09:45 | 2026-08-16 09:47 | 2026-08-16 09:53 | 2026-08-16 09:54 | 2026-08-16 12:02 | 2026-08-16 12:16 | 2026-08-16 12:17 | 2026-08-16 12:17 |  |  | Fair | No | 😋defective meter need to replace refer to field service
Outage | J.E.26.08.23744 | C001890197 | Roxroy Needham | St.Ann | Completed | Load_256899 | Cardiff Hall - 310 | 2026-08-16 09:46 | 2026-08-16 09:47 | 2026-08-16 10:15 | 2026-08-16 10:16 | 2026-08-16 12:05 | 2026-08-16 12:05 | 2026-08-16 12:12 | 2026-08-16 12:12 | BrokenWire | Y | Fair | No | Remake a span of secondary line and retention a span of neutral used 4 pg clamp and reset a 10 KVA transformer at pole
Outage | J.E.26.08.23167 | C001890199 | Christopher Edwards | KSAN | Completed | Load_579174 | Constant Spring - 210 | 2026-08-16 09:47 | 2026-08-16 09:49 | 2026-08-16 09:54 | 2026-08-16 10:12 | 2026-08-16 10:11 | 2026-08-16 11:05 | 2026-08-16 11:06 | 2026-08-16 11:06 |  |  | Fair | No | Metering department was contacted and meter was turned onHowever customer has a faulty breaker on the premises Customer was advised to get electrician to fix breaker
Outage | J.E.26.08.23718 | C001890200 | Hartley Chin | Clarendon | Completed | Load_247007 | Parnassus - 210 | 2026-08-16 09:51 | 2026-08-16 10:06 | 2026-08-16 12:31 | 2026-08-16 12:36 | 2026-08-16 13:37 | 2026-08-16 13:58 | 2026-08-16 13:59 | 2026-08-16 13:59 | Fire |  | Fair | No | Found blown 25 KVA due to banging wires. Remove banging wire and refused
Non-Outage | J.E.26.08.20855 | C001890203 | Marlon Authors | St.Elizabeth | Completed | Load_291985 | Maggotty - 210 | 2026-08-16 09:53 | 2026-08-16 14:55 | 2026-08-16 17:02 | 2026-08-16 17:02 | 2026-08-16 17:02 | 2026-08-16 17:33 | 2026-08-16 17:34 | 2026-08-16 17:34 |  |  | Fair | No | Supply checked and found low voltage rdg 104v,105v and cross phased 209 volts. Isolate and close 25 kva transformer circuit no pole #, to tap up same to tap 5. Supply leave working ok rdg 111v,112v and cross phased 223 volts
Non-Outage | J.E.26.08.22412 | C001890202 | Raheem Ricketts | St.Elizabeth | Completed | Load_250102 | Maggotty - 210 | 2026-08-16 09:53 | 2026-08-16 09:54 | 2026-08-16 10:00 | 2026-08-16 11:10 | 2026-08-16 11:54 | 2026-08-16 12:41 | 2026-08-16 12:42 | 2026-08-16 12:42 |  |  | Fair | No | Isolate 25kva to Splice and retention 40ft of secondary neutral using 3clamps 1 ;#2preform an reclosed 25kva
Non-Outage | J.E.26.08.22854 | C001890201 | Raheem Ricketts | St.Elizabeth | Completed | Load_413091 | Maggotty - 210 | 2026-08-16 09:53 | 2026-08-16 09:54 | 2026-08-16 10:00 | 2026-08-16 10:34 | 2026-08-16 11:03 | 2026-08-16 11:06 | 2026-08-16 11:06 | 2026-08-16 11:06 |  |  | Fair | No | Check and found customer experiencing an internal problem
Outage | J.E.26.08.23809 | C001890206 | Marlon Authors | St.Elizabeth | Completed | Load_263142 | Maggotty - 110 | 2026-08-16 10:12 | 2026-08-16 10:13 | 2026-08-16 10:26 | 2026-08-16 10:26 | 2026-08-16 11:22 | 2026-08-16 11:59 | 2026-08-16 11:59 | 2026-08-16 11:59 |  |  | Fair | No | Patrol and found clear. Replace one blown 20 amp junction fuse no pole #. Restored supply okay
Outage | J.E.26.08.23822 | C001890207 | Roxroy Needham | St.Ann | Completed | Load_247889 | Cardiff Hall - 310 | 2026-08-16 10:20 | 2026-08-16 10:21 | 2026-08-16 12:12 | 2026-08-16 12:13 | 2026-08-16 13:06 | 2026-08-16 13:08 | 2026-08-16 13:09 | 2026-08-16 13:09 |  | Y | Fair | No | Reset a 25 KVA transformer at pole
Outage | J.E.26.08.23841 | C001890208 | Marlon Authors | St.Elizabeth | Completed | Load_247900 | Maggotty - 110 | 2026-08-16 10:41 | 2026-08-16 10:42 | 2026-08-16 14:12 | 2026-08-16 14:12 | 2026-08-16 14:22 | 2026-08-16 14:37 | 2026-08-16 14:37 | 2026-08-16 14:37 | Fire |  | Fair | No | Supply checked and found lose one bolt clamp at pole. Replace same and supply leave working ok rdg 114 volts
Outage | J.E.26.08.23861 | C001890211 | Nickolas Rodriques | St.Catherine | Completed | Load_251980 | Twickenham - 210 | 2026-08-16 10:59 | 2026-08-16 11:00 | 2026-08-16 11:42 | 2026-08-16 11:52 | 2026-08-16 12:20 | 2026-08-16 12:56 | 2026-08-16 13:02 | 2026-08-16 13:02 |  |  | Fair | No | Checked and found customer without electricity caused by corroded pothead. Repaired by replacing two one-bolt clamps, current reading (114). Customer confirmed that all is well now.
Outage | J.E.26.08.23885 | C001890213 | Richard Samuda | Manchester | Completed | Load_261236 | Porus - 310 | 2026-08-16 11:21 | 2026-08-16 11:29 | 2026-08-16 12:24 | 2026-08-16 12:25 | 2026-08-16 12:43 | 2026-08-16 13:00 | 2026-08-16 13:00 | 2026-08-16 13:00 | Fire |  | Fair | No | Customer meter pole is unable reconnect customer because meter pole is damaged advised customer to fix meter voltage 114
Outage | J.E.26.08.23483 | C001890214 | Neville Spencer | Clarendon | Completed | Load_261428 | May Pen - 210 | 2026-08-16 11:22 | 2026-08-16 11:32 | 2026-08-16 11:43 | 2026-08-16 11:43 | 2026-08-16 12:58 | 2026-08-16 12:58 | 2026-08-16 13:09 | 2026-08-16 13:09 | Fire |  | Fair | No | Found burnt off secondary phase at pole # 146098.Open 10 kva xmfr # 0125893 repair jumper used 2, clamps voltage reading 103 108 211 Burnt 25 kva xmfr at pole # 0123865 need to replaced tp improve voltage.
Outage | J.E.26.08.23661 | C001890215 | Hartley Chin | Clarendon | Completed | Load_270079 | Monymusk - 410 | 2026-08-16 11:32 | 2026-08-16 11:33 | 2026-08-16 16:14 | 2026-08-16 16:15 | 2026-08-16 17:14 | 2026-08-16 17:15 | 2026-08-16 17:21 | 2026-08-16 17:21 |  |  | Fair | No | Found burnt # 6 service wire caused by bush fire. Replaced service conductor.
Outage | J.E.26.08.23863 | C001890216 | Daniel Francis | St.Ann | Completed | Load_261767 | Roaring River - 210 | 2026-08-16 11:34 | 2026-08-16 16:53 | 2026-08-16 21:24 | 2026-08-16 21:24 | 2026-08-16 21:48 | 2026-08-16 22:32 | 2026-08-16 22:35 | 2026-08-16 22:35 |  |  | Fair | No | Patrol and renew transformer fuse 5amp 50kva
Outage | J.E.26.08.23882 | C001890217 | Tyrese Williams | St.Ann | Completed | Load_264808 | Cardiff Hall - 310 | 2026-08-16 11:37 | 2026-08-16 15:33 | 2026-08-16 15:38 | 2026-08-16 17:57 | 2026-08-16 18:24 | 2026-08-16 18:24 | 2026-08-16 18:24 | 2026-08-16 18:24 |  |  | Fair | No | Refer to field service team customer meter is in hexing box
Outage | J.E.26.08.23432 | C001890219 | Oshane Warren | Westmoreland | Completed | Load_257081 | Paradise - 210 | 2026-08-16 11:42 | 2026-08-16 11:44 | 2026-08-16 14:06 | 2026-08-16 14:06 | 2026-08-16 14:06 | 2026-08-16 14:06 | 2026-08-16 14:06 | 2026-08-16 14:06 |  |  | Fair | No | Customer states that power was restored
Outage | J.E.26.08.23949 | C001890221 | Oshane Warren | Westmoreland | Completed | Load_569998 | Paradise - 210 | 2026-08-16 11:43 | 2026-08-16 11:44 | 2026-08-16 14:24 | 2026-08-16 14:24 | 2026-08-16 18:46 | 2026-08-16 19:03 | 2026-08-16 19:10 | 2026-08-16 19:10 |  |  | Rains | No | Lcb6-725 trip carry out patrols and found lightning arrester on a cat bank Defective disconnect arrester and cat bank from line section and Reclose lcb6-725
Outage | J.E.26.08.23883 | C001890224 | Rusean Allen | KSAS | Completed | Load_252961 | Cane River - 310 | 2026-08-16 11:45 | 2026-08-16 11:48 | 2026-08-16 12:32 | 2026-08-16 12:32 | 2026-08-16 12:50 | 2026-08-16 13:18 | 2026-08-16 13:18 | 2026-08-16 13:18 |  |  | Fair | No | 1x 3amp fuse found 1x 3amp fuse replaced.
Outage | J.E.26.08.23894 | C001890225 | Collin Robinson | Portland | Completed | Load_353467 | Port Antonio - 410 | 2026-08-16 11:47 | 2026-08-16 11:49 | 2026-08-16 15:11 | 2026-08-16 15:12 | 2026-08-16 15:39 | 2026-08-16 15:41 | 2026-08-16 15:42 | 2026-08-16 15:42 | BrokenWire |  | Rains | No | Unable to locate customer
Non-Outage | J.E.26.08.23986 | C001890227 | Raheem Ricketts |  | Completed |  |  | 2026-08-16 12:05 | 2026-08-16 12:07 | 2026-08-16 12:43 | 2026-08-16 12:43 | 2026-08-16 14:15 | 2026-08-16 15:31 | 2026-08-16 15:31 | 2026-08-16 15:31 | Fire |  | Fair | No | Retention secondary twisted wire using 3clamps
Non-Outage | J.E.26.08.23992 | C001890228 | Richard Samuda |  | Completed |  |  | 2026-08-16 12:05 | 2026-08-16 12:07 | 2026-08-16 13:05 | 2026-08-16 13:05 | 2026-08-16 13:29 | 2026-08-16 02:34 | 2026-08-16 14:34 | 2026-08-16 14:34 | BrokenWire |  | Rains | No | Remake joint at customer pothead that was burnt off using 1 one bolt clamp causing customer to experience low voltage voltage 116, 115 231
Outage | J.E.26.08.24016 | C001890229 | Marlon Authors | St.Elizabeth | Completed | Load_251773 | Maggotty - 210 | 2026-08-16 12:17 | 2026-08-16 14:55 | 2026-08-16 16:06 | 2026-08-16 16:07 | 2026-08-16 16:06 | 2026-08-16 16:12 | 2026-08-16 16:12 | 2026-08-16 16:12 |  |  | Rains | No | Customer said supply was restored
Outage | J.E.26.08.23814 | C001890230 | Rusean Allen | KSAS | Completed | Load_573563 | Cane River - 410 | 2026-08-16 12:25 | 2026-08-16 12:48 | 2026-08-16 16:18 | 2026-08-16 16:18 | 2026-08-16 16:35 | 2026-08-16 16:36 | 2026-08-16 16:36 | 2026-08-16 16:36 |  |  | Fair | No | Hexing failure, meter was reconnected by customer service.
Non-Outage | J.E.26.08.22271 | C001890231 | Dwayne Cohen | KSAN | Completed | Load_252805 | Hope - 310 | 2026-08-16 12:27 | 2026-08-16 12:28 | 2026-08-16 12:41 | 2026-08-16 15:24 | 2026-08-16 15:23 | 2026-08-16 15:24 | 2026-08-16 15:24 | 2026-08-16 15:24 |  |  | Fair | No | Premises closed
Outage | J.E.26.08.23864 | C001890233 | Fitzroy Turner | KSAS | Completed | Load_245974 | Hunts Bay - 810 | 2026-08-16 12:31 | 2026-08-16 12:45 | 2026-08-16 13:31 | 2026-08-16 13:31 | 2026-08-16 13:53 | 2026-08-16 13:54 | 2026-08-16 13:54 | 2026-08-16 13:54 |  |  | Fair | No | Customer supply restored with the help of the call center
Outage | J.E.26.08.24006 | C001890232 | Fitzroy Turner | KSAS | Completed | Load_575567 | Duhaney - 410 | 2026-08-16 12:31 | 2026-08-16 12:45 | 2026-08-16 13:31 | 2026-08-16 13:57 | 2026-08-16 14:02 | 2026-08-16 14:03 | 2026-08-16 14:03 | 2026-08-16 14:03 |  |  | Fair | No | Customer premises close at this time
Outage | J.E.26.08.24040 | C001890235 | Wayne Dillion | St.Elizabeth | Completed | Load_246006 | Maggotty - 110 | 2026-08-16 12:46 | 2026-08-16 14:54 | 2026-08-16 18:32 | 2026-08-16 18:33 | 2026-08-16 18:32 | 2026-08-16 18:31 | 2026-08-16 18:33 | 2026-08-16 18:33 |  |  | Fair | No | Supply was restored to the area.
Outage | J.E.26.08.24042 | C001890234 | Wayne Dillion | St.Elizabeth | Completed | Load_256896 | Maggotty - 110 | 2026-08-16 12:46 | 2026-08-16 14:54 | 2026-08-16 18:35 | 2026-08-16 18:35 | 2026-08-16 18:35 | 2026-08-16 18:35 | 2026-08-16 18:36 | 2026-08-16 18:36 |  |  | Fair | No | Supply was restored to the area.
Outage | J.E.26.08.24051 | C001890239 | Roxroy Needham | St.Ann | Completed | Load_239011 | Cardiff Hall - 210 | 2026-08-16 13:01 | 2026-08-16 13:02 | 2026-08-16 13:09 | 2026-08-16 13:10 | 2026-08-16 14:27 | 2026-08-16 14:50 | 2026-08-16 14:45 | 2026-08-16 14:45 |  |  | Fair | No | Retention a span of neural and replace 2 30 amps junction fuse at pole
Outage | J.E.26.08.23998 | C001890244 | Milton Charlton | KSAN | Completed | Load_245329 | Hope - 510 | 2026-08-16 13:25 | 2026-08-16 13:28 | 2026-08-16 15:23 | 2026-08-16 15:24 | 2026-08-16 15:57 | 2026-08-16 15:55 | 2026-08-16 16:00 | 2026-08-16 16:00 |  |  | Fair | No | Refused and reclosed 10 amps junction switch at pole #041094 using one 10 amps fuse.
Outage | J.E.26.08.24081 | C001890243 | Milton Charlton | KSAN | Completed | Load_259693 | Hope - 510 | 2026-08-16 13:25 | 2026-08-16 13:28 | 2026-08-16 13:40 | 2026-08-16 13:40 | 2026-08-16 15:17 | 2026-08-16 15:20 | 2026-08-16 15:23 | 2026-08-16 15:23 | BrokenPole |  | Fair | No | Big Jackfruit tree fell 2/0 twisted secondary on 30ft wooden pole and break pole in several pieces. Need to replace pole. Isolate 25 kva transformer at pole#0119052. About 25 customers out of supply.
Outage | J.E.26.08.24072 | C001890245 | Andre Smith | KSAS | Completed | Load_257815 | Up Park Camp - 410 | 2026-08-16 13:27 | 2026-08-16 16:57 | 2026-08-16 19:17 | 2026-08-16 19:18 | 2026-08-16 19:45 | 2026-08-16 20:14 | 2026-08-16 20:15 | 2026-08-16 20:15 |  |  | Fair | No | Premises found okay supply restored already
Outage | J.E.26.08.24069 | C001890246 | Romeo Brissett | St.James | Completed | Load_262522 | Bogue - 510 | 2026-08-16 13:29 | 2026-08-16 13:30 | 2026-08-16 13:46 | 2026-08-16 13:47 | 2026-08-16 14:38 | 2026-08-16 17:38 | 2026-08-16 18:12 | 2026-08-16 18:12 | BrokenPole |  | Fair | No | Isolated (1)25KVA transformer, removed illegal connections, removed secondary from defective pole and attached secondary to new pole. Used 20ft of #2, (3)#2 preformed and 4 clamps.
Outage | J.E.26.08.24019 | C001890247 | Marlon Brown | Trelawny | Completed | Load_241035 | Greenwood - 210 | 2026-08-16 13:30 | 2026-08-16 15:05 | 2026-08-16 21:45 | 2026-08-16 21:46 | 2026-08-16 22:12 | 2026-08-16 22:27 | 2026-08-16 22:27 | 2026-08-16 22:27 |  |  | Fair | No | Found ok, area has electricity.
Outage | J.E.26.08.24076 | C001890248 | Stephen Taylor | St.Thomas | Completed | Load_577217 | Good Year - 210 | 2026-08-16 13:31 | 2026-08-16 13:36 | 2026-08-16 18:19 | 2026-08-16 18:19 | 2026-08-16 18:19 | 2026-08-16 18:19 | 2026-08-16 18:20 | 2026-08-16 18:20 | Fire |  | Fair | No | Patrol area and power is in the area but several calls to single customer and no one answering the phone need more information to locate customer
Outage | J.E.26.08.24098 | C001890251 | Collin Robinson | Portland | Completed | Load_267378 | Port Antonio - 310 | 2026-08-16 13:45 | 2026-08-16 13:45 | 2026-08-16 14:38 | 2026-08-16 14:39 | 2026-08-16 14:54 | 2026-08-16 15:06 | 2026-08-16 15:09 | 2026-08-16 15:09 |  |  | Rains | No | Replace 20 amps junction
Outage | J.E.26.08.23859 | C001890252 | Marlon Brown | Trelawny | Completed | Load_258152 | Duncans - 210 | 2026-08-16 13:58 | 2026-08-16 15:05 | 2026-08-16 15:28 | 2026-08-16 15:29 | 2026-08-16 16:14 | 2026-08-16 16:39 | 2026-08-16 16:39 | 2026-08-16 16:39 | BrokenWire |  | Fair | No | Refer 10amps junction fuse.
Outage | J.E.26.08.24126 | C001890253 | Romeo Brissett | St.James | Completed | Load_243133 | Bogue - 610 | 2026-08-16 13:58 | 2026-08-17 08:44 | 2026-08-17 10:03 | 2026-08-17 10:03 | 2026-08-17 10:56 | 2026-08-17 11:48 | 2026-08-17 11:51 | 2026-08-17 11:51 |  |  | Fair | No | Cut and removed vegetation, replaced (1)10amps junction fuse.
Outage | J.E.26.08.24062 | C001890256 | Marlon Authors | St.Elizabeth | Completed | Load_240670 | Maggotty - 210 | 2026-08-16 14:35 | 2026-08-16 15:49 | 2026-08-16 18:02 | 2026-08-16 18:03 | 2026-08-16 18:02 | 2026-08-16 18:04 | 2026-08-16 18:04 | 2026-08-16 18:04 |  |  | Fair | No | Customer said supply was restored
Outage | J.E.26.08.24113 | C001890255 | Wayne Dillion | St.Elizabeth | Completed | Load_249683 | Maggotty - 110 | 2026-08-16 14:35 | 2026-08-16 14:53 | 2026-08-16 15:51 | 2026-08-16 15:51 | 2026-08-16 17:29 | 2026-08-16 18:25 | 2026-08-16 18:26 | 2026-08-16 18:26 |  |  | Fair | No | Patrol and found one blown 30amp junction fuse no pole # and also the fuse holder is burnt up. Replace fuse and fuse holder and supply restored okay.
Outage | J.E.26.08.24516 | C001890258 | Wan Carlos Scarlett | Portmore | Completed | Load_267254 | Naggo Head - 610 | 2026-08-16 14:43 | 2026-08-16 19:44 | 2026-08-17 11:34 | 2026-08-17 11:35 | 2026-08-17 12:10 | 2026-08-17 12:11 | 2026-08-17 12:13 | 2026-08-17 12:13 | Fire |  | Fair | No | Reach at location did not see any signs of any fire premises found ok
Outage | J.E.26.08.24504 | C001890259 | Swon Miller | St.James | Completed | Load_574885 | Rose Hall - 210 | 2026-08-16 14:44 | 2026-08-16 14:45 | 2026-08-16 15:01 | 2026-08-16 15:06 | 2026-08-16 15:06 | 2026-08-25 03:28 | 2026-08-16 15:30 | 2026-08-16 15:30 | BrokenWire |  | Fair | No | Isolate 3,25 amp junction fuse to facilitate repairs at the royal Caribbean sea.cay primary line was isolated and tag at 3:12 pm
Non-Outage | J.E.26.08.23431 | C001890260 | Lancelot Brown |  | Completed |  |  | 2026-08-16 14:50 | 2026-08-16 14:50 | 2026-08-16 15:04 | 2026-08-16 15:06 | 2026-08-16 15:42 | 2026-08-16 15:43 | 2026-08-16 15:44 | 2026-08-16 15:44 |  |  | Fair | No | Remake corroded joint at pothead used three connectors vl at meter socket 110-112-222 supply restore
Outage | J.E.26.08.24553 | C001890261 | Richard Samuda | Manchester | Completed | Load_260536 | Spur Tree - 210 | 2026-08-16 14:52 | 2026-08-16 14:56 | 2026-08-16 22:01 | 2026-08-16 22:02 | 2026-08-16 22:19 | 2026-08-16 22:30 | 2026-08-16 22:30 | 2026-08-16 22:30 | BrokenWire |  | Fair | No | Splice and reconnected customer service wire using 4ft of service neutral and one 1bolt clamp voltage 118 116 234
Outage | J.E.26.08.24563 | C001890262 | Richard Samuda | Manchester | Completed | Load_270074 | Spur Tree - 310 | 2026-08-16 14:56 | 2026-08-16 14:57 | 2026-08-16 18:39 | 2026-08-16 18:39 | 2026-08-16 18:59 | 2026-08-16 20:50 | 2026-08-16 20:51 | 2026-08-16 20:51 | BrokenWire |  | Fair | No | Splice and reconnected customer two span secondary neutral wire that was broken causing customer to experience low voltage using 6ft number 6 allium wire and 1 1bolt clamps
Outage | J.E.26.08.24528 | C001890263 | Ricky Hall | St.Catherine | Completed | Load_253496 | New Michelton - 210 | 2026-08-16 15:00 | 2026-08-16 15:02 | 2026-08-16 15:43 | 2026-08-16 15:48 | 2026-08-16 17:44 | 2026-08-16 19:09 | 2026-08-16 19:10 | 2026-08-16 19:10 | Fire |  | SevereWind | No | Splice and retention broken secondary lines use 2 automatic splice 2 clamps 70’#2aa(1)2amp fuse 25 kva xfmr
Non-Outage | J.E.26.08.24565 | C001890267 | Edward Royal |  | Completed |  |  | 2026-08-16 15:04 | 2026-08-16 15:09 | 2026-08-16 17:34 | 2026-08-16 17:59 | 2026-08-16 17:58 | 2026-08-16 17:59 | 2026-08-16 17:59 | 2026-08-16 17:59 | Fire |  | Fair | No | Call related
Outage | J.E.26.08.23825 | C001890265 | Elvis Trowers | KSAS | Completed | Load_239090 | Up Park Camp - 310 | 2026-08-16 15:04 | 2026-08-16 15:11 | 2026-08-16 15:39 | 2026-08-16 15:40 | 2026-08-16 16:14 | 2026-08-16 16:15 | 2026-08-16 16:32 | 2026-08-16 16:32 |  |  | Fair | No | Reset customer circuit breaker found tripped.
Outage | J.E.26.08.24602 | C001890266 | Rusean Allen | KSAS | Completed | Load_1003959 | Cane River - 310 | 2026-08-16 15:04 | 2026-08-16 15:08 | 2026-08-16 16:36 | 2026-08-16 16:37 | 2026-08-16 16:51 | 2026-08-16 16:55 | 2026-08-16 16:56 | 2026-08-16 16:56 | BrokenPole |  | Fair | No | Broken 30ft pole containing open secondary wires and streetlight located in apartment complex needs to be changed, refer to maintenance department
Outage | J.E.26.08.24104 | C001890269 | Edward Royal | KSAS | Completed | Load_254508 | Hunts Bay - 310 | 2026-08-16 15:05 | 2026-08-16 15:10 | 2026-08-16 16:30 | 2026-08-16 16:31 | 2026-08-16 17:09 | 2026-08-16 17:10 | 2026-08-16 17:11 | 2026-08-16 17:11 |  |  | Fair | No | Spliced and reconnected service phase using 2 single bolt clamp
Outage | J.E.26.08.24633 | C001890270 | Rusean Allen | KSAS | Completed | Load_1002691 | Cane River - 410 | 2026-08-16 15:05 | 2026-08-16 15:07 | 2026-08-16 15:23 | 2026-08-16 15:23 | 2026-08-16 16:07 | 2026-08-16 16:17 | 2026-08-16 16:17 | 2026-08-16 16:17 |  |  | Fair | No | Broken service wire found at pole, wire was reconnected.
Outage | J.E.26.08.22903 | C001890273 | Stephen Taylor | St.Thomas | Completed | Load_270128 | Good Year - 110 | 2026-08-16 15:07 | 2026-08-16 15:13 | 2026-08-16 18:27 | 2026-08-16 18:27 | 2026-08-16 20:03 | 2026-08-16 20:03 | 2026-08-16 20:08 | 2026-08-16 20:08 | Fire |  | Fair | No | Spice and retention secondary line and close up 25 kva transformer put back 95 % of customer with power 5 % with out…bushing needs to done before power restored to customer
Outage | J.E.26.08.24469 | C001890272 | Stephen Taylor | St.Thomas | Completed | Load_253489 | Good Year - 210 | 2026-08-16 15:07 | 2026-08-16 15:13 | 2026-08-16 18:22 | 2026-08-16 18:22 | 2026-08-16 18:24 | 2026-08-16 18:24 | 2026-08-16 18:25 | 2026-08-16 18:25 | Fire |  | Fair | No | Patrol the area nothing found in the area
Outage | J.E.26.08.24646 | C001890274 | Stephen Taylor | St.Thomas | Completed | Load_247744 | Good Year - 210 | 2026-08-16 15:11 | 2026-08-16 15:13 | 2026-08-16 18:16 | 2026-08-16 18:17 | 2026-08-16 18:16 | 2026-08-16 18:16 | 2026-08-16 18:17 | 2026-08-16 18:17 |  |  | Fair | No | Check with customer and customer said power is back now and okay
Outage | J.E.26.08.24647 | C001890277 | Wayne Dillion | St.Elizabeth | Completed | Load_258971 | Maggotty - 110 | 2026-08-16 15:24 | 2026-08-16 15:27 | 2026-08-16 21:04 | 2026-08-16 21:05 | 2026-08-16 21:04 | 2026-08-16 21:07 | 2026-08-16 21:07 | 2026-08-16 21:07 |  |  | Fair | No | Please refer this call to the field service department to replace a meter that is missing.
Outage | J.E.26.08.23642 | C001890279 | Raymond Carr | St.Ann | Completed | Load_239913 | Upper White River - 110 | 2026-08-16 15:28 | 2026-08-16 16:12 | 2026-08-16 18:07 | 2026-08-16 18:07 | 2026-08-16 18:20 | 2026-08-16 18:31 | 2026-08-16 18:33 | 2026-08-16 18:33 |  |  | Fair | No | Blown junction fuse found at pole number 571234, line patrol and found okay, however tree was suspected. A 10 amp fuse was used to renew supply was restored.
Outage | J.E.26.08.24125 | C001890280 | Raymond Carr | St.Ann | Completed | Load_247813 | Upper White River - 110 | 2026-08-16 15:29 | 2026-08-16 16:12 | 2026-08-16 18:34 | 2026-08-16 18:34 | 2026-08-16 18:34 | 2026-08-16 18:28 | 2026-08-16 18:35 | 2026-08-16 18:35 |  |  | Fair | No | Supply was restored.
Outage | J.E.26.08.23910 | C001890281 | Lancelot Brown | Westmoreland | Completed | Load_263330 | Paradise - 210 | 2026-08-16 15:31 | 2026-08-16 15:32 | 2026-08-16 15:44 | 2026-08-16 15:45 | 2026-08-16 18:25 | 2026-08-16 18:26 | 2026-08-16 18:27 | 2026-08-16 18:27 |  |  | Fair | No | This call was pass on to westmoreland crew
Outage | J.E.26.08.24117 | C001890283 | Tyrese Williams | St.Ann | Completed | Load_253129 | Cardiff Hall - 310 | 2026-08-16 15:33 | 2026-08-16 15:35 | 2026-08-16 15:38 | 2026-08-16 20:35 | 2026-08-16 20:44 | 2026-08-16 20:32 | 2026-08-16 20:46 | 2026-08-16 20:46 |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.08.24615 | C001890284 | Tyrese Williams | St.Ann | Completed | Load_252576 | Cardiff Hall - 310 | 2026-08-16 15:33 | 2026-08-16 15:35 | 2026-08-16 15:38 | 2026-08-16 19:09 | 2026-08-16 20:04 | 2026-08-16 20:31 | 2026-08-16 20:31 | 2026-08-16 20:31 | BrokenWire |  | Fair | No | Replace a 20amp junction fuse at pole
Outage | J.E.26.08.24701 | C001890285 | Tyrese Williams | St.Ann | Completed | Load_267528 | Cardiff Hall - 310 | 2026-08-16 15:33 | 2026-08-16 15:35 | 2026-08-16 15:38 | 2026-08-16 17:43 | 2026-08-16 17:43 | 2026-08-16 17:43 | 2026-08-16 17:44 | 2026-08-16 17:44 |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.08.24710 | C001890286 | Tyrese Williams | St.Ann | Completed | Load_245428 | Cardiff Hall - 310 | 2026-08-16 15:33 | 2026-08-16 15:35 | 2026-08-16 15:38 | 2026-08-16 17:15 | 2026-08-16 17:15 | 2026-08-16 17:27 | 2026-08-16 17:27 | 2026-08-16 17:27 |  |  | Fair | No | Replace a 40amp junction fuse at pole
Outage | J.E.26.08.24721 | C001890287 | Tyrese Williams | St.Ann | Completed | Load_247889 | Cardiff Hall - 310 | 2026-08-16 15:34 | 2026-08-16 15:35 | 2026-08-16 15:38 | 2026-08-16 20:31 | 2026-08-16 20:33 | 2026-08-16 20:34 | 2026-08-16 20:34 | 2026-08-16 20:34 |  |  | Fair | No | Premises found ok Call related to the 20 amp junction fuse
Outage | J.E.26.08.24757 | C001890288 | Tyrese Williams | St.Ann | Completed | Load_266323 | Cardiff Hall - 310 | 2026-08-16 15:34 | 2026-08-16 15:36 | 2026-08-16 15:38 | 2026-08-16 17:37 | 2026-08-16 17:41 | 2026-08-16 17:43 | 2026-08-16 17:43 | 2026-08-16 17:43 |  |  | Fair | No | Premise Found ok call related to 40amp junction fuse at pole
Outage | J.E.26.08.24100 | C001890289 | Daniel Francis | St.Ann | Completed | Load_237805 | Ocho Rios - 310 | 2026-08-16 15:36 | 2026-08-16 15:39 | 2026-08-16 17:09 | 2026-08-16 17:09 | 2026-08-16 17:13 | 2026-08-16 18:03 | 2026-08-16 18:03 | 2026-08-16 18:03 |  |  | Fair | No | Found junction blown at 0024426 one 40 amp. Also at Milford and Shaw pk entrance two 25amp also at0098817 two 15 amp
Outage | J.E.26.08.24617 | C001890290 | Daniel Francis | St.Ann | Completed | Load_248940 | Ocho Rios - 310 | 2026-08-16 15:36 | 2026-08-16 15:39 | 2026-08-16 18:03 | 2026-08-16 18:04 | 2026-08-16 18:22 | 2026-08-16 20:23 | 2026-08-16 20:26 | 2026-08-16 20:26 |  |  | Fair | No | Cut and remove tree limb from primary line area not accessible by vehicle
Non-Outage | J.E.26.08.24773 | C001890294 | Oshane Warren | Westmoreland | Completed | Load_292902 | Paradise - 110 | 2026-08-16 15:37 | 2026-08-16 15:44 | 2026-08-16 21:27 | 2026-08-16 21:28 | 2026-08-16 21:28 | 2026-08-16 21:28 | 2026-08-16 21:28 | 2026-08-16 21:28 | BrokenWire |  | Fair | No | Unable to locate or contact customer
Outage | J.E.26.08.24716 | C001890292 | Clyde Brown | Manchester | Completed | Load_301405 | Porus - 310 | 2026-08-16 15:37 | 2026-08-17 07:30 | 2026-08-17 17:06 | 2026-08-17 17:07 | 2026-08-17 17:06 | 2026-08-17 16:46 | 2026-08-17 17:07 | 2026-08-17 17:07 |  |  | Fair | No | Manchester call
Outage | J.E.26.08.24775 | C001890293 | Richard Samuda | Manchester | Completed | Load_269230 | Kendal - 310 | 2026-08-16 15:37 | 2026-08-16 15:39 | 2026-08-16 18:06 | 2026-08-16 18:06 | 2026-08-16 18:37 | 2026-08-16 06:38 | 2026-08-16 18:39 | 2026-08-16 18:39 |  |  | Fair | No | Found ok customer had a chip breaker
Non-Outage | J.E.26.08.21055 | C001890296 | Richard Samuda | Manchester | Completed | Load_244975 | Spur Tree - 310 | 2026-08-16 15:40 | 2026-08-16 15:42 | 2026-08-16 16:51 | 2026-08-16 16:51 | 2026-08-16 17:36 | 2026-08-16 05:55 | 2026-08-16 17:55 | 2026-08-16 17:55 | LeaningPole |  | Fair | No | Customer reported damaged meter pole advised customer jps is not responsible for meter pole advised customer to get electrician to resolve issue
Non-Outage | J.E.26.08.22888 | C001890295 | Kenroy Dale | Manchester | Completed | Load_265753 | Spur Tree - 310 | 2026-08-16 15:40 | 2026-08-17 07:43 | 2026-08-17 17:46 | 2026-08-17 17:47 | 2026-08-17 18:31 | 2026-08-17 18:42 | 2026-08-17 18:47 | 2026-08-17 18:47 | LeaningPole |  | Fair | No | Leaning 30 foot dead end secondary pole found.
Non-Outage | J.E.26.08.16978 | C001890300 | Ryan Richards | Manchester | Completed | Load_260581 | Porus - 210 | 2026-08-16 15:42 | 2026-08-17 07:43 | 2026-08-17 12:58 | 2026-08-17 12:59 | 2026-08-17 14:38 | 2026-08-17 15:35 | 2026-08-17 15:36 | 2026-08-17 15:36 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | 2 rotten 35 -6 cv pole found rotten at base one of the pole started to lean very badly which caused primary and primary neutral to hang very low in the road way the primary is about 10ft off the ground box truck and tipper truck traverse these area residents are afraid to walk pass urgent attention required to carry out repair
Outage | J.E.26.08.23088 | C001890298 | Neville Spencer | Clarendon | Completed | Load_256154 | May Pen - 110 | 2026-08-16 15:42 | 2026-08-16 15:44 | 2026-08-16 20:34 | 2026-08-17 07:33 | 2026-08-17 10:55 | 2026-08-17 11:24 | 2026-08-17 11:27 | 2026-08-17 11:27 |  |  | Fair | No | Remade corrded phase and neutral joints at pothead used 2, 6 / 6 sleeves voltage reading 114 supply restored.
Outage | J.E.26.08.23526 | C001890297 | Neville Spencer | Clarendon | Completed | Load_352838 | May Pen - 110 | 2026-08-16 15:42 | 2026-08-16 15:44 | 2026-08-16 18:30 | 2026-08-16 18:30 | 2026-08-16 18:30 | 2026-08-16 18:30 | 2026-08-16 18:31 | 2026-08-16 18:31 |  |  | Fair | No | Found ok call resolved this morning.
Outage | J.E.26.08.24680 | C001890299 | Neville Spencer | Clarendon | Completed | Load_258698 | May Pen - 110 | 2026-08-16 15:42 | 2026-08-16 15:44 | 2026-08-16 15:53 | 2026-08-16 15:54 | 2026-08-16 17:18 | 2026-08-16 17:19 | 2026-08-16 17:58 | 2026-08-16 17:58 |  |  | Fair | No | Found primary netural Conductor shorting out on primary phase Conductor slacking netural Conductor, renew blown 15 amp J/ fuse supply restored.Also found 35 c 6 wooden pole leaning badly towards road way construction CV pole need to straighten.
Outage | J.E.26.08.24086 | C001890304 | Daniel Francis | St.Ann | Completed | Load_261588 | Roaring River - 210 | 2026-08-16 15:43 | 2026-08-16 15:45 | 2026-08-16 23:20 | 2026-08-16 23:20 | 2026-08-16 23:44 | 2026-08-17 00:38 | 2026-08-17 00:38 | 2026-08-17 00:38 | BangingWires |  | Fair | No | Retention secondary wire two span also pole need to be replaced 100% bad condition no pole #
Outage | J.E.26.08.24678 | C001890301 | Daniel Francis | St.Ann | Completed | Load_270020 | Ocho Rios - 310 | 2026-08-16 15:43 | 2026-08-16 15:45 | 2026-08-16 21:17 | 2026-08-16 21:18 | 2026-08-16 21:23 | 2026-08-16 21:23 | 2026-08-16 21:23 | 2026-08-16 21:23 |  |  | Fair | No | Found okay
Outage | J.E.26.08.24726 | C001890302 | Daniel Francis | St.Ann | Completed | Load_252597 | Ocho Rios - 310 | 2026-08-16 15:43 | 2026-08-16 15:45 | 2026-08-16 20:35 | 2026-08-16 20:36 | 2026-08-16 21:13 | 2026-08-16 21:14 | 2026-08-16 21:16 | 2026-08-16 21:16 |  |  | Fair | No | Change one 15amp fuse pole #563946 power restored
Outage | J.E.26.08.24771 | C001890303 | Daniel Francis | St.Ann | Completed | Load_246929 | Ocho Rios - 410 | 2026-08-16 15:43 | 2026-08-16 15:45 | 2026-08-16 16:14 | 2026-08-16 16:15 | 2026-08-16 16:41 | 2026-08-16 17:05 | 2026-08-16 17:08 | 2026-08-16 17:08 |  |  | Fair | No | Change 2 fuse one 40amp and one 40amp no pole # power restored
Outage | J.E.26.08.23212 | C001890307 | Hartley Chin | Clarendon | Completed | Load_264754 | May Pen - 210 | 2026-08-16 15:44 | 2026-08-16 15:46 | 2026-08-16 18:53 | 2026-08-16 19:10 | 2026-08-16 19:10 | 2026-08-16 19:10 | 2026-08-16 19:11 | 2026-08-16 19:11 |  |  | Fair | No | Call related to job # 24529
Outage | J.E.26.08.23711 | C001890306 | Hartley Chin | Clarendon | Completed | Load_260256 | Parnassus - 210 | 2026-08-16 15:44 | 2026-08-16 15:46 | 2026-08-16 19:14 | 2026-08-16 19:14 | 2026-08-16 19:17 | 2026-08-16 19:41 | 2026-08-16 19:45 | 2026-08-16 19:45 |  |  | Fair | No | Found 8 AMP junction blown due to tree contact. Tree cut , line refused
Outage | J.E.26.08.24529 | C001890305 | Hartley Chin | Clarendon | Completed | Load_261428 | May Pen - 210 | 2026-08-16 15:44 | 2026-08-16 15:46 | 2026-08-16 17:22 | 2026-08-16 17:22 | 2026-08-16 18:21 | 2026-08-16 19:07 | 2026-08-16 19:09 | 2026-08-16 19:09 |  |  | Fair | No | Found transformer Trip. Line patrolled and found ok. Transformer reset.
Outage | J.E.26.08.24004 | C001890308 | Hartley Chin | Clarendon | Completed | Load_248888 | Monymusk - 410 | 2026-08-16 15:45 | 2026-08-16 15:46 | 2026-08-16 19:45 | 2026-08-16 19:45 | 2026-08-16 20:58 | 2026-08-16 21:27 | 2026-08-16 21:29 | 2026-08-16 21:29 |  |  | Fair | No | Found blown 30 AMP junction fuse blown . Line patrolled and found ok. Junction refused
Outage | J.E.26.08.24774 | C001890310 | Raymond Carr | St.Ann | Completed | Load_261992 | Upper White River - 110 | 2026-08-16 15:47 | 2026-08-16 16:12 | 2026-08-16 16:15 | 2026-08-16 16:16 | 2026-08-16 17:16 | 2026-08-16 18:00 | 2026-08-16 18:04 | 2026-08-16 18:04 |  |  | SevereWind | No | Blown junction fuse found at pole number 0014181, line patrol and found okay, however tree contact, was suspected. A 20 amp fuse was used to renew supply was restored.
Outage | J.E.26.08.24822 | C001890311 | Raymond Carr | St.Ann | Completed | Load_257713 | Upper White River - 110 | 2026-08-16 15:47 | 2026-08-16 16:12 | 2026-08-16 18:35 | 2026-08-16 18:35 | 2026-08-16 18:35 | 2026-08-16 18:35 | 2026-08-16 18:36 | 2026-08-16 18:36 |  |  | Fair | No | Supply was restored.
Outage | J.E.26.08.24831 | C001890313 | Lancelot Brown | Westmoreland | Completed | Load_240095 | Paradise - 210 | 2026-08-16 15:51 | 2026-08-16 15:55 | 2026-08-16 18:35 | 2026-08-16 18:36 | 2026-08-16 18:35 | 2026-08-16 18:36 | 2026-08-16 18:36 | 2026-08-16 18:36 |  |  | Rains | No | Please pass on this call to westmoreland crew
Outage | J.E.26.08.24809 | C001890315 | Donald Cunningham | St.Catherine | Completed | Load_256392 | Tredegar - 410 | 2026-08-16 15:54 | 2026-08-16 15:55 | 2026-08-16 16:41 | 2026-08-16 16:42 | 2026-08-16 17:37 | 2026-08-16 17:42 | 2026-08-16 17:43 | 2026-08-16 17:43 |  |  | Fair | No | Supply restored
Outage | J.E.26.08.24821 | C001890316 | Ricky Hall | St.Catherine | Completed | Load_266216 | New Michelton - 210 | 2026-08-16 15:54 | 2026-08-16 15:55 | 2026-08-16 19:11 | 2026-08-16 19:13 | 2026-08-16 19:53 | 2026-08-16 21:34 | 2026-08-16 21:35 | 2026-08-16 21:35 |  |  | Rains | No | Conduct spot bushing replaced blown 30 amps junction fuse
Outage | J.E.26.08.24861 | C001890317 | Oshane Warren | Westmoreland | Completed | Load_250896 | Paradise - 210 | 2026-08-16 15:54 | 2026-08-16 15:56 | 2026-08-16 19:12 | 2026-08-16 19:13 | 2026-08-16 20:56 | 2026-08-16 21:00 | 2026-08-16 21:02 | 2026-08-16 21:02 |  |  | Rains | No | 25 kva transformer Defective need to change 14 customer left without power refer to maintenance
Outage | J.E.26.08.22924 | C001890320 | Collin Robinson | Portland | Completed | Load_354081 | Port Antonio - 310 | 2026-08-16 15:57 | 2026-08-16 15:59 | 2026-08-16 20:36 | 2026-08-16 20:37 | 2026-08-16 22:37 | 2026-08-16 22:38 | 2026-08-16 22:38 | 2026-08-16 22:38 | TreeContact |  | Rains | No | Unable to locate customer for better direction
Outage | J.E.26.08.24153 | C001890323 | Collin Robinson | Portland | Completed | Load_250879 | Port Antonio - 310 | 2026-08-16 15:57 | 2026-08-16 15:59 | 2026-08-16 17:08 | 2026-08-16 17:09 | 2026-08-16 17:46 | 2026-08-16 18:10 | 2026-08-16 18:10 | 2026-08-16 18:10 |  |  | Rains | No | 25KVA transformer defective no voltage coming secondary side of transformer.transformer also leaking oil refer to maintenance
Outage | J.E.26.08.24559 | C001890319 | Andre Smith | KSAS | Completed | Load_575567 | Duhaney - 410 | 2026-08-16 15:57 | 2026-08-16 17:05 | 2026-08-16 20:17 | 2026-08-16 20:17 | 2026-08-16 20:57 | 2026-08-16 21:20 | 2026-08-16 21:30 | 2026-08-16 21:30 | BrokenPole |  | Fair | No | Broken pole found maintenance department required
Outage | J.E.26.08.24639 | C001890322 | Edward Royal | KSAS | Completed | Load_412792 | Hunts Bay - 810 | 2026-08-16 15:57 | 2026-08-16 17:05 | 2026-08-16 17:33 | 2026-08-16 17:33 | 2026-08-16 17:46 | 2026-08-16 17:47 | 2026-08-16 17:48 | 2026-08-16 17:48 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.24527 | C001890324 | Collin Robinson | Portland | Completed | Load_349025 | Port Antonio - 310 | 2026-08-16 15:58 | 2026-08-16 15:59 | 2026-08-16 16:18 | 2026-08-16 16:18 | 2026-08-16 16:47 | 2026-08-16 17:08 | 2026-08-16 17:08 | 2026-08-16 17:08 |  |  | Rains | No | Remove tree from two phase of primary conductor and replace two 10 amps junction fuse at pole 603786
Outage | J.E.26.08.24642 | C001890325 | Collin Robinson | Portland | Completed | Load_256253 | Port Antonio - 310 | 2026-08-16 15:58 | 2026-08-16 15:59 | 2026-08-16 18:12 | 2026-08-16 18:13 | 2026-08-16 18:34 | 2026-08-16 19:10 | 2026-08-16 19:10 | 2026-08-16 19:10 |  |  | Rains | No | Assist by call center to reconnect several customers Hex box
Outage | J.E.26.08.24588 | C001890328 | Wan Carlos Scarlett | Portmore | Completed | Load_265294 | Naggo Head - 510 | 2026-08-16 15:59 | 2026-08-16 16:01 | 2026-08-16 16:22 | 2026-08-16 16:22 | 2026-08-16 17:02 | 2026-08-16 17:34 | 2026-08-16 17:35 | 2026-08-16 17:35 |  |  | Fair | No | Customer confirm that power supply has been restored
Outage | J.E.26.08.24590 | C001890326 | Wan Carlos Scarlett | Portmore | Completed | Load_268252 | Naggo Head - 510 | 2026-08-16 15:59 | 2026-08-16 16:00 | 2026-08-16 19:20 | 2026-08-16 19:34 | 2026-08-16 19:55 | 2026-08-16 21:34 | 2026-08-16 21:35 | 2026-08-16 21:35 |  |  | Fair | No | Customer was reconnected from escalation department power supply has been restored
Outage | J.E.26.08.24643 | C001890327 | Wan Carlos Scarlett | Portmore | Completed | Load_268932 | Naggo Head - 510 | 2026-08-16 15:59 | 2026-08-16 16:00 | 2026-08-16 19:20 | 2026-08-17 08:02 | 2026-08-17 09:26 | 2026-08-17 09:28 | 2026-08-17 09:29 | 2026-08-17 09:29 | Fire |  | Fair | No | Found one span of open secondary line please jumper burn out from the one bolt clamp use 2 one bolt clamps at pole readings 116-117-234
Outage | J.E.26.08.24758 | C001890329 | Wan Carlos Scarlett | Portmore | Completed | Load_244248 | Naggo Head - 510 | 2026-08-16 16:01 | 2026-08-16 17:09 | 2026-08-16 17:35 | 2026-08-16 17:36 | 2026-08-16 18:23 | 2026-08-16 19:25 | 2026-08-16 19:31 | 2026-08-16 19:31 |  |  | Fair | No | Found 2 phase primary line junction with one of the lower part of the switch jumper burn off use 2 one bolt clamps at pole.isolate and close 3 phase primary line junction to carry out repairs pole # 014305
Outage | J.E.26.08.24843 | C001890333 | Horace Malcolm | St.James | Completed | Load_247579 | Bogue - 310 | 2026-08-16 16:03 | 2026-08-16 16:06 | 2026-08-16 16:29 | 2026-08-16 16:29 | 2026-08-16 16:48 | 2026-08-16 18:53 | 2026-08-16 18:53 | 2026-08-16 18:53 |  |  | SevereWind | No | Refused one 50amp junction fuse and Reclosed one 30amp tripsaver
Outage | J.E.26.08.24784 | C001890334 | Swon Miller | St.James | Completed | Load_250575 | Bogue - 310 | 2026-08-16 16:04 | 2026-08-16 18:01 | 2026-08-16 18:22 | 2026-08-16 18:25 | 2026-08-16 18:45 | 2026-08-18 07:50 | 2026-08-16 19:59 | 2026-08-16 19:59 |  |  | Fair | No | Found 1,30 amp junction fuse blown due to clearance breach of the primary conductor with a customer house also switch needs to be replaced because the fuse had to be string up .maintenance intervention is required to correct the clearance breach as this has been happening for years and it is unsafe for the customer.plz refer maintenance/k.Frazier
Outage | J.E.26.08.24940 | C001890337 | Derrick Dawkins | St.James | Completed | Load_576009 | Bogue - 310 | 2026-08-16 16:05 | 2026-08-17 05:26 | 2026-08-17 05:35 | 2026-08-17 06:55 | 2026-08-17 06:55 | 2026-08-17 06:00 | 2026-08-17 06:57 | 2026-08-17 06:57 |  |  | Fair | No | Found premises ok
Outage | J.E.26.08.24915 | C001890339 | Tyrese Williams | St.Ann | Completed | Load_249771 | Cardiff Hall - 310 | 2026-08-16 16:06 | 2026-08-16 16:08 | 2026-08-16 20:46 | 2026-08-16 20:46 | 2026-08-16 20:46 | 2026-08-16 20:46 | 2026-08-16 20:47 | 2026-08-16 20:47 | BrokenWire |  | Fair | No | Premises not found not getting customer on customer
Outage | J.E.26.08.24549 | C001890340 | Cliton Henry | St.Mary | Completed | Load_245112 | Annotto Bay - 210 | 2026-08-16 16:12 | 2026-08-16 16:14 | 2026-08-16 18:20 | 2026-08-16 18:21 | 2026-08-16 18:45 | 2026-08-16 19:45 | 2026-08-16 19:46 | 2026-08-16 19:46 |  |  | Fair | No | A blown 15 amp junction fuse found at pole #005265 due to a branches found burning on line. Corrective work done to cut and remove branch. Supply restored using 1-15 amp fuse.
Outage | J.E.26.08.24592 | C001890341 | Cliton Henry | St.Mary | Completed | Load_576739 | Annotto Bay - 210 | 2026-08-16 16:13 | 2026-08-16 16:14 | 2026-08-16 19:51 | 2026-08-16 19:51 | 2026-08-16 19:51 | 2026-08-16 19:51 | 2026-08-16 19:52 | 2026-08-16 19:52 | Fire |  | Fair | No | The supply was restored, related to outage #24549
Outage | J.E.26.08.24636 | C001890342 | Cliton Henry | St.Mary | Completed | Load_250719 | Annotto Bay - 210 | 2026-08-16 16:13 | 2026-08-16 16:14 | 2026-08-16 19:52 | 2026-08-16 19:53 | 2026-08-16 20:55 | 2026-08-16 21:15 | 2026-08-16 21:16 | 2026-08-16 21:16 | BrokenWire |  | Fair | No | A 50 kva transformer drop lead bunt off. The transformer was de energized at pole #0005348 to carryout repairs. Corrective work done to reconnected the transformer drop lead using 2 one bolt clamps. Voltages left 119-119/238 volts.
Outage | J.E.26.08.24689 | C001890344 | Cliton Henry | St.Mary | Completed | Load_250540 | Annotto Bay - 310 | 2026-08-16 16:13 | 2026-08-16 16:15 | 2026-08-16 17:40 | 2026-08-16 17:41 | 2026-08-16 17:41 | 2026-08-16 18:14 | 2026-08-16 18:19 | 2026-08-16 18:19 | A blown 50 amp junction fuse found at the underground cables at poles # 0099070 due to lightning. Supply restored using 1-50 amp fuse. |  | Fair | No
Outage | J.E.26.08.24957 | C001890347 | Lancelot Brown | Hanover | Completed | Load_259699 | Orange Bay - 310 | 2026-08-16 16:17 | 2026-08-16 16:19 | 2026-08-16 18:37 | 2026-08-16 20:34 | 2026-08-16 21:03 | 2026-08-16 21:11 | 2026-08-16 21:11 | 2026-08-16 21:11 |  |  | Rains | No | Found 10kva trip patroll found nothing reset 10kva supply restore
Outage | J.E.26.08.24951 | C001890349 | Stephen Taylor | St.Thomas | Completed | Load_577217 | Good Year - 210 | 2026-08-16 16:18 | 2026-08-16 16:58 | 2026-08-16 17:13 | 2026-08-16 17:13 | 2026-08-16 18:14 | 2026-08-16 18:14 | 2026-08-16 18:16 | 2026-08-16 18:16 |  |  | Fair | No | Junction fuse out patrol clear line with switch stick and close up back junction line with a 15 amp fuse safety customer is now okay
Outage | J.E.26.08.24920 | C001890350 | Marlon Brown | Trelawny | Completed | Load_239746 | Greenwood - 210 | 2026-08-16 16:19 | 2026-08-16 16:36 | 2026-08-16 19:36 | 2026-08-16 19:36 | 2026-08-16 20:02 | 2026-08-16 21:01 | 2026-08-16 21:01 | 2026-08-16 21:01 | Fire |  | Fair | No | Retention 1 span secondary
Outage | J.E.26.08.24993 | C001890353 | Damion Reid | Manchester | Completed | Load_262908 | Kendal - 210 | 2026-08-16 16:20 | 2026-08-16 16:23 | 2026-08-16 19:09 | 2026-08-16 19:09 | 2026-08-16 20:19 | 2026-08-16 22:47 | 2026-08-16 22:53 | 2026-08-16 22:53 | BrokenWire |  | Fair | No | 2/0 twisted for 3 wire service found hanging low cause by truck open 25kva transformer fuse link retention service wire reconnect broken #6 service wire retention guy wire and restore power
Non-Outage | J.E.26.08.23812 | C001890354 | Richman Whyte | St.Elizabeth | Completed | Load_245885 | Maggotty - 110 | 2026-08-16 16:22 | 2026-08-16 16:23 | 2026-08-16 17:50 | 2026-08-16 17:50 | 2026-08-16 18:46 | 2026-08-16 19:18 | 2026-08-16 19:20 | 2026-08-16 19:20 |  |  | Fair | No | A follow up visit is required in the morning Mr Richard is aware
Outage | J.E.26.08.24956 | C001890356 | Lancelot Brown | Hanover | Completed | Load_258270 | Orange Bay - 310 | 2026-08-16 16:25 | 2026-08-16 16:33 | 2026-08-16 18:37 | 2026-08-16 18:38 | 2026-08-16 19:34 | 2026-08-16 19:35 | 2026-08-16 19:36 | 2026-08-16 19:36 |  |  | Rains | No | No supply caused by outage on 210 frm orange bay supply restore
Outage | J.E.26.08.25056 | C001890357 | Lancelot Brown | Hanover | Completed | Load_257370 | Orange Bay - 310 | 2026-08-16 16:32 | 2026-08-16 16:33 | 2026-08-16 18:37 | 2026-08-16 19:57 | 2026-08-16 20:19 | 2026-08-16 20:30 | 2026-08-16 20:31 | 2026-08-16 20:31 |  |  | Rains | No | Found junction fuse blown patroll found tree lim contact with primary line cut and remove tree lim from primary line replace 1-10amps junction fuse no pole number supply restore
Outage | J.E.26.08.24842 | C001890359 | Marlon Brown | Trelawny | Completed | Load_250518 | Duncans - 110 | 2026-08-16 16:37 | 2026-08-16 16:39 | 2026-08-16 18:04 | 2026-08-16 18:04 | 2026-08-16 18:26 | 2026-08-16 19:09 | 2026-08-16 19:09 | 2026-08-16 19:09 |  |  | Fair | No | Clear vegetation from transformer pole and replaced 15amps junction @ pole number 586622 and 5amps 50kva Transformer fuse.
Outage | J.E.26.08.25082 | C001890360 | Marlon Brown | Trelawny | Completed | Load_242318 | Duncans - 210 | 2026-08-16 16:38 | 2026-08-16 16:39 | 2026-08-16 16:43 | 2026-08-16 16:44 | 2026-08-16 16:54 | 2026-08-16 18:00 | 2026-08-16 18:02 | 2026-08-16 18:02 |  |  | Fair | No | Isolated 25kva transformer to repair drop neutral, use 2pg clamps also reattach secondary phase to spool insulator. Voltage found at meter socket 0/240=240Voltage leaving at meter socket 117/119=236v.
Outage | J.E.26.08.24878 | C001890361 | Derrick Dawkins | St.James | Completed | Load_254869 | Bogue - 310 | 2026-08-16 16:41 | 2026-08-17 13:09 | 2026-08-17 14:53 | 2026-08-17 14:55 | 2026-08-17 15:24 | 2026-08-17 15:48 | 2026-08-17 15:49 | 2026-08-17 15:49 |  |  | Fair | No | Found junction fuse blown 10 amp replaced 10 amp junction fuse
Non-Outage | J.E.26.08.24923 | C001890364 | Rusean Allen |  | Completed |  |  | 2026-08-16 16:43 | 2026-08-16 16:45 | 2026-08-16 21:06 | 2026-08-16 21:07 | 2026-08-16 21:07 | 2026-08-16 21:07 | 2026-08-16 21:07 | 2026-08-16 21:07 | Fire |  | Fair | No | Related
Outage | J.E.26.08.25060 | C001890365 | Rusean Allen | KSAS | Completed | Load_243330 | Rockfort - 410 | 2026-08-16 16:46 | 2026-08-16 16:51 | 2026-08-16 17:28 | 2026-08-16 17:29 | 2026-08-16 19:02 | 2026-08-16 19:25 | 2026-08-16 19:25 | 2026-08-16 19:25 | BrokenWire |  | Fair | No | Customer reset Circuit breaker
Outage | J.E.26.08.24530 | C001890369 | Andre Smith | KSAN | Completed | Load_266717 | Washington Blvd - 710 | 2026-08-16 16:54 | 2026-08-16 17:02 | 2026-08-16 17:08 | 2026-08-16 17:09 | 2026-08-16 17:50 | 2026-08-16 18:21 | 2026-08-16 18:21 | 2026-08-16 18:21 |  |  | Fair | No | No communication field service department required
Outage | J.E.26.08.24998 | C001890367 | Swon Miller | St.James | Completed | Load_254736 | Bogue - 310 | 2026-08-16 16:54 | 2026-08-16 18:01 | 2026-08-16 22:40 | 2026-08-16 22:41 | 2026-08-16 23:19 | 2026-08-16 23:35 | 2026-08-16 23:36 | 2026-08-16 23:36 |  |  | Fair | No | Check and found areas okay customer states that power supply has been restored
Outage | J.E.26.08.25108 | C001890368 | Andre Smith | KSAN | Completed | Load_293754 | Washington Blvd - 710 | 2026-08-16 16:54 | 2026-08-16 17:02 | 2026-08-16 18:21 | 2026-08-16 18:22 | 2026-08-16 18:52 | 2026-08-16 01:00 | 2026-08-16 19:15 | 2026-08-16 19:15 | BrokenWire |  | Fair | No | Premises found okay supply restored already
Non-Outage | J.E.26.08.25085 | C001890371 | Marlon Brown |  | Completed |  |  | 2026-08-16 17:01 | 2026-08-16 17:03 | 2026-08-16 19:13 | 2026-08-16 19:14 | 2026-08-16 19:34 | 2026-08-16 19:35 | 2026-08-16 19:35 | 2026-08-16 19:35 | Fire |  | Fair | No | Unable to locate customer via telephone nor direction
Outage | J.E.26.08.24660 | C001890372 | Antony Levy | KSAN | Completed | Load_243579 | Constant Spring - 410 | 2026-08-16 17:02 | 2026-08-16 17:07 | 2026-08-16 17:23 | 2026-08-16 17:24 | 2026-08-16 19:18 | 2026-08-16 20:28 | 2026-08-16 20:31 | 2026-08-16 20:31 |  |  | Fair | No | Cx stated no power ..... blown 25kva transformer fuse found at 0000777 ..... secondary patrolled and deemed safe to close... transformer refused with a 3 am fuse ....power restored
Outage | J.E.26.08.19230 | C001890373 | Antony Levy | KSAN | Completed | Load_238744 | Constant Spring - 410 | 2026-08-16 17:06 | 2026-08-16 17:07 | 2026-08-16 20:31 | 2026-08-16 20:32 | 2026-08-16 21:28 | 2026-08-16 21:32 | 2026-08-16 21:32 | 2026-08-16 21:32 |  |  | Fair | No | Premises closed ...unable to reach cx
Non-Outage | J.E.26.08.24650 | C001890374 | Rusean Allen |  | Completed |  |  | 2026-08-16 17:08 | 2026-08-16 17:09 | 2026-08-16 21:05 | 2026-08-16 21:06 | 2026-08-16 21:05 | 2026-08-16 21:06 | 2026-08-16 21:06 | 2026-08-16 21:06 | BrokenWire |  | Fair | No | Related to greenvale rd
Outage | J.E.26.08.25180 | C001890375 | Wayne Dillion | St.Elizabeth | Completed | Load_1002142 | Maggotty - 110 | 2026-08-16 17:16 | 2026-08-16 17:17 | 2026-08-16 20:40 | 2026-08-16 20:40 | 2026-08-16 20:40 | 2026-08-16 20:59 | 2026-08-16 21:00 | 2026-08-16 21:00 |  |  | Fair | No | Patrol and found one blown 10amp junction fuse no pole #. Replace same and supply restored okay.
Outage | J.E.26.08.24960 | C001890377 | Swon Miller | Manchester | Completed | Load_243336 | Kendal - 210 | 2026-08-16 17:21 | 2026-08-16 19:32 | 2026-08-16 21:20 | 2026-08-16 21:43 | 2026-08-16 21:42 | 2026-08-16 22:34 | 2026-08-16 22:40 | 2026-08-16 22:40 |  |  | Fair | No | Found 1,30 amp junction fuse blown cause by contamination re1,30 amp junction fuse no pole number available
Outage | J.E.26.08.25189 | C001890378 | Lancelot Brown | Hanover | Completed | Load_293074 | Orange Bay - 310 | 2026-08-16 17:24 | 2026-08-16 17:27 | 2026-08-16 18:29 | 2026-08-16 18:30 | 2026-08-16 18:29 | 2026-08-16 18:31 | 2026-08-16 18:31 | 2026-08-16 18:31 |  |  | Rains | No | No supply caused by outage on feeder 310 from orange bay supply restore
Outage | J.E.26.08.25186 | C001890380 | Lancelot Brown | Hanover | Completed | Load_249518 | Orange Bay - 310 | 2026-08-16 17:25 | 2026-08-16 17:27 | 2026-08-16 18:37 | 2026-08-16 20:31 | 2026-08-16 20:31 | 2026-08-16 20:32 | 2026-08-16 20:32 | 2026-08-16 20:32 |  |  | Rains | No | This call related to 10amps junction fuse supply restore
Outage | J.E.26.08.25206 | C001890379 | Shawn Medley | St.James | Completed | Load_238044 | Bogue - 310 | 2026-08-16 17:25 | 2026-08-17 12:16 | 2026-08-17 12:36 | 2026-08-17 12:37 | 2026-08-17 13:18 | 2026-08-17 13:30 | 2026-08-17 14:40 | 2026-08-17 14:40 | Fire |  | Fair | No | Found burnt off top phase; open 50kva dropout fuse and used to one bolt clamps to carry out repairs
Outage | J.E.26.08.25089 | C001890383 | Daniel Francis | St.Ann | Completed | Load_256292 | Ocho Rios - 410 | 2026-08-16 17:28 | 2026-08-16 17:29 | 2026-08-17 00:38 | 2026-08-17 00:39 | 2026-08-17 02:27 | 2026-08-17 02:14 | 2026-08-17 02:28 | 2026-08-17 02:28 |  |  | Rains | No | Not found customer not answering phone
Outage | J.E.26.08.24597 | C001890384 | Christopher Edwards | KSAN | Completed | Load_579005 | Washington Blvd - 610 | 2026-08-16 17:34 | 2026-08-16 23:24 | 2026-08-17 00:35 | 2026-08-17 01:01 | 2026-08-17 01:01 | 2026-08-17 02:21 | 2026-08-17 02:22 | 2026-08-17 02:22 |  |  | Fair | No | Check and found ok
Outage | J.E.26.08.24589 | C001890385 | Wan Carlos Scarlett | Portmore | Completed | Load_244248 | Naggo Head - 510 | 2026-08-16 17:37 | 2026-08-16 17:39 | 2026-08-16 19:20 | 2026-08-16 19:32 | 2026-08-16 19:31 | 2026-08-16 19:32 | 2026-08-16 19:32 | 2026-08-16 19:32 |  |  | Fair | No | Customer confirm that power supply has been restored call related
Outage | J.E.26.08.24640 | C001890386 | Wan Carlos Scarlett | Portmore | Completed | Load_260827 | Naggo Head - 510 | 2026-08-16 17:38 | 2026-08-16 17:39 | 2026-08-16 19:20 | 2026-08-16 19:33 | 2026-08-16 19:32 | 2026-08-16 19:33 | 2026-08-16 19:33 | 2026-08-16 19:33 |  |  | Fair | No | Customer confirm that power supply has been restored call related
Outage | J.E.26.08.25072 | C001890387 | Wan Carlos Scarlett | Portmore | Completed | Load_556172 | Naggo Head - 610 | 2026-08-16 17:38 | 2026-08-16 17:41 | 2026-08-16 19:20 | 2026-08-16 21:36 | 2026-08-16 22:09 | 2026-08-16 22:39 | 2026-08-16 22:40 | 2026-08-16 22:40 |  |  | Fair | No | Found customer 3 wire service at pothead with the neutral broken off use one bolt clamp at service wire neutral readings 114-115-230
Outage | J.E.26.08.25109 | C001890389 | Tyrese Williams | St.Ann | Completed | Load_253793 | Cardiff Hall - 310 | 2026-08-16 17:41 | 2026-08-16 17:44 | 2026-08-16 17:51 | 2026-08-16 17:54 | 2026-08-16 17:53 | 2026-08-16 17:55 | 2026-08-16 17:56 | 2026-08-16 17:56 |  |  | Fair | No | Premises found ok call related to the 40 amp junction fuse
Outage | J.E.26.08.24676 | C001890391 | Edward Royal | KSAS | Completed | Load_259182 | Hunts Bay - 810 | 2026-08-16 17:48 | 2026-08-16 18:20 | 2026-08-16 19:17 | 2026-08-16 19:17 | 2026-08-16 19:17 | 2026-08-16 19:17 | 2026-08-16 19:17 | 2026-08-16 19:17 |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.08.25149 | C001890393 | Swon Miller | St.James | Completed | Load_1002560 | Bogue - 310 | 2026-08-16 17:50 | 2026-08-16 18:00 | 2026-08-16 20:00 | 2026-08-16 20:00 | 2026-08-16 20:54 | 2026-08-18 21:11 | 2026-08-16 21:19 | 2026-08-16 21:19 |  |  | Fair | No | Check and found okay voltage found 118/118/206 voltage left 118/118/236/236/238
Outage | J.E.26.08.24630 | C001890395 | Edward Royal | KSAS | Completed | Load_249873 | Hunts Bay - 510 | 2026-08-16 17:56 | 2026-08-16 18:19 | 2026-08-16 19:16 | 2026-08-16 19:17 | 2026-08-16 19:16 | 2026-08-16 19:16 | 2026-08-16 19:17 | 2026-08-16 19:17 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.24806 | C001890403 | Richard Nicholas | St.Catherine | Completed | Load_246091 | Rhodens Pen - 210 | 2026-08-16 18:11 | 2026-08-16 18:16 | 2026-08-16 18:28 | 2026-08-16 18:28 | 2026-08-16 19:51 | 2026-08-16 20:54 | 2026-08-16 21:04 | 2026-08-16 21:04 |  |  | Fair | No | Reset tripped transfer however a premises that is located beside transformer pole,customer alerted the crew that after the supply was restored she saw smoke coming out of the plug and breaker panel a further observation was done by the crew and smoke was seen coming from pothead and inside the house however it was further understood that a generator was tied in the circuit to supply current during the outage period and it was connected to incorrectly as a result current was feeding back to the secondary line,3w supply disconnected at pole for unsafe reason and customer to get private electrician to ensure that housing wiring is ok before then call customer care so supply can be reconnected.
Outage | J.E.26.08.25218 | C001890402 | Donald Cunningham | St.Catherine | Completed | Load_270213 | Tredegar - 410 | 2026-08-16 18:11 | 2026-08-16 18:15 | 2026-08-16 18:26 | 2026-08-16 18:26 | 2026-08-16 19:03 | 2026-08-16 20:01 | 2026-08-16 20:04 | 2026-08-16 20:04 |  |  | Fair | No | Blown junction fuse by entrance to march pen road replace 30 amp fuse and burnt up fuse holder 8 amp fuse near 19 march pen road
Outage | J.E.26.08.25241 | C001890401 | Donald Cunningham | St.Catherine | Completed | Load_574647 | Rhodens Pen - 210 | 2026-08-16 18:11 | 2026-08-16 18:15 | 2026-08-16 20:09 | 2026-08-16 20:10 | 2026-08-16 20:17 | 2026-08-16 20:19 | 2026-08-16 20:20 | 2026-08-16 20:20 |  |  | Fair | No | Supply restored
Outage | J.E.26.08.25271 | C001890400 | Donald Cunningham | St.Catherine | Completed | Load_244163 | Tredegar - 410 | 2026-08-16 18:11 | 2026-08-16 18:15 | 2026-08-16 20:21 | 2026-08-16 20:22 | 2026-08-16 20:32 | 2026-08-16 20:33 | 2026-08-16 20:33 | 2026-08-16 20:33 |  |  | Fair | No | Supply restored
Non-Outage | J.E.26.08.23851 | C001890405 | Richard Nicholas | St.Catherine | Completed | Load_556353 | Rhodens Pen - 210 | 2026-08-16 18:12 | 2026-08-16 18:16 | 2026-08-16 21:59 | 2026-08-16 22:00 | 2026-08-16 22:17 | 2026-08-16 22:29 | 2026-08-16 22:30 | 2026-08-16 22:30 |  |  | Fair | No | Area found ok
Non-Outage | J.E.26.08.19882 | C001890408 | Richard Nicholas | St.Catherine | Completed | Load_1000389 | Rhodens Pen - 410 | 2026-08-16 18:16 | 2026-08-16 18:17 | 2026-08-16 22:30 | 2026-08-16 22:30 | 2026-08-16 22:42 | 2026-08-16 23:02 | 2026-08-16 23:02 | 2026-08-16 23:02 |  |  | Fair | No | Area found ok
Outage | J.E.26.08.25277 | C001890410 | Rusean Allen | KSAS | Completed | Load_255914 | Cane River - 310 | 2026-08-16 18:17 | 2026-08-16 18:19 | 2026-08-16 19:26 | 2026-08-16 19:26 | 2026-08-16 20:03 | 2026-08-16 21:05 | 2026-08-16 21:05 | 2026-08-16 21:05 | Fire |  | Fair | No | Broken secondary wires wire found, wires were disconnected and removed.70ft #6 service wire was installed to accommodate single customer.
Outage | J.E.26.08.25281 | C001890411 | Edward Royal | KSAS | Completed | Load_263200 | Hunts Bay - 310 | 2026-08-16 18:17 | 2026-08-16 18:19 | 2026-08-16 19:00 | 2026-08-16 19:00 | 2026-08-16 19:00 | 2026-08-16 19:16 | 2026-08-16 19:16 | 2026-08-16 19:16 |  |  | Fair | No | Replaced 40A junction fuse
Outage | J.E.26.08.25017 | C001890413 | Ricky Hall | St.Catherine | Completed | Load_269347 | New Michelton - 310 | 2026-08-16 18:18 | 2026-08-16 18:19 | 2026-08-16 21:35 | 2026-08-16 21:36 | 2026-08-16 22:53 | 2026-08-16 22:56 | 2026-08-16 22:57 | 2026-08-16 22:57 | BrokenWire |  | Rains | No | Area unsafe to carry out repairs daylight attention required
Outage | J.E.26.08.25213 | C001890420 | Stephen Taylor | St.Thomas | Completed | Load_266044 | Good Year - 210 | 2026-08-16 18:33 | 2026-08-16 18:35 | 2026-08-16 20:09 | 2026-08-16 20:09 | 2026-08-16 20:09 | 2026-08-16 20:09 | 2026-08-16 20:11 | 2026-08-16 20:11 |  |  | Fair | No | Patrol erea and power is in the area but several calls to single customer and no one answering the phone failed to locate
Outage | J.E.26.08.25337 | C001890424 | Romeo Brissett | St.James | Completed | Load_574041 | Queens Drive - 710 | 2026-08-16 18:40 | 2026-08-16 18:42 | 2026-08-16 21:02 | 2026-08-16 21:02 | 2026-08-16 21:02 | 2026-08-16 19:50 | 2026-08-16 21:08 | 2026-08-16 21:08 |  |  | Fair | No | Isolated (3)30amps junction fuse for clearance, repaired (1)20amps junction switch top.
Outage | J.E.26.08.24490 | C001890425 | Romeo Brissett | St.James | Completed | Load_254331 | Queens Drive - 310 | 2026-08-16 18:42 | 2026-08-16 18:43 | 2026-08-16 22:03 | 2026-08-16 22:03 | 2026-08-16 22:03 | 2026-08-16 23:12 | 2026-08-16 23:12 | 2026-08-16 23:12 |  |  | Fair | No | Found fuse holder for 8amps junction defective. Changed one defective fuse holder.
Outage | J.E.26.08.25103 | C001890427 | Clyde Brown | Clarendon | Completed | Load_249696 | Parnassus - 310 | 2026-08-16 18:46 | 2026-08-17 07:30 | 2026-08-17 08:01 | 2026-08-17 08:02 | 2026-08-17 09:41 | 2026-08-17 10:03 | 2026-08-17 10:13 | 2026-08-17 10:13 | Fire |  | SevereWind | No | Broken secondary neutral,open 25 kva transformer and repaired with 12ft-#2 conductor,2- splicing sleeve,1-preform and 1- clamp.
Outage | J.E.26.08.25145 | C001890431 | Kenroy Dale | Manchester | Completed | Load_292286 | Spur Tree - 310 | 2026-08-16 19:00 | 2026-08-17 07:43 | 2026-08-17 08:28 | 2026-08-17 08:29 | 2026-08-17 09:31 | 2026-08-17 09:38 | 2026-08-17 09:39 | 2026-08-17 09:39 |  |  | Fair | No | Supply found okay, customer also confirmed that supply was restore
Outage | J.E.26.08.25304 | C001890433 | Lancelot Brown | Hanover | Completed | Load_261227 | Orange Bay - 310 | 2026-08-16 19:02 | 2026-08-16 19:03 | 2026-08-16 20:32 | 2026-08-16 21:14 | 2026-08-16 22:52 | 2026-08-16 22:56 | 2026-08-16 22:56 | 2026-08-16 22:56 | BrokenWire |  | Rains | No | Found one span secondary phase cut down caused by slock span also caused 25kva fuse blown splice and retention one span of secondary phase used thirty feet 2/0 conductor one2/0 preform two pg clamps also replace 1-3amps fuse at 25kva supply restore
Non-Outage | J.E.26.08.25395 | C001890434 | Lancelot Brown |  | Completed |  |  | 2026-08-16 19:05 | 2026-08-16 19:17 | 2026-08-16 20:32 | 2026-08-16 20:33 | 2026-08-16 20:32 | 2026-08-16 20:33 | 2026-08-16 20:33 | 2026-08-16 20:33 |  |  | Rains | No | This call related to 10amps junction fuse supply restore
Outage | J.E.26.08.25291 | C001890439 | Raymond Carr | St.Mary | Completed | Load_264056 | Oracabessa - 210 | 2026-08-16 19:13 | 2026-08-16 19:15 | 2026-08-16 20:31 | 2026-08-16 20:31 | 2026-08-16 20:59 | 2026-08-16 21:05 | 2026-08-16 21:13 | 2026-08-16 21:13 |  |  | Fair | No | No access to rammy system.
Outage | J.E.26.08.25353 | C001890441 | Raymond Carr | St.Ann | Completed | Load_238296 | Upper White River - 210 | 2026-08-16 19:14 | 2026-08-16 19:15 | 2026-08-16 19:19 | 2026-08-16 19:19 | 2026-08-16 20:03 | 2026-08-16 20:28 | 2026-08-16 20:27 | 2026-08-16 20:27 |  |  | Fair | No | Blown junction fuse found, line patrol and found okay however lightening suspected caused of outage. A 25 amp fuse was used to renew supply was restored.
Outage | J.E.26.08.25433 | C001890443 | Cliton Henry | St.Mary | Completed | Load_267868 | Annotto Bay - 210 | 2026-08-16 19:21 | 2026-08-16 19:23 | 2026-08-16 19:48 | 2026-08-16 19:48 | 2026-08-16 19:48 | 2026-08-16 19:48 | 2026-08-16 19:49 | 2026-08-16 19:49 | Fire |  | Fair | No | The supply was restored , this report related to outage # 24549
Outage | J.E.26.08.25191 | C001890447 | Donald Cunningham | St.Catherine | Completed | Load_244704 | Twickenham - 310 | 2026-08-16 19:37 | 2026-08-16 19:44 | 2026-08-16 20:33 | 2026-08-16 20:36 | 2026-08-16 21:56 | 2026-08-16 21:56 | 2026-08-16 22:31 | 2026-08-16 22:31 |  |  | Fair | No | Broken secondary phase splice and retention using 60 feet of #2aa and 4 clamps for repair and replace 3 amp fuse for 25 kva transformer
Outage | J.E.26.08.25477 | C001890450 | Derrick Dawkins | St.James | Completed | Load_292197 | Bogue - 310 | 2026-08-16 19:44 | 2026-08-17 07:53 | 2026-08-17 11:15 | 2026-08-17 11:22 | 2026-08-17 11:32 | 2026-08-17 12:12 | 2026-08-17 12:12 | 2026-08-17 12:12 |  |  | Fair | No | Found 50 kva transformer drop lead burn off open 50 kva transformer to carry out repairs clean and remade joint use 1 2/02/0 amp pack Voltage left 119/119=239
Non-Outage | J.E.26.08.25473 | C001890451 | Tajay Bernard |  | Completed |  |  | 2026-08-16 19:45 | 2026-08-17 13:13 | 2026-08-17 14:00 | 2026-08-17 14:00 | 2026-08-17 14:27 | 2026-08-17 14:37 | 2026-08-17 14:37 | 2026-08-17 14:37 | BrokenWire |  | Fair | No | Area check and found okay unable to locate customer on premises multiple phone call to customer number went unanswered
Outage | J.E.26.08.25515 | C001890452 | Raymond Carr | St.Mary | Completed | Load_254195 | Highgate - 210 | 2026-08-16 19:53 | 2026-08-16 19:59 | 2026-08-16 21:14 | 2026-08-16 21:14 | 2026-08-16 21:45 | 2026-08-16 21:37 | 2026-08-16 21:47 | 2026-08-16 21:47 |  |  | Fair | No | Several calls to contact number went straight to voicemail.
Outage | J.E.26.08.25370 | C001890453 | Richard Nicholas | St.Catherine | Completed | Load_289966 | Rhodens Pen - 210 | 2026-08-16 19:59 | 2026-08-16 20:01 | 2026-08-16 21:04 | 2026-08-16 21:05 | 2026-08-16 21:42 | 2026-08-16 21:58 | 2026-08-16 21:59 | 2026-08-16 21:59 |  |  | Fair | No | Rammy system failure,please refer to the relevant department.
Outage | J.E.26.08.24764 | C001890454 | Marlon Brown | Trelawny | Completed | Load_292626 | Greenwood - 210 | 2026-08-16 20:02 | 2026-08-16 20:02 | 2026-08-16 21:03 | 2026-08-16 21:04 | 2026-08-16 21:04 | 2026-08-16 21:07 | 2026-08-16 21:07 | 2026-08-16 21:07 |  |  | Fair | No | Replaced 30amps junction fuse
Outage | J.E.26.08.24974 | C001890456 | Derrick Dawkins | St.James | Completed | Load_244999 | Bogue - 310 | 2026-08-16 20:08 | 2026-08-17 05:28 | 2026-08-17 06:23 | 2026-08-17 06:58 | 2026-08-17 06:57 | 2026-08-17 06:15 | 2026-08-17 06:59 | 2026-08-17 06:59 |  |  | Fair | No | Check and found premises ok
Outage | J.E.26.08.25104 | C001890460 | Shawn Medley | St.James | Completed | Load_258521 | Queens Drive - 710 | 2026-08-16 20:30 | 2026-08-17 10:46 | 2026-08-17 12:12 | 2026-08-17 12:13 | 2026-08-17 12:30 | 2026-08-17 12:25 | 2026-08-17 12:31 | 2026-08-17 12:31 |  |  | Fair | No | Premises checked and found ok
Outage | J.E.26.08.25568 | C001890461 | Lancelot Brown | Hanover | Completed | Load_303169 | Orange Bay - 210 | 2026-08-16 20:41 | 2026-08-16 20:44 | 2026-08-17 00:06 | 2026-08-17 00:06 | 2026-08-17 00:06 | 2026-08-17 00:27 | 2026-08-17 00:27 | 2026-08-17 00:27 |  |  | Rains | No
Outage | J.E.26.08.24504 | C001890465 | Romeo Brissett | St.James | Completed | Load_574885 | Rose Hall - 210 | 2026-08-16 20:54 | 2026-08-16 20:54 | 2026-08-16 21:09 | 2026-08-16 21:09 | 2026-08-16 21:09 | 2026-08-16 21:10 | 2026-08-16 21:13 | 2026-08-16 21:13 |  |  | Fair | No | Found three junction fuse isolated, re-energized three junction fuse.
Non-Outage | J.E.26.08.25558 | C001890468 | Oshane Warren |  | Completed |  |  | 2026-08-16 20:59 | 2026-08-16 21:02 | 2026-08-16 21:35 | 2026-08-16 21:36 | 2026-08-16 23:56 | 2026-08-17 | 2026-08-17 00:03 | 2026-08-17 00:03 | Fire |  | Rains | No | Open 2 amp 15 kva transformer fuse and splice and retention 2 spand secondary neutral conductor used 6 1 bolt clamps voltage 116 117 234
Outage | J.E.26.08.25593 | C001890467 | Oshane Warren | Westmoreland | Completed | Load_258299 | Paradise - 210 | 2026-08-16 20:59 | 2026-08-16 21:02 | 2026-08-17 00:03 | 2026-08-17 00:03 | 2026-08-17 00:03 | 2026-08-17 00:03 | 2026-08-17 00:04 | 2026-08-17 00:04 |  |  | Rains | No | Need daylight attention crew shift ends
Outage | J.E.26.08.25659 | C001890473 | Raymond Carr | St.Ann | Completed | Load_258413 | Upper White River - 210 | 2026-08-16 21:48 | 2026-08-16 21:49 | 2026-08-16 21:52 | 2026-08-16 21:53 | 2026-08-16 22:03 | 2026-08-16 22:00 | 2026-08-16 22:05 | 2026-08-16 22:05 |  |  | Fair | No | Customer couldn’t be contacted.
Outage | J.E.26.08.25655 | C001890475 | Marlon Brown | Trelawny | Completed | Load_269014 | Greenwood - 210 | 2026-08-16 21:57 | 2026-08-16 21:58 | 2026-08-16 22:09 | 2026-08-16 22:28 | 2026-08-16 22:38 | 2026-08-16 23:31 | 2026-08-16 23:31 | 2026-08-16 23:31 | BrokenWire |  | Fair | No | Replaced service wire after hurricane Melissa Voltage found none Voltage leaving at pothead 116/118=234v.
Outage | J.E.26.08.25583 | C001890476 | Damion Reid | Manchester | Completed | Load_258296 | Kendal - 310 | 2026-08-16 22:00 | 2026-08-16 22:03 | 2026-08-16 23:01 | 2026-08-16 23:01 | 2026-08-16 23:17 | 2026-08-17 00:13 | 2026-08-17 00:16 | 2026-08-17 00:16 |  |  | Fair | No | Blown 3amp fuse found for 25kva transformer cause by banging secondary phase an neutral conductor balance conductor and replace blown fuse
Non-Outage | J.E.26.08.25674 | C001890478 | Shawn Medley |  | Completed |  |  | 2026-08-16 22:04 | 2026-08-17 09:17 | 2026-08-17 10:27 | 2026-08-17 10:28 | 2026-08-17 10:52 | 2026-08-17 11:55 | 2026-08-17 11:58 | 2026-08-17 11:58 | Fire |  | Fair | No | Found broken secondary conductor, I isolated 50kva transformer to carryout repair using 100ft of 2/0 AAA conductor and one 2/0 splicing sleeve. Supply now restored. Line section need heavy bushing. Refer to vegetation department.
Non-Outage | J.E.26.08.25556 | C001890480 | Antony Levy |  | Completed |  |  | 2026-08-16 23:12 | 2026-08-17 15:47 | 2026-08-17 15:57 | 2026-08-17 15:57 | 2026-08-17 16:37 | 2026-08-17 16:50 | 2026-08-17 16:51 | 2026-08-17 16:51 | BrokenPole |  | Fair | No | Cx reporting streetlight no broken pole found
Outage | J.E.26.08.24511 | C001890483 | Christopher Edwards | KSAN | Completed | Load_249494 | Constant Spring - 210 | 2026-08-16 23:16 | 2026-08-16 23:19 | 2026-08-16 23:26 | 2026-08-16 23:50 | 2026-08-17 00:09 | 2026-08-17 23:49 | 2026-08-17 00:34 | 2026-08-17 00:34 | LeaningPole |  | Fair | No | Rotten 35 ft wood pole consist of secondary wiresPole is rotten and is already marked to be changed Supply is in the area
Outage | J.E.26.08.24718 | C001890484 | Delano Gayle | St.Catherine | Completed | Load_251630 | Rhodens Pen - 410 | 2026-08-16 23:32 | 2026-08-16 23:34 | 2026-08-16 23:38 | 2026-08-16 23:43 | 2026-08-17 03:01 | 2026-08-17 04:04 | 2026-08-17 04:04 | 2026-08-17 04:04 | BrokenWire |  | Fair | No | Reconnect 4 customers at pothead and pole, string and retention 100 #6 triplex use 3 linkets 6 clamps voltage readings 113-114-227
Outage | J.E.26.08.25302 | C001890486 | Daniel Francis | St.Ann | Completed | Load_249335 | Ocho Rios - 510 | 2026-08-17 00:55 | 2026-08-17 00:57 | 2026-08-17 02:29 | 2026-08-17 02:29 | 2026-08-17 02:55 | 2026-08-17 03:19 | 2026-08-17 03:21 | 2026-08-17 03:21 |  |  | Rains | No | Tree on the line we cut it off also change one 10amp fuse pole #464666 power restored
Outage | J.E.26.08.25749 | C001890487 | Christopher Edwards | KSAN | Completed | Load_264325 | Washington Blvd - 510 | 2026-08-17 01:27 | 2026-08-17 01:29 | 2026-08-17 02:22 | 2026-08-17 02:22 | 2026-08-17 02:22 | 2026-08-17 02:23 | 2026-08-17 02:23 | 2026-08-17 02:23 |  |  | Fair | No | Refuse blown junction fuse Using (1) 30 amps
Outage | J.E.26.08.25785 | C001890491 | Daniel Francis | St.Ann | Completed | Load_242953 | Roaring River - 410 | 2026-08-17 04:57 | 2026-08-17 05:00 | 2026-08-17 06:12 | 2026-08-17 06:12 | 2026-08-17 06:12 | 2026-08-17 06:53 | 2026-08-17 06:56 | 2026-08-17 06:56 |  |  | Fair | No | Found junction blown at0166996 one 25 amp renew
Outage | J.E.26.08.25823 | C001890492 | Delano Gayle | St.Catherine | Completed | Load_238241 | Tredegar - 310 | 2026-08-17 05:20 | 2026-08-17 05:21 | 2026-08-17 05:32 | 2026-08-17 05:35 | 2026-08-17 06:08 | 2026-08-17 06:15 | 2026-08-17 06:15 | 2026-08-17 06:15 |  |  | Fair | No | Blown junction in 2 phase T-off to scheme, patrolled and found okay for closure replace 25amps
Outage | J.E.26.08.25785 | C001890499 | Daniel Francis | St.Ann | Completed | Load_242953 | Roaring River - 410 | 2026-08-17 07:07 | 2026-08-17 07:08 | 2026-08-17 07:23 | 2026-08-17 07:24 | 2026-08-17 07:24 | 2026-08-17 07:25 | 2026-08-17 07:34 | 2026-08-17 07:34 |  |  | Rains | No | Patrol and renew 25amp at pole 0166996 however area still out of power. However shit end at 7am
Non-Outage | J.E.26.08.23868 | C001890503 | Clyde Brown |  | Completed |  |  | 2026-08-17 07:31 | 2026-08-17 07:32 | 2026-08-17 11:05 | 2026-08-17 11:06 | 2026-08-17 11:06 | 2026-08-17 11:05 | 2026-08-17 11:08 | 2026-08-17 11:08 |  |  | Fair | No | Cannot be located customer not answering phone
Outage | J.E.26.08.22845 | C001890504 | Clyde Brown | Clarendon | Completed | Load_257675 | Parnassus - 310 | 2026-08-17 07:31 | 2026-08-17 07:33 | 2026-08-17 10:19 | 2026-08-17 10:19 | 2026-08-17 10:43 | 2026-08-17 10:39 | 2026-08-17 10:48 | 2026-08-17 10:48 | LeaningPole |  | Fair | No | Tall bucket truck needed at location Chin to use bucket truck to complete call.
Outage | J.E.26.08.25416 | C001890502 | Clyde Brown | Clarendon | Completed | Load_261972 | Parnassus - 210 | 2026-08-17 07:31 | 2026-08-17 13:45 | 2026-08-17 14:58 | 2026-08-17 14:58 | 2026-08-17 15:31 | 2026-08-17 15:46 | 2026-08-17 15:56 | 2026-08-17 15:56 | BangingWires |  | SevereWind | No | Blown 3 amps fuse for 25 kva transformer caused by secondary phase and neutral entangled due to heavy wind,line cleared and blown fuse replaced.
Outage | J.E.26.08.25870 | C001890505 | Omar King | St.Ann | Completed | Load_249114 | Ocho Rios - 510 | 2026-08-17 07:31 | 2026-08-17 07:32 | 2026-08-17 08:12 | 2026-08-17 09:08 | 2026-08-17 09:08 | 2026-08-17 09:09 | 2026-08-17 09:09 | 2026-08-17 09:09 |  |  | Fair | No | Found 20 amp junction fuse blow cause by bird fuse as been replaced and customer now with supply.
Outage | J.E.26.08.25835 | C001890506 | Omar King | St.Ann | Completed | Load_249881 | Ocho Rios - 310 | 2026-08-17 07:32 | 2026-08-17 07:33 | 2026-08-17 13:04 | 2026-08-17 14:16 | 2026-08-17 14:16 | 2026-08-17 14:17 | 2026-08-17 14:17 | 2026-08-17 14:17 |  |  | Fair | No | Found 50 amp junction fuse blow fuse has been replaced and customer now with supply..
Outage | J.E.26.08.25909 | C001890507 | Omar King | St.Ann | Completed | Load_264883 | Ocho Rios - 510 | 2026-08-17 07:33 | 2026-08-17 07:34 | 2026-08-17 20:12 | 2026-08-17 20:12 | 2026-08-17 20:12 | 2026-08-17 20:13 | 2026-08-17 20:13 | 2026-08-17 20:13 |  |  | Fair | No | Customer is with supply.
Outage | J.E.26.08.25439 | C001890511 | Omar King | St.Ann | Completed | Load_246811 | Roaring River - 410 | 2026-08-17 07:34 | 2026-08-17 07:36 | 2026-08-17 17:30 | 2026-08-17 17:31 | 2026-08-17 19:03 | 2026-08-17 19:05 | 2026-08-17 19:05 | 2026-08-17 19:05 |  |  | Fair | No | Area need bushing please refer to maintenance customer is still with supply.
Outage | J.E.26.08.25717 | C001890512 | Omar King | St.Ann | Completed | Load_555975 | Roaring River - 210 | 2026-08-17 07:34 | 2026-08-17 07:36 | 2026-08-17 09:15 | 2026-08-17 19:06 | 2026-08-17 20:05 | 2026-08-17 20:07 | 2026-08-17 20:07 | 2026-08-17 20:07 |  |  | Fair | No | Found 7 amp junction fuse blow cause by bird fuse has been replaced and customer now with supply..
Outage | J.E.26.08.25723 | C001890509 | Omar King | St.Ann | Completed | Load_256279 | Roaring River - 410 | 2026-08-17 07:34 | 2026-08-17 07:36 | 2026-08-17 15:45 | 2026-08-17 15:45 | 2026-08-17 16:37 | 2026-08-17 16:38 | 2026-08-17 16:38 | 2026-08-17 16:38 | BangingWires |  | Fair | No | Problem as been resolved
Outage | J.E.26.08.25785 | C001890508 | Omar King | St.Ann | Completed | Load_242953 | Roaring River - 410 | 2026-08-17 07:34 | 2026-08-17 09:45 | 2026-08-17 09:48 | 2026-08-17 09:49 | 2026-08-17 10:35 | 2026-08-17 12:59 | 2026-08-17 13:00 | 2026-08-17 13:00 |  |  | Fair | No | Found 1 span primary phase broken cause by tree bushing has been carried out to remove tree limbs found 20 amp junction fuse blow and 10 amp junction fuse blow primary phase has been splice and retention and fuse has been replaced and area is now with supply
Outage | J.E.26.08.25333 | C001890513 | Omar King | St.Ann | Completed | Load_267166 | Roaring River - 210 | 2026-08-17 07:35 | 2026-08-17 07:41 | 2026-08-17 09:15 | 2026-08-17 17:28 | 2026-08-17 17:30 | 2026-08-17 17:30 | 2026-08-17 17:30 | 2026-08-17 17:30 |  |  | Fair | No | Unable to find customer call several times no answer directions not sufficient
Outage | J.E.26.08.25703 | C001890515 | Wan Carlos Scarlett | Portmore | Completed | Load_262887 | Naggo Head - 510 | 2026-08-17 07:36 | 2026-08-17 08:00 | 2026-08-17 09:30 | 2026-08-17 09:31 | 2026-08-17 09:47 | 2026-08-17 10:10 | 2026-08-17 10:12 | 2026-08-17 10:12 | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Found 25KVA transformer defective no pole # was found
Outage | J.E.26.08.25706 | C001890516 | Wan Carlos Scarlett | Portmore | Completed | Load_269754 | Naggo Head - 510 | 2026-08-17 07:36 | 2026-08-17 08:00 | 2026-08-17 10:12 | 2026-08-17 10:12 | 2026-08-17 11:08 | 2026-08-17 11:34 | 2026-08-17 11:34 | 2026-08-17 11:34 | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Call related to defective transformer
Outage | J.E.26.08.22631 | C001890526 | Kemark Slue | St.Catherine | Completed | Load_251876 | New Michelton - 310 | 2026-08-17 07:37 | 2026-08-17 15:44 | 2026-08-17 21:59 | 2026-08-17 22:23 | 2026-08-17 22:23 | 2026-08-17 19:00 | 2026-08-17 22:41 | 2026-08-17 22:41 |  |  | Fair | No | Not a St Catherine call, please refer to St Mary emergency.
Outage | J.E.26.08.25407 | C001890519 | Raymond Carr | St.Mary | Completed | Load_256631 | Blackstonedge - 110 | 2026-08-17 07:37 | 2026-08-17 07:38 | 2026-08-17 12:03 | 2026-08-17 12:04 | 2026-08-17 14:27 | 2026-08-17 14:55 | 2026-08-17 14:51 | 2026-08-17 14:51 |  |  | Fair | No | Blown junction fuse found at pole number 094598, line patrol and found okay lightening was suspected. A 10a fuse was used to renew supply was
Outage | J.E.26.08.25465 | C001890523 | Richard Grant | St.Catherine | Completed | Load_241129 | New Michelton - 210 | 2026-08-17 07:37 | 2026-08-17 07:38 | 2026-08-17 08:25 | 2026-08-17 08:26 | 2026-08-17 10:21 | 2026-08-17 11:22 | 2026-08-17 11:22 | 2026-08-17 11:22 |  |  | Fair | No | Opened secondary lower phase and neutral found joint together caused by incorrect procedure done by VSP Project. Banging wire caused multiple customers equipment to be damaged. 1 #2 preform, 1 #2 sleeve, approximately 20ft #2 wire and 3 onebolt clamps used to retention wire and correct faults. Supply restored and area left okay. Kindly send email to the claims department to have customers complaint checked.
Outage | J.E.26.08.25553 | C001890521 | Raymond Carr | St.Mary | Completed | Load_243605 | Oracabessa - 110 | 2026-08-17 07:37 | 2026-08-17 07:38 | 2026-08-17 08:37 | 2026-08-17 08:37 | 2026-08-17 10:25 | 2026-08-17 10:35 | 2026-08-17 11:02 | 2026-08-17 11:02 | BrokenWire |  | Fair | No | Spliced and retention 1 span of broken secondary conductor using 50 ft#2aa, 1#2 splicing sleeve, 1 one bolt clamp. Supply was restored.
Outage | J.E.26.08.25618 | C001890524 | Kemark Slue | St.Catherine | Completed | Load_269347 | New Michelton - 310 | 2026-08-17 07:37 | 2026-08-17 15:44 | 2026-08-17 18:07 | 2026-08-17 18:07 | 2026-08-17 21:19 | 2026-08-17 18:00 | 2026-08-17 22:21 | 2026-08-17 22:21 | BrokenWire |  | Fair | No | Upon arrival at the location the crew discovered that a 25 kva 13.8 kv transformer fuse was blown resulting from illegal connections that caused four spans of secondary phase and neutral to bang and break, splice and retention conductors using approximately 80 ft of #2 aaac, four #2 splicing sleeves, two #2 preforms, one 2/0 splicing sleeve, refuse link and re-energized circuit.
Outage | J.E.26.08.25648 | C001890527 | Wayne Dillion | Manchester | Completed | Load_252793 | Spur Tree - 210 | 2026-08-17 07:37 | 2026-08-17 07:41 | 2026-08-17 08:53 | 2026-08-17 08:54 | 2026-08-17 08:53 | 2026-08-17 08:57 | 2026-08-17 09:03 | 2026-08-17 09:03 |  |  | Fair | No | Customer is requesting a tree to cut.
Outage | J.E.26.08.25664 | C001890525 | Richard Grant | St.Catherine | Completed | Load_241129 | New Michelton - 210 | 2026-08-17 07:37 | 2026-08-17 07:38 | 2026-08-17 10:21 | 2026-08-17 11:22 | 2026-08-17 11:22 | 2026-08-17 11:23 | 2026-08-17 11:23 | 2026-08-17 11:23 | Fire |  | Fair | No | Opened secondary lower phase and neutral found joint together caused by incorrect procedure done by VSP Project. Banging wire caused multiple customers equipment to be damaged. 1 #2 preform, 1 #2 sleeve, approximately 20ft #2 wire and 3 onebolt clamps used to retention wire and correct faults. Supply restored and area left okay. Kindly send email to the claims department to have customers complaint checked.
Outage | J.E.26.08.25687 | C001890522 | Raymond Carr | St.Mary | Completed | Load_254195 | Highgate - 210 | 2026-08-17 07:37 | 2026-08-17 07:38 | 2026-08-17 11:04 | 2026-08-17 11:04 | 2026-08-17 11:19 | 2026-08-17 11:20 | 2026-08-17 11:21 | 2026-08-17 11:21 |  |  | Fair | No | JPS maintenance crew found on job site.
Outage | J.E.26.08.25905 | C001890520 | Ryan Richards | Manchester | Completed | Load_261236 | Porus - 310 | 2026-08-17 07:37 | 2026-08-17 07:41 | 2026-08-17 08:12 | 2026-08-17 08:12 | 2026-08-17 09:23 | 2026-08-17 09:52 | 2026-08-17 09:52 | 2026-08-17 09:52 |  |  | Fair | No | Blown 3 amp fuse found for 50 kva transformer line patrol nothing found blown fuse was replaced lighting suspected to be the cause all customers are now with supply
Outage | J.E.26.08.25017 | C001890528 | Kemark Slue | St.Catherine | Completed | Load_269347 | New Michelton - 310 | 2026-08-17 07:38 | 2026-08-17 15:44 | 2026-08-17 18:08 | 2026-08-17 22:22 | 2026-08-17 22:21 | 2026-08-17 18:02 | 2026-08-17 22:22 | 2026-08-17 22:22 | BrokenWire |  | Fair | No | Upon arrival at the location the crew discovered that a 25 kva 13.8 kv transformer fuse was blown resulting from illegal connections that caused four spans of secondary phase and neutral to bang and break, splice and retention conductors using approximately 80 ft of #2 aaac, four #2 splicing sleeves, two #2 preforms, one 2/0 splicing sleeve, refuse link and re-energized circuit.
Non-Outage | J.E.26.08.24450 | C001890530 | Derrick Grubb |  | Completed |  |  | 2026-08-17 07:39 | 2026-08-17 07:41 | 2026-08-17 12:31 | 2026-08-17 12:31 | 2026-08-17 13:12 | 2026-08-17 13:12 | 2026-08-17 13:13 | 2026-08-17 13:13 |  | Y | Fair | No | Large cedar tree overhang primary conductor, refer to maintenance
Outage | J.E.26.08.25523 | C001890529 | Hopeton Henry | St.Thomas | Completed | Load_238274 | Good Year - 210 | 2026-08-17 07:39 | 2026-08-17 08:14 | 2026-08-17 08:48 | 2026-08-17 08:49 | 2026-08-17 08:48 | 2026-08-17 09:12 | 2026-08-17 09:13 | 2026-08-17 09:13 |  |  | Fair | No | Use 3 amp at 50 kva transformer
Outage | J.E.26.08.23835 | C001890532 | Derrick Grubb | St.Thomas | Completed | Load_265904 | Lysson - 410 | 2026-08-17 07:40 | 2026-08-17 07:41 | 2026-08-17 07:52 | 2026-08-17 07:53 | 2026-08-17 08:52 | 2026-08-17 08:52 | 2026-08-17 08:52 | 2026-08-17 08:52 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.24012 | C001890531 | Derrick Grubb | St.Thomas | Completed | Load_270126 | Good Year - 210 | 2026-08-17 07:40 | 2026-08-17 07:41 | 2026-08-17 13:13 | 2026-08-17 13:14 | 2026-08-17 14:19 | 2026-08-17 14:20 | 2026-08-17 14:42 | 2026-08-17 14:42 |  |  | Fair | No | Internal problems suspected reading at meter socket 115,116 and 230v.
Outage | J.E.26.08.25856 | C001890533 | Derrick Grubb | St.Thomas | Completed | Load_238970 | Lysson - 410 | 2026-08-17 07:40 | 2026-08-17 07:41 | 2026-08-17 08:53 | 2026-08-17 08:53 | 2026-08-17 10:48 | 2026-08-17 11:01 | 2026-08-17 11:02 | 2026-08-17 11:02 | BrokenWire | Y | Fair | No | Patrol clear bamboo, splice and retention 3 span open secondary phase and neutral, refuse 25 kva transformer in Panton town
Outage | J.E.26.08.25915 | C001890535 | Tyrese Williams | St.Ann | Completed | Load_261182 | Cardiff Hall - 210 | 2026-08-17 07:41 | 2026-08-17 07:43 | 2026-08-17 08:18 | 2026-08-17 08:39 | 2026-08-17 09:50 | 2026-08-17 12:30 | 2026-08-17 12:30 | 2026-08-17 12:30 |  |  | Fair | No | Splice and retention 5 span of secondary phase and neutral use 130 ft off #2AA and 4 pg clamp and 3 splicing sleeve and reclose a 25kva transformer fuse at pole
Outage | J.E.26.08.25884 | C001890536 | Tyrese Williams | St.Ann | Completed | Load_262761 | Cardiff Hall - 210 | 2026-08-17 07:42 | 2026-08-17 07:43 | 2026-08-17 12:32 | 2026-08-17 12:33 | 2026-08-17 12:32 | 2026-08-17 12:33 | 2026-08-17 12:33 | 2026-08-17 12:33 |  |  | Fair | No | Premises found ok customer said the power was restored
Outage | J.E.26.08.25660 | C001890547 | Omar King | St.Ann | Completed | Load_263941 | Upper White River - 210 | 2026-08-17 07:43 | 2026-08-17 07:46 | 2026-08-17 15:13 | 2026-08-17 15:17 | 2026-08-17 15:16 | 2026-08-17 15:17 | 2026-08-17 15:17 | 2026-08-17 15:17 |  |  | Fair | No | Found 25 amp junction fuse blow cause by bird fuse has been replaced and customer now with supply..
Outage | J.E.26.08.25752 | C001890546 | Fitzroy Turner | KSAS | Completed | Load_260842 | Three Miles - 410 | 2026-08-17 07:43 | 2026-08-17 07:45 | 2026-08-17 08:19 | 2026-08-17 08:20 | 2026-08-17 08:58 | 2026-08-17 09:25 | 2026-08-17 09:29 | 2026-08-17 09:29 |  |  | Fair | No | Found tree phase primary one switch top burn out have switches top adjusted and close up supply restored to areas
Outage | J.E.26.08.25592 | C001890550 | Cliton Henry | St.Mary | Completed | Load_265280 | Highgate - 210 | 2026-08-17 07:48 | 2026-08-17 09:24 | 2026-08-17 11:50 | 2026-08-17 11:51 | 2026-08-17 13:08 | 2026-08-17 13:48 | 2026-08-17 13:53 | 2026-08-17 13:53 |  |  | Fair | No | A blown 20 amp junction fuse found at Nutsfield at pole # 0010851 due to lightning. Supply restored using 1-20 amp fuse.
Outage | J.E.26.08.25812 | C001890549 | Neckell Ormsby | St.Mary | Completed | Load_256631 | Blackstonedge - 110 | 2026-08-17 07:48 | 2026-08-17 17:28 | 2026-08-18 15:26 | 2026-08-18 15:26 | 2026-08-18 16:03 | 2026-08-18 16:10 | 2026-08-18 16:10 | 2026-08-18 16:10 |  |  | Fair | No | Found supply ok in area residents said power came back
Outage | J.E.26.08.25910 | C001890548 | Neckell Ormsby | St.Mary | Completed | Load_259062 | Annotto Bay - 310 | 2026-08-17 07:48 | 2026-08-17 17:28 | 2026-08-17 20:44 | 2026-08-17 20:44 | 2026-08-17 21:05 | 2026-08-17 21:16 | 2026-08-17 21:16 | 2026-08-17 21:16 |  |  | Fair | No | Unable to locate customer after several calls however found supply in lodge lane also Xing metering in lodge lane
Outage | J.E.26.08.25538 | C001890553 | Neckell Ormsby | St.Mary | Completed | Load_256860 | Highgate - 210 | 2026-08-17 07:49 | 2026-08-18 15:35 | 2026-08-18 17:11 | 2026-08-18 17:11 | 2026-08-18 17:52 | 2026-08-18 18:02 | 2026-08-18 18:02 | 2026-08-18 18:02 |  |  | Fair | No | Unable to locate customer after several calls however found supply ok in area residents said it’s from Sunday
Outage | J.E.26.08.25756 | C001890556 | Dwayne Cohen |  | Completed | Load_254964 | Constant Spring - 210 | 2026-08-17 07:50 | 2026-08-17 07:52 | 2026-08-17 10:12 | 2026-08-17 10:13 | 2026-08-17 10:12 | 2026-08-17 10:13 | 2026-08-17 10:13 | 2026-08-17 10:13 |  |  | Fair | No | Refuse blown 2amps transformer link, supply now restore. (Hexing box)
Outage | J.E.26.08.25773 | C001890555 | Dwayne Cohen | KSAN | Completed | Load_247933 | Constant Spring - 210 | 2026-08-17 07:50 | 2026-08-17 07:52 | 2026-08-17 10:10 | 2026-08-17 10:10 | 2026-08-17 10:10 | 2026-08-17 10:10 | 2026-08-17 10:10 | 2026-08-17 10:10 |  |  | Fair | No | Refuse blown 2amps transformer link, supply now restore. (Hexing box)
Outage | J.E.26.08.25912 | C001890554 | Dwayne Cohen | KSAN | Completed | Load_250012 | Constant Spring - 410 | 2026-08-17 07:50 | 2026-08-17 07:52 | 2026-08-17 09:22 | 2026-08-17 09:23 | 2026-08-17 09:47 | 2026-08-17 10:08 | 2026-08-17 10:09 | 2026-08-17 10:09 |  |  | Fair | No | Refuse blown 2amps transformer link, supply now restore. (Hexing box)
Outage | J.E.26.08.25762 | C001890557 | Dwayne Cohen | KSAS | Completed | Load_254801 | Greenwich - 510 | 2026-08-17 07:51 | 2026-08-17 07:52 | 2026-08-17 10:11 | 2026-08-17 10:11 | 2026-08-17 10:11 | 2026-08-17 10:11 | 2026-08-17 10:12 | 2026-08-17 10:12 |  |  | Fair | No | Refuse blown 2amps transformer link, supply now restore. (Hexing box)
Outage | J.E.26.08.23786 | C001890559 | Radcliffe Coleman | St.Catherine | Completed | Load_263389 | Twickenham - 310 | 2026-08-17 07:53 | 2026-08-17 07:54 | 2026-08-17 10:18 | 2026-08-17 10:50 | 2026-08-17 10:50 | 2026-08-17 11:11 | 2026-08-17 11:11 | 2026-08-17 11:11 |  |  | Fair | No | Location found with a transformer (25kva) drop lead burnt at pole 0009624. Repairs were done with the aid of five one bolt clamp, also the lugs were serviced. The transformer was open before repairs were done. Customer supply is now back to normal.
Outage | J.E.26.08.25651 | C001890560 | Radcliffe Coleman | St.Catherine | Completed | Load_267112 | Twickenham - 310 | 2026-08-17 07:53 | 2026-08-17 07:54 | 2026-08-17 09:02 | 2026-08-17 09:03 | 2026-08-17 10:44 | 2026-08-17 10:46 | 2026-08-17 10:47 | 2026-08-17 10:47 |  |  | Fair | No | Premises found okay at the time of visit.
Outage | J.E.26.08.25656 | C001890558 | Radcliffe Coleman | St.Catherine | Completed | Load_257721 | Twickenham - 310 | 2026-08-17 07:53 | 2026-08-17 07:54 | 2026-08-17 09:44 | 2026-08-17 10:47 | 2026-08-17 10:47 | 2026-08-17 10:49 | 2026-08-17 10:50 | 2026-08-17 10:50 |  |  | Fair | No | Premises found closed at the time of visit.
Non-Outage | J.E.26.08.22335 | C001890565 | Elvis Trowers |  | Completed |  |  | 2026-08-17 07:56 | 2026-08-17 07:57 | 2026-08-17 08:12 | 2026-08-17 09:25 | 2026-08-17 09:34 | 2026-08-17 09:35 | 2026-08-17 09:42 | 2026-08-17 09:42 |  |  | Fair | No | Meter mix up customer meter # 2188251 need to be change around meter is mix up whit meter #2180118. Refer to field service
Non-Outage | J.E.26.08.25650 | C001890564 | Elvis Trowers |  | Completed |  |  | 2026-08-17 07:56 | 2026-08-17 07:57 | 2026-08-17 12:04 | 2026-08-17 12:05 | 2026-08-17 12:07 | 2026-08-17 12:10 | 2026-08-17 12:10 | 2026-08-17 12:10 | Fire |  | Fair | No | Call related to call at 16 Henry Morgan avenue.
Outage | J.E.26.08.25582 | C001890562 | Elvis Trowers | KSAN | Completed | Load_268663 | Washington Blvd - 710 | 2026-08-17 07:56 | 2026-08-17 07:57 | 2026-08-17 11:50 | 2026-08-17 11:51 | 2026-08-17 11:50 | 2026-08-17 11:55 | 2026-08-17 11:57 | 2026-08-17 11:57 |  |  | Fair | No | Isolate 50 kva transformer at pole # 565329 and repair burnt off transformer drop lead. Repair using two 1- bolt clamps. And reclosed transformer switch.
Outage | J.E.26.08.25710 | C001890561 | Elvis Trowers | KSAN | Completed | Load_268663 | Washington Blvd - 710 | 2026-08-17 07:56 | 2026-08-17 07:57 | 2026-08-17 12:11 | 2026-08-17 12:11 | 2026-08-17 12:11 | 2026-08-17 02:15 | 2026-08-17 12:12 | 2026-08-17 12:12 | Fire |  | Fair | No | Call related to call at #16 Henry Morgan avenue.
Non-Outage | J.E.26.08.20395 | C001890568 | Andrae Clarke | Portland | Completed | Load_269192 | Port Antonio - 310 | 2026-08-17 07:57 | 2026-08-17 08:06 | 2026-08-17 15:00 | 2026-08-17 15:01 | 2026-08-17 15:00 | 2026-08-17 15:16 | 2026-08-17 15:03 | 2026-08-17 15:03 |  |  | Fair | No | Repair broken wire use two one bolt clamp Check voltage 117/118/236
Non-Outage | J.E.26.08.22375 | C001890567 | Andrae Clarke | Portland | Completed | Load_351269 | Port Antonio - 410 | 2026-08-17 07:57 | 2026-08-17 08:06 | 2026-08-17 11:04 | 2026-08-17 15:04 | 2026-08-17 15:48 | 2026-08-17 16:30 | 2026-08-17 15:54 | 2026-08-17 15:54 |  | Y | Fair | No | Entire area affected due to leaning pole and tree on wireRefer to maintenance Pole leaning Check voltage 116/121/237
Non-Outage | J.E.26.08.25197 | C001890570 | Andrae Clarke | Portland | Completed | Load_268893 | Port Antonio - 410 | 2026-08-17 07:58 | 2026-08-17 08:06 | 2026-08-17 09:33 | 2026-08-17 09:34 | 2026-08-17 10:20 | 2026-08-17 10:26 | 2026-08-17 10:24 | 2026-08-17 10:24 |  | Y | Fair | No | Refer to emergency
Non-Outage | J.E.26.08.25586 | C001890569 | Andrae Clarke | Portland | Completed | Load_263415 | Port Antonio - 410 | 2026-08-17 07:58 | 2026-08-17 08:06 | 2026-08-17 08:38 | 2026-08-17 10:25 | 2026-08-17 11:05 | 2026-08-17 11:59 | 2026-08-17 13:35 | 2026-08-17 13:35 |  | Y | Fair | No | Clear wire from vegetation Change one hundred feet of wire four one bolt clamp Check voltage 117/112/229
Non-Outage | J.E.26.08.13668 | C001890572 | Dwayne Cohen | KSAN | Completed | Load_251797 | Constant Spring - 410 | 2026-08-17 08:00 | 2026-08-17 08:01 | 2026-08-17 10:13 | 2026-08-17 10:14 | 2026-08-17 10:56 | 2026-08-17 11:41 | 2026-08-17 11:43 | 2026-08-17 11:43 |  |  | Fair | No | Repair burnt jumper found in the 4/0 twisted circuit, supply now restore.
Outage | J.E.26.08.25853 | C001890573 | Richman Whyte | Westmoreland | Completed | Load_252691 | Paradise - 310 | 2026-08-17 08:00 | 2026-08-17 08:01 | 2026-08-17 11:41 | 2026-08-17 12:07 | 2026-08-17 12:07 | 2026-08-17 12:07 | 2026-08-17 12:08 | 2026-08-17 12:08 |  |  | Fair | No | Run an connected 110ft #6 triplex service wire voltage # 113 113 226
Outage | J.E.26.08.25923 | C001890571 | Ryan Richards | Manchester | Completed | Load_301405 | Porus - 310 | 2026-08-17 08:00 | 2026-08-17 08:02 | 2026-08-17 09:53 | 2026-08-17 09:53 | 2026-08-17 10:03 | 2026-08-17 10:50 | 2026-08-17 10:54 | 2026-08-17 10:54 |  |  | Fair | No | 'Blown 3 amp fuse found for 50 kva transformer line patrol nothing found blown fuse was replaced lighting suspected to be the cause all customers are now with supply
Non-Outage | J.E.26.07.35299 | C001890587 | Odeanie Davis | KSAS | Completed | Load_243540 | Rockfort - 410 | 2026-08-17 08:06 | 2026-08-17 08:08 | 2026-08-17 09:59 | 2026-08-17 10:00 | 2026-08-17 10:03 | 2026-08-17 10:10 | 2026-08-17 10:10 | 2026-08-17 10:10 |  |  | Fair | No | 116v/108v & 224v at location, customer stated that issue was resolved,
Non-Outage | J.E.26.08.04106 | C001890583 | Odeanie Davis | KSAS | Completed | Load_239845 | Rockfort - 410 | 2026-08-17 08:06 | 2026-08-17 08:08 | 2026-08-17 11:01 | 2026-08-17 11:01 | 2026-08-17 11:01 | 2026-08-17 11:20 | 2026-08-17 11:20 | 2026-08-17 11:20 |  |  | Fair | No | 112v/105v & 217v at location, no power issues found. Meter was ping & communicating fine
Non-Outage | J.E.26.08.04645 | C001890582 | Odeanie Davis | KSAS | Completed | Load_267316 | Rockfort - 410 | 2026-08-17 08:06 | 2026-08-17 08:08 | 2026-08-17 10:53 | 2026-08-17 13:44 | 2026-08-17 13:43 | 2026-08-17 13:57 | 2026-08-17 13:45 | 2026-08-17 13:45 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.04676 | C001890584 | Odeanie Davis | KSAS | Completed | Load_257438 | Rockfort - 410 | 2026-08-17 08:06 | 2026-08-17 08:08 | 2026-08-17 12:14 | 2026-08-17 12:53 | 2026-08-17 12:54 | 2026-08-17 13:08 | 2026-08-17 13:08 | 2026-08-17 13:08 |  |  | Fair | No | Customer defective meter socket, 116v/116v & 233v at location, customer was advised to contact their electrician
Non-Outage | J.E.26.08.15529 | C001890581 | Odeanie Davis | KSAS | Completed | Load_241686 | Rockfort - 410 | 2026-08-17 08:06 | 2026-08-17 08:08 | 2026-08-17 12:14 | 2026-08-17 12:17 | 2026-08-17 12:16 | 2026-08-17 12:22 | 2026-08-17 12:22 | 2026-08-17 12:22 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.15628 | C001890580 | Odeanie Davis | KSAS | Completed | Load_265479 | Rockfort - 410 | 2026-08-17 08:06 | 2026-08-17 08:08 | 2026-08-17 12:14 | 2026-08-17 12:27 | 2026-08-17 12:33 | 2026-08-17 12:52 | 2026-08-17 12:52 | 2026-08-17 12:52 | LowHangingWires |  | Fair | No | 108v/116v at arrival, open circuit at pothead corrected, 1 penn union, 116v/116v & 233v after correction
Non-Outage | J.E.26.08.16495 | C001890578 | Odeanie Davis | KSAS | Completed | Load_266014 | Rockfort - 410 | 2026-08-17 08:06 | 2026-08-17 08:08 | 2026-08-17 10:18 | 2026-08-18 12:28 | 2026-08-18 12:28 | 2026-08-18 12:37 | 2026-08-18 12:31 | 2026-08-18 12:31 |  |  | Fair | No | 111v/118v & 230v at location, meter socket found burnt, customer contacted their electrician & resolved issue, meter was reinstalled and power was restored to customer, meter was ping and communicating fine
Non-Outage | J.E.26.08.16745 | C001890577 | Odeanie Davis | KSAS | Completed | Load_268072 | Rockfort - 410 | 2026-08-17 08:06 | 2026-08-17 08:08 | 2026-08-17 09:09 | 2026-08-17 09:10 | 2026-08-17 09:19 | 2026-08-17 09:58 | 2026-08-17 09:58 | 2026-08-17 09:58 |  |  | Fair | No | 69v/176v at arrival, open neutral on secondary line from transformer corrected, 1 one bolt clamp, 113v/17v & 231v after correction.
Non-Outage | J.E.26.08.19018 | C001890579 | Odeanie Davis | KSAS | Completed | Load_248008 | Rockfort - 410 | 2026-08-17 08:06 | 2026-08-17 08:08 | 2026-08-17 12:01 | 2026-08-17 12:01 | 2026-08-17 12:01 | 2026-08-17 12:08 | 2026-08-17 12:08 | 2026-08-17 12:08 |  |  | Fair | No | 67v/167v at arrival, open neutral on customer line corrected, 1 one bolt clamp, 2 penn union, 2 penn union & 1 pipe rider, 117v/118v & 235v after correction.
Non-Outage | J.E.26.08.21503 | C001890576 | Odeanie Davis | KSAS | Completed | Load_261556 | Rockfort - 410 | 2026-08-17 08:06 | 2026-08-17 08:08 | 2026-08-17 10:12 | 2026-08-17 12:23 | 2026-08-17 12:23 | 2026-08-17 12:33 | 2026-08-17 12:24 | 2026-08-17 12:24 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.21783 | C001890593 | Roemello Brown | Trelawny | Completed | Load_255120 | Martha Brae - 110 | 2026-08-17 08:06 | 2026-08-17 08:39 | 2026-08-17 09:55 | 2026-08-17 10:16 | 2026-08-17 10:19 | 2026-08-17 10:19 | 2026-08-17 10:36 | 2026-08-17 10:36 |  |  | Rains | No | Premises found working okay when I check the premises Voltage found 115/115/231Voltage leave 115/115/231
Non-Outage | J.E.26.08.22719 | C001890594 | Roemello Brown | Trelawny | Completed | Load_570268 | Martha Brae - 110 | 2026-08-17 08:06 | 2026-08-17 08:39 | 2026-08-17 08:51 | 2026-08-17 08:59 | 2026-08-17 09:27 | 2026-08-17 09:27 | 2026-08-17 09:46 | 2026-08-17 09:46 |  |  | Rains | No | Premises found working ok when I check the premises Voltage found 116/116/232Voltage leave 116/116/232
Non-Outage | J.E.26.08.24760 | C001890595 | Roemello Brown | Trelawny | Completed | Load_294320 | Martha Brae - 110 | 2026-08-17 08:06 | 2026-08-17 08:39 | 2026-08-17 08:54 | 2026-08-17 09:47 | 2026-08-17 10:11 | 2026-08-17 10:11 | 2026-08-17 10:15 | 2026-08-17 10:15 |  |  | Rains | No | Premises found working okay when I check premises Voltage found 114/115/229Voltage leave 114/115/229
Non-Outage | J.E.26.08.21831 | C001890600 | Oraine Minto | St.Ann | Completed | Load_304996 | Cardiff Hall - 310 | 2026-08-17 08:08 | 2026-08-17 08:09 | 2026-08-17 11:47 | 2026-08-17 11:49 | 2026-08-17 11:49 | 2026-08-17 11:49 | 2026-08-17 11:50 | 2026-08-17 11:50 |  |  | Fair | No | Power restored
Non-Outage | J.E.26.08.22692 | C001890599 | Oraine Minto | St.Ann | Completed | Load_256738 | Cardiff Hall - 310 | 2026-08-17 08:08 | 2026-08-17 08:09 | 2026-08-17 12:31 | 2026-08-17 12:31 | 2026-08-17 12:33 | 2026-08-17 12:33 | 2026-08-17 12:35 | 2026-08-17 12:35 |  |  | Fair | No | Refer to emergency Customer states the entire area is experiencing the issue and it is happening 3 weeks now
Non-Outage | J.E.26.08.22906 | C001890598 | Oraine Minto | St.Ann | Completed | Load_1007208 | Cardiff Hall - 310 | 2026-08-17 08:08 | 2026-08-17 08:09 | 2026-08-17 12:24 | 2026-08-17 12:25 | 2026-08-17 12:24 | 2026-08-17 12:27 | 2026-08-17 12:30 | 2026-08-17 12:30 |  |  | Fair | No | Refer to field service Voltage is ok but the tenant say the power is in an out Meter in the rami
Non-Outage | J.E.26.08.22906 | C001890602 | Oraine Minto | St.Ann | Completed | Load_1007208 | Cardiff Hall - 310 | 2026-08-17 08:08 | 2026-08-17 08:09 | 2026-08-17 12:22 | 2026-08-17 12:23 | 2026-08-17 12:22 | 2026-08-17 12:23 | 2026-08-17 12:23 | 2026-08-17 12:23 |  |  | Fair | No | 238v 118v 117v
Non-Outage | J.E.26.08.23789 | C001890604 | Oraine Minto | St.Ann | Completed | Load_246438 | Cardiff Hall - 310 | 2026-08-17 08:08 | 2026-08-17 08:09 | 2026-08-17 15:31 | 2026-08-17 15:32 | 2026-08-17 15:31 | 2026-08-17 15:32 | 2026-08-17 15:33 | 2026-08-17 15:33 |  |  | Fair | No | Customer states issue was resolved
Non-Outage | J.E.26.08.24813 | C001890603 | Oraine Minto | St.Ann | Completed | Load_269371 | Cardiff Hall - 310 | 2026-08-17 08:08 | 2026-08-17 08:09 | 2026-08-17 10:44 | 2026-08-17 11:36 | 2026-08-17 11:36 | 2026-08-17 11:36 | 2026-08-17 11:36 | 2026-08-17 11:36 |  |  | Fair | No | Power was restored
Non-Outage | J.E.26.07.27459 | C001890610 | Christopher Edwards | KSAN | Completed | Load_267672 | Constant Spring - 210 | 2026-08-17 08:10 | 2026-08-17 08:12 | 2026-08-17 08:27 | 2026-08-17 09:13 | 2026-08-17 09:35 | 2026-08-17 09:46 | 2026-08-17 09:50 | 2026-08-17 09:50 |  |  | Fair | No | 25 kva transformer is supplying 5 different roads Customer states the low voltage issue only occurs at night Voltage:110,109,211vObserved that poles are being planted to extend the primary line
Non-Outage | J.E.26.08.15618 | C001890612 | Christopher Edwards | KSAN | Completed | Load_263547 | Constant Spring - 410 | 2026-08-17 08:10 | 2026-08-17 08:12 | 2026-08-17 11:50 | 2026-08-17 12:19 | 2026-08-17 12:18 | 2026-08-17 12:18 | 2026-08-17 12:19 | 2026-08-17 12:19 |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Non-Outage | J.E.26.08.20989 | C001890611 | Christopher Edwards | KSAN | Completed | Load_240100 | Constant Spring - 410 | 2026-08-17 08:10 | 2026-08-17 08:12 | 2026-08-17 09:55 | 2026-08-17 09:56 | 2026-08-17 10:40 | 2026-08-17 11:17 | 2026-08-17 11:18 | 2026-08-17 11:18 |  |  | Fair | No | Remake corroded neutral joint Using (1) one bolt clamps Voltage:112,113,219v
Non-Outage | J.E.26.08.22345 | C001890608 | Christopher Edwards | KSAN | Completed | Load_261490 | Constant Spring - 410 | 2026-08-17 08:10 | 2026-08-17 08:12 | 2026-08-17 11:49 | 2026-08-17 11:50 | 2026-08-17 11:49 | 2026-08-17 11:49 | 2026-08-17 11:50 | 2026-08-17 11:50 |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Non-Outage | J.E.26.08.22517 | C001890607 | Christopher Edwards | KSAN | Completed | Load_264959 | Constant Spring - 410 | 2026-08-17 08:10 | 2026-08-17 08:12 | 2026-08-17 11:20 | 2026-08-17 11:45 | 2026-08-17 11:44 | 2026-08-17 11:48 | 2026-08-17 11:49 | 2026-08-17 11:49 |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Outage | J.E.26.08.25950 | C001890609 | Christopher Edwards | KSAN | Completed | Load_267672 | Constant Spring - 210 | 2026-08-17 08:10 | 2026-08-17 08:12 | 2026-08-17 08:15 | 2026-08-17 08:39 | 2026-08-17 08:52 | 2026-08-17 09:11 | 2026-08-17 09:12 | 2026-08-17 09:12 |  |  | Fair | No | Customer meter is burnt and needs to be replaced Meter#2722382
Non-Outage | J.E.26.07.27372 | C001890613 | Christopher Edwards | KSAN | Completed | Load_302960 | Constant Spring - 210 | 2026-08-17 08:11 | 2026-08-17 08:12 | 2026-08-17 09:52 | 2026-08-17 09:55 | 2026-08-17 09:54 | 2026-08-17 09:55 | 2026-08-17 09:55 | 2026-08-17 09:55 |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Non-Outage | J.E.26.08.16781 | C001890621 | Error Coore | Manchester | Completed | Load_292850 | Kendal - 310 | 2026-08-17 08:11 | 2026-08-17 08:13 | 2026-08-18 16:13 | 2026-08-18 16:14 | 2026-08-18 16:53 | 2026-08-18 17:18 | 2026-08-18 17:19 | 2026-08-18 17:19 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.08.17837 | C001890618 | Error Coore | Manchester | Completed | Load_240406 | Kendal - 310 | 2026-08-17 08:11 | 2026-08-17 08:13 | 2026-08-18 08:14 | 2026-08-18 08:14 | 2026-08-18 08:47 | 2026-08-18 09:00 | 2026-08-18 09:01 | 2026-08-18 09:01 |  |  | Fair | No | Premises not found not getting customer on phone
Non-Outage | J.E.26.06.21234 | C001890635 | Error Coore | Manchester | Completed | Load_573426 | Spur Tree - 310 | 2026-08-17 08:15 | 2026-08-17 08:16 | 2026-08-17 16:03 | 2026-08-17 16:04 | 2026-08-18 08:02 | 2026-08-18 08:02 | 2026-08-18 08:05 | 2026-08-18 08:05 |  |  | Fair | No | Not getting on phone premises not found
Non-Outage | J.E.26.06.34940 | C001890636 | Error Coore | Manchester | Completed | Load_294675 | Spur Tree - 310 | 2026-08-17 08:15 | 2026-08-17 08:16 | 2026-08-17 14:51 | 2026-08-17 14:52 | 2026-08-17 15:36 | 2026-08-17 16:01 | 2026-08-17 16:03 | 2026-08-17 16:03 |  |  | Fair | No | Premises found ok voltage reading 118/117/235 volts
Non-Outage | J.E.26.06.38346 | C001890634 | Error Coore | Manchester | Completed | Load_241522 | Spur Tree - 310 | 2026-08-17 08:15 | 2026-08-17 08:16 | 2026-08-17 08:41 | 2026-08-17 08:42 | 2026-08-17 09:28 | 2026-08-17 09:43 | 2026-08-17 09:45 | 2026-08-17 09:45 |  |  | Fair | No | Premises found ok voltage reading 116/114/230 volts
Non-Outage | J.E.26.07.14629 | C001890624 | Rusean Allen | KSAS | Completed | Load_255768 | Hunts Bay - 310 | 2026-08-17 08:15 | 2026-08-17 08:16 | 2026-08-17 13:41 | 2026-08-17 13:41 | 2026-08-17 13:49 | 2026-08-17 14:03 | 2026-08-17 14:04 | 2026-08-17 14:04 |  |  | Fair | No | Voltage: 121 121 241
Non-Outage | J.E.26.07.21284 | C001890623 | Rusean Allen | KSAS | Completed | Load_267729 | Rockfort - 410 | 2026-08-17 08:15 | 2026-08-17 08:16 | 2026-08-17 10:25 | 2026-08-17 10:26 | 2026-08-17 10:32 | 2026-08-17 10:34 | 2026-08-17 10:35 | 2026-08-17 10:35 |  |  | Fair | No | Line side of pothead found okay, customer was advised to contact electrician.Voltage: 117 116 234
Non-Outage | J.E.26.08.04236 | C001890625 | Rusean Allen | KSAS | Completed | Load_289600 | Greenwich - 510 | 2026-08-17 08:15 | 2026-08-17 08:16 | 2026-08-17 09:01 | 2026-08-17 09:02 | 2026-08-17 10:09 | 2026-08-17 10:12 | 2026-08-17 10:13 | 2026-08-17 10:13 |  |  | Fair | No | Premises found locked, customer phone went unanswered.
Non-Outage | J.E.26.08.04804 | C001890629 | Rusean Allen | KSAS | Completed | Load_253177 | Rockfort - 410 | 2026-08-17 08:15 | 2026-08-17 08:16 | 2026-08-17 10:52 | 2026-08-17 11:59 | 2026-08-17 11:59 | 2026-08-17 11:59 | 2026-08-17 12:00 | 2026-08-17 12:00 |  |  | Fair | No | Voltage: 115 115 230
Non-Outage | J.E.26.08.05271 | C001890627 | Rusean Allen | KSAS | Completed | Load_253177 | Rockfort - 410 | 2026-08-17 08:15 | 2026-08-17 08:16 | 2026-08-17 10:52 | 2026-08-17 11:37 | 2026-08-17 11:37 | 2026-08-17 11:39 | 2026-08-17 11:39 | 2026-08-17 11:39 |  |  | Fair | No | Voltage: 115 115 230
Non-Outage | J.E.26.08.06444 | C001890633 | Rusean Allen | KSAS | Completed | Load_246732 | Rockfort - 210 | 2026-08-17 08:15 | 2026-08-17 08:16 | 2026-08-17 10:54 | 2026-08-17 10:54 | 2026-08-17 11:21 | 2026-08-17 11:36 | 2026-08-17 11:36 | 2026-08-17 11:36 |  |  | Fair | No | Burnt clamp Changed at secondary jumper. Voltage: 115 116 231
Non-Outage | J.E.26.08.08102 | C001890626 | Rusean Allen | KSAS | Completed | Load_253177 | Hunts Bay - 210 | 2026-08-17 08:15 | 2026-08-17 08:16 | 2026-08-17 10:36 | 2026-08-17 10:38 | 2026-08-17 10:48 | 2026-08-17 10:50 | 2026-08-17 10:51 | 2026-08-17 10:51 |  |  | Fair | No | Premises okay. Voltage 116 116 231
Non-Outage | J.E.26.08.09743 | C001890628 | Rusean Allen | KSAS | Completed | Load_253177 | Hunts Bay - 210 | 2026-08-17 08:15 | 2026-08-17 08:16 | 2026-08-17 10:51 | 2026-08-17 11:58 | 2026-08-17 11:58 | 2026-08-17 11:58 | 2026-08-17 11:59 | 2026-08-17 11:59 |  |  | Fair | No | Voltage: 115 115 230
Non-Outage | J.E.26.06.12384 | C001890638 | Error Coore | Manchester | Completed | Load_254935 | Spur Tree - 310 | 2026-08-17 08:16 | 2026-08-17 08:16 | 2026-08-17 12:46 | 2026-08-17 12:46 | 2026-08-17 13:16 | 2026-08-17 13:34 | 2026-08-17 13:34 | 2026-08-17 13:34 | Fire |  | Fair | No | Premises not found not getting customer an phone
Non-Outage | J.E.26.06.20698 | C001890637 | Error Coore | Manchester | Completed | Load_292202 | Spur Tree - 310 | 2026-08-17 08:16 | 2026-08-17 08:16 | 2026-08-17 09:45 | 2026-08-17 09:46 | 2026-08-17 10:40 | 2026-08-17 11:30 | 2026-08-17 11:31 | 2026-08-17 11:31 |  |  | EarthMovement | No | Found customer with corroded phase at pothead remade corroded phase using 2 service sleeve voltage reading 117/116/233 volts
Non-Outage | J.E.26.06.20929 | C001890639 | Error Coore | Manchester | Completed | Load_256977 | Spur Tree - 310 | 2026-08-17 08:16 | 2026-08-17 08:16 | 2026-08-17 13:35 | 2026-08-17 13:35 | 2026-08-17 14:26 | 2026-08-17 14:48 | 2026-08-17 14:51 | 2026-08-17 14:51 |  |  | Fair | No | Premises not found not getting customer on phone
Non-Outage | J.E.26.08.25865 | C001890641 | Locksley Allen | St.Mary | Completed | Load_261055 | Highgate - 210 | 2026-08-17 08:17 | 2026-08-17 08:27 | 2026-08-18 13:26 | 2026-08-18 13:27 | 2026-08-18 13:26 | 2026-08-18 13:31 | 2026-08-18 13:30 | 2026-08-18 13:30 |  |  | Fair | No | Need better direction and customer not answering the phone
Non-Outage | J.E.26.08.21684 | C001890642 | Locksley Allen | St.Mary | Completed | Load_242166 | Highgate -110 | 2026-08-17 08:18 | 2026-08-17 08:27 | 2026-08-17 13:26 | 2026-08-17 14:30 | 2026-08-17 14:29 | 2026-08-17 14:36 | 2026-08-17 14:34 | 2026-08-17 14:34 |  |  | Fair | No | Low voltage (145v) problem found at the premises,and several customers in this area is having the same problem. Please refer to emergency
Non-Outage | J.E.26.08.21829 | C001890643 | Locksley Allen | St.Mary | Completed | Load_267302 | Highgate -110 | 2026-08-17 08:18 | 2026-08-17 08:27 | 2026-08-17 10:56 | 2026-08-17 11:26 | 2026-08-17 11:25 | 2026-08-17 11:30 | 2026-08-17 11:30 | 2026-08-17 11:30 |  |  | Fair | No | Meter found blank. The service wire neutral burst at the pole Connect neutral wire at pole. Voltage at meter socket phase to neutral 110vMeter left working okay
Non-Outage | J.E.26.08.21850 | C001890644 | Locksley Allen | St.Mary | Completed | Load_242166 | Highgate -110 | 2026-08-17 08:18 | 2026-08-17 08:27 | 2026-08-17 14:54 | 2026-08-17 14:55 | 2026-08-17 14:54 | 2026-08-17 15:01 | 2026-08-17 15:00 | 2026-08-17 15:00 |  |  | Fair | No | Low voltage problem found at this premises,several customers in this area is having the same problem. The secondary line is slack and needs to be bush urgently. Flow line is resting on the lower conductor near this customer house.
Non-Outage | J.E.26.08.22392 | C001890646 | Locksley Allen | St.Mary | Completed | Load_244255 | Highgate -110 | 2026-08-17 08:18 | 2026-08-17 08:27 | 2026-08-17 12:46 | 2026-08-17 13:14 | 2026-08-17 13:14 | 2026-08-17 13:27 | 2026-08-17 13:23 | 2026-08-17 13:23 |  |  | Fair | No | Pothead found corroded. Clean up pothead Voltage at meter socket phase to phase 228v. Phase to neutral 108&109vMeter left working okay
Non-Outage | J.E.26.08.22618 | C001890645 | Locksley Allen | St.Mary | Completed | Load_242166 | Highgate -110 | 2026-08-17 08:18 | 2026-08-17 08:27 | 2026-08-17 15:01 | 2026-08-17 15:01 | 2026-08-17 15:01 | 2026-08-17 15:06 | 2026-08-17 15:02 | 2026-08-17 15:02 |  |  | Fair | No | Low voltage problem found in this area. Check transformer. Refer to emergency
Non-Outage | J.E.26.08.25461 | C001890648 | Locksley Allen | St.Mary | Completed | Load_256249 | Oracabessa - 110 | 2026-08-17 08:18 | 2026-08-17 08:32 | 2026-08-17 15:03 | 2026-08-17 15:54 | 2026-08-17 15:55 | 2026-08-17 16:11 | 2026-08-17 16:11 | 2026-08-17 16:11 |  |  | Fair | No | Service wire neutral burst at the pole. Connect neutral wire.Voltage at meter socket phase to phase 228v. Phase to neutral 112&111vMeter left
Non-Outage | J.E.26.08.25896 | C001890647 | Locksley Allen | St.Mary | Completed | Load_254745 | Highgate -110 | 2026-08-17 08:18 | 2026-08-17 08:27 | 2026-08-17 11:31 | 2026-08-17 12:29 | 2026-08-17 12:29 | 2026-08-17 12:48 | 2026-08-17 12:46 | 2026-08-17 12:46 |  |  | Fair | No | More than one customer in this area is having the same problem Voltage at meter socket phase to phase 224v. Phase to neutral 115&105Check transformer
Non-Outage | J.E.26.08.25925 | C001890649 | Odeanie Davis | KSAS | Completed | Load_1002691 | Cane River - 410 | 2026-08-17 08:20 | 2026-08-17 08:21 | 2026-08-17 08:37 | 2026-08-17 08:37 | 2026-08-17 08:48 | 2026-08-17 08:58 | 2026-08-17 08:58 | 2026-08-17 08:58 |  |  | Fair | No | 119v/117v & 238v at location, customer stated that issue was resolved by Jps
Outage | J.E.26.08.25960 | C001890651 | Oshane Warren | Westmoreland | Completed | Load_239271 | Paradise - 110 | 2026-08-17 08:22 | 2026-08-17 08:23 | 2026-08-17 08:40 | 2026-08-17 08:40 | 2026-08-17 10:20 | 2026-08-17 10:20 | 2026-08-17 10:21 | 2026-08-17 10:21 |  |  | Fair | No | Unable to locate or contact customer need direction
Non-Outage | J.E.26.07.24243 | C001890658 | Dwain Samuels | St.Elizabeth | Completed | Load_254688 | Maggotty - 110 | 2026-08-17 08:24 | 2026-08-17 08:26 | 2026-08-17 08:40 | 2026-08-17 10:55 | 2026-08-17 11:31 | 2026-08-17 11:42 | 2026-08-17 11:44 | 2026-08-17 11:44 |  |  | Fair | No | Found working okay. Voltage check 117-116-233
Non-Outage | J.E.26.07.24440 | C001890655 | Dwain Samuels | St.Elizabeth | Completed | Load_265987 | Maggotty - 110 | 2026-08-17 08:24 | 2026-08-17 08:26 | 2026-08-17 08:40 | 2026-08-17 10:26 | 2026-08-17 10:28 | 2026-08-17 10:47 | 2026-08-17 10:48 | 2026-08-17 10:48 |  |  | Fair | No | Found working okay. Voltage check 116-116-232
Non-Outage | J.E.26.08.13388 | C001890656 | Dwain Samuels | St.Elizabeth | Completed | Load_238298 | Maggotty - 110 | 2026-08-17 08:24 | 2026-08-17 08:26 | 2026-08-17 08:40 | 2026-08-17 09:02 | 2026-08-17 09:40 | 2026-08-17 10:20 | 2026-08-17 10:23 | 2026-08-17 10:23 |  |  | Fair | Yes | Corrosion found at 3 wire pole. Voltage check 117-72-189. Corrosion clear use 2 one bolt clamp. Voltage check 117-117-234
Non-Outage | J.E.26.08.19662 | C001890657 | Dwain Samuels | St.Elizabeth | Completed | Load_246277 | Maggotty - 110 | 2026-08-17 08:24 | 2026-08-17 08:26 | 2026-08-17 08:40 | 2026-08-17 11:45 | 2026-08-17 11:45 | 2026-08-17 11:54 | 2026-08-17 11:54 | 2026-08-17 11:54 |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.08.25286 | C001890653 | Richman Whyte | Westmoreland | Completed | Load_292769 | Paradise - 210 | 2026-08-17 08:24 | 2026-08-17 16:02 | 2026-08-17 21:43 | 2026-08-17 21:43 | 2026-08-17 21:43 | 2026-08-17 21:43 | 2026-08-17 21:44 | 2026-08-17 21:44 |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.08.25565 | C001890654 | Dwain Samuels | Westmoreland | Completed | Load_245673 | Paradise - 310 | 2026-08-17 08:24 | 2026-08-17 08:26 | 2026-08-17 08:40 | 2026-08-17 12:53 | 2026-08-17 13:02 | 2026-08-17 13:20 | 2026-08-17 13:23 | 2026-08-17 13:23 |  |  | Fair | No | Area affected by low voltage due to thieft lots of throw ups on the line
Non-Outage | J.E.26.08.13734 | C001890677 | Fredrick Hamilton | KSAS | Completed | Load_265850 | Greenwich - 710 | 2026-08-17 08:26 | 2026-08-17 08:28 | 2026-08-17 08:32 | 2026-08-17 09:57 | 2026-08-17 10:04 | 2026-08-17 10:13 | 2026-08-17 10:13 | 2026-08-17 10:13 |  |  | Fair | No | 239.6v/118.4v/120.4v obtained Premises checked and found ok no issues detected
Non-Outage | J.E.26.08.13866 | C001890676 | Fredrick Hamilton | KSAS | Completed | Load_259553 | Greenwich - 710 | 2026-08-17 08:26 | 2026-08-17 08:28 | 2026-08-17 08:32 | 2026-08-17 08:59 | 2026-08-17 08:58 | 2026-08-17 09:00 | 2026-08-17 09:00 | 2026-08-17 09:00 |  |  | Fair | No | Customer contacted and stated that power was restored fully at location About 2 weeks agoPremises is ok
Non-Outage | J.E.26.08.13870 | C001890675 | Fredrick Hamilton | KSAS | Completed | Load_256936 | Greenwich - 710 | 2026-08-17 08:26 | 2026-08-17 08:28 | 2026-08-17 08:32 | 2026-08-17 08:54 | 2026-08-17 08:54 | 2026-08-17 08:56 | 2026-08-17 08:56 | 2026-08-17 08:56 |  |  | Fair | No | Customer contacted and stated that power was restored fully from last week Premises is ok
Non-Outage | J.E.26.08.13876 | C001890674 | Fredrick Hamilton | KSAS | Completed | Load_260758 | Greenwich - 710 | 2026-08-17 08:26 | 2026-08-17 08:28 | 2026-08-17 08:32 | 2026-08-17 09:04 | 2026-08-17 09:04 | 2026-08-17 09:11 | 2026-08-17 09:11 | 2026-08-17 09:11 |  |  | Fair | No | Customer contacted and stated that power was restored fully at location Premises is ok
Non-Outage | J.E.26.08.13881 | C001890673 | Fredrick Hamilton | KSAS | Completed | Load_241259 | Greenwich - 710 | 2026-08-17 08:26 | 2026-08-17 08:28 | 2026-08-17 08:32 | 2026-08-18 08:03 | 2026-08-18 08:03 | 2026-08-18 08:06 | 2026-08-18 08:06 | 2026-08-18 08:06 |  |  | Fair | No | Customer contacted and stated that power was restored fully previously Premises is ok
Non-Outage | J.E.26.08.13885 | C001890671 | Fredrick Hamilton | KSAS | Completed | Load_254799 | Greenwich - 710 | 2026-08-17 08:26 | 2026-08-17 08:28 | 2026-08-17 08:32 | 2026-08-17 11:11 | 2026-08-17 11:11 | 2026-08-17 11:12 | 2026-08-17 11:12 | 2026-08-17 11:12 |  |  | Fair | No | Customer contacted and stated that power was restored fully from last week Premises is ok
Non-Outage | J.E.26.08.13926 | C001890670 | Fredrick Hamilton | KSAS | Completed | Load_248863 | Greenwich - 710 | 2026-08-17 08:26 | 2026-08-17 08:28 | 2026-08-17 08:32 | 2026-08-17 11:03 | 2026-08-17 11:03 | 2026-08-17 11:03 | 2026-08-17 11:03 | 2026-08-17 11:03 |  |  | Fair | No | Customer contacted and stated that power was restored fully from last week Premises is ok
Non-Outage | J.E.26.08.13943 | C001890669 | Fredrick Hamilton | KSAS | Completed | Load_244586 | Greenwich - 710 | 2026-08-17 08:26 | 2026-08-17 08:28 | 2026-08-17 08:32 | 2026-08-17 13:04 | 2026-08-17 13:04 | 2026-08-17 13:05 | 2026-08-17 13:05 | 2026-08-17 13:05 |  |  | Fair | No | Customer contacted and stated that power was restored fully previously Premises is ok
Non-Outage | J.E.26.08.13955 | C001890668 | Fredrick Hamilton | KSAS | Completed | Load_249599 | Greenwich - 710 | 2026-08-17 08:26 | 2026-08-17 08:28 | 2026-08-17 08:32 | 2026-08-17 09:47 | 2026-08-17 09:47 | 2026-08-17 09:49 | 2026-08-17 09:49 | 2026-08-17 09:49 |  |  | Fair | No | Customer contacted and stated that power was restored fully previously Premises is ok
Non-Outage | J.E.26.08.13957 | C001890667 | Fredrick Hamilton | KSAS | Completed | Load_244948 | Greenwich - 710 | 2026-08-17 08:26 | 2026-08-17 08:28 | 2026-08-17 08:32 | 2026-08-17 10:32 | 2026-08-17 10:32 | 2026-08-17 10:36 | 2026-08-17 10:36 | 2026-08-17 10:36 |  |  | Fair | No | Premises visited and customer contacted stated that low voltage issue was resolved previously Premises ok
Non-Outage | J.E.26.08.13959 | C001890666 | Fredrick Hamilton | KSAS | Completed | Load_255961 | Greenwich - 710 | 2026-08-17 08:26 | 2026-08-17 08:28 | 2026-08-17 08:32 | 2026-08-17 10:14 | 2026-08-17 10:16 | 2026-08-17 10:20 | 2026-08-17 10:20 | 2026-08-17 10:20 |  |  | Fair | No | Calls to customer went to voicemail Premises found locked
Non-Outage | J.E.26.08.13962 | C001890665 | Fredrick Hamilton | KSAS | Completed | Load_247729 | Greenwich - 710 | 2026-08-17 08:26 | 2026-08-17 08:28 | 2026-08-17 08:32 | 2026-08-17 11:07 | 2026-08-17 11:06 | 2026-08-17 11:07 | 2026-08-17 11:08 | 2026-08-17 11:08 |  |  | Fair | No | Customer contacted and stated that power was restored fully from last week Premises is ok
Non-Outage | J.E.26.08.13970 | C001890664 | Fredrick Hamilton | KSAS | Completed | Load_249599 | Greenwich - 710 | 2026-08-17 08:26 | 2026-08-17 08:28 | 2026-08-17 08:32 | 2026-08-17 09:45 | 2026-08-17 09:44 | 2026-08-17 09:46 | 2026-08-17 09:46 | 2026-08-17 09:46 |  |  | Fair | No | Customer contacted and stated that power was restored fully at location previously Premises is ok
Non-Outage | J.E.26.08.13996 | C001890663 | Fredrick Hamilton | KSAS | Completed | Load_249599 | Greenwich - 710 | 2026-08-17 08:26 | 2026-08-17 08:28 | 2026-08-17 08:32 | 2026-08-17 09:50 | 2026-08-17 09:49 | 2026-08-17 09:51 | 2026-08-17 09:51 | 2026-08-17 09:51 |  |  | Fair | No | Customer contacted and stated that power was restored fully previously Premises is ok
Non-Outage | J.E.26.08.14015 | C001890662 | Fredrick Hamilton | KSAS | Completed | Load_301578 | Greenwich - 710 | 2026-08-17 08:26 | 2026-08-17 08:28 | 2026-08-17 08:32 | 2026-08-17 11:01 | 2026-08-17 11:00 | 2026-08-17 11:01 | 2026-08-17 11:01 | 2026-08-17 11:01 |  |  | Fair | No | Customer contacted and stated that power was restored fully last week Premises is ok
Non-Outage | J.E.26.08.14047 | C001890661 | Fredrick Hamilton | KSAS | Completed | Load_244728 | Greenwich - 510 | 2026-08-17 08:26 | 2026-08-17 08:28 | 2026-08-17 08:32 | 2026-08-17 10:23 | 2026-08-17 10:24 | 2026-08-17 10:25 | 2026-08-17 10:25 | 2026-08-17 10:25 |  |  | Fair | No | Customer contacted and stated that power was restored fully previously Premises is ok
Non-Outage | J.E.26.08.14055 | C001890659 | Fredrick Hamilton | KSAS | Completed | Load_1002851 | Greenwich - 510 | 2026-08-17 08:26 | 2026-08-17 08:28 | 2026-08-17 08:32 | 2026-08-17 10:47 | 2026-08-17 10:51 | 2026-08-17 10:58 | 2026-08-17 10:58 | 2026-08-17 10:58 |  |  | Fair | No | 236v/118.3v/116.7v obtained no JPS issue detected at location premises Is ok
Non-Outage | J.E.26.08.14496 | C001890660 | Fredrick Hamilton | KSAS | Completed | Load_1002844 | Greenwich - 710 | 2026-08-17 08:26 | 2026-08-17 08:28 | 2026-08-17 08:32 | 2026-08-17 10:39 | 2026-08-17 10:40 | 2026-08-17 10:41 | 2026-08-17 10:41 | 2026-08-17 10:41 |  |  | Fair | No | Customer contacted and stated that power was restored fully previously Premises is ok
Outage | J.E.26.08.25961 | C001890680 | Elvis Trowers | KSAN | Completed | Load_257472 | Washington Blvd - 710 | 2026-08-17 08:30 | 2026-08-17 08:31 | 2026-08-17 09:03 | 2026-08-17 09:03 | 2026-08-17 09:20 | 2026-08-17 09:20 | 2026-08-17 09:25 | 2026-08-17 09:25 | Fire |  | Fair | No
Outage | J.E.26.08.25963 | C001890679 | Elvis Trowers | KSAN | Completed | Load_301236 | Washington Blvd - 710 | 2026-08-17 08:30 | 2026-08-17 08:31 | 2026-08-17 10:15 | 2026-08-17 10:16 | 2026-08-17 10:44 | 2026-08-17 10:45 | 2026-08-17 11:50 | 2026-08-17 11:50 |  |  | Fair | No | Found one 3 amps transformer fuse blown at pole #0114866 refused and reclosed transformer switch and it blow again whit oil coming from the transformer. 10 kva transformer whit two Y.P. Box is defective and need to be change about 16- customers whit out supply.
Non-Outage | J.E.26.08.20608 | C001890684 | Rochaine Hussey | KSAN | Completed | Load_248183 | Hope - 410 | 2026-08-17 08:33 | 2026-08-17 08:34 | 2026-08-17 13:46 | 2026-08-17 13:49 | 2026-08-17 14:04 | 2026-08-17 14:05 | 2026-08-17 14:10 | 2026-08-17 14:10 |  |  | Fair | No | Customer was called multiple times Went to the location unable to locate
Non-Outage | J.E.26.08.20953 | C001890687 | Rochaine Hussey | KSAS | Completed | Load_256910 | Duhaney - 310 | 2026-08-17 08:33 | 2026-08-17 08:34 | 2026-08-17 11:32 | 2026-08-17 11:32 | 2026-08-17 11:36 | 2026-08-17 12:03 | 2026-08-17 12:04 | 2026-08-17 12:04 |  |  | Fair | No | Slack connection in meter socket Customer was advised to get an electrician to change socket 110v
Non-Outage | J.E.26.08.22667 | C001890686 | Rochaine Hussey | KSAS | Completed | Load_258431 | Duhaney - 310 | 2026-08-17 08:33 | 2026-08-17 08:34 | 2026-08-17 09:07 | 2026-08-17 14:20 | 2026-08-17 14:19 | 2026-08-17 14:20 | 2026-08-17 14:20 | 2026-08-17 14:20 |  |  | Fair | No | Customer said issue was already resolved be another team
Non-Outage | J.E.26.08.25307 | C001890685 | Rochaine Hussey | KSAS | Completed | Load_267072 | Duhaney - 310 | 2026-08-17 08:33 | 2026-08-17 08:34 | 2026-08-17 12:06 | 2026-08-17 12:07 | 2026-08-17 12:09 | 2026-08-17 12:46 | 2026-08-17 12:49 | 2026-08-17 12:49 |  |  | Fair | No | Pole is located in another customer back yard Unable to locate because premises is lockVoltage at transformer 121/121/241vVoltage at customer premises 105/105/210v
Non-Outage | J.E.26.08.13426 | C001890688 | Rochaine Hussey | KSAS | Completed | Load_257825 | Duhaney - 310 | 2026-08-17 08:34 | 2026-08-17 08:34 | 2026-08-17 13:03 | 2026-08-17 13:30 | 2026-08-17 13:30 | 2026-08-17 13:43 | 2026-08-17 13:43 | 2026-08-17 13:43 |  |  | Fair | No | Customer said another team already resolved the issue
Non-Outage | J.E.26.08.18867 | C001890689 | Rochaine Hussey | KSAS | Completed | Load_247943 | Duhaney - 310 | 2026-08-17 08:34 | 2026-08-17 08:34 | 2026-08-18 08:15 | 2026-08-18 08:16 | 2026-08-18 08:15 | 2026-08-18 08:21 | 2026-08-18 08:22 | 2026-08-18 08:22 |  |  | Fair | No | Low voltage coming from transformer unable to access the pole due to the amount of cable wires on the pole Bucket truck needed
Non-Outage | J.E.26.08.20741 | C001890690 | Rochaine Hussey | KSAS | Completed | Load_264480 | Duhaney - 310 | 2026-08-17 08:34 | 2026-08-17 08:34 | 2026-08-17 12:56 | 2026-08-17 12:56 | 2026-08-17 12:56 | 2026-08-17 12:58 | 2026-08-17 12:58 | 2026-08-17 12:58 |  |  | Fair | No | Went to premises customer said the issue was resolved Another team resolved the issue
Outage | J.E.26.08.25083 | C001890697 | Derrick Dawkins | St.James | Completed | Load_265973 | Bogue - 310 | 2026-08-17 08:40 | 2026-08-17 08:42 | 2026-08-17 11:14 | 2026-08-17 12:13 | 2026-08-17 12:13 | 2026-08-17 12:26 | 2026-08-17 12:14 | 2026-08-17 12:14 |  |  | Fair | No | Premises ok
Outage | J.E.26.08.25166 | C001890703 | Derrick Dawkins | St.James | Completed | Load_244424 | Bogue - 310 | 2026-08-17 08:40 | 2026-08-17 08:42 | 2026-08-17 13:00 | 2026-08-17 13:00 | 2026-08-17 13:47 | 2026-08-17 13:47 | 2026-08-17 13:48 | 2026-08-17 13:48 |  |  | Fair | No | Premises ok
Outage | J.E.26.08.25576 | C001890704 | Derrick Dawkins | St.James | Completed | Load_265097 | Bogue - 310 | 2026-08-17 08:40 | 2026-08-17 08:42 | 2026-08-17 08:58 | 2026-08-17 09:41 | 2026-08-17 09:45 | 2026-08-17 09:52 | 2026-08-17 09:46 | 2026-08-17 09:46 |  |  | Rains | No | Premises found ok
Outage | J.E.26.08.25602 | C001890698 | Derrick Dawkins | St.James | Completed | Load_249162 | Bogue - 310 | 2026-08-17 08:40 | 2026-08-17 08:42 | 2026-08-17 08:58 | 2026-08-17 11:08 | 2026-08-17 11:10 | 2026-08-17 11:12 | 2026-08-17 11:12 | 2026-08-17 11:12 |  |  | Fair | No | checked general area and it’s ok calls to customer went unanswered cannot locate customer no directions provided
Outage | J.E.26.08.25918 | C001890701 | Derrick Dawkins | St.James | Completed | Load_265607 | Bogue - 310 | 2026-08-17 08:40 | 2026-08-17 08:42 | 2026-08-17 08:58 | 2026-08-17 09:04 | 2026-08-17 09:25 | 2026-08-17 09:39 | 2026-08-17 09:39 | 2026-08-17 09:39 |  |  | Rains | No | Customer was reconnect by customer service
Outage | J.E.26.08.25937 | C001890699 | Derrick Dawkins | St.James | Completed | Load_575161 | Bogue - 310 | 2026-08-17 08:40 | 2026-08-17 08:42 | 2026-08-17 12:13 | 2026-08-17 12:57 | 2026-08-17 12:57 | 2026-08-17 13:03 | 2026-08-17 12:59 | 2026-08-17 12:59 |  |  | Fair | No | Found service disconnected service was reconnected through customer service premises ok
Outage | J.E.26.08.25951 | C001890700 | Derrick Dawkins | St.James | Completed | Load_576009 | Bogue - 310 | 2026-08-17 08:40 | 2026-08-17 08:42 | 2026-08-17 12:13 | 2026-08-17 12:46 | 2026-08-17 12:46 | 2026-08-17 12:56 | 2026-08-17 12:56 | 2026-08-17 12:56 |  |  | Fair | No | Service was reconnected through customer service premises ok
Outage | J.E.26.08.25959 | C001890702 | Derrick Dawkins | St.James | Completed | Load_1002051 | Bogue - 310 | 2026-08-17 08:40 | 2026-08-17 08:42 | 2026-08-17 08:58 | 2026-08-17 11:13 | 2026-08-17 11:13 | 2026-08-17 11:26 | 2026-08-17 11:14 | 2026-08-17 11:14 |  |  | Fair | No | Calls to customer went unanswered cannot locate
Outage | J.E.26.08.25984 | C001890711 | Omar King | St.Ann | Completed | Load_253537 | Upper White River - 210 | 2026-08-17 08:41 | 2026-08-17 08:45 | 2026-08-17 14:33 | 2026-08-17 14:34 | 2026-08-17 15:10 | 2026-08-17 15:16 | 2026-08-17 15:16 | 2026-08-17 15:16 |  |  | Fair | No | Found 25 amp junction fuse blow cause by bird fuse has been replaced and customer now with supply..
Outage | J.E.26.08.25985 | C001890706 | Richard Watson | St.Elizabeth | Completed | Load_242373 | Maggotty - 210 | 2026-08-17 08:41 | 2026-08-17 08:42 | 2026-08-17 09:06 | 2026-08-17 09:07 | 2026-08-17 09:54 | 2026-08-17 10:51 | 2026-08-17 10:56 | 2026-08-17 10:56 |  |  | Fair | No | Replace approximately 120ft of #6 triplex service wire, also use three 1bolt clamps and three #6-#6 service sleeves, voltage left in meter socket 109v, 111v, 220v, customer was out of supply since the passage of hurricane Melissa.
Outage | J.E.26.08.25399 | C001890713 | Romeo Brissett | St.James | Completed | Load_243584 | Bogue - 510 | 2026-08-17 08:44 | 2026-08-18 08:04 | 2026-08-18 09:08 | 2026-08-18 09:09 | 2026-08-18 09:08 | 2026-08-18 09:12 | 2026-08-18 09:22 | 2026-08-18 09:22 |  |  | Fair | No | Hanover call
Outage | J.E.26.08.25846 | C001890714 | Romeo Brissett | Hanover | Completed | Load_573360 | Orange Bay - 310 | 2026-08-17 08:44 | 2026-08-18 08:04 | 2026-08-18 09:06 | 2026-08-18 09:07 | 2026-08-18 09:07 | 2026-08-18 09:00 | 2026-08-18 09:08 | 2026-08-18 09:08 |  |  | Fair | No | Hanover call
Outage | J.E.26.08.25830 | C001890722 | Shawn Medley | St.James | Completed | Load_291442 | Queens Drive - 310 | 2026-08-17 08:46 | 2026-08-17 08:47 | 2026-08-17 08:55 | 2026-08-17 08:56 | 2026-08-17 09:40 | 2026-08-17 10:06 | 2026-08-17 10:12 | 2026-08-17 10:12 |  |  | Fair | No | Found one 25amps junction fuse blown at pole without number and EG fuse at box#01773 cause by rat bat, however I replaced fuses ran test close an it held. The reason why this line section is going out so often is because it pure concrete pole so when there is a fault on the EG fuse it flash over a blown the junction fuse. The fix is to install crossarms to each switch pole. Until then we won’t stop having repeated outages.
Outage | J.E.26.08.25942 | C001890723 | Hopeton Henry | St.Thomas | Completed | Load_258020 | Good Year - 110 | 2026-08-17 08:51 | 2026-08-17 08:56 | 2026-08-17 09:13 | 2026-08-17 13:42 | 2026-08-17 14:29 | 2026-08-17 14:30 | 2026-08-17 14:31 | 2026-08-17 14:31 |  |  | Fair | No | Check and found ok
Non-Outage | J.E.26.08.10124 | C001890747 | Hopeton Henry | St.Thomas | Completed | Load_248874 | Good Year - 210 | 2026-08-17 08:54 | 2026-08-17 08:56 | 2026-08-17 09:13 | 2026-08-18 14:25 | 2026-08-18 14:31 | 2026-08-18 14:34 | 2026-08-18 14:34 | 2026-08-18 14:34 |  |  | Fair | No | Found ok
Non-Outage | J.E.26.08.11400 | C001890746 | Hopeton Henry | St.Thomas | Completed | Load_251658 | Good Year - 210 | 2026-08-17 08:54 | 2026-08-17 08:56 | 2026-08-17 09:13 | 2026-08-18 14:35 | 2026-08-18 14:49 | 2026-08-18 15:01 | 2026-08-18 15:01 | 2026-08-18 15:01 |  |  | Fair | Yes | Reconnect service at pole 115-116-231 volts at meter
Non-Outage | J.E.26.08.20206 | C001890744 | Hopeton Henry | St.Thomas | Completed | Load_244341 | Good Year - 210 | 2026-08-17 08:54 | 2026-08-17 08:56 | 2026-08-17 09:13 | 2026-08-17 09:14 | 2026-08-17 12:22 | 2026-08-17 12:22 | 2026-08-17 12:27 | 2026-08-17 12:27 |  |  | Fair | No | Check and found ok
Non-Outage | J.E.26.08.20560 | C001890742 | Hopeton Henry | St.Thomas | Completed | Load_295201 | Good Year - 210 | 2026-08-17 08:54 | 2026-08-17 08:56 | 2026-08-17 09:13 | 2026-08-17 13:28 | 2026-08-17 13:28 | 2026-08-17 13:28 | 2026-08-17 13:29 | 2026-08-17 13:29 |  |  | Fair | No | Internal problem 115-116-230 at meter socket
Non-Outage | J.E.26.08.20695 | C001890743 | Hopeton Henry | St.Thomas | Completed | Load_295201 | Good Year - 210 | 2026-08-17 08:54 | 2026-08-17 08:56 | 2026-08-17 09:13 | 2026-08-17 13:33 | 2026-08-17 13:32 | 2026-08-17 13:32 | 2026-08-17 13:34 | 2026-08-17 13:34 |  |  | Fair | No | Customer not located
Non-Outage | J.E.26.08.21599 | C001890739 | Hopeton Henry | St.Thomas | Completed | Load_238855 | Good Year - 210 | 2026-08-17 08:54 | 2026-08-17 08:56 | 2026-08-17 09:13 | 2026-08-17 13:30 | 2026-08-17 13:30 | 2026-08-17 13:30 | 2026-08-17 13:30 | 2026-08-17 13:30 |  |  | Fair | No | Customer not located
Non-Outage | J.E.26.08.21744 | C001890740 | Hopeton Henry | St.Thomas | Completed | Load_263358 | Good Year - 210 | 2026-08-17 08:54 | 2026-08-17 08:56 | 2026-08-17 09:13 | 2026-08-17 12:29 | 2026-08-17 12:39 | 2026-08-17 12:39 | 2026-08-17 12:40 | 2026-08-17 12:40 |  |  | Fair | No | Customer not located
Non-Outage | J.E.26.08.25128 | C001890737 | Hopeton Henry | St.Thomas | Completed | Load_268639 | Good Year - 210 | 2026-08-17 08:54 | 2026-08-17 08:56 | 2026-08-17 09:13 | 2026-08-17 14:33 | 2026-08-17 16:47 | 2026-08-17 16:48 | 2026-08-17 16:49 | 2026-08-17 16:49 |  |  | Fair | No | Change defective service wire 50 ft #6 triplex 3 connector 3 clamps Voltage 117-118-236 v
Outage | J.E.26.08.25689 | C001890748 | Tajay Bernard | Hanover | Completed | Load_305014 | Orange Bay - 210 | 2026-08-17 08:55 | 2026-08-17 13:14 | 2026-08-17 14:52 | 2026-08-17 14:53 | 2026-08-17 14:52 | 2026-08-17 14:54 | 2026-08-17 14:54 | 2026-08-17 14:54 |  |  | Fair | No | Unable to get a hold to the customer multiple phone calls to the customer number went unanswered
Outage | J.E.26.08.26000 | C001890752 | Richard Grant | St.Catherine | Completed | Load_248672 | New Michelton - 210 | 2026-08-17 09:01 | 2026-08-17 09:04 | 2026-08-17 11:23 | 2026-08-17 11:23 | 2026-08-17 11:33 | 2026-08-17 13:59 | 2026-08-17 20:15 | 2026-08-17 20:15 | BrokenWire | Y | Fair | No | 4 pole pan of broken opened phases and neutral found caused by tree fallen onto line. Bushing conducted to remove tree from line, 2 #2 preform, 4 2/0 preform, 4 #2 sleeves, 3 2/0 sleeves, approximately 80ft #2 wire, approximately 30ft 2/0 wire and 5 onebolt clamps used to retention line. Supply restored and area left okay.
Non-Outage | J.E.26.08.23226 | C001890757 | Rayon Foster | Hanover | Completed | Load_262897 | Orange Bay - 310 | 2026-08-17 09:04 | 2026-08-17 09:21 | 2026-08-18 13:32 | 2026-08-18 13:32 | 2026-08-18 13:32 | 2026-08-18 13:33 | 2026-08-18 13:33 | 2026-08-18 13:33 |  |  | Fair | No | Unable to reach customer on cell phone and unclear directions are provided to locate premises
Non-Outage | J.E.26.08.23608 | C001890756 | Rayon Foster | Hanover | Completed | Load_242732 | Orange Bay - 310 | 2026-08-17 09:04 | 2026-08-17 09:21 | 2026-08-17 09:34 | 2026-08-17 11:07 | 2026-08-17 11:31 | 2026-08-17 11:53 | 2026-08-17 11:53 | 2026-08-17 11:53 |  |  | Rains | No | Customer received back full power after a power outage yesterday
Non-Outage | J.E.26.08.24140 | C001890755 | Rayon Foster | Hanover | Completed | Load_246056 | Orange Bay - 310 | 2026-08-17 09:04 | 2026-08-17 09:21 | 2026-08-17 14:19 | 2026-08-17 14:20 | 2026-08-17 15:12 | 2026-08-17 15:19 | 2026-08-17 15:19 | 2026-08-17 15:19 |  |  | Rains | No | Unable to reach on cell number or locate premises not enough driving details
Outage | J.E.26.08.24628 | C001890777 | Christopher West | Portmore | Completed | Load_269534 | Naggo Head - 510 | 2026-08-17 09:12 | 2026-08-17 09:15 | 2026-08-17 09:55 | 2026-08-17 09:55 | 2026-08-17 10:27 | 2026-08-17 10:30 | 2026-08-17 10:30 | 2026-08-17 10:30 | LowHangingWires |  | Fair | No | Premises found closed at time of visit.
Outage | J.E.26.08.25317 | C001890778 | Christopher West | Portmore | Completed | Load_237810 | Naggo Head - 510 | 2026-08-17 09:12 | 2026-08-17 09:15 | 2026-08-17 14:02 | 2026-08-17 14:02 | 2026-08-17 14:02 | 2026-08-17 14:05 | 2026-08-17 14:05 | 2026-08-17 14:05 |  |  | Fair | No | Kindly refer to Mr. Elliston.
Outage | J.E.26.08.25688 | C001890779 | Nickolas Rodriques | Portmore | Completed | Load_263072 | Naggo Head - 510 | 2026-08-17 09:13 | 2026-08-18 07:38 | 2026-08-18 12:08 | 2026-08-18 12:09 | 2026-08-18 12:36 | 2026-08-18 13:00 | 2026-08-18 13:01 | 2026-08-18 13:01 |  |  | Fair | No | Checked and found customers single phasing (117) caused by broken jumper wire. Repaired by rebuilt jumper using two clamps, current reading (117-117-234).
Non-Outage | J.E.26.08.20827 | C001890786 | Christopher West | Portmore | Completed | Load_576114 | Naggo Head - 510 | 2026-08-17 09:17 | 2026-08-17 09:18 | 2026-08-17 10:30 | 2026-08-17 10:31 | 2026-08-17 10:58 | 2026-08-17 12:30 | 2026-08-17 13:17 | 2026-08-17 13:17 |  |  | Fair | No | Bank x3 50kva transformers were de-energized and one found on tap position 4 same was placed to tap position 3, V/R before tap change, 247v 241v 242v, 425v, 421v 419v, V/R after tap change 240v 241v 242v, 420v, 419v, 421v, customer now ok.
Non-Outage | J.E.26.08.20279 | C001890787 | Orville Lee | Portmore | Completed | Load_256975 | Naggo Head - 510 | 2026-08-17 09:18 | 2026-08-17 09:19 | 2026-08-17 10:13 | 2026-08-17 10:32 | 2026-08-17 10:39 | 2026-08-17 11:00 | 2026-08-17 11:03 | 2026-08-17 11:03 |  |  | Fair | No | Checks made and found secondary connection corroded Two one bolt clamp’s used Voltage118v119v238v
Non-Outage | J.E.26.08.20402 | C001890790 | Orville Lee | St.Catherine | Completed | Load_576141 | Twickenham - 210 | 2026-08-17 09:18 | 2026-08-17 09:19 | 2026-08-17 10:13 | 2026-08-17 15:48 | 2026-08-17 17:26 | 2026-08-17 17:26 | 2026-08-17 17:29 | 2026-08-17 17:29 |  |  | Fair | No | Checks made and found secondary connection corroded Two oneTransformer drop lead clamps change115v116v231v
Non-Outage | J.E.26.08.20413 | C001890789 | Orville Lee | St.Catherine | Completed | Load_251980 | Twickenham - 210 | 2026-08-17 09:18 | 2026-08-17 09:19 | 2026-08-17 10:13 | 2026-08-18 11:41 | 2026-08-18 12:06 | 2026-08-18 12:13 | 2026-08-18 12:14 | 2026-08-18 12:14 |  |  | Fair | No | Premises found ok upon arrival Issue was solved by a technician Voltage 116117233
Non-Outage | J.E.26.08.20457 | C001890788 | Orville Lee | St.Catherine | Completed | Load_252074 | Twickenham - 210 | 2026-08-17 09:18 | 2026-08-17 09:19 | 2026-08-17 10:13 | 2026-08-17 14:53 | 2026-08-17 15:18 | 2026-08-17 15:44 | 2026-08-17 15:46 | 2026-08-17 15:46 |  |  | Fair | No | Checks made and found pothead and secondary connections corroded One pen union and two one bolt clampVoltage115v116v
Non-Outage | J.E.26.08.18860 | C001890793 | Royston Montague | St.Catherine | Completed | Load_241531 | Tredegar - 210 | 2026-08-17 09:20 | 2026-08-17 09:21 | 2026-08-17 09:38 | 2026-08-17 12:59 | 2026-08-17 13:03 | 2026-08-17 13:05 | 2026-08-17 13:05 | 2026-08-17 13:05 | BrokenWire |  | Fair | No | Broken pole at premises is not Jamaica public service property.
Non-Outage | J.E.26.08.18949 | C001890792 | Royston Montague |  | Completed |  |  | 2026-08-17 09:20 | 2026-08-17 09:21 | 2026-08-17 09:38 | 2026-08-18 11:09 | 2026-08-18 11:14 | 2026-08-18 11:14 | 2026-08-18 11:15 | 2026-08-18 11:15 | BrokenWire |  | Fair | No | Customer confirmed issue resolved
Non-Outage | J.E.26.08.19097 | C001890796 | Royston Montague |  | Completed |  |  | 2026-08-17 09:20 | 2026-08-17 09:21 | 2026-08-17 09:38 | 2026-08-17 14:22 | 2026-08-17 15:41 | 2026-08-17 15:42 | 2026-08-17 15:42 | 2026-08-17 15:42 | LeaningPole |  | Fair | No | Customer concern about a leading pole beside premises.
Non-Outage | J.E.26.08.20703 | C001890794 | Royston Montague | St.Catherine | Completed | Load_261448 | Tredegar - 210 | 2026-08-17 09:20 | 2026-08-17 09:21 | 2026-08-17 09:38 | 2026-08-17 10:28 | 2026-08-17 10:29 | 2026-08-17 10:53 | 2026-08-17 11:15 | 2026-08-17 11:15 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.08.21248 | C001890795 | Royston Montague | St.Catherine | Completed | Load_259014 | Tredegar - 210 | 2026-08-17 09:20 | 2026-08-17 09:21 | 2026-08-17 09:38 | 2026-08-17 09:41 | 2026-08-17 10:26 | 2026-08-17 10:27 | 2026-08-17 10:27 | 2026-08-17 10:27 |  |  | Fair | No | Faulty breaker. Customer confirmed issue resolved her electrician repair same.
Non-Outage | J.E.26.08.09499 | C001890806 | Rayon Foster | Hanover | Completed | Load_242732 | Orange Bay - 310 | 2026-08-17 09:25 | 2026-08-17 09:26 | 2026-08-17 09:33 | 2026-08-17 11:54 | 2026-08-17 12:46 | 2026-08-17 13:04 | 2026-08-17 13:04 | 2026-08-17 13:04 |  |  | Rains | No | When call Noel chambers he said he did not make a report and he have full electricity
Non-Outage | J.E.26.08.10596 | C001890807 | Rayon Foster | Hanover | Completed | Load_261657 | Orange Bay - 310 | 2026-08-17 09:25 | 2026-08-17 09:26 | 2026-08-17 11:37 | 2026-08-17 13:04 | 2026-08-17 13:28 | 2026-08-17 14:07 | 2026-08-17 14:18 | 2026-08-17 14:18 |  |  | Fair | No | Customer said she received back power after a power outage
Non-Outage | J.E.26.08.13837 | C001890808 | Rayon Foster | Hanover | Completed | Load_253913 | Orange Bay - 310 | 2026-08-17 09:25 | 2026-08-17 09:26 | 2026-08-18 10:08 | 2026-08-18 10:09 | 2026-08-18 10:12 | 2026-08-18 10:18 | 2026-08-18 10:18 | 2026-08-18 10:18 |  |  | Fair | No | Customer said she didn’t make a report and her electricity is working fine
Outage | J.E.26.08.25341 | C001890819 | Marlon Brown | Trelawny | Completed | Load_251635 | Greenwood - 210 | 2026-08-17 09:27 | 2026-08-18 15:50 | 2026-08-18 15:54 | 2026-08-18 15:54 | 2026-08-18 15:54 | 2026-08-18 15:55 | 2026-08-18 15:55 | 2026-08-18 15:55 |  |  | Fair | No | St James call
Outage | J.E.26.08.25690 | C001890820 | Lionel Robinson | Trelawny | Completed | Load_292876 | Greenwood - 210 | 2026-08-17 09:28 | 2026-08-18 08:24 | 2026-08-18 09:45 | 2026-08-18 09:46 | 2026-08-18 09:52 | 2026-08-18 09:53 | 2026-08-18 09:53 | 2026-08-18 09:53 |  |  | Fair | No | Customer checked and found ok
Outage | J.E.26.08.26071 | C001890822 | Elvis Trowers | KSAN | Completed | Load_293397 | Washington Blvd - 710 | 2026-08-17 09:29 | 2026-08-17 09:30 | 2026-08-17 09:49 | 2026-08-17 09:49 | 2026-08-17 10:08 | 2026-08-17 10:15 | 2026-08-17 10:15 | 2026-08-17 10:15 | BrokenWire |  | Fair | No | Customer fed from Y.P box #02689 at pole #0114912 and getting low voltage from the Box customer meter in the Y.P. Box need to be check. Readings at the box 110-108 224 volts. Refer to field service.
Outage | J.E.26.08.25840 | C001890823 | Omar King | St.Ann | Completed | Load_237772 | Ocho Rios - 310 | 2026-08-17 09:30 | 2026-08-17 09:30 | 2026-08-17 13:03 | 2026-08-17 13:04 | 2026-08-17 13:32 | 2026-08-17 14:15 | 2026-08-17 14:15 | 2026-08-17 14:15 |  |  | Fair | No | Found 50 amp junction fuse blow fuse has been replaced and customer now with supply..
Non-Outage | J.E.26.08.26073 | C001890832 | Raymond Carr |  | Completed |  |  | 2026-08-17 09:32 | 2026-08-17 09:34 | 2026-08-17 11:21 | 2026-08-17 11:22 | 2026-08-17 12:01 | 2026-08-17 | 2026-08-17 12:03 | 2026-08-17 12:03 |  |  | Fair | No | No access to rammy system. Refer to field service department.
Outage | J.E.26.08.26021 | C001890835 | Oshane Warren | Westmoreland | Completed | Load_258299 | Paradise - 210 | 2026-08-17 09:34 | 2026-08-17 09:36 | 2026-08-17 10:20 | 2026-08-17 10:22 | 2026-08-17 12:54 | 2026-08-17 12:58 | 2026-08-17 13:00 | 2026-08-17 13:00 |  |  | Fair | No | hexing metering system refer to field service
Outage | J.E.26.08.26024 | C001890834 | Richman Whyte | Westmoreland | Completed | Load_292071 | Paradise - 310 | 2026-08-17 09:34 | 2026-08-17 09:36 | 2026-08-17 10:13 | 2026-08-17 10:14 | 2026-08-17 10:13 | 2026-08-17 10:14 | 2026-08-17 10:14 | 2026-08-17 10:14 |  |  | Fair | No | Check and found ok
Outage | J.E.26.08.26017 | C001890836 | Richman Whyte | Westmoreland | Completed | Load_251069 | Paradise - 310 | 2026-08-17 09:35 | 2026-08-17 09:36 | 2026-08-17 10:14 | 2026-08-17 10:15 | 2026-08-17 10:14 | 2026-08-17 10:14 | 2026-08-17 10:15 | 2026-08-17 10:15 |  |  | Fair | No | Check and found ok
Outage | J.E.26.08.26047 | C001890837 | Lionel Robinson | Trelawny | Completed | Load_240904 | Duncans - 210 | 2026-08-17 09:35 | 2026-08-17 09:38 | 2026-08-18 09:14 | 2026-08-18 09:15 | 2026-08-18 09:14 | 2026-08-18 09:16 | 2026-08-18 09:17 | 2026-08-18 09:17 |  |  | Fair | No | Customer checked and found ok
Non-Outage | J.E.26.08.25511 | C001890845 | Derrick Dawkins | St.James | Completed | Load_1001936 | Bogue - 310 | 2026-08-17 09:37 | 2026-08-17 09:38 | 2026-08-17 09:49 | 2026-08-17 10:16 | 2026-08-17 10:26 | 2026-08-17 11:04 | 2026-08-17 11:04 | 2026-08-17 11:04 |  |  | Fair | No | Found junction fuse blown 15 amp replaced 15 amp junction fuse Pole#212986
Outage | J.E.26.08.26113 | C001890846 | Derrick Dawkins | St.James | Completed | Load_230013 | Bogue - 310 | 2026-08-17 09:39 | 2026-08-17 09:39 | 2026-08-17 09:52 | 2026-08-17 09:53 | 2026-08-17 10:00 | 2026-08-17 10:15 | 2026-08-17 10:15 | 2026-08-17 10:15 |  |  | Rains | No | Found 2 100 transformer fuse blown 10 amp replaced 10 amp fuse
Outage | J.E.26.08.25911 | C001890853 | Omar King | St.Ann | Completed | Load_242953 | Roaring River - 410 | 2026-08-17 09:46 | 2026-08-17 09:47 | 2026-08-17 13:01 | 2026-08-17 13:01 | 2026-08-17 13:01 | 2026-08-17 13:03 | 2026-08-17 13:03 | 2026-08-17 13:03 |  |  | Fair | No | Related to other call..
Non-Outage | J.E.26.08.09767 | C001890861 | Oraine Minto | St.Ann | Completed | Load_256006 | Roaring River - 210 | 2026-08-17 09:48 | 2026-08-17 09:48 | 2026-08-18 08:48 | 2026-08-18 08:49 | 2026-08-18 10:07 | 2026-08-18 10:08 | 2026-08-18 10:11 | 2026-08-18 10:11 |  |  | Fair | No | Refer to emergency Customer pole lean a bucket truck would be suitable to complete task
Non-Outage | J.E.26.08.25975 | C001890862 | Neville Spencer | Clarendon | Completed | Load_255751 | May Pen - 110 | 2026-08-17 09:48 | 2026-08-17 09:50 | 2026-08-17 12:50 | 2026-08-17 12:50 | 2026-08-17 14:04 | 2026-08-17 14:04 | 2026-08-17 15:37 | 2026-08-17 15:37 | BrokenWire |  | Fair | No | Remade burnt off phase joint at secondary on 2, wire service used 1, clamp voltage reading 116 supply restored..
Non-Outage | J.E.26.08.22695 | C001890867 | Odaine Johnson | Clarendon | Completed | Load_261816 | Parnassus - 310 | 2026-08-17 09:49 | 2026-08-17 09:50 | 2026-08-17 10:03 | 2026-08-17 10:04 | 2026-08-17 10:13 | 2026-08-17 10:13 | 2026-08-17 10:14 | 2026-08-17 10:14 |  |  | Fair | No | Contacted customer and customer stated that the issue was resolved already
Non-Outage | J.E.26.08.23071 | C001890866 | Odaine Johnson | Clarendon | Completed | Load_238199 | Parnassus - 310 | 2026-08-17 09:49 | 2026-08-17 09:50 | 2026-08-17 10:06 | 2026-08-17 11:05 | 2026-08-17 11:06 | 2026-08-17 11:06 | 2026-08-17 11:09 | 2026-08-17 11:09 |  |  | Fair | No | Lose connection was found at service pole one bolt clamps was replaced and problem was fixed Voltage reading before A107 B123 A231 Voltage reading after A115 B115 AB230
Non-Outage | J.E.26.08.24666 | C001890865 | Odaine Johnson | Clarendon | Completed | Load_259723 | Monymusk - 410 | 2026-08-17 09:49 | 2026-08-17 09:50 | 2026-08-17 10:10 | 2026-08-17 12:55 | 2026-08-17 13:15 | 2026-08-17 13:15 | 2026-08-17 13:16 | 2026-08-17 13:16 |  |  | Fair | No | Premises was found working ok voltage reading is A116 B115 AB231
Non-Outage | J.E.26.08.25164 | C001890863 | Odaine Johnson | Clarendon | Completed | Load_260474 | Monymusk - 410 | 2026-08-17 09:49 | 2026-08-17 09:50 | 2026-08-17 10:13 | 2026-08-17 12:03 | 2026-08-17 12:51 | 2026-08-17 00:52 | 2026-08-17 12:54 | 2026-08-17 12:54 |  |  | Fair | No | Corrosion was found at service pole and at pothead one bolt clamps and pen union was replaced and problem was fixedVoltage reading A114 B115 AB229
Non-Outage | J.E.26.08.25415 | C001890864 | Odaine Johnson | Clarendon | Completed | Load_254560 | Parnassus - 310 | 2026-08-17 09:49 | 2026-08-17 09:50 | 2026-08-17 10:10 | 2026-08-17 11:10 | 2026-08-17 11:19 | 2026-08-17 11:41 | 2026-08-17 11:43 | 2026-08-17 11:43 |  |  | Fair | No | Corrosion was found at service pole 3 one bolt clamps was replaced and problem was fixed Voltage reading before A66 B116 AB182Voltage reading after A117 B116 AB233
Outage | J.E.26.08.26136 | C001890868 | Romeo Brissett | St.James | Completed | Load_239119 | Bogue - 610 | 2026-08-17 09:50 | 2026-08-17 09:52 | 2026-08-17 11:51 | 2026-08-17 11:52 | 2026-08-17 12:09 | 2026-08-17 12:50 | 2026-08-17 12:50 | 2026-08-17 12:50 |  |  | Fair | No | Found customer service wire missing, dislodged from pole and pothead, meter is also defective, Installed 40ft of #6, used 40ft of #6 and 4 clamps V/R 108-113-222. Please send to field service to change meter.
Outage | J.E.26.08.25905 | C001890870 | Ryan Richards | Manchester | Completed | Load_261236 | Porus - 310 | 2026-08-17 09:51 | 2026-08-17 09:52 | 2026-08-17 10:55 | 2026-08-17 10:55 | 2026-08-17 11:47 | 2026-08-17 12:58 | 2026-08-17 12:58 | 2026-08-17 12:58 |  |  | Fair | No | Burn service wire found for 2 w meter replaced 60ft#6 triplex2 penunion 2 one bolt clamps further checks made where 1 span of entangle phase and cable shield wire cut shield all customers supply are now working ok
Outage | J.E.26.08.26096 | C001890869 | Derrick Dawkins | St.James | Completed | Load_568788 | Bogue - 310 | 2026-08-17 09:51 | 2026-08-17 09:52 | 2026-08-17 12:23 | 2026-08-17 12:30 | 2026-08-17 12:29 | 2026-08-17 12:30 | 2026-08-17 12:30 | 2026-08-17 12:30 | BrokenWire |  | Fair | No | Calls to customer went unanswered cannot locate premises
Non-Outage | J.E.26.08.25447 | C001890891 | Denton Williams |  | Completed |  |  | 2026-08-17 09:56 | 2026-08-17 09:57 | 2026-08-17 10:49 | 2026-08-17 10:49 | 2026-08-17 10:49 | 2026-08-17 10:50 | 2026-08-17 10:50 | 2026-08-17 10:50 | BrokenWire | Y | Fair | No | Supply was restored to the area
Outage | J.E.26.08.24700 | C001890888 | Denton Williams | Portland | Completed | Load_350980 | Port Antonio - 410 | 2026-08-17 09:56 | 2026-08-17 09:57 | 2026-08-17 19:16 | 2026-08-17 19:16 | 2026-08-17 19:16 | 2026-08-17 19:17 | 2026-08-17 19:19 | 2026-08-17 19:19 | Fire | Y | Fair | No | Customer states that she is ok, problem was from yesterday.
Outage | J.E.26.08.24704 | C001890890 | Denton Williams | Portland | Completed | Load_240240 | Port Antonio - 410 | 2026-08-17 09:56 | 2026-08-17 09:57 | 2026-08-17 14:25 | 2026-08-17 14:25 | 2026-08-17 15:09 | 2026-08-17 15:22 | 2026-08-17 15:23 | 2026-08-17 15:23 |  | Y | Fair | No | 10amps junction fuse blown cause by tree fall on primary line cut and remove tree branch then restore supply to the area.
Outage | J.E.26.08.25075 | C001890889 | Denton Williams | Portland | Completed | Load_267511 | Port Antonio - 410 | 2026-08-17 09:56 | 2026-08-17 09:57 | 2026-08-17 10:46 | 2026-08-17 10:46 | 2026-08-17 10:46 | 2026-08-17 10:48 | 2026-08-17 10:48 | 2026-08-17 10:48 | BrokenWire | Y | Fair | No | 25kva transformer fuse blown cause by tree cut on secondary conductors patrol line section then restored supply to the area.
Outage | J.E.26.08.26097 | C001890887 | Denton Williams | Portland | Completed | Load_268893 | Port Antonio - 410 | 2026-08-17 09:56 | 2026-08-17 09:57 | 2026-08-17 10:29 | 2026-08-17 10:50 | 2026-08-17 11:52 | 2026-08-17 13:00 | 2026-08-17 13:12 | 2026-08-17 13:12 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards | Y | Fair | No | 25kva transformer fuse blown cause by open secondary neutral conductors burst down cut tree from area then splice and retention conductors close transformer fuse to restore normal supply to the area.Material use 50ft of aaa conductor 4 one bolt clamps 2 number 2 splicing sleeve 1 2amp fuse.
Non-Outage | J.E.26.08.19446 | C001890920 | Junior Scarlett | St.James | Completed | Load_302175 | Bogue - 510 | 2026-08-17 10:04 | 2026-08-17 10:06 | 2026-08-17 10:16 | 2026-08-17 11:06 | 2026-08-17 11:38 | 2026-08-17 11:59 | 2026-08-17 11:59 | 2026-08-17 11:59 |  |  | Fair | No | Check and found okVoltage found 115v 115v 230v 205v
Non-Outage | J.E.26.08.23887 | C001890918 | Junior Scarlett | St.James | Completed | Load_302163 | Bogue - 610 | 2026-08-17 10:04 | 2026-08-17 10:06 | 2026-08-17 10:16 | 2026-08-17 10:23 | 2026-08-17 10:42 | 2026-08-17 10:56 | 2026-08-17 10:55 | 2026-08-17 10:55 |  |  | Fair | No | Mix span connection Required bucket truckVoltage found 114v 0.44v 114v
Non-Outage | J.E.26.08.13287 | C001890924 | Junior Scarlett | St.James | Completed | Load_248632 | Bogue - 510 | 2026-08-17 10:05 | 2026-08-17 10:12 | 2026-08-17 10:16 | 2026-08-17 11:59 | 2026-08-17 13:01 | 2026-08-17 01:29 | 2026-08-17 13:29 | 2026-08-17 13:29 |  |  | Fair | No | Install 3 clamp on pothead Voltage found 113v 113v 226v Voltage leave 113v 113. 226vJob complete
Outage | J.E.26.08.26009 | C001890923 | Denton Williams | Portland | Completed | Load_252130 | Port Antonio - 410 | 2026-08-17 10:05 | 2026-08-17 10:05 | 2026-08-17 13:44 | 2026-08-17 13:47 | 2026-08-17 14:19 | 2026-08-17 14:20 | 2026-08-17 14:24 | 2026-08-17 14:24 |  |  | Fair | No | Use one 3 amp fuse to restore power supply, outage was cause by lightning
Non-Outage | J.E.26.08.24486 | C001890937 | Derrick Grubb | St.Thomas | Completed | Load_264991 | Good Year - 110 | 2026-08-17 10:12 | 2026-08-17 10:13 | 2026-08-17 11:02 | 2026-08-17 11:02 | 2026-08-17 12:26 | 2026-08-17 12:27 | 2026-08-17 12:28 | 2026-08-17 12:28 |  |  | Fair | No | Clear corrosion at pole on transformer drop lead neutral
Outage | J.E.26.08.26183 | C001890960 | Fitzroy Turner | KSAS | Completed | Load_573723 | Cane River - 310 | 2026-08-17 10:26 | 2026-08-17 10:27 | 2026-08-17 12:08 | 2026-08-17 12:09 | 2026-08-17 12:08 | 2026-08-17 12:09 | 2026-08-17 12:15 | 2026-08-17 12:15 |  |  | Fair | No | Found 15 amps junction fuse blown at the intersection Paul bogle hwy palm beach estate 15amp replace supply restored to customer
Non-Outage | J.E.26.08.20712 | C001890993 | Edward Royal | KSAN | Completed | Load_253182 | Hope - 510 | 2026-08-17 10:38 | 2026-08-17 10:39 | 2026-08-17 13:04 | 2026-08-17 13:05 | 2026-08-17 13:47 | 2026-08-17 14:39 | 2026-08-17 14:45 | 2026-08-17 14:45 | Fire |  | Fair | No | Secondary phase open conductor was dislodged from insulator reinstalled open conductor to insulator
Non-Outage | J.E.26.08.21003 | C001890994 | Edward Royal | KSAN | Completed | Load_260016 | Hope - 410 | 2026-08-17 10:38 | 2026-08-17 10:39 | 2026-08-17 12:28 | 2026-08-17 12:29 | 2026-08-17 12:35 | 2026-08-17 12:40 | 2026-08-17 12:41 | 2026-08-17 12:41 | BrokenPole |  | Fair | No | Rotten pole needs be change 30ft class 6 on it open secondary conductor service cable and third party cable pole #216271
Non-Outage | J.E.26.08.25589 | C001890992 | Edward Royal | KSAN | Completed | Load_253696 | Hope - 410 | 2026-08-17 10:38 | 2026-08-17 10:39 | 2026-08-17 11:25 | 2026-08-17 11:25 | 2026-08-17 11:42 | 2026-08-17 12:11 | 2026-08-17 12:12 | 2026-08-17 12:12 | Fire |  | Fair | No | Customer have internal problems customer have faulty wiring advise customer to get a electrician to fix the problem voltage reading 234 117 117 v
Outage | J.E.26.08.25347 | C001890988 | Edward Royal | KSAN | Completed | Load_255460 | West Kings House - 310 | 2026-08-17 10:38 | 2026-08-17 10:39 | 2026-08-17 11:17 | 2026-08-17 11:18 | 2026-08-17 11:17 | 2026-08-17 11:21 | 2026-08-17 11:22 | 2026-08-17 11:22 |  |  | Fair | No | Contact customer by phone customer said the power was restored
Outage | J.E.26.08.25986 | C001890989 | Milton Charlton | KSAN | Completed | Load_266979 | Hope - 510 | 2026-08-17 10:38 | 2026-08-18 07:23 | 2026-08-18 08:34 | 2026-08-18 10:24 | 2026-08-18 11:19 | 2026-08-18 11:20 | 2026-08-18 11:21 | 2026-08-18 11:21 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.25737 | C001890995 | Denton Williams | Portland | Completed | Load_268231 | Port Antonio - 410 | 2026-08-17 10:40 | 2026-08-17 10:42 | 2026-08-17 17:22 | 2026-08-17 17:22 | 2026-08-17 17:22 | 2026-08-17 17:24 | 2026-08-17 17:25 | 2026-08-17 17:25 |  | Y | Fair | No | Use one 15 amp fuse to restore power to area. Bushing cause
Outage | J.E.26.08.26212 | C001890997 | Omar King | St.Ann | Completed | Load_268584 | Ocho Rios - 310 | 2026-08-17 10:40 | 2026-08-17 18:34 | 2026-08-17 21:10 | 2026-08-17 21:11 | 2026-08-17 21:11 | 2026-08-17 21:12 | 2026-08-17 21:12 | 2026-08-17 21:12 |  |  | Fair | No | Found 35 feet class 6 wood Pole top burn off pole construction T cause construction to failed. Pole carry secondary and primary conductor pole hardware two dead end insulator and two dead end clamp eye bolt . Please refer to maintenance Two customer affected
Outage | J.E.26.08.26206 | C001891022 | Elvis Trowers | KSAN | Completed | Load_268663 | Washington Blvd - 710 | 2026-08-17 10:55 | 2026-08-17 10:56 | 2026-08-17 12:12 | 2026-08-17 12:12 | 2026-08-17 12:36 | 2026-08-17 12:30 | 2026-08-17 12:37 | 2026-08-17 12:37 | BrokenWire |  | Fair | No | Call related to call at #16 Henry Morgan avenue.
Non-Outage | J.E.26.08.10291 | C001891027 | Dwayne Cohen | KSAN | Completed | Load_257856 | Washington Blvd - 410 | 2026-08-17 10:56 | 2026-08-17 10:57 | 2026-08-17 12:03 | 2026-08-17 12:03 | 2026-08-17 12:48 | 2026-08-17 12:49 | 2026-08-17 12:49 | 2026-08-17 12:49 |  |  | Fair | No | Premises found okay
Non-Outage | J.E.26.08.13584 | C001891028 | Dwayne Cohen | KSAN | Completed | Load_261467 | Washington Blvd - 410 | 2026-08-17 10:56 | 2026-08-17 10:57 | 2026-08-17 12:49 | 2026-08-17 12:50 | 2026-08-17 13:23 | 2026-08-17 13:40 | 2026-08-17 13:41 | 2026-08-17 13:41 |  |  | Fair | No | Premises found close .
Non-Outage | J.E.26.08.21718 | C001891026 | Dwayne Cohen | KSAN | Completed | Load_264325 | Washington Blvd - 510 | 2026-08-17 10:56 | 2026-08-17 10:57 | 2026-08-17 11:43 | 2026-08-17 11:43 | 2026-08-17 12:01 | 2026-08-17 12:02 | 2026-08-17 12:03 | 2026-08-17 12:03 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.26215 | C001891029 | Raymond Carr | St.Mary | Completed | Load_243605 | Oracabessa - 110 | 2026-08-17 10:56 | 2026-08-17 10:57 | 2026-08-17 11:02 | 2026-08-17 11:03 | 2026-08-17 11:02 | 2026-08-17 11:00 | 2026-08-17 11:03 | 2026-08-17 11:03 |  |  | Fair | No | Supply was restored.
Outage | J.E.26.08.26002 | C001891036 | Denton Williams | Portland | Completed | Load_352475 | Port Antonio - 410 | 2026-08-17 10:57 | 2026-08-17 10:59 | 2026-08-17 15:26 | 2026-08-17 15:26 | 2026-08-17 15:26 | 2026-08-17 15:30 | 2026-08-17 15:31 | 2026-08-17 15:31 |  |  | Fair | No | After calling digicel call center they said that power is at the site.
Outage | J.E.26.08.26035 | C001891035 | Denton Williams | Portland | Completed | Load_263415 | Port Antonio - 410 | 2026-08-17 10:57 | 2026-08-17 10:59 | 2026-08-17 13:13 | 2026-08-17 13:13 | 2026-08-17 13:44 | 2026-08-17 13:46 | 2026-08-17 13:47 | 2026-08-17 13:47 |  |  | Fair | No | Customer supply already restored
Outage | J.E.26.08.26052 | C001891048 | Radcliffe Coleman | St.Catherine | Completed | Load_270093 | Rhodens Pen - 210 | 2026-08-17 11:03 | 2026-08-17 11:04 | 2026-08-17 11:15 | 2026-08-17 11:16 | 2026-08-17 12:27 | 2026-08-17 13:48 | 2026-08-17 13:48 | 2026-08-17 13:48 |  |  | Fair | No | Location found with a bank of three transformer (3-50kva), with a drop lead burnt at pole. Repairs were done with the aid of three one bolt clamp, as the transformer drop leads were serviced. The bank was opened before repairs were done. Location now back to normal.
Outage | J.E.26.08.26156 | C001891047 | Ricky Hall | St.Catherine | Completed | Load_239666 | Rhodens Pen - 210 | 2026-08-17 11:03 | 2026-08-17 15:47 | 2026-08-17 20:20 | 2026-08-17 20:20 | 2026-08-17 22:19 | 2026-08-17 22:20 | 2026-08-17 22:20 | 2026-08-17 22:20 |  |  | Fair | No | Premises not located
Outage | J.E.26.08.26214 | C001891046 | Ricky Hall | St.Catherine | Completed | Load_260204 | Rhodens Pen - 410 | 2026-08-17 11:03 | 2026-08-17 15:47 | 2026-08-17 18:56 | 2026-08-17 18:56 | 2026-08-17 20:16 | 2026-08-17 20:17 | 2026-08-17 20:19 | 2026-08-17 20:19 |  |  | Fair | No | Premises not located
Non-Outage | J.E.26.08.17323 | C001891081 | Christopher West | Portmore | Completed | Load_576114 | Naggo Head - 510 | 2026-08-17 11:22 | 2026-08-17 11:23 | 2026-08-17 13:17 | 2026-08-17 13:18 | 2026-08-17 13:17 | 2026-08-17 14:01 | 2026-08-17 14:01 | 2026-08-17 14:01 |  |  | Fair | No | Defective 50kva transformer in bank x3 (2) 50 (1) 100, requesting a memo be sent to Mr. Wilkie to have same replaced
Outage | J.E.26.08.26329 | C001891088 | Roxroy Needham | St.Ann | Completed | Load_253225 | Roaring River - 210 | 2026-08-17 11:27 | 2026-08-17 22:58 | 2026-08-17 23:10 | 2026-08-17 23:11 | 2026-08-18 00:12 | 2026-08-18 00:28 | 2026-08-18 00:38 | 2026-08-18 00:38 | Fire | Y | Fair | No | Open a 25 KVA transformer at pole to retention 2 span of secondary line
Non-Outage | J.E.26.08.26180 | C001891090 | Horace Malcolm | St.James | Completed | Load_302847 | Bogue - 610 | 2026-08-17 11:29 | 2026-08-17 23:15 | 2026-08-18 01:28 | 2026-08-18 01:28 | 2026-08-18 02:01 | 2026-08-18 02:26 | 2026-08-18 02:26 | 2026-08-18 02:26 | Fire |  | Fair | No | Check and found no fire on pole
Outage | J.E.26.08.26236 | C001891116 | Richard Watson | St.Elizabeth | Completed | Load_265412 | Maggotty - 110 | 2026-08-17 11:37 | 2026-08-17 11:38 | 2026-08-17 12:30 | 2026-08-17 12:31 | 2026-08-17 12:55 | 2026-08-17 13:16 | 2026-08-17 13:20 | 2026-08-17 13:20 |  |  | Fair | No | Replace blown 20amp junction fuse no pole#, also replace blown 8amp junction fuse at pole#0141265, after completing patrol, suspected cause lightning, supply restored.
Outage | J.E.26.08.26311 | C001891117 | Raheem Ricketts | St.Elizabeth | Completed | Load_292664 | Maggotty - 110 | 2026-08-17 11:37 | 2026-08-17 15:36 | 2026-08-17 15:41 | 2026-08-17 15:48 | 2026-08-17 15:48 | 2026-08-17 15:49 | 2026-08-17 15:49 | 2026-08-17 15:49 |  |  | Fair | No | Unable to locate customer cell number went straight voicemail after several calls
Outage | J.E.26.08.26118 | C001891119 | Wan Carlos Scarlett | Portmore | Completed | Load_261848 | Naggo Head - 610 | 2026-08-17 11:38 | 2026-08-17 11:40 | 2026-08-17 12:14 | 2026-08-17 12:14 | 2026-08-17 12:35 | 2026-08-17 13:22 | 2026-08-17 13:23 | 2026-08-17 13:23 |  |  | Fair | No | Customer not available at this time premises closed.readings from secondary line pole to customer service wire 115-116-231
Outage | J.E.26.08.26243 | C001891118 | Richard Watson | St.Elizabeth | Completed | Load_241146 | Maggotty - 110 | 2026-08-17 11:38 | 2026-08-17 11:39 | 2026-08-17 13:23 | 2026-08-17 13:23 | 2026-08-17 13:42 | 2026-08-17 13:53 | 2026-08-17 14:00 | 2026-08-17 14:00 |  |  | Fair | No | Voltage found in meter socket 118v, 118v, 236v, customer meter socket corroded, meter also single phasing and burnt on line and loadside, technician on site for meter change, customer advised to replace meter socket as soon as possible.
Non-Outage | J.E.26.08.26303 | C001891121 | Clyde Brown | Clarendon | Completed | Load_270079 | Monymusk - 410 | 2026-08-17 11:39 | 2026-08-17 11:43 | 2026-08-17 12:42 | 2026-08-17 12:43 | 2026-08-17 12:43 | 2026-08-17 12:41 | 2026-08-17 12:50 | 2026-08-17 12:50 |  |  | SevereWind | No | Blown 40 amps junction fuse on Salt River road ,line patrolled and no fault seen,blown fuse replaced.
Outage | J.E.26.08.26205 | C001891120 | Damion Reid | Manchester | Completed | Load_258296 | Kendal - 310 | 2026-08-17 11:39 | 2026-08-17 15:29 | 2026-08-17 17:43 | 2026-08-17 17:44 | 2026-08-17 18:00 | 2026-08-17 18:06 | 2026-08-17 18:07 | 2026-08-17 18:07 | Fire |  | Fair | No | Area found ok call related to one done last night
Non-Outage | J.E.26.07.39517 | C001891122 | Oraine Minto | St.Ann | Completed | Load_245336 | Roaring River - 210 | 2026-08-17 11:41 | 2026-08-17 11:42 | 2026-08-18 10:59 | 2026-08-18 11:10 | 2026-08-18 11:10 | 2026-08-18 12:15 | 2026-08-18 12:16 | 2026-08-18 12:16 |  |  | Fair | No | 1 one bolt clamp 2 red to red was used 221v
Outage | J.E.26.08.26012 | C001891130 | Cliton Henry | St.Mary | Completed | Load_241132 | Annotto Bay - 310 | 2026-08-17 11:43 | 2026-08-17 11:44 | 2026-08-17 14:26 | 2026-08-17 14:27 | 2026-08-17 14:54 | 2026-08-17 14:57 | 2026-08-17 14:58 | 2026-08-17 14:58 |  |  | Fair | No | The Truck unable to access locate due to rough terrain. A 4 wheel drive required
Outage | J.E.26.08.26266 | C001891131 | Clyde Brown | Clarendon | Completed | Load_267278 | May Pen - 210 | 2026-08-17 11:45 | 2026-08-17 11:51 | 2026-08-17 12:51 | 2026-08-17 12:51 | 2026-08-17 14:44 | 2026-08-17 14:43 | 2026-08-17 14:51 | 2026-08-17 14:51 | BrokenWire | Y | SevereWind | No | Blown 20 amps junction fuse in Race track and 3 amps fuse for 25 kva transformer caused by men cut tree on primary and secondary line ,cleared and blown fuse replaced.
Outage | J.E.26.08.26217 | C001891134 | Clyde Brown | Clarendon | Completed | Load_267198 | Parnassus - 210 | 2026-08-17 11:49 | 2026-08-17 11:51 | 2026-08-17 17:01 | 2026-08-17 17:01 | 2026-08-17 17:01 | 2026-08-17 16:51 | 2026-08-17 17:06 | 2026-08-17 17:06 |  |  | Fair | No | Customer said this call is Manchester call
Non-Outage | J.E.26.08.26158 | C001891151 | Denton Williams |  | Completed |  |  | 2026-08-17 12:05 | 2026-08-17 12:07 | 2026-08-17 15:49 | 2026-08-17 15:50 | 2026-08-17 16:59 | 2026-08-17 17:19 | 2026-08-17 17:21 | 2026-08-17 17:21 | BrokenPole |  | Fair | No | Pole rotten just above ground level. Refer to Zeno nation for follow up.
Outage | J.E.26.08.26312 | C001891163 | Shawn Medley | St.James | Completed | Load_249459 | Bogue - 310 | 2026-08-17 12:13 | 2026-08-17 12:15 | 2026-08-17 14:41 | 2026-08-17 14:42 | 2026-08-17 14:56 | 2026-08-17 14:58 | 2026-08-17 15:01 | 2026-08-17 15:01 | BrokenWire |  | Fair | No | Found burnt off neutral; opend 100kva dropout link and conducted repairs by spice and retention neutral and terminated connections
Outage | J.E.26.08.26379 | C001891162 | Shawn Medley | St.James | Completed | Load_247198 | Bogue - 310 | 2026-08-17 12:13 | 2026-08-18 08:10 | 2026-08-18 13:20 | 2026-08-18 13:20 | 2026-08-18 13:57 | 2026-08-18 13:58 | 2026-08-18 14:06 | 2026-08-18 14:06 |  |  | Fair | No | Premises checked and found ok
Outage | J.E.26.08.26375 | C001891167 | Damion Reid | Manchester | Completed | Load_250031 | Kendal - 210 | 2026-08-17 12:18 | 2026-08-17 15:25 | 2026-08-17 19:15 | 2026-08-17 19:15 | 2026-08-17 19:42 | 2026-08-17 20:19 | 2026-08-17 20:21 | 2026-08-17 20:21 | BrokenPole |  | Fair | No | Broken pole and low hanging wire customer reporting is not JPS property
Outage | J.E.26.08.26387 | C001891166 | Richard Watson | St.Elizabeth | Completed | Load_252931 | Maggotty - 210 | 2026-08-17 12:18 | 2026-08-17 12:19 | 2026-08-17 14:05 | 2026-08-17 14:05 | 2026-08-17 14:50 | 2026-08-17 15:15 | 2026-08-17 15:21 | 2026-08-17 15:21 | BrokenWire |  | Fair | No | Found broken service wire cause by passing truck, service wire disconnected and removed from secondary pole, customer is currently without a stantion and was advised to get an electrician to effect repairs and call back for reconnection.
Non-Outage | J.E.26.08.25212 | C001891170 | Wan Carlos Scarlett | St.Catherine | Completed | Load_265320 | Twickenham - 210 | 2026-08-17 12:26 | 2026-08-17 12:27 | 2026-08-17 13:23 | 2026-08-17 13:24 | 2026-08-17 14:25 | 2026-08-17 14:26 | 2026-08-17 14:29 | 2026-08-17 14:29 |  |  | Fair | No | Found customer service wire delivered use 60ft of # 6 service wire use 3 Penn union at service wire phase and neutral use 3 one bolt clamps at open secondary line readings 115-114-230
Outage | J.E.26.08.26069 | C001891189 | Elvis Trowers | KSAN | Completed | Load_237958 | Washington Blvd - 310 | 2026-08-17 12:36 | 2026-08-17 12:37 | 2026-08-17 14:57 | 2026-08-17 14:58 | 2026-08-17 15:35 | 2026-08-17 15:30 | 2026-08-17 15:37 | 2026-08-17 15:37 | LowHangingWires |  | Fair | No | Customer service wire #6 triplex neutral burn off in mid span. Repair using 5ft #6 triplex wire and two 1- bolt clamps.
Outage | J.E.26.08.26119 | C001891188 | Elvis Trowers | KSAS | Completed | Load_289378 | Greenwich - 510 | 2026-08-17 12:36 | 2026-08-17 12:37 | 2026-08-17 15:37 | 2026-08-17 15:38 | 2026-08-17 15:51 | 2026-08-17 16:10 | 2026-08-17 16:12 | 2026-08-17 16:12 |  |  | Fair | No | Found one 3 transformer fuse blown at pole #( no pole#) refused using one 3 amps fuse and reclosed transformer switch and the fuse blow again and also blow a 15 amps junction fuse oil was seen coming from the transformer. Defective 15 amps transformer whit YP box # cp021. Refer to maintenance.
Outage | J.E.26.08.26185 | C001891190 | Elvis Trowers | KSAS | Completed | Load_575567 | Duhaney - 410 | 2026-08-17 12:36 | 2026-08-17 12:37 | 2026-08-17 14:05 | 2026-08-17 14:05 | 2026-08-17 14:38 | 2026-08-17 14:40 | 2026-08-17 14:55 | 2026-08-17 14:55 |  |  | Fair | No | 40ft concrete pole broken in two pieces by falling transmission pole caught on fire. Pole has on 3- phase primary but only one leg is in used and system neutral whit T.A. Construction pole top and stand off bracket whit post type isolators. Line feeding the bump in rivertan. Refer to maintenance.
Outage | J.E.26.08.26308 | C001891187 | Elvis Trowers | KSAN | Completed | Load_293663 | Washington Blvd - 710 | 2026-08-17 12:36 | 2026-08-17 12:37 | 2026-08-17 13:00 | 2026-08-17 13:01 | 2026-08-17 13:53 | 2026-08-17 13:55 | 2026-08-17 14:01 | 2026-08-17 14:01 |  |  | Fair | No | Y.P box at pole #0064837 burned up and was change to a hexing box #07282 but there is about 3-4 customers still whit out power. J.P.S. Escalation states the box is not registered. Refer to field service.
Outage | J.E.26.08.26138 | C001891211 | Rusean Allen | KSAS | Completed | Load_262317 | Greenwich - 310 | 2026-08-17 12:55 | 2026-08-17 12:58 | 2026-08-17 14:04 | 2026-08-17 14:04 | 2026-08-17 14:13 | 2026-08-17 14:16 | 2026-08-17 14:16 | 2026-08-17 14:16 | TreeContact |  | Fair | No | Secondary bushing required, refer to bushing department
Outage | J.E.26.08.25842 | C001891217 | Derrick Dawkins | St.James | Completed | Load_1002386 | Bogue - 310 | 2026-08-17 13:00 | 2026-08-17 13:01 | 2026-08-17 13:48 | 2026-08-17 13:52 | 2026-08-17 14:17 | 2026-08-17 14:45 | 2026-08-17 14:46 | 2026-08-17 14:46 |  |  | Fair | No | Found fuse holder defective replaced fuse holder
Outage | J.E.26.08.26029 | C001891238 | Derrick Dawkins | St.James | Completed | Load_301719 | Bogue - 310 | 2026-08-17 13:10 | 2026-08-17 13:11 | 2026-08-17 14:49 | 2026-08-17 14:50 | 2026-08-17 14:51 | 2026-08-17 14:52 | 2026-08-17 14:52 | 2026-08-17 14:52 |  |  | Fair | No | Premises not found
Outage | J.E.26.08.26256 | C001891236 | Derrick Dawkins | St.James | Completed | Load_576009 | Bogue - 310 | 2026-08-17 13:10 | 2026-08-17 13:11 | 2026-08-17 13:49 | 2026-08-17 13:51 | 2026-08-17 13:50 | 2026-08-17 13:51 | 2026-08-17 13:52 | 2026-08-17 13:52 |  |  | Fair | No | Premises ok
Non-Outage | J.E.26.08.12233 | C001891246 | Odeanie Davis | KSAS | Completed | Load_253177 | Rockfort - 410 | 2026-08-17 13:12 | 2026-08-17 13:13 | 2026-08-17 13:35 | 2026-08-17 14:57 | 2026-08-17 14:57 | 2026-08-17 14:58 | 2026-08-17 14:58 | 2026-08-17 14:58 |  |  | Fair | No | Customer stated that issue was resolved
Outage | J.E.26.08.26588 | C001891239 | Kenroy Dale | Manchester | Completed | Load_257142 | Spur Tree - 310 | 2026-08-17 13:12 | 2026-08-17 13:14 | 2026-08-17 15:33 | 2026-08-17 15:33 | 2026-08-17 17:16 | 2026-08-17 17:44 | 2026-08-17 17:46 | 2026-08-17 17:46 |  |  | Fair | No | Corrosion found at pole and pothead remade connection using 1 one bolt clamp and 2 Penn union voltage reading 112
Outage | J.E.26.08.26638 | C001891240 | Kenroy Dale | Manchester | Completed | Load_251691 | Spur Tree - 310 | 2026-08-17 13:12 | 2026-08-17 13:14 | 2026-08-17 21:24 | 2026-08-17 21:35 | 2026-08-17 22:38 | 2026-08-17 22:54 | 2026-08-17 22:55 | 2026-08-17 22:55 | BrokenWire |  | Fair | No | Effort to contact customer multiple times was unsuccessful area visited and still not found
Outage | J.E.26.08.26658 | C001891248 | Kenroy Dale | Manchester | Completed | Load_259187 | Spur Tree - 310 | 2026-08-17 13:14 | 2026-08-17 13:17 | 2026-08-17 18:47 | 2026-08-17 19:04 | 2026-08-17 20:32 | 2026-08-17 21:22 | 2026-08-17 21:23 | 2026-08-17 21:23 | BrokenWire |  | Fair | No | Corrosion found at pole remade connection using 2 one bolt clamp voltage reading 112/110/222
Non-Outage | J.E.26.07.00138 | C001891260 | Edward Royal | KSAN | Completed | Load_573772 | Washington Blvd - 310 | 2026-08-17 13:24 | 2026-08-18 10:56 | 2026-08-18 12:53 | 2026-08-18 12:53 | 2026-08-18 12:53 | 2026-08-18 13:20 | 2026-08-18 13:40 | 2026-08-18 13:40 |  |  | Fair | No | Customer have internal problems customer have faulty wiring advise customer to get a electrician to fix the problem voltage reading 231 115 116 v
Non-Outage | J.E.26.08.10298 | C001891261 | Edward Royal | KSAN | Completed | Load_573772 | Washington Blvd - 310 | 2026-08-17 13:24 | 2026-08-18 10:56 | 2026-08-18 13:41 | 2026-08-18 13:42 | 2026-08-18 13:41 | 2026-08-18 13:42 | 2026-08-18 13:42 | 2026-08-18 13:42 |  |  | Fair | No | Call related
Non-Outage | J.E.26.08.22360 | C001891259 | Fredrick Hamilton |  | Completed |  |  | 2026-08-17 13:24 | 2026-08-17 13:25 | 2026-08-17 13:39 | 2026-08-18 12:30 | 2026-08-18 12:29 | 2026-08-18 12:30 | 2026-08-18 12:31 | 2026-08-18 12:31 | BrokenWire |  | Fair | No | Caller was contacted who stated that power was restored fully and broken wire corrected
Non-Outage | J.E.26.08.17353 | C001891266 | Romeo Brissett | St.James | Completed | Load_255363 | Bogue - 610 | 2026-08-17 13:30 | 2026-08-17 13:31 | 2026-08-17 13:33 | 2026-08-17 13:35 | 2026-08-17 13:57 | 2026-08-17 14:05 | 2026-08-17 14:08 | 2026-08-17 14:08 | LeaningPole |  | Fair | No | Found (1)35ft guy pole severely rotten at the foot and broken at the foot, customer stated that her service wire was always been connected to that guy pole and then to the JPS main pole however since Melissa her service has been relocated to a neighbor pole due to defective guy pole. Please send to maintenance to change guy pole, removed and extend customer service wire from neighbor CT pole and relocate it to main transformer pole.
Non-Outage | J.E.26.08.21449 | C001891265 | Romeo Brissett | St.James | Completed | Load_267637 | Bogue - 610 | 2026-08-17 13:30 | 2026-08-17 13:31 | 2026-08-17 14:09 | 2026-08-17 14:09 | 2026-08-17 14:23 | 2026-08-17 15:00 | 2026-08-17 15:02 | 2026-08-17 15:02 |  |  | Fair | No | Spliced and retention customer service wire, used 20ft of #6 and 3 clamps. V/R 116-118-235
Outage | J.E.26.08.26465 | C001891277 | Delano Gayle | Portmore | Completed | Load_244060 | Naggo Head - 610 | 2026-08-17 13:38 | 2026-08-17 23:46 | 2026-08-18 01:27 | 2026-08-18 01:28 | 2026-08-18 02:31 | 2026-08-18 04:02 | 2026-08-18 04:02 | 2026-08-18 04:02 | BrokenWire |  | Fair | No | Broken secondary neutral in 2 span, tree contact, open 50kva transformer fuse no pole number, abandoned span where tree contact is as no customer is connected in that span,splice and retention use 30ft #2aa 4 clamps voltage readings 113-112-226
Non-Outage | J.E.26.08.26280 | C001891293 | Clyde Brown | Clarendon | Completed | Load_247456 | Parnassus - 210 | 2026-08-17 13:47 | 2026-08-17 13:48 | 2026-08-17 19:23 | 2026-08-17 19:24 | 2026-08-17 19:24 | 2026-08-17 18:42 | 2026-08-17 19:29 | 2026-08-17 19:29 | BrokenPole |  | Fair | No | TA-30c6 pole split at top and rotten at base need to be change urgently as pole top where d-iron is
Outage | J.E.26.08.26031 | C001891314 | Andre Smith | KSAS | Completed | Load_257291 | Rockfort - 210 | 2026-08-17 13:57 | 2026-08-17 14:01 | 2026-08-17 16:49 | 2026-08-17 16:50 | 2026-08-17 16:49 | 2026-08-17 21:20 | 2026-08-17 21:21 | 2026-08-17 21:21 |  |  | Fair | No | Repair burnt service wire 150ft #2aaa cause by illegal connections supply restored
Outage | J.E.26.08.26791 | C001891332 | Neville Spencer | Clarendon | Completed | Load_242241 | Parnassus - 210 | 2026-08-17 14:06 | 2026-08-18 07:27 | 2026-08-18 13:01 | 2026-08-18 13:01 | 2026-08-18 15:50 | 2026-08-18 16:47 | 2026-08-18 16:49 | 2026-08-18 16:49 | BrokenWire |  | Fair | No | Found defective 3 wire service installed 95 ft #6 triplex, 3 clamps, 3, 2/6 sleeves voltage reading 113 117 232 supply restored.
Outage | J.E.26.08.26707 | C001891354 | Christopher Edwards | KSAN | Completed | Load_239202 | Constant Spring - 210 | 2026-08-17 14:12 | 2026-08-17 14:13 | 2026-08-17 14:52 | 2026-08-17 14:52 | 2026-08-17 15:08 | 2026-08-17 15:42 | 2026-08-17 15:43 | 2026-08-17 15:43 |  |  | Fair | No | Refuse blown junction fuseUsing (1) 30 amps
Outage | J.E.26.08.26055 | C001891361 | Andre Smith | KSAS | Completed | Load_246167 | Duhaney - 410 | 2026-08-17 14:18 | 2026-08-17 14:19 | 2026-08-17 15:40 | 2026-08-17 15:41 | 2026-08-17 16:22 | 2026-08-17 16:49 | 2026-08-17 16:49 | 2026-08-17 16:49 | LeaningPole |  | Fair | No | Premises found okay supply restored
Non-Outage | J.E.26.08.26162 | C001891363 | Roemello Brown | Trelawny | Completed | Load_267113 | Martha Brae - 110 | 2026-08-17 14:19 | 2026-08-17 14:20 | 2026-08-18 08:25 | 2026-08-18 08:25 | 2026-08-18 08:38 | 2026-08-18 08:39 | 2026-08-18 10:03 | 2026-08-18 10:03 |  |  | Fair | No | Defective service wire have it replaced Voltage found 115/79/46Voltage leave 117/117/234
Non-Outage | J.E.26.08.26190 | C001891365 | Roemello Brown | Trelawny | Completed | Load_251680 | Martha Brae - 210 | 2026-08-17 14:19 | 2026-08-17 14:20 | 2026-08-18 13:19 | 2026-08-18 15:43 | 2026-08-18 16:04 | 2026-08-18 16:04 | 2026-08-18 16:05 | 2026-08-18 16:05 | Fire |  | Fair | No | Premises found working okay Voltage found 116/116/232Voltage leave 116/116/232
Non-Outage | J.E.26.08.26227 | C001891364 | Roemello Brown | Trelawny | Completed | Load_1001480 | Martha Brae - 210 | 2026-08-17 14:19 | 2026-08-17 14:20 | 2026-08-18 13:21 | 2026-08-18 13:24 | 2026-08-18 14:20 | 2026-08-18 14:20 | 2026-08-18 14:34 | 2026-08-18 14:34 |  |  | Fair | No | Premises found working okay Voltage found 116/116/232Voltage leave 116/116/232
Non-Outage | J.E.26.08.26331 | C001891362 | Roemello Brown | Trelawny | Completed | Load_263192 | Martha Brae - 110 | 2026-08-17 14:19 | 2026-08-17 14:20 | 2026-08-18 10:31 | 2026-08-18 11:24 | 2026-08-18 11:24 | 2026-08-18 11:24 | 2026-08-18 11:44 | 2026-08-18 11:44 |  |  | Fair | No | Secondary line giving a low reading needs emergency team to assist also kissing up on th flow line please assist as soon as possible Voltage found 122/89/203Voltage leave 122/89/203
Outage | J.E.26.08.26731 | C001891380 | Derrick Dawkins | St.James | Completed | Load_258487 | Bogue - 310 | 2026-08-17 14:27 | 2026-08-17 14:28 | 2026-08-17 15:55 | 2026-08-17 15:55 | 2026-08-17 16:24 | 2026-08-17 18:11 | 2026-08-17 18:14 | 2026-08-17 18:14 |  |  | Fair | No | Replace 75 feet #6 xxx splice and retention voltage left 105/108=213 used 3 clamp and 3 linket
Outage | J.E.26.08.26645 | C001891386 | Stephen Taylor | St.Thomas | Completed | Load_577217 | Good Year - 210 | 2026-08-17 14:31 | 2026-08-17 14:33 | 2026-08-17 15:06 | 2026-08-17 15:07 | 2026-08-17 15:08 | 2026-08-17 15:08 | 2026-08-17 15:09 | 2026-08-17 15:09 |  |  | Fair | No | Contact customer and customer say that power supply from yesterday
Outage | J.E.26.08.26653 | C001891385 | Stephen Taylor | St.Thomas | Completed | Load_239755 | Good Year - 210 | 2026-08-17 14:31 | 2026-08-17 14:33 | 2026-08-17 17:01 | 2026-08-17 17:02 | 2026-08-17 17:02 | 2026-08-17 17:02 | 2026-08-17 17:03 | 2026-08-17 17:03 | LowHangingWires |  | Fair | No | Jps wires are okay it is the telephone wires are hanging low
Outage | J.E.26.08.26678 | C001891384 | Stephen Taylor | St.Thomas | Completed | Load_577267 | Good Year - 210 | 2026-08-17 14:31 | 2026-08-17 14:33 | 2026-08-17 15:14 | 2026-08-17 15:15 | 2026-08-17 15:14 | 2026-08-17 15:15 | 2026-08-17 15:16 | 2026-08-17 15:16 |  |  | Fair | No | Contact customer and customer say that power is restored and now okay
Outage | J.E.26.08.26777 | C001891383 | Stephen Taylor | St.Thomas | Completed | Load_253693 | Good Year - 210 | 2026-08-17 14:31 | 2026-08-17 14:33 | 2026-08-17 15:16 | 2026-08-17 15:17 | 2026-08-17 15:28 | 2026-08-17 15:28 | 2026-08-17 15:41 | 2026-08-17 15:41 | BrokenWire |  | Fair | No | Clean low hanging service wire from the school premises customer is now okay
Outage | J.E.26.08.24776 | C001891400 | Andre Williams | Trelawny | Completed | Load_1001459 | Martha Brae - 110 | 2026-08-17 14:38 | 2026-08-18 08:12 | 2026-08-18 10:10 | 2026-08-18 10:12 | 2026-08-18 10:12 | 2026-08-18 10:13 | 2026-08-18 10:14 | 2026-08-18 10:14 |  |  | Fair | No | Premises ok and with supply
Outage | J.E.26.08.26537 | C001891444 | Damion Reid | Manchester | Completed | Load_262908 | Kendal - 210 | 2026-08-17 15:24 | 2026-08-17 15:25 | 2026-08-17 18:07 | 2026-08-17 18:07 | 2026-08-17 18:38 | 2026-08-17 19:13 | 2026-08-17 19:15 | 2026-08-17 19:15 |  |  | Fair | No | Customer meter is defective refer to field service meter #2841841
Outage | J.E.26.08.26782 | C001891450 | Damion Reid | Manchester | Completed | Load_261236 | Porus - 310 | 2026-08-17 15:28 | 2026-08-17 15:29 | 2026-08-17 16:08 | 2026-08-17 16:09 | 2026-08-17 17:11 | 2026-08-17 17:39 | 2026-08-17 17:43 | 2026-08-17 17:43 | BrokenPole |  | Fair | No | Unable to contact or locate customer
Non-Outage | J.E.26.08.17254 | C001891456 | Richard Watson | St.Elizabeth | Completed | Load_568323 | Maggotty - 110 | 2026-08-17 15:31 | 2026-08-18 07:46 | 2026-08-18 08:56 | 2026-08-18 08:57 | 2026-08-18 10:56 | 2026-08-18 12:35 | 2026-08-18 12:41 | 2026-08-18 12:41 |  |  | Fair | No | Replace defective 25kva transformer, transformer#R000652 with 15kva transformer, transformer#R016130, use one 1.5amp fuse at pole#616501, voltage left 120v, 120v, 240v, load reading 0amp.
Outage | J.E.26.08.25966 | C001891459 | Nickolas Rodriques | St.Catherine | Completed | Load_237688 | Twickenham - 210 | 2026-08-17 15:34 | 2026-08-17 15:43 | 2026-08-17 19:33 | 2026-08-17 21:31 | 2026-08-17 21:46 | 2026-08-17 22:00 | 2026-08-17 22:03 | 2026-08-17 22:03 |  |  | Fair | No | Checked and found customer without electricity caused by broken service wire at pole. Repaired by connecting the wire using one clamp, current reading is (114). Customer confirmed that all is well now.
Outage | J.E.26.08.25990 | C001891460 | Nickolas Rodriques | St.Catherine | Completed | Load_246296 | Twickenham - 210 | 2026-08-17 15:34 | 2026-08-17 15:43 | 2026-08-17 19:44 | 2026-08-17 19:45 | 2026-08-17 19:59 | 2026-08-17 20:23 | 2026-08-17 20:33 | 2026-08-17 20:33 |  |  | Fair | No | The customer stated that he was experiencing issues with his prepaid box which was later resolved.
Outage | J.E.26.08.26163 | C001891465 | Nickolas Rodriques | St.Catherine | Completed | Load_259926 | Twickenham - 210 | 2026-08-17 15:34 | 2026-08-17 15:43 | 2026-08-17 16:21 | 2026-08-17 16:23 | 2026-08-17 16:52 | 2026-08-17 17:00 | 2026-08-17 17:28 | 2026-08-17 17:28 |  |  | Fair | No | Customer was located and stated that she was having an internal breaker issue that was rectified by her Electrician.
Outage | J.E.26.08.26391 | C001891458 | Dwayne Samuels | Trelawny | Completed | Load_574629 | Greenwood - 110 | 2026-08-17 15:34 | 2026-08-17 15:38 | 2026-08-17 16:15 | 2026-08-17 16:15 | 2026-08-17 16:51 | 2026-08-17 17:02 | 2026-08-17 17:10 | 2026-08-17 17:10 |  |  | Fair | No | Patrol primary line to find 2 blown 15amp junction fuse complete line patrol before replacing 2 15amp junction fuse at same and close
Outage | J.E.26.08.26542 | C001891457 | Lionel Robinson | Trelawny | Completed | Load_269968 | Greenwood - 110 | 2026-08-17 15:34 | 2026-08-18 08:27 | 2026-08-18 09:55 | 2026-08-18 09:56 | 2026-08-18 10:38 | 2026-08-18 10:42 | 2026-08-18 10:45 | 2026-08-18 10:45 | LeaningPole |  | Fair | No | 2 leaning poles; 1 12meter HD concrete pole and a 40 class 4 wood pole please refer to maintenance
Outage | J.E.26.08.26810 | C001891461 | Dwayne Samuels | Trelawny | Completed | Load_241035 | Greenwood - 210 | 2026-08-17 15:34 | 2026-08-17 15:38 | 2026-08-17 19:12 | 2026-08-17 19:53 | 2026-08-17 20:12 | 2026-08-17 20:15 | 2026-08-17 20:15 | 2026-08-17 20:15 |  |  | Fair | No | Customer said that they did not make any report and fail to provide clear directions
Outage | J.E.26.08.26822 | C001891464 | Dwayne Samuels | Trelawny | Completed | Load_270145 | Greenwood - 110 | 2026-08-17 15:34 | 2026-08-17 15:38 | 2026-08-17 16:09 | 2026-08-17 17:13 | 2026-08-17 17:24 | 2026-08-17 17:25 | 2026-08-17 17:25 | 2026-08-17 17:25 |  |  | Fair | No | Patrol primary line to find 2 blown 15amp junction fuse complete line patrol before replacing 2 15amp junction fuse at same and close
Outage | J.E.26.08.26218 | C001891466 | Nickolas Rodriques | St.Catherine | Completed | Load_241679 | Twickenham - 210 | 2026-08-17 15:35 | 2026-08-17 15:43 | 2026-08-17 20:36 | 2026-08-17 20:37 | 2026-08-17 21:06 | 2026-08-17 21:28 | 2026-08-17 21:31 | 2026-08-17 21:31 |  |  | Fair | No | Checked and found customer without power caused by defective meter socket. Reading found (109-111-220). The service wire was isolated for safety and the customer was advised to get an Electrician to do repair.
Outage | J.E.26.08.26373 | C001891470 | Raheem Ricketts | St.Elizabeth | Completed | Load_265377 | Maggotty - 110 | 2026-08-17 15:35 | 2026-08-17 15:36 | 2026-08-17 15:41 | 2026-08-17 18:02 | 2026-08-17 21:38 | 2026-08-17 21:43 | 2026-08-17 21:43 | 2026-08-17 21:43 |  |  | Fair | No | Isolate 25kva to splice an retention 40ft of secondary neutral using 2lamps an one number 2 preform however customer upgraded from 110,connections to 220 customers needs meter upgrade meter # is 3005989
Outage | J.E.26.08.26732 | C001891469 | Raheem Ricketts | St.Elizabeth | Completed | Load_264504 | Maggotty - 110 | 2026-08-17 15:35 | 2026-08-17 15:36 | 2026-08-17 15:41 | 2026-08-17 17:57 | 2026-08-17 17:57 | 2026-08-17 17:58 | 2026-08-17 17:58 | 2026-08-17 17:58 |  |  | Fair | No | Customer says he will report back the issue tomorrow because no one is home
Outage | J.E.26.08.26861 | C001891467 | Raheem Ricketts | St.Elizabeth | Completed | Load_254553 | Maggotty - 210 | 2026-08-17 15:35 | 2026-08-17 15:36 | 2026-08-17 15:41 | 2026-08-17 16:03 | 2026-08-17 17:11 | 2026-08-17 17:52 | 2026-08-17 17:52 | 2026-08-17 17:52 | BangingWires |  | Fair | No | Isolate 25k to retention 1pole span of secondary neutral using 2clamps an one #2,preform
Outage | J.E.26.08.26595 | C001891481 | Dwayne Samuels | Trelawny | Completed | Load_292887 | Greenwood - 210 | 2026-08-17 15:40 | 2026-08-17 15:42 | 2026-08-17 16:08 | 2026-08-17 18:50 | 2026-08-17 19:41 | 2026-08-17 19:52 | 2026-08-17 19:52 | 2026-08-17 19:52 |  |  | Fair | No | Customer was reconnected via call cell center
Outage | J.E.26.08.26919 | C001891478 | Antony Levy | KSAN | Completed | Load_263145 | Washington Blvd - 610 | 2026-08-17 15:40 | 2026-08-17 15:47 | 2026-08-17 16:51 | 2026-08-17 16:52 | 2026-08-17 17:22 | 2026-08-17 19:45 | 2026-08-17 19:48 | 2026-08-17 19:48 |  |  | Fair | No | Cx stated no supply .... defective switch and burnt switch top jumper found for 50kva transformer .... switch replaced fuse closed....power restored
Non-Outage | J.E.26.08.26594 | C001891493 | Richman Whyte | Westmoreland | Completed | Load_295423 | Paradise - 210 | 2026-08-17 15:41 | 2026-08-17 16:02 | 2026-08-17 20:07 | 2026-08-17 20:07 | 2026-08-17 21:42 | 2026-08-17 21:42 | 2026-08-17 21:43 | 2026-08-17 21:43 |  |  | Fair | No | Repair burnt off service wire at secondary line use 1 one bolt clamp
Outage | J.E.26.08.26369 | C001891483 | Nickolas Rodriques | St.Catherine | Completed | Load_250245 | Twickenham - 210 | 2026-08-17 15:41 | 2026-08-17 15:43 | 2026-08-17 17:39 | 2026-08-17 17:39 | 2026-08-17 18:14 | 2026-08-17 18:12 | 2026-08-17 18:36 | 2026-08-17 18:36 |  |  | Fair | No | Checked and found customer with unstable voltage caused by corroded connection. Repaired by replacing two one-bolt clamps and two service sleeves at pole and pothead respectively. Current reading (118)
Non-Outage | J.E.26.08.26584 | C001891496 | Richman Whyte | Westmoreland | Completed | Load_265099 | Paradise - 210 | 2026-08-17 15:42 | 2026-08-17 16:02 | 2026-08-17 18:18 | 2026-08-17 18:18 | 2026-08-17 18:18 | 2026-08-17 20:03 | 2026-08-17 20:07 | 2026-08-17 20:07 |  |  | Fair | No | Change one 1bolt clamp at secondary line voltage #114 114 228 however customer have internal problem advise to fix
Outage | J.E.26.08.24837 | C001891499 | Dwayne Samuels | Trelawny | Completed | Load_249194 | Duncans - 110 | 2026-08-17 15:42 | 2026-08-17 15:43 | 2026-08-17 16:03 | 2026-08-17 17:26 | 2026-08-17 18:23 | 2026-08-17 18:49 | 2026-08-17 18:49 | 2026-08-17 18:49 |  |  | Fair | No | Check and found area ok voltage found at customer pothead is 116v 115v 231v l12345
Outage | J.E.26.08.26737 | C001891494 | Nickolas Rodriques | St.Catherine | Completed | Load_243285 | Twickenham - 210 | 2026-08-17 15:42 | 2026-08-17 15:43 | 2026-08-17 22:03 | 2026-08-17 22:04 | 2026-08-17 23:24 | 2026-08-17 23:32 | 2026-08-17 23:34 | 2026-08-17 23:34 |  |  | Fair | No | Checked and found customer without power due to customer 3w meter that was found burnt. Reading found (118-118-236)). The meter needs to be replaced. Refer to metering department.
Outage | J.E.26.08.26814 | C001891495 | Delano Gayle | St.Catherine | Completed | Load_244601 | Twickenham - 210 | 2026-08-17 15:42 | 2026-08-17 23:47 | 2026-08-18 04:45 | 2026-08-18 04:45 | 2026-08-18 05:08 | 2026-08-18 05:35 | 2026-08-18 05:35 | 2026-08-18 05:35 | BrokenPole |  | Fair | No | Premises not found no answer from customer phone, no broken pole in vicinity of heart academy
Outage | J.E.26.08.26431 | C001891502 | Kemark Slue | St.Catherine | Completed | Load_243450 | New Michelton - 210 | 2026-08-17 15:43 | 2026-08-17 15:44 | 2026-08-17 21:59 | 2026-08-17 22:44 | 2026-08-17 22:44 | 2026-08-17 20:00 | 2026-08-17 22:45 | 2026-08-17 22:45 |  |  | Fair | No | Please refer to Moses PAYG customer without light and is unable to top up Serial 14315151259 Meter2289736 HEX02865 Coll 17473860 XFMR C005159 Pole 0088531 Pos 8
Outage | J.E.26.08.26328 | C001891503 | Kemark Slue | St.Catherine | Completed | Load_249137 | New Michelton - 310 | 2026-08-17 15:44 | 2026-08-17 15:45 | 2026-08-17 18:09 | 2026-08-17 22:46 | 2026-08-17 22:47 | 2026-08-17 21:00 | 2026-08-17 22:52 | 2026-08-17 22:52 |  |  | Fair | No | Premises was checked and found okay.
Outage | J.E.26.08.25640 | C001891509 | Ricky Hall | St.Catherine | Completed | Load_246091 | Rhodens Pen - 210 | 2026-08-17 15:45 | 2026-08-17 15:48 | 2026-08-17 16:06 | 2026-08-17 16:07 | 2026-08-17 17:14 | 2026-08-17 17:41 | 2026-08-17 17:42 | 2026-08-17 17:42 |  |  | Fair | Yes | Reconnect 3W service at pole use 2 clamps 118/118;236
Outage | J.E.26.08.26122 | C001891507 | Ricky Hall | St.Catherine | Completed | Load_261748 | Rhodens Pen - 310 | 2026-08-17 15:45 | 2026-08-17 15:46 | 2026-08-17 17:43 | 2026-08-17 18:20 | 2026-08-17 18:47 | 2026-08-17 18:52 | 2026-08-17 18:55 | 2026-08-17 18:55 |  |  | Fair | No | Customer found with supply
Outage | J.E.26.08.26673 | C001891506 | Ricky Hall | St.Catherine | Completed | Load_556330 | Rhodens Pen - 210 | 2026-08-17 15:45 | 2026-08-17 15:46 | 2026-08-17 17:38 | 2026-08-17 17:42 | 2026-08-17 18:11 | 2026-08-17 18:19 | 2026-08-17 18:19 | 2026-08-17 18:19 |  |  | Fair | No | Customer found with supply 118/118/236
Outage | J.E.26.08.26827 | C001891505 | Swon Miller | St.James | Completed | Load_258432 | Bogue - 510 | 2026-08-17 15:45 | 2026-08-17 15:47 | 2026-08-17 16:33 | 2026-08-17 16:34 | 2026-08-17 16:55 | 2026-08-26 05:28 | 2026-08-17 17:31 | 2026-08-17 17:31 |  |  | Fair | No | Found 1,25 kva transformer fuse blown cause by contamination replace 3 amp in 25 kva transformer voltage found 0.000 voltage left 116/116/232
Outage | J.E.26.08.26900 | C001891511 | Swon Miller | St.James | Completed | Load_249034 | Bogue - 610 | 2026-08-17 15:45 | 2026-08-17 15:46 | 2026-08-17 19:09 | 2026-08-17 19:10 | 2026-08-17 20:19 | 2026-08-17 20:45 | 2026-08-17 20:46 | 2026-08-17 20:46 |  |  | Fair | No | Found customer without supply from hurricane m voltage found 0.000.found customer meter pole overgrown with vegetation no service wire to carry out repairs customer requires a 100ft#6 triplex to carry out repairs voltage left 0.000
Outage | J.E.26.08.26908 | C001891510 | Romeo Brissett | St.James | Completed | Load_263018 | Bogue - 610 | 2026-08-17 15:45 | 2026-08-18 07:57 | 2026-08-18 08:05 | 2026-08-18 11:40 | 2026-08-18 11:39 | 2026-08-18 00:50 | 2026-08-18 12:55 | 2026-08-18 12:55 |  |  | Fair | No | Installed 130ft of #6 and 2 clamps, V/R 112-111-226
Outage | J.E.26.08.26708 | C001891512 | Swon Miller | St.James | Completed | Load_569748 | Bogue - 510 | 2026-08-17 15:46 | 2026-08-17 15:46 | 2026-08-17 15:59 | 2026-08-17 16:00 | 2026-08-17 16:14 | 2026-08-11 04:30 | 2026-08-17 16:33 | 2026-08-17 16:33 |  |  | Fair | No | Check and found customer without supply customer service has been disconnected due to none payment of bill advise customer to make payment before supply can be restored voltage found 0.000 voltage left 0.000
Non-Outage | J.E.26.08.26383 | C001891519 | Javid Vernon |  | Completed |  |  | 2026-08-17 15:47 | 2026-08-18 07:23 | 2026-08-18 07:41 | 2026-08-18 07:41 | 2026-08-18 07:41 | 2026-08-18 07:46 | 2026-08-18 07:47 | 2026-08-18 07:47 |  |  | Fair | No | Unable to get in contact with customer, multiple phone calls to customer number went unanswered
Outage | J.E.26.08.25593 | C001891526 | Richman Whyte | Westmoreland | Completed | Load_258299 | Paradise - 210 | 2026-08-17 15:48 | 2026-08-17 16:02 | 2026-08-17 21:44 | 2026-08-17 21:44 | 2026-08-17 21:44 | 2026-08-17 21:44 | 2026-08-17 21:46 | 2026-08-17 21:46 |  |  | Fair | No | Unable to locate or contact customer on the phone number given
Outage | J.E.26.08.25824 | C001891521 | Richard Nicholas | St.Catherine | Completed | Load_260327 | Tredegar - 310 | 2026-08-17 15:48 | 2026-08-17 15:49 | 2026-08-17 20:26 | 2026-08-17 20:26 | 2026-08-17 21:03 | 2026-08-17 21:12 | 2026-08-17 21:13 | 2026-08-17 21:13 |  |  | EarthMovement | No | Premises found ok
Outage | J.E.26.08.26077 | C001891524 | Richard Nicholas | St.Catherine | Completed | Load_263389 | Twickenham - 310 | 2026-08-17 15:48 | 2026-08-17 15:49 | 2026-08-17 17:52 | 2026-08-17 17:53 | 2026-08-17 18:34 | 2026-08-17 18:44 | 2026-08-17 18:48 | 2026-08-17 18:48 | Fire |  | Fair | No | Premises found ok however customer is more concerned about a nonfunctional led street light at is gate.
Outage | J.E.26.08.26574 | C001891525 | Richard Nicholas | St.Catherine | Completed | Load_238151 | Twickenham - 310 | 2026-08-17 15:48 | 2026-08-17 15:49 | 2026-08-17 16:33 | 2026-08-17 16:34 | 2026-08-17 17:21 | 2026-08-17 17:48 | 2026-08-17 17:51 | 2026-08-17 17:51 |  |  | Fair | No | Rammy system failure,please refer to the relevant department.
Outage | J.E.26.08.26663 | C001891522 | Richard Nicholas | St.Catherine | Completed | Load_252394 | Tredegar - 310 | 2026-08-17 15:48 | 2026-08-17 15:49 | 2026-08-17 18:48 | 2026-08-17 18:48 | 2026-08-17 19:24 | 2026-08-17 20:22 | 2026-08-17 20:23 | 2026-08-17 20:23 |  |  | Fair | No | Remade slack 3w service phase and neutral joint at pole and pothead,3clamp and 1 penunion was used.voltage reading 114x2 and 228v.
Outage | J.E.26.08.26907 | C001891523 | Richard Nicholas | St.Catherine | Completed | Load_246573 | Tredegar - 310 | 2026-08-17 15:48 | 2026-08-17 15:49 | 2026-08-17 21:13 | 2026-08-17 21:14 | 2026-08-17 21:43 | 2026-08-17 21:55 | 2026-08-17 21:57 | 2026-08-17 21:57 |  |  | Fair | No | Premises cannot locate and customer telephone ring without answer.
Outage | J.E.26.08.26377 | C001891527 | Richard Nicholas | St.Catherine | Completed | Load_238125 | Tredegar - 510 | 2026-08-17 15:50 | 2026-08-17 15:51 | 2026-08-17 21:57 | 2026-08-17 21:57 | 2026-08-17 22:25 | 2026-08-17 23:02 | 2026-08-17 23:03 | 2026-08-17 23:03 | LowHangingWires |  | Fair | No | Area found ok
Outage | J.E.26.08.26940 | C001891536 | Dwayne Samuels | Trelawny | Completed | Load_268005 | Greenwood - 110 | 2026-08-17 15:56 | 2026-08-17 16:13 | 2026-08-17 20:16 | 2026-08-17 20:16 | 2026-08-17 21:03 | 2026-08-17 22:19 | 2026-08-17 22:20 | 2026-08-17 22:20 | Fire |  | Fair | No | Customer service neutral is making contact with the lower phase secondary line caused by illegal connections open 1 25kva transformer to carry out repairs splice and retention customer service wire using about 5ft of number 6 wire and 2 one bolt clamps for repair and close voltage left 111v/114v/225v
Non-Outage | J.E.26.07.37319 | C001891544 | Royston Montague |  | Completed |  |  | 2026-08-17 15:59 | 2026-08-17 16:00 | 2026-08-17 16:29 | 2026-08-18 08:28 | 2026-08-18 09:04 | 2026-08-18 09:04 | 2026-08-18 09:04 | 2026-08-18 09:04 | Fire |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.08.26898 | C001891545 | Elvis Trowers |  | Completed |  |  | 2026-08-17 16:01 | 2026-08-17 16:34 | 2026-08-17 18:26 | 2026-08-17 18:26 | 2026-08-17 19:46 | 2026-08-17 19:40 | 2026-08-17 19:52 | 2026-08-17 19:52 |  |  | Fair | No | Found okay upon arrival. Customer has an internal problem. Readings at meter socket line side and loud side 112-113-205 & 234-235-228 volts.
Outage | J.E.26.08.26793 | C001891557 | Andre Smith | KSAS | Completed | Load_266520 | Rockfort - 210 | 2026-08-17 16:01 | 2026-08-17 16:51 | 2026-08-17 22:36 | 2026-08-17 22:36 | 2026-08-17 22:37 | 2026-08-17 22:38 | 2026-08-17 22:38 | 2026-08-17 22:38 |  |  | Fair | No | Replace defective one bolt clamp at pothead on phase supply restored 112V
Outage | J.E.26.08.26857 | C001891556 | Elvis Trowers | KSAS | Completed | Load_260390 | Greenwich - 710 | 2026-08-17 16:01 | 2026-08-17 16:34 | 2026-08-17 17:51 | 2026-08-17 17:52 | 2026-08-17 18:12 | 2026-08-17 18:10 | 2026-08-17 18:26 | 2026-08-17 18:26 | LeaningPole |  | Fair | No | 30ft wooden pole rotten at the foot and leaning towards complex. Pole has on about 7 service wire pole is a pilot pole. Pole at the intersection of Lincoln Crecent and Greenwich crescent.
Outage | J.E.26.08.26904 | C001891546 | Elvis Trowers | KSAS | Completed | Load_262127 | Greenwich - 410 | 2026-08-17 16:01 | 2026-08-17 16:34 | 2026-08-17 17:02 | 2026-08-17 17:24 | 2026-08-17 17:47 | 2026-08-17 17:40 | 2026-08-17 17:51 | 2026-08-17 17:51 |  |  | Fair | No | Found okay upon arrival. Customer has on internal problem. Readings at meter socket 117-118-235 volts.
Outage | J.E.26.08.26741 | C001891559 | Stephen Taylor | St.Thomas | Completed | Load_246185 | Good Year - 210 | 2026-08-17 16:05 | 2026-08-17 16:07 | 2026-08-17 16:29 | 2026-08-17 16:30 | 2026-08-17 16:29 | 2026-08-17 16:30 | 2026-08-17 16:30 | 2026-08-17 16:30 |  |  | Fair | No | Contact customer and customer say that power restore and now okay
Outage | J.E.26.08.26915 | C001891558 | Hopeton Henry | St.Thomas | Completed | Load_260008 | Good Year - 210 | 2026-08-17 16:05 | 2026-08-18 08:14 | 2026-08-18 14:07 | 2026-08-18 14:08 | 2026-08-18 14:07 | 2026-08-18 14:08 | 2026-08-18 14:11 | 2026-08-18 14:11 |  |  | Fair | No | Splice and retention broken conductors
Outage | J.E.26.08.26688 | C001891560 | Stephen Taylor | St.Thomas | Completed | Load_267393 | Good Year - 210 | 2026-08-17 16:06 | 2026-08-17 16:07 | 2026-08-17 16:34 | 2026-08-17 16:35 | 2026-08-17 16:35 | 2026-08-17 16:35 | 2026-08-17 16:35 | 2026-08-17 16:35 |  |  | Fair | No | Contact customer and customer say that power restore and now okay
Outage | J.E.26.08.26694 | C001891562 | Stephen Taylor | St.Thomas | Completed | Load_263467 | Good Year - 210 | 2026-08-17 16:06 | 2026-08-17 16:09 | 2026-08-17 16:33 | 2026-08-17 16:33 | 2026-08-17 16:33 | 2026-08-17 16:33 | 2026-08-17 16:34 | 2026-08-17 16:34 |  |  | Fair | Yes | Contact customer and customer say that power restore and now okay
Outage | J.E.26.08.22903 | C001891570 | Stephen Taylor | St.Thomas | Completed | Load_270128 | Good Year - 110 | 2026-08-17 16:09 | 2026-08-17 16:10 | 2026-08-17 17:33 | 2026-08-17 17:33 | 2026-08-17 17:54 | 2026-08-17 17:54 | 2026-08-17 19:13 | 2026-08-17 19:13 |  |  | Fair | No | Splice and retention 3 pole span 70 feet of secondary wire use 6 clamps and close up back transformer with a 3 amp fuse safely all customer is now okay
Outage | J.E.26.08.26683 | C001891571 | Stephen Taylor | St.Thomas | Completed | Load_246054 | Good Year - 210 | 2026-08-17 16:10 | 2026-08-17 16:11 | 2026-08-17 16:40 | 2026-08-17 16:40 | 2026-08-17 16:40 | 2026-08-17 16:44 | 2026-08-17 16:45 | 2026-08-17 16:45 |  |  | Fair | No | Jps pole was defective and change by the jps maintenance team customer is now okay
Outage | J.E.26.08.26666 | C001891572 | Stephen Taylor | St.Thomas | Completed | Load_267792 | Good Year - 210 | 2026-08-17 16:11 | 2026-08-17 16:11 | 2026-08-17 16:35 | 2026-08-17 16:36 | 2026-08-17 16:35 | 2026-08-17 16:35 | 2026-08-17 16:36 | 2026-08-17 16:36 |  |  | Fair | No | Contact customer and customer say that power restore and now okay
Outage | J.E.26.08.26632 | C001891577 | Daniel Francis | St.Ann | Completed | Load_249771 | Cardiff Hall - 310 | 2026-08-17 16:13 | 2026-08-17 16:14 | 2026-08-17 16:29 | 2026-08-17 16:30 | 2026-08-17 16:31 | 2026-08-17 16:31 | 2026-08-17 16:33 | 2026-08-17 16:33 | BrokenWire |  | Fair | No | Found okay we call customer and she say light come it’s okay now
Non-Outage | J.E.26.08.23696 | C001891588 | Denton Williams |  | Completed |  |  | 2026-08-17 16:19 | 2026-08-17 16:27 | 2026-08-17 18:03 | 2026-08-17 18:04 | 2026-08-17 18:03 | 2026-08-17 18:03 | 2026-08-17 18:05 | 2026-08-17 18:05 |  | Y | Fair | No | Customer stated that the power was restored.
Non-Outage | J.E.26.08.24608 | C001891590 | Denton Williams |  | Completed |  |  | 2026-08-17 16:19 | 2026-08-17 16:27 | 2026-08-17 18:15 | 2026-08-17 18:16 | 2026-08-17 18:17 | 2026-08-17 18:17 | 2026-08-17 18:19 | 2026-08-17 18:19 |  |  | EarthMovement | No | Customer stated she was inquiring about a bill, didn’t report an outage.
Non-Outage | J.E.26.08.26686 | C001891591 | Denton Williams |  | Completed |  |  | 2026-08-17 16:19 | 2026-08-17 16:27 | 2026-08-17 18:10 | 2026-08-17 18:10 | 2026-08-17 18:10 | 2026-08-17 18:10 | 2026-08-17 18:12 | 2026-08-17 18:12 |  |  | Fair | No | Customer stated that his electrician sorted out the issue
Outage | J.E.26.08.24131 | C001891589 | Denton Williams | Portland | Completed | Load_353118 | Port Antonio - 410 | 2026-08-17 16:19 | 2026-08-17 16:27 | 2026-08-17 17:27 | 2026-08-17 17:27 | 2026-08-17 17:27 | 2026-08-17 17:29 | 2026-08-17 17:31 | 2026-08-17 17:31 |  | Y | Fair | No | Use one 15 amp fuse to restore power to area. Bushing cause
Outage | J.E.26.08.25312 | C001891587 | Denton Williams | Portland | Completed | Load_256253 | Port Antonio - 310 | 2026-08-17 16:19 | 2026-08-17 16:27 | 2026-08-17 17:50 | 2026-08-17 17:51 | 2026-08-17 17:50 | 2026-08-17 17:51 | 2026-08-17 17:51 | 2026-08-17 17:51 |  |  | Fair | No | Power was restored from yesterday
Outage | J.E.26.08.25997 | C001891586 | Denton Williams | Portland | Completed | Load_248396 | Port Antonio - 410 | 2026-08-17 16:19 | 2026-08-17 16:27 | 2026-08-17 19:48 | 2026-08-17 19:48 | 2026-08-17 20:11 | 2026-08-17 20:18 | 2026-08-17 20:19 | 2026-08-17 20:19 |  |  | Fair | No | Customer confirmed electrical supply was restored at the site. Customer okay.
Outage | J.E.26.08.25320 | C001891595 | Denton Williams | Portland | Completed | Load_248396 | Port Antonio - 410 | 2026-08-17 16:20 | 2026-08-17 16:27 | 2026-08-17 17:36 | 2026-08-17 17:37 | 2026-08-17 17:36 | 2026-08-17 17:36 | 2026-08-17 17:42 | 2026-08-17 17:42 |  |  | Fair | No | Call was restored about 1:30 pm
Outage | J.E.26.08.26840 | C001891592 | Denton Williams | Portland | Completed | Load_575971 | Port Antonio - 310 | 2026-08-17 16:20 | 2026-08-17 16:27 | 2026-08-17 21:53 | 2026-08-17 21:53 | 2026-08-17 21:56 | 2026-08-17 22:06 | 2026-08-17 22:06 | 2026-08-17 22:06 |  |  | Fair | Yes | No information was provided.
Outage | J.E.26.08.26844 | C001891594 | Denton Williams | Portland | Completed | Load_265522 | Port Antonio - 310 | 2026-08-17 16:20 | 2026-08-17 16:27 | 2026-08-17 18:24 | 2026-08-17 18:24 | 2026-08-17 18:48 | 2026-08-17 19:01 | 2026-08-17 19:08 | 2026-08-17 19:08 | BrokenWire |  | Fair | No | Customer service from pole to meter needs to change, advised customer to get an electrician and repair damage pothead before wire can be replace and contact JPS after completed.
Outage | J.E.26.08.26973 | C001891593 | Denton Williams | Portland | Completed | Load_263415 | Port Antonio - 410 | 2026-08-17 16:20 | 2026-08-17 16:27 | 2026-08-17 20:11 | 2026-08-17 20:19 | 2026-08-17 20:19 | 2026-08-17 20:28 | 2026-08-17 20:31 | 2026-08-17 20:31 |  |  | Fair | No | The customer is experiencing low voltage. However, we’re unable to correct issue. Pole is located on the edge of a cliff, difficult terrain. Daylight attention is recommended.
Non-Outage | J.E.26.08.26918 | C001891602 | Denton Williams |  | Completed |  |  | 2026-08-17 16:22 | 2026-08-17 18:11 | 2026-08-17 20:31 | 2026-08-17 20:31 | 2026-08-17 20:31 | 2026-08-17 20:34 | 2026-08-17 20:35 | 2026-08-17 20:35 |  |  | Fair | No | Visited location and customer was not found. Need directions to locate customer and a valid Jamaica telephone number.
Non-Outage | J.E.26.08.26976 | C001891608 | Richman Whyte | Westmoreland | Completed | Load_244427 | Paradise - 110 | 2026-08-17 16:32 | 2026-08-17 16:34 | 2026-08-17 17:22 | 2026-08-17 17:22 | 2026-08-17 17:22 | 2026-08-17 17:42 | 2026-08-17 17:45 | 2026-08-17 17:45 |  |  | Rains | No | Repair burnt off transformer drop leads used 2pg clamps voltage 115 115 230
Outage | J.E.26.08.26442 | C001891614 | Neckell Ormsby | St.Mary | Completed | Load_252067 | Highgate -110 | 2026-08-17 16:39 | 2026-08-17 16:47 | 2026-08-17 21:17 | 2026-08-17 21:17 | 2026-08-17 21:53 | 2026-08-17 22:12 | 2026-08-17 22:12 | 2026-08-17 22:12 | BrokenWire |  | Fair | No | Unable to locate customer customer after several calls however Patrol cane heap and found no broken also seen no one to ask
Outage | J.E.26.08.26889 | C001891613 | Neckell Ormsby | St.Mary | Completed | Load_267063 | Annotto Bay - 310 | 2026-08-17 16:39 | 2026-08-17 16:47 | 2026-08-17 16:52 | 2026-08-17 16:52 | 2026-08-17 17:51 | 2026-08-17 19:24 | 2026-08-17 19:25 | 2026-08-17 19:25 | BrokenWire |  | Fair | No | Found broken secondary phase and neutral open 25kva transformer no pole # seen to splice and retention 2- pole span secondary using approximately 40 ft#2 AA, 3- one bolt clamps reclose 25 kva transformer
Outage | J.E.26.08.26912 | C001891612 | Neckell Ormsby | St.Mary | Completed | Load_239545 | Highgate - 210 | 2026-08-17 16:39 | 2026-08-17 16:47 | 2026-08-17 22:12 | 2026-08-17 22:13 | 2026-08-17 22:44 | 2026-08-17 22:47 | 2026-08-17 22:57 | 2026-08-17 22:57 | BrokenWire |  | Fair | No | Patrol tremolsworth and found supply in area however residents said the issue was resolved
Outage | J.E.26.08.24134 | C001891620 | Clyde Brown | Clarendon | Completed | Load_261972 | Parnassus - 210 | 2026-08-17 16:44 | 2026-08-17 16:50 | 2026-08-17 18:29 | 2026-08-17 19:30 | 2026-08-17 19:29 | 2026-08-17 15:46 | 2026-08-17 19:33 | 2026-08-17 19:33 |  |  | SevereWind | No | Blown 3 amps fuse for 25 kva transformer caused by secondary phase and neutral entangled by heavy wind ,conductor cleared and blown fuse replaced.
Non-Outage | J.E.26.08.26883 | C001891628 | Andre Williams | Trelawny | Completed | Load_263290 | Martha Brae - 210 | 2026-08-17 16:47 | 2026-08-18 09:46 | 2026-08-18 11:00 | 2026-08-18 11:08 | 2026-08-18 12:28 | 2026-08-18 12:30 | 2026-08-18 12:31 | 2026-08-18 12:31 |  |  | Fair | No | Open 100 kva and one 25 kva in bank of 2 , remake burnt off joint on 2 naut conductor and remove deffective #6 conductor from pole
Outage | J.E.26.08.26016 | C001891630 | Raymond Carr | St.Mary | Completed | Load_352793 | Oracabessa - 210 | 2026-08-17 16:49 | 2026-08-18 07:38 | 2026-08-18 10:04 | 2026-08-18 10:05 | 2026-08-18 10:49 | 2026-08-18 10:55 | 2026-08-18 10:57 | 2026-08-18 10:57 |  |  | Fair | No | No access to rammy system. Refer to field service department.
Outage | J.E.26.08.26033 | C001891635 | Neckell Ormsby | St.Mary | Completed | Load_241164 | Annotto Bay - 310 | 2026-08-17 16:50 | 2026-08-17 17:04 | 2026-08-17 19:30 | 2026-08-17 19:31 | 2026-08-17 20:13 | 2026-08-17 20:42 | 2026-08-17 20:42 | 2026-08-17 20:42 |  |  | Fair | No | Found junction fuse blown however unable to patrol due to terrain daytime attention requires
Outage | J.E.26.08.26311 | C001891631 | Selvin White | St.Elizabeth | Completed | Load_292664 | Maggotty - 110 | 2026-08-17 16:50 | 2026-08-17 20:29 | 2026-08-17 20:33 | 2026-08-17 20:39 | 2026-08-17 21:00 | 2026-08-17 21:56 | 2026-08-17 22:04 | 2026-08-17 22:04 |  |  | Fair | No | Replace a blown 1.5 amp fuse for a 10 KVA transformer circuit after resident removed entangled cow that was rapped around guy resulting tree contact causing secondary conductors to bang. Tree limbs were also cleared. Supply restored to the affected customers.
Outage | J.E.26.08.26802 | C001891632 | Raymond Carr | St.Mary | Completed | Load_353347 | Oracabessa - 210 | 2026-08-17 16:50 | 2026-08-18 07:38 | 2026-08-18 08:21 | 2026-08-18 08:22 | 2026-08-18 09:36 | 2026-08-18 09:00 | 2026-08-18 09:38 | 2026-08-18 09:38 |  |  | Fair | No | Customer reported that internal wiring issues were resolved.
Outage | J.E.26.08.27006 | C001891661 | Elvis Trowers | KSAS | Completed | Load_240764 | Duhaney - 410 | 2026-08-17 17:16 | 2026-08-17 17:17 | 2026-08-17 21:20 | 2026-08-17 21:20 | 2026-08-17 21:37 | 2026-08-17 22:20 | 2026-08-17 22:24 | 2026-08-17 22:24 | BrokenWire |  | Fair | No | Customer service wire #6 triplex pull down in motor vehicle accident. Repair using three 1- bolt clamps. Readings at meter socket 114-115-230 volts.
Outage | J.E.26.08.26366 | C001891668 | Eric Williams | KSAN | Completed | Load_240919 | Constant Spring - 410 | 2026-08-17 17:24 | 2026-08-17 17:25 | 2026-08-17 19:21 | 2026-08-17 21:06 | 2026-08-17 21:15 | 2026-08-17 21:25 | 2026-08-17 21:32 | 2026-08-17 21:32 | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards | Y | Fair | No | Blown 15amps junction fuse found and replaced cause by tree contact, major bushing done
Outage | J.E.26.08.26928 | C001891669 | Eric Williams | KSAN | Completed | Load_251288 | Constant Spring - 410 | 2026-08-17 17:24 | 2026-08-17 17:25 | 2026-08-17 17:32 | 2026-08-17 17:33 | 2026-08-17 19:21 | 2026-08-17 21:04 | 2026-08-17 21:06 | 2026-08-17 21:06 |  | Y | Fair | No | Blown 15amps junction fuse cause by tree contact, major bushing done
Outage | J.E.26.08.26034 | C001891670 | Neckell Ormsby | KSAN | Completed | Load_262426 | Constant Spring - 410 | 2026-08-17 17:26 | 2026-08-17 17:27 | 2026-08-17 19:27 | 2026-08-17 19:28 | 2026-08-17 19:27 | 2026-08-17 19:30 | 2026-08-17 19:30 | 2026-08-17 19:30 | BrokenWire |  | Fair | No | Found broken secondary phase and neutral open 25kva transformer no pole # seen to splice and retention 2- pole span secondary using approximately 40 ft#2 AA, 3- one bolt clamps reclose 25 kva transformer
Outage | J.E.26.08.27012 | C001891676 | Daniel Francis | St.Ann | Completed | Load_248204 | Cardiff Hall - 310 | 2026-08-17 17:39 | 2026-08-17 17:46 | 2026-08-17 21:16 | 2026-08-17 21:16 | 2026-08-17 21:16 | 2026-08-17 21:17 | 2026-08-17 21:19 | 2026-08-17 21:19 | TreeContact |  | Fair | No | Tree not making contact with JPS conducter
Outage | J.E.26.08.27026 | C001891675 | Daniel Francis | St.Ann | Completed | Load_258189 | Cardiff Hall - 210 | 2026-08-17 17:39 | 2026-08-17 17:46 | 2026-08-17 18:09 | 2026-08-17 18:09 | 2026-08-17 19:09 | 2026-08-17 19:28 | 2026-08-17 19:31 | 2026-08-17 19:31 |  |  | Fair | No | Remade joint at pothead voltage 107/107/215
Outage | J.E.26.08.27052 | C001891677 | Kemark Slue | St.Catherine | Completed | Load_263034 | New Michelton - 310 | 2026-08-17 17:41 | 2026-08-17 17:42 | 2026-08-17 18:09 | 2026-08-17 22:52 | 2026-08-17 22:52 | 2026-08-17 21:08 | 2026-08-17 22:53 | 2026-08-17 22:53 | BrokenWire |  | Fair | No | Premises was checked and found okay.
Outage | J.E.26.08.26961 | C001891681 | Antony Levy | KSAS | Completed | Load_267920 | Duhaney - 310 | 2026-08-17 17:46 | 2026-08-17 17:52 | 2026-08-17 20:44 | 2026-08-17 20:44 | 2026-08-17 21:24 | 2026-08-17 22:05 | 2026-08-17 22:06 | 2026-08-17 22:06 |  |  | Fair | No | Customer meter was turned off,power restored.
Outage | J.E.26.08.26901 | C001891686 | Horace Malcolm | St.James | Completed | Load_249993 | Bogue - 310 | 2026-08-17 17:47 | 2026-08-18 15:33 | 2026-08-18 16:36 | 2026-08-18 16:36 | 2026-08-18 16:44 | 2026-08-18 16:46 | 2026-08-18 16:46 | 2026-08-18 16:46 |  |  | Fair | No | Unable to locate meter from directions call to customer unavailable
Outage | J.E.26.08.26914 | C001891687 | Christopher Edwards | KSAN | Completed | Load_267645 | Constant Spring - 410 | 2026-08-17 17:47 | 2026-08-18 07:24 | 2026-08-18 09:34 | 2026-08-18 09:35 | 2026-08-18 10:32 | 2026-08-18 11:37 | 2026-08-18 11:38 | 2026-08-18 11:38 |  |  | Fair | No | Splice and retention broken #6 service wire Using:60ft #6 wire6 one bolt clamps
Outage | J.E.26.08.26922 | C001891685 | Derrick Dawkins | St.James | Completed | Load_253589 | Bogue - 310 | 2026-08-17 17:47 | 2026-08-17 18:37 | 2026-08-17 20:07 | 2026-08-17 20:08 | 2026-08-17 20:17 | 2026-08-17 20:43 | 2026-08-17 20:44 | 2026-08-17 20:44 |  |  | Fair | No | Found a 25 kva transformer fuse blown 2 amp due to the rain replace 2 amp fuse
Outage | J.E.26.08.26990 | C001891684 | Shawn Medley | St.James | Completed | Load_243184 | Bogue - 310 | 2026-08-17 17:47 | 2026-08-18 08:08 | 2026-08-18 14:09 | 2026-08-18 14:10 | 2026-08-18 14:30 | 2026-08-18 14:30 | 2026-08-18 14:41 | 2026-08-18 14:41 |  |  | Fair | No | Premises checked and found ok
Outage | J.E.26.08.26960 | C001891689 | Antony Levy | KSAN | Completed | Load_412897 | Constant Spring - 410 | 2026-08-17 17:50 | 2026-08-17 17:53 | 2026-08-17 19:49 | 2026-08-17 19:49 | 2026-08-17 20:17 | 2026-08-17 20:44 | 2026-08-17 20:44 | 2026-08-17 20:44 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.26819 | C001891692 | Nickolas Rodriques | St.Catherine | Completed | Load_253902 | Twickenham - 210 | 2026-08-17 17:52 | 2026-08-17 17:54 | 2026-08-17 18:39 | 2026-08-17 18:39 | 2026-08-17 19:07 | 2026-08-17 19:29 | 2026-08-17 19:33 | 2026-08-17 19:33 |  |  | Fair | No | Checked and found a 30 amp junction fuse blown. Patrol and found nothing on line. Repaired by replacing the fuse after completing patrol.
Outage | J.E.26.08.26950 | C001891693 | Milton Charlton | KSAN | Completed | Load_259174 | Hope - 510 | 2026-08-17 17:53 | 2026-08-18 07:25 | 2026-08-18 11:21 | 2026-08-18 11:22 | 2026-08-18 14:14 | 2026-08-18 14:05 | 2026-08-18 15:18 | 2026-08-18 15:18 | BrokenWire |  | Fair | No | Isolate 25 kva transformer at pole #(no. Pole. # )and disconnect open wire secondary phase broken by rubbing on concrete church top. Customer would like conductor to raise off the top of the church and we are unable to retrieve broken conductor in gully. Need about 300ft #2 triplex to replace open wire secondary and raise conductor.
Outage | J.E.26.08.24714 | C001891698 | Denton Williams | Portland | Completed | Load_241333 | Port Antonio - 410 | 2026-08-17 18:00 | 2026-08-17 18:11 | 2026-08-17 19:08 | 2026-08-17 19:09 | 2026-08-17 19:08 | 2026-08-17 19:08 | 2026-08-17 19:11 | 2026-08-17 19:11 |  |  | Fair | No | Power restored to community from 3pm earlier today
Non-Outage | J.E.26.08.21796 | C001891708 | Hartley Chin | Clarendon | Completed | Load_352838 | May Pen - 110 | 2026-08-17 18:14 | 2026-08-17 18:15 | 2026-08-17 19:11 | 2026-08-17 19:22 | 2026-08-17 19:22 | 2026-08-17 19:22 | 2026-08-17 19:22 | 2026-08-17 19:22 |  |  | Fair | No | Matter was dealt with last night
Non-Outage | J.E.26.08.21860 | C001891709 | Hartley Chin | Clarendon | Completed | Load_352838 | May Pen - 110 | 2026-08-17 18:14 | 2026-08-17 18:15 | 2026-08-17 19:18 | 2026-08-17 19:19 | 2026-08-17 19:21 | 2026-08-17 19:21 | 2026-08-17 19:22 | 2026-08-17 19:22 |  |  | Fair | No | Matter was dealt with last night
Non-Outage | J.E.26.08.22514 | C001891707 | Hartley Chin | Clarendon | Completed | Load_352838 | May Pen - 110 | 2026-08-17 18:14 | 2026-08-17 18:15 | 2026-08-17 19:22 | 2026-08-17 19:23 | 2026-08-17 19:23 | 2026-08-17 19:23 | 2026-08-17 19:23 | 2026-08-17 19:23 |  |  | Fair | No | Report was corrected last night
Non-Outage | J.E.26.08.26795 | C001891706 | Hartley Chin | Clarendon | Completed | Load_242828 | May Pen - 110 | 2026-08-17 18:14 | 2026-08-17 18:15 | 2026-08-17 19:23 | 2026-08-17 19:24 | 2026-08-17 20:48 | 2026-08-17 20:48 | 2026-08-17 20:51 | 2026-08-17 20:51 |  |  | Fair | No | Customer as internal issues 114v 112v 225v @ pothead. Customer meter socket defective.
Outage | J.E.26.08.26985 | C001891710 | Cliton Henry | St.Ann | Completed | Load_238296 | Upper White River - 210 | 2026-08-17 18:15 | 2026-08-17 21:09 | 2026-08-17 21:34 | 2026-08-17 21:40 | 2026-08-17 22:25 | 2026-08-17 22:34 | 2026-08-17 22:34 | 2026-08-17 22:34 |  |  | Fair | No | A blown 3 amp fuse found for a 25 kva transformer at Daisy Ave at pole 0013692 due to lightning. Supply restored using 1-3 amp fuse
Outage | J.E.26.08.27121 | C001891713 | Javid Vernon | Westmoreland | Completed | Load_270099 | Paradise - 210 | 2026-08-17 18:20 | 2026-08-18 07:23 | 2026-08-18 07:31 | 2026-08-18 07:31 | 2026-08-18 07:31 | 2026-08-18 07:32 | 2026-08-18 07:32 | 2026-08-18 07:32 |  |  | Fair | No | This call belongs to hanover
Outage | J.E.26.08.27141 | C001891716 | Derrick Dawkins | St.James | Completed | Load_258680 | Queens Drive - 810 | 2026-08-17 18:27 | 2026-08-17 18:28 | 2026-08-17 18:34 | 2026-08-17 18:35 | 2026-08-17 19:32 | 2026-08-17 20:06 | 2026-08-17 20:06 | 2026-08-17 20:06 | BrokenWire |  | Fair | No | Tree fall on secondary line break pole tree still on secondary not safe for customer no customer out pole need to change urgent attention need 30 ft pole refer back to maintenance
Outage | J.E.26.08.26426 | C001891717 | Omar King | St.Ann | Completed | Load_267440 | Ocho Rios - 510 | 2026-08-17 18:30 | 2026-08-17 18:34 | 2026-08-17 20:18 | 2026-08-17 20:19 | 2026-08-17 20:18 | 2026-08-17 20:19 | 2026-08-17 20:19 | 2026-08-17 20:19 |  |  | Fair | No | Problem has been resolved..
Outage | J.E.26.08.27073 | C001891719 | Omar King | St.Ann | Completed | Load_256292 | Ocho Rios - 410 | 2026-08-17 18:30 | 2026-08-17 18:34 | 2026-08-17 21:19 | 2026-08-17 21:19 | 2026-08-17 21:55 | 2026-08-17 21:58 | 2026-08-17 21:58 | 2026-08-17 21:58 |  |  | Fair | No | Please refer to field service
Outage | J.E.26.08.27077 | C001891718 | Derrick Dawkins | St.James | Completed | Load_576009 | Bogue - 310 | 2026-08-17 18:30 | 2026-08-17 18:35 | 2026-08-17 21:13 | 2026-08-17 21:13 | 2026-08-17 21:15 | 2026-08-17 21:49 | 2026-08-17 21:49 | 2026-08-17 21:49 |  |  | Fair | No | Found Customer without light customer was reconnected through customer service
Outage | J.E.26.08.27065 | C001891722 | Dean- Smith | Hanover | Completed | Load_250849 | Orange Bay - 310 | 2026-08-17 18:35 | 2026-08-17 18:36 | 2026-08-17 18:49 | 2026-08-17 18:50 | 2026-08-17 19:23 | 2026-08-17 19:23 | 2026-08-17 19:59 | 2026-08-17 19:59 |  |  | Rains | No | Premises closed, unable to patrol line section because of the gate is closed...please have morning team re-visit that location.
Outage | J.E.26.08.25398 | C001891723 | Romeo Brissett | St.James | Completed | Load_241535 | Bogue - 410 | 2026-08-17 18:37 | 2026-08-18 08:05 | 2026-08-18 09:05 | 2026-08-18 09:23 | 2026-08-18 09:59 | 2026-08-18 10:36 | 2026-08-18 11:39 | 2026-08-18 11:39 |  |  | Fair | No | Spliced and retention customer service wire, used 20ft of #6 and 3 clamps V/R 112-114-228.
Outage | J.E.26.08.25906 | C001891727 | Omar King | St.Ann | Completed | Load_242852 | Roaring River - 210 | 2026-08-17 18:38 | 2026-08-17 18:40 | 2026-08-17 20:16 | 2026-08-17 20:17 | 2026-08-17 20:16 | 2026-08-17 20:17 | 2026-08-17 20:17 | 2026-08-17 20:17 |  |  | Fair | No | Problem has been resolved and customer is with supply.
Outage | J.E.26.08.25907 | C001891726 | Omar King | St.Ann | Completed | Load_263588 | Roaring River - 210 | 2026-08-17 18:38 | 2026-08-17 18:40 | 2026-08-17 21:14 | 2026-08-17 21:15 | 2026-08-17 21:15 | 2026-08-17 21:18 | 2026-08-17 21:18 | 2026-08-17 21:18 |  |  | Fair | No | Unable to find customer call several times no answer.
Outage | J.E.26.08.25992 | C001891724 | Omar King | St.Ann | Completed | Load_555975 | Roaring River - 210 | 2026-08-17 18:38 | 2026-08-17 18:40 | 2026-08-17 20:09 | 2026-08-17 20:10 | 2026-08-17 20:10 | 2026-08-17 20:10 | 2026-08-17 20:10 | 2026-08-17 20:10 |  |  | Fair | No | Found 7 amp junction fuse blow cause by bird fuse has been replaced and customer now with supply..
Outage | J.E.26.08.26374 | C001891730 | Omar King | St.Ann | Completed | Load_256000 | Roaring River - 210 | 2026-08-17 18:38 | 2026-08-17 18:40 | 2026-08-17 20:24 | 2026-08-17 20:25 | 2026-08-17 20:54 | 2026-08-17 21:09 | 2026-08-17 21:10 | 2026-08-17 21:10 |  |  | Fair | No | Found 35 feet class 6 wood Pole top burn off pole construction T cause construction to failed. Pole carry secondary and primary conductor pole hardware two dead end insulator and two dead end clamp eye bolt . Please refer to maintenance Two customer affected
Outage | J.E.26.08.26736 | C001891728 | Omar King | St.Ann | Completed | Load_574234 | Roaring River - 410 | 2026-08-17 18:38 | 2026-08-17 18:40 | 2026-08-17 20:14 | 2026-08-17 20:14 | 2026-08-17 20:14 | 2026-08-17 20:16 | 2026-08-17 20:16 | 2026-08-17 20:16 |  |  | Fair | No | Premises is ok and customer is with supply.
Outage | J.E.26.08.25342 | C001891731 | Omar King | St.Ann | Completed | Load_246993 | Roaring River - 210 | 2026-08-17 18:39 | 2026-08-17 18:40 | 2026-08-17 20:08 | 2026-08-17 20:08 | 2026-08-17 20:08 | 2026-08-17 20:08 | 2026-08-17 20:08 | 2026-08-17 20:08 |  |  | Fair | No | Found 7 amp junction fuse blow cause by bird fuse has been replaced and customer now with supply..
Outage | J.E.26.08.27054 | C001891746 | Elvis Trowers | KSAS | Completed | Load_240238 | Duhaney - 410 | 2026-08-17 18:59 | 2026-08-17 19:00 | 2026-08-17 19:53 | 2026-08-17 19:54 | 2026-08-17 20:41 | 2026-08-17 20:45 | 2026-08-17 20:46 | 2026-08-17 20:46 |  |  | Fair | No | Found okay upon arrival. Customer circuit breaker tripped.
Non-Outage | J.E.26.08.27156 | C001891748 | Clyde Brown | Clarendon | Completed | Load_265688 | Monymusk - 210 | 2026-08-17 19:00 | 2026-08-17 19:01 | 2026-08-17 19:33 | 2026-08-17 19:34 | 2026-08-17 21:17 | 2026-08-17 21:17 | 2026-08-17 21:28 | 2026-08-17 21:28 |  |  | Fair | No | Dislodge phase for 3 wire service connection remade with 1- clamp,voltage left 111/108 and 218V.
Outage | J.E.26.08.27074 | C001891747 | Elvis Trowers | KSAS | Completed | Load_249774 | Duhaney - 410 | 2026-08-17 19:00 | 2026-08-17 19:00 | 2026-08-17 20:46 | 2026-08-17 20:46 | 2026-08-17 21:18 | 2026-08-17 21:20 | 2026-08-17 21:20 | 2026-08-17 21:20 |  |  | Fair | No | Reconnect customer meter#3061318 by J.P.S Escalation.
Outage | J.E.26.08.27215 | C001891790 | Neville Spencer | Clarendon | Completed | Load_266435 | Parnassus - 310 | 2026-08-17 19:43 | 2026-08-18 07:27 | 2026-08-18 09:57 | 2026-08-18 09:57 | 2026-08-18 10:19 | 2026-08-18 10:19 | 2026-08-18 10:20 | 2026-08-18 10:20 |  |  | Fair | No | Unable to locate customer.
Outage | J.E.26.08.27212 | C001891800 | Andre Smith | KSAS | Completed | Load_245842 | Rockfort - 210 | 2026-08-17 19:54 | 2026-08-17 19:55 | 2026-08-17 21:21 | 2026-08-17 21:21 | 2026-08-17 21:59 | 2026-08-17 22:36 | 2026-08-17 22:36 | 2026-08-17 22:36 | BrokenWire |  | Fair | No | Replace burnt transformer droplead using 4ft 2/0 copper supply restored
Non-Outage | J.E.26.08.27090 | C001891821 | Stephen Taylor | St.Thomas | Completed | Load_261247 | Port Antonio - 310 | 2026-08-17 20:10 | 2026-08-17 20:12 | 2026-08-17 22:11 | 2026-08-17 22:11 | 2026-08-17 22:11 | 2026-08-17 22:11 | 2026-08-17 22:12 | 2026-08-17 22:12 |  |  | Fair | No | See junction out o number on pole patrol see nothing about close up back junction with a 7 amp fuse safely customer is now okay
Non-Outage | J.E.26.08.26972 | C001891822 | Stephen Taylor | St.Thomas | Completed | Load_239089 | Good Year - 110 | 2026-08-17 20:11 | 2026-08-17 20:12 | 2026-08-18 18:40 | 2026-08-18 18:41 | 2026-08-18 18:40 | 2026-08-18 18:40 | 2026-08-18 18:42 | 2026-08-18 18:42 |  |  | Fair | No | Call to customer and customer
Outage | J.E.26.08.27083 | C001891831 | Cliton Henry | St.Mary | Completed | Load_246610 | Oracabessa - 110 | 2026-08-17 20:13 | 2026-08-17 20:16 | 2026-08-17 20:22 | 2026-08-17 20:22 | 2026-08-17 20:57 | 2026-08-17 21:39 | 2026-08-17 21:39 | 2026-08-17 21:39 |  |  | Fair | No | A single phase condition found.the pothead voltages were 115-116/232 volts.. kindly refer to Field Service Department to unlock meter band so that the customer electrician can check inside the meter socker
Outage | J.E.26.08.27136 | C001891832 | Cliton Henry | St.Mary | Completed | Load_251918 | Oracabessa - 210 | 2026-08-17 20:13 | 2026-08-17 20:16 | 2026-08-17 20:57 | 2026-08-17 22:35 | 2026-08-17 22:59 | 2026-08-17 22:59 | 2026-08-18 15:55 | 2026-08-18 15:55 |  |  | Fair | No | The customer stated that the supply was restored.
Outage | J.E.26.08.27273 | C001891833 | Swon Miller | St.James | Completed | Load_263560 | Bogue - 610 | 2026-08-17 20:14 | 2026-08-17 20:14 | 2026-08-17 20:48 | 2026-08-17 20:49 | 2026-08-17 21:44 | 2026-08-17 22:42 | 2026-08-17 22:47 | 2026-08-17 22:47 |  |  | Fair | No | Found 30 amp junction fuse blown cause by lightning replace 30 amp junction fuse no pole number available
Outage | J.E.26.08.27271 | C001891836 | Neville Spencer | Clarendon | Completed | Load_260333 | Parnassus - 310 | 2026-08-17 20:25 | 2026-08-18 07:27 | 2026-08-18 10:25 | 2026-08-18 10:25 | 2026-08-18 10:55 | 2026-08-18 10:55 | 2026-08-18 10:59 | 2026-08-18 10:59 |  |  | Fair | No | Reconnect 3 wire service at pole voltage reading 113=113 227 supply restored.
Outage | J.E.26.08.27283 | C001891838 | Michael Paterson | Westmoreland | Completed | Load_250869 | Paradise - 310 | 2026-08-17 20:40 | 2026-08-17 20:41 | 2026-08-17 20:46 | 2026-08-17 20:46 | 2026-08-17 21:21 | 2026-08-17 22:04 | 2026-08-17 22:05 | 2026-08-17 22:05 |  |  | Fair | No | Found 25kva xfmr fuse blown, cut and remove shrubs from xfmr, replace 2amps fuse, supply restored, voltage readings, 119v, 119v, 238v., several illegal connections in area, please refer to the losses team.
Outage | J.E.26.08.27308 | C001891844 | Hartley Chin | Clarendon | Completed | Load_242939 | May Pen - 210 | 2026-08-17 21:08 | 2026-08-17 21:10 | 2026-08-17 21:32 | 2026-08-17 21:33 | 2026-08-17 23:20 | 2026-08-17 23:20 | 2026-08-17 23:24 | 2026-08-17 23:24 | BrokenPole,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Ref to Maintenance: broken 30ft with open secondary pole bottom half leans on customer fence while the top half is held by service wire and third party. Needs urgent urgent! Attention. Can be dealt with in the morning. Some customers are single phasing
Outage | J.E.26.08.27239 | C001891850 | Roxroy Needham | St.Ann | Completed | Load_238296 | Upper White River - 210 | 2026-08-17 22:47 | 2026-08-17 22:59 | 2026-08-18 00:38 | 2026-08-18 00:39 | 2026-08-18 01:26 | 2026-08-18 01:29 | 2026-08-18 01:30 | 2026-08-18 01:30 |  |  | Fair | No | Premises found ok customer say that JPS team come before and the light is ok
Non-Outage | J.E.26.08.27262 | C001891853 | Roxroy Needham | St.Ann | Completed | Load_247748 | Cardiff Hall - 310 | 2026-08-17 22:58 | 2026-08-17 22:59 | 2026-08-18 05:04 | 2026-08-18 05:04 | 2026-08-18 06:33 | 2026-08-18 06:30 | 2026-08-18 06:35 | 2026-08-18 06:35 | BrokenWire |  | Fair | No | Remake service wire used 2 pg clamp voltage left at meter 113-112-219
Non-Outage | J.E.26.08.27340 | C001891852 | Roxroy Needham | St.Ann | Completed | Load_252506 | Ocho Rios - 310 | 2026-08-17 22:58 | 2026-08-17 22:59 | 2026-08-18 01:30 | 2026-08-18 01:30 | 2026-08-18 05:02 | 2026-08-18 03:24 | 2026-08-18 05:03 | 2026-08-18 05:03 | Fire |  | Fair | No | Premises not found not getting customer on phone
Non-Outage | J.E.26.08.27219 | C001891857 | Rusean Allen | KSAS | Completed | Load_256007 | Duhaney - 310 | 2026-08-17 23:13 | 2026-08-17 23:14 | 2026-08-18 01:19 | 2026-08-18 01:20 | 2026-08-18 01:53 | 2026-08-18 01:53 | 2026-08-18 01:54 | 2026-08-18 01:54 | BrokenWire |  | Fair | No | Broken wire is of telecommunications company
Outage | J.E.26.08.27208 | C001891856 | Rusean Allen | KSAS | Completed | Load_258681 | Three Miles - 410 | 2026-08-17 23:13 | 2026-08-17 23:14 | 2026-08-18 01:10 | 2026-08-18 03:44 | 2026-08-18 03:57 | 2026-08-18 03:57 | 2026-08-18 03:57 | 2026-08-18 03:57 |  |  | Fair | No | Customer reported streetlight not working
Outage | J.E.26.08.27380 | C001891855 | Rusean Allen | KSAS | Completed | Load_267551 | Cane River - 410 | 2026-08-17 23:13 | 2026-08-17 23:14 | 2026-08-18 02:12 | 2026-08-18 02:12 | 2026-08-18 03:33 | 2026-08-18 03:41 | 2026-08-18 03:41 | 2026-08-18 03:41 | Fire |  | Fair | No | Broken transformer drop lead wire found, wire was reconnected.
Non-Outage | J.E.26.08.26223 | C001891859 | Horace Malcolm | St.James | Completed | Load_267376 | Bogue - 310 | 2026-08-17 23:14 | 2026-08-17 23:15 | 2026-08-18 02:27 | 2026-08-18 02:27 | 2026-08-18 03:13 | 2026-08-18 03:31 | 2026-08-18 03:31 | 2026-08-18 03:31 | Fire |  | Fair | No | Check and found no fire on from direction
Non-Outage | J.E.26.08.26291 | C001891858 | Rusean Allen | KSAN | Completed | Load_254380 | Constant Spring - 410 | 2026-08-17 23:14 | 2026-08-17 23:14 | 2026-08-18 01:54 | 2026-08-18 01:54 | 2026-08-18 02:08 | 2026-08-18 02:11 | 2026-08-18 02:11 | 2026-08-18 02:11 | BrokenPole |  | Fair | No | No broken pole seen at premises.
Outage | J.E.26.08.27397 | C001891861 | Horace Malcolm | St.James | Completed | Load_258825 | Bogue - 310 | 2026-08-17 23:33 | 2026-08-17 23:36 | 2026-08-17 23:47 | 2026-08-17 23:47 | 2026-08-18 00:32 | 2026-08-18 01:27 | 2026-08-18 01:27 | 2026-08-18 01:27 | BrokenWire |  | Fair | No | Clean corrosion and remake joints at customer pothead and pole used 3clamps voltage 111-112-223
Outage | J.E.26.08.27409 | C001891863 | Delano Gayle | Portmore | Completed | Load_268319 | Naggo Head - 610 | 2026-08-18 00:02 | 2026-08-18 00:04 | 2026-08-18 04:06 | 2026-08-18 04:07 | 2026-08-18 04:35 | 2026-08-18 04:45 | 2026-08-18 04:45 | 2026-08-18 04:45 | BrokenWire |  | Fair | No | Broken phase at pole repair use 1 clamp voltage readings 113-114-227
Outage | J.E.26.08.27427 | C001891870 | Rusean Allen | KSAS | Completed | Load_1003929 | Rockfort - 410 | 2026-08-18 02:12 | 2026-08-18 02:14 | 2026-08-18 03:41 | 2026-08-18 03:41 | 2026-08-18 03:41 | 2026-08-18 03:42 | 2026-08-18 03:43 | 2026-08-18 03:43 |  |  | Fair | No | 1x 3amp fuse found 1x 3amp fuse replaced.
Outage | J.E.26.08.27447 | C001891875 | Delano Gayle | Portmore | Completed | Load_267254 | Naggo Head - 610 | 2026-08-18 03:34 | 2026-08-18 03:34 | 2026-08-18 04:03 | 2026-08-18 04:04 | 2026-08-18 04:04 | 2026-08-18 04:05 | 2026-08-18 04:06 | 2026-08-18 04:06 |  |  | Fair | No | Premises found okay related to call where 50kva transformer fuse was opened to carry out repairs to broken conductor
Outage | J.E.26.08.27460 | C001891881 | Shawn Medley | St.James | Completed | Load_245483 | Rose Hall - 110 | 2026-08-18 07:10 | 2026-08-18 08:08 | 2026-08-18 10:02 | 2026-08-18 10:56 | 2026-08-18 10:56 | 2026-08-18 11:04 | 2026-08-18 11:11 | 2026-08-18 11:11 |  |  | Fair | No | Found 50kva transformer tripped at pole without number patrol and found nothing so I reset transformer an it held. Customer now restored.
Outage | J.E.26.08.26703 | C001891883 | Horace Malcolm | St.James | Completed | Load_1002042 | Queens Drive - 710 | 2026-08-18 07:16 | 2026-08-18 15:32 | 2026-08-18 16:21 | 2026-08-18 16:22 | 2026-08-18 16:32 | 2026-08-18 16:35 | 2026-08-18 16:35 | 2026-08-18 16:35 |  |  | Fair | No | Unable to locate customer from multiple phone calls unable to locate premises no direction given
Non-Outage | J.E.26.08.27310 | C001891885 | Javid Vernon |  | Completed |  |  | 2026-08-18 07:20 | 2026-08-18 07:21 | 2026-08-18 07:37 | 2026-08-18 07:38 | 2026-08-18 07:37 | 2026-08-18 07:38 | 2026-08-18 07:38 | 2026-08-18 07:38 |  |  | Fair | No | Customer stated power was restored
Outage | J.E.26.08.27459 | C001891884 | Javid Vernon | Westmoreland | Completed | Load_266095 | Paradise - 210 | 2026-08-18 07:20 | 2026-08-18 07:21 | 2026-08-18 07:38 | 2026-08-18 07:39 | 2026-08-18 07:38 | 2026-08-18 07:39 | 2026-08-18 07:39 | 2026-08-18 07:39 |  |  | Fair | No | Customer stated that the power was restored
Outage | J.E.26.08.26401 | C001891887 | Milton Charlton | KSAN | Completed | Load_254310 | Hope - 410 | 2026-08-18 07:24 | 2026-08-18 07:26 | 2026-08-18 08:51 | 2026-08-18 08:52 | 2026-08-18 10:21 | 2026-08-18 09:55 | 2026-08-18 10:23 | 2026-08-18 10:23 | TreeContact |  | Fair | No | Found okay upon arrival. No entangled wires seen on site .
Outage | J.E.26.08.27176 | C001891888 | Elvis Trowers | KSAN | Completed | Load_255927 | Constant Spring - 210 | 2026-08-18 07:26 | 2026-08-18 07:27 | 2026-08-18 08:14 | 2026-08-18 08:44 | 2026-08-18 09:26 | 2026-08-18 09:10 | 2026-08-18 09:30 | 2026-08-18 09:30 |  |  | Fair | No | Found okay upon arrival. Premises has supply States the work men’s.
Outage | J.E.26.08.27272 | C001891889 | Christopher Edwards | KSAN | Completed | Load_269403 | Constant Spring - 410 | 2026-08-18 07:26 | 2026-08-18 07:27 | 2026-08-18 08:14 | 2026-08-18 08:15 | 2026-08-18 08:54 | 2026-08-18 09:34 | 2026-08-18 09:34 | 2026-08-18 09:34 |  |  | Fair | No | Remake burnt neutral joint Using (1) one bolt clamps Voltage:114,115,230v
Non-Outage | J.E.26.08.21422 | C001891892 | Neville Spencer | Clarendon | Completed | Load_260333 | Parnassus - 310 | 2026-08-18 07:29 | 2026-08-18 07:50 | 2026-08-18 11:04 | 2026-08-18 11:05 | 2026-08-18 11:04 | 2026-08-18 11:05 | 2026-08-18 11:12 | 2026-08-18 11:12 |  |  | Fair | No | Check and found supply ok voltage reading found in meter socket 113 113 227.
Non-Outage | J.E.26.08.22419 | C001891891 | Neville Spencer | Clarendon | Completed | Load_569758 | Parnassus - 210 | 2026-08-18 07:29 | 2026-08-18 07:50 | 2026-08-18 16:50 | 2026-08-18 16:50 | 2026-08-18 17:43 | 2026-08-18 17:43 | 2026-08-18 18:32 | 2026-08-18 18:32 | Fire |  | Fair | No | Open 25 kva xmfr at pole # 0112901 retention 2 spans of secondary phase and neutral conductor used 2, preform supply restored.
Non-Outage | J.E.26.08.25947 | C001891890 | Neville Spencer | Clarendon | Completed | Load_261010 | Parnassus - 310 | 2026-08-18 07:29 | 2026-08-18 07:50 | 2026-08-18 08:00 | 2026-08-18 08:00 | 2026-08-18 09:34 | 2026-08-18 09:34 | 2026-08-18 09:56 | 2026-08-18 09:56 | LowHangingWires |  | Fair | No | Remade slack phase joint at secondary on 2, wire service used 1 clamp voltage reading 116.
Non-Outage | J.E.26.08.20884 | C001891893 | Neville Spencer | Clarendon | Completed | Load_260333 | Parnassus - 310 | 2026-08-18 07:30 | 2026-08-18 07:50 | 2026-08-18 11:12 | 2026-08-18 11:13 | 2026-08-18 11:13 | 2026-08-18 11:13 | 2026-08-18 11:14 | 2026-08-18 11:14 |  |  | Fair | No | Check and found supply ok 113 113 227
Outage | J.E.26.08.26929 | C001891897 | Evan Spaulding | St.Mary | Completed | Load_252067 | Highgate -110 | 2026-08-18 07:34 | 2026-08-18 07:36 | 2026-08-18 08:57 | 2026-08-18 08:57 | 2026-08-18 09:31 | 2026-08-18 10:17 | 2026-08-18 10:19 | 2026-08-18 10:19 | BrokenWire |  | SevereWind | No | Remove fallen tree limb from conductors splice and retention two spans secondary conductors using 90ft #2 AAAC conductor,1-#2 splicing sleeve and 2-1 bolt clamps.
Outage | J.E.26.08.27030 | C001891898 | Evan Spaulding | St.Mary | Completed | Load_244740 | Highgate -110 | 2026-08-18 07:34 | 2026-08-18 07:36 | 2026-08-18 07:57 | 2026-08-18 07:57 | 2026-08-18 08:30 | 2026-08-18 08:52 | 2026-08-18 08:54 | 2026-08-18 08:54 |  |  | Fair | No | Remove fallen bamboo from secondary conductor and replace 1-3 amps Transformer fuse at pole number 0170791
Outage | J.E.26.08.27274 | C001891899 | Evan Spaulding | St.Mary | Completed | Load_244740 | Highgate -110 | 2026-08-18 07:34 | 2026-08-18 07:36 | 2026-08-18 08:55 | 2026-08-18 08:56 | 2026-08-18 08:55 | 2026-08-18 08:55 | 2026-08-18 08:57 | 2026-08-18 08:57 |  |  | Fair | No | Remove bamboo from secondary conductor and replace 1-3 amps Transformer fuse at pole number 0170791.
Non-Outage | J.E.26.08.21854 | C001891907 | Nickolas Rodriques | Portmore | Completed | Load_251619 | Naggo Head - 610 | 2026-08-18 07:35 | 2026-08-18 07:36 | 2026-08-18 14:07 | 2026-08-18 14:12 | 2026-08-18 14:40 | 2026-08-18 14:43 | 2026-08-18 14:46 | 2026-08-18 14:46 |  |  | Fair | No | Checked and found customer single phasing (114) caused by broken service wire at pole. Repaired by connecting wire using one clamp, current reading is (114-115-229). Customer confirmed that all is well now.
Outage | J.E.26.08.24111 | C001891905 | Nickolas Rodriques | Portmore | Completed | Load_259768 | Naggo Head - 510 | 2026-08-18 07:35 | 2026-08-18 07:36 | 2026-08-18 08:57 | 2026-08-18 09:09 | 2026-08-18 09:49 | 2026-08-18 10:22 | 2026-08-18 10:29 | 2026-08-18 10:29 |  |  | Fair | No | Checked and found customer single phasing caused by broken service wire. Repaired by splice and retention wire using two service sleeves, current reading is (112-114-226). Customers confirmed that all is well now.
Outage | J.E.26.08.25348 | C001891900 | Nickolas Rodriques | Portmore | Completed | Load_267254 | Naggo Head - 610 | 2026-08-18 07:35 | 2026-08-18 07:36 | 2026-08-18 13:02 | 2026-08-18 13:04 | 2026-08-18 13:44 | 2026-08-18 14:00 | 2026-08-18 14:07 | 2026-08-18 14:07 | BrokenWire |  | Fair | No | Unable to communicate with the customer. However, the area was patrolled and no broken wire was found.
Outage | J.E.26.08.27070 | C001891903 | Nickolas Rodriques | Portmore | Completed | Load_257194 | Naggo Head - 510 | 2026-08-18 07:35 | 2026-08-18 07:36 | 2026-08-18 07:53 | 2026-08-18 08:03 | 2026-08-18 08:31 | 2026-08-18 08:50 | 2026-08-18 08:55 | 2026-08-18 08:55 |  |  | Fair | No | Unable to communicate with the customer after several attempts.
Outage | J.E.26.08.27188 | C001891902 | Nickolas Rodriques | Portmore | Completed | Load_245024 | Naggo Head - 510 | 2026-08-18 07:35 | 2026-08-18 07:36 | 2026-08-18 10:29 | 2026-08-18 10:34 | 2026-08-18 11:06 | 2026-08-18 11:58 | 2026-08-18 12:07 | 2026-08-18 12:07 |  |  | Fair | No | Customer stated that she is having unstable voltage, reading found (114). All necessary checks were done and it was found that the customer 2-wire meter is defective and needs to be replaced. Refer to metering department.
Non-Outage | J.E.26.08.26194 | C001891909 | Richard Grant |  | Completed |  |  | 2026-08-18 07:39 | 2026-08-18 07:42 | 2026-08-18 14:04 | 2026-08-18 14:05 | 2026-08-18 14:55 | 2026-08-18 14:55 | 2026-08-18 14:56 | 2026-08-18 14:56 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.26933 | C001891910 | Wayne Dillion | Manchester | Completed | Load_238781 | Spur Tree - 210 | 2026-08-18 07:39 | 2026-08-18 07:40 | 2026-08-18 08:24 | 2026-08-18 08:25 | 2026-08-18 08:50 | 2026-08-18 09:10 | 2026-08-18 09:14 | 2026-08-18 09:14 |  |  | Fair | No | Supply check and found customer meter burnt up. A field service crew was onsite one replaced the meter. Meter# changed from 2854486 to 3025417 and supply was restored okay.
Outage | J.E.26.08.27111 | C001891912 | Wayne Dillion | Manchester | Completed | Load_292288 | Spur Tree - 210 | 2026-08-18 07:39 | 2026-08-18 07:40 | 2026-08-18 09:18 | 2026-08-18 09:19 | 2026-08-18 09:18 | 2026-08-18 09:21 | 2026-08-18 09:21 | 2026-08-18 09:21 |  |  | Fair | No | Customer said supply was restored.
Outage | J.E.26.08.27243 | C001891911 | Richard Grant | St.Catherine | Completed | Load_260121 | New Michelton - 210 | 2026-08-18 07:39 | 2026-08-18 07:42 | 2026-08-18 13:44 | 2026-08-18 13:44 | 2026-08-18 14:04 | 2026-08-18 14:04 | 2026-08-18 14:04 | 2026-08-18 14:04 |  |  | Fair | No | Premises found okay
Non-Outage | J.E.26.08.27464 | C001891913 | Shawn Medley | St.James | Completed | Load_574885 | Rose Hall - 210 | 2026-08-18 07:40 | 2026-08-18 08:53 | 2026-08-18 09:20 | 2026-08-18 09:20 | 2026-08-18 09:20 | 2026-08-18 09:55 | 2026-08-18 09:56 | 2026-08-18 09:56 |  |  | Fair | No | Isolated threev50amps junction for at pole without number
Outage | J.E.26.08.27240 | C001891914 | Tyrese Williams | St.Ann | Completed | Load_241902 | Cardiff Hall - 210 | 2026-08-18 07:40 | 2026-08-18 07:42 | 2026-08-18 09:02 | 2026-08-18 11:12 | 2026-08-18 11:51 | 2026-08-18 11:54 | 2026-08-18 11:55 | 2026-08-18 11:55 |  |  | Fair | No | Premises not found followed the directions and not getting customer on phone
Outage | J.E.26.08.27365 | C001891915 | Tyrese Williams | St.Ann | Completed | Load_249820 | Cardiff Hall - 310 | 2026-08-18 07:40 | 2026-08-18 07:42 | 2026-08-18 09:02 | 2026-08-18 09:11 | 2026-08-18 10:17 | 2026-08-18 11:12 | 2026-08-18 11:12 | 2026-08-18 11:12 |  |  | Fair | No | Remade secondary neutral joint and remove illegal connections voltage check 117/119/236
Outage | J.E.26.08.27368 | C001891916 | Tyrese Williams | St.Ann | Completed | Load_269163 | Cardiff Hall - 210 | 2026-08-18 07:40 | 2026-08-18 07:42 | 2026-08-18 09:02 | 2026-08-18 11:56 | 2026-08-18 12:31 | 2026-08-18 12:47 | 2026-08-18 12:52 | 2026-08-18 12:52 |  |  | Fair | No | Not getting customer on phone
Non-Outage | J.E.26.08.23615 | C001891920 | Richard Grant | St.Catherine | Completed | Load_252376 | New Michelton - 310 | 2026-08-18 07:42 | 2026-08-18 07:43 | 2026-08-18 12:10 | 2026-08-18 12:11 | 2026-08-18 12:10 | 2026-08-18 13:08 | 2026-08-18 13:08 | 2026-08-18 13:08 |  |  | Fair | No | Defective service wire seen at premises. Approximately 80ft #6 triplex wire, 3 penunion and 3 onebolt clamps used to correct fault. Supply restored and 117 117 234 voltages left at premises. Premises left okay.
Non-Outage | J.E.26.08.26065 | C001891922 | Richard Grant | St.Catherine | Completed | Load_245363 | New Michelton - 310 | 2026-08-18 07:42 | 2026-08-18 07:43 | 2026-08-18 09:28 | 2026-08-18 09:29 | 2026-08-18 10:56 | 2026-08-18 12:08 | 2026-08-18 12:10 | 2026-08-18 12:10 |  |  | Fair | No | 3 wire service found with corroded phases at pole , use 2 one bolt clamps to correct, customer left with supply
Non-Outage | J.E.26.08.26821 | C001891921 | Richard Grant | St.Catherine | Completed | Load_253001 | New Michelton - 310 | 2026-08-18 07:42 | 2026-08-18 07:43 | 2026-08-18 07:58 | 2026-08-18 07:59 | 2026-08-18 09:27 | 2026-08-18 09:28 | 2026-08-18 09:28 | 2026-08-18 09:28 |  |  | Fair | No | Premises found okay.
Non-Outage | J.E.26.08.26993 | C001891918 | Dwain Samuels | Westmoreland | Completed | Load_569997 | Paradise - 210 | 2026-08-18 07:42 | 2026-08-18 07:43 | 2026-08-18 08:03 | 2026-08-18 10:11 | 2026-08-18 10:11 | 2026-08-18 10:11 | 2026-08-18 10:12 | 2026-08-18 10:12 |  |  | Fair | No | Called customer said supply was restored
Non-Outage | J.E.26.08.27051 | C001891919 | Dwain Samuels | Westmoreland | Completed | Load_292641 | Paradise - 210 | 2026-08-18 07:42 | 2026-08-18 07:43 | 2026-08-18 08:03 | 2026-08-18 09:10 | 2026-08-18 09:57 | 2026-08-18 10:02 | 2026-08-18 10:04 | 2026-08-18 10:04 |  |  | Fair | No | Meter found burnt at premises needs changing urgently
Non-Outage | J.E.26.08.27297 | C001891923 | Javid Vernon |  | Completed |  |  | 2026-08-18 07:42 | 2026-08-18 07:43 | 2026-08-18 07:47 | 2026-08-18 07:49 | 2026-08-18 08:05 | 2026-08-18 08:06 | 2026-08-18 08:09 | 2026-08-18 08:09 | BrokenPole |  | Fair | No | There’s no broken pole, customer is reporting that there’s no street light on the pole info premises since the hurricane
Outage | J.E.26.08.26728 | C001891926 | Rusean Allen | KSAS | Completed | Load_1003959 | Cane River - 310 | 2026-08-18 07:44 | 2026-08-18 07:46 | 2026-08-18 08:34 | 2026-08-18 08:35 | 2026-08-18 08:34 | 2026-08-18 08:36 | 2026-08-18 08:36 | 2026-08-18 08:36 | BrokenPole |  | Fair | No | Maintenance department is already aware of broken pole at premises.
Non-Outage | J.E.26.08.27098 | C001891942 | Richard Samuda |  | Completed |  |  | 2026-08-18 07:45 | 2026-08-18 07:47 | 2026-08-18 10:30 | 2026-08-18 10:38 | 2026-08-18 10:46 | 2026-08-18 00:02 | 2026-08-18 12:02 | 2026-08-18 12:02 |  |  | Fair | No | Replace customer service wire that damaged using 40 ft of number 6 service wire and two 1bolt clamps Voltage 116
Outage | J.E.26.08.25971 | C001891934 | Moses Elliston | St.Catherine | Completed | Load_250453 | New Michelton - 310 | 2026-08-18 07:45 | 2026-08-18 07:46 | 2026-08-19 14:21 | 2026-08-19 14:22 | 2026-08-19 14:21 | 2026-08-19 10:50 | 2026-08-19 14:22 | 2026-08-19 14:22 |  |  | Fair | No | Supply ok at premises
Outage | J.E.26.08.26288 | C001891930 | Edward Royal | KSAS | Completed | Load_295278 | Three Miles - 310 | 2026-08-18 07:45 | 2026-08-18 07:46 | 2026-08-18 11:16 | 2026-08-18 11:17 | 2026-08-18 11:16 | 2026-08-18 11:18 | 2026-08-18 11:35 | 2026-08-18 11:35 | Fire |  | Fair | No | Customer have internal problems customer have faulty wiring advise customer to get a electrician to fix the problem 240 120 120 v
Outage | J.E.26.08.26577 | C001891928 | Fitzroy Turner | KSAS | Completed | Load_240083 | Hunts Bay - 510 | 2026-08-18 07:45 | 2026-08-18 07:46 | 2026-08-18 11:37 | 2026-08-18 11:37 | 2026-08-18 13:22 | 2026-08-18 13:25 | 2026-08-18 13:28 | 2026-08-18 13:28 |  |  | Fair | No | Found tree secondary burnt down cause by fire at market use 160ft off #2 triplex and 6one bolt clamps and two preform supply restored to the areas
Outage | J.E.26.08.26818 | C001891943 | Richard Samuda | Manchester | Completed | Load_301405 | Porus - 310 | 2026-08-18 07:45 | 2026-08-18 07:47 | 2026-08-18 10:27 | 2026-08-18 10:27 | 2026-08-18 10:28 | 2026-08-18 10:30 | 2026-08-18 10:30 | 2026-08-18 10:30 |  |  | Fair | No | Customer said power was restored
Outage | J.E.26.08.27055 | C001891941 | Richard Samuda | Manchester | Completed | Load_269775 | Porus - 310 | 2026-08-18 07:45 | 2026-08-18 07:47 | 2026-08-18 10:24 | 2026-08-18 10:25 | 2026-08-18 10:25 | 2026-08-18 10:26 | 2026-08-18 10:26 | 2026-08-18 10:26 |  |  | Fair | No | Call to phone no answer premises not located
Outage | J.E.26.08.27370 | C001891938 | Barnett Brown | Manchester | Completed | Load_248463 | Kendal - 210 | 2026-08-18 07:45 | 2026-08-18 07:47 | 2026-08-18 13:15 | 2026-08-18 13:15 | 2026-08-18 13:15 | 2026-08-18 13:15 | 2026-08-18 13:16 | 2026-08-18 13:16 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.27381 | C001891939 | Lancelot Brown | Hanover | Completed | Load_245213 | Orange Bay - 310 | 2026-08-18 07:45 | 2026-08-18 07:46 | 2026-08-18 07:49 | 2026-08-18 09:47 | 2026-08-18 09:46 | 2026-08-18 09:47 | 2026-08-18 09:47 | 2026-08-18 09:47 | TreeContact |  | Fair | No | This call related to 2amps fuse at 25kva supply restore caused by vegetation
Outage | J.E.26.08.27394 | C001891936 | Rusean Allen | KSAS | Completed | Load_250421 | Cane River - 410 | 2026-08-18 07:45 | 2026-08-18 07:47 | 2026-08-18 08:39 | 2026-08-18 11:36 | 2026-08-18 11:43 | 2026-08-18 11:48 | 2026-08-18 11:48 | 2026-08-18 11:48 |  |  | Fair | No | Corroded wire found at pothead, wire was disconnected and reconnected with one bolt clamp.
Outage | J.E.26.08.27438 | C001891933 | Lancelot Brown | Hanover | Completed | Load_245213 | Orange Bay - 310 | 2026-08-18 07:45 | 2026-08-18 07:48 | 2026-08-18 07:55 | 2026-08-18 08:51 | 2026-08-18 09:36 | 2026-08-18 09:46 | 2026-08-18 09:46 | 2026-08-18 09:46 |  |  | Fair | No | Found 25kva fuse blown cause by vegetation cut and remove vegetation from 25kva replace 1-2amps no pole number supply restore
Outage | J.E.26.08.27457 | C001891935 | Barnett Brown | Manchester | Completed | Load_248463 | Kendal - 210 | 2026-08-18 07:45 | 2026-08-18 07:47 | 2026-08-18 13:06 | 2026-08-18 13:07 | 2026-08-18 13:13 | 2026-08-18 13:13 | 2026-08-18 13:15 | 2026-08-18 13:15 |  |  | Fair | No | Premises found ok, related to previous call
Outage | J.E.26.08.27470 | C001891932 | Barnett Brown | Manchester | Completed | Load_238794 | Kendal - 210 | 2026-08-18 07:45 | 2026-08-18 07:47 | 2026-08-18 10:37 | 2026-08-18 10:37 | 2026-08-18 10:37 | 2026-08-18 12:45 | 2026-08-18 12:50 | 2026-08-18 12:50 |  |  | Fair | No | Splice and retention one span primary phase, replace blown 50 amp junction fuse
Outage | J.E.26.08.27471 | C001891929 | Barnett Brown | Manchester | Completed | Load_303044 | Kendal - 210 | 2026-08-18 07:45 | 2026-08-18 07:47 | 2026-08-18 12:53 | 2026-08-18 12:54 | 2026-08-18 13:04 | 2026-08-18 13:04 | 2026-08-18 13:06 | 2026-08-18 13:06 |  |  | Fair | No | Related to previous Chudleigh call
Outage | J.E.26.08.27477 | C001891944 | Richard Samuda | Manchester | Completed | Load_295434 | Spur Tree - 310 | 2026-08-18 07:45 | 2026-08-18 07:47 | 2026-08-18 07:59 | 2026-08-18 08:13 | 2026-08-18 09:17 | 2026-08-18 09:41 | 2026-08-18 09:41 | 2026-08-18 09:41 |  |  | Fair | No | Found 25 kva transformer fuse holder burnt out patrol line found nothing replace fuse holder customer back to normal
Outage | J.E.26.08.27478 | C001891931 | Lancelot Brown | Hanover | Completed | Load_292318 | Orange Bay - 310 | 2026-08-18 07:45 | 2026-08-18 07:48 | 2026-08-18 07:55 | 2026-08-18 07:57 | 2026-08-18 07:56 | 2026-08-18 08:33 | 2026-08-18 08:38 | 2026-08-18 08:38 |  |  | SevereWind | No | Found junction fuse blown patroll found vegetation contact with primary line removed vegetation from primary line replace 1-10amps junction fuse pole number not complete supply restore
Non-Outage | J.E.26.08.27002 | C001891947 | Radcliffe Coleman |  | Completed |  |  | 2026-08-18 07:48 | 2026-08-18 07:49 | 2026-08-18 08:30 | 2026-08-18 08:40 | 2026-08-18 09:43 | 2026-08-18 11:52 | 2026-08-18 11:52 | 2026-08-18 11:52 |  |  | Fair | No | Customer service wire was found burnt at the pole ( four customer were affected). This was a result of illegal connections, repairs were done with the aid of two one bolt clamp and approximately 3ft of #6 service wire.
Outage | J.E.26.08.27217 | C001891946 | Radcliffe Coleman | St.Catherine | Completed | Load_250118 | Tredegar - 510 | 2026-08-18 07:48 | 2026-08-18 07:49 | 2026-08-18 11:55 | 2026-08-18 11:56 | 2026-08-18 12:22 | 2026-08-18 12:25 | 2026-08-18 12:26 | 2026-08-18 12:26 |  |  | Fair | No | Customer meter was found disconnected, reconnection was done with the help of CSR. Premises left okay.
Non-Outage | J.E.26.08.25361 | C001891948 | Collin Robinson |  | Completed |  |  | 2026-08-18 07:51 | 2026-08-18 07:54 | 2026-08-18 09:21 | 2026-08-18 09:21 | 2026-08-18 10:34 | 2026-08-18 10:50 | 2026-08-18 10:50 | 2026-08-18 10:50 | LeaningPole |  | Fair | No | Remove falling tree from primary conductor and replace 8 amps junction fuse at pole 013448
Non-Outage | J.E.26.08.25092 | C001891953 | Collin Robinson | Portland | Completed | Load_247232 | Port Antonio - 310 | 2026-08-18 07:52 | 2026-08-18 07:54 | 2026-08-18 10:50 | 2026-08-18 10:51 | 2026-08-18 11:42 | 2026-08-18 11:45 | 2026-08-18 11:45 | 2026-08-18 11:45 |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.08.24898 | C001891959 | Collin Robinson |  | Completed |  |  | 2026-08-18 07:53 | 2026-08-18 07:54 | 2026-08-18 12:37 | 2026-08-18 12:38 | 2026-08-18 13:16 | 2026-08-18 13:22 | 2026-08-18 13:22 | 2026-08-18 13:22 | Fire |  | Fair | No | Information received from customer that the issue was resolved by certified electrician Meter socket voltage 117v 118v 235v
Non-Outage | J.E.26.08.25605 | C001891955 | Collin Robinson | Portland | Completed | Load_260754 | Port Antonio - 410 | 2026-08-18 07:53 | 2026-08-18 07:54 | 2026-08-18 09:01 | 2026-08-18 09:18 | 2026-08-18 09:17 | 2026-08-18 09:20 | 2026-08-18 09:20 | 2026-08-18 09:20 |  |  | Fair | No | Information received from customer that issue resolved from Sunday night
Non-Outage | J.E.26.08.25705 | C001891956 | Collin Robinson | Portland | Completed | Load_252130 | Port Antonio - 410 | 2026-08-18 07:53 | 2026-08-18 07:54 | 2026-08-18 08:05 | 2026-08-18 08:06 | 2026-08-18 08:59 | 2026-08-18 09:00 | 2026-08-18 09:00 | 2026-08-18 09:00 |  |  | Fair | No | Information received from customer that issue was resolved
Outage | J.E.26.08.25671 | C001891958 | Daniel Francis | St.Ann | Completed | Load_267394 | Roaring River - 210 | 2026-08-18 07:53 | 2026-08-18 07:54 | 2026-08-18 12:58 | 2026-08-18 12:58 | 2026-08-18 14:15 | 2026-08-18 14:17 | 2026-08-18 14:20 | 2026-08-18 14:20 |  |  | Fair | No | Found ok power restored from 17 of august
Outage | J.E.26.08.26796 | C001891957 | Daniel Francis | St.Ann | Completed | Load_269472 | Roaring River - 410 | 2026-08-18 07:53 | 2026-08-18 07:54 | 2026-08-18 07:59 | 2026-08-18 08:22 | 2026-08-18 09:23 | 2026-08-18 09:23 | 2026-08-18 09:25 | 2026-08-18 09:25 |  |  | Fair | No | Change 2 one bolt clamp 116 117 232 in all
Outage | J.E.26.08.27419 | C001891960 | Daniel Francis | St.Ann | Completed | Load_247248 | Roaring River - 210 | 2026-08-18 07:53 | 2026-08-18 07:54 | 2026-08-18 11:54 | 2026-08-18 11:55 | 2026-08-18 12:55 | 2026-08-18 12:57 | 2026-08-18 12:58 | 2026-08-18 12:58 |  |  | Fair | No | Not found customer phone number not working
Non-Outage | J.E.26.07.28140 | C001891962 | Odeanie Davis | KSAS | Completed | Load_254615 | Hunts Bay - 810 | 2026-08-18 07:54 | 2026-08-18 07:56 | 2026-08-18 10:32 | 2026-08-18 12:32 | 2026-08-18 12:32 | 2026-08-18 13:59 | 2026-08-18 12:33 | 2026-08-18 12:33 |  |  | Fair | No | Customer stated that they don’t have any power issues
Non-Outage | J.E.26.07.29305 | C001891963 | Odeanie Davis | KSAS | Completed | Load_295258 | Hunts Bay - 710 | 2026-08-18 07:54 | 2026-08-18 07:56 | 2026-08-18 09:15 | 2026-08-18 09:15 | 2026-08-18 09:18 | 2026-08-18 09:58 | 2026-08-18 09:58 | 2026-08-18 09:58 |  |  | Fair | No | Customer’s unicorn was reprogramed and reconnected, customer was able to add and check KW on device
Non-Outage | J.E.26.07.29421 | C001891965 | Odeanie Davis | KSAS | Completed | Load_238838 | Hunts Bay - 710 | 2026-08-18 07:54 | 2026-08-18 07:56 | 2026-08-18 10:12 | 2026-08-18 10:13 | 2026-08-18 10:12 | 2026-08-18 10:26 | 2026-08-18 10:26 | 2026-08-18 10:26 |  |  | Fair | No | 116v/116v & 233v at location, no power issues found at time of visit
Non-Outage | J.E.26.07.30390 | C001891964 | Odeanie Davis | KSAS | Completed | Load_255777 | Hunts Bay - 810 | 2026-08-18 07:54 | 2026-08-18 07:56 | 2026-08-18 08:41 | 2026-08-18 08:42 | 2026-08-18 08:47 | 2026-08-18 08:57 | 2026-08-18 08:56 | 2026-08-18 08:56 |  |  | Fair | No | YPP meter at location, meter not communicating, customer got 3 estimating bill, meter needs to be checked, bucket truck needed,
Outage | J.E.26.08.27467 | C001891961 | Hartley Chin | Clarendon | Completed | Load_568357 | May Pen - 110 | 2026-08-18 07:54 | 2026-08-18 07:57 | 2026-08-18 13:13 | 2026-08-18 13:14 | 2026-08-18 14:39 | 2026-08-18 14:39 | 2026-08-18 14:45 | 2026-08-18 14:45 | TreeContact | Y | Fair | No | Ref: maintenance area needs heavy bushing cut tree but needs more bushing soon
Non-Outage | J.E.26.07.38627 | C001891967 | Odeanie Davis | KSAS | Completed | Load_293369 | Hunts Bay - 810 | 2026-08-18 07:55 | 2026-08-18 07:56 | 2026-08-18 11:20 | 2026-08-18 11:20 | 2026-08-18 11:20 | 2026-08-18 11:57 | 2026-08-18 12:02 | 2026-08-18 12:02 |  |  | Fair | No | Field service team needed, 121v/22v at secondary from rammi box, rammi team needed…
Non-Outage | J.E.26.07.39258 | C001891966 | Odeanie Davis | KSAS | Completed | Load_301920 | Hunts Bay - 810 | 2026-08-18 07:55 | 2026-08-18 07:56 | 2026-08-18 09:09 | 2026-08-18 14:35 | 2026-08-18 14:35 | 2026-08-18 14:59 | 2026-08-18 14:35 | 2026-08-18 14:35 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.01603 | C001891972 | Odeanie Davis | KSAN | Completed | Load_242936 | Washington Blvd - 310 | 2026-08-18 07:55 | 2026-08-18 07:57 | 2026-08-18 10:40 | 2026-08-18 10:44 | 2026-08-18 10:44 | 2026-08-18 10:47 | 2026-08-18 10:50 | 2026-08-18 10:50 |  |  | Fair | No | Ackee tree growing on secondary line needs to be cut. Customer stated that this is an issue that was reported multiple times.
Non-Outage | J.E.26.08.01647 | C001891970 | Odeanie Davis | KSAN | Completed | Load_1002618 | Washington Blvd - 310 | 2026-08-18 07:55 | 2026-08-18 07:57 | 2026-08-18 09:02 | 2026-08-18 09:02 | 2026-08-18 09:02 | 2026-08-18 09:11 | 2026-08-18 09:06 | 2026-08-18 09:06 |  |  | Fair | No | Customer stated that they don’t have any power issues
Non-Outage | J.E.26.08.01688 | C001891969 | Odeanie Davis | KSAN | Completed | Load_244459 | Washington Blvd - 310 | 2026-08-18 07:55 | 2026-08-18 07:57 | 2026-08-18 11:01 | 2026-08-18 11:02 | 2026-08-18 11:09 | 2026-08-18 11:23 | 2026-08-18 11:19 | 2026-08-18 11:19 |  |  | Fair | No | 116v/117v 233v at location, no power issues found at time of visit
Non-Outage | J.E.26.08.01696 | C001891971 | Odeanie Davis | KSAN | Completed | Load_239186 | Washington Blvd - 310 | 2026-08-18 07:55 | 2026-08-18 07:57 | 2026-08-18 10:10 | 2026-08-18 14:35 | 2026-08-18 14:34 | 2026-08-18 14:34 | 2026-08-18 14:35 | 2026-08-18 14:35 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.01835 | C001891968 | Odeanie Davis | KSAS | Completed | Load_244159 | Hunts Bay - 310 | 2026-08-18 07:55 | 2026-08-18 07:56 | 2026-08-18 08:29 | 2026-08-18 14:36 | 2026-08-18 14:35 | 2026-08-18 15:08 | 2026-08-18 14:36 | 2026-08-18 14:36 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.13517 | C001891973 | Hartley Chin | Clarendon | Completed | Load_249266 | May Pen - 110 | 2026-08-18 07:56 | 2026-08-18 07:57 | 2026-08-18 11:35 | 2026-08-18 11:35 | 2026-08-18 13:12 | 2026-08-18 13:13 | 2026-08-18 13:13 | 2026-08-18 13:13 |  |  | Fair | No | Problem was corrected
Non-Outage | J.E.26.08.19207 | C001891975 | Hartley Chin | Clarendon | Completed | Load_237790 | May Pen - 110 | 2026-08-18 07:56 | 2026-08-18 07:57 | 2026-08-18 10:09 | 2026-08-18 11:34 | 2026-08-18 11:33 | 2026-08-18 11:34 | 2026-08-18 11:34 | 2026-08-18 11:34 |  |  | Fair | No | Repair neutral joint. Change one bolt clamp
Non-Outage | J.E.26.08.21857 | C001891976 | Hartley Chin | Clarendon | Completed | Load_352838 | May Pen - 110 | 2026-08-18 07:56 | 2026-08-18 07:57 | 2026-08-18 09:14 | 2026-08-18 09:15 | 2026-08-18 10:07 | 2026-08-18 10:09 | 2026-08-18 10:09 | 2026-08-18 10:09 |  |  | Fair | No | Issue was resolved 2 days ago
Non-Outage | J.E.26.08.26319 | C001891978 | Fredrick Hamilton | KSAN | Completed | Load_269826 | Constant Spring - 210 | 2026-08-18 07:56 | 2026-08-18 07:58 | 2026-08-18 08:01 | 2026-08-18 09:01 | 2026-08-18 09:23 | 2026-08-18 09:35 | 2026-08-18 09:35 | 2026-08-18 09:35 |  |  | Fair | No | 229.2v/114.1v/113.8v obtained Premises is ok at time of visit
Non-Outage | J.E.26.08.26657 | C001891977 | Fredrick Hamilton | KSAN | Completed | Load_260342 | Constant Spring - 410 | 2026-08-18 07:56 | 2026-08-18 07:58 | 2026-08-18 08:01 | 2026-08-18 09:43 | 2026-08-18 09:58 | 2026-08-18 10:41 | 2026-08-18 10:41 | 2026-08-18 10:41 |  |  | Fair | No | Defective service wire observed at location same was corrected 205v119v/56v obtained before repair 236v119v/117v obtained after repair Tape used
Non-Outage | J.E.26.08.26826 | C001891979 | Fredrick Hamilton | KSAN | Completed | Load_248183 | Hope - 410 | 2026-08-18 07:56 | 2026-08-18 07:58 | 2026-08-18 08:01 | 2026-08-18 11:27 | 2026-08-18 11:27 | 2026-08-18 11:41 | 2026-08-18 11:41 | 2026-08-18 11:41 |  |  | Fair | No | Defective meter socket at location customer advised No JPS defect seen at location
Non-Outage | J.E.26.08.26083 | C001891983 | Rochaine Hussey | KSAN | Completed | Load_567617 | Constant Spring - 310 | 2026-08-18 07:58 | 2026-08-18 07:59 | 2026-08-18 11:42 | 2026-08-18 11:42 | 2026-08-18 11:42 | 2026-08-18 12:45 | 2026-08-18 13:39 | 2026-08-18 13:39 |  |  | Fair | No | Went on location Unable to locate
Non-Outage | J.E.26.08.26412 | C001891980 | Fredrick Hamilton | KSAN | Completed | Load_241187 | West Kings House - 310 | 2026-08-18 07:58 | 2026-08-18 07:59 | 2026-08-18 08:01 | 2026-08-18 10:44 | 2026-08-18 10:55 | 2026-08-18 11:12 | 2026-08-18 11:12 | 2026-08-18 11:12 |  |  | Fair | No | 232v/114v/117v obtained Corrosion detected in customer meter socket customer advised
Non-Outage | J.E.26.08.27267 | C001891981 | Rochaine Hussey | KSAN | Completed | Load_269403 | Constant Spring - 410 | 2026-08-18 07:58 | 2026-08-18 07:59 | 2026-08-18 09:59 | 2026-08-18 11:27 | 2026-08-18 11:26 | 2026-08-18 11:28 | 2026-08-18 11:28 | 2026-08-18 11:28 |  |  | Fair | No | Neutral wire was corroded on the secondary line 1 bolt clamp was changed and issue was resolved 119/117/237v
Non-Outage | J.E.26.06.37543 | C001891988 | Royston Montague | St.Catherine | Completed | Load_249566 | Tredegar - 310 | 2026-08-18 07:59 | 2026-08-18 08:01 | 2026-08-18 08:27 | 2026-08-18 15:44 | 2026-08-18 16:31 | 2026-08-18 16:32 | 2026-08-18 16:32 | 2026-08-18 16:32 |  |  | Fair | No | Voltage 224v 111v 114v , location found ok
Non-Outage | J.E.26.07.39718 | C001891987 | Royston Montague |  | Completed |  |  | 2026-08-18 07:59 | 2026-08-18 08:01 | 2026-08-18 08:27 | 2026-08-18 14:42 | 2026-08-18 15:42 | 2026-08-18 15:43 | 2026-08-18 15:43 | 2026-08-18 15:43 |  |  | Fair | No | Fall voltage found, 229v 113v 114v customer asked to get an electrician to check load side.
Non-Outage | J.E.26.08.18056 | C001891986 | Royston Montague | St.Catherine | Completed | Load_249863 | Tredegar - 510 | 2026-08-18 07:59 | 2026-08-18 08:01 | 2026-08-18 08:27 | 2026-08-18 12:19 | 2026-08-18 13:06 | 2026-08-18 13:07 | 2026-08-18 13:07 | 2026-08-18 13:07 |  |  | Fair | No | Customer confirmed issue resolved
Non-Outage | J.E.26.08.21633 | C001891985 | Royston Montague | St.Catherine | Completed | Load_265928 | Tredegar - 510 | 2026-08-18 07:59 | 2026-08-18 08:01 | 2026-08-18 08:27 | 2026-08-18 11:23 | 2026-08-18 12:17 | 2026-08-18 12:18 | 2026-08-18 12:18 | 2026-08-18 12:18 | LowHangingWires |  | Fair | No | Location found ok. Fallen tree removed.
Non-Outage | J.E.26.08.26085 | C001891984 | Royston Montague | St.Catherine | Completed | Load_265584 | Tredegar - 510 | 2026-08-18 07:59 | 2026-08-18 08:01 | 2026-08-18 08:27 | 2026-08-18 10:27 | 2026-08-18 10:55 | 2026-08-18 11:06 | 2026-08-18 11:07 | 2026-08-18 11:07 |  |  | Fair | No | Burn wire in meter socket. Customer informed to get same repair. No continuity on one side of the meter. Please inform field service department of this thanks, customer unable to use 220v equipment. Voltage 217v 107v 106v
Non-Outage | J.E.26.08.25491 | C001891989 | Royston Montague | St.Catherine | Completed | Load_1000336 | Tredegar - 210 | 2026-08-18 08:00 | 2026-08-18 08:01 | 2026-08-18 08:27 | 2026-08-18 09:09 | 2026-08-18 10:13 | 2026-08-18 10:26 | 2026-08-18 10:26 | 2026-08-18 10:26 |  |  | Fair | No | Faulty meter socket, only one side of meter working. Same needs to change. Please inform field service department thanks. Voltage 228v 113v 113v . Customer informed to repair meter socket.
Outage | J.E.26.08.27311 | C001891992 | Andre Williams | Trelawny | Completed | Load_263192 | Martha Brae - 110 | 2026-08-18 08:12 | 2026-08-18 08:13 | 2026-08-18 08:34 | 2026-08-18 08:38 | 2026-08-18 09:03 | 2026-08-18 09:45 | 2026-08-18 09:45 | 2026-08-18 09:45 |  |  | Fair | No | Remake burnt off joint on #naut conductor.voltage on line 116+116=232
Outage | J.E.26.08.26322 | C001891995 | Andre Williams | Trelawny | Completed | Load_256336 | Duncans - 210 | 2026-08-18 08:13 | 2026-08-18 08:31 | 2026-08-18 10:15 | 2026-08-18 10:19 | 2026-08-18 10:44 | 2026-08-18 10:58 | 2026-08-18 10:59 | 2026-08-18 10:59 |  |  | Fair | No | No visible fault seen on open secondary line re fuse and close blown 3 amp on 25kva transformer
Outage | J.E.26.08.27031 | C001891994 | Marlon Brown | Trelawny | Completed | Load_269573 | Greenwood - 110 | 2026-08-18 08:13 | 2026-08-18 15:48 | 2026-08-18 18:16 | 2026-08-18 18:16 | 2026-08-18 18:35 | 2026-08-18 18:51 | 2026-08-18 18:52 | 2026-08-18 18:52 |  |  | Fair | No | Clean and remake joint at pothead,Voltage found at pothead 120vVoltage leaving at pothead 120v.
Outage | J.E.26.08.27275 | C001891993 | Andre Williams | Trelawny | Completed | Load_254504 | Martha Brae - 110 | 2026-08-18 08:13 | 2026-08-18 08:14 | 2026-08-18 09:51 | 2026-08-18 12:42 | 2026-08-18 14:03 | 2026-08-18 15:04 | 2026-08-18 14:04 | 2026-08-18 14:04 |  |  | Flood | No | Unable to locate individual customer
Outage | J.E.26.08.27400 | C001891999 | Daniel Francis | St.Ann | Completed | Load_238296 | Upper White River - 210 | 2026-08-18 08:20 | 2026-08-18 08:21 | 2026-08-18 14:20 | 2026-08-18 14:21 | 2026-08-18 14:51 | 2026-08-18 14:52 | 2026-08-18 14:55 | 2026-08-18 14:55 |  |  | Fair | No | Call is not st Ann
Outage | J.E.26.08.26275 | C001892002 | Raymond Carr | St.Ann | Completed | Load_265764 | Upper White River - 110 | 2026-08-18 08:21 | 2026-08-18 08:23 | 2026-08-18 14:22 | 2026-08-18 14:23 | 2026-08-18 14:22 | 2026-08-18 02:17 | 2026-08-18 14:23 | 2026-08-18 14:23 |  |  | Fair | No | Refer to St Ann.
Outage | J.E.26.08.26317 | C001892001 | Raymond Carr | St.Mary | Completed | Load_256631 | Blackstonedge - 110 | 2026-08-18 08:21 | 2026-08-18 08:23 | 2026-08-18 14:24 | 2026-08-18 14:24 | 2026-08-18 14:46 | 2026-08-18 14:44 | 2026-08-18 14:47 | 2026-08-18 14:47 |  |  | Fair | No | Customer reported that supply was restored yesterday.
Outage | J.E.26.08.26380 | C001892003 | Raymond Carr | St.Ann | Completed | Load_251050 | Upper White River - 110 | 2026-08-18 08:21 | 2026-08-18 08:23 | 2026-08-18 13:44 | 2026-08-18 13:44 | 2026-08-18 13:44 | 2026-08-18 14:15 | 2026-08-18 14:22 | 2026-08-18 14:22 |  |  | Fair | No | Refer to St Ann.
Outage | J.E.26.08.26695 | C001892004 | Raymond Carr | St.Mary | Completed | Load_254854 | Oracabessa - 110 | 2026-08-18 08:21 | 2026-08-18 08:23 | 2026-08-18 10:59 | 2026-08-18 10:59 | 2026-08-18 11:57 | 2026-08-18 11:49 | 2026-08-18 11:58 | 2026-08-18 11:58 |  |  | Fair | No | Customer reported that account was disconnected.
Outage | J.E.26.08.26899 | C001892005 | Raymond Carr | St.Mary | Completed | Load_256925 | Oracabessa - 210 | 2026-08-18 08:22 | 2026-08-18 08:23 | 2026-08-18 09:40 | 2026-08-18 09:40 | 2026-08-18 10:01 | 2026-08-18 09:46 | 2026-08-18 10:03 | 2026-08-18 10:03 |  |  | Fair | No | Customer is requesting a new installation. Refer to field service department.
Outage | J.E.26.08.27027 | C001892006 | Raymond Carr | St.Ann | Completed | Load_259028 | Upper White River - 110 | 2026-08-18 08:22 | 2026-08-18 08:23 | 2026-08-18 12:36 | 2026-08-18 12:37 | 2026-08-18 13:30 | 2026-08-18 13:31 | 2026-08-18 13:43 | 2026-08-18 13:43 |  |  | Fair | No | Customer reported that was restored two weeks ago.
Non-Outage | J.E.26.08.25849 | C001892007 | Daniel Francis |  | Completed |  |  | 2026-08-18 08:23 | 2026-08-18 08:25 | 2026-08-18 09:29 | 2026-08-18 09:29 | 2026-08-18 09:45 | 2026-08-18 09:46 | 2026-08-18 09:46 | 2026-08-18 09:46 |  |  | Fair | No | Found okay customer say light come from yesterday
Non-Outage | J.E.26.08.26059 | C001892008 | Daniel Francis |  | Completed |  |  | 2026-08-18 08:23 | 2026-08-18 08:25 | 2026-08-18 09:51 | 2026-08-18 09:52 | 2026-08-18 10:07 | 2026-08-18 10:08 | 2026-08-18 10:09 | 2026-08-18 10:09 |  |  | Fair | No | Found okay we call customer and she say power restored from yesterday
Outage | J.E.26.08.26428 | C001892009 | Lionel Robinson | Trelawny | Completed | Load_268005 | Greenwood - 110 | 2026-08-18 08:24 | 2026-08-18 08:25 | 2026-08-18 09:26 | 2026-08-18 09:27 | 2026-08-18 09:26 | 2026-08-18 09:27 | 2026-08-18 09:28 | 2026-08-18 09:28 |  |  | Fair | No | Customer contacted and confirmed okay
Outage | J.E.26.08.26726 | C001892010 | Lionel Robinson | Trelawny | Completed | Load_255240 | Greenwood - 110 | 2026-08-18 08:24 | 2026-08-18 08:25 | 2026-08-18 11:23 | 2026-08-18 11:24 | 2026-08-18 11:52 | 2026-08-18 13:41 | 2026-08-18 13:42 | 2026-08-18 13:42 |  |  | Fair | No | Replace 100ft of defective #6 triplex Voltage 114v, 115v, 229v
Non-Outage | J.E.26.08.26938 | C001892011 | Daniel Francis | St.Ann | Completed | Load_261997 | Ocho Rios - 310 | 2026-08-18 08:25 | 2026-08-18 08:26 | 2026-08-18 10:09 | 2026-08-18 10:10 | 2026-08-18 10:25 | 2026-08-18 10:27 | 2026-08-18 10:29 | 2026-08-18 10:29 |  |  | Fair | No | Not found this # not working and not clear enough for us to find it
Outage | J.E.26.08.27029 | C001892017 | Andre Williams | Trelawny | Completed | Load_263192 | Martha Brae - 110 | 2026-08-18 08:27 | 2026-08-18 08:30 | 2026-08-18 09:49 | 2026-08-18 09:50 | 2026-08-18 09:50 | 2026-08-18 09:51 | 2026-08-18 09:51 | 2026-08-18 09:51 |  |  | Fair | No | Remake burnt off joint on #naut conductor.voltage on line 116+116=232
Non-Outage | J.E.26.08.22802 | C001892034 | Locksley Allen | St.Mary | Completed | Load_238360 | Highgate - 210 | 2026-08-18 08:31 | 2026-08-18 08:36 | 2026-08-18 10:35 | 2026-08-18 10:36 | 2026-08-18 10:35 | 2026-08-18 11:00 | 2026-08-18 11:08 | 2026-08-18 11:08 |  |  | Fair | No | Clean up connectors at pole and pothead Voltage at meter socket phase to phase 219v. Phase to neutral 109&107vLights inside bedroom and outside keeps tripping outCustomer has internal problem and was advised to get an electrician
Non-Outage | J.E.26.08.24523 | C001892033 | Locksley Allen | St.Mary | Completed | Load_262790 | Oracabessa - 210 | 2026-08-18 08:31 | 2026-08-18 08:36 | 2026-08-18 15:29 | 2026-08-18 15:31 | 2026-08-18 15:30 | 2026-08-18 15:35 | 2026-08-18 15:32 | 2026-08-18 15:32 |  |  | Fair | No | JPS corrected the problem from Sunday
Non-Outage | J.E.26.08.25269 | C001892032 | Locksley Allen | St.Mary | Completed | Load_266413 | Oracabessa - 210 | 2026-08-18 08:31 | 2026-08-18 08:36 | 2026-08-18 14:51 | 2026-08-18 15:06 | 2026-08-18 15:06 | 2026-08-18 15:25 | 2026-08-18 15:21 | 2026-08-18 15:21 |  |  | Fair | No | Several customers in this area is having the same problem.The neutral at the entrance to Reid’sBvd is burst
Non-Outage | J.E.26.08.26389 | C001892030 | Locksley Allen | St.Mary | Completed | Load_242851 | Oracabessa - 110 | 2026-08-18 08:31 | 2026-08-18 08:36 | 2026-08-18 11:10 | 2026-08-18 12:40 | 2026-08-18 12:39 | 2026-08-18 12:43 | 2026-08-18 12:42 | 2026-08-18 12:42 |  |  | Fair | No | Meter defective (burn). Voltage at meter socket phase to phase 238vPhase to neutral 115&114v. Please refer to field service
Non-Outage | J.E.26.08.26755 | C001892031 | Locksley Allen | St.Mary | Completed | Load_263813 | Oracabessa - 210 | 2026-08-18 08:31 | 2026-08-18 08:36 | 2026-08-18 14:05 | 2026-08-18 14:41 | 2026-08-18 14:41 | 2026-08-18 14:49 | 2026-08-18 14:50 | 2026-08-18 14:50 |  |  | Fair | No | Pothead found corroded at premises,clean up connectors Voltage at meter socket phase to phase 235v. Phase to neutral 115&118Meter left working okay
Non-Outage | J.E.26.08.26829 | C001892018 | Andre Williams |  | Completed |  |  | 2026-08-18 08:31 | 2026-08-18 08:32 | 2026-08-18 10:09 | 2026-08-18 10:15 | 2026-08-18 10:14 | 2026-08-18 10:15 | 2026-08-18 10:15 | 2026-08-18 10:15 |  |  | Fair | No | Premises ok and with supply, confirm by call
Non-Outage | J.E.26.08.26879 | C001892029 | Locksley Allen | St.Mary | Completed | Load_353034 | Oracabessa - 110 | 2026-08-18 08:31 | 2026-08-18 08:36 | 2026-08-18 13:31 | 2026-08-18 13:48 | 2026-08-18 14:01 | 2026-08-18 14:07 | 2026-08-18 14:03 | 2026-08-18 14:03 |  |  | Fair | No | Low voltage problem found at premises,several customers in this area is having the same problem. Phase to phase 145vPlease refer to emergency
Non-Outage | J.E.26.08.27104 | C001892020 | Locksley Allen | St.Mary | Completed | Load_246610 | Oracabessa - 110 | 2026-08-18 08:31 | 2026-08-18 08:36 | 2026-08-18 13:03 | 2026-08-18 13:04 | 2026-08-18 13:03 | 2026-08-18 13:17 | 2026-08-18 13:25 | 2026-08-18 13:25 |  |  | Fair | No | Pothead found corroded,clean up pothead.Voltage at meter socket phase to phase 235v. Phase to neutral 118&110vMeter left working okay
Non-Outage | J.E.26.08.27226 | C001892019 | Locksley Allen | St.Mary | Completed | Load_237863 | Highgate - 210 | 2026-08-18 08:31 | 2026-08-18 08:36 | 2026-08-18 09:34 | 2026-08-18 09:52 | 2026-08-18 09:52 | 2026-08-18 10:07 | 2026-08-18 10:04 | 2026-08-18 10:04 |  |  | Fair | No | No light is in the area from last night. Please refer to emergency
Outage | J.E.26.08.27521 | C001892035 | Richard Samuda | Manchester | Completed | Load_251691 | Spur Tree - 310 | 2026-08-18 08:32 | 2026-08-18 08:33 | 2026-08-18 09:48 | 2026-08-18 09:49 | 2026-08-18 09:51 | 2026-08-18 09:51 | 2026-08-18 09:51 | 2026-08-18 09:51 |  |  | Fair | No | Customer said they didn’t make a call
Outage | J.E.26.08.27555 | C001892037 | Lancelot Brown | Hanover | Completed | Load_245213 | Orange Bay - 310 | 2026-08-18 08:32 | 2026-08-18 09:32 | 2026-08-18 09:49 | 2026-08-18 09:50 | 2026-08-18 09:49 | 2026-08-18 09:50 | 2026-08-18 09:50 | 2026-08-18 09:50 |  |  | Fair | No | This call related to 2amps fuse at 25kva supply restore
Outage | J.E.26.08.27556 | C001892036 | Lancelot Brown | Hanover | Completed | Load_250960 | Orange Bay - 310 | 2026-08-18 08:32 | 2026-08-18 09:32 | 2026-08-18 11:25 | 2026-08-18 11:25 | 2026-08-18 13:33 | 2026-08-18 14:17 | 2026-08-18 14:18 | 2026-08-18 14:18 |  |  | Fair | No | Check and found customer meter diffective contact customer care and was trying to reconnect meter and it’s not working customer care request meter change please pass on to field service department in montegobay bay west to Hanover customer still without supply need ergent attention
Non-Outage | J.E.26.08.26165 | C001892038 | Error Coore | Manchester | Completed | Load_265007 | Kendal - 310 | 2026-08-18 08:33 | 2026-08-18 08:34 | 2026-08-18 09:43 | 2026-08-18 09:43 | 2026-08-18 10:08 | 2026-08-18 10:13 | 2026-08-18 10:14 | 2026-08-18 10:14 |  |  | Fair | No | Premises found locked unable to access meter
Non-Outage | J.E.26.07.05469 | C001892050 | Error Coore | Manchester | Completed | Load_246708 | Spur Tree - 310 | 2026-08-18 08:36 | 2026-08-18 09:46 | 2026-08-18 10:31 | 2026-08-18 10:32 | 2026-08-18 11:31 | 2026-08-18 11:49 | 2026-08-18 11:50 | 2026-08-18 11:50 |  |  | Fair | No | Premises found ok customer have internal problem voltage reading 118 volts
Non-Outage | J.E.26.07.23697 | C001892041 | Error Coore | Manchester | Completed | Load_259390 | Spur Tree - 310 | 2026-08-18 08:36 | 2026-08-18 09:46 | 2026-08-18 14:36 | 2026-08-18 14:37 | 2026-08-18 15:15 | 2026-08-18 16:11 | 2026-08-18 16:13 | 2026-08-18 16:13 |  |  | Fair | No | Found customer with corroded phase and neutral at pothead remade corroded phase and neutral using 3 service sleeve voltage reading 116/117/233 volts
Non-Outage | J.E.26.08.19783 | C001892040 | Error Coore | Manchester | Completed | Load_264906 | Spur Tree - 310 | 2026-08-18 08:36 | 2026-08-18 09:46 | 2026-08-18 13:14 | 2026-08-18 13:15 | 2026-08-18 14:25 | 2026-08-18 14:35 | 2026-08-18 14:36 | 2026-08-18 14:36 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.08.20829 | C001892039 | Error Coore | Manchester | Completed | Load_239126 | Spur Tree - 310 | 2026-08-18 08:36 | 2026-08-18 09:46 | 2026-08-18 12:11 | 2026-08-18 12:12 | 2026-08-18 12:44 | 2026-08-18 13:13 | 2026-08-18 13:14 | 2026-08-18 13:14 |  |  | Fair | No | Found customer with wrap connection at pothead unable to carry out repair due to customer meter pole is badly rotten at base also found customer meter burn
Outage | J.E.26.08.27553 | C001892051 | Evan Spaulding | St.Mary | Completed | Load_260492 | Highgate - 210 | 2026-08-18 08:36 | 2026-08-18 08:59 | 2026-08-18 10:23 | 2026-08-18 10:24 | 2026-08-18 11:07 | 2026-08-18 11:37 | 2026-08-18 11:38 | 2026-08-18 11:38 |  |  | Fair | No | Patrol line section no fault seen replace 1-5 amps Transformer fuse at pole number 0010734.
Outage | J.E.26.08.27560 | C001892049 | Evan Spaulding | St.Mary | Completed | Load_252067 | Highgate -110 | 2026-08-18 08:36 | 2026-08-18 08:59 | 2026-08-18 10:22 | 2026-08-18 10:22 | 2026-08-18 10:22 | 2026-08-18 10:22 | 2026-08-18 10:23 | 2026-08-18 10:23 | BrokenWire |  | SevereWind | No | Associated call
Outage | J.E.26.08.27562 | C001892053 | Daniel Francis | St.Ann | Completed | Load_260937 | Roaring River - 210 | 2026-08-18 08:36 | 2026-08-18 08:58 | 2026-08-18 10:29 | 2026-08-18 10:30 | 2026-08-18 11:20 | 2026-08-18 11:21 | 2026-08-18 11:22 | 2026-08-18 11:22 |  |  | Fair | No | Not found
Outage | J.E.26.08.27565 | C001892054 | Daniel Francis | St.Ann | Completed | Load_556416 | Roaring River - 210 | 2026-08-18 08:36 | 2026-08-18 08:58 | 2026-08-18 11:22 | 2026-08-18 11:23 | 2026-08-18 11:52 | 2026-08-18 11:54 | 2026-08-18 11:54 | 2026-08-18 11:54 |  |  | Fair | No | Found okay 117 116 233 in all
Outage | J.E.26.08.27557 | C001892055 | Daniel Francis | St.Ann | Completed | Load_242953 | Roaring River - 410 | 2026-08-18 08:37 | 2026-08-18 08:58 | 2026-08-18 09:46 | 2026-08-18 09:47 | 2026-08-18 09:49 | 2026-08-18 09:51 | 2026-08-18 09:51 | 2026-08-18 09:51 |  |  | Fair | No | Not found customer not answering phone
Non-Outage | J.E.26.08.27550 | C001892056 | Dwain Samuels | Westmoreland | Completed | Load_246958 | Paradise - 310 | 2026-08-18 08:39 | 2026-08-18 09:36 | 2026-08-18 09:42 | 2026-08-19 10:18 | 2026-08-19 10:47 | 2026-08-19 10:48 | 2026-08-19 11:05 | 2026-08-19 11:05 |  |  | Fair | No | Found working okay. Customer has internal problems. Voltage check 111-110-221
Non-Outage | J.E.26.08.26864 | C001892063 | Lancelot Brown | Hanover | Completed | Load_264368 | Orange Bay - 310 | 2026-08-18 08:43 | 2026-08-18 09:05 | 2026-08-18 11:25 | 2026-08-18 14:39 | 2026-08-18 14:38 | 2026-08-18 14:56 | 2026-08-18 14:56 | 2026-08-18 14:56 |  |  | SevereWind | No | Customer complained on on and supply found one span secondary phase and neural banging caused by slock span and high wind retention one span secondary nutral owed #2 preform
Non-Outage | J.E.26.08.27009 | C001892064 | Tajay Bernard | Hanover | Completed | Load_238388 | Orange Bay - 310 | 2026-08-18 08:43 | 2026-08-19 08:38 | 2026-08-19 08:52 | 2026-08-19 08:53 | 2026-08-19 09:50 | 2026-08-19 09:52 | 2026-08-19 09:53 | 2026-08-19 09:53 |  |  | Fair | No | Area check and found unable to locate customer on premises multiple phone calls to both numbers that was provided went unanswered
Non-Outage | J.E.26.08.27486 | C001892065 | Raymond Lewis | Hanover | Completed | Load_254345 | Orange Bay - 310 | 2026-08-18 08:44 | 2026-08-18 16:02 | 2026-08-18 23:57 | 2026-08-18 23:58 | 2026-08-18 23:57 | 2026-08-18 12:59 | 2026-08-19 | 2026-08-19 |  |  | Fair | No | Not st.anns call
Outage | J.E.26.08.27369 | C001892066 | Neville Spencer | Clarendon | Completed | Load_249787 | Monymusk - 410 | 2026-08-18 08:45 | 2026-08-18 08:46 | 2026-08-18 18:33 | 2026-08-18 18:34 | 2026-08-18 20:08 | 2026-08-18 20:33 | 2026-08-18 20:35 | 2026-08-18 20:35 |  |  | Fair | No | Remade corrded phase and neutral joints at pothead used 2, 6/6 sleeves voltage reading 116 supply restored.
Non-Outage | J.E.26.08.26117 | C001892079 | Moses Elliston |  | Completed |  |  | 2026-08-18 09:00 | 2026-08-18 09:01 | 2026-08-19 14:26 | 2026-08-19 14:27 | 2026-08-19 14:26 | 2026-08-19 14:28 | 2026-08-19 14:29 | 2026-08-19 14:29 |  |  | Fair | No | Supply ok at premises,See report # 1712565.
Outage | J.E.26.08.27591 | C001892086 | Richard Grant | St.Catherine | Completed | Load_1000869 | New Michelton - 210 | 2026-08-18 09:01 | 2026-08-18 09:02 | 2026-08-18 13:08 | 2026-08-18 13:09 | 2026-08-18 13:43 | 2026-08-18 13:43 | 2026-08-18 13:43 | 2026-08-18 13:43 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.27596 | C001892087 | Andre Williams | Trelawny | Completed | Load_1001463 | Martha Brae - 110 | 2026-08-18 09:02 | 2026-08-18 09:04 | 2026-08-18 09:51 | 2026-08-18 10:02 | 2026-08-18 10:02 | 2026-08-18 10:03 | 2026-08-18 10:04 | 2026-08-18 10:04 |  |  | Fair | No | Internal fault voltage at meter 115+115=230 confirm by technician
Non-Outage | J.E.26.08.23373 | C001892092 | Andrae Clarke | Portland | Completed | Load_250839 | Port Antonio - 310 | 2026-08-18 09:03 | 2026-08-18 09:04 | 2026-08-19 10:48 | 2026-08-19 10:49 | 2026-08-19 11:29 | 2026-08-19 11:45 | 2026-08-19 11:52 | 2026-08-19 11:52 |  |  | Fair | No | Repair defective wire connections using three one bolt clamp Check voltage 121/120/241
Non-Outage | J.E.26.08.25982 | C001892091 | Andrae Clarke |  | Completed |  |  | 2026-08-18 09:03 | 2026-08-18 09:04 | 2026-08-18 09:23 | 2026-08-18 09:23 | 2026-08-18 10:46 | 2026-08-18 09:46 | 2026-08-18 12:02 | 2026-08-18 12:02 |  |  | Fair | No | Repair broken wire one one bolt clamp Check voltage 226/118/108
Non-Outage | J.E.26.08.26358 | C001892090 | Andrae Clarke | Portland | Completed | Load_239005 | Port Antonio - 410 | 2026-08-18 09:03 | 2026-08-18 09:04 | 2026-08-18 14:28 | 2026-08-18 14:29 | 2026-08-18 16:38 | 2026-08-18 16:26 | 2026-08-18 16:39 | 2026-08-18 16:39 |  |  | Fair | No | Check voltage 120/119/239Premises found okay
Non-Outage | J.E.26.08.26631 | C001892089 | Andrae Clarke | Portland | Completed | Load_266274 | Port Antonio - 410 | 2026-08-18 09:03 | 2026-08-18 09:04 | 2026-08-18 12:06 | 2026-08-18 12:06 | 2026-08-18 12:38 | 2026-08-18 13:25 | 2026-08-18 14:28 | 2026-08-18 14:28 |  |  | Fair | No | Replace wire 50 feet Used three one bolt clamp Check voltage 110/103/213
Non-Outage | J.E.26.08.26995 | C001892088 | Andrae Clarke | Portland | Completed | Load_263415 | Port Antonio - 410 | 2026-08-18 09:03 | 2026-08-18 09:04 | 2026-08-18 10:58 | 2026-08-18 12:03 | 2026-08-18 12:03 | 2026-08-18 11:22 | 2026-08-18 12:05 | 2026-08-18 12:05 |  |  | Fair | No | Repair broken wire one one bolt clamp Check voltage 108/118/226
Non-Outage | J.E.26.08.19385 | C001892107 | Junior Scarlett | St.James | Completed | Load_250893 | Bogue - 310 | 2026-08-18 09:12 | 2026-08-18 09:13 | 2026-08-18 09:25 | 2026-08-19 10:54 | 2026-08-19 11:24 | 2026-08-19 11:50 | 2026-08-19 11:50 | 2026-08-19 11:50 |  |  | Fair | No | Check and found okVoltage found 115v 115v 230v
Non-Outage | J.E.26.08.19686 | C001892109 | Junior Scarlett | St.James | Completed | Load_574653 | Bogue - 310 | 2026-08-18 09:12 | 2026-08-18 09:13 | 2026-08-18 09:25 | 2026-08-19 08:51 | 2026-08-19 09:06 | 2026-08-19 09:24 | 2026-08-19 09:25 | 2026-08-19 09:25 |  |  | Fair | No | Check and found okVoltage found 115v 115v 230v
Non-Outage | J.E.26.08.19693 | C001892108 | Junior Scarlett | St.James | Completed | Load_574653 | Bogue - 310 | 2026-08-18 09:12 | 2026-08-18 09:13 | 2026-08-18 09:25 | 2026-08-19 09:25 | 2026-08-19 09:31 | 2026-08-19 10:31 | 2026-08-19 10:30 | 2026-08-19 10:30 |  |  | Fair | No | Check and found okVoltage found 115v 115v 230v
Non-Outage | J.E.26.08.19711 | C001892110 | Junior Scarlett | St.James | Completed | Load_264461 | Bogue - 310 | 2026-08-18 09:12 | 2026-08-18 09:13 | 2026-08-18 09:25 | 2026-08-19 14:47 | 2026-08-19 14:47 | 2026-08-19 15:23 | 2026-08-19 15:24 | 2026-08-19 15:24 |  |  | Fair | No | Check and found okVoltage found 112v 111v 221v
Non-Outage | J.E.26.08.22640 | C001892117 | Junior Scarlett | St.James | Completed | Load_250893 | Bogue - 310 | 2026-08-18 09:12 | 2026-08-18 09:13 | 2026-08-18 09:25 | 2026-08-18 10:05 | 2026-08-18 10:27 | 2026-08-18 10:09 | 2026-08-18 10:29 | 2026-08-18 10:29 |  |  | Fair | No | Checks and found ok
Non-Outage | J.E.26.08.22642 | C001892118 | Junior Scarlett | St.James | Completed | Load_250893 | Bogue - 310 | 2026-08-18 09:12 | 2026-08-18 09:13 | 2026-08-18 09:25 | 2026-08-18 09:28 | 2026-08-18 10:03 | 2026-08-18 10:03 | 2026-08-18 10:04 | 2026-08-18 10:04 |  |  | Fair | No | Check and found okVoltage found 115v 115v 230v
Non-Outage | J.E.26.08.26891 | C001892127 | Roemello Brown | Trelawny | Completed | Load_263192 | Martha Brae - 110 | 2026-08-18 09:15 | 2026-08-18 09:20 | 2026-08-18 10:25 | 2026-08-18 10:26 | 2026-08-18 10:44 | 2026-08-18 11:18 | 2026-08-18 11:23 | 2026-08-18 11:23 |  |  | Fair | No | One leg of second giving a low reading also kissing upon on the flow line needs emergency team to assist please Voltage found 122/89/203Voltage leave 122/89/203
Non-Outage | J.E.26.08.26896 | C001892124 | Roemello Brown | Trelawny | Completed | Load_263192 | Martha Brae - 110 | 2026-08-18 09:15 | 2026-08-18 09:20 | 2026-08-18 10:28 | 2026-08-18 11:47 | 2026-08-18 11:47 | 2026-08-18 11:47 | 2026-08-18 11:48 | 2026-08-18 11:48 |  |  | Fair | No | Duplicate order
Non-Outage | J.E.26.08.27004 | C001892125 | Roemello Brown | Trelawny | Completed | Load_251680 | Martha Brae - 210 | 2026-08-18 09:15 | 2026-08-18 09:20 | 2026-08-19 11:51 | 2026-08-19 11:51 | 2026-08-19 12:49 | 2026-08-19 12:49 | 2026-08-19 12:55 | 2026-08-19 12:55 |  |  | Fair | No | Premises found working okay Voltage found 116/116/232Voltage leave 116/116/232
Non-Outage | J.E.26.08.27047 | C001892126 | Roemello Brown | Trelawny | Completed | Load_261797 | Martha Brae - 210 | 2026-08-18 09:15 | 2026-08-18 09:20 | 2026-08-18 13:17 | 2026-08-18 14:34 | 2026-08-18 14:52 | 2026-08-18 14:52 | 2026-08-18 15:11 | 2026-08-18 15:11 |  |  | Fair | No | Premises found working okay Voltage found 116/116/232Voltage leave 116/116/232
Non-Outage | J.E.26.08.27389 | C001892121 | Andre Williams | Trelawny | Completed | Load_263192 | Martha Brae - 110 | 2026-08-18 09:15 | 2026-08-18 09:21 | 2026-08-18 09:45 | 2026-08-18 09:46 | 2026-08-18 09:46 | 2026-08-18 09:45 | 2026-08-18 09:48 | 2026-08-18 09:48 |  |  | Fair | No | Remake burnt off joint on #naut conductor.voltage on line 116+116=232
Non-Outage | J.E.26.08.27476 | C001892122 | Roemello Brown | Trelawny | Completed | Load_1001717 | Greenwood - 210 | 2026-08-18 09:15 | 2026-08-18 09:20 | 2026-08-18 11:45 | 2026-08-18 11:48 | 2026-08-18 12:45 | 2026-08-18 13:07 | 2026-08-18 13:14 | 2026-08-18 13:14 |  |  | Fair | No | Premises found working on when I arrive at the premises Voltage found 115/116/231Voltage leave 115/116/231
Outage | J.E.26.08.27637 | C001892146 | Lancelot Brown | Hanover | Completed | Load_250849 | Orange Bay - 310 | 2026-08-18 09:30 | 2026-08-18 09:31 | 2026-08-18 09:50 | 2026-08-18 09:51 | 2026-08-18 10:35 | 2026-08-18 11:21 | 2026-08-18 11:23 | 2026-08-18 11:23 |  |  | Rains | No | Found 2 junction fuse blown patroll found another junction fuse blown that feed digicel site also carry out another patroll found 25kva cover with vegetation cut and remove vegetation from 25kva replace 1-15-10amps junction pole number 597002 also replace 1-10amps junction fuse at pole number 0095702 feed digicel supply restore to both Rhodes hall and digicel
Outage | J.E.26.08.27501 | C001892149 | Rusean Allen | KSAS | Completed | Load_575102 | Cane River - 410 | 2026-08-18 09:31 | 2026-08-18 09:33 | 2026-08-18 11:29 | 2026-08-18 11:30 | 2026-08-18 11:29 | 2026-08-18 11:30 | 2026-08-18 11:30 | 2026-08-18 11:30 |  |  | Fair | No | Related to 39 dolphin square
Outage | J.E.26.08.27509 | C001892157 | Rusean Allen | KSAS | Completed | Load_255901 | Cane River - 410 | 2026-08-18 09:32 | 2026-08-18 09:33 | 2026-08-18 11:33 | 2026-08-18 11:34 | 2026-08-18 11:33 | 2026-08-18 11:34 | 2026-08-18 11:35 | 2026-08-18 11:35 |  |  | Fair | No | Related to dolphin square
Outage | J.E.26.08.27515 | C001892160 | Rusean Allen | KSAS | Completed | Load_245647 | Cane River - 410 | 2026-08-18 09:32 | 2026-08-18 09:33 | 2026-08-18 10:28 | 2026-08-18 10:29 | 2026-08-18 11:02 | 2026-08-18 11:14 | 2026-08-18 11:14 | 2026-08-18 11:14 |  |  | Fair | No | Broken wire found at switch bottom, wire was reconnected.
Outage | J.E.26.08.27561 | C001892158 | Rusean Allen | KSAS | Completed | Load_1002667 | Cane River - 410 | 2026-08-18 09:32 | 2026-08-18 09:33 | 2026-08-18 11:32 | 2026-08-18 11:33 | 2026-08-18 11:32 | 2026-08-18 11:33 | 2026-08-18 11:33 | 2026-08-18 11:33 |  |  | Fair | No | Related to dolphin square
Outage | J.E.26.08.27633 | C001892161 | Andre Williams | Trelawny | Completed | Load_263192 | Martha Brae - 110 | 2026-08-18 09:32 | 2026-08-18 09:48 | 2026-08-18 10:06 | 2026-08-18 10:06 | 2026-08-18 10:06 | 2026-08-18 10:06 | 2026-08-18 10:07 | 2026-08-18 10:07 |  |  | Fair | No | Issue resolve and previous call since morning
Non-Outage | J.E.26.08.19325 | C001892181 | Hopeton Henry | St.Thomas | Completed | Load_244001 | Good Year - 110 | 2026-08-18 09:42 | 2026-08-18 09:43 | 2026-08-19 10:31 | 2026-08-19 14:49 | 2026-08-19 14:49 | 2026-08-19 14:50 | 2026-08-19 14:51 | 2026-08-19 14:51 |  |  | Fair | No | Found ok , customer state that the issue was resolved
Outage | J.E.26.08.27676 | C001892182 | Andre Williams | Trelawny | Completed | Load_251680 | Martha Brae - 210 | 2026-08-18 09:44 | 2026-08-18 09:47 | 2026-08-18 12:34 | 2026-08-18 12:36 | 2026-08-18 12:39 | 2026-08-18 12:41 | 2026-08-18 12:41 | 2026-08-18 12:41 |  |  | Fair | No | Related to job #26883
Outage | J.E.26.08.27690 | C001892236 | Richman Whyte | Westmoreland | Completed | Load_292085 | Paradise - 310 | 2026-08-18 10:03 | 2026-08-18 10:05 | 2026-08-18 13:08 | 2026-08-18 13:08 | 2026-08-18 13:08 | 2026-08-18 13:08 | 2026-08-18 13:11 | 2026-08-18 13:11 | BrokenWire |  | Fair | No | Maintenance will be following up on call
Outage | J.E.26.08.27684 | C001892250 | Dwayne Cohen | KSAN | Completed | Load_262547 | Hope - 410 | 2026-08-18 10:08 | 2026-08-18 10:09 | 2026-08-18 10:46 | 2026-08-18 10:47 | 2026-08-18 13:49 | 2026-08-18 13:50 | 2026-08-18 13:50 | 2026-08-18 13:50 |  |  | Fair | No | Premises close , calls to customer went unanswered.
Outage | J.E.26.08.27716 | C001892249 | Elvis Trowers | KSAN | Completed | Load_269466 | Washington Blvd - 810 | 2026-08-18 10:08 | 2026-08-18 10:09 | 2026-08-18 10:57 | 2026-08-18 11:00 | 2026-08-18 11:02 | 2026-08-18 11:00 | 2026-08-18 11:03 | 2026-08-18 11:03 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.27622 | C001892253 | Roxroy Needham | St.Ann | Completed | Load_304932 | Cardiff Hall - 310 | 2026-08-18 10:11 | 2026-08-19 07:25 | 2026-08-19 09:03 | 2026-08-19 09:04 | 2026-08-19 10:35 | 2026-08-19 10:44 | 2026-08-19 10:46 | 2026-08-19 10:46 |  |  | Fair | No | Splice and retention customer service wire at pole use 1-1bolt clamp voltage left 113,111,224
Outage | J.E.26.08.27709 | C001892252 | Roxroy Needham | St.Ann | Completed | Load_262615 | Cardiff Hall - 310 | 2026-08-18 10:11 | 2026-08-19 07:26 | 2026-08-19 10:46 | 2026-08-19 10:47 | 2026-08-19 12:14 | 2026-08-19 12:14 | 2026-08-19 12:18 | 2026-08-19 12:18 |  |  | Fair | No | Isolate 15 KVA transformer splice and retention 1 span of secondary neutral use about 120ft of No# 2 acc conductor and 1 splicing sleeve
Outage | J.E.26.08.27678 | C001892272 | Raymond Carr | St.Mary | Completed | Load_573409 | Oracabessa - 210 | 2026-08-18 10:12 | 2026-08-18 10:23 | 2026-08-18 11:59 | 2026-08-18 12:00 | 2026-08-18 12:34 | 2026-08-18 12:27 | 2026-08-18 12:36 | 2026-08-18 12:36 |  |  | Fair | No | Customer couldn’t be contacted.
Outage | J.E.26.08.27745 | C001892302 | Junior Scarlett | St.James | Completed | Load_292127 | Bogue - 310 | 2026-08-18 10:27 | 2026-08-18 10:31 | 2026-08-18 10:43 | 2026-08-18 10:43 | 2026-08-18 11:19 | 2026-08-18 00:34 | 2026-08-18 12:36 | 2026-08-18 12:36 | Fire |  | Fair | No | Customer facing single phase Installation of 3 clampClean corrosion Voltage found 115v 0.33v 115vVoltage leave 115v 115v 230vJob completed
Outage | J.E.26.08.26012 | C001892326 | Evan Spaulding | St.Mary | Completed | Load_241132 | Annotto Bay - 310 | 2026-08-18 10:42 | 2026-08-18 10:44 | 2026-08-18 11:39 | 2026-08-18 11:39 | 2026-08-18 13:22 | 2026-08-18 14:35 | 2026-08-18 14:36 | 2026-08-18 14:36 |  |  | Fair | No | Remove bamboo from primary line and replace 1-15 amps junction fuse at pole number 005099.
Non-Outage | J.E.26.08.23887 | C001892327 | Romeo Brissett | St.James | Completed | Load_302163 | Bogue - 610 | 2026-08-18 10:44 | 2026-08-18 10:46 | 2026-08-18 17:33 | 2026-08-18 17:34 | 2026-08-18 18:03 | 2026-08-18 18:50 | 2026-08-18 18:54 | 2026-08-18 18:54 |  |  | Fair | No | Spliced and retention customer service wire, used 40ft of #6 and 3 clamps
Non-Outage | J.E.26.08.18993 | C001892333 | Shawn Medley | St.James | Completed | Load_240720 | Queens Drive - 810 | 2026-08-18 10:47 | 2026-08-18 10:48 | 2026-08-18 11:11 | 2026-08-18 11:12 | 2026-08-18 12:02 | 2026-08-18 00:03 | 2026-08-18 12:10 | 2026-08-18 12:10 | LowHangingWires |  | Fair | No | 4/0 low hanging wire to be replaced and transformer pole straighten at library , 300 ft 4/0 quad, 2- 4/0 preform,8 - 4/0 to 4/0 ampact needed to complete job ; refer to st. James maintenance
Non-Outage | J.E.26.08.14065 | C001892342 | Edward Royal | KSAN | Completed | Load_266737 | Washington Blvd - 310 | 2026-08-18 10:54 | 2026-08-18 10:55 | 2026-08-18 17:30 | 2026-08-18 17:30 | 2026-08-18 17:30 | 2026-08-18 17:30 | 2026-08-18 17:30 | 2026-08-18 17:30 |  |  | Fair | No | Call related
Outage | J.E.26.08.27736 | C001892343 | Edward Royal | KSAN | Completed | Load_293845 | Washington Blvd - 710 | 2026-08-18 10:55 | 2026-08-18 10:59 | 2026-08-18 11:41 | 2026-08-18 11:41 | 2026-08-18 11:44 | 2026-08-18 12:41 | 2026-08-18 12:43 | 2026-08-18 12:43 |  |  | Fair | No | Meter not responding meter need to be check referred to field service
Outage | J.E.26.08.27756 | C001892344 | Rusean Allen | KSAS | Completed | Load_266339 | Rockfort - 410 | 2026-08-18 10:56 | 2026-08-19 07:29 | 2026-08-19 09:22 | 2026-08-19 09:51 | 2026-08-19 09:50 | 2026-08-19 09:51 | 2026-08-19 09:51 | 2026-08-19 09:51 |  |  | Fair | No | Customer is reporting streetlight Refer to streetlight department
Non-Outage | J.E.26.08.03464 | C001892357 | Fredrick Hamilton | KSAN | Completed | Load_567704 | Washington Blvd - 310 | 2026-08-18 11:01 | 2026-08-18 11:02 | 2026-08-18 11:13 | 2026-08-18 12:31 | 2026-08-18 12:59 | 2026-08-18 13:19 | 2026-08-18 13:19 | 2026-08-18 13:19 | Over crowded pole Multiple flow cables in the way Unable to use ladder |  | Fair | No | Overcrowded pole unable to use ladder Please assign bucket truck to correct single phase at polePole #006638Multiple flow cables at pole
Non-Outage | J.E.26.08.14012 | C001892363 | Edward Royal | KSAN | Completed | Load_266737 | Washington Blvd - 310 | 2026-08-18 11:05 | 2026-08-18 11:05 | 2026-08-18 14:30 | 2026-08-18 14:30 | 2026-08-18 14:30 | 2026-08-18 17:29 | 2026-08-18 17:30 | 2026-08-18 17:30 |  |  | Fair | No | Isolated bank of 3 transformer clean up bushing Spliced and reconnected drop lead to secondary line using 5 ampack voltage reading before repair 217 230 221 107 198 110 voltage reading after repair 114 114 205 228 227 236 v busbar that link transformer together need to be change
Non-Outage | J.E.26.08.09767 | C001892367 | Oraine Minto | St.Ann | Completed | Load_256006 | Roaring River - 210 | 2026-08-18 11:06 | 2026-08-18 11:07 | 2026-08-18 12:29 | 2026-08-18 12:29 | 2026-08-18 16:50 | 2026-08-18 16:53 | 2026-08-18 16:58 | 2026-08-18 16:58 |  |  | Fair | No | Refer to maintenance Low voltage coming from the transformer Some sections of the secondary need to tension lines touching each other Transformer 25kvaPole number 0160691Customer voltage is 207v 100v 105v same voltage i got at all the houses in the street Customers are at the end of the secondary
Outage | J.E.26.08.27758 | C001892366 | Wayne Dillion | St.Elizabeth | Completed | Load_253154 | Maggotty - 210 | 2026-08-18 11:06 | 2026-08-18 11:07 | 2026-08-18 14:53 | 2026-08-18 14:53 | 2026-08-18 14:53 | 2026-08-18 14:54 | 2026-08-18 14:54 | 2026-08-18 14:54 |  |  | Fair | No | Please refer this call to the field service department for reconnection.
Outage | J.E.26.08.27767 | C001892365 | Wayne Dillion | Manchester | Completed | Load_261961 | Spur Tree - 210 | 2026-08-18 11:06 | 2026-08-18 11:07 | 2026-08-18 11:50 | 2026-08-18 11:51 | 2026-08-18 12:13 | 2026-08-18 12:26 | 2026-08-18 12:31 | 2026-08-18 12:31 |  |  | Fair | No | Supply check and found service wire broken at pole. Repair same using 1 clamp supply leave working okay reading 116v, 116v and cross phase 232volts.
Non-Outage | J.E.26.08.27696 | C001892373 | Dwain Samuels | Westmoreland | Completed | Load_257976 | Paradise - 110 | 2026-08-18 11:11 | 2026-08-18 11:12 | 2026-08-18 12:53 | 2026-08-18 13:46 | 2026-08-18 13:45 | 2026-08-18 13:46 | 2026-08-18 13:46 | 2026-08-18 13:46 |  |  | Fair | No | Customer was disconnected for none payment of electricity bill
Outage | J.E.26.08.27651 | C001892375 | Hopeton Henry | St.Thomas | Completed | Load_259566 | Good Year - 210 | 2026-08-18 11:11 | 2026-08-18 11:12 | 2026-08-18 14:11 | 2026-08-18 14:12 | 2026-08-18 14:20 | 2026-08-18 14:23 | 2026-08-18 14:23 | 2026-08-18 14:23 |  |  | Fair | No | Refer to field service
Outage | J.E.26.08.27796 | C001892374 | Derrick Grubb | St.Thomas | Completed | Load_405970 | Lysson - 410 | 2026-08-18 11:11 | 2026-08-19 08:12 | 2026-08-19 11:16 | 2026-08-19 11:17 | 2026-08-19 11:24 | 2026-08-19 11:25 | 2026-08-19 11:26 | 2026-08-19 11:26 |  |  | Fair | No | Customer query is about a high light bill, $ 21000
Outage | J.E.26.08.27802 | C001892372 | Romeo Brissett | St.James | Completed | Load_268849 | Bogue - 610 | 2026-08-18 11:11 | 2026-08-18 11:12 | 2026-08-18 12:56 | 2026-08-18 12:56 | 2026-08-18 13:48 | 2026-08-18 15:50 | 2026-08-18 16:00 | 2026-08-18 16:00 | BrokenWire |  | Fair | No | Isolated (1)15 kva transformer, spliced and retention customer 2 pole span of secondary, used 50ft of #2 and 3 clamps.
Non-Outage | J.E.26.08.27552 | C001892381 | Kenroy Dale |  | Completed |  |  | 2026-08-18 11:14 | 2026-08-18 15:14 | 2026-08-18 20:59 | 2026-08-18 20:59 | 2026-08-18 21:50 | 2026-08-18 22:09 | 2026-08-18 22:10 | 2026-08-18 22:10 |  |  | Fair | No | Supply found okay customer also confirmed that supply was restore
Outage | J.E.26.08.27632 | C001892382 | Kenroy Dale | Manchester | Completed | Load_255541 | Kendal - 210 | 2026-08-18 11:14 | 2026-08-18 15:14 | 2026-08-18 22:10 | 2026-08-18 22:13 | 2026-08-19 | 2026-08-19 | 2026-08-19 00:01 | 2026-08-19 00:01 |  |  | Fair | No | Corrosion found at pothead remade connection using 2 Penn union and 1 one bolt clamp voltage reading 112/115/227
Non-Outage | J.E.26.08.27723 | C001892383 | Kenroy Dale |  | Completed |  |  | 2026-08-18 11:15 | 2026-08-18 15:14 | 2026-08-18 15:38 | 2026-08-18 16:14 | 2026-08-18 17:16 | 2026-08-18 17:43 | 2026-08-18 17:44 | 2026-08-18 17:44 |  |  | Fair | No | Corroded neutral jumper found remade connection using 1 one bolt clamp voltage reading 113/111/224
Outage | J.E.26.08.27813 | C001892393 | Selvin White | St.Elizabeth | Completed | Load_263185 | Maggotty - 110 | 2026-08-18 11:19 | 2026-08-18 15:21 | 2026-08-18 18:01 | 2026-08-18 18:02 | 2026-08-18 18:21 | 2026-08-18 18:29 | 2026-08-18 18:30 | 2026-08-18 18:30 |  |  | Fair | No | Customer cannot be contacted however the escalation department was contacted and said supply was inactive and money was owed outstanding on the account from 2023. So please refer to Clint Johnson and Jesse Morales at the field service department.
Non-Outage | J.E.26.08.15810 | C001892401 | Richard Watson | St.Elizabeth | Completed | Load_256197 | Maggotty - 110 | 2026-08-18 11:25 | 2026-08-18 11:28 | 2026-08-18 12:51 | 2026-08-18 12:51 | 2026-08-18 13:24 | 2026-08-18 14:02 | 2026-08-18 14:08 | 2026-08-18 14:08 | BrokenWire |  | Fair | No | Splice and retention one span of broken secondary phase, use approximately 15ft of #2 aluminum one #2 preform, one #2 splicing sleeve and four 1bolt clamps, cause by severe wind, supply restored to area.
Outage | J.E.26.08.27766 | C001892424 | Richard Samuda | Manchester | Completed | Load_255183 | Spur Tree - 310 | 2026-08-18 11:40 | 2026-08-18 11:41 | 2026-08-18 12:28 | 2026-08-18 12:28 | 2026-08-18 13:42 | 2026-08-18 03:05 | 2026-08-18 15:05 | 2026-08-18 15:05 |  |  | Fair | No | Found ok voltage 115, 116 232
Outage | J.E.26.08.27705 | C001892435 | Neville Spencer | Clarendon | Completed | Load_257473 | Parnassus - 310 | 2026-08-18 11:45 | 2026-08-18 11:46 | 2026-08-18 20:35 | 2026-08-18 20:35 | 2026-08-18 22:11 | 2026-08-18 22:11 | 2026-08-18 22:12 | 2026-08-18 22:12 | LowHangingWires |  | Fair | No | Unable to locate customer.
Outage | J.E.26.08.27824 | C001892445 | Wayne Dillion | St.Elizabeth | Completed | Load_247525 | Maggotty - 210 | 2026-08-18 11:50 | 2026-08-18 11:51 | 2026-08-18 13:54 | 2026-08-18 13:54 | 2026-08-18 14:08 | 2026-08-18 14:40 | 2026-08-18 14:50 | 2026-08-18 14:50 | BrokenWire |  | Fair | No | Supply check and found two service wire neutral and one phase broken. Splice and retention same using 6ft of #6 triplex service wire and 8 linket. Supply leave working okay reading 109v, 110v and cross phase 220volts.
Outage | J.E.26.08.27830 | C001892446 | Wayne Dillion | St.Elizabeth | Completed | Load_265232 | Maggotty - 110 | 2026-08-18 11:51 | 2026-08-18 11:52 | 2026-08-18 15:00 | 2026-08-18 15:00 | 2026-08-18 15:16 | 2026-08-18 15:22 | 2026-08-18 15:24 | 2026-08-18 15:24 | LeaningPole |  | Fair | No | Patrol and found one wooden broken pole from hurricane mellisa leaning on customers meter pole. Please refer to the maintenance department to have pole removed.
Outage | J.E.26.08.27831 | C001892455 | Marlon Brown | Trelawny | Completed | Load_250266 | Greenwood - 110 | 2026-08-18 11:54 | 2026-08-18 15:49 | 2026-08-18 16:04 | 2026-08-18 16:05 | 2026-08-18 17:20 | 2026-08-18 18:07 | 2026-08-18 18:07 | 2026-08-18 18:07 | BrokenWire |  | Fair | No | Isolated 25kva transformer to repair 1 span secondary neutral, Illegal connections cause neutral to be broken. Use 10ft #2 AAC 1 pg clamp& 1 #2 preform to effect repairs Voltage found 134/100=234Voltage leaving at pothead 116/118=234v
Outage | J.E.26.08.27829 | C001892469 | Tyrese Williams | St.Ann | Completed | Load_260530 | Cardiff Hall - 210 | 2026-08-18 12:03 | 2026-08-18 12:08 | 2026-08-18 12:26 | 2026-08-18 13:12 | 2026-08-18 13:12 | 2026-08-18 13:27 | 2026-08-18 13:32 | 2026-08-18 13:32 | Fire |  | Fair | No | Premises found ok at the time of visit
Outage | J.E.26.08.27841 | C001892468 | Tyrese Williams | St.Ann | Completed | Load_248462 | Cardiff Hall - 210 | 2026-08-18 12:03 | 2026-08-18 12:08 | 2026-08-18 12:26 | 2026-08-18 13:33 | 2026-08-18 13:58 | 2026-08-18 15:13 | 2026-08-18 15:13 | 2026-08-18 15:13 |  |  | Fair | No | Remade service wire joint at pole
Non-Outage | J.E.26.08.06812 | C001892505 | Royston Montague | St.Catherine | Completed | Load_294417 | Twickenham - 210 | 2026-08-18 12:23 | 2026-08-18 12:24 | 2026-08-18 13:04 | 2026-08-18 13:08 | 2026-08-18 13:34 | 2026-08-18 14:41 | 2026-08-18 14:42 | 2026-08-18 14:42 |  |  | Fair | No | Full voltage found. 229v 114v 114v customer asked to get an electrician to check load side.
Outage | J.E.26.08.27871 | C001892500 | Selvin White | St.Elizabeth | Completed | Load_261845 | Maggotty - 210 | 2026-08-18 12:23 | 2026-08-18 15:24 | 2026-08-18 16:22 | 2026-08-18 16:26 | 2026-08-18 17:19 | 2026-08-18 17:45 | 2026-08-18 17:50 | 2026-08-18 17:50 |  |  | SevereWind | No | Supply found okay with voltage readings of 239,119,120 volts however customer has some internal problems that was resolved by a private electrician.
Outage | J.E.26.08.27866 | C001892520 | Rusean Allen | KSAS | Completed | Load_1002667 | Cane River - 410 | 2026-08-18 12:29 | 2026-08-18 12:31 | 2026-08-18 12:50 | 2026-08-18 12:51 | 2026-08-18 14:47 | 2026-08-18 16:34 | 2026-08-18 16:34 | 2026-08-18 16:34 |  |  | Fair | No | Broken primary wire found, wire was spliced retention and reconnected.1x 20amp fuse found 1x 20amp fuse replaced.1x 30amp fuse found 1x 30amp fuse replaced.1x 50amp fuse found 1x 50amp fuse replaced.
Outage | J.E.26.08.27868 | C001892531 | Barnett Brown | Manchester | Completed | Load_239382 | Kendal - 210 | 2026-08-18 12:33 | 2026-08-18 12:34 | 2026-08-18 13:17 | 2026-08-18 13:17 | 2026-08-18 14:55 | 2026-08-18 15:20 | 2026-08-18 15:20 | 2026-08-18 15:20 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.27872 | C001892530 | Kenroy Dale | Manchester | Completed | Load_268327 | Kendal - 210 | 2026-08-18 12:33 | 2026-08-18 15:14 | 2026-08-18 17:48 | 2026-08-18 17:48 | 2026-08-18 18:48 | 2026-08-18 19:20 | 2026-08-18 19:22 | 2026-08-18 19:22 |  |  | Fair | No | Burned off phase found pole remade connection using one bolt clamp voltage reading 116/116/232
Non-Outage | J.E.26.08.27876 | C001892532 | Dwain Samuels | Westmoreland | Completed | Load_268175 | Paradise - 110 | 2026-08-18 12:35 | 2026-08-18 12:37 | 2026-08-18 12:53 | 2026-08-19 12:13 | 2026-08-19 12:47 | 2026-08-19 12:54 | 2026-08-19 12:59 | 2026-08-19 12:59 | BrokenWire |  | Fair | No | Connect 3 wire meter . Use 35ft of service wire 3 one bolt clamp,3 pen union .
Non-Outage | J.E.26.08.22754 | C001892539 | Junior Scarlett | St.James | Completed | Load_259998 | Bogue - 310 | 2026-08-18 12:38 | 2026-08-18 12:39 | 2026-08-18 12:51 | 2026-08-18 12:52 | 2026-08-18 13:10 | 2026-08-18 13:18 | 2026-08-18 13:19 | 2026-08-18 13:19 |  |  | Fair | No | Refer to maintenance Incomplete workTransformers set up but not completely connected Voltage found 108v 112v 219vURGENT please assist asap
Non-Outage | J.E.26.08.21848 | C001892558 | Junior Scarlett | St.James | Completed | Load_247453 | Bogue - 310 | 2026-08-18 12:52 | 2026-08-18 12:53 | 2026-08-19 07:46 | 2026-08-19 12:57 | 2026-08-19 13:25 | 2026-08-19 14:25 | 2026-08-19 14:26 | 2026-08-19 14:26 | Fire |  | Fair | No | Check and found okIllegal connections cause voltage fluctuation in areaVoltage found 113v 112v 225v
Outage | J.E.26.08.27907 | C001892559 | Ryan Richards | Manchester | Completed | Load_1002547 | Kendal - 310 | 2026-08-18 12:56 | 2026-08-18 15:15 | 2026-08-18 15:58 | 2026-08-18 15:58 | 2026-08-18 17:08 | 2026-08-18 19:15 | 2026-08-18 19:21 | 2026-08-18 19:21 |  |  | Fair | Yes | Premises found experiencing low voltage line was checked no visible cause was found open 3#100 kva transformer turn up to transformer top 5 and reclose transformer voltage reading 120/120/240/209 volts
Non-Outage | J.E.26.08.26356 | C001892560 | Fitzroy Turner | KSAS | Completed | Load_237939 | Hunts Bay - 310 | 2026-08-18 12:57 | 2026-08-18 12:58 | 2026-08-18 13:29 | 2026-08-18 13:30 | 2026-08-18 14:01 | 2026-08-18 14:30 | 2026-08-18 14:33 | 2026-08-18 14:33 |  |  | Fair | No | Found tree phase line one switch top burnt off and one fuse blown replaced one hot line clamps and 5ft off #4 copper and one 5amps fuses.supply restored to the areas OUT FROM FRIDAY
Outage | J.E.26.08.27923 | C001892575 | Lancelot Brown | Hanover | Completed | Load_254929 | Orange Bay - 310 | 2026-08-18 13:06 | 2026-08-18 19:11 | 2026-08-18 19:20 | 2026-08-18 22:44 | 2026-08-18 23:16 | 2026-08-18 23:16 | 2026-08-18 23:17 | 2026-08-18 23:17 |  |  | Fair | No | Check and found ok supply restore
Outage | J.E.26.08.27939 | C001892600 | Dean- Smith | Hanover | Completed | Load_292847 | Orange Bay - 310 | 2026-08-18 13:34 | 2026-08-18 15:59 | 2026-08-18 18:01 | 2026-08-18 18:01 | 2026-08-18 18:01 | 2026-08-18 18:01 | 2026-08-18 18:02 | 2026-08-18 18:02 |  |  | Fair | No | Replace 50kva 5amp transformer fuse.
Outage | J.E.26.08.27977 | C001892626 | Milton Charlton | KSAN | Completed | Load_257166 | Hope - 510 | 2026-08-18 13:48 | 2026-08-19 07:33 | 2026-08-19 11:30 | 2026-08-19 11:30 | 2026-08-19 11:46 | 2026-08-19 11:20 | 2026-08-19 11:48 | 2026-08-19 11:48 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.19230 | C001892627 | Christopher Edwards | KSAN | Completed | Load_238744 | Constant Spring - 410 | 2026-08-18 13:50 | 2026-08-18 13:51 | 2026-08-18 14:07 | 2026-08-18 14:07 | 2026-08-18 14:39 | 2026-08-18 15:37 | 2026-08-18 15:37 | 2026-08-18 15:37 |  |  | Fair | No | Re-run twisted wireUsing 6 one bolt clamps 150ft #6 service wire
Outage | J.E.26.08.27989 | C001892637 | Lancelot Brown | Hanover | Completed | Load_304944 | Orange Bay - 210 | 2026-08-18 13:55 | 2026-08-18 19:11 | 2026-08-18 19:20 | 2026-08-18 22:24 | 2026-08-18 22:36 | 2026-08-18 22:39 | 2026-08-18 22:40 | 2026-08-18 22:40 | Fire |  | Fair | No | Check area no fire found
Outage | J.E.26.08.28005 | C001892736 | Ryan Richards | Manchester | Completed | Load_267209 | Spur Tree - 310 | 2026-08-18 14:32 | 2026-08-18 15:15 | 2026-08-18 19:21 | 2026-08-18 19:22 | 2026-08-18 20:10 | 2026-08-18 20:51 | 2026-08-18 20:51 | 2026-08-18 20:51 |  |  | Fair | No | Area found with supply customer that made report was unable to locate all the numbers multiple efforts made to contact customers but all went unanswered
Outage | J.E.26.08.28076 | C001892742 | Rayon Foster | Hanover | Completed | Load_292572 | Orange Bay - 310 | 2026-08-18 14:40 | 2026-08-18 14:41 | 2026-08-18 14:49 | 2026-08-18 14:49 | 2026-08-18 14:49 | 2026-08-18 15:01 | 2026-08-18 15:17 | 2026-08-18 15:17 | BrokenWire |  | Fair | No | Customer service wire was damaged by a truck and corroded use about 100ft of number 6 wire and 6 one bolt clamp at same for repairs voltage left after reconnecting 118v/119v/237v
Non-Outage | J.E.26.08.27859 | C001892760 | Roxroy Needham |  | Completed |  |  | 2026-08-18 14:58 | 2026-08-19 07:26 | 2026-08-19 08:11 | 2026-08-19 08:12 | 2026-08-19 09:02 | 2026-08-19 09:00 | 2026-08-19 09:03 | 2026-08-19 09:03 |  |  | Fair | No | Premises found ok customer say that the light is ok
Outage | J.E.26.08.27916 | C001892759 | Raymond Lewis | St.Ann | Completed | Load_258526 | Roaring River - 210 | 2026-08-18 14:58 | 2026-08-18 15:18 | 2026-08-18 18:01 | 2026-08-18 18:02 | 2026-08-18 19:25 | 2026-08-18 19:28 | 2026-08-18 19:28 | 2026-08-18 19:28 |  |  | Fair | No | Remade joint at pole 2 wire service
Outage | J.E.26.08.27870 | C001892769 | Wan Carlos Scarlett | St.Catherine | Completed | Load_263140 | Twickenham - 210 | 2026-08-18 15:02 | 2026-08-18 15:04 | 2026-08-18 19:17 | 2026-08-18 19:18 | 2026-08-18 20:12 | 2026-08-18 20:33 | 2026-08-18 20:42 | 2026-08-18 20:42 |  |  | Fair | No | Found 40 ft wooden pole with T construction 3 phase primary line and open secondary line broken by vehicle accident pole need to be change urgently no pole # was found
Outage | J.E.26.08.26905 | C001892773 | Wan Carlos Scarlett | Portmore | Completed | Load_258410 | Naggo Head - 610 | 2026-08-18 15:03 | 2026-08-18 15:04 | 2026-08-18 16:57 | 2026-08-18 20:42 | 2026-08-18 21:28 | 2026-08-18 21:55 | 2026-08-18 21:56 | 2026-08-18 21:56 |  |  | Fair | No | Found customer with internal problem advised customer to get a licensed electrician to fix the problem.meter socket defective
Outage | J.E.26.08.26963 | C001892774 | Nickolas Rodriques | St.Catherine | Completed | Load_255400 | Twickenham - 210 | 2026-08-18 15:03 | 2026-08-19 07:54 | 2026-08-19 09:55 | 2026-08-19 10:00 | 2026-08-19 10:25 | 2026-08-19 10:49 | 2026-08-19 10:50 | 2026-08-19 10:50 |  |  | Fair | No | Unable to communicate with the customer after several attempts.
Outage | J.E.26.08.27137 | C001892772 | Wan Carlos Scarlett | St.Catherine | Completed | Load_263800 | Twickenham - 210 | 2026-08-18 15:03 | 2026-08-18 15:04 | 2026-08-18 15:26 | 2026-08-18 15:26 | 2026-08-18 16:10 | 2026-08-18 16:31 | 2026-08-18 16:33 | 2026-08-18 16:33 |  |  | Fair | No | Found customer 3 wire service at pothead with phase and neutral corroded use 3 Penn union at service wire phase and neutral readings 113-114-229
Outage | J.E.26.08.27675 | C001892771 | Wan Carlos Scarlett | Portmore | Completed | Load_269627 | Naggo Head - 610 | 2026-08-18 15:03 | 2026-08-18 15:04 | 2026-08-18 21:56 | 2026-08-18 21:56 | 2026-08-19 01:43 | 2026-08-19 01:44 | 2026-08-19 01:45 | 2026-08-19 01:45 |  |  | Fair | No | Been calling customer but no answer premises closed
Outage | J.E.26.08.27803 | C001892770 | Wan Carlos Scarlett | St.Catherine | Completed | Load_244063 | Twickenham - 210 | 2026-08-18 15:03 | 2026-08-18 15:04 | 2026-08-18 15:30 | 2026-08-18 16:34 | 2026-08-18 17:16 | 2026-08-18 17:43 | 2026-08-18 17:44 | 2026-08-18 17:44 |  |  | Fair | No | Customer was reconnected from escalation department power supply has been restored
Outage | J.E.26.08.27909 | C001892777 | Kemark Slue | St.Catherine | Completed | Load_567663 | Tredegar - 310 | 2026-08-18 15:05 | 2026-08-18 15:07 | 2026-08-18 19:35 | 2026-08-18 22:42 | 2026-08-18 22:42 | 2026-08-18 19:48 | 2026-08-18 22:46 | 2026-08-18 22:46 | BrokenPole |  | Fair | No | Upon arrival at the location the crew discovered that two 30 ft cl 6 poles were set but conductors from older poles are yet to be transferred to new poles, one of the older poles is pulling on a customer’s stanchion causing damages, please refer to A. Murray to have conductors transferred asap.
Outage | J.E.26.08.27942 | C001892776 | Kemark Slue | St.Catherine | Completed | Load_556506 | Tredegar - 510 | 2026-08-18 15:05 | 2026-08-18 15:07 | 2026-08-18 19:50 | 2026-08-18 22:38 | 2026-08-18 22:37 | 2026-08-18 19:07 | 2026-08-18 22:42 | 2026-08-18 22:42 | BrokenWire |  | Fair | No | Upon arrival at the location the crew discovered that customer’s service and pothead conductors were missing, its alleged that a truck had made contact with service and ripped service and conductors from pothead out, the customer was advised to contact an licensed electrician to effectively carry out repairs and re log for connection.
Outage | J.E.26.08.28070 | C001892775 | Denton Williams | Portland | Completed | Load_349280 | Port Antonio - 410 | 2026-08-18 15:05 | 2026-08-18 15:27 | 2026-08-18 15:50 | 2026-08-18 15:51 | 2026-08-18 17:03 | 2026-08-18 17:14 | 2026-08-18 17:21 | 2026-08-18 17:21 |  |  | Fair | No | Meter was on disconnection and is now reconnected no power is going to the load, need special pulling tool to access meter socket. Refer to field service, Karl Grant
Outage | J.E.26.08.27708 | C001892781 | Kemark Slue | St.Catherine | Completed | Load_243981 | Tredegar - 310 | 2026-08-18 15:06 | 2026-08-18 15:07 | 2026-08-18 15:33 | 2026-08-18 15:34 | 2026-08-18 16:39 | 2026-08-18 17:00 | 2026-08-18 21:25 | 2026-08-18 21:25 | BrokenPole |  | Fair | No | Upon arrival at the location the crew discovered that a 15 amps junction fuse for single phase T-off was blown resulting from primary conductor making contact with telecommunications cable, splice and retention using one #2 splicing sleeve, refuse link and re-energized line section.
Outage | J.E.26.08.27867 | C001892780 | Kemark Slue | St.Catherine | Completed | Load_266625 | Tredegar - 510 | 2026-08-18 15:06 | 2026-08-18 15:07 | 2026-08-18 21:26 | 2026-08-18 22:53 | 2026-08-18 22:52 | 2026-08-18 21:40 | 2026-08-18 22:54 | 2026-08-18 22:54 | LeaningPole |  | Fair | No | Upon arrival at the location the crew discovered that premises was closed and all calls to number given were unsuccessful.
Outage | J.E.26.08.27869 | C001892779 | Kemark Slue | St.Catherine | Completed | Load_259121 | Tredegar - 510 | 2026-08-18 15:06 | 2026-08-18 15:07 | 2026-08-18 20:24 | 2026-08-18 22:48 | 2026-08-18 22:48 | 2026-08-18 20:19 | 2026-08-18 22:48 | 2026-08-18 22:48 |  |  | Fair | No | Premises was checked and found okay.
Outage | J.E.26.08.27901 | C001892778 | Kemark Slue |  | Completed | Load_575864 | Tredegar - 310 | 2026-08-18 15:06 | 2026-08-18 15:07 | 2026-08-18 15:32 | 2026-08-18 22:47 | 2026-08-18 22:47 | 2026-08-18 18:28 | 2026-08-18 22:47 | 2026-08-18 22:47 | Fire |  | Fair | No | Upon arrival at the location the crew discovered that 30 amps road junction fuse from three phases was blown, further patrol revealed that 20 amps for said line section from three phase T-off was also blown resulting from creepers that had came in contact with conductor, remove creepers, refuse links and re-energized line section.
Outage | J.E.26.08.27965 | C001892782 | Kemark Slue | St.Catherine | Completed | Load_259531 | Tredegar - 510 | 2026-08-18 15:06 | 2026-08-18 15:44 | 2026-08-18 20:20 | 2026-08-18 22:49 | 2026-08-18 22:49 | 2026-08-18 21:20 | 2026-08-18 22:52 | 2026-08-18 22:52 | BrokenPole |  | Fair | No | Upon arrival at the location the crew discovered that two 30 ft cl 6 secondary poles are 95% rotten and one broken, pole consisting of open three wire secondary and two duplex service, please refer to A. Murray to have a detailed patrol done on the line line section and change defective poles asap.
Non-Outage | J.E.26.08.27648 | C001892793 | Neckell Ormsby | St.Mary | Completed | Load_257253 | Highgate - 210 | 2026-08-18 15:08 | 2026-08-18 18:50 | 2026-08-18 20:39 | 2026-08-18 20:39 | 2026-08-18 20:39 | 2026-08-18 20:43 | 2026-08-18 20:45 | 2026-08-18 20:45 |  |  | Fair | No | Troubleshoot and found burnt joint at pot head and pole used 6- one bolt clamps to remade joints voltage left 228v 118v110v
Non-Outage | J.E.26.08.27641 | C001892800 | Cliton Henry |  | Completed |  |  | 2026-08-18 15:10 | 2026-08-18 17:55 | 2026-08-18 21:06 | 2026-08-18 21:07 | 2026-08-18 21:08 | 2026-08-18 21:09 | 2026-08-18 21:09 | 2026-08-18 21:09 |  |  | Fair | No | The supply was restored, related to outage #27968
Non-Outage | J.E.26.08.27712 | C001892798 | Raymond Carr |  | Completed |  |  | 2026-08-18 15:10 | 2026-08-19 07:32 | 2026-08-19 09:36 | 2026-08-19 09:37 | 2026-08-19 10:21 | 2026-08-19 10:06 | 2026-08-19 10:22 | 2026-08-19 10:22 |  |  | Fair | No | Customer couldn’t be contacted.
Outage | J.E.26.08.27905 | C001892799 | Cliton Henry | St.Mary | Completed | Load_270001 | Oracabessa - 110 | 2026-08-18 15:10 | 2026-08-18 15:36 | 2026-08-18 17:11 | 2026-08-18 17:12 | 2026-08-18 17:11 | 2026-08-18 17:22 | 2026-08-18 17:25 | 2026-08-18 17:25 |  |  | Fair | No | RAMI infrastructure, personnel at the property stated that the supply is ok
Outage | J.E.26.08.27968 | C001892796 | Cliton Henry | St.Mary | Completed | Load_240442 | Oracabessa - 210 | 2026-08-18 15:10 | 2026-08-18 15:36 | 2026-08-18 17:26 | 2026-08-18 17:26 | 2026-08-18 17:39 | 2026-08-18 17:52 | 2026-08-18 17:53 | 2026-08-18 17:53 |  |  | Fair | No | A blown 10 amp junction fuse found at the entrance at pole #0115796 due bird. Supply restored using 1-10 amp fuse.
Outage | J.E.26.08.27984 | C001892797 | Neckell Ormsby | St.Mary | Completed | Load_257694 | Annotto Bay - 210 | 2026-08-18 15:10 | 2026-08-18 15:12 | 2026-08-18 16:10 | 2026-08-18 16:11 | 2026-08-18 16:56 | 2026-08-18 17:09 | 2026-08-18 17:11 | 2026-08-18 17:11 |  |  | Fair | No | Pay as you go customer without supply however xing metering, please refer to field service
Outage | J.E.26.08.28120 | C001892811 | Cliton Henry | St.Mary | Completed | Load_245909 | Oracabessa - 110 | 2026-08-18 15:14 | 2026-08-18 15:34 | 2026-08-18 16:28 | 2026-08-18 16:29 | 2026-08-18 16:50 | 2026-08-18 17:02 | 2026-08-18 17:03 | 2026-08-18 17:03 | BrokenWire |  | Fair | No | The customer service wire torn down by a tractor undertaken road repairs was disconnected. The customer advised the carryout repairs and call upon completion to be reconnected.
Non-Outage | J.E.26.08.27519 | C001892813 | Kenroy Dale |  | Completed |  |  | 2026-08-18 15:16 | 2026-08-18 15:20 | 2026-08-18 19:23 | 2026-08-18 19:27 | 2026-08-18 20:47 | 2026-08-18 20:57 | 2026-08-18 20:58 | 2026-08-18 20:58 |  |  | Fair | No | Effort to contact customer multiple times was unsuccessful area visited and found with supply
Outage | J.E.26.08.28058 | C001892812 | Ryan Richards | Manchester | Completed | Load_251691 | Spur Tree - 310 | 2026-08-18 15:16 | 2026-08-18 15:20 | 2026-08-18 20:51 | 2026-08-18 20:52 | 2026-08-19 07:31 | 2026-08-19 07:33 | 2026-08-19 07:33 | 2026-08-19 07:33 | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Area found ok no fire was seen in area customer tat made report was unable to locate multiple efforts made to locate customer but unsuccessful
Outage | J.E.26.08.28028 | C001892821 | Romeo Brissett | St.James | Completed | Load_302386 | Bogue - 510 | 2026-08-18 15:18 | 2026-08-18 15:23 | 2026-08-18 16:06 | 2026-08-18 16:06 | 2026-08-18 16:54 | 2026-08-18 17:30 | 2026-08-18 17:33 | 2026-08-18 17:33 |  |  | Fair | No | Cut and removed vegetation, replaced (1)50kva transformer fuse.
Non-Outage | J.E.26.08.12970 | C001892825 | Raymond Lewis | St.Ann | Completed | Load_243679 | Roaring River - 210 | 2026-08-18 15:21 | 2026-08-18 15:23 | 2026-08-18 16:24 | 2026-08-18 16:24 | 2026-08-18 17:09 | 2026-08-18 17:13 | 2026-08-18 17:14 | 2026-08-18 17:14 |  |  | Fair | No | Low voltage on feeder preamble
Non-Outage | J.E.26.08.17361 | C001892824 | Raymond Lewis | St.Ann | Completed | Load_267348 | Roaring River - 210 | 2026-08-18 15:21 | 2026-08-18 15:23 | 2026-08-18 19:42 | 2026-08-18 19:42 | 2026-08-18 19:42 | 2026-08-18 19:43 | 2026-08-18 19:43 | 2026-08-18 19:43 |  |  | Fair | No | Phone not answering
Non-Outage | J.E.26.08.25607 | C001892823 | Raymond Lewis | St.Ann | Completed | Load_243679 | Roaring River - 210 | 2026-08-18 15:21 | 2026-08-18 15:25 | 2026-08-18 15:59 | 2026-08-18 16:00 | 2026-08-18 16:10 | 2026-08-18 17:13 | 2026-08-18 16:13 | 2026-08-18 16:13 |  |  | Fair | No | System on going problem
Non-Outage | J.E.26.08.26776 | C001892822 | Raymond Lewis | St.Ann | Completed | Load_243819 | Roaring River - 210 | 2026-08-18 15:21 | 2026-08-18 15:24 | 2026-08-18 23:53 | 2026-08-18 23:54 | 2026-08-18 23:53 | 2026-08-18 23:55 | 2026-08-18 23:55 | 2026-08-18 23:55 |  |  | Fair | No | System low voltage
Non-Outage | J.E.26.08.27694 | C001892833 | Kemark Slue | St.Catherine | Completed | Load_263607 | Tredegar - 310 | 2026-08-18 15:22 | 2026-08-18 15:23 | 2026-08-18 15:33 | 2026-08-18 21:30 | 2026-08-18 21:29 | 2026-08-18 18:43 | 2026-08-18 22:36 | 2026-08-18 22:36 |  |  | Fair | No | Upon arrival at the location the crew discovered that 30 amps road junction fuse from three phases was blown, further patrol revealed that 20 amps for said line section from three phase T-off was also blown resulting from creepers that had came in contact with conductor, remove creepers, refuse links and re-energized line section.
Non-Outage | J.E.26.07.36537 | C001892835 | Roxroy Needham | St.Ann | Completed | Load_267230 | Ocho Rios - 410 | 2026-08-18 15:25 | 2026-08-18 15:30 | 2026-08-19 09:48 | 2026-08-19 14:57 | 2026-08-19 16:27 | 2026-08-19 16:22 | 2026-08-19 16:28 | 2026-08-19 16:28 |  |  | Fair | No | Premises found ok call customer and customer say that the light is ok
Non-Outage | J.E.26.08.27539 | C001892834 | Roxroy Needham | St.Ann | Completed | Load_258385 | Cardiff Hall - 310 | 2026-08-18 15:25 | 2026-08-18 15:29 | 2026-08-18 17:58 | 2026-08-18 17:58 | 2026-08-18 18:51 | 2026-08-18 19:16 | 2026-08-18 19:17 | 2026-08-18 19:17 |  |  | Fair | No | Remake joint at pole used 1 pg clamp voltage left at meter 113-114-219
Outage | J.E.26.08.27717 | C001892836 | Swon Miller | St.James | Completed | Load_265198 | Queens Drive - 810 | 2026-08-18 15:25 | 2026-08-19 07:58 | 2026-08-19 08:08 | 2026-08-19 10:33 | 2026-08-19 11:10 | 2026-08-18 11:28 | 2026-08-19 11:31 | 2026-08-19 11:31 |  |  | Fair | No | Check and found okay customer states that the problem was resolved voltage found 116/115/232 voltage left 116/115/232
Outage | J.E.26.08.27974 | C001892837 | Swon Miller | St.James | Completed | Load_258680 | Queens Drive - 810 | 2026-08-18 15:25 | 2026-08-19 07:58 | 2026-08-19 08:08 | 2026-08-19 10:11 | 2026-08-19 10:10 | 2026-08-19 10:26 | 2026-08-19 10:32 | 2026-08-19 10:32 | BrokenWire |  | Fair | No | Found in house team onsite
Outage | J.E.26.08.26843 | C001892840 | Horace Malcolm | St.James | Completed | Load_266914 | Rose Hall - 110 | 2026-08-18 15:26 | 2026-08-18 15:28 | 2026-08-18 20:09 | 2026-08-18 20:10 | 2026-08-18 21:32 | 2026-08-18 21:46 | 2026-08-18 21:46 | 2026-08-18 21:46 |  |  | Fair | No | Check and found area ok supply restored
Outage | J.E.26.08.27972 | C001892838 | Marlon Authors | St.Elizabeth | Completed | Load_252931 | Maggotty - 210 | 2026-08-18 15:26 | 2026-08-18 15:27 | 2026-08-18 20:50 | 2026-08-18 20:50 | 2026-08-18 20:50 | 2026-08-18 20:54 | 2026-08-18 20:54 | 2026-08-18 20:54 | BrokenWire |  | Fair | No | Customer is requesting reconnection , repairs completed. Please refer same to the field services department for further assistance
Outage | J.E.26.08.28067 | C001892839 | Marlon Authors | Manchester | Completed | Load_245643 | Spur Tree - 210 | 2026-08-18 15:26 | 2026-08-18 15:27 | 2026-08-18 16:22 | 2026-08-18 16:23 | 2026-08-18 16:22 | 2026-08-18 16:26 | 2026-08-18 16:26 | 2026-08-18 16:26 |  |  | Rains | No | Customer said supply was restored
Non-Outage | J.E.26.08.28135 | C001892845 | Raymond Lewis |  | Completed |  |  | 2026-08-18 15:27 | 2026-08-18 15:28 | 2026-08-18 22:46 | 2026-08-18 22:47 | 2026-08-18 22:46 | 2026-08-18 22:47 | 2026-08-18 22:47 | 2026-08-18 22:47 | BrokenWire |  | Fair | No | Premises not found
Outage | J.E.26.08.27940 | C001892847 | Donald Cunningham | St.Catherine | Completed | Load_256419 | Rhodens Pen - 210 | 2026-08-18 15:28 | 2026-08-18 15:29 | 2026-08-18 17:47 | 2026-08-18 17:48 | 2026-08-18 19:05 | 2026-08-18 19:05 | 2026-08-18 19:06 | 2026-08-18 19:06 |  |  | Fair | No | Premises not found customer not reachable
Outage | J.E.26.08.27961 | C001892846 | Donald Cunningham | St.Catherine | Completed | Load_256382 | Tredegar - 210 | 2026-08-18 15:28 | 2026-08-18 15:29 | 2026-08-18 15:50 | 2026-08-18 15:51 | 2026-08-18 17:18 | 2026-08-18 17:41 | 2026-08-18 17:46 | 2026-08-18 17:46 |  |  | Fair | No | Blown junction fuse found and replace with 30 amp fuse
Outage | J.E.26.08.27610 | C001892852 | Horace Malcolm | St.James | Completed | Load_250024 | Bogue - 310 | 2026-08-18 15:29 | 2026-08-18 15:30 | 2026-08-18 16:00 | 2026-08-18 16:00 | 2026-08-18 16:17 | 2026-08-18 16:21 | 2026-08-18 16:21 | 2026-08-18 16:21 |  |  | Fair | No | Check and found premises ok voltage 110
Outage | J.E.26.08.27658 | C001892851 | Horace Malcolm | St.James | Completed | Load_243182 | Queens Drive - 710 | 2026-08-18 15:29 | 2026-08-18 15:30 | 2026-08-18 17:33 | 2026-08-18 17:34 | 2026-08-18 17:54 | 2026-08-18 19:20 | 2026-08-18 19:20 | 2026-08-18 19:20 | LeaningPole |  | Fair | No | Clean and remake joints at pole and reconnect customer pothead used 3clamps voltage 115-116-231
Outage | J.E.26.08.27692 | C001892850 | Donald Cunningham | St.Catherine | Completed | Load_261131 | Rhodens Pen - 410 | 2026-08-18 15:29 | 2026-08-18 15:30 | 2026-08-18 19:06 | 2026-08-18 19:06 | 2026-08-18 20:23 | 2026-08-18 20:25 | 2026-08-18 20:28 | 2026-08-18 20:28 |  |  | Fair | No | Premises closed
Outage | J.E.26.08.27754 | C001892848 | Horace Malcolm | St.James | Completed | Load_239915 | Bogue - 310 | 2026-08-18 15:29 | 2026-08-18 15:30 | 2026-08-18 19:20 | 2026-08-18 19:21 | 2026-08-18 20:01 | 2026-08-18 20:09 | 2026-08-18 20:09 | 2026-08-18 20:09 |  |  | Fair | No | Check and found premises ok voltage 115-113-228
Outage | J.E.26.08.27775 | C001892849 | Donald Cunningham | St.Catherine | Completed | Load_266643 | Tredegar - 210 | 2026-08-18 15:29 | 2026-08-18 15:29 | 2026-08-18 20:28 | 2026-08-18 20:29 | 2026-08-18 21:59 | 2026-08-18 22:00 | 2026-08-18 22:08 | 2026-08-18 22:08 |  |  | Fair | No | Supply restored in area customer not located or reachable
Non-Outage | J.E.26.08.25797 | C001892855 | Ricky Hall | St.Catherine | Completed | Load_241129 | New Michelton - 210 | 2026-08-18 15:30 | 2026-08-18 15:32 | 2026-08-18 19:04 | 2026-08-18 19:43 | 2026-08-18 19:43 | 2026-08-18 19:44 | 2026-08-18 19:44 | 2026-08-18 19:44 |  |  | Fair | No | Call associated with outage #25973
Non-Outage | J.E.26.08.25973 | C001892854 | Ricky Hall | St.Catherine | Completed | Load_241129 | New Michelton - 210 | 2026-08-18 15:30 | 2026-08-18 15:32 | 2026-08-18 18:11 | 2026-08-18 19:05 | 2026-08-18 19:34 | 2026-08-18 19:42 | 2026-08-18 19:43 | 2026-08-18 19:43 |  |  | Fair | No | Issue was resolved on previous shift
Outage | J.E.26.08.27877 | C001892853 | Ricky Hall | St.Catherine | Completed | Load_245679 | New Michelton - 210 | 2026-08-18 15:30 | 2026-08-18 15:32 | 2026-08-18 17:30 | 2026-08-18 17:42 | 2026-08-18 17:56 | 2026-08-18 18:13 | 2026-08-18 18:14 | 2026-08-18 18:14 | BrokenWire |  | Fair | Yes | Splice and reconnect 3W service use 70’ #6 triplex 3 clamps 116*2/231
Non-Outage | J.E.26.08.07264 | C001892865 | Ricky Hall | St.Catherine | Completed | Load_243987 | New Michelton - 410 | 2026-08-18 15:31 | 2026-08-18 15:32 | 2026-08-18 16:14 | 2026-08-18 16:15 | 2026-08-18 17:20 | 2026-08-18 17:27 | 2026-08-18 17:27 | 2026-08-18 17:27 |  |  | Fair | No | Customer unaware of report been made
Non-Outage | J.E.26.08.11666 | C001892861 | Ricky Hall | St.Catherine | Completed | Load_255766 | New Michelton - 210 | 2026-08-18 15:31 | 2026-08-18 15:32 | 2026-08-18 18:37 | 2026-08-18 18:37 | 2026-08-18 19:00 | 2026-08-18 19:01 | 2026-08-18 19:04 | 2026-08-18 19:04 |  |  | Fair | No | Premises not found
Non-Outage | J.E.26.08.19184 | C001892858 | Ricky Hall | St.Catherine | Completed | Load_405664 | New Michelton - 310 | 2026-08-18 15:31 | 2026-08-18 15:32 | 2026-08-18 16:14 | 2026-08-18 17:28 | 2026-08-18 17:35 | 2026-08-18 17:41 | 2026-08-18 17:41 | 2026-08-18 17:41 |  |  | Fair | No
Non-Outage | J.E.26.08.21231 | C001892857 | Ricky Hall | St.Catherine | Completed | Load_267167 | New Michelton - 210 | 2026-08-18 15:31 | 2026-08-18 15:32 | 2026-08-18 19:44 | 2026-08-18 19:45 | 2026-08-18 20:41 | 2026-08-18 20:41 | 2026-08-18 20:42 | 2026-08-18 20:42 |  |  | Fair | No | Not located insufficient information
Non-Outage | J.E.26.08.24638 | C001892856 | Ricky Hall | St.Catherine | Completed | Load_243890 | New Michelton - 210 | 2026-08-18 15:31 | 2026-08-18 15:32 | 2026-08-18 18:12 | 2026-08-18 18:16 | 2026-08-18 18:30 | 2026-08-18 18:31 | 2026-08-18 18:32 | 2026-08-18 18:32 |  |  | Fair | No | Premises not located
Non-Outage | J.E.26.08.28088 | C001892867 | Tajay Bernard |  | Completed |  |  | 2026-08-18 15:32 | 2026-08-19 11:40 | 2026-08-19 13:25 | 2026-08-19 13:25 | 2026-08-19 14:13 | 2026-08-19 15:16 | 2026-08-19 15:17 | 2026-08-19 15:17 |  |  | Fair | No | Check and found 1 25kva Transformer with no fuse barrel. A fuse barrel was found and refused and placed in the fuse holder and was close and blown immediately after, transformer seems to be defective, only one customer is affected
Outage | J.E.26.08.27566 | C001892868 | Stephen Taylor | St.Thomas | Completed | Load_249481 | Good Year - 110 | 2026-08-18 15:32 | 2026-08-18 15:34 | 2026-08-18 16:30 | 2026-08-18 16:31 | 2026-08-18 18:35 | 2026-08-18 18:38 | 2026-08-18 18:40 | 2026-08-18 18:40 |  |  | Fair | No | Patrol the area power is in area need local number to call customer
Outage | J.E.26.08.27919 | C001892869 | Stephen Taylor | St.Thomas | Completed | Load_239959 | Good Year - 210 | 2026-08-18 15:32 | 2026-08-18 15:34 | 2026-08-18 19:22 | 2026-08-18 19:23 | 2026-08-18 19:22 | 2026-08-18 19:22 | 2026-08-18 19:23 | 2026-08-18 19:23 |  |  | Fair | No | Call to customer and customer said power is back now and okay
Outage | J.E.26.08.27967 | C001892870 | Stephen Taylor | St.Thomas | Completed | Load_269237 | Good Year - 210 | 2026-08-18 15:32 | 2026-08-18 15:34 | 2026-08-18 19:02 | 2026-08-18 19:02 | 2026-08-18 19:02 | 2026-08-18 19:02 | 2026-08-18 19:04 | 2026-08-18 19:04 |  |  | Fair | No | Call to customer and customer said power is back long time and okay
Outage | J.E.26.08.28011 | C001892871 | Stephen Taylor | St.Thomas | Completed | Load_577282 | Lysson - 410 | 2026-08-18 15:32 | 2026-08-18 15:34 | 2026-08-18 15:48 | 2026-08-18 15:48 | 2026-08-18 16:02 | 2026-08-18 16:02 | 2026-08-18 16:23 | 2026-08-18 16:23 | BrokenWire |  | Fair | No | Patrol clear line and close up back 25 kva transformer safely all customer is now okay
Outage | J.E.26.08.28133 | C001892866 | Michael Paterson | Westmoreland | Completed | Load_258782 | Paradise - 110 | 2026-08-18 15:32 | 2026-08-18 15:33 | 2026-08-18 16:13 | 2026-08-18 19:09 | 2026-08-18 19:36 | 2026-08-18 19:37 | 2026-08-18 19:37 | 2026-08-18 19:37 |  |  | Fair | No | Replace burnt joint at switch bottom jumper, using one #2-#2 linket,supply restored
Outage | J.E.26.08.26922 | C001892872 | Horace Malcolm | St.James | Completed | Load_253589 | Bogue - 310 | 2026-08-18 15:34 | 2026-08-18 15:36 | 2026-08-18 16:48 | 2026-08-18 16:49 | 2026-08-18 17:13 | 2026-08-18 17:32 | 2026-08-18 17:32 | 2026-08-18 17:32 |  |  | Fair | No | Unable to locate premises from direction cannot locate meter calls to customer unavailable
Non-Outage | J.E.26.08.05184 | C001892878 | Eric Williams | KSAN | Completed | Load_249915 | Constant Spring - 410 | 2026-08-18 15:37 | 2026-08-18 15:38 | 2026-08-18 16:51 | 2026-08-18 16:51 | 2026-08-18 19:17 | 2026-08-18 21:37 | 2026-08-18 21:40 | 2026-08-18 21:40 |  |  | Fair | No | 3 wire open secondary broken neutral, wire cut and splice used 3 onebolt clamps
Outage | J.E.26.08.28104 | C001892902 | Tajay Bernard | Hanover | Completed | Load_242763 | Orange Bay - 310 | 2026-08-18 15:56 | 2026-08-19 08:37 | 2026-08-19 10:42 | 2026-08-19 10:42 | 2026-08-19 10:53 | 2026-08-19 10:53 | 2026-08-19 10:54 | 2026-08-19 10:54 |  |  | Fair | No | Premises check and found okay customer stated that the issue has been resolved
Outage | J.E.26.08.28136 | C001892911 | Rusean Allen | KSAS | Completed | Load_257594 | Rockfort - 410 | 2026-08-18 15:58 | 2026-08-19 08:19 | 2026-08-19 09:54 | 2026-08-19 09:55 | 2026-08-19 10:23 | 2026-08-19 10:33 | 2026-08-19 10:33 | 2026-08-19 10:33 | BrokenWire |  | Fair | No | Broken service wire found at pole, wire was reconnected.
Non-Outage | J.E.26.08.27734 | C001892914 | Raymond Lewis | St.Ann | Completed | Load_258244 | Ocho Rios - 310 | 2026-08-18 16:00 | 2026-08-18 16:01 | 2026-08-18 23:48 | 2026-08-18 23:49 | 2026-08-18 23:48 | 2026-08-18 23:49 | 2026-08-18 23:49 | 2026-08-18 23:49 | BrokenWire |  | Fair | No | Phone not answering
Non-Outage | J.E.26.08.27792 | C001892924 | Kemark Slue | St.Catherine | Completed | Load_575864 | Tredegar - 310 | 2026-08-18 16:02 | 2026-08-18 16:03 | 2026-08-18 17:49 | 2026-08-18 22:37 | 2026-08-18 22:36 | 2026-08-18 18:49 | 2026-08-18 22:37 | 2026-08-18 22:37 |  |  | Fair | No | Upon arrival at the location the crew discovered that 30 amps road junction fuse from three phases was blown, further patrol revealed that 20 amps for said line section from three phase T-off was also blown resulting from creepers that had came in contact with conductor, remove creepers, refuse links and re-energized line section.
Non-Outage | J.E.26.08.27405 | C001892925 | Marlon Brown |  | Completed |  |  | 2026-08-18 16:04 | 2026-08-18 16:05 | 2026-08-18 19:32 | 2026-08-18 19:32 | 2026-08-18 20:35 | 2026-08-18 20:54 | 2026-08-18 20:54 | 2026-08-18 20:54 | BrokenWire |  | Fair | No | Reconnect service wire at poleVoltage found none Voltage leaving at pothead 114/116=230v
Outage | J.E.26.08.28167 | C001892927 | Milton Charlton | KSAN | Completed | Load_253549 | Hope - 510 | 2026-08-18 16:04 | 2026-08-18 16:05 | 2026-08-18 18:53 | 2026-08-18 18:53 | 2026-08-18 19:38 | 2026-08-18 19:40 | 2026-08-18 19:40 | 2026-08-18 19:40 |  |  | Fair | No | Customer meter # 2405686 disconnected for debt.
Outage | J.E.26.08.28142 | C001892933 | Shawn Medley | St.James | Completed | Load_254158 | Bogue - 310 | 2026-08-18 16:07 | 2026-08-19 08:18 | 2026-08-19 11:41 | 2026-08-19 11:42 | 2026-08-19 12:54 | 2026-08-19 12:54 | 2026-08-19 12:55 | 2026-08-19 12:55 | BrokenWire |  | Fair | No | Unable to locate customer premises
Outage | J.E.26.08.28145 | C001892931 | Swon Miller | St.James | Completed | Load_256227 | Bogue - 310 | 2026-08-18 16:07 | 2026-08-18 16:10 | 2026-08-18 16:13 | 2026-08-18 21:14 | 2026-08-18 21:40 | 2026-08-18 09:50 | 2026-08-18 22:03 | 2026-08-18 22:03 |  |  | Fair | No | Found one span of primary conductor down one span of primary neutral down cause by tree cut on line open 1,30 amp tripsaver to carry out repairs removed tree from primary conductor and splice and retention two span of primary conductor use about 30ft#2AA conductor and splice and retention two span of primary neutral use about 15ft#2AA conductor 1#2 preform 3pg and close up 2,30 amp tripsaver no pole number available
Outage | J.E.26.08.27800 | C001892937 | Swon Miller | St.James | Completed | Load_256979 | Bogue - 310 | 2026-08-18 16:08 | 2026-08-18 16:10 | 2026-08-18 22:21 | 2026-08-18 22:21 | 2026-08-18 23:04 | 2026-08-18 23:25 | 2026-08-19 00:54 | 2026-08-19 00:54 |  |  | Fair | No | Unable to locate customer phone calls to customer number went unanswered
Outage | J.E.26.08.27906 | C001892936 | Swon Miller | St.James | Completed | Load_258380 | Bogue - 310 | 2026-08-18 16:08 | 2026-08-18 16:10 | 2026-08-18 22:08 | 2026-08-18 22:09 | 2026-08-18 22:09 | 2026-08-26 10:07 | 2026-08-18 22:14 | 2026-08-18 22:14 |  |  | Fair | No | Call related to previous
Outage | J.E.26.08.28075 | C001892935 | Swon Miller | St.James | Completed | Load_266793 | Bogue - 310 | 2026-08-18 16:08 | 2026-08-18 16:10 | 2026-08-18 21:15 | 2026-08-18 22:05 | 2026-08-18 22:05 | 2026-08-19 10:06 | 2026-08-18 22:08 | 2026-08-18 22:08 |  |  | Fair | No | Call related to previous
Outage | J.E.26.08.28086 | C001892934 | Swon Miller | St.James | Completed | Load_301663 | Bogue - 310 | 2026-08-18 16:08 | 2026-08-18 16:10 | 2026-08-18 21:04 | 2026-08-18 21:05 | 2026-08-18 21:04 | 2026-08-12 05:48 | 2026-08-18 21:14 | 2026-08-18 21:14 |  |  | Fair | No | Found one 40 amp junction fuse blown cause by tree cut on line removed tree and replace 40 amp junction fuse blown no pole number available
Non-Outage | J.E.26.07.37955 | C001892940 | Clyde Brown | Clarendon | Completed | Load_258559 | May Pen - 110 | 2026-08-18 16:09 | 2026-08-18 16:10 | 2026-08-18 18:35 | 2026-08-18 18:35 | 2026-08-18 19:01 | 2026-08-18 18:44 | 2026-08-19 07:03 | 2026-08-19 07:03 |  |  | Fair | No | Customer said he already got it sorted out by his electrician
Non-Outage | J.E.26.08.18704 | C001892938 | Clyde Brown | Clarendon | Completed | Load_269144 | May Pen - 110 | 2026-08-18 16:09 | 2026-08-18 16:10 | 2026-08-18 17:51 | 2026-08-18 17:51 | 2026-08-18 18:28 | 2026-08-18 18:23 | 2026-08-18 18:35 | 2026-08-18 18:35 |  |  | Fair | No | No cell site at Morgan’s Pass or Prospect.
Non-Outage | J.E.26.08.28074 | C001892939 | Clyde Brown | Clarendon | Completed | Load_243223 | May Pen - 110 | 2026-08-18 16:09 | 2026-08-18 16:10 | 2026-08-18 16:29 | 2026-08-18 16:30 | 2026-08-18 16:55 | 2026-08-18 17:40 | 2026-08-18 17:50 | 2026-08-18 17:50 |  |  | Fair | No | Broken secondary phase at transformer lug for 3 w primary open 25 kva transformer and replaced broken phase lead same replaced with 4ft-#2/0 ,voltage left 114/114 and 228V
Outage | J.E.26.08.27958 | C001892945 | Milton Charlton | KSAS | Completed | Load_256545 | Up Park Camp - 410 | 2026-08-18 16:15 | 2026-08-18 16:16 | 2026-08-18 16:48 | 2026-08-18 16:48 | 2026-08-18 18:48 | 2026-08-18 18:40 | 2026-08-18 18:53 | 2026-08-18 18:53 |  |  | Fair | No | Customer service wire #6 duplex corroded at pothead and pole. Repair using 3ft #6 triplex phase and two 1- bolt clamps. Reading at pole and pothead 118 volts.
Non-Outage | J.E.26.08.28159 | C001892954 | Raymond Lewis | St.Ann | Completed | Load_261997 | Ocho Rios - 310 | 2026-08-18 16:16 | 2026-08-18 16:18 | 2026-08-18 23:51 | 2026-08-18 23:51 | 2026-08-18 23:51 | 2026-08-18 23:52 | 2026-08-18 23:52 | 2026-08-18 23:52 |  |  | Fair | No | Phone not answering
Non-Outage | J.E.26.08.28180 | C001892948 | Elvis Trowers |  | Completed |  |  | 2026-08-18 16:16 | 2026-08-18 16:17 | 2026-08-18 16:22 | 2026-08-18 17:43 | 2026-08-18 19:19 | 2026-08-18 19:20 | 2026-08-18 19:48 | 2026-08-18 19:48 | LowHangingWires |  | Fair | No | Customer has an internal problem. There is about 6 customers whit there meter pole just above customer premises the meter poles leaning so the service wire hanging low to ground blocking customer premises . The service wires is on customer side the loud side. Customer advised to contact the residents to correct there wires. Entra
Outage | J.E.26.08.27874 | C001892947 | Elvis Trowers | KSAN | Completed | Load_256340 | Constant Spring - 410 | 2026-08-18 16:16 | 2026-08-18 16:17 | 2026-08-18 16:35 | 2026-08-18 16:36 | 2026-08-18 17:41 | 2026-08-18 17:45 | 2026-08-18 17:43 | 2026-08-18 17:43 |  |  | Fair | No | Found okay upon arrival. Customer has an internal problem customer meter socket Is defective. Readings at meter socket 108-110-219 volts.
Outage | J.E.26.08.28129 | C001892946 | Elvis Trowers | KSAN | Completed | Load_254366 | Constant Spring - 210 | 2026-08-18 16:16 | 2026-08-18 16:17 | 2026-08-18 19:49 | 2026-08-18 19:51 | 2026-08-18 20:00 | 2026-08-18 20:05 | 2026-08-18 20:02 | 2026-08-18 20:02 | TreeContact |  | Fair | No | Unable to locate customer by telephone. The telephone number on the report going straight to voicemail.
Outage | J.E.26.08.28189 | C001892967 | Lancelot Brown | Hanover | Completed | Load_252846 | Orange Bay - 210 | 2026-08-18 16:31 | 2026-08-18 19:11 | 2026-08-18 19:20 | 2026-08-18 22:20 | 2026-08-18 22:20 | 2026-08-18 22:21 | 2026-08-18 22:21 | 2026-08-18 22:21 | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | This call related to bank of 100 and 50kva supply restore
Outage | J.E.26.08.28192 | C001892966 | Lancelot Brown | Hanover | Completed | Load_303169 | Orange Bay - 210 | 2026-08-18 16:31 | 2026-08-18 19:11 | 2026-08-18 19:20 | 2026-08-18 21:51 | 2026-08-18 21:59 | 2026-08-18 22:19 | 2026-08-18 22:19 | 2026-08-18 22:19 | Fire |  | Fair | No | Found bank of 1-100 and 1-50kva 100kva fuse blown and 50kva fuse dislodge 100kva leaking oil carry out test closed at bank replace 1-5amps fuse at 100kva also closed 50kva supply restore no fire seen after carry out test closed supply restore
Non-Outage | J.E.26.08.28177 | C001892977 | Denton Williams |  | Completed |  |  | 2026-08-18 16:33 | 2026-08-18 16:34 | 2026-08-18 17:24 | 2026-08-18 17:30 | 2026-08-18 17:30 | 2026-08-18 18:17 | 2026-08-18 18:18 | 2026-08-18 18:18 | Fire |  | Fair | No | Premises found ok, no sparks observed.
Outage | J.E.26.08.28140 | C001892978 | Raymond Lewis | St.Ann | Completed | Load_261997 | Ocho Rios - 310 | 2026-08-18 16:35 | 2026-08-18 16:36 | 2026-08-18 22:48 | 2026-08-18 22:48 | 2026-08-18 23:45 | 2026-08-18 23:46 | 2026-08-18 23:46 | 2026-08-18 23:46 |  |  | Fair | No | Remade joint at pole 3 wire service
Outage | J.E.26.08.28168 | C001892984 | Javid Vernon | Westmoreland | Completed | Load_292366 | Paradise - 210 | 2026-08-18 16:37 | 2026-08-19 07:46 | 2026-08-19 08:09 | 2026-08-19 08:10 | 2026-08-19 09:03 | 2026-08-19 09:30 | 2026-08-19 09:30 | 2026-08-19 09:30 |  |  | Fair | No | Reconnect customer burnt off service wire use two clamps it was cause due to illegal connections on customer pothead voltage found and left 110/111/221
Outage | J.E.26.08.28246 | C001893001 | Raymond Lewis | St.Ann | Completed | Load_247248 | Roaring River - 210 | 2026-08-18 17:05 | 2026-08-18 17:05 | 2026-08-18 17:44 | 2026-08-18 17:44 | 2026-08-18 17:44 | 2026-08-18 17:58 | 2026-08-18 18:00 | 2026-08-18 18:00 |  |  | Fair | No | Replace burn up fuse holder for 25 kva x former
Non-Outage | J.E.26.08.27944 | C001893003 | Michael Paterson | Westmoreland | Completed | Load_242476 | Paradise - 210 | 2026-08-18 17:12 | 2026-08-18 17:13 | 2026-08-18 19:42 | 2026-08-18 19:42 | 2026-08-18 20:06 | 2026-08-18 22:11 | 2026-08-18 22:11 | 2026-08-18 22:11 |  |  | Fair | No | Star star bank at location, three 100kva xfmr, found one fuse blown, due undersized, replace 3amps with 10amp fuse, supply restored, customer was complaint of high voltage, had to isolate transformer and tap down xfmr from tap three to two, supply restored, voltage currently 248v, 233v, 238v, 419v, 428v, 397v. Customer confirm ok.
Outage | J.E.26.08.28202 | C001893015 | Neckell Ormsby | St.Mary | Completed | Load_268134 | Highgate -110 | 2026-08-18 17:49 | 2026-08-18 17:49 | 2026-08-18 20:49 | 2026-08-18 20:50 | 2026-08-18 21:37 | 2026-08-18 22:25 | 2026-08-18 22:26 | 2026-08-18 22:26 |  |  | Fair | No | Found transformer fuse blown and tree on secondary, cut and remove tree, retention 2- pole span secondary phase and neutral using 3- #2 preform and replace 1-3 amp fuse for 25 kva transformer
Outage | J.E.26.08.27952 | C001893016 | Evan Spaulding | St.Mary | Completed | Load_251815 | Annotto Bay - 210 | 2026-08-18 17:50 | 2026-08-19 07:31 | 2026-08-19 08:15 | 2026-08-19 08:15 | 2026-08-19 08:56 | 2026-08-19 09:14 | 2026-08-19 09:15 | 2026-08-19 09:15 |  |  | Fair | No | Use 2-1 bolt clamps at pole, voltage left 115,114v,229v.
Non-Outage | J.E.26.08.28100 | C001893017 | Cliton Henry |  | Completed |  |  | 2026-08-18 17:51 | 2026-08-18 17:52 | 2026-08-18 19:54 | 2026-08-18 19:55 | 2026-08-18 21:02 | 2026-08-18 21:05 | 2026-08-18 21:06 | 2026-08-18 21:06 |  |  | Fair | No | The customer was disconnected for debt however was reconnected
Outage | J.E.26.08.28302 | C001893018 | Raymond Carr | St.Mary | Completed | Load_246448 | Oracabessa - 210 | 2026-08-18 17:52 | 2026-08-19 07:28 | 2026-08-19 10:22 | 2026-08-19 10:22 | 2026-08-19 11:32 | 2026-08-19 11:45 | 2026-08-19 11:49 | 2026-08-19 11:49 |  |  | Fair | No | Voltage readings 119/118/237. Customer was advised to replace defective meter socket.
Outage | J.E.26.08.28247 | C001893019 | Marlon Authors | Manchester | Completed | Load_242344 | Spur Tree - 210 | 2026-08-18 17:56 | 2026-08-18 17:59 | 2026-08-18 18:47 | 2026-08-18 18:48 | 2026-08-18 18:47 | 2026-08-18 17:53 | 2026-08-18 18:53 | 2026-08-18 18:53 |  |  | Fair | No | Customer said supply was restored
Outage | J.E.26.08.28276 | C001893020 | Michael Paterson | St.Elizabeth | Completed | Load_257518 | Maggotty - 110 | 2026-08-18 17:56 | 2026-08-18 17:59 | 2026-08-18 19:38 | 2026-08-18 19:38 | 2026-08-18 19:38 | 2026-08-18 19:38 | 2026-08-18 19:39 | 2026-08-18 19:39 |  |  | Fair | No | St.Elizabeth call.
Outage | J.E.26.08.28266 | C001893021 | Javid Vernon | Westmoreland | Completed | Load_570234 | Paradise - 110 | 2026-08-18 17:57 | 2026-08-19 07:46 | 2026-08-19 09:36 | 2026-08-19 09:36 | 2026-08-19 09:36 | 2026-08-19 09:36 | 2026-08-19 09:40 | 2026-08-19 09:40 |  |  | Fair | No | Unable to locate customer and premises phone call to customer number went unanswered and no directions was given
Outage | J.E.26.08.28190 | C001893022 | Horace Malcolm | St.James | Completed | Load_269279 | Bogue - 310 | 2026-08-18 17:58 | 2026-08-18 18:02 | 2026-08-18 21:47 | 2026-08-18 21:47 | 2026-08-18 22:37 | 2026-08-18 22:56 | 2026-08-18 22:56 | 2026-08-18 22:56 | BrokenWire |  | Fair | No | Unable to locate premises from direction give multiple calls unanswered from customer
Outage | J.E.26.08.28310 | C001893034 | Cliton Henry | St.Mary | Completed | Load_245909 | Oracabessa - 110 | 2026-08-18 18:35 | 2026-08-18 18:36 | 2026-08-18 21:12 | 2026-08-18 21:13 | 2026-08-18 22:13 | 2026-08-18 22:35 | 2026-08-18 22:35 | 2026-08-18 22:35 |  |  | Fair | No | The customer service wire was reconnected using 3 on bolt clamps. Voltages left 118-118/236 volts
Outage | J.E.26.08.28331 | C001893037 | Evan Spaulding | St.Mary | Completed | Load_241639 | Highgate - 210 | 2026-08-18 18:37 | 2026-08-19 07:31 | 2026-08-19 08:13 | 2026-08-19 08:13 | 2026-08-19 08:13 | 2026-08-19 08:13 | 2026-08-19 08:14 | 2026-08-19 08:14 |  |  | Fair | No | Customer says he didn’t make any report to JPS.
Outage | J.E.26.08.28337 | C001893043 | Edward Royal | KSAS | Completed | Load_239591 | Cane River - 610 | 2026-08-18 18:53 | 2026-08-18 18:54 | 2026-08-18 19:31 | 2026-08-18 19:32 | 2026-08-18 19:31 | 2026-08-18 22:32 | 2026-08-18 22:32 | 2026-08-18 22:32 | Fire |  | Fair | No | Defective junction switch need to be changed reffered to live line crew replaced 2 15A junction fuse wash salt from transformer insulator
Outage | J.E.26.08.28384 | C001893045 | Neckell Ormsby | St.Mary | Completed | Load_257253 | Highgate - 210 | 2026-08-18 19:01 | 2026-08-18 19:02 | 2026-08-18 20:45 | 2026-08-18 20:46 | 2026-08-18 20:46 | 2026-08-18 20:48 | 2026-08-18 20:49 | 2026-08-18 20:49 |  |  | Fair | No | Related to previous white road call
Outage | J.E.26.08.28359 | C001893048 | Roxroy Needham | St.Ann | Completed | Load_269163 | Cardiff Hall - 210 | 2026-08-18 19:02 | 2026-08-18 19:04 | 2026-08-18 19:18 | 2026-08-18 19:19 | 2026-08-18 20:36 | 2026-08-18 21:30 | 2026-08-18 21:28 | 2026-08-18 21:28 |  | Y | Fair | No | Retention 2 span of neural and replace a 10 amps junction fuse at pole
Outage | J.E.26.08.28383 | C001893046 | Denton Williams | Portland | Completed | Load_246238 | Port Antonio - 410 | 2026-08-18 19:02 | 2026-08-18 19:03 | 2026-08-18 19:29 | 2026-08-18 19:29 | 2026-08-18 20:02 | 2026-08-20 01:00 | 2026-08-18 20:33 | 2026-08-18 20:33 | Fire |  | Fair | No | Replace one corroded clamp on pole, 117/116/233 volts
Outage | J.E.26.08.28413 | C001893047 | Roxroy Needham | St.Ann | Completed | Load_240306 | Cardiff Hall - 310 | 2026-08-18 19:02 | 2026-08-18 19:03 | 2026-08-18 20:00 | 2026-08-18 22:10 | 2026-08-18 22:21 | 2026-08-18 22:26 | 2026-08-18 22:27 | 2026-08-18 22:27 |  |  | Fair | No | Meter found disconnect for bill
Outage | J.E.26.08.28253 | C001893049 | Roxroy Needham | St.Ann | Completed | Load_256510 | Cardiff Hall - 210 | 2026-08-18 19:03 | 2026-08-18 19:04 | 2026-08-18 20:02 | 2026-08-18 22:28 | 2026-08-18 22:56 | 2026-08-18 22:58 | 2026-08-18 22:59 | 2026-08-18 22:59 |  |  | Fair | No | Customer have next customer meter needs field service to check meter
Outage | J.E.26.08.28416 | C001893055 | Lancelot Brown | Hanover | Completed | Load_303135 | Orange Bay - 210 | 2026-08-18 19:11 | 2026-08-18 19:12 | 2026-08-18 19:20 | 2026-08-18 21:49 | 2026-08-18 21:48 | 2026-08-18 21:49 | 2026-08-18 21:49 | 2026-08-18 21:49 |  |  | Fair | No | This call related to 10amps 15ampsand 20amps junction fuse supply restore
Outage | J.E.26.08.28420 | C001893054 | Lancelot Brown | Hanover | Completed | Load_260650 | Orange Bay - 210 | 2026-08-18 19:11 | 2026-08-18 19:12 | 2026-08-18 19:20 | 2026-08-18 19:48 | 2026-08-18 20:50 | 2026-08-18 21:47 | 2026-08-18 21:48 | 2026-08-18 21:48 |  |  | Fair | No | Found junction fuse blown patroll found bird tangle with led from lower part of switch to transformer bushing removed bird from transformer replace 1-20amps1-15amps also1-10amps junction fuse no pole number supply restore
Outage | J.E.26.08.28429 | C001893061 | Raymond Lewis | St.Ann | Completed | Load_238563 | Roaring River - 210 | 2026-08-18 19:25 | 2026-08-18 19:31 | 2026-08-18 19:43 | 2026-08-18 19:44 | 2026-08-18 22:37 | 2026-08-18 22:42 | 2026-08-18 22:43 | 2026-08-18 22:43 |  |  | Fair | No | System down unbelievable to reconnect box
Non-Outage | J.E.26.08.28464 | C001893069 | Romeo Brissett |  | Completed |  |  | 2026-08-18 19:43 | 2026-08-18 23:46 | 2026-08-19 01:54 | 2026-08-19 01:55 | 2026-08-19 01:54 | 2026-08-19 00:48 | 2026-08-19 01:59 | 2026-08-19 01:59 | Fire |  | Fair | No | Check and found customer disconnected from out of the HEX box, please send to field service. Escalation was contacted and stated that there’s an ongoing issue with HEX boxes.
Outage | J.E.26.08.28205 | C001893070 | Elvis Trowers | KSAS | Completed | Load_264225 | Duhaney - 310 | 2026-08-18 19:46 | 2026-08-18 19:46 | 2026-08-18 20:28 | 2026-08-18 20:29 | 2026-08-18 21:45 | 2026-08-18 21:45 | 2026-08-18 21:47 | 2026-08-18 21:47 |  |  | Fair | No | Found okay customer states matter was resolved.
Outage | J.E.26.08.28404 | C001893071 | Elvis Trowers | KSAN | Completed | Load_248696 | West Kings House - 410 | 2026-08-18 19:46 | 2026-08-18 19:46 | 2026-08-18 20:03 | 2026-08-18 20:04 | 2026-08-18 20:25 | 2026-08-18 20:30 | 2026-08-18 20:28 | 2026-08-18 20:28 |  |  | Fair | No | Customer meter #2399259 was disconnected for debt .
Outage | J.E.26.08.28462 | C001893074 | Roxroy Needham | St.Ann | Completed | Load_253129 | Cardiff Hall - 310 | 2026-08-18 19:50 | 2026-08-19 07:24 | 2026-08-19 13:40 | 2026-08-19 13:40 | 2026-08-19 14:53 | 2026-08-19 02:38 | 2026-08-19 14:56 | 2026-08-19 14:56 |  |  | Fair | No | Resident say light was back
Outage | J.E.26.08.28412 | C001893078 | Raymond Lewis | St.Ann | Completed | Load_248710 | Roaring River - 210 | 2026-08-18 19:57 | 2026-08-18 19:58 | 2026-08-18 22:43 | 2026-08-18 22:44 | 2026-08-18 22:43 | 2026-08-18 22:44 | 2026-08-18 22:44 | 2026-08-18 22:44 |  |  | Fair | No | System down
Non-Outage | J.E.26.08.28329 | C001893093 | Lancelot Brown |  | Completed |  |  | 2026-08-18 20:17 | 2026-08-18 20:18 | 2026-08-18 23:17 | 2026-08-18 23:19 | 2026-08-18 23:18 | 2026-08-18 23:20 | 2026-08-18 23:21 | 2026-08-18 23:21 |  |  | Fair | No | This call related to bank of 100 and-50kva supply restore
Non-Outage | J.E.26.08.28435 | C001893092 | Javid Vernon |  | Completed |  |  | 2026-08-18 20:17 | 2026-08-18 20:18 | 2026-08-18 20:26 | 2026-08-18 20:26 | 2026-08-18 21:01 | 2026-08-18 21:06 | 2026-08-18 21:06 | 2026-08-18 21:06 |  |  | Fair | No | Premises check okay customer stated that power was restored
Outage | J.E.26.08.28393 | C001893091 | Javid Vernon | Westmoreland | Completed | Load_249479 | Paradise - 310 | 2026-08-18 20:17 | 2026-08-18 20:18 | 2026-08-18 21:06 | 2026-08-18 21:06 | 2026-08-18 21:06 | 2026-08-18 21:08 | 2026-08-18 21:08 | 2026-08-18 21:08 |  |  | Fair | No | Customer stated that premises is closed and we won’t be able to access premises until Tomorrow when he is there
Outage | J.E.26.08.28481 | C001893095 | Raymond Lewis | St.Ann | Completed | Load_258077 | Cardiff Hall - 310 | 2026-08-18 20:26 | 2026-08-18 22:55 | 2026-08-19 00:03 | 2026-08-19 00:04 | 2026-08-19 01:12 | 2026-08-19 13:15 | 2026-08-19 01:16 | 2026-08-19 01:16 |  |  | Fair | No | Phone not answering
Outage | J.E.26.08.28483 | C001893097 | Roxroy Needham | St.Ann | Completed | Load_269329 | Cardiff Hall - 210 | 2026-08-18 20:26 | 2026-08-18 20:28 | 2026-08-18 20:33 | 2026-08-18 21:29 | 2026-08-18 22:02 | 2026-08-18 22:08 | 2026-08-18 22:09 | 2026-08-18 22:09 |  |  | Fair | No | Customer get disconnect for bill
Outage | J.E.26.08.28509 | C001893098 | Marlon Authors | St.Elizabeth | Completed | Load_292577 | Maggotty - 210 | 2026-08-18 20:34 | 2026-08-18 20:38 | 2026-08-18 21:18 | 2026-08-18 21:19 | 2026-08-18 22:05 | 2026-08-18 10:47 | 2026-08-18 22:47 | 2026-08-18 22:47 |  |  | Fair | No | Patrol and found tree putting the secondary conductors together whenever the wind blows. Cut and remove same, retention one pole span of secondary neutral and replace one blown 2 amp fuse that protects 25 kva transformer circuit at pole #043724. Restored supply okay
Outage | J.E.26.08.28489 | C001893100 | Elvis Trowers | KSAN | Completed | Load_256666 | Washington Blvd - 710 | 2026-08-18 20:48 | 2026-08-18 21:34 | 2026-08-18 21:52 | 2026-08-18 21:52 | 2026-08-19 | 2026-08-19 | 2026-08-19 00:03 | 2026-08-19 00:03 | Fire |  | Fair | No | Isolate 100 kva transformer at pole #0020671 and repair open wire secondary phase and neutral come together and burned off . Splice and retention using 60ft #2AA conductor and six 1- bolt clamps. Reclose 100 kva transformer switch.
Outage | J.E.26.08.28508 | C001893099 | Elvis Trowers | KSAN | Completed | Load_267231 | Washington Blvd - 710 | 2026-08-18 20:48 | 2026-08-18 21:34 | 2026-08-19 00:03 | 2026-08-19 00:04 | 2026-08-19 00:03 | 2026-08-19 00:05 | 2026-08-19 00:04 | 2026-08-19 00:04 | Fire |  | Fair | No | Call related to call at 3 Sandy Lane.
Outage | J.E.26.08.28526 | C001893101 | Raymond Lewis | St.Ann | Completed | Load_242702 | Ocho Rios - 310 | 2026-08-18 20:55 | 2026-08-18 20:56 | 2026-08-19 01:17 | 2026-08-19 01:17 | 2026-08-19 02:11 | 2026-08-19 14:13 | 2026-08-19 02:14 | 2026-08-19 02:14 | Fire |  | Fair | No | Remove cable wire from secondary
Non-Outage | J.E.26.08.28279 | C001893102 | Andrae Clarke | Portland | Completed | Load_263694 | Port Antonio - 310 | 2026-08-18 20:58 | 2026-08-19 07:34 | 2026-08-19 08:28 | 2026-08-19 08:29 | 2026-08-19 09:21 | 2026-08-19 09:23 | 2026-08-19 09:23 | 2026-08-19 09:23 |  |  | Fair | No | Check voltage 119/121/240Premises found okay
Non-Outage | J.E.26.08.28517 | C001893105 | Marlon Brown |  | Completed |  |  | 2026-08-18 21:07 | 2026-08-18 21:12 | 2026-08-18 21:44 | 2026-08-18 21:44 | 2026-08-18 22:01 | 2026-08-18 22:49 | 2026-08-18 22:49 | 2026-08-18 22:49 | Fire |  | Fair | No | Ampac joint burning out at the line side of LAB 6-594. Refer to maintenance personnel.
Non-Outage | J.E.26.08.28553 | C001893123 | Marlon Authors |  | Completed |  |  | 2026-08-18 21:29 | 2026-08-18 21:31 | 2026-08-19 00:21 | 2026-08-19 00:22 | 2026-08-19 00:21 | 2026-08-19 00:23 | 2026-08-19 00:23 | 2026-08-19 00:23 | Fire |  | Fair | No | Supply restored to the area
Outage | J.E.26.08.28554 | C001893124 | Marlon Authors | St.Elizabeth | Completed | Load_253154 | Maggotty - 210 | 2026-08-18 21:30 | 2026-08-18 21:31 | 2026-08-18 22:51 | 2026-08-18 22:52 | 2026-08-19 00:13 | 2026-08-19 00:20 | 2026-08-19 00:21 | 2026-08-19 00:21 |  |  | Fair | No | Patrol and found clear. Replace one blown 2 amp fuse that protects 25 kva transformer circuit no pole #. Restored supply okay
Outage | J.E.26.08.28555 | C001893125 | Richard Watson | St.Elizabeth | Completed | Load_238577 | Maggotty - 210 | 2026-08-18 21:30 | 2026-08-19 07:35 | 2026-08-19 10:51 | 2026-08-19 10:52 | 2026-08-19 12:59 | 2026-08-19 13:58 | 2026-08-19 14:17 | 2026-08-19 14:17 | Fire |  | Fair | No | De-energize and isolate 10kva transformer on both primary and secondary Leeds, in order to replace defective lightning arrester and defective 1bolt clamp connected to ground leed, transformer re-energized and supply restored.
Non-Outage | J.E.26.08.28231 | C001893126 | Andrae Clarke | Portland | Completed | Load_249256 | Port Antonio - 410 | 2026-08-18 21:35 | 2026-08-19 07:34 | 2026-08-19 09:39 | 2026-08-19 09:40 | 2026-08-19 09:57 | 2026-08-19 10:33 | 2026-08-19 10:48 | 2026-08-19 10:48 |  |  | Fair | No | Check wires and tighten wires using three one bolt clamp Check voltage 121/119/240
Non-Outage | J.E.26.08.27085 | C001893128 | Elvis Trowers | KSAN | Completed | Load_248139 | Constant Spring - 210 | 2026-08-18 21:45 | 2026-08-18 21:46 | 2026-08-19 08:24 | 2026-08-19 08:25 | 2026-08-19 09:19 | 2026-08-19 09:20 | 2026-08-19 09:25 | 2026-08-19 09:25 |  |  | Fair | No | Premises closed. Customer states they won’t be home until next week.
Outage | J.E.26.08.28550 | C001893130 | Hartley Chin | Clarendon | Completed | Load_261428 | May Pen - 210 | 2026-08-18 22:06 | 2026-08-19 07:33 | 2026-08-19 10:32 | 2026-08-19 10:38 | 2026-08-19 10:38 | 2026-08-19 10:38 | 2026-08-19 10:39 | 2026-08-19 10:39 |  |  | Fair | No | Call related to job # 28556 ..
Outage | J.E.26.08.28166 | C001893132 | Hartley Chin | Clarendon | Completed | Load_258999 | Monymusk - 410 | 2026-08-18 22:07 | 2026-08-19 07:33 | 2026-08-19 12:57 | 2026-08-19 12:58 | 2026-08-19 14:44 | 2026-08-19 15:29 | 2026-08-19 15:49 | 2026-08-19 15:49 |  |  | Fair | No | Isolate 25KVA transformer (no pole #) due to broken open secondary phase found , repair broken joint , re-energized transformer…use 2 clamp , 10 ft #2 Conductor..
Outage | J.E.26.08.28548 | C001893131 | Hartley Chin | Clarendon | Completed | Load_237662 | Parnassus - 210 | 2026-08-18 22:07 | 2026-08-19 07:33 | 2026-08-19 15:27 | 2026-08-19 15:49 | 2026-08-19 16:02 | 2026-08-19 16:03 | 2026-08-19 16:04 | 2026-08-19 16:04 |  |  | Fair | No | Premisis not found. Unable to contact customer with the number provided.
Outage | J.E.26.08.28567 | C001893145 | Romeo Brissett | St.James | Completed | Load_249364 | Rose Hall - 210 | 2026-08-18 23:42 | 2026-08-18 23:43 | 2026-08-19 01:53 | 2026-08-19 01:53 | 2026-08-19 01:53 | 2026-08-19 01:44 | 2026-08-19 01:54 | 2026-08-19 01:54 |  |  | Fair | No | Check and found ok
Outage | J.E.26.08.28568 | C001893146 | Romeo Brissett | St.James | Completed | Load_263074 | Rose Hall - 210 | 2026-08-18 23:42 | 2026-08-18 23:43 | 2026-08-18 23:47 | 2026-08-18 23:48 | 2026-08-19 01:17 | 2026-08-19 01:40 | 2026-08-19 01:52 | 2026-08-19 01:52 |  |  | Fair | No | Replaced (1)15amps junction fuse
Outage | J.E.26.08.28172 | C001893149 | Delano Gayle | Portmore | Completed | Load_266484 | Naggo Head - 610 | 2026-08-19 00:04 | 2026-08-19 00:04 | 2026-08-19 00:17 | 2026-08-19 00:35 | 2026-08-19 01:14 | 2026-08-19 01:25 | 2026-08-19 01:25 | 2026-08-19 01:25 | Fire |  | Fair | No | Premises not found, area patrolled and found okay no fire seen
Outage | J.E.26.08.26973 | C001893194 | Collin Robinson | Portland | Completed | Load_263415 | Port Antonio - 410 | 2026-08-19 07:14 | 2026-08-19 07:33 | 2026-08-19 07:40 | 2026-08-19 07:40 | 2026-08-19 08:00 | 2026-08-19 08:02 | 2026-08-19 08:03 | 2026-08-19 08:03 |  |  | Fair | No | Information received from customer that issue was resolved
Outage | J.E.26.08.27949 | C001893249 | Derrick Grubb | St.Thomas | Completed | Load_238731 | Good Year - 210 | 2026-08-19 07:22 | 2026-08-19 07:24 | 2026-08-19 10:06 | 2026-08-19 10:07 | 2026-08-19 10:06 | 2026-08-19 10:07 | 2026-08-19 10:07 | 2026-08-19 10:07 |  |  | Fair | No | Premises found ok, customer was contacted by cellphone
Outage | J.E.26.08.28486 | C001893248 | Derrick Grubb | St.Thomas | Completed | Load_248744 | Good Year - 210 | 2026-08-19 07:22 | 2026-08-19 07:23 | 2026-08-19 08:24 | 2026-08-19 08:25 | 2026-08-19 09:20 | 2026-08-19 10:06 | 2026-08-19 10:06 | 2026-08-19 10:06 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.28638 | C001893247 | Derrick Grubb | St.Thomas | Completed | Load_243941 | Good Year - 110 | 2026-08-19 07:22 | 2026-08-19 07:23 | 2026-08-19 07:29 | 2026-08-19 07:29 | 2026-08-19 07:51 | 2026-08-19 08:21 | 2026-08-19 08:22 | 2026-08-19 08:22 | Fire |  | Fair | No | Splice and retention one span open secondary phase , refuse a 25 kva transformer in seaforth
Outage | J.E.26.08.27969 | C001893258 | Rusean Allen | KSAS | Completed | Load_574068 | Cane River - 410 | 2026-08-19 07:27 | 2026-08-19 07:28 | 2026-08-19 10:33 | 2026-08-19 10:34 | 2026-08-19 10:48 | 2026-08-19 10:49 | 2026-08-19 10:49 | 2026-08-19 10:49 |  |  | Fair | No | Premises inaccessible due to vehicle blockage
Outage | J.E.26.08.28395 | C001893257 | Rusean Allen | KSAS | Completed | Load_245749 | Rockfort - 210 | 2026-08-19 07:27 | 2026-08-19 07:28 | 2026-08-19 09:27 | 2026-08-19 09:52 | 2026-08-19 09:51 | 2026-08-19 09:52 | 2026-08-19 09:52 | 2026-08-19 09:52 |  |  | Fair | No | Found okay
Outage | J.E.26.08.28591 | C001893255 | Rusean Allen | KSAS | Completed | Load_301317 | Hunts Bay - 410 | 2026-08-19 07:27 | 2026-08-19 07:28 | 2026-08-19 09:19 | 2026-08-19 09:22 | 2026-08-19 09:50 | 2026-08-19 09:50 | 2026-08-19 09:50 | 2026-08-19 09:50 |  |  | Fair | No
Outage | J.E.26.08.28594 | C001893256 | Rusean Allen | KSAS | Completed | Load_244500 | Greenwich - 410 | 2026-08-19 07:27 | 2026-08-19 07:28 | 2026-08-19 08:54 | 2026-08-19 08:55 | 2026-08-19 09:19 | 2026-08-19 09:19 | 2026-08-19 09:19 | 2026-08-19 09:19 |  |  | Fair | No
Outage | J.E.26.08.27400 | C001893269 | Raymond Carr | St.Ann | Completed | Load_238296 | Upper White River - 210 | 2026-08-19 07:31 | 2026-08-19 07:33 | 2026-08-19 09:13 | 2026-08-19 09:13 | 2026-08-19 09:34 | 2026-08-19 09:27 | 2026-08-19 09:35 | 2026-08-19 09:35 |  |  | Fair | No | Several calls to contact number went unanswered.
Outage | J.E.26.08.28584 | C001893270 | Raymond Carr | St.Ann | Completed | Load_258217 | Upper White River - 210 | 2026-08-19 07:31 | 2026-08-19 07:33 | 2026-08-19 07:47 | 2026-08-19 07:47 | 2026-08-19 09:11 | 2026-08-19 09:00 | 2026-08-19 09:12 | 2026-08-19 09:12 |  |  | Fair | No | Customer reported that supply was restored yesterday.
Outage | J.E.26.08.28601 | C001893261 | Milton Charlton | KSAN | Completed | Load_260762 | West Kings House - 410 | 2026-08-19 07:31 | 2026-08-19 07:34 | 2026-08-19 09:10 | 2026-08-19 09:10 | 2026-08-19 10:32 | 2026-08-19 09:50 | 2026-08-19 10:34 | 2026-08-19 10:34 |  |  | Fair | No | Found okay upon arrival. Customer has an internal problem. Readings at meter socket 116- 117 234 volts.
Outage | J.E.26.08.28312 | C001893271 | Hartley Chin | Clarendon | Completed | Load_260333 | Parnassus - 310 | 2026-08-19 07:32 | 2026-08-19 07:34 | 2026-08-19 16:07 | 2026-08-19 16:07 | 2026-08-19 17:15 | 2026-08-19 17:56 | 2026-08-19 17:56 | 2026-08-19 17:56 |  |  | Fair | No | Replace approximately 60 ft service wire … voltage read 113v , 114v .. ,
Outage | J.E.26.08.28566 | C001893274 | Hartley Chin | Clarendon | Completed | Load_257473 | Parnassus - 310 | 2026-08-19 07:32 | 2026-08-19 07:34 | 2026-08-19 10:39 | 2026-08-19 10:40 | 2026-08-19 11:52 | 2026-08-19 12:01 | 2026-08-19 12:48 | 2026-08-19 12:48 |  |  | Fair | No | Found blown 15 amp junction fuse @ pole # 0159303 line patrolled and found blown 2 amp fuse on 15 KVA transformer @ pole # 582845 due oil leaking from transformer… refused junction… Ref to maintenance!!! Defective 15 KVA .. MAINTENANCE T REPAIR …
Outage | J.E.26.08.28631 | C001893273 | Hartley Chin | Clarendon | Completed | Load_257473 | Parnassus - 310 | 2026-08-19 07:32 | 2026-08-19 07:34 | 2026-08-19 10:39 | 2026-08-19 12:49 | 2026-08-19 12:48 | 2026-08-19 12:49 | 2026-08-19 12:50 | 2026-08-19 12:50 |  |  | Fair | No | Call related to job # 28566
Non-Outage | J.E.26.08.27976 | C001893275 | Collin Robinson | Portland | Completed | Load_352955 | Port Antonio - 310 | 2026-08-19 07:34 | 2026-08-19 11:29 | 2026-08-19 11:46 | 2026-08-19 11:46 | 2026-08-19 12:31 | 2026-08-19 12:42 | 2026-08-19 12:46 | 2026-08-19 12:46 |  |  | Fair | No | Remove bird from transformer switch bottom and replace 3 amps fuse
Non-Outage | J.E.26.08.26623 | C001893276 | Clyde Brown |  | Completed |  |  | 2026-08-19 07:35 | 2026-08-19 07:36 | 2026-08-19 09:00 | 2026-08-19 09:00 | 2026-08-19 09:00 | 2026-08-19 09:00 | 2026-08-19 09:02 | 2026-08-19 09:02 |  |  | Fair | No | Manchester call
Non-Outage | J.E.26.08.26807 | C001893277 | Clyde Brown |  | Completed |  |  | 2026-08-19 07:35 | 2026-08-19 07:36 | 2026-08-19 09:19 | 2026-08-19 09:20 | 2026-08-19 09:19 | 2026-08-19 10:22 | 2026-08-19 10:25 | 2026-08-19 10:25 |  |  | Fair | No | Both phases dislodge at secondary line same remade with 2-clamps ,voltage 111/112 and 224V
Outage | J.E.26.08.28196 | C001893279 | Radcliffe Coleman | St.Catherine | Completed | Load_264063 | Twickenham - 310 | 2026-08-19 07:41 | 2026-08-19 07:42 | 2026-08-19 08:33 | 2026-08-19 08:33 | 2026-08-19 09:26 | 2026-08-19 09:28 | 2026-08-19 09:28 | 2026-08-19 09:28 |  |  | Fair | No | Premises found closed at the time of visit.
Outage | J.E.26.08.28659 | C001893283 | Radcliffe Coleman | St.Catherine | Completed | Load_270057 | Tredegar - 210 | 2026-08-19 07:41 | 2026-08-19 07:42 | 2026-08-19 08:26 | 2026-08-19 10:37 | 2026-08-19 10:36 | 2026-08-19 10:37 | 2026-08-19 10:38 | 2026-08-19 10:38 |  |  | Fair | No | Area found with two blown junction fuse (15A at pole 0076007 and 10A at pole 0063611). Line section was patrolled and no visible fault found. The same value fuses found were replaced. Area now back to normal.
Outage | J.E.26.08.28660 | C001893280 | Radcliffe Coleman | St.Catherine | Completed | Load_253462 | Tredegar - 210 | 2026-08-19 07:41 | 2026-08-19 07:42 | 2026-08-19 08:25 | 2026-08-19 09:29 | 2026-08-19 10:30 | 2026-08-19 10:35 | 2026-08-19 10:35 | 2026-08-19 10:35 |  |  | Fair | No | Area found with two blown junction fuse (15A at pole 0076007 and 10A at pole 0063611). Line section was patrolled and no visible fault found. The same value fuses found were replaced. Area now back to normal.
Outage | J.E.26.08.28682 | C001893281 | Radcliffe Coleman | St.Catherine | Completed | Load_263957 | Tredegar - 310 | 2026-08-19 07:41 | 2026-08-19 07:42 | 2026-08-19 08:26 | 2026-08-19 10:36 | 2026-08-19 10:35 | 2026-08-19 10:36 | 2026-08-19 10:36 | 2026-08-19 10:36 |  |  | Fair | No | Area found with two blown junction fuse (15A at pole 0076007 and 10A at pole 0063611). Line section was patrolled and no visible fault found. The same value fuses found were replaced. Area now back to normal.
Outage | J.E.26.08.28687 | C001893284 | Radcliffe Coleman | St.Catherine | Completed | Load_262399 | Tredegar - 510 | 2026-08-19 07:41 | 2026-08-19 07:42 | 2026-08-19 11:22 | 2026-08-19 11:23 | 2026-08-19 11:37 | 2026-08-19 11:42 | 2026-08-19 11:42 | 2026-08-19 11:42 |  |  | Fair | No | Premises found okay at the time of visit.
Outage | J.E.26.08.28393 | C001893285 | Tajay Bernard | Westmoreland | Completed | Load_249479 | Paradise - 310 | 2026-08-19 07:42 | 2026-08-19 11:41 | 2026-08-19 12:30 | 2026-08-19 12:30 | 2026-08-19 12:43 | 2026-08-19 13:18 | 2026-08-19 13:19 | 2026-08-19 13:19 |  |  | Fair | No | Refuse 1 8amp junction fuse
Outage | J.E.26.08.28204 | C001893306 | Clyde Brown | Clarendon | Completed | Load_243223 | May Pen - 110 | 2026-08-19 07:43 | 2026-08-19 07:44 | 2026-08-19 08:07 | 2026-08-19 08:08 | 2026-08-19 08:55 | 2026-08-19 08:56 | 2026-08-19 08:59 | 2026-08-19 08:59 |  |  | Fair | No | Found ok.already corrected yesterday.
Outage | J.E.26.08.28556 | C001893307 | Hartley Chin | Clarendon | Completed | Load_264754 | May Pen - 210 | 2026-08-19 07:43 | 2026-08-19 07:44 | 2026-08-19 08:47 | 2026-08-19 08:48 | 2026-08-19 09:32 | 2026-08-19 10:34 | 2026-08-19 10:37 | 2026-08-19 10:37 |  |  | Fair | No | Found 25 KVA transformer @ pole # 0123609 breaker on trip , line patrolled thoroughly and found okay , reset transformer… Found approximately 36 customers on transformer circuit and over 20 visible irregularities..
Non-Outage | J.E.26.08.26418 | C001893312 | Christopher West |  | Completed |  |  | 2026-08-19 07:50 | 2026-08-20 08:05 | 2026-08-20 14:27 | 2026-08-20 14:28 | 2026-08-20 14:27 | 2026-08-20 14:28 | 2026-08-20 14:30 | 2026-08-20 14:30 |  |  | Fair | No | Customer now ok as transformer was replaced yesterday.
Non-Outage | J.E.26.08.27598 | C001893309 | Nickolas Rodriques |  | Completed |  |  | 2026-08-19 07:50 | 2026-08-19 07:51 | 2026-08-19 09:14 | 2026-08-19 09:16 | 2026-08-19 09:32 | 2026-08-19 09:48 | 2026-08-19 09:52 | 2026-08-19 09:52 | BrokenPole |  | Fair | No | Checked and found a 30 ft wooden pole rotten and severely leaning that caused customers service wire to be hanging low. It’s a dead end pole which consists of open secondary wires, two guys wires, and customer service wire. Refer to maintenance.
Outage | J.E.26.08.26393 | C001893315 | Nickolas Rodriques | Portmore | Completed | Load_570092 | Naggo Head - 610 | 2026-08-19 07:50 | 2026-08-19 07:51 | 2026-08-19 13:52 | 2026-08-19 13:55 | 2026-08-19 14:08 | 2026-08-19 14:27 | 2026-08-19 14:33 | 2026-08-19 14:33 |  |  | Fair | No | Customer confirmed that the power was later restored.
Outage | J.E.26.08.26578 | C001893314 | Nickolas Rodriques | Portmore | Completed | Load_242817 | Naggo Head - 610 | 2026-08-19 07:50 | 2026-08-19 07:51 | 2026-08-19 12:14 | 2026-08-19 12:14 | 2026-08-19 12:43 | 2026-08-19 12:52 | 2026-08-19 12:53 | 2026-08-19 12:53 |  |  | Fair | No | Unable to locate or communicate with the customer after several attempts. Need proper direction.
Outage | J.E.26.08.27112 | C001893313 | Nickolas Rodriques | Portmore | Completed | Load_570196 | Naggo Head - 610 | 2026-08-19 07:50 | 2026-08-19 07:51 | 2026-08-19 14:33 | 2026-08-19 14:38 | 2026-08-19 14:40 | 2026-08-19 14:43 | 2026-08-19 14:48 | 2026-08-19 14:48 |  |  | Fair | No | Found customer with electricity. The customer was disconnected due to non payment of bill which was later reconnected after payment was made.
Outage | J.E.26.08.27184 | C001893311 | Christopher West | Portmore | Completed | Load_262630 | Naggo Head - 510 | 2026-08-19 07:50 | 2026-08-20 08:04 | 2026-08-20 14:04 | 2026-08-20 14:10 | 2026-08-20 14:24 | 2026-08-20 14:25 | 2026-08-20 14:25 | 2026-08-20 14:25 |  |  | Fair | No | Customer’s service was disconnected however, same has since been reconnected
Outage | J.E.26.08.27277 | C001893310 | Nickolas Rodriques | St.Catherine | Completed | Load_255072 | Twickenham - 210 | 2026-08-19 07:50 | 2026-08-19 07:51 | 2026-08-19 08:06 | 2026-08-19 08:14 | 2026-08-19 08:31 | 2026-08-19 08:43 | 2026-08-19 09:07 | 2026-08-19 09:07 |  |  | Fair | No | Found customer with electricity. However, the customer stated that he is concerned about an ongoing issue with his connection whereas whenever there is a disconnection / connection he is also affected. Both customers are connected EG box(EG 01385). Refer to field service.
Outage | J.E.26.08.25445 | C001893319 | Christopher West | KSAS | Completed | Load_254412 | Duhaney - 210 | 2026-08-19 07:51 | 2026-08-20 08:05 | 2026-08-20 08:56 | 2026-08-20 08:57 | 2026-08-20 09:45 | 2026-08-20 09:46 | 2026-08-20 09:46 | 2026-08-20 09:46 |  |  | Fair | No | Not located, calls made to number provided were unanswered.
Outage | J.E.26.08.26376 | C001893318 | Nickolas Rodriques | Portmore | Completed | Load_579366 | Naggo Head - 610 | 2026-08-19 07:51 | 2026-08-19 07:52 | 2026-08-19 12:55 | 2026-08-19 12:56 | 2026-08-19 13:27 | 2026-08-19 13:44 | 2026-08-19 13:50 | 2026-08-19 13:50 |  |  | Fair | No | Customer stated that the report was made by mistake and she is not having any electrical issues at her premises.
Outage | J.E.26.08.28304 | C001893355 | Nickolas Rodriques | Portmore | Completed | Load_257809 | Naggo Head - 610 | 2026-08-19 07:56 | 2026-08-19 07:57 | 2026-08-19 10:52 | 2026-08-19 10:53 | 2026-08-19 11:54 | 2026-08-19 12:07 | 2026-08-19 12:13 | 2026-08-19 12:13 |  |  | Fair | No | Found premises with electricity. The customer was disconnected due to non payment of bill which was later reconnected after payment was made.
Outage | J.E.26.08.28703 | C001893356 | Swon Miller | St.James | Completed | Load_263606 | Queens Drive - 310 | 2026-08-19 07:57 | 2026-08-19 07:57 | 2026-08-19 08:08 | 2026-08-19 08:12 | 2026-08-19 09:16 | 2026-08-26 09:40 | 2026-08-19 09:46 | 2026-08-19 09:46 |  |  | Fair | No | Found customer without supply due to none payment of bill advise customer to pay bill before power supply can be restored voltage found 0.000 voltage left 0.000
Non-Outage | J.E.26.06.01328 | C001893362 | Orville Lee | St.Catherine | Completed | Load_248359 | Twickenham - 210 | 2026-08-19 07:59 | 2026-08-19 08:01 | 2026-08-19 08:15 | 2026-08-20 12:15 | 2026-08-20 12:15 | 2026-08-20 12:15 | 2026-08-20 12:20 | 2026-08-20 12:20 |  |  | Fair | No | Premises closed upon arrival IssueCustomer was advised to make a report when available
Non-Outage | J.E.26.06.01384 | C001893361 | Orville Lee | Portmore | Completed | Load_249172 | Naggo Head - 610 | 2026-08-19 07:59 | 2026-08-19 08:01 | 2026-08-19 08:15 | 2026-08-19 11:07 | 2026-08-19 11:07 | 2026-08-19 11:11 | 2026-08-19 11:11 | 2026-08-19 11:11 |  |  | Fair | No | Premises closed upon arrival Call to customer unanswered Customer mentioned wrong phone number
Non-Outage | J.E.26.06.03340 | C001893360 | Orville Lee | St.Catherine | Completed | Load_251822 | Twickenham - 210 | 2026-08-19 07:59 | 2026-08-19 08:01 | 2026-08-19 08:15 | 2026-08-20 10:58 | 2026-08-20 10:58 | 2026-08-20 11:05 | 2026-08-20 11:05 | 2026-08-20 11:05 |  |  | Fair | No | Premises ok upon arrival Issue was resolved by a technician 117v
Non-Outage | J.E.26.06.03414 | C001893359 | Orville Lee | Portmore | Completed | Load_243160 | Naggo Head - 610 | 2026-08-19 07:59 | 2026-08-19 08:01 | 2026-08-19 08:15 | 2026-08-19 09:43 | 2026-08-19 09:42 | 2026-08-19 09:42 | 2026-08-19 09:43 | 2026-08-19 09:43 |  |  | Fair | No | Premises closed upon arrival Customer was advised to make a report when available
Non-Outage | J.E.26.06.03567 | C001893358 | Orville Lee | Portmore | Completed | Load_305045 | Naggo Head - 510 | 2026-08-19 07:59 | 2026-08-19 08:01 | 2026-08-19 08:15 | 2026-08-19 12:43 | 2026-08-19 12:51 | 2026-08-19 12:57 | 2026-08-19 13:01 | 2026-08-19 13:01 |  |  | Fair | No | Premises ok upon arrival Issue was resolved by a technician
Non-Outage | J.E.26.05.35106 | C001893367 | Orville Lee | Portmore | Completed | Load_239523 | Naggo Head - 610 | 2026-08-19 08:00 | 2026-08-19 08:01 | 2026-08-19 08:15 | 2026-08-19 10:16 | 2026-08-19 10:41 | 2026-08-19 10:44 | 2026-08-19 10:45 | 2026-08-19 10:45 |  |  | Fair | No | Premises closed upon arrival Call to customer unanswered 115v116v234v
Non-Outage | J.E.26.06.00809 | C001893366 | Orville Lee | Portmore | Completed | Load_247190 | Naggo Head - 610 | 2026-08-19 08:00 | 2026-08-19 08:01 | 2026-08-19 08:15 | 2026-08-19 11:12 | 2026-08-19 11:17 | 2026-08-19 11:22 | 2026-08-19 11:39 | 2026-08-19 11:39 |  |  | Fair | No | Premises closed upon arrival Voltage 116v117v233v
Non-Outage | J.E.26.06.00956 | C001893365 | Orville Lee | Portmore | Completed | Load_570238 | Naggo Head - 610 | 2026-08-19 08:00 | 2026-08-19 08:01 | 2026-08-19 08:15 | 2026-08-20 15:41 | 2026-08-20 15:48 | 2026-08-20 15:51 | 2026-08-20 15:51 | 2026-08-20 15:51 |  |  | Fair | No | Premises found ok upon arrival Issue was solved by a technician Voltage 116v117v
Non-Outage | J.E.26.06.01085 | C001893364 | Orville Lee | Portmore | Completed | Load_268223 | Naggo Head - 610 | 2026-08-19 08:00 | 2026-08-19 08:01 | 2026-08-19 08:15 | 2026-08-19 09:56 | 2026-08-19 10:03 | 2026-08-19 10:04 | 2026-08-19 10:09 | 2026-08-19 10:09 |  |  | Fair | No | Premises closedCall to customer wen to voicemail
Non-Outage | J.E.26.06.01289 | C001893363 | Orville Lee | St.Catherine | Completed | Load_256307 | Twickenham - 210 | 2026-08-19 08:00 | 2026-08-19 08:01 | 2026-08-19 08:15 | 2026-08-20 10:18 | 2026-08-20 10:48 | 2026-08-20 10:52 | 2026-08-20 10:52 | 2026-08-20 10:52 |  |  | Fair | No | Premises closed call to customer unanswered
Non-Outage | J.E.26.08.28401 | C001893368 | Damion Reid | Manchester | Completed | Load_268443 | Kendal - 210 | 2026-08-19 08:00 | 2026-08-19 08:20 | 2026-08-19 08:57 | 2026-08-19 08:58 | 2026-08-19 11:00 | 2026-08-19 11:29 | 2026-08-19 11:31 | 2026-08-19 11:31 | BrokenWire |  | Fair | No | Broken service neutral found for 3 wire service remade broken neutral using one 1 bolt clamp
Non-Outage | J.E.26.06.04528 | C001893378 | Orville Lee | Portmore | Completed | Load_570065 | Naggo Head - 610 | 2026-08-19 08:02 | 2026-08-19 08:03 | 2026-08-19 08:15 | 2026-08-19 14:21 | 2026-08-19 14:43 | 2026-08-19 14:52 | 2026-08-19 14:52 | 2026-08-19 14:52 |  |  | Fair | No | Premises found ok upon arrival Issue was resolved by a technician 116v117v235v
Non-Outage | J.E.26.06.04549 | C001893375 | Orville Lee | Portmore | Completed | Load_570183 | Naggo Head - 610 | 2026-08-19 08:02 | 2026-08-19 08:03 | 2026-08-19 08:15 | 2026-08-19 14:54 | 2026-08-19 15:03 | 2026-08-19 15:05 | 2026-08-19 15:12 | 2026-08-19 15:12 |  |  | Fair | No | Checks made and found upon arrival Issue was resolved by a technician Voltage 117v118v236v
Non-Outage | J.E.26.06.04710 | C001893377 | Orville Lee | Portmore | Completed | Load_253602 | Naggo Head - 510 | 2026-08-19 08:02 | 2026-08-19 08:03 | 2026-08-19 08:15 | 2026-08-19 13:03 | 2026-08-19 13:59 | 2026-08-19 14:16 | 2026-08-19 14:16 | 2026-08-19 14:16 |  |  | Fair | No | Premises found ok upon arrival Voltage 117118235
Non-Outage | J.E.26.06.39025 | C001893379 | Error Coore | Manchester | Completed | Load_261508 | Kendal - 210 | 2026-08-19 08:02 | 2026-08-19 08:07 | 2026-08-19 15:25 | 2026-08-19 15:25 | 2026-08-19 16:04 | 2026-08-19 16:05 | 2026-08-19 16:06 | 2026-08-19 16:06 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.00426 | C001893380 | Error Coore | Manchester | Completed | Load_259832 | Kendal - 210 | 2026-08-19 08:02 | 2026-08-19 08:07 | 2026-08-20 11:05 | 2026-08-20 11:05 | 2026-08-20 12:04 | 2026-08-20 12:33 | 2026-08-20 12:34 | 2026-08-20 12:34 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.01577 | C001893381 | Error Coore | Manchester | Completed | Load_239398 | Kendal - 210 | 2026-08-19 08:02 | 2026-08-19 08:07 | 2026-08-20 12:34 | 2026-08-20 12:35 | 2026-08-20 13:16 | 2026-08-20 13:56 | 2026-08-20 13:57 | 2026-08-20 13:57 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.02209 | C001893382 | Error Coore | Manchester | Completed | Load_256917 | Kendal - 210 | 2026-08-19 08:03 | 2026-08-19 08:07 | 2026-08-19 11:28 | 2026-08-19 11:29 | 2026-08-19 12:10 | 2026-08-19 12:23 | 2026-08-19 12:26 | 2026-08-19 12:26 |  |  | Fair | No | Premises found ok customer said that they did not make any report
Non-Outage | J.E.26.07.04945 | C001893385 | Error Coore | Manchester | Completed | Load_242124 | Spur Tree - 310 | 2026-08-19 08:03 | 2026-08-19 08:07 | 2026-08-20 08:26 | 2026-08-20 08:26 | 2026-08-20 09:08 | 2026-08-20 09:24 | 2026-08-20 09:25 | 2026-08-20 09:25 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.25003 | C001893387 | Error Coore | Manchester | Completed | Load_303157 | Kendal - 210 | 2026-08-19 08:03 | 2026-08-19 08:07 | 2026-08-20 13:57 | 2026-08-20 13:58 | 2026-08-20 15:01 | 2026-08-20 15:10 | 2026-08-20 15:10 | 2026-08-20 15:10 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.08.00851 | C001893389 | Error Coore | Manchester | Completed | Load_254054 | Kendal - 210 | 2026-08-19 08:04 | 2026-08-19 08:07 | 2026-08-19 09:21 | 2026-08-19 09:22 | 2026-08-19 10:22 | 2026-08-19 10:33 | 2026-08-19 10:35 | 2026-08-19 10:35 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.08.00862 | C001893390 | Error Coore | Manchester | Completed | Load_254054 | Kendal - 210 | 2026-08-19 08:04 | 2026-08-19 08:07 | 2026-08-19 10:35 | 2026-08-19 10:36 | 2026-08-19 11:12 | 2026-08-19 11:26 | 2026-08-19 11:27 | 2026-08-19 11:27 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.08.05367 | C001893391 | Error Coore | Manchester | Completed | Load_250463 | Kendal - 210 | 2026-08-19 08:04 | 2026-08-19 08:07 | 2026-08-19 13:33 | 2026-08-19 13:34 | 2026-08-19 14:26 | 2026-08-19 14:37 | 2026-08-19 14:39 | 2026-08-19 14:39 |  |  | Fair | No | Premises found ok customer have internal problem voltage reading 116/114/230 volts
Non-Outage | J.E.26.08.14062 | C001893392 | Error Coore | Manchester | Completed | Load_254334 | Kendal - 210 | 2026-08-19 08:04 | 2026-08-19 08:07 | 2026-08-19 14:39 | 2026-08-19 14:40 | 2026-08-19 15:01 | 2026-08-19 15:14 | 2026-08-19 15:24 | 2026-08-19 15:24 |  |  | Fair | No | Premises found ok voltage reading 116/117/233 volts
Non-Outage | J.E.26.08.15824 | C001893393 | Error Coore |  | Completed |  |  | 2026-08-19 08:05 | 2026-08-19 08:07 | 2026-08-20 09:28 | 2026-08-20 09:31 | 2026-08-20 10:19 | 2026-08-20 11:02 | 2026-08-20 11:04 | 2026-08-20 11:04 |  |  | Fair | No | Found customer phase burn off at pole remade burn off phase using 1 one bolt clamp voltage reading 115/113/228 volts
Non-Outage | J.E.26.08.15903 | C001893394 | Error Coore | Manchester | Completed | Load_269465 | Kendal - 210 | 2026-08-19 08:05 | 2026-08-19 08:15 | 2026-08-19 12:27 | 2026-08-19 12:28 | 2026-08-19 13:17 | 2026-08-19 13:31 | 2026-08-19 13:33 | 2026-08-19 13:33 |  |  | Fair | No | Premises found ok reach at the location customer said that the problem was resolved
Non-Outage | J.E.26.03.33858 | C001893409 | Royston Montague | St.Catherine | Completed | Load_259826 | Rhodens Pen - 310 | 2026-08-19 08:06 | 2026-08-19 08:08 | 2026-08-19 08:19 | 2026-08-19 09:13 | 2026-08-19 10:23 | 2026-08-19 10:46 | 2026-08-19 10:46 | 2026-08-19 10:46 |  |  | Fair | No | Faulty joints at customer take off point, same corrected. Voltage found 210v 100v 116v voltage after 230v 114v 115v
Non-Outage | J.E.26.03.38512 | C001893407 | Royston Montague | St.Catherine | Completed | Load_244674 | Rhodens Pen - 210 | 2026-08-19 08:06 | 2026-08-19 08:08 | 2026-08-19 08:19 | 2026-08-19 08:51 | 2026-08-19 08:58 | 2026-08-19 08:59 | 2026-08-19 08:59 | 2026-08-19 08:59 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.03.42131 | C001893408 | Royston Montague | St.Catherine | Completed | Load_249919 | Rhodens Pen - 210 | 2026-08-19 08:06 | 2026-08-19 08:08 | 2026-08-19 08:19 | 2026-08-19 08:25 | 2026-08-19 08:40 | 2026-08-19 08:43 | 2026-08-19 08:43 | 2026-08-19 08:43 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.04.00994 | C001893406 | Royston Montague | St.Catherine | Completed | Load_269949 | Rhodens Pen - 410 | 2026-08-19 08:06 | 2026-08-19 08:08 | 2026-08-19 08:19 | 2026-08-20 08:55 | 2026-08-20 09:36 | 2026-08-20 09:37 | 2026-08-20 09:37 | 2026-08-20 09:37 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.04.05321 | C001893405 | Royston Montague | St.Catherine | Completed | Load_262322 | Rhodens Pen - 410 | 2026-08-19 08:06 | 2026-08-19 08:08 | 2026-08-19 08:19 | 2026-08-19 12:12 | 2026-08-19 12:12 | 2026-08-19 12:13 | 2026-08-19 12:13 | 2026-08-19 12:13 |  |  | Fair | No | Multiple calls to customer phone, go without answer. GPS coordinate on job not working.
Non-Outage | J.E.26.04.06069 | C001893402 | Royston Montague | St.Catherine | Completed | Load_242303 | Rhodens Pen - 410 | 2026-08-19 08:06 | 2026-08-19 08:08 | 2026-08-19 08:19 | 2026-08-19 13:26 | 2026-08-19 13:26 | 2026-08-19 13:26 | 2026-08-19 13:26 | 2026-08-19 13:26 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.04.06069 | C001893403 | Royston Montague | St.Catherine | Completed | Load_242303 | Rhodens Pen - 410 | 2026-08-19 08:06 | 2026-08-19 08:08 | 2026-08-19 08:19 | 2026-08-19 12:14 | 2026-08-19 13:25 | 2026-08-19 13:25 | 2026-08-19 13:25 | 2026-08-19 13:25 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.04.06197 | C001893404 | Royston Montague | St.Catherine | Completed | Load_263006 | Rhodens Pen - 410 | 2026-08-19 08:06 | 2026-08-19 08:08 | 2026-08-19 08:19 | 2026-08-20 13:21 | 2026-08-20 14:19 | 2026-08-20 14:21 | 2026-08-20 14:22 | 2026-08-20 14:22 |  |  | Fair | No | Not getting through to this customer . Multiple calls to customer phone go without answer
Non-Outage | J.E.26.04.08274 | C001893400 | Royston Montague | St.Catherine | Completed | Load_262493 | Rhodens Pen - 210 | 2026-08-19 08:06 | 2026-08-19 08:08 | 2026-08-19 08:19 | 2026-08-20 08:28 | 2026-08-20 08:51 | 2026-08-20 08:52 | 2026-08-20 08:52 | 2026-08-20 08:52 |  |  | Fair | No | Multiple calls to customer phone go without answer. GPS coordinate on job not working.
Non-Outage | J.E.26.05.13797 | C001893399 | Royston Montague | St.Catherine | Completed | Load_263267 | Rhodens Pen - 210 | 2026-08-19 08:06 | 2026-08-19 08:08 | 2026-08-19 08:19 | 2026-08-19 13:27 | 2026-08-19 14:13 | 2026-08-19 14:13 | 2026-08-19 14:13 | 2026-08-19 14:13 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.05.14340 | C001893398 | Royston Montague | St.Catherine | Completed | Load_265381 | Rhodens Pen - 210 | 2026-08-19 08:06 | 2026-08-19 08:08 | 2026-08-19 08:19 | 2026-08-19 15:00 | 2026-08-19 15:59 | 2026-08-19 15:59 | 2026-08-19 15:59 | 2026-08-19 15:59 |  |  | Fair | No | Customer confirmed issue resolved.
Outage | J.E.26.08.28603 | C001893410 | Dwayne Cohen | KSAN | Completed | Load_245872 | Washington Blvd - 410 | 2026-08-19 08:10 | 2026-08-19 08:12 | 2026-08-19 08:29 | 2026-08-19 08:30 | 2026-08-19 08:58 | 2026-08-19 09:25 | 2026-08-19 09:25 | 2026-08-19 09:25 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.28702 | C001893411 | Milton Charlton | KSAN | Completed | Load_567800 | Hope - 510 | 2026-08-19 08:10 | 2026-08-19 08:12 | 2026-08-19 10:36 | 2026-08-19 10:37 | 2026-08-19 11:27 | 2026-08-19 10:35 | 2026-08-19 11:30 | 2026-08-19 11:30 |  |  | Fair | No | Customer meter #2401578 disconnected for debt.
Outage | J.E.26.08.28681 | C001893416 | Dwayne Cohen | KSAS | Completed | Load_579116 | Greenwich - 510 | 2026-08-19 08:14 | 2026-08-19 08:15 | 2026-08-19 09:24 | 2026-08-19 09:26 | 2026-08-19 09:26 | 2026-08-19 09:26 | 2026-08-19 09:27 | 2026-08-19 09:27 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.28551 | C001893422 | Shawn Medley | St.James | Completed | Load_1001891 | Bogue - 310 | 2026-08-19 08:19 | 2026-08-19 08:20 | 2026-08-19 10:43 | 2026-08-19 10:59 | 2026-08-19 11:28 | 2026-08-19 11:29 | 2026-08-19 11:36 | 2026-08-19 11:36 |  |  | Fair | No | Hexing box with prepaid account, called customer service and they cannot communicate with hexing box; refer field service
Outage | J.E.26.08.28588 | C001893423 | Shawn Medley | St.James | Completed | Load_265607 | Bogue - 310 | 2026-08-19 08:19 | 2026-08-19 08:20 | 2026-08-19 08:40 | 2026-08-19 08:41 | 2026-08-19 09:17 | 2026-08-19 10:17 | 2026-08-19 09:19 | 2026-08-19 09:19 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.28602 | C001893424 | Shawn Medley | St.James | Completed | Load_252713 | Bogue - 310 | 2026-08-19 08:19 | 2026-08-19 08:20 | 2026-08-19 09:19 | 2026-08-19 09:26 | 2026-08-19 10:05 | 2026-08-19 10:12 | 2026-08-19 10:17 | 2026-08-19 10:17 |  |  | EarthMovement | No | Customer meter advancing, check were conducted and customer service was called and it appeared to be customer internal fault. Customer was recommended to call his electrician to check the internal issue
Non-Outage | J.E.26.08.28391 | C001893429 | Floyd Taylor |  | Completed |  |  | 2026-08-19 08:21 | 2026-08-19 08:22 | 2026-08-19 14:55 | 2026-08-19 14:55 | 2026-08-19 14:55 | 2026-08-19 14:55 | 2026-08-19 14:56 | 2026-08-19 14:56 |  |  | Fair | No | Customer found ok
Outage | J.E.26.08.28091 | C001893426 | Floyd Taylor | Trelawny | Completed | Load_257490 | Duncans - 210 | 2026-08-19 08:21 | 2026-08-19 08:22 | 2026-08-19 14:54 | 2026-08-19 14:54 | 2026-08-19 14:54 | 2026-08-19 14:54 | 2026-08-19 14:54 | 2026-08-19 14:54 |  |  | Fair | No | Premises was checked and found ok
Outage | J.E.26.08.28169 | C001893425 | Dwayne Samuels | Trelawny | Completed | Load_269488 | Duncans - 210 | 2026-08-19 08:21 | 2026-08-19 15:30 | 2026-08-19 15:48 | 2026-08-19 15:49 | 2026-08-19 17:32 | 2026-08-19 17:35 | 2026-08-19 17:41 | 2026-08-19 17:41 |  |  | Fair | No | Check and found ok ,Voltage found is 116v 116v 232v
Outage | J.E.26.08.28330 | C001893427 | Floyd Taylor | Trelawny | Completed | Load_239536 | Greenwood - 110 | 2026-08-19 08:21 | 2026-08-19 08:22 | 2026-08-19 11:36 | 2026-08-19 11:37 | 2026-08-19 12:11 | 2026-08-19 12:49 | 2026-08-19 12:51 | 2026-08-19 12:51 | Fire |  | Fair | No | Clean and remake joint at pole voltage reading 116,117 233
Outage | J.E.26.08.28349 | C001893431 | Edward Royal | KSAN | Completed | Load_247312 | Washington Blvd - 710 | 2026-08-19 08:21 | 2026-08-19 08:22 | 2026-08-19 12:54 | 2026-08-19 12:54 | 2026-08-19 13:54 | 2026-08-19 13:56 | 2026-08-19 13:56 | 2026-08-19 13:56 |  |  | Fair | No | Meter have been mixed up advise customer to visit ruthven road for more information
Outage | J.E.26.08.28451 | C001893428 | Floyd Taylor | Trelawny | Completed | Load_238727 | Martha Brae - 110 | 2026-08-19 08:21 | 2026-08-19 08:22 | 2026-08-19 09:07 | 2026-08-19 09:08 | 2026-08-19 10:03 | 2026-08-19 11:24 | 2026-08-19 11:24 | 2026-08-19 11:24 |  |  | Fair | No | Isolated 25kva transformer cut vines from and remake secondary jumper using 2pg clamps voltage readings left 115,116,232
Outage | J.E.26.08.28337 | C001893433 | Fitzroy Turner | KSAS | Completed | Load_239591 | Cane River - 610 | 2026-08-19 08:22 | 2026-08-19 08:22 | 2026-08-19 08:34 | 2026-08-19 08:35 | 2026-08-19 10:37 | 2026-08-19 10:38 | 2026-08-19 10:41 | 2026-08-19 10:41 | Fire |  | Fair | No | Found tree phase line switch top burnt off also one hot line clamps burnt out.use one hot line clamps and one drop outs switches and one 10 amp fuse to carry out repair supply restored to customer
Non-Outage | J.E.26.07.21362 | C001893442 | Nicholas Dillon | St.Elizabeth | Completed | Load_249245 | Maggotty - 110 | 2026-08-19 08:25 | 2026-08-19 08:30 | 2026-08-19 11:23 | 2026-08-19 11:27 | 2026-08-19 11:45 | 2026-08-19 11:46 | 2026-08-19 11:48 | 2026-08-19 11:48 |  |  | Fair | No | Check voltage before at meter 105 97 phase to phase 205 . Whole area experiencing low voltage
Non-Outage | J.E.26.07.22998 | C001893443 | Nicholas Dillon | St.Elizabeth | Completed | Load_259516 | Maggotty - 110 | 2026-08-19 08:25 | 2026-08-19 08:30 | 2026-08-19 13:54 | 2026-08-19 13:55 | 2026-08-19 13:55 | 2026-08-19 13:55 | 2026-08-19 13:58 | 2026-08-19 13:58 |  |  | Fair | No | Check voltage before at 109 105 phase to phase 214 . Whole area experiencing low voltage
Non-Outage | J.E.26.07.31613 | C001893447 | Nicholas Dillon | St.Elizabeth | Completed | Load_253703 | Maggotty - 110 | 2026-08-19 08:26 | 2026-08-19 08:30 | 2026-08-20 12:28 | 2026-08-20 12:29 | 2026-08-20 12:28 | 2026-08-20 12:29 | 2026-08-20 12:30 | 2026-08-20 12:30 |  |  | Fair | No | Check voltage before at meter 114 114 phase to phase 228 premises found working ok
Non-Outage | J.E.26.07.33010 | C001893446 | Nicholas Dillon | St.Elizabeth | Completed | Load_267942 | Maggotty - 110 | 2026-08-19 08:26 | 2026-08-19 08:30 | 2026-08-19 12:38 | 2026-08-19 12:38 | 2026-08-19 12:38 | 2026-08-19 12:38 | 2026-08-19 12:42 | 2026-08-19 12:42 |  |  | Fair | Yes | Check voltage at meter 113 phase to phase 228 .transformer diagram refer to maintenance to replace transformer. One phase coming from the transformer
Non-Outage | J.E.26.07.33560 | C001893448 | Nicholas Dillon | St.Elizabeth | Completed | Load_244860 | Maggotty - 110 | 2026-08-19 08:26 | 2026-08-19 08:30 | 2026-08-20 12:14 | 2026-08-20 12:14 | 2026-08-20 12:14 | 2026-08-20 12:16 | 2026-08-20 12:17 | 2026-08-20 12:17 |  |  | Fair | No | Check voltage before at meter 114 114 phase to phase 228 . Premises found working ok
Non-Outage | J.E.26.07.33757 | C001893453 | Nicholas Dillon | St.Elizabeth | Completed | Load_292293 | Maggotty - 110 | 2026-08-19 08:26 | 2026-08-19 08:30 | 2026-08-20 10:27 | 2026-08-20 10:27 | 2026-08-20 10:27 | 2026-08-20 10:30 | 2026-08-20 10:31 | 2026-08-20 10:31 |  |  | Fair | No | Check and found corrosion at pole clean corrosion use 2 one bolt clamp before I left voltage is 115 115 231
Non-Outage | J.E.26.08.13424 | C001893463 | Nicholas Dillon | St.Elizabeth | Completed | Load_292789 | Maggotty - 110 | 2026-08-19 08:27 | 2026-08-19 08:30 | 2026-08-20 12:05 | 2026-08-20 12:06 | 2026-08-20 12:05 | 2026-08-20 12:05 | 2026-08-20 12:06 | 2026-08-20 12:06 |  |  | Fair | Yes | Check and found corrosion at pole clean corrosion use 2 one bolt clamp before I left voltage is 110 112 phase to phase 222
Non-Outage | J.E.26.08.15496 | C001893464 | Nicholas Dillon | St.Elizabeth | Completed | Load_252841 | Maggotty - 110 | 2026-08-19 08:27 | 2026-08-19 08:30 | 2026-08-20 12:44 | 2026-08-20 12:44 | 2026-08-20 12:47 | 2026-08-20 12:47 | 2026-08-20 12:48 | 2026-08-20 12:48 |  |  | Fair | No | Check and found corrosion at pole clean corrosion use 1 one bolt clamp before I left voltage is 114 115 phase to phase 230
Non-Outage | J.E.26.08.26174 | C001893454 | Horace Malcolm | St.James | Completed | Load_240027 | Bogue - 610 | 2026-08-19 08:27 | 2026-08-19 08:28 | 2026-08-19 08:57 | 2026-08-19 10:17 | 2026-08-19 10:46 | 2026-08-19 12:37 | 2026-08-19 12:37 | 2026-08-19 12:37 |  |  | Fair | No | Isolate one 25kva transformer to repair secondary phase and nuetral drop lead used 6ft #2 conductor 4clamps
Non-Outage | J.E.26.08.27572 | C001893455 | Horace Malcolm | St.James | Completed | Load_244920 | Bogue - 610 | 2026-08-19 08:27 | 2026-08-19 08:28 | 2026-08-19 13:56 | 2026-08-19 13:57 | 2026-08-19 14:57 | 2026-08-19 15:23 | 2026-08-19 15:23 | 2026-08-19 15:23 |  |  | Fair | No | Change burnt out transformer drop lead clamp used 1pg voltage 110-111-220
Non-Outage | J.E.26.08.27687 | C001893456 | Horace Malcolm | St.James | Completed | Load_259225 | Bogue - 610 | 2026-08-19 08:27 | 2026-08-19 08:28 | 2026-08-19 08:48 | 2026-08-19 16:41 | 2026-08-19 17:57 | 2026-08-19 17:59 | 2026-08-19 17:59 | 2026-08-19 17:59 |  |  | Fair | No | Check and found premises closed no occupant
Non-Outage | J.E.26.08.27753 | C001893458 | Horace Malcolm | St.James | Completed | Load_240027 | Bogue - 610 | 2026-08-19 08:27 | 2026-08-19 08:28 | 2026-08-19 12:37 | 2026-08-19 12:38 | 2026-08-19 12:37 | 2026-08-19 12:38 | 2026-08-19 12:38 | 2026-08-19 12:38 |  |  | Fair | No | Related to previous call job number 26174
Non-Outage | J.E.26.08.27884 | C001893459 | Horace Malcolm | St.James | Completed | Load_245304 | Bogue - 610 | 2026-08-19 08:27 | 2026-08-19 08:28 | 2026-08-19 17:59 | 2026-08-19 17:59 | 2026-08-19 18:25 | 2026-08-19 18:27 | 2026-08-19 18:27 | 2026-08-19 18:27 |  |  | Fair | No | Unable to locate customer from multiple phone calls cannot locate premises from direction given
Non-Outage | J.E.26.08.28234 | C001893460 | Horace Malcolm | St.James | Completed | Load_243432 | Bogue - 610 | 2026-08-19 08:27 | 2026-08-19 08:28 | 2026-08-19 12:50 | 2026-08-19 12:51 | 2026-08-19 13:25 | 2026-08-19 13:56 | 2026-08-19 13:56 | 2026-08-19 13:56 |  |  | Fair | No | Check and found one 40ft pole with secondary and single phase primary line leaning down splice service nuetral used 10ft #6 triplex wire voltage 113
Non-Outage | J.E.26.08.28382 | C001893461 | Horace Malcolm | St.James | Completed | Load_267492 | Bogue - 610 | 2026-08-19 08:27 | 2026-08-19 08:28 | 2026-08-19 12:48 | 2026-08-19 12:49 | 2026-08-19 12:48 | 2026-08-19 12:50 | 2026-08-19 12:50 | 2026-08-19 12:50 |  |  | Fair | No | Related to previous call job number 26174
Non-Outage | J.E.26.08.15498 | C001893465 | Nicholas Dillon | St.Elizabeth | Completed | Load_252841 | Maggotty - 110 | 2026-08-19 08:28 | 2026-08-19 08:30 | 2026-08-20 12:48 | 2026-08-20 12:49 | 2026-08-20 12:48 | 2026-08-20 12:48 | 2026-08-20 12:49 | 2026-08-20 12:49 |  |  | Fair | No | Premises found working ok
Non-Outage | J.E.26.08.16291 | C001893467 | Nicholas Dillon | St.Elizabeth | Completed | Load_264506 | Maggotty - 110 | 2026-08-19 08:28 | 2026-08-19 08:30 | 2026-08-19 14:24 | 2026-08-19 14:25 | 2026-08-19 16:58 | 2026-08-19 16:58 | 2026-08-19 17:01 | 2026-08-19 17:01 |  |  | Fair | Yes | Whole area experiencing single phase refer to maintenance to check the transformer
Non-Outage | J.E.26.08.18431 | C001893468 | Nicholas Dillon | St.Elizabeth | Completed | Load_243624 | Maggotty - 110 | 2026-08-19 08:28 | 2026-08-19 08:30 | 2026-08-20 12:51 | 2026-08-20 12:52 | 2026-08-20 13:05 | 2026-08-20 13:08 | 2026-08-20 13:09 | 2026-08-20 13:09 |  |  | Fair | No | Check voltage before at meter 112 114 phase to phase 226. Premises found working ok
Non-Outage | J.E.26.08.19142 | C001893469 | Nicholas Dillon | St.Elizabeth | Completed | Load_250309 | Maggotty - 110 | 2026-08-19 08:28 | 2026-08-19 08:30 | 2026-08-19 14:15 | 2026-08-19 14:16 | 2026-08-19 14:15 | 2026-08-19 14:15 | 2026-08-19 14:17 | 2026-08-19 14:17 |  |  | Fair | Yes | Check and found corrosion at pothead clean joint and use 2 pen union before I left voltage is 114 111
Non-Outage | J.E.26.08.26172 | C001893470 | Nicholas Dillon | St.Elizabeth | Completed | Load_257947 | Maggotty - 110 | 2026-08-19 08:28 | 2026-08-19 08:30 | 2026-08-19 14:07 | 2026-08-19 14:09 | 2026-08-19 14:09 | 2026-08-19 14:09 | 2026-08-19 14:11 | 2026-08-19 14:11 |  |  | Fair | No | Check voltage before at meter 112 111 phase to phase 224 . Premises found working ok
Non-Outage | J.E.26.08.26364 | C001893471 | Nicholas Dillon | St.Elizabeth | Completed | Load_251686 | Maggotty - 110 | 2026-08-19 08:28 | 2026-08-19 08:30 | 2026-08-19 14:01 | 2026-08-19 14:01 | 2026-08-19 14:01 | 2026-08-19 14:01 | 2026-08-19 14:04 | 2026-08-19 14:04 |  |  | Fair | No | Check and found corrosion at pole clean corrosion use 1 one bolt clamp before I left voltage is 118 118 phase to phase 234 high 208
Non-Outage | J.E.26.08.28004 | C001893473 | Hopeton Henry | St.Thomas | Completed | Load_244001 | Good Year - 110 | 2026-08-19 08:29 | 2026-08-19 08:31 | 2026-08-19 10:31 | 2026-08-19 14:47 | 2026-08-19 14:46 | 2026-08-19 14:47 | 2026-08-19 14:47 | 2026-08-19 14:47 |  |  | Fair | No | Internal problem.. customer advised
Non-Outage | J.E.26.08.28316 | C001893474 | Hopeton Henry | St.Thomas | Completed | Load_249841 | Good Year - 210 | 2026-08-19 08:29 | 2026-08-19 08:31 | 2026-08-19 10:31 | 2026-08-19 14:41 | 2026-08-19 14:40 | 2026-08-19 14:40 | 2026-08-19 14:42 | 2026-08-19 14:42 |  |  | Fair | No | Change defective service wire 113-111-224 volts
Non-Outage | J.E.26.07.31082 | C001893483 | Odaine Johnson | Clarendon | Completed | Load_238006 | Parnassus - 210 | 2026-08-19 08:30 | 2026-08-19 08:31 | 2026-08-19 08:46 | 2026-08-19 11:50 | 2026-08-19 11:59 | 2026-08-19 11:59 | 2026-08-19 12:00 | 2026-08-19 12:00 |  |  | Fair | No | Burn off phase found at pole remade connection using 1 one bolt clamp voltage reading 116/114/231 volts
Non-Outage | J.E.26.07.38995 | C001893482 | Odaine Johnson | Clarendon | Completed | Load_238965 | Parnassus - 210 | 2026-08-19 08:30 | 2026-08-19 08:31 | 2026-08-19 08:46 | 2026-08-19 12:00 | 2026-08-19 12:11 | 2026-08-19 12:11 | 2026-08-19 12:12 | 2026-08-19 12:12 |  |  | Fair | No | Contacted customer and customer stated that the issue was resolved already
Non-Outage | J.E.26.08.23732 | C001893484 | Odaine Johnson | Clarendon | Completed | Load_261428 | May Pen - 210 | 2026-08-19 08:30 | 2026-08-19 08:31 | 2026-08-19 08:46 | 2026-08-20 12:53 | 2026-08-20 13:36 | 2026-08-20 13:48 | 2026-08-20 13:49 | 2026-08-20 13:49 |  |  | Fair | No | Rapped on phase and neutral found at pole remade connection using 2 one bolt clamps voltage reading 116 volts
Non-Outage | J.E.26.08.27203 | C001893481 | Hopeton Henry | St.Thomas | Completed | Load_264218 | Lysson - 410 | 2026-08-19 08:30 | 2026-08-19 08:31 | 2026-08-19 10:31 | 2026-08-19 10:32 | 2026-08-19 11:24 | 2026-08-19 12:00 | 2026-08-19 12:01 | 2026-08-19 12:01 |  |  | Fair | No | Rami system, customer not located
Non-Outage | J.E.26.08.27373 | C001893485 | Odaine Johnson | Clarendon | Completed | Load_258194 | May Pen - 210 | 2026-08-19 08:30 | 2026-08-19 08:31 | 2026-08-19 08:46 | 2026-08-19 11:21 | 2026-08-19 11:21 | 2026-08-19 11:22 | 2026-08-19 11:26 | 2026-08-19 11:26 |  |  | Fair | No | Broken class 6 30 ft pole found broken and need replaced area experiencing low voltage
Non-Outage | J.E.26.08.27385 | C001893480 | Hopeton Henry | St.Thomas | Completed | Load_246431 | Good Year - 210 | 2026-08-19 08:30 | 2026-08-19 08:31 | 2026-08-19 10:31 | 2026-08-19 13:49 | 2026-08-19 14:39 | 2026-08-19 14:39 | 2026-08-19 14:40 | 2026-08-19 14:40 |  |  | Fair | No | Premises closed
Non-Outage | J.E.26.08.27393 | C001893478 | Hopeton Henry | St.Thomas | Completed | Load_243896 | Good Year - 210 | 2026-08-19 08:30 | 2026-08-19 08:31 | 2026-08-19 10:31 | 2026-08-19 12:24 | 2026-08-19 12:42 | 2026-08-19 12:42 | 2026-08-19 12:43 | 2026-08-19 12:43 |  |  | Fair | No | Reconnect service at pole 110-110-220 volts
Non-Outage | J.E.26.08.27559 | C001893477 | Hopeton Henry | St.Thomas | Completed | Load_259566 | Good Year - 210 | 2026-08-19 08:30 | 2026-08-19 08:31 | 2026-08-19 10:31 | 2026-08-19 12:43 | 2026-08-19 13:07 | 2026-08-19 13:47 | 2026-08-19 13:48 | 2026-08-19 13:48 | BrokenWire |  | Fair | No | Reconnect service at pole 116-115-231 volts
Non-Outage | J.E.26.08.28732 | C001893486 | Floyd Taylor |  | Completed |  |  | 2026-08-19 08:30 | 2026-08-19 08:31 | 2026-08-19 12:51 | 2026-08-19 12:51 | 2026-08-19 13:47 | 2026-08-19 14:24 | 2026-08-19 14:24 | 2026-08-19 14:24 |  |  | Fair | No | Replace 8amp junction fuse after bird was removed from line voltage reading117,118,235
Non-Outage | J.E.26.07.31389 | C001893493 | Odaine Johnson | Clarendon | Completed | Load_243509 | Parnassus - 210 | 2026-08-19 08:32 | 2026-08-19 08:33 | 2026-08-19 08:45 | 2026-08-19 08:46 | 2026-08-19 08:50 | 2026-08-19 08:58 | 2026-08-19 08:56 | 2026-08-19 08:56 |  |  | Fair | Yes | Corroded neutral found at pole remade connection using 1 one bolt clamp voltage reading 115/115/231 volts
Non-Outage | J.E.26.08.28125 | C001893494 | Dwain Samuels | Westmoreland | Completed | Load_265538 | Paradise - 310 | 2026-08-19 08:32 | 2026-08-19 08:34 | 2026-08-19 09:02 | 2026-08-19 09:20 | 2026-08-19 09:39 | 2026-08-19 10:08 | 2026-08-19 10:16 | 2026-08-19 10:16 |  |  | Fair | No | Replaced broken neutral. Customer said reported the matter from January an no one came until today
Non-Outage | J.E.26.08.28505 | C001893495 | Dwain Samuels | Westmoreland | Completed | Load_239271 | Paradise - 110 | 2026-08-19 08:32 | 2026-08-19 08:34 | 2026-08-19 09:02 | 2026-08-19 11:40 | 2026-08-19 12:06 | 2026-08-19 12:12 | 2026-08-19 12:12 | 2026-08-19 12:12 |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.06.10557 | C001893503 | Odeanie Davis | KSAN | Completed | Load_256424 | Washington Blvd - 710 | 2026-08-19 08:33 | 2026-08-19 08:35 | 2026-08-19 10:07 | 2026-08-19 15:45 | 2026-08-19 15:44 | 2026-08-19 15:41 | 2026-08-19 15:45 | 2026-08-19 15:45 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.06.24102 | C001893496 | Odeanie Davis | KSAS | Completed | Load_262267 | Three Miles - 510 | 2026-08-19 08:33 | 2026-08-19 08:35 | 2026-08-19 11:06 | 2026-08-19 11:06 | 2026-08-19 11:06 | 2026-08-19 11:56 | 2026-08-19 11:56 | 2026-08-19 11:56 |  |  | Fair | No | 119v/33v at arrival, open circuit at secondary corrected, 1 one bolt clamp, 119v/117v after correction.
Non-Outage | J.E.26.06.25298 | C001893497 | Odeanie Davis | KSAS | Completed | Load_261811 | Three Miles - 510 | 2026-08-19 08:33 | 2026-08-19 08:35 | 2026-08-19 08:52 | 2026-08-19 13:09 | 2026-08-19 13:08 | 2026-08-19 13:17 | 2026-08-19 13:09 | 2026-08-19 13:09 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.06.31482 | C001893498 | Odeanie Davis | KSAS | Completed | Load_261811 | Three Miles - 510 | 2026-08-19 08:33 | 2026-08-19 08:35 | 2026-08-19 12:10 | 2026-08-19 13:10 | 2026-08-19 13:09 | 2026-08-19 13:37 | 2026-08-19 13:10 | 2026-08-19 13:10 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.06.36412 | C001893501 | Odeanie Davis | KSAN | Completed | Load_241915 | Washington Blvd - 710 | 2026-08-19 08:33 | 2026-08-19 08:35 | 2026-08-19 09:10 | 2026-08-19 09:11 | 2026-08-19 09:12 | 2026-08-19 10:03 | 2026-08-19 10:03 | 2026-08-19 10:03 |  |  | Fair | No | 115v/116v & 231v in meter socket, however meter found burnt on one side causing the customer to have a single phase at location, technician requested for meter to be changed, temporary power supply left at location.
Non-Outage | J.E.26.06.38400 | C001893499 | Odeanie Davis | KSAS | Completed | Load_292036 | Three Miles - 510 | 2026-08-19 08:33 | 2026-08-19 08:35 | 2026-08-19 08:58 | 2026-08-19 13:12 | 2026-08-19 13:11 | 2026-08-19 13:57 | 2026-08-19 13:12 | 2026-08-19 13:12 |  |  | Fair | No | Customer stated that they don’t have any power issues
Non-Outage | J.E.26.06.38582 | C001893504 | Odeanie Davis | KSAS | Completed | Load_260097 | Up Park Camp - 510 | 2026-08-19 08:33 | 2026-08-19 08:35 | 2026-08-19 08:44 | 2026-08-19 15:46 | 2026-08-19 15:46 | 2026-08-19 15:58 | 2026-08-19 15:46 | 2026-08-19 15:46 |  |  | Fair | No | Customer stated that they don’t have any power issues
Non-Outage | J.E.26.07.10476 | C001893506 | Odeanie Davis | KSAN | Completed | Load_243339 | Washington Blvd - 710 | 2026-08-19 08:33 | 2026-08-19 08:35 | 2026-08-19 10:14 | 2026-08-19 10:15 | 2026-08-19 10:14 | 2026-08-19 10:58 | 2026-08-19 11:02 | 2026-08-19 11:02 |  |  | Fair | No | 99v/130v at arrival, open neutral on secondary line from transformer corrected, 2 one bolt clamps, 114v/117v & 231v after correction
Non-Outage | J.E.26.08.18753 | C001893500 | Odaine Johnson | Clarendon | Completed | Load_239641 | Parnassus - 310 | 2026-08-19 08:33 | 2026-08-19 08:36 | 2026-08-19 08:46 | 2026-08-19 09:44 | 2026-08-19 10:36 | 2026-08-19 22:35 | 2026-08-19 10:38 | 2026-08-19 10:38 |  |  | Fair | No | Burn off phase found at pole remade connection using 1 one bolt clamp voltage reading 114/114/228 volts
Non-Outage | J.E.26.08.20248 | C001893507 | Odaine Johnson | Clarendon | Completed | Load_239641 | Parnassus - 310 | 2026-08-19 08:33 | 2026-08-19 08:36 | 2026-08-19 08:46 | 2026-08-19 10:39 | 2026-08-19 10:38 | 2026-08-19 10:39 | 2026-08-19 10:39 | 2026-08-19 10:39 |  |  | Fair | No | Burn off phase found at pole remade connection using 1 one bolt clamp voltage reading 114/114/228 volts
Non-Outage | J.E.26.08.21535 | C001893502 | Odaine Johnson | Clarendon | Completed | Load_260333 | Parnassus - 310 | 2026-08-19 08:33 | 2026-08-19 08:36 | 2026-08-19 08:46 | 2026-08-19 11:30 | 2026-08-19 11:48 | 2026-08-19 11:48 | 2026-08-19 11:48 | 2026-08-19 11:48 |  |  | Fair | No | Corroded neutral found at pole remade connection using 1 one bolt clamp voltage reading 114/115/229 volts
Non-Outage | J.E.26.08.21949 | C001893505 | Odaine Johnson | Clarendon | Completed | Load_260333 | Parnassus - 310 | 2026-08-19 08:33 | 2026-08-19 08:36 | 2026-08-19 08:46 | 2026-08-19 10:51 | 2026-08-19 10:54 | 2026-08-19 10:54 | 2026-08-19 10:55 | 2026-08-19 10:55 |  |  | Fair | No | Customer stated that the issue was resolved
Non-Outage | J.E.26.07.14783 | C001893510 | Odeanie Davis | KSAS | Completed | Load_241297 | Three Miles - 510 | 2026-08-19 08:34 | 2026-08-19 08:35 | 2026-08-19 12:14 | 2026-08-19 12:30 | 2026-08-19 12:30 | 2026-08-19 13:07 | 2026-08-19 13:08 | 2026-08-19 13:08 |  |  | Fair | No | Maintenance team needed, pad mounted transformer at the back of location needs maintenance, pole seen burnt next to pad mounted transformer, cross arm on pole seen burnt as well and it also dangling with wires still connected, vegetation also on pole and around pad mounted transformer.
Non-Outage | J.E.26.07.15918 | C001893511 | Edward Royal | KSAN | Completed | Load_293564 | Greenwich - 710 | 2026-08-19 08:34 | 2026-08-19 08:38 | 2026-08-19 11:46 | 2026-08-19 11:46 | 2026-08-19 11:46 | 2026-08-19 11:47 | 2026-08-19 11:48 | 2026-08-19 11:48 |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.08.20863 | C001893508 | Odaine Johnson | Clarendon | Completed | Load_260333 | Parnassus - 310 | 2026-08-19 08:34 | 2026-08-19 08:36 | 2026-08-19 08:46 | 2026-08-19 10:55 | 2026-08-19 11:17 | 2026-08-19 11:17 | 2026-08-19 11:19 | 2026-08-19 11:19 |  |  | Fair | No | Premises found okay customer stated that the issue was resolved
Non-Outage | J.E.26.08.21802 | C001893509 | Odaine Johnson | Clarendon | Completed | Load_260333 | Parnassus - 310 | 2026-08-19 08:34 | 2026-08-19 08:36 | 2026-08-19 08:46 | 2026-08-19 10:45 | 2026-08-19 10:50 | 2026-08-19 10:50 | 2026-08-19 10:51 | 2026-08-19 10:51 |  |  | Fair | No | Premises found okay customer stated that the issue was resolved
Non-Outage | J.E.26.08.27680 | C001893515 | Fredrick Hamilton | KSAN | Completed | Load_254044 | Hope - 410 | 2026-08-19 08:35 | 2026-08-19 08:36 | 2026-08-19 08:40 | 2026-08-19 10:50 | 2026-08-19 10:49 | 2026-08-19 10:53 | 2026-08-19 10:53 | 2026-08-19 10:53 | Multiple throwups and sparking |  | Fair | No | Requesting strike force to visit location multiple throwups causing feedback Preventing repair
Non-Outage | J.E.26.08.27957 | C001893514 | Fredrick Hamilton | KSAN | Completed | Load_265649 | Hope - 510 | 2026-08-19 08:35 | 2026-08-19 08:36 | 2026-08-19 08:40 | 2026-08-19 11:26 | 2026-08-19 12:44 | 2026-08-19 13:05 | 2026-08-19 13:05 | 2026-08-19 13:05 |  |  | Fair | No | 238v/118v118v obtained no issue detected on the JPS supply Customer advised to do internal inspection
Non-Outage | J.E.26.08.28114 | C001893513 | Fredrick Hamilton | KSAN | Completed | Load_254044 | Hope - 410 | 2026-08-19 08:35 | 2026-08-19 08:36 | 2026-08-19 08:40 | 2026-08-19 09:54 | 2026-08-19 10:22 | 2026-08-19 10:43 | 2026-08-19 10:43 | 2026-08-19 10:43 | Multiple throwups on line causing feed back |  | Fair | No | Requesting strike force to visit location to remove multiple illegal connections from line in order to correct defects
Non-Outage | J.E.26.08.28590 | C001893522 | Edward Royal |  | Completed |  |  | 2026-08-19 08:37 | 2026-08-19 08:38 | 2026-08-19 11:53 | 2026-08-19 11:53 | 2026-08-19 11:53 | 2026-08-19 11:54 | 2026-08-19 11:54 | 2026-08-19 11:54 |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.08.28605 | C001893523 | Edward Royal |  | Completed |  |  | 2026-08-19 08:37 | 2026-08-19 08:38 | 2026-08-19 12:00 | 2026-08-19 12:01 | 2026-08-19 12:00 | 2026-08-19 12:01 | 2026-08-19 12:28 | 2026-08-19 12:28 | BrokenWire |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.08.28607 | C001893524 | Edward Royal |  | Completed |  |  | 2026-08-19 08:37 | 2026-08-19 08:38 | 2026-08-19 11:28 | 2026-08-19 11:28 | 2026-08-19 11:28 | 2026-08-19 11:42 | 2026-08-19 11:42 | 2026-08-19 11:42 |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.08.28609 | C001893520 | Edward Royal |  | Completed |  |  | 2026-08-19 08:37 | 2026-08-19 08:38 | 2026-08-19 11:48 | 2026-08-19 11:49 | 2026-08-19 11:48 | 2026-08-19 11:49 | 2026-08-19 11:49 | 2026-08-19 11:49 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.28612 | C001893521 | Edward Royal | KSAS | Completed | Load_258629 | Hunts Bay - 310 | 2026-08-19 08:37 | 2026-08-19 08:38 | 2026-08-19 11:49 | 2026-08-19 11:50 | 2026-08-19 11:49 | 2026-08-19 11:52 | 2026-08-19 11:53 | 2026-08-19 11:53 |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.06.08209 | C001893525 | Royston Montague | St.Catherine | Completed | Load_251630 | Rhodens Pen - 410 | 2026-08-19 08:38 | 2026-08-19 08:40 | 2026-08-19 08:59 | 2026-08-19 12:11 | 2026-08-19 12:11 | 2026-08-19 12:11 | 2026-08-19 12:11 | 2026-08-19 12:11 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.06.12575 | C001893526 | Royston Montague | St.Catherine | Completed | Load_267102 | Rhodens Pen - 410 | 2026-08-19 08:38 | 2026-08-19 08:40 | 2026-08-19 08:59 | 2026-08-20 09:38 | 2026-08-20 11:11 | 2026-08-20 11:18 | 2026-08-20 11:19 | 2026-08-20 11:19 |  |  | Fair | No | Full voltage found at customer take off point. Unable to check pothead and meter socket. Customer not at home. Same said she is unable on weekends. Voltage found 228v 113v 114v
Non-Outage | J.E.26.05.14429 | C001893530 | Royston Montague | St.Catherine | Completed | Load_240672 | Rhodens Pen - 410 | 2026-08-19 08:39 | 2026-08-19 08:40 | 2026-08-19 08:59 | 2026-08-19 09:08 | 2026-08-19 09:09 | 2026-08-19 09:10 | 2026-08-19 09:10 | 2026-08-19 09:10 |  |  | Fair | No | Customer confirmed issue resolved,
Non-Outage | J.E.26.05.30782 | C001893529 | Royston Montague | St.Catherine | Completed | Load_265127 | Rhodens Pen - 210 | 2026-08-19 08:39 | 2026-08-19 08:40 | 2026-08-19 08:59 | 2026-08-20 11:19 | 2026-08-20 13:00 | 2026-08-20 13:20 | 2026-08-20 13:21 | 2026-08-20 13:21 |  |  | Fair | No | Customer hang up phone, same not giving details of current status.
Non-Outage | J.E.26.05.30786 | C001893527 | Royston Montague | St.Catherine | Completed | Load_568154 | Rhodens Pen - 210 | 2026-08-19 08:39 | 2026-08-19 08:40 | 2026-08-19 08:59 | 2026-08-19 14:15 | 2026-08-19 14:57 | 2026-08-19 14:58 | 2026-08-19 14:58 | 2026-08-19 14:58 |  |  | Fair | No | Customer confirmed issue resolved
Non-Outage | J.E.26.05.30961 | C001893528 | Royston Montague | St.Catherine | Completed | Load_245337 | Rhodens Pen - 410 | 2026-08-19 08:39 | 2026-08-19 08:40 | 2026-08-19 08:59 | 2026-08-19 10:51 | 2026-08-19 11:28 | 2026-08-19 11:28 | 2026-08-19 11:28 | 2026-08-19 11:28 |  |  | Fair | No | Customer confirmed issue resolved.
Outage | J.E.26.08.28727 | C001893533 | Raheem Ricketts | St.Elizabeth | Completed | Load_239476 | Maggotty - 210 | 2026-08-19 08:42 | 2026-08-19 08:44 | 2026-08-19 08:53 | 2026-08-19 08:53 | 2026-08-19 10:13 | 2026-08-19 11:45 | 2026-08-19 11:45 | 2026-08-19 11:45 | BrokenWire |  | Fair | No | Splice and retention 80ft of customer service wire using 3,clamps 3 links
Outage | J.E.26.08.28724 | C001893534 | Richard Watson | St.Elizabeth | Completed | Load_247865 | Maggotty - 110 | 2026-08-19 08:43 | 2026-08-19 08:44 | 2026-08-19 09:19 | 2026-08-19 09:20 | 2026-08-19 10:14 | 2026-08-19 10:45 | 2026-08-19 10:51 | 2026-08-19 10:51 |  |  | Fair | No | Replace blown 2amp fuse for 25kva transformer no pole#, after completing patrol, resident report that a man of unsound mind hit out meter damaging the socket and causing short circuit, service main secured and taped off, customer advised to get electrician to effect repairs.
Non-Outage | J.E.26.08.27491 | C001893537 | Tajay Bernard |  | Completed |  |  | 2026-08-19 08:48 | 2026-08-19 08:49 | 2026-08-19 09:56 | 2026-08-19 09:56 | 2026-08-19 10:27 | 2026-08-19 10:33 | 2026-08-19 10:41 | 2026-08-19 10:41 | LeaningPole |  | Fair | No | Area check and found okay no leaning pole found
Non-Outage | J.E.26.08.27636 | C001893536 | Tajay Bernard | Hanover | Completed | Load_1001727 | Orange Bay - 310 | 2026-08-19 08:48 | 2026-08-19 08:49 | 2026-08-19 11:00 | 2026-08-19 11:05 | 2026-08-19 11:33 | 2026-08-19 12:25 | 2026-08-19 12:25 | 2026-08-19 12:25 |  |  | Fair | No | Clean and remake joints at jps pole and customer pothead use 2 clamps Voltage found 116Voltage left 116/115/231
Outage | J.E.26.08.28740 | C001893546 | Dwayne Samuels | Trelawny | Completed | Load_258963 | Duncans - 210 | 2026-08-19 08:57 | 2026-08-19 15:30 | 2026-08-19 15:43 | 2026-08-19 17:43 | 2026-08-19 18:40 | 2026-08-19 19:39 | 2026-08-19 19:39 | 2026-08-19 19:39 |  |  | Fair | No | 1 of customer phase was connected to the neutral of the open span secondary wire same was removed and reconnected to phase customer meter is in locking band voltage left at pothead 118v/119v/237v
Outage | J.E.26.08.28722 | C001893553 | Tyrese Williams | St.Ann | Completed | Load_264795 | Roaring River - 410 | 2026-08-19 09:03 | 2026-08-19 09:04 | 2026-08-19 09:33 | 2026-08-19 09:33 | 2026-08-19 11:20 | 2026-08-19 11:45 | 2026-08-19 11:45 | 2026-08-19 11:45 |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.08.28745 | C001893552 | Tyrese Williams | St.Ann | Completed | Load_242953 | Roaring River - 410 | 2026-08-19 09:03 | 2026-08-19 09:04 | 2026-08-19 09:33 | 2026-08-19 11:46 | 2026-08-19 12:41 | 2026-08-19 12:49 | 2026-08-19 12:49 | 2026-08-19 12:49 |  |  | Fair | No | Premises found ok customer breaker was found off
Non-Outage | J.E.26.08.28726 | C001893554 | Locksley Allen | St.Mary | Completed | Load_252159 | Highgate - 210 | 2026-08-19 09:06 | 2026-08-19 09:07 | 2026-08-19 10:25 | 2026-08-19 11:01 | 2026-08-19 11:01 | 2026-08-19 11:33 | 2026-08-19 11:34 | 2026-08-19 11:34 | BrokenWire |  | Fair | No | No meter(empty socket) found at the premises. Pole is lean and socket rotten. Customer needs to change meter pole and socket urgently. Please refer to field service
Non-Outage | J.E.26.08.28418 | C001893561 | Locksley Allen | St.Ann | Completed | Load_249695 | Upper White River - 110 | 2026-08-19 09:09 | 2026-08-19 09:15 | 2026-08-19 11:34 | 2026-08-19 12:41 | 2026-08-19 12:40 | 2026-08-19 13:11 | 2026-08-19 13:12 | 2026-08-19 13:12 |  |  | Fair | No | Meter found defective and needs to change urgently Voltage at meter socket phase to phase 244v. Phase to neutral 119&119vMeter not working, but customer still have supply
Outage | J.E.26.08.28767 | C001893569 | Elvis Trowers | KSAN | Completed | Load_250841 | Constant Spring - 210 | 2026-08-19 09:19 | 2026-08-19 09:20 | 2026-08-19 09:28 | 2026-08-19 09:29 | 2026-08-19 10:03 | 2026-08-19 10:00 | 2026-08-19 10:07 | 2026-08-19 10:07 |  |  | Fair | No | Found okay upon arrival. Customer states matter was resolved.
Outage | J.E.26.08.28737 | C001893583 | Derrick Grubb | St.Thomas | Completed | Load_259414 | Good Year - 210 | 2026-08-19 09:30 | 2026-08-19 09:31 | 2026-08-19 10:08 | 2026-08-19 10:08 | 2026-08-19 11:11 | 2026-08-19 11:12 | 2026-08-19 11:15 | 2026-08-19 11:15 |  |  | Fair | No | Premises not located , number not associated with call
Outage | J.E.26.08.28738 | C001893584 | Derrick Grubb | St.Thomas | Completed | Load_254306 | Lysson - 410 | 2026-08-19 09:30 | 2026-08-19 09:31 | 2026-08-19 12:07 | 2026-08-19 12:08 | 2026-08-19 13:07 | 2026-08-19 13:08 | 2026-08-19 13:09 | 2026-08-19 13:09 | BrokenWire |  | Fair | No | Change damage service wire
Outage | J.E.26.08.28781 | C001893589 | Kenroy Dale | Manchester | Completed | Load_244394 | Spur Tree - 310 | 2026-08-19 09:32 | 2026-08-19 09:53 | 2026-08-19 10:19 | 2026-08-19 10:29 | 2026-08-19 11:55 | 2026-08-19 12:20 | 2026-08-19 12:22 | 2026-08-19 12:22 | BrokenWire |  | Fair | No | Defective service wire found causing from vehicle accident, service wire was splice and retention using 2 one bolt clamp voltage reading 111/113/224
Outage | J.E.26.08.27909 | C001893611 | Radcliffe Coleman | St.Catherine | Completed | Load_567663 | Tredegar - 310 | 2026-08-19 09:42 | 2026-08-19 09:43 | 2026-08-19 12:47 | 2026-08-19 13:42 | 2026-08-19 13:42 | 2026-08-19 13:45 | 2026-08-19 13:45 | 2026-08-19 13:45 | BrokenPole,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | This situation requires the intervention of the field service department. There is an hexing enclosure at the location that has a number of service wires that needs to be transferred to a new pole. Please refer to the field service department for their intervention.
Outage | J.E.26.08.27965 | C001893610 | Radcliffe Coleman | St.Catherine | Completed | Load_259531 | Tredegar - 510 | 2026-08-19 09:42 | 2026-08-19 09:43 | 2026-08-19 11:43 | 2026-08-19 11:43 | 2026-08-19 12:13 | 2026-08-19 01:00 | 2026-08-19 13:38 | 2026-08-19 13:38 | BrokenPole,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | This situation requires the intervention of the field service Department. The wires from an hexing enclosure needs to be transferred to a new pole at the location. Please refer to the field service department for the intervention.
Non-Outage | J.E.26.08.28200 | C001893639 | Rochaine Hussey | KSAS | Completed | Load_264225 | Duhaney - 310 | 2026-08-19 09:52 | 2026-08-19 09:53 | 2026-08-19 11:27 | 2026-08-19 12:02 | 2026-08-19 12:02 | 2026-08-19 13:20 | 2026-08-19 13:20 | 2026-08-19 13:20 |  |  | Fair | No | Customer say the issue was fixed and power was restored
Non-Outage | J.E.26.08.28750 | C001893638 | Milton Charlton | KSAN | Completed | Load_254899 | Hope - 410 | 2026-08-19 09:52 | 2026-08-19 11:55 | 2026-08-19 12:46 | 2026-08-19 12:46 | 2026-08-19 13:52 | 2026-08-19 13:40 | 2026-08-19 14:00 | 2026-08-19 14:00 |  |  | Fair | No | 45ft wooden pole H structure #0110004 with 3- 100 kva transformers two of the switch top burn off at the hot line clamps. Need bucket truck to repair switch top.
Non-Outage | J.E.26.08.28796 | C001893640 | Christopher Edwards | KSAN | Completed | Load_261661 | Constant Spring - 410 | 2026-08-19 09:52 | 2026-08-19 09:53 | 2026-08-19 10:27 | 2026-08-19 12:59 | 2026-08-19 12:59 | 2026-08-19 12:59 | 2026-08-19 12:59 | 2026-08-19 12:59 |  |  | Fair | No | Related to previous call that has been resolved
Outage | J.E.26.08.28774 | C001893650 | Tyrese Williams | St.Ann | Completed | Load_260937 | Roaring River - 210 | 2026-08-19 09:58 | 2026-08-19 10:02 | 2026-08-19 12:24 | 2026-08-19 12:59 | 2026-08-19 12:59 | 2026-08-19 12:59 | 2026-08-19 13:00 | 2026-08-19 13:00 |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.08.28807 | C001893649 | Roxroy Needham | St.Ann | Completed | Load_247748 | Cardiff Hall - 310 | 2026-08-19 09:58 | 2026-08-19 10:03 | 2026-08-19 12:19 | 2026-08-19 12:19 | 2026-08-19 13:38 | 2026-08-19 13:39 | 2026-08-19 13:39 | 2026-08-19 13:39 | LowHangingWires |  | Fair | No | Not getting through to customer on the phone
Outage | J.E.26.08.28805 | C001893706 | Dwayne Cohen | KSAN | Completed | Load_248678 | Constant Spring - 410 | 2026-08-19 10:31 | 2026-08-19 10:33 | 2026-08-19 10:54 | 2026-08-19 10:54 | 2026-08-19 11:30 | 2026-08-19 11:36 | 2026-08-19 11:39 | 2026-08-19 11:39 |  |  | Fair | No | Premises found okay, voltage readings 119v 119v 240v by the meter socket. Internal problem customer were advised
Non-Outage | J.E.26.08.28833 | C001893715 | Christopher Edwards |  | Completed |  |  | 2026-08-19 10:32 | 2026-08-19 10:34 | 2026-08-19 10:48 | 2026-08-19 11:30 | 2026-08-19 12:05 | 2026-08-19 12:57 | 2026-08-19 12:58 | 2026-08-19 12:58 | Fire |  | Fair | No | Isolate bank of 3 transformers to Remake burnt neutral joint Using (2) one bolt clamps
Outage | J.E.26.08.28813 | C001893714 | Derrick Grubb | St.Thomas | Completed | Load_269603 | Good Year - 210 | 2026-08-19 10:32 | 2026-08-19 10:33 | 2026-08-19 11:30 | 2026-08-19 12:00 | 2026-08-19 11:59 | 2026-08-19 12:07 | 2026-08-19 12:07 | 2026-08-19 12:07 | Fire |  | Fair | No | Clear corrosion and replace one bolt clamp
Outage | J.E.26.08.28842 | C001893716 | Tyrese Williams | St.Ann | Completed | Load_248764 | Roaring River - 210 | 2026-08-19 10:33 | 2026-08-19 10:39 | 2026-08-19 12:24 | 2026-08-19 13:01 | 2026-08-19 15:34 | 2026-08-19 14:58 | 2026-08-19 15:36 | 2026-08-19 15:36 | BrokenWire |  | Fair | No | Splice and retention 2 span of secondary neutral use 1 splicing sleeve
Outage | J.E.26.08.28854 | C001893754 | Kenroy Dale | Manchester | Completed | Load_292857 | Porus - 310 | 2026-08-19 11:02 | 2026-08-19 11:11 | 2026-08-19 13:53 | 2026-08-19 14:00 | 2026-08-19 14:46 | 2026-08-19 15:06 | 2026-08-19 15:07 | 2026-08-19 15:07 |  |  | Fair | No | Supply was disconnected for non-payment
Outage | J.E.26.08.28859 | C001893753 | Kenroy Dale | Manchester | Completed | Load_265576 | Kendal - 310 | 2026-08-19 11:02 | 2026-08-19 11:11 | 2026-08-19 12:22 | 2026-08-19 12:38 | 2026-08-19 13:34 | 2026-08-19 13:51 | 2026-08-19 13:53 | 2026-08-19 13:53 |  |  | Fair | No | Customer have internal problems customer was advised to get electrician to chuck premises
Outage | J.E.26.08.28886 | C001893752 | Damion Reid | Manchester | Completed | Load_270122 | Kendal - 210 | 2026-08-19 11:02 | 2026-08-19 11:13 | 2026-08-19 11:31 | 2026-08-19 11:32 | 2026-08-19 12:19 | 2026-08-19 12:52 | 2026-08-19 12:54 | 2026-08-19 12:54 |  |  | Fair | No | Broken 30ft secondary pole found causing secondary conductor to sag conductor need to change to newly erected pole
Outage | J.E.26.08.28768 | C001893763 | Selvin White | St.Elizabeth | Completed | Load_260670 | Maggotty - 110 | 2026-08-19 11:15 | 2026-08-19 15:13 | 2026-08-19 17:33 | 2026-08-19 17:34 | 2026-08-19 17:39 | 2026-08-19 22:41 | 2026-08-19 22:41 | 2026-08-19 22:41 |  |  | Fair | No | Splice and retention pole spans of defective #2 neutral conductor that was resulting in fluctuating voltage due to defective splicing sleeve after isolation of a 25 KVA transformer circuit with no pole number attached. Supply restored to the affected customers however follow up will be required with bucket truck to splice out another splicing sleeve in mid span. Please refer to the morning crew.
Outage | J.E.26.08.28916 | C001893768 | Raheem Ricketts | St.Elizabeth | Completed | Load_292810 | Maggotty - 210 | 2026-08-19 11:17 | 2026-08-19 11:21 | 2026-08-19 11:59 | 2026-08-19 11:59 | 2026-08-19 12:51 | 2026-08-19 12:52 | 2026-08-19 12:52 | 2026-08-19 12:52 |  |  | Fair | No | Check and found okay customer has power an everything however customer needs street light to change
Outage | J.E.26.08.28773 | C001893769 | Javid Vernon | Westmoreland | Completed | Load_255654 | Paradise - 110 | 2026-08-19 11:21 | 2026-08-19 11:35 | 2026-08-19 11:51 | 2026-08-19 11:51 | 2026-08-19 12:31 | 2026-08-19 12:56 | 2026-08-19 12:57 | 2026-08-19 12:57 |  |  | Fair | No | Premises check and found okay customer got disconnected for none payment voltage reading 109/110/220
Outage | J.E.26.08.28830 | C001893770 | Javid Vernon | Westmoreland | Completed | Load_251528 | Paradise - 110 | 2026-08-19 11:21 | 2026-08-19 11:35 | 2026-08-19 12:57 | 2026-08-19 12:58 | 2026-08-19 13:09 | 2026-08-19 13:56 | 2026-08-19 13:56 | 2026-08-19 13:56 |  |  | Fair | No | Check and found customer defective it needs to be replaced urgently customer is still without power the meter is connected but there is no power passing through it refer to field service
Outage | J.E.26.08.28855 | C001893776 | Michael Paterson | Westmoreland | Completed | Load_266879 | Paradise - 210 | 2026-08-19 11:21 | 2026-08-19 16:29 | 2026-08-19 21:30 | 2026-08-19 21:31 | 2026-08-19 21:31 | 2026-08-19 21:31 | 2026-08-20 00:07 | 2026-08-20 00:07 |  |  | Fair | No | Found 25kva xfmr fuse blown, also found six span of secondary broken, spot bushing done, repair done using 5 clamps, 80ft #2 , two #2 preform,replace 2amps fuse, supply restored, voltage readings, 117v, 117v, 234v.
Outage | J.E.26.08.28844 | C001893780 | Edward Royal | KSAS | Completed | Load_260450 | Greenwich - 510 | 2026-08-19 11:25 | 2026-08-19 11:32 | 2026-08-19 12:36 | 2026-08-19 12:37 | 2026-08-19 12:53 | 2026-08-19 12:54 | 2026-08-19 12:54 | 2026-08-19 12:54 |  |  | Fair | No | Premises found close unable to communicate with customer
Outage | J.E.26.08.28858 | C001893779 | Rusean Allen | KSAS | Completed | Load_241355 | Up Park Camp - 510 | 2026-08-19 11:25 | 2026-08-20 07:50 | 2026-08-20 12:03 | 2026-08-20 12:04 | 2026-08-20 12:59 | 2026-08-20 13:07 | 2026-08-20 13:07 | 2026-08-20 13:07 |  |  | Fair | No | Defective 3w meter#3041626 found at premises, meter needs to be changed, refer to field service department.
Outage | J.E.26.08.28865 | C001893778 | Fitzroy Turner | KSAN | Completed | Load_256666 | Washington Blvd - 710 | 2026-08-19 11:25 | 2026-08-19 11:31 | 2026-08-19 11:58 | 2026-08-19 12:46 | 2026-08-19 12:46 | 2026-08-19 13:02 | 2026-08-19 13:06 | 2026-08-19 13:06 | BangingWires,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Found tree wire open secondary top phase burnt down cause by overload.and illegal connections use 200ft of 2/0 aluminum and two preform and 4one bolt clamps supply restored to areas
Outage | J.E.26.08.28866 | C001893777 | Edward Royal | KSAS | Completed | Load_291638 | Hunts Bay - 410 | 2026-08-19 11:25 | 2026-08-19 11:34 | 2026-08-19 12:29 | 2026-08-19 12:29 | 2026-08-19 12:29 | 2026-08-19 12:35 | 2026-08-19 12:36 | 2026-08-19 12:36 |  |  | Fair | No | Replaced 15A junction fuse
Outage | J.E.26.08.28657 | C001893784 | Rusean Allen | KSAS | Completed | Load_300804 | Cane River - 310 | 2026-08-19 11:27 | 2026-08-19 11:30 | 2026-08-19 13:21 | 2026-08-19 13:22 | 2026-08-19 13:56 | 2026-08-19 15:02 | 2026-08-19 15:02 | 2026-08-19 15:02 |  |  | Fair | No | 1x 30amp fuse found 1x 30amp fuse replaced.1x 20amp fuse found 1x 20amp fuse replaced.
Outage | J.E.26.08.28721 | C001893785 | Rusean Allen | KSAS | Completed | Load_300806 | Cane River - 310 | 2026-08-19 11:27 | 2026-08-19 11:30 | 2026-08-20 02:26 | 2026-08-20 02:26 | 2026-08-20 02:27 | 2026-08-20 02:27 | 2026-08-20 02:27 | 2026-08-20 02:27 |  |  | Fair | No | Premises okay
Non-Outage | J.E.26.08.27912 | C001893798 | Oraine Minto | St.Ann | Completed | Load_243646 | Ocho Rios - 310 | 2026-08-19 11:32 | 2026-08-19 11:33 | 2026-08-20 16:20 | 2026-08-20 16:20 | 2026-08-20 16:20 | 2026-08-20 16:20 | 2026-08-20 16:21 | 2026-08-20 16:21 |  |  | Fair | No | Refer to field service One leg of the meter burn and need to replace
Non-Outage | J.E.26.08.28544 | C001893800 | Oraine Minto | St.Ann | Completed | Load_238437 | Ocho Rios - 310 | 2026-08-19 11:32 | 2026-08-19 11:33 | 2026-08-20 12:20 | 2026-08-20 12:51 | 2026-08-20 12:50 | 2026-08-20 12:51 | 2026-08-20 12:52 | 2026-08-20 12:52 | LowHangingWires |  | Fair | No | Refer to maintenance 214v 107v 107v
Non-Outage | J.E.26.08.28823 | C001893801 | Oraine Minto | St.Ann | Completed | Load_266922 | Roaring River - 210 | 2026-08-19 11:32 | 2026-08-19 11:42 | 2026-08-19 15:28 | 2026-08-19 15:49 | 2026-08-19 17:13 | 2026-08-19 17:14 | 2026-08-19 17:16 | 2026-08-19 17:16 |  |  | Fair | No | Refer to emergency The entire area is experiencing low voltage 207v 108v 93v All customer is affected Pole#006382
Non-Outage | J.E.26.08.28928 | C001893802 | Dwayne Cohen |  | Completed |  |  | 2026-08-19 11:34 | 2026-08-19 11:35 | 2026-08-19 11:39 | 2026-08-19 11:40 | 2026-08-19 12:28 | 2026-08-19 12:29 | 2026-08-19 12:31 | 2026-08-19 12:31 | BrokenWire |  | Fair | No | Leaning rotten 30ft Cl6 pole need to change urgently , refer this report to Maintenance Department.
Outage | J.E.26.08.28766 | C001893821 | Christopher West | St.Catherine | Completed | Load_238106 | New Michelton - 310 | 2026-08-19 11:58 | 2026-08-19 11:59 | 2026-08-19 13:36 | 2026-08-19 13:36 | 2026-08-19 14:22 | 2026-08-19 14:29 | 2026-08-19 14:39 | 2026-08-19 14:39 |  |  | Fair | No | Kindly refer to Mr. Elliston
Outage | J.E.26.08.28841 | C001893820 | Christopher West | Portmore | Completed | Load_574643 | Naggo Head - 610 | 2026-08-19 11:58 | 2026-08-19 11:59 | 2026-08-19 14:39 | 2026-08-19 14:41 | 2026-08-19 14:41 | 2026-08-19 14:42 | 2026-08-19 14:42 | 2026-08-19 14:42 |  |  | Fair | No | Kindly refer to Mr. Elliston.
Outage | J.E.26.08.28953 | C001893819 | Christopher West | St.Catherine | Completed | Load_1000332 | Twickenham - 410 | 2026-08-19 11:58 | 2026-08-19 11:59 | 2026-08-19 12:18 | 2026-08-19 12:19 | 2026-08-19 13:35 | 2026-08-19 13:35 | 2026-08-19 13:35 | 2026-08-19 13:35 |  |  | Fair | No | Not located, calls made to number provided were unanswered
Outage | J.E.26.08.28901 | C001893830 | Lionel Robinson | Trelawny | Completed | Load_255143 | Greenwood - 110 | 2026-08-19 12:04 | 2026-08-19 15:29 | 2026-08-19 20:05 | 2026-08-19 20:56 | 2026-08-19 20:59 | 2026-08-19 20:59 | 2026-08-19 21:00 | 2026-08-19 21:00 | BrokenWire |  | Fair | No | Required 100ft #6 twisted as, conductor is damaged
Outage | J.E.26.08.28741 | C001893866 | Hartley Chin | Clarendon | Completed | Load_254038 | Parnassus - 310 | 2026-08-19 12:23 | 2026-08-19 12:28 | 2026-08-19 12:36 | 2026-08-19 12:50 | 2026-08-19 12:50 | 2026-08-19 12:50 | 2026-08-19 12:51 | 2026-08-19 12:51 |  |  | Fair | No | Call related to job # 28566
Outage | J.E.26.08.28978 | C001893877 | Radcliffe Coleman | St.Catherine | Completed | Load_569926 | Tredegar - 210 | 2026-08-19 12:31 | 2026-08-19 12:40 | 2026-08-19 13:46 | 2026-08-19 13:46 | 2026-08-19 14:18 | 2026-08-19 14:36 | 2026-08-19 14:38 | 2026-08-19 14:38 |  |  | Fair | No | Area found with two blown junction fuse (15A at pole 0092613 and a 7A at pole 0093025) and a (50kva) transformer fuse (5A). Line section was patrolled and a dead bird was found at the transformer pole. The same value fuses found were replaced and line section restored. Area now back to normal.
Outage | J.E.26.08.29101 | C001893881 | Clyde Brown | Clarendon | Completed | Load_269566 | May Pen - 110 | 2026-08-19 12:31 | 2026-08-19 12:41 | 2026-08-19 14:31 | 2026-08-19 14:32 | 2026-08-19 14:31 | 2026-08-19 14:24 | 2026-08-19 14:36 | 2026-08-19 14:36 |  |  | SevereWind | No | 15 amps tripsaver tripped at Rockriver,line patrolled and no fault seen,Tripsaver reset.
Outage | J.E.26.08.29068 | C001893890 | Christopher West | St.Catherine | Completed | Load_256621 | Twickenham - 310 | 2026-08-19 12:41 | 2026-08-19 12:43 | 2026-08-20 14:40 | 2026-08-20 14:40 | 2026-08-20 14:40 | 2026-08-20 14:40 | 2026-08-20 14:40 | 2026-08-20 14:40 |  |  | Fair | No | Kindly refer to the evening crew.
Outage | J.E.26.08.29033 | C001893891 | Clyde Brown | Clarendon | Completed | Load_244344 | May Pen - 110 | 2026-08-19 12:42 | 2026-08-19 12:44 | 2026-08-19 13:27 | 2026-08-19 13:27 | 2026-08-19 14:24 | 2026-08-19 14:24 | 2026-08-19 14:31 | 2026-08-19 14:31 |  |  | SevereWind | No | 15 amps tripsaver tripped at Rockriver line patrolled and no fault seen,Tripsaver reset and line now ok.
Outage | J.E.26.08.28979 | C001893898 | Evan Spaulding | St.Mary | Completed | Load_250071 | Highgate - 210 | 2026-08-19 12:51 | 2026-08-19 12:53 | 2026-08-19 14:07 | 2026-08-19 14:07 | 2026-08-19 14:07 | 2026-08-19 14:48 | 2026-08-19 14:49 | 2026-08-19 14:49 |  |  | Fair | No | Patrol line section no fault seen,replace 1-30 amps junction fuse at pole number 0010871.
Outage | J.E.26.08.28984 | C001893907 | Milton Charlton | KSAN | Completed | Load_238235 | Washington Blvd - 610 | 2026-08-19 13:06 | 2026-08-19 13:07 | 2026-08-19 14:01 | 2026-08-19 14:02 | 2026-08-19 15:33 | 2026-08-19 14:55 | 2026-08-19 15:38 | 2026-08-19 15:38 | TreeContact |  | Fair | No | Found okay upon arrival. Customer is telling me that JPS supposed to cut a tree for him.
Non-Outage | J.E.26.08.27203 | C001893910 | Derrick Grubb | St.Thomas | Completed | Load_264218 | Lysson - 410 | 2026-08-19 13:11 | 2026-08-19 13:12 | 2026-08-19 13:16 | 2026-08-19 13:17 | 2026-08-19 13:53 | 2026-08-19 14:25 | 2026-08-19 14:26 | 2026-08-19 14:26 |  |  | Fair | No | Clear corrosion at transformer, voltage readings 117 116 234 volts
Outage | J.E.26.08.29108 | C001893918 | Swon Miller | St.James | Completed | Load_258521 | Queens Drive - 710 | 2026-08-19 13:17 | 2026-08-19 13:18 | 2026-08-19 13:27 | 2026-08-19 13:27 | 2026-08-19 13:38 | 2026-08-20 04:30 | 2026-08-19 16:43 | 2026-08-19 16:43 | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Found two span of secondary phases and neutral down cause by public cutting tree open 50 kva transformer to carry out repairs splice and retention two span of secondary phase and neutral use 80 ft#2AA and 3 pg to carry out repairs replace five amp in 50kva transformer voltage found 0.000 voltage left 116/115/232
Outage | J.E.26.08.28892 | C001893923 | Horace Malcolm | St.James | Completed | Load_240027 | Bogue - 610 | 2026-08-19 13:21 | 2026-08-19 13:22 | 2026-08-19 18:28 | 2026-08-19 18:29 | 2026-08-19 19:33 | 2026-08-19 19:39 | 2026-08-19 19:39 | 2026-08-19 19:39 |  |  | Fair | No | Refused one 25kva transformer used one 3amp fuse
Outage | J.E.26.08.29032 | C001893924 | Swon Miller | St.James | Completed | Load_264952 | Queens Drive - 810 | 2026-08-19 13:23 | 2026-08-20 14:49 | 2026-08-20 16:39 | 2026-08-20 16:43 | 2026-08-20 17:46 | 2026-08-26 06:19 | 2026-08-20 18:19 | 2026-08-20 18:19 |  |  | Fair | No | Check and found okay customer states that power supply has been restored voltage found 114/114/229 voltage left 114/114/229
Outage | J.E.26.08.29215 | C001893925 | Andre Williams | Trelawny | Completed | Load_293023 | Greenwood - 210 | 2026-08-19 13:26 | 2026-08-20 07:55 | 2026-08-20 08:11 | 2026-08-20 08:22 | 2026-08-20 08:24 | 2026-08-20 20:26 | 2026-08-20 08:27 | 2026-08-20 08:27 | Fire |  | Fair | No | Unable to locate , need more directions phone number not working
Outage | J.E.26.08.29222 | C001893933 | Selvin White | St.Elizabeth | Completed | Load_263142 | Maggotty - 110 | 2026-08-19 13:26 | 2026-08-19 15:13 | 2026-08-19 15:38 | 2026-08-19 16:08 | 2026-08-19 16:28 | 2026-08-19 17:05 | 2026-08-19 17:07 | 2026-08-19 17:07 |  |  | Fair | No | Replace a defective 15 amp junction fuse at the entrance to the Lewisville Housing Scheme at pole number 0091216 after patrolling single phase primary line to Green Valley district. Supply restored to the affected customers.12345
Outage | J.E.26.08.29117 | C001893934 | Richard Watson | St.Elizabeth | Completed | Load_241313 | Maggotty - 110 | 2026-08-19 13:27 | 2026-08-20 07:44 | 2026-08-20 08:14 | 2026-08-20 08:15 | 2026-08-20 09:01 | 2026-08-20 09:07 | 2026-08-20 09:07 | 2026-08-20 09:07 |  |  | Fair | No | Found okay, customer breaker was turned off.
Outage | J.E.26.08.29233 | C001893941 | Javid Vernon | Westmoreland | Completed | Load_245261 | Paradise - 110 | 2026-08-19 13:35 | 2026-08-19 13:41 | 2026-08-19 13:57 | 2026-08-19 13:58 | 2026-08-19 13:57 | 2026-08-19 14:57 | 2026-08-19 14:58 | 2026-08-19 14:58 | BrokenWire |  | Fair | No | Unable to locate customer and premises after following the directions phone calls to customer number went unanswered
Non-Outage | J.E.26.06.08828 | C001893951 | Odaine Johnson | St.Catherine | Completed | Load_243824 | Rhodens Pen - 310 | 2026-08-19 13:41 | 2026-08-19 13:42 | 2026-08-20 09:11 | 2026-08-20 12:41 | 2026-08-20 12:48 | 2026-08-20 12:49 | 2026-08-20 12:49 | 2026-08-20 12:49 |  |  | Fair | No | Premises found okay customer stated that the issue was resolved already
Non-Outage | J.E.26.06.20296 | C001893950 | Odaine Johnson | St.Catherine | Completed | Load_250595 | Rhodens Pen - 310 | 2026-08-19 13:41 | 2026-08-19 13:42 | 2026-08-20 09:11 | 2026-08-20 12:50 | 2026-08-20 12:52 | 2026-08-20 12:52 | 2026-08-20 12:52 | 2026-08-20 12:52 |  |  | Fair | No | Customer stated that he didn’t made any report
Non-Outage | J.E.26.08.29229 | C001893947 | Odaine Johnson | Clarendon | Completed | Load_250072 | May Pen - 210 | 2026-08-19 13:41 | 2026-08-19 13:42 | 2026-08-20 09:11 | 2026-08-20 13:49 | 2026-08-20 14:00 | 2026-08-20 14:00 | 2026-08-20 14:01 | 2026-08-20 14:01 |  |  | Fair | No | Premises found okay customer stated that the issue was resolved
Non-Outage | J.E.26.08.29226 | C001893982 | Edward Royal | KSAS | Completed | Load_254739 | Cane River - 610 | 2026-08-19 13:52 | 2026-08-19 15:06 | 2026-08-19 18:21 | 2026-08-19 18:21 | 2026-08-19 18:24 | 2026-08-20 09:17 | 2026-08-20 09:18 | 2026-08-20 09:18 |  |  | Fair | No | Primary line is low for airport reffered to maintenance
Non-Outage | J.E.26.08.29331 | C001893983 | Edward Royal |  | Completed |  |  | 2026-08-19 13:54 | 2026-08-19 16:19 | 2026-08-19 16:23 |  | 2026-08-19 16:23 | 2026-08-19 18:04 | 2026-08-19 18:05 | 2026-08-19 18:05 | BrokenPole |  | Fair | No | Broken 4 north quad need to be repair
Outage | J.E.26.08.29302 | C001894068 | Dean- Smith | Hanover | Completed | Load_252846 | Orange Bay - 210 | 2026-08-19 14:32 | 2026-08-19 15:26 | 2026-08-19 16:34 | 2026-08-19 16:35 | 2026-08-19 19:52 | 2026-08-19 19:52 | 2026-08-19 19:58 | 2026-08-19 19:58 | Fire |  | Fair | No | Defective 50kva transformer across from negril bus park, circuit was tied to another 50kva transformer at DENNIS PAWN SHOP, said transformer was top up from 4-5. Tied location at WESTNET VISA SERVICE. Please note defective transformer leaking oil.
Non-Outage | J.E.26.08.29423 | C001894088 | Rochaine Hussey | KSAN | Completed | Load_266963 | Constant Spring - 410 | 2026-08-19 14:49 | 2026-08-20 13:12 | 2026-08-20 13:23 | 2026-08-20 13:23 | 2026-08-20 13:27 | 2026-08-20 16:08 | 2026-08-20 16:09 | 2026-08-20 16:09 |  |  | Fair | No | Customer meter is burnt which is causing the customer to be experiencing single phaseCustomer unable to use equipments Customer request new meterReferring to field service 118/118/236v
Non-Outage | J.E.26.08.29265 | C001894098 | Fredrick Hamilton | KSAN | Completed | Load_246665 | Washington Blvd - 810 | 2026-08-19 14:52 | 2026-08-19 14:53 | 2026-08-20 06:48 | 2026-08-20 09:25 | 2026-08-20 09:47 | 2026-08-20 10:31 | 2026-08-20 10:32 | 2026-08-20 10:32 |  |  | Fair | No | 238v/116v/117v obtained Slack connection detected at pole same was corrected Premises ok now
Outage | J.E.26.08.29441 | C001894129 | Romaine Roberts | St.Mary | Completed | Load_266701 | Highgate - 210 | 2026-08-19 15:08 | 2026-08-19 15:14 | 2026-08-19 15:30 | 2026-08-19 15:30 | 2026-08-19 17:25 | 2026-08-19 17:44 | 2026-08-19 17:46 | 2026-08-19 17:46 | LowHangingWires |  | Fair | No | Corrosion at pole and pothead clean and remake joints 4 clamps power restore
Outage | J.E.26.08.24014 | C001894130 | Romaine Roberts | St.Mary | Completed | Load_238462 | Highgate -110 | 2026-08-19 15:09 | 2026-08-19 15:14 | 2026-08-19 17:46 | 2026-08-19 17:47 | 2026-08-19 20:44 | 2026-08-19 20:46 | 2026-08-19 20:50 | 2026-08-19 20:50 | LeaningPole |  | Fair | No | High wind and Bamboo bang secondary and burn down one span of secondary neutral splice and retention conductor open and close 25 kva to restore power
Non-Outage | J.E.26.08.29475 | C001894141 | Lionel Robinson | Trelawny | Completed | Load_302540 | Martha Brae - 210 | 2026-08-19 15:13 | 2026-08-19 15:23 | 2026-08-19 15:32 | 2026-08-19 15:53 | 2026-08-19 17:29 | 2026-08-19 17:35 | 2026-08-19 17:37 | 2026-08-19 17:37 |  |  | Fair | No | Clean and remake corroded joints at transformer pole voltage reading left 120, 119, 238v
Outage | J.E.26.08.28733 | C001894143 | Hartley Chin | Clarendon | Completed | Load_262045 | May Pen - 210 | 2026-08-19 15:13 | 2026-08-19 15:14 | 2026-08-19 17:18 | 2026-08-19 17:57 | 2026-08-19 18:56 | 2026-08-19 18:56 | 2026-08-19 18:58 | 2026-08-19 18:58 |  |  | Fair | No | Ref to field service!!! Unable to add credit to PAY AS YOU GO METER… FIELD SERVICE TO REPAIR …
Outage | J.E.26.08.29183 | C001894142 | Hartley Chin | Clarendon | Completed | Load_269670 | May Pen - 110 | 2026-08-19 15:13 | 2026-08-19 15:26 | 2026-08-19 18:58 | 2026-08-19 18:58 | 2026-08-19 19:55 | 2026-08-19 20:32 | 2026-08-19 20:33 | 2026-08-19 20:33 | TreeContact |  | Fair | No | Remove tree limb from secondary line …
Outage | J.E.26.08.28908 | C001894144 | Neckell Ormsby | St.Mary | Completed | Load_243472 | Oracabessa - 210 | 2026-08-19 15:14 | 2026-08-19 15:15 | 2026-08-19 20:29 | 2026-08-19 20:29 | 2026-08-19 21:09 | 2026-08-19 21:26 | 2026-08-19 21:32 | 2026-08-19 21:32 | TreeContact |  | Fair | No | Found customer supply ok however trees growing in secondary needs cutting please refer to maintenance department
Outage | J.E.26.08.29412 | C001894145 | Neckell Ormsby | St.Ann | Completed | Load_244965 | Upper White River - 110 | 2026-08-19 15:14 | 2026-08-19 17:12 | 2026-08-19 18:11 | 2026-08-19 18:11 | 2026-08-19 18:52 | 2026-08-19 19:40 | 2026-08-19 19:49 | 2026-08-19 19:49 |  |  | Fair | No | Found junction fuse blown no pole # seen patrol and found tree on primary cut and remove tree and replace 1-15 amp fuse (line section needs vegetation management)
Outage | J.E.26.08.29086 | C001894148 | Richard Samuda | Manchester | Completed | Load_243336 | Kendal - 210 | 2026-08-19 15:18 | 2026-08-19 15:19 | 2026-08-19 15:28 | 2026-08-19 15:28 | 2026-08-19 15:29 | 2026-08-19 03:30 | 2026-08-19 15:30 | 2026-08-19 15:30 |  |  | Fair | No | Found ok customer said power was restored
Outage | J.E.26.08.29380 | C001894151 | Ryan Richards | Manchester | Completed | Load_252232 | Spur Tree - 310 | 2026-08-19 15:18 | 2026-08-20 07:33 | 2026-08-20 13:04 | 2026-08-20 13:05 | 2026-08-20 14:36 | 2026-08-20 15:49 | 2026-08-20 15:50 | 2026-08-20 15:50 |  |  | Rains | No | Premises found ok customer was disconnected for nonpayment of bill customer paid bill call center was contacted and customer supply was restored
Outage | J.E.26.08.29465 | C001894150 | Barnett Brown | Manchester | Completed | Load_265523 | Spur Tree - 310 | 2026-08-19 15:18 | 2026-08-19 15:19 | 2026-08-19 21:00 | 2026-08-19 21:00 | 2026-08-19 21:38 | 2026-08-19 22:26 | 2026-08-19 22:28 | 2026-08-19 22:28 |  |  | Fair | No | Balance 1 span secondary line
Outage | J.E.26.08.29471 | C001894147 | Barnett Brown | Manchester | Completed | Load_251049 | Kendal - 310 | 2026-08-19 15:18 | 2026-08-19 15:19 | 2026-08-19 19:16 | 2026-08-19 19:16 | 2026-08-19 19:16 | 2026-08-19 19:16 | 2026-08-19 19:17 | 2026-08-19 19:17 |  |  | Fair | No | Related to Lynhurst call where 25 amp junction fuse was replaced
Non-Outage | J.E.26.08.26753 | C001894156 | Richard Samuda | Manchester | Completed | Load_246417 | Kendal - 210 | 2026-08-19 15:19 | 2026-08-19 15:20 | 2026-08-19 16:04 | 2026-08-19 16:04 | 2026-08-19 16:22 | 2026-08-19 04:25 | 2026-08-19 16:26 | 2026-08-19 16:26 | LeaningPole |  | Fair | No | Pole does not belong to jps pole is flown pole
Non-Outage | J.E.26.08.28449 | C001894155 | Richard Samuda | Manchester | Completed | Load_262908 | Kendal - 210 | 2026-08-19 15:19 | 2026-08-19 15:20 | 2026-08-19 16:53 | 2026-08-19 16:53 | 2026-08-19 17:20 | 2026-08-19 17:24 | 2026-08-19 17:25 | 2026-08-19 17:25 |  |  | Fair | No | Splice and reconnected customer service neutral that was broken causing customer to experience low/ voltage using 2 1bolt clamp and 3 ft of aluminum wire voltage 116, 116 232
Non-Outage | J.E.26.08.28788 | C001894153 | Richard Samuda | Manchester | Completed | Load_262908 | Kendal - 210 | 2026-08-19 15:19 | 2026-08-19 15:20 | 2026-08-19 17:27 | 2026-08-19 17:27 | 2026-08-19 17:27 | 2026-08-19 05:27 | 2026-08-19 17:28 | 2026-08-19 17:28 |  |  | Fair | No | Customer back to normal
Non-Outage | J.E.26.08.28890 | C001894152 | Richard Samuda | Manchester | Completed | Load_247561 | Kendal - 210 | 2026-08-19 15:19 | 2026-08-19 15:20 | 2026-08-19 17:29 | 2026-08-19 17:29 | 2026-08-19 17:46 | 2026-08-19 05:48 | 2026-08-19 17:48 | 2026-08-19 17:48 |  |  | Fair | No | Customer said other group came there
Non-Outage | J.E.26.08.29278 | C001894154 | Richard Samuda | Manchester | Completed | Load_266938 | Kendal - 210 | 2026-08-19 15:19 | 2026-08-19 15:20 | 2026-08-19 17:48 | 2026-08-19 17:52 | 2026-08-19 17:59 | 2026-08-19 06:48 | 2026-08-19 18:48 | 2026-08-19 18:48 |  |  | Fair | No | Refer call Customer has. Damaged meter voltage 114 ,116 230
Outage | J.E.26.08.28991 | C001894164 | Richard Nicholas | St.Catherine | Completed | Load_261245 | Tredegar - 510 | 2026-08-19 15:22 | 2026-08-19 15:23 | 2026-08-19 20:45 | 2026-08-19 20:46 | 2026-08-19 22:36 | 2026-08-19 22:36 | 2026-08-19 22:36 | 2026-08-19 22:36 |  |  | Fair | No | Rammy system failure.
Outage | J.E.26.08.29196 | C001894162 | Richard Nicholas | St.Catherine | Completed | Load_258138 | Tredegar - 310 | 2026-08-19 15:22 | 2026-08-19 15:23 | 2026-08-19 15:41 | 2026-08-19 15:42 | 2026-08-19 16:55 | 2026-08-19 17:57 | 2026-08-19 17:59 | 2026-08-19 17:59 |  | Y | Fair | No | Spot bushing done on 25kva transformer and blown 3amp fuse replaced,pole #622655.blown 30amp junctions fuse replaced on pole #050748.
Outage | J.E.26.08.29290 | C001894163 | Richard Nicholas | St.Catherine | Completed | Load_266643 | Tredegar - 210 | 2026-08-19 15:22 | 2026-08-19 15:23 | 2026-08-19 17:59 | 2026-08-19 18:00 | 2026-08-19 18:29 | 2026-08-19 19:13 | 2026-08-19 19:15 | 2026-08-19 19:15 |  |  | Fair | No | Cut and remade burnt 50kva transformer phase drop lead on pole #587303.
Outage | J.E.26.08.28956 | C001894167 | Rusean Allen | KSAS | Completed | Load_261314 | Cane River - 310 | 2026-08-19 15:23 | 2026-08-20 07:35 | 2026-08-20 11:04 | 2026-08-20 11:05 | 2026-08-20 11:09 | 2026-08-20 11:26 | 2026-08-20 11:26 | 2026-08-20 11:26 |  |  | Fair | No | Broken service wire found at pole, wire was reconnected.
Outage | J.E.26.08.28972 | C001894166 | Rusean Allen | KSAS | Completed | Load_265012 | Rockfort - 410 | 2026-08-19 15:23 | 2026-08-19 23:31 | 2026-08-20 01:21 | 2026-08-20 01:22 | 2026-08-20 02:09 | 2026-08-20 02:13 | 2026-08-20 02:14 | 2026-08-20 02:14 |  |  | Fair | No | Defective 50KVA transformer found, transformer needs to be changed refer to maintenance department.
Outage | J.E.26.08.29334 | C001894168 | Lionel Robinson | Trelawny | Completed | Load_269724 | Greenwood - 110 | 2026-08-19 15:23 | 2026-08-19 15:27 | 2026-08-19 20:47 | 2026-08-19 20:47 | 2026-08-19 20:48 | 2026-08-19 20:55 | 2026-08-19 20:55 | 2026-08-19 20:55 | BrokenWire |  | Fair | No | Required 100ft #6 twisted, as wire is defective
Outage | J.E.26.08.29433 | C001894165 | Lionel Robinson | Trelawny | Completed | Load_294490 | Martha Brae - 110 | 2026-08-19 15:23 | 2026-08-19 15:27 | 2026-08-19 22:49 | 2026-08-19 22:50 | 2026-08-19 22:49 | 2026-08-19 22:53 | 2026-08-19 22:53 | 2026-08-19 22:53 |  |  | Fair | No | Remove and resit customer meter
Non-Outage | J.E.26.08.29323 | C001894171 | Elvis Trowers |  | Completed |  |  | 2026-08-19 15:25 | 2026-08-19 15:26 | 2026-08-19 18:32 | 2026-08-19 18:32 | 2026-08-19 18:43 | 2026-08-19 18:50 | 2026-08-19 18:46 | 2026-08-19 18:46 | BrokenWire |  | Fair | No | Reset 100 kva power transformer in bank of 3-100 kva transformer found tripped.
Non-Outage | J.E.26.08.29395 | C001894170 | Elvis Trowers |  | Completed |  |  | 2026-08-19 15:25 | 2026-08-19 15:27 | 2026-08-19 15:54 | 2026-08-19 15:55 | 2026-08-19 16:34 | 2026-08-19 16:35 | 2026-08-19 16:37 | 2026-08-19 16:37 | Fire |  | Fair | No | Y.P.box on 15 kva transformer burnt up at pole # 0100615. Isolate 15 kva transformer about 10 customers out of supply. Refer to field service.
Outage | J.E.26.08.28812 | C001894175 | Elvis Trowers | KSAS | Completed | Load_240329 | Three Miles - 410 | 2026-08-19 15:25 | 2026-08-19 15:26 | 2026-08-19 15:46 | 2026-08-19 17:39 | 2026-08-19 18:30 | 2026-08-19 18:30 | 2026-08-19 18:31 | 2026-08-19 18:31 |  |  | Fair | No | Customer meter #220398 mix up states J.P.S. Escalation. Meter is in pre- paid mood when it should be in post- paid. Refer to field service.
Outage | J.E.26.08.28849 | C001894174 | Elvis Trowers | KSAS | Completed | Load_243786 | Three Miles - 410 | 2026-08-19 15:25 | 2026-08-19 15:26 | 2026-08-19 15:53 | 2026-08-19 17:29 | 2026-08-19 17:37 | 2026-08-19 17:40 | 2026-08-19 17:39 | 2026-08-19 17:39 |  |  | Fair | No | Reconnect customer meter #2204548 by J.P.S. Escalation.
Outage | J.E.26.08.28947 | C001894173 | Elvis Trowers | KSAN | Completed | Load_293815 | Washington Blvd - 710 | 2026-08-19 15:25 | 2026-08-19 15:26 | 2026-08-19 16:37 | 2026-08-19 16:38 | 2026-08-19 16:58 | 2026-08-19 16:55 | 2026-08-19 16:59 | 2026-08-19 16:59 |  |  | Fair | No | Found okay upon arrival. Customer states matter was resolved.
Outage | J.E.26.08.29457 | C001894169 | Dean- Smith | Hanover | Completed | Load_247267 | Orange Bay - 210 | 2026-08-19 15:25 | 2026-08-19 15:26 | 2026-08-19 20:05 | 2026-08-19 20:05 | 2026-08-19 20:05 | 2026-08-19 20:05 | 2026-08-19 20:05 | 2026-08-19 20:05 |  |  | Fair | No | Check and found ok
Outage | J.E.26.08.29459 | C001894172 | Elvis Trowers | KSAN | Completed | Load_293725 | Washington Blvd - 710 | 2026-08-19 15:25 | 2026-08-19 15:26 | 2026-08-19 15:53 | 2026-08-19 17:04 | 2026-08-19 17:25 | 2026-08-19 17:25 | 2026-08-19 17:29 | 2026-08-19 17:29 |  |  | Fair | No | Reconnect customer meter #2282033 by J.P.S. Escalation.
Outage | J.E.26.08.29282 | C001894178 | Derrick Grubb | St.Thomas | Completed | Load_261733 | Good Year - 110 | 2026-08-19 15:28 | 2026-08-20 07:32 | 2026-08-20 08:36 | 2026-08-20 08:37 | 2026-08-20 09:49 | 2026-08-20 09:50 | 2026-08-20 09:50 | 2026-08-20 09:50 |  |  | Fair | No | Reconnect 3 wire service at pole
Non-Outage | J.E.26.08.28754 | C001894181 | Stephen Taylor | St.Thomas | Completed | Load_269057 | Lysson - 410 | 2026-08-19 15:29 | 2026-08-19 15:32 | 2026-08-19 16:53 | 2026-08-19 18:58 | 2026-08-19 18:58 | 2026-08-19 18:58 | 2026-08-19 19:14 | 2026-08-19 19:14 | Fire |  | Fair | No | Patrol clear line and close up 15 kva transformer safely customer is now okay
Non-Outage | J.E.26.08.29315 | C001894182 | Stephen Taylor | St.Thomas | Completed | Load_242525 | Good Year - 110 | 2026-08-19 15:29 | 2026-08-19 15:32 | 2026-08-19 16:29 | 2026-08-19 16:30 | 2026-08-19 16:30 | 2026-08-19 16:30 | 2026-08-19 16:30 | 2026-08-19 16:30 |  |  | Fair | No | Need more information a lot of call to customer no one answered the phone
Outage | J.E.26.08.28897 | C001894183 | Lionel Robinson | Trelawny | Completed | Load_292887 | Greenwood - 210 | 2026-08-19 15:29 | 2026-08-19 15:31 | 2026-08-19 18:24 | 2026-08-19 18:25 | 2026-08-19 18:41 | 2026-08-19 19:04 | 2026-08-19 19:06 | 2026-08-19 19:06 |  |  | Fair | No | Checks revealed that hexin box was off, call center was contacted and customers were re-energize
Non-Outage | J.E.26.08.26790 | C001894185 | Stephen Taylor | St.Thomas | Completed | Load_254904 | Good Year - 110 | 2026-08-19 15:30 | 2026-08-19 15:32 | 2026-08-19 15:52 | 2026-08-19 15:52 | 2026-08-19 16:03 | 2026-08-19 16:03 | 2026-08-19 16:04 | 2026-08-19 16:04 |  |  | Fair | No | Contact customer and customer say that power is back from yesterday
Non-Outage | J.E.26.08.25969 | C001894186 | Stephen Taylor | St.Thomas | Completed | Load_264721 | Good Year - 110 | 2026-08-19 15:31 | 2026-08-19 15:32 | 2026-08-19 16:09 | 2026-08-19 16:09 | 2026-08-19 16:12 | 2026-08-19 16:12 | 2026-08-19 16:15 | 2026-08-19 16:15 |  |  | Fair | No | Jps meter defective and need to change by a jps technician
Non-Outage | J.E.26.08.26182 | C001894187 | Stephen Taylor | St.Thomas | Completed | Load_270128 | Good Year - 110 | 2026-08-19 15:31 | 2026-08-19 15:32 | 2026-08-19 16:29 | 2026-08-19 16:29 | 2026-08-19 16:29 | 2026-08-19 16:29 | 2026-08-19 16:29 | 2026-08-19 16:29 |  |  | Fair | No | Contact customer and customer say that power is back from yesterday
Non-Outage | J.E.26.08.26277 | C001894188 | Stephen Taylor | St.Thomas | Completed | Load_242525 | Good Year - 110 | 2026-08-19 15:31 | 2026-08-19 15:32 | 2026-08-19 16:27 | 2026-08-19 16:28 | 2026-08-19 16:27 | 2026-08-19 16:27 | 2026-08-19 16:28 | 2026-08-19 16:28 |  |  | Fair | No | Need more information a lot of call to customer no one answered the phone
Non-Outage | J.E.26.08.29480 | C001894193 | Eric Williams |  | Completed |  |  | 2026-08-19 15:34 | 2026-08-19 15:36 | 2026-08-19 15:49 | 2026-08-19 15:50 | 2026-08-19 16:52 | 2026-08-19 16:53 | 2026-08-19 17:00 | 2026-08-19 17:00 | BrokenPole |  | Fair | No | Vehicle accident ( broken 30 class 6 pole) refer to maintenance department
Outage | J.E.26.08.29068 | C001894196 | Donald Cunningham | St.Catherine | Completed | Load_256621 | Twickenham - 310 | 2026-08-19 15:34 | 2026-08-19 15:35 | 2026-08-19 15:57 | 2026-08-19 15:58 | 2026-08-19 17:14 | 2026-08-19 17:38 | 2026-08-19 17:39 | 2026-08-19 17:39 |  |  | Fair | No | Blown 25 kva transformer replace 5 amp fuse
Outage | J.E.26.08.29389 | C001894195 | Donald Cunningham | St.Catherine | Completed | Load_252381 | Twickenham - 310 | 2026-08-19 15:34 | 2026-08-19 15:35 | 2026-08-19 17:39 | 2026-08-19 17:41 | 2026-08-19 18:45 | 2026-08-19 18:47 | 2026-08-19 19:19 | 2026-08-19 19:19 |  |  | Fair | No | Broken service wire splice and retention using 60 feet of #6 triplex
Outage | J.E.26.08.29451 | C001894192 | Eric Williams | KSAN | Completed | Load_253549 | Hope - 510 | 2026-08-19 15:34 | 2026-08-19 15:36 | 2026-08-19 17:00 | 2026-08-19 17:01 | 2026-08-19 17:22 | 2026-08-19 18:31 | 2026-08-19 18:32 | 2026-08-19 18:32 |  |  | Fair | No | 2 burnt hotline clamps found and replace,
Outage | J.E.26.08.29486 | C001894194 | Eric Williams | KSAN | Completed | Load_247023 | Constant Spring - 210 | 2026-08-19 15:34 | 2026-08-19 15:36 | 2026-08-19 18:33 | 2026-08-19 18:33 | 2026-08-19 19:38 | 2026-08-19 19:51 | 2026-08-19 19:51 | 2026-08-19 19:51 | LowHangingWires |  | Fair | No | System neutral and Service wire with party wires seen low hanging over premises, sent to maintenance to have same corrected cause it needs a plan outage.
Outage | J.E.26.08.28881 | C001894213 | Raymond Lewis | St.Ann | Completed | Load_246811 | Roaring River - 410 | 2026-08-19 15:47 | 2026-08-19 15:49 | 2026-08-19 20:28 | 2026-08-19 20:28 | 2026-08-19 22:35 | 2026-08-19 23:23 | 2026-08-19 23:23 | 2026-08-19 23:23 |  |  | Fair | No | Remove vegetation from line and splice and retention 2 wire service
Outage | J.E.26.08.29192 | C001894214 | Raymond Lewis | St.Ann | Completed | Load_247798 | Roaring River - 210 | 2026-08-19 15:47 | 2026-08-19 15:49 | 2026-08-19 15:58 | 2026-08-19 15:59 | 2026-08-19 17:03 | 2026-08-19 17:01 | 2026-08-19 17:05 | 2026-08-19 17:05 | BrokenWire |  | Fair | No | Supply restored
Outage | J.E.26.08.28412 | C001894217 | Raymond Lewis | St.Ann | Completed | Load_248710 | Roaring River - 210 | 2026-08-19 15:53 | 2026-08-19 15:55 | 2026-08-19 17:06 | 2026-08-19 17:07 | 2026-08-19 17:07 | 2026-08-19 17:08 | 2026-08-19 17:09 | 2026-08-19 17:09 |  |  | Fair | No | Refer to field service
Non-Outage | J.E.26.08.26231 | C001894221 | Dwayne Samuels | Trelawny | Completed | Load_249194 | Duncans - 110 | 2026-08-19 15:55 | 2026-08-19 15:56 | 2026-08-19 20:52 | 2026-08-19 20:52 | 2026-08-19 21:32 | 2026-08-19 22:13 | 2026-08-19 22:13 | 2026-08-19 22:13 |  |  | Fair | No | Customer is located at the end of the line voltage found at that pole is 89v/109v/197v after further checks at transformer pole voltage found is 119v 119v 237v day light attention required due to the among of illegal connections..
Non-Outage | J.E.26.08.28896 | C001894220 | Dwayne Samuels | Trelawny | Completed | Load_270236 | Duncans - 210 | 2026-08-19 15:55 | 2026-08-19 15:56 | 2026-08-19 17:45 | 2026-08-19 19:40 | 2026-08-19 20:10 | 2026-08-19 20:51 | 2026-08-19 20:51 | 2026-08-19 20:51 |  |  | Fair | No | Corrosion at pole was the cause of customer single phasing use 1 one bolt clamp at same for repair customer meter is in locking band voltage left at pothead 114v/111v/225v
Outage | J.E.26.08.28903 | C001894222 | Roxroy Needham | St.Ann | Completed | Load_266280 | Cardiff Hall - 310 | 2026-08-19 15:55 | 2026-08-19 15:58 | 2026-08-19 17:15 | 2026-08-19 17:16 | 2026-08-19 17:39 | 2026-08-19 17:41 | 2026-08-19 17:42 | 2026-08-19 17:42 | BrokenWire |  | Fair | No | Customer was unable to locate
Outage | J.E.26.08.29088 | C001894219 | Roxroy Needham | St.Ann | Completed | Load_259933 | Cardiff Hall - 310 | 2026-08-19 15:55 | 2026-08-19 15:58 | 2026-08-19 16:29 | 2026-08-19 16:29 | 2026-08-19 17:14 | 2026-08-19 17:15 | 2026-08-19 17:15 | 2026-08-19 17:15 |  |  | Fair | No | Customer light disconnect for nonpayment
Outage | J.E.26.08.29097 | C001894218 | Roxroy Needham | St.Ann | Completed | Load_269661 | Cardiff Hall - 310 | 2026-08-19 15:55 | 2026-08-19 15:58 | 2026-08-19 17:42 | 2026-08-19 17:43 | 2026-08-19 18:53 | 2026-08-19 18:55 | 2026-08-19 18:55 | 2026-08-19 18:55 |  |  | Fair | No | Not getting customer on the phone
Outage | J.E.26.08.28742 | C001894226 | Neckell Ormsby | St.Ann | Completed | Load_576566 | Upper White River - 210 | 2026-08-19 16:00 | 2026-08-19 16:03 | 2026-08-19 17:30 | 2026-08-19 17:30 | 2026-08-19 17:30 | 2026-08-19 17:52 | 2026-08-19 18:10 | 2026-08-19 18:10 |  |  | Fair | No | Found 100kva transformer fuse blown at square o pole # seen replace 1-10 amp fuse
Outage | J.E.26.08.29523 | C001894228 | Dean- Smith | Hanover | Completed | Load_302836 | Orange Bay - 310 | 2026-08-19 16:00 | 2026-08-19 16:01 | 2026-08-19 20:06 | 2026-08-19 20:07 | 2026-08-19 21:53 | 2026-08-19 21:53 | 2026-08-19 21:53 | 2026-08-19 21:53 |  |  | Fair | No | Clean corrosion at customer meter pole and at jps pole. Voltage left 120v,120v,230v.
Outage | J.E.26.08.29531 | C001894227 | Dean- Smith | Hanover | Completed | Load_252846 | Orange Bay - 210 | 2026-08-19 16:00 | 2026-08-19 16:01 | 2026-08-19 19:58 | 2026-08-19 19:59 | 2026-08-19 19:58 | 2026-08-19 19:58 | 2026-08-19 19:59 | 2026-08-19 19:59 |  |  | Fair | No | Customer restored, tied to another circuit.
Outage | J.E.26.08.29413 | C001894236 | Oshane Warren | Westmoreland | Completed | Load_292895 | Paradise - 310 | 2026-08-19 16:01 | 2026-08-19 16:03 | 2026-08-19 18:27 | 2026-08-19 18:27 | 2026-08-19 18:27 | 2026-08-19 18:27 | 2026-08-19 18:29 | 2026-08-19 18:29 | BrokenPole |  | Rains | No | Retired pole in line section need to remove
Outage | J.E.26.08.29190 | C001894239 | Michael Paterson | Westmoreland | Completed | Load_267686 | Paradise - 210 | 2026-08-19 16:02 | 2026-08-19 16:03 | 2026-08-19 19:13 | 2026-08-19 20:03 | 2026-08-19 20:02 | 2026-08-19 21:29 | 2026-08-19 21:29 | 2026-08-19 21:29 |  |  | Fair | No | Found 25kva xfmr fuse blown, also found six span of secondary broken, spot bushing done, repair done using 5 clamps, 80ft #2 , two #2 preform,replace 2amps fuse, supply restored, voltage readings, 117v, 117v, 234v.
Outage | J.E.26.08.29325 | C001894238 | Michael Paterson | Westmoreland | Completed | Load_245389 | Paradise - 210 | 2026-08-19 16:02 | 2026-08-19 16:03 | 2026-08-19 16:44 | 2026-08-19 16:44 | 2026-08-19 19:12 | 2026-08-19 19:12 | 2026-08-19 19:12 | 2026-08-19 19:12 |  |  | Fair | No | Customer confirm ok via phone call.
Outage | J.E.26.08.29195 | C001894242 | Kemark Slue | St.Catherine | Completed | Load_265333 | New Michelton - 210 | 2026-08-19 16:08 | 2026-08-19 16:09 | 2026-08-19 16:18 | 2026-08-19 16:18 | 2026-08-19 18:07 | 2026-08-19 18:13 | 2026-08-19 18:14 | 2026-08-19 18:14 |  |  | Fair | No | Premises was checked and found okay.
Outage | J.E.26.08.29371 | C001894243 | Kemark Slue | St.Catherine | Completed | Load_249743 | New Michelton - 310 | 2026-08-19 16:08 | 2026-08-19 16:09 | 2026-08-19 18:07 | 2026-08-19 18:14 | 2026-08-19 20:06 | 2026-08-19 19:29 | 2026-08-19 20:08 | 2026-08-19 20:08 |  |  | Fair | No | Upon arrival at the location the crew discovered that 10 kva 13.8 kv transformer fuse was blown resulting from creepers that had taken over the pole, cut and clear creepers, refuse link and re-energized circuit.
Outage | J.E.26.08.29391 | C001894244 | Kemark Slue | St.Catherine | Completed | Load_252307 | New Michelton - 210 | 2026-08-19 16:08 | 2026-08-19 16:09 | 2026-08-19 18:57 | 2026-08-19 20:08 | 2026-08-19 20:08 | 2026-08-19 20:01 | 2026-08-19 20:55 | 2026-08-19 20:55 |  |  | Fair | No | Upon arrival at the location the crew discovered that 2-wire meter supplying the customer is defective please refer to Field service department to have meter changed asap.
Outage | J.E.26.08.28495 | C001894245 | Kemark Slue | St.Catherine | Completed | Load_253496 | New Michelton - 210 | 2026-08-19 16:10 | 2026-08-19 16:11 | 2026-08-19 18:59 | 2026-08-19 20:56 | 2026-08-19 21:20 | 2026-08-19 21:22 | 2026-08-19 21:44 | 2026-08-19 21:44 | Fire |  | Fair | No | Upon arrival at the location the crew discovered that illegal connections caused customer’s #6 triplex service to burn, splice and retention #6 service using approximately 20 ft of #6 triplex service and four one bolt clamps.
Outage | J.E.26.08.26275 | C001894248 | Raymond Lewis | St.Ann | Completed | Load_265764 | Upper White River - 110 | 2026-08-19 16:11 | 2026-08-19 19:21 | 2026-08-19 20:06 | 2026-08-19 20:07 | 2026-08-19 20:22 | 2026-08-19 20:24 | 2026-08-19 20:25 | 2026-08-19 20:25 |  |  | Fair | No | St.mary call
Outage | J.E.26.08.29446 | C001894251 | Romeo Brissett | St.James | Completed | Load_261969 | Bogue - 310 | 2026-08-19 16:15 | 2026-08-19 16:19 | 2026-08-19 16:45 | 2026-08-19 16:45 | 2026-08-19 17:36 | 2026-08-19 18:40 | 2026-08-19 19:07 | 2026-08-19 19:07 |  |  | Fair | No | Removed vegetation and replaced (1)15amps junction fuse
Outage | J.E.26.08.29463 | C001894249 | Romeo Brissett | St.James | Completed | Load_576009 | Bogue - 310 | 2026-08-19 16:15 | 2026-08-19 16:19 | 2026-08-19 21:25 | 2026-08-19 21:26 | 2026-08-19 21:25 | 2026-08-19 21:40 | 2026-08-19 21:43 | 2026-08-19 21:43 |  |  | Fair | No | Replaced (1)10amps junction fuse
Outage | J.E.26.08.29491 | C001894256 | Richard Samuda | Manchester | Completed | Load_240486 | Kendal - 210 | 2026-08-19 16:19 | 2026-08-19 16:20 | 2026-08-19 16:28 | 2026-08-19 16:28 | 2026-08-19 16:50 | 2026-08-19 04:51 | 2026-08-19 16:51 | 2026-08-19 16:51 |  |  | Fair | No | Found ok customer said power was restored
Outage | J.E.26.08.29526 | C001894257 | Barnett Brown | Manchester | Completed | Load_238224 | Kendal - 310 | 2026-08-19 16:20 | 2026-08-19 17:18 | 2026-08-19 17:57 | 2026-08-19 17:59 | 2026-08-19 17:59 | 2026-08-19 19:11 | 2026-08-19 19:15 | 2026-08-19 19:15 |  |  | Fair | No | Patrol line, found nothing, replace blown 25 amp junction fuse at Coolie mountain.
Outage | J.E.26.08.29563 | C001894258 | Raymond Lewis | St.Ann | Completed | Load_239944 | Roaring River - 410 | 2026-08-19 16:21 | 2026-08-19 16:22 | 2026-08-19 17:29 | 2026-08-19 17:30 | 2026-08-19 17:48 | 2026-08-19 18:44 | 2026-08-19 18:44 | 2026-08-19 18:44 | BrokenWire |  | Fair | No | Splice and retention 3 wire service
Non-Outage | J.E.26.08.29547 | C001894273 | Denton Williams |  | Completed |  |  | 2026-08-19 16:28 | 2026-08-19 16:29 | 2026-08-19 17:11 | 2026-08-19 17:11 | 2026-08-19 17:11 | 2026-08-19 17:11 | 2026-08-19 17:12 | 2026-08-19 17:12 |  |  | Fair | No | No valid contact info.
Non-Outage | J.E.26.08.29258 | C001894290 | Wan Carlos Scarlett |  | Completed |  |  | 2026-08-19 16:32 | 2026-08-19 16:33 | 2026-08-19 17:28 | 2026-08-19 19:55 | 2026-08-19 20:22 | 2026-08-19 20:34 | 2026-08-19 20:34 | 2026-08-19 20:34 |  |  | Fair | No | Customer confirm that power supply has been restored
Outage | J.E.26.08.28043 | C001894286 | Wan Carlos Scarlett | St.Catherine | Completed | Load_248409 | Twickenham - 210 | 2026-08-19 16:32 | 2026-08-19 16:33 | 2026-08-19 21:11 | 2026-08-19 21:12 | 2026-08-19 21:56 | 2026-08-19 22:20 | 2026-08-19 22:21 | 2026-08-19 22:21 | LowHangingWires |  | Fair | No | Customer report streetlight not working
Outage | J.E.26.08.28700 | C001894287 | Wan Carlos Scarlett | Portmore | Completed | Load_268575 | Naggo Head - 610 | 2026-08-19 16:32 | 2026-08-19 16:33 | 2026-08-19 16:43 | 2026-08-19 16:44 | 2026-08-19 17:16 | 2026-08-19 17:44 | 2026-08-19 17:45 | 2026-08-19 17:45 |  |  | Fair | No | Customer confirmed that power supply has been restored check and found okay
Outage | J.E.26.08.28730 | C001894288 | Wan Carlos Scarlett | St.Catherine | Completed | Load_243634 | Twickenham - 210 | 2026-08-19 16:32 | 2026-08-19 16:33 | 2026-08-19 17:23 | 2026-08-19 17:46 | 2026-08-19 18:32 | 2026-08-19 19:05 | 2026-08-19 19:09 | 2026-08-19 19:09 |  |  | Fair | No | Found 25KVA transformer drop lead wire to open secondary line phase burn off use 3 one bolt clamps at pole readings 116-115-231
Outage | J.E.26.08.28794 | C001894289 | Wan Carlos Scarlett | Portmore | Completed | Load_570186 | Naggo Head - 610 | 2026-08-19 16:32 | 2026-08-19 16:33 | 2026-08-19 20:34 | 2026-08-19 20:35 | 2026-08-19 20:53 | 2026-08-19 21:11 | 2026-08-19 21:11 | 2026-08-19 21:11 |  |  | Fair | No | Customer not available at this time premises closed
Outage | J.E.26.08.29596 | C001894310 | Wayne Dillion | Manchester | Completed | Load_254226 | Spur Tree - 210 | 2026-08-19 16:42 | 2026-08-19 16:46 | 2026-08-19 19:21 | 2026-08-19 19:21 | 2026-08-19 19:21 | 2026-08-19 19:22 | 2026-08-19 19:23 | 2026-08-19 19:23 |  |  | Fair | No | Unable to locate and customer not answering the phone.
Outage | J.E.26.08.29571 | C001894311 | Selvin White | St.Elizabeth | Completed | Load_268311 | Maggotty - 210 | 2026-08-19 16:43 | 2026-08-19 16:47 | 2026-08-19 22:41 | 2026-08-19 22:42 | 2026-08-19 22:56 | 2026-08-19 23:01 | 2026-08-19 23:01 | 2026-08-19 23:01 |  |  | Fair | No | Escalation department was contacted and said order was referred to the field service department due to a bill of that is outstanding that needs to be paid before reconnection can done.
Outage | J.E.26.08.29598 | C001894312 | Selvin White | St.Elizabeth | Completed | Load_292313 | Maggotty - 110 | 2026-08-19 16:43 | 2026-08-19 16:47 | 2026-08-19 17:07 | 2026-08-19 17:08 | 2026-08-19 17:08 | 2026-08-19 17:12 | 2026-08-19 17:12 | 2026-08-19 17:12 |  |  | Fair | No | Replace a defective 15 amp fuse at the entrance to the Lewisville housing scheme after patrolling single phase primary line. Supply restored to the affected customers.
Outage | J.E.26.08.29612 | C001894314 | Wayne Dillion | Manchester | Completed | Load_246480 | Spur Tree - 210 | 2026-08-19 16:45 | 2026-08-19 16:46 | 2026-08-19 17:22 | 2026-08-19 17:22 | 2026-08-19 18:20 | 2026-08-19 18:42 | 2026-08-19 18:42 | 2026-08-19 18:42 |  |  | Fair | No | Supply check on found area having low voltage other check found that customer meter socket on wire burn disconnect at pothead and advise customer to get and electrician to carry out repairs voltage found in area was 137v 78v voltage leave in area 113 v 112v 225v supply working ok
Outage | J.E.26.08.29616 | C001894324 | Wayne Dillion | Manchester | Completed | Load_292330 | Spur Tree - 210 | 2026-08-19 17:01 | 2026-08-19 17:03 | 2026-08-19 17:18 | 2026-08-19 17:19 | 2026-08-19 17:18 | 2026-08-19 17:20 | 2026-08-19 17:21 | 2026-08-19 17:21 |  |  | Fair | No | Unable to locate and customer phone is not working.
Outage | J.E.26.08.29637 | C001894332 | Neckell Ormsby | St.Mary | Completed | Load_258258 | Oracabessa - 210 | 2026-08-19 17:12 | 2026-08-19 18:03 | 2026-08-19 19:50 | 2026-08-19 19:50 | 2026-08-19 20:12 | 2026-08-19 20:27 | 2026-08-19 20:28 | 2026-08-19 20:28 |  |  | Fair | No | Found customer with defective meter please refer to field service to have meter changed customer very irated voltage left 112v ( meter blank)
Outage | J.E.26.08.29631 | C001894333 | Ryan Richards | Manchester | Completed | Load_254997 | Porus - 210 | 2026-08-19 17:13 | 2026-08-20 07:33 | 2026-08-20 08:07 | 2026-08-20 08:07 | 2026-08-20 09:15 | 2026-08-20 09:47 | 2026-08-20 09:47 | 2026-08-20 09:47 |  |  | Fair | No | Burn off phase found at pole an pothead cause by illegal connections remade using 3 penunion 2 one bolt clamps voltage 116/114/230 volts
Outage | J.E.26.08.29638 | C001894334 | Roxroy Needham | St.Ann | Completed | Load_266408 | Cardiff Hall - 210 | 2026-08-19 17:13 | 2026-08-19 17:14 | 2026-08-19 18:55 | 2026-08-19 18:55 | 2026-08-19 18:55 | 2026-08-19 18:57 | 2026-08-19 18:57 | 2026-08-19 18:57 | BrokenWire |  | Fair | No | Retention customer service wire at pole used 1 preformed
Outage | J.E.26.08.29644 | C001894337 | Romeo Brissett | St.James | Completed | Load_244480 | Bogue - 310 | 2026-08-19 17:19 | 2026-08-19 17:22 | 2026-08-19 19:07 | 2026-08-19 19:07 | 2026-08-19 20:08 | 2026-08-19 20:20 | 2026-08-19 20:31 | 2026-08-19 20:31 |  |  | Fair | No | Replaced (1)8amps junction fuse and (1)10KVA transformer fuse.
Outage | J.E.26.08.29646 | C001894351 | Richard Watson | St.Elizabeth | Completed | Load_254522 | Maggotty - 210 | 2026-08-19 17:42 | 2026-08-20 07:55 | 2026-08-20 09:59 | 2026-08-20 10:00 | 2026-08-20 10:26 | 2026-08-20 10:37 | 2026-08-20 10:40 | 2026-08-20 10:40 |  |  | Fair | No | Found junction switch open, patrol and found jumper resting on pole, cleared using switch stick, energized primary line and transformer by closing junction switch, customer still without supply due to missing meter and broken service wire, please refer to Field service department for meter and service wire replacement. Customer out of supply since hurricane Melissa.
Outage | J.E.26.08.29650 | C001894350 | Wayne Dillion | St.Elizabeth | Completed | Load_260745 | Maggotty - 210 | 2026-08-19 17:42 | 2026-08-19 17:43 | 2026-08-19 18:54 | 2026-08-19 18:55 | 2026-08-19 18:55 | 2026-08-19 18:57 | 2026-08-19 18:58 | 2026-08-19 18:58 |  |  | Fair | No | Please refer to day light attention. Customer said we must visit in the morning.
Outage | J.E.26.08.29209 | C001894352 | Richard Nicholas | St.Catherine | Completed | Load_252533 | Tredegar - 310 | 2026-08-19 17:43 | 2026-08-19 17:44 | 2026-08-19 19:15 | 2026-08-19 19:16 | 2026-08-19 20:13 | 2026-08-19 20:43 | 2026-08-19 20:45 | 2026-08-19 20:45 | BrokenWire |  | Fair | No | Splice and retention 2 span of broken secondary phase,5ft of 2/0 aac and 4 clamp was use to complete the repair.
Outage | J.E.26.08.29658 | C001894354 | Raymond Lewis | St.Ann | Completed | Load_576608 | Upper White River - 210 | 2026-08-19 17:44 | 2026-08-19 17:46 | 2026-08-19 19:21 | 2026-08-19 19:22 | 2026-08-19 19:21 | 2026-08-19 20:06 | 2026-08-19 20:06 | 2026-08-19 20:06 |  |  | Fair | No | Definitely switch need to replace fuse solid out
Outage | J.E.26.08.29682 | C001894353 | Dean- Smith | Hanover | Completed | Load_303169 | Orange Bay - 210 | 2026-08-19 17:44 | 2026-08-19 17:51 | 2026-08-19 19:59 | 2026-08-19 20:00 | 2026-08-19 19:59 | 2026-08-19 19:59 | 2026-08-19 20:04 | 2026-08-19 20:04 |  |  | Fair | No | Customer restored, tied to another circuit.
Outage | J.E.26.08.29685 | C001894355 | Denton Williams | Portland | Completed | Load_250580 | Port Antonio - 410 | 2026-08-19 17:46 | 2026-08-19 17:47 | 2026-08-19 17:51 | 2026-08-19 17:52 | 2026-08-19 18:41 | 2026-08-19 19:13 | 2026-08-19 19:16 | 2026-08-19 19:16 | BrokenWire |  | Fair | No | Use 20 feet of #2aaa wire to correct broken phase conductor caused by vehicle accident.
Outage | J.E.26.08.29693 | C001894357 | Neckell Ormsby | St.Mary | Completed | Load_348546 | Oracabessa - 210 | 2026-08-19 17:51 | 2026-08-19 17:52 | 2026-08-19 21:34 | 2026-08-19 21:35 | 2026-08-19 21:58 | 2026-08-19 22:16 | 2026-08-19 22:24 | 2026-08-19 22:24 |  |  | Fair | No | Found customer without supply troubleshoot and customer with internal fault, customer was advised voltage left at meter socket 116v 117v 233v
Outage | J.E.26.08.29651 | C001894361 | Roxroy Needham | St.Ann | Completed | Load_267779 | Cardiff Hall - 310 | 2026-08-19 17:57 | 2026-08-19 17:58 | 2026-08-19 18:57 | 2026-08-19 18:58 | 2026-08-19 20:03 | 2026-08-19 20:04 | 2026-08-19 20:13 | 2026-08-19 20:13 |  |  | Fair | No | Not getting customer on phone
Outage | J.E.26.08.29645 | C001894373 | Richard Samuda | Manchester | Completed | Load_246637 | Kendal - 210 | 2026-08-19 18:23 | 2026-08-19 18:24 | 2026-08-19 18:52 | 2026-08-19 18:52 | 2026-08-19 19:37 | 2026-08-19 08:16 | 2026-08-19 20:16 | 2026-08-19 20:16 |  |  | Fair | No | Pole number: 0176168 found 30 amp junction blown patrol Line found 25 amp junction blown patrol line found nothing replaced 30 amp fuse then 25amp customer back to normal
Outage | J.E.26.08.29696 | C001894374 | Richard Samuda | Manchester | Completed | Load_262155 | Kendal - 210 | 2026-08-19 18:23 | 2026-08-19 18:24 | 2026-08-19 20:46 | 2026-08-19 20:47 | 2026-08-19 20:46 | 2026-08-19 08:48 | 2026-08-19 20:48 | 2026-08-19 20:48 |  |  | Fair | No | Customer back to normal
Non-Outage | J.E.26.08.29331 | C001894377 | Elvis Trowers |  | Completed |  |  | 2026-08-19 18:39 | 2026-08-19 18:40 | 2026-08-19 18:46 | 2026-08-19 18:46 | 2026-08-19 18:46 | 2026-08-19 19:10 | 2026-08-19 18:55 | 2026-08-19 18:55 | BrokenPole |  | Fair | No | Customer service wire #2/0 qaud damage in motor vehicle accident. Unable to repair customer service wire due to broken pilot pole on customer premises . Customer 30ft wooden pole need to be replaced before reconnection. Disconnect 2/0 quad.
Outage | J.E.26.08.29781 | C001894381 | Horace Malcolm | St.James | Completed | Load_263700 | Bogue - 610 | 2026-08-19 18:43 | 2026-08-19 18:45 | 2026-08-19 19:39 | 2026-08-19 19:40 | 2026-08-19 19:48 | 2026-08-19 20:38 | 2026-08-19 20:38 | 2026-08-19 20:38 |  |  | Fair | No | Retention one pole span primary line used one #2 preform and refuse one 15amp junction fuse
Outage | J.E.26.08.29632 | C001894393 | Javid Vernon | Westmoreland | Completed | Load_293106 | Paradise - 110 | 2026-08-19 18:58 | 2026-08-20 07:24 | 2026-08-20 08:43 | 2026-08-20 08:44 | 2026-08-20 09:37 | 2026-08-20 09:43 | 2026-08-20 09:48 | 2026-08-20 09:48 |  |  | Fair | No | Unable to locate customer and premises with directions given phone calls tocustomer number went unanswered
Outage | J.E.26.08.29757 | C001894392 | Wayne Dillion | St.Elizabeth | Completed | Load_292325 | Maggotty - 210 | 2026-08-19 18:58 | 2026-08-19 19:00 | 2026-08-19 22:10 | 2026-08-19 22:10 | 2026-08-19 22:10 | 2026-08-19 22:11 | 2026-08-19 22:11 | 2026-08-19 22:11 |  |  | Fair | No | Customer got disconnected due to none paying of bill
Outage | J.E.26.08.29813 | C001894397 | Romeo Brissett | St.James | Completed | Load_239445 | Queens Drive - 710 | 2026-08-19 19:02 | 2026-08-19 19:04 | 2026-08-19 21:44 | 2026-08-19 22:09 | 2026-08-19 22:41 | 2026-08-19 23:00 | 2026-08-19 23:07 | 2026-08-19 23:07 |  |  | Fair | No | Line patrolled and found power in the area, phone number ring to voicemail
Outage | J.E.26.08.29820 | C001894395 | Lionel Robinson | Trelawny | Completed | Load_260728 | Martha Brae - 110 | 2026-08-19 19:02 | 2026-08-19 19:04 | 2026-08-19 21:18 | 2026-08-19 21:19 | 2026-08-19 22:41 | 2026-08-19 22:42 | 2026-08-19 22:42 | 2026-08-19 22:42 |  |  | Fair | No
Outage | J.E.26.08.29828 | C001894396 | Horace Malcolm | St.James | Completed | Load_567728 | Bogue - 610 | 2026-08-19 19:02 | 2026-08-19 19:04 | 2026-08-19 20:38 | 2026-08-19 20:39 | 2026-08-19 21:23 | 2026-08-19 21:42 | 2026-08-19 21:42 | 2026-08-19 21:42 |  |  | Fair | No | Check an found customer not disconnected multiple calls to customer unavailable
Outage | J.E.26.08.29737 | C001894398 | Tyrese Williams | St.Ann | Completed | Load_266280 | Cardiff Hall - 310 | 2026-08-19 19:04 | 2026-08-20 07:42 | 2026-08-20 10:53 | 2026-08-20 10:53 | 2026-08-20 11:37 | 2026-08-20 11:39 | 2026-08-20 11:41 | 2026-08-20 11:41 | BrokenWire |  | Fair | No | Premises found ok customer had internal problem
Outage | J.E.26.08.29601 | C001894402 | Hartley Chin | Clarendon | Completed | Load_254038 | Parnassus - 310 | 2026-08-19 19:05 | 2026-08-19 19:06 | 2026-08-19 20:33 | 2026-08-19 20:58 | 2026-08-19 20:58 | 2026-08-19 20:58 | 2026-08-19 20:59 | 2026-08-19 20:59 |  |  | Fair | No | Call related to job # 28566 ..
Outage | J.E.26.08.29624 | C001894399 | Clyde Brown | Clarendon | Completed | Load_405784 | Parnassus - 210 | 2026-08-19 19:05 | 2026-08-20 07:24 | 2026-08-20 08:17 | 2026-08-20 08:18 | 2026-08-20 08:50 | 2026-08-20 08:53 | 2026-08-20 09:10 | 2026-08-20 09:10 |  |  | Fair | No | Customer said they told her light is at the premises but she had not been there to confirm
Outage | J.E.26.08.29785 | C001894401 | Hartley Chin | Clarendon | Completed | Load_254038 | Parnassus - 310 | 2026-08-19 19:05 | 2026-08-19 19:06 | 2026-08-19 20:33 | 2026-08-19 20:34 | 2026-08-19 20:57 | 2026-08-19 20:58 | 2026-08-19 20:58 | 2026-08-19 20:58 |  |  | Fair | No | Call related to job # 28566 ..
Non-Outage | J.E.26.08.21382 | C001894415 | Locksley Allen | St.Mary | Completed | Load_249551 | Annotto Bay - 310 | 2026-08-19 19:13 | 2026-08-20 08:20 | 2026-08-20 10:26 | 2026-08-20 11:22 | 2026-08-20 11:22 | 2026-08-20 11:25 | 2026-08-20 11:27 | 2026-08-20 11:27 |  |  | Fair | No | Check transformer
Non-Outage | J.E.26.08.29119 | C001894416 | Locksley Allen | St.Mary | Completed | Load_260130 | Annotto Bay - 310 | 2026-08-19 19:13 | 2026-08-20 08:20 | 2026-08-20 11:27 | 2026-08-20 11:27 | 2026-08-20 11:27 | 2026-08-20 11:47 | 2026-08-20 11:44 | 2026-08-20 11:44 |  |  | Fair | No | Check transformer. Voltage at meter socket phase to phase 321&413(190 leg)
Outage | J.E.26.08.29381 | C001894421 | Barnett Brown | Manchester | Completed | Load_251310 | Kendal - 310 | 2026-08-19 19:16 | 2026-08-19 19:17 | 2026-08-19 19:35 | 2026-08-19 19:35 | 2026-08-19 20:16 | 2026-08-19 20:58 | 2026-08-19 20:59 | 2026-08-19 20:59 | Fire |  | Fair | No | Clear cable neutral from service wire
Non-Outage | J.E.26.08.29823 | C001894422 | Donald Cunningham | St.Catherine | Completed | Load_1000959 | Tredegar - 410 | 2026-08-19 19:17 | 2026-08-19 19:18 | 2026-08-19 20:21 | 2026-08-19 20:21 | 2026-08-19 21:23 | 2026-08-19 21:24 | 2026-08-19 21:28 | 2026-08-19 21:28 |  |  | Fair | No | Premises closed
Non-Outage | J.E.26.08.29845 | C001894439 | Wayne Dillion |  | Completed |  |  | 2026-08-19 19:36 | 2026-08-19 19:38 | 2026-08-19 20:00 | 2026-08-19 20:01 | 2026-08-19 20:13 | 2026-08-19 20:50 | 2026-08-19 20:53 | 2026-08-19 20:53 | BrokenWire |  | Fair | No | Patrol and found clear. Replace one blown 10amp junction fuse no pole# and one 8amp junction fuse no pole#. Supply restored okay.
Non-Outage | J.E.26.08.29866 | C001894440 | Wayne Dillion |  | Completed |  |  | 2026-08-19 19:36 | 2026-08-19 19:38 | 2026-08-19 20:54 | 2026-08-19 20:54 | 2026-08-19 20:54 | 2026-08-19 20:54 | 2026-08-19 20:54 | 2026-08-19 20:54 |  |  | Fair | No | Supply restored to the area.
Outage | J.E.26.08.29856 | C001894443 | Wayne Dillion | St.Elizabeth | Completed | Load_265281 | Maggotty - 210 | 2026-08-19 19:36 | 2026-08-19 19:38 | 2026-08-19 21:33 | 2026-08-19 21:34 | 2026-08-19 21:33 | 2026-08-19 21:35 | 2026-08-19 21:35 | 2026-08-19 21:35 |  |  | Fair | No | Please refer this call to field service customer got disconnected due to an incorrect meter
Non-Outage | J.E.26.08.17312 | C001894477 | Elvis Trowers | KSAS | Completed | Load_301350 | Hunts Bay - 310 | 2026-08-19 20:04 | 2026-08-20 09:33 | 2026-08-20 11:38 | 2026-08-20 11:39 | 2026-08-20 11:52 | 2026-08-20 11:55 | 2026-08-20 12:03 | 2026-08-20 12:03 |  |  | Fair | No | Unable to locate customer by telephone after several attempts. The telephone Number on the report going straight to voicemail.
Non-Outage | J.E.26.08.18803 | C001894478 | Milton Charlton | KSAS | Completed | Load_267402 | Hunts Bay - 310 | 2026-08-19 20:04 | 2026-08-19 20:05 | 2026-08-19 21:58 | 2026-08-19 21:59 | 2026-08-19 23:15 | 2026-08-19 22:40 | 2026-08-19 23:16 | 2026-08-19 23:16 |  |  | Fair | No | Premises closed.
Non-Outage | J.E.26.08.21456 | C001894476 | Elvis Trowers | KSAS | Completed | Load_257637 | Hunts Bay - 510 | 2026-08-19 20:04 | 2026-08-20 09:33 | 2026-08-20 09:57 | 2026-08-20 09:58 | 2026-08-20 11:29 | 2026-08-20 11:20 | 2026-08-20 11:37 | 2026-08-20 11:37 |  |  | Fair | No | Found one 3 amps transformer fuse blown at pole # ( no pole #). Refused using one 3 amps fuse and reclosed transformer switch.
Non-Outage | J.E.26.08.22328 | C001894474 | Milton Charlton | KSAN | Completed | Load_268911 | Greenwich - 710 | 2026-08-19 20:04 | 2026-08-19 20:05 | 2026-08-19 20:36 | 2026-08-19 20:37 | 2026-08-19 21:07 | 2026-08-19 21:15 | 2026-08-19 21:08 | 2026-08-19 21:08 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Non-Outage | J.E.26.08.22347 | C001894475 | Milton Charlton | KSAS | Completed | Load_266562 | Hunts Bay - 310 | 2026-08-19 20:04 | 2026-08-19 20:05 | 2026-08-19 21:12 | 2026-08-19 21:12 | 2026-08-19 21:56 | 2026-08-19 21:55 | 2026-08-19 21:58 | 2026-08-19 21:58 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.29648 | C001894480 | Eric Williams | KSAN | Completed | Load_574990 | West Kings House - 410 | 2026-08-19 20:05 | 2026-08-19 20:06 | 2026-08-19 20:38 | 2026-08-19 20:38 | 2026-08-19 21:15 | 2026-08-19 21:16 | 2026-08-19 21:17 | 2026-08-19 21:17 |  |  | Fair | No | Premises lock, calls to customer went unanswered, security guard stated the customer not at location
Outage | J.E.26.08.29489 | C001894484 | Richard Samuda | Manchester | Completed | Load_253601 | Kendal - 210 | 2026-08-19 20:07 | 2026-08-19 20:08 | 2026-08-19 20:25 | 2026-08-19 20:25 | 2026-08-19 20:26 | 2026-08-19 08:46 | 2026-08-19 20:46 | 2026-08-19 20:46 |  |  | Fair | No | Found 10 amp junction blown patrol line found nothing replaced junction customer back to normal
Outage | J.E.26.08.29849 | C001894483 | Romeo Brissett | St.James | Completed | Load_266571 | Bogue - 310 | 2026-08-19 20:07 | 2026-08-19 20:37 | 2026-08-19 20:48 | 2026-08-19 20:49 | 2026-08-19 20:49 | 2026-08-19 20:54 | 2026-08-19 21:25 | 2026-08-19 21:25 |  |  | Fair | No | Replaced (1)10KVA transformer fuse. Used (1)2amps fuse.
Non-Outage | J.E.26.08.29970 | C001894499 | Dean- Smith |  | Completed |  |  | 2026-08-19 20:42 | 2026-08-19 20:53 | 2026-08-19 21:54 | 2026-08-19 21:55 | 2026-08-19 21:54 | 2026-08-19 21:54 | 2026-08-19 21:55 | 2026-08-19 21:55 | Fire |  | Fair | No | Please note st James call.
Non-Outage | J.E.26.08.29874 | C001894550 | Elvis Trowers |  | Completed |  |  | 2026-08-19 21:26 | 2026-08-20 07:45 | 2026-08-20 12:45 | 2026-08-20 12:46 | 2026-08-20 13:20 | 2026-08-20 13:20 | 2026-08-20 13:22 | 2026-08-20 13:22 | Fire |  | Fair | No | Unable to locate customer by telephone . There is no telephone number on the report .
Non-Outage | J.E.26.08.29978 | C001894549 | Elvis Trowers |  | Completed |  |  | 2026-08-19 21:26 | 2026-08-20 07:45 | 2026-08-20 12:20 | 2026-08-20 12:34 | 2026-08-20 12:39 | 2026-08-20 12:45 | 2026-08-20 12:45 | 2026-08-20 12:45 |  |  | Fair | No | Unable to locate customer by telephone. Telephone number on the report going straight to voicemail.
Outage | J.E.26.08.29726 | C001894548 | Rusean Allen | KSAS | Completed | Load_244887 | Hunts Bay - 310 | 2026-08-19 21:26 | 2026-08-20 07:36 | 2026-08-20 07:49 | 2026-08-20 07:49 | 2026-08-20 07:52 | 2026-08-20 07:53 | 2026-08-20 07:54 | 2026-08-20 07:54 |  |  | Fair | No | Premises okay
Outage | J.E.26.08.29729 | C001894547 | Rusean Allen | KSAS | Completed | Load_253227 | Cane River - 610 | 2026-08-19 21:26 | 2026-08-20 07:35 | 2026-08-20 07:55 | 2026-08-20 07:56 | 2026-08-20 07:57 | 2026-08-20 07:57 | 2026-08-20 07:58 | 2026-08-20 07:58 |  |  | Fair | No | Premises okay
Outage | J.E.26.08.29862 | C001894546 | Rusean Allen | KSAS | Completed | Load_1002656 | Cane River - 310 | 2026-08-19 21:26 | 2026-08-20 07:35 | 2026-08-20 11:26 | 2026-08-20 11:27 | 2026-08-20 11:58 | 2026-08-20 12:02 | 2026-08-20 12:02 | 2026-08-20 12:02 |  |  | Fair | No | PMC meter issues, PMC box#0026 refer to field service department.
Outage | J.E.26.08.29964 | C001894563 | Wayne Dillion | Manchester | Completed | Load_292330 | Spur Tree - 210 | 2026-08-19 21:48 | 2026-08-19 21:51 | 2026-08-19 22:11 | 2026-08-19 22:12 | 2026-08-19 22:12 | 2026-08-19 22:12 | 2026-08-19 22:12 | 2026-08-19 22:12 |  |  | Fair | No | Premises no found and customer phone not working
Outage | J.E.26.08.29982 | C001894565 | Tyrese Williams | St.Ann | Completed | Load_251902 | Cardiff Hall - 310 | 2026-08-19 21:52 | 2026-08-20 07:42 | 2026-08-20 10:08 | 2026-08-20 10:09 | 2026-08-20 10:47 | 2026-08-20 10:52 | 2026-08-20 10:52 | 2026-08-20 10:52 |  |  | Fair | No | Open a bank of two 25kva transformer for temporary disconnection
Outage | J.E.26.08.29634 | C001894569 | Derrick Grubb | St.Thomas | Completed | Load_269505 | Lysson - 410 | 2026-08-19 22:08 | 2026-08-20 07:23 | 2026-08-20 07:48 | 2026-08-20 07:49 | 2026-08-20 08:34 | 2026-08-20 08:36 | 2026-08-20 08:36 | 2026-08-20 08:36 | BrokenWire |  | Fair | No | Leaning concrete pole leaning towards road and is pulling on customer pothead
Non-Outage | J.E.26.08.29823 | C001894573 | Donald Cunningham | St.Catherine | Completed | Load_1000959 | Tredegar - 410 | 2026-08-19 22:24 | 2026-08-19 22:25 | 2026-08-19 23:27 | 2026-08-19 23:28 | 2026-08-19 23:27 | 2026-08-19 23:28 | 2026-08-19 23:29 | 2026-08-19 23:29 |  |  | Fair | Yes | Replace 10 amp junction fuse behind plaza
Outage | J.E.26.08.29985 | C001894577 | Omar King | St.Ann | Completed | Load_251547 | Upper White River - 210 | 2026-08-19 22:40 | 2026-08-19 22:40 | 2026-08-19 23:12 | 2026-08-19 23:13 | 2026-08-19 23:37 | 2026-08-20 00:52 | 2026-08-20 00:52 | 2026-08-20 00:52 |  |  | Fair | No | Suspect a primary jumper open can no be rectified in the night no access to section of the line need daylight attention
Non-Outage | J.E.26.08.30041 | C001894579 | Rusean Allen |  | Completed |  |  | 2026-08-19 22:43 | 2026-08-19 23:28 | 2026-08-20 02:15 | 2026-08-20 02:15 | 2026-08-20 02:25 | 2026-08-20 02:25 | 2026-08-20 02:25 | 2026-08-20 02:25 | Fire |  | Fair | No | More information
Non-Outage | J.E.26.08.30051 | C001894588 | Omar King |  | Completed |  |  | 2026-08-19 23:05 | 2026-08-19 23:07 | 2026-08-20 02:31 | 2026-08-20 02:31 | 2026-08-20 02:35 | 2026-08-20 02:35 | 2026-08-20 02:36 | 2026-08-20 02:36 |  |  | Fair | No | Found 50 KVA transformer defective please refer to maintenance . About 30 customer affected
Non-Outage | J.E.26.08.29581 | C001894592 | Delano Gayle |  | Completed |  |  | 2026-08-19 23:13 | 2026-08-19 23:14 | 2026-08-19 23:19 | 2026-08-19 23:34 | 2026-08-20 00:09 | 2026-08-20 00:26 | 2026-08-20 00:26 | 2026-08-20 00:26 | BrokenWire |  | Fair | No | Premises not found no proper contact information in report
Outage | J.E.26.08.30070 | C001894594 | Shawn Medley | St.James | Completed | Load_250351 | Bogue - 310 | 2026-08-19 23:20 | 2026-08-20 08:14 | 2026-08-20 08:32 | 2026-08-20 08:33 | 2026-08-20 09:30 | 2026-08-20 09:30 | 2026-08-20 09:32 | 2026-08-20 09:32 |  |  | Fair | No | Premises checked and found ok
Outage | J.E.26.08.30068 | C001894598 | Rusean Allen | KSAS | Completed | Load_240238 | Duhaney - 410 | 2026-08-19 23:26 | 2026-08-19 23:27 | 2026-08-19 23:51 | 2026-08-19 23:53 | 2026-08-20 01:16 | 2026-08-20 01:21 | 2026-08-20 01:21 | 2026-08-20 01:21 |  |  | Fair | No | Transformer found chipped, transformer reset was done.
Outage | J.E.26.08.30004 | C001894616 | Omar King | St.Ann | Completed | Load_265554 | Ocho Rios - 310 | 2026-08-20 00:57 | 2026-08-20 00:58 | 2026-08-20 01:23 | 2026-08-20 01:24 | 2026-08-20 01:23 | 2026-08-20 02:30 | 2026-08-20 02:31 | 2026-08-20 02:31 |  |  | Fair | No | Found 50 KVA transformer defective please refer to maintenance . About 30 customer affected
Outage | J.E.26.08.30049 | C001894617 | Antony Levy | KSAN | Completed | Load_244870 | Constant Spring - 310 | 2026-08-20 02:13 | 2026-08-20 07:44 | 2026-08-20 08:56 | 2026-08-20 08:57 | 2026-08-20 10:31 | 2026-08-20 11:26 | 2026-08-20 11:28 | 2026-08-20 11:28 |  |  | Fair | No | Defective joint ampact using 2 2/0 to 2/0 amp acts and shell and left a voltage reading of 117 116 232
Outage | J.E.26.08.30158 | C001894646 | Fitzroy Turner | KSAS | Completed | Load_254986 | Duhaney - 410 | 2026-08-20 06:47 | 2026-08-20 07:45 | 2026-08-20 13:01 | 2026-08-20 13:09 | 2026-08-20 13:09 | 2026-08-20 13:09 | 2026-08-20 13:10 | 2026-08-20 13:10 |  |  | Fair | No | Unable to locate customer phone ringing with out answering
Non-Outage | J.E.26.08.29767 | C001894654 | Andrae Clarke | Portland | Completed | Load_250580 | Port Antonio - 410 | 2026-08-20 07:14 | 2026-08-20 07:16 | 2026-08-20 12:59 | 2026-08-20 13:01 | 2026-08-20 13:47 | 2026-08-20 13:49 | 2026-08-20 13:49 | 2026-08-20 13:49 |  |  | Fair | No | Premises found okCheck voltage 119/123/242
Non-Outage | J.E.26.08.29795 | C001894655 | Collin Robinson | Portland | Completed | Load_244330 | Port Antonio - 310 | 2026-08-20 07:14 | 2026-08-20 07:16 | 2026-08-20 07:46 | 2026-08-20 07:46 | 2026-08-20 08:57 | 2026-08-20 09:03 | 2026-08-20 09:04 | 2026-08-20 09:04 |  |  | Fair | No | Change two corroded one bolt clamp at pole Voltage reading 118v two wire service
Non-Outage | J.E.26.08.22730 | C001894659 | Collin Robinson |  | Completed |  |  | 2026-08-20 07:15 | 2026-08-20 07:19 | 2026-08-20 10:10 | 2026-08-20 10:11 | 2026-08-20 10:15 | 2026-08-20 10:18 | 2026-08-20 10:22 | 2026-08-20 10:22 | LowHangingWires |  | Fair | No | Information received from customer that issue was resolved
Non-Outage | J.E.26.08.23152 | C001894657 | Andrae Clarke | Portland | Completed | Load_252130 | Port Antonio - 410 | 2026-08-20 07:15 | 2026-08-20 07:16 | 2026-08-20 11:53 | 2026-08-20 11:53 | 2026-08-20 12:45 | 2026-08-20 12:46 | 2026-08-20 12:47 | 2026-08-20 12:47 |  |  | Fair | No | Repair corroded wireUse two one bolt clamp Check voltage 117/116/234
Non-Outage | J.E.26.08.28784 | C001894658 | Andrae Clarke | Portland | Completed | Load_259997 | Port Antonio - 410 | 2026-08-20 07:15 | 2026-08-20 07:16 | 2026-08-20 10:16 | 2026-08-20 10:16 | 2026-08-20 10:52 | 2026-08-20 11:34 | 2026-08-20 11:41 | 2026-08-20 11:41 |  |  | Fair | No | Repair corroded wire use three one bolt clamp Check voltage 117/112/229
Non-Outage | J.E.26.08.29517 | C001894656 | Andrae Clarke | Portland | Completed | Load_568777 | Port Antonio - 410 | 2026-08-20 07:15 | 2026-08-20 07:16 | 2026-08-20 08:13 | 2026-08-20 08:13 | 2026-08-20 10:12 | 2026-08-20 09:40 | 2026-08-20 10:16 | 2026-08-20 10:16 |  |  | Fair | No | Refer to Emergency Department Pad lock close on boxNeed key to open box power was tripping out yesterday
Non-Outage | J.E.26.08.29990 | C001894661 | Omar King |  | Completed |  |  | 2026-08-20 07:17 | 2026-08-20 15:22 | 2026-08-20 16:07 | 2026-08-20 16:10 | 2026-08-20 16:09 | 2026-08-20 16:10 | 2026-08-20 16:10 | 2026-08-20 16:10 |  |  | Fair | No | Found 50: KVA transformer chip transformer has been reset and customer now with supply..
Outage | J.E.26.08.30153 | C001894660 | Cliton Henry | St.Ann | Completed | Load_265477 | Upper White River - 110 | 2026-08-20 07:17 | 2026-08-20 07:26 | 2026-08-20 09:27 | 2026-08-20 09:27 | 2026-08-20 09:27 | 2026-08-20 09:29 | 2026-08-20 09:29 | 2026-08-20 09:29 |  |  | Fair | No | The supply was restored, this report is related to outage # 30162
Outage | J.E.26.08.29972 | C001894665 | Clyde Brown | Clarendon | Completed | Load_254560 | Parnassus - 310 | 2026-08-20 07:22 | 2026-08-20 07:25 | 2026-08-20 09:22 | 2026-08-20 10:33 | 2026-08-20 10:33 | 2026-08-20 10:26 | 2026-08-20 10:38 | 2026-08-20 10:38 |  |  | Fair | No | Found ok,voltage reading 115/116 and 231V
Outage | J.E.26.08.30140 | C001894663 | Javid Vernon | Westmoreland | Completed | Load_268497 | Paradise - 110 | 2026-08-20 07:22 | 2026-08-20 07:23 | 2026-08-20 08:36 | 2026-08-20 08:37 | 2026-08-20 08:36 | 2026-08-20 08:36 | 2026-08-20 08:37 | 2026-08-20 08:37 | BrokenPole |  | Fair | No | Related to previous call job #30181
Outage | J.E.26.08.30181 | C001894662 | Javid Vernon | Westmoreland | Completed | Load_268497 | Paradise - 110 | 2026-08-20 07:22 | 2026-08-20 07:23 | 2026-08-20 08:02 | 2026-08-20 08:02 | 2026-08-20 08:22 | 2026-08-20 08:36 | 2026-08-20 08:36 | 2026-08-20 08:36 |  |  | Fair | No | Check and found one 35ft class 6 pole broken with single primary and secondary lines due to vehicle accident needs to replace urgently refer to maintenance customer are without power
Non-Outage | J.E.26.08.30208 | C001894666 | Javid Vernon |  | Completed |  |  | 2026-08-20 07:24 | 2026-08-20 07:28 | 2026-08-20 08:37 | 2026-08-20 08:38 | 2026-08-20 08:37 | 2026-08-20 08:38 | 2026-08-20 08:38 | 2026-08-20 08:38 | BrokenPole |  | Fair | No | Related to previous call job #30181
Outage | J.E.26.08.30183 | C001894667 | Richman Whyte | Westmoreland | Completed | Load_239484 | Paradise - 310 | 2026-08-20 07:25 | 2026-08-20 07:29 | 2026-08-20 10:44 | 2026-08-20 10:45 | 2026-08-20 10:45 | 2026-08-20 10:45 | 2026-08-20 10:45 | 2026-08-20 10:45 | BrokenWire |  | Fair | No | Customer had internal problem and already got it fix
Outage | J.E.26.08.29647 | C001894668 | Nickolas Rodriques | St.Catherine | Completed | Load_406138 | Rhodens Pen - 210 | 2026-08-20 07:26 | 2026-08-20 07:28 | 2026-08-20 07:43 | 2026-08-20 08:15 | 2026-08-20 09:32 | 2026-08-20 09:50 | 2026-08-20 09:52 | 2026-08-20 09:52 |  |  | Fair | No | Found customer with electricity. He was disconnected due to non-payment of bill which was subsequently restored after payment was made.
Outage | J.E.26.08.30195 | C001894669 | Nickolas Rodriques | St.Catherine | Completed | Load_556352 | Rhodens Pen - 210 | 2026-08-20 07:26 | 2026-08-20 07:28 | 2026-08-20 10:02 | 2026-08-20 10:19 | 2026-08-20 11:02 | 2026-08-20 11:32 | 2026-08-20 11:37 | 2026-08-20 11:37 |  |  | Fair | No | Unable to communicate with the customer after several attempts. The escalation team was then contacted and stated that the customer was disconnected due to non-payment of bill. However, a connection order was placed on the account after payment was made but he is unable to communicate with the meter. He also confirmed that this customer is a hexing customer.
Outage | J.E.26.08.29396 | C001894671 | Nickolas Rodriques | St.Catherine | Completed | Load_256833 | Rhodens Pen - 210 | 2026-08-20 07:27 | 2026-08-20 07:28 | 2026-08-20 11:37 | 2026-08-20 11:41 | 2026-08-20 12:28 | 2026-08-20 12:46 | 2026-08-20 12:56 | 2026-08-20 12:56 |  |  | Fair | No | Checked and found customer single phasing, reading found (116). All necessary checks were done and it was found that the issue is stemming from the hexing box (HEX 01984). Refer to field service.
Outage | J.E.26.08.29510 | C001894670 | Ricky Hall | St.Catherine | Completed | Load_238669 | Rhodens Pen - 410 | 2026-08-20 07:27 | 2026-08-20 15:22 | 2026-08-20 15:30 | 2026-08-20 15:38 | 2026-08-20 18:16 | 2026-08-20 19:39 | 2026-08-20 19:40 | 2026-08-20 19:40 |  |  | Fair | No | Make jumper at secondary neutral splicing sleeve use 3’#2aa 2 clamps 110/110/220
Outage | J.E.26.08.29743 | C001894673 | Richard Grant | St.Catherine | Completed | Load_256849 | New Michelton - 210 | 2026-08-20 07:28 | 2026-08-20 07:30 | 2026-08-21 07:42 | 2026-08-21 07:42 | 2026-08-21 07:42 | 2026-08-21 07:43 | 2026-08-21 07:43 | 2026-08-21 07:43 |  |  | Fair | No | Premise located in Kingston
Outage | J.E.26.08.29993 | C001894672 | Richard Grant | St.Catherine | Completed | Load_253711 | New Michelton - 310 | 2026-08-20 07:28 | 2026-08-20 07:30 | 2026-08-20 09:17 | 2026-08-20 09:17 | 2026-08-20 09:30 | 2026-08-20 09:31 | 2026-08-20 09:31 | 2026-08-20 09:31 |  |  | Fair | No | Checks revealed customer has internal issues. Customer was advised.
Non-Outage | J.E.26.08.29549 | C001894674 | Richard Grant |  | Completed |  |  | 2026-08-20 07:29 | 2026-08-20 07:30 | 2026-08-20 07:48 | 2026-08-20 07:48 | 2026-08-20 09:15 | 2026-08-20 09:16 | 2026-08-20 09:17 | 2026-08-20 09:17 |  |  | Fair | No | Premises found okay
Non-Outage | J.E.25.11.27972 | C001894675 | Edward Royal | KSAN | Completed | Load_243564 | Washington Blvd - 310 | 2026-08-20 07:30 | 2026-08-20 07:31 | 2026-08-20 09:19 | 2026-08-20 09:20 | 2026-08-20 09:29 | 2026-08-20 13:52 | 2026-08-20 13:53 | 2026-08-20 13:53 | TreeContact |  | Fair | No | Spliced and reconnected 4 north quad using 8 one bolt clamps 2 4 north perform voltage reading 115v 116 V 211v 231v 230V 236v
Outage | J.E.26.08.30201 | C001894676 | Evan Spaulding | St.Mary | Completed | Load_246199 | Highgate - 210 | 2026-08-20 07:30 | 2026-08-20 07:31 | 2026-08-20 08:01 | 2026-08-20 08:01 | 2026-08-20 08:01 | 2026-08-20 08:01 | 2026-08-20 08:02 | 2026-08-20 08:02 |  |  | Fair | No | Power was restored yesterday.
Non-Outage | J.E.26.08.29663 | C001894677 | Javid Vernon | Westmoreland | Completed | Load_240178 | Paradise - 210 | 2026-08-20 07:31 | 2026-08-20 07:32 | 2026-08-20 09:56 | 2026-08-20 09:57 | 2026-08-20 11:02 | 2026-08-20 11:40 | 2026-08-20 11:40 | 2026-08-20 11:40 |  |  | Fair | No | After contacting the customer and reaching the area unable to locate the customer and premises the customer is not answering their phone
Non-Outage | J.E.26.08.29740 | C001894678 | Javid Vernon | Westmoreland | Completed | Load_251332 | Paradise - 210 | 2026-08-20 07:31 | 2026-08-20 07:32 | 2026-08-20 11:40 | 2026-08-20 11:40 | 2026-08-20 12:13 | 2026-08-20 12:41 | 2026-08-20 12:43 | 2026-08-20 12:43 |  |  | Fair | No | Reconnect customer service wire use one clamp voltage found 111 voltage left 111/112/223
Non-Outage | J.E.26.08.29753 | C001894681 | Ryan Richards |  | Completed |  |  | 2026-08-20 07:33 | 2026-08-20 07:34 | 2026-08-20 18:33 | 2026-08-20 18:34 | 2026-08-20 20:39 | 2026-08-20 21:00 | 2026-08-20 21:01 | 2026-08-20 21:01 |  |  | Fair | No | Blown 2 amp fuse found for 25 kva transformer line patrol nothing found lighting suspected to be the cause blown fuse was replaced all customers are now with supply
Outage | J.E.26.08.30119 | C001894680 | Ryan Richards | Manchester | Completed | Load_269303 | Spur Tree - 310 | 2026-08-20 07:33 | 2026-08-20 07:34 | 2026-08-20 15:50 | 2026-08-20 15:50 | 2026-08-20 16:48 | 2026-08-20 18:14 | 2026-08-20 18:16 | 2026-08-20 18:16 |  |  | Rains | No | Broken service wire found cause by pear tree limb splice and retention using 10ft#6 triplex 2 one voltage 112/110/223 volts
Outage | J.E.26.08.29364 | C001894683 | Eric Williams | KSAN | Completed | Load_264765 | Washington Blvd - 310 | 2026-08-20 07:36 | 2026-08-20 16:04 | 2026-08-20 16:22 | 2026-08-20 17:31 | 2026-08-20 18:02 | 2026-08-20 18:02 | 2026-08-20 18:03 | 2026-08-20 18:03 | BrokenPole |  | Fair | No | Premises found okay customer stated issues was resolved from yesterday
Non-Outage | J.E.26.08.30058 | C001894684 | Cliton Henry | St.Mary | Completed | Load_243605 | Oracabessa - 110 | 2026-08-20 07:37 | 2026-08-20 07:38 | 2026-08-20 11:54 | 2026-08-20 12:09 | 2026-08-20 12:09 | 2026-08-20 12:26 | 2026-08-20 12:27 | 2026-08-20 12:27 |  |  | Fair | No | A broken secondary neutral conductor found suspended. A 50 kva transformer was de energized at Gauf Ave. to carryout repairs. Corrective work done to spliced and retensioned the secondary neutral conductor and reconnected the jumper using 1#2 preform, 3 feet #2 AA conductor and 2 one bolt clamp. Supply restored to energized the 50 kva transformer.
Non-Outage | J.E.26.08.28223 | C001894686 | Fitzroy Turner |  | Completed |  |  | 2026-08-20 07:38 | 2026-08-20 11:32 | 2026-08-20 14:18 | 2026-08-20 14:19 | 2026-08-20 15:00 | 2026-08-20 15:01 | 2026-08-20 15:01 | 2026-08-20 15:01 |  |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.08.26275 | C001894687 | Cliton Henry | St.Ann | Completed | Load_265764 | Upper White River - 110 | 2026-08-20 07:39 | 2026-08-20 07:40 | 2026-08-20 13:10 | 2026-08-20 13:11 | 2026-08-20 15:29 | 2026-08-20 15:37 | 2026-08-20 15:43 | 2026-08-20 15:43 |  |  | Fair | No | A blown 15 amp junction fuse found at Bellevue due to tree contact. Supply restored using 1-15 amp fuse.
Outage | J.E.26.08.30162 | C001894688 | Cliton Henry | St.Ann | Completed | Load_261553 | Upper White River - 110 | 2026-08-20 07:39 | 2026-08-20 07:40 | 2026-08-20 08:54 | 2026-08-20 08:54 | 2026-08-20 08:54 | 2026-08-20 09:21 | 2026-08-20 09:25 | 2026-08-20 09:25 |  |  | Fair | No | A 20 amp trip saver found tripped at Hyatt Hill Sortie Gate at pole #0014033 due to tree contact at Richards Pen. The branch was removed and supply restored to energized the 20 20 trip saver at Hyatt Hill
Outage | J.E.26.08.29260 | C001894692 | Tyrese Williams | St.Ann | Completed | Load_243240 | Cardiff Hall - 310 | 2026-08-20 07:41 | 2026-08-20 07:43 | 2026-08-20 10:53 | 2026-08-20 11:45 | 2026-08-20 13:01 | 2026-08-20 13:50 | 2026-08-20 13:50 | 2026-08-20 13:50 |  |  | Fair | No | Remade secondary neutral jumper and Remade service wire joint at pole
Outage | J.E.26.08.30182 | C001894689 | Raymond Lewis | St.Ann | Completed | Load_265554 | Ocho Rios - 310 | 2026-08-20 07:41 | 2026-08-20 07:43 | 2026-08-20 08:35 | 2026-08-20 08:36 | 2026-08-20 09:10 | 2026-08-20 21:13 | 2026-08-20 09:13 | 2026-08-20 09:13 |  |  | Fair | No | Related to burn x former
Outage | J.E.26.08.30200 | C001894691 | Cliton Henry | St.Ann | Completed | Load_246815 | Upper White River - 210 | 2026-08-20 07:41 | 2026-08-20 08:28 | 2026-08-20 09:35 | 2026-08-20 09:36 | 2026-08-20 10:18 | 2026-08-20 10:24 | 2026-08-20 10:29 | 2026-08-20 10:29 |  |  | Fair | No | Supply found ok, voltages found at the metering point were 118-118/236 volts
Outage | J.E.26.08.30209 | C001894690 | Omar King | St.Ann | Completed | Load_269625 | Roaring River - 410 | 2026-08-20 07:41 | 2026-08-20 15:26 | 2026-08-20 16:57 | 2026-08-20 16:57 | 2026-08-20 18:06 | 2026-08-20 19:43 | 2026-08-20 19:43 | 2026-08-20 19:43 |  |  | Fair | No | Found customer 1 bolt clamp defective at phot head and clamps has been replaced and customer now with supply..
Non-Outage | J.E.26.08.29362 | C001894694 | Milton Charlton | KSAN | Completed | Load_264066 | West Kings House - 410 | 2026-08-20 07:45 | 2026-08-20 07:52 | 2026-08-20 09:36 | 2026-08-20 09:36 | 2026-08-20 11:56 | 2026-08-20 11:50 | 2026-08-20 12:14 | 2026-08-20 12:14 | Fire |  | Fair | No | Isolate bank of transformers((1-100 and 2-25 kva) at pole #0033413 and repair burnt twisted secondary conductors and transformer drop leads using 10ft. #6 triplex and twelve 1- bolt clamps, one3 amps transformer fuse and reclosed transformer switches.
Non-Outage | J.E.26.08.12270 | C001894701 | Christopher Edwards |  | Completed |  |  | 2026-08-20 07:46 | 2026-08-20 07:52 | 2026-08-20 07:57 | 2026-08-20 08:40 | 2026-08-20 08:55 | 2026-08-20 09:04 | 2026-08-20 09:05 | 2026-08-20 09:05 | LowHangingWires |  | Fair | No | Unable to reach customer by phone Went to location and observed supply is in the area
Non-Outage | J.E.26.08.28706 | C001894697 | Elvis Trowers | KSAN | Completed | Load_263212 | Washington Blvd - 810 | 2026-08-20 07:46 | 2026-08-21 08:01 | 2026-08-21 10:19 | 2026-08-21 10:20 | 2026-08-21 10:49 | 2026-08-21 10:55 | 2026-08-21 10:57 | 2026-08-21 10:57 | BrokenWire |  | Fair | No | Customer has an internal problem. Customer advise to get on electrician to repair damaged wire.
Non-Outage | J.E.26.08.29484 | C001894695 | Richard Watson | St.Elizabeth | Completed | Load_263142 | Maggotty - 110 | 2026-08-20 07:46 | 2026-08-20 07:46 | 2026-08-20 13:11 | 2026-08-20 13:11 | 2026-08-20 13:56 | 2026-08-20 14:00 | 2026-08-20 14:00 | 2026-08-20 14:00 |  |  | Fair | No | Customer is actually making a complaint about receiving electricity bills even though there has been no electricity at the premises since the passage of hurricane Melissa.
Non-Outage | J.E.26.08.13968 | C001894703 | Odeanie Davis | KSAS | Completed | Load_244348 | Greenwich - 710 | 2026-08-20 07:47 | 2026-08-20 07:49 | 2026-08-20 08:47 | 2026-08-20 09:55 | 2026-08-20 09:55 | 2026-08-20 10:23 | 2026-08-20 09:56 | 2026-08-20 09:56 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.13973 | C001894705 | Odeanie Davis | KSAS | Completed | Load_257830 | Greenwich - 710 | 2026-08-20 07:47 | 2026-08-20 07:49 | 2026-08-20 08:52 | 2026-08-20 09:57 | 2026-08-20 09:56 | 2026-08-20 10:32 | 2026-08-20 09:57 | 2026-08-20 09:57 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.13978 | C001894706 | Odeanie Davis | KSAS | Completed | Load_257830 | Greenwich - 710 | 2026-08-20 07:47 | 2026-08-20 07:49 | 2026-08-20 08:52 | 2026-08-20 09:58 | 2026-08-20 09:57 | 2026-08-20 10:51 | 2026-08-20 09:58 | 2026-08-20 09:58 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.28293 | C001894704 | Odeanie Davis | KSAS | Completed | Load_246833 | Greenwich - 710 | 2026-08-20 07:47 | 2026-08-20 07:49 | 2026-08-20 08:54 | 2026-08-20 08:54 | 2026-08-20 09:02 | 2026-08-20 09:59 | 2026-08-20 09:55 | 2026-08-20 09:55 |  |  | Fair | No | 107v under load at arrival, corrosion at pothead and secondary cleaned and reclaimed, 2 penn union & 2 one bolt clamps, 113v under load after correction.
Non-Outage | J.E.26.08.03354 | C001894707 | Odeanie Davis | KSAS | Completed | Load_254827 | Hunts Bay - 110 | 2026-08-20 07:48 | 2026-08-20 07:49 | 2026-08-20 08:22 | 2026-08-20 14:19 | 2026-08-20 14:18 | 2026-08-20 14:28 | 2026-08-20 14:19 | 2026-08-20 14:19 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.06304 | C001894708 | Odeanie Davis | KSAS | Completed | Load_265823 | Hunts Bay - 210 | 2026-08-20 07:48 | 2026-08-20 07:49 | 2026-08-20 08:18 | 2026-08-20 14:20 | 2026-08-20 14:19 | 2026-08-20 14:48 | 2026-08-20 14:20 | 2026-08-20 14:20 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.17610 | C001894709 | Odeanie Davis | KSAS | Completed | Load_240320 | Hunts Bay - 210 | 2026-08-20 07:48 | 2026-08-20 07:49 | 2026-08-20 08:25 | 2026-08-20 08:26 | 2026-08-20 08:26 | 2026-08-20 08:38 | 2026-08-20 08:38 | 2026-08-20 08:38 |  |  | Fair | No | Customer stated that they hear sparking sound coming from transformer, customer also stated that this affects their power quality, productivity and damaging their equipments, bucket truck needed.
Non-Outage | J.E.26.08.21356 | C001894711 | Elvis Trowers | KSAS | Completed | Load_253829 | Hunts Bay - 210 | 2026-08-20 07:48 | 2026-08-20 07:52 | 2026-08-20 13:22 | 2026-08-20 13:23 | 2026-08-20 14:09 | 2026-08-20 13:45 | 2026-08-20 14:10 | 2026-08-20 14:10 |  |  | Fair | No | Found okay upon arrival. Matter was resolved. Customer states there circuit breaker tripped.
Non-Outage | J.E.26.08.29565 | C001894710 | Elvis Trowers | KSAS | Completed | Load_240795 | Hunts Bay - 210 | 2026-08-20 07:48 | 2026-08-20 07:52 | 2026-08-20 12:04 | 2026-08-20 12:04 | 2026-08-20 12:18 | 2026-08-20 12:20 | 2026-08-20 12:20 | 2026-08-20 12:20 |  |  | Fair | No | Found okay upon arrival. Customer states matter was resolved.
Non-Outage | J.E.26.08.16378 | C001894712 | Raheem Ricketts | St.Elizabeth | Completed | Load_263711 | Maggotty - 210 | 2026-08-20 07:49 | 2026-08-20 07:51 | 2026-08-20 07:54 | 2026-08-20 08:03 | 2026-08-20 08:26 | 2026-08-20 08:27 | 2026-08-20 08:27 | 2026-08-20 08:27 |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.08.20721 | C001894714 | Raheem Ricketts | St.Elizabeth | Completed | Load_252693 | Maggotty - 210 | 2026-08-20 07:49 | 2026-08-20 07:51 | 2026-08-20 07:54 | 2026-08-20 08:32 | 2026-08-20 08:32 | 2026-08-20 08:33 | 2026-08-20 08:33 | 2026-08-20 08:33 |  |  | Fair | No | Check and found customer experiencing internal problems
Non-Outage | J.E.26.07.14643 | C001894715 | Raheem Ricketts | St.Elizabeth | Completed | Load_238861 | Maggotty - 210 | 2026-08-20 07:50 | 2026-08-20 07:51 | 2026-08-20 07:54 | 2026-08-20 08:35 | 2026-08-20 08:34 | 2026-08-20 08:35 | 2026-08-20 08:35 | 2026-08-20 08:35 |  |  | Fair | No
Outage | J.E.26.08.30221 | C001894716 | Antony Levy | KSAN | Completed | Load_267680 | Washington Blvd - 410 | 2026-08-20 07:50 | 2026-08-20 09:22 | 2026-08-20 14:24 | 2026-08-20 14:25 | 2026-08-20 15:00 | 2026-08-20 15:00 | 2026-08-20 15:02 | 2026-08-20 15:02 |  |  | Fair | No | customer left a toll free number unable to reach customer, went by address and can’t find the premises.
Non-Outage | J.E.26.05.31010 | C001894721 | Richard Watson | Manchester | Completed | Load_267059 | Spur Tree - 210 | 2026-08-20 07:51 | 2026-08-20 07:52 | 2026-08-20 10:41 | 2026-08-20 10:41 | 2026-08-20 11:49 | 2026-08-20 12:27 | 2026-08-20 12:34 | 2026-08-20 12:34 |  |  | Fair | No | Remade drop leed connection to secondary circuit, use two 1bolt clamps and one 2amp fuse, voltage left 111v, 111v, 187v, and 215v, 220v, 222v phase to phase.
Non-Outage | J.E.26.07.01895 | C001894722 | Richard Watson | Manchester | Completed | Load_292829 | Spur Tree - 210 | 2026-08-20 07:51 | 2026-08-20 07:52 | 2026-08-20 12:38 | 2026-08-20 12:39 | 2026-08-20 12:55 | 2026-08-20 13:00 | 2026-08-20 13:01 | 2026-08-20 13:01 |  |  | Fair | No | Found okay, customer stated that the issue was resolved about a month ago.
Non-Outage | J.E.26.08.26787 | C001894736 | Christopher Edwards | KSAN | Completed | Load_257494 | Constant Spring - 410 | 2026-08-20 07:58 | 2026-08-20 07:59 | 2026-08-20 09:05 | 2026-08-20 09:05 | 2026-08-20 10:08 | 2026-08-20 10:30 | 2026-08-20 10:32 | 2026-08-20 10:32 | BrokenWire |  | Fair | No | 3 phase primary line (covered conductor) is hanging low A new pole is planted beside old pole for primary line to be transferred Maintenance crew is already aware of issue Supply is in the area
Non-Outage | J.E.26.08.29309 | C001894735 | Rochaine Hussey | KSAN | Completed | Load_264247 | Constant Spring - 410 | 2026-08-20 07:58 | 2026-08-20 08:01 | 2026-08-20 11:10 | 2026-08-20 11:12 | 2026-08-20 11:33 | 2026-08-20 13:07 | 2026-08-20 13:08 | 2026-08-20 13:08 |  |  | Fair | No | Transformer was isolated and top upHowever maintenance team arrived onsite to do a transformer upgrade
Non-Outage | J.E.26.08.29501 | C001894734 | Fredrick Hamilton | KSAN | Completed | Load_253371 | Constant Spring - 210 | 2026-08-20 07:58 | 2026-08-20 08:25 | 2026-08-20 08:34 | 2026-08-20 10:37 | 2026-08-20 10:52 | 2026-08-20 10:59 | 2026-08-20 10:59 | 2026-08-20 10:59 |  |  | Fair | No | 240v/120v/120v obtained Slack connectionNo issue detected on JPS supply Premises is ok
Non-Outage | J.E.26.08.29620 | C001894733 | Rochaine Hussey | KSAN | Completed | Load_248982 | Constant Spring - 410 | 2026-08-20 07:58 | 2026-08-20 08:00 | 2026-08-20 10:31 | 2026-08-20 10:54 | 2026-08-20 10:53 | 2026-08-20 11:04 | 2026-08-20 11:04 | 2026-08-20 11:04 |  | Y | Fair | No | Bushing needed Bamboo on secondary twisted wire which is causing customers to be experiencing low voltage More than one customer affected
Non-Outage | J.E.26.08.30093 | C001894731 | Fredrick Hamilton | KSAS | Completed | Load_254408 | Duhaney - 310 | 2026-08-20 07:58 | 2026-08-20 08:27 | 2026-08-20 08:34 | 2026-08-20 11:00 | 2026-08-20 11:15 | 2026-08-20 11:19 | 2026-08-20 11:19 | 2026-08-20 11:19 |  |  | Fair | No | No high voltage detected in area 236v/117v/118v obtained no issue detected on JPS supply
Outage | J.E.26.08.30225 | C001894732 | Ryan Richards | Manchester | Completed | Load_261060 | Spur Tree - 310 | 2026-08-20 07:58 | 2026-08-20 07:59 | 2026-08-20 09:56 | 2026-08-20 09:56 | 2026-08-20 11:30 | 2026-08-20 13:04 | 2026-08-20 13:04 | 2026-08-20 13:04 | Fire |  | Fair | No | Rotten service wire found replace 80ft#6 triplex 3 penunion 3 one bolt clamps voltage 115/117/233 volts
Non-Outage | J.E.26.08.27840 | C001894737 | Kenroy Dale | Manchester | Completed | Load_239651 | Porus - 310 | 2026-08-20 07:59 | 2026-08-20 08:00 | 2026-08-20 10:50 | 2026-08-20 10:51 | 2026-08-20 11:47 | 2026-08-20 12:09 | 2026-08-20 12:12 | 2026-08-20 12:12 |  |  | Fair | No | Corroded neutral jumper found connection was remade using 1 one bolt clamp voltage reading 114/116/230
Non-Outage | J.E.26.08.28015 | C001894738 | Kenroy Dale | Manchester | Completed | Load_239651 | Porus - 310 | 2026-08-20 07:59 | 2026-08-20 08:00 | 2026-08-20 12:13 | 2026-08-20 12:14 | 2026-08-20 12:48 | 2026-08-20 13:21 | 2026-08-20 13:22 | 2026-08-20 13:22 |  |  | Fair | No | Corroded phase found at pole remade connection using 2 one bolt clamp voltage reading 114/110/224
Non-Outage | J.E.26.08.28042 | C001894739 | Kenroy Dale | Manchester | Completed | Load_262729 | Porus - 310 | 2026-08-20 07:59 | 2026-08-20 08:00 | 2026-08-20 15:04 | 2026-08-20 15:05 | 2026-08-20 15:06 | 2026-08-20 15:06 | 2026-08-20 15:08 | 2026-08-20 15:08 |  |  | Rains | No | Duplicated service order
Non-Outage | J.E.26.08.28045 | C001894741 | Kenroy Dale | Manchester | Completed | Load_262729 | Porus - 310 | 2026-08-20 07:59 | 2026-08-20 08:00 | 2026-08-20 13:23 | 2026-08-20 13:45 | 2026-08-20 14:24 | 2026-08-20 15:02 | 2026-08-20 15:04 | 2026-08-20 15:04 |  |  | Rains | No | Customer have internal problems voltage reading 117/116/233
Non-Outage | J.E.26.08.28047 | C001894740 | Kenroy Dale | Manchester | Completed | Load_262729 | Porus - 310 | 2026-08-20 07:59 | 2026-08-20 08:00 | 2026-08-20 15:04 | 2026-08-20 15:09 | 2026-08-20 15:22 | 2026-08-20 15:23 | 2026-08-20 15:23 | 2026-08-20 15:23 |  |  | Rains | No | Duplicated service order
Outage | J.E.26.08.29738 | C001894742 | Christopher West | St.Catherine | Completed | Load_241679 | Twickenham - 210 | 2026-08-20 08:00 | 2026-08-20 08:03 | 2026-08-20 09:46 | 2026-08-20 09:46 | 2026-08-20 10:35 | 2026-08-20 10:39 | 2026-08-20 10:40 | 2026-08-20 10:40 |  |  | Fair | No | Premises found ok.
Non-Outage | J.E.26.08.19720 | C001894754 | Hopeton Henry | St.Thomas | Completed | Load_264721 | Good Year - 110 | 2026-08-20 08:02 | 2026-08-20 08:02 | 2026-08-20 10:38 | 2026-08-20 14:58 | 2026-08-20 15:11 | 2026-08-20 15:20 | 2026-08-20 15:21 | 2026-08-20 15:21 |  |  | Fair | No | Found defective meter , refer to field service 114-113-227 at meter socket
Non-Outage | J.E.26.08.21286 | C001894755 | Hopeton Henry | St.Thomas | Completed | Load_243261 | Good Year - 110 | 2026-08-20 08:02 | 2026-08-20 08:02 | 2026-08-20 10:38 | 2026-08-20 13:37 | 2026-08-20 13:37 | 2026-08-20 14:20 | 2026-08-20 14:20 | 2026-08-20 14:20 |  |  | Fair | No | Customer not located
Non-Outage | J.E.26.08.22299 | C001894753 | Hopeton Henry | St.Thomas | Completed | Load_242525 | Good Year - 110 | 2026-08-20 08:02 | 2026-08-20 08:02 | 2026-08-20 10:38 | 2026-08-20 13:36 | 2026-08-20 13:36 | 2026-08-20 13:36 | 2026-08-20 13:36 | 2026-08-20 13:36 |  |  | Fair | Yes | Splice and retention service wire Voltage reading 114
Non-Outage | J.E.26.08.25350 | C001894752 | Hopeton Henry | St.Thomas | Completed | Load_243261 | Good Year - 110 | 2026-08-20 08:02 | 2026-08-20 08:02 | 2026-08-20 10:38 | 2026-08-20 14:21 | 2026-08-20 14:21 | 2026-08-20 14:21 | 2026-08-20 14:22 | 2026-08-20 14:22 |  |  | Fair | No | Customer not located
Non-Outage | J.E.26.08.25482 | C001894751 | Hopeton Henry | St.Thomas | Completed | Load_264991 | Good Year - 110 | 2026-08-20 08:02 | 2026-08-20 08:02 | 2026-08-20 10:38 | 2026-08-20 10:42 | 2026-08-20 11:54 | 2026-08-20 11:55 | 2026-08-20 11:55 | 2026-08-20 11:55 |  |  | Fair | No | Reconnect service wire
Non-Outage | J.E.26.08.25686 | C001894750 | Hopeton Henry | St.Thomas | Completed | Load_243261 | Good Year - 110 | 2026-08-20 08:02 | 2026-08-20 08:02 | 2026-08-20 10:38 | 2026-08-20 14:37 | 2026-08-20 14:36 | 2026-08-20 14:36 | 2026-08-20 14:37 | 2026-08-20 14:37 |  |  | Fair | No | Found ok
Non-Outage | J.E.26.08.26300 | C001894749 | Hopeton Henry | St.Thomas | Completed | Load_259566 | Good Year - 210 | 2026-08-20 08:02 | 2026-08-20 08:02 | 2026-08-20 10:38 | 2026-08-20 10:40 | 2026-08-20 10:40 | 2026-08-20 10:40 | 2026-08-20 10:41 | 2026-08-20 10:41 |  |  | Fair | No | Use 3 connector at pot head 115-116-231 volts
Non-Outage | J.E.26.08.26839 | C001894744 | Hopeton Henry | St.Thomas | Completed | Load_264991 | Good Year - 110 | 2026-08-20 08:02 | 2026-08-20 08:02 | 2026-08-20 10:38 | 2026-08-20 15:21 | 2026-08-21 11:55 | 2026-08-21 11:55 | 2026-08-21 11:55 | 2026-08-21 11:55 |  |  | Fair | No | Check and found ok
Outage | J.E.26.08.30179 | C001894756 | Christopher West | Portmore | Completed | Load_576085 | Naggo Head - 510 | 2026-08-20 08:02 | 2026-08-20 08:03 | 2026-08-20 10:40 | 2026-08-20 10:40 | 2026-08-20 11:30 | 2026-08-20 11:48 | 2026-08-20 11:57 | 2026-08-20 11:57 |  |  | Fair | No | 3 wire service had corroded connections at pole, used 3 clamps for repairs, customer now okay.
Non-Outage | J.E.26.08.29600 | C001894759 | Lancelot Brown | Hanover | Completed | Load_253734 | Orange Bay - 210 | 2026-08-20 08:03 | 2026-08-20 08:04 | 2026-08-20 08:08 | 2026-08-20 08:10 | 2026-08-20 08:59 | 2026-08-20 09:20 | 2026-08-20 09:20 | 2026-08-20 09:20 |  |  | Fair | No | Check and found voltage at meter socket 112-113-225 customer has internal trouble meter socket diffective advise customer to carry out repair
Outage | J.E.26.08.29525 | C001894758 | Fitzroy Turner | KSAN | Completed | Load_293564 | Washington Blvd - 710 | 2026-08-20 08:03 | 2026-08-20 09:22 | 2026-08-20 10:28 | 2026-08-20 10:28 | 2026-08-20 11:04 | 2026-08-20 11:05 | 2026-08-20 11:06 | 2026-08-20 11:06 |  |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.08.29719 | C001894757 | Fitzroy Turner | KSAS | Completed | Load_269830 | Three Miles - 410 | 2026-08-20 08:03 | 2026-08-20 09:22 | 2026-08-20 14:05 | 2026-08-20 14:05 | 2026-08-20 14:14 | 2026-08-20 14:16 | 2026-08-20 14:17 | 2026-08-20 14:17 |  |  | Fair | No | Unable to communicate with customer meter please send email to field service department to have issues resolved
Non-Outage | J.E.26.08.13878 | C001894761 | Fredrick Hamilton | KSAS | Completed | Load_260300 | Greenwich - 710 | 2026-08-20 08:07 | 2026-08-20 08:10 | 2026-08-20 08:15 | 2026-08-20 09:12 | 2026-08-20 09:15 | 2026-08-20 09:22 | 2026-08-20 09:22 | 2026-08-20 09:22 |  |  | Fair | No | 229v/114v/114.4v obtained No occupant seen and calls to customer went to voicemail No issues detected on JPS supply
Non-Outage | J.E.26.06.10430 | C001894770 | Orville Lee | Portmore | Completed | Load_243231 | Naggo Head - 510 | 2026-08-20 08:08 | 2026-08-20 08:10 | 2026-08-20 08:51 | 2026-08-20 08:52 | 2026-08-20 09:03 | 2026-08-20 09:14 | 2026-08-20 09:14 | 2026-08-20 09:14 |  |  | Fair | No | Premises closed upon arrival Voltage 119v120v240v
Non-Outage | J.E.26.06.11576 | C001894771 | Orville Lee | Portmore | Completed | Load_257437 | Naggo Head - 510 | 2026-08-20 08:08 | 2026-08-20 08:10 | 2026-08-20 09:18 | 2026-08-20 09:18 | 2026-08-20 09:19 | 2026-08-20 10:16 | 2026-08-20 10:17 | 2026-08-20 10:17 |  |  | Fair | No | Change defective service wire80ft #6 service wire, 4 one bolt clamps and 5 Penn union usedVoltage 117V117V235V
Non-Outage | J.E.26.08.28888 | C001894776 | Fitzroy Turner | KSAS | Completed | Load_253161 | Hunts Bay - 810 | 2026-08-20 08:09 | 2026-08-20 09:22 | 2026-08-20 13:10 | 2026-08-20 13:11 | 2026-08-20 13:58 | 2026-08-20 14:00 | 2026-08-20 14:04 | 2026-08-20 14:04 | Fire |  | Fair | No | Found switches tops burning have switches top repair areas is now safe
Non-Outage | J.E.26.08.27994 | C001894788 | Andrae Dawkins | St.James | Completed | Load_246427 | Bogue - 310 | 2026-08-20 08:10 | 2026-08-20 08:12 | 2026-08-20 08:31 | 2026-08-20 11:40 | 2026-08-20 11:39 | 2026-08-20 11:39 | 2026-08-20 11:40 | 2026-08-20 11:40 |  |  | Fair | No | Found multiple customers experiencing low voltage due 100kva transformer fuse blown refer back to emergency crew
Non-Outage | J.E.26.08.28829 | C001894782 | Roemello Brown | Trelawny | Completed | Load_263973 | Martha Brae - 110 | 2026-08-20 08:10 | 2026-08-20 08:12 | 2026-08-20 08:50 | 2026-08-20 08:51 | 2026-08-20 09:19 | 2026-08-20 09:19 | 2026-08-20 09:22 | 2026-08-20 09:22 |  |  | Fair | No | Premises found working okay Voltage found 115/115/231Voltage leave 115/115/231
Non-Outage | J.E.26.08.28870 | C001894780 | Roemello Brown | Trelawny | Completed | Load_263192 | Martha Brae - 110 | 2026-08-20 08:10 | 2026-08-20 08:12 | 2026-08-20 08:52 | 2026-08-20 09:25 | 2026-08-20 10:00 | 2026-08-20 10:04 | 2026-08-20 10:06 | 2026-08-20 10:06 |  |  | Fair | No | Premises found working okay Voltage found 111/113/224Voltage leave 111/113/224
Non-Outage | J.E.26.08.29019 | C001894777 | Roemello Brown | Trelawny | Completed | Load_239232 | Greenwood - 110 | 2026-08-20 08:10 | 2026-08-20 08:12 | 2026-08-20 13:28 | 2026-08-20 13:29 | 2026-08-20 13:28 | 2026-08-20 13:28 | 2026-08-20 13:31 | 2026-08-20 13:31 |  |  | Fair | No | This call is for st.James please transfer to st.James team
Non-Outage | J.E.26.08.29036 | C001894787 | Andrae Dawkins | St.James | Completed | Load_242949 | Queens Drive - 710 | 2026-08-20 08:10 | 2026-08-20 08:12 | 2026-08-20 08:35 | 2026-08-20 11:41 | 2026-08-20 12:05 | 2026-08-20 12:04 | 2026-08-20 12:07 | 2026-08-20 12:07 |  |  | Fair | No | Cannot locate unable to reach customers mobile phone
Non-Outage | J.E.26.08.29038 | C001894786 | Andrae Dawkins | St.James | Completed | Load_246427 | Bogue - 310 | 2026-08-20 08:10 | 2026-08-20 08:12 | 2026-08-20 08:32 | 2026-08-20 11:32 | 2026-08-20 11:31 | 2026-08-20 11:39 | 2026-08-20 11:39 | 2026-08-20 11:39 |  |  | Fair | No | Found multiple customers experiencing low voltage due 100kva transformer fuse blown refer back to emergency crew
Non-Outage | J.E.26.08.29369 | C001894785 | Andrae Dawkins | St.James | Completed | Load_252409 | Bogue - 310 | 2026-08-20 08:10 | 2026-08-20 08:12 | 2026-08-20 08:32 | 2026-08-20 08:47 | 2026-08-20 08:46 | 2026-08-20 08:48 | 2026-08-20 08:53 | 2026-08-20 08:53 |  |  | Fair | No | Found customer without power since Tuesday from EG box 00568 customer also said that she has been experiencing low voltage refer back to field service
Non-Outage | J.E.26.08.29918 | C001894781 | Lionel Robinson | Trelawny | Completed | Load_246391 | Martha Brae - 210 | 2026-08-20 08:10 | 2026-08-20 15:26 | 2026-08-20 21:39 | 2026-08-20 21:40 | 2026-08-20 21:46 | 2026-08-20 22:48 | 2026-08-20 22:51 | 2026-08-20 22:51 |  |  | Fair | No | Change clamps on pole. Also customer meter is damaged and needs to be replaced outage left 118volts
Non-Outage | J.E.26.08.30033 | C001894779 | Andrae Dawkins | St.James | Completed | Load_263504 | Bogue - 310 | 2026-08-20 08:10 | 2026-08-20 08:12 | 2026-08-20 12:07 | 2026-08-20 12:12 | 2026-08-20 12:18 | 2026-08-20 12:59 | 2026-08-20 12:59 | 2026-08-20 12:59 |  |  | Fair | No | Found customer experiencing low voltage due to corrosion at pothead clean and remade joints voltage left 116/11234
Non-Outage | J.E.26.08.30083 | C001894783 | Roemello Brown | Trelawny | Completed | Load_243995 | Greenwood - 110 | 2026-08-20 08:10 | 2026-08-20 08:12 | 2026-08-20 10:06 | 2026-08-20 10:07 | 2026-08-20 10:48 | 2026-08-20 10:48 | 2026-08-20 11:11 | 2026-08-20 11:11 |  |  | Fair | No | Have premises check problem coming from hexing box please send field service technician to have this check out Voltage found 134/103/237Voltage leave 134/103/237Hex# 04520Hx# 22655474
Non-Outage | J.E.26.08.30175 | C001894784 | Roemello Brown | Trelawny | Completed | Load_294253 | Duncans - 110 | 2026-08-20 08:10 | 2026-08-20 08:12 | 2026-08-20 08:25 | 2026-08-20 08:26 | 2026-08-20 08:36 | 2026-08-20 08:36 | 2026-08-20 08:49 | 2026-08-20 08:49 |  |  | Fair | No | Customer meter burn please send field service technician to have meter change Voltage found 116/117/234Voltage leave 116/117/234
Non-Outage | J.E.26.08.27861 | C001894790 | Andrae Dawkins | St.James | Completed | Load_264886 | Bogue - 310 | 2026-08-20 08:11 | 2026-08-20 08:15 | 2026-08-20 08:35 | 2026-08-20 09:10 | 2026-08-20 09:56 | 2026-08-20 11:17 | 2026-08-20 11:20 | 2026-08-20 11:20 |  |  | Fair | No | Found multiple customers experiencing low voltage voltage found 110/114/224 refer back to emergency
Non-Outage | J.E.26.08.30014 | C001894789 | Marlon Authors | Manchester | Completed | Load_292330 | Spur Tree - 210 | 2026-08-20 08:11 | 2026-08-20 08:12 | 2026-08-20 10:06 | 2026-08-20 10:07 | 2026-08-20 10:06 | 2026-08-20 10:08 | 2026-08-20 10:09 | 2026-08-20 10:09 |  |  | Fair | No | Customer says that she is living in red hills not braes river
Non-Outage | J.E.26.08.26853 | C001894791 | Andrae Dawkins | St.James | Completed | Load_237873 | Bogue - 510 | 2026-08-20 08:12 | 2026-08-20 08:15 | 2026-08-20 17:12 | 2026-08-20 17:13 | 2026-08-20 17:12 | 2026-08-20 16:58 | 2026-08-20 17:14 | 2026-08-20 17:14 |  |  | Fair | No | Cannot locate unable to reach customers mobile phone
Non-Outage | J.E.26.08.26541 | C001894795 | Andrae Dawkins | St.James | Completed | Load_247453 | Bogue - 310 | 2026-08-20 08:13 | 2026-08-20 08:15 | 2026-08-20 14:55 | 2026-08-20 14:56 | 2026-08-20 14:56 | 2026-08-20 14:57 | 2026-08-20 14:58 | 2026-08-20 14:58 |  |  | Fair | No | Found multiple customer experiencing low voltage voltage found on secondary line 101/100/201
Outage | J.E.26.08.26906 | C001894792 | Shawn Medley | St.James | Completed | Load_268413 | Bogue - 310 | 2026-08-20 08:13 | 2026-08-20 08:15 | 2026-08-20 09:45 | 2026-08-20 09:46 | 2026-08-20 10:56 | 2026-08-20 10:58 | 2026-08-20 11:01 | 2026-08-20 11:01 |  |  | Fair | No | Found broken #6 service wire, however i replaced 100ft #6 and using six one bolt clamps.customer now restored.
Non-Outage | J.E.26.08.22618 | C001894799 | Evan Spaulding | St.Mary | Completed | Load_242166 | Highgate -110 | 2026-08-20 08:17 | 2026-08-20 08:19 | 2026-08-20 13:23 | 2026-08-20 13:24 | 2026-08-20 13:59 | 2026-08-20 14:29 | 2026-08-20 14:31 | 2026-08-20 14:31 |  |  | Fair | No | Retention secondary conductors using 2-1 bolt clamps, voltage left 116v,117v.233v.
Non-Outage | J.E.26.08.29239 | C001894800 | Evan Spaulding | St.Mary | Completed | Load_238360 | Highgate - 210 | 2026-08-20 08:17 | 2026-08-20 08:19 | 2026-08-20 11:19 | 2026-08-20 11:20 | 2026-08-20 11:19 | 2026-08-20 11:20 | 2026-08-20 11:22 | 2026-08-20 11:22 |  |  | Fair | No | When to this location last week and clamp up the line side of the pot head and on the pole,then advise the customer to get the load side of pot head and on the house top ,customer is yet to do that.
Non-Outage | J.E.26.08.28900 | C001894801 | Evan Spaulding | St.Mary | Completed | Load_256416 | Highgate -110 | 2026-08-20 08:18 | 2026-08-20 08:19 | 2026-08-20 11:27 | 2026-08-20 11:27 | 2026-08-20 12:11 | 2026-08-20 13:01 | 2026-08-20 13:02 | 2026-08-20 13:02 |  |  | Fair | No | Use 4-1 bolt clamps on Transformer drop leads,voltage left 115v,115v,230v.
Non-Outage | J.E.26.08.30185 | C001894802 | Locksley Allen | St.Mary | Completed | Load_251410 | Annotto Bay - 210 | 2026-08-20 08:19 | 2026-08-20 08:21 | 2026-08-20 09:39 | 2026-08-20 10:22 | 2026-08-20 10:21 | 2026-08-20 10:26 | 2026-08-20 10:24 | 2026-08-20 10:24 |  |  | Fair | No | No problem found at premises. Voltage at meter socket phase to neutral 111v. Streetlight at the gate is not working. Please refer to maintainance
Non-Outage | J.E.26.08.21212 | C001894804 | Locksley Allen | St.Mary | Completed | Load_254255 | Oracabessa - 210 | 2026-08-20 08:20 | 2026-08-20 08:21 | 2026-08-20 13:35 | 2026-08-20 14:24 | 2026-08-20 14:24 | 2026-08-20 14:31 | 2026-08-20 14:28 | 2026-08-20 14:28 |  |  | Fair | No | Pothead found corroded corroded. Install 3 clamps at pothead Voltage at meter socket phase to phase 235v. Phase to neutral 114&115vMeter left
Non-Outage | J.E.26.08.22489 | C001894805 | Locksley Allen | St.Mary | Completed | Load_265475 | Oracabessa - 210 | 2026-08-20 08:20 | 2026-08-20 08:21 | 2026-08-20 14:31 | 2026-08-20 14:52 | 2026-08-20 14:51 | 2026-08-20 14:57 | 2026-08-20 14:54 | 2026-08-20 14:54 |  |  | Fair | No | Gate lock
Non-Outage | J.E.26.08.23778 | C001894803 | Locksley Allen | St.Mary | Completed | Load_249759 | Oracabessa - 210 | 2026-08-20 08:20 | 2026-08-20 08:21 | 2026-08-20 12:21 | 2026-08-20 13:20 | 2026-08-20 13:20 | 2026-08-20 13:36 | 2026-08-20 13:34 | 2026-08-20 13:34 | LeaningPole |  | Fair | No | No problem found at this premises. Several customers service wire near this customer premises,is hanging very low. Not JPS service wire
Non-Outage | J.E.26.08.23171 | C001894806 | Locksley Allen | St.Mary | Completed | Load_237863 | Highgate - 210 | 2026-08-20 08:21 | 2026-08-20 08:22 | 2026-08-20 12:07 | 2026-08-20 12:07 | 2026-08-20 12:07 | 2026-08-20 12:16 | 2026-08-20 12:13 | 2026-08-20 12:13 | BrokenPole |  | Fair | No | No problem found at premises. Check transformer,please refer to emergency
Non-Outage | J.E.26.08.29378 | C001894808 | Locksley Allen | St.Ann | Completed | Load_256734 | Upper White River - 110 | 2026-08-20 08:21 | 2026-08-20 08:22 | 2026-08-20 15:17 | 2026-08-20 15:46 | 2026-08-20 15:45 | 2026-08-20 15:56 | 2026-08-20 15:53 | 2026-08-20 15:53 |  |  | Fair | No | Voltage at meter socket phase to phase 237v. Phase to neutral 127&101vSeveral customers in this area is having the same problem Check transformer
Non-Outage | J.E.26.08.22184 | C001894818 | Odaine Johnson | Clarendon | Completed | Load_260333 | Parnassus - 310 | 2026-08-20 08:23 | 2026-08-20 08:26 | 2026-08-20 09:11 | 2026-08-20 11:40 | 2026-08-20 11:46 | 2026-08-20 11:48 | 2026-08-20 11:48 | 2026-08-20 11:48 |  |  | Fair | No | Premises found okay customer stated that the issue was resolved
Non-Outage | J.E.26.08.22980 | C001894817 | Odaine Johnson | Clarendon | Completed | Load_568978 | Monymusk - 210 | 2026-08-20 08:23 | 2026-08-20 08:26 | 2026-08-20 09:11 | 2026-08-20 11:03 | 2026-08-20 11:32 | 2026-08-20 11:36 | 2026-08-20 11:37 | 2026-08-20 11:37 |  |  | Fair | No | Corroded phase and neutral found at pothead remade connection using 2 pen union voltage reading 117/117/235 volts
Non-Outage | J.E.26.08.23042 | C001894816 | Odaine Johnson | Clarendon | Completed | Load_572144 | Parnassus - 310 | 2026-08-20 08:23 | 2026-08-20 08:26 | 2026-08-20 09:11 | 2026-08-20 11:49 | 2026-08-20 11:53 | 2026-08-20 11:56 | 2026-08-20 11:55 | 2026-08-20 11:55 |  |  | Fair | No | Premises found okay customer stated that the issue was resolved
Non-Outage | J.E.26.08.28148 | C001894814 | Odaine Johnson | Clarendon | Completed | Load_301225 | Monymusk - 410 | 2026-08-20 08:23 | 2026-08-20 08:26 | 2026-08-20 09:11 | 2026-08-20 12:38 | 2026-08-20 12:40 | 2026-08-20 12:40 | 2026-08-20 12:41 | 2026-08-20 12:41 |  |  | Fair | No | Multiple efforts made to contact customer but was unsuccessful
Non-Outage | J.E.26.08.28696 | C001894815 | Odaine Johnson | Clarendon | Completed | Load_250979 | Monymusk - 210 | 2026-08-20 08:23 | 2026-08-20 08:26 | 2026-08-20 09:11 | 2026-08-20 10:34 | 2026-08-20 10:45 | 2026-08-20 10:58 | 2026-08-20 11:02 | 2026-08-20 11:02 |  |  | Fair | No | Corroded phase and neutral found at pole remade connection using 2 one bolt clamps voltage reading 112/112/225 volts
Non-Outage | J.E.26.08.28861 | C001894813 | Odaine Johnson | Clarendon | Completed | Load_260474 | Monymusk - 410 | 2026-08-20 08:23 | 2026-08-20 08:26 | 2026-08-20 09:11 | 2026-08-20 11:56 | 2026-08-20 12:05 | 2026-08-20 12:31 | 2026-08-20 12:33 | 2026-08-20 12:33 |  |  | Fair | No | Corrosion found at pole remade connection using 1: one bolt clamp voltage reading 112 volts
Outage | J.E.26.08.30246 | C001894821 | Rusean Allen | KSAS | Completed | Load_242988 | Cane River - 410 | 2026-08-20 08:27 | 2026-08-20 08:29 | 2026-08-20 10:28 | 2026-08-20 10:28 | 2026-08-20 10:56 | 2026-08-20 11:04 | 2026-08-20 11:04 | 2026-08-20 11:04 | BrokenWire |  | Fair | No | 500ft of customer #6 service wire apparently cut down by RPD, customer is without power, refer to field service department to further investigation.
Outage | J.E.26.08.30250 | C001894820 | Rusean Allen | KSAS | Completed | Load_250802 | Rockfort - 410 | 2026-08-20 08:27 | 2026-08-20 08:29 | 2026-08-20 10:06 | 2026-08-20 10:06 | 2026-08-20 10:23 | 2026-08-20 10:23 | 2026-08-20 10:24 | 2026-08-20 10:24 | Fire |  | Fair | No | Found okay
Non-Outage | J.E.26.08.28686 | C001894833 | Derrick Grubb | St.Thomas | Completed | Load_259463 | Lysson - 410 | 2026-08-20 08:43 | 2026-08-20 08:55 | 2026-08-20 09:55 | 2026-08-20 09:55 | 2026-08-20 10:56 | 2026-08-20 10:56 | 2026-08-20 10:57 | 2026-08-20 10:57 |  |  | Fair | No | Premises found ok, issue resolved from yesterday
Non-Outage | J.E.26.08.29317 | C001894832 | Derrick Grubb | St.Thomas | Completed | Load_248385 | Lysson - 410 | 2026-08-20 08:43 | 2026-08-20 08:54 | 2026-08-20 10:55 | 2026-08-20 10:58 | 2026-08-20 12:18 | 2026-08-20 12:20 | 2026-08-20 12:20 | 2026-08-20 12:20 |  |  | Fair | No | Clear corrosion at pole, voltage readings 119 118 237 volts
Non-Outage | J.E.26.08.29674 | C001894853 | Derrick Grubb | St.Thomas | Completed | Load_242640 | Lysson - 410 | 2026-08-20 08:54 | 2026-08-20 08:55 | 2026-08-20 12:20 | 2026-08-20 12:21 | 2026-08-20 12:44 | 2026-08-20 12:46 | 2026-08-20 12:46 | 2026-08-20 12:46 |  |  | Fair | No | Clear corrosion a pole and reconnect 3wire service
Outage | J.E.26.08.30264 | C001894862 | Raymond Lewis | St.Ann | Completed | Load_244589 | Upper White River - 210 | 2026-08-20 09:04 | 2026-08-20 09:05 | 2026-08-20 09:13 | 2026-08-20 09:14 | 2026-08-20 10:17 | 2026-08-20 12:42 | 2026-08-20 12:43 | 2026-08-20 12:43 |  |  | Fair | No | Open 3 80 amp chip saver to remade primary jumper
Outage | J.E.26.08.30270 | C001894861 | Christopher West | St.Catherine | Completed | Load_262410 | Twickenham - 210 | 2026-08-20 09:04 | 2026-08-20 10:03 | 2026-08-20 13:54 | 2026-08-20 13:55 | 2026-08-20 14:02 | 2026-08-20 14:09 | 2026-08-20 14:09 | 2026-08-20 14:09 | LeaningPole |  | Fair | No | 30’C6 open secondary D/E pole is leaning with extremely low hanging service lines in need of URGENT ATTENTION, requesting a memo be sent to Mr. Wilkie to have matter addressed ASAP.
Non-Outage | J.E.26.08.30296 | C001894899 | Richard Grant | St.Catherine | Completed | Load_244637 | New Michelton - 210 | 2026-08-20 09:26 | 2026-08-20 09:27 | 2026-08-20 09:32 | 2026-08-20 09:33 | 2026-08-20 10:14 | 2026-08-20 11:27 | 2026-08-20 11:27 | 2026-08-20 11:27 |  |  | Fair | No | Defective joint found at pole and corrosion found at pothead. 3 onebolt clamps and 2 penunions used to orrery fault. 111 111 222 voltages left at premises. Premises left okay
Outage | J.E.26.08.30308 | C001894901 | Fitzroy Turner | KSAS | Completed | Load_243339 | Greenwich - 710 | 2026-08-20 09:31 | 2026-08-20 09:33 | 2026-08-20 11:08 | 2026-08-20 11:09 | 2026-08-20 12:17 | 2026-08-20 12:47 | 2026-08-20 12:52 | 2026-08-20 12:52 |  |  | Fair | No | Found 120ft of number #2 triplex burnt up and break down causing single phasing.use 120 ft off #2 triplex to replace defective service wires with preform and 6 one bolt clamps supply restored to areas
Non-Outage | J.E.26.08.30306 | C001894914 | Milton Charlton | KSAN | Completed | Load_240381 | Hope - 510 | 2026-08-20 09:33 | 2026-08-20 09:34 | 2026-08-20 13:23 | 2026-08-20 13:23 | 2026-08-20 14:29 | 2026-08-20 13:35 | 2026-08-20 14:33 | 2026-08-20 14:33 |  |  | Fair | No | Found okay upon arrival. Customer has an internal problem.
Non-Outage | J.E.26.08.30289 | C001894922 | Clyde Brown |  | Completed |  |  | 2026-08-20 09:36 | 2026-08-20 09:37 | 2026-08-20 10:39 | 2026-08-20 17:35 | 2026-08-20 19:31 | 2026-08-20 19:27 | 2026-08-20 19:35 | 2026-08-20 19:35 |  |  | Rains | No | Found ok
Non-Outage | J.E.26.08.30218 | C001894925 | Omar King |  | Completed |  |  | 2026-08-20 09:37 | 2026-08-20 15:21 | 2026-08-20 16:06 | 2026-08-20 16:08 | 2026-08-20 16:07 | 2026-08-20 16:09 | 2026-08-20 16:09 | 2026-08-20 16:09 |  |  | Fair | No | Found 50: KVA transformer chip transformer has been reset and customer now with supply..
Non-Outage | J.E.26.07.14514 | C001894975 | Rayon Foster | Hanover | Completed | Load_241702 | Orange Bay - 310 | 2026-08-20 09:56 | 2026-08-20 09:59 | 2026-08-21 09:16 | 2026-08-21 09:17 | 2026-08-21 09:50 | 2026-08-21 10:36 | 2026-08-21 11:02 | 2026-08-21 11:02 |  |  | Fair | No | One of customer phase on jps light pole was burn off causing the customer to single phase use 2 one bolt clamps at same for repair voltage check 109/110AB219volts
Non-Outage | J.E.26.07.15518 | C001894972 | Rayon Foster | Hanover | Completed | Load_265525 | Orange Bay - 310 | 2026-08-20 09:56 | 2026-08-20 09:59 | 2026-08-21 11:02 | 2026-08-21 11:03 | 2026-08-21 11:02 | 2026-08-21 12:31 | 2026-08-21 12:31 | 2026-08-21 12:31 |  |  | Fair | No | Voltage check at customer pothead on arrival 109/110AB219 however customer circuit was tired out after the hurricane last year customer meter is in locking band customer meter is 10 pole span away from transformer the customer house is about 400ft to 500ft from meter pole secondary line is being prepared a hole for the post has already been dug and line already bushed in preparation for new transformer replacement
Non-Outage | J.E.26.08.05000 | C001895009 | Odeanie Davis | KSAS | Completed | Load_239049 | Rockfort - 410 | 2026-08-20 10:08 | 2026-08-20 10:09 | 2026-08-20 10:28 | 2026-08-20 10:29 | 2026-08-20 10:28 | 2026-08-20 10:43 | 2026-08-20 10:30 | 2026-08-20 10:30 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.05065 | C001895010 | Odeanie Davis | KSAS | Completed | Load_269212 | Rockfort - 410 | 2026-08-20 10:08 | 2026-08-20 10:09 | 2026-08-20 10:31 | 2026-08-20 14:21 | 2026-08-20 14:20 | 2026-08-20 14:59 | 2026-08-20 14:21 | 2026-08-20 14:21 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.12898 | C001895012 | Odeanie Davis | KSAS | Completed | Load_258334 | Rockfort - 410 | 2026-08-20 10:08 | 2026-08-20 10:09 | 2026-08-20 10:38 | 2026-08-20 15:31 | 2026-08-20 15:31 | 2026-08-13 15:43 | 2026-08-20 15:32 | 2026-08-20 15:32 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.14039 | C001895011 | Odeanie Davis | KSAS | Completed | Load_264942 | Rockfort - 410 | 2026-08-20 10:08 | 2026-08-20 10:09 | 2026-08-20 12:11 | 2026-08-20 12:12 | 2026-08-20 12:24 | 2026-08-20 12:56 | 2026-08-20 12:56 | 2026-08-20 12:56 |  |  | Fair | No | 96v/129v at arrival. Open neutral at pothead corrected, 1 one bolt clamp, 111v/112v & 224v After correction.
Non-Outage | J.E.26.08.15940 | C001895013 | Odeanie Davis | KSAS | Completed | Load_239504 | Rockfort - 410 | 2026-08-20 10:08 | 2026-08-20 10:09 | 2026-08-20 11:29 | 2026-08-20 11:30 | 2026-08-20 11:36 | 2026-08-20 12:11 | 2026-08-20 12:11 | 2026-08-20 12:11 |  |  | Fair | No | 117v/118v at arrival, open neutral at pothead corrected, 1 one bolt clamp, 117v/118v & 236v after correction
Non-Outage | J.E.26.08.22284 | C001895014 | Odeanie Davis | KSAS | Completed | Load_238569 | Rockfort - 410 | 2026-08-20 10:08 | 2026-08-20 10:09 | 2026-08-20 10:43 | 2026-08-21 08:25 | 2026-08-21 08:24 | 2026-08-21 08:36 | 2026-08-21 08:36 | 2026-08-21 08:36 |  |  | Fair | No | Customer stated that fuse on transformer keeps opening on the weekend when the factory is closed, customer is requesting for this issue to be looked into
Non-Outage | J.E.26.08.26051 | C001895016 | Odeanie Davis | KSAS | Completed | Load_254390 | Rockfort - 410 | 2026-08-20 10:08 | 2026-08-20 10:09 | 2026-08-20 13:19 | 2026-08-20 13:20 | 2026-08-20 13:19 | 2026-08-20 14:08 | 2026-08-20 14:08 | 2026-08-20 14:08 |  |  | Fair | No | 112v/116v & 229v at location, customer defect, customer was advised to contact their electrician
Non-Outage | J.E.26.08.26601 | C001895015 | Odeanie Davis | KSAS | Completed | Load_240722 | Rockfort - 410 | 2026-08-20 10:08 | 2026-08-20 10:09 | 2026-08-20 10:50 | 2026-08-20 10:50 | 2026-08-20 10:50 | 2026-08-20 11:15 | 2026-08-20 11:15 | 2026-08-20 11:15 |  |  | Fair | No | 116v/117v at arrival, open neutral in meter socket corrected, 117v/116v & 233v after correction.
Non-Outage | J.E.26.08.28123 | C001895017 | Odeanie Davis | KSAS | Completed | Load_266339 | Rockfort - 410 | 2026-08-20 10:08 | 2026-08-21 07:45 | 2026-08-21 12:22 | 2026-08-21 12:22 | 2026-08-21 12:22 | 2026-08-21 12:30 | 2026-08-21 12:28 | 2026-08-21 12:28 |  |  | Fair | No | 106v at arrival, 83v/102v at secondary line, open neutral on secondary line corrected, 2 one bolt clamps,115v in meter socket after correction.
Non-Outage | J.E.26.08.28976 | C001895018 | Odeanie Davis | KSAS | Completed | Load_254509 | Rockfort - 410 | 2026-08-20 10:08 | 2026-08-21 07:47 | 2026-08-21 09:12 | 2026-08-21 09:23 | 2026-08-21 09:22 | 2026-08-21 09:59 | 2026-08-21 09:59 | 2026-08-21 09:59 |  |  | Fair | No | 113v/113v at arrival, both wires were on the same phase, wire was relocated to the other phase, 1 one bolt clamps, 113v/117v & 231v after correction.
Outage | J.E.26.08.30333 | C001895019 | Antony Levy | KSAS | Completed | Load_254965 | Duhaney - 310 | 2026-08-20 10:09 | 2026-08-20 10:10 | 2026-08-20 12:51 | 2026-08-20 12:51 | 2026-08-20 13:21 | 2026-08-20 13:23 | 2026-08-20 13:25 | 2026-08-20 13:25 | BrokenPole |  | Fair | No | No broken pole found at address unable to reach customer by phone...
Non-Outage | J.E.26.08.29357 | C001895022 | Nickolas Rodriques |  | Completed |  |  | 2026-08-20 10:11 | 2026-08-20 10:14 | 2026-08-20 12:57 | 2026-08-20 12:57 | 2026-08-20 13:44 | 2026-08-20 14:02 | 2026-08-20 14:04 | 2026-08-20 14:04 |  |  | Fair | No | Found customers with electricity. The customer confirmed that the outage was restored.
Outage | J.E.26.08.29328 | C001895023 | Nickolas Rodriques | St.Catherine | Completed | Load_557177 | Tredegar - 210 | 2026-08-20 10:11 | 2026-08-20 10:14 | 2026-08-20 14:05 | 2026-08-20 14:05 | 2026-08-20 14:34 | 2026-08-20 14:53 | 2026-08-20 15:02 | 2026-08-20 15:02 |  |  | Fair | No | Customer stated that he is having issues topping up his prepaid box. Refer to field service.
Outage | J.E.26.08.29988 | C001895021 | Richard Nicholas | St.Catherine | Completed | Load_244132 | Tredegar - 510 | 2026-08-20 10:11 | 2026-08-20 15:42 | 2026-08-20 17:48 | 2026-08-20 17:48 | 2026-08-20 18:18 | 2026-08-20 18:30 | 2026-08-20 18:33 | 2026-08-20 18:33 |  |  | Fair | No | At Mr.campbell chicken farm,the 4w meter and meter socket found burnt however work seen in progress repairing damaged meter socket.please refer to the field service department to replace burnt 4w meter.follow up required.
Outage | J.E.26.08.30274 | C001895020 | Richard Nicholas | St.Catherine | Completed | Load_257696 | Tredegar - 510 | 2026-08-20 10:11 | 2026-08-20 15:42 | 2026-08-20 18:57 | 2026-08-20 18:57 | 2026-08-20 19:49 | 2026-08-20 21:24 | 2026-08-20 21:26 | 2026-08-20 21:26 |  | Y | Fair | No | Spot bushing done.splice and retention 2 span of broken secondary phase and neutral conductors.15ft of #2aac and 5 clamp was used to complete the repairs.
Non-Outage | J.E.26.08.22313 | C001895045 | Derrick Grubb | St.Thomas | Completed | Load_246020 | Lysson - 410 | 2026-08-20 10:18 | 2026-08-20 10:19 | 2026-08-20 14:30 | 2026-08-20 14:31 | 2026-08-20 14:30 | 2026-08-20 14:31 | 2026-08-20 14:31 | 2026-08-20 14:31 |  |  | Fair | No | Premises not located and several calls to customer went unanswered
Outage | J.E.26.08.29481 | C001895046 | Cliton Henry | St.Mary | Completed | Load_351415 | Oracabessa - 210 | 2026-08-20 10:19 | 2026-08-20 10:20 | 2026-08-20 10:29 | 2026-08-20 10:30 | 2026-08-20 11:12 | 2026-08-20 11:21 | 2026-08-20 11:24 | 2026-08-20 11:24 |  |  | Fair | No | Zero volts found at the customer’s pothead. RAMI infrastructure, kindly refer to Field Service Department for corrective action
Outage | J.E.26.08.30370 | C001895054 | Milton Charlton | KSAN | Completed | Load_253549 | Hope - 510 | 2026-08-20 10:21 | 2026-08-20 10:22 | 2026-08-20 14:38 | 2026-08-20 14:38 | 2026-08-20 15:25 | 2026-08-20 15:05 | 2026-08-20 15:27 | 2026-08-20 15:27 |  |  | Fair | No | Customer meter #2405687 disconnected for debt.
Non-Outage | J.E.26.08.26103 | C001895055 | Orville Lee | St.Catherine | Completed | Load_267629 | Twickenham - 210 | 2026-08-20 10:22 | 2026-08-20 10:23 | 2026-08-20 11:48 | 2026-08-20 11:49 | 2026-08-20 11:48 | 2026-08-20 12:10 | 2026-08-20 12:11 | 2026-08-20 12:11 |  |  | Fair | No | Checks made and found pothead connection corroded Two pen union and one1bolt clamps used
Outage | J.E.26.08.30298 | C001895056 | Tyrese Williams | St.Ann | Completed | Load_260937 | Roaring River - 210 | 2026-08-20 10:22 | 2026-08-21 08:26 | 2026-08-21 08:33 | 2026-08-21 12:21 | 2026-08-21 12:50 | 2026-08-21 12:52 | 2026-08-21 12:52 | 2026-08-21 12:52 |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.08.30354 | C001895057 | Raymond Lewis | St.Ann | Completed | Load_256803 | Upper White River - 210 | 2026-08-20 10:24 | 2026-08-20 10:27 | 2026-08-20 13:08 | 2026-08-20 13:08 | 2026-08-20 13:08 | 2026-08-20 13:12 | 2026-08-20 13:12 | 2026-08-20 13:12 |  |  | Fair | No | Open 3 80 amp switch saver to remade primary jumper also joints need to ampake
Outage | J.E.26.08.30330 | C001895058 | Collin Robinson | Portland | Completed | Load_1003540 | Port Antonio - 310 | 2026-08-20 10:25 | 2026-08-20 10:27 | 2026-08-20 10:57 | 2026-08-20 10:57 | 2026-08-20 11:37 | 2026-08-20 11:39 | 2026-08-20 11:39 | 2026-08-20 11:39 |  |  | Fair | No | Customer was disconnected for none payment
Non-Outage | J.E.26.08.30237 | C001895063 | Clyde Brown |  | Completed |  |  | 2026-08-20 10:29 | 2026-08-20 11:52 | 2026-08-20 12:15 | 2026-08-20 12:16 | 2026-08-20 12:57 | 2026-08-20 12:49 | 2026-08-20 13:01 | 2026-08-20 13:01 | BangingWires |  | Fair | No | Cannot be located customer not answering phone
Outage | J.E.26.08.30341 | C001895062 | Shawn Medley | St.James | Completed | Load_240011 | Bogue - 310 | 2026-08-20 10:29 | 2026-08-20 10:30 | 2026-08-20 11:17 | 2026-08-20 11:17 | 2026-08-20 13:46 | 2026-08-20 13:55 | 2026-08-20 14:20 | 2026-08-20 14:20 | LowHangingWires |  | Rains | No | Burnt 25kva at browns town, secondary need maintenance; refer to maintenance Materials 3 D iron and Spool, 3 -10” bolts and washer, 50’ - #2 AAAC Wire
Non-Outage | J.E.26.08.30319 | C001895107 | Lancelot Brown |  | Completed |  |  | 2026-08-20 11:04 | 2026-08-20 11:05 | 2026-08-20 11:41 | 2026-08-20 11:41 | 2026-08-20 14:57 | 2026-08-20 15:00 | 2026-08-20 15:00 | 2026-08-20 15:00 |  |  | Fair | No | Found 10kva fuse blown cause by rotten fuse replace 1-1amp at 10kva pole number 102924 supply restore
Outage | J.E.26.08.30422 | C001895106 | Andre Williams | Trelawny | Completed | Load_292356 | Duncans - 210 | 2026-08-20 11:04 | 2026-08-20 11:05 | 2026-08-20 11:36 | 2026-08-20 11:38 | 2026-08-20 12:39 | 2026-08-20 12:46 | 2026-08-20 12:46 | 2026-08-20 12:46 |  |  | Fair | No | Cell tower out as a result of work been carried out on line section by Jps personnel’s
Outage | J.E.26.08.30389 | C001895129 | Raymond Lewis | St.Ann | Completed | Load_268103 | Upper White River - 210 | 2026-08-20 11:21 | 2026-08-20 11:22 | 2026-08-20 12:43 | 2026-08-20 12:44 | 2026-08-20 13:05 | 2026-08-20 13:07 | 2026-08-20 13:07 | 2026-08-20 13:07 |  |  | Fair | No | Meter burn up 2884343
Outage | J.E.26.08.30493 | C001895126 | Tyrese Williams | St.Ann | Completed | Load_241157 | Cardiff Hall - 310 | 2026-08-20 11:21 | 2026-08-20 11:24 | 2026-08-20 11:43 | 2026-08-20 11:43 | 2026-08-20 11:43 | 2026-08-20 11:44 | 2026-08-20 11:44 | 2026-08-20 11:44 |  |  | Fair | No | Premises not found not getting customer on phone
Non-Outage | J.E.26.08.26245 | C001895139 | Raymond Lewis | St.Ann | Completed | Load_572667 | Roaring River - 410 | 2026-08-20 11:23 | 2026-08-20 11:24 | 2026-08-20 13:12 | 2026-08-20 13:13 | 2026-08-20 14:09 | 2026-08-20 14:10 | 2026-08-20 14:10 | 2026-08-20 14:10 |  |  | Fair | No | Phone not answering
Non-Outage | J.E.26.08.29620 | C001895141 | Christopher Edwards | KSAN | Completed | Load_248982 | Constant Spring - 410 | 2026-08-20 11:23 | 2026-08-20 11:54 | 2026-08-20 12:32 | 2026-08-20 14:31 | 2026-08-20 14:30 | 2026-08-20 14:33 | 2026-08-20 14:36 | 2026-08-20 14:36 |  |  | Fair | No | Required bucket truck to cut bamboo off #2 twisted wire
Non-Outage | J.E.26.08.30472 | C001895142 | Christopher Edwards | KSAN | Completed | Load_256340 | Constant Spring - 410 | 2026-08-20 11:23 | 2026-08-20 11:54 | 2026-08-20 12:16 | 2026-08-20 13:02 | 2026-08-20 13:50 | 2026-08-20 14:16 | 2026-08-20 14:30 | 2026-08-20 14:30 |  |  | Fair | No | Customer service wire is damaged Customer is approximately 650ft from JPS service poleCustomer was advised to get electrician and upgrade their wire from #6 to number 2
Outage | J.E.26.08.29650 | C001895140 | Marlon Authors | St.Elizabeth | Completed | Load_260745 | Maggotty - 210 | 2026-08-20 11:23 | 2026-08-20 11:24 | 2026-08-20 12:33 | 2026-08-20 12:34 | 2026-08-20 13:03 | 2026-08-20 13:50 | 2026-08-20 13:56 | 2026-08-20 13:56 |  |  | Fair | No | Supply check and found working okay. Voltage reading 116v, 114v and cross phase 231volts.
Outage | J.E.26.08.30381 | C001895143 | Neckell Ormsby | St.Mary | Completed | Load_349471 | Oracabessa - 210 | 2026-08-20 11:24 | 2026-08-20 15:19 | 2026-08-20 15:27 | 2026-08-20 15:27 | 2026-08-20 16:32 | 2026-08-20 16:36 | 2026-08-20 16:36 | 2026-08-20 16:36 |  |  | Fair | No | Restoration work needs to be done to restore customer supply please refer to maintenance department
Outage | J.E.26.08.30425 | C001895158 | Javid Vernon | Westmoreland | Completed | Load_247446 | Paradise - 110 | 2026-08-20 11:38 | 2026-08-20 11:39 | 2026-08-20 12:43 | 2026-08-20 12:44 | 2026-08-20 13:28 | 2026-08-20 13:58 | 2026-08-20 13:58 | 2026-08-20 13:58 |  |  | Fair | No | Refuse one 10 amp junction fuse
Outage | J.E.26.08.30372 | C001895170 | Marlon Authors | Manchester | Completed | Load_266341 | Spur Tree - 210 | 2026-08-20 11:45 | 2026-08-20 11:46 | 2026-08-20 15:28 | 2026-08-20 15:29 | 2026-08-20 15:28 | 2026-08-20 15:46 | 2026-08-20 15:47 | 2026-08-20 15:47 |  |  | Rains | No | Patrol and found clear. Replace one blown 10 amp junction fuse no pole #. Restored supply okay
Outage | J.E.26.08.30489 | C001895175 | Collin Robinson | Portland | Completed | Load_265522 | Port Antonio - 310 | 2026-08-20 11:49 | 2026-08-20 11:49 | 2026-08-20 12:09 | 2026-08-20 12:09 | 2026-08-20 12:59 | 2026-08-20 13:12 | 2026-08-20 13:30 | 2026-08-20 13:30 | BrokenWire |  | Fair | No | Reconnect broken 3 wire service at pole Voltage reading 118 v 117v 235v
Non-Outage | J.E.26.08.30545 | C001895182 | Milton Charlton | KSAN | Completed | Load_243399 | Hope - 410 | 2026-08-20 11:52 | 2026-08-20 11:54 | 2026-08-20 12:17 | 2026-08-20 12:17 | 2026-08-20 13:18 | 2026-08-20 12:45 | 2026-08-20 13:20 | 2026-08-20 13:20 |  |  | Fair | No | Found okay upon arrival. Customer has an internal problem.
Outage | J.E.26.08.30503 | C001895184 | Christopher West | St.Catherine | Completed | Load_254383 | Twickenham - 210 | 2026-08-20 11:56 | 2026-08-20 12:20 | 2026-08-20 13:17 | 2026-08-20 13:18 | 2026-08-20 13:44 | 2026-08-20 13:54 | 2026-08-20 13:54 | 2026-08-20 13:54 |  |  | Fair | No | Premises found closed at time of visit.
Outage | J.E.26.08.30555 | C001895183 | Cliton Henry | St.Mary | Completed | Load_254195 | Highgate - 210 | 2026-08-20 11:56 | 2026-08-20 11:58 | 2026-08-20 12:43 | 2026-08-20 12:44 | 2026-08-20 12:43 | 2026-08-20 12:50 | 2026-08-20 12:51 | 2026-08-20 12:51 | BrokenWire |  | Fair | No | St. Mary Operations team found working in the area.
Non-Outage | J.E.26.08.30584 | C001895212 | Christopher West | Portmore | Completed | Load_256296 | Naggo Head - 510 | 2026-08-20 12:11 | 2026-08-20 12:11 | 2026-08-20 12:31 | 2026-08-20 12:31 | 2026-08-20 12:31 | 2026-08-20 13:10 | 2026-08-20 13:17 | 2026-08-20 13:17 |  |  | Fair | No | A burnt off open secondary jumper, burnt drop lead connections were found at pole#014215 housing a bank x2 50 & 25kva transformers, the power transformer was also missing a fuse holder, the NWC sewage pump was also affected by the situation, transformer was de-energized, used 6 clamps to remake all connections, a fuse holder with a 3A fuse was installed, transformers were re-energized, customers now okay..
Outage | J.E.26.08.30561 | C001895224 | Neville Spencer | Clarendon | Completed | Load_258698 | May Pen - 110 | 2026-08-20 12:12 | 2026-08-20 12:14 | 2026-08-20 12:28 | 2026-08-20 12:29 | 2026-08-20 13:47 | 2026-08-20 13:47 | 2026-08-20 17:27 | 2026-08-20 17:27 |  |  | Fair | No | Found planned outage in area.
Outage | J.E.26.08.30580 | C001895225 | Clyde Brown | Clarendon | Completed | Load_246356 | Parnassus - 310 | 2026-08-20 12:12 | 2026-08-20 12:14 | 2026-08-20 13:01 | 2026-08-20 13:02 | 2026-08-20 13:14 | 2026-08-20 14:30 | 2026-08-20 14:36 | 2026-08-20 14:36 |  |  | SevereWind | No | Blown 2-50 amps junction fuse at phase 1 line patrolled and no fault seen ,2-switch defective and need to be replaced ,temporary string fuse .
Non-Outage | J.E.26.08.30569 | C001895227 | Clyde Brown |  | Completed |  |  | 2026-08-20 12:13 | 2026-08-20 12:14 | 2026-08-20 13:01 | 2026-08-20 14:42 | 2026-08-20 15:32 | 2026-08-20 15:30 | 2026-08-20 15:39 | 2026-08-20 15:39 | LeaningPole |  | SevereWind | No | T 30c6 secondary pole lean over with base rotten and need to be change urgently
Outage | J.E.26.08.30563 | C001895228 | Clyde Brown | Clarendon | Completed | Load_270064 | May Pen - 210 | 2026-08-20 12:13 | 2026-08-20 12:15 | 2026-08-20 13:01 | 2026-08-20 17:12 | 2026-08-20 17:12 | 2026-08-20 17:31 | 2026-08-20 17:34 | 2026-08-20 17:34 | TreeContact | Y | SevereWind | No | Big mango tree near primary and secondary line for vegetation crew to cut.
Outage | J.E.26.08.30571 | C001895226 | Clyde Brown | Clarendon | Completed | Load_248640 | Parnassus - 310 | 2026-08-20 12:13 | 2026-08-20 12:14 | 2026-08-20 13:01 | 2026-08-20 14:37 | 2026-08-20 14:37 | 2026-08-20 14:30 | 2026-08-20 14:41 | 2026-08-20 14:41 |  |  | SevereWind | No | Blown 2-50 amps junction fuse at Hayes phase #1,line patrolled and 2- defective switch need to be replaced,fuse temporary replaced .
Non-Outage | J.E.26.08.30610 | C001895252 | Denton Williams |  | Completed |  |  | 2026-08-20 12:40 | 2026-08-20 15:29 | 2026-08-20 16:00 | 2026-08-20 16:01 | 2026-08-20 16:54 | 2026-08-20 16:55 | 2026-08-20 17:16 | 2026-08-20 17:16 |  |  | Fair | No | Visited location and found electrical supply okay. No blown fuse seen.
Non-Outage | J.E.26.08.30653 | C001895276 | Daniel Francis |  | Completed |  |  | 2026-08-20 13:00 | 2026-08-20 15:35 | 2026-08-20 19:56 | 2026-08-20 19:56 | 2026-08-20 21:41 | 2026-08-20 21:39 | 2026-08-20 21:45 | 2026-08-20 21:45 |  |  | Fair | No | Change 1 one bolt clamp 115 116 230 in all
Outage | J.E.26.08.30616 | C001895278 | Daniel Francis | St.Ann | Completed | Load_244116 | Cardiff Hall - 310 | 2026-08-20 13:00 | 2026-08-20 15:27 | 2026-08-21 03:42 | 2026-08-21 03:43 | 2026-08-21 03:42 | 2026-08-21 03:43 | 2026-08-21 03:44 | 2026-08-21 03:44 |  |  | Fair | No | Already completed
Outage | J.E.26.08.30626 | C001895277 | Neckell Ormsby | St.Ann | Completed | Load_253027 | Upper White River - 210 | 2026-08-20 13:00 | 2026-08-20 15:27 | 2026-08-20 17:15 | 2026-08-20 17:16 | 2026-08-20 17:54 | 2026-08-20 17:55 | 2026-08-20 17:55 | 2026-08-20 17:55 |  |  | Fair | No | Customer not aware of any report to jps
Non-Outage | J.E.26.08.29327 | C001895284 | Tyrese Williams | St.Ann | Completed | Load_262327 | Cardiff Hall - 310 | 2026-08-20 13:05 | 2026-08-20 13:07 | 2026-08-20 13:51 | 2026-08-20 13:51 | 2026-08-20 14:38 | 2026-08-20 15:04 | 2026-08-20 15:04 | 2026-08-20 15:04 |  |  | Fair | No | Remade service wire joint at pole use 2 pg clamp
Outage | J.E.26.08.30665 | C001895301 | Daniel Francis | St.Ann | Completed | Load_241565 | Cardiff Hall - 310 | 2026-08-20 13:20 | 2026-08-20 15:25 | 2026-08-21 02:24 | 2026-08-21 02:25 | 2026-08-21 02:48 | 2026-08-21 03:11 | 2026-08-21 03:12 | 2026-08-21 03:12 | BrokenWire |  | Fair | No | Splice and retention service wire also use 3 one bolt clamp
Non-Outage | J.E.26.08.30692 | C001895342 | Elvis Trowers |  | Completed |  |  | 2026-08-20 13:39 | 2026-08-20 13:40 | 2026-08-20 15:10 | 2026-08-20 15:11 | 2026-08-20 15:35 | 2026-08-20 16:05 | 2026-08-20 16:12 | 2026-08-20 16:12 | Fire |  | Fair | No | Isolate bank of 1-25&1-50 kva transformers at pole #0051328 and repair burnt off transformer drop lead . Repair using 8ft # 2/0 conductor and four 1- bolt clamps. And reclose transformers switches.
Outage | J.E.26.08.30494 | C001895346 | Richard Nicholas | St.Catherine | Completed | Load_265602 | Tredegar - 510 | 2026-08-20 13:41 | 2026-08-20 15:42 | 2026-08-20 16:10 | 2026-08-20 16:10 | 2026-08-20 17:09 | 2026-08-20 17:29 | 2026-08-20 17:31 | 2026-08-20 17:31 |  |  | Fair | No | Coconut bow that rest against single phase primary,removed.replaced blown 10amp junctions fuse at the intersection of Fraser blvd and st.gerard rd.
Non-Outage | J.E.26.08.30287 | C001895387 | Royston Montague | St.Catherine | Completed | Load_238202 | Rhodens Pen - 410 | 2026-08-20 14:15 | 2026-08-20 14:17 | 2026-08-20 14:23 | 2026-08-20 14:27 | 2026-08-20 15:14 | 2026-08-20 16:03 | 2026-08-20 16:03 | 2026-08-20 16:03 |  |  | Fair | No | Blown primary junction fuse 25amp. Line patrol, nothing unusual observed. 25amps fuse replace.
Non-Outage | J.E.26.08.26625 | C001895393 | Royston Montague | St.Catherine | Completed | Load_1000366 | Rhodens Pen - 410 | 2026-08-20 14:16 | 2026-08-20 14:17 | 2026-08-20 14:23 | 2026-08-20 16:04 | 2026-08-20 16:42 | 2026-08-20 17:02 | 2026-08-20 17:02 | 2026-08-20 17:02 |  |  | Fair | No | Corrosion at customer take off point. Same corrected. Voltage found 115v 97v voltage after job completion are 230v 115v 114v
Non-Outage | J.E.26.08.27546 | C001895388 | Royston Montague | St.Catherine | Completed | Load_269589 | Rhodens Pen - 410 | 2026-08-20 14:16 | 2026-08-20 14:17 | 2026-08-20 14:23 | 2026-08-21 13:21 | 2026-08-21 13:27 | 2026-08-21 13:32 | 2026-08-21 13:32 | 2026-08-21 13:32 |  |  | Fair | No | Rami system in area, please assign to the relevant team thanks customers on Peres complaint of fluctuations of voltage. Street lights also affected.
Non-Outage | J.E.26.08.30741 | C001895399 | Elvis Trowers |  | Completed |  |  | 2026-08-20 14:30 | 2026-08-20 14:34 | 2026-08-20 16:12 | 2026-08-20 16:14 | 2026-08-20 16:49 | 2026-08-20 17:20 | 2026-08-20 17:19 | 2026-08-20 17:19 | BrokenWire |  | Fair | No | Customer service wire #6 triplex neutral burned off at pole. Repair using 6ft of #6 triplex neutral and two 1- bolt clamps.
Outage | J.E.26.08.30514 | C001895410 | Dean- Smith | Hanover | Completed | Load_252433 | Orange Bay - 210 | 2026-08-20 14:42 | 2026-08-20 16:02 | 2026-08-20 22:04 | 2026-08-20 22:04 | 2026-08-20 22:57 | 2026-08-20 22:57 | 2026-08-20 22:58 | 2026-08-20 22:58 |  |  | Rains | No | Check and found ok
Outage | J.E.26.08.30650 | C001895408 | Floyd Taylor | Trelawny | Completed | Load_255152 | Martha Brae - 110 | 2026-08-20 14:42 | 2026-08-21 07:52 | 2026-08-21 08:05 | 2026-08-21 08:40 | 2026-08-21 09:14 | 2026-08-21 09:15 | 2026-08-21 09:15 | 2026-08-21 09:15 |  |  | Fair | No | Found customer with light
Outage | J.E.26.08.30313 | C001895416 | Romeo Brissett | St.James | Completed | Load_258108 | Bogue - 610 | 2026-08-20 14:43 | 2026-08-20 17:31 | 2026-08-21 11:40 | 2026-08-21 11:44 | 2026-08-21 11:43 | 2026-08-21 11:55 | 2026-08-21 11:57 | 2026-08-21 11:57 |  |  | Fair | No | Check and found internal fault customer was advised to get an electrician V/R found and left 111-112-224.
Outage | J.E.26.08.30548 | C001895415 | Romeo Brissett | St.James | Completed | Load_249549 | Bogue - 610 | 2026-08-20 14:43 | 2026-08-20 16:20 | 2026-08-21 09:37 | 2026-08-21 09:37 | 2026-08-21 10:22 | 2026-08-21 10:30 | 2026-08-21 10:43 | 2026-08-21 10:43 |  |  | Fair | No | Customer was reconnected by escalation.
Outage | J.E.26.08.30710 | C001895414 | Romeo Brissett | St.James | Completed | Load_266451 | Bogue - 610 | 2026-08-20 14:43 | 2026-08-20 16:21 | 2026-08-20 16:24 | 2026-08-20 16:25 | 2026-08-20 16:57 | 2026-08-20 19:30 | 2026-08-20 19:37 | 2026-08-20 19:37 |  |  | Fair | No | Isolated (1)15amps junction fuse, repaired junction switch bottom, installed (1)10amps junction fuse and replaced (1)15KVA transformer fuse. Used 2 hotline clamps, (1)8amps junction and (1)2 amps Transformer fuse.
Outage | J.E.26.08.30717 | C001895413 | Dean- Smith | Hanover | Completed | Load_292864 | Orange Bay - 310 | 2026-08-20 14:43 | 2026-08-20 16:02 | 2026-08-20 16:36 | 2026-08-20 16:36 | 2026-08-20 20:35 | 2026-08-20 20:35 | 2026-08-20 20:35 | 2026-08-20 20:35 |  |  | Rains | No | Premises closed
Outage | J.E.26.08.30411 | C001895417 | Swon Miller | St.James | Completed | Load_237795 | Bogue - 310 | 2026-08-20 14:45 | 2026-08-20 14:48 | 2026-08-20 21:02 | 2026-08-20 21:03 | 2026-08-20 21:40 | 2026-08-20 22:01 | 2026-08-20 22:06 | 2026-08-20 22:06 |  |  | Fair | No | Found customer without supply voltage found 0.000 contact customer care to restore power supply to customer.customer care agent was unsuccessful plz refer to field service voltage left 0.000
Outage | J.E.26.08.30681 | C001895418 | Swon Miller | St.James | Completed | Load_259518 | Bogue - 310 | 2026-08-20 14:45 | 2026-08-20 14:48 | 2026-08-20 15:01 | 2026-08-20 15:05 | 2026-08-20 15:42 | 2026-08-20 16:41 | 2026-08-20 16:33 | 2026-08-20 16:33 |  |  | Fair | No | Found customer single phasing due to contamination at pole voltage found 116/clean and remake joints use 2pg voltage left 115/116/231
Outage | J.E.26.08.30613 | C001895440 | Clyde Brown | Clarendon | Completed | Load_241665 | Parnassus - 310 | 2026-08-20 15:14 | 2026-08-20 15:14 | 2026-08-20 16:00 | 2026-08-20 16:01 | 2026-08-20 16:26 | 2026-08-20 16:45 | 2026-08-20 17:02 | 2026-08-20 17:02 |  |  | SevereWind | No | 50 amps junction fuse with defective switch drop off same replaced and need defective switch to be replaced same temporary fixed.
Outage | J.E.26.08.30690 | C001895441 | Clyde Brown | Clarendon | Completed | Load_258144 | Parnassus - 210 | 2026-08-20 15:15 | 2026-08-20 15:16 | 2026-08-20 19:35 | 2026-08-20 19:36 | 2026-08-20 21:27 | 2026-08-20 21:24 | 2026-08-20 21:33 | 2026-08-20 21:33 |  |  | Rains | No | Customer said his light was restored after paying the light bill
Outage | J.E.26.08.30722 | C001895447 | Romaine Roberts | St.Mary | Completed | Load_263802 | Highgate -110 | 2026-08-20 15:18 | 2026-08-20 15:20 | 2026-08-20 20:12 | 2026-08-20 22:10 | 2026-08-20 22:10 | 2026-08-20 22:10 | 2026-08-20 22:11 | 2026-08-20 22:11 |  |  | Fair | No | Banging secondary conductor open and close 25 kva to clear line power restore no pole number
Outage | J.E.26.08.30932 | C001895446 | Romaine Roberts |  | Completed | Load_265502 | Highgate -110 | 2026-08-20 15:18 | 2026-08-20 15:20 | 2026-08-20 22:11 | 2026-08-20 22:15 | 2026-08-20 22:14 | 2026-08-20 22:16 | 2026-08-20 22:17 | 2026-08-20 22:17 | BrokenWire |  | Fair | No | Premises not found phone number not valid
Outage | J.E.26.08.30474 | C001895449 | Neckell Ormsby | St.Ann | Completed | Load_259886 | Upper White River - 110 | 2026-08-20 15:19 | 2026-08-20 15:20 | 2026-08-20 16:36 | 2026-08-20 16:37 | 2026-08-20 16:36 | 2026-08-20 16:37 | 2026-08-20 16:37 | 2026-08-20 16:37 |  |  | Fair | No | St Ann call wrong parish
Outage | J.E.26.08.30624 | C001895448 | Neckell Ormsby | St.Mary | Completed | Load_574221 | Oracabessa - 210 | 2026-08-20 15:19 | 2026-08-20 15:20 | 2026-08-20 16:38 | 2026-08-20 16:38 | 2026-08-20 17:05 | 2026-08-20 17:15 | 2026-08-20 17:15 | 2026-08-20 17:15 |  |  | Fair | No | Remade joint at pole using 1- one bolt clamp voltage left 230v 114v 115v
Non-Outage | J.E.26.08.25653 | C001895450 | Marlon Brown | Trelawny | Completed | Load_302800 | Duncans - 110 | 2026-08-20 15:20 | 2026-08-20 20:03 | 2026-08-20 21:25 | 2026-08-20 21:25 | 2026-08-20 22:36 | 2026-08-20 22:42 | 2026-08-20 22:42 | 2026-08-20 22:42 |  |  | Fair | No | Unable to locate customer via telephone nor direction
Non-Outage | J.E.26.08.29838 | C001895453 | Lionel Robinson | Trelawny | Completed | Load_241008 | Martha Brae - 110 | 2026-08-20 15:20 | 2026-08-20 15:25 | 2026-08-20 18:29 | 2026-08-20 18:30 | 2026-08-20 19:30 | 2026-08-20 19:30 | 2026-08-20 19:34 | 2026-08-20 19:34 |  |  | Fair | No | Remake secondaryneutral jumper on transformers pole, voltage reading 118 v, 117v, 235v
Non-Outage | J.E.26.08.30830 | C001895451 | Omar King |  | Completed |  |  | 2026-08-20 15:20 | 2026-08-20 15:23 | 2026-08-20 21:52 | 2026-08-20 21:52 | 2026-08-20 22:33 | 2026-08-20 22:33 | 2026-08-20 22:34 | 2026-08-20 22:34 | Fire |  | Fair | No | Unable to find customer directions not sufficient.
Outage | J.E.26.08.30664 | C001895456 | Omar King | St.Ann | Completed | Load_265554 | Ocho Rios - 310 | 2026-08-20 15:20 | 2026-08-20 15:23 | 2026-08-20 20:58 | 2026-08-20 21:00 | 2026-08-20 21:50 | 2026-08-20 21:51 | 2026-08-20 21:52 | 2026-08-20 21:52 |  |  | Fair | No | Outage related to defective transformer..
Outage | J.E.26.08.30721 | C001895452 | Omar King | St.Ann | Completed | Load_246903 | Roaring River - 210 | 2026-08-20 15:20 | 2026-08-20 15:23 | 2026-08-20 16:16 | 2026-08-20 16:17 | 2026-08-20 16:39 | 2026-08-20 16:51 | 2026-08-20 16:51 | 2026-08-20 16:51 |  |  | Fair | No | Found 25 KVA transformer fuse blown cause by bird fuse has been replaced and customer now with supply
Outage | J.E.26.08.30759 | C001895467 | Oshane Warren | Westmoreland | Completed | Load_249908 | Paradise - 310 | 2026-08-20 15:22 | 2026-08-20 15:26 | 2026-08-20 15:37 | 2026-08-20 15:37 | 2026-08-20 18:12 | 2026-08-20 18:16 | 2026-08-20 18:17 | 2026-08-20 18:17 | BrokenWire |  | Rains | No | Reconnection back service wire neutral at secondary line voltage 110
Non-Outage | J.E.26.08.26245 | C001895468 | Omar King | St.Ann | Completed | Load_572667 | Roaring River - 410 | 2026-08-20 15:23 | 2026-08-20 15:24 | 2026-08-20 19:45 | 2026-08-20 19:46 | 2026-08-20 20:46 | 2026-08-20 20:54 | 2026-08-20 20:54 | 2026-08-20 20:54 |  |  | Fair | No | Found customer meter defective meter #2311545 please refer to relevant personnel
Outage | J.E.26.08.30720 | C001895471 | Tyrese Williams | St.Ann | Completed | Load_241408 | Roaring River - 210 | 2026-08-20 15:25 | 2026-08-21 08:24 | 2026-08-21 08:33 | 2026-08-21 10:47 | 2026-08-21 12:01 | 2026-08-21 12:20 | 2026-08-21 12:20 | 2026-08-21 12:20 |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.08.27794 | C001895472 | Lionel Robinson | Trelawny | Completed | Load_263192 | Martha Brae - 110 | 2026-08-20 15:26 | 2026-08-20 15:27 | 2026-08-21 16:23 | 2026-08-21 16:24 | 2026-08-21 17:05 | 2026-08-21 17:17 | 2026-08-21 17:17 | 2026-08-21 17:17 |  |  | Fair | No | Customer checked and found ok
Non-Outage | J.E.26.08.28020 | C001895473 | Lionel Robinson | Trelawny | Completed | Load_263192 | Martha Brae - 110 | 2026-08-20 15:26 | 2026-08-20 15:27 | 2026-08-20 20:59 | 2026-08-20 20:59 | 2026-08-20 21:33 | 2026-08-20 21:33 | 2026-08-20 21:35 | 2026-08-20 21:35 |  |  | Fair | No | Premises can’t be located also customer contact is not working
Non-Outage | J.E.26.08.24973 | C001895481 | Marlon Brown | Trelawny | Completed | Load_242318 | Duncans - 210 | 2026-08-20 15:28 | 2026-08-20 15:30 | 2026-08-20 17:28 | 2026-08-20 17:28 | 2026-08-20 17:56 | 2026-08-20 18:35 | 2026-08-20 18:37 | 2026-08-20 18:37 |  |  | Fair | No | Check and found ok Voltage found at meter socket 116/114=230Voltage leaving at meter socket 114/116=230
Non-Outage | J.E.26.08.30353 | C001895480 | Marlon Brown | Trelawny | Completed | Load_241073 | Duncans - 210 | 2026-08-20 15:28 | 2026-08-20 15:29 | 2026-08-20 16:46 | 2026-08-20 16:46 | 2026-08-20 16:46 | 2026-08-20 17:27 | 2026-08-20 17:27 | 2026-08-20 17:27 |  |  | Fair | No | Clean and remake joint at pole use 1 pg clampVoltage found at meter socket 120vVoltage leaving at meter socket 120/120=240v.
Outage | J.E.26.08.30727 | C001895482 | Hartley Chin | Clarendon | Completed | Load_244344 | May Pen - 110 | 2026-08-20 15:28 | 2026-08-20 15:30 | 2026-08-20 16:17 | 2026-08-20 18:27 | 2026-08-20 18:26 | 2026-08-20 18:29 | 2026-08-20 18:32 | 2026-08-20 18:32 |  |  | Fair | No | Found 10 KVA transformer breaker on trip , line patrolled and found oaky , reset transformer…
Non-Outage | J.E.26.08.30431 | C001895486 | Denton Williams | Portland | Completed | Load_240694 | Port Antonio - 410 | 2026-08-20 15:29 | 2026-08-20 15:31 | 2026-08-20 18:32 | 2026-08-20 18:33 | 2026-08-20 18:37 | 2026-08-20 18:43 | 2026-08-20 18:47 | 2026-08-20 18:47 | LeaningPole |  | Fair | No | The customer stated that they want to carry out work on the grounding wire form the meter socket. There’s a locking band installed around meter. Please refer to field service to remove locking band.
Non-Outage | J.E.26.08.30506 | C001895485 | Andrae Clarke | Portland | Completed | Load_244330 | Port Antonio - 310 | 2026-08-20 15:29 | 2026-08-21 08:33 | 2026-08-21 10:08 | 2026-08-21 10:08 | 2026-08-21 11:51 | 2026-08-21 12:59 | 2026-08-21 12:58 | 2026-08-21 12:58 |  |  | Fair | No | Repair broken wires used two one bolt clamp Check voltage 126
Non-Outage | J.E.26.08.30689 | C001895484 | Denton Williams | Portland | Completed | Load_253288 | Port Antonio - 410 | 2026-08-20 15:29 | 2026-08-20 15:31 | 2026-08-20 15:35 | 2026-08-20 15:36 | 2026-08-20 15:45 | 2026-08-20 15:46 | 2026-08-20 15:51 | 2026-08-20 15:51 | BrokenPole |  | Fair | No | When we reached out to the customer, they clarified that their electrical supply is okay. However, their concern is with the electrical connectors.
Non-Outage | J.E.26.08.24579 | C001895488 | Marlon Brown | Trelawny | Completed | Load_292567 | Duncans - 210 | 2026-08-20 15:30 | 2026-08-20 15:31 | 2026-08-20 18:37 | 2026-08-20 18:37 | 2026-08-20 19:55 | 2026-08-20 21:17 | 2026-08-20 21:17 | 2026-08-20 21:17 |  |  | Fair | No | Isolated 25kva transformer to repair 1 span of broken secondary neutral AAC, use 100ft #2 AAC, 2 #2 preforms and 2 pg clamps to effect repairs. Voltage found at meter socket 135/95=230Voltage leaving at meter socket 114/116=230
Non-Outage | J.E.26.08.29404 | C001895504 | Daniel Francis | St.Ann | Completed | Load_247748 | Cardiff Hall - 310 | 2026-08-20 15:31 | 2026-08-20 15:33 | 2026-08-21 03:13 | 2026-08-21 03:14 | 2026-08-21 03:31 | 2026-08-21 03:40 | 2026-08-21 03:41 | 2026-08-21 03:41 | LowHangingWires |  | Fair | No | Unable to locate customer not answering phone
Non-Outage | J.E.26.08.30380 | C001895490 | Neckell Ormsby | St.Mary | Completed | Load_349209 | Oracabessa - 210 | 2026-08-20 15:31 | 2026-08-20 15:33 | 2026-08-20 17:55 | 2026-08-20 17:56 | 2026-08-20 19:07 | 2026-08-20 19:09 | 2026-08-20 19:09 | 2026-08-20 19:09 | Fire |  | Fair | No | Unable to locate customer after several calls also no proper directions
Outage | J.E.26.08.30627 | C001895503 | Donald Cunningham | St.Catherine | Completed | Load_289089 | Twickenham - 210 | 2026-08-20 15:31 | 2026-08-20 15:32 | 2026-08-20 16:51 | 2026-08-20 16:51 | 2026-08-20 17:01 | 2026-08-20 17:03 | 2026-08-20 17:05 | 2026-08-20 17:05 |  |  | Fair | No | Eg system box need to check refer to mr Ellison urgent attention required customer have sick daughter at home
Outage | J.E.26.08.30733 | C001895489 | Donald Cunningham | Portmore | Completed | Load_241653 | Naggo Head - 610 | 2026-08-20 15:31 | 2026-08-20 15:32 | 2026-08-20 15:40 | 2026-08-20 15:40 | 2026-08-20 16:44 | 2026-08-20 16:50 | 2026-08-20 16:50 | 2026-08-20 16:50 | BrokenPole |  | Fair | No | No broken pole seen
Outage | J.E.26.08.30738 | C001895492 | Donald Cunningham | Portmore | Completed | Load_258650 | Naggo Head - 610 | 2026-08-20 15:31 | 2026-08-20 15:32 | 2026-08-20 18:34 | 2026-08-20 18:35 | 2026-08-20 19:15 | 2026-08-20 19:27 | 2026-08-20 19:29 | 2026-08-20 19:29 |  |  | Fair | No | Corroded phase and neural by pothead corrected voltage readings by meter socket 119/120/241
Non-Outage | J.E.26.08.30533 | C001895506 | Lionel Robinson | Trelawny | Completed | Load_292808 | Greenwood - 110 | 2026-08-20 15:34 | 2026-08-20 15:35 | 2026-08-20 16:10 | 2026-08-20 16:47 | 2026-08-20 16:46 | 2026-08-20 18:04 | 2026-08-20 18:04 | 2026-08-20 18:04 |  |  | SevereWind | No | Replace 100ft #6 triplex voltage reading 118, 117, 235 volts
Outage | J.E.26.08.28991 | C001895507 | Moses Elliston | St.Catherine | Completed | Load_261245 | Tredegar - 510 | 2026-08-20 15:34 | 2026-08-20 15:35 | 2026-08-21 08:51 | 2026-08-21 08:51 | 2026-08-21 08:51 | 2026-08-21 08:36 | 2026-08-21 08:53 | 2026-08-21 08:53 |  |  | Fair | No | Not located,no answer from cell
Outage | J.E.26.08.30957 | C001895508 | Hartley Chin | St.Ann | Completed | Load_262673 | Cardiff Hall - 310 | 2026-08-20 15:35 | 2026-08-20 15:36 | 2026-08-20 16:06 | 2026-08-20 21:24 | 2026-08-20 21:23 | 2026-08-20 21:24 | 2026-08-20 21:24 | 2026-08-20 21:24 |  |  | Fair | No | Call related to job # 31257 ..
Outage | J.E.26.08.30820 | C001895514 | Selvin White | St.Elizabeth | Completed | Load_302915 | Maggotty - 110 | 2026-08-20 15:36 | 2026-08-20 15:38 | 2026-08-20 18:50 | 2026-08-20 18:51 | 2026-08-20 18:51 | 2026-08-20 18:52 | 2026-08-20 19:03 | 2026-08-20 19:03 |  |  | Rains | No | Customer says supply was restored. Outage was as a result of a blown 10 amp junction fuse at the entrance of the scheme along with two blown 30 amps junction fuse at Rhyiene with no pole number found at location.. Lightning strike was said to be the cause.
Outage | J.E.26.08.30889 | C001895516 | Selvin White | St.Elizabeth | Completed | Load_255127 | Maggotty - 110 | 2026-08-20 15:36 | 2026-08-20 15:38 | 2026-08-20 15:52 | 2026-08-20 15:52 | 2026-08-20 17:24 | 2026-08-20 18:38 | 2026-08-20 18:49 | 2026-08-20 18:49 |  |  | Rains | No | Replace two 30 amps junction fuse at Rhyiene ,also re- close a 30 amp trip saver at LAB6- 747 at Moggotty roundabout after patrolling 3 phase primary line. Supply restored to the affected customers. Heavy rain and lightning was happening at the time of the outages.
Non-Outage | J.E.26.08.29119 | C001895520 | Romaine Roberts | St.Mary | Completed | Load_260130 | Annotto Bay - 310 | 2026-08-20 15:37 | 2026-08-20 15:38 | 2026-08-20 17:00 | 2026-08-20 17:00 | 2026-08-20 17:00 | 2026-08-20 19:26 | 2026-08-20 19:27 | 2026-08-20 19:27 |  |  | Fair | No | Open and close 3 -25kva transformer to clean and remake joints at brop lead voltage found 234-229-228 414-113-410 after finishing found that customer also have a internal fault in breaker panel
Outage | J.E.26.08.30611 | C001895519 | Richard Nicholas | St.Catherine | Completed | Load_253973 | Tredegar - 510 | 2026-08-20 15:37 | 2026-08-20 15:40 | 2026-08-20 18:34 | 2026-08-20 18:35 | 2026-08-20 18:56 | 2026-08-20 18:56 | 2026-08-20 18:57 | 2026-08-20 18:57 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.30662 | C001895521 | Richard Nicholas | St.Catherine | Completed | Load_556507 | Tredegar - 510 | 2026-08-20 15:37 | 2026-08-20 15:40 | 2026-08-20 21:26 | 2026-08-20 21:27 | 2026-08-20 21:45 | 2026-08-20 21:45 | 2026-08-20 21:46 | 2026-08-20 21:46 |  |  | Fair | No | Rammy prepaid failure,please refer to Mr.moses.
Outage | J.E.26.08.30779 | C001895522 | Richard Nicholas | St.Catherine | Completed | Load_242360 | Tredegar - 510 | 2026-08-20 15:38 | 2026-08-20 15:40 | 2026-08-20 17:32 | 2026-08-20 17:33 | 2026-08-20 17:46 | 2026-08-20 17:47 | 2026-08-20 17:47 | 2026-08-20 17:47 |  |  | EarthMovement | No | Area found ok
Outage | J.E.26.08.30917 | C001895524 | Milton Charlton | KSAN | Completed | Load_264066 | West Kings House - 410 | 2026-08-20 15:40 | 2026-08-20 15:45 | 2026-08-20 15:51 | 2026-08-20 16:09 | 2026-08-20 16:09 | 2026-08-20 16:35 | 2026-08-20 16:18 | 2026-08-20 16:18 |  |  | Fair | No | Twisted 4/0 secondary feeding fifteen meters( eight at 20 PhoenixAve.and seven across the road)crystalize and cause fire at transformer pole. Crystalize 4/0 triplex was disconnected. Need about 200ft 2/0 triplex to replace conductor.i
Outage | J.E.26.08.30985 | C001895523 | Marlon Authors | Manchester | Completed | Load_242417 | Spur Tree - 210 | 2026-08-20 15:40 | 2026-08-20 15:41 | 2026-08-20 16:01 | 2026-08-20 16:02 | 2026-08-20 16:25 | 2026-08-20 16:29 | 2026-08-20 16:29 | 2026-08-20 16:29 |  |  | Fair | No | Unable to locate and the customer not answering the phone
Outage | J.E.26.08.30421 | C001895537 | Radcliffe Coleman | St.Catherine | Completed | Load_302499 | Tredegar - 210 | 2026-08-20 15:42 | 2026-08-21 08:14 | 2026-08-21 08:43 | 2026-08-21 10:12 | 2026-08-21 10:44 | 2026-08-21 10:51 | 2026-08-21 10:51 | 2026-08-21 10:51 |  |  | Fair | No | Customer is being supplied from a meter center at pole 0116185, that has become defective (the meter center is 100% rotten) and needs to be replaced. Please refer this situation to the field service department for their intervention has customer is experiencing unstable supply.
Outage | J.E.26.08.30666 | C001895538 | Richard Nicholas | St.Catherine | Completed | Load_1001429 | Tredegar - 210 | 2026-08-20 15:42 | 2026-08-20 15:44 | 2026-08-20 21:46 | 2026-08-20 21:47 | 2026-08-20 22:07 | 2026-08-20 22:07 | 2026-08-20 22:22 | 2026-08-20 22:22 |  |  | Fair | No | Rammy failure
Outage | J.E.26.08.30973 | C001895541 | Donald Cunningham | Portmore | Completed | Load_247848 | Naggo Head - 610 | 2026-08-20 15:46 | 2026-08-20 15:47 | 2026-08-20 17:05 | 2026-08-20 17:06 | 2026-08-20 18:29 | 2026-08-20 18:30 | 2026-08-20 18:34 | 2026-08-20 18:34 |  |  | Fair | No | Crew was working in area today supply restored
Outage | J.E.26.08.31008 | C001895562 | Marlon Authors | Manchester | Completed | Load_239389 | Spur Tree - 210 | 2026-08-20 15:57 | 2026-08-20 15:58 | 2026-08-20 16:30 | 2026-08-20 16:30 | 2026-08-20 17:33 | 2026-08-20 20:39 | 2026-08-20 20:39 | 2026-08-20 20:39 | TreeContact |  | Fair | No | Patrol and found coconut tree falls on the line leaving five poles spans of secondary conductors on the ground. Splice and retention same using forty feet of 2/0 , twenty feet of #2 conductor, three #2, six 2/0 preforms, 12 clamps and replace one blown 25 amp junction fuse at pole #530758. Restored supply okay
Outage | J.E.26.08.30981 | C001895563 | Eric Williams | KSAN | Completed | Load_266480 | Washington Blvd - 310 | 2026-08-20 15:59 | 2026-08-20 16:08 | 2026-08-20 17:21 | 2026-08-20 17:21 | 2026-08-20 17:23 | 2026-08-20 17:30 | 2026-08-20 17:30 | 2026-08-20 17:30 | BrokenWire |  | Fair | No | Wire found connected and customer has electricity
Outage | J.E.26.08.31001 | C001895564 | Elvis Trowers | KSAS | Completed | Load_254610 | Rockfort - 210 | 2026-08-20 16:00 | 2026-08-20 16:02 | 2026-08-20 16:12 | 2026-08-20 17:19 | 2026-08-20 18:40 | 2026-08-20 18:45 | 2026-08-20 18:45 | 2026-08-20 18:45 |  |  | Fair | No | Customer service wire #6 triplex phase and neutral corroded at pothead. Repair using five 1- bolt clamps. Readings at pothead 112-113-226 volts.
Non-Outage | J.E.26.08.30942 | C001895568 | Neckell Ormsby | St.Mary | Completed | Load_260764 | Oracabessa - 110 | 2026-08-20 16:03 | 2026-08-20 16:04 | 2026-08-20 19:10 | 2026-08-20 19:11 | 2026-08-20 19:48 | 2026-08-20 20:03 | 2026-08-20 20:03 | 2026-08-20 20:03 |  |  | Fair | No | Low voltage, troubleshoot and remade 3- separate secondary neutral jumper also transformer drop lead neutral using approximately 7- one bolt clamps voltage left 120v 120v 240v however customer still complaining of low voltage she was advised to check her wiring beyond the meter
Outage | J.E.26.08.30998 | C001895572 | Denton Williams | Portland | Completed | Load_247906 | Port Antonio - 410 | 2026-08-20 16:04 | 2026-08-20 16:05 | 2026-08-20 17:16 | 2026-08-20 17:17 | 2026-08-20 17:32 | 2026-08-20 18:14 | 2026-08-20 18:18 | 2026-08-20 18:18 |  | Y | Fair | No | 15amps trip saver operates as a result of a fallen tree on primary line. Cut and remove tree from line and closed trip saver to restore power supply.
Non-Outage | J.E.26.08.31006 | C001895573 | Michael Paterson | Westmoreland | Completed | Load_252470 | Paradise - 210 | 2026-08-20 16:06 | 2026-08-20 16:07 | 2026-08-20 16:45 | 2026-08-20 16:45 | 2026-08-20 19:34 | 2026-08-20 19:39 | 2026-08-20 19:40 | 2026-08-20 19:40 |  |  | Fair | No | Rami in areas please refer to to field service deferment at paradise Mr tressing Beckford
Outage | J.E.26.08.31055 | C001895580 | Kemark Slue | St.Catherine | Completed | Load_267673 | New Michelton - 210 | 2026-08-20 16:13 | 2026-08-20 16:14 | 2026-08-20 16:30 | 2026-08-20 16:30 | 2026-08-20 19:00 | 2026-08-20 19:07 | 2026-08-20 19:12 | 2026-08-20 19:12 | Fire |  | Fair | No | Upon arrival at the location the crew discovered that #6 triplex service supplying the customer was entangled with telecommunications cable which caused a fire, isolate service, untangled cables, string and retention conductor and remake joints using three Penn-unions.
Outage | J.E.26.08.31058 | C001895581 | Oshane Warren | Westmoreland | Completed | Load_249902 | Paradise - 310 | 2026-08-20 16:13 | 2026-08-20 16:14 | 2026-08-20 18:51 | 2026-08-20 18:51 | 2026-08-20 18:51 | 2026-08-20 18:51 | 2026-08-20 18:52 | 2026-08-20 18:52 |  |  | Fair | No | Customer stated that power was restored
Outage | J.E.26.08.31016 | C001895582 | Clyde Brown | Clarendon | Completed | Load_241665 | Parnassus - 310 | 2026-08-20 16:15 | 2026-08-20 16:16 | 2026-08-20 17:08 | 2026-08-20 17:09 | 2026-08-20 17:09 | 2026-08-20 16:44 | 2026-08-20 17:11 | 2026-08-20 17:11 |  |  | SevereWind | No | Defective switch with 50 amps junction fuse same temporary fixed and need to be replaced urgently
Outage | J.E.26.08.31057 | C001895595 | Romeo Brissett | St.James | Completed | Load_250986 | Bogue - 510 | 2026-08-20 16:19 | 2026-08-20 16:21 | 2026-08-20 19:37 | 2026-08-20 19:38 | 2026-08-20 20:08 | 2026-08-20 23:18 | 2026-08-20 23:29 | 2026-08-20 23:29 |  |  | Fair | No | Removed defective arrester and replaced (1)25amps junction fuse and (1)15amps junction fuse.
Outage | J.E.26.08.30893 | C001895607 | Romeo Brissett | St.James | Completed | Load_569747 | Bogue - 510 | 2026-08-20 16:21 | 2026-08-21 07:50 | 2026-08-21 07:59 | 2026-08-21 08:00 | 2026-08-21 08:35 | 2026-08-21 09:24 | 2026-08-21 09:37 | 2026-08-21 09:37 |  |  | Fair | No | Customer meter was disconnected due to late bill payment, however a receipt was given and customer was reconnected by escalation.
Non-Outage | J.E.26.08.10457 | C001895619 | Marlon Authors | St.Elizabeth | Completed | Load_266995 | Maggotty - 210 | 2026-08-20 16:27 | 2026-08-20 16:29 | 2026-08-20 22:22 | 2026-08-20 22:23 | 2026-08-20 22:27 | 2026-08-20 22:51 | 2026-08-20 22:51 | 2026-08-20 22:51 |  |  | Fair | No | Supply checked and found service wire neutral burnt off caused by severe wind. Splice and retention same using 10 feet of #6 triplex service wire and two clamps. Unable to do voltage check gate locked no one home
Outage | J.E.26.08.30986 | C001895633 | Selvin White | St.Elizabeth | Completed | Load_239118 | Maggotty - 110 | 2026-08-20 16:31 | 2026-08-20 16:32 | 2026-08-20 20:39 | 2026-08-20 20:39 | 2026-08-20 21:07 | 2026-08-20 23:02 | 2026-08-20 23:08 | 2026-08-20 23:08 |  |  | Fair | No | Isolate a section of the single phase primary line and reclose a 10 amp trip saver a Springfield just above the square. Supply restored to some customers.
Outage | J.E.26.08.31072 | C001895634 | Selvin White | St.Elizabeth | Completed | Load_242928 | Maggotty - 110 | 2026-08-20 16:31 | 2026-08-20 16:32 | 2026-08-20 23:08 | 2026-08-20 23:09 | 2026-08-20 23:08 | 2026-08-20 23:15 | 2026-08-20 23:15 | 2026-08-20 23:15 |  |  | Fair | No | Daylight attention is required due to foggy conditions and poor visibility . A section of was isolated to Maybole. Please refer to the morning crew for follow up.
Non-Outage | J.E.26.08.31054 | C001895638 | Denton Williams |  | Completed |  |  | 2026-08-20 16:33 | 2026-08-20 16:34 | 2026-08-20 18:21 | 2026-08-20 18:22 | 2026-08-20 18:22 | 2026-08-20 18:31 | 2026-08-20 18:32 | 2026-08-20 18:32 |  | Y | Fair | No | 15amps trip saver operates as a result of a fallen tree on primary line. Cut and remove tree from line and closed trip saver to restore power supply.
Outage | J.E.26.08.30909 | C001895635 | Richard Samuda | Manchester | Completed | Load_244185 | Kendal - 210 | 2026-08-20 16:33 | 2026-08-20 17:27 | 2026-08-20 17:44 | 2026-08-20 17:44 | 2026-08-20 18:21 | 2026-08-20 06:55 | 2026-08-20 18:55 | 2026-08-20 18:55 |  |  | Fair | No | Found 30amp junction blown patrol line found 20amp junction blown patrol line found nothing replaced 30amp fuse then 20amp fuse customer back to normal
Outage | J.E.26.08.30963 | C001895640 | Richard Samuda | Manchester | Completed | Load_245077 | Kendal - 210 | 2026-08-20 16:33 | 2026-08-20 16:34 | 2026-08-20 20:19 | 2026-08-20 20:29 | 2026-08-20 21:09 | 2026-08-20 10:12 | 2026-08-20 22:12 | 2026-08-20 22:12 |  |  | Fair | No | Pole Nu018436 found 25 amp junction blown patrol line found one span of secondary down tree fell on line daylight needed to carry out repair due the terrain of the line bucket truck required and cut tree off line open switch 108436 at crown land about 20 customers affected
Outage | J.E.26.08.30994 | C001895641 | Richard Samuda | Manchester | Completed | Load_255541 | Kendal - 210 | 2026-08-20 16:33 | 2026-08-20 16:34 | 2026-08-20 19:20 | 2026-08-20 19:21 | 2026-08-20 19:39 | 2026-08-20 20:19 | 2026-08-20 20:19 | 2026-08-20 20:19 |  |  | Fair | No | Found 10 amp junction blown patrol line found nothing replaced fuse customer back to normal
Outage | J.E.26.08.31042 | C001895637 | Richard Samuda | Manchester | Completed | Load_251321 | Kendal - 210 | 2026-08-20 16:33 | 2026-08-20 16:34 | 2026-08-20 18:55 | 2026-08-20 18:56 | 2026-08-20 19:04 | 2026-08-20 19:12 | 2026-08-20 19:13 | 2026-08-20 19:13 |  |  | Fair | No | Found 20 amp junction blown patrol line found nothing replaced fuse
Outage | J.E.26.08.31065 | C001895639 | Denton Williams | Portland | Completed | Load_243073 | Port Antonio - 410 | 2026-08-20 16:33 | 2026-08-20 16:34 | 2026-08-20 18:19 | 2026-08-20 18:20 | 2026-08-20 18:19 | 2026-08-20 18:20 | 2026-08-20 18:20 | 2026-08-20 18:20 | BrokenWire | Y | Fair | No | 15amps trip saver operates as a result of a fallen tree on primary line. Cut and remove tree from line and closed trip saver to restore power supply.
Outage | J.E.26.08.31080 | C001895636 | Richard Samuda | Manchester | Completed | Load_1002477 | Kendal - 210 | 2026-08-20 16:33 | 2026-08-20 16:34 | 2026-08-20 17:33 | 2026-08-20 17:33 | 2026-08-20 17:39 | 2026-08-20 05:42 | 2026-08-20 17:43 | 2026-08-20 17:43 |  |  | Fair | No | 098228 found 10 amp junction blown replaced fuse customer back to normal
Outage | J.E.26.08.31094 | C001895655 | Hartley Chin | Clarendon | Completed | Load_568436 | May Pen - 110 | 2026-08-20 16:43 | 2026-08-20 16:50 | 2026-08-20 18:32 | 2026-08-20 18:34 | 2026-08-20 19:35 | 2026-08-20 20:06 | 2026-08-20 20:07 | 2026-08-20 20:07 |  |  | Fair | No | Found blown 10 amp junction fuse (no pole #) line patrolled and found okay , junction refused…
Outage | J.E.26.08.31095 | C001895656 | Hartley Chin | Clarendon | Completed | Load_568435 | May Pen - 110 | 2026-08-20 16:43 | 2026-08-20 16:50 | 2026-08-20 18:32 | 2026-08-20 20:08 | 2026-08-20 20:07 | 2026-08-20 20:08 | 2026-08-20 20:09 | 2026-08-20 20:09 |  |  | Fair | No | Found okay , call related to job # 31094 …
Outage | J.E.26.08.31103 | C001895657 | Roxroy Needham | St.Ann | Completed | Load_256057 | Cardiff Hall - 310 | 2026-08-20 16:43 | 2026-08-21 07:36 | 2026-08-21 08:03 | 2026-08-21 08:03 | 2026-08-21 09:19 | 2026-08-21 09:20 | 2026-08-21 09:20 | 2026-08-21 09:20 | LeaningPole |  | Fair | No | Not getting customer on phone
Outage | J.E.26.08.31104 | C001895666 | Radcliffe Coleman | St.Catherine | Completed | Load_557143 | Tredegar - 410 | 2026-08-20 16:52 | 2026-08-21 08:10 | 2026-08-21 08:43 | 2026-08-21 10:52 | 2026-08-21 11:17 | 2026-08-21 11:21 | 2026-08-21 11:21 | 2026-08-21 11:21 |  |  | Fair | No | Location found okay at the time of visit.
Outage | J.E.26.08.31134 | C001895667 | Hartley Chin | St.Ann | Completed | Load_251603 | Cardiff Hall - 310 | 2026-08-20 16:53 | 2026-08-20 16:56 | 2026-08-20 20:09 | 2026-08-20 21:22 | 2026-08-20 21:21 | 2026-08-20 21:23 | 2026-08-20 21:23 | 2026-08-20 21:23 |  |  | Fair | No | Call related to job # 31257 ..
Outage | J.E.26.08.31147 | C001895668 | Kemark Slue | St.Catherine | Completed | Load_256325 | New Michelton - 210 | 2026-08-20 16:54 | 2026-08-20 16:56 | 2026-08-20 19:12 | 2026-08-20 19:13 | 2026-08-20 19:20 | 2026-08-20 20:19 | 2026-08-20 21:20 | 2026-08-20 21:20 |  | Y | Fair | No | Upon arrival at the location the crew discovered that 25 amps junction for single phase line section at pole # 209511 was blown further patrol revealed that a 15 amps junction at pole # 209659 for said line section was also blown resulting from bamboo trees that came in contact with the primary conductor, cut and remove Bamboo trees, refuse links and re-energized line section, please refer to A. Murray to have vegetation management done on line section.
Outage | J.E.26.08.31122 | C001895669 | Richard Nicholas | St.Catherine | Completed | Load_573904 | Tredegar - 510 | 2026-08-20 16:56 | 2026-08-20 17:47 | 2026-08-20 22:22 | 2026-08-20 22:22 | 2026-08-20 22:52 | 2026-08-20 22:52 | 2026-08-20 22:53 | 2026-08-20 22:53 |  |  | Fair | No | Rammy system
Non-Outage | J.E.26.08.31118 | C001895678 | Donald Cunningham |  | Completed |  |  | 2026-08-20 16:59 | 2026-08-20 17:51 | 2026-08-20 19:29 | 2026-08-20 19:30 | 2026-08-20 20:56 | 2026-08-20 20:56 | 2026-08-20 21:01 | 2026-08-20 21:01 |  |  | Fair | No | Premises not located customer not reachable
Outage | J.E.26.08.31140 | C001895681 | Milton Charlton | KSAN | Completed | Load_241187 | West Kings House - 310 | 2026-08-20 17:03 | 2026-08-20 17:04 | 2026-08-20 17:13 | 2026-08-20 17:13 | 2026-08-20 17:49 | 2026-08-20 18:05 | 2026-08-20 18:20 | 2026-08-20 18:20 | Fire |  | Fair | No | 30ft wooden pole #( no pole#) at the corner of Paddington Terrace and Liguanea Ave. broken in motor vehicle accident causing open wire secondary to entangle with telephone strand causing fire. Isolate 50 kva transformer at pole #0009143. About 50 customers estimated are without supply.Pole has on open wire 4- wire secondary return on 8ft crossarms.
Outage | J.E.26.08.30474 | C001895682 | Omar King | St.Ann | Completed | Load_259886 | Upper White River - 110 | 2026-08-20 17:10 | 2026-08-21 15:19 | 2026-08-21 17:44 | 2026-08-21 17:45 | 2026-08-21 18:36 | 2026-08-21 18:36 | 2026-08-21 18:37 | 2026-08-21 18:37 |  |  | Fair | No | Customer as supply
Non-Outage | J.E.26.08.30240 | C001895690 | Ryan Richards | Manchester | Completed | Load_244647 | Spur Tree - 310 | 2026-08-20 17:27 | 2026-08-20 17:28 | 2026-08-21 07:37 | 2026-08-21 08:20 | 2026-08-21 09:24 | 2026-08-21 11:19 | 2026-08-21 11:19 | 2026-08-21 11:19 |  |  | Fair | No | Unable to locate customer multiple efforts made to contact customer but unsuccessful
Non-Outage | J.E.26.08.30694 | C001895691 | Richard Samuda | Manchester | Completed | Load_263494 | Spur Tree - 310 | 2026-08-20 17:27 | 2026-08-21 09:19 | 2026-08-21 10:14 | 2026-08-21 10:15 | 2026-08-21 10:29 | 2026-08-21 10:50 | 2026-08-21 10:50 | 2026-08-21 10:50 |  |  | Fair | No | Found ok customer has a damaged meter socket advised customer to repair damaged meter socket voltage: 111 , 110 221
Non-Outage | J.E.26.08.31207 | C001895689 | Richard Samuda | Manchester | Completed | Load_243787 | Spur Tree - 310 | 2026-08-20 17:27 | 2026-08-21 09:19 | 2026-08-21 09:27 | 2026-08-21 09:28 | 2026-08-21 10:13 | 2026-08-21 10:14 | 2026-08-21 10:14 | 2026-08-21 10:14 |  |  | Fair | No | Found ok customer said they are back to normal
Outage | J.E.26.08.31199 | C001895694 | Elvis Trowers | KSAS | Completed | Load_257838 | Up Park Camp - 510 | 2026-08-20 17:33 | 2026-08-20 17:39 | 2026-08-20 20:28 | 2026-08-20 20:36 | 2026-08-20 20:36 | 2026-08-20 20:40 | 2026-08-20 20:37 | 2026-08-20 20:37 |  |  | Fair | No | Call related to call at #37 Abengway.
Outage | J.E.26.08.31202 | C001895693 | Elvis Trowers | KSAS | Completed | Load_268988 | Up Park Camp - 510 | 2026-08-20 17:33 | 2026-08-20 17:39 | 2026-08-20 20:31 | 2026-08-20 22:27 | 2026-08-20 22:27 | 2026-08-20 22:40 | 2026-08-20 22:27 | 2026-08-20 22:27 |  |  | Fair | No | Call related to call at #37 Abengway.
Outage | J.E.26.08.31200 | C001895695 | Christopher Edwards | KSAN | Completed | Load_243019 | Constant Spring - 410 | 2026-08-20 17:34 | 2026-08-20 17:39 | 2026-08-20 17:56 | 2026-08-20 18:47 | 2026-08-20 19:22 | 2026-08-20 19:45 | 2026-08-20 19:46 | 2026-08-20 19:46 |  |  | Fair | No | Unable to reach customer byVisit location and observed supply is in the area
Outage | J.E.26.08.31021 | C001895699 | Oshane Warren | St.Elizabeth | Completed | Load_1002136 | Maggotty - 110 | 2026-08-20 17:35 | 2026-08-20 17:36 | 2026-08-20 22:04 | 2026-08-20 22:04 | 2026-08-20 22:04 | 2026-08-20 22:06 | 2026-08-20 22:06 | 2026-08-20 22:06 |  |  | Rains | No | Replace 8 amp junction fuse
Outage | J.E.26.08.31143 | C001895696 | Oshane Warren | St.Elizabeth | Completed | Load_557832 | Maggotty - 110 | 2026-08-20 17:35 | 2026-08-20 17:36 | 2026-08-20 18:52 | 2026-08-20 18:53 | 2026-08-20 21:06 | 2026-08-20 21:12 | 2026-08-20 21:12 | 2026-08-20 21:12 |  |  | Rains | No | Replace two 2amp 25kva transformer fuse and a 20 junction fuse
Outage | J.E.26.08.31227 | C001895700 | Milton Charlton | KSAN | Completed | Load_556202 | West Kings House - 410 | 2026-08-20 17:35 | 2026-08-20 17:38 | 2026-08-20 19:40 | 2026-08-20 19:41 | 2026-08-20 19:40 | 2026-08-20 19:35 | 2026-08-20 19:43 | 2026-08-20 19:43 |  |  | Fair | No | Call related to call at 22 Waterloo Avenue.
Outage | J.E.26.08.31231 | C001895701 | Milton Charlton | KSAN | Completed | Load_249503 | West Kings House - 410 | 2026-08-20 17:35 | 2026-08-20 17:38 | 2026-08-20 18:24 | 2026-08-20 18:24 | 2026-08-20 19:36 | 2026-08-20 19:35 | 2026-08-20 19:40 | 2026-08-20 19:40 |  |  | Fair | No | Refused and reclosed 40 amps junction at pole#0180107 using one 40 amps fuse.
Non-Outage | J.E.26.08.31151 | C001895703 | Milton Charlton |  | Completed |  |  | 2026-08-20 17:45 | 2026-08-20 17:48 | 2026-08-20 18:20 | 2026-08-20 18:21 | 2026-08-20 18:20 | 2026-08-20 18:05 | 2026-08-20 18:23 | 2026-08-20 18:23 | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Call related to other call at 24 Paddington Terrace.
Outage | J.E.26.08.31257 | C001895704 | Hartley Chin | St.Ann | Completed | Load_257509 | Cardiff Hall - 310 | 2026-08-20 17:50 | 2026-08-20 18:01 | 2026-08-20 20:09 | 2026-08-20 21:18 | 2026-08-20 21:18 | 2026-08-20 21:20 | 2026-08-20 21:21 | 2026-08-20 21:21 |  |  | Fair | No | Found blown 20 amp junction fuse @ pole # 0055734 line patrolled and found okay , junction refused…
Outage | J.E.26.08.31263 | C001895706 | Elvis Trowers | KSAS | Completed | Load_243394 | Up Park Camp - 510 | 2026-08-20 17:55 | 2026-08-20 18:06 | 2026-08-20 18:48 | 2026-08-20 18:49 | 2026-08-20 20:13 | 2026-08-20 20:15 | 2026-08-20 20:25 | 2026-08-20 20:25 |  |  | Fair | No | Found one 25 amps junction fuse blown at pole#025572 and one 15 amps junction fuse blown at pole#040175. Refused using one 25 amps fuse and one 15 amps fuse and reclosed both junction switches.
Outage | J.E.26.08.25341 | C001895707 | Swon Miller | Trelawny | Completed | Load_251635 | Greenwood - 210 | 2026-08-20 17:57 | 2026-08-20 17:58 | 2026-08-20 18:20 | 2026-08-20 18:21 | 2026-08-20 18:54 | 2026-08-19 07:21 | 2026-08-20 19:21 | 2026-08-20 19:21 |  |  | Fair | No | Unable to locate customer phone calls to customer went unanswered
Outage | J.E.26.08.31190 | C001895708 | Lionel Robinson | Trelawny | Completed | Load_250230 | Greenwood - 210 | 2026-08-20 17:58 | 2026-08-20 17:59 | 2026-08-20 19:37 | 2026-08-20 19:38 | 2026-08-20 20:04 | 2026-08-20 20:55 | 2026-08-20 20:56 | 2026-08-20 20:56 | BrokenWire |  | Fair | No | Spice and retention #6 triplex service wire voltage reading 118, 119, 237 volts
Outage | J.E.26.08.31128 | C001895709 | Tajay Bernard | Hanover | Completed | Load_257973 | Orange Bay - 310 | 2026-08-20 18:00 | 2026-08-21 07:16 | 2026-08-21 09:37 | 2026-08-21 09:37 | 2026-08-21 09:37 | 2026-08-21 09:37 | 2026-08-21 09:38 | 2026-08-21 09:38 |  |  | Fair | No | Related to previous call job number 31269
Non-Outage | J.E.26.08.30945 | C001895711 | Locksley Allen | St.Mary | Completed | Load_267776 | Oracabessa - 210 | 2026-08-20 18:08 | 2026-08-21 08:39 | 2026-08-21 11:13 | 2026-08-21 11:27 | 2026-08-21 11:26 | 2026-08-21 11:53 | 2026-08-21 11:51 | 2026-08-21 11:51 |  |  | Fair | No | No problem found at premises. JPS corrected the problem last night Voltage at meter socket phase to phase 230v. Phase to neutral 113&103vMeter left working okay
Non-Outage | J.E.26.08.31295 | C001895713 | Milton Charlton |  | Completed |  |  | 2026-08-20 18:15 | 2026-08-20 18:59 | 2026-08-20 21:43 | 2026-08-20 21:44 | 2026-08-20 21:56 | 2026-08-20 22:05 | 2026-08-20 21:58 | 2026-08-20 21:58 | BrokenWire |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.30795 | C001895718 | Hartley Chin | St.Ann | Completed | Load_264617 | Cardiff Hall - 310 | 2026-08-20 18:18 | 2026-08-20 18:19 | 2026-08-20 20:09 | 2026-08-20 21:25 | 2026-08-20 22:06 | 2026-08-20 22:07 | 2026-08-20 22:08 | 2026-08-20 22:08 |  |  | Fair | No | Call related to job # 31257
Outage | J.E.26.08.31276 | C001895721 | Kemark Slue | St.Catherine | Completed | Load_568242 | New Michelton - 210 | 2026-08-20 18:22 | 2026-08-20 18:23 | 2026-08-20 19:12 | 2026-08-20 21:20 | 2026-08-20 21:20 | 2026-08-20 20:37 | 2026-08-20 21:23 | 2026-08-20 21:23 |  | Y | Fair | No | Upon arrival at the location the crew discovered that 25 amps junction for single phase line section at pole # 209511 was blown further patrol revealed that a 15 amps junction at pole # 209659 for said line section was also blown resulting from bamboo trees that came in contact with the primary conductor, cut and remove Bamboo trees, refuse links and re-energized line section, please refer to A. Murray to have vegetation management done on line section.
Outage | J.E.26.08.31292 | C001895722 | Elvis Trowers | KSAS | Completed | Load_237939 | Hunts Bay - 310 | 2026-08-20 18:25 | 2026-08-20 18:51 | 2026-08-20 20:13 | 2026-08-20 20:38 | 2026-08-20 21:23 | 2026-08-20 21:25 | 2026-08-20 21:24 | 2026-08-20 21:24 | BrokenWire |  | Fair | No | Found okay upon arrival.
Outage | J.E.26.08.31344 | C001895736 | Selvin White | St.Elizabeth | Completed | Load_292880 | Maggotty - 110 | 2026-08-20 18:49 | 2026-08-20 18:50 | 2026-08-20 19:11 | 2026-08-20 19:11 | 2026-08-20 19:24 | 2026-08-20 19:47 | 2026-08-20 19:47 | 2026-08-20 19:47 |  |  | Rains | No | Replace a blown 10 amp junction fuse at pole number 008553 after patrolling single phase primary line. Supply restored to the affected customers. Lightning strike was said to be the cause earlier today.
Outage | J.E.26.08.31356 | C001895735 | Selvin White | St.Elizabeth | Completed | Load_574140 | Maggotty - 110 | 2026-08-20 18:49 | 2026-08-20 18:50 | 2026-08-20 19:49 | 2026-08-20 19:49 | 2026-08-20 20:10 | 2026-08-20 20:36 | 2026-08-20 20:36 | 2026-08-20 20:36 |  |  | Rains | No | Defective 25 KVA transformer in a bank of two found at location that supplied a block factory . Please advise Delroy Crew.
Non-Outage | J.E.26.08.31335 | C001895741 | Milton Charlton |  | Completed |  |  | 2026-08-20 18:55 | 2026-08-20 18:59 | 2026-08-20 19:44 | 2026-08-20 19:45 | 2026-08-20 21:38 | 2026-08-20 21:10 | 2026-08-20 21:43 | 2026-08-20 21:43 |  |  | Fair | No | Call related to crystalized conductor on Phoenix Ave. that was disconnected
Non-Outage | J.E.26.08.31351 | C001895743 | Kemark Slue |  | Completed |  |  | 2026-08-20 18:58 | 2026-08-20 18:59 | 2026-08-20 19:12 | 2026-08-20 21:25 | 2026-08-20 21:26 | 2026-08-20 20:28 | 2026-08-20 21:27 | 2026-08-20 21:27 |  | Y | Fair | No | Upon arrival at the location the crew discovered that 25 amps junction for single phase line section at pole # 209511 was blown further patrol revealed that a 15 amps junction at pole # 209659 for said line section was also blown resulting from bamboo trees that came in contact with the primary conductor, cut and remove Bamboo trees, refuse links and re-energized line section, please refer to A. Murray to have vegetation management done on line section.
Outage | J.E.26.08.31140 | C001895744 | Eric Williams | KSAN | Completed | Load_241187 | West Kings House - 310 | 2026-08-20 19:04 | 2026-08-20 19:09 | 2026-08-20 19:27 | 2026-08-20 19:28 | 2026-08-20 20:20 | 2026-08-20 20:49 | 2026-08-20 20:50 | 2026-08-20 20:50 | Fire |  | Fair | No | Vehicle accident broken pole, wire remove from cable wires, refer to maintenance department
Outage | J.E.26.08.31309 | C001895750 | Hartley Chin | St.Ann | Completed | Load_246166 | Cardiff Hall - 310 | 2026-08-20 19:14 | 2026-08-20 19:16 | 2026-08-20 20:09 | 2026-08-20 22:08 | 2026-08-20 22:08 | 2026-08-20 22:08 | 2026-08-20 22:09 | 2026-08-20 22:09 |  |  | Fair | No | Call related to job # 31257 ..
Outage | J.E.26.08.31112 | C001895752 | Dean- Smith | Hanover | Completed | Load_244774 | Orange Bay - 310 | 2026-08-20 19:17 | 2026-08-20 19:18 | 2026-08-20 20:36 | 2026-08-20 20:36 | 2026-08-20 22:02 | 2026-08-20 22:02 | 2026-08-20 22:03 | 2026-08-20 22:03 |  |  | Rains | No | Replace 8amp junction fuse at fish river bridge. Pole number n/a.
Outage | J.E.26.08.31394 | C001895753 | Elvis Trowers | KSAS | Completed | Load_249227 | Up Park Camp - 510 | 2026-08-20 19:18 | 2026-08-20 19:21 | 2026-08-20 20:31 | 2026-08-20 22:26 | 2026-08-20 22:25 | 2026-08-20 22:35 | 2026-08-20 22:27 | 2026-08-20 22:27 |  |  | Fair | No | Call related to call at#37 Abengway.
Non-Outage | J.E.26.08.31004 | C001895760 | Andrae Clarke | Portland | Completed | Load_246094 | Port Antonio - 410 | 2026-08-20 19:36 | 2026-08-21 08:33 | 2026-08-21 09:22 | 2026-08-21 09:22 | 2026-08-21 10:01 | 2026-08-21 10:13 | 2026-08-21 10:08 | 2026-08-21 10:08 |  |  | Fair | No | Went to premises check voltage at pole 196/123/121/242Meter is in a locked box Keyes needed to check meterRefer to in house technician with access Customer reports that it tripped out four times on Wednesday and three times on Thursday
Non-Outage | J.E.26.08.29987 | C001895768 | Donald Cunningham | Portmore | Completed | Load_257194 | Naggo Head - 510 | 2026-08-20 19:38 | 2026-08-20 19:49 | 2026-08-20 21:01 | 2026-08-20 21:02 | 2026-08-20 21:24 | 2026-08-20 21:25 | 2026-08-20 21:29 | 2026-08-20 21:29 |  |  | Fair | No | Premises closed customer not reachable
Outage | J.E.26.08.31311 | C001895774 | Michael Paterson | Westmoreland | Completed | Load_292088 | Paradise - 210 | 2026-08-20 19:49 | 2026-08-20 19:50 | 2026-08-20 21:37 | 2026-08-20 21:38 | 2026-08-20 21:37 | 2026-08-20 21:38 | 2026-08-20 21:38 | 2026-08-20 21:38 |  |  | Fair | No | Customer request daylight attention.
Non-Outage | J.E.26.08.31459 | C001895782 | Elvis Trowers |  | Completed |  |  | 2026-08-20 19:57 | 2026-08-20 20:01 | 2026-08-20 20:26 | 2026-08-20 20:34 | 2026-08-20 20:33 | 2026-08-20 20:35 | 2026-08-20 20:36 | 2026-08-20 20:36 |  |  | Fair | No | Call related to call at #37 Abengway.
Outage | J.E.26.08.31433 | C001895781 | Elvis Trowers | KSAS | Completed | Load_251357 | Cane River - 310 | 2026-08-20 19:57 | 2026-08-20 20:01 | 2026-08-20 21:24 | 2026-08-20 21:25 | 2026-08-20 22:21 | 2026-08-20 22:25 | 2026-08-20 22:24 | 2026-08-20 22:24 |  |  | Fair | No | Customer service wire #6 triplex on the loud side from the meter to the house was vandalism customer responsibility.
Outage | J.E.26.08.31468 | C001895783 | Daniel Francis | St.Ann | Completed | Load_269592 | Cardiff Hall - 310 | 2026-08-20 19:58 | 2026-08-20 19:59 | 2026-08-20 21:46 | 2026-08-20 21:46 | 2026-08-20 23:36 | 2026-08-21 02:05 | 2026-08-21 02:05 | 2026-08-21 02:05 | BrokenWire |  | Fair | No | Found secondary phase and neutral broken splice andRetention 3 span of secondary neutral and 2of secondary phase
Non-Outage | J.E.26.08.20600 | C001895787 | Marlon Brown | Trelawny | Completed | Load_239814 | Duncans - 210 | 2026-08-20 20:03 | 2026-08-20 20:04 | 2026-08-20 21:19 | 2026-08-20 21:19 | 2026-08-20 21:20 | 2026-08-20 21:22 | 2026-08-20 21:23 | 2026-08-20 21:23 |  |  | Fair | No | Customer says she doesn’t want any JPS personnel at her premises at night.
Outage | J.E.26.08.31469 | C001895797 | Eric Williams | KSAN | Completed | Load_264378 | Washington Blvd - 810 | 2026-08-20 20:31 | 2026-08-20 20:49 | 2026-08-20 21:56 | 2026-08-20 21:57 | 2026-08-20 22:40 | 2026-08-20 22:40 | 2026-08-20 22:41 | 2026-08-20 22:41 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.31512 | C001895798 | Daniel Francis | St.Ann | Completed | Load_269504 | Cardiff Hall - 310 | 2026-08-20 20:40 | 2026-08-20 20:41 | 2026-08-21 03:45 | 2026-08-21 03:46 | 2026-08-21 03:45 | 2026-08-21 03:46 | 2026-08-21 03:51 | 2026-08-21 03:51 |  |  | Fair | No | Please refer to relevant person
Non-Outage | J.E.26.08.30517 | C001895799 | Romeo Brissett |  | Completed |  |  | 2026-08-20 20:46 | 2026-08-20 20:47 | 2026-08-21 11:41 | 2026-08-21 11:42 | 2026-08-21 11:42 | 2026-08-21 11:34 | 2026-08-21 11:43 | 2026-08-21 11:43 |  |  | Fair | No | Customer was called and stated that the power was restored.
Outage | J.E.26.08.31495 | C001895800 | Swon Miller | St.James | Completed | Load_269145 | Bogue - 310 | 2026-08-20 20:49 | 2026-08-20 20:50 | 2026-08-21 07:21 | 2026-08-21 10:46 | 2026-08-21 11:50 | 2026-08-21 12:05 | 2026-08-21 12:11 | 2026-08-21 12:11 |  |  | Fair | No | Check and found areas okay voltage found 114/115/232 customer states that power supply has been restored voltage left 115/114/232
Outage | J.E.26.08.31368 | C001895802 | Swon Miller | St.James | Completed | Load_261423 | Bogue - 310 | 2026-08-20 20:52 | 2026-08-20 20:54 | 2026-08-20 22:06 | 2026-08-20 22:07 | 2026-08-20 22:33 | 2026-08-20 22:47 | 2026-08-20 23:03 | 2026-08-20 23:03 |  |  | Fair | No | Found customer without supply voltage found 0.000.with the help of customer care agent Tamara power supply was restored to customer voltage left 115/114/231
Outage | J.E.26.08.31525 | C001895803 | Swon Miller | St.James | Completed | Load_293233 | Queens Drive - 310 | 2026-08-20 20:52 | 2026-08-20 20:53 | 2026-08-21 09:43 | 2026-08-21 09:45 | 2026-08-21 10:13 | 2026-08-19 10:45 | 2026-08-21 10:46 | 2026-08-21 10:46 |  |  | Fair | No | Found customer without supply contact customer care agent Kevon restored power to customer however it was unsuccessful please refer to field service voltage found 0.000 voltage left 0.000
Outage | J.E.26.08.25399 | C001895805 | Tajay Bernard | St.James | Completed | Load_243584 | Bogue - 510 | 2026-08-20 20:55 | 2026-08-21 07:16 | 2026-08-21 09:38 | 2026-08-21 09:38 | 2026-08-21 09:38 | 2026-08-21 09:39 | 2026-08-21 09:39 | 2026-08-21 09:39 |  |  | Fair | No | Customer stated that power was restored
Outage | J.E.26.08.31269 | C001895813 | Tajay Bernard | Hanover | Completed | Load_251315 | Orange Bay - 310 | 2026-08-20 21:20 | 2026-08-21 07:16 | 2026-08-21 07:28 | 2026-08-21 07:53 | 2026-08-21 08:48 | 2026-08-21 09:34 | 2026-08-21 09:36 | 2026-08-21 09:36 |  |  | Fair | No | Refuse 1 20amp junction fuse
Outage | J.E.26.08.31552 | C001895817 | Swon Miller | St.James | Completed | Load_243665 | Queens Drive - 710 | 2026-08-20 21:33 | 2026-08-20 21:34 | 2026-08-21 07:24 | 2026-08-21 12:12 | 2026-08-21 12:24 | 2026-08-11 00:30 | 2026-08-21 12:45 | 2026-08-21 12:45 |  |  | Fair | No | Check and found okay customer states that power supply was restored voltage found 114/113/228 voltage left 114/113/228
Outage | J.E.26.08.31418 | C001895822 | Daniel Francis | St.Ann | Completed | Load_255880 | Cardiff Hall - 310 | 2026-08-20 21:53 | 2026-08-20 21:56 | 2026-08-21 02:23 | 2026-08-21 02:23 | 2026-08-21 02:23 | 2026-08-21 02:24 | 2026-08-21 02:24 | 2026-08-21 02:24 |  |  | Fair | No | Not for st Ann
Outage | J.E.26.08.31566 | C001895827 | Tajay Bernard | Hanover | Completed | Load_252846 | Orange Bay - 210 | 2026-08-20 22:17 | 2026-08-21 07:16 | 2026-08-21 10:13 | 2026-08-21 10:13 | 2026-08-21 12:09 | 2026-08-21 16:04 | 2026-08-21 16:06 | 2026-08-21 16:06 | BrokenWire |  | Fair | No | Check and found a 1 50kva transformer that needs to be upgraded Amp reading found 169/147( continuously rising)Voltage readings 118/119/237Refer to maintenance
Outage | J.E.26.08.30521 | C001895845 | Derrick Dawkins | St.James | Completed | Load_243274 | Bogue - 310 | 2026-08-20 23:22 | 2026-08-20 23:23 | 2026-08-21 00:11 | 2026-08-21 00:12 | 2026-08-21 00:11 | 2026-08-21 00:13 | 2026-08-21 00:13 | 2026-08-21 00:13 |  |  | Fair | No | Check and found premises ok
Outage | J.E.26.08.31495 | C001895843 | Derrick Dawkins | St.James | Completed | Load_269145 | Bogue - 310 | 2026-08-20 23:22 | 2026-08-20 23:23 | 2026-08-21 00:14 | 2026-08-21 00:14 | 2026-08-21 00:14 | 2026-08-21 00:15 | 2026-08-21 00:15 | 2026-08-21 00:15 |  |  | Fair | No | Check and found premises ok
Outage | J.E.26.08.31521 | C001895842 | Derrick Dawkins | St.James | Completed | Load_238476 | Bogue - 610 | 2026-08-20 23:22 | 2026-08-20 23:23 | 2026-08-21 00:15 | 2026-08-21 00:16 | 2026-08-21 00:35 | 2026-08-21 01:10 | 2026-08-21 01:55 | 2026-08-21 01:55 |  |  | Fair | No | Found (1) 100 kva transformer drop lead burn off due sock connection open transformer to clean and remade joint used 2 pg clamp
Outage | J.E.26.08.31552 | C001895844 | Derrick Dawkins | St.James | Completed | Load_243665 | Queens Drive - 710 | 2026-08-20 23:22 | 2026-08-20 23:23 | 2026-08-20 23:30 | 2026-08-20 23:31 | 2026-08-20 23:50 | 2026-08-21 00:03 | 2026-08-21 00:10 | 2026-08-21 00:10 |  |  | Fair | No | Found 50 kva transformer fuse blown replace 5amp fuse no pole number available
Outage | J.E.26.08.31663 | C001895860 | Edward Royal | KSAS | Completed | Load_242532 | Cane River - 610 | 2026-08-21 01:15 | 2026-08-21 01:15 | 2026-08-21 02:36 | 2026-08-21 02:37 | 2026-08-21 02:36 | 2026-08-21 03:26 | 2026-08-21 03:27 | 2026-08-21 03:27 | BrokenWire |  | Fair | No | Premises found ok when arrived at location no broken wire or broken pole seen area is with power
Outage | J.E.26.08.31799 | C001895945 | Swon Miller | St.James | Completed | Load_253635 | Queens Drive - 310 | 2026-08-21 06:58 | 2026-08-21 06:59 | 2026-08-21 09:34 | 2026-08-21 09:35 | 2026-08-21 09:35 | 2026-08-11 09:40 | 2026-08-21 09:40 | 2026-08-21 09:40 |  |  | Fair | No | Call related to previous
Outage | J.E.26.08.31766 | C001895957 | Derrick Grubb | St.Thomas | Completed | Load_258338 | Good Year - 210 | 2026-08-21 07:10 | 2026-08-21 07:21 | 2026-08-21 07:49 | 2026-08-21 07:49 | 2026-08-21 07:49 | 2026-08-21 07:49 | 2026-08-21 07:50 | 2026-08-21 07:50 |  |  | Fair | No | Premises found ok, customer was contacted by cellphone
Outage | J.E.26.08.31790 | C001895956 | Derrick Grubb | St.Thomas | Completed | Load_350062 | Lysson - 410 | 2026-08-21 07:10 | 2026-08-21 07:21 | 2026-08-21 07:55 | 2026-08-21 08:07 | 2026-08-21 08:06 | 2026-08-21 08:07 | 2026-08-21 08:07 | 2026-08-21 08:07 |  |  | Fair | No | Premises found ok customer was contacted by cellphone
Outage | J.E.26.08.31793 | C001895955 | Derrick Grubb | St.Thomas | Completed | Load_240338 | Lysson - 410 | 2026-08-21 07:10 | 2026-08-21 07:21 | 2026-08-21 07:53 | 2026-08-21 07:54 | 2026-08-21 07:53 | 2026-08-21 07:54 | 2026-08-21 07:54 | 2026-08-21 07:54 |  |  | Fair | No | Premises found ok, customer was contacted by cellphone
Outage | J.E.26.08.31800 | C001895954 | Derrick Grubb | St.Thomas | Completed | Load_270078 | Lysson - 410 | 2026-08-21 07:10 | 2026-08-21 07:21 | 2026-08-21 09:10 | 2026-08-21 09:11 | 2026-08-21 10:45 | 2026-08-21 11:44 | 2026-08-21 11:44 | 2026-08-21 11:44 | BrokenWire |  | Fair | No | Customer pothead wires are damaged, service was disconnected, customer advised to make repairs
Outage | J.E.26.08.31828 | C001895953 | Rusean Allen | KSAS | Completed | Load_238206 | Cane River - 410 | 2026-08-21 07:10 | 2026-08-21 07:23 | 2026-08-21 11:13 | 2026-08-21 11:13 | 2026-08-21 11:19 | 2026-08-21 11:43 | 2026-08-21 11:43 | 2026-08-21 11:43 |  |  | Fair | No | 1x 20amp fuse found 1x 20amp replaced.
Outage | J.E.26.08.31871 | C001895951 | Rusean Allen | KSAS | Completed | Load_257291 | Rockfort - 210 | 2026-08-21 07:10 | 2026-08-21 07:23 | 2026-08-21 11:52 | 2026-08-21 11:56 | 2026-08-21 12:04 | 2026-08-21 12:05 | 2026-08-21 12:06 | 2026-08-21 12:06 | Fire |  | Fair | No | Secondary bushing needs to be done, refer bushing team
Outage | J.E.26.08.31878 | C001895959 | Rusean Allen | KSAS | Completed | Load_1002929 | Hunts Bay - 810 | 2026-08-21 07:23 | 2026-08-21 07:26 | 2026-08-21 09:21 | 2026-08-21 09:21 | 2026-08-21 10:30 | 2026-08-21 10:32 | 2026-08-21 10:32 | 2026-08-21 10:32 | BrokenWire |  | Fair | No | Excessive amount of illegal connections needs to be removed before any repairs can be done, refer to RPD
Outage | J.E.26.08.31784 | C001895961 | Richard Samuda | Manchester | Completed | Load_250578 | Spur Tree - 310 | 2026-08-21 07:24 | 2026-08-21 07:25 | 2026-08-21 07:49 | 2026-08-21 08:01 | 2026-08-21 08:26 | 2026-08-21 09:13 | 2026-08-21 09:13 | 2026-08-21 09:13 | Fire |  | Fair | No | Found chip saver down patrol line found three span of primary line down tree cut on line causing insulator to break out of pole top about 70 customers affected refer call to maintenance
Outage | J.E.26.08.31845 | C001895962 | Richard Samuda | Manchester | Completed | Load_295434 | Spur Tree - 310 | 2026-08-21 07:24 | 2026-08-21 07:25 | 2026-08-21 12:46 | 2026-08-21 12:47 | 2026-08-21 12:48 | 2026-08-21 12:49 | 2026-08-21 12:50 | 2026-08-21 12:50 | BrokenWire |  | Fair | No | Call is associated with broken line at broken hurst and other crew currently working on the line
Outage | J.E.26.08.31854 | C001895964 | Richard Samuda | Manchester | Completed | Load_253176 | Spur Tree - 310 | 2026-08-21 07:24 | 2026-08-21 07:25 | 2026-08-21 12:50 | 2026-08-21 12:50 | 2026-08-21 12:50 | 2026-08-21 12:52 | 2026-08-21 12:52 | 2026-08-21 12:52 | BrokenWire |  | Fair | No | Call is associated with broken line at broken hurst and other crew currently working on line
Outage | J.E.26.08.31857 | C001895963 | Richard Samuda | Manchester | Completed | Load_254529 | Spur Tree - 310 | 2026-08-21 07:24 | 2026-08-21 07:25 | 2026-08-21 12:53 | 2026-08-21 12:53 | 2026-08-21 12:53 | 2026-08-21 12:57 | 2026-08-21 18:35 | 2026-08-21 18:35 |  |  | Fair | No | Other crew on call
Non-Outage | J.E.26.08.00054 | C001895966 | Elvis Trowers |  | Completed |  |  | 2026-08-21 07:27 | 2026-08-21 07:59 | 2026-08-21 08:50 | 2026-08-21 08:51 | 2026-08-21 09:35 | 2026-08-21 09:35 | 2026-08-21 09:37 | 2026-08-21 09:37 | LowHangingWires |  | Fair | No | Retention primary neutral broken in motor vehicle accident. Using two 1- bolt clamps and 4ft #2AA conductor. Low hanging wire on the ground belongs to telephone company.
Non-Outage | J.E.26.08.30929 | C001895968 | Odeanie Davis | KSAS | Completed | Load_244313 | Rockfort - 210 | 2026-08-21 07:29 | 2026-08-21 07:46 | 2026-08-21 10:26 | 2026-08-21 10:26 | 2026-08-21 10:26 | 2026-08-21 10:57 | 2026-08-21 10:57 | 2026-08-21 10:57 |  |  | Fair | No | 117v/123v at arrival, open neutral at secondary corrected, 2 one bolt clamps, 121v/120v & 241v after correction
Non-Outage | J.E.26.08.31142 | C001895967 | Milton Charlton |  | Completed |  |  | 2026-08-21 07:29 | 2026-08-21 08:13 | 2026-08-21 08:49 | 2026-08-21 08:49 | 2026-08-21 10:08 | 2026-08-21 10:05 | 2026-08-21 10:18 | 2026-08-21 10:18 | Fire |  | Fair | No | Found okay upon arrival. No fire seen on any JPS pole on Liguanea Avenue.JPS maintenance crew seen at 30ft wooden pole broken in motor vehicle accident at the corner of Paddington Terrace and Liguanea Avenue.
Outage | J.E.26.08.30986 | C001895970 | Richard Watson | St.Elizabeth | Completed | Load_239118 | Maggotty - 110 | 2026-08-21 07:29 | 2026-08-21 07:31 | 2026-08-21 09:00 | 2026-08-21 09:01 | 2026-08-21 09:59 | 2026-08-21 13:15 | 2026-08-21 13:17 | 2026-08-21 13:17 |  |  | Fair | No | Replace blown 10amp junction fuse twice no pole#, after completing patrol, disconnect and isolate multiple suspected lightning arresters, supply restored to affected customers.
Non-Outage | J.E.26.08.29175 | C001895972 | Andre Smith | KSAS | Completed | Load_413076 | Up Park Camp - 310 | 2026-08-21 07:30 | 2026-08-21 07:36 | 2026-08-21 08:04 | 2026-08-21 08:04 | 2026-08-21 09:34 | 2026-08-21 10:09 | 2026-08-21 10:09 | 2026-08-21 10:09 |  |  | Fair | No | Premises found okay feeder voltage restored to normal
Non-Outage | J.E.26.08.30190 | C001895974 | Odeanie Davis | KSAS | Completed | Load_254610 | Cane River - 610 | 2026-08-21 07:32 | 2026-08-21 08:13 | 2026-08-21 08:53 | 2026-08-21 10:00 | 2026-08-21 10:00 | 2026-08-21 10:15 | 2026-08-21 10:00 | 2026-08-21 10:00 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.28344 | C001895980 | Rusean Allen | KSAS | Completed | Load_239591 | Cane River - 610 | 2026-08-21 07:33 | 2026-08-21 07:41 | 2026-08-21 10:58 | 2026-08-21 10:58 | 2026-08-21 11:10 | 2026-08-21 11:12 | 2026-08-21 11:12 | 2026-08-21 11:12 |  |  | Fair | No | Found okay
Non-Outage | J.E.26.08.29438 | C001895976 | Milton Charlton |  | Completed |  |  | 2026-08-21 07:33 | 2026-08-21 08:14 | 2026-08-21 10:20 | 2026-08-21 10:20 | 2026-08-21 13:18 | 2026-08-21 11:40 | 2026-08-21 13:21 | 2026-08-21 13:21 | LowHangingWires |  | Fair | No | Low hanging wire belongs to cable company.
Outage | J.E.26.08.31779 | C001895982 | Richard Grant | St.Catherine | Completed | Load_269763 | New Michelton - 210 | 2026-08-21 07:35 | 2026-08-21 07:42 | 2026-08-21 08:17 | 2026-08-21 08:18 | 2026-08-21 09:45 | 2026-08-21 10:58 | 2026-08-21 10:58 | 2026-08-21 10:58 |  |  | Fair | No | 10amps fuse found blown for 100kva transformer. No visible cause seen after patrol conducted. 10amps fuse replaced with same size fuse and supply restored. Area left okay.
Outage | J.E.26.08.31826 | C001895983 | Roxroy Needham | St.Ann | Completed | Load_246921 | Cardiff Hall - 310 | 2026-08-21 07:36 | 2026-08-21 07:37 | 2026-08-21 09:21 | 2026-08-21 09:22 | 2026-08-21 10:36 | 2026-08-21 12:41 | 2026-08-21 12:54 | 2026-08-21 12:54 |  |  | Fair | No | Cut tree from line splice and retention 5 spans of secondary phase and neutral use 300 ft of No.2 aa conductor, 4 splicing sleeve and 10- 1bolt clamps also retention 4 triplex wire and replace 1- 3 amp fuse for 25 KVA transformer
Outage | J.E.26.08.31311 | C001895984 | Javid Vernon | Westmoreland | Completed | Load_292088 | Paradise - 210 | 2026-08-21 07:37 | 2026-08-21 07:39 | 2026-08-21 08:44 | 2026-08-21 08:45 | 2026-08-21 09:32 | 2026-08-21 09:42 | 2026-08-21 09:42 | 2026-08-21 09:42 |  |  | Fair | No | Customer got disconnected for none payment
Outage | J.E.26.08.31883 | C001895985 | Javid Vernon | Westmoreland | Completed | Load_293106 | Paradise - 110 | 2026-08-21 07:37 | 2026-08-21 07:39 | 2026-08-21 07:47 | 2026-08-21 07:48 | 2026-08-21 08:13 | 2026-08-21 08:43 | 2026-08-21 08:43 | 2026-08-21 08:43 |  |  | Fair | No | Customer got disconnected for none payment voltage left at premises 115/115/230
Non-Outage | J.E.26.08.06354 | C001895986 | Odeanie Davis | KSAS | Completed | Load_268072 | Rockfort - 410 | 2026-08-21 07:41 | 2026-08-21 07:43 | 2026-08-21 08:50 | 2026-08-21 09:04 | 2026-08-21 09:04 | 2026-08-21 09:04 | 2026-08-21 09:10 | 2026-08-21 09:10 |  |  | Fair | No | 179v/69v at arrival, open neutral on secondary line from transformer corrected, 1 one bolt clamp, 113v/117v & 231v in meter socket after correction
Non-Outage | J.E.26.08.07179 | C001895988 | Odeanie Davis | KSAS | Completed | Load_239499 | Rockfort - 410 | 2026-08-21 07:42 | 2026-08-21 07:43 | 2026-08-21 10:16 | 2026-08-21 13:34 | 2026-08-21 13:34 | 2026-08-21 13:38 | 2026-08-21 13:35 | 2026-08-21 13:35 |  |  | Fair | No
Non-Outage | J.E.26.08.12156 | C001895987 | Odeanie Davis | KSAS | Completed | Load_268072 | Rockfort - 410 | 2026-08-21 07:42 | 2026-08-21 07:43 | 2026-08-21 08:50 | 2026-08-21 09:10 | 2026-08-21 09:10 | 2026-08-21 09:23 | 2026-08-21 09:11 | 2026-08-21 09:11 |  |  | Fair | No | 179v/69v at arrival, open neutral on secondary line from transformer corrected, 1 one bolt clamp, 113v/117v & 231v in meter socket after correction
Outage | J.E.26.08.31672 | C001896011 | Cliton Henry | St.Mary | Completed | Load_264995 | Oracabessa - 210 | 2026-08-21 07:46 | 2026-08-21 07:47 | 2026-08-21 09:39 | 2026-08-21 09:39 | 2026-08-21 09:39 | 2026-08-21 09:40 | 2026-08-21 09:40 | 2026-08-21 09:40 |  |  | Fair | No | Supply restored, related to outage 31743
Outage | J.E.26.08.31675 | C001896015 | Cliton Henry | St.Mary | Completed | Load_351191 | Oracabessa - 210 | 2026-08-21 07:46 | 2026-08-21 07:47 | 2026-08-21 09:35 | 2026-08-21 09:36 | 2026-08-21 09:35 | 2026-08-21 09:36 | 2026-08-21 09:36 | 2026-08-21 09:36 |  |  | Fair | No | Supply restored, related to outage #31743
Outage | J.E.26.08.31743 | C001896007 | Cliton Henry | St.Mary | Completed | Load_265841 | Oracabessa - 210 | 2026-08-21 07:46 | 2026-08-21 07:47 | 2026-08-21 08:45 | 2026-08-21 08:45 | 2026-08-21 09:06 | 2026-08-21 09:28 | 2026-08-21 09:30 | 2026-08-21 09:30 |  |  | Fair | No | A blown 30 amp junction fuse found at Fernandez Garden at pole #0013485 due to a burnt fuse holder. Supply restored using 1 fuse holder and a 30 amp fuse.
Outage | J.E.26.08.31777 | C001896008 | Wan Carlos Scarlett | Portmore | Completed | Load_257194 | Naggo Head - 510 | 2026-08-21 07:46 | 2026-08-21 07:47 | 2026-08-21 08:25 | 2026-08-21 08:26 | 2026-08-21 09:44 | 2026-08-21 10:02 | 2026-08-21 10:03 | 2026-08-21 10:03 |  |  | Fair | No | Found customer 3 wire service at pothead with 1 of the phase corroded use 1 Penn union at pothead reading 115 115 230
Outage | J.E.26.08.31817 | C001896006 | Wan Carlos Scarlett | Portmore | Completed | Load_239324 | Naggo Head - 610 | 2026-08-21 07:46 | 2026-08-21 07:47 | 2026-08-21 10:45 | 2026-08-21 10:46 | 2026-08-21 11:29 | 2026-08-21 11:45 | 2026-08-21 11:47 | 2026-08-21 11:47 |  |  | Fair | No | Found customer 2 wire service at pothead with neutral and phase corroded use 2 Penn union at pothead reading 116
Outage | J.E.26.08.31625 | C001896018 | Neville Spencer | Clarendon | Completed | Load_249472 | May Pen - 110 | 2026-08-21 07:47 | 2026-08-21 07:47 | 2026-08-21 11:10 | 2026-08-21 11:11 | 2026-08-21 11:10 | 2026-08-21 11:11 | 2026-08-21 11:12 | 2026-08-21 11:12 |  |  | Fair | No | Renew blown 15 amp j/ fuse supply restored.
Outage | J.E.26.08.31626 | C001896016 | Neville Spencer | Clarendon | Completed | Load_249472 | May Pen - 110 | 2026-08-21 07:47 | 2026-08-21 07:47 | 2026-08-21 07:58 | 2026-08-21 07:58 | 2026-08-21 10:43 | 2026-08-21 11:08 | 2026-08-21 11:10 | 2026-08-21 11:10 |  |  | Fair | No | Renew blown 15 amp j/ fuse supply restored.
Outage | J.E.26.08.31627 | C001896017 | Neville Spencer | Clarendon | Completed | Load_249472 | May Pen - 110 | 2026-08-21 07:47 | 2026-08-21 07:47 | 2026-08-21 11:12 | 2026-08-21 11:12 | 2026-08-21 11:12 | 2026-08-21 11:12 | 2026-08-21 11:13 | 2026-08-21 11:13 |  |  | EarthMovement | No | Renew blown 15 amp j/ fuse supply restored.
Non-Outage | J.E.26.08.30672 | C001896024 | Fredrick Hamilton | KSAN | Completed | Load_243399 | Hope - 410 | 2026-08-21 07:49 | 2026-08-21 07:55 | 2026-08-21 08:11 | 2026-08-21 08:11 | 2026-08-21 08:11 | 2026-08-21 08:12 | 2026-08-21 08:12 | 2026-08-21 08:12 |  |  | Fair | No | Please assign to emergency
Non-Outage | J.E.26.08.31535 | C001896023 | Rochaine Hussey | KSAN | Completed | Load_248558 | Constant Spring - 410 | 2026-08-21 07:49 | 2026-08-21 08:00 | 2026-08-21 09:29 | 2026-08-21 10:20 | 2026-08-21 10:31 | 2026-08-21 12:00 | 2026-08-21 12:01 | 2026-08-21 12:01 |  |  | Fair | No | Pothead was corroded Pothead was cleaned upIssue resolved 121/120/242v
Outage | J.E.26.08.31881 | C001896021 | Collin Robinson | Portland | Completed | Load_240223 | Port Antonio - 410 | 2026-08-21 07:49 | 2026-08-21 07:49 | 2026-08-21 08:05 | 2026-08-21 08:05 | 2026-08-21 08:15 | 2026-08-21 08:17 | 2026-08-21 08:17 | 2026-08-21 08:17 |  |  | Fair | No | Unable locate customer
Outage | J.E.26.08.31887 | C001896022 | Collin Robinson | Portland | Completed | Load_256253 | Port Antonio - 310 | 2026-08-21 07:49 | 2026-08-21 07:49 | 2026-08-21 12:48 | 2026-08-21 12:48 | 2026-08-21 13:44 | 2026-08-21 13:45 | 2026-08-21 13:45 | 2026-08-21 13:45 |  |  | Fair | No | Information received from customer that issue was resolved
Outage | J.E.26.08.31419 | C001896026 | Hartley Chin | St.Catherine | Completed | Load_263189 | Rhodens Pen - 310 | 2026-08-21 07:50 | 2026-08-21 07:52 | 2026-08-21 08:11 | 2026-08-21 09:57 | 2026-08-21 10:58 | 2026-08-21 11:33 | 2026-08-21 11:34 | 2026-08-21 11:34 |  |  | SevereWind | No | Found blown 3 amp fuse on 25 KVA transformer @ pole # 0113215 line patrolled and found oaky , transformer refused…
Outage | J.E.26.08.31582 | C001896025 | Hartley Chin | Clarendon | Completed | Load_254560 | Parnassus - 310 | 2026-08-21 07:50 | 2026-08-21 07:52 | 2026-08-21 08:11 | 2026-08-21 09:53 | 2026-08-21 09:53 | 2026-08-21 09:53 | 2026-08-21 09:57 | 2026-08-21 09:57 |  |  | SevereWind | No | Ref to field service!!! Customer meter is burnt .. customer has no supply and is requesting an urgent meter change …customer meter # 2529651 …
Outage | J.E.26.08.31589 | C001896027 | Romeo Brissett | St.James | Completed | Load_253292 | Bogue - 610 | 2026-08-21 07:50 | 2026-08-21 07:51 | 2026-08-21 10:43 | 2026-08-21 10:43 | 2026-08-21 11:06 | 2026-08-21 11:24 | 2026-08-21 11:40 | 2026-08-21 11:40 |  |  | Fair | No | Removed vegetation and replaced (1)25KVA transformer fuse. Used (1)2amps fuse.
Outage | J.E.26.08.31830 | C001896028 | Evan Spaulding | St.Mary | Completed | Load_240846 | Highgate -110 | 2026-08-21 07:52 | 2026-08-21 07:54 | 2026-08-21 08:18 | 2026-08-21 08:43 | 2026-08-21 09:25 | 2026-08-21 10:24 | 2026-08-21 10:25 | 2026-08-21 10:25 |  | Y | Fair | No | Cut bamboo from primary line and replace 1-30 amps junction fuse at pole number 0010509.also line section needs bushing.
Outage | J.E.26.08.31836 | C001896029 | Richard Nicholas | St.Catherine | Completed | Load_573724 | Rhodens Pen - 310 | 2026-08-21 07:52 | 2026-08-21 15:54 | 2026-08-21 16:01 | 2026-08-21 16:02 | 2026-08-21 17:25 | 2026-08-21 17:44 | 2026-08-21 17:47 | 2026-08-21 17:47 | Fire |  | Fair | No | Area found ok,broken telephone and cable pole seen at the premises with private twisted service wire that is supplying some private street light that they install on some the telephone poles however Mr.andrew white was advised during a telephone conversation.
Non-Outage | J.E.26.08.31387 | C001896033 | Elvis Trowers | KSAN | Completed | Load_241064 | Washington Blvd - 510 | 2026-08-21 07:53 | 2026-08-21 08:01 | 2026-08-21 09:37 | 2026-08-21 10:03 | 2026-08-21 10:03 | 2026-08-21 10:05 | 2026-08-21 10:10 | 2026-08-21 10:10 |  |  | Fair | No | Customer getting low supply form J.P.S main as a result of a lot of illegal connections. Readings at pole 102-98-202 volts. Refer to R.P.D.
Outage | J.E.26.08.31896 | C001896031 | Raymond Lewis | St.Ann | Completed | Load_238498 | Cardiff Hall - 310 | 2026-08-21 07:53 | 2026-08-21 15:07 | 2026-08-21 17:51 | 2026-08-21 17:55 | 2026-08-21 19:03 | 2026-08-21 19:26 | 2026-08-21 19:27 | 2026-08-21 19:27 |  |  | Fair | No | Reclose x former 25&50 kva
Outage | J.E.26.08.31914 | C001896030 | Roxroy Needham | St.Ann | Completed | Load_261488 | Cardiff Hall - 310 | 2026-08-21 07:53 | 2026-08-21 07:53 | 2026-08-21 12:54 | 2026-08-21 12:55 | 2026-08-21 12:54 | 2026-08-21 12:55 | 2026-08-21 12:55 | 2026-08-21 12:55 |  |  | Fair | No | Cut tree from line splice and retention 5 spans of secondary phase and neutral use 300 ft of No.2 aa conductor, 4 splicing sleeve and 10- 1bolt clamps also retention 4 triplex wire and replace 1- 3 amp fuse for 25 KVA transformer
Outage | J.E.26.08.31448 | C001896034 | Neville Spencer | Clarendon | Completed | Load_579452 | May Pen - 110 | 2026-08-21 07:55 | 2026-08-21 07:56 | 2026-08-21 11:14 | 2026-08-21 11:14 | 2026-08-21 12:17 | 2026-08-21 13:12 | 2026-08-21 13:18 | 2026-08-21 13:18 |  |  | Fair | No | Open 25 kva xmfr at pole #01016162 repair burnt up secondary phase drop lead used 7 ft pvc copper 2, clamps supply restored.
Outage | J.E.26.08.31624 | C001896036 | Radcliffe Coleman | St.Catherine | Completed | Load_268179 | Tredegar - 310 | 2026-08-21 07:57 | 2026-08-21 07:59 | 2026-08-21 08:44 | 2026-08-21 14:06 | 2026-08-21 14:05 | 2026-08-21 14:07 | 2026-08-21 14:07 | 2026-08-21 14:07 |  |  | Fair | No | Unable to locate customer due to inadequate direction. The telephone number provided is not valid.
Non-Outage | J.E.26.08.03136 | C001896039 | Rusean Allen |  | Completed |  |  | 2026-08-21 07:59 | 2026-08-21 08:11 | 2026-08-21 11:43 | 2026-08-21 11:44 | 2026-08-21 11:48 | 2026-08-21 11:49 | 2026-08-21 11:49 | 2026-08-21 11:49 | BrokenPole |  | Fair | No | Found okay
Non-Outage | J.E.26.08.31024 | C001896038 | Evan Spaulding |  | Completed |  |  | 2026-08-21 07:59 | 2026-08-21 08:00 | 2026-08-21 08:40 | 2026-08-21 08:41 | 2026-08-21 08:41 | 2026-08-21 08:41 | 2026-08-21 08:42 | 2026-08-21 08:42 | BrokenWire |  | Fair | No | Patrol farmers heights no tree on wire seen.
Outage | J.E.26.08.31811 | C001896037 | Oshane Warren | Westmoreland | Completed | Load_292071 | Paradise - 310 | 2026-08-21 07:59 | 2026-08-21 08:00 | 2026-08-21 13:22 | 2026-08-21 13:23 | 2026-08-21 13:23 | 2026-08-21 13:28 | 2026-08-21 13:35 | 2026-08-21 13:35 |  |  | Fair | No | Disconnect defective lighting arrester from 25kva transformer and replace 2amp 25kva transformer fuse on 15 amp junction fuse
Outage | J.E.26.08.31401 | C001896040 | Raheem Ricketts | St.Elizabeth | Completed | Load_248974 | Maggotty - 110 | 2026-08-21 08:02 | 2026-08-21 08:03 | 2026-08-21 08:08 | 2026-08-21 10:37 | 2026-08-21 12:11 | 2026-08-21 13:01 | 2026-08-21 13:10 | 2026-08-21 13:10 |  |  | Fair | No | Check and found one 15 ,amp junction fuse blown an two pole span of secondary neutral down caused by tree cut an remove tree from line then splice an retention secondary neutral using 80ft of conductor 2#2, preform 6clamps
Non-Outage | J.E.26.08.05643 | C001896041 | Christopher Edwards | KSAN | Completed | Load_253684 | Constant Spring - 210 | 2026-08-21 08:05 | 2026-08-21 08:11 | 2026-08-21 09:03 | 2026-08-21 09:55 | 2026-08-21 09:55 | 2026-08-21 09:09 | 2026-08-21 10:34 | 2026-08-21 10:34 |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Outage | J.E.26.08.30917 | C001896043 | Edward Royal | KSAN | Completed | Load_264066 | West Kings House - 410 | 2026-08-21 08:06 | 2026-08-21 08:07 | 2026-08-21 11:25 | 2026-08-21 11:26 | 2026-08-21 11:25 | 2026-08-21 12:48 | 2026-08-21 12:49 | 2026-08-21 12:49 |  |  | Fair | No | Spliced and reconnected secondary phase using 40ft 4north tripe x cable 3 ampack
Outage | J.E.26.08.31441 | C001896044 | Raheem Ricketts | St.Elizabeth | Completed | Load_251753 | Maggotty - 110 | 2026-08-21 08:08 | 2026-08-21 08:09 | 2026-08-21 08:50 | 2026-08-21 08:51 | 2026-08-21 10:20 | 2026-08-21 10:36 | 2026-08-21 10:36 | 2026-08-21 10:36 |  |  | Fair | No | Check and found 15am junction fuse blown refuse junction using one 15 amp fuse
Non-Outage | J.E.26.08.27904 | C001896049 | Error Coore | Manchester | Completed | Load_255680 | Spur Tree - 310 | 2026-08-21 08:15 | 2026-08-21 08:16 | 2026-08-21 15:48 | 2026-08-21 15:49 | 2026-08-21 16:48 | 2026-08-21 16:52 | 2026-08-21 16:53 | 2026-08-21 16:53 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.08.27963 | C001896052 | Error Coore | Manchester | Completed | Load_238520 | Spur Tree - 310 | 2026-08-21 08:15 | 2026-08-21 08:16 | 2026-08-21 10:53 | 2026-08-21 10:53 | 2026-08-21 11:34 | 2026-08-21 12:11 | 2026-08-21 12:13 | 2026-08-21 12:13 |  |  | Fair | No | Premises found locked unable to access meter not getting customer on phone
Non-Outage | J.E.26.08.28534 | C001896053 | Error Coore | Manchester | Completed | Load_244647 | Spur Tree - 310 | 2026-08-21 08:15 | 2026-08-21 08:16 | 2026-08-21 12:13 | 2026-08-21 12:14 | 2026-08-21 13:29 | 2026-08-21 13:47 | 2026-08-21 13:48 | 2026-08-21 13:48 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Outage | J.E.26.08.31934 | C001896054 | Hartley Chin | St.Catherine | Completed | Load_263189 | Rhodens Pen - 310 | 2026-08-21 08:15 | 2026-08-21 08:17 | 2026-08-21 09:42 | 2026-08-21 11:34 | 2026-08-21 11:34 | 2026-08-21 11:34 | 2026-08-21 11:35 | 2026-08-21 11:35 | Fire |  | SevereWind | No | Call related to job # 31419
Outage | J.E.26.08.31919 | C001896059 | Hartley Chin | Clarendon | Completed | Load_259800 | Monymusk - 410 | 2026-08-21 08:16 | 2026-08-21 08:17 | 2026-08-21 11:40 | 2026-08-21 11:41 | 2026-08-21 12:54 | 2026-08-21 13:13 | 2026-08-21 13:20 | 2026-08-21 13:20 |  |  | SevereWind | No | Found okay .. voltage read 112v , 114v ..
Outage | J.E.26.08.31915 | C001896060 | Moses Elliston | St.Catherine | Completed | Load_557147 | Tredegar - 210 | 2026-08-21 08:17 | 2026-08-21 08:18 | 2026-08-21 09:01 | 2026-08-21 09:02 | 2026-08-21 09:01 | 2026-08-21 09:02 | 2026-08-21 09:03 | 2026-08-21 09:03 |  |  | Fair | No | Not located,no answer from cell.
Outage | J.E.26.08.31928 | C001896062 | Evan Spaulding | St.Mary | Completed | Load_251193 | Highgate -110 | 2026-08-21 08:18 | 2026-08-21 08:19 | 2026-08-21 08:43 | 2026-08-21 10:26 | 2026-08-21 10:26 | 2026-08-21 10:26 | 2026-08-21 10:26 | 2026-08-21 10:26 |  |  | Fair | No | Associated call.
Outage | J.E.26.08.31929 | C001896061 | Rusean Allen | KSAS | Completed | Load_242988 | Cane River - 410 | 2026-08-21 08:18 | 2026-08-21 08:30 | 2026-08-21 10:32 | 2026-08-21 10:32 | 2026-08-21 10:57 | 2026-08-21 10:57 | 2026-08-21 10:57 | 2026-08-21 10:57 |  |  | Fair | No | Found okay
Non-Outage | J.E.26.08.21490 | C001896074 | Odaine Johnson | Clarendon | Completed | Load_261816 | Parnassus - 310 | 2026-08-21 08:21 | 2026-08-21 08:24 | 2026-08-21 09:12 | 2026-08-21 12:05 | 2026-08-21 12:07 | 2026-08-21 12:07 | 2026-08-21 12:08 | 2026-08-21 12:08 |  |  | Fair | No | Premises not found multiple efforts made to contact customer but unsuccessful
Non-Outage | J.E.26.08.21752 | C001896073 | Odaine Johnson | Clarendon | Completed | Load_244812 | Parnassus - 310 | 2026-08-21 08:21 | 2026-08-21 08:24 | 2026-08-21 09:12 | 2026-08-21 12:04 | 2026-08-21 12:04 | 2026-08-21 12:05 | 2026-08-21 12:05 | 2026-08-21 12:05 |  |  | Fair | No | Premises not found multiple efforts made to contact customer but unsuccessful
Non-Outage | J.E.26.08.22850 | C001896072 | Odaine Johnson | Clarendon | Completed | Load_257675 | Parnassus - 310 | 2026-08-21 08:21 | 2026-08-21 08:24 | 2026-08-21 09:12 | 2026-08-21 12:00 | 2026-08-21 11:59 | 2026-08-21 12:00 | 2026-08-21 12:00 | 2026-08-21 12:00 |  |  | Fair | No | Premises experiencing low voltage requesting a bucket truck for job
Non-Outage | J.E.26.08.30348 | C001896070 | Odaine Johnson | Clarendon | Completed | Load_252366 | Parnassus - 310 | 2026-08-21 08:21 | 2026-08-21 08:24 | 2026-08-21 09:12 | 2026-08-21 13:00 | 2026-08-21 13:05 | 2026-08-21 13:06 | 2026-08-21 13:07 | 2026-08-21 13:07 |  |  | Fair | No | Premises found okay voltage reading 115/114/230 volts
Outage | J.E.26.08.31881 | C001896063 | Collin Robinson | Portland | Completed | Load_240223 | Port Antonio - 410 | 2026-08-21 08:21 | 2026-08-21 08:21 | 2026-08-21 08:31 | 2026-08-21 08:31 | 2026-08-21 10:23 | 2026-08-21 10:53 | 2026-08-21 10:53 | 2026-08-21 10:53 |  |  | Fair | No | Remove johncrow primary conductor replace 10 amps junction
Non-Outage | J.E.26.07.31997 | C001896077 | Odaine Johnson | Clarendon | Completed | Load_267981 | Parnassus - 310 | 2026-08-21 08:22 | 2026-08-21 08:24 | 2026-08-21 09:11 | 2026-08-21 11:06 | 2026-08-21 11:13 | 2026-08-21 11:13 | 2026-08-21 11:14 | 2026-08-21 11:14 |  |  | Fair | No | Premises not found multiple efforts made to contact customer but was unsuccessful
Non-Outage | J.E.26.07.38361 | C001896079 | Odaine Johnson | Clarendon | Completed | Load_579463 | Parnassus - 310 | 2026-08-21 08:22 | 2026-08-21 08:24 | 2026-08-21 09:11 | 2026-08-21 12:13 | 2026-08-21 12:22 | 2026-08-21 12:22 | 2026-08-21 12:22 | 2026-08-21 12:22 |  |  | Fair | No | Premises found okay customer stated that the issue was resolved
Non-Outage | J.E.26.08.19729 | C001896075 | Odaine Johnson | Clarendon | Completed | Load_1002606 | Parnassus - 310 | 2026-08-21 08:22 | 2026-08-21 08:24 | 2026-08-21 09:11 | 2026-08-21 12:59 | 2026-08-21 12:59 | 2026-08-21 12:59 | 2026-08-21 13:00 | 2026-08-21 13:00 |  |  | Fair | No | Customer stated that they did not make any report
Non-Outage | J.E.26.08.20349 | C001896076 | Odaine Johnson | Clarendon | Completed | Load_1002606 | Parnassus - 310 | 2026-08-21 08:22 | 2026-08-21 08:24 | 2026-08-21 09:11 | 2026-08-21 11:15 | 2026-08-21 11:31 | 2026-08-21 11:51 | 2026-08-21 11:52 | 2026-08-21 11:52 |  |  | Fair | No | Corroded neutral found at pole remade connection using 1 one bolt clamp voltage reading 110/116/227 volts
Outage | J.E.26.08.31842 | C001896078 | Evan Spaulding | St.Mary | Completed | Load_261235 | Highgate -110 | 2026-08-21 08:22 | 2026-08-21 08:23 | 2026-08-21 10:30 | 2026-08-21 10:30 | 2026-08-21 10:30 | 2026-08-21 10:30 | 2026-08-21 10:32 | 2026-08-21 10:32 |  | Y | Fair | No | Cut bamboo from primary line and replace 1-30 amps junction fuse at pole number 0010509,Associated call.
Non-Outage | J.E.26.08.30343 | C001896080 | Odaine Johnson | Clarendon | Completed | Load_264051 | Parnassus - 310 | 2026-08-21 08:24 | 2026-08-21 08:26 | 2026-08-21 09:11 | 2026-08-21 12:08 | 2026-08-21 12:11 | 2026-08-21 12:12 | 2026-08-21 12:12 | 2026-08-21 12:12 |  |  | Fair | No | Multiple efforts made to contact customer but was unsuccessful
Non-Outage | J.E.26.08.29269 | C001896081 | Odaine Johnson | Clarendon | Completed | Load_574466 | Parnassus - 310 | 2026-08-21 08:25 | 2026-08-21 08:26 | 2026-08-21 09:11 | 2026-08-21 11:03 | 2026-08-21 11:05 | 2026-08-21 11:05 | 2026-08-21 11:06 | 2026-08-21 11:06 |  |  | Fair | No | Contacted customer and customer stated that they did not make any report
Non-Outage | J.E.26.08.28636 | C001896094 | Derrick Grubb |  | Completed |  |  | 2026-08-21 08:27 | 2026-08-21 08:30 | 2026-08-21 13:34 | 2026-08-21 13:35 | 2026-08-21 14:24 | 2026-08-21 14:24 | 2026-08-21 14:24 | 2026-08-21 14:24 | Fire |  | Fair | No | Premises not located, number going straight to voicemail
Outage | J.E.26.08.31940 | C001896093 | Omar King | St.Ann | Completed | Load_243240 | Cardiff Hall - 310 | 2026-08-21 08:27 | 2026-08-21 18:56 | 2026-08-21 21:21 | 2026-08-21 21:21 | 2026-08-21 22:46 | 2026-08-21 22:47 | 2026-08-21 22:47 | 2026-08-21 22:47 | TreeContact |  | Fair | No | Unable to find customer call several times no answer directions not sufficient
Non-Outage | J.E.26.06.02195 | C001896095 | Derrick Grubb | St.Thomas | Completed | Load_264837 | Good Year - 110 | 2026-08-21 08:28 | 2026-08-21 08:30 | 2026-08-21 11:44 | 2026-08-21 11:45 | 2026-08-21 11:44 | 2026-08-21 11:44 | 2026-08-21 11:45 | 2026-08-21 11:45 |  |  | Fair | No | Premises found ok, customer was contacted by cellphone
Non-Outage | J.E.26.06.17438 | C001896103 | Orville Lee | St.Catherine | Completed | Load_269729 | Twickenham - 210 | 2026-08-21 08:28 | 2026-08-21 08:30 | 2026-08-21 08:37 | 2026-08-21 08:42 | 2026-08-21 09:37 | 2026-08-21 09:48 | 2026-08-21 09:49 | 2026-08-21 09:49 |  |  | Fair | No | Premises found ok upon arrival Issue was resolved by a technician Voltage116v117v234v
Non-Outage | J.E.26.06.17625 | C001896102 | Orville Lee | St.Catherine | Completed | Load_262854 | Twickenham - 210 | 2026-08-21 08:28 | 2026-08-21 08:30 | 2026-08-21 08:37 | 2026-08-21 09:51 | 2026-08-21 10:00 | 2026-08-21 10:15 | 2026-08-21 10:15 | 2026-08-21 10:15 |  |  | Fair | No | Premise found ok upon arrival Issue was resolved by a technician Voltage 116V117V234V
Non-Outage | J.E.26.06.17765 | C001896101 | Orville Lee | St.Catherine | Completed | Load_238600 | Twickenham - 210 | 2026-08-21 08:28 | 2026-08-21 08:30 | 2026-08-21 08:37 | 2026-08-21 11:06 | 2026-08-21 11:38 | 2026-08-21 11:54 | 2026-08-21 11:54 | 2026-08-21 11:54 |  |  | Fair | No | Premises found ok upon arrival Customer mentioned that they had defective breaker in their distribution panel Voltage115v116v231v
Non-Outage | J.E.26.06.18725 | C001896098 | Orville Lee | St.Catherine | Completed | Load_251412 | Twickenham - 210 | 2026-08-21 08:28 | 2026-08-21 08:30 | 2026-08-21 08:37 | 2026-08-21 12:16 | 2026-08-21 12:41 | 2026-08-21 12:51 | 2026-08-21 12:51 | 2026-08-21 12:51 |  |  | Fair | No | Premises closed upon Customer was advised to makes a report when available
Non-Outage | J.E.26.06.20089 | C001896097 | Orville Lee | St.Catherine | Completed | Load_266603 | Twickenham - 210 | 2026-08-21 08:28 | 2026-08-21 08:30 | 2026-08-21 08:37 | 2026-08-21 13:01 | 2026-08-21 13:29 | 2026-08-21 13:42 | 2026-08-21 13:42 | 2026-08-21 13:42 |  |  | Fair | No | Checks made and found premises okVoltage 117V118V236V
Non-Outage | J.E.26.08.31906 | C001896109 | Cliton Henry |  | Completed |  |  | 2026-08-21 08:29 | 2026-08-21 08:30 | 2026-08-21 09:32 | 2026-08-21 09:32 | 2026-08-21 09:32 | 2026-08-21 09:33 | 2026-08-21 09:33 | 2026-08-21 09:33 |  |  | Fair | No | Supply restored, related to outage #31743
Non-Outage | J.E.26.08.31909 | C001896108 | Cliton Henry |  | Completed |  |  | 2026-08-21 08:29 | 2026-08-21 08:30 | 2026-08-21 11:33 | 2026-08-21 11:34 | 2026-08-21 11:34 | 2026-08-21 11:36 | 2026-08-21 11:36 | 2026-08-21 11:36 |  |  | Fair | No | Unable to locate customer, the customer contact number provided went unanswered after several attempts. This report need proper direction
Non-Outage | J.E.26.08.22967 | C001896124 | Hopeton Henry | St.Thomas | Completed | Load_256235 | Lysson - 410 | 2026-08-21 08:31 | 2026-08-21 08:32 | 2026-08-21 10:07 | 2026-08-21 12:21 | 2026-08-21 12:27 | 2026-08-21 12:56 | 2026-08-21 13:06 | 2026-08-21 13:06 |  |  | Fair | No | Premises not located
Non-Outage | J.E.26.08.25817 | C001896126 | Hopeton Henry | St.Thomas | Completed | Load_577136 | Lysson - 410 | 2026-08-21 08:31 | 2026-08-21 08:32 | 2026-08-21 10:07 | 2026-08-21 14:40 | 2026-08-21 14:39 | 2026-08-21 14:41 | 2026-08-21 14:41 | 2026-08-21 14:41 |  |  | Fair | No | Customer not located, cellphone went unanswered
Non-Outage | J.E.26.08.30234 | C001896123 | Andrae Clarke | Portland | Completed | Load_259997 | Port Antonio - 410 | 2026-08-21 08:31 | 2026-08-21 08:32 | 2026-08-21 09:02 | 2026-08-21 09:16 | 2026-08-21 09:19 | 2026-08-21 09:18 | 2026-08-21 09:21 | 2026-08-21 09:21 |  |  | Fair | No | Repair corroded wire used two one bolt clamp Check voltage 117/112/229
Non-Outage | J.E.26.08.30712 | C001896112 | Hopeton Henry | St.Thomas | Completed | Load_264475 | Good Year - 110 | 2026-08-21 08:31 | 2026-08-21 08:32 | 2026-08-21 10:07 | 2026-08-21 12:19 | 2026-08-21 12:19 | 2026-08-21 12:19 | 2026-08-21 12:20 | 2026-08-21 12:20 |  |  | Fair | No | Bucket truck required, refer to emergency department
Non-Outage | J.E.26.08.30323 | C001896129 | Locksley Allen | St.Mary | Completed | Load_269896 | Oracabessa - 210 | 2026-08-21 08:35 | 2026-08-21 08:35 | 2026-08-21 09:56 | 2026-08-21 11:11 | 2026-08-21 11:10 | 2026-08-21 11:16 | 2026-08-21 11:13 | 2026-08-21 11:13 |  |  | Fair | No | Customer said she paid the bill and everything is okay,so there is no need for us to come to her premises
Outage | J.E.26.08.30668 | C001896130 | Derrick Dawkins | St.James | Completed | Load_301640 | Bogue - 310 | 2026-08-21 08:35 | 2026-08-21 15:45 | 2026-08-22 11:47 | 2026-08-22 11:47 | 2026-08-22 11:47 | 2026-08-22 11:55 | 2026-08-22 11:56 | 2026-08-22 11:56 |  |  | Fair | No | Checked and found ok 115/115=234
Outage | J.E.26.08.30704 | C001896131 | Derrick Dawkins | St.James | Completed | Load_265224 | Bogue - 410 | 2026-08-21 08:35 | 2026-08-22 08:10 | 2026-08-22 11:17 | 2026-08-22 12:54 | 2026-08-22 12:54 | 2026-08-22 12:55 | 2026-08-22 12:56 | 2026-08-22 12:56 |  |  | Fair | No | Calls to customer went unanswered cannot locate
Non-Outage | J.E.26.06.12777 | C001896151 | Royston Montague | St.Catherine | Completed | Load_568284 | New Michelton - 310 | 2026-08-21 08:36 | 2026-08-21 08:38 | 2026-08-21 08:42 | 2026-08-21 10:37 | 2026-08-21 12:06 | 2026-08-21 12:08 | 2026-08-21 12:09 | 2026-08-21 12:09 |  |  | Fair | No | Not getting through to customer. Invalid phone number.
Non-Outage | J.E.26.06.12857 | C001896149 | Royston Montague | St.Catherine | Completed | Load_248469 | New Michelton - 310 | 2026-08-21 08:36 | 2026-08-21 08:38 | 2026-08-21 08:42 | 2026-08-21 09:26 | 2026-08-21 10:35 | 2026-08-21 10:35 | 2026-08-21 10:36 | 2026-08-21 10:36 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.06.21392 | C001896148 | Royston Montague | St.Catherine | Completed | Load_252303 | New Michelton - 310 | 2026-08-21 08:36 | 2026-08-21 08:38 | 2026-08-21 08:42 | 2026-08-21 12:10 | 2026-08-21 13:19 | 2026-08-21 13:21 | 2026-08-21 13:21 | 2026-08-21 13:21 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.07.25440 | C001896146 | Royston Montague | St.Catherine | Completed | Load_268365 | New Michelton - 410 | 2026-08-21 08:36 | 2026-08-21 08:38 | 2026-08-21 08:42 | 2026-08-21 08:57 | 2026-08-21 09:23 | 2026-08-21 09:25 | 2026-08-21 09:25 | 2026-08-21 09:25 |  |  | Fair | No | Customer confirmed she not having this problem anymore. Please update thanks.
Non-Outage | J.E.26.08.20461 | C001896136 | Roxroy Needham | St.Ann | Completed | Load_238745 | Cardiff Hall - 210 | 2026-08-21 08:36 | 2026-08-21 08:36 | 2026-08-21 12:55 | 2026-08-21 12:56 | 2026-08-21 13:56 | 2026-08-21 14:23 | 2026-08-21 14:24 | 2026-08-21 14:24 |  |  | Fair | No | Open a 25 KVA transformer at pole and report service wire used 5 ft of # 6 service wire 3 pg clamp
Outage | J.E.26.08.28018 | C001896135 | Derrick Dawkins | St.James | Completed | Load_240548 | Bogue - 310 | 2026-08-21 08:36 | 2026-08-21 15:45 | 2026-08-22 11:19 | 2026-08-22 11:57 | 2026-08-22 12:38 | 2026-08-22 12:44 | 2026-08-22 12:44 | 2026-08-22 12:44 |  |  | Fair | No | Illegal connection causing banging of secondary wire premises ok
Outage | J.E.26.08.31126 | C001896133 | Derrick Dawkins | St.James | Completed | Load_556782 | Bogue - 310 | 2026-08-21 08:36 | 2026-08-21 15:45 | 2026-08-22 11:01 | 2026-08-22 13:13 | 2026-08-22 13:13 | 2026-08-22 13:16 | 2026-08-22 13:14 | 2026-08-22 13:14 |  |  | Fair | No | Customer without light from the hexing box
Outage | J.E.26.08.31352 | C001896134 | Derrick Dawkins | St.James | Completed | Load_250235 | Bogue - 310 | 2026-08-21 08:36 | 2026-08-21 15:45 | 2026-08-21 18:31 | 2026-08-21 22:03 | 2026-08-21 22:03 | 2026-08-21 21:56 | 2026-08-21 22:04 | 2026-08-21 22:04 |  |  | Fair | No | Found premises ok
Outage | J.E.26.08.31613 | C001896132 | Derrick Dawkins | St.James | Completed | Load_262175 | Bogue - 310 | 2026-08-21 08:36 | 2026-08-21 15:45 | 2026-08-21 18:31 | 2026-08-21 21:22 | 2026-08-21 21:39 | 2026-08-21 21:42 | 2026-08-21 22:03 | 2026-08-21 22:03 |  |  | Fair | No | Found premises ok
Non-Outage | J.E.26.05.16001 | C001896155 | Royston Montague | St.Catherine | Completed | Load_250886 | New Michelton - 310 | 2026-08-21 08:37 | 2026-08-21 08:38 | 2026-08-21 08:42 | 2026-08-21 13:33 | 2026-08-21 15:06 | 2026-08-21 15:06 | 2026-08-21 15:07 | 2026-08-21 15:07 |  |  | Fair | No | Customer confirmed issue resolved. Please update thanks.
Non-Outage | J.E.26.05.16944 | C001896154 | Royston Montague | St.Catherine | Completed | Load_250039 | New Michelton - 310 | 2026-08-21 08:37 | 2026-08-21 08:38 | 2026-08-21 08:42 | 2026-08-21 16:34 | 2026-08-21 16:34 | 2026-08-21 16:34 | 2026-08-21 16:34 | 2026-08-21 16:34 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.06.07905 | C001896152 | Royston Montague | St.Catherine | Completed | Load_257901 | New Michelton - 310 | 2026-08-21 08:37 | 2026-08-21 08:38 | 2026-08-21 08:42 | 2026-08-21 15:09 | 2026-08-21 16:33 | 2026-08-21 16:33 | 2026-08-21 16:33 | 2026-08-21 16:33 |  |  | Fair | No | Multiple calls to customer phone go without answer. GPS coordinate on job not working.
Outage | J.E.26.08.31955 | C001896167 | Andre Smith | KSAS | Completed | Load_261811 | Three Miles - 510 | 2026-08-21 08:41 | 2026-08-21 08:42 | 2026-08-21 10:10 | 2026-08-21 10:10 | 2026-08-21 10:59 | 2026-08-21 13:47 | 2026-08-21 13:48 | 2026-08-21 13:48 |  |  | Fair | No | Replace 120ft 4/0 triplex supply restored cause by illegal connections supply
Non-Outage | J.E.26.08.21812 | C001896184 | Oraine Minto | St.Ann | Completed | Load_269707 | Cardiff Hall - 210 | 2026-08-21 08:54 | 2026-08-21 08:55 | 2026-08-21 10:47 | 2026-08-21 10:48 | 2026-08-21 11:13 | 2026-08-21 11:50 | 2026-08-21 11:51 | 2026-08-21 11:51 |  |  | Fair | No | Power was restored
Non-Outage | J.E.26.08.26611 | C001896183 | Oraine Minto | St.Ann | Completed | Load_248462 | Cardiff Hall - 210 | 2026-08-21 08:54 | 2026-08-21 08:55 | 2026-08-21 17:26 | 2026-08-21 17:26 | 2026-08-21 17:26 | 2026-08-21 17:26 | 2026-08-21 17:29 | 2026-08-21 17:29 |  |  | Fair | No | 100ft #6 change 3 one bolt clamp 234v 117v 118v
Non-Outage | J.E.26.08.30394 | C001896185 | Oraine Minto | St.Ann | Completed | Load_255700 | Cardiff Hall - 310 | 2026-08-21 08:54 | 2026-08-21 08:55 | 2026-08-21 13:14 | 2026-08-21 13:15 | 2026-08-21 13:14 | 2026-08-21 13:16 | 2026-08-21 13:16 | 2026-08-21 13:16 |  |  | Fair | No | 2 one bolt clamp was used 234v 117v 117v
Non-Outage | J.E.26.08.31082 | C001896182 | Oraine Minto | St.Ann | Completed | Load_256510 | Cardiff Hall - 210 | 2026-08-21 08:54 | 2026-08-21 08:55 | 2026-08-21 15:51 | 2026-08-21 15:52 | 2026-08-21 15:52 | 2026-08-21 15:52 | 2026-08-21 15:53 | 2026-08-21 15:53 |  |  | Fair | No | Issue resolved
Outage | J.E.26.08.31983 | C001896200 | Christopher Edwards | KSAN | Completed | Load_243019 | Constant Spring - 410 | 2026-08-21 09:04 | 2026-08-21 09:05 | 2026-08-21 10:34 | 2026-08-21 10:34 | 2026-08-21 10:56 | 2026-08-21 11:26 | 2026-08-21 11:26 | 2026-08-21 11:26 |  |  | Fair | No | Refuse blown junction fuseUsing (1) 10 amps
Non-Outage | J.E.26.08.31979 | C001896208 | Hartley Chin |  | Completed |  |  | 2026-08-21 09:07 | 2026-08-21 09:09 | 2026-08-21 10:23 | 2026-08-21 13:20 | 2026-08-21 14:31 | 2026-08-21 14:53 | 2026-08-21 15:00 | 2026-08-21 15:00 | BrokenPole |  | SevereWind | No | Ref to maintenance!!!! Found rotten 35 ft pole with single phase Primary and 2/0 twisted… pole foot is rotten .need to be changed … note : customer supply is okay …
Outage | J.E.26.08.31784 | C001896229 | Ryan Richards | Manchester | Completed | Load_250578 | Spur Tree - 310 | 2026-08-21 09:18 | 2026-08-21 09:19 | 2026-08-21 11:19 | 2026-08-21 11:19 | 2026-08-21 12:58 | 2026-08-21 15:53 | 2026-08-21 15:54 | 2026-08-21 15:54 | Fire |  | Fair | No | 2 trip tripsavers found trip along the May Day main road line patrol dislodged cv insulator found …removed cv insulator and replaced with a small crossarm and insulators and retention conductor and reclose the tripped Saver…trip saver held successfully line was rechecked all customers are with supply
Non-Outage | J.E.26.08.32001 | C001896230 | Elvis Trowers |  | Completed |  |  | 2026-08-21 09:19 | 2026-08-22 08:01 | 2026-08-22 09:05 | 2026-08-22 09:06 | 2026-08-22 09:29 | 2026-08-22 09:30 | 2026-08-22 09:30 | 2026-08-22 09:30 |  |  | Fair | No | Found okay upon arrival. Customer states matter was resolved.
Outage | J.E.26.08.32034 | C001896254 | Richard Grant | St.Catherine | Completed | Load_265588 | New Michelton - 310 | 2026-08-21 09:46 | 2026-08-21 09:47 | 2026-08-21 12:05 | 2026-08-21 12:05 | 2026-08-21 12:59 | 2026-08-21 13:36 | 2026-08-21 13:36 | 2026-08-21 13:36 | BrokenWire |  | Fair | No | Broken service neutral set at pole. 1 onebolt clamp used to reattach joint. Supply restored and premises left okay
Non-Outage | J.E.26.08.32044 | C001896258 | Elvis Trowers | KSAN | Completed | Load_265878 | Washington Blvd - 410 | 2026-08-21 09:48 | 2026-08-21 09:49 | 2026-08-21 10:57 | 2026-08-21 10:57 | 2026-08-21 11:55 | 2026-08-21 12:15 | 2026-08-21 12:21 | 2026-08-21 12:21 |  |  | Fair | No | Customer apply for 415 volts feed but getting 365 volts. Isolate bank of 3- 100 kva transformer at pole #0215027 and change transformer top from top#3 to #4 . Readings now 233-234-236 & 415-416-418 volts.
Non-Outage | J.E.26.08.27726 | C001896259 | Elvis Trowers | KSAN | Completed | Load_268885 | Washington Blvd - 310 | 2026-08-21 09:49 | 2026-08-21 09:50 | 2026-08-21 10:10 | 2026-08-21 10:11 | 2026-08-21 10:15 | 2026-08-21 10:20 | 2026-08-21 10:19 | 2026-08-21 10:19 |  |  | Fair | No | Premises closed. Nobody won’t be home until 3:00 clock today. States customer.
Non-Outage | J.E.26.08.28286 | C001896264 | Wan Carlos Scarlett | Portmore | Completed | Load_257194 | Naggo Head - 510 | 2026-08-21 09:51 | 2026-08-21 09:54 | 2026-08-21 10:04 | 2026-08-21 10:04 | 2026-08-21 10:39 | 2026-08-21 10:42 | 2026-08-21 10:45 | 2026-08-21 10:45 |  |  | Fair | No | Found customer 3 wire service at pothead with both phase and neutral corroded use 3 Penn union at pothead reading 115 116 231
Outage | J.E.26.08.31935 | C001896273 | Neville Spencer | Clarendon | Completed | Load_568356 | May Pen - 110 | 2026-08-21 09:59 | 2026-08-21 10:51 | 2026-08-21 13:21 | 2026-08-21 13:22 | 2026-08-21 14:21 | 2026-08-21 14:46 | 2026-08-21 14:52 | 2026-08-21 14:52 |  | Y | Fair | No | Open 25 kva xmfr cleared tree from 2/0 twisted secondary. Also splice and retention broken netural and phase conductor used 4 clamps supply restored.
Outage | J.E.26.08.31941 | C001896272 | Richard Grant | St.Catherine | Completed | Load_241379 | New Michelton - 210 | 2026-08-21 09:59 | 2026-08-21 10:50 | 2026-08-21 11:02 | 2026-08-21 11:02 | 2026-08-21 12:03 | 2026-08-21 12:04 | 2026-08-21 12:04 | 2026-08-21 12:04 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.32096 | C001896329 | Derrick Grubb | St.Thomas | Completed | Load_577136 | Lysson - 410 | 2026-08-21 10:35 | 2026-08-21 10:37 | 2026-08-21 13:33 | 2026-08-21 13:33 | 2026-08-21 13:33 | 2026-08-21 13:33 | 2026-08-21 13:34 | 2026-08-21 13:34 |  |  | Fair | No | Premises Not located and several calls to customer went unanswered
Outage | J.E.26.08.32070 | C001896339 | Oshane Warren | Westmoreland | Completed | Load_270152 | Paradise - 310 | 2026-08-21 10:36 | 2026-08-21 10:37 | 2026-08-21 13:35 | 2026-08-21 17:16 | 2026-08-21 17:15 | 2026-08-21 17:22 | 2026-08-21 17:22 | 2026-08-21 17:22 |  |  | Fair | No | Customer was disconnected however customer doesn’t owed any bills meter need to be reconnect
Outage | J.E.26.08.32074 | C001896330 | Derrick Grubb | St.Thomas | Completed | Load_239668 | Good Year - 110 | 2026-08-21 10:36 | 2026-08-21 10:37 | 2026-08-21 11:44 | 2026-08-21 11:46 | 2026-08-21 12:46 | 2026-08-21 12:49 | 2026-08-21 13:33 | 2026-08-21 13:33 |  |  | Fair | No | Patrol and refuse one10 amp junction at Pole number 015848
Outage | J.E.26.08.32088 | C001896340 | Christopher Edwards | KSAN | Completed | Load_246880 | Constant Spring - 210 | 2026-08-21 10:37 | 2026-08-21 10:38 | 2026-08-21 11:26 | 2026-08-21 11:27 | 2026-08-21 12:10 | 2026-08-21 12:38 | 2026-08-21 12:39 | 2026-08-21 12:39 |  |  | Fair | No | Remake burnt phase joint at poleUsing (1) one bolt clamps Voltage:115,116,230v
Outage | J.E.26.08.26950 | C001896349 | Milton Charlton | KSAN | Completed | Load_259174 | Hope - 510 | 2026-08-21 10:41 | 2026-08-21 10:42 | 2026-08-21 13:21 | 2026-08-21 13:22 | 2026-08-21 16:52 | 2026-08-21 17:55 | 2026-08-21 18:03 | 2026-08-21 18:03 | BrokenWire |  | Fair | No | Isolate 25 kva transformer at pole #( no pole #) and retire one span open wire three wire secondary and install 300ft #2 triplex, two #2 preform and eight 1-bolt clamps and reclosed transformer switch
Outage | J.E.26.08.32093 | C001896357 | Radcliffe Coleman | St.Catherine | Completed | Load_569927 | Tredegar - 210 | 2026-08-21 10:49 | 2026-08-21 10:51 | 2026-08-21 11:15 | 2026-08-21 11:22 | 2026-08-21 13:02 | 2026-08-21 13:03 | 2026-08-21 13:03 | 2026-08-21 13:03 |  |  | Fair | No | Premises found okay at the time of visit.
Outage | J.E.26.08.32136 | C001896358 | Radcliffe Coleman | St.Catherine | Completed | Load_239495 | Tredegar - 410 | 2026-08-21 10:49 | 2026-08-21 10:51 | 2026-08-21 13:03 | 2026-08-21 13:04 | 2026-08-21 13:03 | 2026-08-21 13:18 | 2026-08-21 13:18 | 2026-08-21 13:18 |  |  | Fair | No | Location found with two blown junction fuse (50A at pole 587234) at T-off into oasis Plaza. Line section was patrolled and two transformer fuse (10A), which supply a bank of three (3-100kva, meter # 2163890) were found blown. This was a result of wisp growing on the transformer bank. The wisp was removed, the same value fuses found at the junction and transformer was replaced. Location back to normal.
Outage | J.E.26.08.32055 | C001896373 | Collin Robinson | Portland | Completed | Load_269192 | Port Antonio - 310 | 2026-08-21 11:00 | 2026-08-21 11:01 | 2026-08-21 13:55 | 2026-08-21 13:55 | 2026-08-21 14:27 | 2026-08-21 14:32 | 2026-08-21 14:32 | 2026-08-21 14:32 |  |  | Fair | No | Premises found with supply Voltage reading 117v 118v 235v
Outage | J.E.26.08.32091 | C001896374 | Collin Robinson | Portland | Completed | Load_267159 | Port Antonio - 410 | 2026-08-21 11:00 | 2026-08-21 11:01 | 2026-08-21 11:39 | 2026-08-21 11:39 | 2026-08-21 12:42 | 2026-08-21 12:47 | 2026-08-21 12:47 | 2026-08-21 12:47 |  |  | Fair | No | Remove vine from pole and replace 3 amps fuse
Outage | J.E.26.08.32027 | C001896381 | Raheem Ricketts | St.Elizabeth | Completed | Load_264525 | Maggotty - 110 | 2026-08-21 11:06 | 2026-08-21 11:06 | 2026-08-21 13:24 | 2026-08-21 13:34 | 2026-08-21 13:34 | 2026-08-21 13:34 | 2026-08-21 13:34 | 2026-08-21 13:34 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Westmoreland call
Outage | J.E.26.08.32102 | C001896380 | Raheem Ricketts | St.Elizabeth | Completed | Load_248070 | Maggotty - 210 | 2026-08-21 11:06 | 2026-08-21 11:06 | 2026-08-21 13:10 | 2026-08-21 13:11 | 2026-08-21 13:10 | 2026-08-21 13:11 | 2026-08-21 13:12 | 2026-08-21 13:12 | BrokenWire |  | Fair | No | Unable to locate customer cell number went voicemail after several calls
Outage | J.E.26.08.32135 | C001896398 | Evan Spaulding | St.Mary | Completed | Load_238782 | Highgate -110 | 2026-08-21 11:22 | 2026-08-21 11:23 | 2026-08-21 11:27 | 2026-08-21 11:27 | 2026-08-21 11:27 | 2026-08-21 12:12 | 2026-08-21 12:14 | 2026-08-21 12:14 |  |  | Fair | No | Use 5 ft 2/0 PVC copper,1-2/0 to #2 ampact and 2-#2 to #2 ampacts voltage left 119v,119v,238v.
Outage | J.E.26.08.32028 | C001896399 | Horace Malcolm | St.James | Completed | Load_255280 | Queens Drive - 710 | 2026-08-21 11:23 | 2026-08-22 08:02 | 2026-08-22 09:36 | 2026-08-22 09:36 | 2026-08-22 10:02 | 2026-08-22 10:22 | 2026-08-22 10:22 | 2026-08-22 10:22 |  |  | Fair | No | Check and found premises closed unable to locate meter multiple calls to customer unavailable
Outage | J.E.26.08.31884 | C001896400 | Swon Miller | St.James | Completed | Load_266360 | Queens Drive - 810 | 2026-08-21 11:24 | 2026-08-21 11:25 | 2026-08-21 11:58 | 2026-08-21 13:08 | 2026-08-21 13:28 | 2026-08-18 01:49 | 2026-08-21 13:49 | 2026-08-21 13:49 |  |  | Fair | No | Check and found okay voltage 117/117/236 voltage left 117/117/236
Outage | J.E.26.08.31884 | C001896403 | Swon Miller | St.James | Completed | Load_266360 | Queens Drive - 810 | 2026-08-21 11:24 | 2026-08-21 11:25 | 2026-08-21 11:55 | 2026-08-21 13:50 | 2026-08-21 13:50 | 2026-08-25 01:52 | 2026-08-21 13:53 | 2026-08-21 13:53 |  |  | Fair | No | Call related to previous voltage found 117/117/236 voltage left 117/117/236
Outage | J.E.26.08.31926 | C001896402 | Swon Miller | St.James | Completed | Load_252519 | Queens Drive - 710 | 2026-08-21 11:24 | 2026-08-21 11:25 | 2026-08-21 12:45 | 2026-08-21 12:47 | 2026-08-21 12:50 | 2026-08-24 01:07 | 2026-08-21 13:07 | 2026-08-21 13:07 |  |  | Fair | No | Found customer load side in meter socket burnt out and meter defective also the meter pole is leaning at a 70 degree angle advise customer to straighten meter pole and replace meter socket before power supply can be restored voltage found on line side 117/116.5/234
Outage | J.E.26.08.32138 | C001896404 | Dean- Smith | Hanover | Completed | Load_245732 | Orange Bay - 310 | 2026-08-21 11:25 | 2026-08-21 16:06 | 2026-08-21 18:46 | 2026-08-21 18:47 | 2026-08-21 18:46 | 2026-08-21 18:46 | 2026-08-21 19:25 | 2026-08-21 19:25 |  |  | Rains | No | Defective 25kva transformer by the water catchment. Unable tie to another because on both sides of circuit there are burn transformer that already tied out. Please forward to mr andrae Richard maintenance dept to have transformer replace. There are now 3 defective 25kva transformer in a row
Outage | J.E.26.08.32210 | C001896423 | Milton Charlton | KSAN | Completed | Load_252462 | Hope - 510 | 2026-08-21 11:39 | 2026-08-22 07:55 | 2026-08-22 14:38 | 2026-08-22 14:38 | 2026-08-22 17:14 | 2026-08-22 13:25 | 2026-08-22 17:16 | 2026-08-22 17:16 |  |  | Fair | No | Call duplicated.
Outage | J.E.26.08.32229 | C001896430 | Rusean Allen | KSAS | Completed | Load_257838 | Up Park Camp - 510 | 2026-08-21 11:43 | 2026-08-21 11:44 | 2026-08-21 12:06 | 2026-08-21 12:06 | 2026-08-21 12:06 | 2026-08-21 12:08 | 2026-08-21 12:08 | 2026-08-21 12:08 |  |  | Fair | No | Switch top burnt off in main line, refer in-house team.
Outage | J.E.26.08.32241 | C001896458 | Radcliffe Coleman | St.Catherine | Completed | Load_267694 | Tredegar - 310 | 2026-08-21 12:06 | 2026-08-21 12:07 | 2026-08-21 13:18 | 2026-08-21 13:19 | 2026-08-21 13:38 | 2026-08-21 14:05 | 2026-08-21 14:05 | 2026-08-21 14:05 |  |  | Fair | No | Area found with a blown junction fuse (15A) at pole 0076318. Line section was patrolled and no visible fault found. The same value fuse found was replaced, area now back to normal.
Outage | J.E.26.08.32229 | C001896460 | Andre Smith | KSAS | Completed | Load_257838 | Up Park Camp - 510 | 2026-08-21 12:07 | 2026-08-21 12:11 | 2026-08-21 13:48 | 2026-08-21 13:48 | 2026-08-21 15:01 | 2026-08-21 15:22 | 2026-08-21 15:22 | 2026-08-21 15:22 |  |  | Fair | No | Repair burnt switch top supply restored
Non-Outage | J.E.26.08.17610 | C001896474 | Rusean Allen | KSAS | Completed | Load_240320 | Hunts Bay - 210 | 2026-08-21 12:16 | 2026-08-21 12:18 | 2026-08-21 14:05 | 2026-08-21 16:13 | 2026-08-21 18:08 | 2026-08-21 18:17 | 2026-08-21 18:17 | 2026-08-21 18:17 |  |  | Fair | No | Premises found locked
Outage | J.E.26.08.32007 | C001896507 | Raymond Lewis | St.Ann | Completed | Load_255880 | Cardiff Hall - 310 | 2026-08-21 12:45 | 2026-08-21 15:07 | 2026-08-21 17:41 | 2026-08-21 17:42 | 2026-08-21 17:42 | 2026-08-21 17:44 | 2026-08-21 17:44 | 2026-08-21 17:44 |  |  | Fair | No | Clarendon call
Outage | J.E.26.08.32254 | C001896508 | Tyrese Williams | St.Ann | Completed | Load_242320 | Upper White River - 210 | 2026-08-21 12:45 | 2026-08-21 12:47 | 2026-08-21 12:52 | 2026-08-21 13:18 | 2026-08-21 14:13 | 2026-08-21 14:58 | 2026-08-21 15:27 | 2026-08-21 15:27 |  |  | Fair | No | Premises found ok customer has internal problem
Outage | J.E.26.08.32270 | C001896509 | Omar King | St.Ann | Completed | Load_303102 | Ocho Rios - 410 | 2026-08-21 12:46 | 2026-08-21 15:06 | 2026-08-21 19:47 | 2026-08-21 19:47 | 2026-08-21 21:19 | 2026-08-21 21:20 | 2026-08-21 21:21 | 2026-08-21 21:21 |  |  | Fair | No | Hexin meter failed to produce please refer to field service
Outage | J.E.26.08.32207 | C001896521 | Neckell Ormsby | St.Mary | Completed | Load_351007 | Oracabessa - 210 | 2026-08-21 12:47 | 2026-08-21 15:18 | 2026-08-21 15:28 | 2026-08-21 15:35 | 2026-08-21 16:53 | 2026-08-21 17:00 | 2026-08-21 17:00 | 2026-08-21 17:00 | BrokenWire |  | Fair | No | Found supply ok
Non-Outage | J.E.26.08.32282 | C001896523 | Denton Williams |  | Completed |  |  | 2026-08-21 12:48 | 2026-08-21 15:16 | 2026-08-21 16:23 | 2026-08-21 18:17 | 2026-08-21 18:34 | 2026-08-21 19:21 | 2026-08-21 19:30 | 2026-08-21 19:30 | BrokenWire |  | Fair | No | Splice and tension broken secondary neutral caused by tree cutting
Outage | J.E.26.08.32240 | C001896522 | Collin Robinson | Portland | Completed | Load_256253 | Port Antonio - 310 | 2026-08-21 12:48 | 2026-08-21 12:49 | 2026-08-21 13:46 | 2026-08-21 13:47 | 2026-08-21 13:46 | 2026-08-21 13:48 | 2026-08-21 13:49 | 2026-08-21 13:49 |  |  | Fair | No | Information received from customer that supply was restored
Outage | J.E.26.08.32126 | C001896539 | Neckell Ormsby | St.Mary | Completed | Load_252639 | Oracabessa - 110 | 2026-08-21 13:04 | 2026-08-21 15:18 | 2026-08-21 17:02 | 2026-08-21 17:04 | 2026-08-21 17:38 | 2026-08-21 17:40 | 2026-08-21 17:41 | 2026-08-21 17:41 |  |  | Fair | No | Unable to locate customer after several calls however found supply at grants Kennedy learning center
Outage | J.E.26.08.31862 | C001896540 | Neckell Ormsby | St.Mary | Completed | Load_265841 | Oracabessa - 210 | 2026-08-21 13:05 | 2026-08-21 15:18 | 2026-08-21 15:28 | 2026-08-21 17:01 | 2026-08-21 17:01 | 2026-08-21 17:01 | 2026-08-21 17:01 | 2026-08-21 17:01 |  |  | Fair | No | Found supply ok
Outage | J.E.26.08.32132 | C001896548 | Neville Spencer | Clarendon | Completed | Load_579452 | May Pen - 110 | 2026-08-21 13:11 | 2026-08-21 13:12 | 2026-08-21 13:19 | 2026-08-21 13:19 | 2026-08-21 13:19 | 2026-08-21 13:19 | 2026-08-21 13:21 | 2026-08-21 13:21 |  |  | Fair | No | Open 25 kva xmfr at pole # 0106162 repair burnt up burnt up secondary phase drop phase drop lead used 7 ft #2 pvc copper, 2 clamps supply restored.
Outage | J.E.26.08.32238 | C001896550 | Wan Carlos Scarlett | St.Catherine | Completed | Load_258071 | Twickenham - 210 | 2026-08-21 13:12 | 2026-08-21 13:14 | 2026-08-21 13:29 | 2026-08-21 13:29 | 2026-08-21 14:18 | 2026-08-21 14:45 | 2026-08-21 14:45 | 2026-08-21 14:45 |  |  | Fair | No | Customer got connected by escalation department power supply has been restored
Outage | J.E.26.08.32124 | C001896559 | Richard Samuda | Manchester | Completed | Load_252755 | Spur Tree - 310 | 2026-08-21 13:18 | 2026-08-22 07:16 | 2026-08-22 07:28 | 2026-08-22 07:32 | 2026-08-22 07:31 | 2026-08-22 07:32 | 2026-08-22 07:32 | 2026-08-22 07:32 | BrokenWire |  | Fair | No | Found ok power was restored
Non-Outage | J.E.26.08.24085 | C001896560 | Edward Royal | KSAS | Completed | Load_262317 | Greenwich - 310 | 2026-08-21 13:19 | 2026-08-21 13:21 | 2026-08-21 23:41 | 2026-08-21 23:42 | 2026-08-21 23:41 | 2026-08-21 23:42 | 2026-08-21 23:42 | 2026-08-21 23:42 |  |  | Fair | No | When contacted customer by phone customer said that the power was restored
Outage | J.E.26.08.32010 | C001896561 | Neckell Ormsby | St.Ann | Completed | Load_350215 | Upper White River - 110 | 2026-08-21 13:20 | 2026-08-21 15:18 | 2026-08-21 19:15 | 2026-08-21 19:16 | 2026-08-21 20:15 | 2026-08-21 20:39 | 2026-08-21 20:48 | 2026-08-21 20:48 |  |  | Fair | No | Troubleshoot and found customer with internal fault voltage left 117v 116v 233v
Outage | J.E.26.08.32144 | C001896562 | Neckell Ormsby | St.Ann | Completed | Load_242897 | Upper White River - 110 | 2026-08-21 13:20 | 2026-08-21 15:18 | 2026-08-21 15:25 | 2026-08-21 15:26 | 2026-08-21 15:25 | 2026-08-21 15:27 | 2026-08-21 15:27 | 2026-08-21 15:27 |  |  | Fair | No | St Ann call, wrong parish
Non-Outage | J.E.26.08.32206 | C001896577 | Antony Levy | KSAN | Completed | Load_250041 | Constant Spring - 410 | 2026-08-21 13:22 | 2026-08-21 13:25 | 2026-08-21 13:53 | 2026-08-21 13:54 | 2026-08-21 14:10 | 2026-08-21 14:34 | 2026-08-21 14:35 | 2026-08-21 14:35 |  |  | Fair | No | Customer has an internal issue customer advised left a voltage reading of 119 118 238
Non-Outage | J.E.26.08.32243 | C001896576 | Milton Charlton | KSAN | Completed | Load_252462 | Hope - 510 | 2026-08-21 13:22 | 2026-08-22 07:57 | 2026-08-22 12:15 | 2026-08-22 13:14 | 2026-08-22 13:55 | 2026-08-22 13:10 | 2026-08-22 14:37 | 2026-08-22 14:37 |  |  | Fair | No | Unable to locate customer by telephone. Premises closed. Nobody at home.
Outage | J.E.26.08.32181 | C001896584 | Romeo Brissett | St.James | Completed | Load_1001321 | Bogue - 510 | 2026-08-21 13:31 | 2026-08-21 13:32 | 2026-08-21 13:38 | 2026-08-21 13:39 | 2026-08-21 14:26 | 2026-08-21 15:00 | 2026-08-21 15:10 | 2026-08-21 15:10 |  |  | Fair | No | Customer meter was found disconnected, however was reconnected by escalation. V/R 116-116-232
Outage | J.E.26.08.32363 | C001896594 | Dwayne Samuels | Trelawny | Completed | Load_240520 | Greenwood - 210 | 2026-08-21 13:36 | 2026-08-21 16:03 | 2026-08-21 16:22 | 2026-08-21 16:23 | 2026-08-21 17:34 | 2026-08-21 18:16 | 2026-08-21 18:16 | 2026-08-21 18:16 | BrokenWire |  | Fair | No | Customer service wire was damaged and torn down by truck use 6 one bolt clamp and 1 linket and 60ft of number 6 wire at same for repairs voltage left at pothead after repair 116v/119v/234v
Non-Outage | J.E.26.08.32421 | C001896603 | Orville Lee |  | Completed |  |  | 2026-08-21 13:48 | 2026-08-21 13:51 | 2026-08-21 13:57 | 2026-08-21 13:58 | 2026-08-21 14:42 | 2026-08-21 15:50 | 2026-08-21 15:51 | 2026-08-21 15:51 |  |  | Fair | No | Suspected defective transformer Devon Wilkie was informed by Mackoy Legg
Outage | J.E.26.08.32002 | C001896605 | Barnett Brown | Manchester | Completed | Load_293020 | Spur Tree - 310 | 2026-08-21 13:53 | 2026-08-21 16:48 | 2026-08-21 21:11 | 2026-08-21 21:11 | 2026-08-21 22:03 | 2026-08-22 22:50 | 2026-08-22 00:58 | 2026-08-22 00:58 |  |  | Fair | No | Patrol line found nothing, replace blown 10 amp junction fuse
Outage | J.E.26.08.32330 | C001896618 | Raheem Ricketts | St.Elizabeth | Completed | Load_250102 | Maggotty - 210 | 2026-08-21 14:03 | 2026-08-21 14:04 | 2026-08-21 14:30 | 2026-08-21 14:30 | 2026-08-21 14:56 | 2026-08-21 14:57 | 2026-08-21 14:57 | 2026-08-21 14:57 | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Unable to communicate with customer cell number went unanswered after several calls
Outage | J.E.26.08.32448 | C001896625 | Christopher Edwards | KSAN | Completed | Load_262126 | Constant Spring - 210 | 2026-08-21 14:06 | 2026-08-21 14:07 | 2026-08-21 14:21 | 2026-08-21 14:54 | 2026-08-21 15:07 | 2026-08-21 16:22 | 2026-08-21 16:23 | 2026-08-21 16:23 |  |  | Fair | No | Refuse blown junction fuseUsing (1) 40 amps
Outage | J.E.26.08.32453 | C001896633 | Elvis Trowers | KSAS | Completed | Load_267134 | Cane River - 310 | 2026-08-21 14:17 | 2026-08-21 15:54 | 2026-08-21 17:36 | 2026-08-21 17:42 | 2026-08-21 18:13 | 2026-08-21 18:20 | 2026-08-21 18:20 | 2026-08-21 18:20 | BrokenWire |  | Fair | No | Customer service wire #6 triplex neutral broken by falling tree limb. Repaired using two 1- bolt clamps. Readings at pothead and meter socket 114-115-230 volts.
Outage | J.E.26.08.32475 | C001896634 | Stephen Taylor | St.Thomas | Completed | Load_239755 | Good Year - 210 | 2026-08-21 14:17 | 2026-08-21 16:54 | 2026-08-21 19:26 | 2026-08-21 19:27 | 2026-08-21 20:39 | 2026-08-21 20:40 | 2026-08-21 20:41 | 2026-08-21 20:41 |  |  | Fair | No | Clean up single phase and use 3 one bolts clamp
Outage | J.E.26.08.32472 | C001896643 | Denton Williams | Portland | Completed | Load_255641 | Port Antonio - 410 | 2026-08-21 14:30 | 2026-08-21 15:16 | 2026-08-21 19:31 | 2026-08-21 19:31 | 2026-08-21 19:31 | 2026-08-21 19:31 | 2026-08-21 19:32 | 2026-08-21 19:32 |  |  | Fair | No | Splice and tension broken secondary neutral caused by tree cutting
Outage | J.E.26.08.32171 | C001896652 | Neville Spencer | Clarendon | Completed | Load_568357 | May Pen - 110 | 2026-08-21 14:39 | 2026-08-21 14:40 | 2026-08-21 14:52 | 2026-08-21 14:53 | 2026-08-21 14:52 | 2026-08-21 14:52 | 2026-08-21 14:56 | 2026-08-21 14:56 | TreeContact | Y | Fair | No | Open 25 kva xmfr cleared tree from 2/0 twisted secondary ,Also splice and retention broken phase and neutral conductor used 4, clamps supply restored.
Outage | J.E.26.08.32498 | C001896651 | Neville Spencer | Clarendon | Completed | Load_266352 | May Pen - 110 | 2026-08-21 14:39 | 2026-08-21 14:40 | 2026-08-21 14:56 | 2026-08-21 14:57 | 2026-08-21 15:27 | 2026-08-21 15:27 | 2026-08-21 15:57 | 2026-08-21 15:57 |  |  | Fair | No | Renew blown 8 amp j/ fuse supply restored.
Outage | J.E.26.08.32502 | C001896679 | Omar King | St.Ann | Completed | Load_250756 | Roaring River - 410 | 2026-08-21 15:04 | 2026-08-21 15:06 | 2026-08-21 15:50 | 2026-08-21 15:50 | 2026-08-21 16:34 | 2026-08-21 16:37 | 2026-08-21 16:37 | 2026-08-21 16:37 |  |  | Fair | No | Customer as been disconnected
Non-Outage | J.E.26.08.32481 | C001896680 | Roxroy Needham |  | Completed |  |  | 2026-08-21 15:05 | 2026-08-22 07:23 | 2026-08-22 09:51 | 2026-08-22 09:51 | 2026-08-22 11:00 | 2026-08-22 11:02 | 2026-08-22 11:03 | 2026-08-22 11:03 |  |  | Fair | No | Replace a 25 KVA transformer fuse with a 3 amps at pole
Outage | J.E.26.08.32251 | C001896681 | Selvin White | St.Elizabeth | Completed | Load_250909 | Maggotty - 110 | 2026-08-21 15:05 | 2026-08-21 15:17 | 2026-08-21 15:40 | 2026-08-21 15:44 | 2026-08-21 15:44 | 2026-08-21 15:46 | 2026-08-21 15:46 | 2026-08-21 15:46 |  |  | Fair | No | Replace a defective 2 amp fuse for a 25 KVA transformer circuit at the entrance to the Hilltop community at Crawford district. Supply restored to the affected customers.
Outage | J.E.26.08.31329 | C001896689 | Selvin White | St.Elizabeth | Completed | Load_251946 | Maggotty - 110 | 2026-08-21 15:06 | 2026-08-21 15:12 | 2026-08-21 15:16 | 2026-08-21 15:16 | 2026-08-21 15:24 | 2026-08-21 15:39 | 2026-08-21 15:40 | 2026-08-21 15:40 |  |  | Fair | No | Replace a defective 2 amp fuse for a 25 KVA transformer circuit at the entrance to the Hilltop community . Supply restored to the affected customers.
Outage | J.E.26.08.31512 | C001896688 | Raymond Lewis | St.Ann | Completed | Load_269504 | Cardiff Hall - 310 | 2026-08-21 15:06 | 2026-08-21 15:08 | 2026-08-21 16:38 | 2026-08-21 16:39 | 2026-08-21 17:33 | 2026-08-21 17:35 | 2026-08-21 17:36 | 2026-08-21 17:36 |  |  | Fair | No | Customer complained about street light
Outage | J.E.26.08.32517 | C001896687 | Raymond Lewis | St.Ann | Completed | Load_251360 | Cardiff Hall - 310 | 2026-08-21 15:06 | 2026-08-21 15:08 | 2026-08-21 19:30 | 2026-08-21 19:30 | 2026-08-21 20:13 | 2026-08-21 20:14 | 2026-08-21 20:14 | 2026-08-21 20:14 |  |  | Fair | No | Phone not answering
Non-Outage | J.E.26.08.31943 | C001896691 | Omar King |  | Completed |  |  | 2026-08-21 15:07 | 2026-08-21 18:03 | 2026-08-21 18:37 | 2026-08-21 18:38 | 2026-08-21 19:45 | 2026-08-21 19:46 | 2026-08-21 19:47 | 2026-08-21 19:47 | LowHangingWires |  | Fair | No | Customer stantion low not anything can be done at the moment
Outage | J.E.26.08.32509 | C001896698 | Denton Williams | Portland | Completed | Load_1003592 | Port Antonio - 410 | 2026-08-21 15:15 | 2026-08-21 15:17 | 2026-08-21 19:35 | 2026-08-21 19:36 | 2026-08-21 19:35 | 2026-08-21 19:36 | 2026-08-21 19:38 | 2026-08-21 19:38 |  |  | Fair | No | Customer end call when I was trying to get the driving directions
Outage | J.E.26.08.32526 | C001896696 | Denton Williams | Portland | Completed | Load_256253 | Port Antonio - 310 | 2026-08-21 15:15 | 2026-08-21 15:17 | 2026-08-21 15:26 | 2026-08-21 15:27 | 2026-08-21 15:47 | 2026-08-21 16:08 | 2026-08-21 16:13 | 2026-08-21 16:13 |  |  | Fair | No | Hexing customer was disconnected. JPS escalation team was contacted to reconnect customer. Customer confirmed electrical supply has been restored.
Outage | J.E.26.08.32534 | C001896697 | Denton Williams | Portland | Completed | Load_241254 | Port Antonio - 310 | 2026-08-21 15:15 | 2026-08-21 15:17 | 2026-08-21 17:10 | 2026-08-21 17:12 | 2026-08-21 17:24 | 2026-08-21 18:10 | 2026-08-21 18:16 | 2026-08-21 18:16 |  |  | Fair | No | Replace one 8 amp fuse after clean transformer drop leads.
Outage | J.E.26.08.32375 | C001896703 | Neckell Ormsby | St.Mary | Completed | Load_255663 | Blackstonedge - 110 | 2026-08-21 15:17 | 2026-08-21 15:18 | 2026-08-21 21:42 | 2026-08-21 21:42 | 2026-08-21 21:42 | 2026-08-21 21:42 | 2026-08-21 21:59 | 2026-08-21 21:59 |  |  | Fair | No | Found 50 kva transformer fuse blown patrol and found no permanent fault replace 1-5 amp fuse
Outage | J.E.26.08.32293 | C001896710 | Damion Reid | Manchester | Completed | Load_303115 | Kendal - 210 | 2026-08-21 15:21 | 2026-08-21 15:23 | 2026-08-21 20:21 | 2026-08-21 20:21 | 2026-08-21 20:57 | 2026-08-21 21:27 | 2026-08-21 21:28 | 2026-08-21 21:28 |  |  | Fair | No | Remade burnt off neutral at secondary pole for 3 wire service using one 1 bolt clamp
Outage | J.E.26.08.32366 | C001896712 | Kenroy Dale | Manchester | Completed | Load_269019 | Kendal - 210 | 2026-08-21 15:21 | 2026-08-22 07:45 | 2026-08-22 16:04 | 2026-08-22 16:05 | 2026-08-22 17:21 | 2026-08-22 18:02 | 2026-08-22 18:03 | 2026-08-22 18:03 |  |  | Fair | No | Customer have internal problems
Outage | J.E.26.08.32426 | C001896714 | Damion Reid | Manchester | Completed | Load_237646 | Kendal - 210 | 2026-08-21 15:21 | 2026-08-21 15:24 | 2026-08-21 19:49 | 2026-08-21 19:49 | 2026-08-21 19:57 | 2026-08-21 20:18 | 2026-08-21 20:20 | 2026-08-21 20:20 |  |  | Fair | No | Remade corroded phase at secondary pole for 3 wire service using one 1 bolt clamp voltage reading at meter socket phase to neutral 114v-115v across phase 231v
Outage | J.E.26.08.32493 | C001896708 | Eric Williams | KSAS | Completed | Load_240610 | Duhaney - 310 | 2026-08-21 15:21 | 2026-08-21 15:29 | 2026-08-21 15:57 | 2026-08-21 15:58 | 2026-08-21 16:21 | 2026-08-21 16:40 | 2026-08-21 16:42 | 2026-08-21 16:42 |  |  | Fair | No | Customer apply for the wrong meter, found meter connected but that meter not supplying customer premises, meter mix up
Outage | J.E.26.08.32512 | C001896713 | Damion Reid | Manchester | Completed | Load_259311 | Kendal - 210 | 2026-08-21 15:21 | 2026-08-21 15:25 | 2026-08-21 16:17 | 2026-08-21 16:18 | 2026-08-21 17:42 | 2026-08-21 19:07 | 2026-08-21 19:09 | 2026-08-21 19:09 |  |  | Rains | No | Replace 60ft of defective #6 triplex service wire for 3 wire service using 3 pen union and 3 one bolt clamp
Outage | J.E.26.08.32548 | C001896704 | Eric Williams | KSAN | Completed | Load_258921 | Constant Spring - 210 | 2026-08-21 15:21 | 2026-08-21 15:29 | 2026-08-21 20:01 | 2026-08-21 20:02 | 2026-08-21 20:51 | 2026-08-21 21:19 | 2026-08-21 21:20 | 2026-08-21 21:20 | LeaningPole |  | Fair | No | Rotten 35 foot pole, refer to maintenance department
Outage | J.E.26.08.32566 | C001896705 | Eric Williams | KSAN | Completed | Load_241670 | West Kings House - 310 | 2026-08-21 15:21 | 2026-08-21 15:29 | 2026-08-21 16:42 | 2026-08-21 16:42 | 2026-08-21 17:31 | 2026-08-21 17:32 | 2026-08-21 17:32 | 2026-08-21 17:32 | BrokenWire |  | Fair | No | Premises found okay
Non-Outage | J.E.26.08.23171 | C001896721 | Romaine Roberts | St.Mary | Completed | Load_237863 | Highgate - 210 | 2026-08-21 15:24 | 2026-08-21 15:26 | 2026-08-21 19:24 | 2026-08-21 19:24 | 2026-08-21 20:49 | 2026-08-21 20:13 | 2026-08-21 21:33 | 2026-08-21 21:33 | BrokenPole |  | Fair | No | Found ok
Non-Outage | J.E.26.08.27226 | C001896719 | Romaine Roberts | St.Mary | Completed | Load_237863 | Highgate - 210 | 2026-08-21 15:24 | 2026-08-21 15:26 | 2026-08-21 16:18 | 2026-08-21 16:18 | 2026-08-21 18:55 | 2026-08-21 19:22 | 2026-08-21 19:23 | 2026-08-21 19:23 |  |  | Fair | No | Splice and retention 3 span of secondary phase and neutral open and close 25 kva power restore line need bushing
Non-Outage | J.E.26.08.29378 | C001896718 | Neckell Ormsby | St.Ann | Completed | Load_256734 | Upper White River - 110 | 2026-08-21 15:24 | 2026-08-21 15:25 | 2026-08-21 17:44 | 2026-08-21 17:44 | 2026-08-21 18:23 | 2026-08-21 19:00 | 2026-08-21 19:15 | 2026-08-21 19:15 |  |  | Fair | No | Troubleshoot and found burnt joint at transformer pole open 25kva transformer to remade joint using - one bolt clamps voltage left 120v 120v 240v
Non-Outage | J.E.26.08.32531 | C001896728 | Wayne Dillion |  | Completed |  |  | 2026-08-21 15:26 | 2026-08-21 15:27 | 2026-08-21 20:12 | 2026-08-21 20:13 | 2026-08-21 20:12 | 2026-08-21 20:13 | 2026-08-21 20:13 | 2026-08-21 20:13 | BrokenWire |  | Fair | No | Supply restored to the area.
Outage | J.E.26.08.32144 | C001896731 | Omar King | St.Ann | Completed | Load_242897 | Upper White River - 110 | 2026-08-21 15:26 | 2026-08-21 15:27 | 2026-08-21 16:42 | 2026-08-21 16:43 | 2026-08-21 17:38 | 2026-08-21 17:39 | 2026-08-21 17:40 | 2026-08-21 17:40 |  |  | Fair | No | Premises found with internal faults I advise customer to use electrician
Outage | J.E.26.08.32537 | C001896730 | Marlon Authors | St.Elizabeth | Completed | Load_245402 | Maggotty - 210 | 2026-08-21 15:26 | 2026-08-22 08:09 | 2026-08-22 14:11 | 2026-08-22 14:12 | 2026-08-22 14:12 | 2026-08-22 14:15 | 2026-08-22 14:16 | 2026-08-22 14:16 |  |  | Fair | No | Customer said supply wasn’t connected from the hurricane and he is requesting recollection. Please refer same to the the field services department for further assistance
Outage | J.E.26.08.31992 | C001896732 | Richman Whyte | St.Elizabeth | Completed | Load_246277 | Maggotty - 110 | 2026-08-21 15:28 | 2026-08-21 16:29 | 2026-08-21 21:34 | 2026-08-21 21:34 | 2026-08-21 21:34 | 2026-08-21 21:34 | 2026-08-21 21:35 | 2026-08-21 21:35 |  |  | Fair | No | Customer stated that power was restored and she is okay now
Non-Outage | J.E.26.08.32355 | C001896733 | Richman Whyte | Westmoreland | Completed | Load_248847 | Paradise - 210 | 2026-08-21 15:31 | 2026-08-21 15:31 | 2026-08-21 17:20 | 2026-08-21 17:21 | 2026-08-21 17:20 | 2026-08-21 17:22 | 2026-08-21 17:23 | 2026-08-21 17:23 |  |  | Fair | No | Check and find ok voltage # 115 115 205 230 230 230
Outage | J.E.26.08.31939 | C001896748 | Ricky Hall | St.Catherine | Completed | Load_259448 | New Michelton - 310 | 2026-08-21 15:31 | 2026-08-21 15:33 | 2026-08-21 15:45 | 2026-08-21 16:22 | 2026-08-21 16:29 | 2026-08-21 16:29 | 2026-08-21 16:30 | 2026-08-21 16:30 |  |  | Fair | No | Prepaid customer unable to top up plz refer to the relevant team
Outage | J.E.26.08.32061 | C001896749 | Ricky Hall |  | Completed | Load_257620 | Tredegar - 310 | 2026-08-21 15:31 | 2026-08-21 15:33 | 2026-08-21 16:33 | 2026-08-21 17:54 | 2026-08-21 18:07 | 2026-08-21 18:28 | 2026-08-21 18:29 | 2026-08-21 18:29 |  |  | Fair | No | Disconnect 4w service replace blow 10 a junction fuse( meter to be replaced as well customer advised
Outage | J.E.26.08.32082 | C001896751 | Ricky Hall | St.Catherine | Completed | Load_1000768 | Tredegar - 210 | 2026-08-21 15:31 | 2026-08-21 15:33 | 2026-08-21 15:45 | 2026-08-21 16:04 | 2026-08-21 16:20 | 2026-08-21 16:21 | 2026-08-21 16:22 | 2026-08-21 16:22 |  |  | Fair | No | Prepaid customer unable to top up plz refer to the relevant team
Outage | J.E.26.08.32133 | C001896750 | Ricky Hall | St.Catherine | Completed | Load_567663 | Tredegar - 310 | 2026-08-21 15:31 | 2026-08-21 15:33 | 2026-08-21 16:35 | 2026-08-21 18:30 | 2026-08-21 18:52 | 2026-08-21 18:55 | 2026-08-21 18:55 | 2026-08-21 18:55 | LowHangingWires |  | Fair | No | New pols already planted waiting to be transferred
Outage | J.E.26.08.32137 | C001896752 | Ricky Hall | St.Catherine | Completed | Load_261464 | Tredegar - 210 | 2026-08-21 15:31 | 2026-08-21 15:33 | 2026-08-21 18:59 | 2026-08-21 18:59 | 2026-08-21 19:11 | 2026-08-21 19:12 | 2026-08-21 19:12 | 2026-08-21 19:12 |  |  | Fair | No | Premises closed
Outage | J.E.26.08.32239 | C001896753 | Ricky Hall | St.Catherine | Completed | Load_242765 | Twickenham - 310 | 2026-08-21 15:31 | 2026-08-21 15:33 | 2026-08-21 19:49 | 2026-08-21 19:49 | 2026-08-21 20:26 | 2026-08-21 20:47 | 2026-08-21 20:47 | 2026-08-21 20:47 |  |  | Fair | No
Outage | J.E.26.08.32402 | C001896747 | Ricky Hall | St.Catherine | Completed | Load_269713 | Twickenham - 310 | 2026-08-21 15:31 | 2026-08-21 15:33 | 2026-08-21 19:12 | 2026-08-21 19:13 | 2026-08-21 19:48 | 2026-08-21 19:48 | 2026-08-21 19:48 | 2026-08-21 19:48 |  |  | Fair | No | Premises closed
Outage | J.E.26.08.32495 | C001896746 | Ricky Hall | St.Catherine | Completed | Load_556504 | Tredegar - 510 | 2026-08-21 15:31 | 2026-08-21 15:33 | 2026-08-21 16:33 | 2026-08-21 16:36 | 2026-08-21 17:10 | 2026-08-21 17:25 | 2026-08-21 17:26 | 2026-08-21 17:26 |  |  | Fair | No | Rami failure plz refer to the relevant team
Outage | J.E.26.08.32584 | C001896754 | Cliton Henry | St.Mary | Completed | Load_248329 | Highgate - 210 | 2026-08-21 15:33 | 2026-08-22 10:57 | 2026-08-22 12:28 | 2026-08-22 12:28 | 2026-08-22 12:28 | 2026-08-22 12:42 | 2026-08-22 12:46 | 2026-08-22 12:46 | Fire |  | Fair | No | The secondary conductors found touching when the wind blows. A 15 kv day transformer was de energized at pole #0185148 to carryout repairs. Corrective work done to retensioned the secondary neutral conductor. Supply restored to energized the 15 kva transformer.
Outage | J.E.26.08.32245 | C001896755 | Richard Samuda | Manchester | Completed | Load_302329 | Spur Tree - 310 | 2026-08-21 15:35 | 2026-08-22 07:16 | 2026-08-22 07:33 | 2026-08-22 07:34 | 2026-08-22 08:05 | 2026-08-22 08:53 | 2026-08-22 08:53 | 2026-08-22 08:53 |  |  | Fair | No | Found 25 amp junction blown patrol line 25 kva transformer fuses blown patrol line found nothing replaced 25 amp fuse. Fuse hold replaced transformer fuse blown defective 25 kva transformer refer call
Outage | J.E.26.08.32580 | C001896756 | Barnett Brown | Manchester | Completed | Load_267284 | Spur Tree - 310 | 2026-08-21 15:35 | 2026-08-21 16:46 | 2026-08-22 00:58 | 2026-08-22 00:59 | 2026-08-22 00:58 | 2026-08-22 00:59 | 2026-08-22 01:02 | 2026-08-22 01:02 |  |  | Fair | No | Section of line was isolated earlier and maintenance require
Outage | J.E.26.08.32550 | C001896766 | Clyde Brown | Clarendon | Completed | Load_244406 | Monymusk - 410 | 2026-08-21 15:38 | 2026-08-21 15:44 | 2026-08-21 16:45 | 2026-08-21 16:46 | 2026-08-21 19:59 | 2026-08-21 19:42 | 2026-08-21 20:08 | 2026-08-21 20:08 |  | Y | SevereWind | No | Blown 2-25 amps junction fuse along Sciptio foot road line patrolled and tree contact cleared blown fuse replaced.
Outage | J.E.26.08.32575 | C001896765 | Clyde Brown | Clarendon | Completed | Load_262352 | Parnassus - 310 | 2026-08-21 15:38 | 2026-08-21 15:44 | 2026-08-21 22:29 | 2026-08-21 22:29 | 2026-08-21 22:29 | 2026-08-21 22:28 | 2026-08-21 22:32 | 2026-08-21 22:32 |  |  | SevereWind | No | Found ok
Non-Outage | J.E.26.08.30398 | C001896768 | Oshane Warren | Westmoreland | Completed | Load_245296 | Paradise - 310 | 2026-08-21 15:42 | 2026-08-21 15:43 | 2026-08-21 17:23 | 2026-08-21 17:36 | 2026-08-21 17:37 | 2026-08-21 18:21 | 2026-08-21 18:22 | 2026-08-21 18:22 |  |  | Fair | No | Check and found okInternal problem advice to be checked out
Non-Outage | J.E.26.08.31337 | C001896767 | Oshane Warren | Westmoreland | Completed | Load_253220 | Paradise - 310 | 2026-08-21 15:42 | 2026-08-21 15:42 | 2026-08-21 19:44 | 2026-08-21 19:44 | 2026-08-21 20:05 | 2026-08-21 20:06 | 2026-08-21 20:07 | 2026-08-21 20:07 |  |  | Fair | No | Customer stated that they got back power from yesterday
Outage | J.E.26.08.32167 | C001896769 | Derrick Dawkins | St.James | Completed | Load_244480 | Bogue - 310 | 2026-08-21 15:44 | 2026-08-21 15:46 | 2026-08-21 18:31 | 2026-08-21 20:53 | 2026-08-21 21:05 | 2026-08-21 21:18 | 2026-08-21 21:18 | 2026-08-21 21:18 |  |  | Fair | No | Found 15 kva transformer fuse blown due to vegetation remove vegetation and replace 2amp fuse hex box no pole number available
Outage | J.E.26.08.32371 | C001896770 | Derrick Dawkins | St.James | Completed | Load_266889 | Bogue - 310 | 2026-08-21 15:45 | 2026-08-21 15:46 | 2026-08-21 18:31 | 2026-08-21 20:02 | 2026-08-21 20:01 | 2026-08-21 20:02 | 2026-08-21 20:08 | 2026-08-21 20:08 |  |  | Fair | No | Found 3 fuses blow 2 junction 1 hex box. Replace 10 amp / 8amp / 2amp no pole number available for 10 amp junction
Outage | J.E.26.08.32588 | C001896771 | Derrick Dawkins | St.James | Completed | Load_261423 | Bogue - 310 | 2026-08-21 15:45 | 2026-08-21 15:46 | 2026-08-21 18:31 | 2026-08-21 20:43 | 2026-08-21 20:43 | 2026-08-21 20:45 | 2026-08-21 20:51 | 2026-08-21 20:51 |  |  | Fair | No | Found customer with out supply customer service wire defective splice and remade joints used 10ft of #6 triplex voltage left 115/118/233
Non-Outage | J.E.26.08.17459 | C001896775 | Elvis Trowers | KSAS | Completed | Load_242913 | Cane River - 410 | 2026-08-21 15:51 | 2026-08-21 15:52 | 2026-08-21 16:16 | 2026-08-21 16:16 | 2026-08-21 17:26 | 2026-08-21 17:40 | 2026-08-21 17:41 | 2026-08-21 17:41 | BrokenWire |  | Fair | No | Isolate 25 kva transformer at pole#( no pole#) and repair burnt off transformer neutral drop lead. Repair using two 1- bolt clamps. Reclose transformer switch.
Non-Outage | J.E.26.08.32190 | C001896774 | Milton Charlton | KSAN | Completed | Load_240009 | Hope - 410 | 2026-08-21 15:51 | 2026-08-21 15:52 | 2026-08-21 20:46 | 2026-08-21 20:47 | 2026-08-21 21:55 | 2026-08-21 21:35 | 2026-08-21 21:58 | 2026-08-21 21:58 | BrokenPole |  | Fair | No | Found okay upon arrival. Customer reporting broken pole at Paddington Terrace and Liguanea Avenue.
Outage | J.E.26.08.32606 | C001896785 | Neville Spencer | Clarendon | Completed | Load_568438 | May Pen - 110 | 2026-08-21 15:57 | 2026-08-21 15:58 | 2026-08-21 16:20 | 2026-08-21 16:20 | 2026-08-21 19:17 | 2026-08-21 19:17 | 2026-08-21 19:30 | 2026-08-21 19:30 |  |  | Fair | No | Found 35 c6 wooden pole leaning badly across road way construction CV With single phase primary line and open secondary. Disconnect and remove wire from pole. One customer out of supply renew blown 8 amp j/ fuse supply restored NEED Urgent Attention need guy rod and block and guy wire.
Outage | J.E.26.08.32593 | C001896786 | Swon Miller | Portmore | Completed | Load_576229 | Naggo Head - 510 | 2026-08-21 15:59 | 2026-08-21 16:00 | 2026-08-21 18:12 | 2026-08-21 18:12 | 2026-08-21 18:24 | 2026-08-18 07:15 | 2026-08-21 19:24 | 2026-08-21 19:24 | BrokenWire |  | Fair | No | Found customer without supply cause contamination at pole clean and remake joints use 2pg voltage found 0.000 voltage left 116/116/233
Outage | J.E.26.08.32258 | C001896787 | Donald Cunningham | Portmore | Completed | Load_576246 | Naggo Head - 510 | 2026-08-21 16:00 | 2026-08-21 16:01 | 2026-08-21 16:05 | 2026-08-21 16:05 | 2026-08-21 17:09 | 2026-08-21 17:36 | 2026-08-21 17:37 | 2026-08-21 17:37 |  |  | Fair | No | Banging secondary conductor corrected and reset 100 kva transformer by pole #0071581
Outage | J.E.26.08.32528 | C001896788 | Donald Cunningham | Portmore | Completed | Load_576246 | Naggo Head - 510 | 2026-08-21 16:00 | 2026-08-21 16:01 | 2026-08-21 17:38 | 2026-08-21 17:39 | 2026-08-21 17:38 | 2026-08-21 17:39 | 2026-08-21 17:39 | 2026-08-21 17:39 |  |  | Fair | No | Supply restored
Outage | J.E.26.08.32438 | C001896791 | Dwayne Samuels | Trelawny | Completed | Load_241300 | Duncans - 210 | 2026-08-21 16:02 | 2026-08-21 16:52 | 2026-08-21 18:32 | 2026-08-21 18:32 | 2026-08-21 20:47 | 2026-08-21 21:59 | 2026-08-21 22:00 | 2026-08-21 22:00 |  |  | Fair | No | Check and found customer ok Voltage left is 114v 117v 231v
Outage | J.E.26.08.32590 | C001896792 | Dean- Smith | Hanover | Completed | Load_265275 | Orange Bay - 310 | 2026-08-21 16:03 | 2026-08-21 16:05 | 2026-08-21 23:12 | 2026-08-21 23:12 | 2026-08-21 23:12 | 2026-08-21 23:12 | 2026-08-21 23:12 | 2026-08-21 23:12 |  |  | Fair | No | Shift ended
Outage | J.E.26.08.32561 | C001896795 | Dean- Smith | Hanover | Completed | Load_302747 | Orange Bay - 310 | 2026-08-21 16:04 | 2026-08-21 16:05 | 2026-08-21 23:11 | 2026-08-21 23:12 | 2026-08-21 23:11 | 2026-08-21 23:11 | 2026-08-21 23:12 | 2026-08-21 23:12 |  |  | Fair | No | Shift ended
Outage | J.E.26.08.32568 | C001896794 | Dean- Smith | Hanover | Completed | Load_241288 | Orange Bay - 310 | 2026-08-21 16:04 | 2026-08-21 16:05 | 2026-08-21 16:46 | 2026-08-21 19:28 | 2026-08-21 21:53 | 2026-08-21 21:53 | 2026-08-21 23:09 | 2026-08-21 23:09 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Spliced and retention (2) span of primary conductor. Recluse junction that was found open
Outage | J.E.26.08.32625 | C001896797 | Christopher Edwards | KSAN | Completed | Load_246618 | Constant Spring - 310 | 2026-08-21 16:05 | 2026-08-21 16:07 | 2026-08-21 16:23 | 2026-08-21 16:47 | 2026-08-21 16:47 | 2026-08-21 16:52 | 2026-08-21 17:29 | 2026-08-21 17:29 |  |  | Fair | No | Refuse blown junction fuseUsing (1) 30 amps
Non-Outage | J.E.26.08.32600 | C001896800 | Denton Williams |  | Completed |  |  | 2026-08-21 16:06 | 2026-08-21 16:07 | 2026-08-21 19:38 | 2026-08-21 19:39 | 2026-08-21 20:16 | 2026-08-21 20:33 | 2026-08-21 20:34 | 2026-08-21 20:34 |  |  | Fair | No | Two 5amps fuse found blown. Suspect lightening caused outage. Replace both fuses to restore power supply.
Outage | J.E.26.08.32587 | C001896801 | Richard Samuda | Manchester | Completed | Load_1002314 | Porus - 210 | 2026-08-21 16:07 | 2026-08-22 07:16 | 2026-08-22 10:16 | 2026-08-22 11:52 | 2026-08-22 11:56 | 2026-08-22 11:56 | 2026-08-22 11:57 | 2026-08-22 11:57 |  |  | Fair | No | Call to phone no answer premises not located
Outage | J.E.26.08.32630 | C001896802 | Milton Charlton | KSAN | Completed | Load_257562 | Hope - 510 | 2026-08-21 16:09 | 2026-08-21 16:13 | 2026-08-21 18:04 | 2026-08-21 18:04 | 2026-08-21 20:40 | 2026-08-21 20:25 | 2026-08-21 20:43 | 2026-08-21 20:43 |  |  | Fair | No | Refused and reclosed 30 amps junction switch at pole #098123 using one 30 amps fuse.
Outage | J.E.26.08.32650 | C001896827 | Clyde Brown | Clarendon | Completed | Load_253205 | Monymusk - 410 | 2026-08-21 16:31 | 2026-08-21 16:32 | 2026-08-21 20:16 | 2026-08-21 20:17 | 2026-08-21 20:16 | 2026-08-21 19:40 | 2026-08-21 20:19 | 2026-08-21 20:19 |  | Y | SevereWind | No | Blown 2-25 amps junction fuse at Sciptio foot road caused by tree contact,line cleared and blown fuse replaced
Outage | J.E.26.08.32597 | C001896828 | Christopher Edwards | KSAN | Completed | Load_245094 | Constant Spring - 210 | 2026-08-21 16:35 | 2026-08-21 16:36 | 2026-08-21 17:29 | 2026-08-21 17:29 | 2026-08-21 17:42 | 2026-08-21 18:14 | 2026-08-21 18:14 | 2026-08-21 18:14 | Fire |  | Fair | No | Check and found okSupply is at the premises
Outage | J.E.26.08.31356 | C001896832 | Selvin White | St.Elizabeth | Completed | Load_574140 | Maggotty - 110 | 2026-08-21 16:36 | 2026-08-21 16:37 | 2026-08-21 17:59 | 2026-08-21 18:00 | 2026-08-21 17:59 | 2026-08-21 19:53 | 2026-08-21 19:53 | 2026-08-21 19:53 |  |  | Fair | No | Replace a defective 25 KVA transformer in a bank of two transformers that supply 3 phase customer. Supply restored with voltage readings of 113,113, 195,225,225,225 volts. Ground readings is 4.8 Ohms.12345
Outage | J.E.26.08.31861 | C001896840 | Andre Smith | KSAS | Completed | Load_266481 | Hunts Bay - 410 | 2026-08-21 16:37 | 2026-08-22 07:50 | 2026-08-22 09:36 | 2026-08-22 09:37 | 2026-08-22 10:59 | 2026-08-22 11:14 | 2026-08-22 11:14 | 2026-08-22 11:14 |  |  | Fair | No | Premises found close
Outage | J.E.26.08.31902 | C001896841 | Andre Smith | KSAS | Completed | Load_240809 | Greenwich - 310 | 2026-08-21 16:37 | 2026-08-22 07:49 | 2026-08-22 08:16 | 2026-08-22 08:16 | 2026-08-22 09:07 | 2026-08-22 09:35 | 2026-08-22 09:36 | 2026-08-22 09:36 |  |  | Fair | No | Supply restored with the assistance of callcenter
Outage | J.E.26.08.31947 | C001896839 | Elvis Trowers | KSAN | Completed | Load_249802 | Washington Blvd - 310 | 2026-08-21 16:37 | 2026-08-21 16:40 | 2026-08-21 18:59 | 2026-08-21 19:01 | 2026-08-21 19:30 | 2026-08-21 19:40 | 2026-08-21 19:49 | 2026-08-21 19:49 | BrokenWire |  | Fair | No | Customer service wire #6 triplex neutral burn off at pole. Repair using one 1- bolt clamp. Readings at pothead 115-116-232 volts.
Outage | J.E.26.08.32569 | C001896834 | Elvis Trowers | KSAS | Completed | Load_254799 | Greenwich - 710 | 2026-08-21 16:37 | 2026-08-22 08:03 | 2026-08-22 08:18 | 2026-08-22 08:19 | 2026-08-22 09:03 | 2026-08-22 08:40 | 2026-08-22 09:05 | 2026-08-22 09:05 |  |  | Fair | No | Found okay upon arrival. Customer states matter was resolved.
Outage | J.E.26.08.32620 | C001896836 | Edward Royal | KSAS | Completed | Load_249432 | Greenwich - 710 | 2026-08-21 16:37 | 2026-08-22 08:04 | 2026-08-22 09:36 | 2026-08-22 09:36 | 2026-08-22 09:36 | 2026-08-22 09:37 | 2026-08-22 09:37 | 2026-08-22 09:37 |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.08.32656 | C001896833 | Edward Royal | KSAS | Completed | Load_1002844 | Greenwich - 710 | 2026-08-21 16:37 | 2026-08-21 23:27 | 2026-08-21 23:50 | 2026-08-21 23:51 | 2026-08-22 00:03 | 2026-08-22 00:04 | 2026-08-22 00:04 | 2026-08-22 00:04 | BrokenPole |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.32672 | C001896847 | Neville Spencer | Clarendon | Completed | Load_348670 | May Pen - 110 | 2026-08-21 16:46 | 2026-08-21 16:58 | 2026-08-22 13:05 | 2026-08-22 13:05 | 2026-08-22 13:05 | 2026-08-22 13:05 | 2026-08-22 13:06 | 2026-08-22 13:06 |  |  | Fair | No | Renew blown 8 amp j/ fuse supply restored.
Outage | J.E.26.08.32673 | C001896846 | Ricky Hall | St.Catherine | Completed | Load_556034 | Tredegar - 510 | 2026-08-21 16:46 | 2026-08-21 16:58 | 2026-08-21 17:26 | 2026-08-21 17:27 | 2026-08-21 17:52 | 2026-08-21 17:53 | 2026-08-21 17:53 | 2026-08-21 17:53 |  |  | Fair | No | Customer found with supply
Non-Outage | J.E.26.08.32671 | C001896851 | Derrick Dawkins |  | Completed |  |  | 2026-08-21 16:51 | 2026-08-21 16:52 | 2026-08-21 18:22 | 2026-08-21 18:23 | 2026-08-21 18:23 | 2026-08-21 18:23 | 2026-08-21 18:29 | 2026-08-21 18:29 | BrokenWire |  | Fair | No | Found customer service wire bust down due to vehicle accident open transformer to carry out repairs used 3 pg clamp
Non-Outage | J.E.26.08.32675 | C001896855 | Edward Royal |  | Completed |  |  | 2026-08-21 16:53 | 2026-08-22 04:16 | 2026-08-22 09:35 | 2026-08-22 09:35 | 2026-08-22 09:35 | 2026-08-22 09:36 | 2026-08-22 09:36 | 2026-08-22 09:36 | Fire |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.32642 | C001896854 | Stephen Taylor | St.Thomas | Completed | Load_240744 | Good Year - 110 | 2026-08-21 16:53 | 2026-08-21 16:54 | 2026-08-21 18:39 | 2026-08-21 18:39 | 2026-08-21 19:06 | 2026-08-21 19:15 | 2026-08-21 19:18 | 2026-08-21 19:18 |  |  | Fair | No | Clean up single phase an use 2 one bolt clamp
Outage | J.E.26.08.32690 | C001896859 | Eric Williams | KSAS | Completed | Load_255484 | Duhaney - 310 | 2026-08-21 16:56 | 2026-08-21 16:58 | 2026-08-21 17:33 | 2026-08-21 17:33 | 2026-08-21 18:37 | 2026-08-21 18:38 | 2026-08-21 18:42 | 2026-08-21 18:42 |  |  | Fair | No | Customer change over switch was off. corrected by advising customer, power supply restored.
Outage | J.E.26.08.32687 | C001896860 | Donald Cunningham | Portmore | Completed | Load_260244 | Naggo Head - 510 | 2026-08-21 16:57 | 2026-08-21 16:58 | 2026-08-21 18:35 | 2026-08-21 18:35 | 2026-08-21 18:35 | 2026-08-21 19:07 | 2026-08-21 19:09 | 2026-08-21 19:09 |  |  | Fair | No | Corroded phase and neural by pothead corrected voltage readings by meter socket 119/120/239
Outage | J.E.26.08.32693 | C001896861 | Raymond Lewis | St.Ann | Completed | Load_251707 | Cardiff Hall - 210 | 2026-08-21 16:59 | 2026-08-21 17:02 | 2026-08-21 17:47 | 2026-08-21 17:47 | 2026-08-21 17:47 | 2026-08-21 17:48 | 2026-08-21 17:49 | 2026-08-21 17:49 |  |  | Fair | No | Supply restored
Outage | J.E.26.08.32330 | C001896862 | Wayne Dillion | St.Elizabeth | Completed | Load_250102 | Maggotty - 210 | 2026-08-21 17:00 | 2026-08-21 17:01 | 2026-08-21 17:19 | 2026-08-21 17:20 | 2026-08-21 18:45 | 2026-08-21 19:54 | 2026-08-21 19:54 | 2026-08-21 19:54 | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Patrol and found two pole span of secondary neutral broken. Isolate 25kva transformer circuit no pole # to splice and retention same using 50ft of #2 conductor, one #2 splicing sleeve and 3 clamps. Close transformer circuit and supply restored to the area.
Non-Outage | J.E.26.08.32704 | C001896865 | Lionel Robinson | Trelawny | Completed | Load_1001631 | Greenwood - 110 | 2026-08-21 17:01 | 2026-08-21 17:04 | 2026-08-21 17:19 | 2026-08-21 17:19 | 2026-08-21 17:38 | 2026-08-21 18:28 | 2026-08-21 18:28 | 2026-08-21 18:28 |  |  | Fair | No | Replace 100ft #6 triplex voltage reading 118, 118, 236 volts
Non-Outage | J.E.26.08.32204 | C001896866 | Lionel Robinson | Trelawny | Completed | Load_555893 | Martha Brae - 210 | 2026-08-21 17:02 | 2026-08-21 17:04 | 2026-08-21 19:58 | 2026-08-21 19:59 | 2026-08-21 20:39 | 2026-08-21 20:46 | 2026-08-21 20:46 | 2026-08-21 20:46 | BrokenPole |  | Fair | No | 30 class 6 secondary pole defective needs to be changed urgently please refer to maintenance.
Non-Outage | J.E.26.08.31584 | C001896867 | Lionel Robinson | Trelawny | Completed | Load_294590 | Martha Brae - 110 | 2026-08-21 17:03 | 2026-08-21 17:05 | 2026-08-21 18:43 | 2026-08-21 18:44 | 2026-08-21 19:09 | 2026-08-21 19:36 | 2026-08-21 19:37 | 2026-08-21 19:37 |  |  | Fair | No | Suspected damage in meter socket need locking band puller for access. voltage reading at customer pot head 114,114, 228 volts, voltage reading at Jps pole 114, 115, 229 volts
Outage | J.E.26.08.32613 | C001896888 | Richman Whyte | Westmoreland | Completed | Load_261471 | Paradise - 110 | 2026-08-21 17:28 | 2026-08-21 17:32 | 2026-08-21 18:36 | 2026-08-21 18:37 | 2026-08-21 19:28 | 2026-08-21 20:19 | 2026-08-21 20:20 | 2026-08-21 20:20 | BrokenWire |  | Fair | No | Clair secondary conductor and reset twenty five kva transformer voltage 114 114 195 228 228 230
Outage | J.E.26.08.32623 | C001896889 | Richman Whyte | Westmoreland | Completed | Load_246361 | Paradise - 110 | 2026-08-21 17:28 | 2026-08-21 17:31 | 2026-08-21 18:27 | 2026-08-21 18:27 | 2026-08-21 18:27 | 2026-08-21 18:35 | 2026-08-21 18:36 | 2026-08-21 18:36 |  |  | Fair | No | Customer have internal problem advise to fix voltage 110
Outage | J.E.26.08.32712 | C001896890 | Oshane Warren | Westmoreland | Completed | Load_268880 | Paradise - 310 | 2026-08-21 17:28 | 2026-08-21 17:30 | 2026-08-21 18:24 | 2026-08-21 18:24 | 2026-08-21 19:39 | 2026-08-21 19:40 | 2026-08-21 19:41 | 2026-08-21 19:41 |  |  | Fair | No | Replace 20amp junction fuse
Outage | J.E.26.08.32566 | C001896893 | Milton Charlton | KSAN | Completed | Load_241670 | West Kings House - 310 | 2026-08-21 17:38 | 2026-08-21 17:39 | 2026-08-21 22:02 | 2026-08-21 22:03 | 2026-08-21 22:03 | 2026-08-21 22:20 | 2026-08-21 22:35 | 2026-08-21 22:35 | BrokenWire |  | Fair | No | Unable too locate customer by telephone and there,s no low hanging wire belongs to JPS
Outage | J.E.26.08.32745 | C001896894 | Lionel Robinson | Trelawny | Completed | Load_556059 | Martha Brae - 110 | 2026-08-21 17:38 | 2026-08-21 17:39 | 2026-08-21 19:39 | 2026-08-21 19:39 | 2026-08-21 19:39 | 2026-08-21 19:56 | 2026-08-21 19:57 | 2026-08-21 19:57 |  |  | Fair | No | Meter was laying on the ground when we got to the location. Meter was reinstalled after voltage readings 239, 237, 239 volts phase to neutral and 413, 415, 411 volts across phases were taken.
Outage | J.E.26.08.32758 | C001896905 | Eric Williams | KSAS | Completed | Load_268579 | Duhaney - 310 | 2026-08-21 18:03 | 2026-08-21 18:04 | 2026-08-21 21:20 | 2026-08-21 21:21 | 2026-08-21 22:22 | 2026-08-21 22:22 | 2026-08-21 22:22 | 2026-08-21 22:22 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.32768 | C001896904 | Eric Williams | KSAN | Completed | Load_255617 | Constant Spring - 210 | 2026-08-21 18:03 | 2026-08-21 18:04 | 2026-08-21 18:50 | 2026-08-21 18:51 | 2026-08-21 19:10 | 2026-08-21 19:42 | 2026-08-21 19:47 | 2026-08-21 19:47 | BrokenWire |  | Fair | No | Small vehicle with required at location to tension service drop and re clamp wrap joints at pot head.
Outage | J.E.26.08.32727 | C001896910 | Clyde Brown | Clarendon | Completed | Load_405499 | Parnassus - 210 | 2026-08-21 18:17 | 2026-08-21 18:18 | 2026-08-21 20:20 | 2026-08-21 20:20 | 2026-08-21 21:41 | 2026-08-21 21:39 | 2026-08-21 21:46 | 2026-08-21 21:46 | Fire |  | SevereWind | No | Blown 3 amps fuse for 25 kva transformer,line patrolled and no fault seen,blown fuse replaced
Outage | J.E.26.08.32730 | C001896911 | Clyde Brown | Clarendon | Completed | Load_240655 | Monymusk - 410 | 2026-08-21 18:17 | 2026-08-21 18:18 | 2026-08-21 20:12 | 2026-08-21 20:13 | 2026-08-21 20:13 | 2026-08-21 19:40 | 2026-08-21 20:16 | 2026-08-21 20:16 |  | Y | SevereWind | No | Blown 2-25amps junction fuse at Sciptio foot road,line patrolled and tree contact found,line cleared and blown fuse replaced.
Outage | J.E.26.08.32786 | C001896912 | Christopher Edwards | KSAN | Completed | Load_262953 | Constant Spring - 410 | 2026-08-21 18:17 | 2026-08-21 18:19 | 2026-08-21 18:24 | 2026-08-21 19:11 | 2026-08-21 19:11 | 2026-08-21 19:13 | 2026-08-21 19:14 | 2026-08-21 19:14 |  |  | Fair | No | Customer meter pole is damaged Customer was advised to fix meter pole before service can be restored
Outage | J.E.26.08.32776 | C001896913 | Neckell Ormsby | St.Mary | Completed | Load_255663 | Blackstonedge - 110 | 2026-08-21 18:19 | 2026-08-21 18:20 | 2026-08-21 20:48 | 2026-08-21 20:48 | 2026-08-21 21:18 | 2026-08-21 21:42 | 2026-08-21 21:42 | 2026-08-21 21:42 |  |  | Fair | No | Found 50 kva transformer fuse blown patrol and found no permanent fault replace 1-5 amp fuse
Non-Outage | J.E.26.08.32767 | C001896915 | Elvis Trowers |  | Completed |  |  | 2026-08-21 18:21 | 2026-08-21 18:24 | 2026-08-21 21:35 | 2026-08-21 21:36 | 2026-08-21 22:09 | 2026-08-21 22:25 | 2026-08-21 22:22 | 2026-08-21 22:22 | BrokenWire |  | Fair | No | Isolate 100 kva transformer at pole# 0120542. And repair transformer primary neutral bushings damaged by falling tree limb. Repair using two 1- bolt clamps. And reclose transformer switch.
Outage | J.E.26.08.32763 | C001896916 | Elvis Trowers | KSAS | Completed | Load_255198 | Three Miles - 510 | 2026-08-21 18:22 | 2026-08-21 18:24 | 2026-08-21 19:49 | 2026-08-21 19:49 | 2026-08-21 20:13 | 2026-08-21 20:16 | 2026-08-21 20:18 | 2026-08-21 20:18 | BrokenWire |  | Fair | No | Customer service wire #6 triplex neutral corroded at pothead. Repair using one 1- bolt clamp. Readings at pothead 114-114-229 volts.
Outage | J.E.26.08.32775 | C001896917 | Richard Nicholas | St.Catherine | Completed | Load_249216 | Rhodens Pen - 310 | 2026-08-21 18:22 | 2026-08-21 18:25 | 2026-08-21 19:11 | 2026-08-21 19:12 | 2026-08-21 20:26 | 2026-08-21 21:49 | 2026-08-21 21:51 | 2026-08-21 21:51 |  |  | Fair | No | Remade 1 set of found open 3phase jumper on pole at the gate of the premises,3 clamp was used.
Outage | J.E.26.08.32616 | C001896918 | Wayne Dillion | St.Elizabeth | Completed | Load_251175 | Maggotty - 210 | 2026-08-21 18:27 | 2026-08-21 18:28 | 2026-08-21 20:16 | 2026-08-21 20:16 | 2026-08-21 20:16 | 2026-08-21 20:17 | 2026-08-21 20:17 | 2026-08-21 20:17 |  |  | Fair | No | Supply restored to the area.
Outage | J.E.26.08.32750 | C001896919 | Wayne Dillion | Manchester | Completed | Load_258101 | Spur Tree - 210 | 2026-08-21 18:27 | 2026-08-21 18:28 | 2026-08-21 21:38 | 2026-08-21 21:38 | 2026-08-21 21:38 | 2026-08-21 21:59 | 2026-08-21 21:59 | 2026-08-21 21:59 | Fire |  | Fair | No | Patrol and found no fire on wire and no broken wires in the area.
Outage | J.E.26.08.32521 | C001896921 | Elvis Trowers | KSAN | Completed | Load_573771 | Washington Blvd - 310 | 2026-08-21 18:28 | 2026-08-21 18:29 | 2026-08-21 20:18 | 2026-08-21 20:23 | 2026-08-21 21:31 | 2026-08-21 21:30 | 2026-08-21 21:35 | 2026-08-21 21:35 | BrokenWire |  | Fair | No | Customer service wire #6 triplex phase and neutral corroded at pothead. Repair using two 1- bolt clamps. Readings at pothead 113-114-228 volts.
Outage | J.E.26.08.32800 | C001896920 | Wayne Dillion | St.Elizabeth | Completed | Load_269917 | Maggotty - 110 | 2026-08-21 18:28 | 2026-08-22 07:37 | 2026-08-22 09:54 | 2026-08-22 09:55 | 2026-08-22 10:06 | 2026-08-22 11:18 | 2026-08-22 11:20 | 2026-08-22 11:20 | BrokenWire |  | Fair | No | Patrol and found one pole span of secondary neutral broken. Isolate 25kva transformer circuit no pole# to splice and retention same using 4 clamps, 1 #2 splicing sleeve and 50 ft of #2 conductor. Close transformer circuit and supply restored okay.
Outage | J.E.26.08.32792 | C001896922 | Wayne Dillion | St.Elizabeth | Completed | Load_268404 | Maggotty - 210 | 2026-08-21 18:29 | 2026-08-21 18:30 | 2026-08-21 20:17 | 2026-08-21 20:17 | 2026-08-21 20:17 | 2026-08-21 20:18 | 2026-08-21 20:18 | 2026-08-21 20:18 |  |  | Fair | No | Unable to locate and customer number is not working.
Outage | J.E.26.08.32082 | C001896926 | Moses Elliston | St.Catherine | Completed | Load_1000768 | Tredegar - 210 | 2026-08-21 18:36 | 2026-08-21 18:37 | 2026-08-22 09:58 | 2026-08-22 09:59 | 2026-08-22 09:59 | 2026-08-28 16:46 | 2026-08-22 10:00 | 2026-08-22 10:00 |  |  | Fair | No | Credit added to prepaid account.
Non-Outage | J.E.26.08.19715 | C001896928 | Damion Reid | Manchester | Completed | Load_244185 | Kendal - 210 | 2026-08-21 18:48 | 2026-08-21 18:49 | 2026-08-21 21:30 | 2026-08-21 21:30 | 2026-08-21 21:50 | 2026-08-21 22:05 | 2026-08-21 22:06 | 2026-08-21 22:06 |  |  | Fair | No | Customer say he did not make any report
Non-Outage | J.E.26.08.32659 | C001896929 | Clyde Brown | Clarendon | Completed | Load_253205 | Monymusk - 410 | 2026-08-21 18:48 | 2026-08-21 18:49 | 2026-08-21 20:08 | 2026-08-21 20:09 | 2026-08-21 20:08 | 2026-08-21 19:40 | 2026-08-21 20:11 | 2026-08-21 20:11 |  | Y | SevereWind | No | Blown 2-25 amps junction fuse at sciptio foot road caused by tree contact,line cleared and blown fuse replaced.
Outage | J.E.26.08.32684 | C001896930 | Derrick Dawkins | St.James | Completed | Load_252075 | Bogue - 310 | 2026-08-21 18:51 | 2026-08-22 07:55 | 2026-08-22 12:59 | 2026-08-22 13:18 | 2026-08-22 14:16 | 2026-08-22 14:17 | 2026-08-22 14:17 | 2026-08-22 14:17 |  |  | Fair | No | Cannot locate premises calls to customer went unanswered
Outage | J.E.26.08.32826 | C001896933 | Barnett Brown | Manchester | Completed | Load_251076 | Spur Tree - 310 | 2026-08-21 18:56 | 2026-08-21 18:57 | 2026-08-21 19:07 | 2026-08-21 19:07 | 2026-08-21 19:07 | 2026-08-21 21:00 | 2026-08-21 21:10 | 2026-08-21 21:10 |  |  | Fair | No | Isolate section of primary line, maintenance crew require to replace two poles, 35 class 6 TA. Three transformer circuits are out presently.
Outage | J.E.26.08.32852 | C001896934 | Romaine Roberts | St.Mary | Completed | Load_309966 | Highgate -110 | 2026-08-21 18:58 | 2026-08-21 18:59 | 2026-08-21 21:33 | 2026-08-21 21:34 | 2026-08-21 22:02 | 2026-08-21 22:57 | 2026-08-21 22:59 | 2026-08-21 22:59 |  |  | Fair | No | Found junction fuse blown patrol line and clear tree from line replace 15 amp no pole number power restore
Non-Outage | J.E.26.08.32541 | C001896940 | Christopher Edwards | KSAN | Completed | Load_261006 | Constant Spring - 410 | 2026-08-21 19:16 | 2026-08-21 19:18 | 2026-08-21 19:25 | 2026-08-21 19:38 | 2026-08-21 19:38 | 2026-08-21 20:18 | 2026-08-21 20:18 | 2026-08-21 20:18 |  |  | Fair | No | Check and found okSupply is at the premises
Non-Outage | J.E.26.08.32573 | C001896939 | Christopher Edwards | KSAN | Completed | Load_263999 | Constant Spring - 410 | 2026-08-21 19:16 | 2026-08-21 19:18 | 2026-08-21 20:18 | 2026-08-22 11:02 | 2026-08-22 11:02 | 2026-08-22 11:02 | 2026-08-22 11:02 | 2026-08-22 11:02 |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Non-Outage | J.E.26.08.31004 | C001896942 | Denton Williams | Portland | Completed | Load_246094 | Port Antonio - 410 | 2026-08-21 19:41 | 2026-08-21 19:42 | 2026-08-21 20:35 | 2026-08-21 20:35 | 2026-08-21 21:04 | 2026-08-21 21:05 | 2026-08-21 21:08 | 2026-08-21 21:08 |  |  | Fair | No | Lifespan water company is currently closed, also we’re unable to reach customer via telephone call. Day visit is required.
Non-Outage | J.E.26.08.32645 | C001896946 | Denton Williams | Portland | Completed | Load_249717 | Port Antonio - 410 | 2026-08-21 19:41 | 2026-08-21 19:42 | 2026-08-21 21:08 | 2026-08-21 21:09 | 2026-08-21 21:49 | 2026-08-21 21:51 | 2026-08-21 21:55 | 2026-08-21 21:55 |  |  | Fair | No | Customer requesting locking band to be removed from around meter to facilitate further checks on meter socket. Please refer to field service department.
Outage | J.E.26.08.32768 | C001896947 | Christopher Edwards | KSAN | Completed | Load_255617 | Constant Spring - 210 | 2026-08-21 19:45 | 2026-08-22 09:26 | 2026-08-22 10:02 | 2026-08-22 10:02 | 2026-08-22 10:02 | 2026-08-22 10:40 | 2026-08-22 10:41 | 2026-08-22 10:41 | BrokenWire |  | Fair | No | Customer was contacted and stated that they requested a visit at 7 pm today
Outage | J.E.26.08.32926 | C001896955 | Romaine Roberts | St.Mary | Completed | Load_246518 | Highgate - 210 | 2026-08-21 19:59 | 2026-08-21 20:04 | 2026-08-21 23:03 | 2026-08-21 23:04 | 2026-08-21 23:36 | 2026-08-22 02:10 | 2026-08-22 02:22 | 2026-08-22 02:22 |  |  | Fair | No | Found junction fuse blown also 25 kva transformer patrol and clear line and replace 15 amp and 3 amp
Outage | J.E.26.08.32701 | C001896959 | Dwayne Samuels | Trelawny | Completed | Load_256592 | Duncans - 210 | 2026-08-21 20:05 | 2026-08-21 20:07 | 2026-08-21 22:35 | 2026-08-21 22:36 | 2026-08-21 22:41 | 2026-08-21 22:42 | 2026-08-21 22:42 | 2026-08-21 22:42 |  |  | Fair | No | Customer said that their power supply was already restored
Non-Outage | J.E.26.08.32934 | C001896962 | Romaine Roberts |  | Completed |  |  | 2026-08-21 20:07 | 2026-08-21 20:08 | 2026-08-22 02:22 | 2026-08-22 02:23 | 2026-08-22 02:23 | 2026-08-22 02:28 | 2026-08-22 02:28 | 2026-08-22 02:28 | Fire |  | Fair | No | Found junction fuse blown also 25 kva transformer patrol and clear line and replace 15 amp and 3 amp
Outage | J.E.26.08.32859 | C001896963 | Ricky Hall | St.Catherine | Completed | Load_257717 | Rhodens Pen - 210 | 2026-08-21 20:15 | 2026-08-22 09:12 | 2026-08-22 09:24 | 2026-08-22 09:43 | 2026-08-22 10:28 | 2026-08-22 10:28 | 2026-08-22 10:31 | 2026-08-22 10:31 |  |  | Fair | No | Rami failure prepaid customer unable to add credit plz refer to the relevant team
Non-Outage | J.E.26.08.32885 | C001896966 | Oshane Warren |  | Completed |  |  | 2026-08-21 20:23 | 2026-08-21 20:27 | 2026-08-21 21:40 | 2026-08-21 21:41 | 2026-08-21 21:40 | 2026-08-21 21:45 | 2026-08-21 21:45 | 2026-08-21 21:45 |  |  | Fair | No | Unable to contact customer directions needed
Outage | J.E.26.08.32923 | C001896968 | Richard Samuda | Manchester | Completed | Load_302329 | Spur Tree - 310 | 2026-08-21 20:28 | 2026-08-22 07:16 | 2026-08-22 08:54 | 2026-08-22 08:55 | 2026-08-22 08:55 | 2026-08-22 08:55 | 2026-08-22 08:55 | 2026-08-22 08:55 | Fire |  | Fair | No | Power was restored
Outage | J.E.26.08.32960 | C001896972 | Daniel Francis | St.Ann | Completed | Load_261460 | Cardiff Hall - 310 | 2026-08-21 20:44 | 2026-08-21 23:41 | 2026-08-22 01:14 | 2026-08-22 01:15 | 2026-08-22 01:34 | 2026-08-22 02:26 | 2026-08-22 02:30 | 2026-08-22 02:30 | BrokenWire |  | Fair | No | Found secondary phase and neutral broken splice and retention 1span of2wire
Outage | J.E.26.08.33114 | C001896980 | Richman Whyte | Westmoreland | Completed | Load_265324 | Paradise - 210 | 2026-08-21 22:19 | 2026-08-21 22:20 | 2026-08-22 07:58 | 2026-08-22 07:59 | 2026-08-22 09:02 | 2026-08-22 12:11 | 2026-08-22 12:12 | 2026-08-22 12:12 |  |  | Fair | No | Open 15amp junction fuse and change defective switch at 25 kva transformer switch voltage #115 115 230
Outage | J.E.26.08.33101 | C001896981 | Christopher Edwards | KSAN | Completed | Load_239582 | Constant Spring - 210 | 2026-08-21 22:24 | 2026-08-22 07:42 | 2026-08-22 07:47 | 2026-08-22 08:42 | 2026-08-22 08:59 | 2026-08-22 08:59 | 2026-08-22 09:35 | 2026-08-22 09:35 |  |  | Fair | No | Check and found okSupply is in the area Unable to reach customer by phone
Non-Outage | J.E.26.08.32976 | C001896984 | Edward Royal |  | Completed |  |  | 2026-08-21 23:22 | 2026-08-21 23:26 | 2026-08-21 23:42 | 2026-08-21 23:43 | 2026-08-21 23:43 | 2026-08-21 23:43 | 2026-08-21 23:43 | 2026-08-21 23:43 | Fire |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.32940 | C001896985 | Edward Royal | KSAS | Completed | Load_251755 | Rockfort - 410 | 2026-08-21 23:22 | 2026-08-21 23:26 | 2026-08-21 23:44 | 2026-08-21 23:44 | 2026-08-21 23:44 | 2026-08-21 23:44 | 2026-08-21 23:45 | 2026-08-21 23:45 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.32113 | C001896986 | Horace Malcolm | St.James | Completed | Load_238595 | Bogue - 510 | 2026-08-21 23:29 | 2026-08-21 23:34 | 2026-08-22 00:58 | 2026-08-22 00:58 | 2026-08-22 01:31 | 2026-08-22 01:49 | 2026-08-22 01:49 | 2026-08-22 01:49 | BrokenPole |  | Fair | No | Check and found no broken pole from direction given
Non-Outage | J.E.26.08.30707 | C001896987 | Romeo Brissett |  | Completed |  |  | 2026-08-21 23:31 | 2026-08-22 08:10 | 2026-08-22 10:26 | 2026-08-22 10:27 | 2026-08-22 10:26 | 2026-08-22 10:20 | 2026-08-22 10:31 | 2026-08-22 10:31 | Fire |  | Fair | No | Found customer service wire burned off, spliced and retention customer service wire, used 20ft of #6 and 3 clamps. V/R 112-113-226
Outage | J.E.26.08.29419 | C001896989 | Horace Malcolm | St.James | Completed | Load_246427 | Bogue - 310 | 2026-08-21 23:31 | 2026-08-21 23:34 | 2026-08-22 02:23 | 2026-08-22 02:24 | 2026-08-22 02:39 | 2026-08-22 02:46 | 2026-08-22 02:46 | 2026-08-22 02:46 | Fire |  | Fair | No | Check and found premises closed voltage reading at pothead 115-113-228
Outage | J.E.26.08.30202 | C001896988 | Horace Malcolm | St.James | Completed | Load_301676 | Bogue - 310 | 2026-08-21 23:31 | 2026-08-21 23:34 | 2026-08-22 01:52 | 2026-08-22 01:52 | 2026-08-22 02:04 | 2026-08-22 02:15 | 2026-08-22 02:23 | 2026-08-22 02:23 | BrokenWire |  | Fair | No | Unable to locate premises no direction given multiple calls to customer unavailable
Non-Outage | J.E.26.08.32446 | C001896990 | Horace Malcolm | St.James | Completed | Load_264211 | Bogue - 310 | 2026-08-21 23:32 | 2026-08-21 23:34 | 2026-08-21 23:49 | 2026-08-21 23:50 | 2026-08-22 00:16 | 2026-08-22 00:57 | 2026-08-22 00:57 | 2026-08-22 00:57 |  |  | Fair | No | Refused one 25kva transformer used one 3amp fuse
Outage | J.E.26.08.32943 | C001896991 | Horace Malcolm | St.James | Completed | Load_254515 | Bogue - 510 | 2026-08-21 23:33 | 2026-08-21 23:34 | 2026-08-21 23:49 | 2026-08-22 07:08 | 2026-08-22 07:08 | 2026-08-22 07:10 | 2026-08-22 07:10 | 2026-08-22 07:10 |  |  | Fair | No | Isolate two 25kva transformer for customer to carry out repairs
Non-Outage | J.E.26.08.33276 | C001896995 | Delano Gayle |  | Completed |  |  | 2026-08-22 03:50 | 2026-08-22 03:50 | 2026-08-22 04:48 | 2026-08-22 04:49 | 2026-08-22 04:50 | 2026-08-22 04:51 | 2026-08-22 04:51 | 2026-08-22 04:51 | BrokenPole |  | Fair | No | Premises not found no proper contact information in report
Outage | J.E.26.08.33333 | C001897079 | Collin Robinson | Portland | Completed | Load_242614 | Port Antonio - 410 | 2026-08-22 07:05 | 2026-08-22 07:07 | 2026-08-22 09:55 | 2026-08-22 09:55 | 2026-08-22 10:26 | 2026-08-22 11:09 | 2026-08-22 11:09 | 2026-08-22 11:09 |  |  | Rains | No | Remove tree branches from primary conductor and replace 8 amps junction fuse
Non-Outage | J.E.26.08.32384 | C001897081 | Collin Robinson | Portland | Completed | Load_250580 | Port Antonio - 410 | 2026-08-22 07:07 | 2026-08-22 07:08 | 2026-08-22 07:33 | 2026-08-22 07:34 | 2026-08-22 09:48 | 2026-08-22 09:54 | 2026-08-22 09:55 | 2026-08-22 09:55 |  |  | Fair | No | Change one corroded grease nipple at pothead Voltage reading 115 v 115v 230v
Non-Outage | J.E.26.08.28885 | C001897084 | Raymond Lewis | St.Ann | Completed | Load_257486 | Upper White River - 110 | 2026-08-22 07:10 | 2026-08-22 07:31 | 2026-08-22 09:57 | 2026-08-22 09:57 | 2026-08-22 16:35 | 2026-08-22 16:37 | 2026-08-22 16:37 | 2026-08-22 16:37 |  |  | Fair | No | Phone not answering
Non-Outage | J.E.26.08.32228 | C001897085 | Cliton Henry | St.Mary | Completed | Load_255663 | Blackstonedge - 110 | 2026-08-22 07:11 | 2026-08-22 07:12 | 2026-08-22 14:20 | 2026-08-22 14:20 | 2026-08-22 14:31 | 2026-08-22 14:32 | 2026-08-22 14:34 | 2026-08-22 14:34 |  |  | Fair | No | The NWC personal on property said that the supply was restored from last night by another team.
Outage | J.E.26.08.33265 | C001897087 | Roxroy Needham | St.Ann | Completed | Load_261460 | Cardiff Hall - 310 | 2026-08-22 07:12 | 2026-08-22 07:22 | 2026-08-22 11:03 | 2026-08-22 11:03 | 2026-08-22 12:55 | 2026-08-22 13:31 | 2026-08-22 13:32 | 2026-08-22 13:32 |  |  | Fair | No | Premises found ok cable wire hanging
Non-Outage | J.E.26.08.31363 | C001897089 | Raymond Lewis | St.Ann | Completed | Load_267348 | Roaring River - 210 | 2026-08-22 07:13 | 2026-08-22 07:26 | 2026-08-22 08:44 | 2026-08-22 08:44 | 2026-08-22 09:38 | 2026-08-22 09:40 | 2026-08-22 09:40 | 2026-08-22 09:40 |  |  | Fair | No | Premises not found and phone not answering
Non-Outage | J.E.26.08.31571 | C001897088 | Raymond Lewis | St.Ann | Completed | Load_245545 | Roaring River - 210 | 2026-08-22 07:13 | 2026-08-22 07:14 | 2026-08-22 16:37 | 2026-08-22 16:38 | 2026-08-22 17:45 | 2026-08-22 17:48 | 2026-08-22 17:49 | 2026-08-22 17:49 |  |  | Fair | No | Remade joints at pothead and pole 3 wire service,voltages 231/115/115/
Outage | J.E.26.08.33307 | C001897093 | Roxroy Needham | St.Ann | Completed | Load_268908 | Cardiff Hall - 310 | 2026-08-22 07:21 | 2026-08-22 07:23 | 2026-08-22 07:49 | 2026-08-22 07:49 | 2026-08-22 09:33 | 2026-08-22 09:32 | 2026-08-22 09:50 | 2026-08-22 09:50 |  |  | Fair | No | Remake joint at pole used 1 pg clamp voltage left at meter 113-114-219
Non-Outage | J.E.26.08.32269 | C001897094 | Richard Samuda |  | Completed |  |  | 2026-08-22 07:22 | 2026-08-22 07:24 | 2026-08-22 10:16 | 2026-08-22 10:17 | 2026-08-22 10:31 | 2026-08-22 10:32 | 2026-08-22 10:32 | 2026-08-22 10:32 |  |  | Fair | No | Customer back to normal
Non-Outage | J.E.26.08.30502 | C001897095 | Richard Samuda |  | Completed |  |  | 2026-08-22 07:23 | 2026-08-22 07:24 | 2026-08-22 10:16 | 2026-08-22 15:16 | 2026-08-22 15:28 | 2026-08-22 15:29 | 2026-08-22 15:29 | 2026-08-22 15:29 |  |  | Fair | No | Call to phone no answer premises not located
Non-Outage | J.E.26.08.32342 | C001897096 | Raymond Lewis | St.Ann | Completed | Load_256455 | Roaring River - 210 | 2026-08-22 07:24 | 2026-08-22 08:28 | 2026-08-22 08:35 | 2026-08-22 08:35 | 2026-08-22 08:35 | 2026-08-22 08:40 | 2026-08-22 08:41 | 2026-08-22 08:41 | LeaningPole |  | Fair | No | Down guy was removed course pole coming to road
Non-Outage | J.E.26.08.26879 | C001897099 | Cliton Henry | St.Mary | Completed | Load_353034 | Oracabessa - 110 | 2026-08-22 07:27 | 2026-08-22 07:28 | 2026-08-22 09:16 | 2026-08-22 09:17 | 2026-08-22 09:31 | 2026-08-22 11:11 | 2026-08-22 11:21 | 2026-08-22 11:21 |  |  | Fair | No | A span of secondary phase conductor found missing. A 15 kva transformer was de energized at pole # 005052 to carryout repairs. Corrective work done to string and tensioned one span of secondary phase conductor using approximately 150 feet #2 AA conductor, 2 #2 preforms and 3 one bolt clamps. The customer service wire was also reconnected using 3 one bolt clamps. Voltages left 116-117/233 volts
Outage | J.E.26.08.32920 | C001897100 | Wayne Dillion | St.Elizabeth | Completed | Load_239662 | Maggotty - 110 | 2026-08-22 07:29 | 2026-08-22 07:36 | 2026-08-22 14:42 | 2026-08-22 14:42 | 2026-08-22 15:18 | 2026-08-22 15:20 | 2026-08-22 15:22 | 2026-08-22 15:22 |  |  | Fair | No | Patrol and found one blown 3amp fuse that protects 25kva transformer circuit no pole #. Replace same and supply restored okay.
Outage | J.E.26.08.32921 | C001897101 | Wayne Dillion | St.Elizabeth | Completed | Load_240962 | Maggotty - 110 | 2026-08-22 07:29 | 2026-08-22 07:36 | 2026-08-22 15:30 | 2026-08-22 15:31 | 2026-08-22 15:30 | 2026-08-22 15:31 | 2026-08-22 15:31 | 2026-08-22 15:31 |  |  | Fair | No | Supply restored to the area.
Non-Outage | J.E.26.08.33324 | C001897102 | Hartley Chin |  | Completed |  |  | 2026-08-22 07:32 | 2026-08-22 07:44 | 2026-08-22 10:46 | 2026-08-22 11:07 | 2026-08-22 11:19 | 2026-08-22 11:42 | 2026-08-22 11:44 | 2026-08-22 11:44 |  |  | SevereWind | No | Found 2 of 3 blown 100KVA transformer @ pole # 0055036 line patrolled and found okay , transformer refused… voltage read 116v , 116v , 206v .
Outage | J.E.26.08.32027 | C001897103 | Oshane Warren | St.Elizabeth | Completed | Load_264525 | Maggotty - 110 | 2026-08-22 07:34 | 2026-08-22 07:35 | 2026-08-22 08:46 | 2026-08-22 08:47 | 2026-08-22 10:47 | 2026-08-22 11:12 | 2026-08-22 11:15 | 2026-08-22 11:15 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Reconnection back service wire at pathead and secondary line used 3 service connector 3 1 bolt clamps 90 ft #6 twisted wire voltage 120 120 240
Non-Outage | J.E.26.08.33242 | C001897106 | Hartley Chin |  | Completed |  |  | 2026-08-22 07:36 | 2026-08-22 07:43 | 2026-08-22 12:02 | 2026-08-22 17:58 | 2026-08-22 17:58 | 2026-08-22 17:58 | 2026-08-22 17:58 | 2026-08-22 17:58 |  |  | Fair | No | Prem not found … unable t contact customer with contact # provided…
Non-Outage | J.E.26.08.33244 | C001897105 | Hartley Chin |  | Completed |  |  | 2026-08-22 07:36 | 2026-08-22 07:43 | 2026-08-22 12:02 | 2026-08-22 17:57 | 2026-08-22 17:56 | 2026-08-22 17:57 | 2026-08-22 17:57 | 2026-08-22 17:57 |  |  | Fair | No | Contacted customer she stated that issue was resolved…
Outage | J.E.26.08.33252 | C001897104 | Hartley Chin | Clarendon | Completed | Load_246015 | Monymusk - 410 | 2026-08-22 07:36 | 2026-08-22 07:43 | 2026-08-22 12:03 | 2026-08-22 18:00 | 2026-08-22 17:59 | 2026-08-22 18:00 | 2026-08-22 18:00 | 2026-08-22 18:00 |  |  | Fair | No | Contacted customer.. was told that supply was restored…
Outage | J.E.26.08.31975 | C001897109 | Oshane Warren | St.Elizabeth | Completed | Load_557806 | Maggotty - 110 | 2026-08-22 07:37 | 2026-08-22 07:38 | 2026-08-22 11:18 | 2026-08-22 11:18 | 2026-08-22 11:18 | 2026-08-22 11:18 | 2026-08-22 11:19 | 2026-08-22 11:19 |  |  | Fair | No | Customer states that he didn’t make any report
Outage | J.E.26.08.33181 | C001897110 | Christopher Edwards | KSAN | Completed | Load_239844 | Constant Spring - 210 | 2026-08-22 07:37 | 2026-08-22 07:45 | 2026-08-22 09:35 | 2026-08-22 09:36 | 2026-08-22 09:42 | 2026-08-22 10:00 | 2026-08-22 10:01 | 2026-08-22 10:01 |  |  | Fair | No | Remake burnt phase joint at poleUsing (2) one bolt clamps Voltage:116,115,230v
Outage | J.E.26.08.33369 | C001897108 | Christopher Edwards | KSAN | Completed | Load_242513 | Washington Blvd - 510 | 2026-08-22 07:37 | 2026-08-22 07:49 | 2026-08-22 09:38 | 2026-08-22 10:01 | 2026-08-22 10:01 | 2026-08-22 10:01 | 2026-08-22 10:01 | 2026-08-22 10:01 |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Non-Outage | J.E.26.08.30440 | C001897114 | Tajay Bernard | Hanover | Completed | Load_269776 | Orange Bay - 310 | 2026-08-22 07:38 | 2026-08-22 07:40 | 2026-08-22 09:04 | 2026-08-22 09:05 | 2026-08-22 09:30 | 2026-08-22 09:39 | 2026-08-22 09:50 | 2026-08-22 09:50 | Fire |  | Fair | No | Premises check and found okay, no visible occurrence of fire on the lineVoltage found 117/118/235
Non-Outage | J.E.26.08.32544 | C001897113 | Tajay Bernard | Hanover | Completed | Load_240310 | Orange Bay - 310 | 2026-08-22 07:38 | 2026-08-22 07:40 | 2026-08-22 08:50 | 2026-08-22 08:51 | 2026-08-22 08:54 | 2026-08-22 09:03 | 2026-08-22 09:03 | 2026-08-22 09:03 | Fire |  | Fair | No | Area check and found okay no broken wire was found nor any visible occurrence of fire on the line
Non-Outage | J.E.26.08.33034 | C001897116 | Hartley Chin |  | Completed |  |  | 2026-08-22 07:38 | 2026-08-22 07:41 | 2026-08-22 12:02 | 2026-08-22 17:55 | 2026-08-22 17:54 | 2026-08-22 17:54 | 2026-08-22 17:55 | 2026-08-22 17:55 |  |  | Fair | No | Prem not found .. unable t contact customer with contact # provided..
Non-Outage | J.E.26.08.33338 | C001897112 | Tajay Bernard |  | Completed |  |  | 2026-08-22 07:38 | 2026-08-22 07:40 | 2026-08-22 09:07 | 2026-08-22 09:51 | 2026-08-22 09:50 | 2026-08-22 09:51 | 2026-08-22 09:52 | 2026-08-22 09:52 | Fire |  | Fair | No | This calll belongs to st james
Outage | J.E.26.08.31916 | C001897115 | Wayne Dillion | St.Elizabeth | Completed | Load_250909 | Maggotty - 110 | 2026-08-22 07:38 | 2026-08-22 07:39 | 2026-08-22 16:24 | 2026-08-22 16:24 | 2026-08-22 16:24 | 2026-09-03 16:24 | 2026-08-22 16:26 | 2026-08-22 16:26 |  |  | Fair | No | Customer said supply was restored okay.
Outage | J.E.26.08.31277 | C001897117 | Wayne Dillion | St.Elizabeth | Completed | Load_244009 | Maggotty - 110 | 2026-08-22 07:39 | 2026-08-22 07:39 | 2026-08-22 16:28 | 2026-08-22 16:28 | 2026-08-22 16:28 | 2026-08-22 16:28 | 2026-08-22 16:32 | 2026-08-22 16:32 |  |  | Fair | No | Customer said supply was restored.
Outage | J.E.26.08.32804 | C001897124 | Hartley Chin | Clarendon | Completed | Load_266041 | May Pen - 110 | 2026-08-22 07:39 | 2026-08-22 07:41 | 2026-08-22 08:22 | 2026-08-22 08:22 | 2026-08-22 09:04 | 2026-08-22 09:14 | 2026-08-22 09:14 | 2026-08-22 09:14 |  |  | Fair | No | Found okay … voltage read 112v , 113v ..
Outage | J.E.26.08.32857 | C001897119 | Hartley Chin | Clarendon | Completed | Load_1000142 | May Pen - 110 | 2026-08-22 07:39 | 2026-08-22 07:41 | 2026-08-22 08:58 | 2026-08-22 09:15 | 2026-08-22 09:35 | 2026-08-22 09:35 | 2026-08-22 09:35 | 2026-08-22 09:35 |  |  | Fair | No | Found okay .. customer stated issue was resolved..
Outage | J.E.26.08.32895 | C001897123 | Tajay Bernard | Hanover | Completed | Load_292056 | Orange Bay - 310 | 2026-08-22 07:39 | 2026-08-22 07:56 | 2026-08-22 08:47 | 2026-08-22 08:48 | 2026-08-22 08:47 | 2026-08-22 08:50 | 2026-08-22 08:50 | 2026-08-22 08:50 |  |  | Fair | No | Related to previous call job number 33367
Outage | J.E.26.08.33315 | C001897122 | Tajay Bernard | Hanover | Completed | Load_303137 | Orange Bay - 210 | 2026-08-22 07:39 | 2026-08-22 07:40 | 2026-08-22 11:53 | 2026-08-22 11:53 | 2026-08-22 11:53 | 2026-08-22 11:53 | 2026-08-22 11:54 | 2026-08-22 11:54 |  |  | Fair | No | Related to previous call job number 33318
Outage | J.E.26.08.33318 | C001897121 | Tajay Bernard | Hanover | Completed | Load_303135 | Orange Bay - 210 | 2026-08-22 07:39 | 2026-08-22 07:40 | 2026-08-22 09:52 | 2026-08-22 09:52 | 2026-08-22 11:22 | 2026-08-22 11:47 | 2026-08-22 11:48 | 2026-08-22 11:48 |  |  | Fair | No | Refuse a 20,15 and a 10amp junction fuse
Outage | J.E.26.08.33360 | C001897120 | Tajay Bernard | Hanover | Completed | Load_303134 | Orange Bay - 210 | 2026-08-22 07:39 | 2026-08-22 07:40 | 2026-08-22 11:50 | 2026-08-22 11:50 | 2026-08-22 11:50 | 2026-08-22 11:50 | 2026-08-22 11:50 | 2026-08-22 11:50 |  |  | Fair | No | Related to previous call job number 33318
Outage | J.E.26.08.33367 | C001897118 | Tajay Bernard | Hanover | Completed | Load_295102 | Orange Bay - 310 | 2026-08-22 07:39 | 2026-08-22 07:40 | 2026-08-22 08:01 | 2026-08-22 08:01 | 2026-08-22 08:09 | 2026-08-22 08:45 | 2026-08-22 08:47 | 2026-08-22 08:47 |  |  | Fair | No | Isolate 1 50kva Transformer to remake transformer drop leed that was burned off. 1 clamp was usedVoltage found 114Voltage left 114/114/228
Outage | J.E.26.08.32723 | C001897126 | Kenroy Dale | Manchester | Completed | Load_244824 | Kendal - 210 | 2026-08-22 07:45 | 2026-08-22 07:46 | 2026-08-22 18:05 | 2026-08-22 18:20 | 2026-08-22 19:41 | 2026-08-22 20:48 | 2026-08-22 20:51 | 2026-08-22 20:51 |  |  | Fair | No | Open 25 kva transformer to retention 2 span of secondary phase and one span of neutral that was banging and causing fire. Spacer was also applied and transformer re-closed and area now safe
Outage | J.E.26.08.33357 | C001897127 | Wan Carlos Scarlett | St.Catherine | Completed | Load_251518 | Twickenham - 210 | 2026-08-22 07:45 | 2026-08-22 07:47 | 2026-08-22 07:59 | 2026-08-22 07:59 | 2026-08-22 09:12 | 2026-08-22 09:13 | 2026-08-22 09:14 | 2026-08-22 09:14 | LowHangingWires |  | Fair | No | Reach on location been calling customer but got no answer premises closed
Outage | J.E.26.08.32169 | C001897128 | Kenroy Dale | Manchester | Completed | Load_259930 | Kendal - 210 | 2026-08-22 07:46 | 2026-08-22 07:46 | 2026-08-22 11:32 | 2026-08-22 11:42 | 2026-08-22 13:00 | 2026-08-22 13:14 | 2026-08-22 13:18 | 2026-08-22 13:18 |  |  | Fair | No | No service wire found at premises, service wire was replaced with approximately 40 feet of #6 triplex and 3 one bolt clamp voltage reading 111/114/226
Outage | J.E.26.08.32732 | C001897132 | Derrick Dawkins | St.James | Completed | Load_575159 | Bogue - 310 | 2026-08-22 07:54 | 2026-08-22 07:56 | 2026-08-22 11:01 | 2026-08-22 13:10 | 2026-08-22 13:10 | 2026-08-22 13:12 | 2026-08-22 13:12 | 2026-08-22 13:12 |  |  | Fair | No | Only customer without light in the hexing box box #05614
Non-Outage | J.E.26.08.32738 | C001897134 | Milton Charlton | KSAN | Completed | Load_256251 | Hope - 510 | 2026-08-22 07:55 | 2026-08-22 07:56 | 2026-08-22 09:39 | 2026-08-22 09:39 | 2026-08-22 12:15 | 2026-08-22 11:20 | 2026-08-22 12:24 | 2026-08-22 12:24 |  |  | Fair | No | Isolate 15 kva transformer at pole #0110477 and change 1- bolt clamps on transformer neutral drop lead using two 1- bolt clamps. Readings at transformer drop lead using 115-116-231 volts.
Non-Outage | J.E.26.08.32753 | C001897133 | Milton Charlton | KSAN | Completed | Load_578840 | Hope - 510 | 2026-08-22 07:55 | 2026-08-22 07:56 | 2026-08-22 09:03 | 2026-08-22 09:04 | 2026-08-22 09:34 | 2026-08-22 09:35 | 2026-08-22 09:37 | 2026-08-22 09:37 | LowHangingWires |  | Fair | No | Low hanging wire belongs to cable company.
Outage | J.E.26.08.29968 | C001897135 | Derrick Dawkins | St.James | Completed | Load_1002485 | Bogue - 310 | 2026-08-22 07:55 | 2026-08-22 07:56 | 2026-08-22 10:10 | 2026-08-22 10:24 | 2026-08-22 10:52 | 2026-08-22 11:00 | 2026-08-22 11:00 | 2026-08-22 11:00 |  |  | Fair | No | Customer complained about street light not working
Outage | J.E.26.08.30990 | C001897136 | Horace Malcolm | St.James | Completed | Load_576009 | Bogue - 310 | 2026-08-22 07:55 | 2026-08-23 10:28 | 2026-08-23 12:41 | 2026-08-23 12:41 | 2026-08-23 12:44 | 2026-08-23 12:52 | 2026-08-23 12:52 | 2026-08-23 12:52 |  |  | Fair | No | Call customer,customer say supply ress
Non-Outage | J.E.26.08.33255 | C001897137 | Edward Royal |  | Completed |  |  | 2026-08-22 07:56 | 2026-08-22 07:57 | 2026-08-22 09:27 | 2026-08-22 09:27 | 2026-08-22 09:27 | 2026-08-22 09:29 | 2026-08-22 09:29 | 2026-08-22 09:29 |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.08.32143 | C001897141 | Derrick Dawkins | St.James | Completed | Load_241769 | Queens Drive - 310 | 2026-08-22 07:57 | 2026-08-22 08:09 | 2026-08-22 08:30 | 2026-08-22 10:22 | 2026-08-22 10:22 | 2026-08-22 10:27 | 2026-08-22 10:23 | 2026-08-22 10:23 |  |  | Fair | No | Calls to customer went unanswered cannot locate
Outage | J.E.26.08.33293 | C001897140 | Derrick Dawkins | St.James | Completed | Load_251375 | Bogue - 310 | 2026-08-22 07:57 | 2026-08-22 07:58 | 2026-08-22 08:32 | 2026-08-22 08:32 | 2026-08-22 09:47 | 2026-08-22 10:08 | 2026-08-22 10:09 | 2026-08-22 10:09 |  |  | Fair | No | Found 50 kva transformer fuse blown 4 amp due to vehicle accident banging of secondary wire replaced 4 amp transformer fuse
Outage | J.E.26.08.33375 | C001897138 | Horace Malcolm | St.James | Completed | Load_247836 | Queens Drive - 710 | 2026-08-22 07:57 | 2026-08-22 07:59 | 2026-08-22 08:16 | 2026-08-22 08:16 | 2026-08-22 08:47 | 2026-08-22 09:35 | 2026-08-22 09:35 | 2026-08-22 09:35 |  |  | Fair | No | Isolate one 100kva transformer to splice and retention one pole span secondary phase used 20ft #2 conductor and one clamp voltage 115-116-231
Non-Outage | J.E.26.08.32231 | C001897143 | Wayne Dillion |  | Completed |  |  | 2026-08-22 07:58 | 2026-08-22 08:04 | 2026-08-22 12:12 | 2026-08-22 12:12 | 2026-08-22 13:08 | 2026-08-22 14:33 | 2026-08-22 14:35 | 2026-08-22 14:35 | Fire |  | Fair | No | Supply check and found voltage reading 100v, 138v. Further checks reveals that the secondary neutral conductor jumper burnt off. Repair same using two clamps. Supply restored to the area with voltage reading 120v, 120v and cross phase 240volts.
Outage | J.E.26.08.32830 | C001897144 | Edward Royal | KSAS | Completed | Load_289123 | Greenwich - 710 | 2026-08-22 07:59 | 2026-08-22 08:00 | 2026-08-22 08:28 | 2026-08-22 08:29 | 2026-08-22 09:09 | 2026-08-22 09:26 | 2026-08-22 09:27 | 2026-08-22 09:27 |  |  | Fair | No | Replaced 3A transformer fuse
Non-Outage | J.E.26.08.32295 | C001897152 | Marlon Authors |  | Completed |  |  | 2026-08-22 08:00 | 2026-08-22 08:01 | 2026-08-22 09:31 | 2026-08-22 09:31 | 2026-08-22 09:31 | 2026-08-22 09:32 | 2026-08-22 09:32 | 2026-08-22 09:32 | BangingWires |  | Fair | No | Customer said supply was restored
Outage | J.E.26.08.32437 | C001897153 | Romeo Brissett | St.James | Completed | Load_1001851 | Bogue - 510 | 2026-08-22 08:04 | 2026-08-22 08:08 | 2026-08-22 09:34 | 2026-08-22 10:31 | 2026-08-22 11:20 | 2026-08-22 11:00 | 2026-08-22 11:36 | 2026-08-22 11:36 |  |  | Fair | No | Cut and removed vegetation and replaced (1)50kva transformer fuse.
Outage | J.E.26.08.32162 | C001897156 | Marlon Authors | St.Elizabeth | Completed | Load_267211 | Maggotty - 210 | 2026-08-22 08:05 | 2026-08-22 08:05 | 2026-08-22 10:11 | 2026-08-22 10:11 | 2026-08-22 11:03 | 2026-08-22 11:20 | 2026-08-22 11:21 | 2026-08-22 11:21 |  |  | Fair | No | Customer supply was disconnected for none payment m#3008391
Outage | J.E.26.08.32950 | C001897157 | Marlon Authors | St.Elizabeth | Completed | Load_248070 | Maggotty - 210 | 2026-08-22 08:05 | 2026-08-22 08:06 | 2026-08-22 11:21 | 2026-08-22 11:21 | 2026-08-22 13:00 | 2026-08-22 13:06 | 2026-08-22 13:06 | 2026-08-22 13:06 | Fire |  | Fair | No | Patrol and found one 35 feet wooden DV pole with overhead guy broken off at the foot caused by vehicle accident, the 30 feet overhead guy pole also needs to be replaced as the foot is almost burnt off by fire. Retention two poles spans of secondary neutral and replace one blown 2 amp fuse that protects 25 kva transformer circuit no pole #. Restored supply okay. Please refer same to the maintenance department for further assistance
Outage | J.E.26.08.33184 | C001897158 | Rusean Allen | KSAS | Completed | Load_249574 | Cane River - 310 | 2026-08-22 08:05 | 2026-08-22 08:09 | 2026-08-22 11:06 | 2026-08-22 11:07 | 2026-08-22 11:06 | 2026-08-22 11:07 | 2026-08-22 11:07 | 2026-08-22 11:07 |  |  | Fair | No | Premises okay
Outage | J.E.26.08.33331 | C001897154 | Romeo Brissett | St.James | Completed | Load_246289 | Bogue - 610 | 2026-08-22 08:05 | 2026-08-22 08:08 | 2026-08-22 13:25 | 2026-08-22 13:25 | 2026-08-22 13:25 | 2026-08-22 13:20 | 2026-08-22 13:26 | 2026-08-22 13:26 |  |  | Fair | No | Customer was call and she said power restored
Outage | J.E.26.08.33366 | C001897155 | Romeo Brissett | St.James | Completed | Load_292474 | Bogue - 610 | 2026-08-22 08:05 | 2026-08-22 08:08 | 2026-08-22 13:22 | 2026-08-22 13:23 | 2026-08-22 13:22 | 2026-08-22 13:18 | 2026-08-22 13:24 | 2026-08-22 13:24 |  |  | Fair | No | Line patrolled and found clear and safe to energize, replaced (1)15amps junction fuse and (1)8amps junction fuse.
Outage | J.E.26.08.29460 | C001897160 | Romeo Brissett | St.James | Completed | Load_260374 | Bogue - 610 | 2026-08-22 08:06 | 2026-08-22 08:08 | 2026-08-22 16:04 | 2026-08-22 16:04 | 2026-08-22 16:04 | 2026-08-22 16:00 | 2026-08-22 16:11 | 2026-08-22 16:11 |  |  | Fair | No | Found customer service wire dislodged and missed due to hurricane Melissa, installed 30ft of #6 and 4 clamps, V/R 107-105-213
Outage | J.E.26.08.32527 | C001897161 | Marlon Authors | St.Elizabeth | Completed | Load_292267 | Maggotty - 210 | 2026-08-22 08:06 | 2026-08-22 08:08 | 2026-08-22 09:11 | 2026-08-22 09:11 | 2026-08-22 09:11 | 2026-08-22 09:22 | 2026-08-22 09:22 | 2026-08-22 09:22 |  |  | Fair | No | Customer supply was disconnected for none payment
Outage | J.E.26.08.32706 | C001897159 | Rusean Allen | KSAS | Completed | Load_240364 | Cane River - 410 | 2026-08-22 08:06 | 2026-08-22 08:09 | 2026-08-22 10:02 | 2026-08-22 10:03 | 2026-08-22 11:05 | 2026-08-22 11:06 | 2026-08-22 11:06 | 2026-08-22 11:06 |  |  | Fair | No | Customer phone went unanswered
Outage | J.E.26.08.33373 | C001897162 | Rusean Allen | KSAS | Completed | Load_266429 | Up Park Camp - 510 | 2026-08-22 08:06 | 2026-08-22 08:19 | 2026-08-22 09:19 | 2026-08-22 09:19 | 2026-08-22 09:45 | 2026-08-22 09:51 | 2026-08-22 09:51 | 2026-08-22 09:51 |  |  | Fair | No | Found a 30 amps fuse Replace a 30 amps fuse Found a15 amp fuse Replaced a 15 amps fuse
Non-Outage | J.E.26.08.31665 | C001897164 | Romeo Brissett |  | Completed |  |  | 2026-08-22 08:11 | 2026-08-22 08:12 | 2026-08-22 08:30 | 2026-08-22 08:31 | 2026-08-22 09:25 | 2026-08-22 09:28 | 2026-08-22 09:34 | 2026-08-22 09:34 |  |  | Fair | No | Check and found rammy box issue, customer was reconnected by an escalation technician.
Non-Outage | J.E.26.08.32668 | C001897166 | Derrick Dawkins |  | Completed |  |  | 2026-08-22 08:11 | 2026-08-22 08:12 | 2026-08-22 08:30 | 2026-08-22 13:16 | 2026-08-22 13:16 | 2026-08-22 13:19 | 2026-08-22 13:16 | 2026-08-22 13:16 |  |  | Fair | No | Premises ok
Non-Outage | J.E.26.08.33327 | C001897167 | Romeo Brissett |  | Completed |  |  | 2026-08-22 08:11 | 2026-08-22 08:12 | 2026-08-22 13:26 | 2026-08-22 13:26 | 2026-08-22 13:26 | 2026-08-22 13:26 | 2026-08-22 13:29 | 2026-08-22 13:29 |  |  | Fair | No | Check and found ok
Outage | J.E.26.08.32679 | C001897168 | Rusean Allen | KSAS | Completed | Load_259161 | Cane River - 410 | 2026-08-22 08:11 | 2026-08-22 08:13 | 2026-08-22 09:58 | 2026-08-22 09:59 | 2026-08-22 10:00 | 2026-08-22 10:01 | 2026-08-22 10:01 | 2026-08-22 10:01 |  |  | Fair | No | Meter was reconnected by customer service
Non-Outage | J.E.26.08.28375 | C001897172 | Stephen Taylor |  | Completed |  |  | 2026-08-22 08:13 | 2026-08-22 08:14 | 2026-08-22 12:21 | 2026-08-22 12:22 | 2026-08-22 12:21 | 2026-08-22 12:22 | 2026-08-22 12:23 | 2026-08-22 12:23 | LowHangingWires |  | Fair | No | Contact customer and customer say that power is restored and now okay
Non-Outage | J.E.26.08.29113 | C001897169 | Stephen Taylor |  | Completed |  |  | 2026-08-22 08:13 | 2026-08-22 08:14 | 2026-08-22 13:19 | 2026-08-22 13:19 | 2026-08-22 14:22 | 2026-08-22 14:24 | 2026-08-22 14:24 | 2026-08-22 14:24 | LeaningPole |  | Fair | No | Mango tree need to cut from service wire
Non-Outage | J.E.26.08.29954 | C001897171 | Stephen Taylor | St.Thomas | Completed | Load_240601 | Good Year - 110 | 2026-08-22 08:13 | 2026-08-22 08:14 | 2026-08-22 11:46 | 2026-08-22 12:26 | 2026-08-22 12:26 | 2026-08-22 12:28 | 2026-08-22 12:28 | 2026-08-22 12:28 | LeaningPole |  | Fair | No | The pole is cable and wireless pole not jps
Non-Outage | J.E.26.08.31803 | C001897170 | Stephen Taylor | St.Thomas | Completed | Load_270078 | Lysson - 410 | 2026-08-22 08:13 | 2026-08-22 08:14 | 2026-08-22 16:03 | 2026-08-22 16:04 | 2026-08-22 17:53 | 2026-08-22 17:53 | 2026-08-22 18:06 | 2026-08-22 18:06 | LeaningPole |  | Fair | No | Jps pole lean and need to be straightened primary pole
Non-Outage | J.E.26.08.32009 | C001897173 | Stephen Taylor | St.Thomas | Completed | Load_242945 | Lysson - 410 | 2026-08-22 08:13 | 2026-08-22 08:14 | 2026-08-22 09:12 | 2026-08-22 09:12 | 2026-08-22 11:22 | 2026-08-22 11:22 | 2026-08-22 11:23 | 2026-08-22 11:23 |  |  | Fair | No | Patrol area and area is okay but several calls to single customer and no one answering the phone
Non-Outage | J.E.26.08.24085 | C001897174 | Edward Royal | KSAS | Completed | Load_262317 | Greenwich - 310 | 2026-08-22 08:17 | 2026-08-22 08:18 | 2026-08-22 09:29 | 2026-08-22 09:30 | 2026-08-22 09:29 | 2026-08-22 09:31 | 2026-08-22 09:31 | 2026-08-22 09:31 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.33394 | C001897176 | Hartley Chin | Clarendon | Completed | Load_258999 | Monymusk - 410 | 2026-08-22 08:27 | 2026-08-22 08:29 | 2026-08-22 10:46 | 2026-08-22 10:46 | 2026-08-22 11:00 | 2026-08-22 11:06 | 2026-08-22 11:06 | 2026-08-22 11:06 |  |  | Fair | No | Ref to field service!!! Customer has no supply , back of customer meter is burnt , customer meter # 2491714 … customer requesting an urgent meter change . ..
Non-Outage | J.E.26.08.33213 | C001897180 | Hartley Chin |  | Completed |  |  | 2026-08-22 08:30 | 2026-08-22 09:07 | 2026-08-22 09:20 | 2026-08-22 09:37 | 2026-08-22 10:43 | 2026-08-22 10:44 | 2026-08-22 10:45 | 2026-08-22 10:45 |  |  | Fair | No | Found okay .. Customer stated issue was resolved..
Outage | J.E.26.08.32945 | C001897182 | Donald Cunningham | St.Catherine | Completed | Load_268950 | Tredegar - 510 | 2026-08-22 08:30 | 2026-08-22 08:35 | 2026-08-22 09:09 | 2026-08-22 09:09 | 2026-08-22 10:02 | 2026-08-22 10:04 | 2026-08-22 10:05 | 2026-08-22 10:05 |  |  | Fair | No | Premises closed
Outage | J.E.26.08.33048 | C001897181 | Hartley Chin | St.Catherine | Completed | Load_260335 | Rhodens Pen - 310 | 2026-08-22 08:30 | 2026-08-22 09:04 | 2026-08-22 09:20 | 2026-08-22 10:45 | 2026-08-22 10:45 | 2026-08-22 10:45 | 2026-08-22 10:45 | 2026-08-22 10:45 |  |  | Fair | No | Call related to job # 33213 ..
Outage | J.E.26.08.33309 | C001897179 | Donald Cunningham | St.Catherine | Completed | Load_268816 | Tredegar - 310 | 2026-08-22 08:30 | 2026-08-22 09:05 | 2026-08-22 10:06 | 2026-08-22 10:07 | 2026-08-22 11:05 | 2026-08-22 11:14 | 2026-08-22 11:16 | 2026-08-22 11:16 |  |  | Fair | No | Supply in area customer not reachable
Outage | J.E.26.08.33361 | C001897178 | Richard Nicholas | St.Catherine | Completed | Load_260071 | New Michelton - 210 | 2026-08-22 08:30 | 2026-08-22 08:34 | 2026-08-22 08:46 | 2026-08-22 08:47 | 2026-08-22 10:37 | 2026-08-22 11:33 | 2026-08-22 11:34 | 2026-08-22 11:34 |  |  | Fair | No | Replaced blown 30amp junctions fuse on pole #055517.
Outage | J.E.26.08.33393 | C001897183 | Tajay Bernard | Hanover | Completed | Load_303133 | Orange Bay - 210 | 2026-08-22 08:33 | 2026-08-22 08:44 | 2026-08-22 11:48 | 2026-08-22 11:48 | 2026-08-22 11:48 | 2026-08-22 11:49 | 2026-08-22 11:49 | 2026-08-22 11:49 |  |  | Fair | No | Related to previous call job number 33318
Outage | J.E.26.08.33371 | C001897184 | Damion Reid | Manchester | Completed | Load_251252 | Porus - 310 | 2026-08-22 08:38 | 2026-08-23 07:26 | 2026-08-23 09:28 | 2026-08-23 09:29 | 2026-08-23 10:17 | 2026-08-23 10:47 | 2026-08-23 10:48 | 2026-08-23 10:48 |  |  | Fair | No | Area found ok
Outage | J.E.26.08.30963 | C001897185 | Kenroy Dale | Manchester | Completed | Load_256466 | Kendal - 210 | 2026-08-22 08:40 | 2026-08-22 08:42 | 2026-08-22 14:31 | 2026-08-22 14:31 | 2026-08-22 15:20 | 2026-08-22 15:59 | 2026-08-22 16:01 | 2026-08-22 16:01 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Blown 20 amp junction fuse found line patrol tree branch found on primary contractor switch stick was use to remove tree branch blown fuse replace and area now with supply
Outage | J.E.26.08.33400 | C001897186 | Richard Samuda | Manchester | Completed | Load_244799 | Spur Tree - 310 | 2026-08-22 08:41 | 2026-08-22 08:42 | 2026-08-22 09:15 | 2026-08-22 09:17 | 2026-08-22 09:19 | 2026-08-22 10:04 | 2026-08-22 10:04 | 2026-08-22 10:04 |  |  | Fair | No | Found 25amp jfuse blown patrol line found 25kva transformer blown patrol line found nothing close 25 amp fuse then Transformer customer back to normal
Outage | J.E.26.08.33420 | C001897190 | Richard Nicholas | St.Catherine | Completed | Load_256974 | New Michelton - 210 | 2026-08-22 09:05 | 2026-08-22 09:08 | 2026-08-22 11:35 | 2026-08-22 11:35 | 2026-08-22 12:18 | 2026-08-22 15:39 | 2026-08-22 15:44 | 2026-08-22 15:44 | BrokenWire |  | Fair | No | Splice and retention 4 span of broken single phase primary and secondary phase and neutral.top of the pole split and a part broken off however pole left working temporary.14 clamp,4 preform,20ft if 2/0aac, 20ft #2aac and one splicing sleeve was used to complete the repair.blown 15amp junctions fuse replaced on pole #0130010.
Outage | J.E.26.08.32054 | C001897191 | Wayne Dillion | Manchester | Completed | Load_292330 | Spur Tree - 210 | 2026-08-22 09:06 | 2026-08-22 09:07 | 2026-08-22 09:21 | 2026-08-22 09:21 | 2026-08-22 09:32 | 2026-08-22 09:44 | 2026-08-22 09:46 | 2026-08-22 09:46 |  |  | Fair | No | Patrol found one blown 1amp fuse that protects 25kva transformer circuit no pole #. Replace same and supply restored okay.
Outage | J.E.26.08.29496 | C001897192 | Ricky Hall | St.Catherine | Completed | Load_249525 | Rhodens Pen - 410 | 2026-08-22 09:13 | 2026-08-22 09:14 | 2026-08-22 10:26 | 2026-08-22 10:31 | 2026-08-22 11:20 | 2026-08-22 11:27 | 2026-08-22 11:28 | 2026-08-22 11:28 |  |  | Fair | No | Customer found with supply
Non-Outage | J.E.26.08.32825 | C001897193 | Roxroy Needham | St.Ann | Completed | Load_261460 | Cardiff Hall - 310 | 2026-08-22 09:19 | 2026-08-22 09:20 | 2026-08-22 12:54 | 2026-08-22 13:33 | 2026-08-22 13:49 | 2026-08-22 13:51 | 2026-08-22 13:52 | 2026-08-22 13:52 | BrokenWire |  | Fair | No | Premises found ok cable wire hanging down
Outage | J.E.26.08.33415 | C001897194 | Richard Samuda | Manchester | Completed | Load_244024 | Spur Tree - 310 | 2026-08-22 09:19 | 2026-08-22 09:20 | 2026-08-22 10:16 | 2026-08-22 19:06 | 2026-08-22 20:00 | 2026-08-22 20:01 | 2026-08-22 20:01 | 2026-08-22 20:01 |  |  | Fair | No | Found ok situation was resolved
Non-Outage | J.E.26.08.33449 | C001897196 | Wan Carlos Scarlett | Portmore | Completed | Load_556172 | Naggo Head - 610 | 2026-08-22 09:24 | 2026-08-22 09:28 | 2026-08-22 09:36 | 2026-08-22 09:37 | 2026-08-22 10:48 | 2026-08-22 12:56 | 2026-08-22 12:59 | 2026-08-22 12:59 |  |  | Fair | No | Found 25KVA transformer drop lead wire to secondary line phase and neutral corroded use 4 one bolt clamps at pole readings 115-116-232
Outage | J.E.26.08.33451 | C001897200 | Neville Spencer | Clarendon | Completed | Load_242828 | May Pen - 110 | 2026-08-22 09:31 | 2026-08-22 09:33 | 2026-08-22 13:06 | 2026-08-22 13:07 | 2026-08-22 14:48 | 2026-08-22 15:33 | 2026-08-22 15:37 | 2026-08-22 15:37 | BrokenWire |  | Fair | No | Remade corrded phase and neutral joints at pothead and secondary on 2, wire service used 2, clamps, 2, 6/6 sleeves voltage reading 117 in meter socket.
Outage | J.E.26.08.22845 | C001897201 | Hartley Chin | Clarendon | Completed | Load_257675 | Parnassus - 310 | 2026-08-22 09:35 | 2026-08-22 09:37 | 2026-08-22 12:03 | 2026-08-22 18:01 | 2026-08-22 18:00 | 2026-08-22 18:00 | 2026-08-22 18:02 | 2026-08-22 18:02 | LeaningPole |  | Fair | No | Repair broken service phase found @ service pole … voltage read 112v , 112v …
Outage | J.E.26.08.32589 | C001897205 | Marlon Brown | Trelawny | Completed | Load_256099 | Duncans - 210 | 2026-08-22 09:42 | 2026-08-22 09:43 | 2026-08-22 12:22 | 2026-08-22 12:23 | 2026-08-22 13:45 | 2026-08-22 13:46 | 2026-08-22 13:46 | 2026-08-22 13:46 |  |  | Fair | No | Electricity in the community
Outage | J.E.26.08.32762 | C001897204 | Marlon Brown | Trelawny | Completed | Load_264746 | Duncans - 210 | 2026-08-22 09:42 | 2026-08-22 09:43 | 2026-08-22 13:47 | 2026-08-22 13:47 | 2026-08-22 13:47 | 2026-08-22 14:02 | 2026-08-22 14:02 | 2026-08-22 14:02 |  |  | Fair | No | Found ok customer has electricity.
Outage | J.E.26.08.33041 | C001897207 | Marlon Brown | Trelawny | Completed | Load_262457 | Greenwood - 110 | 2026-08-22 09:42 | 2026-08-22 09:43 | 2026-08-22 14:03 | 2026-08-22 14:03 | 2026-08-22 15:28 | 2026-08-22 15:29 | 2026-08-22 15:29 | 2026-08-22 15:29 |  |  | Fair | No | Unable to locate customer via telephone nor direction
Outage | J.E.26.08.33455 | C001897209 | Elvis Trowers | KSAN | Completed | Load_573771 | Washington Blvd - 310 | 2026-08-22 09:48 | 2026-08-22 09:51 | 2026-08-22 10:59 | 2026-08-22 10:59 | 2026-08-22 12:04 | 2026-08-22 12:05 | 2026-08-22 12:09 | 2026-08-22 12:09 | BrokenWire |  | Fair | No | Found okay upon arrival. Customer has an internal problem. Readings at meter socket 113-114-228 volts.
Non-Outage | J.E.26.08.33437 | C001897210 | Romeo Brissett | St.James | Completed | Load_254515 | Bogue - 510 | 2026-08-22 09:56 | 2026-08-22 09:56 | 2026-08-22 11:36 | 2026-08-22 11:37 | 2026-08-22 11:36 | 2026-08-22 11:40 | 2026-08-22 11:44 | 2026-08-22 11:44 |  |  | Fair | No | Found (2)25KVA transformer isolated, re energized (2)25 kva transformer.
Outage | J.E.26.08.33457 | C001897212 | Richard Samuda | Manchester | Completed | Load_252232 | Spur Tree - 310 | 2026-08-22 10:02 | 2026-08-22 10:03 | 2026-08-22 10:16 | 2026-08-22 10:46 | 2026-08-22 11:20 | 2026-08-22 11:45 | 2026-08-22 11:45 | 2026-08-22 11:45 |  |  | Fair | No | Refer call to field service Customer meter defective meter needs to be replaced voltage 116 ,116 232
Outage | J.E.26.08.33422 | C001897214 | Romaine Roberts | St.Mary | Completed | Load_252410 | Highgate -110 | 2026-08-22 10:04 | 2026-08-22 15:17 | 2026-08-22 19:03 | 2026-08-22 19:03 | 2026-08-22 20:29 | 2026-08-22 20:51 | 2026-08-22 20:51 | 2026-08-22 20:51 |  |  | Fair | No | House fire burn off customer service main from jps pole also service to customer home a day light attention is next also 130 foot of number 6 triplex is needed advise customer to carry out their repairs
Outage | J.E.26.08.33431 | C001897213 | Romaine Roberts | St.Mary | Completed | Load_254109 | Highgate - 210 | 2026-08-22 10:04 | 2026-08-22 15:17 | 2026-08-22 21:32 | 2026-08-22 21:33 | 2026-08-22 22:16 | 2026-08-22 22:16 | 2026-08-22 22:16 | 2026-08-22 22:16 |  |  | Fair | No | Call to phone not reachable
Non-Outage | J.E.26.08.33465 | C001897215 | Horace Malcolm |  | Completed |  |  | 2026-08-22 10:11 | 2026-08-22 10:13 | 2026-08-22 10:27 | 2026-08-22 10:27 | 2026-08-22 10:49 | 2026-08-22 11:07 | 2026-08-22 11:08 | 2026-08-22 11:08 | BrokenWire |  | Fair | No | Check and found no broken in area ,area check and found ok apply voltage reading 113-116-229
Outage | J.E.26.08.33470 | C001897216 | Romeo Brissett | St.James | Completed | Load_292128 | Bogue - 610 | 2026-08-22 10:12 | 2026-08-22 10:14 | 2026-08-22 13:29 | 2026-08-22 13:29 | 2026-08-22 13:29 | 2026-08-22 13:28 | 2026-08-22 13:29 | 2026-08-22 13:29 |  |  | Fair | No | Customer was called and she stated power restored
Outage | J.E.26.08.33387 | C001897218 | Christopher Edwards | KSAN | Completed | Load_239844 | Constant Spring - 210 | 2026-08-22 10:14 | 2026-08-22 10:19 | 2026-08-22 10:41 | 2026-08-22 15:38 | 2026-08-22 15:37 | 2026-08-22 15:38 | 2026-08-22 15:38 | 2026-08-22 15:38 |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Outage | J.E.26.08.33435 | C001897221 | Derrick Dawkins | St.James | Completed | Load_243344 | Bogue - 310 | 2026-08-22 10:19 | 2026-08-22 10:25 | 2026-08-22 12:59 | 2026-08-22 13:07 | 2026-08-22 13:07 | 2026-08-22 13:07 | 2026-08-22 13:08 | 2026-08-22 13:08 |  |  | Fair | No | Premises ok
Outage | J.E.26.08.29334 | C001897222 | Marlon Brown | Trelawny | Completed | Load_255143 | Greenwood - 110 | 2026-08-22 10:24 | 2026-08-22 10:25 | 2026-08-22 10:41 | 2026-08-22 10:43 | 2026-08-22 12:15 | 2026-08-22 12:17 | 2026-08-22 12:17 | 2026-08-22 12:17 | BrokenWire |  | Fair | No | Requires 100ft #6 triplex
Non-Outage | J.E.26.08.31004 | C001897224 | Collin Robinson | Portland | Completed | Load_246094 | Port Antonio - 410 | 2026-08-22 10:34 | 2026-08-22 10:34 | 2026-08-22 11:11 | 2026-08-22 11:11 | 2026-08-22 11:22 | 2026-08-22 11:23 | 2026-08-22 11:24 | 2026-08-22 11:24 |  |  | Fair | No | Premises found with supply
Non-Outage | J.E.26.08.33526 | C001897227 | Milton Charlton | KSAN | Completed | Load_249495 | Hope - 510 | 2026-08-22 11:10 | 2026-08-22 11:11 | 2026-08-22 12:27 | 2026-08-22 12:27 | 2026-08-22 13:06 | 2026-08-22 12:15 | 2026-08-22 13:11 | 2026-08-22 13:11 |  |  | Fair | No | Premises closed. Nobody at home.
Outage | J.E.26.08.33522 | C001897229 | Christopher Edwards | KSAN | Completed | Load_252608 | Washington Blvd - 410 | 2026-08-22 11:12 | 2026-08-22 11:12 | 2026-08-22 15:28 | 2026-08-22 16:38 | 2026-08-22 16:38 | 2026-08-22 16:38 | 2026-08-22 16:39 | 2026-08-22 16:39 |  |  | Fair | No | Check and found okSupply is at the premises
Non-Outage | J.E.26.08.33282 | C001897231 | Christopher Edwards | KSAN | Completed | Load_239844 | Constant Spring - 210 | 2026-08-22 11:15 | 2026-08-22 11:16 | 2026-08-22 11:19 | 2026-08-22 11:20 | 2026-08-22 11:19 | 2026-08-22 11:58 | 2026-08-22 12:41 | 2026-08-22 12:41 |  |  | Fair | No | Remake corroded phase joint at pole Using (1) one bolt clamps Voltage:114,115,230v
Non-Outage | J.E.26.08.33507 | C001897230 | Christopher Edwards | KSAN | Completed | Load_267645 | Constant Spring - 410 | 2026-08-22 11:15 | 2026-08-22 11:16 | 2026-08-22 13:18 | 2026-08-22 13:19 | 2026-08-22 14:33 | 2026-08-22 15:24 | 2026-08-22 15:28 | 2026-08-22 15:28 |  |  | Fair | No | Remake corroded phase joint at pole Using (1) one bolt clamps Voltage:115,114,230v
Outage | J.E.26.08.33535 | C001897233 | Donald Cunningham | St.Catherine | Completed | Load_262711 | Tredegar - 310 | 2026-08-22 11:22 | 2026-08-22 11:24 | 2026-08-22 11:41 | 2026-08-22 11:41 | 2026-08-22 13:00 | 2026-08-22 13:08 | 2026-08-22 13:10 | 2026-08-22 13:10 | BrokenWire |  | Fair | No | Broken stanchion customer advised but leave with a supply
Outage | J.E.26.08.33538 | C001897236 | Wan Carlos Scarlett | KSAS | Completed | Load_254412 | Duhaney - 210 | 2026-08-22 11:32 | 2026-08-22 11:32 | 2026-08-22 20:33 | 2026-08-22 20:34 | 2026-08-22 21:34 | 2026-08-22 21:45 | 2026-08-22 21:52 | 2026-08-22 21:52 |  |  | Fair | No | Reset 10 KVA 13.8 KV transformer after separating phase from neutral that was entangled resulting from a truck that came into contact with conductors.
Outage | J.E.26.08.33493 | C001897237 | Hartley Chin | Clarendon | Completed | Load_242599 | Parnassus - 310 | 2026-08-22 11:33 | 2026-08-22 11:59 | 2026-08-22 12:04 | 2026-08-22 13:21 | 2026-08-22 13:22 | 2026-08-22 13:25 | 2026-08-22 13:27 | 2026-08-22 13:27 | BrokenWire |  | Fair | No | Prem not found .., unable to contact customer with contact # provided…
Outage | J.E.26.08.33496 | C001897238 | Clyde Brown | Clarendon | Completed | Load_252966 | Parnassus - 210 | 2026-08-22 11:33 | 2026-08-23 08:07 | 2026-08-23 10:23 | 2026-08-23 10:24 | 2026-08-23 13:10 | 2026-08-23 12:53 | 2026-08-23 13:17 | 2026-08-23 13:17 | BrokenWire |  | Fair | No | Broken secondary neutral,open 25kva transformer and repair with 2- splicing sleeve,8ft-#2 conductor,1- preform and 1-clamp.
Non-Outage | J.E.26.08.33564 | C001897240 | Christopher Edwards | KSAN | Completed | Load_257120 | Constant Spring - 210 | 2026-08-22 11:34 | 2026-08-22 11:34 | 2026-08-22 12:41 | 2026-08-22 12:41 | 2026-08-22 13:00 | 2026-08-22 13:15 | 2026-08-22 13:18 | 2026-08-22 13:18 | Fire |  | Fair | No | Knife switch is leaking and fire is seen coming from the top of the switch Required further inspection from maintenance crewSupply is in the area
Outage | J.E.26.08.33537 | C001897239 | Hartley Chin | Clarendon | Completed | Load_237777 | Parnassus - 310 | 2026-08-22 11:34 | 2026-08-22 11:59 | 2026-08-22 13:25 | 2026-08-22 14:25 | 2026-08-22 14:33 | 2026-08-22 14:50 | 2026-08-22 14:53 | 2026-08-22 14:53 |  |  | Fair | No | Found blown 5 amp fuse on 25 KVA transformer @ bank of 3 @ pole # 0108590 .. line patrolled and found okay , transformer refused?..
Outage | J.E.26.08.33571 | C001897242 | Raymond Lewis | St.Ann | Completed | Load_260937 | Roaring River - 210 | 2026-08-22 11:47 | 2026-08-22 11:48 | 2026-08-22 14:33 | 2026-08-22 14:34 | 2026-08-22 14:34 | 2026-08-22 14:36 | 2026-08-22 14:36 | 2026-08-22 14:36 | BrokenWire |  | Fair | No | Remade joints at pole 3 wire service
Outage | J.E.26.08.33570 | C001897243 | Delano Gayle | Clarendon | Completed | Load_568396 | May Pen - 110 | 2026-08-22 11:56 | 2026-08-22 15:18 | 2026-08-22 15:32 | 2026-08-22 15:32 | 2026-08-22 17:46 | 2026-08-22 18:18 | 2026-08-22 18:19 | 2026-08-22 18:19 | BrokenPole |  | Fair | No | Broken 35c6 pole with 3 phase primary 5ft crossarm and neutral,T construction isolate line section by opening 3 junction fuses no pole#, NWC pump on Ty Dixon road without supply send call to maintenance
Outage | J.E.26.08.33554 | C001897244 | Richman Whyte | Westmoreland | Completed | Load_240178 | Paradise - 210 | 2026-08-22 12:02 | 2026-08-22 12:06 | 2026-08-22 14:13 | 2026-08-22 14:13 | 2026-08-22 14:13 | 2026-08-22 14:13 | 2026-08-22 14:14 | 2026-08-22 14:14 | Fire |  | Fair | No | Clean corrosion at pat head use 2 service connectors voltage 110 110 220
Outage | J.E.26.08.33569 | C001897245 | Rusean Allen | KSAS | Completed | Load_255355 | Rockfort - 410 | 2026-08-22 12:02 | 2026-08-22 12:03 | 2026-08-22 12:59 | 2026-08-22 13:00 | 2026-08-22 14:23 | 2026-08-22 14:26 | 2026-08-22 14:26 | 2026-08-22 14:26 |  |  | Fair | No | Burnt clamp found at pole, clamp was changed.
Outage | J.E.26.08.33582 | C001897246 | Wan Carlos Scarlett | Portmore | Completed | Load_245024 | Naggo Head - 510 | 2026-08-22 12:03 | 2026-08-22 12:06 | 2026-08-22 12:59 | 2026-08-22 13:00 | 2026-08-22 14:01 | 2026-08-22 14:45 | 2026-08-22 14:46 | 2026-08-22 14:46 |  |  | Fair | No | Found customer 3 wire service at pothead phase and neutral corroded use 3 Penn union at service wire phase and neutral readings 114-114-230
Outage | J.E.26.08.33579 | C001897248 | Marlon Brown | Trelawny | Completed | Load_261256 | Greenwood - 210 | 2026-08-22 12:04 | 2026-08-22 12:05 | 2026-08-22 15:29 | 2026-08-22 15:30 | 2026-08-22 15:54 | 2026-08-22 16:36 | 2026-08-22 16:41 | 2026-08-22 16:41 |  |  | Fair | No | Isolated 3 50kva transformers to repair burnt joint, use 1 pg. clampVoltage found at pothead 245/239/244=415/418/419vVoltage leaving at pothead 245/239/244=415/418/419vOne of the 50kva transformer in the bank which is a trip type is leaking oil, please refer to maintenance personnel to have it checked out.
Outage | J.E.26.08.33587 | C001897247 | Roxroy Needham | St.Ann | Completed | Load_294552 | Cardiff Hall - 210 | 2026-08-22 12:04 | 2026-08-22 12:05 | 2026-08-22 13:53 | 2026-08-22 13:53 | 2026-08-22 14:46 | 2026-08-22 14:56 | 2026-08-22 14:56 | 2026-08-22 14:56 | BrokenWire |  | Fair | No | Premises not found not getting customer on phone
Non-Outage | J.E.26.08.33567 | C001897249 | Wan Carlos Scarlett |  | Completed |  |  | 2026-08-22 12:05 | 2026-08-22 12:06 | 2026-08-22 14:47 | 2026-08-22 14:47 | 2026-08-22 15:00 | 2026-08-22 15:38 | 2026-08-22 15:40 | 2026-08-22 15:40 | BrokenWire |  | Fair | No | Found cable and wireless wire broken on the ground advised customer to contact cable provider for assistance
Outage | J.E.26.08.33555 | C001897251 | Cliton Henry | St.Mary | Completed | Load_351648 | Oracabessa - 110 | 2026-08-22 12:05 | 2026-08-22 12:06 | 2026-08-22 14:41 | 2026-08-22 14:41 | 2026-08-22 16:11 | 2026-08-22 16:30 | 2026-08-22 16:30 | 2026-08-22 16:30 | Fire |  | Fair | No | No fire seen, bathe customer meter socket is locked with a locking band. Kindly refer to Field Service Department to open the locking band to all the customer electrician to check in the meter socket.
Outage | J.E.26.08.33558 | C001897252 | Cliton Henry | St.Mary | Completed | Load_239531 | Oracabessa - 210 | 2026-08-22 12:05 | 2026-08-22 12:06 | 2026-08-22 16:33 | 2026-08-22 16:56 | 2026-08-22 16:56 | 2026-08-22 17:11 | 2026-08-22 17:11 | 2026-08-22 17:11 |  |  | Fair | No | RAMI INFRASTRUCTURE, zero volts found at the customer pothead. Kindly refer to Field Service Department for follow up. HEX 06674 HX 27122011
Outage | J.E.26.08.33591 | C001897250 | Raymond Lewis | St.Ann | Completed | Load_248940 | Ocho Rios - 310 | 2026-08-22 12:05 | 2026-08-22 12:05 | 2026-08-22 17:52 | 2026-08-22 17:52 | 2026-08-22 21:01 | 2026-08-22 21:00 | 2026-08-22 21:06 | 2026-08-22 21:06 |  |  | Fair | No | Refuse and close 20 A junction fuse
Outage | J.E.26.08.33395 | C001897253 | Marlon Authors | St.Elizabeth | Completed | Load_248070 | Maggotty - 210 | 2026-08-22 12:06 | 2026-08-22 14:42 | 2026-08-22 14:59 | 2026-08-22 14:59 | 2026-08-22 14:59 | 2026-08-22 15:01 | 2026-08-22 15:01 | 2026-08-22 15:01 | BrokenPole,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Supply restored to the area
Outage | J.E.26.08.33592 | C001897254 | Daniel Francis | St.Ann | Completed | Load_265457 | Cardiff Hall - 210 | 2026-08-22 12:06 | 2026-08-22 15:14 | 2026-08-22 16:44 | 2026-08-22 16:45 | 2026-08-22 17:41 | 2026-08-22 17:46 | 2026-08-22 17:47 | 2026-08-22 17:47 |  |  | Fair | No
Outage | J.E.26.08.33549 | C001897256 | Richard Samuda | Manchester | Completed | Load_254529 | Spur Tree - 310 | 2026-08-22 12:25 | 2026-08-22 12:27 | 2026-08-22 12:58 | 2026-08-22 12:58 | 2026-08-22 13:44 | 2026-08-22 01:52 | 2026-08-22 13:52 | 2026-08-22 13:52 |  |  | Fair | No | Due to broken poles and line in area site will not able to get back supply until situation remedy and proper authority has already been alerted
Outage | J.E.26.08.33565 | C001897257 | Richard Samuda | Manchester | Completed | Load_268006 | Spur Tree - 310 | 2026-08-22 12:25 | 2026-08-22 12:27 | 2026-08-22 13:57 | 2026-08-22 13:58 | 2026-08-22 14:45 | 2026-08-22 03:15 | 2026-08-22 15:16 | 2026-08-22 15:16 |  |  | Fair | No | Found fuse blown 50 kva transformer patrol replaced fuse customer back to normal
Outage | J.E.26.08.33614 | C001897259 | Daniel Francis | St.Ann | Completed | Load_266511 | Cardiff Hall - 310 | 2026-08-22 12:32 | 2026-08-23 07:42 | 2026-08-23 11:06 | 2026-08-23 11:07 | 2026-08-23 11:18 | 2026-08-23 13:09 | 2026-08-23 13:10 | 2026-08-23 13:10 |  |  | Fair | No | Remade joints at pole voltage 103 /103 206
Outage | J.E.26.08.33637 | C001897260 | Daniel Francis | St.Ann | Completed | Load_258564 | Roaring River - 410 | 2026-08-22 13:02 | 2026-08-22 15:14 | 2026-08-22 15:42 | 2026-08-22 15:42 | 2026-08-22 15:57 | 2026-08-22 16:15 | 2026-08-22 16:15 | 2026-08-22 16:15 |  |  | Fair | No | Disconnected for nonpayment
Outage | J.E.26.08.33617 | C001897261 | Milton Charlton | KSAN | Completed | Load_248124 | Hope - 510 | 2026-08-22 13:03 | 2026-08-22 13:04 | 2026-08-22 16:10 | 2026-08-22 17:58 | 2026-08-22 19:38 | 2026-08-22 19:40 | 2026-08-22 19:43 | 2026-08-22 19:43 |  |  | Fair | No | Found okay upon arrival. Readings at meter socket 119-119-238 volts.
Outage | J.E.26.08.33640 | C001897262 | Milton Charlton | KSAN | Completed | Load_573544 | Hope - 410 | 2026-08-22 13:03 | 2026-08-22 13:04 | 2026-08-22 19:38 | 2026-08-22 19:43 | 2026-08-22 20:11 | 2026-08-22 20:10 | 2026-08-22 20:14 | 2026-08-22 20:14 |  |  | Fair | No | Found okay upon arrival. Readings at meter socket 119-119-238 volts.
Outage | J.E.26.08.33633 | C001897263 | Wan Carlos Scarlett | St.Catherine | Completed | Load_251518 | Twickenham - 210 | 2026-08-22 13:18 | 2026-08-22 13:20 | 2026-08-22 19:02 | 2026-08-22 19:03 | 2026-08-22 19:58 | 2026-08-22 20:28 | 2026-08-22 20:33 | 2026-08-22 20:33 | BrokenWire |  | Fair | No | Found customer 3 wire service with neutral broken off use 2 Penn union and 10ft #6 service neutral reading 115 116 231
Outage | J.E.26.08.33618 | C001897264 | Marlon Authors | St.Elizabeth | Completed | Load_292060 | Maggotty - 210 | 2026-08-22 13:19 | 2026-08-22 13:20 | 2026-08-22 14:04 | 2026-08-22 14:05 | 2026-08-22 14:04 | 2026-08-22 14:08 | 2026-08-22 14:08 | 2026-08-22 14:08 |  |  | Fair | No | Customer said she is the only one without supply, hexing systems in this area. Please refer same to the field services department for further assistance
Outage | J.E.26.08.33600 | C001897266 | Romeo Brissett | St.James | Completed | Load_269279 | Bogue - 310 | 2026-08-22 13:25 | 2026-08-22 15:31 | 2026-08-23 00:35 | 2026-08-23 00:35 | 2026-08-23 02:49 | 2026-08-23 00:32 | 2026-08-23 02:52 | 2026-08-23 02:52 | BrokenWire |  | Fair | No | area was checked and broken wire was found.
Outage | J.E.26.08.33622 | C001897265 | Derrick Dawkins | St.James | Completed | Load_1002484 | Bogue - 310 | 2026-08-22 13:25 | 2026-08-22 13:48 | 2026-08-22 14:40 | 2026-08-22 14:40 | 2026-08-22 15:22 | 2026-08-22 15:25 | 2026-08-22 15:25 | 2026-08-22 15:25 |  |  | Fair | No | Checked and found ok
Outage | J.E.26.08.33609 | C001897267 | Neville Spencer | Clarendon | Completed | Load_251963 | May Pen - 110 | 2026-08-22 13:30 | 2026-08-22 13:34 | 2026-08-22 15:37 | 2026-08-22 15:38 | 2026-08-22 16:08 | 2026-08-22 18:26 | 2026-08-22 18:29 | 2026-08-22 18:29 | BrokenWire |  | Fair | No | Splice and retention broken 3, wire service used 70 ft #6 triplex, 2, clamps 114 117 231 supply restored.
Outage | J.E.26.08.33675 | C001897269 | Hartley Chin | Clarendon | Completed | Load_243050 | Parnassus - 310 | 2026-08-22 13:34 | 2026-08-22 13:36 | 2026-08-22 13:44 | 2026-08-22 13:45 | 2026-08-22 13:56 | 2026-08-22 14:21 | 2026-08-22 14:24 | 2026-08-22 14:24 | BrokenWire |  | SevereWind | No | Isolate 25 KVA transformer @ pole # 0125637 due to broken open secondary phase found in 1 span , repair broken neutral, re-energized transformer… use 40 ft conductor, 2 clamp ..
Outage | J.E.26.08.33641 | C001897270 | Richard Samuda | Manchester | Completed | Load_259187 | Spur Tree - 310 | 2026-08-22 13:36 | 2026-08-22 13:38 | 2026-08-22 17:38 | 2026-08-22 17:39 | 2026-08-22 18:17 | 2026-08-22 19:05 | 2026-08-22 19:05 | 2026-08-22 19:05 |  |  | Fair | No | Found 30 amp junction blown patrol line found nothing replaced fuse customer back to normal
Outage | J.E.26.08.33545 | C001897271 | Wayne Dillion | St.Elizabeth | Completed | Load_230094 | Maggotty - 110 | 2026-08-22 13:46 | 2026-08-22 13:49 | 2026-08-22 16:21 | 2026-08-22 16:21 | 2026-08-22 16:21 | 2026-08-22 16:22 | 2026-08-22 16:24 | 2026-08-22 16:24 |  |  | Fair | No | Please refer this call to the field services department.
Non-Outage | J.E.26.08.32770 | C001897276 | Romeo Brissett |  | Completed |  |  | 2026-08-22 13:50 | 2026-08-22 15:31 | 2026-08-22 23:14 | 2026-08-22 23:14 | 2026-08-23 00:11 | 2026-08-23 00:22 | 2026-08-23 00:33 | 2026-08-23 00:33 |  |  | Fair | No | Customer was found disconnected from rammy service and Customers was reconnected by escalation.
Outage | J.E.26.08.32362 | C001897283 | Tajay Bernard | Hanover | Completed | Load_251315 | Orange Bay - 310 | 2026-08-22 13:50 | 2026-08-22 13:52 | 2026-08-22 14:44 | 2026-08-22 14:45 | 2026-08-22 14:44 | 2026-08-22 14:45 | 2026-08-22 14:45 | 2026-08-22 14:45 |  |  | Fair | No | Customer stated that power was restored
Outage | J.E.26.08.32719 | C001897281 | Tajay Bernard | Hanover | Completed | Load_264390 | Orange Bay - 210 | 2026-08-22 13:50 | 2026-08-22 13:52 | 2026-08-22 15:51 | 2026-08-22 15:51 | 2026-08-22 17:15 | 2026-08-22 17:17 | 2026-08-22 17:17 | 2026-08-22 17:17 |  |  | Fair | No | Premises check and found okay Voltage found 111/111/222
Outage | J.E.26.08.32807 | C001897282 | Tajay Bernard | Hanover | Completed | Load_260075 | Orange Bay - 310 | 2026-08-22 13:50 | 2026-08-22 13:52 | 2026-08-22 14:37 | 2026-08-22 14:37 | 2026-08-22 14:37 | 2026-08-22 14:37 | 2026-08-22 14:38 | 2026-08-22 14:38 |  |  | Fair | No | Customer stated that power was restored, she’s okay now
Outage | J.E.26.08.33407 | C001897280 | Tajay Bernard | Hanover | Completed | Load_260650 | Orange Bay - 210 | 2026-08-22 13:50 | 2026-08-22 13:52 | 2026-08-22 14:36 | 2026-08-22 14:36 | 2026-08-22 14:36 | 2026-08-22 14:37 | 2026-08-22 14:37 | 2026-08-22 14:37 |  |  | Fair | No | Customer stated that power was restored, she’s okay now
Outage | J.E.26.08.33445 | C001897275 | Romeo Brissett | St.James | Completed | Load_267492 | Bogue - 610 | 2026-08-22 13:50 | 2026-08-22 13:51 | 2026-08-22 16:11 | 2026-08-22 16:12 | 2026-08-22 18:33 | 2026-08-22 21:40 | 2026-08-22 21:45 | 2026-08-22 21:45 |  |  | Fair | No | Found low voltage on secondary circuit due to illegal connections and distance of secondary line, Isolated (1)25KVA transformer, removed several illegal connections, retention one span of secondary. Voltage reading 103-104-209. Recommending secondary circuit to be split because transformer circuit is found over loaded. Please send to maintenance.
Outage | J.E.26.08.33487 | C001897279 | Derrick Dawkins | St.James | Completed | Load_244480 | Bogue - 310 | 2026-08-22 13:50 | 2026-08-22 13:51 | 2026-08-22 15:27 | 2026-08-22 15:28 | 2026-08-22 15:38 | 2026-08-22 15:43 | 2026-08-22 15:43 | 2026-08-22 15:43 |  |  | Fair | No | Customer service was reconnected through customer service
Outage | J.E.26.08.33551 | C001897278 | Horace Malcolm | St.James | Completed | Load_254051 | Rose Hall - 210 | 2026-08-22 13:50 | 2026-08-22 13:52 | 2026-08-22 15:01 | 2026-08-22 15:01 | 2026-08-22 15:15 | 2026-08-22 15:58 | 2026-08-22 15:58 | 2026-08-22 15:58 |  |  | Fair | No | Removed vegetables from pole and clean and remake joints at pole used 2clamps voltage 117-120-236
Outage | J.E.26.08.33599 | C001897277 | Horace Malcolm | St.James | Completed | Load_242821 | Bogue - 310 | 2026-08-22 13:50 | 2026-08-23 07:14 | 2026-08-23 07:22 | 2026-08-23 07:22 | 2026-08-23 07:35 | 2026-08-23 07:36 | 2026-08-23 07:36 | 2026-08-23 07:36 |  |  | Fair | No | Call to customer,Customer says supply restored
Non-Outage | J.E.26.08.33654 | C001897285 | Collin Robinson | Portland | Completed | Load_252574 | Port Antonio - 410 | 2026-08-22 13:56 | 2026-08-22 13:57 | 2026-08-22 14:27 | 2026-08-22 14:27 | 2026-08-22 15:04 | 2026-08-22 15:08 | 2026-08-22 15:08 | 2026-08-22 15:08 |  |  | Fair | No | Issue on customer load side . Voltage 115 114 229v
Outage | J.E.26.08.33665 | C001897286 | Daniel Francis | St.Ann | Completed | Load_241902 | Cardiff Hall - 210 | 2026-08-22 13:57 | 2026-08-22 15:14 | 2026-08-22 17:55 | 2026-08-22 17:57 | 2026-08-22 19:26 | 2026-08-22 19:27 | 2026-08-22 19:33 | 2026-08-22 19:33 | BrokenPole |  | Fair | No | Junction leading to premises 187749 down also conducter not able to access fully
Outage | J.E.26.08.33646 | C001897287 | Milton Charlton | KSAN | Completed | Load_269021 | Hope - 510 | 2026-08-22 13:58 | 2026-08-22 13:58 | 2026-08-22 17:22 | 2026-08-22 17:22 | 2026-08-22 17:53 | 2026-08-22 17:50 | 2026-08-22 17:57 | 2026-08-22 17:57 |  |  | Fair | No | Customer service wire #6 triplex phase and neutral burn off in mid-span. Disconnect, lower and splice using 50ft #6 triplex and four 1- bolt clamps and reconnect triplex service wire.
Outage | J.E.26.08.33656 | C001897289 | Milton Charlton | KSAN | Completed | Load_251352 | West Kings House - 310 | 2026-08-22 13:58 | 2026-08-22 19:58 | 2026-08-22 20:14 | 2026-08-22 20:15 | 2026-08-22 20:16 | 2026-08-22 22:10 | 2026-08-22 22:47 | 2026-08-22 22:47 | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Isolate 167kva transformer at pole #(no pole #) repair broken secondary rack fallen from pole. Tie up secondary rack to make it safe and reclosed transformer switch. Secondary need to be transferred to new poleurgently.
Outage | J.E.26.08.33676 | C001897288 | Milton Charlton | KSAN | Completed | Load_251881 | Washington Blvd - 610 | 2026-08-22 13:58 | 2026-08-22 19:58 | 2026-08-22 22:50 | 2026-08-22 22:51 | 2026-08-22 22:50 | 2026-08-22 22:40 | 2026-08-22 22:52 | 2026-08-22 22:52 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.33667 | C001897290 | Marlon Authors | St.Elizabeth | Completed | Load_256668 | Maggotty - 210 | 2026-08-22 13:59 | 2026-08-22 14:00 | 2026-08-22 14:47 | 2026-08-22 14:48 | 2026-08-22 14:47 | 2026-08-22 14:49 | 2026-08-22 14:49 | 2026-08-22 14:49 |  |  | Fair | No | Supply was disconnected for none payment
Outage | J.E.26.08.32590 | C001897291 | Tajay Bernard | Hanover | Completed | Load_265275 | Orange Bay - 310 | 2026-08-22 14:09 | 2026-08-22 14:11 | 2026-08-22 14:45 | 2026-08-22 14:46 | 2026-08-22 15:44 | 2026-08-22 15:50 | 2026-08-22 15:50 | 2026-08-22 15:50 |  |  | Fair | No | Refuse 1 5kva transformer use 1amp fuse
Outage | J.E.26.08.32648 | C001897292 | Tajay Bernard | Hanover | Completed | Load_240292 | Orange Bay - 310 | 2026-08-22 14:09 | 2026-08-22 14:11 | 2026-08-22 17:20 | 2026-08-22 17:20 | 2026-08-22 17:20 | 2026-08-22 17:22 | 2026-08-22 17:22 | 2026-08-22 17:22 |  |  | Fair | No | Unable to get in contact with the customer, multiple phone call to both numbers that was provided went unanswered
Non-Outage | J.E.26.08.33727 | C001897293 | Collin Robinson | Portland | Completed | Load_556159 | Port Antonio - 310 | 2026-08-22 14:27 | 2026-08-22 14:28 | 2026-08-22 18:10 | 2026-08-22 18:10 | 2026-08-22 18:10 | 2026-08-22 18:11 | 2026-08-22 18:11 | 2026-08-22 18:11 |  |  | Fair | No | Issue related to previous job
Outage | J.E.26.08.33739 | C001897296 | Collin Robinson | Portland | Completed | Load_244552 | Port Antonio - 310 | 2026-08-22 14:56 | 2026-08-22 14:57 | 2026-08-22 15:09 | 2026-08-22 15:09 | 2026-08-22 15:49 | 2026-08-22 16:08 | 2026-08-22 16:08 | 2026-08-22 16:08 |  |  | Fair | No | Remove falling breadfruit tree primary conductor and replace 3 amps fuse
Outage | J.E.26.08.33743 | C001897297 | Collin Robinson | Portland | Completed | Load_251087 | Port Antonio - 410 | 2026-08-22 14:56 | 2026-08-22 14:57 | 2026-08-22 16:08 | 2026-08-22 16:09 | 2026-08-22 17:04 | 2026-08-22 17:17 | 2026-08-22 17:18 | 2026-08-22 17:18 |  |  | Fair | No | Change 1 burn one bolt clamp at pole Voltage reading 118v 118v 236v
Outage | J.E.26.08.33744 | C001897299 | Romaine Roberts | St.Mary | Completed | Load_268858 | Highgate -110 | 2026-08-22 14:59 | 2026-08-22 15:16 | 2026-08-22 15:50 | 2026-08-22 15:50 | 2026-08-22 18:51 | 2026-08-22 18:55 | 2026-08-22 19:00 | 2026-08-22 19:00 |  | Y | Fair | No | Tree fall on primary and secondary conductor and burst down 2 span of conductor splice and retention conductor also clear tree from line replace 15 amp power restore
Outage | J.E.26.08.33757 | C001897300 | Javid Vernon | Westmoreland | Completed | Load_292395 | Paradise - 110 | 2026-08-22 15:08 | 2026-08-22 15:10 | 2026-08-22 15:20 | 2026-08-22 15:21 | 2026-08-22 15:49 | 2026-08-22 15:52 | 2026-08-22 15:52 | 2026-08-22 15:52 |  |  | Fair | No | customer stated that power was restored
Outage | J.E.26.08.33732 | C001897301 | Wan Carlos Scarlett | St.Catherine | Completed | Load_579394 | Twickenham - 410 | 2026-08-22 15:11 | 2026-08-22 15:17 | 2026-08-22 17:31 | 2026-08-22 17:31 | 2026-08-22 18:34 | 2026-08-22 18:53 | 2026-08-22 18:59 | 2026-08-22 18:59 |  |  | Fair | No | Customer apply for new installation from hexing service box call refer to field service
Outage | J.E.26.08.33684 | C001897305 | Christopher Edwards | KSAS | Completed | Load_248646 | Duhaney - 310 | 2026-08-22 15:18 | 2026-08-23 11:06 | 2026-08-23 11:10 | 2026-08-23 12:16 | 2026-08-23 12:16 | 2026-08-23 12:21 | 2026-08-23 12:24 | 2026-08-23 12:24 |  |  | Fair | No | Metering department was contacted and stated that field service should go to location to resolve issues
Outage | J.E.26.08.33776 | C001897306 | Wan Carlos Scarlett | Portmore | Completed | Load_570209 | Naggo Head - 610 | 2026-08-22 15:22 | 2026-08-22 15:24 | 2026-08-22 16:05 | 2026-08-22 16:06 | 2026-08-22 17:02 | 2026-08-22 17:29 | 2026-08-22 17:31 | 2026-08-22 17:31 |  |  | Fair | No | Customer got reconnected from escalation department power supply has been restored
Non-Outage | J.E.26.08.32033 | C001897308 | Stephen Taylor | St.Thomas | Completed | Load_264475 | Good Year - 110 | 2026-08-22 15:28 | 2026-08-22 15:30 | 2026-08-22 15:47 | 2026-08-22 18:18 | 2026-08-22 18:46 | 2026-08-22 18:46 | 2026-08-22 18:47 | 2026-08-22 18:47 |  |  | Fair | No | Contact customer and customer say that tomorrow is the best time to visit the premises
Non-Outage | J.E.26.08.32516 | C001897309 | Stephen Taylor | St.Thomas | Completed | Load_242435 | Good Year - 210 | 2026-08-22 15:28 | 2026-08-22 15:30 | 2026-08-23 17:51 | 2026-08-23 17:51 | 2026-08-23 17:51 | 2026-08-23 17:52 | 2026-08-23 17:53 | 2026-08-23 17:53 |  |  | Fair | No | Need better contacts to call this number not working
Outage | J.E.26.08.33621 | C001897310 | Hartley Chin | Clarendon | Completed | Load_252936 | Parnassus - 310 | 2026-08-22 15:29 | 2026-08-22 15:31 | 2026-08-22 16:54 | 2026-08-22 16:54 | 2026-08-22 16:54 | 2026-08-22 16:54 | 2026-08-22 16:56 | 2026-08-22 16:56 |  |  | Fair | No | Wrong Parish… St Ann
Outage | J.E.26.08.33626 | C001897311 | Hartley Chin | Clarendon | Completed | Load_405727 | Parnassus - 210 | 2026-08-22 15:29 | 2026-08-22 15:31 | 2026-08-22 15:50 | 2026-08-22 15:50 | 2026-08-22 16:13 | 2026-08-22 16:41 | 2026-08-22 16:47 | 2026-08-22 16:47 |  |  | Fair | No | Ref to maintenance!!! Defective 50 KVA TRANSFORMER on bank of 3 … X3 bushing completely burnt on lighting transformer … transformer supply power to chicken farm … customer request urgent change of transformer..
Outage | J.E.26.08.33768 | C001897312 | Hartley Chin | Clarendon | Completed | Load_242599 | Parnassus - 310 | 2026-08-22 15:29 | 2026-08-22 15:31 | 2026-08-22 16:59 | 2026-08-22 17:03 | 2026-08-22 17:25 | 2026-08-22 17:27 | 2026-08-22 17:27 | 2026-08-22 17:27 |  |  | Fair | No | Call related to job # 33675
Outage | J.E.26.08.33747 | C001897313 | Floyd Taylor | Trelawny | Completed | Load_266607 | Martha Brae - 110 | 2026-08-22 15:32 | 2026-08-22 15:33 | 2026-08-22 15:58 | 2026-08-22 16:31 | 2026-08-22 16:40 | 2026-08-22 16:40 | 2026-08-22 16:43 | 2026-08-22 16:43 | Fire |  | Fair | No | Customer said that she saw a sparks on a pole on market street, patrolled area No sparks was seen.
Non-Outage | J.E.26.08.31937 | C001897318 | Elvis Trowers | KSAS | Completed | Load_238723 | Rockfort - 410 | 2026-08-22 15:41 | 2026-08-22 15:43 | 2026-08-22 20:11 | 2026-08-22 20:41 | 2026-08-22 20:40 | 2026-08-22 20:45 | 2026-08-22 21:17 | 2026-08-22 21:17 |  |  | Fair | No | Customer service wire #6 triplex neutral corroded at pole. Repair using two 1- bolt clamps. Readings at meter socket 117-118-236 volts.
Non-Outage | J.E.26.08.32147 | C001897317 | Elvis Trowers | KSAN | Completed | Load_268885 | Washington Blvd - 310 | 2026-08-22 15:41 | 2026-08-22 15:43 | 2026-08-22 19:32 | 2026-08-22 19:35 | 2026-08-22 19:39 | 2026-08-22 20:00 | 2026-08-22 20:11 | 2026-08-22 20:11 |  |  | Fair | No | Found okay upon arrival. Customer has an internal problem. Readings at meter socket and pothead. 113-114-228 volts.
Non-Outage | J.E.26.08.33533 | C001897315 | Elvis Trowers | KSAS | Completed | Load_573721 | Up Park Camp - 310 | 2026-08-22 15:41 | 2026-08-22 15:43 | 2026-08-22 21:56 | 2026-08-22 21:57 | 2026-08-22 23:04 | 2026-08-22 23:00 | 2026-08-22 23:05 | 2026-08-22 23:05 |  |  | Fair | No | Unable to locate customer by telephone. Number on the report going straight to voicemail.
Non-Outage | J.E.26.08.33576 | C001897316 | Elvis Trowers |  | Completed |  |  | 2026-08-22 15:41 | 2026-08-22 15:43 | 2026-08-22 21:17 | 2026-08-22 21:18 | 2026-08-22 21:32 | 2026-08-22 21:55 | 2026-08-22 21:56 | 2026-08-22 21:56 | BrokenWire |  | Fair | No | Found okay upon arrival. Loose wires is on a transformer that is no longer action and need to be retired at pole #0111997.
Non-Outage | J.E.26.08.29609 | C001897319 | Elvis Trowers | KSAS | Completed | Load_267391 | Three Miles - 410 | 2026-08-22 15:42 | 2026-08-22 15:43 | 2026-08-22 17:54 | 2026-08-22 17:54 | 2026-08-22 19:24 | 2026-08-22 18:45 | 2026-08-22 19:33 | 2026-08-22 19:33 |  |  | Fair | No | Found okay upon arrival. Customer states matter was resolved.
Non-Outage | J.E.26.08.30106 | C001897320 | Elvis Trowers | KSAS | Completed | Load_293222 | Three Miles - 410 | 2026-08-22 15:42 | 2026-08-22 15:43 | 2026-08-22 18:09 | 2026-08-22 19:33 | 2026-08-22 19:33 | 2026-08-22 19:25 | 2026-08-22 19:34 | 2026-08-22 19:34 |  |  | Fair | No | Found okay upon arrival. Customer states matter was resolved.
Outage | J.E.26.08.31324 | C001897324 | Kenroy Dale | Manchester | Completed | Load_249343 | Kendal - 210 | 2026-08-22 15:49 | 2026-08-22 15:51 | 2026-08-22 23:01 | 2026-08-22 23:01 | 2026-08-23 02:29 | 2026-08-23 02:30 | 2026-08-23 02:33 | 2026-08-23 02:33 |  |  | Fair | No | Blown 20 amp junction fuse found line patrol nothing found customer states that the fuse blown after there was a lightning, blown fuse was replaced and area now with supply
Outage | J.E.26.08.33800 | C001897325 | Elvis Trowers | KSAS | Completed | Load_250310 | Greenwich - 510 | 2026-08-22 15:57 | 2026-08-22 15:58 | 2026-08-22 16:03 | 2026-08-22 16:05 | 2026-08-22 17:45 | 2026-08-22 17:50 | 2026-08-22 17:51 | 2026-08-22 17:51 |  |  | Fair | No | Isolate bank of transformers at pole # 611664 and repair customer service wire #2 triplex phase and neutral come together and burnt off. Repair using seven 1- bolt clamps and 30ft of #2 twisted wire. And reclose transformer switch
Outage | J.E.26.08.33786 | C001897327 | Richard Samuda | Manchester | Completed | Load_255312 | Spur Tree - 310 | 2026-08-22 16:07 | 2026-08-22 16:09 | 2026-08-22 17:36 | 2026-08-22 17:36 | 2026-08-22 17:37 | 2026-08-22 17:38 | 2026-08-22 17:38 | 2026-08-22 17:38 |  |  | Fair | No | Power was restored
Outage | J.E.26.08.33765 | C001897331 | Omar King | St.Ann | Completed | Load_268908 | Cardiff Hall - 310 | 2026-08-22 16:48 | 2026-08-23 01:25 | 2026-08-23 05:01 | 2026-08-23 05:01 | 2026-08-23 05:01 | 2026-08-23 05:01 | 2026-08-23 05:02 | 2026-08-23 05:02 |  |  | Fair | No | Found 25 KVA transformer trip cause by illegal connection as being reset customer is now with supply supply
Non-Outage | J.E.26.08.32233 | C001897337 | Nickolas Rodriques | St.Catherine | Completed | Load_267740 | Tredegar - 410 | 2026-08-22 17:04 | 2026-08-22 17:05 | 2026-08-22 17:32 | 2026-08-22 18:00 | 2026-08-22 18:40 | 2026-08-22 19:12 | 2026-08-22 19:32 | 2026-08-22 19:32 |  |  | Fair | No | Checked and found the tap changer switch burnt and drop lead of a 100 KVA transformer which forms a part of a bank of three transformer burnt and isolated. There was also noticeable oil spewing from it. All three fuses were isolated for safety. Further checks required.
Non-Outage | J.E.26.08.32368 | C001897335 | Richard Nicholas | St.Catherine | Completed | Load_241213 | Twickenham - 310 | 2026-08-22 17:04 | 2026-08-23 09:00 | 2026-08-23 10:05 | 2026-08-23 10:05 | 2026-08-23 10:16 | 2026-08-23 11:42 | 2026-08-23 11:44 | 2026-08-23 11:44 |  |  | Fair | No | Replaced one span of missing secondary neutral.2 preform,100 ft #2aac and 2 one bolt clamp.voltage 3 reading 118x2 and 236v.
Non-Outage | J.E.26.08.32699 | C001897336 | Ricky Hall | St.Catherine | Completed | Load_244132 | Tredegar - 510 | 2026-08-22 17:04 | 2026-08-23 08:59 | 2026-08-23 10:29 | 2026-08-23 10:30 | 2026-08-23 10:44 | 2026-08-23 10:49 | 2026-08-23 10:49 | 2026-08-23 10:49 |  |  | Fair | No | Customer found with supply
Non-Outage | J.E.26.08.32978 | C001897334 | Nickolas Rodriques |  | Completed |  |  | 2026-08-22 17:04 | 2026-08-22 17:05 | 2026-08-22 20:59 | 2026-08-22 21:00 | 2026-08-22 21:46 | 2026-08-22 21:55 | 2026-08-22 22:08 | 2026-08-22 22:08 | Fire |  | Fair | No | Unable to communicate with this specific customer. However, the area was patrolled and no noticeable fire was seen.
Non-Outage | J.E.26.08.33486 | C001897332 | Nickolas Rodriques | St.Catherine | Completed | Load_256615 | Tredegar - 310 | 2026-08-22 17:04 | 2026-08-22 17:05 | 2026-08-22 22:08 | 2026-08-22 22:09 | 2026-08-22 22:28 | 2026-08-22 22:52 | 2026-08-22 22:54 | 2026-08-22 22:54 |  |  | Fair | No | Checked and found customer with unstable voltage caused by defective meter wires and socket. Isolate service wire for safety. The customer was then advised to consult a private electrician to do repairs.
Non-Outage | J.E.26.08.33524 | C001897333 | Nickolas Rodriques | St.Catherine | Completed | Load_264677 | Tredegar - 410 | 2026-08-22 17:04 | 2026-08-22 17:05 | 2026-08-22 20:12 | 2026-08-22 20:13 | 2026-08-22 20:32 | 2026-08-22 20:52 | 2026-08-22 20:59 | 2026-08-22 20:59 |  |  | Fair | No | The customer confirmed that the issue was already resolved by another team.
Non-Outage | J.E.26.08.31070 | C001897338 | Nickolas Rodriques | St.Catherine | Completed | Load_267392 | Tredegar - 410 | 2026-08-22 17:05 | 2026-08-22 17:05 | 2026-08-22 19:32 | 2026-08-22 19:33 | 2026-08-22 19:57 | 2026-08-22 20:04 | 2026-08-22 20:12 | 2026-08-22 20:12 |  |  | Fair | No | Found premises locked. The customer was contacted and stated that she would like to reschedule a team for tomorrow Sunday August 23.
Non-Outage | J.E.26.08.31592 | C001897341 | Delano Gayle | St.Catherine | Completed | Load_288537 | Rhodens Pen - 310 | 2026-08-22 17:05 | 2026-08-22 17:07 | 2026-08-22 21:43 | 2026-08-22 21:44 | 2026-08-22 22:12 | 2026-08-22 22:22 | 2026-08-22 22:22 | 2026-08-22 22:22 |  |  | Fair | No | Premises not found no answer from customer phone
Non-Outage | J.E.26.08.30312 | C001897343 | Delano Gayle | St.Catherine | Completed | Load_569939 | Tredegar - 210 | 2026-08-22 17:06 | 2026-08-22 17:07 | 2026-08-22 18:19 | 2026-08-22 19:40 | 2026-08-22 19:50 | 2026-08-22 19:51 | 2026-08-22 19:52 | 2026-08-22 19:52 |  |  | Fair | No | Premises not found no answer from customer phone
Non-Outage | J.E.26.08.31107 | C001897342 | Delano Gayle | St.Catherine | Completed | Load_255418 | Rhodens Pen - 210 | 2026-08-22 17:06 | 2026-08-22 17:07 | 2026-08-22 19:52 | 2026-08-22 19:53 | 2026-08-22 20:40 | 2026-08-22 20:54 | 2026-08-22 20:54 | 2026-08-22 20:54 |  |  | Fair | No | Broken phase at pole, splice and repair use 3ft #6 phase 1 linket 1 clamp voltage reading 113-112-226
Non-Outage | J.E.26.08.25489 | C001897353 | Donald Cunningham | St.Catherine | Completed | Load_241129 | New Michelton - 210 | 2026-08-22 17:07 | 2026-08-22 17:08 | 2026-08-22 19:35 | 2026-08-22 19:35 | 2026-08-22 20:10 | 2026-08-22 20:11 | 2026-08-22 20:15 | 2026-08-22 20:15 |  |  | Fair | No | Premises closed
Non-Outage | J.E.26.08.25900 | C001897354 | Donald Cunningham | St.Catherine | Completed | Load_241129 | New Michelton - 210 | 2026-08-22 17:07 | 2026-08-22 17:08 | 2026-08-22 17:22 | 2026-08-22 17:22 | 2026-08-22 19:29 | 2026-08-22 19:32 | 2026-08-22 19:35 | 2026-08-22 19:35 |  |  | Fair | No | Issues already resolved
Non-Outage | J.E.26.08.29478 | C001897351 | Donald Cunningham | St.Catherine | Completed | Load_268156 | New Michelton - 210 | 2026-08-22 17:07 | 2026-08-22 17:08 | 2026-08-22 20:15 | 2026-08-22 20:16 | 2026-08-22 20:58 | 2026-08-22 21:01 | 2026-08-22 21:02 | 2026-08-22 21:02 |  |  | Fair | No | Premises not located customer not reachable
Non-Outage | J.E.26.08.33399 | C001897355 | Floyd Taylor | Trelawny | Completed | Load_264734 | Greenwood - 110 | 2026-08-22 17:12 | 2026-08-22 17:13 | 2026-08-22 18:15 | 2026-08-22 18:15 | 2026-08-22 19:19 | 2026-08-22 20:43 | 2026-08-22 20:43 | 2026-08-22 20:43 |  |  | Fair | No | Clean and remake joints at pole also clean and remake secondary neutral jumper voltage readings 116,115,232
Non-Outage | J.E.26.08.33483 | C001897356 | Dwayne Samuels | Trelawny | Completed | Load_262457 | Greenwood - 110 | 2026-08-22 17:12 | 2026-08-23 07:57 | 2026-08-23 13:50 | 2026-08-23 13:51 | 2026-08-23 14:22 | 2026-08-23 14:42 | 2026-08-23 14:43 | 2026-08-23 14:43 |  |  | Fair | No | Defective number 2 service wire carry out a temporary jumper for customer neutral wire voltage found on arrival 88v/119v/236v voltage left 113v/125v/238v refer to field service team
Outage | J.E.26.08.33793 | C001897361 | Hartley Chin | Clarendon | Completed | Load_250072 | May Pen - 210 | 2026-08-22 17:38 | 2026-08-22 17:39 | 2026-08-22 18:38 | 2026-08-22 18:41 | 2026-08-22 19:33 | 2026-08-22 19:43 | 2026-08-22 19:51 | 2026-08-22 19:51 |  |  | Fair | No | Ref to maintenance!!! Found defective 25 KVA transformer @ pole # 0125898 causing customers to single phase … voltage read found on 1 bushing 10v , voltage read found on X3 bushing 117v .. observed X1 bushing leaking excessive oil … ref to maintenance!!! MAINTENANCE TO REPALCE 25 KVA transformer causing approximately 35 customers to single phase ..
Outage | J.E.26.08.33833 | C001897362 | Hartley Chin | Clarendon | Completed | Load_266602 | May Pen - 210 | 2026-08-22 17:38 | 2026-08-22 17:39 | 2026-08-22 18:02 | 2026-08-22 18:03 | 2026-08-22 18:27 | 2026-08-22 18:34 | 2026-08-22 18:37 | 2026-08-22 18:37 |  |  | Fair | No | Found 1 of 3 junction (20 amp) open due to drop-out switch being slack , remove fuse barrel.. junction string fused ..
Outage | J.E.26.08.33860 | C001897363 | Hartley Chin | Clarendon | Completed | Load_242545 | Parnassus - 210 | 2026-08-22 17:38 | 2026-08-22 17:39 | 2026-08-22 18:40 | 2026-08-22 20:41 | 2026-08-22 21:21 | 2026-08-22 22:25 | 2026-08-22 22:25 | 2026-08-22 22:25 |  |  | Fair | No | Replace 90ft service wire … use 4 clamp …
Outage | J.E.26.08.32590 | C001897365 | Tajay Bernard | Hanover | Completed | Load_265275 | Orange Bay - 310 | 2026-08-22 18:05 | 2026-08-22 18:07 | 2026-08-22 20:24 | 2026-08-22 20:24 | 2026-08-22 20:49 | 2026-08-22 20:50 | 2026-08-22 20:50 | 2026-08-22 20:50 |  |  | Fair | No | Customer stated that power was restored
Non-Outage | J.E.26.08.32872 | C001897366 | Tajay Bernard | Hanover | Completed | Load_265958 | Orange Bay - 310 | 2026-08-22 18:08 | 2026-08-22 18:09 | 2026-08-22 20:05 | 2026-08-22 20:06 | 2026-08-22 20:09 | 2026-08-22 20:22 | 2026-08-22 20:23 | 2026-08-22 20:23 |  |  | Fair | No | Customer has internal problems, customer was advised Voltage found 110/108/218
Non-Outage | J.E.26.08.32952 | C001897367 | Tajay Bernard | Hanover | Completed | Load_265958 | Orange Bay - 310 | 2026-08-22 18:08 | 2026-08-22 18:09 | 2026-08-22 18:40 | 2026-08-22 18:41 | 2026-08-22 19:19 | 2026-08-22 20:04 | 2026-08-22 20:05 | 2026-08-22 20:05 |  |  | Fair | No | Clean and remake jumper at jps pole use use 1 clamp Voltage found 111Voltage left 111/112/223
Outage | J.E.26.08.33915 | C001897370 | Romeo Brissett | St.James | Completed | Load_250986 | Bogue - 510 | 2026-08-22 18:32 | 2026-08-22 21:28 | 2026-08-22 21:46 | 2026-08-22 21:46 | 2026-08-22 21:59 | 2026-08-22 22:00 | 2026-08-22 22:00 | 2026-08-22 22:00 | Fire |  | Fair | No | Customer requested daylight attention.
Outage | J.E.26.08.32768 | C001897371 | Christopher Edwards | KSAN | Completed | Load_255617 | Constant Spring - 210 | 2026-08-22 18:50 | 2026-08-22 18:51 | 2026-08-22 19:03 | 2026-08-22 19:28 | 2026-08-22 19:52 | 2026-08-22 20:22 | 2026-08-22 20:32 | 2026-08-22 20:32 | BrokenWire |  | Fair | No | Customer got someone to reattach the broken wireHowever customer want someone from JPS to check the connections Customer is not at the premises to give access to premises
Outage | J.E.26.08.33936 | C001897372 | Wayne Dillion | Manchester | Completed | Load_251650 | Spur Tree - 210 | 2026-08-22 18:53 | 2026-08-22 18:57 | 2026-08-22 19:57 | 2026-08-22 19:57 | 2026-08-22 19:57 | 2026-08-22 19:58 | 2026-08-22 19:59 | 2026-08-22 19:59 |  |  | Fair | No | Customer is disconnected due to none payment of bill. Meter#2782609.
Outage | J.E.26.08.33891 | C001897373 | Javid Vernon | Westmoreland | Completed | Load_257812 | Paradise - 110 | 2026-08-22 18:57 | 2026-08-22 18:58 | 2026-08-22 19:14 | 2026-08-22 19:14 | 2026-08-22 20:27 | 2026-08-22 21:07 | 2026-08-22 21:08 | 2026-08-22 21:08 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Isolate one 50 kva transformer to remove illegal connection to splice and retention one pole span of secondary phase use 10ft #2 conductor 4 clamps and reclose 50 kva transformer
Outage | J.E.26.08.33951 | C001897374 | Javid Vernon | Westmoreland | Completed | Load_249422 | Paradise - 210 | 2026-08-22 18:57 | 2026-08-22 18:58 | 2026-08-22 21:08 | 2026-08-22 21:08 | 2026-08-22 21:51 | 2026-08-22 22:18 | 2026-08-22 22:19 | 2026-08-22 22:19 |  |  | Fair | No | Refuse one 25kva transformer use 3amp fuse
Non-Outage | J.E.26.08.25269 | C001897375 | Cliton Henry | St.Mary | Completed | Load_266413 | Oracabessa - 210 | 2026-08-22 18:58 | 2026-08-22 18:59 | 2026-08-22 19:42 | 2026-08-22 19:43 | 2026-08-22 20:06 | 2026-08-22 21:21 | 2026-08-22 21:26 | 2026-08-22 21:26 |  |  | Fair | No | Corroded joint found at pole and pothead were reconnected using 5 one bolt clamps. Voltages left at the pothead were 119-119/238 volts. The customer was advised to get a licensed electrician to check private line and internally.
Outage | J.E.26.08.33900 | C001897376 | Horace Malcolm | St.James | Completed | Load_1002045 | Queens Drive - 710 | 2026-08-22 19:12 | 2026-08-22 19:15 | 2026-08-22 19:36 | 2026-08-22 19:37 | 2026-08-22 19:58 | 2026-08-22 22:09 | 2026-08-22 22:09 | 2026-08-22 22:09 |  |  | Fair | No | Isolate three primary junctions fuses to connect burnt off primary switch bottom wire
Outage | J.E.26.08.33922 | C001897377 | Horace Malcolm | St.James | Completed | Load_263688 | Queens Drive - 710 | 2026-08-22 19:13 | 2026-08-22 19:15 | 2026-08-22 19:27 | 2026-08-22 19:28 | 2026-08-22 19:29 | 2026-08-22 19:36 | 2026-08-22 19:36 | 2026-08-22 19:36 | BrokenPole |  | Fair | No | Customer says report was made for trelawny not st James
Outage | J.E.26.08.33916 | C001897379 | Damion Reid | Manchester | Completed | Load_240559 | Porus - 310 | 2026-08-22 19:17 | 2026-08-23 07:25 | 2026-08-23 12:33 | 2026-08-23 12:34 | 2026-08-23 12:53 | 2026-08-23 12:54 | 2026-08-23 12:55 | 2026-08-23 12:55 |  |  | Fair | No | Area found ok
Non-Outage | J.E.26.08.32661 | C001897381 | Christopher Edwards | KSAN | Completed | Load_267196 | Constant Spring - 210 | 2026-08-22 19:24 | 2026-08-22 19:25 | 2026-08-22 20:32 | 2026-08-22 20:47 | 2026-08-22 21:01 | 2026-08-22 22:05 | 2026-08-22 22:06 | 2026-08-22 22:06 |  |  | Fair | No | Customer is having an issue with faulty breaker Customer was advised to get electrician to rectify issue
Outage | J.E.26.08.34005 | C001897385 | Richard Samuda | Manchester | Completed | Load_295696 | Spur Tree - 310 | 2026-08-22 19:45 | 2026-08-22 19:46 | 2026-08-22 20:02 | 2026-08-22 20:03 | 2026-08-22 21:01 | 2026-08-22 09:01 | 2026-08-22 21:01 | 2026-08-22 21:01 | Fire |  | Fair | No | Found ok power was restored
Non-Outage | J.E.26.08.34020 | C001897386 | Raymond Lewis |  | Completed |  |  | 2026-08-22 19:55 | 2026-08-22 19:56 | 2026-08-22 22:29 | 2026-08-22 22:29 | 2026-08-22 22:29 | 2026-08-22 22:31 | 2026-08-22 22:32 | 2026-08-22 22:32 | Fire |  | Fair | No | No fire seen
Outage | J.E.26.08.33865 | C001897387 | Donald Cunningham | St.Catherine | Completed | Load_260241 | New Michelton - 210 | 2026-08-22 19:55 | 2026-08-22 19:57 | 2026-08-22 21:02 | 2026-08-22 21:02 | 2026-08-22 21:31 | 2026-08-22 21:48 | 2026-08-22 22:08 | 2026-08-22 22:08 |  |  | Fair | No | Blown junction by entrance to braham road replace with 10 amp fuse by pole #0180008
Outage | J.E.26.08.34023 | C001897390 | Collin Robinson | Portland | Completed | Load_239330 | Port Antonio - 410 | 2026-08-22 20:03 | 2026-08-22 20:04 | 2026-08-22 20:18 | 2026-08-22 20:18 | 2026-08-22 21:30 | 2026-08-22 21:43 | 2026-08-22 21:46 | 2026-08-22 21:46 |  |  | Fair | No | Defective 10 KVA transformer found at location no voltage coming from secondary side of transformer refer to maintenance
Outage | J.E.26.08.33956 | C001897394 | Christopher Edwards | KSAS | Completed | Load_256426 | Duhaney - 310 | 2026-08-22 20:17 | 2026-08-23 11:07 | 2026-08-23 11:12 | 2026-08-23 11:15 | 2026-08-23 11:37 | 2026-08-23 11:57 | 2026-08-23 11:57 | 2026-08-23 11:57 | TreeContact |  | Fair | No | Premises closedVisit location and no one is at the premises to give access Supply is in the area
Outage | J.E.26.08.34021 | C001897395 | Delano Gayle | St.Catherine | Completed | Load_264508 | Rhodens Pen - 410 | 2026-08-22 20:17 | 2026-08-22 20:19 | 2026-08-22 20:54 | 2026-08-22 20:55 | 2026-08-22 21:30 | 2026-08-22 21:40 | 2026-08-22 21:41 | 2026-08-22 21:41 |  |  | Fair | No | Blown 25kva transformer fuse no pole number, patrolled and found okay for closure replace 3amps
Outage | J.E.26.08.33921 | C001897397 | Richard Nicholas | St.Catherine | Completed | Load_244489 | Tredegar - 310 | 2026-08-22 20:18 | 2026-08-23 09:01 | 2026-08-23 11:45 | 2026-08-23 11:45 | 2026-08-23 12:26 | 2026-08-23 12:41 | 2026-08-23 12:46 | 2026-08-23 12:46 | BrokenWire |  | Fair | No | A truck come in contact with low hanging rammy service that’s run across the main road as a result a private wooden pole that the wire anchor to,broken in the half section of the pole.3 Rammy service wire disconnected for unsafe reason and customer advised to call customer care to have supply restore after broken pole is replace.
Outage | J.E.26.08.33997 | C001897396 | Delano Gayle | St.Catherine | Completed | Load_264508 | Rhodens Pen - 410 | 2026-08-22 20:18 | 2026-08-22 20:19 | 2026-08-22 21:42 | 2026-08-22 21:42 | 2026-08-22 21:42 | 2026-08-22 21:42 | 2026-08-22 21:42 | 2026-08-22 21:42 |  |  | Fair | No | Premises found okay related to call where 3amps was replaced at 25kva
Outage | J.E.26.08.33993 | C001897398 | Raymond Carr | St.Mary | Completed | Load_238939 | Blackstonedge - 110 | 2026-08-22 20:21 | 2026-08-23 07:23 | 2026-08-23 07:51 | 2026-08-23 07:51 | 2026-08-23 10:16 | 2026-08-23 12:25 | 2026-08-23 12:55 | 2026-08-23 12:55 | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Spliced and retention two spans of broken secondary conductors, using 100ft#2aa, 3 one bolt clamps, 3#2 preforms, 4#2 splicing sleeves. Supply was restored.
Outage | J.E.26.08.34066 | C001897403 | Raymond Lewis | St.Ann | Completed | Load_267348 | Roaring River - 210 | 2026-08-22 21:07 | 2026-08-23 07:16 | 2026-08-23 08:02 | 2026-08-23 08:03 | 2026-08-23 08:27 | 2026-08-23 10:27 | 2026-08-23 10:27 | 2026-08-23 10:27 |  |  | Fair | No | Low voltage in area
Outage | J.E.26.08.34063 | C001897405 | Romeo Brissett | St.James | Completed | Load_247836 | Queens Drive - 710 | 2026-08-22 21:24 | 2026-08-22 23:55 | 2026-08-23 06:20 | 2026-08-23 06:21 | 2026-08-23 06:20 | 2026-08-23 06:00 | 2026-08-23 06:21 | 2026-08-23 06:21 | Fire |  | Fair | No | Line patrolled and found ok resident stated issue was resolved from yesterday
Outage | J.E.26.08.34051 | C001897406 | Wan Carlos Scarlett | St.Catherine | Completed | Load_239984 | Twickenham - 210 | 2026-08-22 21:25 | 2026-08-22 21:26 | 2026-08-22 21:52 | 2026-08-22 21:52 | 2026-08-22 22:32 | 2026-08-22 22:56 | 2026-08-22 23:05 | 2026-08-22 23:05 |  |  | Fair | No | Upon arrival at the location the crew discovered that 65 amps bush phase from three phase is blown at pole # 6101570, further observation revealed that the switch is defective please refer to the relevant authorities to have drop out switch changed asap.
Outage | J.E.26.08.34060 | C001897410 | Lancelot Brown | Hanover | Completed | Load_253569 | Orange Bay - 310 | 2026-08-22 21:27 | 2026-08-23 07:44 | 2026-08-23 07:56 | 2026-08-23 09:30 | 2026-08-23 09:30 | 2026-08-23 09:35 | 2026-08-23 09:35 | 2026-08-23 09:35 |  |  | Fair | No | Found 10kva single phasing coming from transformer voltage reading found at transformer lug 112-09-121 transformer need to replace please pass on to maintenance department at Bogue mr Gibbs need ergent attention
Outage | J.E.26.08.34143 | C001897411 | Tajay Bernard | Hanover | Completed | Load_264055 | Orange Bay - 310 | 2026-08-22 21:39 | 2026-08-22 21:40 | 2026-08-22 22:27 | 2026-08-22 22:28 | 2026-08-22 22:27 | 2026-08-22 22:30 | 2026-08-22 22:31 | 2026-08-22 22:31 | Fire |  | Fair | No | Check and found a joint on a knife switch burning, maintenance is notified about the situation and going to attend to the issue tomorrow
Outage | J.E.26.08.34166 | C001897414 | Fitzroy Turner | KSAN | Completed | Load_242711 | Constant Spring - 210 | 2026-08-22 22:01 | 2026-08-22 22:02 | 2026-08-22 23:10 | 2026-08-22 23:10 | 2026-08-22 23:10 | 2026-08-22 23:10 | 2026-08-22 23:15 | 2026-08-22 23:15 |  |  | Fair | No | Found l a b 6/146 load buster blade burnt use one 4/0 ampac to jump out switches .supply restored to areas after repair was carry out.please send email to district to carry repairs at a later date
Outage | J.E.26.08.34175 | C001897416 | Raheem Ricketts | Manchester | Completed | Load_239027 | Spur Tree - 210 | 2026-08-22 22:31 | 2026-08-23 08:16 | 2026-08-23 08:22 | 2026-08-23 08:35 | 2026-08-23 10:11 | 2026-08-23 11:36 | 2026-08-23 11:37 | 2026-08-23 11:37 | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Check and found 40ft class 6 pole burn cause an defective switch that’s need to change also a 25 kva over 30,customers are affected pole construction dv pole both primary and open secondary area is prone to electricity theft pole is severely damaged by fire an needs to be replaced before transformer can put up back
Outage | J.E.26.08.34077 | C001897417 | Delano Gayle | St.Catherine | Completed | Load_569977 | Twickenham - 210 | 2026-08-22 23:16 | 2026-08-22 23:17 | 2026-08-22 23:24 | 2026-08-22 23:25 | 2026-08-23 00:22 | 2026-08-23 00:34 | 2026-08-23 00:34 | 2026-08-23 00:34 |  |  | Fair | No | Defective drop out switch in 3phase line which T off to Portmore drive, blown 65amps fuse, send call to maintenance to carry out repairs
Outage | J.E.26.08.34102 | C001897418 | Delano Gayle | St.Catherine | Completed | Load_256290 | Tredegar - 510 | 2026-08-22 23:20 | 2026-08-22 23:21 | 2026-08-23 00:35 | 2026-08-23 00:36 | 2026-08-23 01:40 | 2026-08-23 02:49 | 2026-08-23 02:49 | 2026-08-23 02:49 |  |  | Fair | No | Trip 10kva transformer no pole number, found line section okay, reset transformer
Outage | J.E.26.08.33887 | C001897420 | Omar King | St.Ann | Completed | Load_268908 | Cardiff Hall - 310 | 2026-08-22 23:26 | 2026-08-22 23:28 | 2026-08-23 05:00 | 2026-08-23 05:00 | 2026-08-23 05:00 | 2026-08-23 05:00 | 2026-08-23 05:00 | 2026-08-23 05:00 |  |  | Fair | No | Found 25 KVA transformer trip cause by illegal connection as being reset customer is now with supply supply
Outage | J.E.26.08.34053 | C001897422 | Omar King | St.Ann | Completed | Load_268908 | Cardiff Hall - 310 | 2026-08-22 23:48 | 2026-08-22 23:49 | 2026-08-23 02:40 | 2026-08-23 02:41 | 2026-08-23 04:00 | 2026-08-23 04:59 | 2026-08-23 05:00 | 2026-08-23 05:00 |  |  | Fair | No | Found 25 KVA transformer trip cause by illegal connection as being reset customer is now with supply supply
Outage | J.E.26.08.34581 | C001897423 | Romeo Brissett | St.James | Completed | Load_247836 | Queens Drive - 710 | 2026-08-22 23:52 | 2026-08-22 23:59 | 2026-08-23 06:19 | 2026-08-23 06:19 | 2026-08-23 06:19 | 2026-08-23 06:00 | 2026-08-23 06:20 | 2026-08-23 06:20 | Fire |  | Fair | No | Line patrolled and found ok resident stated power was restored.
Outage | J.E.26.08.34582 | C001897424 | Romeo Brissett | St.James | Completed | Load_247836 | Queens Drive - 710 | 2026-08-22 23:53 | 2026-08-22 23:58 | 2026-08-23 06:06 | 2026-08-23 06:07 | 2026-08-23 06:06 | 2026-08-23 06:00 | 2026-08-23 06:17 | 2026-08-23 06:17 |  |  | Fair | No | Line patrolled and found ok, resident stated issue was resolved from yesterday.
Outage | J.E.26.08.34607 | C001897426 | Romeo Brissett | St.James | Completed | Load_269145 | Bogue - 310 | 2026-08-23 00:12 | 2026-08-23 00:12 | 2026-08-23 06:21 | 2026-08-23 06:22 | 2026-08-23 06:47 | 2026-08-23 07:40 | 2026-08-23 08:18 | 2026-08-23 08:18 |  |  | Fair | No | Found secondary conductor dislodged from D iron retention one of secondary and replaced (1)50kva transformer fuse. Used (1)#2 preformed and (1)5amps fuse.
Outage | J.E.26.08.34614 | C001897430 | Rusean Allen | KSAS | Completed | Load_253639 | Up Park Camp - 510 | 2026-08-23 01:00 | 2026-08-23 01:01 | 2026-08-23 01:11 | 2026-08-23 01:12 | 2026-08-23 02:01 | 2026-08-23 02:23 | 2026-08-23 02:23 | 2026-08-23 02:23 | Fire |  | Fair | No | Burnt service wire was found, wire was spliced and reconnected.
Outage | J.E.26.08.34633 | C001897434 | Delano Gayle | St.Catherine | Completed | Load_247583 | Tredegar - 310 | 2026-08-23 02:08 | 2026-08-23 02:09 | 2026-08-23 02:50 | 2026-08-23 02:50 | 2026-08-23 05:26 | 2026-08-23 06:02 | 2026-08-23 06:02 | 2026-08-23 06:02 |  |  | Fair | No | Blown junction on main in 2 phase T-off line,blown 15amps junction on single phase T-off line no pole#, blown 25kva transformer fuse no pole number, oil running from transformer, replace 25amps on main at 2 phase T-off line and 15amps at junction on single phase line, transformer circuit remains out as transformer is defective send call to maintenance,
Outage | J.E.26.08.34634 | C001897435 | Delano Gayle | St.Catherine | Completed | Load_267379 | Tredegar - 310 | 2026-08-23 02:09 | 2026-08-23 02:09 | 2026-08-23 06:04 | 2026-08-23 06:04 | 2026-08-23 06:08 | 2026-08-23 06:10 | 2026-08-23 06:10 | 2026-08-23 06:10 |  |  | Fair | No | Related to call with defective 25kva transformer, send call to maintenance
Outage | J.E.26.08.34643 | C001897437 | Delano Gayle | St.Catherine | Completed | Load_256403 | Tredegar - 310 | 2026-08-23 02:43 | 2026-08-23 02:44 | 2026-08-23 06:02 | 2026-08-23 06:03 | 2026-08-23 06:02 | 2026-08-23 06:04 | 2026-08-23 06:04 | 2026-08-23 06:04 | BangingWires |  | Fair | No | Blown junction on main in 2 phase T-off line,blown 15amps junction on single phase T-off line no pole#, blown 25kva transformer fuse no pole number, oil running from transformer, replace 25amps on main at 2 phase T-off line and 15amps at junction on single phase line, transformer circuit remains out as transformer is defective send call to maintenance, - 08/23/26 06:02
Outage | J.E.26.08.34323 | C001897442 | Richman Whyte | Westmoreland | Completed | Load_243369 | Paradise - 210 | 2026-08-23 07:06 | 2026-08-23 07:08 | 2026-08-23 13:04 | 2026-08-23 13:05 | 2026-08-23 13:04 | 2026-08-23 13:04 | 2026-08-23 13:05 | 2026-08-23 13:05 |  |  | Fair | No | Customer states that the power was restored from last night
Outage | J.E.26.08.34697 | C001897443 | Raymond Lewis | St.Ann | Completed | Load_262385 | Roaring River - 210 | 2026-08-23 07:06 | 2026-08-23 07:16 | 2026-08-23 13:46 | 2026-08-23 13:47 | 2026-08-23 13:46 | 2026-08-23 13:47 | 2026-08-23 13:47 | 2026-08-23 13:47 | BrokenWire |  | Fair | No | Phone not answering
Non-Outage | J.E.26.08.33919 | C001897444 | Elvis Trowers | KSAN | Completed | Load_253615 | West Kings House - 310 | 2026-08-23 07:08 | 2026-08-23 07:13 | 2026-08-23 08:06 | 2026-08-23 08:06 | 2026-08-23 08:46 | 2026-08-23 09:20 | 2026-08-23 09:24 | 2026-08-23 09:24 |  |  | Fair | No | Found two 15 amps fuse feeding U/G cable feeding pad mount transformer reclosed one of the 15 switch and it exploded. U/g cable and P.M transformer need to be checked. Refer to S.M.D
Outage | J.E.26.08.33915 | C001897445 | Romeo Brissett | St.James | Completed | Load_250986 | Bogue - 510 | 2026-08-23 07:09 | 2026-08-23 07:13 | 2026-08-23 09:52 | 2026-08-23 09:52 | 2026-08-23 10:24 | 2026-08-23 11:00 | 2026-08-23 11:05 | 2026-08-23 11:05 | Fire |  | Fair | No | Check and found crossed country system neutral for (1)25KVA transformer on private property burst since Melissa, 2 men team is unable to repair due to heavy bushings and terrain. Please send to maintenance, no customer is out.
Outage | J.E.26.08.34256 | C001897447 | Romeo Brissett | St.James | Completed | Load_244772 | Bogue - 610 | 2026-08-23 07:09 | 2026-08-23 07:13 | 2026-08-23 13:50 | 2026-08-23 13:51 | 2026-08-23 14:46 | 2026-08-23 17:00 | 2026-08-23 17:13 | 2026-08-23 17:13 |  |  | Fair | Yes | Line patrolled and found power in area, customer name was given to residents and 2 locations was given by residents to find customers premises however locations was visited and customer still not found.
Outage | J.E.26.08.34259 | C001897446 | Romeo Brissett | St.James | Completed | Load_268145 | Bogue - 610 | 2026-08-23 07:09 | 2026-08-23 07:13 | 2026-08-23 09:52 | 2026-08-23 11:07 | 2026-08-23 11:32 | 2026-08-23 11:44 | 2026-08-23 11:46 | 2026-08-23 11:46 |  |  | Fair | No | Check and found ok.
Outage | J.E.26.08.26900 | C001897449 | Romeo Brissett | St.James | Completed | Load_249034 | Bogue - 610 | 2026-08-23 07:10 | 2026-08-23 07:13 | 2026-08-23 11:49 | 2026-08-23 11:49 | 2026-08-23 12:35 | 2026-08-23 13:46 | 2026-08-23 13:50 | 2026-08-23 13:50 |  |  | Fair | No | Found customer service wire dislodged damaged and covered in bushes by hurricane Melissa. change customer service wire used 100ft of #6 and 2 clamps. V/R 110-111-222
Non-Outage | J.E.26.08.33338 | C001897453 | Romeo Brissett |  | Completed |  |  | 2026-08-23 07:11 | 2026-08-23 07:13 | 2026-08-23 08:19 | 2026-08-23 08:20 | 2026-08-23 08:52 | 2026-08-23 09:48 | 2026-08-23 09:51 | 2026-08-23 09:51 | Fire |  | Fair | No | Isolated (1)25 kva transformer and (1)50kva transformer, removed illegal connections, retention one span of secondary repaired secondary jumper, used (1)#2 preformed and 2 clamps. V/R 115-115-231.
Non-Outage | J.E.26.08.33519 | C001897455 | Richman Whyte | Westmoreland | Completed | Load_248892 | Paradise - 110 | 2026-08-23 07:11 | 2026-08-23 07:12 | 2026-08-23 08:56 | 2026-08-23 08:56 | 2026-08-23 09:47 | 2026-08-23 11:27 | 2026-08-23 11:28 | 2026-08-23 11:28 |  |  | Fair | No | Change defective service wire use 65 feet #6 triplex service wire voltage 115 114 230
Non-Outage | J.E.26.08.33826 | C001897454 | Oshane Warren |  | Completed |  |  | 2026-08-23 07:11 | 2026-08-23 11:28 | 2026-08-23 13:43 | 2026-08-23 13:43 | 2026-08-23 13:43 | 2026-08-23 13:43 | 2026-08-23 13:44 | 2026-08-23 13:44 | BrokenPole |  | Fair | No | Check and found okay
Non-Outage | J.E.26.08.33924 | C001897452 | Richman Whyte | Westmoreland | Completed | Load_257812 | Paradise - 110 | 2026-08-23 07:11 | 2026-08-23 07:12 | 2026-08-23 08:49 | 2026-08-23 08:50 | 2026-08-23 08:50 | 2026-08-23 08:50 | 2026-08-23 08:51 | 2026-08-23 08:51 |  |  | Fair | No | Customer state that the problem was fixed from last night
Non-Outage | J.E.26.08.33927 | C001897451 | Richman Whyte | Westmoreland | Completed | Load_257812 | Paradise - 110 | 2026-08-23 07:11 | 2026-08-23 07:12 | 2026-08-23 08:47 | 2026-08-23 08:47 | 2026-08-23 08:47 | 2026-08-23 08:47 | 2026-08-23 08:49 | 2026-08-23 08:49 |  |  | Fair | No | Customer stated that some one came and fixed the problem from last night it was the hole community has the problem
Non-Outage | J.E.26.08.34645 | C001897450 | Richman Whyte | Westmoreland | Completed | Load_243369 | Paradise - 210 | 2026-08-23 07:11 | 2026-08-23 07:12 | 2026-08-23 11:34 | 2026-08-23 11:35 | 2026-08-23 12:58 | 2026-08-23 13:02 | 2026-08-23 13:03 | 2026-08-23 13:03 |  |  | Fair | No | Clean corrosion on service wire at pothead voltage 112 112 224 use the one bolt clamps
Outage | J.E.26.08.34588 | C001897456 | Horace Malcolm | St.James | Completed | Load_569159 | Bogue - 310 | 2026-08-23 07:13 | 2026-08-23 07:17 | 2026-08-23 07:47 | 2026-08-23 07:48 | 2026-08-23 07:49 | 2026-08-23 07:50 | 2026-08-23 07:50 | 2026-08-23 07:50 |  |  | Fair | No | Call to customer,customer says supply restored
Outage | J.E.26.08.32648 | C001897457 | Lancelot Brown | Hanover | Completed | Load_240292 | Orange Bay - 310 | 2026-08-23 07:15 | 2026-08-23 07:19 | 2026-08-23 07:56 | 2026-08-23 09:41 | 2026-08-23 10:42 | 2026-08-23 10:44 | 2026-08-23 10:44 | 2026-08-23 10:44 |  |  | Fair | No | Check and found voltage at meter socket 112-114-227 customer breaker trip elderman reset breaker supply restore
Non-Outage | J.E.26.08.32256 | C001897458 | Lancelot Brown | Hanover | Completed | Load_253734 | Orange Bay - 210 | 2026-08-23 07:16 | 2026-08-23 07:19 | 2026-08-23 07:56 | 2026-08-23 12:42 | 2026-08-23 13:41 | 2026-08-23 14:31 | 2026-08-23 14:31 | 2026-08-23 14:31 |  |  | Fair | No | Remake corroded joint at pole used three pg clamps vl at meter socket 112-114-226 supply restore also remove vegetation from 50kva
Non-Outage | J.E.26.08.32536 | C001897462 | Lancelot Brown | Hanover | Completed | Load_302747 | Orange Bay - 310 | 2026-08-23 07:16 | 2026-08-23 07:19 | 2026-08-23 07:56 | 2026-08-23 07:58 | 2026-08-23 08:08 | 2026-08-23 08:16 | 2026-08-23 08:16 | 2026-08-23 08:16 |  |  | Fair | No | Check and found ok supply restore a crew visit yesterday voltage found and leave 118-128-236
Non-Outage | J.E.26.08.32565 | C001897459 | Lancelot Brown | Hanover | Completed | Load_302747 | Orange Bay - 310 | 2026-08-23 07:16 | 2026-08-23 07:19 | 2026-08-23 07:56 | 2026-08-23 08:17 | 2026-08-23 08:27 | 2026-08-23 08:35 | 2026-08-23 08:36 | 2026-08-23 08:36 |  |  | Fair | No | Check and found ok voltage found and leave 115-115 230 no one at location to advise
Non-Outage | J.E.26.08.32692 | C001897460 | Lancelot Brown | Hanover | Completed | Load_292871 | Orange Bay - 310 | 2026-08-23 07:16 | 2026-08-23 07:19 | 2026-08-23 07:56 | 2026-08-23 17:15 | 2026-08-23 18:09 | 2026-08-23 18:13 | 2026-08-23 18:13 | 2026-08-23 18:13 |  |  | Fair | No | Found connectors did not crimp properly removed connectors and replace 2 vl at meter socket 109-107-216 supply restore this reading may cause by distance of feed
Non-Outage | J.E.26.08.32939 | C001897461 | Lancelot Brown | Hanover | Completed | Load_238534 | Orange Bay - 310 | 2026-08-23 07:16 | 2026-08-23 07:19 | 2026-08-23 07:56 | 2026-08-23 10:45 | 2026-08-23 12:40 | 2026-08-23 12:41 | 2026-08-23 12:41 | 2026-08-23 12:41 |  |  | Fair | No | Check and found ok customer said fix by private electrician supply restore voltage at meter socket 115-115-230
Outage | J.E.26.08.33854 | C001897467 | Nickolas Rodriques | St.Catherine | Completed | Load_248403 | Twickenham - 210 | 2026-08-23 07:18 | 2026-08-23 07:19 | 2026-08-23 12:41 | 2026-08-23 12:41 | 2026-08-23 13:17 | 2026-08-23 13:37 | 2026-08-23 13:38 | 2026-08-23 13:38 |  |  | Fair | No | Unable to locate or communicate with the customer after several attempts.
Outage | J.E.26.08.33895 | C001897468 | Nickolas Rodriques | Portmore | Completed | Load_261773 | Naggo Head - 610 | 2026-08-23 07:18 | 2026-08-23 07:19 | 2026-08-23 13:38 | 2026-08-23 13:40 | 2026-08-23 14:27 | 2026-08-23 15:26 | 2026-08-23 15:28 | 2026-08-23 15:28 |  |  | Fair | No | Unable to locate or communicate with this specific customer. However, the area was patrolled and no noticeable outage was observed.
Outage | J.E.26.08.34087 | C001897469 | Elvis Trowers | KSAN | Completed | Load_252957 | West Kings House - 310 | 2026-08-23 07:18 | 2026-08-23 07:19 | 2026-08-23 09:26 | 2026-08-23 09:26 | 2026-08-23 09:34 | 2026-08-23 09:35 | 2026-08-23 09:38 | 2026-08-23 09:38 |  |  | Fair | No | Call belongs to St Catherine district independent city.
Outage | J.E.26.08.34612 | C001897466 | Nickolas Rodriques | Portmore | Completed | Load_261280 | Naggo Head - 510 | 2026-08-23 07:18 | 2026-08-23 07:19 | 2026-08-23 10:01 | 2026-08-23 10:02 | 2026-08-23 10:35 | 2026-08-23 11:13 | 2026-08-23 11:14 | 2026-08-23 11:14 |  |  | Fair | No | Found customer with electricity. The customer confirmed that the power was restored.
Outage | J.E.26.08.34681 | C001897465 | Nickolas Rodriques | St.Catherine | Completed | Load_242375 | Rhodens Pen - 410 | 2026-08-23 07:18 | 2026-08-23 07:19 | 2026-08-23 07:59 | 2026-08-23 08:14 | 2026-08-23 08:52 | 2026-08-23 09:23 | 2026-08-23 09:25 | 2026-08-23 09:25 |  |  | Fair | No | This report is related to a defective switch that needs to be replaced which the maintenance team is already aware of.
Non-Outage | J.E.26.08.28194 | C001897473 | Raymond Lewis | St.Ann | Completed | Load_241019 | Roaring River - 210 | 2026-08-23 07:20 | 2026-08-23 07:27 | 2026-08-24 13:52 | 2026-08-24 13:53 | 2026-08-24 14:00 | 2026-08-24 14:03 | 2026-08-24 14:04 | 2026-08-24 14:04 | LowHangingWires |  | Fair | No | Not found
Non-Outage | J.E.26.08.33463 | C001897470 | Horace Malcolm | St.James | Completed | Load_574039 | Queens Drive - 710 | 2026-08-23 07:20 | 2026-08-23 07:22 | 2026-08-23 09:34 | 2026-08-23 09:35 | 2026-08-23 09:57 | 2026-08-23 10:05 | 2026-08-23 10:05 | 2026-08-23 10:05 | BrokenWire |  | Fair | No | Retention customer service wire due to wire hanging low
Non-Outage | J.E.26.08.34169 | C001897472 | Horace Malcolm | St.James | Completed | Load_247836 | Queens Drive - 710 | 2026-08-23 07:20 | 2026-08-23 07:22 | 2026-08-23 07:51 | 2026-08-23 07:52 | 2026-08-23 08:16 | 2026-08-23 09:32 | 2026-08-23 09:32 | 2026-08-23 09:32 |  |  | Fair | No | Isolate one 100 kva transformer to splice and retention one pole span secondary phase used 15ft 2/0 conductor one 2/0 splicing sleeve one clamp voltage 117-119-236
Non-Outage | J.E.26.08.34263 | C001897474 | Damion Reid |  | Completed |  |  | 2026-08-23 07:20 | 2026-08-23 07:24 | 2026-08-23 10:48 | 2026-08-23 10:49 | 2026-08-23 12:15 | 2026-08-23 12:32 | 2026-08-23 12:32 | 2026-08-23 12:32 |  |  | Fair | No | Area found ok
Outage | J.E.26.08.33827 | C001897475 | Damion Reid | Manchester | Completed | Load_240559 | Porus - 310 | 2026-08-23 07:22 | 2026-08-23 07:24 | 2026-08-23 07:33 | 2026-08-23 07:33 | 2026-08-23 08:35 | 2026-08-23 09:23 | 2026-08-23 09:25 | 2026-08-23 09:25 |  |  | Fair | No | Blown 3amp fuse found for 25kva transformer cause by tree cut on secondary line cut tree from line and replace blown fuse
Non-Outage | J.E.26.08.34709 | C001897476 | Nickolas Rodriques |  | Completed |  |  | 2026-08-23 07:26 | 2026-08-23 07:30 | 2026-08-23 09:26 | 2026-08-23 09:26 | 2026-08-23 09:50 | 2026-08-23 09:59 | 2026-08-23 10:01 | 2026-08-23 10:01 |  |  | Fair | No | This report relates to a defective switch that needs to be replaced which the maintenance team is already aware of.
Outage | J.E.26.08.34704 | C001897477 | Wayne Dillion | St.Elizabeth | Completed | Load_230094 | Maggotty - 110 | 2026-08-23 07:27 | 2026-08-23 07:30 | 2026-08-23 08:26 | 2026-08-23 11:15 | 2026-08-23 11:14 | 2026-08-23 11:10 | 2026-08-23 11:17 | 2026-08-23 11:17 |  |  | Fair | No | Reconnect customer using 70 feet of number 6 triplex 3 linket 3 one bolt clamp voltage reading 111v 110v 222v supply leave working ok
Outage | J.E.26.08.34692 | C001897479 | Milton Charlton | KSAN | Completed | Load_269211 | Hope - 510 | 2026-08-23 07:29 | 2026-08-23 07:30 | 2026-08-23 08:55 | 2026-08-23 08:56 | 2026-08-23 11:03 | 2026-08-23 11:15 | 2026-08-23 11:12 | 2026-08-23 11:12 |  |  | Fair | No | Customer service wire #6 triplex caught fire and tripped 25 kva transformer at pole #0112517. Repair #6 triplex and #6 duplex using 10ft #6 triplex and 15ft #6 triplex phase and neutral and nine 1- bolt clamps and reset 25 kva transformer.
Non-Outage | J.E.26.08.34714 | C001897480 | Raymond Lewis | St.Ann | Completed | Load_252531 | Ocho Rios - 310 | 2026-08-23 07:30 | 2026-08-23 07:31 | 2026-08-23 13:12 | 2026-08-23 13:12 | 2026-08-23 13:12 | 2026-08-23 13:14 | 2026-08-23 13:14 | 2026-08-23 13:14 |  |  | Fair | No | Remade joints at pothead and pole 3 wire service
Non-Outage | J.E.26.08.27671 | C001897482 | Raymond Lewis | St.Ann | Completed | Load_266296 | Roaring River - 210 | 2026-08-23 07:33 | 2026-08-23 07:34 | 2026-08-23 10:38 | 2026-08-23 10:38 | 2026-08-23 11:01 | 2026-08-23 23:01 | 2026-08-23 11:01 | 2026-08-23 11:01 |  |  | Fair | No | Phone not answering
Outage | J.E.26.08.33930 | C001897481 | Ryan Richards | Manchester | Completed | Load_265440 | Kendal - 210 | 2026-08-23 07:33 | 2026-08-23 07:34 | 2026-08-23 11:23 | 2026-08-23 11:24 | 2026-08-23 12:43 | 2026-08-23 13:28 | 2026-08-23 13:31 | 2026-08-23 13:31 |  |  | Fair | No | Blown 3 amp fuse found for 25 kva transformer line patrol a lot of illegal connections was seen few was removed and blown was replaced and held all customers are now with supply
Non-Outage | J.E.26.08.33880 | C001897483 | Raymond Carr | St.Mary | Completed | Load_264013 | Blackstonedge - 110 | 2026-08-23 07:34 | 2026-08-23 07:35 | 2026-08-23 12:56 | 2026-08-23 12:57 | 2026-08-23 12:56 | 2026-08-23 12:26 | 2026-08-23 12:58 | 2026-08-23 12:58 |  |  | Fair | No | Broken conductors restored.
Non-Outage | J.E.26.08.33514 | C001897484 | Raymond Carr | St.Mary | Completed | Load_238939 | Blackstonedge - 110 | 2026-08-23 07:35 | 2026-08-23 07:39 | 2026-08-23 12:59 | 2026-08-23 12:59 | 2026-08-23 12:59 | 2026-08-23 00:28 | 2026-08-23 13:00 | 2026-08-23 13:00 |  |  | Fair | No | Broken wire was restored.
Non-Outage | J.E.26.08.28636 | C001897486 | Stephen Taylor |  | Completed |  |  | 2026-08-23 07:38 | 2026-08-23 07:42 | 2026-08-23 13:36 | 2026-08-23 13:36 | 2026-08-23 15:24 | 2026-08-23 15:26 | 2026-08-23 15:27 | 2026-08-23 15:27 | Fire |  | Fair | No | Patrol area and power is in the area but several calls to single customer and no one answer
Non-Outage | J.E.26.08.32629 | C001897485 | Christopher Edwards | KSAN | Completed | Load_249464 | Constant Spring - 210 | 2026-08-23 07:38 | 2026-08-23 07:39 | 2026-08-23 08:17 | 2026-08-23 08:58 | 2026-08-23 09:13 | 2026-08-23 09:35 | 2026-08-23 09:35 | 2026-08-23 09:35 |  |  | Fair | No | Customer meter is burnt and needs to be replaced Customer currently having single phase
Non-Outage | J.E.26.08.30712 | C001897487 | Stephen Taylor | St.Thomas | Completed | Load_264475 | Good Year - 110 | 2026-08-23 07:39 | 2026-08-23 07:42 | 2026-08-23 10:45 | 2026-08-23 10:46 | 2026-08-23 11:39 | 2026-08-23 11:46 | 2026-08-23 11:47 | 2026-08-23 11:47 |  |  | Fair | No | Premese found okay customer advise to get ant electrician to fix internal problem
Non-Outage | J.E.26.08.27387 | C001897489 | Stephen Taylor | St.Thomas | Completed | Load_246431 | Good Year - 210 | 2026-08-23 07:40 | 2026-08-23 07:42 | 2026-08-23 18:00 | 2026-08-23 18:01 | 2026-08-23 18:10 | 2026-08-23 18:31 | 2026-08-23 18:35 | 2026-08-23 18:35 |  |  | Fair | No | Clean up single phase line using 3 one bolt clamp
Non-Outage | J.E.26.08.28636 | C001897490 | Stephen Taylor |  | Completed |  |  | 2026-08-23 07:40 | 2026-08-23 07:42 | 2026-08-23 13:37 | 2026-08-23 18:56 | 2026-08-23 18:56 | 2026-08-23 18:56 | 2026-08-23 18:57 | 2026-08-23 18:57 | Fire |  | Fair | No | Patrol the area power is in the area several calls to single customer and no one answer
Non-Outage | J.E.26.08.29576 | C001897488 | Stephen Taylor | St.Thomas | Completed | Load_245650 | Good Year - 210 | 2026-08-23 07:40 | 2026-08-23 07:42 | 2026-08-23 18:35 | 2026-08-23 18:36 | 2026-08-23 18:35 | 2026-08-23 18:36 | 2026-08-23 18:37 | 2026-08-23 18:37 |  |  | Fair | No | Clean up single phase line using 3 one bolt clamp
Non-Outage | J.E.26.08.26090 | C001897491 | Daniel Francis | St.Ann | Completed | Load_339987 | Roaring River - 410 | 2026-08-23 07:43 | 2026-08-23 07:44 | 2026-08-23 09:10 | 2026-08-23 09:10 | 2026-08-23 09:43 | 2026-08-23 09:44 | 2026-08-23 09:46 | 2026-08-23 09:46 |  |  | Fair | No | Un able to make contact with customer gated community
Outage | J.E.26.08.32988 | C001897492 | Neville Spencer | Clarendon | Completed | Load_568340 | May Pen - 110 | 2026-08-23 07:55 | 2026-08-23 15:48 | 2026-08-24 09:10 | 2026-08-24 09:10 | 2026-08-24 09:12 | 2026-08-24 09:12 | 2026-08-24 09:13 | 2026-08-24 09:13 |  |  | Fair | No | Unable to locate customer.
Outage | J.E.26.08.33123 | C001897493 | Clyde Brown | Clarendon | Completed | Load_243483 | Monymusk - 210 | 2026-08-23 07:55 | 2026-08-23 07:56 | 2026-08-23 10:15 | 2026-08-23 10:16 | 2026-08-23 10:16 | 2026-08-23 10:14 | 2026-08-23 10:18 | 2026-08-23 10:18 |  |  | Fair | No | Found ok ,customer said the supply was restored
Outage | J.E.26.08.33967 | C001897495 | Neville Spencer | Clarendon | Completed | Load_250809 | Parnassus - 210 | 2026-08-23 07:55 | 2026-08-23 15:48 | 2026-08-23 20:55 | 2026-08-23 20:55 | 2026-08-23 21:58 | 2026-08-23 21:58 | 2026-08-23 21:59 | 2026-08-23 21:59 |  |  | Fair | No | Unable to locate customer.
Outage | J.E.26.08.34031 | C001897494 | Neville Spencer | Clarendon | Completed | Load_248579 | Parnassus - 210 | 2026-08-23 07:55 | 2026-08-23 15:48 | 2026-08-23 19:15 | 2026-08-23 19:15 | 2026-08-23 19:15 | 2026-08-23 19:15 | 2026-08-23 19:17 | 2026-08-23 19:17 |  | Y | Fair | No | Cleared bamboo from 13.8 kv line renew blown 15 amp J/ fuse at pole # 0059701 area restored.
Outage | J.E.26.08.34236 | C001897496 | Clyde Brown | Clarendon | Completed | Load_250072 | May Pen - 210 | 2026-08-23 07:55 | 2026-08-23 07:56 | 2026-08-23 08:41 | 2026-08-23 08:41 | 2026-08-23 09:03 | 2026-08-23 10:09 | 2026-08-23 10:10 | 2026-08-23 10:10 |  |  | Fair | No | Burnt off 25 kva transformer phase lead ,open transformer and replaced burnt off clamp at connection to secondary line ,voltage left 109/111and 213V
Outage | J.E.26.08.34723 | C001897497 | Neville Spencer | Clarendon | Completed | Load_243929 | Parnassus - 210 | 2026-08-23 07:55 | 2026-08-23 15:48 | 2026-08-23 15:54 | 2026-08-23 15:55 | 2026-08-23 18:50 | 2026-08-23 18:50 | 2026-08-23 19:12 | 2026-08-23 19:12 |  | Y | Fair | No | Cleared bamboo from 13.8 kv line renew blown 15 amp j/ fuse at pole # 0059701 area restored.
Non-Outage | J.E.26.08.32041 | C001897501 | Roemello Brown | Trelawny | Completed | Load_245182 | Duncans - 210 | 2026-08-23 07:56 | 2026-08-24 09:33 | 2026-08-24 14:37 | 2026-08-24 14:38 | 2026-08-24 15:57 | 2026-08-24 16:45 | 2026-08-24 17:36 | 2026-08-24 17:36 | BrokenWire |  | Fair | No | Neutral burst have it re-join Voltage found 122/89/203Voltage leave 117/117/234
Non-Outage | J.E.26.08.33944 | C001897503 | Dwayne Samuels | Trelawny | Completed | Load_251680 | Martha Brae - 210 | 2026-08-23 07:56 | 2026-08-23 07:58 | 2026-08-23 08:31 | 2026-08-23 08:31 | 2026-08-23 09:24 | 2026-08-23 09:54 | 2026-08-23 09:55 | 2026-08-23 09:55 |  |  | Fair | No | Corrosion at pole was the cause of customer low voltage use 1 one bolt clamp at same for repairs voltage left 116v/119v/233v
Non-Outage | J.E.26.08.34674 | C001897502 | Dwayne Samuels | Trelawny | Completed | Load_249410 | Greenwood - 210 | 2026-08-23 07:56 | 2026-08-23 07:58 | 2026-08-23 12:59 | 2026-08-23 13:00 | 2026-08-23 13:22 | 2026-08-23 13:49 | 2026-08-23 13:50 | 2026-08-23 13:50 |  |  | Fair | No | Corrosion at pole was the cause of customer low voltage use 1 one bolt clamp at same for repairs voltage left after repair 117v/118v/235v
Outage | J.E.26.08.34047 | C001897499 | Milton Charlton | Trelawny | Completed | Load_241073 | Duncans - 210 | 2026-08-23 07:56 | 2026-08-23 08:05 | 2026-08-23 08:45 | 2026-08-23 08:46 | 2026-08-23 08:51 | 2026-08-23 09:05 | 2026-08-23 08:53 | 2026-08-23 08:53 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.34661 | C001897498 | Dwayne Samuels | Trelawny | Completed | Load_249410 | Greenwood - 210 | 2026-08-23 07:56 | 2026-08-23 07:58 | 2026-08-23 09:30 | 2026-08-23 09:58 | 2026-08-23 11:13 | 2026-08-23 12:58 | 2026-08-23 12:59 | 2026-08-23 12:59 |  |  | Fair | No | Illegal connection on line cause transformer lower phase drop lead to burn off open 1 25kva transformer to reconnect transformer drop lead using 1 one bolt clamp at same and remove illegal connection voltage left 116v/118v/234v
Non-Outage | J.E.26.08.33839 | C001897505 | Edward Royal |  | Completed |  |  | 2026-08-23 08:17 | 2026-08-23 08:18 | 2026-08-23 08:32 | 2026-08-23 09:23 | 2026-08-23 10:04 | 2026-08-23 11:18 | 2026-08-23 11:23 | 2026-08-23 11:23 |  |  | Fair | No | Spliced and reconnected secondary phase using 20ft number 2 tripe x cable 2 single bolt clamp
Non-Outage | J.E.26.06.19217 | C001897506 | Richard Nicholas | St.Catherine | Completed | Load_260971 | New Michelton - 210 | 2026-08-23 08:25 | 2026-08-23 08:26 | 2026-08-23 08:48 | 2026-08-23 08:48 | 2026-08-23 09:46 | 2026-08-23 10:04 | 2026-08-23 10:05 | 2026-08-23 10:05 |  |  | Fair | No | Premises found locked and customer telephone number is unreachable.
Non-Outage | J.E.26.06.19800 | C001897507 | Richard Nicholas | St.Catherine | Completed | Load_264438 | Twickenham - 210 | 2026-08-23 08:25 | 2026-08-23 08:26 | 2026-08-23 12:48 | 2026-08-23 12:48 | 2026-08-23 13:42 | 2026-08-23 13:57 | 2026-08-23 13:58 | 2026-08-23 13:58 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.34764 | C001897509 | Horace Malcolm | St.James | Completed | Load_254051 | Rose Hall - 210 | 2026-08-23 08:26 | 2026-08-23 08:28 | 2026-08-23 10:18 | 2026-08-23 10:18 | 2026-08-23 10:18 | 2026-08-23 10:18 | 2026-08-23 10:18 | 2026-08-23 10:18 |  |  | Fair | No | Call to customer,customer says supply restored
Outage | J.E.26.08.34766 | C001897510 | Horace Malcolm | St.James | Completed | Load_574038 | Queens Drive - 710 | 2026-08-23 08:26 | 2026-08-23 08:28 | 2026-08-23 10:06 | 2026-08-23 10:07 | 2026-08-23 10:16 | 2026-08-23 10:17 | 2026-08-23 10:17 | 2026-08-23 10:17 |  |  | Fair | No | Check and found premises ok supply restored voltage 119-120-239
Non-Outage | J.E.26.08.30523 | C001897511 | Shamour Haughton |  | Completed |  |  | 2026-08-23 08:27 | 2026-08-24 08:28 | 2026-08-24 13:51 | 2026-08-24 13:51 | 2026-08-24 14:35 | 2026-08-24 14:35 | 2026-08-24 14:37 | 2026-08-24 14:37 |  |  | Fair | No | Customer number went unanswered after several attempts, needs better directions
Outage | J.E.26.08.34738 | C001897512 | Daniel Francis | St.Ann | Completed | Load_239011 | Cardiff Hall - 210 | 2026-08-23 08:28 | 2026-08-23 15:10 | 2026-08-23 15:36 | 2026-08-23 15:37 | 2026-08-23 15:36 | 2026-08-23 15:39 | 2026-08-23 15:44 | 2026-08-23 15:44 |  |  | Fair | No | Patrol and renew junction at. 616430. twenty amp fuse
Non-Outage | J.E.26.08.15116 | C001897513 | Ricky Hall | St.Catherine | Completed | Load_267523 | Tredegar - 410 | 2026-08-23 08:30 | 2026-08-23 08:31 | 2026-08-23 08:50 | 2026-08-23 08:54 | 2026-08-23 09:18 | 2026-08-23 09:21 | 2026-08-23 09:21 | 2026-08-23 09:21 |  |  | Fair | No | Issue was resolved on previous shift customer found with supply
Non-Outage | J.E.26.08.18139 | C001897514 | Ricky Hall | St.Catherine | Completed | Load_238037 | Tredegar - 510 | 2026-08-23 08:30 | 2026-08-23 08:31 | 2026-08-23 09:22 | 2026-08-23 09:24 | 2026-08-23 10:22 | 2026-08-23 10:27 | 2026-08-23 10:28 | 2026-08-23 10:28 |  |  | Fair | No | Premises closed
Non-Outage | J.E.26.08.20903 | C001897516 | Romaine Roberts | St.Mary | Completed | Load_238645 | Highgate - 210 | 2026-08-23 08:43 | 2026-08-23 08:44 | 2026-08-23 08:56 | 2026-08-23 08:56 | 2026-08-23 09:31 | 2026-08-23 09:42 | 2026-08-23 09:42 | 2026-08-23 09:42 | BrokenPole |  | Fair | No | No broken pole found near police station also customer said she never make any call
Non-Outage | J.E.26.08.33664 | C001897517 | Romaine Roberts | St.Mary | Completed | Load_241990 | Highgate - 210 | 2026-08-23 08:43 | 2026-08-23 08:43 | 2026-08-23 09:42 | 2026-08-23 09:42 | 2026-08-23 10:21 | 2026-08-23 10:28 | 2026-08-23 10:29 | 2026-08-23 10:29 |  |  | Fair | No | Corrosion at pole clean and remake joints 3 clamps use voltage 113-114-228
Outage | J.E.26.08.34787 | C001897519 | Raymond Lewis | St.Ann | Completed | Load_258982 | Ocho Rios - 310 | 2026-08-23 08:51 | 2026-08-23 08:52 | 2026-08-23 11:02 | 2026-08-23 11:03 | 2026-08-23 11:28 | 2026-08-23 11:30 | 2026-08-23 11:31 | 2026-08-23 11:31 | BrokenWire |  | Fair | No | Customer need a electrician to complete job for connection
Outage | J.E.26.08.34783 | C001897520 | Nickolas Rodriques | St.Catherine | Completed | Load_261066 | Twickenham - 210 | 2026-08-23 08:56 | 2026-08-23 08:58 | 2026-08-23 11:16 | 2026-08-23 11:18 | 2026-08-23 12:04 | 2026-08-23 12:38 | 2026-08-23 12:41 | 2026-08-23 12:41 |  |  | Fair | No | Unable to communicate with this specific customer. However, the area was patrolled and no noticeable outage was seen.
Outage | J.E.26.08.34796 | C001897522 | Romeo Brissett | St.James | Completed | Load_557427 | Bogue - 610 | 2026-08-23 08:57 | 2026-08-23 09:00 | 2026-08-23 11:46 | 2026-08-23 11:47 | 2026-08-23 11:46 | 2026-08-23 11:45 | 2026-08-23 11:47 | 2026-08-23 11:47 |  |  | Fair | No | Removed bird and replaced (1)8amps junction fuse.
Outage | J.E.26.08.34803 | C001897523 | Horace Malcolm | St.James | Completed | Load_241696 | Bogue - 310 | 2026-08-23 08:59 | 2026-08-23 09:01 | 2026-08-23 10:19 | 2026-08-23 10:20 | 2026-08-23 10:55 | 2026-08-23 11:34 | 2026-08-23 11:34 | 2026-08-23 11:34 |  |  | Fair | No | Isolate one 25kva transformer to splice and retention one pole span secondary phase used 10ft 2/0 conductor one 2/0 preform one clamp voltage 113-116-229
Outage | J.E.26.08.34810 | C001897527 | Milton Charlton | KSAN | Completed | Load_251538 | Hope - 310 | 2026-08-23 09:14 | 2026-08-23 09:15 | 2026-08-23 15:01 | 2026-08-23 15:02 | 2026-08-23 15:01 | 2026-08-23 14:50 | 2026-08-23 15:04 | 2026-08-23 15:04 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.34813 | C001897526 | Christopher Edwards | KSAN | Completed | Load_261228 | Constant Spring - 210 | 2026-08-23 09:14 | 2026-08-23 09:14 | 2026-08-23 09:35 | 2026-08-23 09:36 | 2026-08-23 10:01 | 2026-08-23 10:27 | 2026-08-23 11:05 | 2026-08-23 11:05 |  |  | Fair | No | Customer meter is burnt And needs to be replaced
Outage | J.E.26.08.34775 | C001897528 | Milton Charlton | KSAS | Completed | Load_1003916 | Up Park Camp - 410 | 2026-08-23 09:15 | 2026-08-23 09:15 | 2026-08-23 15:04 | 2026-08-23 15:05 | 2026-08-23 16:10 | 2026-08-23 16:10 | 2026-08-23 16:11 | 2026-08-23 16:11 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.34818 | C001897529 | Raymond Lewis | St.Ann | Completed | Load_247851 | Roaring River - 210 | 2026-08-23 09:16 | 2026-08-23 09:17 | 2026-08-23 13:44 | 2026-08-23 13:45 | 2026-08-23 13:45 | 2026-08-23 13:46 | 2026-08-23 13:46 | 2026-08-23 13:46 | BrokenWire |  | Fair | No | Phone not answering
Outage | J.E.26.08.34795 | C001897530 | Raymond Carr | St.Ann | Completed | Load_247813 | Upper White River - 110 | 2026-08-23 09:17 | 2026-08-23 09:17 | 2026-08-23 13:06 | 2026-08-23 13:07 | 2026-08-23 13:53 | 2026-08-23 14:00 | 2026-08-23 14:13 | 2026-08-23 14:13 |  |  | Fair | No | Blown 50 kva transformer fuse found at pole number 0014196, line patrol and okay, however tree contact was suspected. A 5 amp fuse was used to renew, supply was restored.
Non-Outage | J.E.26.08.34825 | C001897532 | Stephen Taylor | St.Thomas | Completed | Load_577201 | Good Year - 210 | 2026-08-23 09:27 | 2026-08-23 09:28 | 2026-08-23 17:45 | 2026-08-23 17:46 | 2026-08-23 17:45 | 2026-08-23 17:47 | 2026-08-23 17:47 | 2026-08-23 17:47 |  |  | Fair | No | Patrol the area power is in the area make to customer and customer say soon call back
Non-Outage | J.E.26.08.34833 | C001897534 | Antony Levy | KSAN | Completed | Load_252805 | Hope - 310 | 2026-08-23 09:33 | 2026-08-23 09:34 | 2026-08-23 10:15 | 2026-08-23 10:16 | 2026-08-23 11:25 | 2026-08-23 11:46 | 2026-08-23 11:48 | 2026-08-23 11:48 |  |  | Fair | No | Customer experiencing low voltage tap up transformer to tap position 2 and left a voltage reading of 118 118 236.
Outage | J.E.26.08.34816 | C001897539 | Clyde Brown | Clarendon | Completed | Load_569764 | Parnassus - 210 | 2026-08-23 10:07 | 2026-08-23 10:09 | 2026-08-23 13:17 | 2026-08-23 13:18 | 2026-08-23 13:17 | 2026-08-23 12:51 | 2026-08-23 13:20 | 2026-08-23 13:20 | BrokenWire |  | Fair | No | Broken secondary neutral,open 25 kva transformer and repaired with 8ft-#2 conductor,2-splicing sleeve,1- preform and 1- clamp.
Outage | J.E.26.08.34827 | C001897538 | Ricky Hall | St.Catherine | Completed | Load_246252 | Rhodens Pen - 210 | 2026-08-23 10:07 | 2026-08-23 10:12 | 2026-08-23 10:50 | 2026-08-23 10:51 | 2026-08-23 12:15 | 2026-08-23 12:32 | 2026-08-23 12:34 | 2026-08-23 12:34 | BrokenWire |  | Fair | No | Defective stantion customer advised disconnected 3W service at pole
Outage | J.E.26.08.34850 | C001897540 | Raheem Ricketts | St.Elizabeth | Completed | Load_1002212 | Maggotty - 210 | 2026-08-23 10:10 | 2026-08-23 13:45 | 2026-08-23 13:52 | 2026-08-23 13:58 | 2026-08-23 13:58 | 2026-08-23 13:59 | 2026-08-23 13:59 | 2026-08-23 13:59 |  |  | Fair | No | Check and found customer experiencing an internal problem customer meter socket needs changing
Outage | J.E.26.08.34855 | C001897541 | Richard Nicholas | St.Catherine | Completed | Load_248750 | Tredegar - 410 | 2026-08-23 10:11 | 2026-08-23 10:13 | 2026-08-23 13:58 | 2026-08-23 13:59 | 2026-08-23 14:31 | 2026-08-23 15:26 | 2026-08-23 15:28 | 2026-08-23 15:28 | BrokenWire |  | Fair | No | Spot bushing done.remade burnt off 3w service phase joint at pole,1 clamp was used.voltage reading 116x2 and 232v.
Non-Outage | J.E.26.08.32696 | C001897543 | Neville Spencer | Clarendon | Completed | Load_557165 | May Pen - 210 | 2026-08-23 10:15 | 2026-08-23 10:17 | 2026-08-23 10:27 | 2026-08-23 10:27 | 2026-08-23 10:47 | 2026-08-23 10:47 | 2026-08-23 11:48 | 2026-08-23 11:48 |  |  | Fair | No | Open 3, 5 amp fuse protecting 50 kva xmfr in bank of 3,
Outage | J.E.26.08.33922 | C001897545 | Andre Williams | St.James | Completed | Load_263688 | Queens Drive - 710 | 2026-08-23 10:27 | 2026-08-23 15:05 | 2026-08-23 17:16 | 2026-08-23 17:17 | 2026-08-23 17:16 | 2026-08-23 17:17 | 2026-08-23 17:17 | 2026-08-23 17:17 | BrokenPole |  | Fair | No | Reffer to Montego Bay emergency
Non-Outage | J.E.26.08.32864 | C001897546 | Horace Malcolm |  | Completed |  |  | 2026-08-23 10:28 | 2026-08-23 10:29 | 2026-08-23 11:35 | 2026-08-23 11:35 | 2026-08-23 12:23 | 2026-08-23 12:41 | 2026-08-23 12:41 | 2026-08-23 12:41 |  |  | Fair | No | Check and found customer having no supply coming from meter referred to field service zero voltage coming to customer pothead
Outage | J.E.26.08.34879 | C001897547 | Wayne Dillion | St.Elizabeth | Completed | Load_239662 | Maggotty - 110 | 2026-08-23 10:29 | 2026-08-23 10:29 | 2026-08-23 11:19 | 2026-08-23 11:19 | 2026-08-23 13:26 | 2026-08-23 15:36 | 2026-08-23 15:37 | 2026-08-23 15:37 |  |  | Rains | No | Patrol and found one blown 3amp fuse that protects 25kva transformer circuit no pole #. Replace same and supply restored okay.
Outage | J.E.26.08.34877 | C001897549 | Raymond Carr | St.Mary | Completed | Load_254773 | Blackstonedge - 110 | 2026-08-23 10:33 | 2026-08-23 10:34 | 2026-08-23 13:01 | 2026-08-23 13:02 | 2026-08-23 13:01 | 2026-08-23 12:00 | 2026-08-23 13:02 | 2026-08-23 13:02 |  |  | Fair | No | Broken wire was restored.
Outage | J.E.26.08.34880 | C001897548 | Raymond Carr | St.Mary | Completed | Load_237761 | Oracabessa - 210 | 2026-08-23 10:33 | 2026-08-23 10:34 | 2026-08-23 14:18 | 2026-08-23 14:19 | 2026-08-23 15:33 | 2026-08-23 15:39 | 2026-08-23 15:44 | 2026-08-23 15:44 |  |  | Fair | No | Blown junction fuse found, line patrol and found okay, however bird contact was suspected. A 10 amp fuse was used to renew supply was restored.
Outage | J.E.26.08.34178 | C001897551 | Milton Charlton | KSAN | Completed | Load_252138 | Hope - 510 | 2026-08-23 10:37 | 2026-08-23 10:38 | 2026-08-23 11:16 | 2026-08-23 17:17 | 2026-08-23 17:16 | 2026-08-23 17:20 | 2026-08-23 17:18 | 2026-08-23 17:18 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.34904 | C001897554 | Damion Reid | Manchester | Completed | Load_1002538 | Kendal - 310 | 2026-08-23 10:58 | 2026-08-23 10:59 | 2026-08-23 13:22 | 2026-08-23 13:22 | 2026-08-23 13:46 | 2026-08-23 14:46 | 2026-08-23 14:48 | 2026-08-23 14:48 |  |  | Fair | No | Blown 7amp fuse found for 100kva transformer cause by burnt off transformer drop lead remade burnt off lead and replace blown fuse
Non-Outage | J.E.26.08.34857 | C001897555 | Oshane Warren | Westmoreland | Completed | Load_556532 | Paradise - 310 | 2026-08-23 10:59 | 2026-08-23 11:00 | 2026-08-23 11:35 | 2026-08-23 11:36 | 2026-08-23 12:55 | 2026-08-23 12:57 | 2026-08-23 13:08 | 2026-08-23 13:08 |  |  | Fair | No | Replace 30 amp junction fuse
Outage | J.E.26.08.34902 | C001897556 | Milton Charlton | KSAN | Completed | Load_253447 | Hope - 510 | 2026-08-23 11:00 | 2026-08-23 11:01 | 2026-08-23 11:26 | 2026-08-23 11:27 | 2026-08-23 13:11 | 2026-08-23 13:16 | 2026-08-23 13:13 | 2026-08-23 13:13 |  |  | Fair | No | Refused and reclosed 30 amps junction switch at pole #556752 using one 30 amps fuse.
Non-Outage | J.E.26.08.34921 | C001897557 | Horace Malcolm |  | Completed |  |  | 2026-08-23 11:01 | 2026-08-23 11:02 | 2026-08-23 12:53 | 2026-08-23 12:53 | 2026-08-23 13:14 | 2026-08-23 13:22 | 2026-08-23 13:22 | 2026-08-23 13:22 | LeaningPole |  | Fair | No | Check and found one 40ft wooden pole with hexing box and single phase primary line leaning down
Outage | J.E.26.08.34912 | C001897563 | Stephen Taylor | St.Thomas | Completed | Load_249685 | Lysson - 410 | 2026-08-23 11:23 | 2026-08-23 11:23 | 2026-08-23 11:47 | 2026-08-23 11:48 | 2026-08-23 13:14 | 2026-08-23 13:14 | 2026-08-23 13:16 | 2026-08-23 13:16 | BrokenPole |  | Fair | No | Jps class 4 pole broken and need to replace by the jps maintenance team urgent junction fuse out no # on pole
Outage | J.E.26.08.34937 | C001897564 | Damion Reid | Manchester | Completed | Load_265861 | Spur Tree - 310 | 2026-08-23 11:25 | 2026-08-23 11:27 | 2026-08-23 14:49 | 2026-08-23 14:49 | 2026-08-23 16:14 | 2026-08-23 16:45 | 2026-08-23 16:46 | 2026-08-23 16:46 |  |  | Fair | No | Remade broken service neutral at secondary pole for 2 wire service using one pen union
Outage | J.E.26.08.34925 | C001897566 | Raymond Carr | St.Ann | Completed | Load_247813 | Upper White River - 110 | 2026-08-23 11:34 | 2026-08-23 11:44 | 2026-08-23 14:13 | 2026-08-23 14:14 | 2026-08-23 14:13 | 2026-08-16 14:00 | 2026-08-23 14:15 | 2026-08-23 14:15 |  |  | Fair | No | Supply was restored. Related to Russel Hall.
Non-Outage | J.E.26.08.25896 | C001897567 | Romaine Roberts | St.Mary | Completed | Load_254745 | Highgate -110 | 2026-08-23 11:36 | 2026-08-23 11:36 | 2026-08-23 12:00 | 2026-08-23 12:01 | 2026-08-23 13:44 | 2026-08-23 13:50 | 2026-08-23 14:11 | 2026-08-23 14:11 |  |  | Fair | No | Corrosion at pole and pothead clean and remake joints 3 clamp and 3 penunion
Non-Outage | J.E.26.08.21850 | C001897568 | Romaine Roberts | St.Mary | Completed | Load_242166 | Highgate -110 | 2026-08-23 11:38 | 2026-08-23 11:39 | 2026-08-23 15:32 | 2026-08-23 15:33 | 2026-08-23 15:32 | 2026-08-23 15:33 | 2026-08-23 15:33 | 2026-08-23 15:33 |  |  | Fair | No | Open and close 25 kva transformer to clear and retention conductor also remake jumper
Outage | J.E.26.08.34915 | C001897571 | Raymond Carr | St.Mary | Completed | Load_239857 | Oracabessa - 210 | 2026-08-23 11:44 | 2026-08-23 11:45 | 2026-08-23 15:45 | 2026-08-23 15:45 | 2026-08-23 15:45 | 2026-08-23 15:30 | 2026-08-23 15:46 | 2026-08-23 15:46 |  |  | Fair | No | Supply was restored.
Outage | J.E.26.08.34939 | C001897574 | Raymond Carr | St.Mary | Completed | Load_262786 | Blackstonedge - 110 | 2026-08-23 11:55 | 2026-08-23 11:56 | 2026-08-23 13:02 | 2026-08-23 13:03 | 2026-08-23 13:02 | 2026-08-23 00:24 | 2026-08-23 13:03 | 2026-08-23 13:03 |  |  | Fair | No | Broken wire repaired, Supply was restored.
Non-Outage | J.E.26.08.21684 | C001897578 | Romaine Roberts | St.Mary | Completed | Load_242166 | Highgate -110 | 2026-08-23 12:22 | 2026-08-23 12:23 | 2026-08-23 14:12 | 2026-08-23 14:12 | 2026-08-23 15:19 | 2026-08-23 15:30 | 2026-08-23 15:32 | 2026-08-23 15:32 |  |  | Fair | No | Open and close 25 kva transformer to clear and retention conductor also remake jumper
Non-Outage | J.E.26.08.34995 | C001897580 | Richman Whyte | Westmoreland | Completed | Load_249422 | Paradise - 210 | 2026-08-23 12:38 | 2026-08-23 12:40 | 2026-08-23 13:54 | 2026-08-23 13:54 | 2026-08-23 13:54 | 2026-08-23 14:05 | 2026-08-23 14:06 | 2026-08-23 14:06 |  |  | Fair | No | Clean corrosion on service wire at pothead use 1 one bolt clamp voltage 110 110 220
Outage | J.E.26.08.34990 | C001897581 | Raheem Ricketts | St.Elizabeth | Completed | Load_254148 | Maggotty - 210 | 2026-08-23 12:51 | 2026-08-23 12:52 | 2026-08-23 13:52 | 2026-08-23 13:53 | 2026-08-23 13:55 | 2026-08-23 13:58 | 2026-08-23 13:58 | 2026-08-23 13:58 |  |  | Fair | No | Check and found 25kva trip reset 25kva
Outage | J.E.26.08.35019 | C001897582 | Ryan Richards | Manchester | Completed | Load_256270 | Kendal - 210 | 2026-08-23 12:58 | 2026-08-23 13:02 | 2026-08-23 21:16 | 2026-08-23 21:16 | 2026-08-23 22:54 | 2026-08-24 05:45 | 2026-08-24 05:45 | 2026-08-24 05:45 |  |  | Fair | No | Broken service wire found replace service wire using 10ft#6 triplex 3 one bolt clamps and reclose voltage 115/118/234 volts
Non-Outage | J.E.26.08.34950 | C001897584 | Roemello Brown | Trelawny | Completed | Load_294305 | Duncans - 110 | 2026-08-23 13:04 | 2026-08-24 08:02 | 2026-08-24 12:03 | 2026-08-24 12:12 | 2026-08-24 12:56 | 2026-08-24 12:57 | 2026-08-24 12:58 | 2026-08-24 12:58 |  |  | Fair | No | Premises found working okVoltage found 117/116/233Voltage leave 117/116/233
Outage | J.E.26.08.33763 | C001897583 | Ryan Richards | Manchester | Completed | Load_248128 | Kendal - 210 | 2026-08-23 13:04 | 2026-08-23 13:05 | 2026-08-23 13:31 | 2026-08-23 13:32 | 2026-08-23 15:47 | 2026-08-23 17:30 | 2026-08-23 17:30 | 2026-08-23 17:30 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Rains | Yes | One span of broken 2/0 triplex found cause by rubbish truck open 25 kva transformer disconnect broken wire replaced 130ft#6 triplex to supply the 2 customer at the end of the line 6 one bolt clamps and reclose transformer all customers are now with supply
Outage | J.E.26.08.34997 | C001897586 | Milton Charlton | KSAN | Completed | Load_253615 | West Kings House - 310 | 2026-08-23 13:36 | 2026-08-23 13:36 | 2026-08-23 17:13 | 2026-08-23 17:19 | 2026-08-23 17:24 | 2026-08-23 17:25 | 2026-08-23 17:26 | 2026-08-23 17:26 |  |  | Fair | No | Customer transformer defective.
Outage | J.E.26.08.35052 | C001897587 | Christopher Edwards | KSAN | Completed | Load_241758 | Constant Spring - 310 | 2026-08-23 13:36 | 2026-08-24 07:24 | 2026-08-24 07:27 | 2026-08-24 14:26 | 2026-08-24 14:54 | 2026-08-24 14:56 | 2026-08-24 15:00 | 2026-08-24 15:00 |  |  | Fair | No | Metering department was contacted and supply has returned to premises
Outage | J.E.26.08.34991 | C001897588 | Roxroy Needham | St.Ann | Completed | Load_246291 | Cardiff Hall - 210 | 2026-08-23 13:39 | 2026-08-23 15:04 | 2026-08-23 15:18 | 2026-08-23 15:18 | 2026-08-23 15:18 | 2026-08-23 15:12 | 2026-08-23 15:19 | 2026-08-23 15:19 |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.08.35034 | C001897589 | Neville Spencer | Clarendon | Completed | Load_258960 | Monymusk - 410 | 2026-08-23 13:43 | 2026-08-23 15:48 | 2026-08-23 20:49 | 2026-08-23 20:49 | 2026-08-23 20:49 | 2026-08-23 20:49 | 2026-08-23 20:51 | 2026-08-23 20:51 | BrokenWire | Y | Fair | No | Cleared tree limb from secondary lines renew blown 3 amp fuse protecting 25 kva xmfr at pole # 016479 supply restored.
Outage | J.E.26.08.34820 | C001897591 | Ricky Hall | St.Catherine | Completed | Load_267733 | Rhodens Pen - 210 | 2026-08-23 13:48 | 2026-08-23 13:51 | 2026-08-23 16:13 | 2026-08-23 16:20 | 2026-08-23 17:13 | 2026-08-23 17:15 | 2026-08-23 17:16 | 2026-08-23 17:16 |  |  | Fair | No | Call is located in the ksa region plz reassign to the relevant parish
Outage | J.E.26.08.34933 | C001897592 | Ricky Hall | St.Catherine | Completed | Load_406138 | Rhodens Pen - 210 | 2026-08-23 13:48 | 2026-08-23 13:51 | 2026-08-23 17:17 | 2026-08-23 17:17 | 2026-08-23 18:01 | 2026-08-23 18:20 | 2026-08-23 18:21 | 2026-08-23 18:21 |  |  | Fair | No | Issue exists in hexing #0027 plz refer to the relevant team
Outage | J.E.26.08.35033 | C001897593 | Ricky Hall | St.Catherine | Completed | Load_291532 | Rhodens Pen - 210 | 2026-08-23 13:48 | 2026-08-23 13:51 | 2026-08-23 18:21 | 2026-08-23 18:21 | 2026-08-23 18:21 | 2026-08-23 18:21 | 2026-08-23 18:22 | 2026-08-23 18:22 |  |  | Fair | No | Call associated with outage #34933
Outage | J.E.26.08.35057 | C001897590 | Marlon Authors | St.Elizabeth | Completed | Load_295435 | Maggotty - 210 | 2026-08-23 13:48 | 2026-08-23 16:52 | 2026-08-23 17:54 | 2026-08-23 17:54 | 2026-08-23 18:20 | 2026-08-23 18:30 | 2026-08-23 18:30 | 2026-08-23 18:30 |  |  | Fair | No | Supply checked and found working ok rdg 119v,120v and cross phased 239 volts. Customer was told to reset breaker, supply restored
Non-Outage | J.E.26.08.28521 | C001897594 | Shamour Haughton |  | Completed |  |  | 2026-08-23 13:51 | 2026-08-24 12:13 | 2026-08-24 12:57 | 2026-08-24 12:58 | 2026-08-24 13:45 | 2026-08-24 13:45 | 2026-08-24 13:49 | 2026-08-24 13:49 |  |  | Fair | No | Found customer okay, voltage left at pothead 115,117,232
Outage | J.E.26.08.35065 | C001897596 | Raymond Carr | St.Mary | Completed | Load_239399 | Oracabessa - 210 | 2026-08-23 14:02 | 2026-08-23 14:03 | 2026-08-23 15:46 | 2026-08-23 15:46 | 2026-08-23 17:18 | 2026-08-23 17:00 | 2026-08-23 17:19 | 2026-08-23 17:19 | Fire |  | Fair | No | Customer couldn’t be contacted.
Outage | J.E.26.08.35069 | C001897597 | Romaine Roberts | St.Mary | Completed | Load_238782 | Highgate -110 | 2026-08-23 14:02 | 2026-08-23 14:03 | 2026-08-23 15:33 | 2026-08-23 17:19 | 2026-08-23 17:26 | 2026-08-23 17:26 | 2026-08-23 17:30 | 2026-08-23 17:30 | BrokenWire |  | Fair | No | After carrying out several checks voltage found 118-112 -232 however customer have internal fault at premises advise customer to get electrician
Outage | J.E.26.08.35071 | C001897600 | Omar King | St.Ann | Completed | Load_258982 | Ocho Rios - 310 | 2026-08-23 14:06 | 2026-08-23 14:58 | 2026-08-23 16:06 | 2026-08-23 16:07 | 2026-08-23 18:11 | 2026-08-23 18:50 | 2026-08-23 18:51 | 2026-08-23 18:51 |  |  | Fair | No | Found customer service wire broken from premises as been repaired customer is now with supply
Outage | J.E.26.08.35062 | C001897602 | Damion Reid | Manchester | Completed | Load_293020 | Spur Tree - 310 | 2026-08-23 14:09 | 2026-08-23 15:12 | 2026-08-23 16:48 | 2026-08-23 16:48 | 2026-08-23 17:44 | 2026-08-23 18:17 | 2026-08-23 18:19 | 2026-08-23 18:19 |  |  | Fair | No | Customer say she did not make any report
Outage | J.E.26.08.35079 | C001897603 | Andre Williams | Trelawny | Completed | Load_302690 | Duncans - 210 | 2026-08-23 14:21 | 2026-08-23 15:02 | 2026-08-23 17:27 | 2026-08-23 17:28 | 2026-08-23 18:46 | 2026-08-23 18:48 | 2026-08-23 18:48 | 2026-08-23 18:48 |  |  | Fair | No | Voltage at meter pole 116+117=233 current heading to premises 117+116=233 on load side of meter
Outage | J.E.26.08.35078 | C001897604 | Wayne Dillion | St.Elizabeth | Completed | Load_264993 | Maggotty - 110 | 2026-08-23 14:26 | 2026-08-23 14:27 | 2026-08-23 15:55 | 2026-08-23 15:55 | 2026-08-23 15:55 | 2026-08-23 15:56 | 2026-08-23 15:56 | 2026-08-23 15:56 |  |  | Fair | No | Please refer this call to the field services department.
Outage | J.E.26.08.35097 | C001897614 | Lancelot Brown | Hanover | Completed | Load_259314 | Orange Bay - 310 | 2026-08-23 14:51 | 2026-08-23 14:52 | 2026-08-23 16:18 | 2026-08-23 16:19 | 2026-08-23 17:03 | 2026-08-23 17:14 | 2026-08-23 17:15 | 2026-08-23 17:15 |  |  | Fair | No | Check and found customer disconnected customer pay bill but did not got reconnected with the assistance of customer care customer was reconnected vl at meter socket 115-113-228 supply restore
Non-Outage | J.E.26.08.34961 | C001897620 | Milton Charlton | KSAN | Completed | Load_253447 | Hope - 510 | 2026-08-23 15:06 | 2026-08-23 15:06 | 2026-08-23 16:12 | 2026-08-23 16:13 | 2026-08-23 17:14 | 2026-08-23 17:15 | 2026-08-23 17:16 | 2026-08-23 17:16 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.34845 | C001897622 | Edward Royal | KSAN | Completed | Load_262331 | Washington Blvd - 310 | 2026-08-23 15:08 | 2026-08-23 15:09 | 2026-08-23 17:21 | 2026-08-23 17:21 | 2026-08-23 17:41 | 2026-08-23 17:41 | 2026-08-23 17:45 | 2026-08-23 17:45 |  |  | Fair | No | Premises found ok voltage reading 115v 116v 230v
Outage | J.E.26.08.35042 | C001897621 | Edward Royal | KSAS | Completed | Load_263472 | Hunts Bay - 310 | 2026-08-23 15:08 | 2026-08-23 15:09 | 2026-08-23 17:48 | 2026-08-23 17:49 | 2026-08-23 18:12 | 2026-08-23 18:57 | 2026-08-23 18:58 | 2026-08-23 18:58 |  |  | Fair | No | Customer have internal problems advice customer to get a electrician to fix the problem voltage reading 115v 114 v 228.7
Non-Outage | J.E.26.08.32291 | C001897629 | Derrick Dawkins |  | Completed |  |  | 2026-08-23 15:09 | 2026-08-23 15:10 | 2026-08-23 16:12 | 2026-08-23 16:12 | 2026-08-23 17:28 | 2026-08-23 17:29 | 2026-08-23 17:33 | 2026-08-23 17:33 | BrokenWire |  | Fair | No | Flow cable wire hanging low
Non-Outage | J.E.26.08.32622 | C001897628 | Derrick Dawkins | St.James | Completed | Load_264461 | Bogue - 310 | 2026-08-23 15:09 | 2026-08-23 15:10 | 2026-08-23 20:15 | 2026-08-23 20:39 | 2026-08-23 20:39 | 2026-08-23 20:47 | 2026-08-23 20:48 | 2026-08-23 20:48 |  |  | Fair | No | Found 30ft class6 pole rotten twisted secondary. needs be change also customer station holding up pole refer back to m
Outage | J.E.26.08.35111 | C001897630 | Roxroy Needham | St.Ann | Completed | Load_264943 | Cardiff Hall - 210 | 2026-08-23 15:11 | 2026-08-23 15:11 | 2026-08-23 15:20 | 2026-08-23 15:20 | 2026-08-23 15:55 | 2026-08-23 15:54 | 2026-08-23 15:56 | 2026-08-23 15:56 |  |  | Fair | No | Premises found ok customer say that JPS team come before
Non-Outage | J.E.26.08.32123 | C001897636 | Andre Williams | Trelawny | Completed | Load_302540 | Martha Brae - 210 | 2026-08-23 15:12 | 2026-08-23 15:13 | 2026-08-23 15:37 | 2026-08-23 20:50 | 2026-08-23 21:57 | 2026-08-23 22:25 | 2026-08-23 22:39 | 2026-08-23 22:39 |  |  | Fair | No | Area found with supply after driving through
Non-Outage | J.E.26.08.32175 | C001897635 | Andre Williams | Trelawny | Completed | Load_292361 | Greenwood - 210 | 2026-08-23 15:12 | 2026-08-23 15:13 | 2026-08-23 15:50 | 2026-08-23 15:50 | 2026-08-23 16:20 | 2026-08-23 17:13 | 2026-08-23 17:14 | 2026-08-23 17:14 |  |  | Fair | No | Illegal conection causing voltage to drop volage at 100 kva transformer 116+116=232 voltage after 2 pole span was down 105+103=208 after removing four illegal conection voltage rose to 116+114= 230 volts multiple illegal conection at end still causing drop to 108+105=213; reffer to loses to remove illegal conection on line ( 100 kva also leaking but still in service )
Non-Outage | J.E.26.08.32409 | C001897634 | Andre Williams | Trelawny | Completed | Load_260728 | Martha Brae - 110 | 2026-08-23 15:12 | 2026-08-23 15:13 | 2026-08-23 19:45 | 2026-08-23 19:46 | 2026-08-23 20:07 | 2026-08-23 20:08 | 2026-08-23 20:08 | 2026-08-23 20:08 |  |  | Fair | No | area with supply
Non-Outage | J.E.26.08.32716 | C001897633 | Andre Williams | Trelawny | Completed | Load_302479 | Duncans - 210 | 2026-08-23 15:12 | 2026-08-23 15:13 | 2026-08-23 18:52 | 2026-08-23 18:53 | 2026-08-23 19:37 | 2026-08-23 19:38 | 2026-08-23 19:45 | 2026-08-23 19:45 |  |  | Fair | No | Area ok and with supply power was restored two days ago
Non-Outage | J.E.26.08.34666 | C001897632 | Andre Williams | Trelawny | Completed | Load_249410 | Greenwood - 210 | 2026-08-23 15:12 | 2026-08-23 15:13 | 2026-08-23 17:21 | 2026-08-23 17:22 | 2026-08-23 17:22 | 2026-08-23 17:22 | 2026-08-23 17:23 | 2026-08-23 17:23 |  |  | Fair | No | Unable to locate individual customer
Non-Outage | J.E.26.08.34831 | C001897631 | Andre Williams | Trelawny | Completed | Load_249410 | Greenwood - 210 | 2026-08-23 15:12 | 2026-08-23 15:13 | 2026-08-23 17:20 | 2026-08-23 17:20 | 2026-08-23 17:20 | 2026-08-23 17:21 | 2026-08-23 17:21 | 2026-08-23 17:21 |  |  | Fair | No | Unable to locate phone not answering need more directions to locate individual customer
Non-Outage | J.E.26.08.10348 | C001897639 | Stephen Taylor | St.Thomas | Completed | Load_251845 | Lysson - 410 | 2026-08-23 15:14 | 2026-08-23 15:15 | 2026-08-23 16:20 | 2026-08-23 16:20 | 2026-08-23 16:20 | 2026-08-23 16:20 | 2026-08-23 16:21 | 2026-08-23 16:21 |  |  | Fair | No | Retention service wire 3 clamps customer is now okay
Non-Outage | J.E.26.08.11311 | C001897640 | Stephen Taylor | St.Thomas | Completed | Load_239634 | Lysson - 410 | 2026-08-23 15:14 | 2026-08-23 15:15 | 2026-08-23 15:32 | 2026-08-23 15:33 | 2026-08-23 15:33 | 2026-08-23 15:33 | 2026-08-23 15:33 | 2026-08-23 15:33 | Fire |  | Fair | No | Call to customer and customer said power is back now and okay
Non-Outage | J.E.26.08.12462 | C001897641 | Stephen Taylor | St.Thomas | Completed | Load_239634 | Lysson - 410 | 2026-08-23 15:14 | 2026-08-23 15:15 | 2026-08-23 15:31 | 2026-08-23 15:31 | 2026-08-23 15:31 | 2026-08-23 15:31 | 2026-08-23 15:32 | 2026-08-23 15:32 | Fire |  | Fair | No | Retention service wire 3 clamps
Non-Outage | J.E.26.08.13208 | C001897643 | Stephen Taylor | St.Thomas | Completed | Load_254225 | Lysson - 410 | 2026-08-23 15:14 | 2026-08-23 15:15 | 2026-08-23 15:34 | 2026-08-23 15:35 | 2026-08-23 16:13 | 2026-08-23 16:14 | 2026-08-23 16:16 | 2026-08-23 16:16 |  |  | Fair | No | Need a local # to contact customer to find location
Non-Outage | J.E.26.08.16779 | C001897642 | Stephen Taylor | St.Thomas | Completed | Load_249385 | Lysson - 410 | 2026-08-23 15:14 | 2026-08-23 15:15 | 2026-08-23 16:22 | 2026-08-23 16:22 | 2026-08-23 16:24 | 2026-08-23 16:29 | 2026-08-23 16:30 | 2026-08-23 16:30 |  |  | Fair | No | Clean up single phase and use one one bolt clamp
Outage | J.E.26.08.35006 | C001897647 | Richard Nicholas | St.Catherine | Completed | Load_264519 | New Michelton - 210 | 2026-08-23 15:19 | 2026-08-23 15:28 | 2026-08-23 15:44 | 2026-08-23 15:45 | 2026-08-23 18:10 | 2026-08-23 19:36 | 2026-08-23 19:38 | 2026-08-23 19:38 |  |  | Rains | No | Replaced blown 20amp junctions fuse on pole #199871, replaced blown 15amp junctions fuse near to pole #0128311 and blown 8amp junctions fuse near to pole #0104063.
Outage | J.E.26.08.35009 | C001897645 | Richard Nicholas | St.Catherine | Completed | Load_267801 | New Michelton - 210 | 2026-08-23 15:19 | 2026-08-23 15:28 | 2026-08-23 20:24 | 2026-08-23 20:25 | 2026-08-23 21:13 | 2026-08-23 21:45 | 2026-08-23 21:48 | 2026-08-23 21:48 |  |  | Fair | No | Premises not located however supply found ok in the area.
Outage | J.E.26.08.35011 | C001897646 | Richard Nicholas | St.Catherine | Completed | Load_244435 | New Michelton - 210 | 2026-08-23 15:19 | 2026-08-23 15:28 | 2026-08-23 19:40 | 2026-08-23 19:41 | 2026-08-23 19:40 | 2026-08-23 19:40 | 2026-08-23 19:41 | 2026-08-23 19:41 |  |  | Rains | No | Area found ok
Outage | J.E.26.08.35114 | C001897650 | Richard Nicholas | St.Catherine | Completed | Load_242271 | New Michelton - 310 | 2026-08-23 15:28 | 2026-08-23 15:29 | 2026-08-23 19:41 | 2026-08-23 19:42 | 2026-08-23 20:07 | 2026-08-23 20:23 | 2026-08-23 20:24 | 2026-08-23 20:24 |  |  | Fair | No | Area found ok
Outage | J.E.26.08.35070 | C001897651 | Nickolas Rodriques | Portmore | Completed | Load_252969 | Naggo Head - 610 | 2026-08-23 15:29 | 2026-08-23 15:30 | 2026-08-23 18:14 | 2026-08-23 18:21 | 2026-08-23 18:56 | 2026-08-23 19:24 | 2026-08-23 19:34 | 2026-08-23 19:34 |  |  | Fair | No | Unable to locate or communicate with the customer after several attempts. Need proper directions.
Non-Outage | J.E.26.08.34761 | C001897653 | Horace Malcolm | St.James | Completed | Load_258893 | Bogue - 610 | 2026-08-23 15:31 | 2026-08-24 08:46 | 2026-08-24 13:54 | 2026-08-24 13:55 | 2026-08-24 14:04 | 2026-08-24 15:18 | 2026-08-24 15:18 | 2026-08-24 15:18 |  |  | Fair | No | Check and found transformer at top 3 voltage 104-106-212 after putting transformer at top 4 voltage 115-116-232
Outage | J.E.26.08.35099 | C001897652 | Wan Carlos Scarlett | St.Catherine | Completed | Load_248503 | Tredegar - 310 | 2026-08-23 15:31 | 2026-08-23 15:34 | 2026-08-23 15:39 | 2026-08-23 15:39 | 2026-08-23 16:27 | 2026-08-23 16:48 | 2026-08-23 16:52 | 2026-08-23 16:52 |  |  | Fair | No | Refuse 25 KVA Transformer with 3 Amp fuse no pole # was found also found transformer dripping oil power supply has been restored
Outage | J.E.26.08.34968 | C001897655 | Wan Carlos Scarlett | St.Catherine | Completed | Load_267379 | Tredegar - 310 | 2026-08-23 15:32 | 2026-08-23 15:34 | 2026-08-23 16:39 | 2026-08-23 16:52 | 2026-08-23 17:04 | 2026-08-23 17:07 | 2026-08-23 17:08 | 2026-08-23 17:08 |  |  | Fair | No | Customer confirmed power supply was restored call related to outage earlier
Outage | J.E.26.08.34910 | C001897657 | Wan Carlos Scarlett | St.Catherine | Completed | Load_261464 | Tredegar - 210 | 2026-08-23 15:33 | 2026-08-23 15:34 | 2026-08-23 17:08 | 2026-08-23 17:08 | 2026-08-23 17:28 | 2026-08-23 17:42 | 2026-08-23 17:43 | 2026-08-23 17:43 |  |  | Fair | No | Reach on location been calling customer but got no answer premises closed
Non-Outage | J.E.26.08.35144 | C001897658 | Nickolas Rodriques | Portmore | Completed | Load_261773 | Naggo Head - 610 | 2026-08-23 15:43 | 2026-08-23 15:45 | 2026-08-23 15:51 | 2026-08-23 16:08 | 2026-08-23 17:07 | 2026-08-23 18:01 | 2026-08-23 18:13 | 2026-08-23 18:13 |  |  | Fair | No | Customer stated that she is experiencing on and off supply, reading found (120-120-240). Three one-bolt clamps were replaced both at pothead and pole. Current reading (120-120-240). Customer confirmed that all is well now.
Outage | J.E.26.08.35112 | C001897659 | Hartley Chin | Clarendon | Completed | Load_266472 | May Pen - 110 | 2026-08-23 15:48 | 2026-08-23 15:49 | 2026-08-23 16:01 | 2026-08-23 20:10 | 2026-08-23 20:10 | 2026-08-23 19:48 | 2026-08-23 20:10 | 2026-08-23 20:10 |  |  | Fair | No | Found blown 3 amp fuse on 25 KVA transformer @ 0106491 line patrolled and found okay , transformer refused …
Outage | J.E.26.08.34951 | C001897660 | Neville Spencer | St.Catherine | Completed | Load_263189 | Rhodens Pen - 310 | 2026-08-23 15:50 | 2026-08-23 15:51 | 2026-08-24 09:16 | 2026-08-24 09:17 | 2026-08-24 09:48 | 2026-08-24 09:48 | 2026-08-24 09:50 | 2026-08-24 09:50 | Fire |  | Fair | No | Found supply at location no fire seen at location
Outage | J.E.26.08.34861 | C001897662 | Neville Spencer | Clarendon | Completed | Load_267623 | Parnassus - 210 | 2026-08-23 15:52 | 2026-08-23 16:01 | 2026-08-23 19:12 | 2026-08-23 19:13 | 2026-08-23 19:13 | 2026-08-23 19:13 | 2026-08-23 19:15 | 2026-08-23 19:15 |  | Y | Fair | No | Cleared bamboo from 13.8 kv line renew blown 15 amp J / fuse at pole # 0059701 supply restored.
Outage | J.E.26.08.35149 | C001897664 | Neville Spencer | Clarendon | Completed | Load_258960 | Monymusk - 410 | 2026-08-23 15:58 | 2026-08-23 16:01 | 2026-08-23 19:18 | 2026-08-23 19:19 | 2026-08-23 20:27 | 2026-08-23 20:27 | 2026-08-23 20:48 | 2026-08-23 20:48 |  | Y | Fair | No | Cleared tree limb from secondary lines renew blown 3 amp fuse protecting 25 kva xmfr at pole # 016479 supply restored.
Outage | J.E.26.08.35000 | C001897667 | Raymond Carr | St.Mary | Completed | Load_268047 | Oracabessa - 210 | 2026-08-23 16:05 | 2026-08-23 16:06 | 2026-08-23 17:20 | 2026-08-23 17:20 | 2026-08-23 17:56 | 2026-08-23 17:37 | 2026-08-23 17:57 | 2026-08-23 17:57 |  |  | Fair | No | Supply was restored.
Outage | J.E.26.08.35163 | C001897668 | Omar King | St.Ann | Completed | Load_247851 | Roaring River - 210 | 2026-08-23 16:06 | 2026-08-23 16:07 | 2026-08-23 18:51 | 2026-08-23 18:51 | 2026-08-23 20:19 | 2026-08-23 20:21 | 2026-08-23 20:21 | 2026-08-23 20:21 | BrokenWire |  | Fair | No | Unable to find customer call several times no answer directions not sufficient
Outage | J.E.26.08.35121 | C001897670 | Fitzroy Turner | KSAS | Completed | Load_248011 | Duhaney - 310 | 2026-08-23 16:07 | 2026-08-23 16:39 | 2026-08-23 17:52 | 2026-08-23 17:52 | 2026-08-23 18:02 | 2026-08-23 18:03 | 2026-08-23 18:05 | 2026-08-23 18:05 |  |  | Fair | No | Customer supply restored after replace 30amps junction fuse at pole number 515983 cause by bird
Outage | J.E.26.08.35170 | C001897672 | Derrick Dawkins | St.James | Completed | Load_260989 | Bogue - 510 | 2026-08-23 16:10 | 2026-08-23 16:10 | 2026-08-23 21:48 | 2026-08-23 21:49 | 2026-08-23 21:48 | 2026-08-23 20:40 | 2026-08-23 21:52 | 2026-08-23 21:52 |  |  | Fair | No | Found area ok
Outage | J.E.26.08.35182 | C001897671 | Derrick Dawkins | St.James | Completed | Load_1001320 | Bogue - 510 | 2026-08-23 16:10 | 2026-08-23 16:10 | 2026-08-23 17:35 | 2026-08-23 17:35 | 2026-08-23 17:59 | 2026-08-23 20:07 | 2026-08-23 20:15 | 2026-08-23 20:15 |  |  | Fair | No | Found 2 80amp junction fuse blown due to rain also switch defective need to replace refer to maintenance
Outage | J.E.26.08.35178 | C001897673 | Elvis Trowers | KSAN | Completed | Load_557772 | Washington Blvd - 810 | 2026-08-23 16:11 | 2026-08-23 16:12 | 2026-08-23 17:38 | 2026-08-23 17:38 | 2026-08-23 18:07 | 2026-08-23 18:00 | 2026-08-23 18:09 | 2026-08-23 18:09 |  |  | Fair | No | Found okay upon arrival. Customer states matter was resolved.
Outage | J.E.26.08.35117 | C001897678 | Fitzroy Turner | KSAS | Completed | Load_578715 | Duhaney - 310 | 2026-08-23 16:12 | 2026-08-23 16:16 | 2026-08-23 17:27 | 2026-08-23 17:28 | 2026-08-23 17:43 | 2026-08-23 17:50 | 2026-08-23 17:51 | 2026-08-23 17:51 |  |  | Fair | No | Customer supply restored after replace blown 30amps junction fuse pole number 515983
Outage | J.E.26.08.35138 | C001897677 | Fitzroy Turner | KSAS | Completed | Load_268920 | Duhaney - 310 | 2026-08-23 16:12 | 2026-08-23 16:16 | 2026-08-23 16:32 | 2026-08-23 16:33 | 2026-08-23 16:58 | 2026-08-23 17:22 | 2026-08-23 17:27 | 2026-08-23 17:27 |  |  | Fair | No | Found 30amps junction fuse blown at the intersection of ebenezer avenue new heaven dr cause by birds replaced one 30amps fuse supply restored to the areas
Non-Outage | J.E.26.08.34770 | C001897679 | Hartley Chin | Clarendon | Completed | Load_245514 | Parnassus - 210 | 2026-08-23 16:13 | 2026-08-23 16:14 | 2026-08-23 16:21 | 2026-08-23 16:22 | 2026-08-23 16:21 | 2026-08-23 16:38 | 2026-08-23 16:40 | 2026-08-23 16:40 |  |  | Fair | No | Found blown 20 amp junction fuse, line patrolled and found okay , junction refused..
Outage | J.E.26.08.35118 | C001897680 | Elvis Trowers | KSAN | Completed | Load_238415 | Washington Blvd - 510 | 2026-08-23 16:16 | 2026-08-23 16:41 | 2026-08-23 18:09 | 2026-08-23 18:09 | 2026-08-23 18:32 | 2026-08-23 18:35 | 2026-08-23 18:35 | 2026-08-23 18:35 |  |  | Fair | No | Found okay upon arrival. Customer states matter was resolved.
Outage | J.E.26.08.35174 | C001897681 | Edward Royal | KSAN | Completed | Load_262209 | Washington Blvd - 310 | 2026-08-23 16:18 | 2026-08-23 16:19 | 2026-08-23 16:29 | 2026-08-23 16:30 | 2026-08-23 16:29 | 2026-08-23 17:20 | 2026-08-23 17:21 | 2026-08-23 17:21 |  |  | Fair | No | Spliced and reconnected secondary phase open conductor using 2 one bolt clamps 20 ft #2 open conductor voltage reading 114v 115v 229v
Non-Outage | J.E.26.08.35199 | C001897683 | Raheem Ricketts |  | Completed |  |  | 2026-08-23 16:28 | 2026-08-23 16:53 | 2026-08-23 17:05 | 2026-08-23 17:09 | 2026-08-23 18:54 | 2026-08-23 19:14 | 2026-08-23 19:14 | 2026-08-23 19:14 |  |  | Fair | No | Check and found customer experiencing an internal problem voltage 113,113 226
Non-Outage | J.E.26.08.34808 | C001897685 | Collin Robinson | Portland | Completed | Load_259632 | Port Antonio - 410 | 2026-08-23 16:37 | 2026-08-23 16:38 | 2026-08-23 16:51 | 2026-08-23 16:52 | 2026-08-23 18:08 | 2026-08-23 18:22 | 2026-08-23 18:22 | 2026-08-23 18:22 |  |  | Fair | No | Change one corroded one bolt clamp that connects service neutral to pothead Voltage reading 117v 118v 235v
Outage | J.E.26.08.35204 | C001897686 | Elvis Trowers | KSAN | Completed | Load_248841 | Constant Spring - 210 | 2026-08-23 16:41 | 2026-08-23 19:51 | 2026-08-23 20:00 | 2026-08-23 20:41 | 2026-08-23 21:00 | 2026-08-23 21:20 | 2026-08-23 21:31 | 2026-08-23 21:31 |  |  | Fair | No | Found one 15 amps junction fuse blown at pole# 0011020 and one 5 amps transformer fuse blown at pole #0011021. Refused using one 15 amps fuse and one 5 amps fuse and reclosed junction and transformer switches. Remove wisp and vine from transformer primary bushing.
Outage | J.E.26.08.35137 | C001897687 | Damion Reid | Manchester | Completed | Load_237923 | Porus - 310 | 2026-08-23 16:44 | 2026-08-23 16:48 | 2026-08-23 18:19 | 2026-08-23 18:20 | 2026-08-23 19:46 | 2026-08-23 20:26 | 2026-08-23 20:29 | 2026-08-23 20:29 |  |  | Fair | No | Blown 2amp fuse found for 5kva transformer line patrol nothing was found blown fuse replace
Outage | J.E.26.08.35201 | C001897689 | Milton Charlton | KSAS | Completed | Load_269244 | Up Park Camp - 310 | 2026-08-23 16:46 | 2026-08-23 16:46 | 2026-08-23 17:26 | 2026-08-23 17:27 | 2026-08-23 18:21 | 2026-08-23 17:55 | 2026-08-23 18:28 | 2026-08-23 18:28 |  |  | Fair | No | Pole #0052665 with 3-100 kva transformer bank. Middle switch top blow off fuse holder burn up. Need to replace defective D/O switch.
Non-Outage | J.E.26.08.34948 | C001897691 | Javid Vernon |  | Completed |  |  | 2026-08-23 16:49 | 2026-08-23 18:44 | 2026-08-23 18:52 | 2026-08-23 18:53 | 2026-08-23 18:52 | 2026-08-23 18:54 | 2026-08-23 18:54 | 2026-08-23 18:54 | Fire |  | Fair | No | Customer stated that the issue was resolved from earlier today
Outage | J.E.26.08.35053 | C001897692 | Richman Whyte | Westmoreland | Completed | Load_292821 | Paradise - 310 | 2026-08-23 16:49 | 2026-08-23 16:58 | 2026-08-23 18:45 | 2026-08-23 18:46 | 2026-08-23 18:45 | 2026-08-23 18:46 | 2026-08-23 18:47 | 2026-08-23 18:47 |  |  | Fair | No | Customer states she never reported any problems and light is in the area
Non-Outage | J.E.26.08.34285 | C001897693 | Richman Whyte |  | Completed |  |  | 2026-08-23 16:51 | 2026-08-23 16:58 | 2026-08-23 18:47 | 2026-08-23 18:48 | 2026-08-23 18:47 | 2026-08-23 18:47 | 2026-08-23 18:48 | 2026-08-23 18:48 |  |  | Fair | No | Customer states that power was restored from yesterday
Outage | J.E.26.08.34280 | C001897695 | Richman Whyte | Westmoreland | Completed | Load_245296 | Paradise - 310 | 2026-08-23 16:55 | 2026-08-23 16:58 | 2026-08-23 18:56 | 2026-08-23 18:56 | 2026-08-23 18:56 | 2026-08-23 18:56 | 2026-08-23 18:57 | 2026-08-23 18:57 |  |  | Fair | No | Need direction and call to customer went unanswered
Outage | J.E.26.08.34247 | C001897698 | Richman Whyte | Westmoreland | Completed | Load_244780 | Paradise - 310 | 2026-08-23 16:56 | 2026-08-23 16:58 | 2026-08-23 18:32 | 2026-08-23 18:32 | 2026-08-23 18:32 | 2026-08-23 18:32 | 2026-08-23 18:33 | 2026-08-23 18:33 |  |  | Fair | No | Customer states that power was restored
Outage | J.E.26.08.34272 | C001897697 | Richman Whyte | Westmoreland | Completed | Load_244225 | Paradise - 310 | 2026-08-23 16:56 | 2026-08-23 16:58 | 2026-08-23 18:48 | 2026-08-23 18:49 | 2026-08-23 18:48 | 2026-08-23 18:49 | 2026-08-23 18:50 | 2026-08-23 18:50 |  |  | Fair | No | Customer states that power is okay in the area and at his premises
Outage | J.E.26.08.34275 | C001897696 | Richman Whyte | Westmoreland | Completed | Load_251525 | Paradise - 310 | 2026-08-23 16:56 | 2026-08-23 16:58 | 2026-08-23 18:29 | 2026-08-23 18:30 | 2026-08-23 18:29 | 2026-08-23 18:30 | 2026-08-23 18:31 | 2026-08-23 18:31 |  |  | Fair | No | Customer stated power was restored from yesterday
Outage | J.E.26.08.34601 | C001897699 | Richman Whyte | Westmoreland | Completed | Load_244384 | Paradise - 310 | 2026-08-23 16:57 | 2026-08-23 17:00 | 2026-08-23 18:57 | 2026-08-23 18:58 | 2026-08-23 18:57 | 2026-08-23 18:58 | 2026-08-23 18:59 | 2026-08-23 18:59 |  |  | Fair | No | Unable to locate need direction and call to customer went unanswered
Outage | J.E.26.08.34289 | C001897701 | Javid Vernon | Westmoreland | Completed | Load_268497 | Paradise - 110 | 2026-08-23 16:58 | 2026-08-23 17:01 | 2026-08-23 17:28 | 2026-08-23 17:29 | 2026-08-23 17:28 | 2026-08-23 17:29 | 2026-08-23 17:30 | 2026-08-23 17:30 |  |  | Fair | No | Customer stated that power was restored
Outage | J.E.26.08.34290 | C001897700 | Javid Vernon | Westmoreland | Completed | Load_292400 | Paradise - 110 | 2026-08-23 16:58 | 2026-08-23 17:01 | 2026-08-23 17:30 | 2026-08-23 17:30 | 2026-08-23 17:30 | 2026-08-23 17:30 | 2026-08-23 17:31 | 2026-08-23 17:31 |  |  | Fair | No | Customer stated that power was restored
Outage | J.E.26.08.34270 | C001897702 | Javid Vernon | Westmoreland | Completed | Load_292588 | Paradise - 110 | 2026-08-23 16:59 | 2026-08-23 17:01 | 2026-08-23 17:06 | 2026-08-23 17:07 | 2026-08-23 17:21 | 2026-08-23 17:26 | 2026-08-23 17:26 | 2026-08-23 17:26 |  |  | Fair | No | Customer stated that power was restored
Outage | J.E.26.08.35241 | C001897707 | Milton Charlton | KSAS | Completed | Load_240363 | Up Park Camp - 410 | 2026-08-23 17:14 | 2026-08-24 07:28 | 2026-08-24 09:08 | 2026-08-24 09:08 | 2026-08-24 09:48 | 2026-08-24 09:35 | 2026-08-24 09:50 | 2026-08-24 09:50 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Non-Outage | J.E.26.08.34959 | C001897708 | Milton Charlton |  | Completed |  |  | 2026-08-23 17:17 | 2026-08-23 17:18 | 2026-08-23 18:28 | 2026-08-23 18:28 | 2026-08-23 19:10 | 2026-08-23 19:05 | 2026-08-23 19:16 | 2026-08-23 19:16 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Non-Outage | J.E.26.08.34908 | C001897709 | Milton Charlton | KSAN | Completed | Load_244468 | Hope - 410 | 2026-08-23 17:20 | 2026-08-24 07:28 | 2026-08-24 08:25 | 2026-08-24 08:26 | 2026-08-24 09:02 | 2026-08-24 09:05 | 2026-08-24 09:03 | 2026-08-24 09:03 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Non-Outage | J.E.26.08.34917 | C001897710 | Milton Charlton | KSAN | Completed | Load_244468 | Hope - 410 | 2026-08-23 17:20 | 2026-08-23 19:17 | 2026-08-23 20:15 | 2026-08-23 20:16 | 2026-08-23 20:42 | 2026-08-23 21:10 | 2026-08-23 21:10 | 2026-08-23 21:10 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.35219 | C001897712 | Elvis Trowers | KSAN | Completed | Load_240204 | Constant Spring - 210 | 2026-08-23 17:21 | 2026-08-23 19:51 | 2026-08-23 20:01 | 2026-08-23 21:31 | 2026-08-23 22:38 | 2026-08-23 22:40 | 2026-08-23 22:39 | 2026-08-23 22:39 |  |  | Fair | No | Found okay upon arrival. Customer states matter was resolved. Breaker tripped.
Outage | J.E.26.08.35275 | C001897721 | Raheem Ricketts | St.Elizabeth | Completed | Load_295424 | Maggotty - 210 | 2026-08-23 18:06 | 2026-08-23 18:14 | 2026-08-23 19:58 | 2026-08-23 19:58 | 2026-08-23 20:42 | 2026-08-23 20:43 | 2026-08-23 20:53 | 2026-08-23 20:53 | Fire |  | Fair | No | Unable to locate customer cell number went straight voicemail after multiple calls however I drove through the community an power is everywhere
Outage | J.E.26.08.35283 | C001897722 | Marlon Authors | St.Elizabeth | Completed | Load_239122 | Maggotty - 210 | 2026-08-23 18:06 | 2026-08-23 18:15 | 2026-08-23 20:14 | 2026-08-23 20:15 | 2026-08-23 21:30 | 2026-08-23 22:15 | 2026-08-23 22:15 | 2026-08-23 22:15 |  |  | Fair | No | Patrol and found clear. Replace one blown 15 amp junction fuse no pole #. Restored supply ok
Outage | J.E.26.08.35272 | C001897723 | Marlon Authors | Manchester | Completed | Load_260168 | Spur Tree - 210 | 2026-08-23 18:07 | 2026-08-23 18:15 | 2026-08-24 16:54 | 2026-08-24 16:55 | 2026-08-24 16:54 | 2026-08-24 16:56 | 2026-08-24 16:55 | 2026-08-24 16:55 |  |  | Fair | No | Customer said supply was restored
Outage | J.E.26.08.35286 | C001897724 | Marlon Authors | St.Elizabeth | Completed | Load_292313 | Maggotty - 110 | 2026-08-23 18:11 | 2026-08-23 18:15 | 2026-08-23 18:32 | 2026-08-23 18:32 | 2026-08-23 19:58 | 2026-08-23 20:03 | 2026-08-23 20:03 | 2026-08-23 20:03 |  |  | Fair | No | Patrol and found clear. Replace one blown 15 amp junction fuse no pole #. Restored supply okay
Non-Outage | J.E.26.08.31899 | C001897728 | Lancelot Brown | Hanover | Completed | Load_292794 | Orange Bay - 310 | 2026-08-23 18:26 | 2026-08-23 18:27 | 2026-08-23 19:10 | 2026-08-23 21:23 | 2026-08-23 22:20 | 2026-08-23 22:37 | 2026-08-23 22:38 | 2026-08-23 22:38 |  |  | Fair | No | Splice and retention triplex service nutral used five feet #6 vl at pothead 112-114-227 supply restore
Non-Outage | J.E.26.08.32021 | C001897727 | Lancelot Brown | Hanover | Completed | Load_239009 | Orange Bay - 310 | 2026-08-23 18:26 | 2026-08-23 18:27 | 2026-08-23 19:10 | 2026-08-23 19:18 | 2026-08-23 19:56 | 2026-08-23 21:22 | 2026-08-23 21:22 | 2026-08-23 21:22 |  |  | Fair | No | Customers complained of low voltage checks voltage at customer location 92-96-188 a closer to transformer voltage reading 99-97-196 at transformer location voltage reading 111-110-221 check secondary topping and it is all out circuit need to split please pass on to maintenance department in Hanover mr Richards need ergent
Non-Outage | J.E.26.08.32318 | C001897726 | Rayon Foster | Hanover | Completed | Load_252846 | Orange Bay - 210 | 2026-08-23 18:26 | 2026-08-24 08:22 | 2026-08-24 12:20 | 2026-08-24 12:21 | 2026-08-24 12:59 | 2026-08-24 14:02 | 2026-08-24 14:02 | 2026-08-24 14:02 |  |  | Fair | No | Voltage check at pathead 110/109AB219 head of clinic said we could not do a meter pull presently because the clinic is in full apparation now meter is blank refer to field service to check blank meter
Outage | J.E.26.08.35266 | C001897735 | Hartley Chin | Clarendon | Completed | Load_239300 | May Pen - 110 | 2026-08-23 18:38 | 2026-08-23 18:39 | 2026-08-23 18:56 | 2026-08-23 18:57 | 2026-08-23 18:56 | 2026-08-23 19:02 | 2026-08-23 19:02 | 2026-08-23 19:02 | BrokenPole,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards | Y | Fair | No | Ref to maintenance!!! Found broken 30ft pole with 2/0 twisted … pole requires urgent attention … service wire was isolated @ a point leaving approximately 4 customers without supply… tree fell on pole and impact causes it to break ..
Outage | J.E.26.08.35284 | C001897734 | Hartley Chin | Clarendon | Completed | Load_246673 | May Pen - 110 | 2026-08-23 18:38 | 2026-08-23 18:39 | 2026-08-23 20:12 | 2026-08-23 21:20 | 2026-08-23 21:19 | 2026-08-23 21:34 | 2026-08-23 21:52 | 2026-08-23 21:52 | BrokenWire |  | Fair | No | Isolate 25 KVA transformer @ pole # 0106464 due to broken open secondary neutral found in 1 span , repair broken neutral, re-energized transformer…
Outage | J.E.26.08.35301 | C001897733 | Wan Carlos Scarlett | St.Catherine | Completed | Load_247583 | Tredegar - 310 | 2026-08-23 18:38 | 2026-08-23 18:39 | 2026-08-23 18:46 | 2026-08-23 18:47 | 2026-08-23 19:10 | 2026-08-23 19:10 | 2026-08-23 19:16 | 2026-08-23 19:16 |  |  | Fair | No | Found 25 KVA transformer defective transformer leaking oil no pole # was found need maintenance department to replace transformer
Outage | J.E.26.08.35291 | C001897736 | Nickolas Rodriques | Portmore | Completed | Load_251066 | Naggo Head - 610 | 2026-08-23 18:39 | 2026-08-23 18:40 | 2026-08-23 19:37 | 2026-08-23 19:41 | 2026-08-23 20:17 | 2026-08-23 21:33 | 2026-08-23 21:37 | 2026-08-23 21:37 | BrokenPole |  | Fair | No | Customer is reporting a defective streetlight. Refer to streetlight department.
Outage | J.E.26.08.35313 | C001897740 | Wayne Dillion | St.Elizabeth | Completed | Load_239662 | Maggotty - 110 | 2026-08-23 18:59 | 2026-08-24 07:57 | 2026-08-24 10:05 | 2026-08-24 10:05 | 2026-08-24 10:05 | 2026-08-24 10:06 | 2026-08-24 10:06 | 2026-08-24 10:06 |  |  | Fair | No | Customer said supply has been restored from yesterday
Outage | J.E.26.08.35321 | C001897739 | Raheem Ricketts | St.Elizabeth | Completed | Load_261991 | Maggotty - 210 | 2026-08-23 18:59 | 2026-08-23 19:29 | 2026-08-23 19:33 | 2026-08-23 19:33 | 2026-08-23 19:48 | 2026-08-23 19:54 | 2026-08-23 19:54 | 2026-08-23 19:54 |  |  | Fair | No | Check and found okay
Outage | J.E.26.08.35322 | C001897738 | Marlon Authors | St.Elizabeth | Completed | Load_257518 | Maggotty - 110 | 2026-08-23 18:59 | 2026-08-23 19:02 | 2026-08-23 20:04 | 2026-08-23 20:05 | 2026-08-23 20:04 | 2026-08-23 20:13 | 2026-08-23 20:14 | 2026-08-23 20:14 |  |  | Fair | No | Supply restored to the area
Non-Outage | J.E.26.08.35013 | C001897741 | Milton Charlton | KSAN | Completed | Load_575759 | Hope - 310 | 2026-08-23 19:16 | 2026-08-23 19:18 | 2026-08-23 21:10 | 2026-08-23 21:11 | 2026-08-23 21:50 | 2026-08-23 22:15 | 2026-08-23 22:17 | 2026-08-23 22:17 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.35159 | C001897742 | Raheem Ricketts | St.Elizabeth | Completed | Load_261202 | Maggotty - 210 | 2026-08-23 19:18 | 2026-08-23 19:19 | 2026-08-23 19:53 | 2026-08-23 19:55 | 2026-08-23 19:55 | 2026-08-23 19:57 | 2026-08-23 19:58 | 2026-08-23 19:58 |  |  | Fair | No | Customer needs to get an electrician to repair pothead before any connection make
Outage | J.E.26.08.35390 | C001897743 | Elvis Trowers | KSAN | Completed | Load_255898 | Constant Spring - 210 | 2026-08-23 19:19 | 2026-08-24 07:29 | 2026-08-24 12:26 | 2026-08-24 12:26 | 2026-08-24 12:48 | 2026-08-24 13:35 | 2026-08-24 13:37 | 2026-08-24 13:37 | Fire |  | Fair | No | Isolate 25 kva transformer at pole 0011402 and repair open wire phase and neutral come together on burn off. Repair using 50ft #2AA conductor, one #2 preform,one #2/0 preform and four 1- bolt clamps. Reclose 25 kva transformer.
Outage | J.E.26.08.35201 | C001897744 | Fitzroy Turner | KSAS | Completed | Load_269244 | Up Park Camp - 310 | 2026-08-23 19:47 | 2026-08-23 19:49 | 2026-08-23 19:58 | 2026-08-23 19:58 | 2026-08-23 21:17 | 2026-08-23 21:39 | 2026-08-23 21:48 | 2026-08-23 21:48 |  |  | Fair | No | Found bank of three 100kva transformer switches top lick off and tree arrester blown up cause by BUSHING .replace one defective switch one hot line clamps 5ft off #4 copper and tree 10amps fuses .supply restored to customer. Have some tree cut from off transformer.URGENCY BUSHING Needs TO CARRY Out AT THIS Location .please send email to district to have bushing carry out
Outage | J.E.26.08.35169 | C001897746 | Marlon Brown | Trelawny | Completed | Load_264249 | Greenwood - 110 | 2026-08-23 19:50 | 2026-08-24 07:58 | 2026-08-24 12:11 | 2026-08-24 12:12 | 2026-08-24 12:46 | 2026-08-24 12:51 | 2026-08-24 12:51 | 2026-08-24 12:51 |  |  | Fair | No | Defective meter pole, customer service wire is on the ground, customer needs to effect repairs and has been advised to do so.
Outage | J.E.26.08.35267 | C001897747 | Andre Williams | Trelawny | Completed | Load_294305 | Duncans - 110 | 2026-08-23 19:50 | 2026-08-23 19:52 | 2026-08-23 20:09 | 2026-08-23 20:11 | 2026-08-23 20:43 | 2026-08-23 20:48 | 2026-08-23 20:50 | 2026-08-23 20:50 |  |  | Fair | No | Customer meter burnt and defective,reffer to field service to change meter premises without supply
Outage | J.E.26.08.35403 | C001897749 | Damion Reid | Manchester | Completed | Load_293020 | Spur Tree - 310 | 2026-08-23 19:51 | 2026-08-23 19:53 | 2026-08-23 21:54 | 2026-08-23 21:55 | 2026-08-23 22:05 | 2026-08-23 22:42 | 2026-08-23 22:43 | 2026-08-23 22:43 |  |  | Fair | No | Blown 2amp fuse found for 25kva transformer cause by contamination line patrol and replace blown fuse
Outage | J.E.26.08.35134 | C001897750 | Elvis Trowers | KSAS | Completed | Load_267072 | Duhaney - 310 | 2026-08-23 20:01 | 2026-08-23 20:02 | 2026-08-23 21:35 | 2026-08-24 10:11 | 2026-08-24 11:24 | 2026-08-24 11:25 | 2026-08-24 11:28 | 2026-08-24 11:28 | TreeContact |  | Fair | No | Customer service wire #6 triplex wire crystallized and damaged one multiple places. Repair using 80ft #6 triplex wire and six 1- bolt clamps.
Outage | J.E.26.08.35122 | C001897753 | Edward Royal | KSAN | Completed | Load_575320 | Washington Blvd - 710 | 2026-08-23 20:18 | 2026-08-24 08:06 | 2026-08-24 08:40 | 2026-08-24 08:41 | 2026-08-24 11:37 | 2026-08-24 10:18 | 2026-08-24 11:40 | 2026-08-24 11:40 |  |  | Fair | No | Replaced 30 junction fuse
Outage | J.E.26.08.35244 | C001897754 | Omar King | St.Ann | Completed | Load_262385 | Roaring River - 210 | 2026-08-23 20:20 | 2026-08-23 20:20 | 2026-08-23 22:42 | 2026-08-23 22:43 | 2026-08-24 | 2026-08-24 01:34 | 2026-08-24 01:34 | 2026-08-24 01:34 | BrokenWire |  | Fair | No | Found four (4) span of secondary phase and neutral broken as been repaired customer is now with supply
Non-Outage | J.E.26.08.35460 | C001897755 | Milton Charlton |  | Completed |  |  | 2026-08-23 20:29 | 2026-08-24 07:28 | 2026-08-24 12:38 | 2026-08-24 12:39 | 2026-08-24 12:38 | 2026-08-24 11:35 | 2026-08-24 12:40 | 2026-08-24 12:40 | BrokenWire |  | Fair | No | Call related to call at 130 Old Hope Road.
Outage | J.E.26.08.35234 | C001897758 | Derrick Dawkins | St.James | Completed | Load_253468 | Bogue - 310 | 2026-08-23 20:41 | 2026-08-23 20:43 | 2026-08-23 20:53 | 2026-08-23 20:54 | 2026-08-23 21:35 | 2026-08-23 21:46 | 2026-08-23 21:47 | 2026-08-23 21:47 |  |  | Fair | No | Found 50 kva transformer fuse barrel burn up replace barrel and 4amp fuse no pole number available
Outage | J.E.26.08.35343 | C001897757 | Romeo Brissett | St.James | Completed | Load_302124 | Bogue - 610 | 2026-08-23 20:41 | 2026-08-23 20:43 | 2026-08-23 20:47 | 2026-08-23 20:48 | 2026-08-23 21:38 | 2026-08-23 23:25 | 2026-08-23 23:27 | 2026-08-23 23:27 | BrokenWire |  | Fair | No | Isolated (1)25KVA transformer, removed illegal connections, spliced and retention 2 pole span of secondary. V/R 114-116-232
Outage | J.E.26.08.35447 | C001897759 | Lancelot Brown | Hanover | Completed | Load_292525 | Orange Bay - 310 | 2026-08-23 20:50 | 2026-08-24 15:29 | 2026-08-24 16:42 | 2026-08-24 16:43 | 2026-08-24 16:42 | 2026-08-24 16:46 | 2026-08-24 16:47 | 2026-08-24 16:47 |  |  | Fair | No | Check and found voltage at pothead 115-115-230 please refer this call to field service department in montegobay bay west need ergent attention
Outage | J.E.26.08.35336 | C001897762 | Hartley Chin | Clarendon | Completed | Load_239364 | May Pen - 110 | 2026-08-23 20:55 | 2026-08-23 21:04 | 2026-08-23 21:52 | 2026-08-24 08:19 | 2026-08-24 10:58 | 2026-08-24 11:25 | 2026-08-24 11:27 | 2026-08-24 11:27 |  |  | Fair | No | Found blown 100 KVA bank of 2 transformer @ pole # 0106155 line patrolled and found oaky , transformer refused..
Outage | J.E.26.08.35263 | C001897763 | Stephen Taylor | St.Thomas | Completed | Load_265545 | Lysson - 410 | 2026-08-23 20:56 | 2026-08-23 20:57 | 2026-08-24 12:15 | 2026-08-24 12:15 | 2026-08-24 12:15 | 2026-08-24 12:15 | 2026-08-24 12:18 | 2026-08-24 12:18 | Fire |  | Fair | No | Replace broken service wire use 6 clamps customer is now okay reading 111,112,224 customer is now okay
Outage | J.E.26.08.35314 | C001897764 | Wan Carlos Scarlett | St.Catherine | Completed | Load_269841 | Tredegar - 310 | 2026-08-23 21:00 | 2026-08-23 21:01 | 2026-08-23 21:15 | 2026-08-23 21:50 | 2026-08-23 21:50 | 2026-08-23 21:55 | 2026-08-23 21:55 | 2026-08-23 21:55 |  |  | Fair | No | Refuse 25 Amp junction no pole # was found nothing was found on primary line
Outage | J.E.26.08.35332 | C001897765 | Wan Carlos Scarlett | St.Catherine | Completed | Load_237824 | Tredegar - 210 | 2026-08-23 21:01 | 2026-08-23 21:04 | 2026-08-23 21:09 | 2026-08-23 21:10 | 2026-08-23 21:47 | 2026-08-23 21:48 | 2026-08-23 21:49 | 2026-08-23 21:49 |  |  | Fair | No | Divert to Daffodils Ave Area Out
Outage | J.E.26.08.35441 | C001897766 | Neville Spencer | Clarendon | Completed | Load_268922 | Parnassus - 310 | 2026-08-23 21:04 | 2026-08-23 21:05 | 2026-08-23 22:00 | 2026-08-23 22:00 | 2026-08-23 22:12 | 2026-08-23 22:12 | 2026-08-23 23:10 | 2026-08-23 23:10 |  |  | Fair | No | Renew blown 30 amp j/ fuse at pole # 0206201 supply restored.
Outage | J.E.26.08.35342 | C001897768 | Wan Carlos Scarlett | St.Catherine | Completed | Load_1000328 | Tredegar - 210 | 2026-08-23 21:06 | 2026-08-23 21:07 | 2026-08-23 21:56 | 2026-08-23 21:56 | 2026-08-23 22:31 | 2026-08-23 22:32 | 2026-08-23 22:45 | 2026-08-23 22:45 |  |  | Fair | No | Reset 25 KVA transformer and retention 1 span open secondary line top phase was touching open secondary line neutral 115 116 231
Outage | J.E.26.08.35387 | C001897767 | Wan Carlos Scarlett | St.Catherine | Completed | Load_266787 | Tredegar - 210 | 2026-08-23 21:06 | 2026-08-23 21:07 | 2026-08-23 22:45 | 2026-08-23 22:46 | 2026-08-23 22:45 | 2026-08-23 22:49 | 2026-08-23 22:51 | 2026-08-23 22:51 |  |  | Fair | No | Call related to trip transformer customer confirmed that power supply has been restored
Outage | J.E.26.08.35239 | C001897772 | Elvis Trowers | KSAS | Completed | Load_248011 | Duhaney - 310 | 2026-08-23 21:25 | 2026-08-23 21:25 | 2026-08-24 07:45 | 2026-08-24 07:45 | 2026-08-24 09:26 | 2026-08-24 10:00 | 2026-08-24 10:06 | 2026-08-24 10:06 |  |  | Fair | No | Found one 30 amps junction fuse blown at pole # 0076775 one 20 junction fuse blown at pole #041101 and one 10 junction fuse blown at pole #0052930. Refused using one 30 amps fuse, one 20 amps fuse and one 10 amp fuse and reclosed all three switches
Non-Outage | J.E.26.08.35579 | C001897778 | Delano Gayle |  | Completed |  |  | 2026-08-23 23:34 | 2026-08-23 23:38 | 2026-08-23 23:46 | 2026-08-23 23:46 | 2026-08-24 00:31 | 2026-08-24 00:41 | 2026-08-24 00:42 | 2026-08-24 00:42 | Fire |  | Fair | No | Area patrolled and found okay no fire seen
Outage | J.E.26.08.35373 | C001897780 | Swon Miller | St.James | Completed | Load_268282 | Bogue - 610 | 2026-08-23 23:43 | 2026-08-23 23:44 | 2026-08-24 00:04 | 2026-08-24 00:05 | 2026-08-24 00:58 | 2026-08-24 01:23 | 2026-08-24 01:23 | 2026-08-24 01:23 |  |  | Fair | No | Check and found areas okay voltage found 116/117/234 customer states that power supply has been restored voltage left 117/116/234
Outage | J.E.26.08.35429 | C001897781 | Swon Miller | St.James | Completed | Load_572116 | Bogue - 510 | 2026-08-23 23:43 | 2026-08-23 23:44 | 2026-08-24 02:34 | 2026-08-24 02:34 | 2026-08-24 03:36 | 2026-08-24 03:52 | 2026-08-24 03:54 | 2026-08-24 03:54 |  |  | Fair | No | Check and found area okay voltage i117/116/234 customer states that power is now back 117/116/234
Outage | J.E.26.08.35466 | C001897782 | Swon Miller | St.James | Completed | Load_238682 | Bogue - 510 | 2026-08-23 23:43 | 2026-08-23 23:44 | 2026-08-24 01:24 | 2026-08-24 01:24 | 2026-08-24 01:59 | 2026-08-24 02:26 | 2026-08-24 02:34 | 2026-08-24 02:34 |  |  | Fair | No | Check and found okay voltage found 115/114/231 customer states that power supply has been restored voltage left 114/115/231
Outage | J.E.26.08.35238 | C001897783 | Christopher Edwards | KSAS | Completed | Load_578715 | Duhaney - 310 | 2026-08-23 23:46 | 2026-08-23 23:47 | 2026-08-23 23:52 | 2026-08-24 00:04 | 2026-08-24 00:03 | 2026-08-24 00:10 | 2026-08-24 00:11 | 2026-08-24 00:11 |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Outage | J.E.26.08.35239 | C001897784 | Christopher Edwards | KSAS | Completed | Load_248011 | Duhaney - 310 | 2026-08-23 23:46 | 2026-08-23 23:47 | 2026-08-24 00:11 | 2026-08-24 00:12 | 2026-08-24 00:11 | 2026-08-24 00:12 | 2026-08-24 00:12 | 2026-08-24 00:12 |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Outage | J.E.26.08.35740 | C001897788 | Wan Carlos Scarlett | Portmore | Completed | Load_412901 | Naggo Head - 510 | 2026-08-24 07:05 | 2026-08-24 07:13 | 2026-08-24 07:26 | 2026-08-24 07:27 | 2026-08-24 08:40 | 2026-08-24 10:46 | 2026-08-24 10:54 | 2026-08-24 10:54 |  |  | Fair | No | Refuse 40 Amp junction pole#016275 found cable and wireless pole broken and found 5 span of system neutral wire broken use 100 ft #2 aluminum wire and 2 splicing sleeve
Outage | J.E.26.08.26380 | C001897790 | Tyrese Williams | St.Ann | Completed | Load_251050 | Upper White River - 110 | 2026-08-24 07:14 | 2026-08-24 07:15 | 2026-08-24 08:42 | 2026-08-24 09:18 | 2026-08-24 11:33 | 2026-08-24 11:47 | 2026-08-24 11:48 | 2026-08-24 11:48 |  |  | Fair | No | Premises not found reach closed by the area and not getting customer on phone
Outage | J.E.26.08.35571 | C001897791 | Wan Carlos Scarlett | St.Catherine | Completed | Load_238469 | Twickenham - 210 | 2026-08-24 07:14 | 2026-08-24 07:49 | 2026-08-24 10:25 | 2026-08-24 12:13 | 2026-08-24 12:35 | 2026-08-24 12:37 | 2026-08-24 12:39 | 2026-08-24 12:39 | BrokenWire |  | Fair | No | Customer confirm that power supply has been restored call related to broken wire
Outage | J.E.26.08.35337 | C001897795 | Hartley Chin | Clarendon | Completed | Load_262567 | May Pen - 110 | 2026-08-24 07:15 | 2026-08-24 07:17 | 2026-08-24 11:27 | 2026-08-24 11:31 | 2026-08-24 11:31 | 2026-08-24 11:31 | 2026-08-24 11:33 | 2026-08-24 11:33 |  |  | Fair | No | Call related to job # 35336 ..
Outage | J.E.26.08.35771 | C001897793 | Neville Spencer | Clarendon | Completed | Load_246249 | Monymusk - 210 | 2026-08-24 07:15 | 2026-08-24 07:16 | 2026-08-24 11:56 | 2026-08-24 11:57 | 2026-08-24 12:53 | 2026-08-24 12:59 | 2026-08-24 13:04 | 2026-08-24 13:04 |  |  | Fair | No | Cleared bird from xmfr pole renew blown 8 amp J/ fuse supply restored.
Outage | J.E.26.08.35778 | C001897794 | Cliton Henry | St.Mary | Completed | Load_251918 | Oracabessa - 210 | 2026-08-24 07:15 | 2026-08-24 07:18 | 2026-08-24 08:51 | 2026-08-24 08:51 | 2026-08-24 08:51 | 2026-08-24 09:04 | 2026-08-24 09:07 | 2026-08-24 09:07 |  |  | Fair | No | A 15 kva transformer fuse holder found on the ground at pole #040506 due to a motor vehicle accident. The supply was restored to replace the fuse holder with a 2 amp fuse.
Non-Outage | J.E.26.08.35528 | C001897797 | Christopher Edwards | KSAN | Completed | Load_248982 | Constant Spring - 410 | 2026-08-24 07:22 | 2026-08-24 07:24 | 2026-08-24 07:29 | 2026-08-24 08:15 | 2026-08-24 10:29 | 2026-08-24 12:14 | 2026-08-24 12:18 | 2026-08-24 12:18 | BrokenWire |  | Fair | No | Clear fallen tree limb off open secondary line Splice and retention broken open secondary line Using (40ft #2 AA conductor 2-one bolt clamps 1- #2preform Refuse blown 50 kva transformer using (1) 5 amps 40ft concrete pole is leaning causing open secondary to hang low Big trucks will tear back down wire if pole is not straightened Concrete pole consist of 3 phase primary and open secondary line
Outage | J.E.26.08.35733 | C001897799 | Christopher Edwards | KSAN | Completed | Load_263722 | Constant Spring - 410 | 2026-08-24 07:23 | 2026-08-24 07:24 | 2026-08-24 12:19 | 2026-08-24 12:19 | 2026-08-24 13:40 | 2026-08-24 14:25 | 2026-08-24 14:26 | 2026-08-24 14:26 |  | Y | Fair | No | Clear bamboo off single phase primary lineReclose 15 amps trip saver
Outage | J.E.26.08.35781 | C001897802 | Kemark Slue | St.Catherine | Completed | Load_556137 | New Michelton - 310 | 2026-08-24 07:26 | 2026-08-24 07:28 | 2026-08-24 07:59 | 2026-08-24 08:00 | 2026-08-24 09:53 | 2026-08-24 09:17 | 2026-08-24 12:06 | 2026-08-24 12:06 |  | Y | Fair | No | Upon arrival at the location the crew discovered that 10 amps junction fuse was blown, further patrol revealed that a few Poinciana trees were making contact with the primary conductor, cut away trees from conductor, refuse link and re-energized line section, please refer to A. Murre to have vegetation management done on line section.
Non-Outage | J.E.26.08.30672 | C001897805 | Milton Charlton | KSAN | Completed | Load_243399 | Hope - 410 | 2026-08-24 07:28 | 2026-08-24 07:29 | 2026-08-24 12:33 | 2026-08-24 12:33 | 2026-08-24 12:33 | 2026-08-24 12:05 | 2026-08-24 12:38 | 2026-08-24 12:38 |  |  | Fair | No | Found okay upon arrival. Customer did not made a report to JPS.
Outage | J.E.26.08.33032 | C001897806 | Neville Spencer | St.Catherine | Completed | Load_246941 | Rhodens Pen - 310 | 2026-08-24 07:28 | 2026-08-24 07:29 | 2026-08-24 07:41 | 2026-08-24 07:41 | 2026-08-24 09:09 | 2026-08-24 09:09 | 2026-08-24 09:09 | 2026-08-24 09:09 |  |  | Fair | No | Found ok.
Outage | J.E.26.08.35742 | C001897807 | Wan Carlos Scarlett | KSAN | Completed | Load_253353 | Hope - 410 | 2026-08-24 07:29 | 2026-08-24 07:30 | 2026-08-24 09:12 | 2026-08-24 10:54 | 2026-08-24 10:54 | 2026-08-24 10:58 | 2026-08-24 11:00 | 2026-08-24 11:00 |  |  | Fair | No | Call related to cable and wireless broken pole customer confirmed that power supply has been restored
Non-Outage | J.E.26.08.23159 | C001897812 | Stephen Taylor | St.Thomas | Completed | Load_249385 | Lysson - 410 | 2026-08-24 07:32 | 2026-08-24 07:33 | 2026-08-24 08:42 | 2026-08-24 08:42 | 2026-08-24 08:58 | 2026-08-24 09:24 | 2026-08-24 09:26 | 2026-08-24 09:26 |  |  | Fair | No | Clean up single phase line 3 clamps Rdg 113–112–226
Non-Outage | J.E.26.08.27090 | C001897810 | Stephen Taylor | St.Thomas | Completed | Load_261247 | Port Antonio - 310 | 2026-08-24 07:32 | 2026-08-24 07:41 | 2026-08-24 09:58 | 2026-08-24 09:58 | 2026-08-24 10:47 | 2026-08-24 10:47 | 2026-08-24 10:49 | 2026-08-24 10:49 |  |  | Fair | No | Close up back 50 amp transformer with a 5 amp fuse customer is now okay
Non-Outage | J.E.26.08.35140 | C001897809 | Stephen Taylor | St.Thomas | Completed | Load_265771 | Lysson - 410 | 2026-08-24 07:32 | 2026-08-24 07:33 | 2026-08-24 10:53 | 2026-08-24 11:11 | 2026-08-24 11:28 | 2026-08-24 11:28 | 2026-08-24 11:29 | 2026-08-24 11:29 |  |  | Fair | No | Clean up single phase use 2 clamps reading 111,112,224 customer is now okay
Outage | J.E.26.08.35777 | C001897811 | Nickolas Rodriques | St.Catherine | Completed | Load_239948 | Twickenham - 410 | 2026-08-24 07:32 | 2026-08-24 07:37 | 2026-08-24 11:19 | 2026-08-24 11:24 | 2026-08-24 11:38 | 2026-08-24 11:50 | 2026-08-24 11:57 | 2026-08-24 11:57 |  |  | Fair | No | Call relates to the 30 amp junction fuses that was replaced. Power restored.
Non-Outage | J.E.26.08.35486 | C001897816 | Nickolas Rodriques |  | Completed |  |  | 2026-08-24 07:33 | 2026-08-24 07:38 | 2026-08-24 07:48 | 2026-08-24 07:49 | 2026-08-24 08:28 | 2026-08-24 08:43 | 2026-08-24 08:47 | 2026-08-24 08:47 | Fire |  | Fair | No | Unable to communicate with the customer. However, the area was patrolled and no fire was seen.
Outage | J.E.26.08.35547 | C001897813 | Nickolas Rodriques | St.Catherine | Completed | Load_256498 | Tredegar - 310 | 2026-08-24 07:33 | 2026-08-24 07:38 | 2026-08-24 14:48 | 2026-08-24 14:49 | 2026-08-24 15:04 | 2026-08-24 15:05 | 2026-08-24 15:08 | 2026-08-24 15:08 |  |  | Fair | No | Unable to locate or communicate with the specific customer. However the area was patrolled and no noticeable outage was found.
Outage | J.E.26.08.35743 | C001897815 | Nickolas Rodriques | St.Catherine | Completed | Load_256403 | Tredegar - 310 | 2026-08-24 07:33 | 2026-08-24 07:38 | 2026-08-24 14:02 | 2026-08-24 14:03 | 2026-08-24 14:30 | 2026-08-24 14:41 | 2026-08-24 14:46 | 2026-08-24 14:46 |  |  | Fair | No | Found customer with electricity. Customer confirmed that the power outage was later resolved.
Outage | J.E.26.08.35467 | C001897818 | Rusean Allen | KSAS | Completed | Load_239090 | Up Park Camp - 310 | 2026-08-24 07:34 | 2026-08-24 07:57 | 2026-08-24 08:22 | 2026-08-24 09:09 | 2026-08-24 09:52 | 2026-08-24 09:58 | 2026-08-24 09:59 | 2026-08-24 09:59 |  |  | Fair | No | Premises okay
Outage | J.E.26.08.35816 | C001897820 | Rusean Allen | KSAS | Completed | Load_250802 | Rockfort - 410 | 2026-08-24 07:34 | 2026-08-24 07:57 | 2026-08-24 10:07 | 2026-08-24 10:07 | 2026-08-24 10:16 | 2026-08-24 10:22 | 2026-08-24 10:23 | 2026-08-24 10:23 | Fire |  | Fair | No | Corroded clamp found at pole at pole, clamp was changed.
Non-Outage | J.E.26.08.35819 | C001897822 | Milton Charlton |  | Completed |  |  | 2026-08-24 07:42 | 2026-08-24 07:43 | 2026-08-24 10:35 | 2026-08-24 10:35 | 2026-08-24 12:06 | 2026-08-24 11:36 | 2026-08-24 12:12 | 2026-08-24 12:12 | BrokenPole |  | Fair | No | 30ft wooden pole broken in motor vehicle accident belongs to telephone company with streetlights wire attached. Retire #6 triplex service wire feeding street lights.
Outage | J.E.26.08.35756 | C001897821 | Dean- Smith | Hanover | Completed | Load_241288 | Orange Bay - 310 | 2026-08-24 07:42 | 2026-08-24 07:43 | 2026-08-24 14:17 | 2026-08-24 14:17 | 2026-08-24 14:17 | 2026-08-24 14:17 | 2026-08-24 14:19 | 2026-08-24 14:19 | Fire |  | Fair | No | Defective 25kva defective, found secondary bushing burnt out, banging sec conductors. Banging conductors was retentioned, area left with single phasing. Please for to maintenance dept to replace transformer.
Outage | J.E.26.08.35418 | C001897825 | Shawn Medley | St.James | Completed | Load_238865 | Queens Drive - 710 | 2026-08-24 07:47 | 2026-08-24 07:59 | 2026-08-24 08:09 | 2026-08-24 08:27 | 2026-08-24 09:34 | 2026-08-24 09:00 | 2026-08-24 09:36 | 2026-08-24 09:36 |  |  | Fair | No | Premises found ok.
Outage | J.E.26.08.35457 | C001897826 | Horace Malcolm | St.James | Completed | Load_263602 | Bogue - 610 | 2026-08-24 07:48 | 2026-08-24 07:49 | 2026-08-24 08:01 | 2026-08-24 08:01 | 2026-08-24 08:58 | 2026-08-24 10:00 | 2026-08-24 10:00 | 2026-08-24 10:00 |  |  | Rains | No | Refused one 10amp junction fuse
Outage | J.E.26.08.35827 | C001897827 | Christopher West | Portmore | Completed | Load_265851 | Naggo Head - 610 | 2026-08-24 07:48 | 2026-08-24 16:44 | 2026-08-24 22:51 | 2026-08-24 22:52 | 2026-08-24 22:54 | 2026-08-24 22:55 | 2026-08-24 22:55 | 2026-08-24 22:55 |  |  | Fair | No | Premises found with supply however, a defective streetlight is at said location, kindly refer to the relevant department.
Outage | J.E.26.08.35821 | C001897829 | Shamour Haughton | St.James | Completed | Load_252075 | Bogue - 310 | 2026-08-24 07:50 | 2026-08-24 07:59 | 2026-08-24 08:08 | 2026-08-24 10:15 | 2026-08-24 10:14 | 2026-08-24 10:14 | 2026-08-24 10:16 | 2026-08-24 10:16 |  |  | Fair | No | Found 1,167kva defective of a bank of 3, transformer needs changing, please refer to maintenance
Outage | J.E.26.08.35570 | C001897831 | Marlon Brown | Trelawny | Completed | Load_249410 | Greenwood - 210 | 2026-08-24 07:55 | 2026-08-24 07:55 | 2026-08-24 08:02 | 2026-08-24 08:03 | 2026-08-24 09:02 | 2026-08-24 09:22 | 2026-08-24 09:22 | 2026-08-24 09:22 | Fire |  | Fair | No | Replaced 2amps 25kva transformer fuse
Non-Outage | J.E.26.08.32288 | C001897837 | Ryan Richards | Manchester | Completed | Load_262432 | Spur Tree - 310 | 2026-08-24 07:58 | 2026-08-24 08:00 | 2026-08-24 08:56 | 2026-08-24 08:57 | 2026-08-24 10:15 | 2026-08-24 11:21 | 2026-08-24 11:21 | 2026-08-24 11:21 |  |  | Fair | No | Field Service work requires to remove barrel lock so customer can carry out repairs
Non-Outage | J.E.26.08.25471 | C001897838 | Odeanie Davis | KSAN | Completed | Load_262116 | Washington Blvd - 710 | 2026-08-24 07:59 | 2026-08-24 08:00 | 2026-08-24 10:56 | 2026-08-24 11:02 | 2026-08-24 11:02 | 2026-08-24 11:09 | 2026-08-24 11:15 | 2026-08-24 11:15 |  |  | Fair | No | 99v/107v & 206v on secondary line, technician request for transformer to be checked,
Non-Outage | J.E.26.08.25534 | C001897839 | Odeanie Davis | KSAN | Completed | Load_268663 | Washington Blvd - 710 | 2026-08-24 07:59 | 2026-08-24 08:00 | 2026-08-24 11:24 | 2026-08-24 11:25 | 2026-08-24 11:24 | 2026-08-24 11:36 | 2026-08-24 11:36 | 2026-08-24 11:36 |  |  | Fair | No | 94v/105v & 200v at location, customer stated that the issue was fixed however low voltage still persists in the area.
Non-Outage | J.E.26.08.25715 | C001897841 | Odeanie Davis | KSAN | Completed | Load_256467 | Washington Blvd - 310 | 2026-08-24 07:59 | 2026-08-24 08:00 | 2026-08-24 12:27 | 2026-08-24 12:28 | 2026-08-24 12:27 | 2026-08-24 12:52 | 2026-08-24 12:53 | 2026-08-24 12:53 |  |  | Fair | No | 104v/99v & 203v from transformer, technician request for transformer to be checked
Non-Outage | J.E.26.08.26015 | C001897840 | Odeanie Davis | KSAN | Completed | Load_256467 | Washington Blvd - 310 | 2026-08-24 07:59 | 2026-08-24 08:00 | 2026-08-24 11:42 | 2026-08-24 13:25 | 2026-08-24 13:25 | 2026-08-24 13:36 | 2026-08-24 13:28 | 2026-08-24 13:28 |  |  | Fair | No | 104v/99v & 203v from transformer, technician request for transformer to be checked.
Non-Outage | J.E.26.08.26112 | C001897842 | Odeanie Davis | KSAN | Completed | Load_256666 | Washington Blvd - 710 | 2026-08-24 07:59 | 2026-08-24 08:00 | 2026-08-24 08:33 | 2026-08-24 08:34 | 2026-08-24 09:02 | 2026-08-24 09:37 | 2026-08-24 09:37 | 2026-08-24 09:37 |  |  | Fair | No | 101v/102v & 203v on secondary line, technician request for transformer to be checked
Non-Outage | J.E.26.08.26980 | C001897843 | Odeanie Davis | KSAN | Completed | Load_270258 | Washington Blvd - 710 | 2026-08-24 07:59 | 2026-08-24 08:00 | 2026-08-24 11:43 | 2026-08-24 11:44 | 2026-08-24 11:44 | 2026-08-24 11:57 | 2026-08-24 11:58 | 2026-08-24 11:58 |  |  | Fair | No | 116v/25v at location from rammi box, rammi key needed
Non-Outage | J.E.26.08.32156 | C001897844 | Kenroy Dale | Manchester | Completed | Load_244824 | Kendal - 210 | 2026-08-24 07:59 | 2026-08-24 08:00 | 2026-08-24 09:05 | 2026-08-24 09:23 | 2026-08-24 11:03 | 2026-08-24 11:57 | 2026-08-24 12:06 | 2026-08-24 12:06 |  |  | Fair | No | Corroded jumper found remade connection using 1 one bolt clamp voltage reading 115/111/226
Non-Outage | J.E.26.08.34653 | C001897845 | Shamour Haughton | St.James | Completed | Load_302847 | Bogue - 610 | 2026-08-24 07:59 | 2026-08-24 08:00 | 2026-08-24 12:50 | 2026-08-24 12:52 | 2026-08-24 12:51 | 2026-08-24 12:52 | 2026-08-24 12:54 | 2026-08-24 12:54 | BangingWires |  | Fair | No | Unable to locate customer, number went straight to voicemail after several attempts, need better directions
Non-Outage | J.E.26.08.28095 | C001897847 | Odeanie Davis | KSAN | Completed | Load_250296 | Washington Blvd - 310 | 2026-08-24 08:00 | 2026-08-24 08:00 | 2026-08-24 12:02 | 2026-08-24 12:02 | 2026-08-24 12:02 | 2026-08-24 12:20 | 2026-08-24 12:21 | 2026-08-24 12:21 |  |  | Fair | No | 103v/104v & 207v from transformer, technician request for transformer to be checked.
Non-Outage | J.E.26.08.30273 | C001897853 | Error Coore | Manchester | Completed | Load_244478 | Spur Tree - 310 | 2026-08-24 08:00 | 2026-08-24 08:01 | 2026-08-24 08:31 | 2026-08-24 08:31 | 2026-08-24 10:19 | 2026-08-24 11:08 | 2026-08-24 11:11 | 2026-08-24 11:11 |  |  | Fair | No | Premises found ok voltage reading 114/115/229 volts
Non-Outage | J.E.26.08.30281 | C001897851 | Error Coore | Manchester | Completed | Load_239869 | Porus - 310 | 2026-08-24 08:00 | 2026-08-24 08:01 | 2026-08-25 15:39 | 2026-08-25 18:21 | 2026-08-25 18:20 | 2026-08-25 18:21 | 2026-08-25 18:21 | 2026-08-25 18:21 |  |  | Fair | No | Premises not found not getting customer on phone
Non-Outage | J.E.26.08.30619 | C001897852 | Error Coore | Manchester | Completed | Load_238016 | Kendal - 310 | 2026-08-24 08:00 | 2026-08-24 08:01 | 2026-08-24 14:20 | 2026-08-24 14:20 | 2026-08-24 15:19 | 2026-08-24 15:37 | 2026-08-24 15:38 | 2026-08-24 15:38 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.08.30794 | C001897850 | Error Coore | Manchester | Completed | Load_252632 | Kendal - 210 | 2026-08-24 08:00 | 2026-08-24 08:01 | 2026-08-25 08:31 | 2026-08-25 08:32 | 2026-08-25 09:48 | 2026-08-25 10:06 | 2026-08-25 10:08 | 2026-08-25 10:08 |  |  | Fair | No | Premises not found not getting customer on phone
Non-Outage | J.E.26.08.31093 | C001897848 | Error Coore | Manchester | Completed | Load_237646 | Kendal - 210 | 2026-08-24 08:00 | 2026-08-24 08:01 | 2026-08-25 10:08 | 2026-08-25 10:08 | 2026-08-25 10:50 | 2026-08-25 11:39 | 2026-08-25 11:41 | 2026-08-25 11:41 |  |  | Fair | No | Found customer with wrap connection at pothead remade wrap connection using 2 service sleeve voltage reading 115/116/231 volts
Non-Outage | J.E.26.08.31579 | C001897849 | Error Coore | Manchester | Completed | Load_244557 | Kendal - 310 | 2026-08-24 08:00 | 2026-08-24 08:01 | 2026-08-24 11:24 | 2026-08-24 11:24 | 2026-08-24 12:41 | 2026-08-24 12:58 | 2026-08-24 13:02 | 2026-08-24 13:02 |  |  | Fair | No | Unable to carry out repair due to leaning pole refer to emergency bucket truck crew
Non-Outage | J.E.26.08.29929 | C001897854 | Error Coore | Manchester | Completed | Load_265861 | Spur Tree - 310 | 2026-08-24 08:01 | 2026-08-24 08:01 | 2026-08-24 15:39 | 2026-08-24 15:40 | 2026-08-24 16:36 | 2026-08-24 16:59 | 2026-08-24 17:00 | 2026-08-24 17:00 |  |  | Fair | No | Premises found ok customer have internal problem voltage reading 116/117/233 volts
Non-Outage | J.E.26.08.32087 | C001897858 | Odeanie Davis | KSAN | Completed | Load_249802 | Washington Blvd - 310 | 2026-08-24 08:01 | 2026-08-24 08:02 | 2026-08-24 13:35 | 2026-08-25 08:08 | 2026-08-25 08:07 | 2026-08-25 08:26 | 2026-08-25 08:08 | 2026-08-25 08:08 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.32099 | C001897857 | Odeanie Davis | KSAN | Completed | Load_259248 | Washington Blvd - 310 | 2026-08-24 08:01 | 2026-08-24 08:02 | 2026-08-24 09:37 | 2026-08-24 09:40 | 2026-08-24 09:39 | 2026-08-24 09:50 | 2026-08-24 09:41 | 2026-08-24 09:41 | LeaningPole |  | Fair | No | Customer stated that this address is incorrect, location in Portland
Non-Outage | J.E.26.08.35050 | C001897856 | Odeanie Davis | KSAN | Completed | Load_243339 | Washington Blvd - 710 | 2026-08-24 08:01 | 2026-08-24 08:02 | 2026-08-24 12:55 | 2026-08-24 13:28 | 2026-08-24 13:28 | 2026-08-24 13:59 | 2026-08-24 13:32 | 2026-08-24 13:32 |  |  | Fair | No | 94v/105v & 200v from secondary line, customer stated that the issue was fixed however low voltage still persists in the area
Non-Outage | J.E.26.08.35376 | C001897855 | Roemello Brown | Trelawny | Completed | Load_238727 | Martha Brae - 110 | 2026-08-24 08:01 | 2026-08-24 08:01 | 2026-08-24 12:11 | 2026-08-24 12:59 | 2026-08-24 14:08 | 2026-08-24 14:11 | 2026-08-24 14:12 | 2026-08-24 14:12 |  |  | Fair | No | Customer needs to update proper directions an landmark phone number rings without answering please provide proper directions
Non-Outage | J.E.26.08.34002 | C001897865 | Roemello Brown | Trelawny | Completed | Load_257490 | Duncans - 210 | 2026-08-24 08:02 | 2026-08-24 08:03 | 2026-08-24 09:15 | 2026-08-24 09:15 | 2026-08-24 09:28 | 2026-08-24 10:47 | 2026-08-24 10:48 | 2026-08-24 10:48 |  |  | Fair | No | Corrosion at pole side have 3 clamps change Voltage found 116/111/227Voltage leave 117/115/232
Non-Outage | J.E.26.08.35132 | C001897864 | Odeanie Davis | KSAN | Completed | Load_567702 | Washington Blvd - 310 | 2026-08-24 08:02 | 2026-08-24 08:03 | 2026-08-24 13:40 | 2026-08-25 08:06 | 2026-08-25 08:06 | 2026-08-25 08:15 | 2026-08-25 08:07 | 2026-08-25 08:07 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.32442 | C001897874 | Fredrick Hamilton | KSAN | Completed | Load_257676 | Constant Spring - 210 | 2026-08-24 08:03 | 2026-08-24 08:04 | 2026-08-24 08:15 | 2026-08-24 08:19 | 2026-08-24 08:19 | 2026-08-24 08:21 | 2026-08-24 08:21 | 2026-08-24 08:21 |  |  | Fair | No | Customer contacted and stated that no issue is at location full supply at premises Premises is ok
Non-Outage | J.E.26.08.33461 | C001897867 | Roemello Brown | Trelawny | Completed | Load_266214 | Duncans - 210 | 2026-08-24 08:03 | 2026-08-24 08:04 | 2026-08-24 10:52 | 2026-08-24 10:54 | 2026-08-24 11:28 | 2026-08-24 11:30 | 2026-08-24 11:33 | 2026-08-24 11:33 |  |  | Fair | No | Customer meter burn up please send field service technician to have meter change Voltage found 116/115/231Voltage leave 116/115/231
Non-Outage | J.E.26.08.33897 | C001897873 | Fredrick Hamilton | KSAN | Completed | Load_251722 | Constant Spring - 310 | 2026-08-24 08:03 | 2026-08-24 08:04 | 2026-08-24 08:15 | 2026-08-24 11:47 | 2026-08-24 11:58 | 2026-08-24 12:13 | 2026-08-24 12:14 | 2026-08-24 12:14 |  |  | Fair | No | 239v/119v/118v obtained No issues detected on the JPS supply PremisesPremises is ok
Non-Outage | J.E.26.08.34148 | C001897872 | Fredrick Hamilton | KSAN | Completed | Load_257522 | Constant Spring - 210 | 2026-08-24 08:03 | 2026-08-24 08:04 | 2026-08-24 08:15 | 2026-08-24 08:52 | 2026-08-24 08:52 | 2026-08-24 08:54 | 2026-08-24 08:54 | 2026-08-24 08:54 |  |  | Fair | No | Customer contacted and stated that power was restored fully previously Premises is ok
Non-Outage | J.E.26.08.34590 | C001897871 | Fredrick Hamilton | KSAN | Completed | Load_254123 | Constant Spring - 210 | 2026-08-24 08:03 | 2026-08-24 08:04 | 2026-08-24 08:15 | 2026-08-24 08:32 | 2026-08-24 08:32 | 2026-08-24 08:33 | 2026-08-24 08:33 | 2026-08-24 08:33 |  |  | Fair | No | Customer contacted and stated that power was restored fully to premises previously Premises is ok
Non-Outage | J.E.26.08.35255 | C001897870 | Fredrick Hamilton | KSAN | Completed | Load_252194 | Constant Spring - 210 | 2026-08-24 08:03 | 2026-08-24 08:04 | 2026-08-24 08:15 | 2026-08-24 08:59 | 2026-08-24 09:36 | 2026-08-24 10:23 | 2026-08-24 10:23 | 2026-08-24 10:23 |  |  | Fair | No | 233v/116.7v/116v obtained no issues detected on the JPS supply Premises is ok
Non-Outage | J.E.26.08.35794 | C001897869 | Fredrick Hamilton | KSAN | Completed | Load_254712 | Constant Spring - 210 | 2026-08-24 08:03 | 2026-08-24 08:04 | 2026-08-24 08:15 | 2026-08-24 10:35 | 2026-08-24 10:58 | 2026-08-24 11:25 | 2026-08-24 11:25 | 2026-08-24 11:25 |  |  | Fair | No | Corrosion detected at pole same was corrected 3 clamps used237v/117v/118v obtained
Non-Outage | J.E.26.08.23401 | C001897877 | Royston Montague | St.Catherine | Completed | Load_1000771 | Tredegar - 210 | 2026-08-24 08:04 | 2026-08-24 08:06 | 2026-08-24 08:29 | 2026-08-24 13:21 | 2026-08-24 15:34 | 2026-08-24 15:35 | 2026-08-24 15:35 | 2026-08-24 15:35 |  |  | Fair | No | Not locating this premises. Rami system. Residents not familiar with name.
Non-Outage | J.E.26.08.26836 | C001897876 | Royston Montague | St.Catherine | Completed | Load_1001062 | Tredegar - 210 | 2026-08-24 08:04 | 2026-08-24 08:06 | 2026-08-24 08:29 | 2026-08-25 14:16 | 2026-08-25 14:39 | 2026-08-25 14:40 | 2026-08-25 14:40 | 2026-08-25 14:40 |  |  | Fair | No | Rami system in area. Please assign this job to relevant team thanks
Non-Outage | J.E.26.08.28491 | C001897878 | Royston Montague | St.Catherine | Completed | Load_253962 | Tredegar - 210 | 2026-08-24 08:04 | 2026-08-24 08:06 | 2026-08-24 08:29 | 2026-08-25 08:36 | 2026-08-25 09:24 | 2026-08-25 11:15 | 2026-08-25 11:15 | 2026-08-25 11:15 |  |  | Fair | No | Faulty jumper joint on transformer circuit, same corrected. Voltage found 122v 100v voltage after job completion are 222v 112v 108v
Non-Outage | J.E.26.08.28938 | C001897879 | Royston Montague | St.Catherine | Completed | Load_260588 | Tredegar - 210 | 2026-08-24 08:04 | 2026-08-24 08:06 | 2026-08-24 08:29 | 2026-08-24 12:51 | 2026-08-24 13:17 | 2026-08-24 13:17 | 2026-08-24 13:18 | 2026-08-24 13:18 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.08.30377 | C001897880 | Royston Montague | St.Catherine | Completed | Load_247171 | Tredegar - 210 | 2026-08-24 08:04 | 2026-08-24 08:06 | 2026-08-24 08:29 | 2026-08-24 15:36 | 2026-08-24 15:43 | 2026-08-24 15:59 | 2026-08-24 15:59 | 2026-08-24 15:59 |  |  | Fair | No | Open phase at pothead. Same corrected, voltage found 112v voltage after job completion are. 229v 114v 113v
Non-Outage | J.E.26.08.32612 | C001897875 | Roemello Brown | Trelawny | Completed | Load_241073 | Duncans - 210 | 2026-08-24 08:04 | 2026-08-24 08:05 | 2026-08-24 10:50 | 2026-08-24 11:36 | 2026-08-24 11:58 | 2026-08-24 11:58 | 2026-08-24 12:03 | 2026-08-24 12:03 |  |  | Fair | No | Premises found working okay Voltage found 118/118/236Voltage leave 118/118/236
Non-Outage | J.E.26.08.35561 | C001897881 | Royston Montague | St.Catherine | Completed | Load_246714 | Tredegar - 210 | 2026-08-24 08:04 | 2026-08-24 08:06 | 2026-08-24 08:29 | 2026-08-24 13:19 | 2026-08-24 13:19 | 2026-08-24 13:20 | 2026-08-24 13:20 | 2026-08-24 13:20 |  |  | EarthMovement | No | Observed that meter has been changed. New meter number 3052094. Full voltage found, 228v 114v 111v
Non-Outage | J.E.26.06.36617 | C001897882 | Royston Montague | St.Catherine | Completed | Load_254315 | Tredegar - 310 | 2026-08-24 08:05 | 2026-08-24 08:06 | 2026-08-24 08:29 | 2026-08-24 08:55 | 2026-08-24 09:34 | 2026-08-24 09:34 | 2026-08-24 09:34 | 2026-08-24 09:34 |  |  | Fair | No | Customer confirmed issue resolved. Please update thanks.
Non-Outage | J.E.26.07.20546 | C001897884 | Royston Montague | St.Catherine | Completed | Load_1001612 | Tredegar - 310 | 2026-08-24 08:05 | 2026-08-24 08:06 | 2026-08-24 08:29 | 2026-08-24 11:31 | 2026-08-24 11:37 | 2026-08-24 11:38 | 2026-08-24 11:38 | 2026-08-24 11:38 |  |  | Fair | No | Customer confirmed issue resolved
Non-Outage | J.E.26.07.27601 | C001897883 | Royston Montague | St.Catherine | Completed | Load_1001597 | Tredegar - 310 | 2026-08-24 08:05 | 2026-08-24 08:06 | 2026-08-24 08:29 | 2026-08-24 11:40 | 2026-08-24 12:47 | 2026-08-24 12:48 | 2026-08-24 12:49 | 2026-08-24 12:49 |  |  | Fair | No | Not locating this premises, rami system in area. Multiple calls to customer phone go without answer
Non-Outage | J.E.26.07.27816 | C001897886 | Royston Montague | St.Catherine | Completed | Load_246739 | Tredegar - 310 | 2026-08-24 08:05 | 2026-08-24 08:08 | 2026-08-24 08:29 | 2026-08-24 10:31 | 2026-08-24 10:49 | 2026-08-24 11:28 | 2026-08-24 11:28 | 2026-08-24 11:28 |  |  | Fair | No | Broken neutral on #6 service wire, same repair, voltage found 127v 100v voltage after job completion are 227v 113v 112v
Non-Outage | J.E.26.07.34759 | C001897885 | Royston Montague | St.Catherine | Completed | Load_252365 | Tredegar - 310 | 2026-08-24 08:05 | 2026-08-24 08:08 | 2026-08-24 08:29 | 2026-08-24 09:40 | 2026-08-24 10:28 | 2026-08-24 10:29 | 2026-08-24 10:29 | 2026-08-24 10:29 |  |  | Fair | No | Customer confirmed issue resolved. Please update thanks.
Non-Outage | J.E.26.08.26107 | C001897887 | Roemello Brown | Trelawny | Completed | Load_255240 | Greenwood - 110 | 2026-08-24 08:05 | 2026-08-24 08:07 | 2026-08-25 09:05 | 2026-08-25 09:26 | 2026-08-25 09:28 | 2026-08-25 09:29 | 2026-08-25 09:30 | 2026-08-25 09:30 |  |  | Fair | No | Premises found working okay Voltage found 112/113/225Voltage leave 112/113/225
Non-Outage | J.E.26.08.32416 | C001897888 | Odaine Johnson | Clarendon | Completed | Load_244406 | Monymusk - 410 | 2026-08-24 08:06 | 2026-08-24 08:20 | 2026-08-24 08:27 | 2026-08-24 12:42 | 2026-08-24 12:41 | 2026-08-24 12:41 | 2026-08-24 12:42 | 2026-08-24 12:42 |  |  | Fair | No | Corroded phase found at pole remade connection using 1 one bolt clamp
Non-Outage | J.E.26.08.32451 | C001897890 | Odaine Johnson | Clarendon | Completed | Load_244406 | Monymusk - 410 | 2026-08-24 08:06 | 2026-08-24 08:20 | 2026-08-24 08:27 | 2026-08-24 11:39 | 2026-08-24 11:46 | 2026-08-24 11:47 | 2026-08-24 11:47 | 2026-08-24 11:47 |  |  | Fair | No | Premises found okay customer stated that the issue was resolved
Non-Outage | J.E.26.08.32639 | C001897889 | Odaine Johnson | Clarendon | Completed | Load_301225 | Monymusk - 410 | 2026-08-24 08:06 | 2026-08-24 08:20 | 2026-08-24 08:27 | 2026-08-24 09:46 | 2026-08-24 11:32 | 2026-08-24 11:32 | 2026-08-24 11:33 | 2026-08-24 11:33 |  |  | Fair | No | Premises found okay voltage reading 115/115/231 volts
Non-Outage | J.E.26.08.32811 | C001897893 | Odaine Johnson | Clarendon | Completed | Load_240655 | Monymusk - 410 | 2026-08-24 08:06 | 2026-08-24 08:20 | 2026-08-24 08:28 | 2026-08-24 11:47 | 2026-08-24 11:47 | 2026-08-24 11:47 | 2026-08-24 11:47 | 2026-08-24 11:47 |  |  | Fair | No | Premises found okay customer stated that the issue was resolved
Non-Outage | J.E.26.08.33607 | C001897891 | Odaine Johnson | Clarendon | Completed | Load_250072 | May Pen - 210 | 2026-08-24 08:06 | 2026-08-24 08:20 | 2026-08-24 08:27 | 2026-08-24 12:39 | 2026-08-24 12:40 | 2026-08-24 12:41 | 2026-08-24 12:41 | 2026-08-24 12:41 |  |  | Fair | No | Premises found okay customer stated that the issue was resolved
Non-Outage | J.E.26.08.33857 | C001897892 | Odaine Johnson | Clarendon | Completed | Load_263977 | Monymusk - 410 | 2026-08-24 08:06 | 2026-08-24 08:20 | 2026-08-24 08:28 | 2026-08-24 11:35 | 2026-08-24 11:36 | 2026-08-24 11:36 | 2026-08-24 11:37 | 2026-08-24 11:37 |  |  | Fair | No | Corroded phase found at pole remade connection using 1 one bolt clamp voltage reading 115 volts
Non-Outage | J.E.26.08.33625 | C001897896 | Odaine Johnson | Clarendon | Completed | Load_250072 | May Pen - 210 | 2026-08-24 08:07 | 2026-08-24 08:20 | 2026-08-24 08:28 | 2026-08-24 12:35 | 2026-08-24 12:38 | 2026-08-24 12:38 | 2026-08-24 12:38 | 2026-08-24 12:38 |  |  | Fair | No | Premises found okay customer stated that the issue was resolved
Non-Outage | J.E.26.08.33636 | C001897897 | Odaine Johnson | Clarendon | Completed | Load_250072 | May Pen - 210 | 2026-08-24 08:07 | 2026-08-24 08:20 | 2026-08-24 08:28 | 2026-08-24 12:42 | 2026-08-24 12:45 | 2026-08-24 12:45 | 2026-08-24 12:45 | 2026-08-24 12:45 |  |  | Fair | No | Premises found okay customer stated that the issue was resolved
Non-Outage | J.E.26.08.33683 | C001897898 | Odaine Johnson | Clarendon | Completed | Load_250072 | May Pen - 210 | 2026-08-24 08:07 | 2026-08-24 08:20 | 2026-08-24 08:28 | 2026-08-24 13:27 | 2026-08-24 13:30 | 2026-08-24 13:30 | 2026-08-24 13:31 | 2026-08-24 13:31 |  |  | Fair | No | Corrosion was found at pothead remade connection using one pen union voltage reading 110/109/220 volts
Non-Outage | J.E.26.08.34695 | C001897899 | Odaine Johnson | Clarendon | Completed | Load_250072 | May Pen - 210 | 2026-08-24 08:07 | 2026-08-24 08:20 | 2026-08-24 08:29 | 2026-08-24 12:46 | 2026-08-24 12:47 | 2026-08-24 12:47 | 2026-08-24 12:48 | 2026-08-24 12:48 |  |  | Fair | No | Premises found okay customer stated that the issue was resolved
Non-Outage | J.E.26.08.34763 | C001897904 | Orville Lee | St.Catherine | Completed | Load_243931 | Twickenham - 210 | 2026-08-24 08:08 | 2026-08-24 08:10 | 2026-08-24 10:01 | 2026-08-24 10:01 | 2026-08-24 10:06 | 2026-08-24 10:11 | 2026-08-24 10:16 | 2026-08-24 10:16 |  |  | Fair | No | Premises found ok upon arrival Issue was resolved by a technician Customer was reporting a outage Voltage 116117233
Non-Outage | J.E.26.08.34791 | C001897905 | Orville Lee | St.Catherine | Completed | Load_256499 | Twickenham - 210 | 2026-08-24 08:08 | 2026-08-24 08:10 | 2026-08-24 11:01 | 2026-08-24 11:01 | 2026-08-24 11:11 | 2026-08-24 11:25 | 2026-08-24 11:25 | 2026-08-24 11:25 |  |  | Fair | No | Premises found ok upon arrival Voltage 117v118v235v
Non-Outage | J.E.26.08.34152 | C001897912 | Orville Lee | St.Catherine | Completed | Load_243421 | Twickenham - 210 | 2026-08-24 08:09 | 2026-08-24 08:10 | 2026-08-24 10:46 | 2026-08-24 10:47 | 2026-08-24 10:47 | 2026-08-24 10:58 | 2026-08-24 10:58 | 2026-08-24 10:58 |  |  | Fair | No | Premises found ok upon arrival Voltage 115v116v231v
Non-Outage | J.E.26.08.34728 | C001897911 | Orville Lee | St.Catherine | Completed | Load_267930 | Twickenham - 210 | 2026-08-24 08:09 | 2026-08-24 08:10 | 2026-08-24 13:29 | 2026-08-24 13:29 | 2026-08-24 13:48 | 2026-08-24 13:59 | 2026-08-24 13:59 | 2026-08-24 13:59 |  |  | Fair | No | Premises found ok upon arrival Customer was making report prior to an outage in the area Voltage 115V116V232V
Non-Outage | J.E.26.08.34731 | C001897908 | Orville Lee | St.Catherine | Completed | Load_239984 | Twickenham - 210 | 2026-08-24 08:09 | 2026-08-24 08:10 | 2026-08-24 10:17 | 2026-08-24 10:24 | 2026-08-24 10:24 | 2026-08-24 10:38 | 2026-08-24 10:38 | 2026-08-24 10:38 |  |  | Fair | No | Premises found ok upon arrival Voltage 112115227
Non-Outage | J.E.26.08.34735 | C001897907 | Orville Lee | St.Catherine | Completed | Load_243421 | Twickenham - 210 | 2026-08-24 08:09 | 2026-08-24 08:10 | 2026-08-24 14:01 | 2026-08-24 14:02 | 2026-08-24 14:06 | 2026-08-24 14:10 | 2026-08-24 14:10 | 2026-08-24 14:10 |  |  | Fair | No | Premises found ok upon arrival Customer was reporting outage in the areaVoltage 115V116V231V
Outage | J.E.26.08.35842 | C001897917 | Nickolas Rodriques | St.Catherine | Completed | Load_252298 | Twickenham - 410 | 2026-08-24 08:11 | 2026-08-24 08:12 | 2026-08-24 08:47 | 2026-08-24 08:54 | 2026-08-24 09:41 | 2026-08-24 11:14 | 2026-08-24 11:16 | 2026-08-24 11:16 |  |  | Fair | No | Checked and found two 30 amp junction fuses blown. Two 10 amp junction fuses from the same line were also found blown. Patrol and found nothing on line. Repaired by replacing the fuses after completing patrol.
Outage | J.E.26.08.35845 | C001897920 | Elvis Trowers | KSAS | Completed | Load_579135 | Duhaney - 310 | 2026-08-24 08:13 | 2026-08-24 08:16 | 2026-08-24 10:04 | 2026-08-24 10:06 | 2026-08-24 10:06 | 2026-08-24 10:05 | 2026-08-24 10:07 | 2026-08-24 10:07 |  |  | Fair | No | Call related to call at #27 Gordon terrace.
Non-Outage | J.E.26.08.35849 | C001897921 | Fredrick Hamilton | KSAN | Completed | Load_573709 | Washington Blvd - 510 | 2026-08-24 08:15 | 2026-08-24 08:53 | 2026-08-24 10:24 | 2026-08-24 12:15 | 2026-08-24 12:44 | 2026-08-24 12:45 | 2026-08-24 12:46 | 2026-08-24 12:46 |  |  | Fair | No | Defective meter socket at location/ burnt wires in socket Customer advised to have electrician correct same
Outage | J.E.26.08.29334 | C001897930 | Marlon Brown | Trelawny | Completed | Load_255143 | Greenwood - 110 | 2026-08-24 08:17 | 2026-08-24 08:17 | 2026-08-24 12:51 | 2026-08-24 12:51 | 2026-08-24 13:48 | 2026-08-24 14:48 | 2026-08-24 14:48 | 2026-08-24 14:48 | BrokenWire |  | Fair | No | Repair defective joint at service wire, however meter # 2613028 @ Stanchion was disconnected due to wires being burnt in the conduit, meter is also burnt, this customer has been advised to have repairs done. Voltage found at pothead 117Voltage leaving at pothead 117/117=234v.
Outage | J.E.26.08.35850 | C001897931 | Milton Charlton | KSAN | Completed | Load_578921 | Hope - 510 | 2026-08-24 08:17 | 2026-08-24 08:19 | 2026-08-24 10:33 | 2026-08-24 10:33 | 2026-08-24 10:33 | 2026-08-24 09:30 | 2026-08-24 10:35 | 2026-08-24 10:35 | BrokenWire |  | Fair | No | Premises closed. Nobody at home..
Non-Outage | J.E.26.08.33409 | C001897932 | Wayne Dillion | St.Elizabeth | Completed | Load_292293 | Maggotty - 110 | 2026-08-24 08:20 | 2026-08-24 08:21 | 2026-08-24 10:04 | 2026-08-24 10:04 | 2026-08-24 10:04 | 2026-08-24 10:05 | 2026-08-24 10:05 | 2026-08-24 10:05 |  |  | Fair | No | Customer said problem has been resolved
Non-Outage | J.E.26.08.30906 | C001897938 | Nicholas Dillon | St.Elizabeth | Completed | Load_292777 | Maggotty - 210 | 2026-08-24 08:21 | 2026-08-24 08:24 | 2026-08-24 11:15 | 2026-08-24 11:16 | 2026-08-24 11:15 | 2026-08-24 11:15 | 2026-08-24 11:19 | 2026-08-24 11:19 |  |  | Fair | No | Check and found one side of the customer meter burn up refer to maintenance to change customer meter
Non-Outage | J.E.26.08.31318 | C001897939 | Nicholas Dillon | St.Elizabeth | Completed | Load_292293 | Maggotty - 110 | 2026-08-24 08:21 | 2026-08-24 08:24 | 2026-08-24 11:24 | 2026-08-24 11:24 | 2026-08-24 11:24 | 2026-08-24 11:24 | 2026-08-24 11:25 | 2026-08-24 11:25 |  |  | Fair | Yes | Check and found corrosion at pole clean corrosion use 1 one bolt clamp before I left voltage is 115 115 phase to phase 230
Non-Outage | J.E.26.08.31463 | C001897937 | Nicholas Dillon | St.Elizabeth | Completed | Load_267210 | Maggotty - 110 | 2026-08-24 08:21 | 2026-08-24 08:24 | 2026-08-24 11:07 | 2026-08-24 11:07 | 2026-08-24 11:07 | 2026-08-24 11:07 | 2026-08-24 11:11 | 2026-08-24 11:11 |  |  | Fair | No | Customer not ready for connection meter socket damage
Non-Outage | J.E.26.08.32180 | C001897936 | Nicholas Dillon | St.Elizabeth | Completed | Load_269917 | Maggotty - 110 | 2026-08-24 08:21 | 2026-08-24 08:24 | 2026-08-24 11:03 | 2026-08-24 11:04 | 2026-08-24 11:03 | 2026-08-24 11:03 | 2026-08-24 11:04 | 2026-08-24 11:04 |  |  | Fair | No | Check and found corrosion at pole clean corrosion use 2 one bolt clamp before I left voltage is 117 116 phase to phase 233
Non-Outage | J.E.26.08.32277 | C001897935 | Nicholas Dillon | St.Elizabeth | Completed | Load_258926 | Maggotty - 110 | 2026-08-24 08:21 | 2026-08-24 08:24 | 2026-08-24 10:54 | 2026-08-24 10:54 | 2026-08-24 10:54 | 2026-08-24 10:56 | 2026-08-24 10:57 | 2026-08-24 10:57 |  |  | Fair | No | Check voltage before at meter 111 113 phase to phase 225 . Premises found working ok
Non-Outage | J.E.26.08.33948 | C001897934 | Nicholas Dillon | Manchester | Completed | Load_256490 | Spur Tree - 210 | 2026-08-24 08:21 | 2026-08-24 08:24 | 2026-08-24 10:36 | 2026-08-24 10:37 | 2026-08-24 10:36 | 2026-08-24 10:36 | 2026-08-24 10:43 | 2026-08-24 10:43 |  |  | Fair | No | Check meter before at meter 112 114 phase to phase 226 . Whole area experiencing low voltage at night time only
Non-Outage | J.E.26.08.31405 | C001897948 | Odaine Johnson | Clarendon | Completed | Load_245032 | Parnassus - 210 | 2026-08-24 08:23 | 2026-08-24 08:24 | 2026-08-24 08:29 | 2026-08-24 11:48 | 2026-08-24 12:09 | 2026-08-24 12:30 | 2026-08-24 12:33 | 2026-08-24 12:33 |  |  | Fair | No | Single phase coming out of transformer meter but two phase going to meter, one phase was jump temporarily so that the customer on transformer circuit could receive both phase voltage reading 118/118/237 volts
Non-Outage | J.E.26.08.33808 | C001897949 | Odaine Johnson | Clarendon | Completed | Load_258199 | Parnassus - 210 | 2026-08-24 08:23 | 2026-08-24 08:24 | 2026-08-24 08:29 | 2026-08-24 12:52 | 2026-08-24 13:25 | 2026-08-24 13:25 | 2026-08-24 13:26 | 2026-08-24 13:26 |  |  | Fair | No | Area experiencing low voltage requesting a emergency team
Non-Outage | J.E.26.08.34726 | C001897950 | Odaine Johnson | Clarendon | Completed | Load_248579 | Parnassus - 210 | 2026-08-24 08:23 | 2026-08-24 08:24 | 2026-08-24 08:30 | 2026-08-24 12:49 | 2026-08-24 12:50 | 2026-08-24 12:51 | 2026-08-24 12:51 | 2026-08-24 12:51 |  |  | Fair | No | Corroded phase found at pole remade connection using 1 one bolt clamp voltage reading 114/113/228 volts
Non-Outage | J.E.26.08.35544 | C001897954 | Orville Lee | St.Catherine | Completed | Load_557330 | Twickenham - 210 | 2026-08-24 08:24 | 2026-08-24 08:25 | 2026-08-24 09:12 | 2026-08-24 09:13 | 2026-08-24 09:51 | 2026-08-24 09:52 | 2026-08-24 10:00 | 2026-08-24 10:00 |  |  | Fair | No | Premises found ok upon arrival Customer was reporting a outage in the area 117v116v234v
Non-Outage | J.E.26.08.35852 | C001897953 | Andre Smith | KSAS | Completed | Load_247734 | Three Miles - 510 | 2026-08-24 08:24 | 2026-08-24 09:54 | 2026-08-24 10:17 | 2026-08-24 10:18 | 2026-08-24 10:42 | 2026-08-24 10:43 | 2026-08-24 10:43 | 2026-08-24 10:43 |  |  | Fair | No | Defective 50kva transformer found maintenance department required
Non-Outage | J.E.26.08.35858 | C001897951 | Rusean Allen |  | Completed |  |  | 2026-08-24 08:24 | 2026-08-24 08:28 | 2026-08-24 09:53 | 2026-08-24 10:06 | 2026-08-24 10:06 | 2026-08-24 10:06 | 2026-08-24 10:06 | 2026-08-24 10:06 | BrokenPole |  | Fair | No | Related
Outage | J.E.26.08.35856 | C001897956 | Dwain Samuels | St.Elizabeth | Completed | Load_269458 | Maggotty - 110 | 2026-08-24 08:25 | 2026-08-24 08:33 | 2026-08-24 08:38 | 2026-08-24 08:38 | 2026-08-24 09:33 | 2026-08-24 09:45 | 2026-08-24 09:49 | 2026-08-24 09:49 |  |  | Fair | No | Connect 3 wire service. Use 65ft service wire 3 one bolt clamp 3 pen union clamp. Voltage check 114-115- 229
Non-Outage | J.E.26.08.35864 | C001897959 | Rayon Foster | Hanover | Completed | Load_265958 | Orange Bay - 310 | 2026-08-24 08:26 | 2026-08-24 08:27 | 2026-08-24 08:40 | 2026-08-24 08:41 | 2026-08-24 10:11 | 2026-08-24 12:15 | 2026-08-24 12:16 | 2026-08-24 12:16 |  |  | Fair | No | Voltage check at transformer pole when arrived on location116/116AB232 volts open one 25kva transformer to repair burn out drop lead joints connected to secondary line repair burn out drop lead joints with four one bolt clamps voltage check after closing one 25kva transformer 120/120AB240volts voltage check in customer meter socket 117/115AB232volts spoke with another customer in the community her name is Larissa haughton/Arlena James meter #2476490 also check with customers at meters#2886636 /(#2953247) and they where ok with there electricity
Outage | J.E.26.08.33922 | C001897957 | Shawn Medley | St.James | Completed | Load_263688 | Queens Drive - 710 | 2026-08-24 08:26 | 2026-08-24 08:26 | 2026-08-24 09:37 | 2026-08-24 10:14 | 2026-08-24 10:14 | 2026-08-24 10:15 | 2026-08-24 10:23 | 2026-08-24 10:23 | BrokenPole |  | Fair | No | Customer states they are located in trelawny and will make another report with correct adress
Non-Outage | J.E.26.08.35312 | C001897968 | Hopeton Henry | St.Thomas | Completed | Load_350229 | Good Year - 210 | 2026-08-24 08:29 | 2026-08-24 08:33 | 2026-08-24 10:12 | 2026-08-24 10:13 | 2026-08-24 11:02 | 2026-08-24 13:36 | 2026-08-24 13:37 | 2026-08-24 13:37 |  |  | Fair | No | Premises found ok 116-117-234 volts
Non-Outage | J.E.26.08.35785 | C001897969 | Hopeton Henry | St.Thomas | Completed | Load_258338 | Good Year - 210 | 2026-08-24 08:29 | 2026-08-24 08:33 | 2026-08-24 10:12 | 2026-08-24 13:48 | 2026-08-24 13:49 | 2026-08-24 14:26 | 2026-08-24 14:27 | 2026-08-24 14:27 |  |  | Fair | No | Reconnect service at pole reading 110-112-222 volts
Non-Outage | J.E.26.08.23980 | C001897970 | Hopeton Henry | St.Thomas | Completed | Load_240667 | Good Year - 110 | 2026-08-24 08:30 | 2026-08-24 08:33 | 2026-08-24 10:12 | 2026-08-24 14:28 | 2026-08-25 09:27 | 2026-08-25 09:34 | 2026-08-25 09:37 | 2026-08-25 09:37 |  | Y | Fair | No | Bucket truck required to cut tree, tree make contact to primary conductor when ever it gets windy
Non-Outage | J.E.26.08.27994 | C001897976 | Shamour Haughton | St.James | Completed | Load_246427 | Bogue - 310 | 2026-08-24 08:33 | 2026-08-24 08:33 | 2026-08-24 10:24 | 2026-08-24 10:24 | 2026-08-24 11:50 | 2026-08-24 11:50 | 2026-08-24 11:58 | 2026-08-24 11:58 |  |  | Fair | No | Found 1,100kva fuse blown,refuse 100kva use 1,10amp fuse, voltage left 111,112,223
Non-Outage | J.E.26.08.29038 | C001897978 | Shamour Haughton | St.James | Completed | Load_246427 | Bogue - 310 | 2026-08-24 08:33 | 2026-08-24 08:34 | 2026-08-24 11:59 | 2026-08-24 11:59 | 2026-08-24 11:59 | 2026-08-24 11:59 | 2026-08-24 11:59 | 2026-08-24 11:59 |  |  | Fair | No | Related to previous report
Non-Outage | J.E.26.08.35862 | C001897977 | Ryan Richards | Manchester | Completed | Load_252232 | Spur Tree - 310 | 2026-08-24 08:33 | 2026-08-24 08:34 | 2026-08-24 11:21 | 2026-08-24 11:22 | 2026-08-24 13:00 | 2026-08-24 13:40 | 2026-08-24 13:40 | 2026-08-24 13:40 |  |  | Fair | Yes | Defective service wire found at premises removed old wire replaced 55ft#6 triplex 3 penunion 3 one bolt clamps voltage 113/110/224 volts
Outage | J.E.26.08.35869 | C001897979 | Andre Smith | KSAS | Completed | Load_251195 | Three Miles - 410 | 2026-08-24 08:34 | 2026-08-24 08:38 | 2026-08-24 09:47 | 2026-08-24 09:48 | 2026-08-24 10:16 | 2026-08-24 10:17 | 2026-08-24 10:17 | 2026-08-24 10:17 |  |  | Fair | No | Premises found okay supply restored already
Non-Outage | J.E.26.08.30362 | C001897991 | Andrae Dawkins | St.James | Completed | Load_246501 | Queens Drive - 810 | 2026-08-24 08:39 | 2026-08-24 08:39 | 2026-08-24 11:06 | 2026-08-24 11:07 | 2026-08-24 11:10 | 2026-08-24 11:42 | 2026-08-24 11:42 | 2026-08-24 11:42 |  |  | Fair | No | Found customer experiencing low voltage due to fuse blown refer back to emergency crew
Non-Outage | J.E.26.08.20571 | C001897992 | Andrae Dawkins | St.James | Completed | Load_240776 | Queens Drive - 810 | 2026-08-24 08:40 | 2026-08-24 08:40 | 2026-08-24 08:59 | 2026-08-24 10:27 | 2026-08-24 10:39 | 2026-08-24 10:58 | 2026-08-24 11:01 | 2026-08-24 11:01 |  |  | Fair | No | Found multiple customers single phasing due to secondary jumper burnt off cleaned and remade joint voltage left 115/117/232
Non-Outage | J.E.26.08.27854 | C001897993 | Andrae Dawkins | St.James | Completed | Load_267418 | Queens Drive - 710 | 2026-08-24 08:41 | 2026-08-24 08:42 | 2026-08-24 13:02 | 2026-08-24 13:02 | 2026-08-24 13:02 | 2026-08-24 13:19 | 2026-08-24 13:23 | 2026-08-24 13:23 |  |  | Fair | No | Found customer meter 200ft from JPS pole advised customer to get an electrician
Non-Outage | J.E.26.08.18402 | C001898009 | Andrae Dawkins | St.James | Completed | Load_248155 | Queens Drive - 710 | 2026-08-24 08:43 | 2026-08-24 08:44 | 2026-08-24 09:00 | 2026-08-24 10:19 | 2026-08-24 10:21 | 2026-08-24 10:23 | 2026-08-24 10:24 | 2026-08-24 10:24 |  |  | Fair | No | Cannot locate customer due to no proper directions also unable to reach customers mobile phone
Outage | J.E.26.08.35890 | C001898026 | Rusean Allen | KSAS | Completed | Load_244940 | Cane River - 410 | 2026-08-24 08:52 | 2026-08-24 08:54 | 2026-08-24 10:23 | 2026-08-24 10:24 | 2026-08-24 11:06 | 2026-08-24 12:31 | 2026-08-24 12:31 | 2026-08-24 12:31 | BrokenWire |  | Fair | No | Wires burnt at meter socket, customer was advised to contact electrician.
Non-Outage | J.E.26.08.35879 | C001898035 | Rusean Allen | KSAS | Completed | Load_237680 | Cane River - 410 | 2026-08-24 09:00 | 2026-08-24 09:03 | 2026-08-24 10:56 | 2026-08-24 13:42 | 2026-08-24 14:42 | 2026-08-24 14:43 | 2026-08-24 14:43 | 2026-08-24 14:43 | BrokenWire |  | Fair | No | Defective wires found at meter socket, customer was advised to contact electrician.
Non-Outage | J.E.26.08.35881 | C001898036 | Rusean Allen | KSAS | Completed | Load_257873 | Rockfort - 210 | 2026-08-24 09:00 | 2026-08-24 09:03 | 2026-08-24 09:52 | 2026-08-24 10:01 | 2026-08-24 10:00 | 2026-08-24 10:04 | 2026-08-24 10:05 | 2026-08-24 10:05 | BrokenPole |  | Fair | No | Broken pole containing open secondary wire, 3phase primary wires and a streetlight. Service wires were disconnected and removed from roadway Maintenance department already aware of problem
Outage | J.E.26.08.35897 | C001898037 | Marlon Brown | Trelawny | Completed | Load_261243 | Greenwood - 110 | 2026-08-24 09:01 | 2026-08-24 09:02 | 2026-08-24 12:05 | 2026-08-24 12:06 | 2026-08-24 12:05 | 2026-08-24 12:06 | 2026-08-24 12:06 | 2026-08-24 12:06 |  |  | Fair | No | Same as call number 35929.
Outage | J.E.26.08.35904 | C001898051 | Marlon Brown | Trelawny | Completed | Load_246009 | Greenwood - 110 | 2026-08-24 09:02 | 2026-08-24 09:02 | 2026-08-24 12:06 | 2026-08-24 12:06 | 2026-08-24 12:06 | 2026-08-24 12:06 | 2026-08-24 12:07 | 2026-08-24 12:07 |  |  | Fair | No | Same as call number 35929
Outage | J.E.26.08.35914 | C001898052 | Stephen Taylor | St.Thomas | Completed | Load_265545 | Lysson - 410 | 2026-08-24 09:02 | 2026-08-24 09:06 | 2026-08-24 11:43 | 2026-08-24 11:44 | 2026-08-24 11:53 | 2026-08-24 12:10 | 2026-08-24 12:11 | 2026-08-24 12:11 | BrokenWire |  | Fair | No | Clean up single phase use 2 clamps reading 111,112,224 customer is now okay
Outage | J.E.26.08.35905 | C001898067 | Michael Paterson | Westmoreland | Completed | Load_556292 | Paradise - 210 | 2026-08-24 09:08 | 2026-08-24 09:11 | 2026-08-24 11:02 | 2026-08-24 11:03 | 2026-08-24 12:14 | 2026-08-24 13:06 | 2026-08-24 13:06 | 2026-08-24 13:06 |  |  | Fair | No | Patrol done, found two junction fuse blown, also found a 15kva xfmr fuse blown, spot bushing done, upgrade 10amp fuse 25amps at main junction, 15amp at second junction, replace 2amps fuse at xfmr, supply restored.
Non-Outage | J.E.26.08.35583 | C001898084 | Christopher West |  | Completed |  |  | 2026-08-24 09:12 | 2026-08-24 16:44 | 2026-08-24 20:33 | 2026-08-24 20:34 | 2026-08-24 21:35 | 2026-08-24 21:35 | 2026-08-24 21:35 | 2026-08-24 21:35 |  |  | Fair | No | Customer stated that matter was resolved from yesterday.
Outage | J.E.26.08.35745 | C001898082 | Wan Carlos Scarlett | St.Catherine | Completed | Load_238600 | Twickenham - 210 | 2026-08-24 09:12 | 2026-08-24 09:13 | 2026-08-24 13:47 | 2026-08-24 13:47 | 2026-08-24 14:29 | 2026-08-24 14:32 | 2026-08-24 14:33 | 2026-08-24 14:33 |  |  | Fair | No | Customer confirm that power supply has been restored
Outage | J.E.26.08.35884 | C001898086 | Kenroy Dale | Manchester | Completed | Load_265749 | Kendal - 310 | 2026-08-24 09:13 | 2026-08-24 09:14 | 2026-08-24 12:06 | 2026-08-24 12:31 | 2026-08-24 14:22 | 2026-08-24 14:49 | 2026-08-24 14:52 | 2026-08-24 14:52 | BrokenWire |  | Fair | No | Meter defective and need to be replace in order for customers to have supply voltage reading 112/118/230
Outage | J.E.26.08.35929 | C001898085 | Marlon Brown | Trelawny | Completed | Load_247038 | Greenwood - 110 | 2026-08-24 09:13 | 2026-08-24 09:14 | 2026-08-24 09:30 | 2026-08-24 09:31 | 2026-08-24 10:58 | 2026-08-24 12:02 | 2026-08-24 12:04 | 2026-08-24 12:04 |  |  | Fair | No | Close 2 65amps trip savers at cane field and 1 40amps junction fuse at Dumfries square, however this drop out switch is sparking needs to be replaced, it’s the switch at the bush phase.
Outage | J.E.26.08.35931 | C001898089 | Horace Malcolm | St.James | Completed | Load_246135 | Bogue - 610 | 2026-08-24 09:14 | 2026-08-24 09:15 | 2026-08-24 12:04 | 2026-08-24 12:05 | 2026-08-24 12:04 | 2026-08-24 13:49 | 2026-08-24 13:49 | 2026-08-24 13:49 |  | Y | Rains | Yes | Refused one 50amp junction fuse pole number 215467
Outage | J.E.26.08.35844 | C001898103 | Omar King | St.Ann | Completed | Load_294552 | Cardiff Hall - 210 | 2026-08-24 09:18 | 2026-08-24 15:26 | 2026-08-24 19:01 | 2026-08-24 19:01 | 2026-08-24 19:06 | 2026-08-24 19:35 | 2026-08-24 19:36 | 2026-08-24 19:36 | BrokenWire |  | Fair | No | Found customer three(3) wire service open as been repaired customer is now with supply
Non-Outage | J.E.26.08.35908 | C001898118 | Oraine Minto | St.Ann | Completed | Load_264120 | Cardiff Hall - 310 | 2026-08-24 09:22 | 2026-08-24 09:24 | 2026-08-24 11:55 | 2026-08-24 13:47 | 2026-08-24 13:47 | 2026-08-24 13:48 | 2026-08-24 13:56 | 2026-08-24 13:56 |  |  | Fair | No | Refer to maintenance Transformer voltage is too low to this customer 214v 105v 108v Customer is far away from the transformer Pole#0186963
Non-Outage | J.E.26.08.35868 | C001898119 | Locksley Allen | St.Mary | Completed | Load_239399 | Oracabessa - 210 | 2026-08-24 09:25 | 2026-08-24 09:26 | 2026-08-24 11:09 | 2026-08-24 12:20 | 2026-08-24 12:19 | 2026-08-24 13:16 | 2026-08-24 13:15 | 2026-08-24 13:15 |  |  | Fair | No | Meter found blank. Install 3 clamps at pole and 2 clamps at pothead Voltage at meter socket phase to phase 238v. Phase to neutral 115&116vMeter left working okay
Non-Outage | J.E.26.08.35962 | C001898130 | Rochaine Hussey | KSAN | Completed | Load_252601 | Constant Spring - 310 | 2026-08-24 09:28 | 2026-08-24 09:34 | 2026-08-24 09:45 | 2026-08-24 12:51 | 2026-08-24 12:53 | 2026-08-24 13:23 | 2026-08-24 13:26 | 2026-08-24 13:26 |  |  | Fair | No | Slack connection on poleIssue was resolved 121/121/242v
Non-Outage | J.E.26.08.35970 | C001898132 | Neckell Ormsby |  | Completed |  |  | 2026-08-24 09:29 | 2026-08-24 09:31 | 2026-08-24 09:36 | 2026-08-24 09:40 | 2026-08-24 10:57 | 2026-08-24 11:11 | 2026-08-24 11:12 | 2026-08-24 11:12 | TreeContact |  | Fair | No | Found trees growing into secondary please refer to maintenance department t have line section bushed
Outage | J.E.26.08.35906 | C001898133 | Neville Spencer |  | Completed | Load_556152 | Parnassus - 310 | 2026-08-24 09:29 | 2026-08-24 09:31 | 2026-08-24 09:50 | 2026-08-24 09:51 | 2026-08-24 10:25 | 2026-08-24 10:25 | 2026-08-24 11:53 | 2026-08-24 11:53 |  |  | Fair | No | Renew 2 blown 30 and j/ fuse . Also found burnt off Primary phase jumper at pole # 0112106 in main line REF To Maintenance.
Outage | J.E.26.08.35920 | C001898134 | Elvis Trowers | KSAN | Completed | Load_254366 | Constant Spring - 210 | 2026-08-24 09:30 | 2026-08-24 09:39 | 2026-08-24 20:09 | 2026-08-24 20:14 | 2026-08-24 20:13 | 2026-08-24 20:15 | 2026-08-24 20:15 | 2026-08-24 20:15 | TreeContact |  | Fair | No | Primary and secondary bushings require urgently. Refer to vegetation control team .
Outage | J.E.26.08.35951 | C001898146 | Tyrese Williams | St.Ann | Completed | Load_256279 | Roaring River - 410 | 2026-08-24 09:35 | 2026-08-24 09:36 | 2026-08-24 11:33 | 2026-08-24 11:50 | 2026-08-24 12:59 | 2026-08-24 13:14 | 2026-08-24 13:14 | 2026-08-24 13:14 | LeaningPole |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.08.35955 | C001898144 | Tyrese Williams | St.Ann | Completed | Load_247617 | Roaring River - 210 | 2026-08-24 09:35 | 2026-08-24 09:36 | 2026-08-24 11:33 | 2026-08-24 13:15 | 2026-08-24 14:02 | 2026-08-24 14:15 | 2026-08-24 14:15 | 2026-08-24 14:15 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Remade service wire joint at pole use 1pg clamp
Outage | J.E.26.08.35960 | C001898145 | Omar King | St.Ann | Completed | Load_256510 | Cardiff Hall - 210 | 2026-08-24 09:35 | 2026-08-24 15:28 | 2026-08-24 16:07 | 2026-08-24 16:08 | 2026-08-24 18:34 | 2026-08-24 18:38 | 2026-08-24 18:38 | 2026-08-24 18:38 | LowHangingWires |  | Fair | No | The problem has been resolved the meter has been changed
Non-Outage | J.E.26.08.35957 | C001898151 | Andrae Clarke | Portland | Completed | Load_266281 | Port Antonio - 410 | 2026-08-24 09:39 | 2026-08-24 09:41 | 2026-08-24 09:52 | 2026-08-24 09:55 | 2026-08-24 11:40 | 2026-08-24 12:12 | 2026-08-24 12:11 | 2026-08-24 12:11 |  |  | Fair | No | Check and found wire loose Thighen wire and check voltage 114/117/231
Non-Outage | J.E.26.08.35996 | C001898155 | Rochaine Hussey | KSAS | Completed | Load_261568 | Duhaney - 310 | 2026-08-24 09:43 | 2026-08-24 09:48 | 2026-08-24 13:33 | 2026-08-24 14:18 | 2026-08-24 14:17 | 2026-08-24 14:19 | 2026-08-24 14:19 | 2026-08-24 14:19 |  |  | Fair | No | Customer said the issue was already resolved
Non-Outage | J.E.26.08.26109 | C001898175 | Edward Royal | KSAS | Completed | Load_293369 | Hunts Bay - 810 | 2026-08-24 09:53 | 2026-08-24 09:54 | 2026-08-24 11:41 | 2026-08-24 11:41 | 2026-08-24 11:41 | 2026-08-24 12:01 | 2026-08-24 12:02 | 2026-08-24 12:02 |  |  | Fair | No | Meter not responding referred to field service
Outage | J.E.26.08.35801 | C001898176 | Horace Malcolm |  | Completed | Load_246939 | Bogue - 610 | 2026-08-24 09:53 | 2026-08-24 09:54 | 2026-08-24 10:33 | 2026-08-24 10:34 | 2026-08-24 10:34 | 2026-08-24 11:37 | 2026-08-24 11:37 | 2026-08-24 11:37 |  | Y | Fair | No | Cut and clear coconut tre limb from primary line and replace one 30amp junction fuse
Non-Outage | J.E.26.08.35985 | C001898177 | Edward Royal | KSAS | Completed | Load_243181 | Hunts Bay - 310 | 2026-08-24 09:54 | 2026-08-24 09:55 | 2026-08-24 12:02 | 2026-08-24 12:02 | 2026-08-24 12:21 | 2026-08-24 12:26 | 2026-08-24 12:26 | 2026-08-24 12:26 |  |  | Fair | No | Premises found close
Outage | J.E.26.08.36010 | C001898184 | Elvis Trowers | KSAN | Completed | Load_265459 | Constant Spring - 210 | 2026-08-24 09:58 | 2026-08-24 09:59 | 2026-08-24 11:28 | 2026-08-24 11:29 | 2026-08-24 12:20 | 2026-08-24 12:20 | 2026-08-24 12:25 | 2026-08-24 12:25 |  |  | Fair | No | Unable to locate customer by telephone. Calls to customer went unanswered.
Outage | J.E.26.08.35999 | C001898191 | Nickolas Rodriques | St.Catherine | Completed | Load_240984 | Tredegar - 510 | 2026-08-24 10:06 | 2026-08-24 10:07 | 2026-08-24 11:58 | 2026-08-24 12:24 | 2026-08-24 12:33 | 2026-08-24 12:49 | 2026-08-24 12:55 | 2026-08-24 12:55 |  |  | Fair | No | Customer was located and confirmed that the power outage was resorted.
Outage | J.E.26.08.36008 | C001898192 | Wan Carlos Scarlett | St.Catherine | Completed | Load_267611 | Twickenham - 210 | 2026-08-24 10:06 | 2026-08-24 10:07 | 2026-08-24 10:26 | 2026-08-24 11:01 | 2026-08-24 11:03 | 2026-08-24 11:59 | 2026-08-24 12:04 | 2026-08-24 12:04 | BrokenWire |  | Fair | No | Found 2 span of open secondary line top phase burn down use 200ft of # 2 loom wire use 2 splicing sleeve 4 one bolt clamps isolate and close 25KVA transformer pole # 020953 power supply has been installed
Outage | J.E.26.08.35992 | C001898205 | Javid Vernon | Westmoreland | Completed | Load_245455 | Paradise - 310 | 2026-08-24 10:07 | 2026-08-24 10:08 | 2026-08-24 10:34 | 2026-08-24 10:35 | 2026-08-24 11:29 | 2026-08-24 11:38 | 2026-08-24 11:38 | 2026-08-24 11:38 |  |  | Fair | No | Reclose one 25kva transformer
Non-Outage | J.E.26.08.36022 | C001898215 | Wan Carlos Scarlett |  | Completed |  |  | 2026-08-24 10:13 | 2026-08-24 10:14 | 2026-08-24 10:26 | 2026-08-24 12:39 | 2026-08-24 13:01 | 2026-08-24 13:02 | 2026-08-24 13:04 | 2026-08-24 13:04 | BrokenWire |  | Fair | No | Customer confirm that power supply has been restored.Call related
Outage | J.E.26.08.36040 | C001898261 | Shamour Haughton | St.James | Completed | Load_256381 | Bogue - 310 | 2026-08-24 10:38 | 2026-08-24 10:38 | 2026-08-24 11:59 | 2026-08-24 12:00 | 2026-08-24 12:36 | 2026-08-24 12:36 | 2026-08-24 12:43 | 2026-08-24 12:43 |  |  | Fair | No | Customer needs 200ft of #6, the telephone pole that the service wire was attached to, has been down from hurricane Melissa, meter number that are affected are, 2632889, 2234359, 2598937,2632888, 2632887, please refer to field service
Outage | J.E.26.08.36056 | C001898263 | Lionel Robinson | Trelawny | Completed | Load_268469 | Duncans - 210 | 2026-08-24 10:39 | 2026-08-24 10:40 | 2026-08-24 12:05 | 2026-08-24 12:06 | 2026-08-24 12:49 | 2026-08-24 14:18 | 2026-08-24 14:19 | 2026-08-24 14:19 |  |  | Fair | No | Splice and retention 1 spans of 2/0 conductor and replace 20amp junction fuse
Outage | J.E.26.08.36071 | C001898277 | Neville Spencer | Clarendon | Completed | Load_264004 | Parnassus - 210 | 2026-08-24 10:44 | 2026-08-24 11:00 | 2026-08-24 14:45 | 2026-08-24 14:46 | 2026-08-24 17:38 | 2026-08-24 17:40 | 2026-08-24 17:41 | 2026-08-24 17:41 |  |  | Fair | No | Found ok call resolved.
Outage | J.E.26.08.36061 | C001898294 | Ryan Richards | Manchester | Completed | Load_292371 | Spur Tree - 310 | 2026-08-24 10:56 | 2026-08-24 10:57 | 2026-08-24 13:41 | 2026-08-24 13:42 | 2026-08-24 14:25 | 2026-08-24 14:39 | 2026-08-24 14:39 | 2026-08-24 14:39 |  |  | Fair | No | Unable to locate customer multiple efforts made to contact customer but unsuccessful area found with supply
Outage | J.E.26.08.36086 | C001898295 | Derrick Dawkins | St.James | Completed | Load_262522 | Bogue - 510 | 2026-08-24 10:56 | 2026-08-24 15:18 | 2026-08-24 17:39 | 2026-08-24 17:39 | 2026-08-24 17:40 | 2026-08-24 17:56 | 2026-08-24 17:41 | 2026-08-24 17:41 |  |  | Fair | No | Premises ok 117/118=236
Outage | J.E.26.08.36052 | C001898296 | Javid Vernon | Westmoreland | Completed | Load_265142 | Paradise - 310 | 2026-08-24 10:57 | 2026-08-24 10:58 | 2026-08-24 11:39 | 2026-08-24 11:52 | 2026-08-24 12:36 | 2026-08-24 13:44 | 2026-08-24 13:47 | 2026-08-24 13:47 |  |  | Fair | No | Isolate one 50kva transformer to reconnect transformer drop lead use two clamps and after reclosing transformer voltage left 116/117/234
Outage | J.E.26.08.35986 | C001898310 | Wayne Dillion | St.Elizabeth | Completed | Load_292795 | Maggotty - 110 | 2026-08-24 11:00 | 2026-08-24 11:01 | 2026-08-24 13:25 | 2026-08-24 13:25 | 2026-08-24 13:31 | 2026-08-24 14:17 | 2026-08-24 14:18 | 2026-08-24 14:18 |  |  | Fair | No | Supply check and found customer experiencing low voltage reading found 112v 99v remade joint at pole and pothead using 3 linket 3 one bolt clamp voltage leave at premises 112v 114v 228v supply leave working ok
Non-Outage | J.E.26.08.35875 | C001898311 | Nicholas Dillon | St.Elizabeth | Completed | Load_255437 | Maggotty - 210 | 2026-08-24 11:01 | 2026-08-24 11:19 | 2026-08-25 07:56 | 2026-08-25 09:04 | 2026-08-25 09:06 | 2026-08-25 09:06 | 2026-08-25 09:08 | 2026-08-25 09:08 |  |  | Fair | Yes | Check voltage before at meter 112 112 phase to phase 224 . Premises found working ok problem resolve
Non-Outage | J.E.26.08.35888 | C001898312 | Wayne Dillion | St.Elizabeth | Completed | Load_295222 | Maggotty - 110 | 2026-08-24 11:01 | 2026-08-24 12:13 | 2026-08-24 12:16 | 2026-08-24 12:17 | 2026-08-24 12:19 | 2026-08-24 13:17 | 2026-08-24 13:17 | 2026-08-24 13:17 |  |  | Fair | No | Supply check and found customer single phasing other check found a joint at pothead burn off remade the same using one linket voltage reading leave at premises 116v 115v 230v supply working ok
Non-Outage | J.E.26.08.35900 | C001898316 | Rusean Allen | KSAS | Completed | Load_243699 | Rockfort - 210 | 2026-08-24 11:02 | 2026-08-24 11:05 | 2026-08-24 12:48 | 2026-08-24 12:48 | 2026-08-24 13:08 | 2026-08-24 13:16 | 2026-08-24 13:17 | 2026-08-24 13:17 |  |  | Fair | No | Corroded clamp found at pole, clamp was changed.Voltage:118 117 235
Non-Outage | J.E.26.08.36042 | C001898314 | Odeanie Davis | KSAN | Completed | Load_252123 | Washington Blvd - 310 | 2026-08-24 11:02 | 2026-08-24 11:05 | 2026-08-24 12:57 | 2026-08-24 13:01 | 2026-08-24 13:01 | 2026-08-24 13:14 | 2026-08-24 13:14 | 2026-08-24 13:14 |  |  | Fair | No | 115v at location, customer is receiving same phase on both side from rammi box
Outage | J.E.26.08.36085 | C001898315 | Milton Charlton | KSAN | Completed | Load_579112 | West Kings House - 410 | 2026-08-24 11:02 | 2026-08-24 11:03 | 2026-08-24 12:06 | 2026-08-24 12:13 | 2026-08-24 12:20 | 2026-08-24 12:05 | 2026-08-24 12:27 | 2026-08-24 12:27 | Fire |  | Fair | No | Broken 30ft wooden pole#(no pole #) broken in three pieces in motor vehicle accident. Pole has on open wire secondary on 5ft crossarm. Need immediate attention. No customer lost supply.
Outage | J.E.26.08.36125 | C001898337 | Omar King | St.Ann | Completed | Load_1007080 | Cardiff Hall - 210 | 2026-08-24 11:16 | 2026-08-24 15:27 | 2026-08-24 18:40 | 2026-08-24 18:40 | 2026-08-24 18:56 | 2026-08-24 18:59 | 2026-08-24 19:00 | 2026-08-24 19:00 |  |  | Fair | No | Unable to contact the customer, call several times however no answer.
Outage | J.E.26.08.36097 | C001898339 | Derrick Dawkins | St.James | Completed | Load_258108 | Bogue - 610 | 2026-08-24 11:17 | 2026-08-24 15:33 | 2026-08-24 17:42 | 2026-08-24 17:43 | 2026-08-24 18:43 | 2026-08-24 19:02 | 2026-08-24 19:03 | 2026-08-24 19:03 |  |  | Fair | No | Found customer pothead corroded clean and remade joint voltage 112/111=224
Outage | J.E.26.08.36034 | C001898351 | Javid Vernon | St.Elizabeth | Completed | Load_238298 | Maggotty - 110 | 2026-08-24 11:19 | 2026-08-24 11:34 | 2026-08-24 13:50 | 2026-08-24 13:50 | 2026-08-24 14:34 | 2026-08-24 14:36 | 2026-08-24 14:38 | 2026-08-24 14:38 |  |  | Fair | No | Customer got disconnected because of none payment but was reconnected after payment
Outage | J.E.26.08.36140 | C001898362 | Javid Vernon | Westmoreland | Completed | Load_238512 | Paradise - 310 | 2026-08-24 11:30 | 2026-08-24 11:41 | 2026-08-24 14:39 | 2026-08-24 14:39 | 2026-08-24 15:13 | 2026-08-24 15:16 | 2026-08-24 15:16 | 2026-08-24 15:16 |  |  | Fair | No | Unable locate customer and premises after following directions to the area phone calls to customer number went unanswered
Non-Outage | J.E.26.08.36159 | C001898367 | Nickolas Rodriques |  | Completed |  |  | 2026-08-24 11:36 | 2026-08-24 11:41 | 2026-08-24 12:55 | 2026-08-24 12:56 | 2026-08-24 13:28 | 2026-08-24 13:57 | 2026-08-24 13:58 | 2026-08-24 13:58 | BrokenPole |  | Fair | No | No broken pole seen upon arrival. The customer is reporting a defective streetlight. Refer to streetlight department.
Non-Outage | J.E.26.08.35988 | C001898368 | Shawn Medley | St.James | Completed | Load_259501 | Queens Drive - 810 | 2026-08-24 11:37 | 2026-08-24 11:38 | 2026-08-24 12:08 | 2026-08-24 12:09 | 2026-08-24 12:52 | 2026-08-24 12:57 | 2026-08-24 12:59 | 2026-08-24 12:59 |  |  | Fair | No | Unable to conduct proper tests without volt meter ; unable to restore customer supply
Outage | J.E.26.08.36161 | C001898369 | Elvis Trowers | KSAS | Completed | Load_578720 | Duhaney - 310 | 2026-08-24 11:37 | 2026-08-24 11:40 | 2026-08-24 13:38 | 2026-08-24 15:23 | 2026-08-24 16:02 | 2026-08-24 16:00 | 2026-08-24 16:04 | 2026-08-24 16:04 |  |  | Fair | No | Found one 20 amps junction fuse blown at pole # 0052504 and one 2 amps transformer fuse blown at pole #( no pole #). Refused using one 20 amps fuse and one 2 amps fuse and reclosed junction And transformer switches.
Outage | J.E.26.08.36150 | C001898372 | Lionel Robinson | Trelawny | Completed | Load_302479 | Duncans - 210 | 2026-08-24 11:41 | 2026-08-24 11:42 | 2026-08-24 14:19 | 2026-08-24 14:20 | 2026-08-24 14:19 | 2026-08-24 14:21 | 2026-08-24 14:21 | 2026-08-24 14:21 | BrokenWire |  | Fair | No | Call related to previous work done
Outage | J.E.26.08.36160 | C001898373 | Shamour Haughton | St.James | Completed | Load_245056 | Bogue - 310 | 2026-08-24 11:42 | 2026-08-24 11:43 | 2026-08-24 12:55 | 2026-08-24 12:55 | 2026-08-24 12:55 | 2026-08-24 12:55 | 2026-08-24 12:57 | 2026-08-24 12:57 |  |  | Fair | No | Unable to locate customer without, needs better directions, cell number keeps going voicemail after several attempts
Outage | J.E.26.08.36012 | C001898380 | Horace Malcolm | St.James | Completed | Load_292985 | Bogue - 610 | 2026-08-24 11:46 | 2026-08-24 11:47 | 2026-08-24 13:51 | 2026-08-24 13:52 | 2026-08-24 13:51 | 2026-08-24 13:52 | 2026-08-24 13:52 | 2026-08-24 13:52 |  |  | Fair | No | Related to previous call job number 35931
Non-Outage | J.E.26.08.36077 | C001898389 | Roemello Brown | Trelawny | Completed | Load_247929 | Martha Brae - 110 | 2026-08-24 11:48 | 2026-08-24 11:49 | 2026-08-24 13:47 | 2026-08-24 14:13 | 2026-08-24 14:27 | 2026-08-24 14:27 | 2026-08-24 14:28 | 2026-08-24 14:28 |  |  | Fair | No | Customer meter socket defective inform customer to get an private electrician to have it replaced Voltage found 117/116/233Voltage leave 117/116/233
Outage | J.E.26.08.36151 | C001898395 | Shawn Medley | St.James | Completed | Load_246386 | Queens Drive - 810 | 2026-08-24 11:51 | 2026-08-24 11:52 | 2026-08-24 12:59 | 2026-08-24 13:20 | 2026-08-24 14:21 | 2026-08-24 14:21 | 2026-08-24 14:38 | 2026-08-24 14:38 | LowHangingWires |  | Fair | No | Premises need 2- 30ft poles, 6-D iron and spool ,1- guy attachment, 4- 2/0 to 2/0 ampacts 1 guy, strain 8- 10” bolt and washers, 4- 2/0 preform; low hanging 2/0 quad; pole to be replaced refer to maintenance, customer states she has been repeatedly reporting issue for three months and urgently needs poles to replaced by Wednesday, it was observed that one pole hole was already dug
Non-Outage | J.E.26.08.36171 | C001898404 | Hopeton Henry | St.Thomas | Completed | Load_256308 | Good Year - 110 | 2026-08-24 11:53 | 2026-08-24 11:56 | 2026-08-24 13:10 | 2026-08-24 14:27 | 2026-08-24 14:27 | 2026-08-24 14:27 | 2026-08-24 14:28 | 2026-08-24 14:28 |  |  | Fair | Yes | Internal problem, customer advised
Non-Outage | J.E.26.08.28423 | C001898406 | Wan Carlos Scarlett | St.Catherine | Completed | Load_249289 | Twickenham - 210 | 2026-08-24 11:54 | 2026-08-24 11:55 | 2026-08-24 13:05 | 2026-08-24 13:05 | 2026-08-24 13:28 | 2026-08-24 13:45 | 2026-08-24 13:47 | 2026-08-24 13:47 |  |  | Fair | No | Customer found 3 wire service at pole with one of the phase corroded use one bolt clamp at open secondary line phase readings 114-115-230
Outage | J.E.26.08.36191 | C001898421 | Rusean Allen | KSAS | Completed | Load_259617 | Up Park Camp - 510 | 2026-08-24 12:03 | 2026-08-24 12:04 | 2026-08-24 12:32 | 2026-08-24 12:32 | 2026-08-24 12:39 | 2026-08-24 12:47 | 2026-08-24 12:47 | 2026-08-24 12:47 |  |  | Fair | No | Customer phone went unanswered
Non-Outage | J.E.26.08.36189 | C001898423 | Edward Royal | KSAS | Completed | Load_301269 | Hunts Bay - 510 | 2026-08-24 12:04 | 2026-08-24 12:05 | 2026-08-24 12:30 | 2026-08-24 12:31 | 2026-08-24 12:33 | 2026-08-24 13:01 | 2026-08-24 13:04 | 2026-08-24 13:04 |  |  | Fair | No | Customer have internal problems customer have defective meter socket advise customer to get a electrician to fix the problem voltage reading 234 118 117 v
Outage | J.E.26.08.36202 | C001898432 | Andre Smith | KSAS | Completed | Load_248351 | Duhaney - 410 | 2026-08-24 12:11 | 2026-08-24 12:19 | 2026-08-24 14:44 | 2026-08-24 14:44 | 2026-08-24 15:11 | 2026-08-24 15:28 | 2026-08-24 15:28 | 2026-08-24 15:28 |  |  | Fair | No | Replace blown transformer fuse 5A supply restored
Non-Outage | J.E.26.08.36200 | C001898433 | Andre Smith | KSAS | Completed | Load_263614 | Hunts Bay - 210 | 2026-08-24 12:12 | 2026-08-24 12:14 | 2026-08-24 12:19 | 2026-08-24 12:19 | 2026-08-24 12:35 | 2026-08-24 13:32 | 2026-08-24 13:33 | 2026-08-24 13:33 | LowHangingWires |  | Fair | No | Replace defective switch link and repair burnt conductor using 20ft #2aa supply restored
Outage | J.E.26.08.29460 | C001898436 | Horace Malcolm | St.James | Completed | Load_260374 | Bogue - 610 | 2026-08-24 12:13 | 2026-08-24 12:25 | 2026-08-24 13:50 | 2026-08-24 13:50 | 2026-08-24 13:50 | 2026-08-24 13:51 | 2026-08-24 13:51 | 2026-08-24 13:51 |  |  | Fair | No | Related to previous call job number 35931
Non-Outage | J.E.26.08.29970 | C001898459 | Derrick Dawkins |  | Completed |  |  | 2026-08-24 12:24 | 2026-08-24 16:09 | 2026-08-24 16:53 | 2026-08-24 16:53 | 2026-08-24 17:36 | 2026-08-24 17:37 | 2026-08-24 17:38 | 2026-08-24 17:38 | Fire |  | Fair | No | Customer complained about illegal connection
Outage | J.E.26.08.36222 | C001898458 | Rusean Allen | KSAS | Completed | Load_253994 | Rockfort - 410 | 2026-08-24 12:24 | 2026-08-24 12:39 | 2026-08-24 13:17 | 2026-08-24 13:18 | 2026-08-24 13:36 | 2026-08-24 13:41 | 2026-08-24 13:41 | 2026-08-24 13:41 |  |  | Fair | No | Burnt wire and burnt meter lug found at meter socket customer was advised to contact electrician.
Outage | J.E.26.08.36176 | C001898464 | Moses Elliston | St.Catherine | Completed | Load_557177 | Tredegar - 210 | 2026-08-24 12:29 | 2026-08-24 12:29 | 2026-08-25 14:34 | 2026-08-25 14:34 | 2026-08-25 14:34 | 2026-08-25 14:34 | 2026-08-25 14:35 | 2026-08-25 14:35 |  |  | Fair | No | Credit added to prepaid account.See rep # 1715023
Non-Outage | J.E.26.08.36226 | C001898469 | Elvis Trowers | KSAN | Completed | Load_241548 | Washington Blvd - 410 | 2026-08-24 12:33 | 2026-08-24 12:38 | 2026-08-24 17:46 | 2026-08-24 17:46 | 2026-08-24 18:37 | 2026-08-24 18:45 | 2026-08-24 18:50 | 2026-08-24 18:50 |  |  | Fair | No | Check the voltage going to customer premises readings at pothead and pole 108-108-216 volts transfer customer main to the adjacent pole now customer getting a readings of 115-115-231 volts
Non-Outage | J.E.26.08.36243 | C001898480 | Milton Charlton | KSAN | Completed | Load_261591 | Hope - 510 | 2026-08-24 12:38 | 2026-08-24 12:41 | 2026-08-24 13:19 | 2026-08-24 13:20 | 2026-08-24 15:23 | 2026-08-24 15:15 | 2026-08-24 15:34 | 2026-08-24 15:34 | BangingWires |  | Fair | No | Two 40ft wooden poles #0214044 and 0143796 DV construction 1-wire primary and open wire secondary leaning and marked to changed,pulled down by motor vehicle causing conductors to be saggy and banging. Need to straightened or changed poles #0214044 and pole #0143796. Wires are hanging low above roadway. Need immediate attention.
Non-Outage | J.E.26.08.36240 | C001898482 | Neville Spencer |  | Completed |  |  | 2026-08-24 12:39 | 2026-08-24 12:45 | 2026-08-24 13:33 | 2026-08-24 13:34 | 2026-08-24 14:33 | 2026-08-24 14:33 | 2026-08-24 14:45 | 2026-08-24 14:45 |  |  | Fair | No | Found no supply at pothead REF to field service HEX # 06049.
Outage | J.E.26.08.36261 | C001898492 | Andre Smith | KSAS | Completed | Load_1002943 | Hunts Bay - 110 | 2026-08-24 12:45 | 2026-08-24 12:54 | 2026-08-24 13:33 | 2026-08-24 13:33 | 2026-08-24 14:41 | 2026-08-24 14:43 | 2026-08-24 14:44 | 2026-08-24 14:44 |  |  | Fair | No | Premises found okay supply restored already associated call
Outage | J.E.26.08.36268 | C001898512 | Michael Paterson | Westmoreland | Completed | Load_293032 | Paradise - 110 | 2026-08-24 12:59 | 2026-08-24 13:00 | 2026-08-24 13:26 | 2026-08-24 13:26 | 2026-08-24 13:26 | 2026-08-24 13:27 | 2026-08-24 13:27 | 2026-08-24 13:27 |  |  | Fair | No | Inadequate information, unable to locate premises.
Outage | J.E.26.08.36316 | C001898538 | Floyd Taylor | Trelawny | Completed | Load_237793 | Greenwood - 210 | 2026-08-24 13:20 | 2026-08-24 15:40 | 2026-08-24 20:00 | 2026-08-24 20:00 | 2026-08-24 20:23 | 2026-08-24 20:23 | 2026-08-24 20:24 | 2026-08-24 20:24 | BrokenPole |  | Fair | No | Call belong to ST JAMES
Outage | J.E.26.08.36227 | C001898553 | Andrae Dawkins | St.James | Completed | Load_261935 | Bogue - 310 | 2026-08-24 13:25 | 2026-08-24 13:26 | 2026-08-24 14:38 | 2026-08-25 08:28 | 2026-08-25 08:37 | 2026-08-25 08:45 | 2026-08-25 08:46 | 2026-08-25 08:46 |  |  | Fair | No | Cannot locate customer unable to reach customer’s mobile phone directions not clear
Outage | J.E.26.08.36327 | C001898554 | Edward Royal | KSAS | Completed | Load_1002764 | Greenwich - 410 | 2026-08-24 13:25 | 2026-08-24 13:27 | 2026-08-24 14:11 | 2026-08-24 14:11 | 2026-08-24 14:11 | 2026-08-24 14:13 | 2026-08-24 14:14 | 2026-08-24 14:14 |  |  | Fair | No | Meter not responding meter need to be check reffered to field
Non-Outage | J.E.26.08.36279 | C001898560 | Ryan Richards | Manchester | Completed | Load_259722 | Spur Tree - 310 | 2026-08-24 13:27 | 2026-08-24 13:28 | 2026-08-24 14:39 | 2026-08-24 14:40 | 2026-08-24 15:50 | 2026-08-24 17:16 | 2026-08-24 17:16 | 2026-08-24 17:16 |  |  | Rains | No | Burn off neutral at pole remade burn off neutral using 1and 1 penunion voltage 117/117/234 volts
Non-Outage | J.E.26.08.36339 | C001898564 | Edward Royal |  | Completed |  |  | 2026-08-24 13:33 | 2026-08-24 15:57 | 2026-08-24 20:47 | 2026-08-24 20:48 | 2026-08-24 20:59 | 2026-08-24 21:16 | 2026-08-24 21:17 | 2026-08-24 21:17 |  |  | Fair | No | Advice customer to visit the ruthven road for more information
Outage | J.E.26.08.36343 | C001898565 | Elvis Trowers | KSAS | Completed | Load_247940 | Duhaney - 310 | 2026-08-24 13:33 | 2026-08-24 13:34 | 2026-08-24 13:41 | 2026-08-24 16:05 | 2026-08-24 16:04 | 2026-08-24 16:05 | 2026-08-24 16:05 | 2026-08-24 16:05 |  |  | Fair | No | Call related to call at #39 Queensborough Avenue.
Non-Outage | J.E.26.08.32619 | C001898567 | Michael Paterson | St.Elizabeth | Completed | Load_265987 | Maggotty - 110 | 2026-08-24 13:34 | 2026-08-24 13:35 | 2026-08-25 08:26 | 2026-08-25 08:33 | 2026-08-25 10:37 | 2026-08-25 11:38 | 2026-08-25 11:39 | 2026-08-25 11:39 |  |  | Fair | No | Assessment done at location, voltage readings, 116v, 117v, 233v, highleg 221v. Had to isolate open bank to tap down power transformer from tap three to tap one, presently voltage readings 116v, 117v, 233v, highleg 210v.
Outage | J.E.26.08.36319 | C001898566 | Floyd Taylor | Trelawny | Completed | Load_302922 | Greenwood - 110 | 2026-08-24 13:34 | 2026-08-24 15:38 | 2026-08-24 15:55 | 2026-08-24 15:55 | 2026-08-24 16:31 | 2026-08-24 16:43 | 2026-08-24 16:43 | 2026-08-24 16:43 |  |  | Fair | No | Unable to locate or contact customer several attempts were made
Outage | J.E.26.08.36168 | C001898570 | Shamour Haughton |  | Completed | Load_557027 |  | 2026-08-24 13:36 | 2026-08-24 13:37 | 2026-08-24 14:38 | 2026-08-24 14:38 | 2026-08-24 15:56 | 2026-08-24 15:56 | 2026-08-24 15:57 | 2026-08-24 15:57 |  |  | Fair | No | Customer states that power was restored
Non-Outage | J.E.26.08.36302 | C001898573 | Rayon Foster | Hanover | Completed | Load_238259 | Orange Bay - 310 | 2026-08-24 13:37 | 2026-08-24 13:38 | 2026-08-25 14:53 | 2026-08-25 14:54 | 2026-08-25 14:54 | 2026-08-25 14:54 | 2026-08-25 14:55 | 2026-08-25 14:55 |  |  | Rains | No | Customer reported low voltage that affects the entire community Voltage check at transformer pole when arrived on location 100/100AB200volts troubleshoot line to customer meter voltage check in customer meter socket 98/101AB199volts change three clamps on customer pathead,open one 15kva transformer top up form tap 3 to tap 5 volts after closing 106/108AB214volts.voltage test at customer meter socket 108/106AB214volts customer house is 800ft form meter poleTransformer may need to upgrade form 15kva to a 25kva to accommodate housing development in community
Outage | J.E.26.08.36209 | C001898572 | Collin Robinson | Portland | Completed | Load_556159 | Port Antonio - 310 | 2026-08-24 13:37 | 2026-08-24 15:13 | 2026-08-24 15:35 | 2026-08-24 15:36 | 2026-08-24 16:01 | 2026-08-24 16:17 | 2026-08-24 16:24 | 2026-08-24 16:24 |  |  | Rains | No | Change one corroded grease nipple that connect from service wire to pothead Voltage reading 117v 118v 235 v
Outage | J.E.26.08.36345 | C001898574 | Ricky Hall | St.Catherine | Completed | Load_242025 | Tredegar - 510 | 2026-08-24 13:37 | 2026-08-25 09:46 | 2026-08-25 10:27 | 2026-08-25 10:28 | 2026-08-25 11:52 | 2026-08-25 11:54 | 2026-08-25 11:54 | 2026-08-25 11:54 |  |  | Fair | No | Premises closed
Non-Outage | J.E.26.08.29426 | C001898583 | Raymond Lewis | St.Ann | Completed | Load_264877 | Roaring River - 410 | 2026-08-24 13:51 | 2026-08-24 13:52 | 2026-08-24 14:04 | 2026-08-24 14:05 | 2026-08-24 14:32 | 2026-08-24 15:29 | 2026-08-24 15:29 | 2026-08-24 15:29 |  |  | Fair | No | Cut and remove tree from link and remade service joint at pothead
Outage | J.E.26.08.36373 | C001898589 | Christopher West | Portmore | Completed | Load_412901 | Naggo Head - 510 | 2026-08-24 13:57 | 2026-08-24 16:44 | 2026-08-24 21:35 | 2026-08-24 21:36 | 2026-08-24 22:29 | 2026-08-24 22:42 | 2026-08-24 22:42 | 2026-08-24 22:42 |  |  | Fair | No | A burnt off switch top jumper was found at the entrance of the fishing village, switch was opened and 1 clamp used for repairs, line was re-energized, area now ok.
Outage | J.E.26.08.36367 | C001898592 | Radcliffe Coleman | St.Catherine | Completed | Load_1001269 | Twickenham - 410 | 2026-08-24 13:59 | 2026-08-25 15:33 | 2026-08-25 16:14 | 2026-08-25 16:36 | 2026-08-25 17:56 | 2026-08-25 18:00 | 2026-08-25 18:00 | 2026-08-25 18:00 |  |  | Fair | No | Premises found okay at the time of visit.
Non-Outage | J.E.26.08.36234 | C001898598 | Hopeton Henry | St.Thomas | Completed | Load_266044 | Good Year - 210 | 2026-08-24 14:06 | 2026-08-24 14:18 | 2026-08-24 14:29 | 2026-08-25 14:13 | 2026-08-25 14:13 | 2026-08-25 14:14 | 2026-08-25 14:17 | 2026-08-25 14:17 |  |  | Fair | No | Use 4 connectors at pot head 109-110-220 volts
Non-Outage | J.E.26.08.36390 | C001898610 | Hopeton Henry | St.Thomas | Completed | Load_249385 | Lysson - 410 | 2026-08-24 14:17 | 2026-08-24 14:18 | 2026-08-24 14:29 | 2026-08-25 09:37 | 2026-08-25 12:18 | 2026-08-25 14:09 | 2026-08-25 14:12 | 2026-08-25 14:12 |  |  | Fair | No | Use 3 connector at pot head 120-116-236 volts at meter
Non-Outage | J.E.26.08.35417 | C001898632 | Andrae Dawkins | St.James | Completed | Load_263456 | Rose Hall - 210 | 2026-08-24 14:29 | 2026-08-24 14:30 | 2026-08-24 14:38 | 2026-08-24 15:13 | 2026-08-24 15:13 | 2026-08-24 15:29 | 2026-08-24 15:51 | 2026-08-24 15:51 |  |  | Fair | No | Found customer single phasing due to slack connection cleaned and remade joints voltage left 117/117/235
Non-Outage | J.E.26.08.29448 | C001898633 | Wan Carlos Scarlett | Portmore | Completed | Load_265725 | Naggo Head - 510 | 2026-08-24 14:30 | 2026-08-24 14:31 | 2026-08-24 14:51 | 2026-08-24 14:51 | 2026-08-24 15:20 | 2026-08-24 15:34 | 2026-08-24 15:37 | 2026-08-24 15:37 |  |  | Fair | No | Found customer 4 wire service at pole with one of the phase corroded use 2 one bolt clamps at pole readings from pole and pothead 115-117-239-205-237-239 power supply has been restored
Non-Outage | J.E.26.07.25233 | C001898636 | Milton Charlton | KSAS | Completed | Load_256079 | Up Park Camp - 410 | 2026-08-24 14:34 | 2026-08-24 14:35 | 2026-08-24 15:39 | 2026-08-24 15:40 | 2026-08-24 15:40 | 2026-08-24 16:50 | 2026-08-24 16:50 | 2026-08-24 16:50 | TreeContact |  | Fair | No | Secondary bushing is required. Tree limb touching twisted secondary.
Non-Outage | J.E.26.08.36255 | C001898637 | Milton Charlton | KSAN | Completed | Load_261591 | Hope - 510 | 2026-08-24 14:36 | 2026-08-24 14:38 | 2026-08-24 15:34 | 2026-08-24 15:35 | 2026-08-24 15:35 | 2026-08-24 15:15 | 2026-08-24 15:37 | 2026-08-24 15:37 | Fire |  | Fair | No | Call related to other call at Constitution Hill District.
Non-Outage | J.E.26.08.36331 | C001898639 | Rochaine Hussey | KSAN | Completed | Load_239127 | Washington Blvd - 510 | 2026-08-24 14:36 | 2026-08-24 14:38 | 2026-08-24 14:50 | 2026-08-24 14:51 | 2026-08-24 16:01 | 2026-08-24 16:06 | 2026-08-24 16:07 | 2026-08-24 16:07 |  |  | Fair | No | Found premises ok
Non-Outage | J.E.26.08.36402 | C001898642 | Dwain Samuels | Westmoreland | Completed | Load_249880 | Paradise - 210 | 2026-08-24 14:36 | 2026-08-24 14:37 | 2026-08-24 17:48 | 2026-08-25 13:23 | 2026-08-25 13:22 | 2026-08-25 13:22 | 2026-08-25 13:27 | 2026-08-25 13:27 | LeaningPole |  | Fair | No | Pole found broken and is leaning over the school grounds needs urgent attention asap
Outage | J.E.26.08.36237 | C001898641 | Raymond Lewis | St.Ann | Completed | Load_242953 | Roaring River - 410 | 2026-08-24 14:36 | 2026-08-24 14:38 | 2026-08-24 22:13 | 2026-08-24 22:14 | 2026-08-24 22:13 | 2026-08-24 22:15 | 2026-08-24 22:15 | 2026-08-24 22:15 |  |  | Fair | No | Premises not found
Outage | J.E.26.08.36361 | C001898640 | Raymond Lewis | St.Ann | Completed | Load_252642 | Ocho Rios - 510 | 2026-08-24 14:36 | 2026-08-24 14:38 | 2026-08-24 17:08 | 2026-08-24 17:09 | 2026-08-24 17:40 | 2026-08-24 17:41 | 2026-08-24 17:42 | 2026-08-24 17:42 |  |  | Fair | No | Supply restored
Outage | J.E.26.08.35951 | C001898644 | Raymond Lewis | St.Ann | Completed | Load_256279 | Roaring River - 410 | 2026-08-24 14:37 | 2026-08-24 14:38 | 2026-08-24 16:37 | 2026-08-24 16:37 | 2026-08-24 16:46 | 2026-08-24 17:07 | 2026-08-24 17:08 | 2026-08-24 17:08 |  |  | Fair | No | Customer meter pole need to be straighten
Outage | J.E.26.08.36420 | C001898648 | Milton Charlton | KSAN | Completed | Load_260225 | West Kings House - 410 | 2026-08-24 14:40 | 2026-08-24 17:44 | 2026-08-25 09:42 | 2026-08-25 09:51 | 2026-08-25 09:51 | 2026-08-24 12:05 | 2026-08-25 09:53 | 2026-08-25 09:53 | BrokenWire |  | Fair | No | Call related to call at 25 Hope Road.
Non-Outage | J.E.26.08.36443 | C001898666 | Milton Charlton |  | Completed |  |  | 2026-08-24 14:52 | 2026-08-24 16:00 | 2026-08-25 09:53 | 2026-08-25 09:54 | 2026-08-25 09:53 | 2026-08-24 12:05 | 2026-08-25 09:56 | 2026-08-25 09:56 | BrokenPole |  | Fair | No | Call related to call at 25 Hope Road.
Outage | J.E.26.08.36435 | C001898671 | Elvis Trowers | KSAS | Completed | Load_267203 | Duhaney - 310 | 2026-08-24 14:57 | 2026-08-24 14:58 | 2026-08-24 15:09 | 2026-08-24 15:10 | 2026-08-24 15:09 | 2026-08-24 15:10 | 2026-08-24 15:17 | 2026-08-24 15:17 |  |  | Fair | No | Found one 3 amps transformer switch blown at pole #0113426. Refused using one 3 amps fuse and reclosed transformer switch.
Outage | J.E.26.08.36456 | C001898672 | Edward Royal | KSAN | Completed | Load_264452 | Constant Spring - 310 | 2026-08-24 14:57 | 2026-08-24 14:58 | 2026-08-24 15:41 | 2026-08-24 15:42 | 2026-08-24 15:53 | 2026-08-24 16:53 | 2026-08-24 16:55 | 2026-08-24 16:55 |  |  | Fair | No | Customer was doing some work in there premises the dig up underground cable and damaged it we isolated transformer to disconnected and make area safe transformer was re engerize
Outage | J.E.26.08.36140 | C001898695 | Javid Vernon | Westmoreland | Completed | Load_238512 | Paradise - 310 | 2026-08-24 15:15 | 2026-08-24 15:18 | 2026-08-24 15:24 | 2026-08-24 15:30 | 2026-08-24 15:49 | 2026-08-24 16:02 | 2026-08-24 16:03 | 2026-08-24 16:03 |  |  | Fair | No | Customer was disconnected for none payment and was reconnected after payment voltage found 111/110/221
Outage | J.E.26.08.36381 | C001898693 | Evan Spaulding | St.Mary | Completed | Load_268858 | Highgate -110 | 2026-08-24 15:15 | 2026-08-24 15:16 | 2026-08-24 18:31 | 2026-08-24 18:32 | 2026-08-24 18:32 | 2026-08-24 18:32 | 2026-08-24 18:33 | 2026-08-24 18:33 |  |  | Fair | No | Remove bamboo from primary conductor and replace 1-15 amps junction fuse at pole number 0199515.
Outage | J.E.26.08.36403 | C001898694 | Evan Spaulding | St.Mary | Completed | Load_261725 | Highgate -110 | 2026-08-24 15:15 | 2026-08-24 15:16 | 2026-08-24 15:26 | 2026-08-24 15:26 | 2026-08-24 17:09 | 2026-08-24 18:26 | 2026-08-24 18:28 | 2026-08-24 18:28 |  |  | Fair | No | Remove Bamboo from primary conductor and replace 1-10 amps junction fuse at pole number 512191.
Non-Outage | J.E.26.08.30362 | C001898704 | Derrick Dawkins | St.James | Completed | Load_246501 | Queens Drive - 810 | 2026-08-24 15:18 | 2026-08-24 15:19 | 2026-08-24 16:11 | 2026-08-24 16:48 | 2026-08-24 16:47 | 2026-08-24 16:27 | 2026-08-24 16:48 | 2026-08-24 16:48 |  |  | Fair | No | Found 20amp junction fuse blown replaced 20 amp junction fuse no pole number available
Non-Outage | J.E.26.08.35988 | C001898703 | Derrick Dawkins | St.James | Completed | Load_259501 | Queens Drive - 810 | 2026-08-24 15:18 | 2026-08-24 15:19 | 2026-08-24 16:11 | 2026-08-24 16:12 | 2026-08-24 16:40 | 2026-08-24 16:29 | 2026-08-24 16:47 | 2026-08-24 16:47 |  |  | Fair | No | Found 20amp junction fuse blown replaced 20 amp junction fuse no pole number available
Outage | J.E.26.08.36413 | C001898706 | Romaine Roberts | St.Mary | Completed | Load_262458 | Oracabessa - 110 | 2026-08-24 15:20 | 2026-08-24 15:21 | 2026-08-24 16:23 | 2026-08-24 16:24 | 2026-08-24 18:36 | 2026-08-24 18:37 | 2026-08-24 18:53 | 2026-08-24 18:53 | Fire |  | Fair | No | Found 3 wire service phase and neutral burn off at pole clean and remake joints to restore supply ‘
Outage | J.E.26.08.36466 | C001898707 | Romaine Roberts | St.Ann | Completed | Load_354886 | Upper White River - 110 | 2026-08-24 15:20 | 2026-08-24 15:23 | 2026-08-24 18:53 | 2026-08-24 18:54 | 2026-08-24 19:15 | 2026-08-24 19:51 | 2026-08-24 19:51 | 2026-08-24 19:51 |  |  | Fair | No | Patrol line and found 25 kva transformer fuse blown nothing found replace 3 amp to restore power no pole number
Outage | J.E.26.08.36426 | C001898715 | Barrington Brown | St.James | Completed | Load_238066 | Queens Drive - 710 | 2026-08-24 15:22 | 2026-08-24 15:50 | 2026-08-24 21:57 | 2026-08-24 21:57 | 2026-08-24 21:57 | 2026-08-24 21:57 | 2026-08-24 21:57 | 2026-08-24 21:57 | BrokenWire |  | Fair | No | Crew found 4 span of open neutral and phase secondary wires burnt on location caused by illegal connections. Crew open 100kva transformer on location to conduct repairs. Crew used 4 one bolt clamps 3 splicing sleeve 1 preform and 50 ft on #2 and 2/0 aluminum conductors. All customers now restored. However spot bushing needs in area please refer to maintenance department.
Outage | J.E.26.08.36488 | C001898716 | Shamour Haughton | St.James | Completed | Load_264619 | Bogue - 310 | 2026-08-24 15:22 | 2026-08-24 15:24 | 2026-08-24 15:58 | 2026-08-24 15:59 | 2026-08-24 16:27 | 2026-08-24 16:27 | 2026-08-24 16:30 | 2026-08-24 16:30 |  |  | Fair | No | Found 1,25kva trip, remove vegetation from transformer and reset 25kva
Outage | J.E.26.08.36489 | C001898713 | Romeo Brissett | St.James | Completed | Load_292357 | Queens Drive - 810 | 2026-08-24 15:22 | 2026-08-24 23:01 | 2026-08-25 02:03 | 2026-08-25 02:04 | 2026-08-25 04:13 | 2026-08-25 03:35 | 2026-08-25 04:16 | 2026-08-25 04:16 |  |  | Fair | No | Escalation technician checked and found meter powered at the site
Outage | J.E.26.08.36506 | C001898717 | Lancelot Brown | Hanover | Completed | Load_266154 | Orange Bay - 310 | 2026-08-24 15:24 | 2026-08-24 15:26 | 2026-08-24 16:42 | 2026-08-24 16:48 | 2026-08-24 17:21 | 2026-08-24 17:26 | 2026-08-24 17:26 | 2026-08-24 17:26 | TreeContact |  | Rains | No | Pear tree on customer premises growing into primary line need to cut please pass on to maintenance department in Hanover bushing personnel mr Bruce Barrett
Outage | J.E.26.08.36247 | C001898718 | Clyde Brown | St.Ann | Completed | Load_250095 | Cardiff Hall - 310 | 2026-08-24 15:25 | 2026-08-25 08:50 | 2026-08-25 11:46 | 2026-08-25 11:46 | 2026-08-25 14:01 | 2026-08-25 14:21 | 2026-08-25 14:32 | 2026-08-25 14:32 | BrokenWire | Y | Fair | No | Broken secondary neutral caused by bamboo,line cleared and open 25 kva transformer and repaired with 10ft-#2 conductor,1-preform,2- splicing sleeve and 1- clamp.
Outage | J.E.26.08.36193 | C001898719 | Omar King | St.Ann | Completed | Load_258385 | Cardiff Hall - 310 | 2026-08-24 15:26 | 2026-08-24 15:27 | 2026-08-24 19:50 | 2026-08-24 19:50 | 2026-08-24 20:15 | 2026-08-24 20:20 | 2026-08-24 20:20 | 2026-08-24 20:20 |  |  | Fair | No | Found three (3) wire neutral open as been repaired customer is now with supply
Non-Outage | J.E.26.08.36296 | C001898734 | Richard Samuda |  | Completed |  |  | 2026-08-24 15:28 | 2026-08-24 15:44 | 2026-08-24 15:49 | 2026-08-24 15:50 | 2026-08-24 15:50 | 2026-08-24 03:55 | 2026-08-24 15:56 | 2026-08-24 15:56 |  |  | Fair | No | Customer back to normal customer was cut off due to bad debt c thanks to the relevant department
Outage | J.E.26.08.36184 | C001898735 | Ryan Richards | Manchester | Completed | Load_260683 | Kendal - 310 | 2026-08-24 15:28 | 2026-08-24 15:40 | 2026-08-24 17:22 | 2026-08-24 17:23 | 2026-08-24 19:48 | 2026-08-24 19:49 | 2026-08-24 19:50 | 2026-08-24 19:50 |  |  | Fair | No | Rami box found with supply only 3 customers that’s coming form the box wasn’t getting any power call center was contacted and the customer was reconnected all customers are now with supply
Outage | J.E.26.08.36380 | C001898733 | Richard Samuda | Manchester | Completed | Load_241376 | Spur Tree - 310 | 2026-08-24 15:28 | 2026-08-24 15:29 | 2026-08-24 16:42 | 2026-08-24 16:51 | 2026-08-24 17:17 | 2026-08-24 05:18 | 2026-08-24 17:18 | 2026-08-24 17:18 | LeaningPole |  | Fair | No | Customer stated they didn’t make a calll
Outage | J.E.26.08.36481 | C001898736 | Richard Samuda | Manchester | Completed | Load_261691 | Spur Tree - 310 | 2026-08-24 15:28 | 2026-08-25 07:08 | 2026-08-25 07:16 | 2026-08-25 07:32 | 2026-08-25 07:44 | 2026-08-25 07:55 | 2026-08-25 07:56 | 2026-08-25 07:56 |  |  | Fair | No | Found ok voltage 116, 118 234
Outage | J.E.26.08.36509 | C001898737 | Richard Samuda | Manchester | Completed | Load_241324 | Spur Tree - 310 | 2026-08-24 15:28 | 2026-08-24 15:29 | 2026-08-24 15:57 | 2026-08-24 15:58 | 2026-08-24 16:36 | 2026-08-24 04:41 | 2026-08-24 16:42 | 2026-08-24 16:42 |  |  | Fair | No | Found ok customer said power was restored
Outage | J.E.26.08.36375 | C001898747 | Barrington Brown | St.James | Completed | Load_240704 | Rose Hall - 110 | 2026-08-24 15:34 | 2026-08-24 15:50 | 2026-08-24 16:20 | 2026-08-24 21:58 | 2026-08-24 21:58 | 2026-08-24 22:14 | 2026-08-24 22:14 | 2026-08-24 22:14 |  |  | Fair | No | Customer premises is locked and unable to conduct checks at pot head due to thorn bushes over ground and customer meter pole. Crew also unable to contact customer via phone
Outage | J.E.26.08.36228 | C001898749 | Dwayne Samuels | Trelawny | Completed | Load_257082 | Duncans - 110 | 2026-08-24 15:35 | 2026-08-25 08:01 | 2026-08-25 11:53 | 2026-08-25 11:58 | 2026-08-25 12:34 | 2026-08-25 12:58 | 2026-08-25 12:58 | 2026-08-25 12:58 |  |  | Fair | No | Customer is connected via call to call center voltage left at customer pothead is l17v 117v 234v.
Outage | J.E.26.08.36453 | C001898750 | Elvis Trowers | KSAS | Completed | Load_239161 | Duhaney - 310 | 2026-08-24 15:35 | 2026-08-24 15:37 | 2026-08-24 16:11 | 2026-08-24 16:11 | 2026-08-24 16:47 | 2026-08-24 16:50 | 2026-08-24 16:53 | 2026-08-24 16:53 |  |  | Fair | No | Found one 50 amps junction fuse blown at pole#227774. Refused using one 50 amps fuse and reclosed junction switch.
Outage | J.E.26.08.36454 | C001898761 | Elvis Trowers | KSAS | Completed | Load_254879 | Duhaney - 310 | 2026-08-24 15:37 | 2026-08-24 15:37 | 2026-08-24 16:56 | 2026-08-24 16:57 | 2026-08-24 17:24 | 2026-08-24 17:35 | 2026-08-24 17:42 | 2026-08-24 17:42 |  |  | Fair | No | Found one 25 amps junction fuse blown at pole # 0113415. Refused using one 25 amps fuse and reclosed junction switch.
Outage | J.E.26.08.36003 | C001898763 | Edward Royal | KSAN | Completed | Load_260614 | Constant Spring - 410 | 2026-08-24 15:39 | 2026-08-24 15:41 | 2026-08-24 17:00 | 2026-08-24 17:01 | 2026-08-24 17:58 | 2026-08-24 18:21 | 2026-08-24 18:21 | 2026-08-24 18:21 |  |  | Fair | No | Spliced and reconnected secondary phase using 20ft number 2 tripe x cable 2 single bolt clamp
Outage | J.E.26.08.36516 | C001898762 | Edward Royal | KSAN | Completed | Load_252158 | Constant Spring - 410 | 2026-08-24 15:39 | 2026-08-24 15:41 | 2026-08-24 18:57 | 2026-08-24 18:57 | 2026-08-24 18:57 | 2026-08-24 19:00 | 2026-08-24 19:06 | 2026-08-24 19:06 |  |  | Fair | No | Contact by phone customer said no one is at the premises
Outage | J.E.26.08.36518 | C001898774 | Radcliffe Coleman | St.Catherine | Completed | Load_258321 | Tredegar - 210 | 2026-08-24 15:46 | 2026-08-24 15:48 | 2026-08-24 16:41 | 2026-08-24 16:52 | 2026-08-24 18:33 | 2026-08-24 18:35 | 2026-08-24 18:46 | 2026-08-24 18:46 | Fire |  | Fair | No | Customer service wire was found wrapped at the pole, repairs were done with the aid of one bolt clamp. Premises left okay.
Non-Outage | J.E.26.08.36415 | C001898786 | Ricky Hall |  | Completed |  |  | 2026-08-24 15:47 | 2026-08-25 08:49 | 2026-08-25 09:15 | 2026-08-25 09:16 | 2026-08-25 10:21 | 2026-08-25 10:26 | 2026-08-25 10:26 | 2026-08-25 10:26 | BrokenWire |  | Fair | No | Remove dislocated 3W service to make area safe
Outage | J.E.26.08.36448 | C001898778 | Radcliffe Coleman | St.Catherine | Completed | Load_256615 | Tredegar - 310 | 2026-08-24 15:47 | 2026-08-24 15:48 | 2026-08-24 16:41 | 2026-08-24 19:51 | 2026-08-24 19:50 | 2026-08-24 20:26 | 2026-08-24 20:27 | 2026-08-24 20:27 |  |  | Fair | No | Customer service was disconnected due to a defective meter socket. Repairs were done and service wire reconnected, this was done with the aid of three penunion. The meter was reinstalled and service restored. Premises left with supply. Voltage left at the premises 119, 120, 239 (V).
Outage | J.E.26.08.36479 | C001898787 | Milton Charlton | KSAN | Completed | Load_252462 | Hope - 510 | 2026-08-24 15:48 | 2026-08-24 15:48 | 2026-08-24 19:15 | 2026-08-24 19:16 | 2026-08-24 20:18 | 2026-08-24 20:25 | 2026-08-24 20:22 | 2026-08-24 20:22 |  |  | Fair | No | Customer service wire #6 triplex corroded at pole and pothead repair using four 1- boli clamps.Readings at pole pothead and meter socket 115-112-227 volts.
Outage | J.E.26.08.36521 | C001898788 | Milton Charlton | KSAN | Completed | Load_246913 | West Kings House - 410 | 2026-08-24 15:48 | 2026-08-24 15:49 | 2026-08-24 16:50 | 2026-08-24 16:50 | 2026-08-24 17:32 | 2026-08-24 17:25 | 2026-08-24 17:40 | 2026-08-24 17:40 |  |  | Fair | No | Refused and reclosed 40 amps junction at pole #000220 and 15 amps transformer switch at pole#000218 using one 15 amps and one 40 amps fuses.
Non-Outage | J.E.26.08.35912 | C001898790 | Richard Grant | St.Catherine | Completed | Load_254276 | New Michelton - 310 | 2026-08-24 15:49 | 2026-08-24 15:51 | 2026-08-24 16:24 | 2026-08-24 16:24 | 2026-08-24 18:20 | 2026-08-24 18:59 | 2026-08-24 18:59 | 2026-08-24 18:59 |  |  | Rains | No | Corrosion found at pothead and wrapped on. 3 penunions, 1 onebolt clamp and 2ft #6 neutral used to correct fault. Supply restored, 113 113 226 voltages left at premises. Premises left okay
Outage | J.E.26.08.36424 | C001898789 | Richard Grant | St.Catherine | Completed | Load_246207 | New Michelton - 310 | 2026-08-24 15:49 | 2026-08-24 15:51 | 2026-08-24 18:59 | 2026-08-24 19:00 | 2026-08-24 20:37 | 2026-08-24 21:13 | 2026-08-24 21:13 | 2026-08-24 21:13 |  |  | Rains | No | Corrosion found at pole & pothead. Meter also found disconnected. 3 onebolt clamps and 3 penunions used to correct faults at pole and pothead. Call made to office to have meter reconnected. Supply restored and premises left okay
Non-Outage | J.E.26.08.31967 | C001898806 | Ricky Hall | St.Catherine | Completed | Load_259990 | Rhodens Pen - 210 | 2026-08-24 15:51 | 2026-08-24 15:56 | 2026-08-24 16:32 | 2026-08-24 16:48 | 2026-08-24 17:49 | 2026-08-24 18:04 | 2026-08-24 18:05 | 2026-08-24 18:05 | LeaningPole |  | Fair | No | Retired abandoned pole make area safe
Non-Outage | J.E.26.08.34773 | C001898803 | Ricky Hall | St.Catherine | Completed | Load_256983 | Rhodens Pen - 310 | 2026-08-24 15:51 | 2026-08-24 15:56 | 2026-08-24 18:05 | 2026-08-24 18:06 | 2026-08-24 18:27 | 2026-08-24 18:29 | 2026-08-24 18:29 | 2026-08-24 18:29 |  |  | Fair | No | Premises closed
Non-Outage | J.E.26.08.35162 | C001898802 | Ricky Hall | St.Catherine | Completed | Load_1000368 | Rhodens Pen - 410 | 2026-08-24 15:51 | 2026-08-24 15:56 | 2026-08-24 19:18 | 2026-08-24 19:19 | 2026-08-24 19:37 | 2026-08-24 20:23 | 2026-08-24 20:23 | 2026-08-24 20:23 |  |  | Fair | No | Customer not located
Non-Outage | J.E.26.08.35262 | C001898800 | Ricky Hall | St.Catherine | Completed | Load_252117 | Rhodens Pen - 410 | 2026-08-24 15:51 | 2026-08-24 15:56 | 2026-08-24 18:28 | 2026-08-24 18:29 | 2026-08-24 18:54 | 2026-08-24 19:17 | 2026-08-24 19:17 | 2026-08-24 19:17 |  |  | Fair | No | Clean and reconnect 3W service at pole use 2 clamps 112/114/228
Non-Outage | J.E.26.08.36083 | C001898798 | Christopher West | St.Catherine | Completed | Load_246867 | Rhodens Pen - 410 | 2026-08-24 15:51 | 2026-08-24 15:53 | 2026-08-24 19:03 | 2026-08-24 19:04 | 2026-08-24 20:03 | 2026-08-24 20:04 | 2026-08-24 20:04 | 2026-08-24 20:04 |  |  | Fair | No | Not located, calls made to phone number provided went to voicemail.
Non-Outage | J.E.26.08.36167 | C001898799 | Christopher West | St.Catherine | Completed | Load_1000390 | Rhodens Pen - 410 | 2026-08-24 15:51 | 2026-08-24 15:53 | 2026-08-24 16:46 | 2026-08-24 16:47 | 2026-08-24 18:36 | 2026-08-24 19:03 | 2026-08-24 19:03 | 2026-08-24 19:03 |  |  | Fair | No | Customer is making reference to what she says is the frequent cycling and outages on the feeder, the most recent being Saturday which lasted for about four minutes.
Non-Outage | J.E.26.08.36539 | C001898801 | Barrington Brown |  | Completed |  |  | 2026-08-24 15:51 | 2026-08-24 15:52 | 2026-08-24 18:53 | 2026-08-24 18:53 | 2026-08-24 19:32 | 2026-08-24 21:57 | 2026-08-24 21:57 | 2026-08-24 21:57 | Fire |  | Fair | No | Crew found 4 span of open neutral and phase secondary wires burnt on location caused by illegal connections. Crew open 100kva transformer on location to conduct repairs. Crew used 4 one bolt clamps 3 splicing sleeve 1 preform and 50 ft on #2 and 2/0 aluminum conductors. All customers now restored. However spot bushing needs in area please refer to maintenance department.
Non-Outage | J.E.26.08.36542 | C001898807 | Neville Spencer |  | Completed |  |  | 2026-08-24 15:54 | 2026-08-24 16:27 | 2026-08-24 20:59 | 2026-08-24 21:00 | 2026-08-24 21:29 | 2026-08-24 21:29 | 2026-08-24 21:30 | 2026-08-24 21:30 |  |  | Fair | No | Found supply in area.
Outage | J.E.26.08.36476 | C001898809 | Neville Spencer |  | Completed | Load_571990 | Parnassus - 310 | 2026-08-24 15:54 | 2026-08-24 16:27 | 2026-08-24 20:54 | 2026-08-24 20:55 | 2026-08-24 20:57 | 2026-08-24 20:58 | 2026-08-24 20:59 | 2026-08-24 20:59 |  |  | Fair | No | Found supply in area
Outage | J.E.26.08.36504 | C001898808 | Neville Spencer | Clarendon | Completed | Load_569764 | Parnassus - 210 | 2026-08-24 15:54 | 2026-08-24 16:27 | 2026-08-24 19:37 | 2026-08-24 19:37 | 2026-08-24 19:37 | 2026-08-24 19:37 | 2026-08-24 19:50 | 2026-08-24 19:50 | BrokenWire |  | Fair | No | Remade broken off phase joint at secondary on 3, wire service used 2 clamps voltage reading 114 117 231 supply restored.
Outage | J.E.26.08.36604 | C001898840 | Richard Samuda | Manchester | Completed | Load_241983 | Kendal - 210 | 2026-08-24 16:11 | 2026-08-24 20:02 | 2026-08-24 20:11 | 2026-08-24 20:11 | 2026-08-24 20:50 | 2026-08-24 20:58 | 2026-08-24 20:58 | 2026-08-24 20:58 | BrokenWire |  | Fair | No | In Area Can’t see to locate customer premises can’t find broken wire call to phone no answer daylight attention
Outage | J.E.26.08.16576 | C001898851 | Shamour Haughton | St.James | Completed | Load_301723 | Bogue - 310 | 2026-08-24 16:12 | 2026-08-24 16:13 | 2026-08-24 16:37 | 2026-08-24 17:22 | 2026-08-24 17:22 | 2026-08-24 17:22 | 2026-08-24 17:27 | 2026-08-24 17:27 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Area needs bushing, customer was advised to bush the area, then remake a report
Outage | J.E.26.08.36635 | C001898852 | Evan Spaulding | St.Mary | Completed | Load_341063 | Highgate -110 | 2026-08-24 16:14 | 2026-08-24 16:15 | 2026-08-24 18:30 | 2026-08-24 18:30 | 2026-08-24 18:30 | 2026-08-24 18:30 | 2026-08-24 18:31 | 2026-08-24 18:31 |  |  | Fair | No | Remove bamboo from primary line and replace 1-10 amps junction fuse at pole number 512191
Outage | J.E.26.08.36576 | C001898856 | Floyd Taylor | Trelawny | Completed | Load_249410 | Greenwood - 210 | 2026-08-24 16:18 | 2026-08-24 16:20 | 2026-08-24 17:20 | 2026-08-24 17:21 | 2026-08-24 18:44 | 2026-08-24 19:03 | 2026-08-24 19:05 | 2026-08-24 19:05 |  |  | Fair | No | Customer complained about illegal connection, voltage readings left 113,115,228
Outage | J.E.26.08.36719 | C001898870 | Floyd Taylor | Trelawny | Completed | Load_246009 | Greenwood - 110 | 2026-08-24 16:32 | 2026-08-24 16:36 | 2026-08-24 16:52 | 2026-08-24 16:52 | 2026-08-24 17:18 | 2026-08-24 17:19 | 2026-08-24 17:20 | 2026-08-24 17:20 |  |  | Fair | No | Found ok customer say reports was made this morning and that power was restored
Outage | J.E.26.08.36746 | C001898875 | Richard Samuda | Manchester | Completed | Load_264039 | Kendal - 210 | 2026-08-24 16:44 | 2026-08-24 16:45 | 2026-08-24 17:18 | 2026-08-24 17:19 | 2026-08-24 18:49 | 2026-08-24 18:50 | 2026-08-24 18:50 | 2026-08-24 18:50 |  |  | Fair | No | Found ok situation was resolved
Outage | J.E.26.08.36829 | C001898882 | Barrington Brown | St.James | Completed | Load_251418 | Queens Drive - 710 | 2026-08-24 16:56 | 2026-08-24 16:59 | 2026-08-24 22:15 | 2026-08-24 22:16 | 2026-08-24 22:41 | 2026-08-24 22:58 | 2026-08-24 22:58 | 2026-08-24 22:58 |  |  | Fair | No | Checked and found ok reading found 112 115 228
Non-Outage | J.E.26.08.36358 | C001898887 | Error Coore | Manchester | Completed | Load_268967 | Porus - 310 | 2026-08-24 16:58 | 2026-08-25 08:10 | 2026-08-25 11:41 | 2026-08-25 14:04 | 2026-08-25 15:14 | 2026-08-25 16:00 | 2026-08-25 16:03 | 2026-08-25 16:03 |  |  | Rains | No | Premises not found. Not getting Customer on phone.
Outage | J.E.26.08.36828 | C001898888 | Lancelot Brown | Hanover | Completed | Load_260650 | Orange Bay - 210 | 2026-08-24 16:59 | 2026-08-24 17:00 | 2026-08-24 17:27 | 2026-08-24 17:28 | 2026-08-24 18:31 | 2026-08-24 18:38 | 2026-08-24 18:38 | 2026-08-24 18:38 |  |  | Fair | No | Check and found ok customer said it was disconnected and she paid the bill and she got reconnected supply restore
Outage | J.E.26.08.36893 | C001898897 | Edward Royal | KSAN | Completed | Load_262628 | Constant Spring - 410 | 2026-08-24 17:03 | 2026-08-24 18:13 | 2026-08-24 19:17 | 2026-08-24 19:17 | 2026-08-24 19:17 | 2026-08-24 20:43 | 2026-08-24 20:44 | 2026-08-24 20:44 |  |  | Fair | No | Spliced and reconnected service phase using 2 single bolt clamp
Outage | J.E.26.08.36906 | C001898896 | Derrick Dawkins | St.James | Completed | Load_302094 | Bogue - 610 | 2026-08-24 17:03 | 2026-08-24 17:04 | 2026-08-24 19:03 | 2026-08-24 19:03 | 2026-08-24 19:50 | 2026-08-24 21:03 | 2026-08-24 21:03 | 2026-08-24 21:03 |  | Y | Fair | No | Found junction fuse and transformer fuse blown due to vegetation replace 8 amp junction fuse at pole #034289 and 2 amp transformer fuse
Outage | J.E.26.08.36803 | C001898899 | Derrick Grubb | St.Thomas | Completed | Load_250017 | Good Year - 110 | 2026-08-24 17:06 | 2026-08-24 17:07 | 2026-08-24 17:27 | 2026-08-24 17:28 | 2026-08-24 18:05 | 2026-08-24 18:06 | 2026-08-24 18:06 | 2026-08-24 18:06 |  |  | Fair | No | Premises found okay.
Outage | J.E.26.08.36517 | C001898920 | Omar King | St.Ann | Completed | Load_269390 | Cardiff Hall - 310 | 2026-08-24 17:36 | 2026-08-24 17:37 | 2026-08-24 20:21 | 2026-08-24 20:22 | 2026-08-24 20:35 | 2026-08-24 20:36 | 2026-08-24 20:36 | 2026-08-24 20:36 | Fire |  | Fair | No | Unable to find customer call several times no answer directions not clear
Outage | J.E.26.08.36706 | C001898917 | Raymond Lewis | St.Ann | Completed | Load_239345 | Ocho Rios - 510 | 2026-08-24 17:36 | 2026-08-24 17:37 | 2026-08-24 19:29 | 2026-08-24 19:29 | 2026-08-24 20:47 | 2026-08-24 21:19 | 2026-08-24 21:19 | 2026-08-24 21:19 |  |  | Fair | No | Premises not found
Outage | J.E.26.08.36720 | C001898919 | Raymond Lewis | St.Ann | Completed | Load_413061 | Roaring River - 410 | 2026-08-24 17:36 | 2026-08-24 17:37 | 2026-08-24 19:07 | 2026-08-24 19:08 | 2026-08-24 19:14 | 2026-08-24 19:15 | 2026-08-24 19:16 | 2026-08-24 19:16 |  |  | Fair | No | Customer say that supply was restored
Outage | J.E.26.08.37071 | C001898918 | Raymond Lewis | St.Ann | Completed | Load_252888 | Upper White River - 210 | 2026-08-24 17:36 | 2026-08-24 17:37 | 2026-08-24 19:20 | 2026-08-24 19:28 | 2026-08-24 19:27 | 2026-08-24 19:28 | 2026-08-24 19:28 | 2026-08-24 19:28 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.37096 | C001898922 | Collin Robinson | Portland | Completed | Load_238055 | Port Antonio - 310 | 2026-08-24 17:37 | 2026-08-24 17:40 | 2026-08-24 18:23 | 2026-08-24 18:24 | 2026-08-24 18:53 | 2026-08-24 20:00 | 2026-08-24 20:35 | 2026-08-24 20:35 |  |  | Fair | No | Debush and replace 60ft of defective #6 twisted wire voltage 115 115 230v
Outage | J.E.26.08.36885 | C001898923 | Fitzroy Turner | KSAN | Completed | Load_262563 | Greenwich - 710 | 2026-08-24 17:46 | 2026-08-24 17:49 | 2026-08-24 18:51 | 2026-08-24 18:52 | 2026-08-24 19:15 | 2026-08-24 19:19 | 2026-08-24 19:19 | 2026-08-24 19:19 |  |  | Fair | No | Customer premises found with electricity supply. Customer disrespectful
Outage | J.E.26.08.36628 | C001898925 | Fitzroy Turner | KSAS | Completed | Load_259473 | Hunts Bay - 710 | 2026-08-24 17:48 | 2026-08-24 17:49 | 2026-08-24 18:01 | 2026-08-24 18:01 | 2026-08-24 18:45 | 2026-08-24 18:48 | 2026-08-24 18:49 | 2026-08-24 18:49 |  |  | Fair | No | Found bank of tree 167 kva transformer one fuse found blown replaced with one 15 amps fuse supply restored to customer
Outage | J.E.26.08.37123 | C001898924 | Fitzroy Turner | KSAS | Completed | Load_300900 | Greenwich - 410 | 2026-08-24 17:48 | 2026-08-24 17:49 | 2026-08-24 19:20 | 2026-08-24 19:21 | 2026-08-24 19:58 | 2026-08-24 20:23 | 2026-08-24 20:23 | 2026-08-24 20:23 | BrokenWire |  | Fair | No | Customer breaker found trip have breaker reset supply restored to customer
Non-Outage | J.E.26.08.37066 | C001898927 | Lancelot Brown | Hanover | Completed | Load_292525 | Orange Bay - 310 | 2026-08-24 17:53 | 2026-08-24 17:54 | 2026-08-24 18:39 | 2026-08-24 18:39 | 2026-08-24 21:09 | 2026-08-24 22:16 | 2026-08-24 22:16 | 2026-08-24 22:16 |  |  | Fair | No | Isolate 10kva no pole number remake corroded dropleed joint used three pg clamps vl at transformer location 113-114-227 on load
Non-Outage | J.E.26.08.36508 | C001898928 | Floyd Taylor | Trelawny | Completed | Load_260629 | Duncans - 110 | 2026-08-24 17:54 | 2026-08-24 17:58 | 2026-08-24 20:25 | 2026-08-24 20:25 | 2026-08-24 22:47 | 2026-08-24 22:49 | 2026-08-24 22:51 | 2026-08-24 22:51 |  |  | Fair | No | Replace 1-2amp fuse for a 10kva transformer, voltage reading left 113,115,191,235,238,239
Outage | J.E.26.08.36382 | C001898930 | Richman Whyte | Westmoreland | Completed | Load_258837 | Paradise - 210 | 2026-08-24 17:57 | 2026-08-24 18:00 | 2026-08-24 18:57 | 2026-08-24 18:57 | 2026-08-24 18:57 | 2026-08-24 18:57 | 2026-08-24 18:58 | 2026-08-24 18:58 |  |  | Fair | No | Unable to locate or contact customer
Outage | J.E.26.08.36593 | C001898931 | Richman Whyte | Westmoreland | Completed | Load_242251 | Paradise - 110 | 2026-08-24 18:00 | 2026-08-24 18:01 | 2026-08-24 18:11 | 2026-08-24 18:14 | 2026-08-24 18:14 | 2026-08-24 18:56 | 2026-08-24 18:57 | 2026-08-24 18:57 |  |  | Fair | No | Premises locked
Outage | J.E.26.08.37092 | C001898933 | Romeo Brissett | St.James | Completed | Load_255229 | Bogue - 610 | 2026-08-24 18:03 | 2026-08-24 22:59 | 2026-08-25 02:03 | 2026-08-25 04:17 | 2026-08-25 04:16 | 2026-08-25 05:00 | 2026-08-25 05:12 | 2026-08-25 05:12 |  |  | Fair | No | Isolated (1)25KVA transformer, removed illegal connections, repaired secondary jumper, retention secondary. V/R found 112-76-130. V/R 111-112-223
Outage | J.E.26.08.37195 | C001898934 | Derrick Grubb | St.Thomas | Completed | Load_243194 | Good Year - 210 | 2026-08-24 18:03 | 2026-08-24 18:05 | 2026-08-24 18:20 | 2026-08-24 18:21 | 2026-08-24 19:21 | 2026-08-24 19:39 | 2026-08-24 19:39 | 2026-08-24 19:39 | BrokenWire |  | Fair | No | Damage service wire needs to be replaced. No broken wires area is safe. Needs daylight attention to carry out repair.
Outage | J.E.26.08.37185 | C001898935 | Ryan Richards | Manchester | Completed | Load_253440 | Porus - 310 | 2026-08-24 18:11 | 2026-08-24 18:13 | 2026-08-24 19:51 | 2026-08-24 19:51 | 2026-08-24 20:45 | 2026-08-24 20:48 | 2026-08-24 20:49 | 2026-08-24 20:49 | BrokenPole |  | Fair | No | Broken 36-6TDE pole found broken at base and lean an a building top maintenance team needed to carry out repairs
Outage | J.E.26.08.37291 | C001898937 | Elvis Trowers | KSAS | Completed | Load_267706 | Duhaney - 310 | 2026-08-24 18:28 | 2026-08-24 18:29 | 2026-08-24 18:50 | 2026-08-24 18:51 | 2026-08-24 19:45 | 2026-08-24 19:45 | 2026-08-24 20:09 | 2026-08-24 20:09 |  |  | Fair | No | Customer service wire #6 triplex corrosion at pothead. Repair using one 1- bolt clamp. Readings at pothead and meter socket 115-116-232 volts.
Outage | J.E.26.08.37325 | C001898938 | Elvis Trowers | KSAN | Completed | Load_254044 | Hope - 410 | 2026-08-24 18:31 | 2026-08-24 20:15 | 2026-08-24 20:51 | 2026-08-24 20:51 | 2026-08-24 20:51 | 2026-08-24 21:10 | 2026-08-24 21:08 | 2026-08-24 21:08 |  |  | Fair | No | 40ft c4 wooden pole #( no pole #) broken about 2ft from ground in motor vehicle accident. Pole has on 3-phase primary main line T.A construction 8ft crossarm, primary neutral,twisted 2/0 secondary D.E and one street light. #2 twisted secondary going into 79 Barbican rd which a line the twisted wire burnt up. Need about 200ft of #2 twisted wire to reconnect customer in the lane. About 15 customers is whit out supply.
Outage | J.E.26.08.37247 | C001898939 | Raymond Lewis | St.Ann | Completed | Load_574269 | Roaring River - 210 | 2026-08-24 18:32 | 2026-08-24 18:33 | 2026-08-24 19:19 | 2026-08-24 19:20 | 2026-08-24 19:19 | 2026-08-24 19:20 | 2026-08-24 19:20 | 2026-08-24 19:20 |  |  | Fair | No | Phone not working
Non-Outage | J.E.26.08.36909 | C001898940 | Milton Charlton | KSAN | Completed | Load_579112 | West Kings House - 410 | 2026-08-24 18:34 | 2026-08-24 18:36 | 2026-08-24 20:42 | 2026-08-24 20:43 | 2026-08-25 09:42 | 2026-08-24 12:05 | 2026-08-25 09:51 | 2026-08-25 09:51 | BrokenPole |  | Fair | No | Broken 30ft wooden pole #( no pole #). Broken in three pieces in motor vehicle accident. Pole has on open wire secondary on 5ft crossarm. See pictures sent Ms. Spaulding and Mr. Tyndall.
Non-Outage | J.E.26.08.36486 | C001898941 | Edward Royal | KSAN | Completed | Load_238924 | Constant Spring - 210 | 2026-08-24 18:35 | 2026-08-24 18:37 | 2026-08-25 08:19 | 2026-08-25 08:20 | 2026-08-25 08:19 | 2026-08-25 08:23 | 2026-08-25 08:23 | 2026-08-25 08:23 | LowHangingWires |  | Fair | No | Third party cable was hanging low
Outage | J.E.26.08.37345 | C001898942 | Collin Robinson | Portland | Completed | Load_349580 | Port Antonio - 410 | 2026-08-24 18:39 | 2026-08-24 18:40 | 2026-08-24 20:35 | 2026-08-24 20:36 | 2026-08-24 21:48 | 2026-08-24 21:50 | 2026-08-24 21:50 | 2026-08-24 21:50 |  |  | Fair | No | Premises found with supply
Non-Outage | J.E.26.08.37278 | C001898943 | Cliton Henry | St.Mary | Completed | Load_354661 | Oracabessa - 110 | 2026-08-24 18:40 | 2026-08-25 15:55 | 2026-08-25 16:58 | 2026-08-25 16:59 | 2026-08-25 18:23 | 2026-08-25 18:24 | 2026-08-25 18:25 | 2026-08-25 18:25 | LeaningPole |  | Fair | No | A leaning 30 ‘ secondary pole found. Kindly refer to St. Mary Operations for maintenance work.
Non-Outage | J.E.26.08.37339 | C001898944 | Kenroy Dale | Manchester | Completed | Load_576003 | Kendal - 310 | 2026-08-24 18:41 | 2026-08-25 15:34 | 2026-08-25 17:30 | 2026-08-25 17:31 | 2026-08-25 18:11 | 2026-08-25 18:11 | 2026-08-25 18:12 | 2026-08-25 18:12 | BrokenPole |  | Fair | No | Area checked and customer confirmed that broken pole was replaced from last night
Outage | J.E.26.08.37409 | C001898963 | Shamour Haughton | St.James | Completed | Load_238476 | Bogue - 610 | 2026-08-24 19:13 | 2026-08-24 19:17 | 2026-08-24 19:26 | 2026-08-24 20:50 | 2026-08-24 20:50 | 2026-08-24 20:50 | 2026-08-24 20:53 | 2026-08-24 20:53 |  |  | Fair | No | Customer was disconnected because of none payment of bill
Non-Outage | J.E.26.08.36377 | C001898967 | Radcliffe Coleman | St.Catherine | Completed | Load_253958 | Tredegar - 210 | 2026-08-24 19:17 | 2026-08-24 19:18 | 2026-08-24 20:34 | 2026-08-24 21:20 | 2026-08-24 21:40 | 2026-08-24 21:41 | 2026-08-24 21:42 | 2026-08-24 21:42 |  |  | Fair | No | Premises closed at the time of visit.
Outage | J.E.26.08.37150 | C001898968 | Radcliffe Coleman | St.Catherine | Completed | Load_261464 | Tredegar - 210 | 2026-08-24 19:17 | 2026-08-24 19:18 | 2026-08-24 20:27 | 2026-08-24 20:27 | 2026-08-24 21:14 | 2026-08-24 21:19 | 2026-08-24 21:20 | 2026-08-24 21:20 |  |  | Fair | No | Customer is having a issue with his account, he was advised to visit the JPS office to get the issue resolved.
Outage | J.E.26.08.37215 | C001898966 | Radcliffe Coleman | St.Catherine | Completed | Load_253958 | Tredegar - 210 | 2026-08-24 19:17 | 2026-08-24 19:18 | 2026-08-24 21:00 | 2026-08-24 21:42 | 2026-08-24 22:59 | 2026-08-24 22:59 | 2026-08-24 23:00 | 2026-08-24 23:00 |  |  | Fair | No | Premises found okay at the time of visit.
Outage | J.E.26.08.36174 | C001898971 | Ricky Hall | St.Catherine | Completed | Load_245944 | Rhodens Pen - 210 | 2026-08-24 19:20 | 2026-08-24 19:21 | 2026-08-24 20:29 | 2026-08-24 22:24 | 2026-08-24 22:24 | 2026-08-24 22:24 | 2026-08-24 22:24 | 2026-08-24 22:24 |  |  | Fair | No | Call associated with outage #36636
Outage | J.E.26.08.36680 | C001898974 | Donald Cunningham | St.Catherine | Completed | Load_290293 | Rhodens Pen - 210 | 2026-08-24 19:20 | 2026-08-25 07:57 | 2026-08-25 10:06 | 2026-08-25 10:07 | 2026-08-25 10:48 | 2026-08-25 10:56 | 2026-08-25 10:59 | 2026-08-25 10:59 | Fire |  | Fair | No | Supply restored
Outage | J.E.26.08.36838 | C001898977 | Ricky Hall | St.Catherine | Completed | Load_245944 | Rhodens Pen - 210 | 2026-08-24 19:20 | 2026-08-24 19:21 | 2026-08-24 20:29 | 2026-08-24 20:29 | 2026-08-24 21:36 | 2026-08-24 22:23 | 2026-08-24 22:24 | 2026-08-24 22:24 |  |  | Fair | No | Splice and retention broken secondary lines use 2 clamps
Outage | J.E.26.08.37196 | C001898975 | Richard Samuda | Manchester | Completed | Load_247510 | Kendal - 210 | 2026-08-24 19:20 | 2026-08-24 19:25 | 2026-08-24 19:44 | 2026-08-24 19:44 | 2026-08-24 19:44 | 2026-08-24 19:45 | 2026-08-24 19:45 | 2026-08-24 19:45 |  |  | Fair | No | Customer stated they didn’t make a call
Outage | J.E.26.08.37490 | C001898976 | Richard Samuda | Manchester | Completed | Load_239341 | Kendal - 210 | 2026-08-24 19:20 | 2026-08-24 19:25 | 2026-08-24 19:46 | 2026-08-24 19:46 | 2026-08-24 19:46 | 2026-08-24 19:47 | 2026-08-24 19:47 | 2026-08-24 19:47 |  |  | Fair | No | Customer said they didn’t make a report
Outage | J.E.26.08.37079 | C001898982 | Jermaine Williams | Clarendon | Completed | Load_251545 | Parnassus - 310 | 2026-08-24 19:30 | 2026-08-25 08:14 | 2026-08-25 09:07 | 2026-08-25 09:08 | 2026-08-25 09:31 | 2026-08-25 09:31 | 2026-08-25 09:31 | 2026-08-25 09:31 |  |  | Fair | No | Premises not located.
Outage | J.E.26.08.37133 | C001898981 | Neville Spencer | Clarendon | Completed | Load_249099 | May Pen - 210 | 2026-08-24 19:30 | 2026-08-24 19:31 | 2026-08-24 19:50 | 2026-08-24 19:51 | 2026-08-24 20:50 | 2026-08-24 20:50 | 2026-08-24 20:51 | 2026-08-24 20:51 |  |  | Fair | No | Found supply in area .
Outage | J.E.26.08.37506 | C001898980 | Neville Spencer | Clarendon | Completed | Load_266580 | May Pen - 210 | 2026-08-24 19:30 | 2026-08-24 19:31 | 2026-08-24 21:30 | 2026-08-24 21:31 | 2026-08-25 15:28 | 2026-08-25 15:29 | 2026-08-25 15:29 | 2026-08-25 15:29 |  |  | Fair | No | Found supply in area.
Outage | J.E.26.08.37838 | C001898989 | Lancelot Brown | Hanover | Completed | Load_238848 | Orange Bay - 310 | 2026-08-24 19:49 | 2026-08-24 19:52 | 2026-08-24 22:16 | 2026-08-24 22:17 | 2026-08-24 22:16 | 2026-08-24 22:17 | 2026-08-24 22:18 | 2026-08-24 22:18 |  |  | Fair | No | Check and found ok customer said supply ok
Outage | J.E.26.08.36796 | C001898990 | Richman Whyte | Westmoreland | Completed | Load_292237 | Paradise - 110 | 2026-08-24 19:51 | 2026-08-24 19:52 | 2026-08-24 20:26 | 2026-08-24 20:26 | 2026-08-24 20:26 | 2026-08-24 20:26 | 2026-08-24 20:27 | 2026-08-24 20:27 |  |  | Fair | No | Customer stated that power was restored
Outage | J.E.26.08.37436 | C001898991 | Richman Whyte | Westmoreland | Completed | Load_259530 | Paradise - 110 | 2026-08-24 19:51 | 2026-08-24 19:52 | 2026-08-24 20:30 | 2026-08-24 20:30 | 2026-08-24 20:30 | 2026-08-24 20:30 | 2026-08-24 20:31 | 2026-08-24 20:31 |  |  | Fair | No | Customer stated that power was restored
Outage | J.E.26.08.37554 | C001898992 | Richman Whyte | Westmoreland | Completed | Load_257635 | Paradise - 110 | 2026-08-24 19:51 | 2026-08-24 19:52 | 2026-08-24 20:29 | 2026-08-24 20:29 | 2026-08-24 20:29 | 2026-08-24 20:29 | 2026-08-24 20:30 | 2026-08-24 20:30 |  |  | Fair | No | Customer stated that power was restored
Outage | J.E.26.08.37628 | C001898995 | Richman Whyte | Westmoreland | Completed | Load_292703 | Paradise - 210 | 2026-08-24 19:52 | 2026-08-24 19:53 | 2026-08-24 20:32 | 2026-08-24 20:32 | 2026-08-24 20:32 | 2026-08-24 20:32 | 2026-08-24 20:33 | 2026-08-24 20:33 |  |  | Fair | No | Customer stated that power was restored
Outage | J.E.26.08.37711 | C001898994 | Richman Whyte | Westmoreland | Completed | Load_258299 | Paradise - 210 | 2026-08-24 19:52 | 2026-08-24 19:53 | 2026-08-24 20:31 | 2026-08-24 20:32 | 2026-08-24 20:31 | 2026-08-24 20:31 | 2026-08-24 20:32 | 2026-08-24 20:32 |  |  | Fair | No | Customer stated that power was restored
Non-Outage | J.E.26.08.36217 | C001898996 | Fitzroy Turner |  | Completed |  |  | 2026-08-24 19:53 | 2026-08-24 19:53 | 2026-08-24 20:24 | 2026-08-24 20:25 | 2026-08-24 20:45 | 2026-08-24 21:55 | 2026-08-24 21:58 | 2026-08-24 21:58 | BrokenWire |  | Fair | No | Found three wire open secondary lower phase jumper burnt off use too one bolt clamps and 3ft aluminum conductors to carry out repair supply restored to areas
Outage | J.E.26.08.36884 | C001898998 | Richard Samuda | Manchester | Completed | Load_267716 | Kendal - 210 | 2026-08-24 20:02 | 2026-08-24 20:03 | 2026-08-24 21:04 | 2026-08-24 21:04 | 2026-08-24 21:46 | 2026-08-24 21:47 | 2026-08-24 21:47 | 2026-08-24 21:47 |  |  | Fair | No | Found ok customer said power was restored
Outage | J.E.26.08.38090 | C001899003 | Richard Samuda | Manchester | Completed | Load_267454 | Kendal - 210 | 2026-08-24 20:49 | 2026-08-24 20:49 | 2026-08-24 21:47 | 2026-08-24 21:48 | 2026-08-24 22:32 | 2026-08-24 22:37 | 2026-08-24 22:37 | 2026-08-24 22:37 |  |  | Fair | No | Found ok customer stated that he doesn’t live at the premises anymore
Outage | J.E.26.08.38199 | C001899004 | Shamour Haughton | St.James | Completed | Load_301838 | Bogue - 310 | 2026-08-24 20:51 | 2026-08-24 20:53 | 2026-08-24 22:11 | 2026-08-24 22:11 | 2026-08-24 22:11 | 2026-08-24 22:11 | 2026-08-24 22:12 | 2026-08-24 22:12 |  |  | Fair | No | Customer is without power, eg box number is 01249
Outage | J.E.26.08.38050 | C001899005 | Derrick Dawkins | St.James | Completed | Load_248632 | Bogue - 510 | 2026-08-24 20:52 | 2026-08-24 20:59 | 2026-08-24 21:04 | 2026-08-24 21:04 | 2026-08-25 09:19 | 2026-08-25 09:23 | 2026-08-25 09:23 | 2026-08-25 09:23 |  |  | Fair | No | Check and found premises ok
Outage | J.E.26.08.37325 | C001899006 | Elvis Trowers | KSAN | Completed | Load_254044 | Hope - 410 | 2026-08-24 21:08 | 2026-08-24 21:09 | 2026-08-24 21:14 | 2026-08-24 21:14 | 2026-08-24 21:14 | 2026-08-24 21:20 | 2026-08-24 21:37 | 2026-08-24 21:37 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | 40ftc4 wooden pole#( no pole#) damage in motor vehicle accident and damage #2 twisted secondary conductor feeding #79 Barbican Road which is a lane pole is located across from #79 Barbican Road. Pole has on 3- phase primary main line T.A construction whit 8ft crossarm , system , #2/0 twisted secondary D/E, one streetlight and one O/H Guy . #2 twisted secondary feed the lane need to be change wire is burnt in multiple area need about 200ft of #2 twisted wire. About 15. Customers are whit out supply. Refer to maintenance.
Outage | J.E.26.08.38288 | C001899009 | Richman Whyte | Westmoreland | Completed | Load_292222 | Paradise - 210 | 2026-08-24 21:17 | 2026-08-24 21:29 | 2026-08-24 21:51 | 2026-08-24 21:52 | 2026-08-24 21:51 | 2026-08-24 21:52 | 2026-08-24 21:52 | 2026-08-24 21:52 |  |  | Fair | No | Customer stated that power was restored to the area
Outage | J.E.26.08.38414 | C001899012 | Radcliffe Coleman | St.Catherine | Completed | Load_253146 | Tredegar - 310 | 2026-08-24 21:30 | 2026-08-24 21:32 | 2026-08-24 23:00 | 2026-08-24 23:00 | 2026-08-24 23:00 | 2026-08-24 23:08 | 2026-08-24 23:08 | 2026-08-24 23:08 | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Area found with a blown junction fuse (20A) at pole 0084766. This was a truck coming in contact with third party wire. The wire was removed and line section re-energized with the value fuse found. However, the pole is now leaning and need to be straightened. Please refer to the maintenance department for their intervention.
Outage | J.E.26.08.38578 | C001899013 | Ryan Richards | Manchester | Completed | Load_292951 | Spur Tree - 310 | 2026-08-24 21:31 | 2026-08-24 21:31 | 2026-08-24 21:57 | 2026-08-24 22:22 | 2026-08-24 22:35 | 2026-08-25 01:13 | 2026-08-25 01:14 | 2026-08-25 01:14 |  |  | Fair | No | Blown 30 amp junction fuse found line patrol nothing found blown fuse was replaced all customers are now with supply
Outage | J.E.26.08.38635 | C001899014 | Denton Williams | Portland | Completed | Load_241871 | Port Antonio - 410 | 2026-08-24 21:37 | 2026-08-25 08:48 | 2026-08-25 10:37 | 2026-08-25 10:38 | 2026-08-25 11:02 | 2026-08-25 11:12 | 2026-08-25 11:12 | 2026-08-25 11:12 |  |  | Fair | No | After making several calls and drive through the area we could not locate the customer however supply is in the area.
Outage | J.E.26.08.38790 | C001899018 | Collin Robinson | Portland | Completed | Load_248393 | Port Antonio - 310 | 2026-08-24 21:38 | 2026-08-24 21:38 | 2026-08-24 21:56 | 2026-08-24 21:56 | 2026-08-24 22:22 | 2026-08-24 22:29 | 2026-08-24 22:29 | 2026-08-24 22:29 |  |  | Fair | No | Patrol Area and found Area with supply
Outage | J.E.26.08.38882 | C001899038 | Michael Paterson | Westmoreland | Completed | Load_240901 | Paradise - 310 | 2026-08-24 21:54 | 2026-08-25 08:07 | 2026-08-25 08:28 | 2026-08-25 11:42 | 2026-08-25 11:42 | 2026-08-25 11:43 | 2026-08-25 11:43 | 2026-08-25 11:43 | Fire |  | Fair | No | Inadequate information, unable to location premises, customer no responding to phone calls.
Outage | J.E.26.08.39470 | C001899048 | Rusean Allen | KSAN | Completed | Load_261791 | Hope - 510 | 2026-08-24 22:44 | 2026-08-24 22:46 | 2026-08-24 23:22 | 2026-08-24 23:23 | 2026-08-25 00:05 | 2026-08-25 00:05 | 2026-08-25 00:06 | 2026-08-25 00:06 |  |  | Fair | No | Customer say light is back
Outage | J.E.26.08.38056 | C001899050 | Rusean Allen | KSAS | Completed | Load_244881 | Duhaney - 310 | 2026-08-24 22:46 | 2026-08-24 22:47 | 2026-08-24 23:29 | 2026-08-25 00:06 | 2026-08-25 00:06 | 2026-08-25 00:06 | 2026-08-25 00:06 | 2026-08-25 00:06 |  |  | Fair | No
Outage | J.E.26.08.37904 | C001899053 | Rusean Allen | KSAN | Completed | Load_262237 | Washington Blvd - 310 | 2026-08-24 22:47 | 2026-08-24 22:48 | 2026-08-24 23:46 | 2026-08-25 00:07 | 2026-08-25 05:01 | 2026-08-25 05:01 | 2026-08-25 05:01 | 2026-08-25 05:01 |  |  | Fair | No
Outage | J.E.26.08.39229 | C001899054 | Rusean Allen | KSAS | Completed | Load_240364 | Cane River - 410 | 2026-08-24 22:48 | 2026-08-24 22:49 | 2026-08-25 05:02 | 2026-08-25 05:02 | 2026-08-25 05:04 | 2026-08-25 05:04 | 2026-08-25 05:04 | 2026-08-25 05:04 |  |  | Fair | No
Outage | J.E.26.08.39431 | C001899055 | Rusean Allen | KSAN | Completed | Load_247699 | Washington Blvd - 310 | 2026-08-24 22:48 | 2026-08-24 22:49 | 2026-08-25 05:04 | 2026-08-25 05:05 | 2026-08-25 09:32 | 2026-08-25 09:32 | 2026-08-25 09:32 | 2026-08-25 09:32 |  |  | Fair | No
Outage | J.E.26.08.39509 | C001899056 | Daniel Francis | St.Ann | Completed | Load_242953 | Roaring River - 410 | 2026-08-24 22:49 | 2026-08-24 22:50 | 2026-08-25 00:08 | 2026-08-25 00:08 | 2026-08-25 00:37 | 2026-08-25 00:40 | 2026-08-25 00:41 | 2026-08-25 00:41 |  |  | Fair | No | Found otk
Outage | J.E.26.08.38024 | C001899060 | Delano Gayle | St.Catherine | Completed | Load_267024 | Twickenham - 210 | 2026-08-24 22:51 | 2026-08-24 23:36 | 2026-08-24 23:44 | 2026-08-25 01:49 | 2026-08-25 02:13 | 2026-08-25 02:16 | 2026-08-25 02:17 | 2026-08-25 02:17 |  |  | Fair | No | Premises not located no proper contact information or directions in report
Outage | J.E.26.08.38640 | C001899058 | Donald Cunningham | St.Catherine | Completed | Load_245944 | Rhodens Pen - 210 | 2026-08-24 22:51 | 2026-08-25 07:48 | 2026-08-25 07:57 | 2026-08-25 07:57 | 2026-08-25 09:00 | 2026-08-25 09:01 | 2026-08-25 09:02 | 2026-08-25 09:02 |  |  | Fair | No | Supply restored to area
Outage | J.E.26.08.39036 | C001899057 | Delano Gayle | St.Catherine | Completed | Load_253958 | Tredegar - 210 | 2026-08-24 22:51 | 2026-08-25 00:06 | 2026-08-25 03:05 | 2026-08-25 03:06 | 2026-08-25 03:58 | 2026-08-25 04:05 | 2026-08-25 04:06 | 2026-08-25 04:06 |  |  | Fair | No | Premises and area found okay power was restored
Outage | J.E.26.08.39541 | C001899061 | Romeo Brissett | St.James | Completed | Load_253128 | Bogue - 310 | 2026-08-24 22:57 | 2026-08-24 22:58 | 2026-08-24 23:09 | 2026-08-24 23:09 | 2026-08-24 23:52 | 2026-08-25 02:50 | 2026-08-25 02:03 | 2026-08-25 02:03 |  |  | Fair | No | Found low voltage in the area V/R before 87-52-182-Isolated (1)100kva transformer, removed illegal connections, repaired secondary jumper, V/R after 106-103-210. Too much illegal connections in lane please send to losses department.
Outage | J.E.26.08.38593 | C001899064 | Jermaine Williams | St.Catherine | Completed | Load_567911 | Rhodens Pen - 310 | 2026-08-24 23:05 | 2026-08-25 10:12 | 2026-08-25 11:10 | 2026-08-25 11:11 | 2026-08-25 12:57 | 2026-08-25 12:32 | 2026-08-25 12:58 | 2026-08-25 12:58 | BrokenWire |  | SevereWind | No | Splice and retention broken service wire using 20’ #6 triplex.
Outage | J.E.26.08.39709 | C001899065 | Delano Gayle | St.Catherine | Completed | Load_240110 | Twickenham - 210 | 2026-08-24 23:37 | 2026-08-24 23:38 | 2026-08-25 02:18 | 2026-08-25 02:19 | 2026-08-25 03:03 | 2026-08-25 03:05 | 2026-08-25 03:05 | 2026-08-25 03:05 |  |  | Fair | No | Area found okay
Outage | J.E.26.08.39812 | C001899066 | Delano Gayle | St.Catherine | Completed | Load_253278 | Rhodens Pen - 210 | 2026-08-25 00:06 | 2026-08-25 00:07 | 2026-08-25 04:06 | 2026-08-25 04:06 | 2026-08-25 05:26 | 2026-08-25 05:36 | 2026-08-25 05:36 | 2026-08-25 05:36 |  |  | Fair | No | Premises not found no answer from the multiple phone numbers in report, no proper directions to state which new harbour village customers are located in
Non-Outage | J.E.26.08.39844 | C001899067 | Romeo Brissett |  | Completed |  |  | 2026-08-25 00:10 | 2026-08-25 00:11 | 2026-08-25 05:12 | 2026-08-25 05:13 | 2026-08-25 05:56 | 2026-08-25 07:30 | 2026-08-25 08:04 | 2026-08-25 08:04 | BrokenWire |  | Fair | No | Removed illegal connections, spliced and detention 2 span of secondary conductor dislodged, used 100ft of #2,100ft of 2/0, (2)#2 #2 sleeve and 8 clamps.
Outage | J.E.26.08.39746 | C001899068 | Swon Miller | St.James | Completed | Load_264164 | Queens Drive - 310 | 2026-08-25 00:10 | 2026-08-25 07:02 | 2026-08-25 10:21 | 2026-08-25 10:21 | 2026-08-25 10:21 | 2026-08-25 10:21 | 2026-08-25 10:22 | 2026-08-25 10:22 | Fire |  | Fair | No | Found 20 amp and 8 amp junction fuse blown cause by defective 10 kva transformer EG # 02365 replace 20 amp junction fuse at pole number 233385 and replace 8 amp junction fuse at pole number 532247 oil leaking from transformer transformer needs to be replace plz refer to maintenance and field service
Outage | J.E.26.08.39729 | C001899075 | Daniel Francis | St.Ann | Completed | Load_253998 | Cardiff Hall - 210 | 2026-08-25 02:31 | 2026-08-25 02:33 | 2026-08-25 04:05 | 2026-08-25 04:05 | 2026-08-25 04:32 | 2026-08-25 04:33 | 2026-08-25 04:38 | 2026-08-25 04:38 |  |  | Fair | No | Need day time attention location is very remote don’t feel safe at this time
Outage | J.E.26.08.39881 | C001899074 | Daniel Francis | St.Ann | Completed | Load_239038 | Roaring River - 210 | 2026-08-25 02:31 | 2026-08-25 02:31 | 2026-08-25 03:52 | 2026-08-25 03:53 | 2026-08-25 03:53 | 2026-08-25 03:53 | 2026-08-25 03:54 | 2026-08-25 03:54 |  |  | Fair | No | Customers did not makes report
Outage | J.E.26.08.39872 | C001899076 | Derrick Dawkins | St.James | Completed | Load_256177 | Bogue - 610 | 2026-08-25 02:33 | 2026-08-25 08:05 | 2026-08-25 09:13 | 2026-08-25 09:24 | 2026-08-25 11:28 | 2026-08-25 11:52 | 2026-08-25 11:53 | 2026-08-25 11:53 | BrokenWire |  | Fair | No | Found premises with out service wire due to hurricane replace 26ft of number six triplex used 3 red to red linket and 3 pg clamp voltage left 119/119/239
Outage | J.E.26.08.39913 | C001899092 | Swon Miller | St.James | Completed | Load_242411 | Rose Hall - 210 | 2026-08-25 07:03 | 2026-08-25 07:04 | 2026-08-25 08:11 | 2026-08-25 08:11 | 2026-08-25 08:56 | 2026-08-25 10:20 | 2026-08-25 10:20 | 2026-08-25 10:20 |  |  | Fair | No | Found 20 amp and 8 amp junction fuse blown cause by defective 10 kva transformer EG # 02365 replace 20 amp junction fuse at pole number 233385 and replace 8 amp junction fuse at pole number 532247 oil leaking from transformer transformer needs to be replace plz refer to maintenance and field service
Outage | J.E.26.08.37426 | C001899093 | Richard Samuda | Manchester | Completed | Load_250755 | Spur Tree - 310 | 2026-08-25 07:06 | 2026-08-25 07:07 | 2026-08-25 08:05 | 2026-08-25 08:07 | 2026-08-25 08:44 | 2026-08-25 09:27 | 2026-08-25 09:28 | 2026-08-25 09:28 | BrokenWire |  | Fair | No | Pole number:469852 found 8 amps junction blown patrol line found 25 kva transformer blown patrol line found tree growing on secondary line causing line to bang out l carry out spot bushing in area and balance line close transformer fuse then 8 amp junction customer back to normal area needs de bushing
Outage | J.E.26.08.38959 | C001899102 | Richard Samuda | Manchester | Completed | Load_255995 | Spur Tree - 210 | 2026-08-25 07:13 | 2026-08-25 07:15 | 2026-08-25 09:28 | 2026-08-25 09:28 | 2026-08-25 10:10 | 2026-08-25 10:11 | 2026-08-25 10:11 | 2026-08-25 10:11 |  |  | Fair | No | Found ok situation was resolved
Outage | J.E.26.08.40270 | C001899103 | Wayne Dillion | Manchester | Completed | Load_258714 | Spur Tree - 210 | 2026-08-25 07:13 | 2026-08-25 07:15 | 2026-08-25 08:56 | 2026-08-25 08:57 | 2026-08-25 09:14 | 2026-08-25 09:28 | 2026-08-25 09:33 | 2026-08-25 09:33 | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Patrol and found clear. Reset chip type transformer circuit at pole #531035. Supply restored okay.
Outage | J.E.26.08.38110 | C001899110 | Selvin White | St.Elizabeth | Completed | Load_265624 | Maggotty - 110 | 2026-08-25 07:26 | 2026-08-25 07:27 | 2026-08-25 08:32 | 2026-08-25 08:33 | 2026-08-25 08:54 | 2026-08-25 09:12 | 2026-08-25 09:33 | 2026-08-25 09:33 |  |  | Fair | No | Defective 3 wire meter found at location. Please refer to Jessie Morales and Clint Johnson at the field service department so arrangements can be made to replace meter.
Outage | J.E.26.08.36232 | C001899113 | Selvin White | St.Elizabeth | Completed | Load_270212 | Maggotty - 110 | 2026-08-25 07:27 | 2026-08-25 07:27 | 2026-08-25 10:38 | 2026-08-25 10:41 | 2026-08-25 11:27 | 2026-08-25 11:32 | 2026-08-25 11:32 | 2026-08-25 11:32 |  |  | Fair | No | Customer has no supply because there is no meter at the location so please refer to C Johnson and Jessie Morales at the field service department for follow up.
Outage | J.E.26.08.36256 | C001899112 | Selvin White | St.Elizabeth | Completed | Load_264070 | Maggotty - 110 | 2026-08-25 07:27 | 2026-08-25 07:27 | 2026-08-25 11:34 | 2026-08-25 13:35 | 2026-08-25 14:07 | 2026-08-25 14:29 | 2026-08-25 14:29 | 2026-08-25 14:29 |  |  | Fair | No | Empty and defective meter socket found at location. Customer was advised to have repairs done before supply can be restored.
Outage | J.E.26.08.36356 | C001899111 | Selvin White | St.Elizabeth | Completed | Load_265795 | Maggotty - 110 | 2026-08-25 07:27 | 2026-08-25 07:27 | 2026-08-25 07:51 | 2026-08-25 09:34 | 2026-08-25 10:24 | 2026-08-25 10:34 | 2026-08-25 10:38 | 2026-08-25 10:38 |  |  | Fair | Yes | Customer’s supply was found okay at the time of visit however customer says supply was wrongfully disconnected yesterday and was reconnected shortly after.
Outage | J.E.26.08.40511 | C001899130 | Denton Williams | Portland | Completed | Load_266709 | Port Antonio - 410 | 2026-08-25 07:32 | 2026-08-25 07:34 | 2026-08-25 07:42 | 2026-08-25 07:43 | 2026-08-25 08:25 | 2026-08-25 08:59 | 2026-08-25 08:59 | 2026-08-25 08:59 |  | Y | Fair | No | 10kva transformer fuse blown cause by vegetation on transformer pole cut and remove vine then restored supply to the area.
Outage | J.E.26.08.40536 | C001899134 | Omar King | St.Ann | Completed | Load_243588 | Roaring River - 210 | 2026-08-25 07:33 | 2026-08-25 07:34 | 2026-08-25 08:33 | 2026-08-25 08:33 | 2026-08-25 11:26 | 2026-08-25 11:29 | 2026-08-25 11:29 | 2026-08-25 11:29 |  |  | Fair | No | Found 10 KVA transformer fuse blown and fuse barrel defective. Fuse and fuse holder as been replaced customer is now with supply
Non-Outage | J.E.26.08.36496 | C001899136 | Tyrese Williams | St.Ann | Completed | Load_238745 | Cardiff Hall - 210 | 2026-08-25 07:34 | 2026-08-25 07:35 | 2026-08-25 07:47 | 2026-08-25 08:25 | 2026-08-25 08:51 | 2026-08-25 09:09 | 2026-08-25 09:09 | 2026-08-25 09:09 |  |  | Fair | No | Premises not found not getting customer on phone
Non-Outage | J.E.26.08.36625 | C001899135 | Tyrese Williams | St.Ann | Completed | Load_260025 | Cardiff Hall - 210 | 2026-08-25 07:34 | 2026-08-25 07:35 | 2026-08-25 07:47 | 2026-08-25 09:09 | 2026-08-25 10:25 | 2026-08-25 11:53 | 2026-08-25 11:53 | 2026-08-25 11:53 |  |  | Fair | No | Remade joint at pole use 1 pg. lamp
Outage | J.E.26.08.39729 | C001899137 | Tyrese Williams | St.Ann | Completed | Load_253998 | Cardiff Hall - 210 | 2026-08-25 07:35 | 2026-08-25 07:35 | 2026-08-25 07:47 | 2026-08-25 11:56 | 2026-08-25 13:15 | 2026-08-25 13:41 | 2026-08-25 13:41 | 2026-08-25 13:41 |  |  | Fair | No | Premises found ok customer has internal problem
Outage | J.E.26.08.40097 | C001899143 | Kemark Slue | St.Catherine | Completed | Load_257117 | New Michelton - 210 | 2026-08-25 07:38 | 2026-08-25 07:39 | 2026-08-25 07:45 | 2026-08-25 07:45 | 2026-08-25 08:58 | 2026-08-25 09:25 | 2026-08-25 09:36 | 2026-08-25 09:36 |  |  | Fair | No | Upon arrival at the location the crew discovered that a 10 amps junction for single phase line section was blown at pole # 563585, further patrol revealed that a 10 kva 13.8 kv transformer is defective, refuse link for junction and re-energized line section energizing one 25 kva 13.8 kv and leaving approximately 45 customers without supply please refer to A. Murray to have defective transformer change and upgrade to a 25 kva 13.8 kv transformer.
Outage | J.E.26.08.40424 | C001899141 | Kemark Slue | St.Catherine | Completed | Load_255806 | New Michelton - 310 | 2026-08-25 07:38 | 2026-08-25 07:39 | 2026-08-25 07:45 | 2026-08-25 09:37 | 2026-08-25 09:37 | 2026-08-25 09:37 | 2026-08-25 09:37 | 2026-08-25 09:37 |  |  | Fair | No | Upon arrival at the location the crew discovered that a 10 amps junction for single phase line section was blown at pole # 563585, further patrol revealed that a 10 kva 13.8 kv transformer is defective, refuse link for junction and re-energized line section energizing one 25 kva 13.8 kv and leaving approximately 45 customers without supply please refer to A. Murray to have defective transformer change and upgrade to a 25 kva 13.8 kv transformer.
Outage | J.E.26.08.40660 | C001899142 | Kemark Slue | St.Catherine | Completed | Load_259729 | New Michelton - 310 | 2026-08-25 07:38 | 2026-08-25 07:39 | 2026-08-25 09:37 | 2026-08-25 09:38 | 2026-08-25 10:44 | 2026-08-25 10:05 | 2026-08-25 10:46 | 2026-08-25 10:46 | LowHangingWires |  | Fair | No | Unable to locate customer’s premises due to inadequate directions and all calls to number given were futile.
Outage | J.E.26.08.40599 | C001899144 | Donald Cunningham | St.Catherine | Completed | Load_253278 | Rhodens Pen - 210 | 2026-08-25 07:43 | 2026-08-25 07:47 | 2026-08-25 09:04 | 2026-08-25 09:05 | 2026-08-25 09:41 | 2026-08-25 10:05 | 2026-08-25 10:06 | 2026-08-25 10:06 |  |  | Fair | No | Blown transformer fuse by pole #0114739 replace 5 amp fuse for 25 kva
Non-Outage | J.E.26.08.38941 | C001899145 | Ricky Hall |  | Completed |  |  | 2026-08-25 07:44 | 2026-08-25 07:47 | 2026-08-25 08:20 | 2026-08-25 08:41 | 2026-08-25 09:07 | 2026-08-25 09:12 | 2026-08-25 09:15 | 2026-08-25 09:15 | LowHangingWires |  | Fair | No | 40’TA w /r construction pole down guy to be replaced to prevent constant banging of secondary conductor which result in outage plz refer to maintenance (intersection of Fairfield dr and Henry close
Outage | J.E.26.08.40633 | C001899176 | Cliton Henry | St.Ann | Completed | Load_269054 | Upper White River - 110 | 2026-08-25 07:45 | 2026-08-25 07:46 | 2026-08-25 11:36 | 2026-08-25 11:36 | 2026-08-25 11:36 | 2026-08-25 11:36 | 2026-08-25 11:37 | 2026-08-25 11:37 |  |  | Fair | No | Supply restored, related to outage #40740
Outage | J.E.26.08.40635 | C001899177 | Cliton Henry | St.Mary | Completed | Load_252304 | Oracabessa - 210 | 2026-08-25 07:45 | 2026-08-25 07:46 | 2026-08-25 07:53 | 2026-08-25 08:39 | 2026-08-25 08:39 | 2026-08-25 09:08 | 2026-08-25 09:16 | 2026-08-25 09:16 |  |  | Fair | No | A blown 15 amp junction fuse found at pole #005435 due to lightning, supply restored using 1-15 amp fuse.
Outage | J.E.26.08.40674 | C001899178 | Denton Williams | Portland | Completed | Load_247147 | Port Antonio - 410 | 2026-08-25 07:46 | 2026-08-25 07:47 | 2026-08-25 09:01 | 2026-08-25 09:01 | 2026-08-25 10:00 | 2026-08-25 10:36 | 2026-08-25 10:36 | 2026-08-25 10:36 |  |  | Fair | No | 10amp junction fuse blown also 25kva transformer fuse cause by vegetation on line section cut and removed vegetation then restored supply to the area material use 8amp fuse 2amp fuse.
Outage | J.E.26.08.39605 | C001899179 | Stephen Taylor | St.Thomas | Completed | Load_252007 | Good Year - 210 | 2026-08-25 07:47 | 2026-08-25 07:48 | 2026-08-25 09:05 | 2026-08-25 09:05 | 2026-08-25 09:28 | 2026-08-25 09:28 | 2026-08-25 09:31 | 2026-08-25 09:31 | BrokenPole |  | Fair | No | Jps secondary pole lean and need to be straightened urgently no # and pole
Outage | J.E.26.08.40672 | C001899180 | Derrick Dawkins | St.James | Completed | Load_302094 | Bogue - 610 | 2026-08-25 07:47 | 2026-08-25 07:48 | 2026-08-25 14:37 | 2026-08-25 18:04 | 2026-08-25 18:03 | 2026-08-25 13:58 | 2026-08-25 18:18 | 2026-08-25 18:18 |  |  | Fair | No | Found junction 8 amp junction fuse blown due to vegetation removed vegetation and replaced 8 amp junction fuse at fuse at pole number 034289
Outage | J.E.26.08.37230 | C001899184 | Elvis Trowers | KSAS | Completed | Load_263472 | Hunts Bay - 310 | 2026-08-25 07:48 | 2026-08-25 07:50 | 2026-08-25 11:43 | 2026-08-25 11:43 | 2026-08-25 12:30 | 2026-08-25 13:00 | 2026-08-25 13:20 | 2026-08-25 13:20 |  |  | Fair | No | Customer service wire #6 triplex phase corroded at pothead. Repair using two one bolt clamps. Readings at meter socket 115-117-234 volts.
Outage | J.E.26.08.38064 | C001899183 | Elvis Trowers | KSAN | Completed | Load_567704 | Washington Blvd - 310 | 2026-08-25 07:48 | 2026-08-25 07:50 | 2026-08-25 09:03 | 2026-08-25 09:04 | 2026-08-25 09:51 | 2026-08-25 09:35 | 2026-08-25 09:52 | 2026-08-25 09:52 |  |  | Fair | No | Found okay upon arrival. Customer is not home but her meter is active
Outage | J.E.26.08.40445 | C001899182 | Derrick Dawkins | St.James | Completed | Load_255377 | Bogue - 610 | 2026-08-25 07:48 | 2026-08-25 07:49 | 2026-08-25 14:37 | 2026-08-25 14:38 | 2026-08-25 15:32 | 2026-08-25 15:16 | 2026-08-25 16:26 | 2026-08-25 16:26 |  |  | Fair | No | Found 8 amp junction fuse blown due to vegetation removed vegetation and replaced 8 amp junction fuse at pole number 034289
Outage | J.E.26.08.39233 | C001899185 | Elvis Trowers | KSAN | Completed | Load_247699 | Washington Blvd - 310 | 2026-08-25 07:49 | 2026-08-25 07:50 | 2026-08-25 09:53 | 2026-08-25 09:53 | 2026-08-25 11:32 | 2026-08-25 11:30 | 2026-08-25 11:43 | 2026-08-25 11:43 |  |  | Fair | No | Customer getting low voltage as a result of large amount of illegal connections. At customer service main readings 86-98-196 volts at transformer drop lead 109-110-219 volts. After charging the transformer topping at the transformer getting 117-118-235 volts and at customer service main 106-105-214 volts. Illegal connections need to be removed. Refer to R.P.D.
Outage | J.E.26.08.39446 | C001899186 | Collin Robinson | Portland | Completed | Load_246537 | Port Antonio - 310 | 2026-08-25 07:49 | 2026-08-25 15:58 | 2026-08-25 17:45 | 2026-08-25 17:45 | 2026-08-25 17:53 | 2026-08-25 17:58 | 2026-08-25 17:58 | 2026-08-25 17:58 |  |  | Fair | No | Premises found with supply
Outage | J.E.26.08.39689 | C001899187 | Edward Royal | KSAN | Completed | Load_252603 | Hope - 510 | 2026-08-25 07:51 | 2026-08-25 07:58 | 2026-08-25 08:23 | 2026-08-25 09:48 | 2026-08-25 09:54 | 2026-08-25 09:55 | 2026-08-25 09:55 | 2026-08-25 09:55 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.40689 | C001899188 | Edward Royal | KSAN | Completed | Load_256182 | Hope - 510 | 2026-08-25 07:51 | 2026-08-25 07:58 | 2026-08-25 09:44 | 2026-08-25 09:45 | 2026-08-25 09:45 | 2026-08-25 09:46 | 2026-08-25 09:47 | 2026-08-25 09:47 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.36745 | C001899286 | Moses Elliston | St.Catherine | Completed | Load_294020 | Tredegar - 210 | 2026-08-25 07:56 | 2026-08-25 10:34 | 2026-08-25 14:30 | 2026-08-25 14:31 | 2026-08-25 14:31 | 2026-08-25 11:10 | 2026-08-25 14:33 | 2026-08-25 14:33 |  |  | EarthMovement | No | Supply reconnected from s# 14461575442.
Outage | J.E.26.08.36761 | C001899285 | Ricky Hall | St.Catherine | Completed | Load_1001058 | Twickenham - 410 | 2026-08-25 07:56 | 2026-08-25 08:19 | 2026-08-25 12:51 | 2026-08-25 12:52 | 2026-08-25 13:55 | 2026-08-25 13:55 | 2026-08-25 13:59 | 2026-08-25 13:59 |  |  | Fair | No | Customer connected mid span in rami system sagging across rdwy which constantly being torn down by passing vehicles a intermediate 30’ pole will remedy the situation plz refer to maintenance
Outage | J.E.26.08.37374 | C001899284 | Radcliffe Coleman | St.Catherine | Completed | Load_240276 | Tredegar - 210 | 2026-08-25 07:56 | 2026-08-25 15:33 | 2026-08-25 16:37 | 2026-08-25 18:01 | 2026-08-25 18:22 | 2026-08-25 19:14 | 2026-08-25 19:15 | 2026-08-25 19:15 |  |  | Fair | No | Hexing enclosure at the location, please refer to Moses Eliston for his intervention.
Outage | J.E.26.08.37051 | C001899287 | Dwayne Samuels | Trelawny | Completed | Load_257987 | Duncans - 210 | 2026-08-25 07:59 | 2026-08-25 08:00 | 2026-08-25 08:17 | 2026-08-25 08:17 | 2026-08-25 09:33 | 2026-08-25 10:19 | 2026-08-25 10:19 | 2026-08-25 10:19 |  |  | Fair | No | 25 kva trip transformer trip because of broken neutral, splice and retention same voltage left is 115v 116v 231v.
Non-Outage | J.E.26.08.36075 | C001899289 | Locksley Allen | St.Ann | Completed | Load_259886 | Upper White River - 110 | 2026-08-25 08:00 | 2026-08-25 08:03 | 2026-08-25 14:08 | 2026-08-25 14:08 | 2026-08-25 14:08 | 2026-08-25 14:12 | 2026-08-25 14:10 | 2026-08-25 14:10 |  |  | Fair | No | This is in St.Ann,assign to the wrong person
Outage | J.E.26.08.38085 | C001899288 | Dwayne Samuels | Trelawny | Completed | Load_257987 | Duncans - 210 | 2026-08-25 08:00 | 2026-08-25 08:00 | 2026-08-25 10:20 | 2026-08-25 10:21 | 2026-08-25 10:29 | 2026-08-25 10:39 | 2026-08-25 10:39 | 2026-08-25 10:39 |  |  | Fair | No | Call is linked to broken neutral that was repaired…
Non-Outage | J.E.26.08.36267 | C001899294 | Locksley Allen | St.Mary | Completed | Load_349209 | Oracabessa - 210 | 2026-08-25 08:01 | 2026-08-25 08:03 | 2026-08-25 11:09 | 2026-08-25 12:03 | 2026-08-25 12:02 | 2026-08-25 12:08 | 2026-08-25 12:05 | 2026-08-25 12:05 |  |  | Fair | No | Unable to check the voltage. This is a Rami section. Please refer to emergency
Non-Outage | J.E.26.08.36313 | C001899295 | Locksley Allen | St.Ann | Completed | Load_354886 | Upper White River - 110 | 2026-08-25 08:01 | 2026-08-25 08:03 | 2026-08-25 14:01 | 2026-08-25 14:05 | 2026-08-25 14:05 | 2026-08-25 14:07 | 2026-08-25 14:06 | 2026-08-25 14:06 |  |  | Fair | No | Customer said JPS corrected the problem from last night
Non-Outage | J.E.26.08.36468 | C001899293 | Locksley Allen | St.Mary | Completed | Load_260700 | Highgate - 210 | 2026-08-25 08:01 | 2026-08-25 08:03 | 2026-08-25 12:07 | 2026-08-25 12:52 | 2026-08-25 12:52 | 2026-08-25 12:58 | 2026-08-25 12:55 | 2026-08-25 12:55 |  |  | Fair | No | Meter burn up and needs to change urgently. Please refer to field service.Voltage at meter socket phase to phase 218v. Phase to neutral 103&110
Outage | J.E.26.08.40729 | C001899297 | Dean- Smith | Hanover | Completed | Load_259890 | Orange Bay - 310 | 2026-08-25 08:01 | 2026-08-25 08:02 | 2026-08-25 10:10 | 2026-08-25 10:10 | 2026-08-25 11:53 | 2026-08-25 11:53 | 2026-08-25 11:55 | 2026-08-25 11:55 |  |  | SevereWind | No | Cut and remove vegetation , replace 10amp junction fuse at pole # 009241
Outage | J.E.26.08.39626 | C001899298 | Oshane Warren | Westmoreland | Completed | Load_292703 | Paradise - 210 | 2026-08-25 08:02 | 2026-08-25 08:03 | 2026-08-25 09:00 | 2026-08-25 09:00 | 2026-08-25 09:00 | 2026-08-25 09:00 | 2026-08-25 09:01 | 2026-08-25 09:01 |  |  | Fair | No | Check on found ok
Outage | J.E.26.08.39811 | C001899299 | Oshane Warren | Westmoreland | Completed | Load_293032 | Paradise - 110 | 2026-08-25 08:02 | 2026-08-25 08:03 | 2026-08-25 09:30 | 2026-08-25 09:30 | 2026-08-25 09:31 | 2026-08-25 09:31 | 2026-08-25 09:31 | 2026-08-25 09:31 |  |  | Fair | No | Unable to locate or contact customer on the phone need direction
Outage | J.E.26.08.39698 | C001899302 | Wan Carlos Scarlett | St.Catherine | Completed | Load_255400 | Twickenham - 210 | 2026-08-25 08:05 | 2026-08-25 08:06 | 2026-08-25 08:14 | 2026-08-25 08:14 | 2026-08-25 09:05 | 2026-08-25 09:21 | 2026-08-25 09:25 | 2026-08-25 09:25 |  |  | Fair | No | Reach on location been calling customer but no answer premises.check secondary line pole found secondary line jumper clamp burn out from the one bolt clamp use 2 one bolt clamps at pole readings 114-115-231
Outage | J.E.26.08.40240 | C001899301 | Wan Carlos Scarlett | St.Catherine | Completed | Load_265364 | Twickenham - 210 | 2026-08-25 08:05 | 2026-08-25 08:06 | 2026-08-25 09:31 | 2026-08-25 09:32 | 2026-08-25 09:56 | 2026-08-25 11:01 | 2026-08-25 11:05 | 2026-08-25 11:05 | Fire |  | Fair | No | Found a set of bank of 2 transformer with the lightning defective leaking oil pole # 618624 isolate bank of 2 transformers
Non-Outage | J.E.26.08.37087 | C001899305 | Jermaine Williams |  | Completed |  |  | 2026-08-25 08:06 | 2026-08-25 08:07 | 2026-08-25 09:01 | 2026-08-25 09:01 | 2026-08-25 09:05 | 2026-08-25 09:06 | 2026-08-25 09:06 | 2026-08-25 09:06 |  |  | Fair | No | Premises found ok.
Outage | J.E.26.08.39270 | C001899304 | Jermaine Williams | Clarendon | Completed | Load_268788 | Monymusk - 210 | 2026-08-25 08:06 | 2026-08-25 09:12 | 2026-08-25 14:06 | 2026-08-25 14:07 | 2026-08-25 15:01 | 2026-08-25 14:56 | 2026-08-25 15:02 | 2026-08-25 15:02 |  |  | Fair | No | Premises not located.
Outage | J.E.26.08.40636 | C001899303 | Clyde Brown | Clarendon | Completed | Load_240729 | May Pen - 110 | 2026-08-25 08:06 | 2026-08-25 08:08 | 2026-08-25 08:23 | 2026-08-25 08:23 | 2026-08-25 09:51 | 2026-08-25 09:49 | 2026-08-25 09:58 | 2026-08-25 09:58 |  |  | Fair | No | Found supply disconnected
Non-Outage | J.E.26.08.39783 | C001899308 | Derrick Dawkins | St.James | Completed | Load_238758 | Bogue - 610 | 2026-08-25 08:11 | 2026-08-25 08:12 | 2026-08-25 09:26 | 2026-08-25 14:36 | 2026-08-25 14:35 | 2026-08-25 14:37 | 2026-08-25 14:37 | 2026-08-25 14:37 |  |  | Fair | No | Check and found ok customer has internal problem voltage found 110/111/222
Outage | J.E.26.08.36208 | C001899306 | Wan Carlos Scarlett | Portmore | Completed | Load_243287 | Naggo Head - 510 | 2026-08-25 08:11 | 2026-08-25 08:18 | 2026-08-25 12:15 | 2026-08-25 12:57 | 2026-08-25 13:07 | 2026-08-25 13:07 | 2026-08-25 13:08 | 2026-08-25 13:08 |  |  | Fair | No | Reset customer breaker power supply has been restored
Non-Outage | J.E.26.08.36552 | C001899311 | Dwain Samuels | Westmoreland | Completed | Load_254219 | Paradise - 110 | 2026-08-25 08:12 | 2026-08-25 08:14 | 2026-08-25 08:50 | 2026-08-25 10:35 | 2026-08-25 11:02 | 2026-08-25 11:19 | 2026-08-25 11:21 | 2026-08-25 11:21 |  |  | Fair | No | Corrosion found at 2 wire pothead . Voltage check 108 . corrosion clear use 2 pen unions . Voltage check 119
Non-Outage | J.E.26.08.37849 | C001899312 | Dwain Samuels | Westmoreland | Completed | Load_256052 | Paradise - 210 | 2026-08-25 08:12 | 2026-08-25 08:14 | 2026-08-25 08:50 | 2026-08-25 08:51 | 2026-08-25 09:37 | 2026-08-25 10:11 | 2026-08-25 10:14 | 2026-08-25 10:14 |  |  | Fair | No | Corrosion found at 3 wire pole. Voltage check 116-60-166. Corrosion clear use 1 one bolt clamp. Voltage check 116-116-232
Non-Outage | J.E.26.08.38175 | C001899310 | Dwain Samuels | Westmoreland | Completed | Load_249902 | Paradise - 310 | 2026-08-25 08:12 | 2026-08-25 08:14 | 2026-08-25 08:50 | 2026-08-25 11:53 | 2026-08-25 12:04 | 2026-08-25 12:45 | 2026-08-25 12:47 | 2026-08-25 12:47 |  |  | Fair | No | Area affected by low voltage due to theift
Non-Outage | J.E.26.08.40684 | C001899309 | Derrick Dawkins | St.James | Completed | Load_251647 | Bogue - 610 | 2026-08-25 08:12 | 2026-08-25 08:13 | 2026-08-25 09:26 | 2026-08-25 13:08 | 2026-08-25 13:40 | 2026-08-25 14:03 | 2026-08-25 14:35 | 2026-08-25 14:35 |  |  | Fair | No | Found multiple customers single phasing sue to one span of secondary phase burnt down due to illegal connection open 25 kva transformer to splice and retention one span of secondary phase used one pg clamp voltage left 115/118/233
Non-Outage | J.E.26.08.37031 | C001899313 | Andrae Dawkins | St.James | Completed | Load_568783 | Bogue - 310 | 2026-08-25 08:13 | 2026-08-25 08:14 | 2026-08-25 09:55 | 2026-08-26 08:39 | 2026-08-26 10:14 | 2026-08-26 10:34 | 2026-08-26 10:48 | 2026-08-26 10:48 |  |  | Fair | No | Check and found premises okay voltage found 116/116/233
Outage | J.E.26.08.40740 | C001899316 | Cliton Henry | St.Ann | Completed | Load_255850 | Upper White River - 110 | 2026-08-25 08:15 | 2026-08-25 08:16 | 2026-08-25 09:16 | 2026-08-25 09:17 | 2026-08-25 10:05 | 2026-08-25 11:23 | 2026-08-25 11:34 | 2026-08-25 11:34 |  |  | Fair | No | A trip saver found tripped at Lamkin Hil towards Dressikie at pole #400571 due to broken primary and 2/0 triplex secondary conductors cause by a fallen tree. Corrective work done to cut and remove tree, string and tension the primary conductor using approximately 70 feet #2 AA conductor , 1- dead end clamp and 2 one bolt clamps. The 2/0 triplex secondary was spliced and retention using 1-2/0 splicing sleeve and 4- one bolt clamps. Supply restored to energized the trip saver at Lamkin Hill pole #400571
Outage | J.E.26.08.40765 | C001899314 | Derrick Dawkins | St.James | Completed | Load_268842 | Bogue - 510 | 2026-08-25 08:15 | 2026-08-25 08:16 | 2026-08-25 19:14 | 2026-08-25 19:15 | 2026-08-25 20:00 | 2026-08-25 20:05 | 2026-08-25 20:05 | 2026-08-25 20:05 |  |  | Fair | No | Check and found premises ok. But customer has internal problem advice customer to get on electrician voltage left 119/119 238
Outage | J.E.26.08.40780 | C001899317 | Omar Harris | St.Ann | Completed | Load_339517 | Roaring River - 410 | 2026-08-25 08:20 | 2026-08-25 08:21 | 2026-08-25 08:39 | 2026-08-25 08:40 | 2026-08-25 08:52 | 2026-08-25 08:59 | 2026-08-25 09:00 | 2026-08-25 09:00 |  |  | Fair | No | Voltage at meter 115 115 231
Non-Outage | J.E.26.08.36306 | C001899321 | Rayon Foster | Hanover | Completed | Load_238259 | Orange Bay - 310 | 2026-08-25 08:22 | 2026-08-25 08:22 | 2026-08-25 08:52 | 2026-08-25 08:52 | 2026-08-25 12:22 | 2026-08-25 14:53 | 2026-08-25 14:53 | 2026-08-25 14:53 |  |  | Rains | No | Customer reported low voltage that affects the entire community Voltage check at transformer pole when arrived on location 100/100AB200volts troubleshoot line to customer meter voltage check in customer meter socket 98/101AB199volts change three clamps on customer pathead,open one 15kva transformer top up form tap 3 to tap 5 volts after closing 106/108AB214volts.voltage test at customer meter socket 108/106AB214volts customer house is 800ft form meter poleTransformer may need to upgrade form 15kva to a 25kva to accommodate housing development in community
Non-Outage | J.E.26.08.36464 | C001899322 | Hopeton Henry | St.Thomas | Completed | Load_238113 | Good Year - 110 | 2026-08-25 08:22 | 2026-08-25 08:24 | 2026-08-25 09:27 | 2026-08-25 14:18 | 2026-08-25 15:22 | 2026-08-25 15:24 | 2026-08-25 15:28 | 2026-08-25 15:28 |  |  | Fair | No | No problem found , possible internal problem 118-117-236 volts
Non-Outage | J.E.26.08.32019 | C001899324 | Andrae Dawkins | St.James | Completed | Load_301671 | Bogue - 310 | 2026-08-25 08:26 | 2026-08-25 08:27 | 2026-08-25 08:58 | 2026-08-25 08:59 | 2026-08-25 09:33 | 2026-08-25 09:51 | 2026-08-25 09:54 | 2026-08-25 09:54 |  |  | Fair | No | Found customer experiencing low voltage due to slack connection at pole clean and remade joints voltage found 114/45/157 voltage left 113/114/228
Non-Outage | J.E.26.08.25989 | C001899329 | Andrae Dawkins | St.James | Completed | Load_292197 | Bogue - 310 | 2026-08-25 08:27 | 2026-08-25 08:28 | 2026-08-25 09:54 | 2026-08-25 09:56 | 2026-08-25 10:54 | 2026-08-25 10:56 | 2026-08-25 10:58 | 2026-08-25 10:58 |  |  | Fair | No | Found customer experiencing low voltage due to corrosion at pothead clean and remade joints voltage left 118/119/237
Non-Outage | J.E.26.07.10865 | C001899332 | Fredrick Hamilton | KSAS | Completed | Load_253028 | Greenwich - 510 | 2026-08-25 08:28 | 2026-08-25 08:30 | 2026-08-25 08:37 | 2026-08-25 09:01 | 2026-08-25 09:00 | 2026-08-25 09:04 | 2026-08-25 09:04 | 2026-08-25 09:04 |  |  | Fair | No | Customer contacted and stated that meter is burnt causing single phaseAfter checks by his electrician Please assign to field service for a meter change Customer stated that electrician installed a direct connection in socket to facilitate full power
Non-Outage | J.E.26.08.04737 | C001899334 | Fredrick Hamilton | KSAS | Completed | Load_579113 | Greenwich - 510 | 2026-08-25 08:28 | 2026-08-25 08:30 | 2026-08-25 08:37 | 2026-08-25 08:49 | 2026-08-25 08:49 | 2026-08-25 08:50 | 2026-08-25 08:51 | 2026-08-25 08:51 |  |  | Fair | No | Customer contacted and stated that issue was resolved 2 weeks ago Premises is ok
Non-Outage | J.E.26.08.05082 | C001899333 | Fredrick Hamilton | KSAS | Completed | Load_1002810 | Greenwich - 510 | 2026-08-25 08:28 | 2026-08-25 08:30 | 2026-08-25 08:37 | 2026-08-25 10:47 | 2026-08-25 10:47 | 2026-08-25 10:49 | 2026-08-25 10:49 | 2026-08-25 10:49 |  |  | Fair | No | Customer contacted and stated that power was restored previously Premises is ok
Non-Outage | J.E.26.08.35038 | C001899331 | Fredrick Hamilton | KSAN | Completed | Load_300723 | Constant Spring - 310 | 2026-08-25 08:28 | 2026-08-25 08:30 | 2026-08-25 08:37 | 2026-08-25 10:53 | 2026-08-25 11:23 | 2026-08-25 11:37 | 2026-08-25 11:37 | 2026-08-25 11:37 |  |  | Fair | No | 247v/123.5/122.8v obtained High voltage detected affecting area please have field service inspect transformer
Non-Outage | J.E.26.08.35041 | C001899335 | Fredrick Hamilton | KSAS | Completed | Load_253639 | Up Park Camp - 510 | 2026-08-25 08:28 | 2026-08-25 08:30 | 2026-08-25 08:37 | 2026-08-25 08:46 | 2026-08-25 08:45 | 2026-08-25 08:47 | 2026-08-25 08:47 | 2026-08-25 08:47 |  |  | Fair | No | Customer contacted and stated that power was restored fully previously Premises is ok
Non-Outage | J.E.26.08.36515 | C001899330 | Fredrick Hamilton | KSAS | Completed | Load_268260 | Greenwich - 310 | 2026-08-25 08:28 | 2026-08-25 08:30 | 2026-08-25 08:37 | 2026-08-25 09:42 | 2026-08-25 10:20 | 2026-08-25 10:46 | 2026-08-25 10:46 | 2026-08-25 10:46 |  |  | Fair | No | 239.3v/121.1v/118.4v obtained no issues detected on JPS supply premises is ok
Non-Outage | J.E.26.08.36548 | C001899336 | Eric Williams | KSAN | Completed | Load_256268 | Constant Spring - 210 | 2026-08-25 08:28 | 2026-08-25 08:40 | 2026-08-25 08:58 | 2026-08-25 08:58 | 2026-08-25 10:20 | 2026-08-25 10:20 | 2026-08-25 10:21 | 2026-08-25 10:21 |  |  | Fair | No | 4 wire service, wire disconnected at pole
Non-Outage | J.E.26.08.34584 | C001899341 | Rochaine Hussey | KSAN | Completed | Load_245505 | Constant Spring - 310 | 2026-08-25 08:35 | 2026-08-25 08:36 | 2026-08-25 09:34 | 2026-08-25 09:56 | 2026-08-25 09:56 | 2026-08-25 10:14 | 2026-08-25 10:14 | 2026-08-25 10:14 |  |  | Fair | No | Customer say the issue was already resolved and power was restored
Non-Outage | J.E.26.08.36731 | C001899342 | Roemello Brown | Trelawny | Completed | Load_294490 | Martha Brae - 110 | 2026-08-25 08:35 | 2026-08-25 08:36 | 2026-08-25 11:26 | 2026-08-25 11:57 | 2026-08-25 12:51 | 2026-08-25 12:53 | 2026-08-25 13:17 | 2026-08-25 13:17 |  |  | Fair | No | Customer was requesting a disconnection so I informed her to visit one of the office or she can request it on the app
Non-Outage | J.E.26.08.37058 | C001899343 | Roemello Brown | Trelawny | Completed | Load_302475 | Duncans - 110 | 2026-08-25 08:36 | 2026-08-25 08:36 | 2026-08-25 13:39 | 2026-08-25 16:03 | 2026-08-25 16:34 | 2026-08-25 16:34 | 2026-08-25 16:40 | 2026-08-25 16:40 |  |  | Fair | No | Customer meter burn up needs field service technician to have meter change please Voltage found 111/110/221Voltage leave 111/110/221
Non-Outage | J.E.26.08.40324 | C001899352 | Royston Montague | St.Catherine | Completed | Load_238151 | Twickenham - 310 | 2026-08-25 08:37 | 2026-08-25 09:48 | 2026-08-25 10:22 | 2026-08-25 15:00 | 2026-08-25 15:00 | 2026-08-25 15:01 | 2026-08-25 15:06 | 2026-08-25 15:06 |  |  | Fair | No | Customer unable to add credit to ciu box, please inform field service department thanks.
Non-Outage | J.E.26.08.40387 | C001899351 | Royston Montague | St.Catherine | Completed | Load_243946 | Rhodens Pen - 410 | 2026-08-25 08:37 | 2026-08-25 09:47 | 2026-08-25 10:22 | 2026-08-25 11:19 | 2026-08-25 12:44 | 2026-08-25 12:44 | 2026-08-25 12:44 | 2026-08-25 12:44 |  |  | Fair | No | Slack connection in meter socket, same corrected. Voltage 212v 105v 105v
Outage | J.E.26.08.40833 | C001899350 | Derrick Dawkins | St.James | Completed | Load_253450 | Bogue - 610 | 2026-08-25 08:37 | 2026-08-25 08:38 | 2026-08-25 09:25 | 2026-08-25 12:54 | 2026-08-25 12:54 | 2026-08-25 13:05 | 2026-08-25 13:07 | 2026-08-25 13:07 | TreeContact |  | Fair | No | Check and found premises ok voltage left 105/116/225
Non-Outage | J.E.26.08.37316 | C001899357 | Royston Montague | St.Catherine | Completed | Load_250553 | Tredegar - 410 | 2026-08-25 08:38 | 2026-08-26 08:09 | 2026-08-26 08:34 | 2026-08-26 08:55 | 2026-08-26 09:22 | 2026-08-26 09:22 | 2026-08-26 09:22 | 2026-08-26 09:22 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.08.38659 | C001899356 | Royston Montague | St.Catherine | Completed | Load_253146 | Tredegar - 310 | 2026-08-25 08:38 | 2026-08-25 09:48 | 2026-08-25 10:22 | 2026-08-25 12:47 | 2026-08-25 13:32 | 2026-08-25 13:33 | 2026-08-25 13:33 | 2026-08-25 13:33 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.08.39858 | C001899355 | Royston Montague | St.Catherine | Completed | Load_241531 | Tredegar - 210 | 2026-08-25 08:38 | 2026-08-25 09:48 | 2026-08-25 10:22 | 2026-08-25 13:34 | 2026-08-25 14:02 | 2026-08-25 14:15 | 2026-08-25 14:15 | 2026-08-25 14:15 |  |  | Fair | No | Low voltage coming from rami box 112v 49v . Please assign this job to the relevant team thanks.
Non-Outage | J.E.26.08.31452 | C001899359 | Roemello Brown | Trelawny | Completed | Load_255143 | Greenwood - 110 | 2026-08-25 08:39 | 2026-08-25 08:40 | 2026-08-25 11:40 | 2026-08-25 13:18 | 2026-08-25 14:27 | 2026-08-25 14:27 | 2026-08-25 16:03 | 2026-08-25 16:03 |  |  | Fair | No | Premises found working okay Voltage found 116/115/231Voltage leave 116/115/231
Non-Outage | J.E.26.08.32048 | C001899358 | Roemello Brown | Trelawny | Completed | Load_248283 | Duncans - 210 | 2026-08-25 08:39 | 2026-08-25 08:39 | 2026-08-26 12:37 | 2026-08-26 12:39 | 2026-08-26 14:39 | 2026-08-26 14:39 | 2026-08-26 16:07 | 2026-08-26 16:07 |  |  | Fair | No | Premises found working okay Voltage found 117/118/235Voltage leave 117/118/235
Non-Outage | J.E.26.08.05674 | C001899367 | Odeanie Davis | KSAS | Completed | Load_263506 | Cane River - 310 | 2026-08-25 08:40 | 2026-08-25 08:41 | 2026-08-25 12:32 | 2026-08-26 08:18 | 2026-08-26 08:18 | 2026-08-26 08:18 | 2026-08-26 08:21 | 2026-08-26 08:21 |  |  | Fair | No | Customer stated tray they are not having the issue at this time, however back office confirmed that this meter and others in the area are receiving high voltage, technician request for transformer to be checked,
Non-Outage | J.E.26.08.05699 | C001899365 | Odeanie Davis | KSAS | Completed | Load_263506 | Cane River - 310 | 2026-08-25 08:40 | 2026-08-25 08:41 | 2026-08-25 11:40 | 2026-08-25 11:41 | 2026-08-25 11:41 | 2026-08-25 11:50 | 2026-08-25 11:46 | 2026-08-25 11:46 |  |  | Fair | No | Customer stated that they aren’t having any issues over a week now, however
Non-Outage | J.E.26.08.05766 | C001899366 | Odeanie Davis | KSAS | Completed | Load_263506 | Cane River - 310 | 2026-08-25 08:40 | 2026-08-25 08:41 | 2026-08-25 12:32 | 2026-08-26 08:21 | 2026-08-26 08:21 | 2026-08-26 08:30 | 2026-08-26 08:22 | 2026-08-26 08:22 |  |  | Fair | No | Customer stated tray they are not having the issue at this time, however back office confirmed that this meter and others in the area are receiving high voltage, technician request for transformer to be checked,
Non-Outage | J.E.26.08.05798 | C001899363 | Odeanie Davis | KSAS | Completed | Load_263506 | Cane River - 310 | 2026-08-25 08:40 | 2026-08-25 08:41 | 2026-08-25 11:46 | 2026-08-25 11:47 | 2026-08-25 11:46 | 2026-08-25 12:06 | 2026-08-25 11:47 | 2026-08-25 11:47 |  |  | Fair | No | Customer stated that they aren’t having any issues over a week now, however
Non-Outage | J.E.26.08.05960 | C001899362 | Odeanie Davis | KSAS | Completed | Load_263506 | Cane River - 310 | 2026-08-25 08:40 | 2026-08-25 08:41 | 2026-08-25 11:16 | 2026-08-25 11:17 | 2026-08-25 11:16 | 2026-08-25 11:30 | 2026-08-25 11:28 | 2026-08-25 11:28 |  |  | Fair | No | Back office confirmed this meter and others in the area receiving high voltage, technician request for transformer to checked, 115V/117v at arrival, corrosion at pothead and secondary corrected, 2 one bolt clamps & 1 penn union, 115v/117v & 233v after correction
Non-Outage | J.E.26.08.05963 | C001899361 | Odeanie Davis | KSAS | Completed | Load_263506 | Cane River - 310 | 2026-08-25 08:40 | 2026-08-25 08:41 | 2026-08-25 10:38 | 2026-08-25 10:38 | 2026-08-25 10:43 | 2026-08-25 11:15 | 2026-08-25 11:16 | 2026-08-25 11:16 |  |  | Fair | No | 115V/117v at arrival, corrosion at pothead and secondary corrected, 2 one bolt clamps & 1 penn union, 115v/117v & 233v after correction
Non-Outage | J.E.26.08.06278 | C001899360 | Odeanie Davis | KSAS | Completed | Load_242999 | Cane River - 410 | 2026-08-25 08:40 | 2026-08-25 08:41 | 2026-08-25 10:02 | 2026-08-25 10:03 | 2026-08-25 10:31 | 2026-08-25 10:31 | 2026-08-25 10:33 | 2026-08-25 10:33 |  |  | Fair | No | Corrosion at pothead cleaned and reclaimed, 1 one bolt clamp & 1 penn union, 114v/116v & 230v after correction
Non-Outage | J.E.26.08.38121 | C001899372 | Roemello Brown |  | Completed |  |  | 2026-08-25 08:43 | 2026-08-25 08:44 | 2026-08-26 08:20 | 2026-08-26 09:53 | 2026-08-26 10:26 | 2026-08-26 10:26 | 2026-08-26 10:28 | 2026-08-26 10:28 |  |  | Fair | No | Premises found working okay problem was not on jps side Voltage found 118/118/236Voltage leave 118/118/236
Outage | J.E.26.08.40809 | C001899373 | Clyde Brown | Clarendon | Completed | Load_568356 | May Pen - 110 | 2026-08-25 08:44 | 2026-08-25 08:44 | 2026-08-25 10:29 | 2026-08-25 10:30 | 2026-08-25 11:10 | 2026-08-25 11:05 | 2026-08-25 11:19 | 2026-08-25 11:19 | Fire |  | Fair | No | No fire seen and trees are cleared from secondary line ,JPS crew repaired line that guinep tree fell on .
Outage | J.E.26.08.36540 | C001899379 | Jermaine Williams | St.Catherine | Completed | Load_255385 | Rhodens Pen - 310 | 2026-08-25 08:49 | 2026-08-25 08:50 | 2026-08-25 09:31 | 2026-08-25 09:32 | 2026-08-25 10:33 | 2026-08-25 10:10 | 2026-08-25 10:35 | 2026-08-25 10:35 | BrokenPole |  | Fair | No | Defective cable pole.
Outage | J.E.26.08.40819 | C001899381 | Omar King | St.Ann | Completed | Load_263870 | Ocho Rios - 310 | 2026-08-25 08:49 | 2026-08-25 08:50 | 2026-08-25 12:24 | 2026-08-25 12:25 | 2026-08-25 13:04 | 2026-08-25 13:05 | 2026-08-25 13:05 | 2026-08-25 13:05 |  |  | Fair | No | Customer found with internal issues I advise customer to use electrician
Non-Outage | J.E.26.08.35964 | C001899382 | Omar Harris | St.Ann | Completed | Load_243376 | Roaring River - 210 | 2026-08-25 08:51 | 2026-08-25 08:52 | 2026-08-25 09:28 | 2026-08-25 09:29 | 2026-08-25 09:40 | 2026-08-25 09:40 | 2026-08-25 09:41 | 2026-08-25 09:41 |  |  | Fair | No | Not getting customer on phone
Non-Outage | J.E.26.08.36212 | C001899383 | Omar Harris | St.Ann | Completed | Load_239038 | Roaring River - 210 | 2026-08-25 08:51 | 2026-08-25 08:52 | 2026-08-25 09:41 | 2026-08-25 09:42 | 2026-08-25 10:36 | 2026-08-25 11:33 | 2026-08-25 11:33 | 2026-08-25 11:33 |  |  | Fair | No | Remake neutral joint in secondary line using 1 one bolt clamp voltage 107 112 220
Non-Outage | J.E.26.08.17251 | C001899392 | Swon Miller |  | Completed |  |  | 2026-08-25 09:10 | 2026-08-25 09:11 | 2026-08-26 09:52 | 2026-08-26 09:53 | 2026-08-26 09:52 | 2026-08-26 10:24 | 2026-08-26 10:29 | 2026-08-26 10:29 |  |  | Fair | No | Customer at the end of the circuit experiencing low voltage.this is an ongoing issue this problem has been reported multiple times further assessment is required by the maintenance plz refer to maintenance voltage found line side 105/105/210/load side 98/102/202 voltage left 102/98 /200
Outage | J.E.26.08.40949 | C001899399 | Cliton Henry | St.Mary | Completed | Load_352448 | Oracabessa - 210 | 2026-08-25 09:14 | 2026-08-25 09:16 | 2026-08-25 11:41 | 2026-08-25 11:42 | 2026-08-25 12:50 | 2026-08-25 14:03 | 2026-08-25 14:10 | 2026-08-25 14:10 | Fire |  | Fair | No | A customer with meter number 2877575 service wire found broken cause by known person cutting tree which branches fell on the service wire . The customer service wire was disconnected and taped by an electrician and made safe. The service wire was was reconnected using approximately 60 feet #6 triplex and 3 one bolt clamps. Voltages left were 116-117/234 volts. NB. Other customers complaints of damage equipment.
Non-Outage | J.E.26.08.31342 | C001899413 | Andrae Dawkins | St.James | Completed | Load_568783 | Bogue - 310 | 2026-08-25 09:29 | 2026-08-25 09:31 | 2026-08-25 09:54 | 2026-08-26 10:49 | 2026-08-26 10:49 | 2026-08-26 10:34 | 2026-08-26 10:50 | 2026-08-26 10:50 |  |  | Fair | No | Check and found premises okay voltage found 116/116/233
Outage | J.E.26.08.40941 | C001899412 | Shawn Medley | St.James | Completed | Load_301642 | Bogue - 310 | 2026-08-25 09:29 | 2026-08-25 09:30 | 2026-08-25 09:39 | 2026-08-26 09:21 | 2026-08-26 09:20 | 2026-08-26 09:21 | 2026-08-26 09:22 | 2026-08-26 09:22 |  |  | Fair | No | Duplicate report customer said supply already restored
Outage | J.E.26.08.36489 | C001899419 | Swon Miller | St.James | Completed | Load_292357 | Queens Drive - 810 | 2026-08-25 09:33 | 2026-08-25 09:34 | 2026-08-25 10:25 | 2026-08-25 10:26 | 2026-08-25 11:23 | 2026-08-18 01:00 | 2026-08-25 13:10 | 2026-08-25 13:10 |  |  | Fair | No | Found customer single phasing due one phase not connected use 3ft#2 twisted and two pg to carry out repairs voltage found 115 voltage left 116/115/231
Outage | J.E.26.08.40707 | C001899441 | Selvin White | St.Elizabeth | Completed | Load_244450 | Maggotty - 110 | 2026-08-25 09:48 | 2026-08-25 09:49 | 2026-08-25 11:41 | 2026-08-25 11:41 | 2026-08-25 12:48 | 2026-08-25 13:32 | 2026-08-25 13:34 | 2026-08-25 13:34 |  |  | Fair | No | Remade corroded connections at customer’s pothead on customer’s phase conductors . Supply restored with voltage readings of 118,117,236 volts left inside customer’s meter socket.
Outage | J.E.26.08.40940 | C001899443 | Roemello Brown | Trelawny | Completed | Load_302922 | Greenwood - 110 | 2026-08-25 09:48 | 2026-08-25 09:49 | 2026-08-25 10:34 | 2026-08-25 10:35 | 2026-08-25 10:55 | 2026-08-25 10:55 | 2026-08-25 11:48 | 2026-08-25 11:48 |  |  | Fair | No | Please transfer this call to Mr.couch field service department
Outage | J.E.26.08.40995 | C001899442 | Wayne Dillion | Manchester | Completed | Load_258714 | Spur Tree - 210 | 2026-08-25 09:48 | 2026-08-25 09:49 | 2026-08-25 11:23 | 2026-08-25 11:23 | 2026-08-25 11:23 | 2026-08-25 12:06 | 2026-08-25 12:12 | 2026-08-25 12:12 |  |  | Fair | No | Supply check and found area experiencing high voltage, voltage reading 135v, 47v and amp reading phase one 161 and phase two 47 and the neutral 99. Further checks reveals that customer meter wires are burnt. Disconnect same at pot head and customer was advised to have same repaired. After resolving the problem area still has low voltage, voltage found at transformer 107v, 108v cross phase 216v and amp reading phase one 47 and phase two 42 and neutral 4. Check another transformer circuit and voltage is the same. Suspect primary voltage coming in low. Please refer same to maintenance to resolve the issue.
Outage | J.E.26.08.40917 | C001899444 | Roxroy Needham | St.Ann | Completed | Load_269390 | Cardiff Hall - 310 | 2026-08-25 09:49 | 2026-08-25 15:39 | 2026-08-25 17:11 | 2026-08-25 17:12 | 2026-08-25 19:05 | 2026-08-25 19:53 | 2026-08-25 19:57 | 2026-08-25 19:57 | Fire | Y | Fair | No | Open a 25 KVA transformer at pole to repair 3 span of secondary line used 80 ft of # 2 aa wire and 6 pg clamp
Outage | J.E.26.08.40942 | C001899447 | Wan Carlos Scarlett | St.Catherine | Completed | Load_266814 | Twickenham - 210 | 2026-08-25 09:49 | 2026-08-25 09:52 | 2026-08-25 11:11 | 2026-08-25 11:12 | 2026-08-25 11:22 | 2026-08-25 12:48 | 2026-08-25 12:50 | 2026-08-25 12:50 |  |  | Fair | No | Found 50KVA transformer drop lead wire to open secondary line corroded use 5 one bolt clamps at pole readings 116-117-234. Isolate and close 50KVA transformer pole # 624797
Outage | J.E.26.08.41028 | C001899445 | Roxroy Needham | St.Ann | Completed | Load_242766 | Cardiff Hall - 310 | 2026-08-25 09:49 | 2026-08-25 15:43 | 2026-08-25 19:59 | 2026-08-25 19:59 | 2026-08-25 21:51 | 2026-08-25 21:30 | 2026-08-25 21:52 | 2026-08-25 21:52 |  |  | Fair | No | Remake joint at pole used 1 pg clamp voltage left at meter 113-114-219
Outage | J.E.26.08.41075 | C001899446 | Omar King | St.Ann | Completed | Load_258244 | Ocho Rios - 310 | 2026-08-25 09:49 | 2026-08-25 09:50 | 2026-08-25 11:31 | 2026-08-25 11:32 | 2026-08-25 12:23 | 2026-08-25 12:24 | 2026-08-25 12:24 | 2026-08-25 12:24 | Fire |  | Fair | No | Customer stantion need to be rectify
Outage | J.E.26.08.40931 | C001899448 | Omar Harris | St.Ann | Completed | Load_574269 | Roaring River - 210 | 2026-08-25 09:50 | 2026-08-25 09:51 | 2026-08-25 12:22 | 2026-08-25 12:23 | 2026-08-25 12:53 | 2026-08-25 12:53 | 2026-08-25 12:54 | 2026-08-25 12:54 |  |  | Fair | No | Refer to field service
Non-Outage | J.E.26.08.36701 | C001899468 | Odaine Johnson | Clarendon | Completed | Load_260282 | Parnassus - 310 | 2026-08-25 09:52 | 2026-08-25 09:55 | 2026-08-25 10:46 | 2026-08-25 12:55 | 2026-08-25 13:25 | 2026-08-25 13:25 | 2026-08-25 13:26 | 2026-08-25 13:26 |  |  | Fair | No | Corroded phase found at pole remade connection using 1 one bolt clamp voltage reading 110 volts
Non-Outage | J.E.26.08.37153 | C001899469 | Odaine Johnson | Clarendon | Completed | Load_574466 | Parnassus - 310 | 2026-08-25 09:52 | 2026-08-25 09:55 | 2026-08-25 10:46 | 2026-08-25 12:40 | 2026-08-25 12:52 | 2026-08-25 12:53 | 2026-08-25 12:54 | 2026-08-25 12:54 |  |  | Fair | No | Customer received low voltage from rami box number
Non-Outage | J.E.26.08.37877 | C001899466 | Dwain Samuels | Westmoreland | Completed | Load_256052 | Paradise - 210 | 2026-08-25 09:52 | 2026-08-25 09:54 | 2026-08-25 10:01 | 2026-08-25 10:22 | 2026-08-25 10:22 | 2026-08-25 10:22 | 2026-08-25 10:24 | 2026-08-25 10:24 |  |  | Fair | No | Corrosion found at 3 wire pole. Voltage check 116-60-166. Corrosion clear use 1 one bolt clamp. Voltage check 116-116-232
Non-Outage | J.E.26.08.40844 | C001899465 | Odaine Johnson | Clarendon | Completed | Load_570300 | Parnassus - 310 | 2026-08-25 09:52 | 2026-08-25 09:55 | 2026-08-25 10:46 | 2026-08-25 13:27 | 2026-08-25 13:41 | 2026-08-25 13:44 | 2026-08-25 13:45 | 2026-08-25 13:45 |  |  | Fair | No | Corroded neutral found at pole remade connection using 1 one bolt clamp voltage reading 115/115/231 volts
Non-Outage | J.E.26.08.41062 | C001899462 | Dwain Samuels | Westmoreland | Completed | Load_248847 | Paradise - 210 | 2026-08-25 09:52 | 2026-08-25 09:54 | 2026-08-25 10:01 | 2026-08-25 10:25 | 2026-08-25 10:25 | 2026-08-25 10:33 | 2026-08-25 10:34 | 2026-08-25 10:34 |  |  | Fair | No | Called customer and customer confirm that supply was restored
Outage | J.E.26.08.40918 | C001899463 | Damion Reid | Manchester | Completed | Load_1002314 | Porus - 210 | 2026-08-25 09:52 | 2026-08-26 08:12 | 2026-08-26 10:41 | 2026-08-26 10:41 | 2026-08-26 12:14 | 2026-08-26 12:26 | 2026-08-26 12:30 | 2026-08-26 12:30 |  |  | Fair | No | Remade corroded service phase at secondary pole for 3 wire service using one 1 bolt clamp voltage reading at meter socket phase to neutral 114v-113v across phase 229v
Outage | J.E.26.08.40932 | C001899464 | Richard Samuda | Manchester | Completed | Load_265696 | Spur Tree - 310 | 2026-08-25 09:52 | 2026-08-25 09:55 | 2026-08-25 10:11 | 2026-08-25 10:12 | 2026-08-25 10:39 | 2026-08-25 00:04 | 2026-08-25 12:04 | 2026-08-25 12:04 |  |  | Fair | No | Replace burnt out one bolt clamp on transformer lead and remake burnt jumper using 3 ft of aluminum wire and 3 1 bolt clamp voltage: 116,116 232 customer back to normal
Non-Outage | J.E.26.08.34794 | C001899476 | Neville Spencer | Clarendon | Completed | Load_260045 | May Pen - 110 | 2026-08-25 09:53 | 2026-08-26 17:25 | 2026-08-26 17:28 | 2026-08-26 17:29 | 2026-08-26 17:57 | 2026-08-26 17:57 | 2026-08-26 18:01 | 2026-08-26 18:01 |  |  | Fair | No | Found defective 3, wire meter # 2549976 voltage reading in meter socket 110 112=223 meter need to replace customer advised.
Non-Outage | J.E.26.08.35806 | C001899473 | Odaine Johnson | Clarendon | Completed | Load_239364 | May Pen - 110 | 2026-08-25 09:53 | 2026-08-25 09:55 | 2026-08-25 10:46 | 2026-08-25 11:38 | 2026-08-25 12:38 | 2026-08-25 12:38 | 2026-08-25 12:39 | 2026-08-25 12:39 |  |  | Fair | No | Transformer neutral drop lead corroded remade connection using 2 one bolt clamps voltage voltage 120/122/242 volts
Non-Outage | J.E.26.08.36111 | C001899471 | Odaine Johnson | Clarendon | Completed | Load_268249 | Parnassus - 310 | 2026-08-25 09:53 | 2026-08-25 09:55 | 2026-08-25 10:46 | 2026-08-25 13:46 | 2026-08-25 13:51 | 2026-08-25 14:29 | 2026-08-25 14:30 | 2026-08-25 14:30 |  |  | Fair | No | Corroded phase found at pole remade connection using one bolt clamp voltage reading 115/115/231 volts
Outage | J.E.26.08.41100 | C001899474 | Swon Miller | St.James | Completed | Load_261013 | Queens Drive - 710 | 2026-08-25 09:53 | 2026-08-25 09:54 | 2026-08-25 13:13 | 2026-08-25 13:14 | 2026-08-25 14:14 | 2026-08-20 02:48 | 2026-08-25 14:48 | 2026-08-25 14:48 | BrokenWire |  | Fair | No | Found customer service wire disconnected at pothead use use 1 pg to carry out repairs voltage found 0.000 voltage left 116
Outage | J.E.26.08.41121 | C001899477 | Wan Carlos Scarlett | Portmore | Completed | Load_245535 | Naggo Head - 610 | 2026-08-25 09:56 | 2026-08-25 09:57 | 2026-08-25 11:49 | 2026-08-25 13:08 | 2026-08-25 13:33 | 2026-08-25 14:37 | 2026-08-25 14:46 | 2026-08-25 14:46 |  |  | Fair | No | Found one span of open secondary line neutral burn down use 180ft of # 2 loom wire 2 splicing sleeve 8 one bolt clamps isolate and close 50KVA transformer no pole # was found Some customer equipment get damaged because of the broken neutral pole # 082186
Non-Outage | J.E.26.08.40066 | C001899487 | Odaine Johnson | Clarendon | Completed | Load_253361 | Monymusk - 410 | 2026-08-25 09:57 | 2026-08-25 10:02 | 2026-08-25 10:46 | 2026-08-25 10:58 | 2026-08-25 11:37 | 2026-08-25 11:37 | 2026-08-25 11:37 | 2026-08-25 11:37 |  |  | Fair | No | Corroded phase found at pole remade connection using 1 one bolt clamp voltage reading 115/114/230 volts
Non-Outage | J.E.26.08.36536 | C001899488 | Jermaine Williams | Clarendon | Completed | Load_268249 | Parnassus - 310 | 2026-08-25 09:58 | 2026-08-25 10:02 | 2026-08-25 10:35 | 2026-08-25 10:36 | 2026-08-25 11:07 | 2026-08-25 11:07 | 2026-08-25 11:10 | 2026-08-25 11:10 | BrokenWire |  | Fair | No | Suspected at meter socket, barrel lock on meter unable to access. Refer to field service dept. Hpoeton Daley
Non-Outage | J.E.26.08.28878 | C001899489 | Andrae Dawkins | St.James | Completed | Load_253415 | Bogue - 610 | 2026-08-25 09:59 | 2026-08-25 10:00 | 2026-08-26 15:01 | 2026-08-26 15:02 | 2026-08-26 15:42 | 2026-08-26 15:45 | 2026-08-26 15:45 | 2026-08-26 15:45 |  |  | Fair | No | Found customer pothead corroded clean and and remade joints used three pg clamp voltage left 120/119/239 also found customer meter socket defective advise customer to get an electrician
Non-Outage | J.E.26.08.35981 | C001899490 | Andrae Dawkins | St.James | Completed | Load_253026 | Bogue - 610 | 2026-08-25 10:00 | 2026-08-25 10:01 | 2026-08-25 11:56 | 2026-08-25 12:04 | 2026-08-25 12:04 | 2026-08-25 13:05 | 2026-08-25 13:08 | 2026-08-25 13:08 |  |  | Fair | No | Found multiple customers experiencing low voltage due to secondary neutral jumper corroded cleaned and remade joints voltage left 114/115/229
Non-Outage | J.E.26.08.31556 | C001899491 | Andrae Dawkins | St.James | Completed | Load_238476 | Bogue - 610 | 2026-08-25 10:01 | 2026-08-25 10:02 | 2026-08-25 10:17 | 2026-08-25 10:18 | 2026-08-25 12:02 | 2026-08-25 10:56 | 2026-08-25 12:03 | 2026-08-25 12:03 |  |  | Fair | No | Found customer experiencing low voltage due to corrosion at pothead clean and remade joints voltage left 118/119/237
Non-Outage | J.E.26.08.36494 | C001899497 | Andrae Dawkins | St.James | Completed | Load_240972 | Bogue - 610 | 2026-08-25 10:02 | 2026-08-25 10:03 | 2026-08-25 13:16 | 2026-08-25 13:17 | 2026-08-25 15:56 | 2026-08-25 14:21 | 2026-08-25 16:41 | 2026-08-25 16:41 |  |  | Fair | No | Check and found ok customer has internal problem voltage found 115/117/232
Non-Outage | J.E.26.08.40854 | C001899499 | Stephen Taylor |  | Completed |  |  | 2026-08-25 10:03 | 2026-08-25 10:05 | 2026-08-25 11:14 | 2026-08-25 11:14 | 2026-08-25 12:01 | 2026-08-25 12:01 | 2026-08-25 12:04 | 2026-08-25 12:04 |  |  | Fair | No | Patrol the area power is in the area a lot of call to customer no one answered the phone
Outage | J.E.26.08.37195 | C001899500 | Derrick Grubb | St.Thomas | Completed | Load_243194 | Good Year - 210 | 2026-08-25 10:03 | 2026-08-25 15:38 | 2026-08-25 17:16 | 2026-08-25 17:16 | 2026-08-25 19:12 | 2026-08-25 19:17 | 2026-08-25 19:17 | 2026-08-25 19:17 | BrokenWire |  | Fair | No | Replace defective service wire using approximately 100ft of #6aaa triplex wire and six one bolt clamps. Voltage readings when leaving 115v, 116v, 232v.
Non-Outage | J.E.26.08.27667 | C001899502 | Andrae Dawkins | St.James | Completed | Load_266117 | Bogue - 510 | 2026-08-25 10:04 | 2026-08-25 10:05 | 2026-08-25 18:29 | 2026-08-25 18:30 | 2026-08-25 18:29 | 2026-08-25 15:21 | 2026-08-25 18:35 | 2026-08-25 18:35 |  |  | Fair | No | Cannot to locate customer unable to reach customer mobile
Non-Outage | J.E.26.08.32184 | C001899501 | Andrae Dawkins | St.James | Completed | Load_247912 | Bogue - 510 | 2026-08-25 10:04 | 2026-08-25 10:04 | 2026-08-26 10:51 | 2026-08-26 10:52 | 2026-08-26 11:14 | 2026-08-26 11:48 | 2026-08-26 11:52 | 2026-08-26 11:52 |  |  | Fair | No | Found customer experiencing low voltage due to contamination at pothead clean and remade joints voltage found 125/103/228 voltage eft 110/115/225
Outage | J.E.26.08.41138 | C001899508 | Donald Cunningham | St.Catherine | Completed | Load_556352 | Rhodens Pen - 210 | 2026-08-25 10:07 | 2026-08-25 10:14 | 2026-08-25 11:01 | 2026-08-25 11:02 | 2026-08-25 11:49 | 2026-08-25 12:00 | 2026-08-25 12:00 | 2026-08-25 12:00 |  |  | Fair | No | Premises found ok supply restored
Outage | J.E.26.08.41144 | C001899509 | Delano Gayle | St.Catherine | Completed | Load_557279 | Tredegar - 210 | 2026-08-25 10:07 | 2026-08-25 23:28 | 2026-08-26 02:16 | 2026-08-26 02:16 | 2026-08-26 03:28 | 2026-08-26 03:59 | 2026-08-26 03:59 | 2026-08-26 03:59 |  |  | Fair | No | Prepaid customer send call to Moses
Outage | J.E.26.08.41098 | C001899510 | Delano Gayle | St.Catherine | Completed | Load_265271 | Tredegar - 310 | 2026-08-25 10:08 | 2026-08-25 23:28 | 2026-08-26 01:28 | 2026-08-26 01:28 | 2026-08-26 02:08 | 2026-08-26 02:15 | 2026-08-26 02:15 | 2026-08-26 02:15 |  |  | Fair | No | Prepaid customer unable to add credit, states his CIU not displaying send call to field service or Moses to be of some assistance
Outage | J.E.26.08.41120 | C001899526 | Dwayne Samuels | Trelawny | Completed | Load_247110 | Duncans - 110 | 2026-08-25 10:13 | 2026-08-25 10:14 | 2026-08-25 10:40 | 2026-08-25 10:40 | 2026-08-25 11:42 | 2026-08-25 11:47 | 2026-08-25 11:48 | 2026-08-25 11:48 |  |  | Fair | No | Unable to locate customer,no answer from telephone and directions is not right…
Outage | J.E.26.08.41143 | C001899527 | Jermaine Williams | Clarendon | Completed | Load_251249 | Monymusk - 410 | 2026-08-25 10:14 | 2026-08-25 10:15 | 2026-08-25 12:59 | 2026-08-25 12:59 | 2026-08-25 13:58 | 2026-08-25 13:58 | 2026-08-25 14:06 | 2026-08-25 14:06 | BrokenWire |  | SevereWind | No | Isolate 25kva xfmr to splice and retention three spans broken secondary neutral.
Non-Outage | J.E.26.08.40856 | C001899588 | Andrae Clarke | Portland | Completed | Load_259997 | Port Antonio - 410 | 2026-08-25 10:34 | 2026-08-25 10:35 | 2026-08-25 12:06 | 2026-08-25 12:07 | 2026-08-25 12:07 | 2026-08-25 11:00 | 2026-08-25 14:10 | 2026-08-25 14:10 |  |  | Fair | No | Premises found okay Check voltage 115/115/230
Outage | J.E.26.08.41044 | C001899585 | Milton Charlton | KSAN | Completed | Load_252653 | West Kings House - 310 | 2026-08-25 10:34 | 2026-08-25 10:35 | 2026-08-25 10:50 | 2026-08-25 10:51 | 2026-08-25 10:56 | 2026-08-25 11:15 | 2026-08-25 11:22 | 2026-08-25 11:22 |  |  | Fair | No | Found okay upon arrival. Customer has an internal problem.
Outage | J.E.26.08.41096 | C001899587 | Eric Williams | KSAN | Completed | Load_239844 | Constant Spring - 210 | 2026-08-25 10:34 | 2026-08-25 10:35 | 2026-08-25 10:51 | 2026-08-25 11:36 | 2026-08-25 12:08 | 2026-08-25 12:15 | 2026-08-25 12:17 | 2026-08-25 12:17 |  |  | Fair | No | Customer was disconnected for nonpayment, customer was connected with help from escalation
Outage | J.E.26.08.41141 | C001899586 | Eric Williams | KSAN | Completed | Load_261228 | Constant Spring - 210 | 2026-08-25 10:34 | 2026-08-25 10:35 | 2026-08-25 12:55 | 2026-08-25 12:56 | 2026-08-25 13:38 | 2026-08-25 13:47 | 2026-08-25 13:47 | 2026-08-25 13:47 |  |  | Fair | No | Premises found ok.
Outage | J.E.26.08.41173 | C001899589 | Rusean Allen | KSAN | Completed | Load_567709 | Washington Blvd - 310 | 2026-08-25 10:35 | 2026-08-25 10:36 | 2026-08-25 11:12 | 2026-08-25 11:12 | 2026-08-25 11:20 | 2026-08-25 11:29 | 2026-08-25 11:30 | 2026-08-25 11:30 |  |  | Fair | No | Customer asked for disconnection to conduct internal repairs3 drop out switch at transformer was isolated.
Outage | J.E.26.08.41239 | C001899595 | Omar King | St.Ann | Completed | Load_256447 | Roaring River - 210 | 2026-08-25 10:38 | 2026-08-25 10:39 | 2026-08-25 11:30 | 2026-08-25 11:30 | 2026-08-25 11:30 | 2026-08-25 11:30 | 2026-08-25 11:31 | 2026-08-25 11:31 |  |  | Fair | No | Related to recent outage
Outage | J.E.26.08.41272 | C001899596 | Ricky Hall | St.Catherine | Completed | Load_574952 | Tredegar - 310 | 2026-08-25 10:39 | 2026-08-25 10:42 | 2026-08-25 11:53 | 2026-08-25 11:56 | 2026-08-25 12:37 | 2026-08-25 12:41 | 2026-08-25 12:43 | 2026-08-25 12:43 |  |  | Fair | No | Customer advised account was disconnected for nonpayment of bill
Outage | J.E.26.08.41212 | C001899597 | Denton Williams | Portland | Completed | Load_266385 | Port Antonio - 410 | 2026-08-25 10:41 | 2026-08-25 10:42 | 2026-08-25 11:12 | 2026-08-25 11:13 | 2026-08-25 13:28 | 2026-08-25 13:29 | 2026-08-25 13:31 | 2026-08-25 13:31 |  |  | Fair | No | Customer states that no one is home and he does not know if anyone make a call to JPS
Outage | J.E.26.08.39605 | C001899609 | Stephen Taylor | St.Thomas | Completed | Load_252007 | Good Year - 210 | 2026-08-25 10:42 | 2026-08-25 11:01 | 2026-08-25 14:09 | 2026-08-25 14:09 | 2026-08-25 14:09 | 2026-08-25 14:09 | 2026-08-25 14:10 | 2026-08-25 14:10 | BrokenPole |  | Fair | No | Jps secondary pole lean and need to be straightened by the jps maintenance team
Outage | J.E.26.08.41048 | C001899611 | Milton Charlton | KSAN | Completed | Load_266843 | Hope - 410 | 2026-08-25 10:43 | 2026-08-25 11:11 | 2026-08-25 11:23 | 2026-08-25 11:59 | 2026-08-25 11:59 | 2026-08-25 11:55 | 2026-08-25 12:00 | 2026-08-25 12:00 |  |  | EarthMovement | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.41145 | C001899610 | Milton Charlton | KSAN | Completed | Load_250041 | Constant Spring - 410 | 2026-08-25 10:43 | 2026-08-25 11:11 | 2026-08-25 11:27 | 2026-08-25 12:01 | 2026-08-25 12:39 | 2026-08-25 12:40 | 2026-08-25 12:41 | 2026-08-25 12:41 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.41324 | C001899617 | Donald Cunningham | St.Catherine | Completed | Load_568140 | Rhodens Pen - 210 | 2026-08-25 10:49 | 2026-08-25 10:52 | 2026-08-25 12:00 | 2026-08-25 12:01 | 2026-08-25 13:23 | 2026-08-25 14:17 | 2026-08-25 14:43 | 2026-08-25 14:43 |  |  | Fair | No | Broken secondary neural splice and retention using 80 feet of #2aa 1 automatic splice 1#2 preform and 1 clamp for repair
Outage | J.E.26.08.41132 | C001899618 | Kemark Slue | St.Catherine | Completed | Load_244844 | New Michelton - 210 | 2026-08-25 10:50 | 2026-08-25 10:52 | 2026-08-25 11:28 | 2026-08-25 11:29 | 2026-08-25 12:25 | 2026-08-25 13:00 | 2026-08-25 13:50 | 2026-08-25 13:50 | Fire |  | Fair | No | Upon arrival at the location the crew discovered that a 50 kva 13.8 kv transformer fuse was blown resulting from a backhoe that had came in contact with telecommunications cable and cause open secondary conductors to fall from spool and onto secondary rack, anchor sec. conductors to spool, make a jumper for one phase using approximately 2 ft of #4 copper, two one bolt clamps, refuse link and re-energized circuit.
Non-Outage | J.E.26.08.35397 | C001899689 | Oraine Minto | St.Ann | Completed | Load_249153 | Roaring River - 210 | 2026-08-25 11:38 | 2026-08-25 11:39 | 2026-08-25 12:54 | 2026-08-25 12:55 | 2026-08-25 15:45 | 2026-08-25 15:45 | 2026-08-25 15:47 | 2026-08-25 15:47 |  |  | Fair | No | Refer to maintenance Voltage 214v 108v 105v Transformer need to turn up Customer at the end of the secondary low
Non-Outage | J.E.26.08.36277 | C001899688 | Oraine Minto | St.Ann | Completed | Load_267750 | Roaring River - 210 | 2026-08-25 11:38 | 2026-08-25 11:39 | 2026-08-25 16:04 | 2026-08-25 16:24 | 2026-08-25 16:24 | 2026-08-25 16:24 | 2026-08-25 16:25 | 2026-08-25 16:25 |  |  | Fair | No | Premises not found and customer contact not answering
Non-Outage | J.E.26.08.41544 | C001899690 | Oraine Minto | St.Ann | Completed | Load_260616 | Cardiff Hall - 210 | 2026-08-25 11:39 | 2026-08-25 11:39 | 2026-08-25 16:25 | 2026-08-26 11:44 | 2026-08-26 11:44 | 2026-08-26 11:44 | 2026-08-26 11:46 | 2026-08-26 11:46 |  |  | Fair | No | Refer to field service Meter burnt on one side Meter need to change customer replaced the meter socket
Outage | J.E.26.08.41290 | C001899691 | Javid Vernon | Westmoreland | Completed | Load_250249 | Paradise - 110 | 2026-08-25 11:40 | 2026-08-25 15:19 | 2026-08-25 16:08 | 2026-08-25 16:09 | 2026-08-25 16:29 | 2026-08-25 16:51 | 2026-08-25 16:55 | 2026-08-25 16:55 | BrokenPole |  | Fair | No | Check and found one retired JPS pole broken that needs to be removed because broken pole is pulling down and causing damage to customer stancion an it is danger to the community customer needs urgent assistance refer to maintenance
Outage | J.E.26.08.41359 | C001899693 | Oshane Warren | Westmoreland | Completed | Load_265484 | Paradise - 110 | 2026-08-25 11:40 | 2026-08-25 11:42 | 2026-08-25 12:57 | 2026-08-25 12:57 | 2026-08-25 12:57 | 2026-08-25 12:57 | 2026-08-25 13:00 | 2026-08-25 13:00 |  |  | Fair | No | Check and found ok
Outage | J.E.26.08.41447 | C001899694 | Denton Williams | Portland | Completed | Load_262852 | Port Antonio - 410 | 2026-08-25 11:40 | 2026-08-25 11:41 | 2026-08-25 13:28 | 2026-08-25 13:32 | 2026-08-25 14:22 | 2026-08-25 14:22 | 2026-08-25 14:27 | 2026-08-25 14:27 |  |  | Fair | No | Customer is on disconnection for electricity extraction
Outage | J.E.26.08.41514 | C001899695 | Collin Robinson | Portland | Completed | Load_352955 | Port Antonio - 310 | 2026-08-25 11:40 | 2026-08-25 15:16 | 2026-08-25 17:58 | 2026-08-25 17:59 | 2026-08-25 18:46 | 2026-08-25 18:54 | 2026-08-25 18:54 | 2026-08-25 18:54 |  |  | Fair | No | Clear vine from pole transformer and replace 3 amps fuse
Outage | J.E.26.08.41420 | C001899703 | Oshane Warren | St.Elizabeth | Completed | Load_253139 | Maggotty - 110 | 2026-08-25 11:46 | 2026-08-25 15:30 | 2026-08-25 19:32 | 2026-08-25 20:04 | 2026-08-25 20:04 | 2026-08-25 20:04 | 2026-08-25 20:05 | 2026-08-25 20:05 |  |  | Fair | No | Clean corrosion on pathead used 2service connector
Outage | J.E.26.08.41448 | C001899702 | Richard Samuda | Manchester | Completed | Load_246581 | Spur Tree - 310 | 2026-08-25 11:46 | 2026-08-25 11:47 | 2026-08-25 12:04 | 2026-08-25 12:05 | 2026-08-25 13:08 | 2026-08-25 14:02 | 2026-08-25 14:02 | 2026-08-25 14:02 |  |  | Fair | No | Customer was disconnected because of bad debt
Outage | J.E.26.08.41517 | C001899706 | Raheem Ricketts | Manchester | Completed | Load_250749 | Spur Tree - 210 | 2026-08-25 11:48 | 2026-08-25 15:15 | 2026-08-25 15:19 | 2026-08-25 17:00 | 2026-08-25 16:59 | 2026-08-25 17:05 | 2026-08-25 17:20 | 2026-08-25 17:20 |  |  | Fair | No | Check and found customer experiencing internal problems
Outage | J.E.26.08.41454 | C001899716 | Rusean Allen | KSAN | Completed | Load_248785 | Washington Blvd - 710 | 2026-08-25 11:52 | 2026-08-25 11:53 | 2026-08-25 12:37 | 2026-08-25 12:37 | 2026-08-25 13:17 | 2026-08-25 13:34 | 2026-08-25 13:34 | 2026-08-25 13:34 | BrokenWire |  | Fair | No | Broken secondary jumper found, wire was reconnected at pole.
Outage | J.E.26.08.41574 | C001899717 | Eric Williams | KSAN | Completed | Load_244204 | Constant Spring - 410 | 2026-08-25 11:53 | 2026-08-25 11:55 | 2026-08-25 12:18 | 2026-08-25 12:19 | 2026-08-25 12:53 | 2026-08-25 12:54 | 2026-08-25 12:55 | 2026-08-25 12:55 | BrokenPole |  | Fair | No | Private pole on customer property
Outage | J.E.26.08.41713 | C001899737 | Shawn Medley | St.James | Completed | Load_243756 | Queens Drive - 710 | 2026-08-25 12:03 | 2026-08-25 12:04 | 2026-08-25 12:19 | 2026-08-25 12:20 | 2026-08-25 13:35 | 2026-08-25 13:45 | 2026-08-25 13:45 | 2026-08-25 13:45 | Fire |  | Fair | No
Non-Outage | J.E.26.08.41493 | C001899745 | Roemello Brown | Trelawny | Completed | Load_268051 | Duncans - 210 | 2026-08-25 12:10 | 2026-08-25 12:10 | 2026-08-26 11:02 | 2026-08-26 11:03 | 2026-08-26 11:53 | 2026-08-26 11:54 | 2026-08-26 12:37 | 2026-08-26 12:37 |  |  | Fair | No | Corrosion at the pole an the pothead have clamps change at the pole and installed linkets at the pothead Voltage found 118/86Voltage leave 116/118/235
Outage | J.E.26.08.41700 | C001899744 | Clyde Brown | Clarendon | Completed | Load_249266 | May Pen - 110 | 2026-08-25 12:10 | 2026-08-26 07:41 | 2026-08-26 08:17 | 2026-08-26 08:18 | 2026-08-26 09:07 | 2026-08-26 11:04 | 2026-08-26 11:12 | 2026-08-26 11:12 |  |  | Fair | No | Corroded phase for 25kva transformer,open transformer and replaced with 1- clamp ,voltage 115/109 and225V
Outage | J.E.26.08.41613 | C001899752 | Elvis Trowers | KSAS | Completed | Load_242988 | Cane River - 410 | 2026-08-25 12:13 | 2026-08-25 12:19 | 2026-08-25 13:43 | 2026-08-25 13:43 | 2026-08-25 15:12 | 2026-08-25 15:00 | 2026-08-25 15:23 | 2026-08-25 15:23 | BrokenWire |  | Fair | No | Customer meter #2887388 is about 900ft away from main line R.P.D went in the area and cut blown about 400ft of customer wire. Customer is whit out power. Refer to field service.
Outage | J.E.26.08.41267 | C001899755 | Milton Charlton | KSAN | Completed | Load_261317 | Hope - 410 | 2026-08-25 12:17 | 2026-08-25 12:18 | 2026-08-25 12:39 | 2026-08-25 12:43 | 2026-08-25 14:34 | 2026-08-25 14:35 | 2026-08-25 14:44 | 2026-08-25 14:44 |  |  | Fair | No | Bushing single phase distribution line and refused and reclosed 20 amps junction switch and one 3 amps transformer switch using one 20 amps and one 3 amps fuses.
Outage | J.E.26.08.41581 | C001899756 | Elvis Trowers | KSAS | Completed | Load_240364 | Cane River - 410 | 2026-08-25 12:18 | 2026-08-25 12:19 | 2026-08-25 15:23 | 2026-08-25 15:24 | 2026-08-25 15:32 | 2026-08-25 15:35 | 2026-08-25 15:34 | 2026-08-25 15:34 |  |  | Fair | No | R.P.D visit area and cut down about 400ft of customer service wire because customer meter is about 900ft away from main line or open wire secondary. Customer is whit out supply. Refer to field service.
Outage | J.E.26.08.41789 | C001899768 | Milton Charlton | KSAN | Completed | Load_254044 | Hope - 410 | 2026-08-25 12:26 | 2026-08-25 12:28 | 2026-08-25 14:48 | 2026-08-25 14:49 | 2026-08-25 16:08 | 2026-08-25 16:10 | 2026-08-25 16:18 | 2026-08-25 16:18 | BrokenWire |  | Fair | No | 40ft wooden pole broken in motor vehicle accident. Pole has on three primary and neutral and twisted 2/0 secondary.#2 twisted service wire feeding the lane at 79 Barbican Road burn up . Need about 350ft #2 triplex to replace Conductor.
Outage | J.E.26.08.41878 | C001899791 | Rusean Allen | KSAN | Completed | Load_567705 | Washington Blvd - 310 | 2026-08-25 12:40 | 2026-08-25 12:41 | 2026-08-25 13:47 | 2026-08-25 13:48 | 2026-08-25 14:48 | 2026-08-25 14:48 | 2026-08-25 14:49 | 2026-08-25 14:49 |  |  | Fair | No | Premises okay
Outage | J.E.26.08.41173 | C001899793 | Rusean Allen | KSAN | Completed | Load_567709 | Washington Blvd - 310 | 2026-08-25 12:41 | 2026-08-25 12:42 | 2026-08-25 13:08 | 2026-08-25 13:35 | 2026-08-25 13:34 | 2026-08-25 13:35 | 2026-08-25 13:35 | 2026-08-25 13:35 |  |  | Fair | No | 3 drop out switch was re energized
Outage | J.E.26.08.41301 | C001899794 | Elvis Trowers | KSAS | Completed | Load_266544 | Hunts Bay - 310 | 2026-08-25 12:42 | 2026-08-25 12:44 | 2026-08-25 13:21 | 2026-08-25 13:22 | 2026-08-25 13:39 | 2026-08-25 13:20 | 2026-08-25 13:43 | 2026-08-25 13:43 |  |  | Fair | No | Found okay. Customer doing some maintenance on there pothead.
Outage | J.E.26.08.41405 | C001899801 | Eric Williams | KSAS | Completed | Load_579262 | Duhaney - 310 | 2026-08-25 12:43 | 2026-08-25 12:44 | 2026-08-25 13:48 | 2026-08-25 13:48 | 2026-08-25 14:18 | 2026-08-25 14:18 | 2026-08-25 14:18 | 2026-08-25 14:18 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.41408 | C001899800 | Christopher Edwards | KSAN | Completed | Load_260317 | Constant Spring - 310 | 2026-08-25 12:43 | 2026-08-25 12:44 | 2026-08-25 12:57 | 2026-08-25 13:06 | 2026-08-25 13:05 | 2026-08-25 13:29 | 2026-08-25 13:29 | 2026-08-25 13:29 |  |  | Fair | No | Customer was disconnected for late payment Metering department was contacted and supply has returned to premises
Outage | J.E.26.08.41551 | C001899803 | Derrick Grubb | St.Thomas | Completed | Load_243904 | Good Year - 210 | 2026-08-25 12:43 | 2026-08-25 15:38 | 2026-08-25 17:14 | 2026-08-25 17:15 | 2026-08-25 17:14 | 2026-08-25 17:15 | 2026-08-25 17:16 | 2026-08-25 17:16 |  |  | Fair | No | Premises closed several calls to customer phone went unanswered.
Outage | J.E.26.08.41852 | C001899802 | Stephen Taylor | St.Thomas | Completed | Load_577172 | Good Year - 110 | 2026-08-25 12:43 | 2026-08-25 12:46 | 2026-08-25 13:03 | 2026-08-25 13:04 | 2026-08-25 13:33 | 2026-08-25 13:33 | 2026-08-25 13:35 | 2026-08-25 13:35 |  |  | Fair | No | Customer meter is defective and needs to be changed by a technician from Jps reading 111,112,225
Outage | J.E.26.08.41811 | C001899812 | Omar King | St.Ann | Completed | Load_242320 | Upper White River - 210 | 2026-08-25 12:50 | 2026-08-25 12:52 | 2026-08-25 13:06 | 2026-08-25 13:06 | 2026-08-25 14:04 | 2026-08-25 14:04 | 2026-08-25 14:04 | 2026-08-25 14:04 |  |  | Fair | No | Unable to find customer call several times no answer directions not sufficient
Outage | J.E.26.08.41741 | C001899813 | Derrick Dawkins | St.James | Completed | Load_262774 | Bogue - 610 | 2026-08-25 12:51 | 2026-08-25 12:52 | 2026-08-25 17:59 | 2026-08-25 18:20 | 2026-08-25 19:08 | 2026-08-25 18:03 | 2026-08-25 19:12 | 2026-08-25 19:12 |  |  | Fair | No | Check and found premises ok
Outage | J.E.26.08.41281 | C001899817 | Rusean Allen | KSAS | Completed | Load_240320 | Hunts Bay - 210 | 2026-08-25 12:56 | 2026-08-25 13:02 | 2026-08-25 13:35 | 2026-08-25 13:36 | 2026-08-25 13:46 | 2026-08-25 13:47 | 2026-08-25 13:47 | 2026-08-25 13:47 | Fire |  | Fair | No | Premises found locked
Outage | J.E.26.08.42088 | C001899840 | Nickolas Rodriques | St.Catherine | Completed | Load_252827 | Rhodens Pen - 210 | 2026-08-25 13:16 | 2026-08-25 15:41 | 2026-08-25 16:31 | 2026-08-25 16:37 | 2026-08-25 17:56 | 2026-08-25 18:22 | 2026-08-25 18:23 | 2026-08-25 18:23 |  |  | Fair | No | Unable to locate the customer after several attempts. The customer was contacted and stated that he’s not having any issue with his power supply.
Outage | J.E.26.08.42005 | C001899844 | Edward Royal | KSAN | Completed | Load_257312 | Washington Blvd - 310 | 2026-08-25 13:21 | 2026-08-25 13:22 | 2026-08-25 13:49 | 2026-08-25 13:49 | 2026-08-25 13:49 | 2026-08-25 13:49 | 2026-08-25 13:49 | 2026-08-25 13:49 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.42090 | C001899847 | Milton Charlton | KSAN | Completed | Load_255992 | West Kings House - 310 | 2026-08-25 13:22 | 2026-08-25 13:23 | 2026-08-25 16:22 | 2026-08-25 16:32 | 2026-08-25 16:52 | 2026-08-25 16:52 | 2026-08-25 16:54 | 2026-08-25 16:54 | Fire |  | Fair | No | Customer is having an internal problem found defective meter socket and the meter needs too be changed
Outage | J.E.26.08.42209 | C001899858 | Kemark Slue | St.Catherine | Completed | Load_253579 | New Michelton - 310 | 2026-08-25 13:35 | 2026-08-25 13:36 | 2026-08-25 13:50 | 2026-08-25 13:51 | 2026-08-25 13:50 | 2026-08-25 14:42 | 2026-08-25 15:24 | 2026-08-25 15:24 |  | Y | Fair | No | Upon arrival at the location the crew discovered that a 20 amps junction for single phase line section was blown, further patrol revealed that a tree limb was the caused, cut away tree limb, refuse link and re-energized line section.
Outage | J.E.26.08.42085 | C001899859 | Dean- Smith | Hanover | Completed | Load_244632 | Orange Bay - 210 | 2026-08-25 13:36 | 2026-08-25 13:36 | 2026-08-25 15:05 | 2026-08-25 15:06 | 2026-08-25 15:05 | 2026-08-25 15:06 | 2026-08-25 15:06 | 2026-08-25 15:06 | BrokenWire |  | Fair | No | Shift ended
Non-Outage | J.E.26.08.42234 | C001899863 | Edward Royal |  | Completed |  |  | 2026-08-25 13:39 | 2026-08-25 13:40 | 2026-08-25 14:02 | 2026-08-25 14:03 | 2026-08-25 14:26 | 2026-08-25 15:21 | 2026-08-25 15:22 | 2026-08-25 15:22 | Fire |  | Fair | No | Tension secondary line using 3 number 2 perform 3 single bolt clamp
Outage | J.E.26.08.42037 | C001899868 | Wayne Dillion | Manchester | Completed | Load_262788 | Spur Tree - 210 | 2026-08-25 13:44 | 2026-08-25 13:47 | 2026-08-25 14:03 | 2026-08-25 14:03 | 2026-08-25 14:03 | 2026-08-25 14:04 | 2026-08-25 14:04 | 2026-08-25 14:04 | LowHangingWires |  | Fair | No | Defective pole in area wires cannot be retention. Maintenance already know about this issue.
Outage | J.E.26.08.42301 | C001899869 | Ricky Hall | St.Catherine | Completed | Load_250201 | Tredegar - 410 | 2026-08-25 13:45 | 2026-08-25 13:45 | 2026-08-25 14:22 | 2026-08-25 14:22 | 2026-08-25 14:39 | 2026-08-25 15:00 | 2026-08-25 15:00 | 2026-08-25 15:00 | BrokenWire |  | Fair | No | No broken wire seen
Outage | J.E.26.08.41288 | C001899880 | Derrick Dawkins | St.James | Completed | Load_241713 | Bogue - 610 | 2026-08-25 14:00 | 2026-08-25 14:00 | 2026-08-25 16:28 | 2026-08-25 16:31 | 2026-08-25 16:50 | 2026-08-25 16:57 | 2026-08-25 17:53 | 2026-08-25 17:53 |  |  | Fair | No | Customer said that the problem was already resolved
Outage | J.E.26.08.42051 | C001899885 | Roxroy Needham | St.Ann | Completed | Load_252510 | Cardiff Hall - 210 | 2026-08-25 14:03 | 2026-08-25 15:40 | 2026-08-25 17:04 | 2026-08-25 17:05 | 2026-08-25 17:05 | 2026-08-25 17:05 | 2026-08-25 17:06 | 2026-08-25 17:06 |  |  | Fair | No | Customer say issue was resolved
Outage | J.E.26.08.41353 | C001899900 | Derrick Dawkins | St.James | Completed | Load_261201 | Bogue - 610 | 2026-08-25 14:17 | 2026-08-25 14:18 | 2026-08-25 16:27 | 2026-08-25 20:06 | 2026-08-25 20:58 | 2026-08-25 20:58 | 2026-08-25 21:00 | 2026-08-25 21:00 |  |  | Fair | No | Check and found area ok
Non-Outage | J.E.26.08.42372 | C001899907 | Derrick Dawkins |  | Completed |  |  | 2026-08-25 14:18 | 2026-08-25 14:18 | 2026-08-25 16:45 | 2026-08-25 17:53 | 2026-08-25 17:53 | 2026-08-25 17:43 | 2026-08-25 17:58 | 2026-08-25 17:58 |  |  | Fair | No | Check and found ok customer has internal problem voltage found 118/119/237
Non-Outage | J.E.26.08.41412 | C001899920 | Locksley Allen | St.Mary | Completed | Load_351648 | Oracabessa - 110 | 2026-08-25 14:28 | 2026-08-25 14:29 | 2026-08-26 11:35 | 2026-08-26 12:01 | 2026-08-26 12:00 | 2026-08-26 12:23 | 2026-08-26 12:23 | 2026-08-26 12:23 |  |  | Fair | No | Pothead found corroded. Clean up pothead and install 2 clamps Voltage at meter socket phase to phase 241v. Phase to neutral 119&117vMeter left working okay
Non-Outage | J.E.26.08.41434 | C001899921 | Locksley Allen | St.Mary | Completed | Load_269770 | Blackstonedge - 110 | 2026-08-25 14:28 | 2026-08-25 14:29 | 2026-08-26 13:04 | 2026-08-26 14:54 | 2026-08-26 14:54 | 2026-08-26 14:57 | 2026-08-26 14:56 | 2026-08-26 14:56 |  |  | Fair | No | Need better direction and customer not answering the phone
Non-Outage | J.E.26.08.41702 | C001899922 | Locksley Allen | St.Mary | Completed | Load_246610 | Oracabessa - 110 | 2026-08-25 14:28 | 2026-08-25 14:29 | 2026-08-26 12:50 | 2026-08-26 12:50 | 2026-08-26 12:50 | 2026-08-26 12:58 | 2026-08-26 12:55 | 2026-08-26 12:55 |  |  | Fair | No | No low voltage problem found at premises at present. Several customers in this area is complaining about low voltage. Please check transformer
Outage | J.E.26.08.41790 | C001899947 | Raheem Ricketts | Manchester | Completed | Load_249751 | Spur Tree - 210 | 2026-08-25 15:07 | 2026-08-25 15:12 | 2026-08-25 15:19 | 2026-08-25 15:22 | 2026-08-25 15:22 | 2026-08-25 15:23 | 2026-08-25 15:23 | 2026-08-25 15:23 |  |  | Fair | No | Check and found okay customer says she didn’t make any report an power is at home
Outage | J.E.26.08.42077 | C001899949 | Raheem Ricketts | Manchester | Completed | Load_262725 | Spur Tree - 210 | 2026-08-25 15:07 | 2026-08-25 15:12 | 2026-08-25 15:19 | 2026-08-25 15:36 | 2026-08-25 16:37 | 2026-08-25 16:39 | 2026-08-25 16:39 | 2026-08-25 16:39 | BrokenWire |  | Fair | No | Change customer neutral clamp at pole using one clamp voltage left 110,110,220
Outage | J.E.26.08.42529 | C001899948 | Raheem Ricketts | St.Elizabeth | Completed | Load_248202 | Maggotty - 210 | 2026-08-25 15:07 | 2026-08-25 15:12 | 2026-08-25 15:19 | 2026-08-25 18:02 | 2026-08-25 18:13 | 2026-08-25 18:16 | 2026-08-25 18:16 | 2026-08-25 18:16 |  |  | Fair | No | Unable to get back to customer after we spoke however Check and found transformer trip reset 25kva
Outage | J.E.26.08.40909 | C001899971 | Collin Robinson | Portland | Completed | Load_249793 | Port Antonio - 310 | 2026-08-25 15:14 | 2026-08-25 15:15 | 2026-08-25 16:16 | 2026-08-25 16:16 | 2026-08-25 17:21 | 2026-08-25 17:42 | 2026-08-25 17:44 | 2026-08-25 17:44 | BrokenWire |  | Fair | No | Entangle open secondary conductor and replace 3 amps fuse
Outage | J.E.26.08.42559 | C001899970 | Collin Robinson | Portland | Completed | Load_263585 | Port Antonio - 410 | 2026-08-25 15:14 | 2026-08-25 15:15 | 2026-08-25 15:30 | 2026-08-25 15:31 | 2026-08-25 16:08 | 2026-08-25 16:11 | 2026-08-25 16:11 | 2026-08-25 16:11 |  |  | Fair | No | Premises found with supply
Outage | J.E.26.08.42553 | C001899972 | Raheem Ricketts | St.Elizabeth | Completed | Load_254651 | Maggotty - 210 | 2026-08-25 15:15 | 2026-08-25 15:18 | 2026-08-25 17:50 | 2026-08-25 17:51 | 2026-08-25 17:50 | 2026-08-25 17:52 | 2026-08-25 17:52 | 2026-08-25 17:52 |  |  | Fair | No | Check and found okay customer says power was restored from earlier today
Outage | J.E.26.08.41859 | C001899990 | Javid Vernon | Westmoreland | Completed | Load_258837 | Paradise - 210 | 2026-08-25 15:22 | 2026-08-25 15:24 | 2026-08-25 16:04 | 2026-08-25 16:07 | 2026-08-25 16:07 | 2026-08-25 16:07 | 2026-08-25 16:08 | 2026-08-25 16:08 |  |  | Fair | No | Customer stated that the power was restored
Outage | J.E.26.08.41113 | C001899991 | Javid Vernon | Westmoreland | Completed | Load_292237 | Paradise - 110 | 2026-08-25 15:23 | 2026-08-25 15:24 | 2026-08-25 16:04 | 2026-08-25 16:06 | 2026-08-25 16:06 | 2026-08-25 16:06 | 2026-08-25 16:07 | 2026-08-25 16:07 |  |  | Fair | No | Customer stated that the power was restored
Outage | J.E.26.08.41119 | C001899992 | Javid Vernon | Westmoreland | Completed | Load_292222 | Paradise - 210 | 2026-08-25 15:23 | 2026-08-25 15:24 | 2026-08-25 16:04 | 2026-08-25 16:05 | 2026-08-25 16:05 | 2026-08-25 16:05 | 2026-08-25 16:06 | 2026-08-25 16:06 |  |  | Fair | No | Customer stated that the power was restored
Outage | J.E.26.08.40644 | C001900001 | Christopher West | Portmore | Completed | Load_244738 | Naggo Head - 610 | 2026-08-25 15:27 | 2026-08-25 15:30 | 2026-08-25 18:30 | 2026-08-25 18:30 | 2026-08-25 19:11 | 2026-08-25 19:12 | 2026-08-25 19:12 | 2026-08-25 19:12 |  |  | Fair | No | Premises found closed at time of visit.
Outage | J.E.26.08.41230 | C001899999 | Christopher West | Portmore | Completed | Load_270138 | Naggo Head - 610 | 2026-08-25 15:27 | 2026-08-25 15:30 | 2026-08-25 16:43 | 2026-08-25 16:43 | 2026-08-25 17:46 | 2026-08-25 18:23 | 2026-08-25 18:30 | 2026-08-25 18:30 |  |  | Fair | No | Customer had a defective meter socket due to a slack connection which in turn burnt the 2 wire meter, socket was replaced by an electrician, kWh meter was replaced, V/R 117v, customer now ok.
Outage | J.E.26.08.42493 | C001900000 | Christopher West | St.Catherine | Completed | Load_267556 | Twickenham - 210 | 2026-08-25 15:27 | 2026-08-25 15:30 | 2026-08-25 15:54 | 2026-08-25 15:55 | 2026-08-25 16:42 | 2026-08-25 16:42 | 2026-08-25 16:42 | 2026-08-25 16:42 |  |  | Fair | No | Not located, calls made to number provided were unanswered.
Non-Outage | J.E.26.08.36293 | C001900007 | Christopher West | Portmore | Completed | Load_248203 | Naggo Head - 510 | 2026-08-25 15:28 | 2026-08-25 15:30 | 2026-08-25 22:07 | 2026-08-25 22:08 | 2026-08-25 22:29 | 2026-08-25 22:30 | 2026-08-25 22:32 | 2026-08-25 22:32 |  |  | Fair | No | Premises closed
Non-Outage | J.E.26.08.41007 | C001900006 | Christopher West | Portmore | Completed | Load_253799 | Naggo Head - 510 | 2026-08-25 15:28 | 2026-08-25 15:30 | 2026-08-25 19:56 | 2026-08-25 19:57 | 2026-08-25 20:39 | 2026-08-25 21:15 | 2026-08-25 21:21 | 2026-08-25 21:21 |  |  | Fair | No | 3 wire had a burnt neutral connection, phase connections were corroded as well as the connections at pole, used 3 pen unions and 3 clamps for repairs, V/R 116v x2 232v, customer now okay however, customer is complaining of damaged equipment, customer was advised accordingly.
Non-Outage | J.E.26.08.41274 | C001900005 | Christopher West | Portmore | Completed | Load_240059 | Naggo Head - 510 | 2026-08-25 15:28 | 2026-08-25 15:30 | 2026-08-25 19:56 | 2026-08-25 21:22 | 2026-08-25 21:57 | 2026-08-25 22:03 | 2026-08-25 22:07 | 2026-08-25 22:07 |  |  | Fair | No | Premises found closed at time of visit.
Non-Outage | J.E.26.08.41512 | C001900004 | Christopher West | Portmore | Completed | Load_230005 | Naggo Head - 610 | 2026-08-25 15:28 | 2026-08-25 15:30 | 2026-08-25 19:13 | 2026-08-25 19:14 | 2026-08-25 19:46 | 2026-08-25 19:56 | 2026-08-25 19:56 | 2026-08-25 19:56 |  |  | Fair | No | From directions given, the last White House on right is lot # 5, calls made to number provided were unanswered.
Non-Outage | J.E.26.08.38175 | C001900009 | Oshane Warren | Westmoreland | Completed | Load_249902 | Paradise - 310 | 2026-08-25 15:30 | 2026-08-25 15:32 | 2026-08-25 16:23 | 2026-08-25 16:24 | 2026-08-25 20:01 | 2026-08-25 20:02 | 2026-08-25 20:02 | 2026-08-25 20:02 |  |  | Fair | No | Internal problem advice to fix
Non-Outage | J.E.26.08.34234 | C001900010 | Raheem Ricketts |  | Completed |  |  | 2026-08-25 15:31 | 2026-08-25 15:32 | 2026-08-25 16:43 | 2026-08-25 16:43 | 2026-08-25 16:43 | 2026-08-25 16:44 | 2026-08-25 16:44 | 2026-08-25 16:44 | Fire |  | Fair | No | Unable to locate customer cell number went straight voicemail
Non-Outage | J.E.26.08.12993 | C001900018 | Elvis Trowers | KSAS | Completed | Load_240902 | Cane River - 410 | 2026-08-25 15:32 | 2026-08-25 15:34 | 2026-08-25 15:43 | 2026-08-25 15:44 | 2026-08-25 16:40 | 2026-08-25 16:20 | 2026-08-25 16:42 | 2026-08-25 16:42 |  |  | Fair | No | Found okay upon arrival. Customer states matter was resolved.
Non-Outage | J.E.26.08.21166 | C001900020 | Elvis Trowers | KSAS | Completed | Load_1003913 | Cane River - 410 | 2026-08-25 15:32 | 2026-08-25 15:34 | 2026-08-25 16:42 | 2026-08-25 16:43 | 2026-08-25 17:05 | 2026-08-25 17:06 | 2026-08-25 17:08 | 2026-08-25 17:08 | BrokenWire |  | Fair | No | Customer service wire #6 triplex neutral and phase broken in mid span . Lower splice and retention using four 1- bolt clamps and 6ft #6 triplex wire.
Outage | J.E.26.08.36604 | C001900016 | Damion Reid | Manchester | Completed | Load_241983 | Kendal - 210 | 2026-08-25 15:32 | 2026-08-25 15:33 | 2026-08-25 15:43 | 2026-08-25 15:44 | 2026-08-25 17:32 | 2026-08-25 18:04 | 2026-08-25 18:05 | 2026-08-25 18:05 | BrokenWire |  | Fair | No | Broken service neutral found for 3 wire service cause by vehicle accident remade broken neutral using one 1 bolt clamp
Outage | J.E.26.08.40073 | C001900017 | Damion Reid | Manchester | Completed | Load_264039 | Kendal - 210 | 2026-08-25 15:32 | 2026-08-25 15:33 | 2026-08-25 21:02 | 2026-08-25 21:02 | 2026-08-25 21:26 | 2026-08-25 21:33 | 2026-08-25 21:35 | 2026-08-25 21:35 |  |  | Fair | No | Area found ok call related to one done at coley Vill earlier
Non-Outage | J.E.26.08.04387 | C001900025 | Elvis Trowers | KSAS | Completed | Load_556657 | Cane River - 410 | 2026-08-25 15:33 | 2026-08-25 15:34 | 2026-08-25 17:13 | 2026-08-25 17:13 | 2026-08-25 17:34 | 2026-08-25 17:40 | 2026-08-25 17:58 | 2026-08-25 17:58 |  |  | Fair | No | Found okay upon arrival. Readings at meter socket 114-113-228 volts.
Non-Outage | J.E.26.08.09962 | C001900021 | Elvis Trowers | KSAS | Completed | Load_237680 | Cane River - 410 | 2026-08-25 15:33 | 2026-08-25 15:34 | 2026-08-25 17:58 | 2026-08-25 17:59 | 2026-08-25 18:31 | 2026-08-25 18:35 | 2026-08-25 18:33 | 2026-08-25 18:33 |  |  | Fair | No | Found okay upon arrival. Customer states matter was resolved.
Non-Outage | J.E.26.08.12074 | C001900023 | Elvis Trowers | KSAS | Completed | Load_263100 | Cane River - 410 | 2026-08-25 15:33 | 2026-08-25 15:34 | 2026-08-25 18:34 | 2026-08-25 18:34 | 2026-08-25 18:42 | 2026-08-25 18:45 | 2026-08-25 18:43 | 2026-08-25 18:43 |  |  | Fair | No | Customer fed from hexing box and getting on and off supply from the box . Refer to field service.
Non-Outage | J.E.26.08.41389 | C001900029 | Kenroy Dale | Manchester | Completed | Load_263928 | Spur Tree - 310 | 2026-08-25 15:33 | 2026-08-25 15:34 | 2026-08-25 18:12 | 2026-08-25 18:13 | 2026-08-25 19:27 | 2026-08-25 19:50 | 2026-08-25 19:51 | 2026-08-25 19:51 | BrokenPole |  | Fair | No | Dead end secondary pole found broken, maintenance already aware
Outage | J.E.26.08.42461 | C001900030 | Cliton Henry | St.Mary | Completed | Load_263198 | Oracabessa - 210 | 2026-08-25 15:33 | 2026-08-25 15:36 | 2026-08-25 15:44 | 2026-08-25 15:44 | 2026-08-25 16:13 | 2026-08-25 16:55 | 2026-08-25 16:58 | 2026-08-25 16:58 | LowHangingWires |  | Fair | No | The secondary lower phase conductor found entangled with Flow cables. A 15 kva transformer was de energized to carryout repairs. Corrective work done to retensioned 1- span of secondary conductors. The supply was restored to energized the 15 kva transformer..
Outage | J.E.26.08.41987 | C001900031 | Romaine Roberts | St.Mary | Completed | Load_352260 | Annotto Bay - 210 | 2026-08-25 15:34 | 2026-08-25 15:41 | 2026-08-25 16:59 | 2026-08-25 17:00 | 2026-08-25 17:59 | 2026-08-25 18:01 | 2026-08-25 18:02 | 2026-08-25 18:02 |  |  | Fair | No | Junction fuse found blown patrol line nothing found replace 30 amp power restore no pole number at location
Outage | J.E.26.08.42368 | C001900032 | Romaine Roberts | St.Mary | Completed | Load_249545 | Annotto Bay - 210 | 2026-08-25 15:34 | 2026-08-25 15:41 | 2026-08-25 18:02 | 2026-08-25 18:03 | 2026-08-25 18:03 | 2026-08-25 18:03 | 2026-08-25 18:04 | 2026-08-25 18:04 |  |  | Fair | No | Junction fuse found blown patrol line nothing found replace 30 amp power restore no pole number at location
Outage | J.E.26.08.42328 | C001900035 | Derrick Grubb | St.Thomas | Completed | Load_577217 | Good Year - 210 | 2026-08-25 15:35 | 2026-08-25 15:37 | 2026-08-25 19:17 | 2026-08-25 19:18 | 2026-08-25 19:39 | 2026-08-25 20:06 | 2026-08-25 20:07 | 2026-08-25 20:07 |  |  | Fair | No | Patrol, found no visible faults on the line and refuse one 15amp junction at pole number 0208722. Power restored.
Outage | J.E.26.08.42645 | C001900037 | Derrick Grubb | St.Thomas | Completed | Load_249913 | Good Year - 110 | 2026-08-25 15:35 | 2026-08-25 15:37 | 2026-08-25 16:22 | 2026-08-25 16:23 | 2026-08-25 16:36 | 2026-08-25 17:00 | 2026-08-25 17:00 | 2026-08-25 17:00 |  |  | Fair | No | Troubleshoot and found service wire corroded at pole. Clear corrosion using a one bolt clamp. Voltage reading when leaving 112v.
Outage | J.E.26.08.42899 | C001900034 | Damion Reid | Manchester | Completed | Load_242079 | Kendal - 210 | 2026-08-25 15:35 | 2026-08-25 15:36 | 2026-08-25 18:06 | 2026-08-25 18:07 | 2026-08-25 18:12 | 2026-08-25 20:54 | 2026-08-25 20:59 | 2026-08-25 20:59 |  |  | Fair | No | 65amp trip saver found down cause by primary phase conductor lodge against bolt cable pole release conductor and reset trip saver
Outage | J.E.26.08.42555 | C001900039 | Horace Malcolm | St.James | Completed | Load_244479 | Queens Drive - 810 | 2026-08-25 15:36 | 2026-08-25 23:18 | 2026-08-26 03:44 | 2026-08-26 03:45 | 2026-08-26 04:03 | 2026-08-26 04:08 | 2026-08-26 04:09 | 2026-08-26 04:09 |  |  | Fair | No | Unable to locate premises
Outage | J.E.26.08.42818 | C001900044 | Roxroy Needham | St.Ann | Completed | Load_263703 | Cardiff Hall - 210 | 2026-08-25 15:37 | 2026-08-25 15:39 | 2026-08-25 23:53 | 2026-08-25 23:54 | 2026-08-26 00:28 | 2026-08-26 00:33 | 2026-08-26 00:34 | 2026-08-26 00:34 |  |  | Fair | No | Replace a 8 amps junction fuse at pole # 574206
Outage | J.E.26.08.41991 | C001900051 | Edward Royal | KSAS | Completed | Load_245717 | Duhaney - 310 | 2026-08-25 15:42 | 2026-08-25 15:43 | 2026-08-25 21:40 | 2026-08-25 21:40 | 2026-08-25 21:40 | 2026-08-25 21:42 | 2026-08-25 21:42 | 2026-08-25 21:42 |  |  | Fair | No | Replaced 20A junction fuse pole 603646
Outage | J.E.26.08.42276 | C001900050 | Edward Royal | KSAN | Completed | Load_256268 | Constant Spring - 210 | 2026-08-25 15:42 | 2026-08-25 15:43 | 2026-08-25 16:50 | 2026-08-25 16:50 | 2026-08-25 16:50 | 2026-08-25 20:53 | 2026-08-25 20:55 | 2026-08-25 20:55 |  |  | Fair | No | Spliced and reconnected secondary quad using 6 single bolt clamp
Outage | J.E.26.08.42882 | C001900049 | Edward Royal | KSAN | Completed | Load_574897 | Washington Blvd - 610 | 2026-08-25 15:42 | 2026-08-25 15:43 | 2026-08-25 16:29 | 2026-08-25 16:29 | 2026-08-25 16:29 | 2026-08-25 16:29 | 2026-08-25 16:30 | 2026-08-25 16:30 |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.08.33585 | C001900056 | Nickolas Rodriques | St.Catherine | Completed | Load_238202 | Rhodens Pen - 410 | 2026-08-25 15:44 | 2026-08-25 15:45 | 2026-08-25 21:10 | 2026-08-25 21:11 | 2026-08-25 22:03 | 2026-08-25 22:38 | 2026-08-25 22:45 | 2026-08-25 22:45 | Fire |  | Fair | No | Unable to communicate with the customer after several attempts. The area was patrolled and no fire on pole was seen.
Non-Outage | J.E.26.08.42275 | C001900054 | Nickolas Rodriques | St.Catherine | Completed | Load_556353 | Rhodens Pen - 210 | 2026-08-25 15:44 | 2026-08-25 15:45 | 2026-08-25 18:26 | 2026-08-25 18:29 | 2026-08-25 18:57 | 2026-08-25 19:14 | 2026-08-25 19:17 | 2026-08-25 19:17 |  |  | Fair | No | Checked and found customer single phasing (114). All necessary checks were done which revealed that the issue is stemming from the EG box (EG 05043). Refer to field service.
Outage | J.E.26.08.42404 | C001900053 | Andre Williams | Trelawny | Completed | Load_259574 | Greenwood - 110 | 2026-08-25 15:44 | 2026-08-25 15:51 | 2026-08-25 15:56 | 2026-08-25 16:21 | 2026-08-25 17:36 | 2026-08-25 17:38 | 2026-08-25 17:40 | 2026-08-25 17:40 |  |  | Fair | No | Patrol line section close 40 amp main fuse on 3 phase line ( switch bracket defective adjust switch barel to compensate for issue to fit barrels in switch bracket ) reffer to maintenance switch pole at dumfries square
Outage | J.E.26.08.42561 | C001900057 | Andre Williams | Trelawny | Completed | Load_556059 | Martha Brae - 110 | 2026-08-25 15:46 | 2026-08-25 15:51 | 2026-08-25 18:48 | 2026-08-25 18:49 | 2026-08-25 20:36 | 2026-08-25 20:42 | 2026-08-25 20:42 | 2026-08-25 20:42 |  |  | Fair | No | Open bank of 3 transformer to isolate meter at sewage plant 4 wire meter socket burnt as well as meter, technician was advice to replace meter socket before contacting for replacement meter, reffer to field service to contact customer to install new meter after repairs are done. ( conection type 120/240/208 )
Outage | J.E.26.08.42689 | C001900058 | Andre Williams | Trelawny | Completed | Load_247755 | Martha Brae - 210 | 2026-08-25 15:46 | 2026-08-25 15:51 | 2026-08-25 20:44 | 2026-08-25 20:59 | 2026-08-25 20:59 | 2026-08-25 21:01 | 2026-08-25 21:01 | 2026-08-25 21:01 |  |  | Fair | No | Premises not found need more directions to locate individual customer
Non-Outage | J.E.26.08.39584 | C001900060 | Richard Grant | St.Catherine | Completed | Load_250825 | New Michelton - 210 | 2026-08-25 15:48 | 2026-08-25 15:50 | 2026-08-25 18:35 | 2026-08-25 19:15 | 2026-08-25 19:55 | 2026-08-25 20:40 | 2026-08-25 20:40 | 2026-08-25 20:40 |  |  | Fair | No | Low voltage found at premises caused by corrosion at pothead and at pole. 3 onebolt clamps and 3 penunions used to correct faults. Further checks revealed customer also had internal issues. Customer was advised. 114 114 228 voltages left at premises. Premises left okay.
Outage | J.E.26.08.42587 | C001900059 | Richard Grant | St.Catherine | Completed | Load_260475 | New Michelton - 210 | 2026-08-25 15:48 | 2026-08-25 15:50 | 2026-08-25 16:14 | 2026-08-25 16:15 | 2026-08-25 18:03 | 2026-08-25 19:15 | 2026-08-25 19:15 | 2026-08-25 19:15 |  |  | Fair | No | 25amps fuse found blown at 3 phase junction pole caused by defective 25kva transformer. 25amps fuse replaced with same and supply restored in area. Kindly send email to A Murray to have 25kva transformer replaced. Multiple customers left without supply
Non-Outage | J.E.26.08.33386 | C001900062 | Richard Grant | St.Catherine | Completed | Load_257579 | New Michelton - 210 | 2026-08-25 15:49 | 2026-08-25 15:50 | 2026-08-26 17:51 | 2026-08-26 17:52 | 2026-08-26 18:23 | 2026-08-26 18:52 | 2026-08-26 18:52 | 2026-08-26 18:52 |  |  | Fair | No | Defective meter found at premises caused by slack connections in meter socket. Meter socket replaced by customer, defective meter #2499730 replaced with new meter #3023455 and supply restored. Premises left okay.
Non-Outage | J.E.26.08.33447 | C001900063 | Richard Grant | St.Catherine | Completed | Load_262168 | New Michelton - 210 | 2026-08-25 15:49 | 2026-08-25 15:50 | 2026-08-25 18:35 | 2026-08-25 20:41 | 2026-08-25 21:41 | 2026-08-25 21:56 | 2026-08-25 21:56 | 2026-08-25 21:56 |  |  | Fair | No | Corroded neural joint found at pothead and wrapped on. 2 penunions used to correct faults. 114 114 228 voltages left at premises. Premises left okay
Non-Outage | J.E.26.08.41319 | C001900065 | Daniel Francis |  | Completed |  |  | 2026-08-25 15:49 | 2026-08-25 16:38 | 2026-08-25 17:11 | 2026-08-25 17:12 | 2026-08-25 18:11 | 2026-08-25 18:35 | 2026-08-25 18:39 | 2026-08-25 18:39 |  |  | Fair | No | Replace transformer fuse 1amp 10 kva
Outage | J.E.26.08.42085 | C001900073 | Tajay Bernard | Hanover | Completed | Load_244632 | Orange Bay - 210 | 2026-08-25 15:53 | 2026-08-25 15:53 | 2026-08-25 16:33 | 2026-08-25 16:35 | 2026-08-25 17:28 | 2026-08-25 18:21 | 2026-08-25 18:22 | 2026-08-25 18:22 | BrokenWire |  | Fair | No | Isolate 100kva transformer at pole #013882 to splice and retention 1 pole span of secondary neutral, 3 splicing sleeves was used
Non-Outage | J.E.26.08.42428 | C001900074 | Romaine Roberts | St.Mary | Completed | Load_257745 | Highgate - 210 | 2026-08-25 15:54 | 2026-08-25 15:56 | 2026-08-25 20:06 | 2026-08-25 20:06 | 2026-08-25 21:01 | 2026-08-25 21:16 | 2026-08-25 21:16 | 2026-08-25 21:16 | Fire |  | Fair | No
Outage | J.E.26.08.42476 | C001900075 | Fitzroy Turner | KSAN | Completed | Load_258426 | Washington Blvd - 310 | 2026-08-25 15:54 | 2026-08-25 15:56 | 2026-08-25 16:34 | 2026-08-25 16:34 | 2026-08-25 18:26 | 2026-08-25 18:26 | 2026-08-25 18:30 | 2026-08-25 18:30 | BrokenPole |  | Fair | No | Found tree wire service burst down by garbage truck along with pothead.customer advised to get electrician to carry out repair.customer still have supply
Non-Outage | J.E.26.08.33239 | C001900080 | Hartley Chin | Clarendon | Completed | Load_264051 | Parnassus - 310 | 2026-08-25 15:56 | 2026-08-25 15:58 | 2026-08-25 18:12 | 2026-08-25 21:33 | 2026-08-25 21:35 | 2026-08-25 21:35 | 2026-08-25 21:35 | 2026-08-25 21:35 |  |  | Fair | No | Found okay …. Voltage read 115v , 113v …
Non-Outage | J.E.26.08.33544 | C001900079 | Hartley Chin | Clarendon | Completed | Load_242599 | Parnassus - 310 | 2026-08-25 15:56 | 2026-08-25 15:58 | 2026-08-25 17:25 | 2026-08-25 17:26 | 2026-08-25 17:26 | 2026-08-25 17:26 | 2026-08-25 17:27 | 2026-08-25 17:27 |  |  | Fair | No | Customer stated issue was resolved..
Outage | J.E.26.08.40964 | C001900078 | Fitzroy Turner | KSAS | Completed | Load_243671 | Greenwich - 510 | 2026-08-25 15:56 | 2026-08-25 15:57 | 2026-08-25 18:30 | 2026-08-25 18:31 | 2026-08-25 19:01 | 2026-08-25 19:01 | 2026-08-25 19:05 | 2026-08-25 19:05 | LeaningPole |  | Fair | No | Found #2 triplex having low and customer premises customer advised to have electrician to carry out repair and service wire needs pole in middle of premises and tree to cut off wires
Outage | J.E.26.08.42319 | C001900076 | Hartley Chin | Clarendon | Completed | Load_245925 | May Pen - 210 | 2026-08-25 15:56 | 2026-08-25 15:58 | 2026-08-25 16:46 | 2026-08-25 18:17 | 2026-08-25 18:17 | 2026-08-25 18:52 | 2026-08-25 18:53 | 2026-08-25 18:53 |  | Y | Fair | No | Isolate 3 of 3 junction @ pole # 0210858 to cut tree from line , cute tree from line , refused 15 amp junction @ pole # 146132 … re-energized 3 of 3 junction …
Non-Outage | J.E.26.08.32430 | C001900086 | Hartley Chin | Clarendon | Completed | Load_243050 | Parnassus - 310 | 2026-08-25 15:57 | 2026-08-25 15:58 | 2026-08-25 17:29 | 2026-08-25 17:30 | 2026-08-25 17:45 | 2026-08-25 17:45 | 2026-08-25 17:45 | 2026-08-25 17:45 | BrokenWire |  | Fair | No | Found okay … voltage read 112 v , 113v .
Non-Outage | J.E.26.08.33018 | C001900083 | Hartley Chin | Clarendon | Completed | Load_264303 | Parnassus - 310 | 2026-08-25 15:57 | 2026-08-25 15:58 | 2026-08-25 16:44 | 2026-08-25 17:48 | 2026-08-25 17:54 | 2026-08-25 18:05 | 2026-08-25 18:06 | 2026-08-25 18:06 |  |  | Fair | No | Customer stated supply was restored..
Non-Outage | J.E.26.08.42273 | C001900089 | Hartley Chin | Clarendon | Completed | Load_263004 | Monymusk - 310 | 2026-08-25 15:57 | 2026-08-25 15:58 | 2026-08-25 20:35 | 2026-08-25 20:36 | 2026-08-25 20:35 | 2026-08-25 20:54 | 2026-08-25 21:10 | 2026-08-25 21:10 |  |  | SevereWind | No | Found 1 of 3 blown 3 amp fuse on 25 KVA transformer (bank of 3) no pole # , line patrolled and found okay , transformer refused… Voltage read 239v , 236v , 238v ..
Non-Outage | J.E.26.08.36358 | C001900099 | Error Coore | Manchester | Completed | Load_268967 | Porus - 310 | 2026-08-25 16:04 | 2026-08-25 16:05 | 2026-08-25 18:17 | 2026-08-25 18:18 | 2026-08-25 18:17 | 2026-08-25 18:17 | 2026-08-25 18:20 | 2026-08-25 18:20 |  |  | Fair | No | Premises found ok voltage reading 115/115/230 volts however found customer meter and meter socket burn customer have internal problem
Non-Outage | J.E.26.08.32622 | C001900104 | Romeo Brissett | St.James | Completed | Load_264461 | Bogue - 310 | 2026-08-25 16:07 | 2026-08-25 16:08 | 2026-08-25 17:03 | 2026-08-25 17:04 | 2026-08-25 17:03 | 2026-08-25 19:28 | 2026-08-25 20:02 | 2026-08-25 20:02 |  |  | Fair | No | Troubleshooted and found transformer circuit overload, secondary joint was changed, secondary circuit is extended too far from transformer pole, during the daytime power is up however by peak hours the voltage drop severely, transformer is found and left at top 4, V/R at transformer pole 122-123-245, amperage is fluctuating between 219-222 top phase, bottom phase 217-225 and neutral 38.7-43.6, Voltage readings At the middle of the line, 5 Pole span from transformer pole is 107-111-219, amperage is fluctuating between 71.4.5-81.3 top phase, 91.7-112.3 bottom phase and neutral is13.59-14.7. Please send to maintenance.
Non-Outage | J.E.26.08.43375 | C001900125 | Derrick Grubb | St.Thomas | Completed | Load_258585 | Good Year - 210 | 2026-08-25 16:21 | 2026-08-25 16:23 | 2026-08-25 17:03 | 2026-08-25 17:03 | 2026-08-25 17:11 | 2026-08-25 17:12 | 2026-08-25 17:12 | 2026-08-25 17:12 |  |  | Fair | No | Contact customer by phone and customer said this is an old report.
Non-Outage | J.E.26.08.41550 | C001900134 | Raheem Ricketts |  | Completed |  |  | 2026-08-25 16:24 | 2026-08-25 16:29 | 2026-08-25 17:54 | 2026-08-25 17:54 | 2026-08-25 17:58 | 2026-08-25 18:00 | 2026-08-25 18:01 | 2026-08-25 18:01 |  |  | Fair | No | Unable to locate customer phone number is or of service
Outage | J.E.26.08.42616 | C001900133 | Raheem Ricketts | Manchester | Completed | Load_258771 | Spur Tree - 210 | 2026-08-25 16:24 | 2026-08-25 16:29 | 2026-08-25 17:46 | 2026-08-25 17:46 | 2026-08-25 17:48 | 2026-08-25 17:49 | 2026-08-25 17:50 | 2026-08-25 17:50 |  |  | Fair | No | Phone number went straight voicemail After several calls
Non-Outage | J.E.26.08.43103 | C001900137 | Oshane Warren |  | Completed |  |  | 2026-08-25 16:25 | 2026-08-25 17:01 | 2026-08-25 20:07 | 2026-08-25 20:08 | 2026-08-25 21:38 | 2026-08-25 21:39 | 2026-08-25 21:39 | 2026-08-25 21:39 |  |  | Fair | No | Need daylight attention to carry out repair
Outage | J.E.26.08.42874 | C001900139 | Javid Vernon | Westmoreland | Completed | Load_265484 | Paradise - 110 | 2026-08-25 16:25 | 2026-08-25 16:33 | 2026-08-25 17:05 | 2026-08-25 17:06 | 2026-08-25 17:05 | 2026-08-25 17:10 | 2026-08-25 17:12 | 2026-08-25 17:12 |  |  | Fair | No | Customers stated that the power was restored
Outage | J.E.26.08.43270 | C001900142 | Tajay Bernard | Hanover | Completed | Load_246056 | Orange Bay - 310 | 2026-08-25 16:27 | 2026-08-25 16:27 | 2026-08-25 19:14 | 2026-08-25 19:15 | 2026-08-25 20:49 | 2026-08-25 20:50 | 2026-08-25 20:51 | 2026-08-25 20:51 |  |  | Fair | No | Area check ad found okay unable to locate customer on premises multiple phone calls to customer number went unanswered
Non-Outage | J.E.26.08.37701 | C001900145 | Javid Vernon |  | Completed |  |  | 2026-08-25 16:28 | 2026-08-25 16:29 | 2026-08-25 16:56 | 2026-08-25 16:57 | 2026-08-25 16:56 | 2026-08-25 16:57 | 2026-08-25 16:57 | 2026-08-25 16:57 |  |  | Fair | No | This call belongs to st James
Outage | J.E.26.08.37325 | C001900155 | Fitzroy Turner | KSAN | Completed | Load_254044 | Hope - 410 | 2026-08-25 16:39 | 2026-08-25 16:40 | 2026-08-25 20:56 | 2026-08-25 20:56 | 2026-08-25 22:02 | 2026-08-25 22:02 | 2026-08-25 22:05 | 2026-08-25 22:05 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Found lane with out electricity splice and retention #2 triplex using 6 one bolt clamps and two preform supply restored to areas
Outage | J.E.26.08.43495 | C001900158 | Edward Royal | KSAN | Completed | Load_257856 | Washington Blvd - 410 | 2026-08-25 16:42 | 2026-08-25 16:43 | 2026-08-25 21:02 | 2026-08-25 21:02 | 2026-08-25 21:02 | 2026-08-25 21:10 | 2026-08-25 21:11 | 2026-08-25 21:11 |  |  | Fair | No | Premises found close
Outage | J.E.26.08.41205 | C001900159 | Romeo Brissett | St.James | Completed | Load_302094 | Bogue - 610 | 2026-08-25 16:43 | 2026-08-26 08:11 | 2026-08-26 08:16 | 2026-08-26 12:09 | 2026-08-26 12:08 | 2026-08-26 13:06 | 2026-08-26 13:13 | 2026-08-26 13:13 |  |  | Fair | No | Isolated (1)25 kva transformer, removed tree limb, removed illegal connections, spliced retention one span of secondary. No phone service in the area.
Outage | J.E.26.08.35815 | C001900171 | Javid Vernon | Westmoreland | Completed | Load_556300 | Paradise - 210 | 2026-08-25 17:00 | 2026-08-25 17:04 | 2026-08-25 17:13 | 2026-08-25 17:14 | 2026-08-25 17:36 | 2026-08-25 17:53 | 2026-08-25 17:53 | 2026-08-25 17:53 |  |  | Fair | No | Area checked and found ok unable to locate the customer and premises phone call to customer number went unanswered
Outage | J.E.26.08.43548 | C001900175 | Daniel Francis | St.Ann | Completed | Load_261002 | Ocho Rios - 510 | 2026-08-25 17:19 | 2026-08-25 17:21 | 2026-08-25 18:41 | 2026-08-25 18:42 | 2026-08-25 20:27 | 2026-08-25 20:31 | 2026-08-25 20:31 | 2026-08-25 20:31 | BrokenWire |  | Fair | No | Splice and retention secondary neutral wire 70ft
Outage | J.E.26.08.43551 | C001900177 | Roxroy Needham | St.Ann | Completed | Load_246914 | Cardiff Hall - 310 | 2026-08-25 17:20 | 2026-08-25 17:21 | 2026-08-25 23:43 | 2026-08-25 23:44 | 2026-08-25 23:52 | 2026-08-25 23:53 | 2026-08-25 23:53 | 2026-08-25 23:53 |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.08.43597 | C001900181 | Andre Williams | Trelawny | Completed | Load_268005 | Greenwood - 110 | 2026-08-25 17:27 | 2026-08-25 17:28 | 2026-08-25 17:41 | 2026-08-25 17:42 | 2026-08-25 18:24 | 2026-08-25 18:47 | 2026-08-25 18:48 | 2026-08-25 18:48 | Fire |  | Fair | No | Remake burnt off joint at jumper on open secondary, outage on line after repairs, 113+113=226
Outage | J.E.26.08.43411 | C001900185 | Nickolas Rodriques | St.Catherine | Completed | Load_290530 | Rhodens Pen - 210 | 2026-08-25 17:40 | 2026-08-25 17:41 | 2026-08-25 20:05 | 2026-08-25 20:07 | 2026-08-25 20:44 | 2026-08-25 21:08 | 2026-08-25 21:10 | 2026-08-25 21:10 | BrokenWire |  | Fair | No | Customer is requesting a team for tomorrow August 26 to do repairs.
Outage | J.E.26.08.43783 | C001900186 | Nickolas Rodriques | St.Catherine | Completed | Load_556329 | Rhodens Pen - 210 | 2026-08-25 17:40 | 2026-08-25 17:41 | 2026-08-25 19:17 | 2026-08-25 19:17 | 2026-08-25 19:39 | 2026-08-25 20:00 | 2026-08-25 20:05 | 2026-08-25 20:05 |  |  | Fair | No | Found premises locked. Efforts to reach the customer on the contact number provided were unsuccessful.
Non-Outage | J.E.26.08.43638 | C001900188 | Tajay Bernard |  | Completed |  |  | 2026-08-25 17:46 | 2026-08-25 17:47 | 2026-08-25 18:22 | 2026-08-25 18:23 | 2026-08-25 18:54 | 2026-08-25 19:13 | 2026-08-25 19:14 | 2026-08-25 19:14 |  |  | Fair | No | Refuse 1 25kva Transformer use 3amp fuse
Outage | J.E.26.08.42596 | C001900194 | Raheem Ricketts | St.Elizabeth | Completed | Load_264506 | Maggotty - 110 | 2026-08-25 18:03 | 2026-08-25 18:04 | 2026-08-25 19:02 | 2026-08-25 19:02 | 2026-08-25 19:22 | 2026-08-25 19:23 | 2026-08-25 19:23 | 2026-08-25 19:23 |  |  | Fair | No | Refer to field service customer service wire needs to reconnect
Non-Outage | J.E.26.08.41755 | C001900199 | Elvis Trowers | KSAS | Completed | Load_259934 | Hunts Bay - 210 | 2026-08-25 18:14 | 2026-08-25 18:16 | 2026-08-25 18:44 | 2026-08-25 18:45 | 2026-08-25 19:06 | 2026-08-25 20:25 | 2026-08-25 20:35 | 2026-08-25 20:35 |  |  | Fair | No | Isolate bank of 3-100 kva transformer at pole #0052380 and repair burnt off transformer phase drop lead. Repaired using two 1- bolt clamps. Readings at pothead 111-111-205& 229-232-225 volts
Outage | J.E.26.08.43256 | C001900204 | Damion Reid | Manchester | Completed | Load_248356 | Kendal - 210 | 2026-08-25 18:42 | 2026-08-25 18:46 | 2026-08-25 22:18 | 2026-08-25 22:18 | 2026-08-25 22:59 | 2026-08-25 22:59 | 2026-08-25 23:00 | 2026-08-25 23:00 |  |  | Fair | No | Unable to contact or locate customer
Outage | J.E.26.08.44002 | C001900205 | Raheem Ricketts | St.Elizabeth | Completed | Load_574150 | Maggotty - 110 | 2026-08-25 18:44 | 2026-08-25 18:46 | 2026-08-25 19:23 | 2026-08-25 19:24 | 2026-08-25 19:23 | 2026-08-25 19:24 | 2026-08-25 19:24 | 2026-08-25 19:24 | BrokenWire |  | Fair | No | Customer requested daylight attention
Non-Outage | J.E.26.08.43997 | C001900210 | Romeo Brissett |  | Completed |  |  | 2026-08-25 18:47 | 2026-08-25 19:23 | 2026-08-26 12:06 | 2026-08-26 12:07 | 2026-08-26 12:06 | 2026-08-26 10:23 | 2026-08-26 12:07 | 2026-08-26 12:07 |  |  | Fair | No | Customer stated power restored
Outage | J.E.26.08.43731 | C001900209 | Horace Malcolm | St.James | Completed | Load_237795 | Queens Drive - 710 | 2026-08-25 18:47 | 2026-08-25 23:18 | 2026-08-25 23:53 | 2026-08-25 23:54 | 2026-08-26 00:26 | 2026-08-26 00:27 | 2026-08-26 00:28 | 2026-08-26 00:28 |  |  | Fair | Yes | Check and found area ok supply restored
Outage | J.E.26.08.44151 | C001900219 | Javid Vernon | Westmoreland | Completed | Load_292703 | Paradise - 210 | 2026-08-25 19:01 | 2026-08-25 19:02 | 2026-08-25 19:17 | 2026-08-25 19:17 | 2026-08-25 19:17 | 2026-08-25 19:19 | 2026-08-25 19:19 | 2026-08-25 19:19 |  |  | Fair | No | Customer stated that power is at their premises
Outage | J.E.26.08.44189 | C001900220 | Javid Vernon | Westmoreland | Completed | Load_257635 | Paradise - 110 | 2026-08-25 19:01 | 2026-08-25 19:02 | 2026-08-25 19:15 | 2026-08-25 19:16 | 2026-08-25 19:16 | 2026-08-25 19:17 | 2026-08-25 19:17 | 2026-08-25 19:17 |  |  | Fair | No | Customers stated that power is at there premises
Non-Outage | J.E.26.08.44063 | C001900234 | Romaine Roberts |  | Completed |  |  | 2026-08-25 19:22 | 2026-08-25 19:30 | 2026-08-25 21:17 | 2026-08-25 21:17 | 2026-08-25 22:05 | 2026-08-25 22:05 | 2026-08-25 22:10 | 2026-08-25 22:10 |  |  | Fair | No | Customer is with out supply for 7 days now drew to rami meter not reachable by call center field service is required also please call customer rami box number is not visible refer to mr coach
Non-Outage | J.E.26.08.44217 | C001900235 | Romeo Brissett |  | Completed |  |  | 2026-08-25 19:22 | 2026-08-25 19:35 | 2026-08-25 20:04 | 2026-08-25 20:05 | 2026-08-25 22:25 | 2026-08-25 23:27 | 2026-08-25 23:52 | 2026-08-25 23:52 | BrokenWire |  | Fair | No | removed illegal connections, spliced and retention 4 span of secondary, used 100ft of #2 50ft of 2/0, 6 clamps and replaced (1)50 kva transformer fuse with 5 amps. Fire watch was done and line found ok and left energized
Outage | J.E.26.08.43855 | C001900237 | Daniel Francis | St.Ann | Completed | Load_253007 | Upper White River - 210 | 2026-08-25 19:24 | 2026-08-25 19:25 | 2026-08-25 20:32 | 2026-08-25 20:32 | 2026-08-25 20:58 | 2026-08-25 21:00 | 2026-08-25 21:00 | 2026-08-25 21:00 |  |  | Fair | No | We call customer and she say light come
Outage | J.E.26.08.44099 | C001900236 | Roxroy Needham | St.Ann | Completed | Load_260540 | Cardiff Hall - 310 | 2026-08-25 19:24 | 2026-08-25 19:25 | 2026-08-25 23:08 | 2026-08-25 23:08 | 2026-08-25 23:08 | 2026-08-25 23:10 | 2026-08-25 23:09 | 2026-08-25 23:09 |  |  | Fair | No | Premises found ok call customer and customer say that the light is ok
Outage | J.E.26.08.44271 | C001900238 | Horace Malcolm | St.James | Completed | Load_238073 | Queens Drive - 710 | 2026-08-25 19:29 | 2026-08-25 23:18 | 2026-08-25 23:52 | 2026-08-26 02:17 | 2026-08-26 02:17 | 2026-08-26 02:49 | 2026-08-26 02:49 | 2026-08-26 02:49 | Fire |  | Fair | No | Check and found area ok
Outage | J.E.26.08.44505 | C001900240 | Kenroy Dale | Manchester | Completed | Load_243297 | Kendal - 310 | 2026-08-25 19:32 | 2026-08-25 19:34 | 2026-08-25 19:59 | 2026-08-25 20:00 | 2026-08-25 21:09 | 2026-08-25 21:51 | 2026-08-25 21:53 | 2026-08-25 21:53 |  |  | Fair | No | Burn off jumper found remade connection using 2 one bolt clamp voltage reading 111/115/226
Non-Outage | J.E.26.08.44478 | C001900241 | Roxroy Needham |  | Completed |  |  | 2026-08-25 19:36 | 2026-08-25 19:39 | 2026-08-25 21:52 | 2026-08-25 21:53 | 2026-08-25 23:06 | 2026-08-25 23:06 | 2026-08-25 23:08 | 2026-08-25 23:08 |  | Y | Fair | No | Open a 50 KVA transformer at pole to repair transformer leed used 2 pg clamp
Non-Outage | J.E.26.08.42391 | C001900250 | Collin Robinson | Portland | Completed | Load_248037 | Port Antonio - 410 | 2026-08-25 19:41 | 2026-08-25 19:42 | 2026-08-25 20:01 | 2026-08-25 20:01 | 2026-08-25 20:59 | 2026-08-25 21:08 | 2026-08-25 21:08 | 2026-08-25 21:08 |  |  | Fair | No | Customer meter socket defective
Non-Outage | J.E.26.08.43659 | C001900251 | Andrae Clarke | Portland | Completed | Load_242386 | Port Antonio - 410 | 2026-08-25 19:41 | 2026-08-26 08:00 | 2026-08-26 08:14 | 2026-08-26 08:17 | 2026-08-26 10:36 | 2026-08-26 10:04 | 2026-08-26 11:54 | 2026-08-26 11:54 |  |  | Fair | No | Remove defective wire Run out new wire 80 feetUse three one bolt clamp Check voltage 117/117/234
Outage | J.E.26.08.41029 | C001900249 | Horace Malcolm | St.James | Completed | Load_301642 | Bogue - 310 | 2026-08-25 19:41 | 2026-08-25 23:18 | 2026-08-25 23:47 | 2026-08-26 16:09 | 2026-08-26 16:50 | 2026-08-26 17:10 | 2026-08-26 17:11 | 2026-08-26 17:11 |  |  | Fair | No | Refused one 8amp junction fuse
Outage | J.E.26.08.43898 | C001900257 | Tajay Bernard | Hanover | Completed | Load_250299 | Orange Bay - 310 | 2026-08-25 19:49 | 2026-08-25 19:50 | 2026-08-25 20:51 | 2026-08-25 20:53 | 2026-08-25 21:24 | 2026-08-25 21:37 | 2026-08-25 21:41 | 2026-08-25 21:41 | Fire |  | Fair | No | Check and found a customer meter burnt which cause the transformer to trip. Repairs need to be done in customer meter socket before meter can be replaced, customer was advised. Refer to field service Rest 10kva transformerMeter number 2966147
Outage | J.E.26.08.44649 | C001900256 | Roxroy Needham | St.Ann | Completed | Load_252066 | Cardiff Hall - 310 | 2026-08-25 19:49 | 2026-08-25 20:04 | 2026-08-25 23:10 | 2026-08-25 23:10 | 2026-08-25 23:39 | 2026-08-25 23:41 | 2026-08-25 23:43 | 2026-08-25 23:43 |  |  | Fair | No | Premises found ok customer have internal problem power is going from meter to house
Non-Outage | J.E.26.08.44455 | C001900262 | Raheem Ricketts |  | Completed |  |  | 2026-08-25 19:55 | 2026-08-25 20:01 | 2026-08-25 20:32 | 2026-08-25 21:02 | 2026-08-25 21:02 | 2026-08-25 21:03 | 2026-08-25 21:04 | 2026-08-25 21:04 |  |  | Fair | No | Check and found okay however customer problem customer wants to get an transformer customer says he’s going to the office tomorrow to find out how it goes
Outage | J.E.26.08.44377 | C001900263 | Raheem Ricketts | St.Elizabeth | Completed | Load_292549 | Maggotty - 210 | 2026-08-25 19:55 | 2026-08-25 20:01 | 2026-08-25 20:32 | 2026-08-25 20:40 | 2026-08-25 21:01 | 2026-08-25 21:01 | 2026-08-25 21:01 | 2026-08-25 21:01 |  |  | Fair | No | Customer cell number went straight voicemail
Non-Outage | J.E.26.08.44292 | C001900269 | Horace Malcolm | St.James | Completed | Load_264211 | Queens Drive - 710 | 2026-08-25 20:09 | 2026-08-25 22:34 | 2026-08-26 00:29 | 2026-08-26 02:50 | 2026-08-26 03:16 | 2026-08-26 03:21 | 2026-08-26 03:21 | 2026-08-26 03:21 |  |  | Fair | No | Check and found ok voltage 119-117-236-204
Outage | J.E.26.08.44746 | C001900271 | Horace Malcolm | St.James | Completed | Load_555841 | Queens Drive - 710 | 2026-08-25 20:13 | 2026-08-25 23:18 | 2026-08-25 23:45 | 2026-08-25 23:46 | 2026-08-25 23:46 | 2026-08-25 23:47 | 2026-08-25 23:47 | 2026-08-25 23:47 |  |  | Fair | No | Customer says supply restored
Outage | J.E.26.08.43893 | C001900283 | Romeo Brissett | St.James | Completed | Load_292204 | Bogue - 610 | 2026-08-25 20:22 | 2026-08-26 09:42 | 2026-08-26 12:07 | 2026-08-26 12:08 | 2026-08-26 12:07 | 2026-08-26 10:33 | 2026-08-26 12:08 | 2026-08-26 12:08 |  |  | Fair | No | Customer stated power was restored from last night
Outage | J.E.26.08.42857 | C001900284 | Neville Spencer | Clarendon | Completed | Load_249472 | May Pen - 110 | 2026-08-25 20:26 | 2026-08-25 20:33 | 2026-08-25 20:38 | 2026-08-25 20:38 | 2026-08-25 21:51 | 2026-08-25 22:23 | 2026-08-25 22:25 | 2026-08-25 22:25 |  |  | Fair | No | Test closed 15 amp j/ fuse . Fuse rejected need daylight attention road impassible.
Outage | J.E.26.08.44004 | C001900285 | Hartley Chin | Clarendon | Completed | Load_240599 | May Pen - 210 | 2026-08-25 20:26 | 2026-08-25 20:28 | 2026-08-25 21:30 | 2026-08-25 21:31 | 2026-08-25 21:30 | 2026-08-25 21:31 | 2026-08-25 21:31 | 2026-08-25 21:31 |  |  | Fair | No | Contacted customer… issue was resolved..
Outage | J.E.26.08.44325 | C001900286 | Hartley Chin | Clarendon | Completed | Load_246426 | May Pen - 210 | 2026-08-25 20:26 | 2026-08-25 20:28 | 2026-08-25 21:34 | 2026-08-25 21:36 | 2026-08-25 22:00 | 2026-08-25 22:47 | 2026-08-25 22:48 | 2026-08-25 22:48 |  |  | Fair | No | Isolate 50 KVA transformer @ pole # 0125838 due to broken X3 drop lead found , repair drop lead , change X1 drop lead clamp , re-energized transformer …
Outage | J.E.26.08.44061 | C001900302 | Andre Williams | Trelawny | Completed | Load_574709 | Greenwood - 210 | 2026-08-25 20:41 | 2026-08-25 20:48 | 2026-08-25 21:13 | 2026-08-25 21:13 | 2026-08-25 21:37 | 2026-08-25 21:38 | 2026-08-25 21:39 | 2026-08-25 21:39 |  |  | Flood | No | Premises ok and with supply power was restored to area during the day
Outage | J.E.26.08.42381 | C001900305 | Andre Williams | Trelawny | Completed | Load_251727 | Greenwood - 110 | 2026-08-25 20:47 | 2026-08-25 20:50 | 2026-08-25 20:58 | 2026-08-25 21:57 | 2026-08-25 21:56 | 2026-08-25 21:58 | 2026-08-25 21:58 | 2026-08-25 21:58 |  |  | Fair | No | Premises ok and with supply, call related to earlier outage in area
Outage | J.E.26.08.45388 | C001900308 | Tajay Bernard | Hanover | Completed | Load_246056 | Orange Bay - 310 | 2026-08-25 20:50 | 2026-08-25 20:56 | 2026-08-25 21:41 | 2026-08-25 21:41 | 2026-08-25 22:40 | 2026-08-25 22:45 | 2026-08-25 22:45 | 2026-08-25 22:45 |  |  | Fair | No | Unable to get to the location, road has been blocked by container and a tractor, we are also unable to turn around due to build up traffic
Non-Outage | J.E.26.08.45360 | C001900311 | Collin Robinson |  | Completed |  |  | 2026-08-25 20:56 | 2026-08-25 21:02 | 2026-08-25 21:14 | 2026-08-25 21:14 | 2026-08-25 22:04 | 2026-08-25 22:19 | 2026-08-25 22:19 | 2026-08-25 22:19 | Fire |  | Fair | No | Cut tree branches from open secondary phase and neutral conductor
Outage | J.E.26.08.45472 | C001900310 | Andre Williams | Trelawny | Completed | Load_265828 | Duncans - 110 | 2026-08-25 20:56 | 2026-08-25 20:57 | 2026-08-25 21:11 | 2026-08-25 21:12 | 2026-08-25 21:11 | 2026-08-25 21:12 | 2026-08-25 21:13 | 2026-08-25 21:13 |  |  | Fair | No | Area with supply confirm by customers
Outage | J.E.26.08.43512 | C001900318 | Damion Reid | Manchester | Completed | Load_250851 | Kendal - 210 | 2026-08-25 21:10 | 2026-08-25 21:15 | 2026-08-25 21:35 | 2026-08-25 21:36 | 2026-08-25 22:11 | 2026-08-25 22:17 | 2026-08-25 22:18 | 2026-08-25 22:18 |  |  | Fair | No | Unable to contact or locate customer
Non-Outage | J.E.26.08.43955 | C001900330 | Delano Gayle |  | Completed |  |  | 2026-08-25 21:30 | 2026-08-25 23:28 | 2026-08-26 03:59 | 2026-08-26 04:00 | 2026-08-26 04:32 | 2026-08-26 04:37 | 2026-08-26 04:37 | 2026-08-26 04:37 | BrokenWire |  | Fair | No | Premises not found no proper contact information or directions in report
Outage | J.E.26.08.42611 | C001900331 | Delano Gayle | St.Catherine | Completed | Load_258468 | Tredegar - 410 | 2026-08-25 21:30 | 2026-08-25 23:28 | 2026-08-26 00:09 | 2026-08-26 00:10 | 2026-08-26 01:17 | 2026-08-26 01:27 | 2026-08-26 01:27 | 2026-08-26 01:27 |  |  | Fair | No | Hexing customer send call to Moses, most customers from hexing box are without supply along with street lights
Outage | J.E.26.08.44226 | C001900329 | Richard Nicholas | St.Catherine | Completed | Load_261008 | Tredegar - 310 | 2026-08-25 21:30 | 2026-08-26 08:10 | 2026-08-26 08:23 | 2026-08-26 08:24 | 2026-08-26 09:18 | 2026-08-26 09:59 | 2026-08-26 10:01 | 2026-08-26 10:01 |  |  | Fair | No | Customer switch Rammy prepaid account to postpaid,request is now completed with the assistance of the commercial office in sp.towm.supply left working ok.
Outage | J.E.26.08.45020 | C001900338 | Raheem Ricketts | Manchester | Completed | Load_246114 | Spur Tree - 210 | 2026-08-25 21:37 | 2026-08-25 21:43 | 2026-08-25 22:15 | 2026-08-25 22:16 | 2026-08-25 22:53 | 2026-08-25 22:54 | 2026-08-25 22:54 | 2026-08-25 22:54 |  |  | Fair | No | Splice and retention customer neutral wire using one clamp
Outage | J.E.26.08.46061 | C001900348 | Michael Paterson | Westmoreland | Completed | Load_292343 | Paradise - 210 | 2026-08-25 21:53 | 2026-08-26 07:47 | 2026-08-26 08:15 | 2026-08-26 08:16 | 2026-08-26 09:43 | 2026-08-26 09:45 | 2026-08-26 09:47 | 2026-08-26 09:47 | BrokenWire |  | Fair | No | Found 25kva xfmr fuse blown, further assessment done, found fuse holder damage, replace fuse holder, replace 2amps fuse, supply restored, voltage readings, 117v, 117v, 234v. Several illegal connections in area, please refer to the appropriate department.
Outage | J.E.26.08.46072 | C001900356 | Christopher Edwards | KSAS | Completed | Load_261930 | Duhaney - 310 | 2026-08-25 22:08 | 2026-08-25 23:22 | 2026-08-26 00:26 | 2026-08-26 01:10 | 2026-08-26 01:10 | 2026-08-26 01:10 | 2026-08-26 01:10 | 2026-08-26 01:10 |  |  | Fair | No | Check and found okSupply is at the location
Outage | J.E.26.08.44035 | C001900358 | Christopher Edwards | KSAS | Completed | Load_242388 | Duhaney - 310 | 2026-08-25 22:09 | 2026-08-25 23:22 | 2026-08-25 23:29 | 2026-08-26 00:32 | 2026-08-26 00:32 | 2026-08-26 01:05 | 2026-08-26 01:09 | 2026-08-26 01:09 |  |  | Fair | No | Required daylight attention Customer is connected in hexing box However after using noisy tester to check switch bottom And transformer bushing power is going into the hexing box but none is coming out .seems the hexing box has shut down
Outage | J.E.26.08.46016 | C001900357 | Christopher Edwards | KSAS | Completed | Load_246988 | Duhaney - 310 | 2026-08-25 22:09 | 2026-08-25 23:22 | 2026-08-25 23:57 | 2026-08-25 23:58 | 2026-08-26 00:11 | 2026-08-26 00:29 | 2026-08-26 00:30 | 2026-08-26 00:30 |  |  | Fair | No | Refuse blown junction fuse Using (1) 20 ampsClear bird nest off blown junction switch
Outage | J.E.26.08.44357 | C001900367 | Horace Malcolm | St.James | Completed | Load_556969 | Queens Drive - 710 | 2026-08-25 22:40 | 2026-08-25 22:41 | 2026-08-25 23:11 | 2026-08-25 23:12 | 2026-08-25 23:42 | 2026-08-25 23:44 | 2026-08-25 23:44 | 2026-08-25 23:44 |  |  | Fair | No | Check and found area ok supply is in area
Outage | J.E.26.08.45418 | C001900379 | Horace Malcolm | St.James | Completed | Load_251385 | Bogue - 310 | 2026-08-25 23:21 | 2026-08-25 23:24 | 2026-08-26 00:52 | 2026-08-26 00:53 | 2026-08-26 00:52 | 2026-08-26 02:16 | 2026-08-26 02:16 | 2026-08-26 02:16 |  |  | Fair | Yes | Remove drop lead from retired transformer and replace one 100kva transformer used one 8amp fuse
Outage | J.E.26.08.45718 | C001900381 | Christopher Edwards | KSAN | Completed | Load_242860 | Constant Spring - 210 | 2026-08-25 23:23 | 2026-08-25 23:24 | 2026-08-26 01:11 | 2026-08-26 01:11 | 2026-08-26 01:25 | 2026-08-26 01:36 | 2026-08-26 01:36 | 2026-08-26 01:36 |  |  | Fair | No | Check and found okSupply is at the premises
Outage | J.E.26.08.46164 | C001900382 | Milton Charlton | KSAS | Completed | Load_259128 | Up Park Camp - 410 | 2026-08-25 23:23 | 2026-08-26 15:33 | 2026-08-26 16:28 | 2026-08-26 16:28 | 2026-08-26 17:15 | 2026-08-26 16:50 | 2026-08-26 17:18 | 2026-08-26 17:18 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.46193 | C001900380 | Christopher Edwards | KSAS | Completed | Load_259468 | Duhaney - 310 | 2026-08-25 23:23 | 2026-08-25 23:24 | 2026-08-25 23:30 | 2026-08-26 00:31 | 2026-08-26 00:30 | 2026-08-26 00:31 | 2026-08-26 00:31 | 2026-08-26 00:31 |  |  | Fair | No | Check and found okRelated to previous call that was resolved
Outage | J.E.26.08.46964 | C001900389 | Roxroy Needham | St.Ann | Completed | Load_242953 | Roaring River - 410 | 2026-08-26 00:06 | 2026-08-26 00:07 | 2026-08-26 00:34 | 2026-08-26 00:35 | 2026-08-26 00:35 | 2026-08-26 00:36 | 2026-08-26 00:36 | 2026-08-26 00:36 |  |  | Fair | No | Call customer and customer say that he didn’t make a report
Outage | J.E.26.08.46524 | C001900400 | Edward Royal | KSAS | Completed | Load_245842 | Up Park Camp - 510 | 2026-08-26 03:00 | 2026-08-26 03:01 | 2026-08-26 09:02 | 2026-08-26 11:09 | 2026-08-26 11:54 | 2026-08-26 12:12 | 2026-08-26 12:22 | 2026-08-26 12:22 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Spliced and reconnected secondary jumper using 2 single bolt clamp
Outage | J.E.26.08.47220 | C001900401 | Daniel Francis | St.Ann | Completed | Load_256522 | Roaring River - 210 | 2026-08-26 03:00 | 2026-08-26 07:59 | 2026-08-26 08:45 | 2026-08-26 08:46 | 2026-08-26 09:33 | 2026-08-26 09:36 | 2026-08-26 09:36 | 2026-08-26 09:36 | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | No fire seen there and next thing pole is not for JPS were them say the fire was
Outage | J.E.26.08.44357 | C001900402 | Horace Malcolm | St.James | Completed | Load_556969 | Queens Drive - 710 | 2026-08-26 03:01 | 2026-08-26 03:02 | 2026-08-26 03:21 | 2026-08-26 03:22 | 2026-08-26 03:38 | 2026-08-26 03:44 | 2026-08-26 03:44 | 2026-08-26 03:44 |  |  | Fair | No | Check and found area ok,info saying artwell found premises closed
Non-Outage | J.E.26.08.44415 | C001900413 | Swon Miller | St.James | Completed | Load_238073 | Queens Drive - 710 | 2026-08-26 07:11 | 2026-08-26 07:55 | 2026-08-26 08:20 | 2026-08-26 08:20 | 2026-08-26 09:03 | 2026-08-26 09:31 | 2026-08-26 09:33 | 2026-08-26 09:33 |  |  | Fair | No | Check and found area okay voltage found 115/114/231 customer states that problem was resolved last night voltage left 115/114/231
Non-Outage | J.E.26.08.44428 | C001900412 | Swon Miller | St.James | Completed | Load_238073 | Queens Drive - 710 | 2026-08-26 07:11 | 2026-08-26 07:55 | 2026-08-26 11:13 | 2026-08-26 11:14 | 2026-08-26 12:20 | 2026-08-26 12:37 | 2026-08-26 12:38 | 2026-08-26 12:38 |  |  | Fair | No | Check and found area okay customer states that the problem was resolved last night
Outage | J.E.26.08.45884 | C001900414 | Wan Carlos Scarlett | St.Catherine | Completed | Load_257054 | Twickenham - 210 | 2026-08-26 07:15 | 2026-08-26 07:30 | 2026-08-26 07:36 | 2026-08-26 07:36 | 2026-08-26 08:06 | 2026-08-26 08:49 | 2026-08-26 08:50 | 2026-08-26 08:50 | BrokenWire |  | Fair | No | Found customer 3 wire service at pole with one of the phase broken off use 2 one bolt clamps at open secondary line phase and neutral readings 116-115-231
Outage | J.E.26.08.46387 | C001900417 | Collin Robinson | Portland | Completed | Load_575971 | Port Antonio - 310 | 2026-08-26 07:19 | 2026-08-26 07:27 | 2026-08-26 08:49 | 2026-08-26 08:50 | 2026-08-26 09:08 | 2026-08-26 09:12 | 2026-08-26 09:12 | 2026-08-26 09:12 |  |  | Rains | No | No access to premises to check meter socket voltage
Outage | J.E.26.08.46923 | C001900418 | Collin Robinson | Portland | Completed | Load_252674 | Port Antonio - 310 | 2026-08-26 07:19 | 2026-08-26 07:27 | 2026-08-26 07:35 | 2026-08-26 07:36 | 2026-08-26 08:45 | 2026-08-26 08:49 | 2026-08-26 08:49 | 2026-08-26 08:49 | Fire |  | Rains | No | Issue resolved from last night
Outage | J.E.26.08.47102 | C001900423 | Selvin White | St.Elizabeth | Completed | Load_267781 | Maggotty - 110 | 2026-08-26 07:22 | 2026-08-26 07:43 | 2026-08-26 12:42 | 2026-08-26 12:43 | 2026-08-26 12:45 | 2026-08-26 13:02 | 2026-08-26 13:02 | 2026-08-26 13:02 | BrokenWire |  | Fair | No
Outage | J.E.26.08.45818 | C001900424 | Selvin White | St.Elizabeth | Completed | Load_245123 | Maggotty - 110 | 2026-08-26 07:23 | 2026-08-26 07:24 | 2026-08-26 08:31 | 2026-08-26 08:31 | 2026-08-26 09:04 | 2026-08-26 09:31 | 2026-08-26 09:31 | 2026-08-26 09:31 |  |  | Fair | No | Burnt 3 wire,240 volts meter found at location caused by defective meter socket. Customer advised to carry out repairs and contact jpsco for meter replacement.. Customer left with supply.
Outage | J.E.26.08.47814 | C001900425 | Selvin White | St.Elizabeth | Completed | Load_292549 | Maggotty - 210 | 2026-08-26 07:26 | 2026-08-26 07:42 | 2026-08-26 10:59 | 2026-08-26 11:00 | 2026-08-26 11:19 | 2026-08-26 11:32 | 2026-08-26 11:35 | 2026-08-26 11:35 |  |  | Fair | No | Replaced a defective 1.5 amp fuse for a 15 kva transformer with no pole number at location. Supply restored to the two customers that were affected.
Outage | J.E.26.08.44002 | C001900431 | Selvin White | St.Elizabeth | Completed | Load_574150 | Maggotty - 110 | 2026-08-26 07:27 | 2026-08-26 07:28 | 2026-08-26 10:47 | 2026-08-26 10:47 | 2026-08-26 10:53 | 2026-08-26 10:59 | 2026-08-26 10:59 | 2026-08-26 10:59 | BrokenWire |  | Fair | No | Please refer to C. Johnson and Jessie Morales at the field service department so arrangements can be made to replace service wire and meter that were damaged during the recent hurricane . Customer has finished repairs so reconnection is needed.
Outage | J.E.26.08.43256 | C001900432 | Kenroy Dale | Manchester | Completed | Load_248356 | Kendal - 210 | 2026-08-26 07:28 | 2026-08-26 12:17 | 2026-08-26 14:15 | 2026-08-26 14:16 | 2026-08-26 14:59 | 2026-08-26 15:27 | 2026-08-26 15:30 | 2026-08-26 15:30 |  |  | Fair | No | Corroded phase found at pole remade connection using 1 one bolt clamp voltage reading 113/111/224
Outage | J.E.26.08.47802 | C001900433 | Elvis Trowers | KSAS | Completed | Load_247482 | Greenwich - 510 | 2026-08-26 07:28 | 2026-08-26 07:30 | 2026-08-26 07:39 | 2026-08-26 07:39 | 2026-08-26 09:13 | 2026-08-26 09:05 | 2026-08-26 09:23 | 2026-08-26 09:23 | BrokenWire |  | Fair | No | Isolate bank of 3-100 kva transformer at pole#( no pole#) and repair broken open wire secondary neutral. Repaired using 80ft of #2 AA conductor, one #2 preform and four 1- bolt clamps.
Non-Outage | J.E.26.08.44982 | C001900434 | Kenroy Dale |  | Completed |  |  | 2026-08-26 07:30 | 2026-08-26 07:31 | 2026-08-26 07:59 | 2026-08-26 08:25 | 2026-08-26 09:38 | 2026-08-26 10:02 | 2026-08-26 10:04 | 2026-08-26 10:04 |  |  | Fair | No | Customer meter lost signal meter was unplugged and then re-install, customer service was contacted and customer now with supply
Outage | J.E.26.08.43856 | C001900437 | Milton Charlton | KSAN | Completed | Load_248575 | Hope - 510 | 2026-08-26 07:35 | 2026-08-26 07:39 | 2026-08-26 11:46 | 2026-08-26 11:55 | 2026-08-26 12:58 | 2026-08-26 12:40 | 2026-08-26 13:00 | 2026-08-26 13:00 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Non-Outage | J.E.26.08.42726 | C001900438 | Milton Charlton |  | Completed |  |  | 2026-08-26 07:36 | 2026-08-26 07:39 | 2026-08-26 07:53 | 2026-08-26 07:54 | 2026-08-26 11:50 | 2026-08-26 11:15 | 2026-08-26 11:52 | 2026-08-26 11:52 | BrokenWire |  | Fair | No | Unable to locate customer by telephone. Nobody answering telephone number on the report.
Non-Outage | J.E.26.08.41335 | C001900441 | Christopher Edwards |  | Completed |  |  | 2026-08-26 07:40 | 2026-08-26 07:43 | 2026-08-26 07:58 | 2026-08-26 08:58 | 2026-08-26 08:57 | 2026-08-26 10:22 | 2026-08-26 10:23 | 2026-08-26 10:23 |  |  | Fair | No | Unable to reach customer by phone Went in area and supply is in the area
Outage | J.E.26.08.42857 | C001900443 | Clyde Brown | Clarendon | Completed | Load_249472 | May Pen - 110 | 2026-08-26 07:41 | 2026-08-26 07:42 | 2026-08-26 12:04 | 2026-08-26 12:05 | 2026-08-26 12:54 | 2026-08-26 13:27 | 2026-08-26 13:32 | 2026-08-26 13:32 |  |  | Fair | No | Blown 15 amps junction fuse at Alston,line patrolled and no fault seen,blown fuse replaced.
Outage | J.E.26.08.46814 | C001900449 | Jermaine Williams | Clarendon | Completed | Load_245032 | Parnassus - 210 | 2026-08-26 07:42 | 2026-08-26 07:45 | 2026-08-26 11:45 | 2026-08-26 11:46 | 2026-08-26 12:10 | 2026-08-26 12:10 | 2026-08-26 12:11 | 2026-08-26 12:11 |  |  | Fair | No | Isolate 25kva xfmr to remade burnt off droplead using two clamps.
Non-Outage | J.E.26.08.47745 | C001900453 | Elvis Trowers |  | Completed |  |  | 2026-08-26 07:43 | 2026-08-26 07:44 | 2026-08-26 09:24 | 2026-08-26 09:25 | 2026-08-26 10:17 | 2026-08-26 22:20 | 2026-08-26 10:22 | 2026-08-26 10:22 | BrokenWire |  | Fair | No | Isolate bank of 1-50 kva and 2- 25 kva transformers and remove customer metal light pole fall on open wire secondary phase and neutral. And reclose bank of transformers.
Outage | J.E.26.08.43981 | C001900454 | Jermaine Williams | Clarendon | Completed | Load_248081 | May Pen - 210 | 2026-08-26 07:43 | 2026-08-26 07:45 | 2026-08-26 11:15 | 2026-08-26 11:15 | 2026-08-26 11:21 | 2026-08-26 11:22 | 2026-08-26 11:45 | 2026-08-26 11:45 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.44677 | C001900451 | Jermaine Williams | Clarendon | Completed | Load_259026 | Parnassus - 210 | 2026-08-26 07:43 | 2026-08-26 07:45 | 2026-08-26 07:52 | 2026-08-26 08:27 | 2026-08-26 09:28 | 2026-08-26 09:30 | 2026-08-26 09:32 | 2026-08-26 09:32 | BrokenWire |  | Fair | No | Patrol and replaced blown 25kva 3amp xfmr fuse. Low hanging conductors due to badly leaning pole, refer to Devon Brown.
Outage | J.E.26.08.47482 | C001900450 | Jermaine Williams | Clarendon | Completed | Load_246426 | May Pen - 210 | 2026-08-26 07:43 | 2026-08-26 07:45 | 2026-08-26 13:14 | 2026-08-26 13:14 | 2026-08-26 13:55 | 2026-08-26 13:28 | 2026-08-26 13:55 | 2026-08-26 13:55 |  |  | Fair | No | Premises found ok.
Outage | J.E.26.08.47792 | C001900452 | Elvis Trowers | KSAS | Completed | Load_261218 | Greenwich - 310 | 2026-08-26 07:43 | 2026-08-26 07:44 | 2026-08-26 10:26 | 2026-08-26 10:27 | 2026-08-26 10:40 | 2026-08-26 10:40 | 2026-08-26 11:00 | 2026-08-26 11:00 |  |  | Fair | No | Customer fed from E.N box #05889 and getting no supply from the. Refer to field service.
Outage | J.E.26.08.43478 | C001900458 | Eric Williams | KSAS | Completed | Load_578715 | Duhaney - 310 | 2026-08-26 07:45 | 2026-08-26 07:46 | 2026-08-26 10:02 | 2026-08-26 10:03 | 2026-08-26 10:42 | 2026-08-26 10:46 | 2026-08-26 10:46 | 2026-08-26 10:46 |  |  | Fair | No | Streetlight issue refer to streetlight department
Outage | J.E.26.08.44035 | C001900457 | Eric Williams | KSAS | Completed | Load_242388 | Duhaney - 310 | 2026-08-26 07:45 | 2026-08-26 07:46 | 2026-08-26 09:27 | 2026-08-26 09:27 | 2026-08-26 09:54 | 2026-08-26 10:02 | 2026-08-26 10:02 | 2026-08-26 10:02 |  |  | Fair | No | Twisted secondary was disconnected and hex box was installed, customer had socket type meter and was not transferred to hexing. Refer to service
Outage | J.E.26.08.47548 | C001900460 | Eric Williams | KSAS | Completed | Load_261930 | Duhaney - 310 | 2026-08-26 07:45 | 2026-08-26 07:46 | 2026-08-26 08:36 | 2026-08-26 08:37 | 2026-08-26 08:49 | 2026-08-26 09:25 | 2026-08-26 09:27 | 2026-08-26 09:27 |  |  | Fair | No | 3 wire service corroded phase at pothead, wire cut and splice using 1 onebolt clamp
Outage | J.E.26.08.47614 | C001900459 | Eric Williams | KSAS | Completed | Load_241997 | Duhaney - 310 | 2026-08-26 07:45 | 2026-08-26 07:46 | 2026-08-26 11:05 | 2026-08-26 11:05 | 2026-08-26 11:17 | 2026-08-26 11:17 | 2026-08-26 11:17 | 2026-08-26 11:17 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.47894 | C001900461 | Michael Paterson | Westmoreland | Completed | Load_251655 | Paradise - 110 | 2026-08-26 07:46 | 2026-08-26 07:47 | 2026-08-26 09:47 | 2026-08-26 09:48 | 2026-08-26 10:40 | 2026-08-26 11:08 | 2026-08-26 11:09 | 2026-08-26 11:09 |  |  | Fair | No | Found junction fuse blown, remove John crow from line, replace 10amps fuse, supply restored,
Non-Outage | J.E.26.08.43103 | C001900465 | Richman Whyte |  | Completed |  |  | 2026-08-26 07:47 | 2026-08-26 07:51 | 2026-08-26 10:34 | 2026-08-26 10:34 | 2026-08-26 10:34 | 2026-08-26 10:36 | 2026-08-26 10:36 | 2026-08-26 10:36 |  |  | Fair | No | Customer has internal problem disconnect to carry out repair however need 110 number 6 twisted wire to carry out repair
Outage | J.E.26.08.46189 | C001900469 | Rusean Allen | KSAS | Completed | Load_238170 | Rockfort - 210 | 2026-08-26 07:48 | 2026-08-26 07:52 | 2026-08-26 08:59 | 2026-08-26 09:21 | 2026-08-26 09:54 | 2026-08-26 09:56 | 2026-08-26 09:57 | 2026-08-26 09:57 |  |  | Fair | No | Premises okay
Outage | J.E.26.08.46788 | C001900468 | Rusean Allen | KSAS | Completed | Load_270172 | Cane River - 310 | 2026-08-26 07:48 | 2026-08-26 07:52 | 2026-08-26 09:57 | 2026-08-26 09:57 | 2026-08-26 10:25 | 2026-08-26 10:42 | 2026-08-26 10:43 | 2026-08-26 10:43 |  |  | Fair | No | Broken service wire found at pole, wire was spliced and reconnected.
Outage | J.E.26.08.47882 | C001900467 | Wan Carlos Scarlett | St.Catherine | Completed | Load_254666 | Twickenham - 210 | 2026-08-26 07:48 | 2026-08-26 07:49 | 2026-08-26 11:11 | 2026-08-26 11:12 | 2026-08-26 11:44 | 2026-08-26 11:58 | 2026-08-26 11:59 | 2026-08-26 11:59 |  |  | Fair | No | Customer was reconnected from escalation department power supply has been restored
Outage | J.E.26.08.43258 | C001900471 | Richard Nicholas | St.Catherine | Completed | Load_250891 | Tredegar - 310 | 2026-08-26 07:49 | 2026-08-26 07:50 | 2026-08-26 10:16 | 2026-08-26 10:17 | 2026-08-26 10:44 | 2026-08-26 11:02 | 2026-08-26 11:06 | 2026-08-26 11:06 |  |  | Fair | No | Premises found locked however Rammy system installed at the premises.please refer to the rammy department.
Outage | J.E.26.08.45774 | C001900470 | Richard Nicholas | St.Catherine | Completed | Load_246778 | Tredegar - 310 | 2026-08-26 07:49 | 2026-08-26 07:50 | 2026-08-26 11:06 | 2026-08-26 11:07 | 2026-08-26 11:37 | 2026-08-26 12:15 | 2026-08-26 12:18 | 2026-08-26 12:18 |  |  | Fair | No | Premises found ok,is a 58watt led street light customer reported that is not working,please refer to the relevant department.
Outage | J.E.26.08.43411 | C001900472 | Donald Cunningham | St.Catherine | Completed | Load_290530 | Rhodens Pen - 210 | 2026-08-26 07:50 | 2026-08-26 11:38 | 2026-08-26 12:20 | 2026-08-26 12:21 | 2026-08-26 13:05 | 2026-08-26 13:14 | 2026-08-26 13:16 | 2026-08-26 13:16 | BrokenWire |  | Fair | No | Broken service wire from rami box refer to mr Ellison
Non-Outage | J.E.26.08.43910 | C001900477 | Edward Royal |  | Completed |  |  | 2026-08-26 07:52 | 2026-08-26 07:55 | 2026-08-26 11:06 | 2026-08-26 11:06 | 2026-08-26 11:06 | 2026-08-26 11:06 | 2026-08-26 11:08 | 2026-08-26 11:08 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.43495 | C001900479 | Edward Royal | KSAN | Completed | Load_257856 | Washington Blvd - 410 | 2026-08-26 07:52 | 2026-08-26 07:55 | 2026-08-26 10:13 | 2026-08-26 10:14 | 2026-08-26 10:13 | 2026-08-26 10:15 | 2026-08-26 10:16 | 2026-08-26 10:16 |  |  | Fair | No | Illegal connections burn off customer pothead wire customer got electrician to do repairs
Outage | J.E.26.08.43864 | C001900478 | Edward Royal | KSAN | Completed | Load_247331 | Washington Blvd - 810 | 2026-08-26 07:52 | 2026-08-26 07:55 | 2026-08-26 10:16 | 2026-08-26 10:17 | 2026-08-26 10:16 | 2026-08-26 10:17 | 2026-08-26 10:17 | 2026-08-26 10:17 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.45138 | C001900482 | Shawn Medley | St.James | Completed | Load_576009 | Bogue - 310 | 2026-08-26 07:56 | 2026-08-26 07:57 | 2026-08-26 08:12 | 2026-08-26 09:22 | 2026-08-26 09:45 | 2026-08-26 09:46 | 2026-08-26 09:47 | 2026-08-26 09:47 |  |  | Fair | No | Contact customer supply has been restored
Outage | J.E.26.08.45388 | C001900486 | Rayon Foster | Hanover | Completed | Load_246056 | Orange Bay - 310 | 2026-08-26 07:57 | 2026-08-26 07:58 | 2026-08-26 10:01 | 2026-08-26 10:14 | 2026-08-26 11:16 | 2026-08-26 12:18 | 2026-08-26 12:18 | 2026-08-26 12:18 |  |  | Fair | No | Patrol secondary line to find 1 blown 25kva transformer fuse complete line patrol before replacing 1 2amp fuse at same and close
Outage | J.E.26.08.45863 | C001900483 | Elvis Trowers | KSAS | Completed | Load_269531 | Up Park Camp - 410 | 2026-08-26 07:57 | 2026-08-26 08:05 | 2026-08-26 11:00 | 2026-08-26 11:13 | 2026-08-26 11:27 | 2026-08-26 11:30 | 2026-08-26 11:32 | 2026-08-26 11:32 |  |  | Fair | No | Reset customer circuit breakers Found tripped.
Outage | J.E.26.08.46091 | C001900484 | Rayon Foster | Hanover | Completed | Load_250299 | Orange Bay - 310 | 2026-08-26 07:57 | 2026-08-26 07:58 | 2026-08-26 08:11 | 2026-08-26 09:50 | 2026-08-26 09:50 | 2026-08-26 09:50 | 2026-08-26 09:50 | 2026-08-26 09:50 |  |  | Fair | No | Damage meter voltage check in meter socket 108/108AB216 refer to field service to have meter change
Outage | J.E.26.08.46093 | C001900485 | Rayon Foster | Hanover | Completed | Load_250299 | Orange Bay - 310 | 2026-08-26 07:57 | 2026-08-26 07:58 | 2026-08-26 08:11 | 2026-08-26 08:14 | 2026-08-26 09:31 | 2026-08-26 09:40 | 2026-08-26 09:50 | 2026-08-26 09:50 |  |  | Fair | No | Damage meter voltage check in meter socket 108/108AB216 refer to field service to have meter change
Outage | J.E.26.08.41029 | C001900487 | Shawn Medley | St.James | Completed | Load_301642 | Bogue - 310 | 2026-08-26 07:58 | 2026-08-26 07:59 | 2026-08-26 08:12 | 2026-08-26 08:52 | 2026-08-26 09:19 | 2026-08-26 09:19 | 2026-08-26 09:20 | 2026-08-26 09:20 |  |  | Fair | No | Customer said supply has been restored
Outage | J.E.26.08.42689 | C001900488 | Marlon Brown | Trelawny | Completed | Load_247755 | Martha Brae - 210 | 2026-08-26 07:59 | 2026-08-26 08:00 | 2026-08-26 08:12 | 2026-08-26 08:13 | 2026-08-26 08:38 | 2026-08-26 08:55 | 2026-08-26 08:55 | 2026-08-26 08:55 |  |  | Fair | No | Defective meter, refer to Field Service Voltage at pothead 120/120=240Voltage leaving at pothead 120/120=240. Franklyn Coach.
Non-Outage | J.E.26.08.28027 | C001900491 | Kenroy Dale |  | Completed |  |  | 2026-08-26 08:00 | 2026-08-26 08:01 | 2026-08-26 10:11 | 2026-08-26 10:13 | 2026-08-26 12:05 | 2026-08-26 12:08 | 2026-08-26 12:09 | 2026-08-26 12:09 |  |  | Fair | No | Customer has internal problems voltage reading 114/111/225
Outage | J.E.26.08.42356 | C001900490 | Marlon Brown | Trelawny | Completed | Load_251635 | Greenwood - 210 | 2026-08-26 08:00 | 2026-08-26 08:00 | 2026-08-26 08:09 | 2026-08-26 08:10 | 2026-08-26 08:09 | 2026-08-26 08:10 | 2026-08-26 08:10 | 2026-08-26 08:10 |  |  | Fair | No | St James call
Outage | J.E.26.08.42561 | C001900489 | Marlon Brown | Trelawny | Completed | Load_556059 | Martha Brae - 110 | 2026-08-26 08:00 | 2026-08-26 08:00 | 2026-08-26 08:56 | 2026-08-26 08:57 | 2026-08-26 09:11 | 2026-08-26 09:13 | 2026-08-26 09:13 | 2026-08-26 09:13 |  |  | Fair | No | Customer meter socket is defective, however supply has been disconnected for customer to effect repairs by a previous emergency team.
Non-Outage | J.E.26.08.41116 | C001900498 | Dwain Samuels | Westmoreland | Completed | Load_245109 | Paradise - 210 | 2026-08-26 08:05 | 2026-08-26 08:06 | 2026-08-26 08:24 | 2026-08-26 10:05 | 2026-08-26 10:28 | 2026-08-26 11:10 | 2026-08-26 11:11 | 2026-08-26 11:11 |  |  | Fair | No | Area affected by low voltage transformer serving too far . Voltage check 109-109-218
Outage | J.E.26.08.38131 | C001900497 | Eric Williams | KSAS | Completed | Load_257381 | Duhaney - 310 | 2026-08-26 08:05 | 2026-08-26 08:06 | 2026-08-26 10:47 | 2026-08-26 10:48 | 2026-08-26 10:57 | 2026-08-26 11:04 | 2026-08-26 11:05 | 2026-08-26 11:05 |  |  | Fair | No | Meter reconnected with help from escalation
Outage | J.E.26.08.43465 | C001900496 | Romeo Brissett | St.James | Completed | Load_1001859 | Bogue - 610 | 2026-08-26 08:05 | 2026-08-26 08:05 | 2026-08-26 08:31 | 2026-08-26 08:32 | 2026-08-26 08:32 | 2026-08-26 08:14 | 2026-08-26 08:33 | 2026-08-26 08:33 |  |  | Fair | No | Customer stated power was restored from last night.
Non-Outage | J.E.26.08.40138 | C001900501 | Error Coore | Manchester | Completed | Load_265696 | Spur Tree - 310 | 2026-08-26 08:07 | 2026-08-26 08:08 | 2026-08-26 14:02 | 2026-08-26 14:02 | 2026-08-26 15:06 | 2026-08-26 15:26 | 2026-08-26 15:28 | 2026-08-26 15:28 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.08.41018 | C001900500 | Error Coore | Manchester | Completed | Load_244647 | Spur Tree - 310 | 2026-08-26 08:07 | 2026-08-26 08:07 | 2026-08-26 08:24 | 2026-08-26 08:24 | 2026-08-26 09:26 | 2026-08-26 09:42 | 2026-08-26 09:45 | 2026-08-26 09:45 |  |  | Fair | No | Found customer service wire defective unable to carry out repair due to customer defective wire holder customer was advised to get repair done
Non-Outage | J.E.26.08.37009 | C001900502 | Error Coore | Manchester | Completed | Load_1002366 | Spur Tree - 310 | 2026-08-26 08:08 | 2026-08-26 08:08 | 2026-08-26 09:45 | 2026-08-26 09:46 | 2026-08-26 10:31 | 2026-08-26 11:24 | 2026-08-26 11:27 | 2026-08-26 11:27 |  |  | Fair | No | Found customer with wrap connection at pothead remade wrap connection using 3 service sleeve voltage reading 118/117/235 volts
Non-Outage | J.E.26.08.41602 | C001900503 | Error Coore | Manchester | Completed | Load_264906 | Spur Tree - 310 | 2026-08-26 08:09 | 2026-08-26 08:10 | 2026-08-26 11:28 | 2026-08-26 11:29 | 2026-08-26 12:21 | 2026-08-26 12:28 | 2026-08-26 12:29 | 2026-08-26 12:29 |  |  | Fair | No | Unable to carry out repair due to leaning pole refer to a emergency bucket truck crew
Non-Outage | J.E.26.08.28709 | C001900504 | Error Coore | Manchester | Completed | Load_251691 | Spur Tree - 310 | 2026-08-26 08:10 | 2026-08-26 08:11 | 2026-08-26 12:30 | 2026-08-26 12:31 | 2026-08-26 13:47 | 2026-08-26 13:59 | 2026-08-26 14:01 | 2026-08-26 14:01 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.08.35505 | C001900518 | Royston Montague | St.Catherine | Completed | Load_245058 | Tredegar - 510 | 2026-08-26 08:11 | 2026-08-26 08:14 | 2026-08-26 08:34 | 2026-08-26 13:26 | 2026-08-26 14:00 | 2026-08-26 14:01 | 2026-08-26 14:01 | 2026-08-26 14:01 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.08.35791 | C001900511 | Royston Montague | St.Catherine | Completed | Load_245058 | Tredegar - 510 | 2026-08-26 08:11 | 2026-08-26 08:14 | 2026-08-26 08:34 | 2026-08-26 12:25 | 2026-08-26 12:34 | 2026-08-26 12:36 | 2026-08-26 12:36 | 2026-08-26 12:36 |  |  | Fair | No | Location found ok. 228v 113v 114v
Non-Outage | J.E.26.08.35950 | C001900514 | Royston Montague | St.Catherine | Completed | Load_1000334 | Tredegar - 210 | 2026-08-26 08:11 | 2026-08-26 08:14 | 2026-08-26 08:34 | 2026-08-26 12:37 | 2026-08-26 13:08 | 2026-08-26 13:25 | 2026-08-26 13:26 | 2026-08-26 13:26 |  |  | Fair | No | Faulty meter socket, customer informed to get same repair. 230v 110v 115v
Non-Outage | J.E.26.08.36324 | C001900512 | Royston Montague | St.Catherine | Completed | Load_1001538 | Tredegar - 510 | 2026-08-26 08:11 | 2026-08-26 08:14 | 2026-08-26 08:34 | 2026-08-26 14:02 | 2026-08-26 14:10 | 2026-08-26 14:10 | 2026-08-26 14:10 | 2026-08-26 14:10 |  |  | Fair | No | Rami system in area. Please assign this job to the relevant team thanks.
Non-Outage | J.E.26.08.36491 | C001900510 | Royston Montague | St.Catherine | Completed | Load_239794 | Tredegar - 210 | 2026-08-26 08:11 | 2026-08-26 08:14 | 2026-08-26 08:34 | 2026-08-26 14:11 | 2026-08-26 14:35 | 2026-08-26 14:36 | 2026-08-26 14:36 | 2026-08-26 14:36 |  |  | Fair | No | Location found ok. Full voltage 225v 113v 110v
Non-Outage | J.E.26.08.37289 | C001900509 | Royston Montague | St.Catherine | Completed | Load_260913 | Tredegar - 210 | 2026-08-26 08:11 | 2026-08-26 08:14 | 2026-08-26 08:34 | 2026-08-26 14:55 | 2026-08-26 14:55 | 2026-08-27 08:18 | 2026-08-27 08:18 | 2026-08-27 08:18 |  |  | Fair | No | Faulty meter socket, customer electrician repair same, voltage 224v 112v 110v
Non-Outage | J.E.26.08.41661 | C001900507 | Royston Montague | St.Catherine | Completed | Load_266660 | Twickenham - 310 | 2026-08-26 08:11 | 2026-08-26 08:14 | 2026-08-26 08:35 | 2026-08-26 10:10 | 2026-08-26 10:22 | 2026-08-26 10:40 | 2026-08-26 10:40 | 2026-08-26 10:40 |  |  | Fair | No | Faulty neutral at pothead, same corrected voltage found 126v 100v voltage after job completion are 226v 110v 112v
Non-Outage | J.E.26.08.43350 | C001900508 | Royston Montague | St.Catherine | Completed | Load_267960 | Twickenham - 310 | 2026-08-26 08:11 | 2026-08-26 08:14 | 2026-08-26 08:35 | 2026-08-26 09:23 | 2026-08-26 09:54 | 2026-08-26 10:08 | 2026-08-26 10:08 | 2026-08-26 10:08 |  |  | Fair | No | Open phase at customer pothead. Same corrected. Voltage found 114v voltage after job completion are 228v 114v 112v
Non-Outage | J.E.26.08.35233 | C001900519 | Royston Montague | St.Catherine | Completed | Load_245058 | Tredegar - 510 | 2026-08-26 08:12 | 2026-08-26 08:14 | 2026-08-26 08:34 | 2026-08-26 10:48 | 2026-08-26 11:37 | 2026-08-26 12:23 | 2026-08-26 12:23 | 2026-08-26 12:23 |  |  | Fair | No | Burn joint at pothead. Same corrected. Voltage found 110v 99v 211v voltage after job completion are 227v 113v 112v
Non-Outage | J.E.26.08.26450 | C001900522 | Omar Harris | St.Ann | Completed | Load_264883 | Ocho Rios - 510 | 2026-08-26 08:15 | 2026-08-26 08:16 | 2026-08-26 08:41 | 2026-08-26 09:26 | 2026-08-26 09:26 | 2026-08-26 09:27 | 2026-08-26 09:27 | 2026-08-26 09:27 |  |  | Fair | No | Not getting through to customer, several attempts made.
Non-Outage | J.E.26.08.27100 | C001900521 | Omar Harris | St.Ann | Completed | Load_245767 | Ocho Rios - 310 | 2026-08-26 08:15 | 2026-08-26 08:16 | 2026-08-26 10:11 | 2026-08-26 10:12 | 2026-08-26 11:22 | 2026-08-26 11:22 | 2026-08-26 11:24 | 2026-08-26 11:24 |  |  | Fair | No | Customer cell is going straight voicemail.. several attempts made .
Non-Outage | J.E.26.08.27721 | C001900520 | Omar Harris | St.Ann | Completed | Load_295275 | Ocho Rios - 410 | 2026-08-26 08:15 | 2026-08-26 08:16 | 2026-08-26 12:42 | 2026-08-26 12:42 | 2026-08-26 12:42 | 2026-08-26 12:43 | 2026-08-26 12:44 | 2026-08-26 12:44 |  |  | Fair | No | Rami in area refer to field service.. area needs traffic management.
Non-Outage | J.E.26.08.26204 | C001900523 | Omar Harris | St.Ann | Completed | Load_249489 | Ocho Rios - 510 | 2026-08-26 08:16 | 2026-08-26 08:16 | 2026-08-26 09:28 | 2026-08-26 09:28 | 2026-08-26 10:04 | 2026-08-26 10:06 | 2026-08-26 10:11 | 2026-08-26 10:11 |  |  | Fair | No | Not getting through to customer, several attempts made .
Non-Outage | J.E.26.08.46054 | C001900530 | Orville Lee | St.Catherine | Completed | Load_257054 | Twickenham - 210 | 2026-08-26 08:18 | 2026-08-26 08:20 | 2026-08-26 11:00 | 2026-08-26 11:01 | 2026-08-26 11:01 | 2026-08-26 12:07 | 2026-08-26 12:09 | 2026-08-26 12:09 |  |  | Fair | No | Checks made and found pothead and secondary connections corroded 5 one bolt clamps usedVoltage114v117v231v
Non-Outage | J.E.26.08.46848 | C001900529 | Wan Carlos Scarlett | St.Catherine | Completed | Load_266814 | Twickenham - 210 | 2026-08-26 08:18 | 2026-08-26 08:18 | 2026-08-26 08:50 | 2026-08-26 08:51 | 2026-08-26 09:29 | 2026-08-26 11:08 | 2026-08-26 11:11 | 2026-08-26 11:11 |  |  | Fair | No | Found customer 3 wire service at pole with phase and neutral corroded use 3 one bolt clamps at open secondary line phase and neutral readings 113-114-229
Non-Outage | J.E.26.08.38656 | C001900534 | Orville Lee | Portmore | Completed | Load_245174 | Naggo Head - 610 | 2026-08-26 08:19 | 2026-08-26 08:20 | 2026-08-26 09:54 | 2026-08-26 09:56 | 2026-08-26 10:24 | 2026-08-26 10:24 | 2026-08-26 10:31 | 2026-08-26 10:31 |  |  | Fair | No | Checks made and found secondary connection corroded Four one bolt clamps usedVoltage121v119v240v
Non-Outage | J.E.26.08.40815 | C001900533 | Orville Lee | Portmore | Completed | Load_557225 | Naggo Head - 610 | 2026-08-26 08:19 | 2026-08-26 08:20 | 2026-08-26 09:14 | 2026-08-26 09:33 | 2026-08-26 09:34 | 2026-08-26 09:41 | 2026-08-26 09:42 | 2026-08-26 09:42 |  |  | Fair | No | Premises closed upon arrival Call to customer unanswered Customer has a defective meter socket Voltage122v121v244v
Non-Outage | J.E.26.08.29274 | C001900540 | Error Coore | Manchester | Completed | Load_241957 | Spur Tree - 310 | 2026-08-26 08:21 | 2026-08-26 08:22 | 2026-08-26 15:28 | 2026-08-26 15:29 | 2026-08-26 15:54 | 2026-08-26 16:15 | 2026-08-26 16:16 | 2026-08-26 16:16 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.08.42257 | C001900551 | Odaine Johnson | Clarendon | Completed | Load_254971 | Monymusk - 410 | 2026-08-26 08:23 | 2026-08-26 08:25 | 2026-08-26 08:58 | 2026-08-26 13:09 | 2026-08-26 13:32 | 2026-08-26 13:39 | 2026-08-26 13:40 | 2026-08-26 13:40 |  |  | Fair | No | Corroded phase found at pothead remade connection using 1 pen union voltage reading 110/111/222 volts
Non-Outage | J.E.26.08.43352 | C001900549 | Odaine Johnson | Clarendon | Completed | Load_242680 | Parnassus - 210 | 2026-08-26 08:23 | 2026-08-26 08:25 | 2026-08-26 08:58 | 2026-08-26 09:47 | 2026-08-26 10:29 | 2026-08-26 10:29 | 2026-08-26 10:30 | 2026-08-26 10:30 |  |  | Fair | No | Corroded phase found at pole remade connection using 1 one bolt clamp voltage reading 114/114/229 volts
Non-Outage | J.E.26.08.44664 | C001900550 | Odaine Johnson | Clarendon | Completed | Load_573392 | Parnassus - 310 | 2026-08-26 08:23 | 2026-08-26 08:25 | 2026-08-26 08:58 | 2026-08-26 10:30 | 2026-08-26 11:55 | 2026-08-26 11:55 | 2026-08-26 11:56 | 2026-08-26 11:56 |  |  | Fair | No | Premises found okay customer stated that the issue was resolved
Non-Outage | J.E.26.08.46050 | C001900548 | Odaine Johnson | Clarendon | Completed | Load_246426 | May Pen - 210 | 2026-08-26 08:23 | 2026-08-26 08:25 | 2026-08-26 08:58 | 2026-08-26 11:56 | 2026-08-26 13:08 | 2026-08-26 13:08 | 2026-08-26 13:08 | 2026-08-26 13:08 |  |  | Fair | No | Premises not found multiple efforts made to contact customer but unsuccessful
Non-Outage | J.E.26.08.36153 | C001900554 | Odaine Johnson | Clarendon | Completed | Load_267585 | Parnassus - 310 | 2026-08-26 08:24 | 2026-08-26 08:25 | 2026-08-26 08:58 | 2026-08-26 09:44 | 2026-08-26 09:46 | 2026-08-26 09:46 | 2026-08-26 09:46 | 2026-08-26 09:46 |  |  | Fair | No | Emergency team needed to rectify issue
Non-Outage | J.E.26.08.41323 | C001900552 | Neville Spencer | Clarendon | Completed | Load_268208 | May Pen - 110 | 2026-08-26 08:24 | 2026-08-27 15:30 | 2026-08-27 15:58 | 2026-08-27 15:58 | 2026-08-27 17:10 | 2026-08-27 17:37 | 2026-08-27 17:41 | 2026-08-27 17:41 |  |  | Fair | No | Splice and retention broken neutral on 3, wire service used 20 ft#6 triplex , 2 clamps voltage reading 112 114 228 supply restored.
Outage | J.E.26.08.32859 | C001900562 | Moses Elliston | St.Catherine | Completed | Load_257717 | Rhodens Pen - 210 | 2026-08-26 08:27 | 2026-08-26 11:36 | 2026-08-26 17:12 | 2026-08-26 17:13 | 2026-08-26 17:12 | 2026-08-26 16:40 | 2026-08-26 17:14 | 2026-08-26 17:14 |  |  | Fair | No | Not located .Customer not at location
Non-Outage | J.E.26.08.36392 | C001900563 | Dwain Samuels | St.Elizabeth | Completed | Load_262020 | Maggotty - 110 | 2026-08-26 08:29 | 2026-08-26 08:30 | 2026-08-26 08:50 | 2026-08-27 09:00 | 2026-08-27 10:15 | 2026-08-27 10:37 | 2026-08-27 10:40 | 2026-08-27 10:40 |  |  | Fair | No | Connect 3 wire meter. Use 115ft #6 service wire. Use 3 pen union clamp and 3 one bolt clamp. Voltage check 115-114-229
Non-Outage | J.E.26.08.42479 | C001900564 | Marlon Authors | Manchester | Completed | Load_292943 | Spur Tree - 210 | 2026-08-26 08:30 | 2026-08-26 08:31 | 2026-08-26 09:32 | 2026-08-26 09:32 | 2026-08-26 09:49 | 2026-08-26 10:21 | 2026-08-26 10:21 | 2026-08-26 10:21 |  |  | Fair | No | Supply checked and found corrosion. Repair pole, pothead and mid- span using three clamps and five linkets. Supply leave working ok rdg 112v,111v and cross phased 223 volts
Non-Outage | J.E.26.08.32653 | C001900565 | Marlon Authors | Manchester | Completed | Load_258101 | Spur Tree - 210 | 2026-08-26 08:31 | 2026-08-26 08:31 | 2026-08-26 11:01 | 2026-08-26 11:02 | 2026-08-26 11:01 | 2026-08-26 11:18 | 2026-08-26 11:18 | 2026-08-26 11:18 | BangingWires |  | Fair | No | Patrol and found illegal connections putting the secondary conductors close together. Please refer same to the field services department for further assistance
Outage | J.E.26.08.47976 | C001900574 | Selvin White | St.Elizabeth | Completed | Load_264727 | Maggotty - 110 | 2026-08-26 08:37 | 2026-08-26 08:38 | 2026-08-26 13:11 | 2026-08-26 13:12 | 2026-08-26 13:49 | 2026-08-26 14:31 | 2026-08-26 14:31 | 2026-08-26 14:31 |  |  | Fair | No | Replaced a blown 8 amp junction fuse and also a 2 amp fuse for a 25 kva transformer circuit that supply the cell site in Johnson district after patrolling single phase primary line. Supply restored. Lightning strikes were said to be the cause.
Non-Outage | J.E.26.05.36275 | C001900577 | Odeanie Davis | KSAS | Completed | Load_293562 | Three Miles - 410 | 2026-08-26 08:38 | 2026-08-26 08:40 | 2026-08-26 08:56 | 2026-08-26 12:54 | 2026-08-26 12:53 | 2026-08-26 13:20 | 2026-08-26 12:54 | 2026-08-26 12:54 |  |  | Fair | No
Non-Outage | J.E.26.05.36305 | C001900578 | Odeanie Davis | KSAS | Completed | Load_240971 | Three Miles - 410 | 2026-08-26 08:38 | 2026-08-26 08:40 | 2026-08-26 09:03 | 2026-08-26 15:20 | 2026-08-26 15:20 | 2026-08-26 15:20 | 2026-08-26 15:21 | 2026-08-26 15:21 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.06.20161 | C001900576 | Odeanie Davis | KSAN | Completed | Load_293710 | Washington Blvd - 710 | 2026-08-26 08:38 | 2026-08-26 08:40 | 2026-08-26 09:26 | 2026-08-26 09:26 | 2026-08-26 09:26 | 2026-08-26 09:54 | 2026-08-26 09:56 | 2026-08-26 09:56 |  |  | Fair | No | 112v/100v at arrival, Loose circuit at pothead corrected, 1 penn union, 112v/113v & 225v after correction
Non-Outage | J.E.26.06.31813 | C001900575 | Odeanie Davis | KSAS | Completed | Load_240685 | Hunts Bay - 510 | 2026-08-26 08:38 | 2026-08-26 08:40 | 2026-08-26 09:22 | 2026-08-26 12:52 | 2026-08-26 12:52 | 2026-08-26 13:00 | 2026-08-26 12:53 | 2026-08-26 12:53 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.05.14859 | C001900580 | Odeanie Davis | KSAS | Completed | Load_245982 | Three Miles - 410 | 2026-08-26 08:39 | 2026-08-26 08:40 | 2026-08-26 10:56 | 2026-08-26 11:14 | 2026-08-26 11:41 | 2026-08-26 11:43 | 2026-08-26 11:43 | 2026-08-26 11:43 |  |  | Fair | No | 119v/120v & 239v at location under load , customer power found ok, no issues found
Non-Outage | J.E.26.05.14964 | C001900581 | Odeanie Davis | KSAS | Completed | Load_257442 | Three Miles - 410 | 2026-08-26 08:39 | 2026-08-26 08:40 | 2026-08-26 09:57 | 2026-08-26 09:58 | 2026-08-26 10:17 | 2026-08-26 10:54 | 2026-08-26 10:51 | 2026-08-26 10:51 |  |  | Fair | No | 116v/0V in panel at arrival, customer states that light bill too high, customer wires was tampered with and an illegal connection was on customer’s wire, customer was only receiving a single phase, technician removed Illegal connection and reconnected customer, 1 penn union, 117v/116v & 235v after correction.
Non-Outage | J.E.26.08.05293 | C001900582 | Odeanie Davis | KSAS | Completed | Load_255919 | Hunts Bay - 310 | 2026-08-26 08:39 | 2026-08-26 08:40 | 2026-08-26 11:44 | 2026-08-26 12:08 | 2026-08-26 12:07 | 2026-08-26 12:17 | 2026-08-26 12:08 | 2026-08-26 12:08 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.07179 | C001900579 | Odeanie Davis | KSAS | Completed | Load_239499 | Rockfort - 410 | 2026-08-26 08:39 | 2026-08-26 08:40 | 2026-08-26 08:51 | 2026-08-26 15:21 | 2026-08-26 15:21 | 2026-08-26 15:33 | 2026-08-26 15:21 | 2026-08-26 15:21 |  |  | Fair | No
Non-Outage | J.E.26.08.43252 | C001900587 | Damion Reid | Manchester | Completed | Load_254433 | Spur Tree - 310 | 2026-08-26 08:45 | 2026-08-26 08:46 | 2026-08-26 12:30 | 2026-08-26 12:31 | 2026-08-26 13:24 | 2026-08-26 14:09 | 2026-08-26 14:11 | 2026-08-26 14:11 |  |  | Fair | No | Remade corroded phase at secondary pole for 3 wire service using one 1 bolt clamp
Non-Outage | J.E.26.08.29246 | C001900596 | Rochaine Hussey | KSAS | Completed | Load_252777 | Greenwich - 510 | 2026-08-26 08:48 | 2026-08-26 08:50 | 2026-08-26 09:49 | 2026-08-27 16:54 | 2026-08-27 16:54 | 2026-08-27 16:55 | 2026-08-27 16:55 | 2026-08-27 16:55 |  |  | Fair | No | Customer said issue was already resolved
Non-Outage | J.E.26.08.29513 | C001900595 | Rochaine Hussey | KSAN | Completed | Load_245786 | Washington Blvd - 310 | 2026-08-26 08:48 | 2026-08-26 08:50 | 2026-08-26 09:18 | 2026-08-26 13:32 | 2026-08-26 13:32 | 2026-08-26 13:33 | 2026-08-26 13:33 | 2026-08-26 13:33 |  |  | Fair | No | Customer say the issue was resolved and power was restored
Non-Outage | J.E.26.08.35193 | C001900597 | Rochaine Hussey | KSAS | Completed | Load_237669 | Up Park Camp - 310 | 2026-08-26 08:48 | 2026-08-26 08:50 | 2026-08-26 09:20 | 2026-08-27 16:13 | 2026-08-27 16:12 | 2026-08-27 16:13 | 2026-08-27 16:13 | 2026-08-27 16:13 |  |  | Fair | No | Customer said issue was already resolved
Non-Outage | J.E.26.08.36274 | C001900598 | Rochaine Hussey | KSAS | Completed | Load_257911 | Rockfort - 410 | 2026-08-26 08:48 | 2026-08-26 08:50 | 2026-08-26 14:18 | 2026-08-26 14:18 | 2026-08-26 14:18 | 2026-08-26 14:19 | 2026-08-26 14:19 | 2026-08-26 14:19 |  |  | Fair | No | Slack connection on pole Issue was resolved 115v
Non-Outage | J.E.26.08.36283 | C001900600 | Rochaine Hussey | KSAS | Completed | Load_257911 | Rockfort - 410 | 2026-08-26 08:48 | 2026-08-26 08:50 | 2026-08-26 13:54 | 2026-08-26 13:54 | 2026-08-26 13:56 | 2026-08-26 14:16 | 2026-08-26 14:16 | 2026-08-26 14:16 |  |  | Fair | No | Slack connection on pole issue resolved 115v
Non-Outage | J.E.26.08.36901 | C001900599 | Rochaine Hussey | KSAS | Completed | Load_265623 | Rockfort - 210 | 2026-08-26 08:48 | 2026-08-26 08:50 | 2026-08-26 11:43 | 2026-08-26 11:44 | 2026-08-26 12:38 | 2026-08-26 13:31 | 2026-08-26 13:32 | 2026-08-26 13:32 |  |  | Fair | No | Display on customer meter is out meter needs to be changed Voltage at Premesis is found okay 117/119/236v
Outage | J.E.26.08.47949 | C001900594 | Kemark Slue | St.Catherine | Completed | Load_243706 | New Michelton - 210 | 2026-08-26 08:48 | 2026-08-26 08:49 | 2026-08-26 08:55 | 2026-08-26 08:56 | 2026-08-26 11:18 | 2026-08-26 09:00 | 2026-08-26 11:18 | 2026-08-26 11:18 |  |  | Fair | No | Premises was checked and found okay.
Non-Outage | J.E.26.08.37718 | C001900601 | Rochaine Hussey | KSAS | Completed | Load_247938 | Hunts Bay - 310 | 2026-08-26 08:49 | 2026-08-26 08:50 | 2026-08-26 11:25 | 2026-08-27 12:28 | 2026-08-27 12:28 | 2026-08-27 13:13 | 2026-08-27 13:14 | 2026-08-27 13:14 |  |  | Fair | No | Customer say the issue was resolved
Non-Outage | J.E.26.08.45811 | C001900602 | Rochaine Hussey | KSAS | Completed | Load_245842 | Up Park Camp - 510 | 2026-08-26 08:49 | 2026-08-26 08:50 | 2026-08-26 14:27 | 2026-08-26 14:27 | 2026-08-26 14:27 | 2026-08-26 14:32 | 2026-08-26 14:32 | 2026-08-26 14:32 |  |  | Fair | No | Bucket truck needed 107/107Transformer needs to be check
Non-Outage | J.E.26.07.14712 | C001900604 | Odeanie Davis | KSAS | Completed | Load_247734 | Three Miles - 510 | 2026-08-26 08:51 | 2026-08-26 08:51 | 2026-08-26 09:03 | 2026-08-26 15:22 | 2026-08-26 15:22 | 2026-08-26 15:52 | 2026-08-26 15:23 | 2026-08-26 15:23 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.07.18026 | C001900606 | Fredrick Hamilton | KSAN | Completed | Load_267241 | Washington Blvd - 310 | 2026-08-26 08:51 | 2026-08-26 08:54 | 2026-08-26 09:00 | 2026-08-26 12:26 | 2026-08-26 12:26 | 2026-08-26 12:29 | 2026-08-26 12:29 | 2026-08-26 12:29 |  |  | Fair | No | Customer contacted and stated that power was restored fully previously Premises is ok
Non-Outage | J.E.26.07.37828 | C001900611 | Fredrick Hamilton | KSAN | Completed | Load_265180 | Washington Blvd - 310 | 2026-08-26 08:52 | 2026-08-26 08:54 | 2026-08-26 09:00 | 2026-08-26 10:58 | 2026-08-26 11:16 | 2026-08-26 11:37 | 2026-08-26 11:37 | 2026-08-26 11:37 |  |  | Fair | No | Premises is ok at time of visit no JPS issue detected 238v/118v/120v obtained
Non-Outage | J.E.26.08.01149 | C001900612 | Fredrick Hamilton | KSAN | Completed | Load_267816 | Washington Blvd - 310 | 2026-08-26 08:52 | 2026-08-26 08:54 | 2026-08-26 09:00 | 2026-08-26 10:49 | 2026-08-26 10:51 | 2026-08-26 10:53 | 2026-08-26 10:53 | 2026-08-26 10:53 |  |  | Fair | No | Customer contacted and stated that power was restored fully weeks ago Premises is ok
Non-Outage | J.E.26.08.01493 | C001900613 | Fredrick Hamilton | KSAN | Completed | Load_242936 | Washington Blvd - 310 | 2026-08-26 08:52 | 2026-08-26 08:54 | 2026-08-26 09:00 | 2026-08-26 10:36 | 2026-08-26 10:41 | 2026-08-26 10:48 | 2026-08-26 10:48 | 2026-08-26 10:48 |  |  | Fair | No | Bushing required at location tree causing secondary to be banging together Bushing team required
Non-Outage | J.E.26.08.14030 | C001900614 | Fredrick Hamilton | KSAN | Completed | Load_254100 | Washington Blvd - 310 | 2026-08-26 08:53 | 2026-08-26 08:54 | 2026-08-26 09:00 | 2026-08-26 10:32 | 2026-08-26 10:32 | 2026-08-26 10:33 | 2026-08-26 10:33 | 2026-08-26 10:33 |  |  | Fair | No | Customer contacted and stated that power was restored fully at location 2 weeks agoPremises is ok
Non-Outage | J.E.26.08.14200 | C001900615 | Fredrick Hamilton | KSAN | Completed | Load_246286 | Washington Blvd - 310 | 2026-08-26 08:53 | 2026-08-26 08:54 | 2026-08-26 09:00 | 2026-08-26 11:38 | 2026-08-26 11:45 | 2026-08-26 12:16 | 2026-08-26 12:16 | 2026-08-26 12:16 |  |  | Fair | No | Single phase detected at pole same was corrected 1 clamp used
Non-Outage | J.E.26.08.14536 | C001900616 | Fredrick Hamilton | KSAN | Completed | Load_249371 | Washington Blvd - 710 | 2026-08-26 08:53 | 2026-08-26 08:54 | 2026-08-26 09:00 | 2026-08-26 09:20 | 2026-08-26 09:42 | 2026-08-26 10:28 | 2026-08-26 10:30 | 2026-08-26 10:30 |  |  | Fair | No | 215v/105v/110v Low voltage detected on secondary line requesting emergency to check transformer Pothead,meter socket and pole checked
Non-Outage | J.E.26.08.29847 | C001900621 | Oraine Minto | St.Ann | Completed | Load_241168 | Upper White River - 210 | 2026-08-26 08:53 | 2026-08-26 08:54 | 2026-08-26 12:02 | 2026-08-26 12:03 | 2026-08-26 12:03 | 2026-08-26 12:03 | 2026-08-26 12:03 | 2026-08-26 12:03 |  |  | Fair | No | Customer states power was restored
Non-Outage | J.E.26.08.31050 | C001900620 | Oraine Minto | St.Ann | Completed | Load_264396 | Upper White River - 210 | 2026-08-26 08:53 | 2026-08-26 08:54 | 2026-08-27 13:35 | 2026-08-27 14:06 | 2026-08-27 14:06 | 2026-08-27 14:06 | 2026-08-27 14:08 | 2026-08-27 14:08 |  |  | Fair | No | 224v 109v 115v Issue look the be on the customer wire leading to the house Customer was advised to get a licensed electrician to check and fix the issue
Non-Outage | J.E.26.08.35215 | C001900618 | Oraine Minto | St.Ann | Completed | Load_261813 | Upper White River - 210 | 2026-08-26 08:53 | 2026-08-26 08:54 | 2026-08-27 15:06 | 2026-08-27 15:07 | 2026-08-27 15:06 | 2026-08-27 15:07 | 2026-08-27 15:41 | 2026-08-27 15:41 |  |  | Fair | No | 237v 117v 118v Customer was advised to change meter socket
Non-Outage | J.E.26.08.35804 | C001900619 | Oraine Minto | St.Ann | Completed | Load_261813 | Upper White River - 210 | 2026-08-26 08:53 | 2026-08-26 08:54 | 2026-08-27 15:09 | 2026-08-27 15:42 | 2026-08-27 15:41 | 2026-08-27 15:42 | 2026-08-27 15:42 | 2026-08-27 15:42 |  |  | Fair | No | 237v 117v 118v
Non-Outage | J.E.26.08.36326 | C001900617 | Oraine Minto | St.Ann | Completed | Load_245539 | Roaring River - 210 | 2026-08-26 08:53 | 2026-08-26 08:54 | 2026-08-26 12:10 | 2026-08-26 12:10 | 2026-08-26 12:10 | 2026-08-26 12:10 | 2026-08-26 12:11 | 2026-08-26 12:11 |  |  | Fair | No | Need better directions and customer not answering
Non-Outage | J.E.26.08.27042 | C001900624 | Oraine Minto | St.Ann | Completed | Load_238296 | Upper White River - 210 | 2026-08-26 08:54 | 2026-08-26 08:54 | 2026-08-26 12:04 | 2026-08-26 12:04 | 2026-08-26 12:04 | 2026-08-26 12:05 | 2026-08-26 12:06 | 2026-08-26 12:06 |  |  | Fair | No
Non-Outage | J.E.26.08.27292 | C001900623 | Oraine Minto | St.Ann | Completed | Load_255449 | Roaring River - 210 | 2026-08-26 08:54 | 2026-08-26 08:54 | 2026-08-26 11:55 | 2026-08-26 11:55 | 2026-08-26 11:55 | 2026-08-26 11:55 | 2026-08-26 11:59 | 2026-08-26 11:59 |  |  | Fair | No | Power was restored
Non-Outage | J.E.26.08.29232 | C001900622 | Oraine Minto | St.Ann | Completed | Load_242320 | Upper White River - 210 | 2026-08-26 08:54 | 2026-08-26 08:54 | 2026-08-27 14:08 | 2026-08-27 14:44 | 2026-08-27 14:44 | 2026-08-27 14:44 | 2026-08-27 14:45 | 2026-08-27 14:45 |  |  | Fair | No | 1 one bolt clamp was used 238v 120v 118v
Non-Outage | J.E.26.08.30491 | C001900625 | Locksley Allen | St.Ann | Completed | Load_259886 | Upper White River - 110 | 2026-08-26 08:56 | 2026-08-26 08:57 | 2026-08-26 14:56 | 2026-08-26 14:57 | 2026-08-26 14:56 | 2026-08-26 15:02 | 2026-08-26 14:58 | 2026-08-26 14:58 |  |  | Fair | No | This is in St.Ann and it is assign to the wrong
Non-Outage | J.E.26.08.31990 | C001900627 | Locksley Allen | St.Mary | Completed | Load_254195 | Highgate - 210 | 2026-08-26 08:56 | 2026-08-26 08:57 | 2026-08-26 10:26 | 2026-08-26 11:30 | 2026-08-26 11:30 | 2026-08-26 11:37 | 2026-08-26 11:33 | 2026-08-26 11:33 |  |  | Fair | No | Pothead and pole found corroded.Install 3 clamps at pothead and clean up connectors at pole. Voltage at meter socket phase to phase 213vPhase to neutral 104&103v. Meter left working okay
Non-Outage | J.E.26.08.43751 | C001900626 | Locksley Allen | St.Mary | Completed | Load_265161 | Highgate - 210 | 2026-08-26 08:56 | 2026-08-26 08:57 | 2026-08-26 10:19 | 2026-08-26 10:20 | 2026-08-26 10:19 | 2026-08-26 10:28 | 2026-08-26 10:25 | 2026-08-26 10:25 |  |  | Fair | No | Meter burn up and needs to change urgently. Voltage at meter socket phase to phase 226v. Phase to neutral 109&111v
Outage | J.E.26.08.48023 | C001900636 | Christopher Edwards | KSAN | Completed | Load_247395 | Constant Spring - 410 | 2026-08-26 09:01 | 2026-08-26 09:02 | 2026-08-26 10:23 | 2026-08-26 10:24 | 2026-08-26 11:13 | 2026-08-26 11:39 | 2026-08-26 11:40 | 2026-08-26 11:40 |  |  | Fair | No | Customer is having an internal issue Customer was advised to get electrician to rectify issue
Non-Outage | J.E.26.08.40957 | C001900639 | Christopher Edwards | KSAN | Completed | Load_256340 | Constant Spring - 410 | 2026-08-26 09:03 | 2026-08-26 09:04 | 2026-08-26 11:40 | 2026-08-26 11:40 | 2026-08-26 11:56 | 2026-08-26 11:47 | 2026-08-26 12:51 | 2026-08-26 12:51 |  |  | Fair | No | Remake corroded joint at poleUsing (1) one bolt clamps However there is a plan outage in area Unable to take voltage readings
Outage | J.E.26.08.48348 | C001900640 | Selvin White | St.Elizabeth | Completed | Load_245863 | Maggotty - 110 | 2026-08-26 09:06 | 2026-08-26 09:07 | 2026-08-26 09:55 | 2026-08-26 09:56 | 2026-08-26 10:01 | 2026-08-26 10:36 | 2026-08-26 10:36 | 2026-08-26 10:36 |  |  | Fair | No | Replaced a defective 20 amp junction fuse at the entrance to Ashton subdivision after patrolling single phase primary line. Supply to the affected customers.
Outage | J.E.26.08.47931 | C001900647 | Michael Paterson | Westmoreland | Completed | Load_257812 | Paradise - 110 | 2026-08-26 09:13 | 2026-08-26 09:14 | 2026-08-26 11:09 | 2026-08-26 11:09 | 2026-08-26 11:09 | 2026-08-26 11:10 | 2026-08-26 11:10 | 2026-08-26 11:10 |  |  | Fair | No | Junction fuse blown, remove bird from line, replace 10amps fuse, supply restored.
Outage | J.E.26.08.48349 | C001900648 | Selvin White | St.Elizabeth | Completed | Load_257510 | Maggotty - 110 | 2026-08-26 09:14 | 2026-08-26 09:15 | 2026-08-26 10:37 | 2026-08-26 10:37 | 2026-08-26 10:40 | 2026-08-26 10:42 | 2026-08-26 10:42 | 2026-08-26 10:42 |  |  | Fair | No | Replaced a defective 20 amp junction fuse at the entrance to Ashton subdivision after patrolling single phase primary line. Supply restored to the affected customers.
Non-Outage | J.E.26.08.47966 | C001900650 | Jermaine Williams |  | Completed |  |  | 2026-08-26 09:17 | 2026-08-26 09:17 | 2026-08-26 09:33 | 2026-08-26 09:34 | 2026-08-26 10:58 | 2026-08-26 11:13 | 2026-08-26 11:14 | 2026-08-26 11:14 |  |  | Fair | No | Retention four spans sagging secondary conductors and replaced blown 25kva 3amp xfmr fuse.
Outage | J.E.26.08.47952 | C001900649 | Jermaine Williams | Clarendon | Completed | Load_256031 | Parnassus - 210 | 2026-08-26 09:17 | 2026-08-26 09:17 | 2026-08-26 13:55 | 2026-08-26 13:56 | 2026-08-26 13:57 | 2026-08-26 13:57 | 2026-08-26 13:58 | 2026-08-26 13:58 |  |  | Fair | No | Call was completed earlier.
Outage | J.E.26.08.47934 | C001900674 | Shawn Medley | St.James | Completed | Load_244737 | Bogue - 310 | 2026-08-26 09:32 | 2026-08-26 09:33 | 2026-08-26 10:00 | 2026-08-26 10:22 | 2026-08-26 12:01 | 2026-08-26 00:04 | 2026-08-26 12:06 | 2026-08-26 12:06 |  |  | Fair | No | Customer house and meter was damaged from the passing of hurricane Melissa , she is complaining that she is still be charged. Refer to customer service department . Customer stated meter can’t be found since the hurricane.
Outage | J.E.26.08.47971 | C001900676 | Shawn Medley | St.James | Completed | Load_262783 | Bogue - 310 | 2026-08-26 09:32 | 2026-08-26 09:33 | 2026-08-26 09:59 | 2026-08-26 12:07 | 2026-08-26 13:23 | 2026-08-26 13:24 | 2026-08-26 13:24 | 2026-08-26 13:24 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.47987 | C001900675 | Shawn Medley | St.James | Completed | Load_1001886 | Bogue - 310 | 2026-08-26 09:32 | 2026-08-26 09:33 | 2026-08-26 09:45 | 2026-08-26 09:58 | 2026-08-26 10:16 | 2026-08-26 10:20 | 2026-08-26 10:20 | 2026-08-26 10:20 |  |  | Fair | No | Found blown fuse for 15kva hexing transformer with 2 customers no faults seen at customer potheads refused transformer using a 1.5A fuse. Transformer closed and held supply restored
Non-Outage | J.E.26.08.48446 | C001900690 | Shawn Medley | St.James | Completed | Load_268015 | Bogue - 310 | 2026-08-26 09:34 | 2026-08-26 09:34 | 2026-08-26 13:24 | 2026-08-26 13:25 | 2026-08-26 14:22 | 2026-08-26 14:22 | 2026-08-26 14:24 | 2026-08-26 14:24 | Fire |  | Fair | No | Unable to troubleshoot, no volts meter
Outage | J.E.26.08.48405 | C001900689 | Clyde Brown | Clarendon | Completed | Load_240026 | May Pen - 110 | 2026-08-26 09:34 | 2026-08-26 12:02 | 2026-08-26 13:32 | 2026-08-26 13:33 | 2026-08-26 14:27 | 2026-08-26 14:59 | 2026-08-26 15:08 | 2026-08-26 15:08 |  |  | Fair | No | Blown 20 junction fuse at Sangsters heights,line patrolled and no fault seen ,entire line need heavy overhead heavy bushing,blown fuse replaced.
Outage | J.E.26.08.44791 | C001900693 | Swon Miller | St.James | Completed | Load_240097 | Rose Hall - 210 | 2026-08-26 09:35 | 2026-08-26 09:36 | 2026-08-26 12:39 | 2026-08-26 12:40 | 2026-08-26 13:24 | 2026-08-26 13:45 | 2026-08-26 13:48 | 2026-08-26 13:48 |  |  | Fair | No | Check and found areas okay voltage found 117/116/234 customer states that power supply was restored yesterday about 9pm voltage left 117/116/234
Outage | J.E.26.08.44877 | C001900692 | Swon Miller | St.James | Completed | Load_237906 | Rose Hall - 210 | 2026-08-26 09:35 | 2026-08-26 09:36 | 2026-08-26 13:48 | 2026-08-26 13:49 | 2026-08-26 14:03 | 2026-08-26 14:37 | 2026-08-26 14:39 | 2026-08-26 14:39 |  |  | Flood | No | Check and found area okay voltage found 115/115/231 customer states that power supply was restored voltage left 115/115/231
Outage | J.E.26.08.47973 | C001900691 | Horace Malcolm | St.James | Completed | Load_245463 | Bogue - 310 | 2026-08-26 09:35 | 2026-08-26 15:07 | 2026-08-26 17:31 | 2026-08-26 17:32 | 2026-08-26 18:13 | 2026-08-26 18:26 | 2026-08-26 18:26 | 2026-08-26 18:26 |  |  | Fair | No | Unable to locate customer or premises multiple calls to customer unavailable
Non-Outage | J.E.26.08.44513 | C001900704 | Romeo Brissett | St.James | Completed | Load_238926 | Bogue - 610 | 2026-08-26 09:40 | 2026-08-26 09:40 | 2026-08-26 13:14 | 2026-08-26 13:14 | 2026-08-26 15:00 | 2026-08-26 16:50 | 2026-08-26 17:00 | 2026-08-26 17:00 | Fire |  | Fair | No | Isolated (1)10amps junction, cut and removed bamboos, spliced and retention 2 span of system neutral, used 20ft of #2 and 2 clamps.
Outage | J.E.26.08.44824 | C001900705 | Romeo Brissett | St.James | Completed | Load_573595 | Bogue - 610 | 2026-08-26 09:40 | 2026-08-26 09:40 | 2026-08-26 12:04 | 2026-08-26 12:05 | 2026-08-26 12:05 | 2026-08-26 10:00 | 2026-08-26 12:06 | 2026-08-26 12:06 |  |  | Fair | No | Customer stated power restored from last night
Outage | J.E.26.08.47948 | C001900706 | Swon Miller | St.James | Completed | Load_244260 | Rose Hall - 210 | 2026-08-26 09:41 | 2026-08-26 09:41 | 2026-08-26 10:29 | 2026-08-26 10:30 | 2026-08-26 10:58 | 2026-08-19 11:10 | 2026-08-26 11:10 | 2026-08-26 11:10 |  |  | Fair | No | Found 100 kva transformer trip due to public due to public cutting tree remove tree from line and reset 100 kva transformer voltage found 0.000 voltage left 114/113/228
Outage | J.E.26.08.48453 | C001900707 | Marlon Authors | St.Elizabeth | Completed | Load_262537 | Maggotty - 110 | 2026-08-26 09:41 | 2026-08-26 16:30 | 2026-08-26 21:30 | 2026-08-26 21:31 | 2026-08-26 21:30 | 2026-08-26 21:35 | 2026-08-26 21:35 | 2026-08-26 21:35 | BrokenWire |  | Fair | No | Customer said no connection science the hurricane and repairs completed. Please refer same to the field services department for further assistance
Non-Outage | J.E.26.08.33681 | C001900719 | Andrae Dawkins | St.James | Completed | Load_242100 | Bogue - 510 | 2026-08-26 09:47 | 2026-08-26 09:48 | 2026-08-26 12:39 | 2026-08-26 12:40 | 2026-08-26 13:20 | 2026-08-26 13:21 | 2026-08-26 13:22 | 2026-08-26 13:22 |  |  | Fair | No | Check and found okay voltage found 119/119/238
Non-Outage | J.E.26.08.35021 | C001900718 | Andrae Dawkins | St.James | Completed | Load_249040 | Bogue - 510 | 2026-08-26 09:47 | 2026-08-26 09:48 | 2026-08-26 13:23 | 2026-08-26 13:56 | 2026-08-26 14:58 | 2026-08-26 14:57 | 2026-08-26 15:00 | 2026-08-26 15:00 |  |  | Fair | No | Customer said that they didnt have any issue there
Non-Outage | J.E.26.08.35341 | C001900717 | Andrae Dawkins | St.James | Completed | Load_270045 | Bogue - 510 | 2026-08-26 09:47 | 2026-08-26 09:48 | 2026-08-26 11:57 | 2026-08-26 11:58 | 2026-08-26 12:34 | 2026-08-26 12:35 | 2026-08-26 12:39 | 2026-08-26 12:39 |  |  | Fair | No | Customer said they didn’t make any report and that they don’t have any problem there
Non-Outage | J.E.26.08.36095 | C001900716 | Andrae Dawkins | St.James | Completed | Load_264647 | Bogue - 510 | 2026-08-26 09:47 | 2026-08-26 09:48 | 2026-08-26 12:39 | 2026-08-26 13:22 | 2026-08-26 13:43 | 2026-08-26 13:55 | 2026-08-26 13:55 | 2026-08-26 13:55 |  |  | Fair | No | Found customer single phasing due to one leg of customer service wire burnt off due to slack connection cleaned and remade joint voltage left 115/115/231
Non-Outage | J.E.26.08.20665 | C001900737 | Rayon Foster | St.James | Completed | Load_247445 | Bogue - 510 | 2026-08-26 10:01 | 2026-08-26 10:02 | 2026-08-26 12:57 | 2026-08-26 12:57 | 2026-08-26 12:57 | 2026-08-26 13:55 | 2026-08-26 13:55 | 2026-08-26 13:55 |  |  | Fair | No | St James call
Outage | J.E.26.08.48502 | C001900746 | Marlon Authors | St.Elizabeth | Completed | Load_259140 | Maggotty - 210 | 2026-08-26 10:03 | 2026-08-26 10:05 | 2026-08-26 13:57 | 2026-08-26 13:58 | 2026-08-26 15:41 | 2026-08-26 18:15 | 2026-08-26 18:15 | 2026-08-26 18:15 |  |  | Fair | No | Patrol and found clear. Replace three blown 40 amp junction fuses and one fuse holder no pole #. Restored supply ok
Outage | J.E.26.08.48521 | C001900747 | Selvin White | St.Elizabeth | Completed | Load_238313 | Maggotty - 110 | 2026-08-26 10:05 | 2026-08-26 10:06 | 2026-08-26 11:35 | 2026-08-26 11:36 | 2026-08-26 12:14 | 2026-08-26 12:40 | 2026-08-26 12:40 | 2026-08-26 12:40 |  |  | SevereWind | No | Replaced a blown 8 amp junction fuse after patrolling single phase primary line that supply a 10 kva transformer circuit with 2 customers. Supply restored to the affected customers. Tree limb was found to be the cause.
Outage | J.E.26.08.48463 | C001900757 | Kemark Slue | St.Catherine | Completed | Load_568283 | New Michelton - 310 | 2026-08-26 10:08 | 2026-08-26 10:09 | 2026-08-26 11:17 | 2026-08-26 11:19 | 2026-08-26 11:20 | 2026-08-26 10:00 | 2026-08-26 11:35 | 2026-08-26 11:35 |  |  | Fair | No | Premises was checked and found okay.
Non-Outage | J.E.26.08.48320 | C001900765 | Dwain Samuels | Westmoreland | Completed | Load_292200 | Paradise - 110 | 2026-08-26 10:14 | 2026-08-26 10:15 | 2026-08-26 10:51 | 2026-08-26 12:55 | 2026-08-26 12:57 | 2026-08-26 13:09 | 2026-08-26 13:10 | 2026-08-26 13:10 |  |  | Fair | No | Gate is locked can’t access premises
Non-Outage | J.E.26.08.46842 | C001900767 | Nicholas Dillon | St.Elizabeth | Completed | Load_266865 | Maggotty - 210 | 2026-08-26 10:15 | 2026-08-26 10:16 | 2026-08-27 08:42 | 2026-08-27 08:43 | 2026-08-27 08:42 | 2026-08-27 08:45 | 2026-08-27 08:47 | 2026-08-27 08:47 |  |  | Fair | Yes | Check and found corrosion at pole clean corrosion use 2 one bolt clamp before I left voltage is 115 115 phase to phase 230
Non-Outage | J.E.26.08.36459 | C001900792 | Error Coore | Manchester | Completed | Load_241957 | Spur Tree - 310 | 2026-08-26 10:30 | 2026-08-26 10:31 | 2026-08-26 16:17 | 2026-08-26 16:17 | 2026-08-26 17:07 | 2026-08-26 17:13 | 2026-08-26 17:13 | 2026-08-26 17:13 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Outage | J.E.26.08.48665 | C001900833 | Marlon Authors | St.Elizabeth | Completed | Load_254859 | Maggotty - 210 | 2026-08-26 10:50 | 2026-08-26 10:52 | 2026-08-26 12:36 | 2026-08-26 12:37 | 2026-08-26 13:20 | 2026-08-26 13:57 | 2026-08-26 13:57 | 2026-08-26 13:57 | Fire |  | Fair | No | Supply checked and found service wire connections to the transformer drop leads burnt. Isolate and close 25 kva transformer no pole # to repair same using two clamps, supply leave working ok rdg 117v,117v and cross phased 234 volts
Outage | J.E.26.08.48587 | C001900838 | Richard Nicholas | St.Catherine | Completed | Load_263651 | New Michelton - 310 | 2026-08-26 10:54 | 2026-08-26 11:17 | 2026-08-26 12:18 | 2026-08-26 12:19 | 2026-08-26 13:35 | 2026-08-26 14:17 | 2026-08-26 14:22 | 2026-08-26 14:22 | Fire |  | Fair | No | At the premises,the customer was not home at the time of visit however the crew spoke to a Rasta man that was there however he knows nothing about the fault that was reported.all six meter at the premises is displaying and pothead connections and service wire inspected and no visible defects seen.
Non-Outage | J.E.26.08.48659 | C001901008 | Stephen Taylor |  | Completed |  |  | 2026-08-26 11:33 | 2026-08-26 11:58 | 2026-08-26 13:35 | 2026-08-26 13:35 | 2026-08-26 14:42 | 2026-08-26 14:42 | 2026-08-26 14:43 | 2026-08-26 14:43 | BrokenWire |  | Fair | No | Premese found okay rdg 113–112–225
Non-Outage | J.E.26.08.48828 | C001901010 | Omar Harris |  | Completed |  |  | 2026-08-26 11:33 | 2026-08-26 11:34 | 2026-08-26 12:44 | 2026-08-26 12:45 | 2026-08-26 13:01 | 2026-08-26 13:26 | 2026-08-26 13:27 | 2026-08-26 13:27 |  |  | Fair | No | Premises found ok. Voltage left at time of visit 119v 119v 238v
Outage | J.E.26.08.48522 | C001901009 | Hopeton Henry | St.Thomas | Completed | Load_353659 | Good Year - 110 | 2026-08-26 11:33 | 2026-08-26 16:00 | 2026-08-26 16:08 | 2026-08-26 16:09 | 2026-08-26 18:35 | 2026-08-26 18:35 | 2026-08-26 18:36 | 2026-08-26 18:36 | Fire |  | Fair | No | Customer not located Cellphone went unanswered
Outage | J.E.26.08.47951 | C001901012 | Collin Robinson | Portland | Completed | Load_575883 | Port Antonio - 410 | 2026-08-26 11:34 | 2026-08-26 11:35 | 2026-08-26 12:19 | 2026-08-26 12:20 | 2026-08-26 13:54 | 2026-08-26 14:09 | 2026-08-26 14:10 | 2026-08-26 14:10 |  |  | Fair | No | Remove rotten tree from primary conductor and replace 8 amps
Outage | J.E.26.08.48844 | C001901011 | Marlon Authors | St.Elizabeth | Completed | Load_263142 | Maggotty - 110 | 2026-08-26 11:34 | 2026-08-26 16:32 | 2026-08-26 21:00 | 2026-08-26 21:00 | 2026-08-26 21:00 | 2026-08-26 21:02 | 2026-08-26 21:03 | 2026-08-26 21:03 |  |  | Fair | No | Customer said repairs are now completed and he is requesting reconnection. Please refer same to the field services department for further assistance
Outage | J.E.26.08.48639 | C001901013 | Cliton Henry | St.Ann | Completed | Load_242413 | Upper White River - 110 | 2026-08-26 11:35 | 2026-08-26 11:35 | 2026-08-26 13:08 | 2026-08-26 13:08 | 2026-08-26 14:13 | 2026-08-26 14:36 | 2026-08-26 14:38 | 2026-08-26 14:38 | Fire |  | Fair | No | The customer service wire found wrapped at pole were reconnected using 3- one bolt clamps. Voltages left 114-114/229 volts.
Outage | J.E.26.08.43258 | C001901015 | Moses Elliston | St.Catherine | Completed | Load_250891 | Tredegar - 310 | 2026-08-26 11:37 | 2026-08-26 11:38 | 2026-08-27 12:41 | 2026-08-27 12:42 | 2026-08-27 12:41 | 2026-08-27 11:15 | 2026-08-27 12:43 | 2026-08-27 12:43 |  |  | Fair | No | Supply ok at premises.
Outage | J.E.26.08.44009 | C001901046 | Jermaine Williams | Clarendon | Completed | Load_258571 | May Pen - 210 | 2026-08-26 11:53 | 2026-08-26 11:54 | 2026-08-26 12:12 | 2026-08-26 12:13 | 2026-08-26 12:50 | 2026-08-26 01:00 | 2026-08-26 12:51 | 2026-08-26 12:51 |  |  | Fair | No | Premises found ok.
Non-Outage | J.E.26.08.48958 | C001901056 | Kenroy Dale |  | Completed |  |  | 2026-08-26 12:01 | 2026-08-26 12:02 | 2026-08-26 12:19 | 2026-08-26 12:20 | 2026-08-26 13:24 | 2026-08-26 14:09 | 2026-08-26 14:15 | 2026-08-26 14:15 | BrokenWire |  | Fair | No | Defective service wire found cause from vehicle accident, service wire was replaced with approximately 70 feet of #6 triplex and 3 one bolt clamp voltage reading 110/114/224
Outage | J.E.26.08.48889 | C001901061 | Daniel Francis | St.Ann | Completed | Load_1003803 | Cardiff Hall - 210 | 2026-08-26 12:04 | 2026-08-26 12:05 | 2026-08-26 12:50 | 2026-08-26 12:50 | 2026-08-26 13:31 | 2026-08-26 13:57 | 2026-08-26 13:57 | 2026-08-26 13:57 | Fire |  | Fair | No | Found pen Union discharge so we use pen union to replace it now power restored
Non-Outage | J.E.26.08.36136 | C001901062 | Nicholas Dillon | St.Elizabeth | Completed | Load_248075 | Maggotty - 210 | 2026-08-26 12:05 | 2026-08-26 12:06 | 2026-08-26 12:25 | 2026-08-26 12:25 | 2026-08-26 12:48 | 2026-08-26 12:50 | 2026-08-26 12:51 | 2026-08-26 12:51 |  |  | Fair | Yes | Check and found corrosion at pole clean joint and use 1 one bolt clamp before I left voltage is 111 110 phase to phase 222
Outage | J.E.26.08.48880 | C001901063 | Romeo Brissett | St.James | Completed | Load_242778 | Bogue - 510 | 2026-08-26 12:06 | 2026-08-26 12:07 | 2026-08-26 17:01 | 2026-08-26 17:01 | 2026-08-26 18:22 | 2026-08-26 18:27 | 2026-08-26 19:13 | 2026-08-26 19:13 | TreeContact |  | Fair | No | Found (1)45ft CV construction pole with 3 phase Primary and open secondary broken, no of which maintenance has already been aware of and there should be a schedule operation to be carried out soon to change pole, Customer suggesting that whenever JPS maintenance replacing broken pole, if possible they should cut Her breadfruit that’s closed to the line. Please send to maintenance.
Outage | J.E.26.08.48473 | C001901070 | Milton Charlton | KSAN | Completed | Load_252653 | West Kings House - 310 | 2026-08-26 12:08 | 2026-08-26 12:10 | 2026-08-26 13:38 | 2026-08-26 13:39 | 2026-08-26 14:10 | 2026-08-26 14:10 | 2026-08-26 14:13 | 2026-08-26 14:13 |  |  | Fair | No | Found okay upon arrival. Customer did not made a report to JPS.
Outage | J.E.26.08.48583 | C001901087 | Rusean Allen | KSAS | Completed | Load_266544 | Hunts Bay - 310 | 2026-08-26 12:18 | 2026-08-26 12:20 | 2026-08-26 14:51 | 2026-08-26 14:55 | 2026-08-26 15:23 | 2026-08-26 15:23 | 2026-08-26 15:24 | 2026-08-26 15:24 |  |  | Fair | No | Electrician carrying out repair
Outage | J.E.26.08.48683 | C001901088 | Christopher Edwards | KSAN | Completed | Load_256383 | Constant Spring - 410 | 2026-08-26 12:20 | 2026-08-26 12:22 | 2026-08-26 12:51 | 2026-08-26 12:51 | 2026-08-26 12:51 | 2026-08-26 12:51 | 2026-08-26 12:52 | 2026-08-26 12:52 |  |  | Fair | No | Related to planned outage in area
Outage | J.E.26.08.48947 | C001901089 | Stephen Taylor | St.Thomas | Completed | Load_242811 | Good Year - 210 | 2026-08-26 12:21 | 2026-08-26 12:23 | 2026-08-26 14:43 | 2026-08-26 14:44 | 2026-08-26 15:49 | 2026-09-03 01:00 | 2026-08-26 15:52 | 2026-08-26 15:52 |  |  | Fair | No | Close up 25kva transformer with 3ams fuse
Outage | J.E.26.08.48751 | C001901096 | Elvis Trowers | KSAS | Completed | Load_567705 | Washington Blvd - 310 | 2026-08-26 12:23 | 2026-08-26 12:24 | 2026-08-26 14:12 | 2026-08-26 14:12 | 2026-08-26 14:33 | 2026-08-26 15:21 | 2026-08-26 15:22 | 2026-08-26 15:22 |  |  | Fair | No | Customer service wire #6 triplex crystalize and burn up. Change using 30ft #6 triplex and six 1- bolt clamps. Readings at pothead 115-116-232 volts.
Outage | J.E.26.08.48910 | C001901095 | Elvis Trowers | KSAS | Completed | Load_239177 | Greenwich - 510 | 2026-08-26 12:23 | 2026-08-26 12:24 | 2026-08-26 15:23 | 2026-08-26 15:23 | 2026-08-26 16:06 | 2026-08-26 16:05 | 2026-08-26 16:07 | 2026-08-26 16:07 |  |  | Fair | No | Found okay upon arrival. Customer states matter was resolved.
Non-Outage | J.E.26.08.48581 | C001901098 | Eric Williams |  | Completed |  |  | 2026-08-26 12:25 | 2026-08-26 12:26 | 2026-08-26 14:14 | 2026-08-26 14:14 | 2026-08-26 14:14 | 2026-08-26 14:14 | 2026-08-26 14:15 | 2026-08-26 14:15 |  |  | Fair | No | Found hot line clamp burnt for middle phase, same corrected, section power supply restored.
Outage | J.E.26.08.48500 | C001901097 | Eric Williams | KSAN | Completed | Load_557885 | Constant Spring - 210 | 2026-08-26 12:25 | 2026-08-26 12:26 | 2026-08-26 14:15 | 2026-08-26 14:16 | 2026-08-26 14:51 | 2026-08-26 15:01 | 2026-08-26 15:01 | 2026-08-26 15:01 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.49062 | C001901099 | Collin Robinson | Portland | Completed | Load_351269 | Port Antonio - 410 | 2026-08-26 12:25 | 2026-08-26 12:27 | 2026-08-26 14:10 | 2026-08-26 14:10 | 2026-08-26 16:27 | 2026-08-26 16:33 | 2026-08-26 16:34 | 2026-08-26 16:34 | LeaningPole |  | Fair | No | transformer pole foot rotten and pole leaning towards customer house
Outage | J.E.26.08.48572 | C001901100 | Eric Williams | KSAN | Completed | Load_263399 | Washington Blvd - 410 | 2026-08-26 12:26 | 2026-08-26 12:27 | 2026-08-26 13:14 | 2026-08-26 13:15 | 2026-08-26 14:04 | 2026-08-26 14:11 | 2026-08-26 14:13 | 2026-08-26 14:13 | Fire |  | Fair | No | Found hot line clamp burnt for middle phase, same corrected, section power supply restored.
Outage | J.E.26.08.49053 | C001901101 | Collin Robinson | Portland | Completed | Load_353041 | Port Antonio - 410 | 2026-08-26 12:27 | 2026-08-26 12:27 | 2026-08-26 16:40 | 2026-08-26 16:40 | 2026-08-26 17:49 | 2026-08-26 17:59 | 2026-08-26 17:59 | 2026-08-26 17:59 |  |  | Fair | No | Meter defective refer to field service
Outage | J.E.26.08.48775 | C001901108 | Milton Charlton | KSAN | Completed | Load_578921 | Hope - 510 | 2026-08-26 12:29 | 2026-08-26 12:34 | 2026-08-26 13:00 | 2026-08-26 13:01 | 2026-08-26 13:31 | 2026-08-26 13:25 | 2026-08-26 13:34 | 2026-08-26 13:34 |  |  | Fair | No | Customer is fed from Hexing box and is getting no supply from the box. JPS escalation is unable to turn on meter. Refer to field service
Outage | J.E.26.08.48656 | C001901115 | Rayon Foster | Hanover | Completed | Load_246056 | Orange Bay - 310 | 2026-08-26 12:34 | 2026-08-26 12:35 | 2026-08-26 14:26 | 2026-08-26 14:45 | 2026-08-26 14:44 | 2026-08-26 15:04 | 2026-08-26 15:04 | 2026-08-26 15:04 |  |  | Fair | No | Call was done by my team earlier today
Outage | J.E.26.08.48831 | C001901116 | Edward Royal | KSAS | Completed | Load_406171 | Three Miles - 410 | 2026-08-26 12:36 | 2026-08-26 13:27 | 2026-08-26 13:31 | 2026-08-26 13:32 | 2026-08-26 14:09 | 2026-08-26 14:09 | 2026-08-26 14:22 | 2026-08-26 14:22 |  |  | Fair | No | When we arrived a was a fuse blown the engineer on premises requested a disconnection for the two other fuses to carry out work on underground cables I advice the engineer when work is completed he should contact jps customer service for reconnection
Outage | J.E.26.08.48781 | C001901118 | Marlon Brown | Trelawny | Completed | Load_237820 | Martha Brae - 110 | 2026-08-26 12:38 | 2026-08-26 12:39 | 2026-08-26 13:40 | 2026-08-26 13:40 | 2026-08-26 14:10 | 2026-08-26 15:30 | 2026-08-26 15:30 | 2026-08-26 15:30 |  |  | Fair | No | 130ft 2/0 triplex defective, however 3 customers were transferred to another Transformer circuit. Refer to maintenance to have 2/0 triplex wire replaced as this supports the neutral for the primary. Voltage found at pothead none Voltage leaving at pothead 113/11q=224v.
Outage | J.E.26.08.48733 | C001901119 | Shawn Medley | St.James | Completed | Load_556846 | Bogue - 410 | 2026-08-26 12:39 | 2026-08-26 12:41 | 2026-08-26 14:24 | 2026-08-26 14:24 | 2026-08-26 14:29 | 2026-08-26 14:40 | 2026-08-26 14:39 | 2026-08-26 14:39 |  |  | Fair | No | New connection call center said there’s and issue with the meter or a meter mix up, please refer to field service at Bogue
Outage | J.E.26.08.48944 | C001901120 | Edward Royal | KSAS | Completed | Load_259381 | Greenwich - 410 | 2026-08-26 12:40 | 2026-08-26 12:41 | 2026-08-26 15:08 | 2026-08-26 15:09 | 2026-08-26 15:52 | 2026-08-26 15:52 | 2026-08-26 15:56 | 2026-08-26 15:56 | TreeContact |  | Fair | No | Requesting primary bushing brew with buckets truck required
Non-Outage | J.E.26.08.49156 | C001901121 | Fitzroy Turner |  | Completed |  |  | 2026-08-26 12:42 | 2026-08-26 16:31 | 2026-08-26 20:24 | 2026-08-26 20:25 | 2026-08-26 22:01 | 2026-08-26 22:02 | 2026-08-26 22:05 | 2026-08-26 22:05 | TreeContact |  | Fair | No | Tree growing up in service wire needs to be cut soon
Outage | J.E.26.08.48894 | C001901133 | Tyrese Williams | St.Ann | Completed | Load_269390 | Cardiff Hall - 310 | 2026-08-26 12:48 | 2026-08-26 13:42 | 2026-08-26 13:58 | 2026-08-26 14:59 | 2026-08-26 16:13 | 2026-08-26 16:34 | 2026-08-26 16:34 | 2026-08-26 16:34 |  |  | Fair | No | Remade joint at pole use 1 pg clamp
Outage | J.E.26.08.49101 | C001901134 | Daniel Francis | St.Ann | Completed | Load_267528 | Cardiff Hall - 310 | 2026-08-26 12:48 | 2026-08-26 12:49 | 2026-08-26 13:58 | 2026-08-26 13:58 | 2026-08-26 14:30 | 2026-08-26 14:53 | 2026-08-26 14:56 | 2026-08-26 14:56 |  |  | Fair | No | Found JPS meter defective case from defective meter socket meter need to be replace
Outage | J.E.26.08.49013 | C001901140 | Kemark Slue | St.Catherine | Completed | Load_250825 | New Michelton - 210 | 2026-08-26 12:55 | 2026-08-26 12:56 | 2026-08-26 13:04 | 2026-08-26 13:05 | 2026-08-26 13:36 | 2026-08-26 13:52 | 2026-08-26 13:52 | 2026-08-26 13:52 |  |  | Fair | No | Premises was checked and found okay.
Outage | J.E.26.08.49204 | C001901139 | Kemark Slue | St.Catherine | Completed | Load_262099 | New Michelton - 210 | 2026-08-26 12:55 | 2026-08-26 12:56 | 2026-08-26 13:52 | 2026-08-26 13:53 | 2026-08-26 13:53 | 2026-08-26 14:37 | 2026-08-26 14:38 | 2026-08-26 14:38 |  |  | Fair | No | Premises was checked and found okay.
Outage | J.E.26.08.48853 | C001901144 | Ricky Hall | St.Catherine | Completed | Load_242419 | Rhodens Pen - 410 | 2026-08-26 12:58 | 2026-08-27 07:59 | 2026-08-27 10:55 | 2026-08-27 10:55 | 2026-08-27 11:21 | 2026-08-27 11:33 | 2026-08-27 11:34 | 2026-08-27 11:34 | TreeContact |  | Fair | No | Tree poses no immediate danger to line section
Outage | J.E.26.08.49067 | C001901143 | Donald Cunningham | St.Catherine | Completed | Load_251534 | Rhodens Pen - 410 | 2026-08-26 12:58 | 2026-08-26 12:59 | 2026-08-26 13:16 | 2026-08-26 13:17 | 2026-08-26 14:26 | 2026-08-26 14:36 | 2026-08-26 14:38 | 2026-08-26 14:38 |  |  | Fair | No | Premises not located customer not reachable
Non-Outage | J.E.26.08.48864 | C001901188 | Moses Elliston |  | Completed |  |  | 2026-08-26 13:37 | 2026-08-26 13:38 | 2026-08-26 13:59 | 2026-08-26 14:00 | 2026-08-26 13:59 | 2026-08-26 13:45 | 2026-08-26 14:01 | 2026-08-26 14:01 |  |  | Fair | No | Credit added to prepaid account
Outage | J.E.26.08.43411 | C001901185 | Moses Elliston | St.Catherine | Completed | Load_290530 | Rhodens Pen - 210 | 2026-08-26 13:37 | 2026-08-26 13:37 | 2026-08-26 16:01 | 2026-08-26 16:01 | 2026-08-26 16:01 | 2026-08-26 16:21 | 2026-08-26 16:24 | 2026-08-26 16:24 |  |  | Fair | No | 60 ‘ #6 broken 3 wire service replaced using 5 linkets,1 clamp.116-116-232 volts
Outage | J.E.26.08.49443 | C001901204 | Richman Whyte | Westmoreland | Completed | Load_303217 | Paradise - 310 | 2026-08-26 13:51 | 2026-08-26 13:52 | 2026-08-26 17:00 | 2026-08-26 17:00 | 2026-08-26 17:00 | 2026-08-26 17:03 | 2026-08-26 17:03 | 2026-08-26 17:03 |  |  | Fair | No | The is no secondary line at location for customer to get connected need 240ft of 2nart twisted wire that customer can get connected
Non-Outage | J.E.26.08.49011 | C001901205 | Oshane Warren | Westmoreland | Completed | Load_247031 | Paradise - 110 | 2026-08-26 13:52 | 2026-08-26 15:54 | 2026-08-26 20:30 | 2026-08-26 20:30 | 2026-08-26 20:42 | 2026-08-26 20:43 | 2026-08-26 20:43 | 2026-08-26 20:43 | BrokenWire |  | Fair | No | Need daylight attention to carry out repairs
Outage | J.E.26.08.36038 | C001901212 | Moses Elliston | St.Catherine | Completed | Load_291532 | Rhodens Pen - 210 | 2026-08-26 13:54 | 2026-08-26 13:55 | 2026-08-26 15:26 | 2026-08-26 15:26 | 2026-08-26 15:26 | 2026-08-26 15:39 | 2026-08-26 15:40 | 2026-08-26 15:40 |  |  | Fair | No | Meter relay reset.116-116-232 volts.
Outage | J.E.26.08.49378 | C001901218 | Christopher West | St.Catherine | Completed | Load_294338 | Twickenham - 210 | 2026-08-26 14:02 | 2026-08-26 16:01 | 2026-08-26 17:17 | 2026-08-26 17:18 | 2026-08-26 17:49 | 2026-08-26 18:12 | 2026-08-26 18:12 | 2026-08-26 18:12 | BrokenWire |  | Fair | No | Customer has a defective meter socket and was advised accordingly.
Non-Outage | J.E.26.08.48869 | C001901227 | Edward Royal | KSAS | Completed | Load_261609 | Three Miles - 410 | 2026-08-26 14:04 | 2026-08-26 14:05 | 2026-08-26 14:23 | 2026-08-26 14:23 | 2026-08-26 14:23 | 2026-08-26 14:29 | 2026-08-26 14:32 | 2026-08-26 14:32 |  |  | Fair | No | When arrived at location we notified that a junction fuse is blown however 2 car park under pole unable to work 7038LJ 5445 LX those are the license plate for the 2 vehicle
Outage | J.E.26.08.34997 | C001901237 | Milton Charlton | KSAN | Completed | Load_253615 | West Kings House - 310 | 2026-08-26 14:18 | 2026-08-26 14:18 | 2026-08-26 14:23 | 2026-08-26 14:23 | 2026-08-26 16:18 | 2026-08-26 16:10 | 2026-08-26 16:27 | 2026-08-26 16:27 |  |  | Fair | No | U/G high voltage feeding N.W.C. Pump MKWWB at East Kings House Road at pole #0018899 middle D/O switch is defective. Need to change. Middle D/O switch feeding UG high voltage cable.
Outage | J.E.26.08.49176 | C001901248 | Collin Robinson | Portland | Completed | Load_352999 | Port Antonio - 310 | 2026-08-26 14:26 | 2026-08-26 15:12 | 2026-08-26 17:59 | 2026-08-26 18:00 | 2026-08-26 19:08 | 2026-08-26 19:13 | 2026-08-26 19:13 | 2026-08-26 19:13 | LowHangingWires |  | Fair | No | Customer stanchion need to fix before service wire can install back premises
Outage | J.E.26.08.49196 | C001901260 | Romeo Brissett | St.James | Completed | Load_242100 | Bogue - 510 | 2026-08-26 14:28 | 2026-08-26 14:29 | 2026-08-26 19:13 | 2026-08-26 19:14 | 2026-08-26 19:13 | 2026-08-26 20:00 | 2026-08-26 20:07 | 2026-08-26 20:07 |  |  | Fair | No | Found customer service wire joints contaminated, isolated (1)50kva transformer for clearance, changed customer service wire, used 5ft of #6 and 4 clamps V/R 122-123-245.
Outage | J.E.26.08.49496 | C001901259 | Horace Malcolm | St.James | Completed | Load_244515 | Bogue - 310 | 2026-08-26 14:28 | 2026-08-26 15:06 | 2026-08-26 15:41 | 2026-08-26 15:41 | 2026-08-26 15:47 | 2026-08-26 15:48 | 2026-08-26 15:48 | 2026-08-26 15:48 |  |  | Fair | No | Customer says supply was restored
Outage | J.E.26.08.49733 | C001901287 | Lancelot Brown | Hanover | Completed | Load_264328 | Orange Bay - 310 | 2026-08-26 14:57 | 2026-08-26 15:28 | 2026-08-26 15:42 | 2026-08-26 15:44 | 2026-08-26 15:53 | 2026-08-26 15:56 | 2026-08-26 15:56 | 2026-08-26 15:56 |  |  | Fair | No | Check and found area ok no one at Dundas premises and gate is lock all others customer have supply
Outage | J.E.26.08.49767 | C001901288 | Lancelot Brown | Hanover | Completed | Load_569916 | Orange Bay - 310 | 2026-08-26 14:57 | 2026-08-26 15:28 | 2026-08-26 15:42 | 2026-08-26 16:12 | 2026-08-26 18:00 | 2026-08-26 18:03 | 2026-08-26 18:04 | 2026-08-26 18:04 |  |  | Fair | No | Customer meter socket was diffective also meter burnt customer carry out repair on meter socket need meter to replace please pass on to field service department in montegobay bay west and Hanover need ergent attention customer still without supply
Outage | J.E.26.08.49773 | C001901303 | Marlon Authors | St.Elizabeth | Completed | Load_266249 | Maggotty - 210 | 2026-08-26 15:09 | 2026-08-26 15:10 | 2026-08-26 18:34 | 2026-08-26 18:35 | 2026-08-26 19:04 | 2026-08-26 19:39 | 2026-08-26 19:39 | 2026-08-26 19:39 |  |  | Fair | No | Patrol and found overgrown vegetation covering the transformer. Cut and remove same and replace one blown 10 amp junction fuse at pole #043858 and one blown 3 amp fuse that protects 25 kva transformer circuit no pole #. Restored supply okay
Outage | J.E.26.08.49865 | C001901305 | Richard Grant | St.Catherine | Completed | Load_249813 | Tredegar - 310 | 2026-08-26 15:11 | 2026-08-26 15:11 | 2026-08-26 15:44 | 2026-08-26 15:45 | 2026-08-26 16:40 | 2026-08-26 17:33 | 2026-08-26 17:33 | 2026-08-26 17:33 |  |  | Fair | No | Meter found disconnected. Call made to office and supply restored. Premises left okay.
Outage | J.E.26.08.49003 | C001901310 | Hartley Chin | Clarendon | Completed | Load_259757 | Parnassus - 310 | 2026-08-26 15:13 | 2026-08-26 20:32 | 2026-08-26 21:52 | 2026-08-26 22:23 | 2026-08-26 22:47 | 2026-08-26 22:57 | 2026-08-26 23:21 | 2026-08-26 23:21 |  |  | Fair | No | Found 2 of 3 blown 3 amp fuse on 25 KVA bank of 3 transformer @ pole # 0125782 line patrolled and found okay , transformer refused..
Outage | J.E.26.08.49234 | C001901312 | Hartley Chin | Clarendon | Completed | Load_267198 | Parnassus - 210 | 2026-08-26 15:13 | 2026-08-26 15:15 | 2026-08-26 17:27 | 2026-08-26 17:28 | 2026-08-26 18:02 | 2026-08-26 18:05 | 2026-08-26 18:06 | 2026-08-26 18:06 |  |  | SevereWind | No | Found blown 2 amp fuse on 100kva transformer (no pole #) line patrolled and found okay , transformer refused…
Outage | J.E.26.08.49488 | C001901311 | Hartley Chin | Clarendon | Completed | Load_267175 | Parnassus - 210 | 2026-08-26 15:13 | 2026-08-26 15:15 | 2026-08-26 17:29 | 2026-08-26 18:06 | 2026-08-26 19:05 | 2026-08-26 19:09 | 2026-08-26 19:11 | 2026-08-26 19:11 | LeaningPole |  | Fair | No | Premisis not found. Unable to contact customer with the number provided. Area patrolled and found ok.
Outage | J.E.26.08.48567 | C001901314 | Hartley Chin | Clarendon | Completed | Load_265179 | Parnassus - 210 | 2026-08-26 15:14 | 2026-08-26 15:15 | 2026-08-26 17:27 | 2026-08-26 20:08 | 2026-08-26 20:08 | 2026-08-26 20:08 | 2026-08-26 20:08 | 2026-08-26 20:08 |  |  | Fair | No | Cal related to job # 50167 ..
Outage | J.E.26.08.48881 | C001901313 | Hartley Chin | Clarendon | Completed | Load_238006 | Parnassus - 210 | 2026-08-26 15:14 | 2026-08-26 20:31 | 2026-08-26 20:35 |  | 2026-08-26 20:35 | 2026-08-26 20:36 | 2026-08-26 20:37 | 2026-08-26 20:37 |  |  | Fair | No | Found 1 of 3 junction blown 20 amp fuse (no pole #) line patrolled and found okay , junction refused..,
Outage | J.E.26.08.49750 | C001901315 | Jermaine Williams | Clarendon | Completed | Load_263890 | Monymusk - 410 | 2026-08-26 15:14 | 2026-08-27 08:22 | 2026-08-27 11:57 | 2026-08-27 11:58 | 2026-08-27 12:29 | 2026-08-27 12:29 | 2026-08-27 12:31 | 2026-08-27 12:31 |  |  | Fair | No | Reading found at pothead 114.
Outage | J.E.26.08.48345 | C001901326 | Nickolas Rodriques | St.Catherine | Completed | Load_556366 | Rhodens Pen - 210 | 2026-08-26 15:19 | 2026-08-26 15:20 | 2026-08-26 21:05 | 2026-08-26 21:07 | 2026-08-26 21:34 | 2026-08-26 21:52 | 2026-08-26 21:56 | 2026-08-26 21:56 |  |  | Fair | No | Found area with electricity. Customer confirmed that the power was restored.
Outage | J.E.26.08.48425 | C001901328 | Nickolas Rodriques | St.Catherine | Completed | Load_252183 | Tredegar - 210 | 2026-08-26 15:19 | 2026-08-26 15:20 | 2026-08-26 17:40 | 2026-08-26 17:41 | 2026-08-26 18:15 | 2026-08-26 18:50 | 2026-08-26 18:51 | 2026-08-26 18:51 |  |  | Fair | No | Customer is reporting a defective streetlight. Refer to streetlight department.
Outage | J.E.26.08.48734 | C001901323 | Nickolas Rodriques | St.Catherine | Completed | Load_252815 | Tredegar - 210 | 2026-08-26 15:19 | 2026-08-26 15:20 | 2026-08-26 15:33 | 2026-08-26 15:43 | 2026-08-26 16:50 | 2026-08-26 17:10 | 2026-08-26 17:14 | 2026-08-26 17:14 |  |  | Fair | No | Found customer with electricity. The customer confirmed that the area outage was restored.
Outage | J.E.26.08.48987 | C001901327 | Nickolas Rodriques | St.Catherine | Completed | Load_254276 | New Michelton - 310 | 2026-08-26 15:19 | 2026-08-26 15:20 | 2026-08-26 20:17 | 2026-08-26 20:20 | 2026-08-26 20:52 | 2026-08-26 21:03 | 2026-08-26 21:05 | 2026-08-26 21:05 |  |  | Fair | No | The customer was contacted and confirmed that the power outage was restored.
Outage | J.E.26.08.49525 | C001901325 | Nickolas Rodriques | St.Catherine | Completed | Load_268971 | Tredegar - 210 | 2026-08-26 15:19 | 2026-08-26 15:20 | 2026-08-26 18:52 | 2026-08-26 18:53 | 2026-08-26 19:45 | 2026-08-26 20:13 | 2026-08-26 20:17 | 2026-08-26 20:17 |  |  | Fair | No | Unable to locate or communicate with the customer after several attempts.
Outage | J.E.26.08.49914 | C001901324 | Nickolas Rodriques | St.Catherine | Completed | Load_244526 | Tredegar - 210 | 2026-08-26 15:19 | 2026-08-26 15:20 | 2026-08-26 17:15 | 2026-08-26 17:21 | 2026-08-26 17:34 | 2026-08-26 17:35 | 2026-08-26 17:38 | 2026-08-26 17:38 |  |  | Fair | No | Customer confirmed that the area outage was restored.
Non-Outage | J.E.26.08.20849 | C001901330 | Romeo Brissett | St.James | Completed | Load_301734 | Bogue - 310 | 2026-08-26 15:20 | 2026-08-26 15:21 | 2026-08-26 20:59 | 2026-08-26 21:00 | 2026-08-26 21:00 | 2026-08-26 21:00 | 2026-08-26 21:17 | 2026-08-26 21:17 |  |  | Fair | No | Check and found ok
Non-Outage | J.E.26.08.43384 | C001901341 | Horace Malcolm |  | Completed |  |  | 2026-08-26 15:23 | 2026-08-26 15:24 | 2026-08-26 17:11 | 2026-08-26 17:12 | 2026-08-26 17:24 | 2026-08-26 17:31 | 2026-08-26 17:31 | 2026-08-26 17:31 | BrokenWire |  | Fair | No | Check and found no broken wire no sparking of fire
Outage | J.E.26.08.49964 | C001901340 | Oshane Warren | Westmoreland | Completed | Load_253744 | Paradise - 310 | 2026-08-26 15:23 | 2026-08-26 17:14 | 2026-08-26 21:21 | 2026-08-26 22:41 | 2026-08-26 22:41 | 2026-08-26 22:41 | 2026-08-26 22:45 | 2026-08-26 22:45 |  |  | Fair | No | Need daylight attention in order to connect
Outage | J.E.26.08.49632 | C001901342 | Floyd Taylor | Trelawny | Completed | Load_292047 | Greenwood - 210 | 2026-08-26 15:24 | 2026-08-26 15:25 | 2026-08-26 15:45 | 2026-08-26 15:45 | 2026-08-26 16:02 | 2026-08-26 16:04 | 2026-08-26 16:05 | 2026-08-26 16:05 |  |  | Fair | No | Found customer with light
Outage | J.E.26.08.47897 | C001901347 | Romaine Roberts | St.Mary | Completed | Load_248728 | Highgate -110 | 2026-08-26 15:25 | 2026-08-26 15:29 | 2026-08-26 16:29 | 2026-08-26 16:30 | 2026-08-26 19:49 | 2026-08-26 20:20 | 2026-08-26 20:20 | 2026-08-26 20:20 | BrokenWire |  | Fair | No | Tree fall on secondary line burst down 2span secondary phase and neutral open and close 25 kva to splice and retention conductor clear tree from line
Outage | J.E.26.08.48477 | C001901348 | Raymond Carr | St.Mary | Completed | Load_270196 | Oracabessa - 210 | 2026-08-26 15:25 | 2026-08-26 15:29 | 2026-08-26 16:33 | 2026-08-26 16:34 | 2026-08-26 17:10 | 2026-08-26 17:02 | 2026-08-26 17:19 | 2026-08-26 17:19 |  |  | Fair | No | Customer reported that supply was restored several days ago.
Outage | J.E.26.08.48960 | C001901346 | Romaine Roberts | St.Mary | Completed | Load_247987 | Highgate - 210 | 2026-08-26 15:25 | 2026-08-26 15:29 | 2026-08-26 20:20 | 2026-08-26 20:21 | 2026-08-26 21:37 | 2026-08-26 21:40 | 2026-08-26 21:53 | 2026-08-26 21:53 | Fire |  | Fair | No | 3 wire service Corrosion at pole clean and remake joints voltage 115-115 232
Outage | J.E.26.08.49516 | C001901345 | Raymond Carr | St.Mary | Completed | Load_349209 | Oracabessa - 210 | 2026-08-26 15:25 | 2026-08-26 15:29 | 2026-08-26 17:19 | 2026-08-26 17:20 | 2026-08-26 18:07 | 2026-08-26 17:23 | 2026-08-26 18:13 | 2026-08-26 18:13 |  |  | Fair | No | Customer reported supply okay, however she would like bushing to be done.
Outage | J.E.26.08.49602 | C001901344 | Raymond Carr | St.Ann | Completed | Load_260263 | Upper White River - 110 | 2026-08-26 15:25 | 2026-08-26 15:30 | 2026-08-26 18:13 | 2026-08-26 18:13 | 2026-08-26 18:50 | 2026-08-26 19:00 | 2026-08-26 18:52 | 2026-08-26 18:52 |  |  | Fair | No | Several calls to contact number went unanswered.
Outage | J.E.26.08.49774 | C001901343 | Raymond Carr | St.Mary | Completed | Load_239187 | Oracabessa - 210 | 2026-08-26 15:25 | 2026-08-26 15:29 | 2026-08-26 15:44 | 2026-08-26 15:44 | 2026-08-26 16:21 | 2026-08-26 15:21 | 2026-08-26 16:29 | 2026-08-26 16:29 |  |  | Fair | No | Several calls to contact number went straight to voicemail.
Outage | J.E.26.08.49849 | C001901349 | Roxroy Needham | St.Ann | Completed | Load_269360 | Cardiff Hall - 210 | 2026-08-26 15:27 | 2026-08-26 15:28 | 2026-08-26 15:50 | 2026-08-26 15:50 | 2026-08-26 16:44 | 2026-08-26 16:52 | 2026-08-26 16:57 | 2026-08-26 16:57 |  |  | Fair | No | Open 2 25 KVA transformer at pole to repair transformer leed used 2 pg clamp
Outage | J.E.26.08.49971 | C001901352 | Lancelot Brown | Hanover | Completed | Load_238848 | Orange Bay - 310 | 2026-08-26 15:27 | 2026-08-26 15:29 | 2026-08-26 15:42 | 2026-08-26 16:00 | 2026-08-26 15:59 | 2026-08-26 16:11 | 2026-08-26 16:12 | 2026-08-26 16:12 |  |  | Fair | No | Check and found ok supply restore
Outage | J.E.26.08.37374 | C001901361 | Moses Elliston | St.Catherine | Completed | Load_240276 | Tredegar - 210 | 2026-08-26 15:33 | 2026-08-26 15:34 | 2026-08-26 17:25 | 2026-08-26 17:26 | 2026-08-26 18:54 | 2026-08-26 17:50 | 2026-08-26 18:57 | 2026-08-26 18:57 |  |  | Fair | No | Supply reconnected from sn14538396855.
Outage | J.E.26.08.49910 | C001901362 | Damion Reid | Manchester | Completed | Load_268498 | Kendal - 210 | 2026-08-26 15:34 | 2026-08-27 07:19 | 2026-08-27 14:52 | 2026-08-27 14:52 | 2026-08-27 15:43 | 2026-08-27 15:50 | 2026-08-27 15:51 | 2026-08-27 15:51 |  |  | Fair | No | Customer say she didn’t make any report
Non-Outage | J.E.26.08.50024 | C001901377 | Fitzroy Turner |  | Completed |  |  | 2026-08-26 15:42 | 2026-08-26 15:43 | 2026-08-26 18:54 | 2026-08-26 18:54 | 2026-08-26 18:55 | 2026-08-26 18:57 | 2026-08-26 18:57 | 2026-08-26 18:57 |  |  | Fair | No | Customer premises close at this time
Outage | J.E.26.08.49457 | C001901376 | Edward Royal | KSAS | Completed | Load_246359 | Greenwich - 710 | 2026-08-26 15:42 | 2026-08-26 15:43 | 2026-08-26 15:56 | 2026-08-26 15:57 | 2026-08-26 15:56 | 2026-08-26 15:57 | 2026-08-26 15:58 | 2026-08-26 15:58 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.49841 | C001901380 | Daniel Francis | St.Ann | Completed | Load_252857 | Roaring River - 210 | 2026-08-26 15:44 | 2026-08-26 15:44 | 2026-08-26 16:37 | 2026-08-26 16:38 | 2026-08-26 17:01 | 2026-08-26 20:30 | 2026-08-26 20:36 | 2026-08-26 20:36 |  |  | Fair | No | Found junction blown at pole 055999 also tree on line and 3 span of 3wire second down spliced and retention 3 span of 3wire
Non-Outage | J.E.26.08.49088 | C001901382 | Daniel Francis |  | Completed |  |  | 2026-08-26 15:47 | 2026-08-26 15:51 | 2026-08-26 20:43 | 2026-08-26 20:56 | 2026-08-26 21:29 | 2026-08-26 21:32 | 2026-08-26 21:34 | 2026-08-26 21:34 |  |  | Fair | No | Internal Affairs not JPS 117 116 232 in all
Non-Outage | J.E.26.08.48643 | C001901388 | Lancelot Brown | Hanover | Completed | Load_261934 | Orange Bay - 210 | 2026-08-26 15:48 | 2026-08-26 15:49 | 2026-08-26 18:05 | 2026-08-26 18:50 | 2026-08-26 19:25 | 2026-08-26 21:45 | 2026-08-26 21:46 | 2026-08-26 21:46 |  |  | Fair | No | Remake burnt off joint at pole used two pg clamps vl at meter socket 112-114-227 supply restore vehicle was giving problem reason for this call held up
Non-Outage | J.E.26.08.49888 | C001901389 | Lancelot Brown | Hanover | Completed | Load_263993 | Orange Bay - 210 | 2026-08-26 15:48 | 2026-08-26 15:49 | 2026-08-26 18:05 | 2026-08-26 18:06 | 2026-08-26 18:42 | 2026-08-26 18:45 | 2026-08-26 18:46 | 2026-08-26 18:46 |  |  | Fair | No | Remake corroded joint at pothead used three connectors vl at meter socket 114-115-230 supply restore
Non-Outage | J.E.26.08.50052 | C001901386 | Lancelot Brown | Hanover | Completed | Load_569907 | Orange Bay - 210 | 2026-08-26 15:48 | 2026-08-26 15:49 | 2026-08-26 18:05 | 2026-08-26 21:52 | 2026-08-26 22:01 | 2026-08-26 22:33 | 2026-08-26 22:33 | 2026-08-26 22:33 |  |  | Fair | No | Check junction fuse and transformer fuse all fuses intact cannot get to a pacts joints and pothead motor vehicle having highjolic problem please carry forward for daylight attention
Non-Outage | J.E.26.08.29488 | C001901393 | Ryan Richards | Manchester | Completed | Load_250978 | Kendal - 210 | 2026-08-26 15:49 | 2026-08-26 15:50 | 2026-08-26 19:07 | 2026-08-26 19:08 | 2026-08-26 19:53 | 2026-08-26 21:52 | 2026-08-26 21:52 | 2026-08-26 21:52 |  |  | Fair | No | Corroded neutral found at premises neutral wire at pothead neural was raped Copper to aluminum removed corroded neutral using 2 penunion voltage @116/118/239 volts
Outage | J.E.26.08.41098 | C001901394 | Moses Elliston | St.Catherine | Completed | Load_265271 | Tredegar - 310 | 2026-08-26 15:50 | 2026-08-26 15:51 | 2026-08-26 17:18 | 2026-08-26 17:19 | 2026-08-26 17:19 | 2026-08-26 17:25 | 2026-08-26 17:25 | 2026-08-26 17:25 |  |  | Fair | No | Supply ok at premises.
Outage | J.E.26.08.50079 | C001901397 | Daniel Francis | St.Ann | Completed | Load_267394 | Roaring River - 210 | 2026-08-26 15:51 | 2026-08-26 15:53 | 2026-08-26 20:36 | 2026-08-26 20:37 | 2026-08-26 20:37 | 2026-08-19 17:35 | 2026-08-26 20:43 | 2026-08-26 20:43 |  |  | Fair | No | Powered restored at closing trip saver
Outage | J.E.26.08.49811 | C001901405 | Oshane Warren | Westmoreland | Completed | Load_259530 | Paradise - 110 | 2026-08-26 15:53 | 2026-08-26 15:57 | 2026-08-26 16:46 | 2026-08-26 16:47 | 2026-08-26 16:46 | 2026-08-26 16:46 | 2026-08-26 16:47 | 2026-08-26 16:47 |  |  | Fair | No | Check and found ok
Outage | J.E.26.08.49884 | C001901406 | Oshane Warren | Westmoreland | Completed | Load_242251 | Paradise - 110 | 2026-08-26 15:53 | 2026-08-26 15:57 | 2026-08-26 17:51 | 2026-08-26 17:51 | 2026-08-26 20:21 | 2026-08-26 20:29 | 2026-08-26 20:29 | 2026-08-26 20:29 |  |  | Fair | No | Customer experiencing low voltage after carrying out several checks top up back a 2 transformer voltage found 106 106 215 168 voltage left 110 110 220 203
Outage | J.E.26.08.49912 | C001901407 | Oshane Warren | Westmoreland | Completed | Load_259530 | Paradise - 110 | 2026-08-26 15:53 | 2026-08-26 15:57 | 2026-08-26 17:06 | 2026-08-26 17:07 | 2026-08-26 17:21 | 2026-08-26 17:30 | 2026-08-26 17:30 | 2026-08-26 17:30 |  |  | Fair | No | Miss Kayon McDonald’s located sav she’s the Principal for the Kindergarten near the stop light coming from paradise , there is A retired pole in the line section leaning on the kindergarteners fences , need to be removed in order for repairs for reopening of school refer to maintenance
Non-Outage | J.E.26.08.44052 | C001901411 | Neville Spencer |  | Completed |  |  | 2026-08-26 15:54 | 2026-08-26 15:55 | 2026-08-26 18:10 | 2026-08-26 18:11 | 2026-08-26 19:11 | 2026-08-26 19:11 | 2026-08-26 19:37 | 2026-08-26 19:37 |  |  | Fair | No | Customer internal fault supply disconnect at meter customer advised.
Outage | J.E.26.08.41144 | C001901412 | Moses Elliston | St.Catherine | Completed | Load_557279 | Tredegar - 210 | 2026-08-26 15:55 | 2026-08-26 15:56 | 2026-08-27 10:29 | 2026-08-27 10:30 | 2026-08-27 10:29 | 2026-08-27 10:20 | 2026-08-27 10:31 | 2026-08-27 10:31 |  |  | Fair | No | Supply ok at premises.
Non-Outage | J.E.26.08.49740 | C001901414 | Horace Malcolm | St.James | Completed | Load_258824 | Queens Drive - 310 | 2026-08-26 15:56 | 2026-08-27 08:47 | 2026-08-27 08:51 | 2026-08-27 08:52 | 2026-08-27 09:30 | 2026-08-27 10:22 | 2026-08-27 10:22 | 2026-08-27 10:22 | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Clean corrosion and remake joints at pole and splice customer service nuetral used 10ft #6 triplex wire and 1clamp voltage 116-126-233-206
Outage | J.E.26.08.42611 | C001901413 | Moses Elliston | St.Catherine | Completed | Load_258468 | Tredegar - 410 | 2026-08-26 15:56 | 2026-08-26 15:59 | 2026-08-27 11:27 | 2026-08-27 11:27 | 2026-08-27 11:27 | 2026-08-27 11:26 | 2026-08-27 11:28 | 2026-08-27 11:28 |  |  | Fair | No | Supply found ok in area.
Non-Outage | J.E.26.08.48885 | C001901420 | Jermaine Williams |  | Completed |  |  | 2026-08-26 15:57 | 2026-08-27 08:22 | 2026-08-27 13:36 | 2026-08-27 13:36 | 2026-08-27 15:09 | 2026-08-27 14:39 | 2026-08-27 15:10 | 2026-08-27 15:10 | Fire |  | Fair | No | Premises not located.
Non-Outage | J.E.26.08.50087 | C001901415 | Lancelot Brown |  | Completed |  |  | 2026-08-26 15:57 | 2026-08-26 15:59 | 2026-08-26 18:04 | 2026-08-26 18:05 | 2026-08-26 18:04 | 2026-08-26 18:05 | 2026-08-26 18:05 | 2026-08-26 18:05 |  |  | Fair | No | Please pass on this call to st James crew
Non-Outage | J.E.26.08.41462 | C001901422 | Hartley Chin |  | Completed |  |  | 2026-08-26 15:58 | 2026-08-26 16:07 | 2026-08-26 16:26 | 2026-08-26 16:42 | 2026-08-26 16:42 | 2026-08-26 16:42 | 2026-08-26 16:59 | 2026-08-26 16:59 | BrokenPole |  | SevereWind | No | Ref to maintenance!!!! Rotten 35ft pole with single phase Primary and open secondary circuit.. pole is also leaning towards customers house (driveway) … pole is being supported by customer service wire … pole requires urgent attention… maintenance to re repair… located n sunny acres
Non-Outage | J.E.26.08.44721 | C001901421 | Hartley Chin |  | Completed |  |  | 2026-08-26 15:58 | 2026-08-26 16:07 | 2026-08-26 18:49 | 2026-08-26 19:13 | 2026-08-26 19:12 | 2026-08-26 19:13 | 2026-08-26 19:14 | 2026-08-26 19:14 | BrokenWire |  | Fair | No | Premisis found ok. Customer stated the issue was resolved from this morning.
Outage | J.E.26.08.48819 | C001901423 | Christopher West | Portmore | Completed | Load_270102 | Naggo Head - 510 | 2026-08-26 16:00 | 2026-08-26 16:01 | 2026-08-26 16:36 | 2026-08-26 16:36 | 2026-08-26 16:36 | 2026-08-26 16:36 | 2026-08-26 16:36 | 2026-08-26 16:36 |  |  | Fair | No | Kindly refer to Mr. Elliston
Outage | J.E.26.08.49266 | C001901425 | Christopher West | Portmore | Completed | Load_248660 | Naggo Head - 610 | 2026-08-26 16:00 | 2026-08-26 16:01 | 2026-08-26 18:48 | 2026-08-26 18:48 | 2026-08-26 19:59 | 2026-08-26 20:05 | 2026-08-26 20:05 | 2026-08-26 20:05 |  |  | Fair | No | Premises closed
Outage | J.E.26.08.50005 | C001901424 | Christopher West | St.Catherine | Completed | Load_266808 | Twickenham - 210 | 2026-08-26 16:00 | 2026-08-26 16:01 | 2026-08-26 18:13 | 2026-08-26 18:13 | 2026-08-26 18:37 | 2026-08-26 18:46 | 2026-08-26 18:46 | 2026-08-26 18:46 |  |  | Fair | Yes | Premises closed
Outage | J.E.26.08.50124 | C001901433 | Neville Spencer | Clarendon | Completed | Load_240810 | May Pen - 110 | 2026-08-26 16:07 | 2026-08-26 16:10 | 2026-08-26 16:28 | 2026-08-26 16:28 | 2026-08-26 16:47 | 2026-08-26 16:47 | 2026-08-26 17:23 | 2026-08-26 17:23 | BrokenWire |  | Fair | No | Open 25 kva xmfr at pole # 01000745 splice and retention broken secondary phase Conductor used 20 ft wire, 2, clamps 1, preform supply restored
Outage | J.E.26.08.49492 | C001901434 | Oshane Warren | Westmoreland | Completed | Load_293032 | Paradise - 110 | 2026-08-26 16:08 | 2026-08-26 16:09 | 2026-08-26 17:39 | 2026-08-26 17:40 | 2026-08-26 17:39 | 2026-08-26 17:40 | 2026-08-26 17:40 | 2026-08-26 17:40 |  |  | Fair | No | Unable to locate or contact customer need direction
Non-Outage | J.E.26.08.36298 | C001901439 | Floyd Taylor | Trelawny | Completed | Load_292517 | Greenwood - 210 | 2026-08-26 16:23 | 2026-08-26 16:24 | 2026-08-26 19:01 | 2026-08-26 19:01 | 2026-08-26 19:21 | 2026-08-26 19:31 | 2026-08-26 19:31 | 2026-08-26 19:31 |  |  | Fair | No | Customer say issues was resolved
Outage | J.E.26.08.34997 | C001901445 | Fitzroy Turner | KSAN | Completed | Load_253615 | West Kings House - 310 | 2026-08-26 16:25 | 2026-08-26 16:25 | 2026-08-26 16:58 | 2026-08-26 16:58 | 2026-08-26 17:34 | 2026-08-26 18:27 | 2026-08-26 18:33 | 2026-08-26 18:33 |  |  | Fair | No | Have one defective drop out switch change and close up supply restored to customer
Outage | J.E.26.08.49364 | C001901447 | Edward Royal | KSAS | Completed | Load_242388 | Duhaney - 310 | 2026-08-26 16:26 | 2026-08-26 16:27 | 2026-08-26 17:05 | 2026-08-26 17:06 | 2026-08-26 17:05 | 2026-08-26 17:07 | 2026-08-26 17:07 | 2026-08-26 17:07 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.50006 | C001901446 | Edward Royal | KSAN | Completed | Load_267672 | Constant Spring - 210 | 2026-08-26 16:26 | 2026-08-26 16:27 | 2026-08-26 17:48 | 2026-08-26 17:49 | 2026-08-26 17:48 | 2026-08-26 17:50 | 2026-08-26 17:50 | 2026-08-26 17:50 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.50067 | C001901448 | Milton Charlton | KSAN | Completed | Load_247141 | Hope - 510 | 2026-08-26 16:26 | 2026-08-26 16:27 | 2026-08-26 17:18 | 2026-08-26 17:18 | 2026-08-26 17:53 | 2026-08-26 18:15 | 2026-08-26 18:01 | 2026-08-26 18:01 |  |  | Fair | No | Cut away wisp and vines from transformer with Hexing box attached and refused and reclosed 3 amps transformer switch at pole #0214100 using one 3 amps fuse.
Outage | J.E.26.08.49829 | C001901453 | Floyd Taylor | Trelawny | Completed | Load_257394 | Martha Brae - 210 | 2026-08-26 16:28 | 2026-08-26 16:30 | 2026-08-26 19:36 | 2026-08-26 19:36 | 2026-08-26 20:17 | 2026-08-26 20:52 | 2026-08-26 20:53 | 2026-08-26 20:53 | Fire |  | Fair | No | Customer pothead damaged customer was advised to get a electrician
Outage | J.E.26.08.49620 | C001901454 | Floyd Taylor | Trelawny | Completed | Load_250746 | Martha Brae - 110 | 2026-08-26 16:29 | 2026-08-26 16:30 | 2026-08-26 17:23 | 2026-08-26 17:24 | 2026-08-26 18:53 | 2026-08-26 18:54 | 2026-08-26 18:54 | 2026-08-26 18:54 |  |  | Fair | No | Replace 1-3amp fuse after found 25kva transformer fused blown
Outage | J.E.26.08.50157 | C001901456 | Marlon Authors | St.Elizabeth | Completed | Load_270212 | Maggotty - 110 | 2026-08-26 16:29 | 2026-08-26 16:31 | 2026-08-26 21:10 | 2026-08-26 21:11 | 2026-08-26 21:10 | 2026-08-26 21:14 | 2026-08-26 21:14 | 2026-08-26 21:14 |  |  | Fair | No | Unable to locate and the customer said it’s the wrong #
Outage | J.E.26.08.50192 | C001901455 | Wayne Dillion | St.Elizabeth | Completed | Load_257403 | Maggotty - 210 | 2026-08-26 16:29 | 2026-08-27 07:48 | 2026-08-27 08:59 | 2026-08-27 09:00 | 2026-08-27 10:51 | 2026-08-27 11:05 | 2026-08-27 11:09 | 2026-08-27 11:09 |  |  | Fair | No | Supply check working okay reading 109v, 110v and cross phase 220volts. Further checks reveals that customer load side wires are burnt. Disconnect line side at pot head at pot head. Customer was advised to get an electrician to carry out repairs.
Non-Outage | J.E.26.08.48399 | C001901457 | Marlon Authors |  | Completed |  |  | 2026-08-26 16:31 | 2026-08-26 16:32 | 2026-08-26 19:41 | 2026-08-26 19:41 | 2026-08-26 20:00 | 2026-08-26 20:22 | 2026-08-26 20:22 | 2026-08-26 20:22 |  |  | Fair | No | Patrol and found illegal connection on line. Remove same and replace one blown 1.5 amp fuse that protects 25 kva transformer circuit no pole #. Restored supply okay
Non-Outage | J.E.26.08.40928 | C001901459 | Richard Samuda | Manchester | Completed | Load_260581 | Porus - 210 | 2026-08-26 16:36 | 2026-08-26 16:38 | 2026-08-26 18:10 | 2026-08-26 18:11 | 2026-08-26 18:43 | 2026-08-26 18:55 | 2026-08-26 18:55 | 2026-08-26 18:55 |  |  | Fair | No | Customer has a defective meter refer call to field
Non-Outage | J.E.26.08.32273 | C001901461 | Richard Samuda | Manchester | Completed | Load_246031 | Spur Tree - 310 | 2026-08-26 16:37 | 2026-08-26 16:38 | 2026-08-26 17:25 | 2026-08-26 17:25 | 2026-08-26 18:00 | 2026-08-26 06:01 | 2026-08-26 18:01 | 2026-08-26 18:01 |  |  | Fair | No | Premises not located and call to phone straight to voicemail
Non-Outage | J.E.26.08.40539 | C001901460 | Ryan Richards | Manchester | Completed | Load_248356 | Kendal - 210 | 2026-08-26 16:37 | 2026-08-26 16:39 | 2026-08-26 16:47 | 2026-08-26 16:48 | 2026-08-26 18:28 | 2026-08-26 19:07 | 2026-08-26 19:07 | 2026-08-26 19:07 |  |  | Fair | Yes | Burn off phase found at pole that is supplying 2 meter cause by illegal connections remade burn off phase using 2 one bolt clamps voltage 113/115/229 volts
Outage | J.E.26.08.48819 | C001901465 | Moses Elliston | Portmore | Completed | Load_270102 | Naggo Head - 510 | 2026-08-26 16:40 | 2026-08-26 16:40 | 2026-08-27 12:33 | 2026-08-27 12:33 | 2026-08-27 12:33 | 2026-08-27 12:32 | 2026-08-27 12:40 | 2026-08-27 12:40 |  |  | Fair | No | Supply ok at premises
Outage | J.E.26.08.50202 | C001901471 | Richman Whyte | Westmoreland | Completed | Load_240901 | Paradise - 310 | 2026-08-26 16:47 | 2026-08-26 16:48 | 2026-08-26 22:47 | 2026-08-26 22:48 | 2026-08-26 22:47 | 2026-08-26 22:49 | 2026-08-26 22:49 | 2026-08-26 22:49 | Fire |  | Fair | No | Replace service wire #120 ft #6 triplex service wire voltage #109 110 220
Outage | J.E.26.08.50258 | C001901474 | Oshane Warren | Westmoreland | Completed | Load_265484 | Paradise - 110 | 2026-08-26 16:47 | 2026-08-26 16:48 | 2026-08-26 17:49 | 2026-08-26 17:49 | 2026-08-26 17:49 | 2026-08-26 17:49 | 2026-08-26 17:50 | 2026-08-26 17:50 |  |  | Fair | No | Unable to locate or contact customer need direction
Outage | J.E.26.08.50246 | C001901476 | Elvis Trowers | KSAS | Completed | Load_252375 | Three Miles - 410 | 2026-08-26 16:50 | 2026-08-26 16:50 | 2026-08-26 17:25 | 2026-08-26 17:27 | 2026-08-26 17:35 | 2026-08-26 17:30 | 2026-08-26 17:56 | 2026-08-26 17:56 |  |  | Fair | No | Customer meter #2439063 is displaying and there is supply at the premises . On the bill it’s showing 0.00 zero usage so customer is concern about the zero usage. Refer to field service.
Outage | J.E.26.08.50291 | C001901491 | Hopeton Henry | St.Thomas | Completed | Load_257335 | Good Year - 210 | 2026-08-26 17:17 | 2026-08-26 17:18 | 2026-08-26 17:37 | 2026-08-26 18:37 | 2026-08-26 18:48 | 2026-08-26 18:48 | 2026-08-26 18:49 | 2026-08-26 18:49 |  |  | Fair | No | Customer not located,, cell phone went unanswered
Outage | J.E.26.08.50306 | C001901492 | Romeo Brissett | St.James | Completed | Load_301723 | Bogue - 310 | 2026-08-26 17:17 | 2026-08-26 18:38 | 2026-08-26 21:44 | 2026-08-26 21:44 | 2026-08-26 21:57 | 2026-08-26 22:06 | 2026-08-26 22:06 | 2026-08-26 22:06 |  |  | Fair | No | Customer requested daylight attention.
Outage | J.E.26.08.50272 | C001901496 | Fitzroy Turner | KSAS | Completed | Load_247100 | Rockfort - 410 | 2026-08-26 17:21 | 2026-08-26 17:22 | 2026-08-26 19:09 | 2026-08-26 19:09 | 2026-08-26 20:10 | 2026-08-26 20:23 | 2026-08-26 20:24 | 2026-08-26 20:24 |  |  | Fair | No | Customer request new connections.advised customer to visit the office
Outage | J.E.26.08.50270 | C001901497 | Damion Reid | Manchester | Completed | Load_258572 | Kendal - 210 | 2026-08-26 17:32 | 2026-08-27 07:19 | 2026-08-27 08:50 | 2026-08-27 08:50 | 2026-08-27 09:43 | 2026-08-27 10:09 | 2026-08-27 10:10 | 2026-08-27 10:10 |  |  | Fair | No | Remade broken service phase at secondary pole for 3 wire service using one 1 bolt clamp
Non-Outage | J.E.26.08.29440 | C001901499 | Richard Samuda | Manchester | Completed | Load_257142 | Spur Tree - 310 | 2026-08-26 17:34 | 2026-08-26 17:37 | 2026-08-26 18:56 | 2026-08-26 18:56 | 2026-08-26 20:10 | 2026-08-26 08:48 | 2026-08-26 20:48 | 2026-08-26 20:48 |  |  | Fair | No | Change corroded 1bolte clamp on customer neutral wire that was corroded causing customer to experience low voltage using 1 Bolt clamp customer back to normal voltage 116
Outage | J.E.26.08.50273 | C001901503 | Hartley Chin | Clarendon | Completed | Load_247003 | May Pen - 210 | 2026-08-26 17:39 | 2026-08-26 17:53 | 2026-08-26 20:10 | 2026-08-26 20:38 | 2026-08-26 21:47 | 2026-08-26 22:20 | 2026-08-26 22:23 | 2026-08-26 22:23 | BrokenWire |  | Fair | No | Found broken #2 twisted caused by overloaded truck … repair broken service … use 2 clamp ..
Outage | J.E.26.08.50167 | C001901504 | Hartley Chin | Clarendon | Completed | Load_265179 | Parnassus - 210 | 2026-08-26 17:40 | 2026-08-26 17:53 | 2026-08-26 18:02 | 2026-08-26 19:15 | 2026-08-26 19:45 | 2026-08-26 20:07 | 2026-08-26 20:08 | 2026-08-26 20:08 |  |  | Fair | No | Prem not found .. unable to contact customer with… area patrolled and found okay ..
Outage | J.E.26.08.50386 | C001901509 | Fitzroy Turner | KSAS | Completed | Load_240364 | Cane River - 410 | 2026-08-26 17:56 | 2026-08-26 17:59 | 2026-08-26 19:02 | 2026-08-26 19:02 | 2026-08-26 19:02 | 2026-08-26 19:03 | 2026-08-26 19:03 | 2026-08-26 19:03 |  |  | Fair | No | Customer premises found with electricity supply
Non-Outage | J.E.26.08.49337 | C001901514 | Edward Royal |  | Completed |  |  | 2026-08-26 18:07 | 2026-08-26 18:08 | 2026-08-26 18:45 | 2026-08-26 18:46 | 2026-08-26 18:45 | 2026-08-26 18:46 | 2026-08-26 18:46 | 2026-08-26 18:46 |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.08.50522 | C001901516 | Oshane Warren |  | Completed |  |  | 2026-08-26 18:07 | 2026-08-26 18:08 | 2026-08-26 20:51 | 2026-08-26 20:51 | 2026-08-26 21:38 | 2026-08-26 21:42 | 2026-08-26 21:43 | 2026-08-26 21:43 |  |  | Fair | No | Remove vegetation from line section and replace 3 amp 25 kva transformer fuse
Outage | J.E.26.08.50467 | C001901519 | Neville Spencer | Clarendon | Completed | Load_353845 | May Pen - 110 | 2026-08-26 18:15 | 2026-08-26 18:19 | 2026-08-26 19:37 | 2026-08-26 19:37 | 2026-08-26 20:55 | 2026-08-26 21:30 | 2026-08-26 21:33 | 2026-08-26 21:33 |  |  | Fair | No | Cleared tree limb from 13.8 kv line renew blown 10 amp J/ fuse supply restored.
Outage | J.E.26.08.50491 | C001901518 | Neville Spencer | Clarendon | Completed | Load_259206 | May Pen - 110 | 2026-08-26 18:15 | 2026-08-26 18:19 | 2026-08-26 21:34 | 2026-08-26 22:00 | 2026-08-26 22:17 | 2026-08-26 22:20 | 2026-08-26 22:26 | 2026-08-26 22:26 |  |  | Fair | No | Found 10 kva xmfr trip at pole # 010604 feeding 2, circuit reset same supply restored, need burnt 10 kva xmfr at pole # 0106046 to replaced voltage reading at the end of line 102 105 210 .
Outage | J.E.26.08.50557 | C001901521 | Roxroy Needham | St.Ann | Completed | Load_239335 | Cardiff Hall - 310 | 2026-08-26 18:27 | 2026-08-26 18:28 | 2026-08-26 20:05 | 2026-08-26 20:06 | 2026-08-26 21:42 | 2026-08-26 21:48 | 2026-08-26 21:49 | 2026-08-26 21:49 |  |  | Fair | No | Remove tree limb from line and replace 1- 8 amp junction fuse
Non-Outage | J.E.26.08.42303 | C001901524 | Hopeton Henry | St.Thomas | Completed | Load_241706 | Good Year - 110 | 2026-08-26 18:35 | 2026-08-26 18:39 | 2026-08-26 18:43 | 2026-08-26 18:50 | 2026-08-26 19:20 | 2026-08-26 19:45 | 2026-08-26 19:46 | 2026-08-26 19:46 |  |  | Fair | No | Day light attention required, premises closed
Non-Outage | J.E.26.08.43375 | C001901525 | Hopeton Henry | St.Thomas | Completed | Load_258585 | Good Year - 210 | 2026-08-26 18:36 | 2026-08-26 18:39 | 2026-08-26 18:43 | 2026-08-27 11:49 | 2026-08-27 12:31 | 2026-08-27 12:32 | 2026-08-27 12:32 | 2026-08-27 12:32 |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.08.50535 | C001901526 | Hopeton Henry | St.Thomas | Completed | Load_267910 | Good Year - 210 | 2026-08-26 18:36 | 2026-08-26 18:39 | 2026-08-26 18:43 | 2026-08-26 19:47 | 2026-08-26 19:54 | 2026-08-26 20:05 | 2026-08-26 20:05 | 2026-08-26 20:05 |  |  | Fair | No | Premises closed.. daylight attention required
Outage | J.E.26.08.50408 | C001901528 | Horace Malcolm | St.James | Completed | Load_244479 | Queens Drive - 810 | 2026-08-26 18:51 | 2026-08-26 18:52 | 2026-08-26 19:13 | 2026-08-26 19:44 | 2026-08-26 19:43 | 2026-08-26 19:45 | 2026-08-26 19:45 | 2026-08-26 19:45 |  |  | Fair | No | Unable to locate costumers or premises multiple calls to customers unavailable
Outage | J.E.26.08.50753 | C001901532 | Oshane Warren | Westmoreland | Completed | Load_250796 | Paradise - 210 | 2026-08-26 18:54 | 2026-08-26 18:58 | 2026-08-26 22:13 | 2026-08-26 22:13 | 2026-08-26 22:13 | 2026-08-26 22:14 | 2026-08-26 22:14 | 2026-08-26 22:14 |  |  | Fair | No | Check and found okay
Outage | J.E.26.08.50539 | C001901538 | Richard Samuda | Manchester | Completed | Load_238520 | Spur Tree - 310 | 2026-08-26 19:07 | 2026-08-26 20:33 | 2026-08-26 22:00 | 2026-08-26 22:03 | 2026-08-26 22:04 | 2026-08-26 22:06 | 2026-08-26 22:06 | 2026-08-26 22:06 |  |  | Fair | No | Premises not located and call to phone no answer
Outage | J.E.26.08.50729 | C001901540 | Romeo Brissett | St.James | Completed | Load_242100 | Bogue - 510 | 2026-08-26 19:09 | 2026-08-26 19:10 | 2026-08-26 21:43 | 2026-08-26 21:43 | 2026-08-26 21:43 | 2026-08-26 21:40 | 2026-08-26 21:43 | 2026-08-26 21:43 |  |  | Fair | No | Check and found ok
Non-Outage | J.E.26.08.50774 | C001901549 | Richman Whyte | Westmoreland | Completed | Load_572162 | Paradise - 310 | 2026-08-26 19:23 | 2026-08-26 19:27 | 2026-08-27 00:24 | 2026-08-27 00:24 | 2026-08-27 00:24 | 2026-08-27 00:25 | 2026-08-27 00:25 | 2026-08-27 00:25 |  |  | Fair | No | Check and found okay pump is working fine # voltage
Outage | J.E.26.08.50619 | C001901550 | Christopher West | St.Catherine | Completed | Load_257054 | Twickenham - 210 | 2026-08-26 19:24 | 2026-08-26 19:25 | 2026-08-26 20:05 | 2026-08-26 20:05 | 2026-08-26 20:23 | 2026-08-26 22:07 | 2026-08-26 22:07 | 2026-08-26 22:07 | Fire |  | Fair | No | A burnt off open secondary jumper was found for the lower phase caused from a kite tail that got entangled, a 50kva transformer was de-energized, kite tail removed, used 2 clamps and 2’ 2/0AA for repairs, transformer was re-energized, area now okay.
Outage | J.E.26.08.50754 | C001901578 | Edward Royal | KSAN | Completed | Load_265722 | Washington Blvd - 810 | 2026-08-26 19:46 | 2026-08-26 19:47 | 2026-08-26 20:17 | 2026-08-26 20:18 | 2026-08-26 20:57 | 2026-08-27 00:13 | 2026-08-27 00:13 | 2026-08-27 00:13 | Fire |  | Fair | No | Spliced and reconnected secondary 2 north cable using 40 ft 2 north tripe x cables 8 single bolt clamp
Outage | J.E.26.08.50983 | C001901577 | Milton Charlton | KSAN | Completed | Load_261791 | Hope - 510 | 2026-08-26 19:46 | 2026-08-26 19:47 | 2026-08-26 20:09 | 2026-08-26 20:29 | 2026-08-26 21:20 | 2026-08-26 20:05 | 2026-08-26 21:22 | 2026-08-26 21:22 |  |  | Fair | No | Fou okay upon arrival. Matter was resolved.
Non-Outage | J.E.26.08.51201 | C001901584 | Oshane Warren | Westmoreland | Completed | Load_239792 | Paradise - 310 | 2026-08-26 19:51 | 2026-08-26 19:52 |  | 2026-08-27 11:26 | 2026-08-27 11:25 | 2026-08-27 11:34 | 2026-08-27 11:35 | 2026-08-27 11:35 |  |  | Fair | No | Check and found ok voltage 234 243 228 418 410 396 found and left pump in working
Non-Outage | J.E.26.08.50965 | C001901612 | Marlon Authors |  | Completed |  |  | 2026-08-26 20:09 | 2026-08-26 20:10 | 2026-08-26 21:43 | 2026-08-26 22:03 | 2026-08-26 22:02 | 2026-08-26 22:03 | 2026-08-26 22:03 | 2026-08-26 22:03 |  |  | Fair | No | Customer said supply was restored
Outage | J.E.26.08.50631 | C001901610 | Selvin White | St.Elizabeth | Completed | Load_239662 | Maggotty - 110 | 2026-08-26 20:09 | 2026-08-27 07:30 | 2026-08-27 08:07 | 2026-08-27 08:07 | 2026-08-27 09:15 | 2026-08-27 10:51 | 2026-08-27 10:55 | 2026-08-27 10:55 |  |  | Fair | No | Replaced a blown 2 amp fuse for a 25 kva transformer after disconnecting a customer with defective service wire beyond the meter and also after removing illegal connections from circuit. Supply restored to the section and the customer was advised.
Outage | J.E.26.08.50955 | C001901611 | Hopeton Henry | St.Thomas | Completed | Load_270128 | Good Year - 110 | 2026-08-26 20:09 | 2026-08-26 20:15 | 2026-08-26 22:07 | 2026-08-26 22:07 | 2026-08-27 08:18 | 2026-08-27 08:18 | 2026-08-27 08:19 | 2026-08-27 08:19 |  |  | Fair | No | Splice and retention service wire , reading 114-116-230 volts
Outage | J.E.26.08.51050 | C001901609 | Hopeton Henry | St.Thomas | Completed | Load_255249 | Good Year - 110 | 2026-08-26 20:09 | 2026-08-26 20:10 | 2026-08-26 21:31 | 2026-08-26 21:34 | 2026-08-26 22:05 | 2026-08-26 22:05 | 2026-08-26 22:07 | 2026-08-26 22:07 |  |  | Fair | No | Premises closed… customer request day visit
Outage | J.E.26.08.50439 | C001901616 | Damion Reid | Manchester | Completed | Load_266716 | Kendal - 210 | 2026-08-26 20:11 | 2026-08-27 07:19 | 2026-08-27 12:49 | 2026-08-27 12:50 | 2026-08-27 14:00 | 2026-08-27 14:50 | 2026-08-27 14:52 | 2026-08-27 14:52 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Remade burnt off phase at secondary jumper using one 1 bolt clamp
Outage | J.E.26.08.51197 | C001901613 | Jermaine Williams | Clarendon | Completed | Load_263164 | Monymusk - 410 | 2026-08-26 20:11 | 2026-08-27 08:22 | 2026-08-27 12:32 | 2026-08-27 12:33 | 2026-08-27 13:06 | 2026-08-27 13:06 | 2026-08-27 13:07 | 2026-08-27 13:07 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.51192 | C001901631 | Horace Malcolm | St.James | Completed | Load_253128 | Queens Drive - 710 | 2026-08-26 20:22 | 2026-08-26 20:29 | 2026-08-26 23:17 | 2026-08-26 23:18 | 2026-08-26 23:18 | 2026-08-26 23:20 | 2026-08-26 23:21 | 2026-08-26 23:21 |  |  | Fair | No | Unable to locate customer or premises multiple calls to customer unavailable no direction given
Outage | J.E.26.08.51660 | C001901639 | Richard Samuda | Manchester | Completed | Load_261060 | Spur Tree - 310 | 2026-08-26 20:31 | 2026-08-26 20:33 | 2026-08-26 20:48 | 2026-08-26 20:49 | 2026-08-26 21:19 | 2026-08-26 09:54 | 2026-08-26 21:54 | 2026-08-26 21:54 |  |  | Fair | No | Change corroded 1bolt clamp on transformer drop lead that was corroded causing customers to experience single phasing using 1 bolt clamp transformer pole needs de bushing
Outage | J.E.26.08.51086 | C001901642 | Elvis Trowers | KSAN | Completed | Load_256666 | Washington Blvd - 710 | 2026-08-26 20:39 | 2026-08-26 20:40 | 2026-08-26 21:12 | 2026-08-26 21:13 | 2026-08-26 21:38 | 2026-08-26 22:15 | 2026-08-26 22:12 | 2026-08-26 22:12 |  |  | Fair | No | Customer is getting low voltage from open wire secondary checks at customer pothead 89-87-177volts at open wire secondary 90-89-182 volts and at transformer drop lead 111-111-223 volts. There’s no topping mechanizing on the out side of transformer. Multiple customers have the same problem.Refer to in- house team.m
Outage | J.E.26.08.51734 | C001901644 | Milton Charlton | KSAN | Completed | Load_252653 | West Kings House - 310 | 2026-08-26 20:51 | 2026-08-26 20:54 | 2026-08-26 21:22 | 2026-08-26 21:23 | 2026-08-26 21:24 | 2026-08-26 21:50 | 2026-08-26 21:56 | 2026-08-26 21:56 |  |  | Fair | No | Found okay upon arrival. Customer has an internal problem.
Outage | J.E.26.08.52000 | C001901645 | Rusean Allen | KSAS | Completed | Load_242836 | Cane River - 310 | 2026-08-26 20:52 | 2026-08-27 07:51 | 2026-08-27 10:51 | 2026-08-27 10:52 | 2026-08-27 12:00 | 2026-08-27 12:14 | 2026-08-27 12:14 | 2026-08-27 12:14 |  |  | Fair | No | Hexing failure, refer to field service department.
Outage | J.E.26.08.52280 | C001901649 | Stephen Taylor | St.Thomas | Completed | Load_258931 | Lysson - 410 | 2026-08-26 21:20 | 2026-08-27 07:17 | 2026-08-27 08:45 | 2026-08-27 08:46 | 2026-08-27 08:45 | 2026-08-27 08:48 | 2026-08-27 08:49 | 2026-08-27 08:49 |  |  | Fair | No | Premese found okay rdg 113–112–226
Outage | J.E.26.08.52136 | C001901653 | Damion Reid | Manchester | Completed | Load_292643 | Kendal - 210 | 2026-08-26 21:52 | 2026-08-27 07:19 | 2026-08-27 10:11 | 2026-08-27 10:11 | 2026-08-27 10:44 | 2026-08-27 11:18 | 2026-08-27 11:19 | 2026-08-27 11:19 | BrokenWire |  | Fair | No | Unable to contact or locate customer
Non-Outage | J.E.26.07.37021 | C001901654 | Raymond Lewis | St.Ann | Completed | Load_315583 | Ocho Rios - 310 | 2026-08-26 22:00 | 2026-08-26 23:20 | 2026-08-27 00:45 | 2026-08-27 00:45 | 2026-08-27 01:43 | 2026-08-27 02:02 | 2026-08-27 02:06 | 2026-08-27 02:06 |  |  | Fair | No | Security say that he don’t learn about any electical problem on the plant
Outage | J.E.26.08.51073 | C001901679 | Delano Gayle | St.Catherine | Completed | Load_254900 | Tredegar - 310 | 2026-08-26 23:18 | 2026-08-26 23:20 | 2026-08-27 02:28 | 2026-08-27 02:29 | 2026-08-27 03:14 | 2026-08-27 03:20 | 2026-08-27 03:20 | 2026-08-27 03:20 | Fire |  | Fair | No | Area/premises found okay no fire seen
Non-Outage | J.E.26.08.50494 | C001901680 | Delano Gayle | Portmore | Completed | Load_249243 | Naggo Head - 610 | 2026-08-26 23:19 | 2026-08-26 23:20 | 2026-08-27 00:11 | 2026-08-27 02:23 | 2026-08-27 02:24 | 2026-08-27 02:27 | 2026-08-27 02:28 | 2026-08-27 02:28 | BrokenWire |  | Fair | No | Premises not found, area found okay
Outage | J.E.26.08.53265 | C001901685 | Rusean Allen | KSAN | Completed | Load_265344 | Constant Spring - 410 | 2026-08-27 00:23 | 2026-08-27 00:24 | 2026-08-27 01:08 | 2026-08-27 01:08 | 2026-08-27 01:08 | 2026-08-27 01:09 | 2026-08-27 01:09 | 2026-08-27 01:09 |  |  | Fair | No | Customer cell phone ring with out answering Daylight attention
Outage | J.E.26.08.53988 | C001901688 | Rusean Allen | KSAN | Completed | Load_245979 | West Kings House - 410 | 2026-08-27 04:53 | 2026-08-27 04:54 | 2026-08-27 05:45 | 2026-08-27 05:45 | 2026-08-27 06:04 | 2026-08-27 06:29 | 2026-08-27 06:29 | 2026-08-27 06:29 |  |  | Fair | No | 1x 15amp fuse found 1x 15amp fuse replaced.1x 3amp fuse found 1x 3amp fuse replaced.
Outage | J.E.26.08.54165 | C001901696 | Donald Cunningham | Portmore | Completed | Load_570222 | Naggo Head - 610 | 2026-08-27 05:48 | 2026-08-27 08:01 | 2026-08-27 12:39 | 2026-08-27 12:40 | 2026-08-27 13:33 | 2026-08-27 14:25 | 2026-08-27 14:31 | 2026-08-27 14:31 |  |  | Fair | No | 3 blown fuse found and replace with 10 amp for junction and 3 amp fuse for 25 kva transformer
Outage | J.E.26.08.49464 | C001901717 | Christopher Edwards | KSAN | Completed | Load_243332 | Constant Spring - 410 | 2026-08-27 07:12 | 2026-08-27 07:48 | 2026-08-27 14:31 | 2026-08-27 14:32 | 2026-08-27 14:37 | 2026-08-27 15:32 | 2026-08-27 15:33 | 2026-08-27 15:33 |  |  | Fair | No | Customer meter is burnt and needs to be replaced
Outage | J.E.26.08.54245 | C001901720 | Cliton Henry | St.Mary | Completed | Load_256925 | Oracabessa - 210 | 2026-08-27 07:16 | 2026-08-27 07:17 | 2026-08-27 07:30 | 2026-08-27 07:57 | 2026-08-27 07:57 | 2026-08-27 07:59 | 2026-08-27 07:59 | 2026-08-27 07:59 |  |  | Fair | No | The customer stated that this is a new installation which require service wire and meter. Kindly refer to Field Service Department
Outage | J.E.26.08.52420 | C001901722 | Edward Royal | KSAN | Completed | Load_293737 | Washington Blvd - 710 | 2026-08-27 07:19 | 2026-08-27 07:52 | 2026-08-27 08:32 | 2026-08-27 08:33 | 2026-08-27 09:25 | 2026-08-27 09:58 | 2026-08-27 09:58 | 2026-08-27 09:58 |  |  | Fair | No | Defective 15kva yp enclosure with transformer attached need to be change it a yp rami box #yp03661 pole#0114879 reffered to field
Outage | J.E.26.08.53330 | C001901723 | Omar Harris | St.Ann | Completed | Load_574259 | Roaring River - 210 | 2026-08-27 07:20 | 2026-08-27 07:23 | 2026-08-27 07:55 | 2026-08-27 08:04 | 2026-08-27 08:29 | 2026-08-27 08:30 | 2026-08-27 08:32 | 2026-08-27 08:32 |  |  | Fair | No | Meter change require refer to field service
Outage | J.E.26.08.51955 | C001901725 | Omar Harris | St.Ann | Completed | Load_260759 | Roaring River - 210 | 2026-08-27 07:21 | 2026-08-27 07:23 | 2026-08-27 10:08 | 2026-08-27 10:09 | 2026-08-27 10:09 | 2026-08-27 10:17 | 2026-08-27 10:17 | 2026-08-27 10:17 |  |  | Fair | No
Outage | J.E.26.08.53118 | C001901724 | Damion Reid | Manchester | Completed | Load_251015 | Kendal - 210 | 2026-08-27 07:21 | 2026-08-27 07:21 | 2026-08-27 11:22 | 2026-08-27 11:22 | 2026-08-27 12:17 | 2026-08-27 12:47 | 2026-08-27 12:48 | 2026-08-27 12:48 |  |  | Fair | No | Blown 2amp fuse found for 25kva transformer cause by contamination line patrol and replace blown fuse
Outage | J.E.26.08.54088 | C001901727 | Collin Robinson | Portland | Completed | Load_244183 | Port Antonio - 310 | 2026-08-27 07:21 | 2026-08-27 07:23 | 2026-08-27 07:49 | 2026-08-27 07:49 | 2026-08-27 08:17 | 2026-08-27 08:37 | 2026-08-27 08:37 | 2026-08-27 08:37 | Fire |  | EarthMovement | No | Isolate 50 KVA transformer to change burn one bolt clamp that connects from transformer to 2/0 twisted neutral conductor Voltage reading 120v 120v 240v
Outage | J.E.26.08.52633 | C001901728 | Selvin White | St.Elizabeth | Completed | Load_239662 | Maggotty - 110 | 2026-08-27 07:29 | 2026-08-27 07:30 | 2026-08-27 10:55 | 2026-08-27 10:56 | 2026-08-27 11:01 | 2026-08-27 11:07 | 2026-08-27 11:07 | 2026-08-27 11:07 |  |  | Fair | No | Customer says supply was okay at the time of visit.
Outage | J.E.26.08.54123 | C001901729 | Selvin White | St.Elizabeth | Completed | Load_259624 | Maggotty - 110 | 2026-08-27 07:29 | 2026-08-27 07:30 | 2026-08-27 11:08 | 2026-08-27 11:09 | 2026-08-27 11:38 | 2026-08-27 12:13 | 2026-08-27 12:13 | 2026-08-27 12:13 |  |  | Fair | No | Please refer to the C.Johnson and Jessie Morales at the field service department for investigation as customer is complaining about bills.
Outage | J.E.26.08.52640 | C001901731 | Kemark Slue | Clarendon | Completed | Load_256506 | May Pen - 110 | 2026-08-27 07:34 | 2026-08-27 07:40 | 2026-08-27 12:21 | 2026-08-27 13:17 | 2026-08-27 13:18 | 2026-08-27 11:49 | 2026-08-27 13:32 | 2026-08-27 13:32 |  |  | Fair | No | Unable to locate premises due to inadequate directions and all calls to number given were unsuccessful. Supply was found in the general area.
Outage | J.E.26.08.54254 | C001901730 | Clyde Brown | Clarendon | Completed | Load_353845 | May Pen - 110 | 2026-08-27 07:34 | 2026-08-27 07:39 | 2026-08-27 08:15 | 2026-08-27 08:16 | 2026-08-27 09:05 | 2026-08-27 08:59 | 2026-08-27 09:07 | 2026-08-27 09:07 |  |  | Fair | No | Found ok
Outage | J.E.26.08.53035 | C001901736 | Michael Paterson | Westmoreland | Completed | Load_265324 | Paradise - 210 | 2026-08-27 07:36 | 2026-08-27 07:37 | 2026-08-27 08:25 | 2026-08-27 08:26 | 2026-08-27 12:12 | 2026-08-27 12:50 | 2026-08-27 12:59 | 2026-08-27 12:59 |  |  | Fair | No | Patrol done, found 25 kva tronsfomer fuse blown,further check confirm transformer defective and needs to change urgently,please refer to James Hudson at paradise,several illegal connections in areas due to migration, recent work done in area parallel to currently affected, the masses are unable to throw up, thus causing an overload on this circuit. Crew recommend removal of open secondary, replace with 2/0 triplex.
Outage | J.E.26.08.53551 | C001901737 | Michael Paterson | Westmoreland | Completed | Load_262638 | Paradise - 110 | 2026-08-27 07:36 | 2026-08-27 07:37 | 2026-08-27 08:05 | 2026-08-27 08:06 | 2026-08-27 08:21 | 2026-08-27 08:22 | 2026-08-27 08:23 | 2026-08-27 08:23 |  |  | Fair | No | Contact customer via phone call customer advised crew that he did not make a report
Non-Outage | J.E.26.08.45927 | C001901740 | Hartley Chin |  | Completed |  |  | 2026-08-27 07:38 | 2026-08-27 20:46 | 2026-08-27 21:25 | 2026-08-27 22:22 | 2026-08-27 22:22 | 2026-08-27 23:08 | 2026-08-27 23:09 | 2026-08-27 23:09 |  |  | Fair | No | Repair service wire …. Use 2 clamp
Outage | J.E.26.08.52430 | C001901742 | Kemark Slue | St.Catherine | Completed | Load_244637 | New Michelton - 210 | 2026-08-27 07:41 | 2026-08-27 07:44 | 2026-08-27 08:01 | 2026-08-27 11:09 | 2026-08-27 11:09 | 2026-08-27 10:17 | 2026-08-27 13:16 | 2026-08-27 13:16 | BrokenWire |  | Fair | No | Upon arrival at the location the crew discovered that duplex service supplying customer was broken, it’s alleged that a truck with an oversized load came in contact with service, splice and retention service using approximately 30 ft of #6 triplex, one penn union, one, one bolt clamp and customer is now okay.
Outage | J.E.26.08.54303 | C001901741 | Donald Cunningham | St.Catherine | Completed | Load_240110 | Twickenham - 210 | 2026-08-27 07:41 | 2026-08-27 07:45 | 2026-08-27 08:02 | 2026-08-27 08:03 | 2026-08-27 09:41 | 2026-08-27 09:46 | 2026-08-27 09:47 | 2026-08-27 09:47 |  |  | Fair | No | Premises found close supply in area
Outage | J.E.26.08.50154 | C001901745 | Richard Nicholas | St.Catherine | Completed | Load_259475 | Tredegar - 310 | 2026-08-27 07:42 | 2026-08-27 07:45 | 2026-08-27 07:53 | 2026-08-27 07:54 | 2026-08-27 09:37 | 2026-08-27 10:03 | 2026-08-27 10:04 | 2026-08-27 10:04 |  |  | Fair | No | Premises found locked however supply found ok in the area.
Outage | J.E.26.08.50211 | C001901744 | Richard Grant | St.Catherine | Completed | Load_265369 | New Michelton - 310 | 2026-08-27 07:42 | 2026-08-27 15:44 | 2026-08-27 18:08 | 2026-08-27 18:08 | 2026-08-27 19:12 | 2026-08-27 19:41 | 2026-08-27 19:41 | 2026-08-27 19:41 |  |  | Fair | No | Meter found disconnected. Call made to office and supply restored. Premises left with supply and okay
Outage | J.E.26.08.50336 | C001901743 | Kemark Slue | St.Catherine | Completed | Load_269938 | New Michelton - 210 | 2026-08-27 07:42 | 2026-08-27 07:44 | 2026-08-27 08:01 | 2026-08-27 08:02 | 2026-08-27 10:57 | 2026-08-27 09:00 | 2026-08-27 11:09 | 2026-08-27 11:09 | Fire | Y | Fair | No | Upon arrival at the location the crew discovered that a large Ponciana tree is within close proximity to primary conductor which is possible to make contact when it’s extremely windy, please refer to A. Murray to have tree cut asap.
Outage | J.E.26.08.49964 | C001901748 | Oshane Warren | Westmoreland | Completed | Load_253744 | Paradise - 310 | 2026-08-27 07:44 | 2026-08-27 07:44 | 2026-08-27 11:36 | 2026-08-27 11:36 | 2026-08-27 13:15 | 2026-08-27 13:15 | 2026-08-27 13:22 | 2026-08-27 13:22 |  |  | Fair | No | Need 100ft #6 twisted to carry out repairs and refer to evening crew due to insolvency wire
Outage | J.E.26.08.50599 | C001901749 | Richard Nicholas | St.Catherine | Completed | Load_263372 | Tredegar - 210 | 2026-08-27 07:45 | 2026-08-27 07:57 | 2026-08-27 13:47 | 2026-08-27 13:48 | 2026-08-27 14:15 | 2026-08-27 14:57 | 2026-08-27 15:03 | 2026-08-27 15:03 |  |  | Fair | No | A truck come in contact with a primary over head guy pole as a result the guy wire come in tangle with a 25kva transformer switch bottom.broken pole removed from the road way and guy wire cleared from switch bottom.blown 25kva transformer 3amp fuse replaced.supply left ok in the area.
Non-Outage | J.E.26.08.50176 | C001901750 | Christopher Edwards |  | Completed |  |  | 2026-08-27 07:46 | 2026-08-27 07:48 | 2026-08-27 18:16 | 2026-08-27 18:16 | 2026-08-27 18:18 | 2026-08-27 18:20 | 2026-08-27 18:20 | 2026-08-27 18:20 |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Outage | J.E.26.08.49146 | C001901755 | Richard Nicholas |  | Completed | Load_568488 | Tredegar - 210 | 2026-08-27 07:46 | 2026-08-27 07:53 | 2026-08-27 10:04 | 2026-08-27 10:05 | 2026-08-27 10:29 | 2026-08-27 10:44 | 2026-08-27 10:45 | 2026-08-27 10:45 |  |  | Fair | No | Rammy failure.please refer to the relevant department.
Outage | J.E.26.08.53634 | C001901752 | Milton Charlton | KSAN | Completed | Load_252603 | Hope - 510 | 2026-08-27 07:46 | 2026-08-27 07:48 | 2026-08-27 09:13 | 2026-08-27 09:14 | 2026-08-27 09:33 | 2026-08-27 09:25 | 2026-08-27 09:35 | 2026-08-27 09:35 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.54014 | C001901754 | Elvis Trowers | KSAN | Completed | Load_242617 | West Kings House - 410 | 2026-08-27 07:46 | 2026-08-27 07:49 | 2026-08-27 09:02 | 2026-08-27 09:27 | 2026-08-27 09:27 | 2026-08-27 09:20 | 2026-08-27 09:28 | 2026-08-27 09:28 |  |  | Fair | No | Found okay upon arrival. Customer states matter was resolved.
Outage | J.E.26.08.54309 | C001901753 | Christopher Edwards | KSAN | Completed | Load_259928 | Constant Spring - 410 | 2026-08-27 07:46 | 2026-08-27 07:47 | 2026-08-27 11:59 | 2026-08-27 11:59 | 2026-08-27 12:54 | 2026-08-27 14:28 | 2026-08-27 14:31 | 2026-08-27 14:31 |  | Y | Fair | No | Splice and retention broken open secondary wireUsing 60ft #2 AA conductor 2-#2 preforms 3 one bolt clamps Refuse blown 25 kva transformer Using (1) 3 ampsClear tree limb from open secondary wire
Non-Outage | J.E.26.08.42195 | C001901757 | Ricky Hall |  | Completed |  |  | 2026-08-27 07:47 | 2026-08-27 07:54 | 2026-08-27 08:15 | 2026-08-27 10:54 | 2026-08-27 10:54 | 2026-08-27 10:54 | 2026-08-27 10:55 | 2026-08-27 10:55 | Fire |  | Fair | No | Premises not located insufficient information
Outage | J.E.26.08.41922 | C001901758 | Ricky Hall | St.Catherine | Completed | Load_264046 | Rhodens Pen - 410 | 2026-08-27 07:47 | 2026-08-27 07:54 | 2026-08-27 08:15 | 2026-08-27 08:26 | 2026-08-27 10:20 | 2026-08-27 10:53 | 2026-08-27 10:53 | 2026-08-27 10:53 | BrokenWire |  | Fair | No | No broken wires seen
Outage | J.E.26.08.35541 | C001901762 | Ricky Hall | St.Catherine | Completed | Load_242365 | Rhodens Pen - 210 | 2026-08-27 07:48 | 2026-08-27 07:54 | 2026-08-27 11:34 | 2026-08-27 11:35 | 2026-08-27 12:58 | 2026-08-27 13:09 | 2026-08-27 13:10 | 2026-08-27 13:10 |  |  | Fair | No | Issue was resolved on previous shift
Non-Outage | J.E.26.08.42017 | C001901766 | Eric Williams | KSAN | Completed | Load_261308 | Constant Spring - 210 | 2026-08-27 07:53 | 2026-08-27 08:14 | 2026-08-27 10:13 | 2026-08-27 10:14 | 2026-08-27 10:38 | 2026-08-27 12:09 | 2026-08-27 12:10 | 2026-08-27 12:10 |  |  | Fair | No | Bank of 2 transformer burnt joint at transformer lug, used 1 transformer lug to carry out repairs
Non-Outage | J.E.26.08.48609 | C001901772 | Rochaine Hussey | KSAN | Completed | Load_241354 | Constant Spring - 210 | 2026-08-27 07:53 | 2026-08-27 07:58 | 2026-08-27 16:55 | 2026-08-27 16:56 | 2026-08-27 16:56 | 2026-08-27 16:58 | 2026-08-27 16:58 | 2026-08-27 16:58 |  |  | Fair | No | Neutral wire burnt off poleWire was reconnected Issue resolved 119/122/242v
Non-Outage | J.E.26.08.48613 | C001901774 | Rochaine Hussey | KSAN | Completed | Load_241354 | Constant Spring - 210 | 2026-08-27 07:53 | 2026-08-27 07:58 | 2026-08-27 13:47 | 2026-08-27 13:47 | 2026-08-27 13:48 | 2026-08-27 14:23 | 2026-08-27 14:23 | 2026-08-27 14:23 |  |  | Fair | No | Neutral wire burnt off poleWire was rejoined Issue resolved 119/122/242v
Non-Outage | J.E.26.08.48986 | C001901775 | Rochaine Hussey | KSAN | Completed | Load_262628 | Constant Spring - 410 | 2026-08-27 07:53 | 2026-08-27 07:58 | 2026-08-27 13:28 | 2026-08-27 16:14 | 2026-08-27 16:13 | 2026-08-27 16:14 | 2026-08-27 16:15 | 2026-08-27 16:15 |  |  | Fair | No | Customer said issue was already resolved
Non-Outage | J.E.26.08.50354 | C001901773 | Christopher Edwards | KSAN | Completed | Load_267896 | Constant Spring - 310 | 2026-08-27 07:53 | 2026-08-28 07:32 | 2026-08-28 07:47 | 2026-08-28 10:15 | 2026-08-28 10:14 | 2026-08-28 10:14 | 2026-08-28 10:15 | 2026-08-28 10:15 |  |  | Fair | No | Related to previous call that was resolved
Non-Outage | J.E.26.08.51330 | C001901764 | Wayne Dillion | St.Elizabeth | Completed | Load_265437 | Maggotty - 210 | 2026-08-27 07:53 | 2026-08-27 07:54 | 2026-08-27 11:22 | 2026-08-27 11:22 | 2026-08-27 11:22 | 2026-08-27 11:24 | 2026-08-27 11:24 | 2026-08-27 11:24 |  |  | Fair | No | Customer said supply is okay.
Non-Outage | J.E.26.08.37945 | C001901777 | Fredrick Hamilton | KSAS | Completed | Load_254756 | Duhaney - 310 | 2026-08-27 07:58 | 2026-08-27 07:59 | 2026-08-27 08:04 | 2026-08-27 10:26 | 2026-08-27 10:39 | 2026-08-27 11:08 | 2026-08-27 11:08 | 2026-08-27 11:08 |  |  | Fair | No | 118v obtained Corrosion and slack connection detected in meter socket same was corrected
Non-Outage | J.E.26.08.45903 | C001901776 | Fredrick Hamilton | KSAS | Completed | Load_242388 | Duhaney - 310 | 2026-08-27 07:58 | 2026-08-27 07:59 | 2026-08-27 08:04 | 2026-08-27 10:11 | 2026-08-27 10:22 | 2026-08-27 10:24 | 2026-08-27 10:25 | 2026-08-27 10:25 |  |  | Fair | No | Premises locked at time of visit no occupant seen Rami customer
Non-Outage | J.E.26.08.49334 | C001901781 | Andrae Clarke | Portland | Completed | Load_255204 | Port Antonio - 310 | 2026-08-27 07:59 | 2026-08-27 08:00 | 2026-08-27 09:15 | 2026-08-27 14:46 | 2026-08-27 14:46 | 2026-08-27 14:48 | 2026-08-27 14:48 | 2026-08-27 14:48 |  |  | Fair | No | Premises not found made several phone calls to the customer and got no response
Non-Outage | J.E.26.08.50122 | C001901779 | Andrae Clarke | Portland | Completed | Load_240878 | Port Antonio - 310 | 2026-08-27 07:59 | 2026-08-27 08:00 | 2026-08-27 11:51 | 2026-08-27 11:52 | 2026-08-27 12:54 | 2026-08-27 12:54 | 2026-08-27 12:58 | 2026-08-27 12:58 |  |  | Fair | No | Check voltage 126/114/240Change one bolt clamp on neutral wire Connection at transformer needs changing as well refer to emergency
Non-Outage | J.E.26.08.50253 | C001901780 | Andrae Clarke | Portland | Completed | Load_258958 | Port Antonio - 410 | 2026-08-27 07:59 | 2026-08-27 08:00 | 2026-08-27 13:56 | 2026-08-27 14:48 | 2026-08-27 15:02 | 2026-08-27 15:30 | 2026-08-27 15:16 | 2026-08-27 15:16 |  |  | Fair | No | Premises locked Made several phone calls to the customer and no response
Non-Outage | J.E.26.08.40805 | C001901785 | Fredrick Hamilton | KSAN | Completed | Load_256666 | Washington Blvd - 710 | 2026-08-27 08:00 | 2026-08-27 08:01 | 2026-08-27 08:04 | 2026-08-27 12:06 | 2026-08-27 12:05 | 2026-08-27 12:20 | 2026-08-27 12:21 | 2026-08-27 12:21 |  |  | Fair | No | Low voltage affecting multiple customers issue coming from transformer Please assign emergency to resolve issue 90v/110v obtained
Non-Outage | J.E.26.08.41151 | C001901786 | Fredrick Hamilton | KSAN | Completed | Load_265054 | Washington Blvd - 710 | 2026-08-27 08:00 | 2026-08-27 08:01 | 2026-08-27 08:04 | 2026-08-27 13:04 | 2026-08-27 13:04 | 2026-08-27 13:04 | 2026-08-27 13:06 | 2026-08-27 13:06 |  |  | Fair | No | Low voltage affecting entire area please assign to emergency Please assess transformer
Non-Outage | J.E.26.08.41225 | C001901783 | Fredrick Hamilton | KSAN | Completed | Load_256666 | Washington Blvd - 710 | 2026-08-27 08:00 | 2026-08-27 08:01 | 2026-08-27 08:04 | 2026-08-27 12:28 | 2026-08-27 12:44 | 2026-08-27 13:02 | 2026-08-27 13:03 | 2026-08-27 13:03 |  |  | Fair | No | 205v/105v/96v obtained Low voltage affecting entire area Please have field service check transformer
Non-Outage | J.E.26.08.49178 | C001901782 | Andrae Clarke | Portland | Completed | Load_264439 | Port Antonio - 310 | 2026-08-27 08:00 | 2026-08-27 08:00 | 2026-08-27 09:19 | 2026-08-27 09:20 | 2026-08-27 11:49 | 2026-08-27 11:29 | 2026-08-27 11:50 | 2026-08-27 11:50 |  |  | Fair | No
Non-Outage | J.E.26.08.52441 | C001901784 | Fredrick Hamilton | KSAN | Completed | Load_243339 | Washington Blvd - 710 | 2026-08-27 08:00 | 2026-08-27 08:01 | 2026-08-27 08:04 | 2026-08-28 09:45 | 2026-08-28 10:19 | 2026-08-28 10:31 | 2026-08-28 10:31 | 2026-08-28 10:31 |  |  | Fair | No | Low voltage affecting entire area please respond with emergency 182v/94.3v/89.9v obtained
Non-Outage | J.E.26.07.10544 | C001901793 | Error Coore | Manchester | Completed | Load_265070 | Kendal - 210 | 2026-08-27 08:01 | 2026-08-27 08:04 | 2026-08-27 12:23 | 2026-08-27 12:24 | 2026-08-27 13:06 | 2026-08-27 13:20 | 2026-08-27 13:22 | 2026-08-27 13:22 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.32111 | C001901791 | Error Coore | Manchester | Completed | Load_258367 | Kendal - 210 | 2026-08-27 08:01 | 2026-08-27 08:04 | 2026-08-28 11:43 | 2026-08-28 11:43 | 2026-08-28 12:51 | 2026-08-28 13:27 | 2026-08-28 13:28 | 2026-08-28 13:28 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.33498 | C001901790 | Error Coore | Manchester | Completed | Load_260503 | Kendal - 210 | 2026-08-27 08:01 | 2026-08-27 08:04 | 2026-08-28 10:39 | 2026-08-28 10:39 | 2026-08-28 11:33 | 2026-08-28 11:42 | 2026-08-28 11:43 | 2026-08-28 11:43 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.08.14971 | C001901789 | Fredrick Hamilton | KSAN | Completed | Load_267241 | Washington Blvd - 310 | 2026-08-27 08:01 | 2026-08-27 08:02 | 2026-08-27 08:05 | 2026-08-27 11:36 | 2026-08-27 11:48 | 2026-08-27 11:55 | 2026-08-27 11:57 | 2026-08-27 11:57 |  |  | Fair | No | Rami customer please assign bucket truck crew single phase issue coming from enclosure Pothead checked and found ok
Non-Outage | J.E.26.08.15916 | C001901792 | Fredrick Hamilton | KSAN | Completed | Load_247699 | Washington Blvd - 310 | 2026-08-27 08:01 | 2026-08-27 08:02 | 2026-08-27 08:05 | 2026-08-27 13:15 | 2026-08-27 13:35 | 2026-08-27 13:37 | 2026-08-27 13:37 | 2026-08-27 13:37 |  |  | Fair | No | Emergency required please check transformer low voltage affecting area
Non-Outage | J.E.26.08.19364 | C001901794 | Fredrick Hamilton | KSAN | Completed | Load_567704 | Washington Blvd - 310 | 2026-08-27 08:01 | 2026-08-27 08:02 | 2026-08-27 08:05 | 2026-08-28 10:32 | 2026-08-28 10:45 | 2026-08-28 10:48 | 2026-08-28 10:48 | 2026-08-28 10:48 |  |  | Fair | No | Bucket truck required issue affecting customers at pole parked vehicle at pole at time of visit and flow cables in the way Please assign to bucket truck crew
Non-Outage | J.E.26.08.23802 | C001901788 | Error Coore | Manchester | Completed | Load_239382 | Kendal - 210 | 2026-08-27 08:01 | 2026-08-27 08:04 | 2026-08-27 14:26 | 2026-08-27 14:26 | 2026-08-27 15:34 | 2026-08-27 16:11 | 2026-08-27 16:13 | 2026-08-27 16:13 |  |  | Fair | No | Found customer with wrap connection at pothead remade wrap connection using 3 service sleeve voltage reading 115/116/231 volts
Outage | J.E.26.08.53897 | C001901787 | Nickolas Rodriques | Portmore | Completed | Load_243335 | Naggo Head - 610 | 2026-08-27 08:01 | 2026-08-27 15:44 | 2026-08-27 21:24 | 2026-08-27 21:25 | 2026-08-27 21:54 | 2026-08-27 22:12 | 2026-08-27 22:15 | 2026-08-27 22:15 |  |  | Fair | No | Customer stated that he did not make any report and he is not having any electrical issues at the premises.
Non-Outage | J.E.26.06.21318 | C001901806 | Error Coore | Manchester | Completed | Load_241328 | Kendal - 210 | 2026-08-27 08:02 | 2026-08-27 08:04 | 2026-08-27 08:15 | 2026-08-27 08:16 | 2026-08-27 10:02 | 2026-08-27 11:15 | 2026-08-27 11:19 | 2026-08-27 11:19 |  |  | Fair | No | Suspect secondary jumper corroded unable to carry out repair due to leaning pole refer to emergency bucket truck crew
Non-Outage | J.E.26.06.22795 | C001901805 | Error Coore | Manchester | Completed | Load_254861 | Kendal - 210 | 2026-08-27 08:02 | 2026-08-27 08:04 | 2026-08-27 11:33 | 2026-08-27 11:34 | 2026-08-27 11:56 | 2026-08-27 12:14 | 2026-08-27 12:16 | 2026-08-27 12:16 |  |  | Fair | No | Premises found okay. Voltage reading 113/110/223. However customer has internal problem.
Non-Outage | J.E.26.06.23576 | C001901802 | Error Coore | Manchester | Completed | Load_248356 | Kendal - 210 | 2026-08-27 08:02 | 2026-08-27 08:04 | 2026-08-28 08:06 | 2026-08-28 08:06 | 2026-08-28 08:30 | 2026-08-28 08:40 | 2026-08-28 08:42 | 2026-08-28 08:42 |  |  | Fair | No | Premises not found. Unable to locate customer, not getting customer on phone
Non-Outage | J.E.26.06.23807 | C001901803 | Error Coore | Manchester | Completed | Load_241328 | Kendal - 210 | 2026-08-27 08:02 | 2026-08-27 08:04 | 2026-08-27 11:19 | 2026-08-27 11:19 | 2026-08-27 11:19 | 2026-08-27 11:19 | 2026-08-27 11:20 | 2026-08-27 11:20 |  |  | Fair | No | Suspect secondary jumper corroded unable to carry out repair due to leaning pole refer to emergency bucket truck crew
Non-Outage | J.E.26.06.30692 | C001901799 | Error Coore | Manchester | Completed | Load_241328 | Kendal - 210 | 2026-08-27 08:02 | 2026-08-27 08:04 | 2026-08-28 08:42 | 2026-08-28 08:43 | 2026-08-28 10:09 | 2026-08-28 10:37 | 2026-08-28 10:39 | 2026-08-28 10:39 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.06.39088 | C001901800 | Error Coore | Manchester | Completed | Load_251344 | Kendal - 210 | 2026-08-27 08:02 | 2026-08-27 08:04 | 2026-08-27 13:22 | 2026-08-27 13:22 | 2026-08-27 14:15 | 2026-08-27 14:24 | 2026-08-27 14:25 | 2026-08-27 14:25 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.00804 | C001901798 | Error Coore | Manchester | Completed | Load_1002481 | Kendal - 210 | 2026-08-27 08:02 | 2026-08-27 08:04 | 2026-08-27 16:13 | 2026-08-27 16:14 | 2026-08-27 16:43 | 2026-08-27 16:50 | 2026-08-27 16:51 | 2026-08-27 16:51 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.00806 | C001901797 | Error Coore | Manchester | Completed | Load_265474 | Kendal - 210 | 2026-08-27 08:02 | 2026-08-27 08:04 | 2026-08-28 13:28 | 2026-08-28 13:29 | 2026-08-28 14:54 | 2026-08-28 15:11 | 2026-08-28 15:12 | 2026-08-28 15:12 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.10521 | C001901796 | Error Coore | Manchester | Completed | Load_1002472 | Kendal - 210 | 2026-08-27 08:02 | 2026-08-27 08:04 | 2026-08-28 15:13 | 2026-08-28 15:13 | 2026-08-28 15:40 | 2026-08-28 15:50 | 2026-08-28 15:51 | 2026-08-28 15:51 |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Outage | J.E.26.08.50269 | C001901807 | Nickolas Rodriques | Portmore | Completed | Load_264074 | Naggo Head - 510 | 2026-08-27 08:02 | 2026-08-27 15:44 | 2026-08-27 20:27 | 2026-08-27 20:28 | 2026-08-27 21:00 | 2026-08-27 21:16 | 2026-08-27 21:21 | 2026-08-27 21:21 |  |  | Fair | No | Found customer with electricity. Reading found (118-117-235)
Outage | J.E.26.08.50375 | C001901804 | Nickolas Rodriques | St.Catherine | Completed | Load_289851 | Twickenham - 210 | 2026-08-27 08:02 | 2026-08-27 15:44 | 2026-08-27 17:57 | 2026-08-27 18:08 | 2026-08-27 18:30 | 2026-08-27 18:48 | 2026-08-27 19:05 | 2026-08-27 19:05 |  |  | Fair | No | Checked and found customer without electricity. All necessary checks were done and it was found that the issue is stemming from the EG box (EG 01156). Refer to field service.
Outage | J.E.26.08.50692 | C001901801 | Donald Cunningham | St.Catherine | Completed | Load_256618 | Twickenham - 210 | 2026-08-27 08:02 | 2026-08-27 08:04 | 2026-08-27 11:31 | 2026-08-27 11:32 | 2026-08-27 12:29 | 2026-08-27 12:38 | 2026-08-27 12:39 | 2026-08-27 12:39 |  |  | Fair | No | Broken service phase corrected using 1 clamp
Outage | J.E.26.08.50698 | C001901795 | Donald Cunningham | St.Catherine | Completed | Load_251822 | Twickenham - 210 | 2026-08-27 08:02 | 2026-08-27 08:04 | 2026-08-27 11:02 | 2026-08-27 11:03 | 2026-08-27 11:23 | 2026-08-27 11:24 | 2026-08-27 11:28 | 2026-08-27 11:28 |  |  | Fair | No | Premises found ok with supply
Non-Outage | J.E.26.08.05674 | C001901809 | Rusean Allen | KSAS | Completed | Load_263506 | Cane River - 310 | 2026-08-27 08:04 | 2026-08-27 08:05 | 2026-08-27 12:15 | 2026-08-27 12:15 | 2026-08-27 12:29 | 2026-08-27 12:30 | 2026-08-27 12:30 | 2026-08-27 12:30 |  |  | Fair | No | Unable to locate, customer phone went unanswered.
Non-Outage | J.E.26.08.54370 | C001901811 | Edward Royal | KSAS | Completed | Load_240820 | Greenwich - 310 | 2026-08-27 08:05 | 2026-08-27 08:07 | 2026-08-27 11:53 | 2026-08-27 11:53 | 2026-08-27 11:53 | 2026-08-27 11:53 | 2026-08-27 11:53 | 2026-08-27 11:53 |  |  | Fair | No | Premises found ok related to outage
Non-Outage | J.E.26.08.36520 | C001901818 | Odeanie Davis | KSAS | Completed | Load_1002859 | Rockfort - 410 | 2026-08-27 08:06 | 2026-08-27 08:09 | 2026-08-27 13:40 | 2026-08-27 13:40 | 2026-08-27 13:40 | 2026-08-27 14:10 | 2026-08-27 13:49 | 2026-08-27 13:49 |  |  | Fair | No | Isolator and wire seen burnt off from transformer to primary, customer left with single phase at location.
Non-Outage | J.E.26.08.36973 | C001901817 | Odeanie Davis | KSAS | Completed | Load_245738 | Up Park Camp - 510 | 2026-08-27 08:06 | 2026-08-27 08:07 | 2026-08-27 11:12 | 2026-08-27 11:13 | 2026-08-27 11:12 | 2026-08-27 11:22 | 2026-08-27 11:23 | 2026-08-27 11:23 |  |  | Fair | No | 107v/116v & 224v at location, no power issues found at time of visit, customer stated that it was a one off occurrence
Non-Outage | J.E.26.08.40778 | C001901816 | Odeanie Davis | KSAS | Completed | Load_260329 | Up Park Camp - 510 | 2026-08-27 08:06 | 2026-08-27 08:07 | 2026-08-27 12:15 | 2026-08-27 12:15 | 2026-08-27 12:15 | 2026-08-27 12:33 | 2026-08-27 12:33 | 2026-08-27 12:33 | LowHangingWires |  | Fair | No | Low hanging wires at location was tensioned 113v after correction
Non-Outage | J.E.26.08.48557 | C001901815 | Odeanie Davis | KSAS | Completed | Load_245842 | Up Park Camp - 510 | 2026-08-27 08:06 | 2026-08-27 08:07 | 2026-08-27 09:19 | 2026-08-27 09:19 | 2026-08-27 09:19 | 2026-08-27 09:21 | 2026-08-27 09:21 | 2026-08-27 09:21 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.49509 | C001901814 | Odeanie Davis | KSAS | Completed | Load_261556 | Rockfort - 410 | 2026-08-27 08:06 | 2026-08-27 08:07 | 2026-08-27 13:06 | 2026-08-27 13:06 | 2026-08-27 13:06 | 2026-08-27 13:21 | 2026-08-27 13:21 | 2026-08-27 13:21 |  |  | Fair | No | 117v/117 & 235v at location, meter found burnt on one side, technician request for meter to be changed, customer’s electrician left them with temporary supply
Non-Outage | J.E.26.08.49954 | C001901812 | Odeanie Davis | KSAS | Completed | Load_261313 | Up Park Camp - 510 | 2026-08-27 08:06 | 2026-08-27 08:07 | 2026-08-27 12:33 | 2026-08-27 12:34 | 2026-08-27 12:33 | 2026-08-27 13:05 | 2026-08-27 13:05 | 2026-08-27 13:05 |  |  | Fair | No | 107v/105v & 212v at secondary line, transformer seen leaking at Mountain View stop light, maintenance team needed,
Non-Outage | J.E.26.08.50101 | C001901813 | Odeanie Davis | KSAS | Completed | Load_245926 | Rockfort - 410 | 2026-08-27 08:06 | 2026-08-27 08:07 | 2026-08-27 11:36 | 2026-08-27 11:37 | 2026-08-27 11:40 | 2026-08-27 12:12 | 2026-08-27 12:13 | 2026-08-27 12:13 |  |  | Fair | No | 118v/115v at arrival, open circuit at secondary corrected, 1 one bolt clamp, 118v/118v and 238v after correction.
Non-Outage | J.E.26.08.50535 | C001901822 | Hopeton Henry | St.Thomas | Completed | Load_267910 | Good Year - 210 | 2026-08-27 08:07 | 2026-08-27 08:11 | 2026-08-27 08:18 | 2026-08-27 10:48 | 2026-08-27 11:19 | 2026-08-27 11:47 | 2026-08-27 11:49 | 2026-08-27 11:49 |  |  | Fair | No | Customer not located, cellphone went unanswered
Non-Outage | J.E.26.08.53022 | C001901821 | Hopeton Henry | St.Thomas | Completed | Load_265771 | Lysson - 410 | 2026-08-27 08:07 | 2026-08-27 08:08 | 2026-08-27 08:18 | 2026-08-27 10:04 | 2026-08-27 10:33 | 2026-08-27 10:46 | 2026-08-27 10:47 | 2026-08-27 10:47 |  |  | Fair | No | Found defective meter , refer to field service for meter change
Outage | J.E.26.08.54106 | C001901820 | Donald Cunningham | St.Catherine | Completed | Load_291660 | Twickenham - 210 | 2026-08-27 08:07 | 2026-08-27 08:08 | 2026-08-27 10:16 | 2026-08-27 10:17 | 2026-08-27 10:58 | 2026-08-27 10:58 | 2026-08-27 11:02 | 2026-08-27 11:02 |  |  | Fair | No | Hex box need to check refer to mr Ellison
Outage | J.E.26.08.54423 | C001901819 | Donald Cunningham | St.Catherine | Completed | Load_576141 | Twickenham - 210 | 2026-08-27 08:07 | 2026-08-27 08:08 | 2026-08-27 09:48 | 2026-08-27 09:48 | 2026-08-27 10:10 | 2026-08-27 10:10 | 2026-08-27 10:15 | 2026-08-27 10:15 |  |  | Fair | No | Premises not located customer not reachable
Outage | J.E.26.08.54414 | C001901823 | Clyde Brown | Clarendon | Completed | Load_257821 | May Pen - 110 | 2026-08-27 08:08 | 2026-08-27 08:10 | 2026-08-27 11:44 | 2026-08-27 11:45 | 2026-08-27 13:15 | 2026-08-27 12:54 | 2026-08-27 13:18 | 2026-08-27 13:18 |  |  | Fair | No | Found supply disconnected for debt.
Non-Outage | J.E.26.08.42303 | C001901824 | Hopeton Henry | St.Thomas | Completed | Load_241706 | Good Year - 110 | 2026-08-27 08:12 | 2026-08-27 08:13 | 2026-08-27 08:18 | 2026-08-27 08:20 | 2026-08-27 09:43 | 2026-08-27 10:03 | 2026-08-27 10:03 | 2026-08-27 10:03 |  |  | Fair | No | Found defective meter , refer to field service for meter change
Non-Outage | J.E.26.08.27076 | C001901837 | Royston Montague |  | Completed |  |  | 2026-08-27 08:13 | 2026-08-27 08:18 | 2026-08-27 08:47 | 2026-08-27 14:36 | 2026-08-27 16:24 | 2026-08-27 16:24 | 2026-08-27 16:24 | 2026-08-27 16:24 | LeaningPole |  | Fair | No | Customer issue is with a leading pole. Please inform maintenance department thanks.
Non-Outage | J.E.26.08.27094 | C001901835 | Royston Montague | St.Catherine | Completed | Load_238030 | Tredegar - 210 | 2026-08-27 08:13 | 2026-08-27 08:18 | 2026-08-27 08:47 | 2026-08-27 14:32 | 2026-08-27 14:32 | 2026-08-27 14:33 | 2026-08-27 14:33 | 2026-08-27 14:33 | LeaningPole |  | Fair | No | Customer confirmed issue is with a leading pole. Please inform maintenance department thanks.
Non-Outage | J.E.26.08.27354 | C001901833 | Royston Montague | St.Catherine | Completed | Load_264063 | Twickenham - 310 | 2026-08-27 08:13 | 2026-08-27 08:19 | 2026-08-27 08:47 | 2026-08-27 08:52 | 2026-08-27 09:52 | 2026-08-27 10:08 | 2026-08-27 10:08 | 2026-08-27 10:08 |  |  | Fair | No | Burn wire at pothead, same corrected, voltage found 116v voltage after job completion are 230v 114v 115v
Non-Outage | J.E.26.08.40939 | C001901832 | Eric Williams | KSAN | Completed | Load_568066 | West Kings House - 410 | 2026-08-27 08:13 | 2026-08-27 08:15 | 2026-08-27 13:27 | 2026-08-27 13:28 | 2026-08-27 13:27 | 2026-08-27 15:23 | 2026-08-27 15:23 | 2026-08-27 15:23 |  |  | Fair | No | Found bank of three 100 kva with the jumper bear copper making contact with the transformer case, also casing ground burnt from system neutral. corrected with 3ft 4/0 insulated copper, 1 - one bolt clamp and 1 - 2/0 - 4/0 ampack. Customer power supply restored.
Non-Outage | J.E.26.08.41786 | C001901834 | Eric Williams | KSAN | Completed | Load_259966 | Washington Blvd - 410 | 2026-08-27 08:13 | 2026-08-27 11:40 | 2026-08-28 08:35 | 2026-08-28 08:36 | 2026-08-28 09:36 | 2026-08-28 11:14 | 2026-08-28 11:24 | 2026-08-28 11:24 |  | Y | Fair | No | 4 wire open secondary broken cause by bushing, major bushing done and wire cut and splice using 3 onebolt clamps, more bushing required refer to maintenance department,( open secondary is behind the plaza).
Non-Outage | J.E.26.08.49011 | C001901839 | Dwain Samuels | Westmoreland | Completed | Load_247031 | Paradise - 110 | 2026-08-27 08:15 | 2026-08-27 08:21 | 2026-08-27 08:47 | 2026-08-27 11:12 | 2026-08-27 11:52 | 2026-08-27 12:19 | 2026-08-27 12:21 | 2026-08-27 12:21 | BrokenWire |  | Fair | No | Connect 3 wire meter use 3 one bolt clamp. Voltage check 113-112 225
Non-Outage | J.E.26.08.42741 | C001901843 | Milton Charlton | KSAS | Completed | Load_568745 | Up Park Camp - 410 | 2026-08-27 08:16 | 2026-08-27 08:17 | 2026-08-27 09:35 | 2026-08-27 09:36 | 2026-08-27 12:05 | 2026-08-27 10:10 | 2026-08-27 12:11 | 2026-08-27 12:11 |  |  | Fair | No | Found okay upon arrival. Customer has an internal problem.
Outage | J.E.26.08.52281 | C001901841 | Derrick Dawkins | St.James | Completed | Load_251236 | Bogue - 610 | 2026-08-27 08:16 | 2026-08-27 08:17 | 2026-08-27 08:58 | 2026-08-27 11:48 | 2026-08-27 11:48 | 2026-08-27 11:48 | 2026-08-27 11:48 | 2026-08-27 11:48 |  |  | Fair | No | Found junction fuse blown due to vegetation 10 amp replaced 10 amp junction fuse at pole #065864
Outage | J.E.26.08.54355 | C001901842 | Derrick Dawkins | St.James | Completed | Load_253875 | Bogue - 610 | 2026-08-27 08:16 | 2026-08-27 08:17 | 2026-08-27 11:49 | 2026-08-27 11:50 | 2026-08-27 12:19 | 2026-08-27 12:57 | 2026-08-27 12:57 | 2026-08-27 12:57 |  |  | Fair | No | Found 1 span secondary cut down due to illegal connection and 25 kva transformer fuse blown 2 amp splice and retention used 1#2/0 free form and 1 pg clamp
Non-Outage | J.E.26.08.48980 | C001901846 | Locksley Allen | St.Mary | Completed | Load_352448 | Oracabessa - 210 | 2026-08-27 08:20 | 2026-08-27 08:21 | 2026-08-27 12:34 | 2026-08-27 12:57 | 2026-08-27 12:58 | 2026-08-27 13:02 | 2026-08-27 13:01 | 2026-08-27 13:01 |  |  | Fair | No | JPS corrected the problem from two nights ago. Customer needs to get rid of the wasp nest at the meter
Non-Outage | J.E.26.08.51718 | C001901849 | Locksley Allen | St.Mary | Completed | Load_262727 | Oracabessa - 110 | 2026-08-27 08:20 | 2026-08-27 08:21 | 2026-08-27 11:54 | 2026-08-27 11:55 | 2026-08-27 11:54 | 2026-08-27 12:04 | 2026-08-27 12:01 | 2026-08-27 12:01 |  |  | Fair | No | Every customer on this street is having a low voltage problem.Please refer to emergency
Non-Outage | J.E.26.08.52781 | C001901847 | Locksley Allen | St.Mary | Completed | Load_351415 | Oracabessa - 210 | 2026-08-27 08:20 | 2026-08-27 08:21 | 2026-08-27 12:31 | 2026-08-27 12:31 | 2026-08-27 12:31 | 2026-08-27 12:34 | 2026-08-27 12:33 | 2026-08-27 12:33 |  |  | Fair | No | This is a Rami section. Gate lock please refer to emergency
Non-Outage | J.E.26.08.54296 | C001901851 | Locksley Allen | St.Mary | Completed | Load_268034 | Highgate -110 | 2026-08-27 08:20 | 2026-08-27 08:21 | 2026-08-27 09:24 | 2026-08-28 10:03 | 2026-08-28 10:03 | 2026-08-28 10:17 | 2026-08-28 10:17 | 2026-08-28 10:17 |  |  | Fair | No | Meter found blank. Service wire found disconnected at pole. Connect service wire at pole. Voltage at meter socket phase to phase 221vPhase to neutral 106&107. Meter left working okay
Outage | J.E.26.08.43853 | C001901848 | Rayon Foster | Hanover | Completed | Load_246952 | Orange Bay - 310 | 2026-08-27 08:20 | 2026-08-27 08:21 | 2026-08-27 11:47 | 2026-08-27 11:48 | 2026-08-27 12:44 | 2026-08-27 01:01 | 2026-08-27 13:07 | 2026-08-27 13:07 |  |  | Fair | No | When call customer she said her power was restored after a power outage on Monday of this week
Outage | J.E.26.08.54277 | C001901854 | Horace Malcolm | St.James | Completed | Load_242510 | Queens Drive - 710 | 2026-08-27 08:23 | 2026-08-27 08:29 | 2026-08-27 11:40 | 2026-08-27 18:50 | 2026-08-27 19:27 | 2026-08-27 19:28 | 2026-08-27 19:28 | 2026-08-27 19:28 |  |  | Fair | No | Can’t locate meter or customer call unavailable to customer
Non-Outage | J.E.26.08.25697 | C001901861 | Royston Montague | St.Catherine | Completed | Load_270093 | Rhodens Pen - 210 | 2026-08-27 08:26 | 2026-08-27 08:29 | 2026-08-27 08:47 | 2026-08-28 08:26 | 2026-08-28 08:46 | 2026-08-28 08:46 | 2026-08-28 08:47 | 2026-08-28 08:47 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.08.26144 | C001901859 | Royston Montague | St.Catherine | Completed | Load_262399 | Tredegar - 510 | 2026-08-27 08:26 | 2026-08-27 08:29 | 2026-08-27 08:47 | 2026-08-27 12:28 | 2026-08-27 13:15 | 2026-08-27 13:45 | 2026-08-27 13:46 | 2026-08-27 13:46 |  |  | Fair | No | Faulty neutral joint at customer take off point. Same corrected. Voltage found 126v. 99v voltage after job completion are 225v 112v 112v
Non-Outage | J.E.26.08.26422 | C001901858 | Royston Montague | St.Catherine | Completed | Load_257696 | Tredegar - 510 | 2026-08-27 08:26 | 2026-08-27 08:29 | 2026-08-27 08:47 | 2026-08-27 13:48 | 2026-08-27 14:19 | 2026-08-27 14:21 | 2026-08-27 14:21 | 2026-08-27 14:21 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.08.26607 | C001901856 | Royston Montague | St.Catherine | Completed | Load_252394 | Tredegar - 310 | 2026-08-27 08:26 | 2026-08-27 08:29 | 2026-08-27 08:47 | 2026-08-27 11:04 | 2026-08-27 12:23 | 2026-08-27 12:26 | 2026-08-27 12:26 | 2026-08-27 12:26 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.08.26836 | C001901855 | Royston Montague | St.Catherine | Completed | Load_1001062 | Tredegar - 210 | 2026-08-27 08:26 | 2026-08-27 08:29 | 2026-08-27 08:47 | 2026-08-27 14:23 | 2026-08-27 14:23 | 2026-08-27 14:31 | 2026-08-27 14:32 | 2026-08-27 14:32 |  |  | Fair | No | Rami system in area. Please assign this job to the relevant team thanks.
Outage | J.E.26.08.54454 | C001901860 | Roxroy Needham | St.Ann | Completed | Load_240030 | Cardiff Hall - 310 | 2026-08-27 08:26 | 2026-08-27 08:28 | 2026-08-27 08:49 | 2026-08-27 08:57 | 2026-08-27 10:07 | 2026-08-27 10:28 | 2026-08-27 10:31 | 2026-08-27 10:31 |  | Y | Fair | No | Replace a 10 amps junction fuse at pole
Non-Outage | J.E.26.08.22452 | C001901876 | Royston Montague | St.Catherine | Completed | Load_294019 | Rhodens Pen - 310 | 2026-08-27 08:27 | 2026-08-27 08:50 | 2026-08-27 08:56 | 2026-08-28 14:15 | 2026-08-28 15:30 | 2026-08-28 15:30 | 2026-08-28 15:30 | 2026-08-28 15:30 |  |  | Fair | No | Rami system in area. Please assign this job to the relevant team thanks.
Non-Outage | J.E.26.08.22461 | C001901872 | Royston Montague | St.Catherine | Completed | Load_294019 | Rhodens Pen - 310 | 2026-08-27 08:27 | 2026-08-27 08:50 | 2026-08-27 08:56 | 2026-08-28 15:31 | 2026-08-28 15:30 | 2026-08-28 15:31 | 2026-08-28 15:31 | 2026-08-28 15:31 |  |  | Fair | No | Rami system in area. Please assign this job to the relevant team thanks.
Non-Outage | J.E.26.08.23635 | C001901868 | Royston Montague | St.Catherine | Completed | Load_263389 | Twickenham - 310 | 2026-08-27 08:27 | 2026-08-27 08:29 | 2026-08-27 08:47 | 2026-08-28 12:18 | 2026-08-28 13:30 | 2026-08-28 13:37 | 2026-08-28 13:37 | 2026-08-28 13:37 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.08.23648 | C001901867 | Royston Montague | St.Catherine | Completed | Load_263389 | Twickenham - 310 | 2026-08-27 08:27 | 2026-08-27 08:29 | 2026-08-27 08:47 | 2026-08-27 10:15 | 2026-08-27 10:26 | 2026-08-27 10:27 | 2026-08-27 10:27 | 2026-08-27 10:27 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.08.23849 | C001901866 | Royston Montague | St.Catherine | Completed | Load_264063 | Twickenham - 310 | 2026-08-27 08:27 | 2026-08-27 08:29 | 2026-08-27 08:47 | 2026-08-27 10:13 | 2026-08-27 10:12 | 2026-08-27 10:13 | 2026-08-27 10:13 | 2026-08-27 10:13 |  |  | Fair | No | Burn wire at pothead. Voltage found 115v voltage after job completion are 230v 115v 114v
Non-Outage | J.E.26.08.24817 | C001901864 | Royston Montague | St.Catherine | Completed | Load_262371 | Twickenham - 410 | 2026-08-27 08:27 | 2026-08-27 08:29 | 2026-08-27 08:47 | 2026-08-28 10:08 | 2026-08-28 11:47 | 2026-08-28 12:16 | 2026-08-28 12:16 | 2026-08-28 12:16 |  |  | Fair | No | Faulty joints at pothead. Same corrected. Voltage found 110v voltage after job completion are 222v 110v 110v
Non-Outage | J.E.26.08.25505 | C001901863 | Royston Montague | St.Catherine | Completed | Load_263389 | Twickenham - 310 | 2026-08-27 08:27 | 2026-08-27 08:29 | 2026-08-27 08:47 | 2026-08-28 13:38 | 2026-08-28 14:13 | 2026-08-28 14:13 | 2026-08-28 14:14 | 2026-08-28 14:14 |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.08.19160 | C001901878 | Royston Montague | St.Catherine | Completed | Load_251791 | Tredegar - 310 | 2026-08-27 08:28 | 2026-08-27 08:50 | 2026-08-27 08:56 | 2026-08-27 10:29 | 2026-08-27 10:55 | 2026-08-27 11:02 | 2026-08-27 11:03 | 2026-08-27 11:03 |  |  | Fair | No | Faulty meter. Only one side working. Same needs to change. Please inform field service department thank. Voltage 225v 112v 111v
Non-Outage | J.E.26.08.19483 | C001901879 | Royston Montague | St.Catherine | Completed | Load_288766 | Rhodens Pen - 210 | 2026-08-27 08:28 | 2026-08-27 08:50 | 2026-08-27 08:56 | 2026-08-28 12:17 | 2026-08-28 12:17 | 2026-08-28 12:17 | 2026-08-28 12:17 | 2026-08-28 12:17 |  |  | Fair | No | Rami system in area, please assign this job to the relevant team thanks.
Outage | J.E.26.08.54450 | C001901880 | Omar Harris | St.Ann | Completed | Load_252102 | Roaring River - 210 | 2026-08-27 08:28 | 2026-08-27 08:29 | 2026-08-27 10:17 | 2026-08-27 10:18 | 2026-08-27 10:55 | 2026-08-27 11:07 | 2026-08-27 11:09 | 2026-08-27 11:09 |  |  | Fair | No | Replace 1 15A junction fuse
Outage | J.E.26.08.54463 | C001901885 | Horace Malcolm | St.James | Completed | Load_268465 | Queens Drive - 710 | 2026-08-27 08:35 | 2026-08-27 08:36 | 2026-08-27 10:22 | 2026-08-27 10:23 | 2026-08-27 11:15 | 2026-08-27 11:40 | 2026-08-27 11:40 | 2026-08-27 11:40 | BrokenWire |  | Fair | No | Check and found no service at customer premises required 70ft #6 triplex wire and 6claps not sufficient wire to carry out work
Non-Outage | J.E.26.08.48394 | C001901890 | Odaine Johnson | Clarendon | Completed | Load_264303 | Parnassus - 310 | 2026-08-27 08:42 | 2026-08-27 08:49 | 2026-08-27 13:06 | 2026-08-27 13:07 | 2026-08-27 13:06 | 2026-08-27 13:07 | 2026-08-27 13:08 | 2026-08-27 13:08 |  |  | Fair | No | Premises found okay voltage reading 115/114/230 volts
Non-Outage | J.E.26.08.49195 | C001901900 | Odaine Johnson | Clarendon | Completed | Load_250405 | May Pen - 110 | 2026-08-27 08:42 | 2026-08-27 08:48 | 2026-08-27 09:50 | 2026-08-27 12:59 | 2026-08-27 12:59 | 2026-08-27 12:59 | 2026-08-27 13:00 | 2026-08-27 13:00 | LowHangingWires |  | Fair | No | Premises found okay customer stated that the issue was resolved
Non-Outage | J.E.26.08.49238 | C001901891 | Neville Spencer | Clarendon | Completed | Load_261931 | May Pen - 110 | 2026-08-27 08:42 | 2026-08-27 15:29 | 2026-08-27 20:47 | 2026-08-27 20:47 | 2026-08-27 20:47 | 2026-08-27 20:47 | 2026-08-27 20:48 | 2026-08-27 20:48 |  |  | Fair | No | Need daylight visit road bad.
Non-Outage | J.E.26.08.49304 | C001901892 | Odaine Johnson | Clarendon | Completed | Load_240026 | May Pen - 110 | 2026-08-27 08:42 | 2026-08-27 08:49 | 2026-08-27 10:10 | 2026-08-27 10:11 | 2026-08-27 10:12 | 2026-08-27 10:12 | 2026-08-27 10:13 | 2026-08-27 10:13 |  |  | Fair | No | Contacted customer and customer stated that the issue was resolved already
Non-Outage | J.E.26.08.52349 | C001901895 | Odaine Johnson | Clarendon | Completed | Load_266881 | May Pen - 110 | 2026-08-27 08:42 | 2026-08-27 08:48 | 2026-08-27 13:15 | 2026-08-27 13:15 | 2026-08-27 13:25 | 2026-08-27 13:26 | 2026-08-27 13:26 | 2026-08-27 13:26 |  |  | Fair | No | Corroded phase found at pole remade connection using 1 one bolt clamp voltage reading 116/114/230 volts
Non-Outage | J.E.26.08.30436 | C001901903 | Odaine Johnson | Clarendon | Completed | Load_248820 | May Pen - 110 | 2026-08-27 08:43 | 2026-08-27 08:48 | 2026-08-27 09:50 | 2026-08-28 10:49 | 2026-08-28 11:45 | 2026-08-28 12:09 | 2026-08-28 12:11 | 2026-08-28 12:11 |  |  | Fair | No | Please refer this issue to a emergency team the area is experiencing low voltage Voltage reading A109 B111 AB220-219
Non-Outage | J.E.26.08.35966 | C001901907 | Odaine Johnson | Clarendon | Completed | Load_254501 | Parnassus - 310 | 2026-08-27 08:44 | 2026-08-27 08:48 | 2026-08-27 09:49 | 2026-08-27 15:46 | 2026-08-27 15:46 | 2026-08-27 15:46 | 2026-08-27 15:47 | 2026-08-27 15:47 |  |  | Fair | No | Please refer this issue to a emergency team
Non-Outage | J.E.26.08.48394 | C001901908 | Odaine Johnson | Clarendon | Completed | Load_264303 | Parnassus - 310 | 2026-08-27 08:44 | 2026-08-27 08:48 | 2026-08-27 09:49 | 2026-08-27 13:01 | 2026-08-27 13:03 | 2026-08-27 13:03 | 2026-08-27 13:04 | 2026-08-27 13:04 |  |  | Fair | No | Premises found okay voltage reading 115/114/230 volts
Non-Outage | J.E.26.08.48423 | C001901909 | Odaine Johnson | Clarendon | Completed | Load_240026 | May Pen - 110 | 2026-08-27 08:44 | 2026-08-27 08:48 | 2026-08-27 09:49 | 2026-08-27 10:24 | 2026-08-27 10:40 | 2026-08-27 10:41 | 2026-08-27 10:42 | 2026-08-27 10:42 |  |  | Fair | No | Contacted customer and customer stated that they did not make any report
Non-Outage | J.E.26.08.49304 | C001901911 | Odaine Johnson | Clarendon | Completed | Load_240026 | May Pen - 110 | 2026-08-27 08:44 | 2026-08-27 08:48 | 2026-08-27 09:49 | 2026-08-27 10:13 | 2026-08-27 10:13 | 2026-08-27 10:14 | 2026-08-27 10:14 | 2026-08-27 10:14 |  |  | Fair | No | Contacted customer and customer stated that the issue was resolved already
Non-Outage | J.E.26.08.52349 | C001901910 | Odaine Johnson | Clarendon | Completed | Load_266881 | May Pen - 110 | 2026-08-27 08:44 | 2026-08-27 08:48 | 2026-08-27 09:49 | 2026-08-27 10:19 | 2026-08-27 10:18 | 2026-08-27 10:19 | 2026-08-27 10:20 | 2026-08-27 10:20 |  |  | Fair | No | This area is have low voltage because of illegal activity going on
Non-Outage | J.E.26.08.43463 | C001901916 | Derrick Dawkins |  | Completed |  |  | 2026-08-27 08:47 | 2026-08-27 08:48 | 2026-08-27 13:49 | 2026-08-27 13:49 | 2026-08-27 13:49 | 2026-08-27 13:54 | 2026-08-27 13:50 | 2026-08-27 13:50 |  |  | Fair | No | 110/116=227 customer has internal problem
Non-Outage | J.E.26.08.43522 | C001901914 | Derrick Dawkins |  | Completed |  |  | 2026-08-27 08:47 | 2026-08-27 08:48 | 2026-08-27 13:40 | 2026-08-27 13:40 | 2026-08-27 13:45 | 2026-08-27 13:48 | 2026-08-27 13:48 | 2026-08-27 13:48 |  |  | Fair | No | Voltage 110/116=227 customer has internal problem
Non-Outage | J.E.26.08.54466 | C001901924 | Richard Nicholas |  | Completed |  |  | 2026-08-27 08:50 | 2026-08-27 08:53 | 2026-08-27 10:46 | 2026-08-27 10:46 | 2026-08-27 11:15 | 2026-08-27 12:22 | 2026-08-27 12:26 | 2026-08-27 12:26 | LowHangingWires |  | Fair | No | Truck come in contact with low hanging service wire as a result service neutral broken.same was splice and retention.4 clamp and 6ft #6 insulated was used to complete the repair.voltage reading 116,117 and 233v.
Non-Outage | J.E.26.08.17192 | C001901926 | Hartley Chin |  | Completed |  |  | 2026-08-27 08:51 | 2026-08-27 15:26 | 2026-08-27 19:22 | 2026-08-27 19:23 | 2026-08-27 20:04 | 2026-08-27 20:11 | 2026-08-27 20:14 | 2026-08-27 20:14 | BrokenPole |  | Fair | No | Ref to maintenance!!!! Broken 30 ft pole with open secondary circuit , pole is broken in the middle and is leaning against customers fence post … pole requires immediate attention!!! Note : customer supply is okay …
Non-Outage | J.E.26.08.27992 | C001901927 | Jermaine Williams |  | Completed |  |  | 2026-08-27 08:51 | 2026-08-27 08:53 | 2026-08-27 13:07 | 2026-08-27 13:08 | 2026-08-27 13:31 | 2026-08-27 13:31 | 2026-08-27 13:34 | 2026-08-27 13:34 | BrokenPole |  | Fair | No | Defective 40’ class 4 three phase primary. Pole 90% rotten, refer to Devon brown.
Outage | J.E.26.08.54448 | C001901942 | Christopher Edwards | KSAN | Completed | Load_240495 | Constant Spring - 210 | 2026-08-27 08:55 | 2026-08-27 10:05 | 2026-08-27 15:33 | 2026-08-27 15:34 | 2026-08-27 15:56 | 2026-08-27 16:56 | 2026-08-27 16:57 | 2026-08-27 16:57 |  |  | Fair | No | Splice and retention broken #6 service wire Using 30ft #6 service wire 3 one bolt clamps
Outage | J.E.26.08.54445 | C001901966 | Rusean Allen | KSAS | Completed | Load_238170 | Rockfort - 210 | 2026-08-27 08:59 | 2026-08-27 09:05 | 2026-08-27 09:11 | 2026-08-27 10:51 | 2026-08-27 10:50 | 2026-08-27 10:51 | 2026-08-27 10:51 | 2026-08-27 10:51 |  |  | Fair | No | Premises okay
Outage | J.E.26.08.54637 | C001901977 | Edward Royal | KSAS | Completed | Load_251084 | Hunts Bay - 810 | 2026-08-27 09:02 | 2026-08-27 09:05 | 2026-08-27 11:54 | 2026-08-27 11:54 | 2026-08-27 12:44 | 2026-08-27 12:44 | 2026-08-27 12:45 | 2026-08-27 12:45 | Fire |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.08.32520 | C001901979 | Rusean Allen | KSAS | Completed | Load_253227 | Rockfort - 210 | 2026-08-27 09:03 | 2026-08-27 09:04 | 2026-08-27 12:41 | 2026-08-27 12:42 | 2026-08-27 12:58 | 2026-08-27 12:58 | 2026-08-27 12:58 | 2026-08-27 12:58 |  |  | Fair | No | More info needed, customer phone went unanswered.
Non-Outage | J.E.26.07.09431 | C001902017 | Junior Scarlett | St.James | Completed | Load_269225 | Queens Drive - 710 | 2026-08-27 09:15 | 2026-08-27 09:20 | 2026-08-27 10:24 | 2026-08-27 14:19 | 2026-08-27 14:39 | 2026-08-27 15:11 | 2026-08-27 15:11 | 2026-08-27 15:11 |  |  | Fair | No | Chancing and found okVoltage found 115v 115 v 230v
Non-Outage | J.E.26.07.09493 | C001902012 | Junior Scarlett | St.James | Completed | Load_257909 | Queens Drive - 710 | 2026-08-27 09:15 | 2026-08-27 09:20 | 2026-08-27 10:24 | 2026-08-27 13:08 | 2026-08-27 13:39 | 2026-08-27 14:08 | 2026-08-27 14:10 | 2026-08-27 14:10 |  |  | Fair | No | Check and fund okVoltage found 115v 115v 230v
Non-Outage | J.E.26.07.12276 | C001902014 | Junior Scarlett | St.James | Completed | Load_265992 | Queens Drive - 710 | 2026-08-27 09:15 | 2026-08-27 09:20 | 2026-08-27 10:24 | 2026-08-28 10:28 | 2026-08-28 10:58 | 2026-08-28 11:59 | 2026-08-28 11:59 | 2026-08-28 11:59 |  |  | Fair | No | Install two clampVoltage found 114v 114v 228vVoltage leave 114v 114v 228v
Non-Outage | J.E.26.07.12468 | C001902013 | Junior Scarlett | St.James | Completed | Load_239445 | Queens Drive - 710 | 2026-08-27 09:15 | 2026-08-27 09:20 | 2026-08-27 10:24 | 2026-08-28 12:30 | 2026-08-28 12:50 | 2026-08-28 13:07 | 2026-08-28 13:08 | 2026-08-28 13:08 |  |  | Fair | No | Unable to locate Voltage from transformer 115v 115v 230v
Non-Outage | J.E.26.07.15495 | C001902016 | Junior Scarlett | St.James | Completed | Load_243259 | Queens Drive - 710 | 2026-08-27 09:15 | 2026-08-27 09:20 | 2026-08-27 10:24 | 2026-08-28 09:26 | 2026-08-28 09:47 | 2026-08-28 10:21 | 2026-08-28 10:24 | 2026-08-28 10:24 |  |  | Fair | No | Check and found okVoltage found 115v 114v 228v12345
Non-Outage | J.E.26.08.24850 | C001902032 | Junior Scarlett | St.James | Completed | Load_259498 | Bogue - 310 | 2026-08-27 09:19 | 2026-08-27 09:20 | 2026-08-27 10:24 | 2026-08-27 10:26 | 2026-08-27 10:58 | 2026-08-27 11:46 | 2026-08-27 11:46 | 2026-08-27 11:46 |  |  | Fair | No | Install two clampVoltage found 114v 113v 226
Non-Outage | J.E.26.08.24858 | C001902031 | Junior Scarlett | St.James | Completed | Load_259498 | Bogue - 310 | 2026-08-27 09:19 | 2026-08-27 09:20 | 2026-08-27 10:24 | 2026-08-27 11:50 | 2026-08-27 12:02 | 2026-08-27 12:51 | 2026-08-27 12:51 | 2026-08-27 12:51 |  |  | Fair | No | Install two clampVoltage found 114v 115v 226vVoltage leave 114v 114v 228v
Outage | J.E.26.08.19030 | C001902038 | Elvis Trowers | KSAS | Completed | Load_579129 | Duhaney - 310 | 2026-08-27 09:21 | 2026-08-27 09:22 | 2026-08-27 09:28 | 2026-08-27 09:33 | 2026-08-27 10:08 | 2026-08-27 10:00 | 2026-08-27 10:11 | 2026-08-27 10:11 |  |  | Fair | No | Customer complaining about the a tree in his back growing up in open wire secondary line need bushing. On the premises of #12 swift avenue.
Non-Outage | J.E.26.08.36545 | C001902055 | Roemello Brown | Trelawny | Completed | Load_251586 | Greenwood - 110 | 2026-08-27 09:26 | 2026-08-27 09:28 | 2026-08-27 12:35 | 2026-08-27 13:15 | 2026-08-27 13:37 | 2026-08-27 13:40 | 2026-08-27 13:42 | 2026-08-27 13:42 |  |  | Fair | No | Customer meter socket is defective i informed the customer to get an private electrician to have the meter socket change Voltage found 114/114/228Voltage leave 114/114/228
Non-Outage | J.E.26.08.49919 | C001902051 | Roemello Brown | Trelawny | Completed | Load_246009 | Greenwood - 110 | 2026-08-27 09:26 | 2026-08-27 09:28 | 2026-08-27 14:58 | 2026-08-27 14:58 | 2026-08-27 14:58 | 2026-08-27 14:58 | 2026-08-27 14:59 | 2026-08-27 14:59 |  |  | Fair | No | This call is not my call please transfer to st.James team please
Non-Outage | J.E.26.08.54708 | C001902052 | Richard Nicholas |  | Completed |  |  | 2026-08-27 09:26 | 2026-08-27 09:28 | 2026-08-27 12:27 | 2026-08-27 12:28 | 2026-08-27 13:20 | 2026-08-27 13:44 | 2026-08-27 13:47 | 2026-08-27 13:47 |  |  | Fair | No | Replaced blown 15amp junctions fuse at 3phase T-off to the premises and bank of 100 +50 x2 kva transformer,replaced blown 50kva transformer 5amp fuse at the premises and bank.
Non-Outage | J.E.26.08.16180 | C001902063 | Roemello Brown | Trelawny | Completed | Load_261243 | Greenwood - 110 | 2026-08-27 09:27 | 2026-08-27 09:28 | 2026-08-28 11:00 | 2026-08-28 11:01 | 2026-08-28 11:58 | 2026-08-28 11:58 | 2026-08-28 12:46 | 2026-08-28 12:46 |  |  | Fair | No | Premises found okay informed customer to get an electrician to check premises Voltage found 114/110/224Voltage leave 114/110/224
Non-Outage | J.E.26.08.23747 | C001902062 | Roemello Brown | Trelawny | Completed | Load_268005 | Greenwood - 110 | 2026-08-27 09:27 | 2026-08-27 09:28 | 2026-08-28 09:16 | 2026-08-28 12:48 | 2026-08-28 13:55 | 2026-08-28 13:55 | 2026-08-28 13:58 | 2026-08-28 13:58 |  |  | Fair | No | Premises found working okay Voltage 114/115/229Voltage leave 114/115/229
Non-Outage | J.E.26.08.24955 | C001902060 | Roemello Brown | Trelawny | Completed | Load_243986 | Greenwood - 110 | 2026-08-27 09:27 | 2026-08-27 09:28 | 2026-08-27 13:51 | 2026-08-27 13:52 | 2026-08-27 14:07 | 2026-08-27 14:07 | 2026-08-27 14:58 | 2026-08-27 14:58 |  |  | Fair | No | Corrosion at pothead have linkets installed Voltage found 115/114/229Voltage leave 114/114/229
Non-Outage | J.E.26.08.25514 | C001902059 | Roemello Brown | Trelawny | Completed | Load_237701 | Greenwood - 110 | 2026-08-27 09:27 | 2026-08-27 09:28 | 2026-08-28 12:47 | 2026-08-28 13:59 | 2026-08-28 14:59 | 2026-08-28 14:59 | 2026-08-28 15:00 | 2026-08-28 15:00 |  |  | Fair | No | Premises found working okay Voltage found 113/112/225Voltage leave 113/112/225
Non-Outage | J.E.26.08.32490 | C001902058 | Roemello Brown | Trelawny | Completed | Load_251599 | Greenwood - 110 | 2026-08-27 09:27 | 2026-08-27 09:28 | 2026-08-27 09:57 | 2026-08-27 10:12 | 2026-08-27 10:33 | 2026-08-27 10:33 | 2026-08-27 11:53 | 2026-08-27 11:53 |  | Y | Fair | No | One leg of the open secondary line drop out of the spoon an kissing up with the flow wire neutral causing low voltage please send emergency team to assist please Voltage found 118/106/224Voltage leave 118/106/224
Non-Outage | J.E.26.08.32773 | C001902057 | Roemello Brown | Trelawny | Completed | Load_251599 | Greenwood - 110 | 2026-08-27 09:27 | 2026-08-27 09:28 | 2026-08-27 09:55 | 2026-08-27 11:53 | 2026-08-27 12:02 | 2026-08-27 12:02 | 2026-08-27 12:02 | 2026-08-27 12:02 |  |  | Fair | No | Duplicate order
Non-Outage | J.E.26.08.35973 | C001902056 | Roemello Brown | Trelawny | Completed | Load_254465 | Greenwood - 110 | 2026-08-27 09:27 | 2026-08-27 09:28 | 2026-08-27 09:51 | 2026-08-27 12:35 | 2026-08-27 12:53 | 2026-08-27 12:53 | 2026-08-27 13:06 | 2026-08-27 13:06 |  |  | Fair | No | Premises found working okay Voltage found 114/113/227Voltage leave 114/113/227
Outage | J.E.26.08.54736 | C001902091 | Delano Gayle | KSAS | Completed | Load_1000995 | Duhaney - 210 | 2026-08-27 09:42 | 2026-08-27 22:45 | 2026-08-27 23:31 | 2026-08-27 23:56 | 2026-08-28 02:27 | 2026-08-28 02:36 | 2026-08-28 02:36 | 2026-08-28 02:36 | BrokenWire |  | Fair | No | Premises not found, area found okay no broken wire seen, hexing system installed in area
Outage | J.E.26.08.54658 | C001902100 | Clyde Brown | Clarendon | Completed | Load_261887 | May Pen - 110 | 2026-08-27 09:43 | 2026-08-27 09:45 | 2026-08-27 10:00 | 2026-08-27 10:00 | 2026-08-27 10:39 | 2026-08-27 10:57 | 2026-08-27 11:21 | 2026-08-27 11:21 |  |  | Fair | No | Blown 3 amps fuse for 25 kva transformer,line patrolled and no fault seen,blown fuse replaced.
Outage | J.E.26.08.54781 | C001902122 | Edward Royal | KSAN | Completed | Load_567705 | Washington Blvd - 310 | 2026-08-27 10:01 | 2026-08-27 13:25 | 2026-08-27 13:32 | 2026-08-27 13:32 | 2026-08-28 00:46 | 2026-08-28 00:47 | 2026-08-28 00:47 | 2026-08-28 00:47 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.54830 | C001902121 | Edward Royal | KSAS | Completed | Load_240820 | Greenwich - 310 | 2026-08-27 10:01 | 2026-08-27 10:04 | 2026-08-27 10:54 | 2026-08-27 10:55 | 2026-08-27 10:54 | 2026-08-27 11:53 | 2026-08-27 11:53 | 2026-08-27 11:53 | Fire |  | Fair | No | Spliced and reconnected secondary neutral using 50ft open number 2 3 single bolt clamp
Non-Outage | J.E.26.08.54861 | C001902141 | Derrick Dawkins |  | Completed |  |  | 2026-08-27 10:16 | 2026-08-27 10:18 | 2026-08-27 13:50 | 2026-08-27 13:50 | 2026-08-27 14:29 | 2026-08-27 14:50 | 2026-08-27 14:50 | 2026-08-27 14:50 |  |  | Fair | No | Planed outage
Outage | J.E.26.08.54814 | C001902140 | Derrick Dawkins | St.James | Completed | Load_269492 | Bogue - 610 | 2026-08-27 10:16 | 2026-08-27 10:18 | 2026-08-27 10:35 | 2026-08-27 11:49 | 2026-08-27 11:49 | 2026-08-27 11:49 | 2026-08-27 11:50 | 2026-08-27 11:50 |  |  | Fair | No | Found junction fuse blown due to vegetation 10 amp replaced 10 amp junction fuse at pole #065864
Outage | J.E.26.08.54858 | C001902139 | Tajay Bernard | Hanover | Completed | Load_253569 | Orange Bay - 310 | 2026-08-27 10:16 | 2026-08-27 15:05 | 2026-08-27 15:16 | 2026-08-27 15:26 | 2026-08-27 15:26 | 2026-08-27 15:28 | 2026-08-27 15:29 | 2026-08-27 15:29 |  |  | Fair | No | This call is related to the emergency outage
Outage | J.E.26.08.54786 | C001902157 | Shawn Medley | St.James | Completed | Load_293052 | Queens Drive - 310 | 2026-08-27 10:20 | 2026-08-27 10:21 | 2026-08-27 10:30 | 2026-08-27 10:39 | 2026-08-27 10:55 | 2026-08-27 11:37 | 2026-08-27 11:37 | 2026-08-27 11:37 | Fire |  | Fair | No | Pole # 0008077 100kva transformer found blown fuse patrol line section refused using 10a fuse supply restored
Outage | J.E.26.08.54817 | C001902158 | Derrick Dawkins | St.James | Completed | Load_253875 | Bogue - 610 | 2026-08-27 10:22 | 2026-08-27 10:24 | 2026-08-27 12:59 | 2026-08-27 13:01 | 2026-08-27 13:00 | 2026-08-27 13:19 | 2026-08-27 13:01 | 2026-08-27 13:01 |  |  | Fair | No | Checked and found ok
Outage | J.E.26.08.54829 | C001902161 | Tajay Bernard | Hanover | Completed | Load_267460 | Orange Bay - 310 | 2026-08-27 10:22 | 2026-08-27 15:05 | 2026-08-27 15:29 | 2026-08-27 15:30 | 2026-08-27 15:29 | 2026-08-27 15:30 | 2026-08-27 15:30 | 2026-08-27 15:30 |  |  | Fair | No | This call is related to the emergency outage
Outage | J.E.26.08.54849 | C001902160 | Derrick Dawkins | St.James | Completed | Load_238926 | Bogue - 610 | 2026-08-27 10:22 | 2026-08-27 10:24 | 2026-08-27 11:12 | 2026-08-27 11:13 | 2026-08-27 11:34 | 2026-08-27 11:46 | 2026-08-27 11:47 | 2026-08-27 11:47 |  |  | Fair | No | Found junction fuse blown due to vegetation 10 amp replaced 10 amp junction fuse at pole #065864
Outage | J.E.26.08.54832 | C001902171 | Dwayne Samuels | Trelawny | Completed | Load_251586 | Greenwood - 110 | 2026-08-27 10:24 | 2026-08-27 10:25 | 2026-08-27 11:02 | 2026-08-27 11:06 | 2026-08-27 12:19 | 2026-08-27 12:54 | 2026-08-27 12:54 | 2026-08-27 12:54 |  |  | Fair | No | Corrosion at pole was the cause of customer single phasing use 1 one bolt clamp at same for repairs voltage found at pothead on arrival 114v/78v voltage left 114v/115v/229v
Outage | J.E.26.08.53974 | C001902175 | Cliton Henry | St.Mary | Completed | Load_264935 | Highgate - 210 | 2026-08-27 10:27 | 2026-08-27 10:28 | 2026-08-27 10:36 | 2026-08-27 10:36 | 2026-08-27 11:48 | 2026-08-27 12:51 | 2026-08-27 12:53 | 2026-08-27 12:53 |  |  | Fair | No | A blown 10 amp junction fuse found at Oxford crossing at pole# 0181724, a blown 10 junction fuse found at Flint St. at pole #0013033 and a blown 2 amp fuse for a 10 kva transformer at pole #0013334 due vines at the transformer location. The vines were remove and supply restored restored using 1- 10 amp fuse at pole #0181724, 1- 5 amp fuse at Flint St. pole #0013033 and 1-3 amp fuse for the 10 kva transformer at pole #0013034. NB. The 2/0 triplex secondary is defective and Ed replacement. Kindly refer to St. Mary Operations for a replacement. The line section also need bushing urgently.
Outage | J.E.26.08.54759 | C001902174 | Cliton Henry | St.Mary | Completed | Load_254414 | Highgate - 210 | 2026-08-27 10:27 | 2026-08-27 10:28 | 2026-08-27 12:54 | 2026-08-27 12:54 | 2026-08-27 13:18 | 2026-08-27 13:50 | 2026-08-27 13:50 | 2026-08-27 13:50 |  |  | Fair | No | Voltages found 99-99/199 volts, Kindly refer to St.Mary Operations for transformer upgrade Or install a transformer an split the circuit.
Outage | J.E.26.08.54984 | C001902185 | Christopher Edwards | KSAN | Completed | Load_579137 | Constant Spring - 210 | 2026-08-27 10:31 | 2026-08-27 10:32 | 2026-08-27 11:21 | 2026-08-27 11:27 | 2026-08-27 11:38 | 2026-08-27 11:56 | 2026-08-27 11:58 | 2026-08-27 11:58 | BrokenWire |  | Fair | No | Remake burnt off phase joint Using (2) one bolt clamps Voltage:115,114,230v
Outage | J.E.26.08.54799 | C001902207 | Kemark Slue | St.Catherine | Completed | Load_253119 | New Michelton - 210 | 2026-08-27 10:40 | 2026-08-27 12:33 | 2026-08-27 13:32 | 2026-08-27 13:33 | 2026-08-27 13:32 | 2026-08-27 14:47 | 2026-08-27 14:56 | 2026-08-27 14:56 |  | Y | Fair | No | Upon arrival at the location the crew discovered that a 15 amps junction fuse for single phase line section was blown resulting from vegetation, clear vegetation from conductor right of way, refuse link and re-energized line section please refer to A. Murray to have vegetation management done on line section.
Non-Outage | J.E.26.08.54827 | C001902208 | Hartley Chin |  | Completed |  |  | 2026-08-27 10:41 | 2026-08-27 15:26 | 2026-08-27 16:37 | 2026-08-27 16:38 | 2026-08-27 16:37 | 2026-08-27 16:38 | 2026-08-27 16:38 | 2026-08-27 16:38 | BrokenWire |  | Fair | No | Wrong parish… St Catherine ..
Outage | J.E.26.08.54859 | C001902217 | Hartley Chin | Clarendon | Completed | Load_264974 | Monymusk - 210 | 2026-08-27 10:42 | 2026-08-27 15:26 | 2026-08-27 16:36 | 2026-08-27 17:56 | 2026-08-27 18:13 | 2026-08-27 18:25 | 2026-08-27 18:25 | 2026-08-27 18:25 | BrokenWire |  | Fair | No | Repair service phase found @ service pole … use 1 clamp …
Outage | J.E.26.08.54930 | C001902219 | Hartley Chin | Clarendon | Completed | Load_245072 | Parnassus - 310 | 2026-08-27 10:43 | 2026-08-27 15:26 | 2026-08-27 15:40 | 2026-08-27 15:40 | 2026-08-27 16:31 | 2026-08-27 16:35 | 2026-08-27 16:36 | 2026-08-27 16:36 |  |  | Fair | No | Planned outage … line is currently isolated due to men conducting work in area …
Outage | J.E.26.08.54968 | C001902223 | Horace Malcolm | St.James | Completed | Load_269145 | Queens Drive - 710 | 2026-08-27 10:45 | 2026-08-27 11:48 | 2026-08-27 12:19 | 2026-08-27 12:20 | 2026-08-27 12:19 | 2026-08-27 12:41 | 2026-08-27 12:41 | 2026-08-27 12:41 |  |  | Fair | No | Unable to locate premises or meter from direction given multiple calls to customer unavailable
Outage | J.E.26.08.55066 | C001902230 | Hartley Chin | Clarendon | Completed | Load_246907 | Monymusk - 210 | 2026-08-27 10:49 | 2026-08-27 15:26 | 2026-08-27 16:36 | 2026-08-27 17:43 | 2026-08-27 17:42 | 2026-08-27 17:49 | 2026-08-27 17:55 | 2026-08-27 17:55 | LeaningPole |  | Fair | No | Ref to maintenance!!! Found rotten 30ft pole in need of immediate attention… pole foot is 100% rotten and is leaning and causing strain to customer stantion … maintenance to repair …
Outage | J.E.26.08.55072 | C001902243 | Eric Williams | KSAN | Completed | Load_265544 | Washington Blvd - 610 | 2026-08-27 10:53 | 2026-08-27 10:54 | 2026-08-27 12:10 | 2026-08-27 12:10 | 2026-08-27 13:12 | 2026-08-27 13:27 | 2026-08-27 13:27 | 2026-08-27 13:27 |  |  | Fair | No | Found wrap joint in middle span of service drop burnt, corrected with 2 - one bolt clamp, voltage readings 118/118/236volt. Customer left with power supply.
Outage | J.E.26.08.55093 | C001902244 | Milton Charlton | KSAN | Completed | Load_255937 | West Kings House - 310 | 2026-08-27 10:53 | 2026-08-27 10:54 | 2026-08-27 11:53 | 2026-08-27 12:13 | 2026-08-27 12:17 | 2026-08-27 12:35 | 2026-08-27 12:59 | 2026-08-27 12:59 |  |  | Fair | No | Found okay upon arrival. Customer has an internal problem. Readings at meter socket 117-117- 234 volts.
Outage | J.E.26.08.55099 | C001902242 | Rusean Allen | KSAS | Completed | Load_239773 | Rockfort - 210 | 2026-08-27 10:53 | 2026-08-27 10:54 | 2026-08-27 12:30 | 2026-08-27 12:31 | 2026-08-27 12:38 | 2026-08-27 12:40 | 2026-08-27 12:41 | 2026-08-27 12:41 |  |  | Fair | No | Meter to be re installed, meter was reported stolen.Refer to field service department.
Outage | J.E.26.08.55057 | C001902255 | Omar Harris | St.Ann | Completed | Load_239038 | Roaring River - 210 | 2026-08-27 10:59 | 2026-08-27 11:00 | 2026-08-27 11:41 | 2026-08-27 11:42 | 2026-08-27 11:53 | 2026-08-27 11:53 | 2026-08-27 11:53 | 2026-08-27 11:53 |  |  | Fair | No
Non-Outage | J.E.26.08.54718 | C001902256 | Roxroy Needham |  | Completed |  |  | 2026-08-27 11:00 | 2026-08-27 11:01 | 2026-08-27 14:01 | 2026-08-27 14:02 | 2026-08-27 14:31 | 2026-08-27 14:31 | 2026-08-27 14:32 | 2026-08-27 14:32 |  |  | Fair | No | Premises found ok customer have internal problem
Outage | J.E.26.08.54646 | C001902257 | Roxroy Needham | St.Ann | Completed | Load_251707 | Cardiff Hall - 210 | 2026-08-27 11:00 | 2026-08-27 11:01 | 2026-08-27 11:23 | 2026-08-27 11:23 | 2026-08-27 13:26 | 2026-08-27 14:00 | 2026-08-27 14:01 | 2026-08-27 14:01 |  |  | Fair | No | Premises found ok customer have internal problem
Non-Outage | J.E.26.08.50052 | C001902259 | Rayon Foster | Hanover | Completed | Load_569907 | Orange Bay - 210 | 2026-08-27 11:01 | 2026-08-27 11:02 | 2026-08-27 11:18 | 2026-08-27 11:19 | 2026-08-27 11:19 | 2026-08-27 11:43 | 2026-08-27 11:44 | 2026-08-27 11:44 |  |  | Fair | No | Found pump in working condition when arrived on location voltage checked at pathead and in main panel (brown/gray)377v (blue/gray)373v (blue/brown)370v. Blue/neutral 215v(brown/neutral 218v (gray/neutral 218v NWC technician was present on location while we where on location and was satisfied with the pump
Outage | J.E.26.08.54106 | C001902297 | Moses Elliston | St.Catherine | Completed | Load_291660 | Twickenham - 210 | 2026-08-27 11:25 | 2026-08-27 11:27 | 2026-08-27 15:28 | 2026-08-27 15:28 | 2026-08-27 15:28 | 2026-08-27 15:20 | 2026-08-27 15:32 | 2026-08-27 15:32 |  |  | Fair | No | Defective collector # 16488779 ,box # 0158 .Customer without light .Refer to P.Francis
Outage | J.E.26.08.42611 | C001902306 | Moses Elliston | St.Catherine | Completed | Load_258468 | Tredegar - 410 | 2026-08-27 11:31 | 2026-08-27 11:32 | 2026-08-27 11:48 | 2026-08-27 11:48 | 2026-08-27 11:48 | 2026-08-27 11:26 | 2026-08-27 11:51 | 2026-08-27 11:51 |  |  | Fair | No | Customer complaining about Street Light that was disconnected due to illegal connections
Outage | J.E.26.08.53551 | C001902326 | Michael Paterson | Westmoreland | Completed | Load_556280 | Paradise - 210 | 2026-08-27 11:40 | 2026-08-27 11:40 | 2026-08-27 13:02 | 2026-08-27 13:02 | 2026-08-27 13:02 | 2026-08-27 13:04 | 2026-08-27 13:05 | 2026-08-27 13:05 |  |  | Fair | No | Found primary conductor broken, splice and retention three span of primary using 30ft #2 and two clamps, supply restored.
Non-Outage | J.E.26.08.32025 | C001902341 | Elvis Trowers | KSAN | Completed | Load_250041 | Constant Spring - 410 | 2026-08-27 11:43 | 2026-08-27 11:44 | 2026-08-27 12:40 | 2026-08-27 13:53 | 2026-08-27 14:37 | 2026-08-27 14:40 | 2026-08-27 14:39 | 2026-08-27 14:39 |  |  | Fair | No | Customer has an internal problem. Readings at meter socket 119-120-240 volts.
Outage | J.E.26.08.54479 | C001902406 | Ryan Richards | Manchester | Completed | Load_240663 | Kendal - 310 | 2026-08-27 12:14 | 2026-08-27 12:16 | 2026-08-27 12:20 | 2026-08-27 12:21 | 2026-08-27 14:00 | 2026-08-27 15:33 | 2026-08-27 15:33 | 2026-08-27 15:33 |  |  | Fair | No | Blown 50 amp junction fuse found line patrol nothing found blown 50 amp junction fuse was replaced all customers are now with supply
Outage | J.E.26.08.54589 | C001902409 | Ryan Richards | Manchester | Completed | Load_248771 | Spur Tree - 310 | 2026-08-27 12:15 | 2026-08-27 12:16 | 2026-08-27 19:00 | 2026-08-27 19:00 | 2026-08-27 20:04 | 2026-08-27 20:28 | 2026-08-27 20:28 | 2026-08-27 20:28 |  |  | Fair | No | Area found ok the area was restored with power by jps maintenance crew
Outage | J.E.26.08.54679 | C001902408 | Ryan Richards | Manchester | Completed | Load_239597 | Spur Tree - 310 | 2026-08-27 12:15 | 2026-08-27 12:16 | 2026-08-27 22:05 | 2026-08-27 22:06 | 2026-08-28 00:39 | 2026-08-28 00:43 | 2026-08-28 00:44 | 2026-08-28 00:44 |  |  | Fair | No | Blown 2 amp fuse found for 10 kva transformer line patrol nothing found fuse was replaced and rejected transformer was isolated from line and retested and also rejected twice transformer suspected to be burnt urgent attention required
Outage | J.E.26.08.54703 | C001902407 | Ryan Richards | Manchester | Completed | Load_302011 | Spur Tree - 310 | 2026-08-27 12:15 | 2026-08-27 12:26 | 2026-08-27 20:28 | 2026-08-27 20:29 | 2026-08-27 21:47 | 2026-08-27 22:05 | 2026-08-27 22:05 | 2026-08-27 22:05 |  |  | Fair | No | Blown 8 amp junction fuse found line patrol nothing found blown fuse was replaced all customers are now with supply
Outage | J.E.26.08.55207 | C001902431 | Hartley Chin | St.Catherine | Completed | Load_241929 | Rhodens Pen - 310 | 2026-08-27 12:29 | 2026-08-27 15:26 | 2026-08-27 16:36 | 2026-08-27 16:41 | 2026-08-27 16:52 | 2026-08-27 16:52 | 2026-08-27 16:54 | 2026-08-27 16:54 |  |  | Fair | No | Found okay … customer stated breaker was turnt off ..
Outage | J.E.26.08.55475 | C001902433 | Ricky Hall | St.Catherine | Completed | Load_261379 | Tredegar - 510 | 2026-08-27 12:30 | 2026-08-27 12:32 | 2026-08-27 13:10 | 2026-08-27 13:11 | 2026-08-27 14:33 | 2026-08-27 14:38 | 2026-08-27 14:38 | 2026-08-27 14:38 |  |  | Fair | No | Customer found with supply
Outage | J.E.26.08.55566 | C001902443 | Richard Grant | St.Catherine | Completed | Load_568237 | New Michelton - 310 | 2026-08-27 12:35 | 2026-08-27 15:44 | 2026-08-27 19:41 | 2026-08-27 19:41 | 2026-08-27 20:32 | 2026-08-27 20:57 | 2026-08-27 20:58 | 2026-08-27 20:58 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.49146 | C001902448 | Moses Elliston |  | Completed | Load_568488 | Tredegar - 210 | 2026-08-27 12:38 | 2026-08-27 12:42 | 2026-08-28 09:46 | 2026-08-28 09:46 | 2026-08-28 09:46 | 2026-08-28 09:30 | 2026-08-28 09:47 | 2026-08-28 09:47 |  |  | Fair | No | Premises not located,no answer from cell.
Outage | J.E.26.08.55626 | C001902468 | Milton Charlton | KSAN | Completed | Load_269886 | Hope - 410 | 2026-08-27 12:55 | 2026-08-27 13:01 | 2026-08-27 13:43 | 2026-08-27 13:44 | 2026-08-27 15:31 | 2026-08-27 14:50 | 2026-08-27 15:33 | 2026-08-27 15:33 |  |  | Fair | No | Reconnect customer meter #2462609 that was disconnected.
Non-Outage | J.E.26.08.55630 | C001902470 | Fitzroy Turner |  | Completed |  |  | 2026-08-27 12:59 | 2026-08-27 16:57 | 2026-08-27 22:20 | 2026-08-27 22:20 | 2026-08-27 22:20 | 2026-08-27 22:20 | 2026-08-27 22:20 | 2026-08-27 22:20 | Fire |  | Fair | No | Customer supply restored
Outage | J.E.26.08.55624 | C001902475 | Fitzroy Turner | KSAN | Completed | Load_258426 | Washington Blvd - 310 | 2026-08-27 13:04 | 2026-08-27 16:57 | 2026-08-27 17:37 | 2026-08-27 17:38 | 2026-08-27 17:40 | 2026-08-27 17:47 | 2026-08-27 17:47 | 2026-08-27 17:47 |  |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.08.55271 | C001902478 | Tyrese Williams | St.Ann | Completed | Load_243889 | Cardiff Hall - 310 | 2026-08-27 13:09 | 2026-08-27 13:10 | 2026-08-27 13:18 | 2026-08-27 13:39 | 2026-08-27 14:13 | 2026-08-27 14:15 | 2026-08-27 14:15 | 2026-08-27 14:15 |  |  | Fair | No | Premises found ok customer breaker was off
Outage | J.E.26.08.55707 | C001902477 | Tyrese Williams | St.Ann | Completed | Load_240030 | Cardiff Hall - 310 | 2026-08-27 13:09 | 2026-08-27 13:10 | 2026-08-27 13:18 | 2026-08-27 14:16 | 2026-08-27 14:16 | 2026-08-27 14:16 | 2026-08-27 14:17 | 2026-08-27 14:17 |  |  | Fair | No | Premises found ok customer said the power was restored
Non-Outage | J.E.26.08.55733 | C001902479 | Fitzroy Turner |  | Completed |  |  | 2026-08-27 13:12 | 2026-08-27 16:57 | 2026-08-27 17:57 | 2026-08-27 17:57 | 2026-08-27 18:48 | 2026-08-27 22:18 | 2026-08-27 22:18 | 2026-08-27 22:18 | Fire |  | Fair | No | Customer supply restored
Outage | J.E.26.08.55625 | C001902483 | Dwayne Samuels | Trelawny | Completed | Load_300482 | Greenwood - 110 | 2026-08-27 13:17 | 2026-08-27 13:24 | 2026-08-27 13:43 | 2026-08-27 13:44 | 2026-08-27 14:30 | 2026-08-27 14:38 | 2026-08-27 14:38 | 2026-08-27 14:38 | BrokenWire |  | Fair | No | Customer service wire was torn down by tree splice and retention customer service wire using about 6 ft of number 6 wire and 2 linket for repairs voltage left 113v/117v/230v
Outage | J.E.26.08.54426 | C001902508 | Nickolas Rodriques | Portmore | Completed | Load_570242 | Naggo Head - 610 | 2026-08-27 13:32 | 2026-08-27 15:44 | 2026-08-27 19:06 | 2026-08-27 19:06 | 2026-08-27 19:50 | 2026-08-27 20:05 | 2026-08-27 20:07 | 2026-08-27 20:07 |  |  | Fair | No | Found customer with electricity. The customer confirmed that the power outage was restored.
Outage | J.E.26.08.55735 | C001902509 | Wayne Dillion | St.Elizabeth | Completed | Load_254503 | Maggotty - 210 | 2026-08-27 13:33 | 2026-08-27 13:35 | 2026-08-27 14:13 | 2026-08-27 14:14 | 2026-08-27 15:03 | 2026-08-27 15:15 | 2026-08-27 15:17 | 2026-08-27 15:17 |  |  | Fair | No | Patrol and found clear. Reset one chip type transformer in bank of two size not visible and supply restored okay.
Outage | J.E.26.08.53330 | C001902544 | Omar Harris | St.Ann | Completed | Load_574259 | Roaring River - 210 | 2026-08-27 14:06 | 2026-08-27 14:06 | 2026-08-27 14:18 | 2026-08-27 14:18 | 2026-08-27 14:18 | 2026-08-27 14:18 | 2026-08-27 14:19 | 2026-08-27 14:19 |  |  | Fair | No | Bohnam spring all for directions 8763728941
Outage | J.E.26.08.55922 | C001902551 | Collin Robinson | Portland | Completed | Load_252444 | Port Antonio - 410 | 2026-08-27 14:11 | 2026-08-27 14:12 | 2026-08-27 14:25 | 2026-08-27 14:26 | 2026-08-27 15:50 | 2026-08-27 15:57 | 2026-08-27 15:57 | 2026-08-27 15:57 |  |  | Fair | No | Unable to locate customer for better direction to premises
Outage | J.E.26.08.56011 | C001902550 | Collin Robinson | Portland | Completed | Load_259052 | Port Antonio - 310 | 2026-08-27 14:11 | 2026-08-27 14:12 | 2026-08-27 15:58 | 2026-08-27 15:59 | 2026-08-27 17:26 | 2026-08-27 17:41 | 2026-08-27 17:41 | 2026-08-27 17:41 |  |  | Fair | No | Repair broken #6 twisted wire at pole Use 1 one bolt clamp Voltage reading 118v 117v 235v
Outage | J.E.26.08.54380 | C001902552 | Collin Robinson | Portland | Completed | Load_354926 | Port Antonio - 310 | 2026-08-27 14:12 | 2026-08-27 14:12 | 2026-08-27 17:41 | 2026-08-27 17:41 | 2026-08-27 18:30 | 2026-08-27 18:48 | 2026-08-27 18:48 | 2026-08-27 18:48 |  |  | Fair | No | Remove tree limb from both primary phase and neutral conductor And replace 8 amps junction at pole0014567
Non-Outage | J.E.26.08.50071 | C001902557 | Elvis Trowers | KSAS | Completed | Load_230020 | Hunts Bay - 810 | 2026-08-27 14:16 | 2026-08-28 08:04 | 2026-08-28 08:11 | 2026-08-28 08:12 | 2026-08-28 09:09 | 2026-08-28 08:50 | 2026-08-28 09:13 | 2026-08-28 09:13 |  |  | Fair | No | Customer service wire #2 quad 190 leg burnt off at pole. Repair using one 1- bolt clamp. Readings at pole 114-115-203& 229-2234-233 volts.
Outage | J.E.26.08.53035 | C001902556 | Michael Paterson | Westmoreland | Completed | Load_249930 | Paradise - 110 | 2026-08-27 14:16 | 2026-08-27 14:17 | 2026-08-27 14:31 | 2026-08-27 14:31 | 2026-08-27 15:28 | 2026-08-27 18:08 | 2026-08-27 18:08 | 2026-08-27 18:08 |  |  | Fair | No | Change defective 25 kva transformer at location supply restored voltage reading at transformer 117-117=234 volts
Outage | J.E.26.08.55258 | C001902558 | Moses Elliston | St.Catherine | Completed | Load_302494 | Tredegar - 210 | 2026-08-27 14:17 | 2026-08-27 14:21 | 2026-08-27 23:33 | 2026-08-27 23:34 | 2026-08-27 23:33 | 2026-08-27 17:20 | 2026-08-27 23:38 | 2026-08-27 23:38 |  |  | Fair | No | Burnt PMC main phase lead repaired 120 volts.
Outage | J.E.26.08.56311 | C001902625 | Omar King | St.Ann | Completed | Load_253395 | Cardiff Hall - 310 | 2026-08-27 15:00 | 2026-08-27 15:28 | 2026-08-27 20:01 | 2026-08-27 20:02 | 2026-08-27 20:25 | 2026-08-27 20:29 | 2026-08-27 20:29 | 2026-08-27 20:29 |  |  | Fair | No | The problem has been resolved
Outage | J.E.26.08.54762 | C001902626 | Omar King | St.Ann | Completed | Load_259477 | Cardiff Hall - 310 | 2026-08-27 15:01 | 2026-08-27 15:12 | 2026-08-27 16:14 | 2026-08-27 16:15 | 2026-08-27 19:05 | 2026-08-27 19:24 | 2026-08-27 19:24 | 2026-08-27 19:24 |  |  | Fair | No | Found 8 amp junction fuse blow cause by bird fuse as been replaced area is now with supply Pole # 031160
Outage | J.E.26.08.55882 | C001902629 | Andre Williams | Trelawny | Completed | Load_556059 | Martha Brae - 110 | 2026-08-27 15:02 | 2026-08-27 15:04 | 2026-08-27 15:14 | 2026-08-27 15:15 | 2026-08-27 15:15 | 2026-08-27 15:19 | 2026-08-27 15:20 | 2026-08-27 15:20 |  |  | Fair | No | Report already forwarded to field service premises without, meter panel was burn as as well as 4 wire meter, customer carry out repairs and is now ready for supply. Reffer to field service (bank of 3 transformer also open)
Non-Outage | J.E.26.08.56142 | C001902631 | Andre Williams |  | Completed |  |  | 2026-08-27 15:03 | 2026-08-27 15:04 | 2026-08-27 15:28 | 2026-08-27 15:28 | 2026-08-27 16:22 | 2026-08-27 18:01 | 2026-08-27 18:02 | 2026-08-27 18:02 |  | Y | Fair | No | Isolate 2 phase line at main switch pole leading to goodhope on 2 phase line , retention t span low hanging primary that was touching tree, region on span primary neutral , close two 25 amp trip saver at switch pole area now with supply.
Outage | J.E.26.08.55323 | C001902633 | Andre Williams | Trelawny | Completed | Load_239166 | Duncans - 110 | 2026-08-27 15:03 | 2026-08-27 15:04 | 2026-08-27 18:02 | 2026-08-27 19:05 | 2026-08-27 19:05 | 2026-08-27 19:05 | 2026-08-27 19:14 | 2026-08-27 19:14 |  |  | Fair | No | Premises found ok and with supply power was restored
Outage | J.E.26.08.56017 | C001902632 | Andre Williams | Trelawny | Completed | Load_251599 | Greenwood - 110 | 2026-08-27 15:03 | 2026-08-27 15:04 | 2026-08-27 19:14 | 2026-08-27 19:20 | 2026-08-27 19:31 | 2026-08-27 19:40 | 2026-08-27 20:39 | 2026-08-27 20:39 |  |  | Fair | No | Open 25 kva transformer remount dislodge secondary phase,Change coroded clamp at Jps pole on customer #6 wire voltage at pole and pothead. 117+113=230, customer still have low voltage issue, meter barrel lock reffer to field service customer was also advice to get electrician to check there side
Outage | J.E.26.08.49964 | C001902635 | Richman Whyte | Westmoreland | Completed | Load_253744 | Paradise - 310 | 2026-08-27 15:05 | 2026-08-27 15:16 | 2026-08-27 16:57 | 2026-08-27 16:58 | 2026-08-27 16:57 | 2026-08-27 16:59 | 2026-08-27 16:59 | 2026-08-27 16:59 |  |  | Fair | No | Customer haven’t completed repair unable to connect
Outage | J.E.26.08.56305 | C001902636 | Raymond Lewis | St.Ann | Completed | Load_252427 | Cardiff Hall - 310 | 2026-08-27 15:05 | 2026-08-27 15:07 | 2026-08-27 20:43 | 2026-08-27 20:44 | 2026-08-27 20:43 | 2026-08-27 20:45 | 2026-08-27 20:45 | 2026-08-27 20:45 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.55467 | C001902642 | Horace Malcolm | St.James | Completed | Load_257587 | Queens Drive - 710 | 2026-08-27 15:07 | 2026-08-27 15:18 | 2026-08-27 17:16 | 2026-08-27 17:17 | 2026-08-27 17:33 | 2026-08-27 17:41 | 2026-08-27 17:41 | 2026-08-27 17:41 |  |  | Fair | No | Check and found the area unable to locate premises from the little direction given call to to unavailable
Outage | J.E.26.08.55777 | C001902641 | Horace Malcolm | St.James | Completed | Load_293052 | Queens Drive - 310 | 2026-08-27 15:07 | 2026-08-27 15:18 | 2026-08-27 16:59 | 2026-08-27 16:59 | 2026-08-27 16:59 | 2026-08-27 17:16 | 2026-08-27 17:16 | 2026-08-27 17:16 |  |  | Fair | No | Check and found premises ok voltage 114-116-230
Outage | J.E.26.08.56125 | C001902639 | Horace Malcolm | St.James | Completed | Load_249886 | Queens Drive - 310 | 2026-08-27 15:07 | 2026-08-27 15:18 | 2026-08-27 16:13 | 2026-08-27 16:14 | 2026-08-27 16:13 | 2026-08-27 16:15 | 2026-08-27 16:15 | 2026-08-27 16:15 |  |  | Fair | No | Check and found ok related to previous call job number 56182
Outage | J.E.26.08.56182 | C001902638 | Horace Malcolm | St.James | Completed | Load_293271 | Queens Drive - 310 | 2026-08-27 15:07 | 2026-08-27 15:18 | 2026-08-27 15:40 | 2026-08-27 15:41 | 2026-08-27 16:08 | 2026-08-27 16:13 | 2026-08-27 16:13 | 2026-08-27 16:13 |  |  | Fair | No | Refused one 20amp junction fuses due to broken cable wire
Outage | J.E.26.08.56227 | C001902637 | Horace Malcolm | St.James | Completed | Load_243547 | Queens Drive - 710 | 2026-08-27 15:07 | 2026-08-27 15:18 | 2026-08-27 18:04 | 2026-08-27 18:05 | 2026-08-27 18:29 | 2026-08-27 18:49 | 2026-08-27 18:49 | 2026-08-27 18:49 |  |  | Fair | No | Check and found area ok
Non-Outage | J.E.26.08.54485 | C001902646 | Raymond Lewis | St.Ann | Completed | Load_245539 | Roaring River - 210 | 2026-08-27 15:08 | 2026-08-27 15:09 | 2026-08-27 19:30 | 2026-08-27 19:30 | 2026-08-27 19:30 | 2026-08-27 20:29 | 2026-08-27 20:29 | 2026-08-27 20:29 |  |  | Fair | No | Meter lock unable to complete job for investigation to premises add visit customer to get and electrical
Non-Outage | J.E.26.08.26946 | C001902649 | Raymond Lewis | St.Ann | Completed | Load_263588 | Roaring River - 210 | 2026-08-27 15:09 | 2026-08-27 15:10 | 2026-08-27 17:18 | 2026-08-27 17:19 | 2026-08-27 17:18 | 2026-08-27 17:21 | 2026-08-27 17:21 | 2026-08-27 17:21 |  |  | Fair | No | Premises lock
Non-Outage | J.E.26.08.48466 | C001902648 | Raymond Lewis | St.Ann | Completed | Load_238508 | Roaring River - 210 | 2026-08-27 15:09 | 2026-08-27 18:29 | 2026-08-27 20:30 | 2026-08-27 20:30 | 2026-08-27 20:38 | 2026-08-27 20:40 | 2026-08-27 20:40 | 2026-08-27 20:40 |  |  | Fair | No | Phone not answering
Non-Outage | J.E.26.08.26316 | C001902651 | Raymond Lewis | St.Ann | Completed | Load_239038 | Roaring River - 210 | 2026-08-27 15:10 | 2026-08-27 15:11 | 2026-08-27 16:03 | 2026-08-27 16:04 | 2026-08-27 17:01 | 2026-08-27 17:05 | 2026-08-27 17:05 | 2026-08-27 17:05 |  |  | Fair | No | System problems also a lot of illegal connection
Outage | J.E.26.08.55479 | C001902657 | Javid Vernon | Westmoreland | Completed | Load_249211 | Paradise - 110 | 2026-08-27 15:17 | 2026-08-27 15:18 | 2026-08-27 15:39 | 2026-08-27 15:46 | 2026-08-27 15:57 | 2026-08-27 16:19 | 2026-08-27 16:21 | 2026-08-27 16:21 |  |  | Fair | No | Premises checked and found ok voltage found 116/115/231
Outage | J.E.26.08.55692 | C001902666 | Ryan Richards | Manchester | Completed | Load_556680 | Spur Tree - 310 | 2026-08-27 15:19 | 2026-08-27 15:20 | 2026-08-27 15:55 | 2026-08-27 15:56 | 2026-08-27 16:34 | 2026-08-27 16:41 | 2026-08-27 16:41 | 2026-08-27 16:41 |  |  | Fair | No | Broken pole found in area jps maintenance crew onsite carrying out repairs
Non-Outage | J.E.26.08.54845 | C001902668 | Neville Spencer | Clarendon | Completed | Load_243522 | May Pen - 110 | 2026-08-27 15:20 | 2026-08-27 15:23 | 2026-08-27 17:41 | 2026-08-27 17:45 | 2026-08-27 20:06 | 2026-08-27 20:47 | 2026-08-27 20:47 | 2026-08-27 20:47 |  |  | Fair | No | Remade wrap joints at pothead and secondary on 3, wire service used 2, clamps, 3 2/4 sleeves voltage reading 110 114 225 supply restored.
Outage | J.E.26.08.56312 | C001902667 | Ryan Richards | Manchester | Completed | Load_251668 | Spur Tree - 310 | 2026-08-27 15:20 | 2026-08-27 15:20 | 2026-08-27 16:41 | 2026-08-27 16:42 | 2026-08-27 17:50 | 2026-08-27 18:59 | 2026-08-27 19:00 | 2026-08-27 19:00 |  |  | Fair | Yes | Broken service wire found cause by rubbish truck replace 80ft#6 3 penunion 3 one bolt clamps voltage 112/115/228 volt
Outage | J.E.26.08.55845 | C001902676 | Fitzroy Turner | KSAN | Completed | Load_248819 | Washington Blvd - 310 | 2026-08-27 15:24 | 2026-08-27 15:52 | 2026-08-27 22:18 | 2026-08-27 22:19 | 2026-08-27 22:18 | 2026-08-27 22:19 | 2026-08-27 22:19 | 2026-08-27 22:19 |  |  | Fair | No | Customer supply restored
Outage | J.E.26.08.55856 | C001902675 | Fitzroy Turner | KSAN | Completed | Load_247497 | Washington Blvd - 710 | 2026-08-27 15:24 | 2026-08-27 15:52 | 2026-08-27 17:16 | 2026-08-27 17:17 | 2026-08-27 17:31 | 2026-08-27 17:32 | 2026-08-27 17:33 | 2026-08-27 17:33 |  |  | Fair | No | Electrician carrying out work pothead at premises
Outage | J.E.26.08.56265 | C001902673 | Edward Royal | KSAS | Completed | Load_1002859 | Rockfort - 410 | 2026-08-27 15:24 | 2026-08-27 22:57 | 2026-08-28 07:19 | 2026-08-28 07:19 | 2026-08-28 07:19 | 2026-08-28 07:50 | 2026-08-28 07:50 | 2026-08-28 07:50 | BrokenWire |  | Fair | No | Reconnected primary jumper from switch top to. Primary line and refuse 20A junction fuse pole #0067715
Outage | J.E.26.08.56369 | C001902674 | Fitzroy Turner | KSAS | Completed | Load_255198 | Hunts Bay - 810 | 2026-08-27 15:24 | 2026-08-27 15:52 | 2026-08-27 17:54 | 2026-08-27 17:54 | 2026-08-27 17:55 | 2026-08-27 17:55 | 2026-08-27 17:56 | 2026-08-27 17:56 |  |  | Fair | No | Customer have internal problems
Outage | J.E.26.08.55355 | C001902679 | Romaine Roberts | St.Mary | Completed | Load_269318 | Annotto Bay - 310 | 2026-08-27 15:28 | 2026-08-28 09:16 | 2026-08-28 13:36 | 2026-08-28 13:37 | 2026-08-28 14:43 | 2026-08-28 14:43 | 2026-08-28 14:52 | 2026-08-28 14:52 |  |  | Fair | No | 2 wire service Corrosion at customer pothead clean and remake joints 114
Outage | J.E.26.08.55998 | C001902678 | Raymond Carr | St.Mary | Completed | Load_246394 | Oracabessa - 110 | 2026-08-27 15:28 | 2026-08-27 15:43 | 2026-08-27 15:54 | 2026-08-27 15:54 | 2026-08-27 16:46 | 2026-08-27 16:28 | 2026-08-27 17:03 | 2026-08-27 17:03 | BrokenWire |  | Fair | No | 25 kva transformer found tripped at pole number 0013256, caused by a motor truck. Sagging conductors were separated, and supply was restored.
Outage | J.E.26.08.56123 | C001902677 | Evan Spaulding | St.Mary | Completed | Load_294640 | Highgate -110 | 2026-08-27 15:28 | 2026-08-28 16:22 | 2026-08-28 17:01 | 2026-08-28 17:02 | 2026-08-28 17:01 | 2026-08-28 17:02 | 2026-08-28 17:03 | 2026-08-28 17:03 |  |  | Fair | No | There was a plan outage in the area yesterday,power was restored.
Outage | J.E.26.08.55639 | C001902698 | Tajay Bernard | Hanover | Completed | Load_246605 | Orange Bay - 210 | 2026-08-27 15:31 | 2026-08-27 15:32 | 2026-08-27 17:33 | 2026-08-27 17:33 | 2026-08-27 19:53 | 2026-08-27 20:19 | 2026-08-27 20:20 | 2026-08-27 20:20 |  |  | Fair | No | Premises check and found okay Voltage found 113/113/186/226/227/237Customer stated that voltage was fluctuating
Outage | J.E.26.08.55954 | C001902699 | Kenroy Dale | Manchester | Completed | Load_263696 | Kendal - 210 | 2026-08-27 15:31 | 2026-08-27 15:32 | 2026-08-27 16:24 | 2026-08-27 16:25 | 2026-08-27 17:50 | 2026-08-27 18:35 | 2026-08-27 18:38 | 2026-08-27 18:38 |  |  | Fair | No | Blown 5 amp fuse and Burn out fuse barrel found in banker 3, fuse barrel and blow fuse was replace and area now with supply
Outage | J.E.26.08.55266 | C001902700 | Kenroy Dale | Manchester | Completed | Load_303028 | Kendal - 210 | 2026-08-27 15:32 | 2026-08-27 15:33 | 2026-08-27 18:38 | 2026-08-27 18:38 | 2026-08-27 19:17 | 2026-08-27 20:15 | 2026-08-27 20:18 | 2026-08-27 20:18 |  |  | Fair | No | Blown 3 amp transformer fuse found for 25 kva transformer line patrol one span of secondary neutral found broken conductor was splice and retention blown fuse was replace and area now with supply
Non-Outage | J.E.26.08.54749 | C001902723 | Christopher West | St.Catherine | Completed | Load_256983 | Rhodens Pen - 310 | 2026-08-27 15:42 | 2026-08-27 16:03 | 2026-08-27 20:10 | 2026-08-27 20:10 | 2026-08-27 21:13 | 2026-08-27 21:13 | 2026-08-27 21:13 | 2026-08-27 21:13 |  |  | Fair | No | Premises closed.
Outage | J.E.26.08.55936 | C001902738 | Richard Grant | St.Catherine | Completed | Load_266860 | New Michelton - 310 | 2026-08-27 15:44 | 2026-08-27 15:45 | 2026-08-27 16:25 | 2026-08-27 16:26 | 2026-08-27 17:22 | 2026-08-27 18:08 | 2026-08-27 18:08 | 2026-08-27 18:08 |  |  | Fair | No | 10amps fuse and 2amps fuse found blown for single phase primary and 25kva transformer, respectively, caused by lizard contact. 10amps fuse replaced with 15amps fuse, 2 amps fuse replaced with same and supply restored. Area left okay
Outage | J.E.26.08.56495 | C001902739 | Raymond Lewis | St.Ann | Completed | Load_242320 | Upper White River - 210 | 2026-08-27 15:44 | 2026-08-27 15:45 | 2026-08-27 17:26 | 2026-08-27 17:27 | 2026-08-27 17:27 | 2026-08-27 17:29 | 2026-08-27 17:30 | 2026-08-27 17:30 |  |  | Fair | No | Premises disconnected
Non-Outage | J.E.26.08.49144 | C001902742 | Raheem Ricketts | Manchester | Completed | Load_242270 | Spur Tree - 210 | 2026-08-27 15:45 | 2026-08-27 15:52 | 2026-08-27 16:00 | 2026-08-27 16:14 | 2026-08-27 17:09 | 2026-08-27 17:18 | 2026-08-27 17:18 | 2026-08-27 17:18 |  |  | Fair | No | Check and found customer experiencing one leg remake joint an customer service wire an change 3,clamps on customer pothead
Outage | J.E.26.08.56025 | C001902740 | Nickolas Rodriques | St.Catherine | Completed | Load_262410 | Twickenham - 210 | 2026-08-27 15:45 | 2026-08-27 15:46 | 2026-08-27 16:18 | 2026-08-27 16:19 | 2026-08-27 16:49 | 2026-08-27 17:42 | 2026-08-27 17:54 | 2026-08-27 17:54 |  |  | Fair | No | Power restored. Found area with electricity.
Outage | J.E.26.08.55191 | C001902743 | Javid Vernon | Westmoreland | Completed | Load_241020 | Paradise - 210 | 2026-08-27 15:46 | 2026-08-27 15:46 | 2026-08-27 16:29 | 2026-08-27 16:30 | 2026-08-27 16:29 | 2026-08-27 16:33 | 2026-08-27 16:33 | 2026-08-27 16:33 |  |  | Fair | No | Unable to locate customer and premises phone calls to customer number went unanswered and no directions were given
Outage | J.E.26.08.55522 | C001902744 | Hartley Chin | Clarendon | Completed | Load_242606 | Monymusk - 210 | 2026-08-27 15:46 | 2026-08-27 15:50 | 2026-08-27 16:36 | 2026-08-27 19:22 | 2026-08-27 19:22 | 2026-08-27 19:22 | 2026-08-27 19:22 | 2026-08-27 19:22 |  |  | Fair | No | Contacted customer… was told that issue was resolved…
Outage | J.E.26.08.56003 | C001902766 | Raheem Ricketts | Manchester | Completed | Load_257441 | Spur Tree - 210 | 2026-08-27 15:51 | 2026-08-27 16:01 | 2026-08-27 16:05 | 2026-08-27 18:59 | 2026-08-27 20:15 | 2026-08-27 20:17 | 2026-08-27 20:17 | 2026-08-27 20:17 |  |  | Fair | No | Change customer neutral clamp at pole voltage left 110,110 220
Outage | J.E.26.08.56582 | C001902776 | Fitzroy Turner | KSAS | Completed | Load_251628 | Three Miles - 410 | 2026-08-27 15:52 | 2026-08-27 15:54 | 2026-08-27 16:36 | 2026-08-27 16:36 | 2026-08-27 17:04 | 2026-08-27 17:08 | 2026-08-27 17:14 | 2026-08-27 17:14 |  |  | Fair | No | Found three phases primary line found one fuse blown replaced one 30amps fuse supply restored to the areas no fault found
Outage | J.E.26.08.56533 | C001902777 | Christopher Edwards | KSAN | Completed | Load_262176 | Constant Spring - 410 | 2026-08-27 15:54 | 2026-08-27 15:56 | 2026-08-27 16:57 | 2026-08-27 16:58 | 2026-08-27 17:48 | 2026-08-27 18:13 | 2026-08-27 18:15 | 2026-08-27 18:15 |  |  | Fair | No | Check and found okSupply is at the premises
Outage | J.E.26.08.55991 | C001902778 | Milton Charlton | KSAN | Completed | Load_259437 | Constant Spring - 210 | 2026-08-27 15:56 | 2026-08-27 15:58 | 2026-08-27 16:08 | 2026-08-27 16:58 | 2026-08-27 17:40 | 2026-08-27 18:05 | 2026-08-27 17:41 | 2026-08-27 17:41 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.56113 | C001902779 | Milton Charlton | KSAS | Completed | Load_557433 | Up Park Camp - 410 | 2026-08-27 15:56 | 2026-08-27 15:58 | 2026-08-27 16:07 | 2026-08-27 16:48 | 2026-08-27 16:56 | 2026-08-27 16:55 | 2026-08-27 16:57 | 2026-08-27 16:57 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.56275 | C001902780 | Milton Charlton | KSAN | Completed | Load_249234 | Constant Spring - 410 | 2026-08-27 15:56 | 2026-08-27 15:58 | 2026-08-27 16:57 | 2026-08-27 17:44 | 2026-08-27 19:48 | 2026-08-27 19:20 | 2026-08-27 19:50 | 2026-08-27 19:50 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.56647 | C001902801 | Christopher West | St.Catherine | Completed | Load_270157 | Rhodens Pen - 210 | 2026-08-27 16:08 | 2026-08-27 16:12 | 2026-08-27 16:38 | 2026-08-27 16:39 | 2026-08-27 18:20 | 2026-08-27 20:10 | 2026-08-27 20:10 | 2026-08-27 20:10 | Fire |  | Fair | No | A 50kva transformer was de-energized at pole#0114513, used 6 clamps, 6’#2AA to splice & jumper out bad spots in the secondary, transformer was re-energized, area now ok.
Outage | J.E.26.08.56264 | C001902802 | Derrick Grubb | St.Thomas | Completed | Load_577167 | Good Year - 110 | 2026-08-27 16:10 | 2026-08-27 16:12 | 2026-08-27 18:01 | 2026-08-27 18:01 | 2026-08-27 19:25 | 2026-08-27 19:35 | 2026-08-27 19:35 | 2026-08-27 19:35 |  |  | Fair | No | Premises close. No meter was seen in customer meter socket. Customer was contacted before going to the premises. However, upon arrival, several calls to customer phone went unanswered.
Outage | J.E.26.08.56330 | C001902804 | Moses Elliston | St.Catherine | Completed | Load_557300 | Tredegar - 410 | 2026-08-27 16:11 | 2026-08-27 16:12 | 2026-08-28 10:50 | 2026-08-28 10:50 | 2026-08-28 10:50 | 2026-08-28 10:50 | 2026-08-28 10:51 | 2026-08-28 10:51 |  |  | Fair | No | Not located ,no answer from cell
Outage | J.E.26.08.56586 | C001902803 | Moses Elliston | St.Catherine | Completed | Load_241292 | Tredegar - 210 | 2026-08-27 16:11 | 2026-08-27 16:12 | 2026-08-28 16:55 | 2026-08-28 16:56 | 2026-08-28 16:55 | 2026-08-28 16:42 | 2026-08-28 16:56 | 2026-08-28 16:56 |  |  | EarthMovement | No | Credit added to prepaid account.
Outage | J.E.26.08.56638 | C001902810 | Antony Levy | KSAS | Completed | Load_242388 | Duhaney - 310 | 2026-08-27 16:15 | 2026-08-27 16:55 | 2026-08-27 17:35 | 2026-08-27 17:36 | 2026-08-27 19:38 | 2026-08-27 20:42 | 2026-08-27 21:19 | 2026-08-27 21:19 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.56669 | C001902826 | Richman Whyte | Westmoreland | Completed | Load_261909 | Paradise - 310 | 2026-08-27 16:42 | 2026-08-28 07:26 | 2026-08-28 11:57 | 2026-08-28 11:57 | 2026-08-28 11:57 | 2026-08-28 11:57 | 2026-08-28 11:59 | 2026-08-28 11:59 |  |  | Fair | No | Run and connect 50ft #6 triplex service wire use 6pg clamp voltage 113 113 226
Non-Outage | J.E.26.08.54402 | C001902830 | Raheem Ricketts |  | Completed |  |  | 2026-08-27 16:43 | 2026-08-27 16:43 | 2026-08-27 18:57 | 2026-08-27 18:58 | 2026-08-27 18:57 | 2026-08-27 18:58 | 2026-08-27 18:58 | 2026-08-27 18:58 |  |  | Fair | No | Check and found okay customer says report was made long ago
Non-Outage | J.E.26.08.56750 | C001902837 | Javid Vernon | Westmoreland | Completed | Load_292603 | Paradise - 210 | 2026-08-27 16:50 | 2026-08-27 16:51 | 2026-08-27 16:59 | 2026-08-27 16:59 | 2026-08-27 17:40 | 2026-08-27 18:03 | 2026-08-27 18:03 | 2026-08-27 18:03 |  |  | Fair | No | Unable to reconnect customer service wire due to defective meter socket and pothead customer was advised
Outage | J.E.26.08.55829 | C001902845 | Richman Whyte | Westmoreland | Completed | Load_255234 | Paradise - 310 | 2026-08-27 17:05 | 2026-08-27 17:06 | 2026-08-27 17:48 | 2026-08-27 19:06 | 2026-08-27 20:08 | 2026-08-27 20:56 | 2026-08-27 21:06 | 2026-08-27 21:06 |  |  | Fair | No | Replace twenty five amp junction fuse
Outage | J.E.26.08.56968 | C001902853 | Antony Levy | KSAN | Completed | Load_257856 | Washington Blvd - 410 | 2026-08-27 17:14 | 2026-08-27 17:15 | 2026-08-27 21:19 | 2026-08-27 21:19 | 2026-08-27 22:33 | 2026-08-27 22:34 | 2026-08-27 22:35 | 2026-08-27 22:35 |  |  | Fair | No | Premises closed customer states it’s a new connections and they we try to be there tomaro.
Non-Outage | J.E.26.08.55132 | C001902863 | Swon Miller |  | Completed |  |  | 2026-08-27 17:23 | 2026-08-27 17:24 | 2026-08-27 17:34 | 2026-08-27 17:37 | 2026-08-27 18:15 | 2026-08-25 06:40 | 2026-08-27 18:51 | 2026-08-27 18:51 |  |  | Fair | No | Check and found okay voltage found 118/118/237 voltage left 118/118/237
Outage | J.E.26.08.56367 | C001902862 | Swon Miller | St.James | Completed | Load_556950 | Bogue - 310 | 2026-08-27 17:23 | 2026-08-27 17:24 | 2026-08-27 22:09 | 2026-08-27 22:09 | 2026-08-27 22:39 | 2026-08-26 10:45 | 2026-08-27 22:45 | 2026-08-27 22:45 |  |  | Fair | No | Check and found premises locked customer states he would not be home until tomorrow between seven and five
Outage | J.E.26.08.56487 | C001902860 | Swon Miller | St.James | Completed | Load_269651 | Bogue - 310 | 2026-08-27 17:23 | 2026-08-27 17:24 | 2026-08-27 18:51 | 2026-08-27 18:51 | 2026-08-27 19:06 | 2026-08-18 07:22 | 2026-08-27 19:24 | 2026-08-27 19:24 |  |  | Fair | No | Check and found okay voltage found 115/114/230 voltage left 115/114/230
Outage | J.E.26.08.56714 | C001902861 | Swon Miller | St.James | Completed | Load_556251 | Bogue - 610 | 2026-08-27 17:23 | 2026-08-27 17:24 | 2026-08-27 20:43 | 2026-08-27 20:43 | 2026-08-27 21:32 | 2026-08-19 10:05 | 2026-08-27 22:09 | 2026-08-27 22:09 |  |  | Fair | No | Found customer single phasing please refer to field service voltage found 116 voltage left 116
Outage | J.E.26.08.56962 | C001902865 | Raheem Ricketts | St.Elizabeth | Completed | Load_292968 | Maggotty - 110 | 2026-08-27 17:26 | 2026-08-27 17:26 | 2026-08-27 20:17 | 2026-08-27 20:18 | 2026-08-27 20:17 | 2026-08-27 20:20 | 2026-08-27 20:20 | 2026-08-27 20:20 |  |  | Fair | No | Check and found customer experiencing an internal problem customer says electrician came an change meter socket
Outage | J.E.26.08.57012 | C001902867 | Milton Charlton | KSAN | Completed | Load_578743 | Hope - 410 | 2026-08-27 17:29 | 2026-08-27 17:30 | 2026-08-27 19:50 | 2026-08-27 19:51 | 2026-08-27 19:54 | 2026-08-27 20:05 | 2026-08-27 19:58 | 2026-08-27 19:58 |  |  | Fair | No | Found okay upon arrival. Customer has an internal problem.Readings at meter socket 118-118-237 volts.
Outage | J.E.26.08.56280 | C001902871 | Ryan Richards | Manchester | Completed | Load_293015 | Kendal - 310 | 2026-08-27 17:43 | 2026-08-28 07:25 | 2026-08-28 10:38 | 2026-08-28 10:39 | 2026-08-28 11:52 | 2026-08-28 13:15 | 2026-08-28 13:15 | 2026-08-28 13:15 |  |  | Fair | No | Corroded secondary neutral jumper found which cause customers to experience low voltage remade corroded neutral using one 1. Bolt clamp voltage 118/115/234
Outage | J.E.26.08.57095 | C001902872 | Raheem Ricketts | Manchester | Completed | Load_244178 | Spur Tree - 210 | 2026-08-27 17:48 | 2026-08-27 17:49 | 2026-08-27 18:23 | 2026-08-27 18:24 | 2026-08-27 18:24 | 2026-08-27 18:56 | 2026-08-27 18:56 | 2026-08-27 18:56 | BrokenWire |  | Fair | No | Splice and retention customer service wire using 6,clamps 40ft service wire
Outage | J.E.26.08.56894 | C001902874 | Omar King | St.Ann | Completed | Load_244788 | Cardiff Hall - 310 | 2026-08-27 17:55 | 2026-08-27 18:16 | 2026-08-27 20:30 | 2026-08-27 20:30 | 2026-08-27 20:42 | 2026-08-27 21:02 | 2026-08-27 21:03 | 2026-08-27 21:03 |  |  | Fair | No | Found 10 amp fuse blown cause by illegal connection.the fuse has been replaced
Outage | J.E.26.08.57120 | C001902878 | Swon Miller | St.James | Completed | Load_301740 | Bogue - 310 | 2026-08-27 18:07 | 2026-08-27 18:08 | 2026-08-27 19:24 | 2026-08-27 19:25 | 2026-08-27 19:45 | 2026-08-12 08:30 | 2026-08-27 20:42 | 2026-08-27 20:42 |  |  | Fair | No | Found 1,15 amp junction fuse blown cause by tree limbs cut and remove tree limbs from primary conductor replace 15 amp junction fuse at pole number 009769 voltage found 0.000 voltage left 115/114/230
Outage | J.E.26.08.56623 | C001902879 | Christopher West | St.Catherine | Completed | Load_294008 | Tredegar - 210 | 2026-08-27 18:11 | 2026-08-27 18:20 | 2026-08-27 22:39 | 2026-08-27 22:39 | 2026-08-27 22:39 | 2026-08-27 22:39 | 2026-08-27 22:40 | 2026-08-27 22:40 |  |  | Fair | No | Kindly refer to Mr. Elliston.
Non-Outage | J.E.26.08.49604 | C001902887 | Christopher West | St.Catherine | Completed | Load_556346 | Rhodens Pen - 210 | 2026-08-27 18:20 | 2026-08-27 18:22 | 2026-08-27 22:31 | 2026-08-27 22:31 | 2026-08-27 22:36 | 2026-08-27 22:38 | 2026-08-27 22:39 | 2026-08-27 22:39 |  |  | Fair | No | Kindly refer to the Field Service Department as customer is complaining of high light bill.
Non-Outage | J.E.26.08.54990 | C001902884 | Richard Grant | St.Catherine | Completed | Load_249294 | New Michelton - 310 | 2026-08-27 18:20 | 2026-08-27 18:22 | 2026-08-27 20:58 | 2026-08-27 20:59 | 2026-08-27 22:12 | 2026-08-27 22:14 | 2026-08-27 22:27 | 2026-08-27 22:27 |  |  | Fair | No | Corroded transformer droplead found causing dim and bright on entire circuit , use two one bolt clamps to repair joint, leave a voltage reading of 114,114,228 volts, customer left okay
Outage | J.E.26.08.54106 | C001902890 | Moses Elliston | St.Catherine | Completed | Load_291660 | Twickenham - 210 | 2026-08-27 18:26 | 2026-08-27 18:41 | 2026-08-27 23:40 | 2026-08-27 23:40 | 2026-08-27 23:40 | 2026-08-27 15:20 | 2026-08-27 23:43 | 2026-08-27 23:43 |  |  | Fair | No | Defective collector to be change ,see report # 1721151.(Duplication)
Outage | J.E.26.08.57259 | C001902891 | Raymond Carr | St.Mary | Completed | Load_259870 | Blackstonedge - 110 | 2026-08-27 18:26 | 2026-08-27 18:27 | 2026-08-27 20:23 | 2026-08-27 20:24 | 2026-08-27 21:34 | 2026-08-27 21:30 | 2026-08-27 21:36 | 2026-08-27 21:36 |  |  | Fair | No | Customers reported that supply was restored.
Non-Outage | J.E.26.08.55535 | C001902894 | Raymond Carr | St.Mary | Completed | Load_258469 | Oracabessa - 210 | 2026-08-27 18:29 | 2026-08-27 18:30 | 2026-08-27 18:40 | 2026-08-27 18:41 | 2026-08-27 19:13 | 2026-08-27 19:00 | 2026-08-27 19:15 | 2026-08-27 19:15 |  |  | Fair | No | Due cobweb situation, daytime attention is needed.
Non-Outage | J.E.26.08.56019 | C001902893 | Raymond Carr | St.Mary | Completed | Load_257282 | Oracabessa - 210 | 2026-08-27 18:29 | 2026-08-27 18:31 | 2026-08-27 19:32 | 2026-08-27 19:33 | 2026-08-27 19:57 | 2026-08-27 20:29 | 2026-08-27 20:23 | 2026-08-27 20:23 |  |  | Fair | No | Meter is fitted with a locking band. Unable to check voltage.
Non-Outage | J.E.26.08.56892 | C001902892 | Raymond Carr | St.Mary | Completed | Load_353382 | Oracabessa - 110 | 2026-08-27 18:29 | 2026-08-27 18:30 | 2026-08-27 21:36 | 2026-08-27 21:37 | 2026-08-27 22:20 | 2026-08-27 22:27 | 2026-08-27 22:21 | 2026-08-27 22:21 | BrokenWire |  | Fair | No | Customer couldn’t be contacted.
Outage | J.E.26.08.57277 | C001902895 | Andre Williams | Trelawny | Completed | Load_302605 | Martha Brae - 110 | 2026-08-27 18:38 | 2026-08-27 18:39 | 2026-08-27 19:14 | 2026-08-27 21:16 | 2026-08-27 21:15 | 2026-08-27 21:45 | 2026-08-27 21:46 | 2026-08-27 21:46 |  |  | Fair | No | Splice and retention broken secondary phase , close 25 kva transformer
Outage | J.E.26.08.57214 | C001902897 | Richman Whyte | Westmoreland | Completed | Load_253169 | Paradise - 310 | 2026-08-27 18:39 | 2026-08-27 18:40 | 2026-08-27 19:02 | 2026-08-27 19:03 | 2026-08-27 19:03 | 2026-08-27 19:03 | 2026-08-27 19:05 | 2026-08-27 19:05 |  |  | Fair | No | Open twenty five kva transformer fuse and repair and retention two span open secondary neutral conductor use three one bolt clamps twenty feet #2 open aluminum conductor voltage 114 114 228
Non-Outage | J.E.26.08.50122 | C001902899 | Collin Robinson | Portland | Completed | Load_240878 | Port Antonio - 310 | 2026-08-27 18:46 | 2026-08-27 18:46 | 2026-08-27 19:01 | 2026-08-27 19:01 | 2026-08-27 19:12 | 2026-08-27 19:27 | 2026-08-27 19:27 | 2026-08-27 19:27 |  |  | Fair | No | Premises found okMeter socket voltage reading 119v 120v 239v
Outage | J.E.26.08.57205 | C001902900 | Edward Royal | KSAS | Completed | Load_300831 | Cane River - 410 | 2026-08-27 18:57 | 2026-08-27 22:54 | 2026-08-28 04:09 | 2026-08-28 04:10 | 2026-08-28 04:09 | 2026-08-28 05:21 | 2026-08-28 05:42 | 2026-08-28 05:42 | LeakingTransformer |  | Fair | No | Replaced defective switch and replaced 20A junction fuse.
Outage | J.E.26.08.57438 | C001902903 | Elvis Trowers | KSAN | Completed | Load_266172 | Washington Blvd - 610 | 2026-08-27 18:58 | 2026-08-27 18:58 | 2026-08-27 19:05 | 2026-08-27 19:06 | 2026-08-27 19:31 | 2026-08-27 19:35 | 2026-08-27 19:34 | 2026-08-27 19:34 |  |  | Fair | No | Found okay upon arrival. Customer states matter was resolved.
Outage | J.E.26.08.57580 | C001902907 | Richman Whyte | Westmoreland | Completed | Load_248174 | Paradise - 310 | 2026-08-27 19:11 | 2026-08-27 19:12 | 2026-08-27 21:07 | 2026-08-27 21:08 | 2026-08-27 21:07 | 2026-08-27 21:08 | 2026-08-27 21:09 | 2026-08-27 21:09 |  |  | Fair | No | Replace twenty five amp junction fuse
Non-Outage | J.E.26.08.57587 | C001902908 | Romaine Roberts |  | Completed |  |  | 2026-08-27 19:12 | 2026-08-28 09:16 | 2026-08-28 09:57 | 2026-08-28 09:58 | 2026-08-28 12:19 | 2026-08-28 12:23 | 2026-08-28 12:53 | 2026-08-28 12:53 | Fire |  | Fair | No | Customer service wire was defective and was change by field service crew
Outage | J.E.26.08.57666 | C001902913 | Richman Whyte | Westmoreland | Completed | Load_261456 | Paradise - 310 | 2026-08-27 19:25 | 2026-08-27 19:26 | 2026-08-27 21:09 | 2026-08-27 21:09 | 2026-08-27 21:09 | 2026-08-27 21:09 | 2026-08-27 21:10 | 2026-08-27 21:10 |  |  | Fair | No | Replace twenty five amp junction fuse
Outage | J.E.26.08.57759 | C001902915 | Ryan Richards | Manchester | Completed | Load_240786 | Kendal - 310 | 2026-08-27 19:33 | 2026-08-28 07:26 | 2026-08-28 08:42 | 2026-08-28 08:42 | 2026-08-28 10:29 | 2026-08-28 10:35 | 2026-08-28 10:38 | 2026-08-28 10:38 |  |  | Fair | No | Blown 2 amp fuse found for 25 kva transformer line patrol nothing was found rain and lightning yesterday suspected of the cause blown fuse was replaced all customers are now with supply
Outage | J.E.26.08.57907 | C001902918 | Javid Vernon | Westmoreland | Completed | Load_241469 | Paradise - 210 | 2026-08-27 19:45 | 2026-08-27 19:56 | 2026-08-27 22:05 | 2026-08-27 22:06 | 2026-08-27 22:05 | 2026-08-27 22:11 | 2026-08-27 22:11 | 2026-08-27 22:11 | Fire |  | Fair | No | Related to previous call job #57744
Non-Outage | J.E.26.08.57744 | C001902920 | Javid Vernon | Westmoreland | Completed | Load_241469 | Paradise - 210 | 2026-08-27 19:56 | 2026-08-27 19:57 | 2026-08-27 20:01 | 2026-08-27 20:02 | 2026-08-27 20:50 | 2026-08-27 22:04 | 2026-08-27 22:05 | 2026-08-27 22:05 | LowHangingWires |  | Fair | No | Isolate one 50kva transformer. To splice and retention one pole span of secondary phase and use 80feet #2 conductor and three clamp after reclosing 50kva transformer voltage left 118/117/235
Outage | J.E.26.08.58040 | C001902925 | Javid Vernon | Westmoreland | Completed | Load_257974 | Paradise - 210 | 2026-08-27 20:05 | 2026-08-27 20:06 | 2026-08-27 22:13 | 2026-08-27 22:14 | 2026-08-27 22:36 | 2026-08-27 23:39 | 2026-08-27 23:40 | 2026-08-27 23:40 |  |  | Fair | No | Check and found one 25kva transformer fuse and one 20amp junction blown after reclosing the junction and transformer the transformer fuse blow right after closing it so I remove the lightning arrester and the secondary drop leads and the fuse was closed and hold so I isolate the 25kva transformer and reconnect the transformer drop leads an reclose the transformer and the fuse blow this circuit requires daylight attention to do a detail patrol on secondary circuit to restore customers
Outage | J.E.26.08.57977 | C001902926 | Milton Charlton | KSAN | Completed | Load_261791 | Hope - 510 | 2026-08-27 20:10 | 2026-08-27 20:14 | 2026-08-27 20:23 | 2026-08-27 20:24 | 2026-08-27 21:18 | 2026-08-27 21:15 | 2026-08-27 21:21 | 2026-08-27 21:21 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.57888 | C001902927 | Elvis Trowers | KSAN | Completed | Load_302261 | Constant Spring - 210 | 2026-08-27 20:14 | 2026-08-27 20:15 | 2026-08-27 20:28 | 2026-08-27 20:29 | 2026-08-27 21:46 | 2026-08-27 22:50 | 2026-08-27 21:57 | 2026-08-27 21:57 |  |  | Fair | No | Customer service wire #6 triplex phase and neutral corroded at pothead. Repair using three 1- bolt clamps.
Outage | J.E.26.08.58008 | C001902928 | Christopher West | St.Catherine | Completed | Load_261546 | Rhodens Pen - 410 | 2026-08-27 20:16 | 2026-08-27 20:19 | 2026-08-27 21:14 | 2026-08-27 21:14 | 2026-08-27 22:02 | 2026-08-27 22:27 | 2026-08-27 22:31 | 2026-08-27 22:31 |  |  | Fair | No | Premises closed
Outage | J.E.26.08.57689 | C001902929 | Edward Royal | KSAS | Completed | Load_243276 | Cane River - 610 | 2026-08-27 20:21 | 2026-08-27 22:55 | 2026-08-28 00:49 | 2026-08-28 00:49 | 2026-08-28 00:49 | 2026-08-28 00:50 | 2026-08-28 00:50 | 2026-08-28 00:50 |  |  | Fair | No | Premises not found unable to communicate with customer
Outage | J.E.26.08.57752 | C001902934 | Omar King | St.Ann | Completed | Load_244788 | Cardiff Hall - 310 | 2026-08-27 20:33 | 2026-08-27 20:34 | 2026-08-27 21:03 | 2026-08-27 21:04 | 2026-08-27 21:03 | 2026-08-27 21:05 | 2026-08-27 21:05 | 2026-08-27 21:05 | BrokenWire |  | Fair | No | Found 10 amp fuse blown cause by illegal connection.the fuse has been replaced. Cable wire was found broken
Outage | J.E.26.08.57902 | C001902936 | Raymond Lewis | St.Ann | Completed | Load_242953 | Roaring River - 410 | 2026-08-27 20:35 | 2026-08-27 21:18 | 2026-08-27 22:16 | 2026-08-27 22:16 | 2026-08-27 22:16 | 2026-08-27 22:19 | 2026-08-27 22:19 | 2026-08-27 22:19 |  |  | Fair | No | I call all the numbers and only got two of dem and they say dem ok
Non-Outage | J.E.26.08.57422 | C001902944 | Andre Williams | Trelawny | Completed | Load_262089 | Martha Brae - 210 | 2026-08-27 20:49 | 2026-08-27 20:50 | 2026-08-27 21:46 | 2026-08-27 21:47 | 2026-08-27 22:27 | 2026-08-27 22:43 | 2026-08-27 22:44 | 2026-08-27 22:44 |  |  | Fair | No | Voltage at pothead and meter 117+113=230 customer breaker was trip customer was advice to reset breaker, premises now with full supply
Outage | J.E.26.08.58633 | C001902958 | Michael Paterson | Westmoreland | Completed | Load_292064 | Paradise - 110 | 2026-08-27 21:16 | 2026-08-28 07:35 | 2026-08-28 13:00 | 2026-08-28 13:01 | 2026-08-28 13:22 | 2026-08-28 14:36 | 2026-08-28 14:36 | 2026-08-28 14:36 |  |  | Fair | No | Found 2/0 triplex burnt down, had to isolate 50kva xfmr, splice and retention secondary using 40ft 2/0 triplex and remade joints using :five clamps, supply restored ,voltage reading, 120v, 120v, 240v
Outage | J.E.26.08.58812 | C001902977 | Stephen Taylor | St.Thomas | Completed | Load_239730 | Good Year - 110 | 2026-08-27 22:01 | 2026-08-28 08:16 | 2026-08-28 09:48 | 2026-08-28 09:49 | 2026-08-28 11:49 | 2026-08-28 11:49 | 2026-08-28 11:50 | 2026-08-28 11:50 | BrokenPole |  | Fair | No | Premese found okay over head guy wire is okay
Outage | J.E.26.08.58877 | C001902978 | Delano Gayle | St.Catherine | Completed | Load_267024 | Twickenham - 210 | 2026-08-27 22:17 | 2026-08-27 23:01 | 2026-08-28 02:59 | 2026-08-28 03:00 | 2026-08-28 03:12 | 2026-08-28 03:20 | 2026-08-28 03:20 | 2026-08-28 03:20 |  |  | Fair | No | Premises not found no answer from customer phone
Outage | J.E.26.08.57509 | C001902981 | Lancelot Brown | Hanover | Completed | Load_251941 | Orange Bay - 310 | 2026-08-27 22:24 | 2026-08-28 15:36 | 2026-08-28 15:44 | 2026-08-28 15:48 | 2026-08-28 16:35 | 2026-08-28 16:47 | 2026-08-28 16:47 | 2026-08-28 16:47 |  |  | Rains | No | Found 25kva fuse blown patroll patroll found vegetation contact with lower part of switch led to transformer bushing cut and remove vegetation from transformer replace 1-3amps fuse at 25kva no pole number supply
Non-Outage | J.E.26.08.58186 | C001902982 | Tyrese Williams | St.Ann | Completed | Load_238381 | Cardiff Hall - 210 | 2026-08-27 22:26 | 2026-08-28 08:51 | 2026-08-28 09:11 | 2026-08-28 09:54 | 2026-08-28 10:39 | 2026-08-28 10:54 | 2026-08-28 10:55 | 2026-08-28 10:55 | Fire |  | Fair | No | Premises found ok at the time of visit
Outage | J.E.26.08.59512 | C001902983 | Omar King | St.Ann | Completed | Load_242953 | Roaring River - 410 | 2026-08-27 22:31 | 2026-08-27 22:32 | 2026-08-27 23:20 | 2026-08-27 23:21 | 2026-08-28 03:02 | 2026-08-28 03:02 | 2026-08-28 03:03 | 2026-08-28 03:03 |  |  | Fair | No | Customer said she did not make a report
Outage | J.E.26.08.56623 | C001902985 | Moses Elliston | St.Catherine | Completed | Load_294008 | Tredegar - 210 | 2026-08-27 22:40 | 2026-08-27 22:41 | 2026-08-28 12:21 | 2026-08-28 12:23 | 2026-08-28 12:22 | 2026-08-28 12:22 | 2026-08-28 12:23 | 2026-08-28 12:23 |  |  | Fair | No | Customer said supply ok at premises.
Outage | J.E.26.08.59570 | C001902986 | Omar King | St.Ann | Completed | Load_253395 | Cardiff Hall - 310 | 2026-08-27 22:43 | 2026-08-27 22:46 | 2026-08-27 22:55 | 2026-08-27 22:56 | 2026-08-27 22:55 | 2026-08-27 22:56 | 2026-08-27 22:56 | 2026-08-27 22:56 |  |  | Fair | No | Problem as been resolved
Outage | J.E.26.08.59187 | C001902988 | Edward Royal | KSAS | Completed | Load_238333 | Greenwich - 510 | 2026-08-27 22:56 | 2026-08-27 22:57 | 2026-08-28 00:51 | 2026-08-28 00:51 | 2026-08-28 00:51 | 2026-08-28 00:51 | 2026-08-28 00:52 | 2026-08-28 00:52 | BrokenPole |  | Fair | No | Premises found close
Non-Outage | J.E.26.08.54827 | C001902992 | Delano Gayle |  | Completed |  |  | 2026-08-27 23:00 | 2026-08-27 23:01 | 2026-08-28 03:21 | 2026-08-28 03:21 | 2026-08-28 04:09 | 2026-08-28 04:19 | 2026-08-28 04:19 | 2026-08-28 04:19 | BrokenWire |  | Fair | No | Premises not located no answer from customer phone, no broken wire seen, area found okay
Outage | J.E.26.08.60131 | C001903015 | Edward Royal | KSAS | Completed | Load_267134 | Cane River - 310 | 2026-08-28 00:36 | 2026-08-28 00:37 | 2026-08-28 00:47 | 2026-08-28 00:48 | 2026-08-28 00:48 | 2026-08-28 00:48 | 2026-08-28 00:49 | 2026-08-28 00:49 |  |  | Fair | No | Premises not found unable to communicate with customer
Outage | J.E.26.08.60131 | C001903019 | Edward Royal | KSAS | Completed | Load_267134 | Cane River - 310 | 2026-08-28 00:57 | 2026-08-28 00:59 | 2026-08-28 05:48 | 2026-08-28 05:48 | 2026-08-28 05:48 | 2026-08-28 06:53 | 2026-08-28 06:53 | 2026-08-28 06:53 |  |  | Fair | No | Replaced defective switch and 10a junction fuse
Outage | J.E.26.08.60180 | C001903020 | Rochaine Palmer | KSAN | Completed | Load_240495 | Constant Spring - 210 | 2026-08-28 00:58 | 2026-08-28 15:45 | 2026-08-28 16:25 | 2026-08-28 16:26 | 2026-08-28 18:42 | 2026-08-28 18:43 | 2026-08-28 18:44 | 2026-08-28 18:44 |  |  | Fair | No | There’s power at premises someone from digicel need to go on check premises.
Outage | J.E.26.08.60036 | C001903021 | Delano Gayle | St.Catherine | Completed | Load_302489 | Tredegar - 210 | 2026-08-28 00:59 | 2026-08-28 01:00 | 2026-08-28 01:58 | 2026-08-28 04:19 | 2026-08-28 04:39 | 2026-08-28 05:00 | 2026-08-28 05:00 | 2026-08-28 05:00 |  |  | Fair | No | Blown 5kva transformer no pole number, defective lightening arrester, disconnect lightening arrester and replace 3amps
Outage | J.E.26.08.60226 | C001903023 | Delano Gayle | St.Catherine | Completed | Load_576141 | Twickenham - 210 | 2026-08-28 01:20 | 2026-08-28 01:21 | 2026-08-28 02:37 | 2026-08-28 02:40 | 2026-08-28 02:57 | 2026-08-28 02:58 | 2026-08-28 02:59 | 2026-08-28 02:59 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.60597 | C001903038 | Swon Miller | St.James | Completed | Load_270234 | Queens Drive - 710 | 2026-08-28 05:26 | 2026-08-28 07:02 | 2026-08-28 07:49 | 2026-08-28 07:49 | 2026-08-28 07:49 | 2026-08-28 09:40 | 2026-08-28 09:44 | 2026-08-28 09:44 | Fire |  | Fair | No | Found one span of secondary phase and neutral bang up due to illegal connections open 50 kva transformer to carry out repairs remove illegal connections and retention two span of secondary phase and neutral.close up 50 kva transformer voltage left 117/116/234
Outage | J.E.26.08.57689 | C001903039 | Edward Royal | KSAS | Completed | Load_243276 | Cane River - 610 | 2026-08-28 05:38 | 2026-08-28 05:39 | 2026-08-28 05:45 | 2026-08-28 05:45 | 2026-08-28 05:45 | 2026-08-28 05:47 | 2026-08-28 05:48 | 2026-08-28 05:48 | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Defective 25 kva transformer need be change referred to bucket truck
Outage | J.E.26.08.56105 | C001903077 | Swon Miller | St.James | Completed | Load_293476 | Queens Drive - 310 | 2026-08-28 07:02 | 2026-08-28 07:04 | 2026-08-28 09:47 | 2026-08-28 09:47 | 2026-08-28 10:45 | 2026-08-28 11:03 | 2026-08-28 11:10 | 2026-08-28 11:10 |  |  | Fair | No | Check and found areas okay voltage found 116/117/234 customer states that power supply was restored yesterday about 5:30pm voltage left 116/117/234
Outage | J.E.26.08.56352 | C001903076 | Swon Miller | St.James | Completed | Load_242556 | Queens Drive - 710 | 2026-08-28 07:02 | 2026-08-28 07:04 | 2026-08-28 11:18 | 2026-08-28 11:19 | 2026-08-28 11:21 | 2026-08-28 11:24 | 2026-08-28 11:24 | 2026-08-28 11:24 |  |  | Fair | No | Check and found areas okay customer states that power supply has been restored
Outage | J.E.26.08.56355 | C001903078 | Swon Miller | St.James | Completed | Load_293234 | Queens Drive - 310 | 2026-08-28 07:02 | 2026-08-28 07:04 | 2026-08-28 12:00 | 2026-08-28 12:00 | 2026-08-28 12:00 | 2026-08-19 | 2026-08-28 12:07 | 2026-08-28 12:07 |  |  | Fair | No | Check and found okay customer states that power supply was restored yesterday voltage found 117/115/233 voltage left 117/115/233
Outage | J.E.26.08.59178 | C001903075 | Swon Miller | St.James | Completed | Load_293233 | Queens Drive - 310 | 2026-08-28 07:02 | 2026-08-28 07:04 | 2026-08-28 11:10 | 2026-08-28 11:17 | 2026-08-28 11:17 | 2026-08-28 11:18 | 2026-08-28 11:18 | 2026-08-28 11:18 |  |  | Fair | No | Check and found areas okay customer states that power supply was restored yesterday about 5:30 pm
Outage | J.E.26.08.58445 | C001903081 | Edward Royal | KSAS | Completed | Load_243577 | Cane River - 310 | 2026-08-28 07:20 | 2026-08-28 07:24 | 2026-08-28 09:52 | 2026-08-28 09:53 | 2026-08-28 09:52 | 2026-08-28 09:53 | 2026-08-28 09:53 | 2026-08-28 09:53 |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.08.17183 | C001903083 | Edward Royal | KSAS | Completed | Load_269025 | Hunts Bay - 210 | 2026-08-28 07:22 | 2026-08-28 07:24 | 2026-08-28 10:25 | 2026-08-28 10:26 | 2026-08-28 10:25 | 2026-08-28 10:28 | 2026-08-28 10:28 | 2026-08-28 10:28 | BrokenWire |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.57768 | C001903086 | Richard Nicholas | St.Catherine | Completed | Load_265799 | New Michelton - 210 | 2026-08-28 07:23 | 2026-08-28 07:26 | 2026-08-28 11:59 | 2026-08-28 11:59 | 2026-08-28 13:03 | 2026-08-28 13:28 | 2026-08-28 13:30 | 2026-08-28 13:30 |  |  | Fair | No | Area found ok
Outage | J.E.26.08.58008 | C001903088 | Richard Nicholas | St.Catherine | Completed | Load_261546 | Rhodens Pen - 410 | 2026-08-28 07:23 | 2026-08-28 07:25 | 2026-08-28 10:22 | 2026-08-28 10:23 | 2026-08-28 10:48 | 2026-08-28 11:57 | 2026-08-28 11:59 | 2026-08-28 11:59 |  |  | Fair | No | Replaced 80ft of defective #6 triplex service wire and 6 clamp.voltage reading 118,119 and 237v.
Outage | J.E.26.08.59990 | C001903089 | Richard Nicholas | St.Catherine | Completed | Load_1000361 | Rhodens Pen - 410 | 2026-08-28 07:23 | 2026-08-28 07:25 | 2026-08-28 08:04 | 2026-08-28 08:05 | 2026-08-28 09:59 | 2026-08-28 10:21 | 2026-08-28 10:22 | 2026-08-28 10:22 |  |  | Fair | No | Premises found locked,supply found ok in the area.
Outage | J.E.26.08.60267 | C001903087 | Richman Whyte | St.Elizabeth | Completed | Load_1002136 | Maggotty - 110 | 2026-08-28 07:23 | 2026-08-28 07:26 | 2026-08-28 09:52 | 2026-08-28 09:53 | 2026-08-28 09:52 | 2026-08-28 09:52 | 2026-08-28 09:53 | 2026-08-28 09:53 |  |  | Fair | No | Replace 10 amp junction fuse
Outage | J.E.26.08.60696 | C001903085 | Selvin White | St.Elizabeth | Completed | Load_265728 | Maggotty - 110 | 2026-08-28 07:23 | 2026-08-28 07:24 | 2026-08-28 07:29 | 2026-08-28 07:49 | 2026-08-28 08:04 | 2026-08-28 08:07 | 2026-08-28 08:10 | 2026-08-28 08:10 |  |  | Fair | No | There is no building or meter found at location as customer says building was destroyed during the recent hurricane.No meter or service wires were seen at the location. Please refer to the field service department as customer is saying bills are still being sent for the premises.
Outage | J.E.26.08.60000 | C001903090 | Ricky Hall | St.Catherine | Completed | Load_568158 | Twickenham - 310 | 2026-08-28 07:25 | 2026-08-28 07:27 | 2026-08-28 07:40 | 2026-08-28 08:09 | 2026-08-28 09:28 | 2026-08-28 09:59 | 2026-08-28 10:00 | 2026-08-28 10:00 |  |  | Fair | No | Retention sagging lines replaced blown 8A junction fuse
Outage | J.E.26.08.60716 | C001903091 | Ricky Hall | St.Catherine | Completed | Load_239334 | Tredegar - 410 | 2026-08-28 07:25 | 2026-08-28 07:27 | 2026-08-28 10:01 | 2026-08-28 10:01 | 2026-08-28 10:21 | 2026-08-28 10:21 | 2026-08-28 10:22 | 2026-08-28 10:22 |  |  | Fair | No | Customer unable to add credit plz refer to the relevant team
Non-Outage | J.E.26.08.58983 | C001903092 | Ricky Hall |  | Completed |  |  | 2026-08-28 07:26 | 2026-08-28 07:27 | 2026-08-28 07:39 | 2026-08-28 10:00 | 2026-08-28 10:00 | 2026-08-28 10:00 | 2026-08-28 10:01 | 2026-08-28 10:01 | LowHangingWires |  | Fair | No | Call associated with outage #60000
Non-Outage | J.E.26.08.50668 | C001903095 | Christopher Edwards | KSAN | Completed | Load_267896 | Constant Spring - 310 | 2026-08-28 07:31 | 2026-08-28 07:32 | 2026-08-28 07:47 | 2026-08-28 09:03 | 2026-08-28 09:37 | 2026-08-28 10:14 | 2026-08-28 10:14 | 2026-08-28 10:14 |  |  | Fair | No | Remake burnt neutral joint at poleUsing (1) one bolt clamps Voltage:119,120,240v
Non-Outage | J.E.26.08.57344 | C001903096 | Christopher Edwards | KSAN | Completed | Load_556035 | Constant Spring - 310 | 2026-08-28 07:31 | 2026-08-28 07:32 | 2026-08-28 10:15 | 2026-08-28 10:16 | 2026-08-28 10:28 | 2026-08-28 11:43 | 2026-08-28 11:46 | 2026-08-28 11:46 |  |  | Fair | No | Isolate bank of 2 transformers To remake burnt phase joint joints Using (2) one bolt clamps Voltage :114,115,230v
Outage | J.E.26.08.59051 | C001903093 | Jermaine Williams | Clarendon | Completed | Load_261428 | May Pen - 210 | 2026-08-28 07:31 | 2026-08-28 07:40 | 2026-08-28 07:43 | 2026-08-28 08:11 | 2026-08-28 08:10 | 2026-08-28 08:11 | 2026-08-28 08:11 | 2026-08-28 08:11 |  |  | Fair | No | Area found ok.
Outage | J.E.26.08.60780 | C001903094 | Jermaine Williams | Clarendon | Completed | Load_246426 | May Pen - 210 | 2026-08-28 07:31 | 2026-08-28 07:32 | 2026-08-28 08:12 | 2026-08-28 08:13 | 2026-08-28 09:09 | 2026-08-28 09:09 | 2026-08-28 09:10 | 2026-08-28 09:10 |  | Y | Fair | No | Isolate 50kva xfmr to repair defective 2/0 twisted secondary.
Outage | J.E.26.08.58040 | C001903097 | Michael Paterson | Westmoreland | Completed | Load_257974 | Paradise - 210 | 2026-08-28 07:35 | 2026-08-28 07:36 | 2026-08-28 08:15 | 2026-08-28 08:16 | 2026-08-28 12:35 | 2026-08-28 12:51 | 2026-08-28 12:59 | 2026-08-28 12:59 |  |  | Fair | No | Check and found 25kva xfmr fuse blown, additional checks done, xfmr confirm defective, however, recent work done in a neighboring community has force those illegally connected to migrate unto this circuit, crew is therefore recommending removal of open secondary, replace with 2/0 triplex,. Customer count 11. Illegal connections approximately 100. Also, found 35ft class 6 pole TA construction rotten, leaning, secondary back-back on this pole, please refer to Mr. James Hudson at paradise, urgent attention needed.
Outage | J.E.26.08.60814 | C001903098 | Kenroy Dale | Manchester | Completed | Load_242198 | Kendal - 210 | 2026-08-28 07:36 | 2026-08-28 07:37 | 2026-08-28 10:07 | 2026-08-28 10:09 | 2026-08-28 10:13 | 2026-08-28 15:13 | 2026-08-28 15:20 | 2026-08-28 15:20 |  |  | Fair | No | Open 25 kva transformer to splice and retention one span of secondary both phase and and neutral, Approximately 300 feet of secondary neutral that was missing from a different span was also replaced area was also de-bushed. Transformer re-close and area now with supply
Non-Outage | J.E.26.08.31321 | C001903100 | Milton Charlton | KSAS | Completed | Load_255821 | Up Park Camp - 410 | 2026-08-28 07:39 | 2026-08-28 07:40 | 2026-08-28 11:02 | 2026-08-28 11:02 | 2026-08-28 11:06 | 2026-08-28 11:05 | 2026-08-28 11:09 | 2026-08-28 11:09 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Non-Outage | J.E.26.08.35038 | C001903099 | Christopher Edwards | KSAN | Completed | Load_300723 | Constant Spring - 310 | 2026-08-28 07:39 | 2026-08-28 09:30 | 2026-08-28 11:46 | 2026-08-28 11:52 | 2026-08-28 12:34 | 2026-08-28 12:38 | 2026-08-28 12:39 | 2026-08-28 12:39 |  |  | Fair | No | Customer was contacted and stated that a JPS personnel already came to the location and rectify the issue
Non-Outage | J.E.26.08.49076 | C001903101 | Milton Charlton | KSAS | Completed | Load_238517 | Up Park Camp - 410 | 2026-08-28 07:39 | 2026-08-28 07:40 | 2026-08-28 10:09 | 2026-08-28 10:10 | 2026-08-28 10:58 | 2026-08-28 10:35 | 2026-08-28 11:01 | 2026-08-28 11:01 |  |  | Fair | No | Found okay upon arrival. Customer has an internal problem. Readings at meter socket 116-115-232 volts.
Non-Outage | J.E.26.08.49411 | C001903104 | Milton Charlton | KSAN | Completed | Load_259451 | Hope - 510 | 2026-08-28 07:39 | 2026-08-28 07:40 | 2026-08-28 12:51 | 2026-08-28 12:51 | 2026-08-28 12:51 | 2026-08-28 12:50 | 2026-08-28 12:54 | 2026-08-28 12:54 |  |  | Fair | No | Customer service wire #6 triplex corroded at pothead. Repair using three 1- bolt clamps. Readings at pothead 116-117-232 volts.
Non-Outage | J.E.26.08.49886 | C001903105 | Milton Charlton | KSAN | Completed | Load_255354 | Hope - 510 | 2026-08-28 07:39 | 2026-08-28 07:40 | 2026-08-28 09:44 | 2026-08-28 13:50 | 2026-08-28 15:07 | 2026-08-28 16:05 | 2026-08-28 15:17 | 2026-08-28 15:17 |  |  | Fair | No | Unable to disconnect service because the request order was for the 27-08-2026.
Non-Outage | J.E.26.08.54298 | C001903103 | Milton Charlton | KSAN | Completed | Load_249495 | Hope - 510 | 2026-08-28 07:39 | 2026-08-28 07:40 | 2026-08-28 12:51 | 2026-08-28 12:55 | 2026-08-28 13:36 | 2026-08-28 12:50 | 2026-08-28 13:49 | 2026-08-28 13:49 |  |  | Fair | No | Premises closed . Nobody at home until Sunday or Monday.
Non-Outage | J.E.26.08.54673 | C001903102 | Milton Charlton | KSAS | Completed | Load_243865 | Up Park Camp - 410 | 2026-08-28 07:39 | 2026-08-28 07:40 | 2026-08-28 11:12 | 2026-08-28 11:13 | 2026-08-28 11:31 | 2026-08-28 11:35 | 2026-08-28 11:34 | 2026-08-28 11:34 |  |  | Fair | No | Found okay upon arrival. Customer has an internal problem. Readings at meter socket 120-120-240 volts.
Outage | J.E.26.08.36334 | C001903108 | Marlon Brown | Trelawny | Completed | Load_268005 | Greenwood - 110 | 2026-08-28 07:40 | 2026-08-28 07:41 | 2026-08-28 08:10 | 2026-08-28 08:11 | 2026-08-28 09:49 | 2026-08-28 10:25 | 2026-08-28 10:25 | 2026-08-28 10:25 |  |  | Fair | No | Check and found ok Voltage found 115/116=231Voltage leaving 115/116=231
Outage | J.E.26.08.53363 | C001903106 | Marlon Brown | Trelawny | Completed | Load_245327 | Duncans - 210 | 2026-08-28 07:40 | 2026-08-28 07:41 | 2026-08-28 07:50 | 2026-08-28 07:50 | 2026-08-28 07:50 | 2026-08-28 07:50 | 2026-08-28 07:51 | 2026-08-28 07:51 |  |  | Fair | No | St James call
Outage | J.E.26.08.56035 | C001903107 | Lionel Robinson | Trelawny | Completed | Load_294577 | Duncans - 110 | 2026-08-28 07:40 | 2026-08-28 07:59 | 2026-08-28 10:29 | 2026-08-28 10:29 | 2026-08-28 10:59 | 2026-08-28 11:41 | 2026-08-28 11:41 | 2026-08-28 11:41 |  |  | Fair | No | Replace corroded 1 bolt clamp on neutral
Outage | J.E.26.08.50618 | C001903109 | Lionel Robinson | Trelawny | Completed | Load_302540 | Martha Brae - 210 | 2026-08-28 07:41 | 2026-08-28 07:43 | 2026-08-28 07:56 | 2026-08-28 07:56 | 2026-08-28 08:08 | 2026-08-28 09:41 | 2026-08-28 09:41 | 2026-08-28 09:41 |  |  | Fair | No | Replace 40ft #6 triplex.. voltage readings; 115,114,229 volts
Outage | J.E.26.08.56885 | C001903110 | Lionel Robinson | Trelawny | Completed | Load_255152 | Martha Brae - 110 | 2026-08-28 07:41 | 2026-08-28 07:43 | 2026-08-28 09:54 | 2026-08-28 09:58 | 2026-08-28 10:20 | 2026-08-28 10:20 | 2026-08-28 10:21 | 2026-08-28 10:21 |  |  | Fair | No
Outage | J.E.26.08.54834 | C001903111 | Jermaine Williams | Clarendon | Completed | Load_572148 | Parnassus - 310 | 2026-08-28 07:42 | 2026-08-28 07:42 | 2026-08-28 09:24 | 2026-08-28 09:25 | 2026-08-28 09:25 | 2026-08-28 09:55 | 2026-08-28 10:21 | 2026-08-28 10:21 |  |  | Fair | No | Premises not located.
Outage | J.E.26.08.43731 | C001903116 | Derrick Dawkins | St.James | Completed | Load_237795 | Queens Drive - 710 | 2026-08-28 07:44 | 2026-08-28 23:09 | 2026-08-29 03:09 | 2026-08-29 03:10 | 2026-08-29 03:27 | 2026-08-29 03:32 | 2026-08-29 03:47 | 2026-08-29 03:47 |  |  | Fair | No | Cannot locate customer
Outage | J.E.26.08.55575 | C001903113 | Donald Cunningham | Portmore | Completed | Load_576117 | Naggo Head - 510 | 2026-08-28 07:44 | 2026-08-28 07:46 | 2026-08-28 09:24 | 2026-08-28 09:25 | 2026-08-28 10:18 | 2026-08-28 10:19 | 2026-08-28 10:26 | 2026-08-28 10:26 |  |  | Fair | No | Premises closed customer not reachable
Outage | J.E.26.08.55619 | C001903114 | Donald Cunningham | St.Catherine | Completed | Load_1000333 | Twickenham - 210 | 2026-08-28 07:44 | 2026-08-28 07:46 | 2026-08-28 07:59 | 2026-08-28 08:00 | 2026-08-28 09:17 | 2026-08-28 09:18 | 2026-08-28 09:22 | 2026-08-28 09:22 | BrokenWire |  | Fair | No | Need more info and directions customer not reachable by phone
Outage | J.E.26.08.55681 | C001903118 | Donald Cunningham | St.Catherine | Completed | Load_238151 | Twickenham - 310 | 2026-08-28 07:44 | 2026-08-28 10:17 | 2026-08-28 14:43 | 2026-08-28 14:44 | 2026-08-28 15:00 | 2026-08-28 15:01 | 2026-08-28 15:02 | 2026-08-28 15:02 |  |  | Fair | No | Customer stated she didn’t make a report
Outage | J.E.26.08.57542 | C001903117 | Kemark Slue | St.Catherine | Completed | Load_249294 | New Michelton - 310 | 2026-08-28 07:44 | 2026-08-28 07:45 | 2026-08-28 07:49 | 2026-08-28 07:50 | 2026-08-28 09:24 | 2026-08-28 09:00 | 2026-08-28 09:26 | 2026-08-28 09:26 |  |  | Fair | No | Premises was checked and found okay.
Outage | J.E.26.08.60846 | C001903115 | Marlon Authors | St.Elizabeth | Completed | Load_266664 | Maggotty - 210 | 2026-08-28 07:44 | 2026-08-28 07:46 | 2026-08-28 20:23 | 2026-08-28 20:23 | 2026-08-28 20:23 | 2026-08-28 20:28 | 2026-08-28 20:30 | 2026-08-28 20:30 | Fire |  | Fair | No | Customer request daylight for visit because he is not there tonight
Non-Outage | J.E.26.08.43437 | C001903123 | Romeo Brissett |  | Completed |  |  | 2026-08-28 07:45 | 2026-08-28 07:47 | 2026-08-28 13:31 | 2026-08-28 13:32 | 2026-08-28 14:57 | 2026-08-28 14:30 | 2026-08-28 15:52 | 2026-08-28 15:52 |  | Y | Fair | No | Removed vegetation and replaced (1)15KVA transformer fuse. (1)2.
Non-Outage | J.E.26.08.43834 | C001903121 | Romeo Brissett |  | Completed |  |  | 2026-08-28 07:45 | 2026-08-28 07:47 | 2026-08-28 11:12 | 2026-08-28 11:12 | 2026-08-28 11:32 | 2026-08-28 12:00 | 2026-08-28 12:01 | 2026-08-28 12:01 |  |  | Fair | No | Customer was reconnected by escalation.
Non-Outage | J.E.26.08.44800 | C001903120 | Romeo Brissett |  | Completed |  |  | 2026-08-28 07:45 | 2026-08-28 07:47 | 2026-08-28 12:01 | 2026-08-28 12:01 | 2026-08-28 12:31 | 2026-08-28 13:20 | 2026-08-28 13:29 | 2026-08-28 13:29 |  |  | Fair | No | Customer premises was found and they stated power restored, however they reported a broken system neutral, spliced and retention system neutral.
Non-Outage | J.E.26.08.44876 | C001903119 | Romeo Brissett |  | Completed |  |  | 2026-08-28 07:45 | 2026-08-28 07:47 | 2026-08-28 13:29 | 2026-08-28 13:29 | 2026-08-28 13:29 | 2026-08-28 13:30 | 2026-08-28 13:31 | 2026-08-28 13:31 |  |  | Fair | No | Check and found ok.
Non-Outage | J.E.26.08.57642 | C001903124 | Romeo Brissett |  | Completed |  |  | 2026-08-28 07:45 | 2026-08-28 07:47 | 2026-08-28 11:10 | 2026-08-28 11:10 | 2026-08-28 11:10 | 2026-08-28 11:10 | 2026-08-28 11:11 | 2026-08-28 11:11 |  |  | Fair | No | Hanover call
Outage | J.E.26.08.57531 | C001903125 | Horace Malcolm | St.James | Completed | Load_269492 | Bogue - 610 | 2026-08-28 07:45 | 2026-08-29 07:39 | 2026-08-29 08:08 | 2026-08-29 08:08 | 2026-08-29 09:19 | 2026-08-29 09:49 | 2026-08-29 09:49 | 2026-08-29 09:49 |  |  | Rains | No | Refused one 8amp junction fuse
Outage | J.E.26.08.58384 | C001903122 | Romeo Brissett | St.James | Completed | Load_302185 | Bogue - 610 | 2026-08-28 07:45 | 2026-08-28 07:47 | 2026-08-28 07:54 | 2026-08-28 07:55 | 2026-08-28 09:14 | 2026-08-28 09:30 | 2026-08-28 09:40 | 2026-08-28 09:40 |  |  | Fair | No | Customer was reconnected by escalation.
Non-Outage | J.E.26.08.16098 | C001903127 | Rusean Allen | KSAS | Completed | Load_269480 | Hunts Bay - 710 | 2026-08-28 07:50 | 2026-08-28 07:56 | 2026-08-28 11:15 | 2026-08-28 11:16 | 2026-08-28 11:20 | 2026-08-28 11:21 | 2026-08-28 11:21 | 2026-08-28 11:21 |  |  | Fair | No | Phone went unanswered
Non-Outage | J.E.26.08.16172 | C001903129 | Rusean Allen | KSAS | Completed | Load_255695 | Greenwich - 310 | 2026-08-28 07:50 | 2026-08-28 07:56 | 2026-08-28 10:27 | 2026-08-28 10:28 | 2026-08-28 10:39 | 2026-08-28 10:39 | 2026-08-28 10:40 | 2026-08-28 10:40 |  |  | Fair | No | Premises okay
Non-Outage | J.E.26.08.22182 | C001903128 | Rusean Allen | KSAS | Completed | Load_579116 | Greenwich - 510 | 2026-08-28 07:50 | 2026-08-28 07:56 | 2026-08-28 13:30 | 2026-08-28 13:31 | 2026-08-28 13:34 | 2026-08-28 13:36 | 2026-08-28 13:36 | 2026-08-28 13:36 |  |  | Fair | No | Disconnection was already made a few days ago
Outage | J.E.26.08.57174 | C001903130 | Rusean Allen | KSAS | Completed | Load_259473 | Hunts Bay - 710 | 2026-08-28 07:50 | 2026-08-28 07:56 | 2026-08-28 10:41 | 2026-08-28 10:42 | 2026-08-28 11:08 | 2026-08-28 11:15 | 2026-08-28 11:15 | 2026-08-28 11:15 |  |  | Fair | No | 1x 15amp fuse found 1x 15amp fuse replaced.
Non-Outage | J.E.26.08.43890 | C001903136 | Rusean Allen | KSAS | Completed | Load_262444 | Hunts Bay - 310 | 2026-08-28 07:56 | 2026-08-28 07:57 | 2026-08-28 09:28 | 2026-08-28 09:29 | 2026-08-28 10:20 | 2026-08-28 10:26 | 2026-08-28 10:26 | 2026-08-28 10:26 |  |  | Fair | No | 1x 10amp fuse found 1x 10amp fuse replaced.
Non-Outage | J.E.26.08.48869 | C001903145 | Elvis Trowers | KSAS | Completed | Load_261609 | Three Miles - 410 | 2026-08-28 07:57 | 2026-08-28 08:15 | 2026-08-28 09:41 | 2026-08-28 09:41 | 2026-08-28 10:47 | 2026-08-28 10:50 | 2026-08-28 10:48 | 2026-08-28 10:48 |  |  | Fair | No | Found okay upon arrival. Customer states matter was resolved.
Outage | J.E.26.08.60865 | C001903146 | Marlon Brown | Trelawny | Completed | Load_250266 | Greenwood - 110 | 2026-08-28 08:00 | 2026-08-28 08:01 | 2026-08-28 10:27 | 2026-08-28 10:27 | 2026-08-28 10:40 | 2026-08-28 10:56 | 2026-08-28 10:56 | 2026-08-28 10:56 |  |  | Fair | No | Clean and remake joint at pole, corrosion was at pole. Voltage found at pothead 112Voltage leaving at pothead 112/114=226v
Outage | J.E.26.08.42356 | C001903147 | Romeo Brissett | Trelawny | Completed | Load_251635 | Greenwood - 210 | 2026-08-28 08:02 | 2026-08-28 08:04 | 2026-08-28 09:40 | 2026-08-28 09:41 | 2026-08-28 10:33 | 2026-08-28 11:05 | 2026-08-28 11:10 | 2026-08-28 11:10 |  |  | Fair | No | Spliced and retention customer service wire, V/R 113-112-236
Outage | J.E.26.08.59843 | C001903159 | Elvis Trowers | KSAN | Completed | Load_240739 | Washington Blvd - 310 | 2026-08-28 08:04 | 2026-08-28 08:06 | 2026-08-28 10:48 | 2026-08-28 10:49 | 2026-08-28 11:41 | 2026-08-28 11:40 | 2026-08-28 11:45 | 2026-08-28 11:45 |  |  | Fair | No | Disconnect burnt #2/0 twisted secondary burn is Honda superior fire yesterday and reclosed isolated junction at pole #( no pole#). And give back about 10 customers supply. J.P.S crew doing the rest of assessments.
Outage | J.E.26.08.60847 | C001903160 | Elvis Trowers | KSAS | Completed | Load_257257 | Hunts Bay - 810 | 2026-08-28 08:04 | 2026-08-28 08:06 | 2026-08-28 09:13 | 2026-08-28 09:14 | 2026-08-28 09:29 | 2026-08-28 09:30 | 2026-08-28 09:41 | 2026-08-28 09:41 |  |  | Fair | No | Found one 25 amps junction fuse blown at pole # ( no pole #). Refused using one 25 amps fuse and reclosed junction switch.
Non-Outage | J.E.26.08.56345 | C001903184 | Hopeton Henry | St.Thomas | Completed | Load_238113 | Good Year - 110 | 2026-08-28 08:20 | 2026-08-28 08:21 | 2026-08-28 08:52 | 2026-08-28 11:01 | 2026-08-28 14:52 | 2026-08-28 16:01 | 2026-08-28 16:04 | 2026-08-28 16:04 |  |  | Fair | No | Check pole and pot head no problem found 120-120-240 volts on load Refer to field service to check hexin box connection because customer is complaining about power serge
Non-Outage | J.E.26.08.56692 | C001903185 | Hopeton Henry | St.Thomas | Completed | Load_244113 | Good Year - 210 | 2026-08-28 08:20 | 2026-08-28 08:21 | 2026-08-28 08:52 | 2026-08-28 08:54 | 2026-08-28 10:17 | 2026-08-28 10:57 | 2026-08-28 11:00 | 2026-08-28 11:00 |  |  | Fair | No | Refresh connections at pole 114-107-220 volts Customer request home visit because of high consumption, refer to field service
Outage | J.E.26.08.60759 | C001903216 | Cliton Henry | St.Mary | Completed | Load_242891 | Oracabessa - 210 | 2026-08-28 08:48 | 2026-08-28 09:14 | 2026-08-28 09:34 | 2026-08-28 09:35 | 2026-08-28 10:15 | 2026-08-28 10:45 | 2026-08-28 10:48 | 2026-08-28 10:48 |  |  | Fair | No | A blown 10 amp junction fuse found at pole #0023654 due to tree contact Supply restored using 1- 10 amp fuse. Kindly refer bushing to St. Mary Operations for vegetation management.
Outage | J.E.26.08.60391 | C001903218 | Tyrese Williams | St.Ann | Completed | Load_237957 | Cardiff Hall - 310 | 2026-08-28 08:49 | 2026-08-28 08:50 | 2026-08-28 09:11 | 2026-08-28 09:13 | 2026-08-28 09:52 | 2026-08-28 09:53 | 2026-08-28 09:53 | 2026-08-28 09:53 |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.08.60775 | C001903217 | Raymond Lewis | St.Ann | Completed | Load_261996 | Roaring River - 210 | 2026-08-28 08:49 | 2026-08-28 18:47 | 2026-08-28 20:55 | 2026-08-28 20:56 | 2026-08-28 20:55 | 2026-08-28 20:57 | 2026-08-28 20:57 | 2026-08-28 20:57 | Fire |  | Fair | No | No fire seen and the phone number short one number
Non-Outage | J.E.26.08.57240 | C001903219 | Roxroy Needham | St.Ann | Completed | Load_247864 | Cardiff Hall - 310 | 2026-08-28 08:51 | 2026-08-28 13:39 | 2026-08-28 12:50 |  | 2026-08-28 13:59 | 2026-08-28 14:00 | 2026-08-28 14:03 | 2026-08-28 14:03 |  |  | Fair | No | Splice and retention customer service use 5 ft of number 6 triplex and three clamp
Non-Outage | J.E.26.08.48887 | C001903220 | Raymond Lewis | St.Ann | Completed | Load_267750 | Roaring River - 210 | 2026-08-28 08:52 | 2026-08-28 16:40 | 2026-08-28 18:33 | 2026-08-28 18:33 | 2026-08-28 20:47 | 2026-08-28 20:49 | 2026-08-28 20:49 | 2026-08-28 20:49 |  |  | Fair | No | Unable to get customer
Non-Outage | J.E.26.08.48983 | C001903226 | Tyrese Williams | St.Ann | Completed | Load_246511 | Cardiff Hall - 210 | 2026-08-28 08:53 | 2026-08-28 08:53 | 2026-08-28 09:11 | 2026-08-28 10:56 | 2026-08-28 11:29 | 2026-08-28 11:56 | 2026-08-28 11:56 | 2026-08-28 11:56 |  |  | Fair | No | Repair secondary neutral jumper use 1 pg clamp voltage check 116/117/232
Non-Outage | J.E.26.08.54825 | C001903227 | Daniel Francis | St.Ann | Completed | Load_270119 | Ocho Rios - 510 | 2026-08-28 08:53 | 2026-08-28 08:54 | 2026-08-28 10:55 | 2026-08-28 10:56 | 2026-08-28 11:44 | 2026-08-28 12:44 | 2026-08-28 13:08 | 2026-08-28 13:08 |  |  | Fair | No | Change 3 one bolt clamp at meter pole also found disconnect wire at JPS pole use 1 one bolt clamp to replace it 118 118 236 in all power restored
Non-Outage | J.E.26.08.60802 | C001903229 | Andrae Clarke | Portland | Completed | Load_244183 | Port Antonio - 310 | 2026-08-28 08:57 | 2026-08-28 08:58 | 2026-08-28 09:24 | 2026-08-28 09:25 | 2026-08-28 12:19 | 2026-08-28 11:07 | 2026-08-28 12:21 | 2026-08-28 12:21 |  |  | Fair | No | Changed wire used eighty ft wire three pen union and three one bolt clamp Check voltage 117/115/235
Non-Outage | J.E.26.08.54571 | C001903231 | Oraine Minto | St.Ann | Completed | Load_300570 | Ocho Rios - 410 | 2026-08-28 08:59 | 2026-08-28 09:00 | 2026-08-28 16:38 | 2026-08-28 16:38 | 2026-08-28 16:38 | 2026-08-28 16:39 | 2026-08-28 16:39 | 2026-08-28 16:39 |  |  | Fair | No | Premises no found customer not answering calls
Non-Outage | J.E.26.08.60850 | C001903230 | Oraine Minto | St.Ann | Completed | Load_260609 | Ocho Rios - 310 | 2026-08-28 08:59 | 2026-08-28 09:00 | 2026-08-28 15:37 | 2026-08-28 15:37 | 2026-08-28 15:37 | 2026-08-28 15:38 | 2026-08-28 15:38 | 2026-08-28 15:38 |  |  | Fair | No | 234v 117v 117v
Non-Outage | J.E.26.08.27664 | C001903233 | Daniel Francis | St.Ann | Completed | Load_569198 | Roaring River - 410 | 2026-08-28 09:00 | 2026-08-28 09:01 | 2026-08-28 10:20 | 2026-08-28 10:21 | 2026-08-28 10:22 | 2026-08-28 10:41 | 2026-08-28 10:45 | 2026-08-28 10:45 |  |  | Fair | No | Change one 3amp fuse pole #0135679 power restored
Non-Outage | J.E.26.08.11049 | C001903248 | Odeanie Davis | KSAS | Completed | Load_268481 | Cane River - 310 | 2026-08-28 09:02 | 2026-08-28 09:04 | 2026-08-28 12:13 | 2026-08-28 12:13 | 2026-08-28 12:13 | 2026-08-28 13:14 | 2026-08-28 13:17 | 2026-08-28 13:17 |  |  | Fair | No | 119v/0V from rammi box, rammi team needed bucket truck needed. Best number 8763588908
Non-Outage | J.E.26.08.11365 | C001903247 | Odeanie Davis | KSAS | Completed | Load_243736 | Cane River - 310 | 2026-08-28 09:02 | 2026-08-28 09:04 | 2026-08-28 13:42 | 2026-08-28 13:43 | 2026-08-28 13:43 | 2026-08-28 13:50 | 2026-08-28 13:46 | 2026-08-28 13:46 |  |  | Fair | No | 116v/117v &234v at location, no power issue found at location
Non-Outage | J.E.26.08.11377 | C001903245 | Odeanie Davis | KSAS | Completed | Load_243736 | Cane River - 310 | 2026-08-28 09:02 | 2026-08-28 09:04 | 2026-08-28 13:21 | 2026-08-28 13:22 | 2026-08-28 13:21 | 2026-08-28 13:36 | 2026-08-28 13:36 | 2026-08-28 13:36 |  |  | Fair | No | 117v/101v at arrival, open circuit at pothead corrected, 2 one bolt clamps, 117v/115v & 233v after correction
Non-Outage | J.E.26.08.12951 | C001903246 | Odeanie Davis | KSAS | Completed | Load_249655 | Cane River - 310 | 2026-08-28 09:02 | 2026-08-28 09:04 | 2026-08-28 16:31 | 2026-08-28 16:31 | 2026-08-28 16:31 | 2026-08-28 16:53 | 2026-08-28 16:33 | 2026-08-28 16:33 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.14376 | C001903244 | Odeanie Davis | KSAS | Completed | Load_240840 | Cane River - 310 | 2026-08-28 09:02 | 2026-08-28 09:04 | 2026-08-28 09:58 | 2026-08-28 10:00 | 2026-08-28 09:59 | 2026-08-28 10:06 | 2026-08-28 10:06 | 2026-08-28 10:06 | LowHangingWires |  | Fair | No | Low hanging primary wire on leaning pole, new pole needed to lift primary wire, maintenance team needed
Non-Outage | J.E.26.08.24747 | C001903235 | Odeanie Davis | KSAS | Completed | Load_263363 | Cane River - 310 | 2026-08-28 09:02 | 2026-08-28 09:04 | 2026-08-28 12:07 | 2026-08-28 12:07 | 2026-08-28 12:07 | 2026-08-28 12:07 | 2026-08-28 12:13 | 2026-08-28 12:13 |  |  | Fair | No | 114v/86v at arrival, open circuit at pothead corrected, 3 one bolt, 114v/117v & 232v after correction,
Non-Outage | J.E.26.08.28760 | C001903236 | Odeanie Davis | KSAS | Completed | Load_300806 | Cane River - 310 | 2026-08-28 09:02 | 2026-08-28 09:04 | 2026-08-28 09:15 | 2026-08-28 09:16 | 2026-08-28 09:15 | 2026-08-28 09:16 | 2026-08-28 09:18 | 2026-08-28 09:18 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.42678 | C001903238 | Odeanie Davis | KSAS | Completed | Load_255516 | Cane River - 310 | 2026-08-28 09:02 | 2026-08-28 09:04 | 2026-08-28 11:18 | 2026-08-28 11:19 | 2026-08-28 11:18 | 2026-08-28 11:28 | 2026-08-28 11:28 | 2026-08-28 11:28 |  |  | Fair | No | 114v/0V at arrival, open circuit in meter box and pothead corrected, jps meter box needs to be changed, 2 penn union, 117V/114v & 232v after correction
Non-Outage | J.E.26.07.07126 | C001903258 | Odeanie Davis | KSAS | Completed | Load_242102 | Cane River - 310 | 2026-08-28 09:03 | 2026-08-28 09:04 | 2026-08-28 14:02 | 2026-08-28 14:02 | 2026-08-28 14:02 | 2026-08-28 14:19 | 2026-08-28 14:04 | 2026-08-28 14:04 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.07.13981 | C001903257 | Odeanie Davis | KSAS | Completed | Load_255914 | Cane River - 310 | 2026-08-28 09:03 | 2026-08-28 09:04 | 2026-08-28 14:48 | 2026-08-28 14:49 | 2026-08-28 14:49 | 2026-08-28 15:12 | 2026-08-28 14:50 | 2026-08-28 14:50 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.00944 | C001903256 | Odeanie Davis | KSAS | Completed | Load_243577 | Cane River - 310 | 2026-08-28 09:03 | 2026-08-28 09:04 | 2026-08-28 16:28 | 2026-08-28 16:29 | 2026-08-28 16:29 | 2026-08-28 16:30 | 2026-08-28 16:30 | 2026-08-28 16:30 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.06809 | C001903255 | Odeanie Davis | KSAS | Completed | Load_253645 | Cane River - 310 | 2026-08-28 09:03 | 2026-08-28 09:04 | 2026-08-28 14:08 | 2026-08-28 14:08 | 2026-08-28 14:08 | 2026-08-28 14:21 | 2026-08-28 14:12 | 2026-08-28 14:12 |  |  | Fair | No | Customer refuse to give direction stating that her son is a minor and done want us to go to the premises without she being there.
Non-Outage | J.E.26.08.06843 | C001903254 | Odeanie Davis | KSAS | Completed | Load_253645 | Cane River - 310 | 2026-08-28 09:03 | 2026-08-28 09:04 | 2026-08-28 14:23 | 2026-08-28 14:23 | 2026-08-28 14:23 | 2026-08-28 14:49 | 2026-08-28 14:39 | 2026-08-28 14:39 |  |  | Fair | No | 101v/99v & 200v on secondary line, technician request for transformer and secondary wire to be checked.
Non-Outage | J.E.26.08.06871 | C001903253 | Odeanie Davis | KSAS | Completed | Load_253645 | Cane River - 310 | 2026-08-28 09:03 | 2026-08-28 09:04 | 2026-08-28 13:58 | 2026-08-28 13:59 | 2026-08-28 13:58 | 2026-08-28 14:07 | 2026-08-28 13:59 | 2026-08-28 13:59 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.06898 | C001903252 | Odeanie Davis | KSAS | Completed | Load_253645 | Cane River - 310 | 2026-08-28 09:03 | 2026-08-28 09:04 | 2026-08-28 14:14 | 2026-08-28 14:15 | 2026-08-28 14:14 | 2026-08-28 14:37 | 2026-08-28 14:15 | 2026-08-28 14:15 |  |  | Fair | No | Unable to contact customer via phone number, unable to locate premise
Non-Outage | J.E.26.08.06935 | C001903250 | Odeanie Davis | KSAS | Completed | Load_253645 | Cane River - 310 | 2026-08-28 09:03 | 2026-08-28 09:04 | 2026-08-28 15:02 | 2026-08-28 15:02 | 2026-08-28 15:02 | 2026-08-28 15:34 | 2026-08-28 15:11 | 2026-08-28 15:11 |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.07143 | C001903249 | Odeanie Davis | KSAS | Completed | Load_253645 | Cane River - 310 | 2026-08-28 09:03 | 2026-08-28 09:04 | 2026-08-28 14:56 | 2026-08-28 14:56 | 2026-08-28 14:56 | 2026-08-28 15:24 | 2026-08-28 14:56 | 2026-08-28 14:56 | Fire |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.08.07630 | C001903251 | Odeanie Davis | KSAS | Completed | Load_253645 | Cane River - 310 | 2026-08-28 09:03 | 2026-08-28 09:04 | 2026-08-28 14:44 | 2026-08-28 14:45 | 2026-08-28 14:45 | 2026-08-28 14:59 | 2026-08-28 14:47 | 2026-08-28 14:47 |  |  | Fair | No | Customer stated that issue was resolved
Outage | J.E.26.08.60335 | C001903259 | Cliton Henry | St.Mary | Completed | Load_353382 | Oracabessa - 110 | 2026-08-28 09:07 | 2026-08-28 09:08 | 2026-08-28 12:35 | 2026-08-28 12:36 | 2026-08-28 12:40 | 2026-08-28 13:47 | 2026-08-28 13:58 | 2026-08-28 13:58 |  |  | Fair | No | A 25 kva transformer found isolated due to broken wire caused by a splicing sleeve. Corrective work done to spliced and retention secondary neutral using 3 feet#2 AA conductor and 3- one bolt clamps, spot bushing was done to cut and remove vines from the secondary line. Supply restored to energized the 25 kva transformer.
Outage | J.E.26.08.61055 | C001903275 | Tyrese Williams | St.Ann | Completed | Load_1007080 | Cardiff Hall - 210 | 2026-08-28 09:12 | 2026-08-28 09:13 | 2026-08-28 11:56 | 2026-08-28 11:57 | 2026-08-28 11:59 | 2026-08-28 12:00 | 2026-08-28 12:00 | 2026-08-28 12:00 |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.08.61060 | C001903276 | Daniel Francis | St.Ann | Completed | Load_243966 | Roaring River - 410 | 2026-08-28 09:16 | 2026-08-28 09:17 | 2026-08-28 09:38 | 2026-08-28 09:39 | 2026-08-28 09:51 | 2026-08-28 10:19 | 2026-08-28 10:20 | 2026-08-28 10:20 |  |  | Fair | No | Customer needs to work on meter box that’s one 2 the JPS meter for that house need to be replaced one side of the meter is broken
Outage | J.E.26.08.58744 | C001903281 | Romaine Roberts | St.Mary | Completed | Load_268674 | Annotto Bay - 310 | 2026-08-28 09:18 | 2026-08-28 09:19 | 2026-08-28 12:53 | 2026-08-28 12:54 | 2026-08-28 13:25 | 2026-08-28 13:32 | 2026-08-28 13:36 | 2026-08-28 13:36 |  |  | Fair | No | 2 wire service Corrosion at pole clean and remake joints 117 2 clamps use
Non-Outage | J.E.26.08.44104 | C001903285 | Eric Williams | KSAN | Completed | Load_262784 | Washington Blvd - 810 | 2026-08-28 09:21 | 2026-08-28 09:24 | 2026-08-28 11:24 | 2026-08-28 11:25 | 2026-08-28 12:16 | 2026-08-28 12:16 | 2026-08-28 12:16 | 2026-08-28 12:16 |  |  | Fair | No | Premises found okay
Non-Outage | J.E.26.08.50326 | C001903284 | Eric Williams | KSAN | Completed | Load_242000 | Constant Spring - 210 | 2026-08-28 09:21 | 2026-08-28 09:24 | 2026-08-28 12:16 | 2026-08-28 12:17 | 2026-08-28 12:53 | 2026-08-28 12:53 | 2026-08-28 12:54 | 2026-08-28 12:54 |  |  | Fair | No | Premises lock customer not at home customer stated they are at a funeral revisit required
Non-Outage | J.E.26.08.54611 | C001903282 | Eric Williams | KSAN | Completed | Load_265722 | Washington Blvd - 810 | 2026-08-28 09:21 | 2026-08-28 09:24 | 2026-08-28 12:57 | 2026-08-28 12:58 | 2026-08-28 13:45 | 2026-08-28 14:08 | 2026-08-28 14:08 | 2026-08-28 14:08 |  |  | Fair | No | Premises found okay
Non-Outage | J.E.26.08.60917 | C001903293 | Kemark Slue |  | Completed |  |  | 2026-08-28 09:24 | 2026-08-28 09:26 | 2026-08-28 09:54 | 2026-08-28 09:54 | 2026-08-28 10:41 | 2026-08-28 10:41 | 2026-08-28 10:46 | 2026-08-28 10:46 |  |  | Fair | No | Unable to locate customer’s premises due to inadequate directions and all calls to number given were futile.
Non-Outage | J.E.26.08.55535 | C001903295 | Cliton Henry | St.Mary | Completed | Load_258469 | Oracabessa - 210 | 2026-08-28 09:27 | 2026-08-28 09:28 | 2026-08-28 11:08 | 2026-08-28 11:08 | 2026-08-28 11:08 | 2026-08-28 11:09 | 2026-08-28 11:10 | 2026-08-28 11:10 |  |  | Fair | No | The customer was advised by the crew last night to change the meter socket.
Non-Outage | J.E.26.08.51718 | C001903299 | Raymond Carr | St.Mary | Completed | Load_262727 | Oracabessa - 110 | 2026-08-28 09:28 | 2026-08-28 16:20 | 2026-08-28 19:50 | 2026-08-28 19:51 | 2026-08-28 20:39 | 2026-08-28 20:20 | 2026-08-28 20:40 | 2026-08-28 20:40 |  |  | Fair | No | Supply found okay.
Non-Outage | J.E.26.08.41702 | C001903301 | Raymond Carr | St.Mary | Completed | Load_246610 | Oracabessa - 110 | 2026-08-28 09:29 | 2026-08-28 16:20 | 2026-08-28 18:26 | 2026-08-28 18:26 | 2026-08-28 19:32 | 2026-08-28 19:28 | 2026-08-28 19:45 | 2026-08-28 19:45 |  |  | Fair | No | Voltage readings 114/116/230.
Non-Outage | J.E.26.08.36075 | C001903311 | Oraine Minto | St.Ann | Completed | Load_259886 | Upper White River - 110 | 2026-08-28 09:39 | 2026-08-28 09:40 | 2026-08-28 12:07 | 2026-08-28 12:08 | 2026-08-28 12:08 | 2026-08-28 12:10 | 2026-08-28 12:10 | 2026-08-28 12:10 |  |  | Fair | No | Refer to emergency Whenever the block factory tun one the power is on and off in the entire area
Non-Outage | J.E.26.08.56769 | C001903312 | Locksley Allen | St.Mary | Completed | Load_247883 | Highgate -110 | 2026-08-28 09:40 | 2026-08-28 09:40 | 2026-08-28 10:19 | 2026-08-28 11:03 | 2026-08-28 11:02 | 2026-08-28 11:08 | 2026-08-28 11:08 | 2026-08-28 11:08 |  |  | Fair | No | Gate lock,but meter is seen with broken glass. Customer is asking JPS to call in advance so that arrangement can be made to have gate open.Please refer to field service
Non-Outage | J.E.26.08.30491 | C001903319 | Oraine Minto | St.Ann | Completed | Load_259886 | Upper White River - 110 | 2026-08-28 09:46 | 2026-08-28 09:46 | 2026-08-28 12:00 | 2026-08-28 12:04 | 2026-08-28 12:04 | 2026-08-28 12:05 | 2026-08-28 12:07 | 2026-08-28 12:07 |  |  | Fair | No | Refer to emergency Customer states that the block factory up the row whenever they tour on the voltage in the area go low more the one customer is affected
Non-Outage | J.E.26.08.61137 | C001903320 | Andrae Clarke | Portland | Completed | Load_258958 | Port Antonio - 410 | 2026-08-28 09:46 | 2026-08-28 09:47 | 2026-08-28 13:48 | 2026-08-28 13:49 | 2026-08-28 13:49 | 2026-08-28 13:36 | 2026-08-28 13:51 | 2026-08-28 13:51 |  |  | Fair | No | Premises locked Made several phone calls to the customer and got no response
Non-Outage | J.E.26.08.60631 | C001903326 | Andrae Clarke | Portland | Completed | Load_256013 | Port Antonio - 410 | 2026-08-28 09:48 | 2026-08-28 09:48 | 2026-08-28 13:48 | 2026-08-28 13:52 | 2026-08-28 17:48 | 2026-08-28 16:31 | 2026-08-28 17:49 | 2026-08-28 17:49 |  |  | Fair | No | Unable to find location
Non-Outage | J.E.26.08.61160 | C001903332 | Cliton Henry |  | Completed |  |  | 2026-08-28 09:54 | 2026-08-28 09:54 | 2026-08-28 11:49 | 2026-08-28 11:50 | 2026-08-28 11:49 | 2026-08-28 11:49 | 2026-08-28 11:51 | 2026-08-28 11:51 |  |  | Fair | No | Restored, related to outage #61529
Outage | J.E.26.08.61068 | C001903333 | Daniel Francis | St.Ann | Completed | Load_269255 | Upper White River - 210 | 2026-08-28 09:54 | 2026-08-28 09:55 | 2026-08-28 13:28 | 2026-08-28 13:29 | 2026-08-28 14:04 | 2026-08-28 14:05 | 2026-08-28 14:05 | 2026-08-28 14:05 |  |  | Fair | No | Not found
Non-Outage | J.E.26.08.61206 | C001903340 | Locksley Allen | St.Mary | Completed | Load_250734 | Blackstonedge - 110 | 2026-08-28 09:59 | 2026-08-28 09:59 | 2026-08-28 11:10 | 2026-08-28 12:30 | 2026-08-28 12:29 | 2026-08-28 12:42 | 2026-08-28 12:41 | 2026-08-28 12:41 |  |  | Fair | No | Meter found blank. Clean up connectors at pothead Voltage at meter socket phase to phase 231v. Phase to neutral 113&113vMeter left
Outage | J.E.26.08.61119 | C001903341 | Marlon Authors | Manchester | Completed | Load_269741 | Spur Tree - 210 | 2026-08-28 09:59 | 2026-08-28 10:00 | 2026-08-28 11:27 | 2026-08-28 11:28 | 2026-08-28 11:27 | 2026-08-28 12:41 | 2026-08-28 12:41 | 2026-08-28 12:41 | Fire |  | Fair | No | Patrol and found two poles spans of secondary neutral burnt off caused by illegal connection. Isolate and close 25 kva transformer circuit no pole # to splice and retention same using 30 feet of #2 conductor three #2 preforms and five clamps. Restored supply ok
Outage | J.E.26.08.61118 | C001903342 | Selvin White | St.Elizabeth | Completed | Load_238773 | Maggotty - 110 | 2026-08-28 10:00 | 2026-08-28 10:01 | 2026-08-28 10:31 | 2026-08-28 10:32 | 2026-08-28 11:13 | 2026-08-28 12:30 | 2026-08-28 12:31 | 2026-08-28 12:31 |  |  | Fair | No | Tap down three 100 kva transformers in a closed bank from tap position 5 to tap position 3 after isolating them . Supply restored to the affected customer. Voltages left inside meter box are 119,120,206,239,240,242 volts.
Non-Outage | J.E.26.08.61024 | C001903350 | Michael Paterson |  | Completed |  |  | 2026-08-28 10:03 | 2026-08-28 10:04 | 2026-08-28 16:08 | 2026-08-28 16:09 | 2026-08-28 16:09 | 2026-08-28 16:10 | 2026-08-28 16:10 | 2026-08-28 16:10 |  |  | Fair | No | Please give call to team on 310 feeder
Outage | J.E.26.08.60931 | C001903351 | Michael Paterson | Westmoreland | Completed | Load_258460 | Paradise - 110 | 2026-08-28 10:03 | 2026-08-28 10:04 | 2026-08-28 14:37 | 2026-08-28 14:38 | 2026-08-28 16:05 | 2026-08-28 16:06 | 2026-08-28 16:08 | 2026-08-28 16:08 |  |  | Fair | No | Premises found closed no one at home unable to make connections
Outage | J.E.26.08.61025 | C001903352 | Edward Royal | KSAS | Completed | Load_240320 | Hunts Bay - 210 | 2026-08-28 10:04 | 2026-08-28 10:04 | 2026-08-28 10:33 | 2026-08-28 10:33 | 2026-08-28 10:33 | 2026-08-28 12:13 | 2026-08-28 12:13 | 2026-08-28 12:13 | Fire |  | Fair | No | Spliced and reconnected 190 leg using 2 single bolt clamp voltage reading 233 234 234 116 117 206 v
Outage | J.E.26.08.61228 | C001903353 | Denton Williams | Portland | Completed | Load_263694 | Port Antonio - 310 | 2026-08-28 10:04 | 2026-08-28 10:04 | 2026-08-28 14:09 | 2026-08-28 14:10 | 2026-08-28 14:09 | 2026-08-28 14:10 | 2026-08-28 14:11 | 2026-08-28 14:11 |  | Y | Fair | No | Cut trees from power line and close one ten amp tripsaver
Outage | J.E.26.08.61229 | C001903354 | Denton Williams | Portland | Completed | Load_261270 | Port Antonio - 310 | 2026-08-28 10:04 | 2026-08-28 10:05 | 2026-08-28 12:25 | 2026-08-28 12:25 | 2026-08-28 12:58 | 2026-08-28 14:05 | 2026-08-28 14:08 | 2026-08-28 14:08 |  | Y | Fair | No | Cut trees from power line and close one ten amp tripsaver
Non-Outage | J.E.26.08.60904 | C001903356 | Selvin White |  | Completed |  |  | 2026-08-28 10:05 | 2026-08-28 10:07 | 2026-08-28 12:31 | 2026-08-28 12:32 | 2026-08-28 12:32 | 2026-08-28 12:36 | 2026-08-28 12:36 | 2026-08-28 12:36 |  |  | Fair | No | Supply was restored after bank of three 100 kva transformers were tapped down from tap 5- tap 3 or normal. Supply restored to the affected customer.
Outage | J.E.26.08.61236 | C001903355 | Denton Williams | Portland | Completed | Load_250256 | Port Antonio - 410 | 2026-08-28 10:05 | 2026-08-28 10:05 | 2026-08-28 10:37 | 2026-08-28 10:38 | 2026-08-28 11:08 | 2026-08-28 12:23 | 2026-08-28 12:24 | 2026-08-28 12:24 | Fire |  | Fair | No | Tree entangle open secondary lines resulting banging wires. Open 50kva transformer, cut 4 trees and split and retention 2 span of secondary lines. Closed transformer. Area is now okay.
Outage | J.E.26.08.60921 | C001903359 | Damion Reid | Manchester | Completed | Load_264065 | Kendal - 210 | 2026-08-28 10:06 | 2026-08-28 15:23 | 2026-08-29 10:44 | 2026-08-29 10:45 | 2026-08-29 11:14 | 2026-08-29 11:19 | 2026-08-29 11:20 | 2026-08-29 11:20 |  |  | Fair | No | Unable to contact or locate customer
Outage | J.E.26.08.60939 | C001903357 | Ryan Richards | Manchester | Completed | Load_250906 | Spur Tree - 310 | 2026-08-28 10:06 | 2026-08-28 10:08 | 2026-08-28 13:16 | 2026-08-28 13:17 | 2026-08-28 14:27 | 2026-08-28 16:33 | 2026-08-28 16:33 | 2026-08-28 16:33 | BrokenWire |  | Fair | No | Broken service wire found cause by market truck splice and retention using 10 ft#6 2 one bolt clamp
Outage | J.E.26.08.61226 | C001903358 | Stephen Taylor | St.Thomas | Completed | Load_264475 | Good Year - 110 | 2026-08-28 10:06 | 2026-08-28 10:06 | 2026-08-28 11:50 | 2026-08-28 11:51 | 2026-08-28 11:51 | 2026-08-28 11:51 | 2026-08-28 11:53 | 2026-08-28 11:53 |  |  | Fair | No | Transformer fuse out nothing found refuse link and close up back with a 3 amp fuse safely customer is now working okay
Outage | J.E.26.08.60914 | C001903363 | Donald Cunningham | St.Catherine | Completed | Load_267573 | Twickenham - 210 | 2026-08-28 10:10 | 2026-08-28 10:12 | 2026-08-28 10:33 | 2026-08-28 10:34 | 2026-08-28 11:11 | 2026-08-28 11:11 | 2026-08-28 11:18 | 2026-08-28 11:18 |  |  | Fair | No | Premises of customer close and stated he will home anytime after 5 pm
Outage | J.E.26.08.61240 | C001903371 | Denton Williams | Portland | Completed | Load_262568 | Port Antonio - 310 | 2026-08-28 10:17 | 2026-08-28 10:55 | 2026-08-28 14:08 | 2026-08-28 14:09 | 2026-08-28 14:08 | 2026-08-28 14:08 | 2026-08-28 14:09 | 2026-08-28 14:09 |  | Y | Fair | No | Cut trees from power line and close one ten amp tripsaver
Outage | J.E.26.08.43274 | C001903373 | Kemark Slue | St.Catherine | Completed | Load_241272 | Rhodens Pen - 410 | 2026-08-28 10:19 | 2026-08-28 12:11 | 2026-08-28 12:45 | 2026-08-28 12:45 | 2026-08-28 13:00 | 2026-08-28 13:07 | 2026-08-28 13:08 | 2026-08-28 13:08 |  |  | Fair | No | Please refer to D. Martin to have a small vehicle to check site.
Outage | J.E.26.08.61162 | C001903375 | Dean- Smith | Hanover | Completed | Load_252053 | Orange Bay - 210 | 2026-08-28 10:19 | 2026-08-28 10:21 | 2026-08-28 12:09 | 2026-08-28 12:11 | 2026-08-28 12:11 | 2026-08-28 12:11 | 2026-08-28 12:12 | 2026-08-28 12:12 |  |  | Fair | No | Area was restored
Outage | J.E.26.08.61163 | C001903374 | Dean- Smith | Hanover | Completed | Load_258609 | Orange Bay - 210 | 2026-08-28 10:19 | 2026-08-28 10:21 | 2026-08-28 10:34 | 2026-08-28 10:35 | 2026-08-28 11:57 | 2026-08-28 11:57 | 2026-08-28 12:02 | 2026-08-28 12:02 |  |  | Fair | No | Cut and remove vegetation,replace 10amp junction fuse at pole number (619054).
Outage | J.E.26.08.57718 | C001903377 | Dean- Smith | Hanover | Completed | Load_257747 | Orange Bay - 310 | 2026-08-28 10:20 | 2026-08-28 10:21 | 2026-08-28 12:13 | 2026-08-28 12:14 | 2026-08-28 12:48 | 2026-08-28 13:23 | 2026-08-28 13:24 | 2026-08-28 13:24 |  |  | Rains | No | Check and found ok
Outage | J.E.26.08.61151 | C001903376 | Dean- Smith | Hanover | Completed | Load_241865 | Orange Bay - 210 | 2026-08-28 10:20 | 2026-08-28 10:21 | 2026-08-28 12:12 | 2026-08-28 12:13 | 2026-08-28 12:12 | 2026-08-28 12:12 | 2026-08-28 12:13 | 2026-08-28 12:13 |  |  | Rains | No | Area was restored
Outage | J.E.26.08.61237 | C001903378 | Moses Elliston | St.Catherine | Completed | Load_557143 | Tredegar - 410 | 2026-08-28 10:21 | 2026-08-28 10:23 | 2026-08-28 11:42 | 2026-08-28 11:43 | 2026-08-28 11:42 | 2026-08-28 11:42 | 2026-08-28 11:44 | 2026-08-28 11:44 |  |  | Fair | No | Credit added to prepaid account.See report # 1721727.(Duplication)
Outage | J.E.26.08.60716 | C001903379 | Moses Elliston | St.Catherine | Completed | Load_239334 | Tredegar - 410 | 2026-08-28 10:22 | 2026-08-28 10:23 | 2026-08-28 11:29 | 2026-08-28 11:29 | 2026-08-28 11:29 | 2026-08-28 11:20 | 2026-08-28 11:31 | 2026-08-28 11:31 |  |  | Fair | No | Credit added to prepaid account
Outage | J.E.26.08.61237 | C001903380 | Moses Elliston | St.Catherine | Completed | Load_557143 | Tredegar - 410 | 2026-08-28 10:22 | 2026-08-28 10:23 | 2026-08-28 11:40 | 2026-08-28 11:41 | 2026-08-28 11:40 | 2026-08-28 11:41 | 2026-08-28 11:42 | 2026-08-28 11:42 |  |  | Fair | No | Credit added to prepaid account
Outage | J.E.26.08.60976 | C001903383 | Horace Malcolm | St.James | Completed | Load_241713 | Bogue - 610 | 2026-08-28 10:26 | 2026-08-29 07:39 | 2026-08-29 09:50 | 2026-08-29 09:50 | 2026-08-29 10:35 | 2026-08-29 10:38 | 2026-08-29 10:38 | 2026-08-29 10:38 |  |  | Fair | No | Check and customer have internal issues defective meter socket
Outage | J.E.26.08.57624 | C001903384 | Dean- Smith | Hanover | Completed | Load_265304 | Orange Bay - 310 | 2026-08-28 10:27 | 2026-08-28 10:28 | 2026-08-28 13:55 | 2026-08-28 13:56 | 2026-08-28 13:56 | 2026-08-28 13:56 | 2026-08-28 13:58 | 2026-08-28 13:58 |  |  | Rains | No | Check and found ok
Outage | J.E.26.08.60936 | C001903392 | Swon Miller | St.James | Completed | Load_255876 | Queens Drive - 710 | 2026-08-28 10:28 | 2026-08-28 10:29 | 2026-08-28 14:15 | 2026-08-28 14:15 | 2026-08-28 14:43 | 2026-08-18 15:05 | 2026-08-28 15:12 | 2026-08-28 15:12 |  |  | Fair | No | Check and found okay customer states that power supply was restored voltage found 117/116/234 voltage left 117/116/234
Non-Outage | J.E.26.08.41157 | C001903393 | Donald Cunningham |  | Completed |  |  | 2026-08-28 10:29 | 2026-08-28 10:30 | 2026-08-28 11:18 | 2026-08-28 11:40 | 2026-08-28 12:27 | 2026-08-28 12:33 | 2026-08-28 12:34 | 2026-08-28 12:34 | LowHangingWires |  | Fair | No | Premises found ok issues already resolved
Outage | J.E.26.08.61314 | C001903394 | Roxroy Needham | St.Ann | Completed | Load_241416 | Cardiff Hall - 310 | 2026-08-28 10:31 | 2026-08-28 13:06 | 2026-08-28 14:04 | 2026-08-28 14:05 | 2026-08-28 14:36 | 2026-08-28 14:47 | 2026-08-28 14:49 | 2026-08-28 14:49 |  |  | Fair | No | Replace a 25 KVA transformer fuse with a 3 amps at pole and a 15 amps junction fuse at pole
Non-Outage | J.E.26.08.61033 | C001903418 | Swon Miller |  | Completed |  |  | 2026-08-28 10:38 | 2026-08-28 10:39 | 2026-08-29 07:46 | 2026-08-29 07:47 | 2026-08-29 08:26 | 2026-08-18 08:40 | 2026-08-29 08:40 | 2026-08-29 08:40 | Fire |  | Fair | No | Check and found okay customer states that the issue was rectified from yesterday voltage found 115/114/230 voltage left 115/114/230
Outage | J.E.26.08.61285 | C001903419 | Collin Robinson | Portland | Completed | Load_256013 | Port Antonio - 410 | 2026-08-28 10:40 | 2026-08-28 20:04 | 2026-08-29 09:37 | 2026-08-29 09:37 | 2026-08-29 10:24 | 2026-08-29 10:29 | 2026-08-29 10:29 | 2026-08-29 10:29 |  |  | Fair | No | Burn meter and meter socket found at location Refer to field service
Non-Outage | J.E.26.08.61316 | C001903434 | Rusean Allen | KSAS | Completed | Load_244355 | Hunts Bay - 210 | 2026-08-28 10:50 | 2026-08-28 10:51 | 2026-08-28 11:41 | 2026-08-28 11:41 | 2026-08-28 11:46 | 2026-08-28 11:49 | 2026-08-28 11:49 | 2026-08-28 11:49 |  |  | Fair | No | Area congested
Outage | J.E.26.08.61049 | C001903435 | Jermaine Williams | Clarendon | Completed | Load_248737 | Parnassus - 210 | 2026-08-28 10:50 | 2026-08-28 10:51 | 2026-08-28 11:03 | 2026-08-28 11:04 | 2026-08-28 11:43 | 2026-08-28 11:54 | 2026-08-28 11:55 | 2026-08-28 11:55 |  |  | Fair | No | Customer advised to get electrician, meter found ok.
Outage | J.E.26.08.61416 | C001903447 | Raymond Carr | St.Ann | Completed | Load_251915 | Upper White River - 110 | 2026-08-28 10:54 | 2026-08-28 16:21 | 2026-08-28 17:11 | 2026-08-28 17:11 | 2026-08-28 17:53 | 2026-08-28 18:00 | 2026-08-28 18:22 | 2026-08-28 18:22 | Fire |  | Fair | No | Two one bolt clamps was replaced at JPS pole. Voltage readings 117/119/236, however after several troubleshooting kWh meter found to be defective. Refer to field service department for replacement.
Non-Outage | J.E.26.08.61352 | C001903451 | Oraine Minto | St.Ann | Completed | Load_243376 | Roaring River - 210 | 2026-08-28 10:59 | 2026-08-28 13:01 | 2026-08-28 13:11 | 2026-08-28 13:12 | 2026-08-28 13:11 | 2026-08-28 13:12 | 2026-08-28 13:14 | 2026-08-28 13:14 |  |  | Fair | No | Refer to field service Customer getting 243v and his ac is not able to work Meter in rami system
Non-Outage | J.E.26.08.61379 | C001903464 | Barnett Brown |  | Completed |  |  | 2026-08-28 11:02 | 2026-08-28 15:28 | 2026-08-28 15:42 | 2026-08-28 15:42 | 2026-08-28 16:04 | 2026-08-28 16:26 | 2026-08-28 16:29 | 2026-08-28 16:29 | LeakingTransformer |  | Fair | No | Customer is concern about illegal connection
Non-Outage | J.E.26.08.61441 | C001903462 | Damion Reid |  | Completed |  |  | 2026-08-28 11:02 | 2026-08-28 15:23 | 2026-08-28 16:13 | 2026-08-28 16:13 | 2026-08-28 16:56 | 2026-08-28 18:56 | 2026-08-28 18:59 | 2026-08-28 18:59 | BrokenPole |  | Rains | No | Broken 30ft secondary pole found cause by vehicle accident lower secondary twisted and cut pole head to restore normality
Outage | J.E.26.08.43853 | C001903463 | Dean- Smith | Hanover | Completed | Load_246952 | Orange Bay - 310 | 2026-08-28 11:02 | 2026-08-28 11:04 | 2026-08-28 13:24 | 2026-08-28 13:25 | 2026-08-28 13:54 | 2026-08-28 13:54 | 2026-08-28 13:55 | 2026-08-28 13:55 |  |  | Rains | No | Check and found ok
Outage | J.E.26.08.61261 | C001903452 | Marlon Authors | Manchester | Completed | Load_268532 | Spur Tree - 210 | 2026-08-28 11:02 | 2026-08-28 11:57 | 2026-08-28 12:47 | 2026-08-28 12:48 | 2026-08-28 12:47 | 2026-08-28 12:48 | 2026-08-28 12:48 | 2026-08-28 12:48 | BrokenWire |  | Fair | No | Supply restored to the area
Outage | J.E.26.08.61444 | C001903453 | Marlon Authors | Manchester | Completed | Load_251627 | Spur Tree - 210 | 2026-08-28 11:02 | 2026-08-28 11:57 | 2026-08-28 14:32 | 2026-08-28 14:33 | 2026-08-28 14:32 | 2026-08-28 14:56 | 2026-08-28 14:56 | 2026-08-28 14:56 | Fire |  | Fair | No | Supply checked and found service wire broken. Repair same using three feet of #6 triplex service wire and two linkets. Supply leave working ok rdg 120v,120v and cross phased 240 volts
Outage | J.E.26.08.61321 | C001903465 | Damion Reid | Manchester | Completed | Load_258689 | Kendal - 210 | 2026-08-28 11:03 | 2026-08-28 15:23 | 2026-08-28 21:55 | 2026-08-28 21:56 | 2026-08-28 23:14 | 2026-08-28 23:16 | 2026-08-28 23:17 | 2026-08-28 23:17 |  |  | Fair | No | Blown 10amp junction fuse found cause by lightning line patrol and replace blown fuse
Non-Outage | J.E.26.08.17091 | C001903482 | Donald Cunningham | St.Catherine | Completed | Load_576132 | Twickenham - 210 | 2026-08-28 11:12 | 2026-08-28 11:14 | 2026-08-28 12:35 | 2026-08-28 13:20 | 2026-08-28 13:27 | 2026-08-28 13:34 | 2026-08-28 13:41 | 2026-08-28 13:41 |  |  | Fair | No | Corroded phase and neural by pothead corrected voltage 3 clamps voltage readings 112/113/226
Non-Outage | J.E.26.08.61529 | C001903483 | Cliton Henry |  | Completed |  |  | 2026-08-28 11:14 | 2026-08-28 11:14 | 2026-08-28 11:33 | 2026-08-28 11:33 | 2026-08-28 11:33 | 2026-08-28 11:48 | 2026-08-28 11:49 | 2026-08-28 11:49 |  |  | Fair | No | A blown 15 amp junction fuse found at the entrance to the property. Supply restored using 1-15 amp fuse.
Non-Outage | J.E.26.08.35050 | C001903529 | Elvis Trowers | KSAN | Completed | Load_243339 | Washington Blvd - 710 | 2026-08-28 11:28 | 2026-08-28 11:30 | 2026-08-28 11:45 | 2026-08-28 11:46 | 2026-08-28 11:58 | 2026-08-28 12:05 | 2026-08-28 12:04 | 2026-08-28 12:04 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Non-Outage | J.E.26.08.25715 | C001903538 | Elvis Trowers | KSAN | Completed | Load_256467 | Washington Blvd - 310 | 2026-08-28 11:29 | 2026-08-28 11:30 | 2026-08-28 12:13 | 2026-08-28 13:06 | 2026-08-28 13:05 | 2026-08-28 13:10 | 2026-08-28 13:12 | 2026-08-28 13:12 |  |  | Fair | No | Customer getting low voltage when checked twisted secondary across from customer premises getting 97-94-193 volts at the transformer drop lead 109-109-218 volts change transformer topping from top 3-5 getting 115-115-231 volts and at customer premises 103-101-206 volts. Line need to be split need one more transformer to split the area.
Non-Outage | J.E.26.08.26015 | C001903539 | Elvis Trowers | KSAN | Completed | Load_256467 | Washington Blvd - 310 | 2026-08-28 11:29 | 2026-08-28 11:30 | 2026-08-28 13:12 | 2026-08-28 13:13 | 2026-08-28 13:13 | 2026-08-28 13:15 | 2026-08-28 13:13 | 2026-08-28 13:13 |  |  | Fair | No | Duplicate call.
Outage | J.E.26.08.60731 | C001903565 | Edward Royal | KSAS | Completed | Load_269111 | Greenwich - 310 | 2026-08-28 11:40 | 2026-08-28 11:41 | 2026-08-28 12:15 | 2026-08-28 12:15 | 2026-08-28 12:40 | 2026-08-28 13:29 | 2026-08-28 14:05 | 2026-08-28 14:05 | Fire |  | Fair | No | Fire was at the market customer was disconnected and spliced and reconnected secondary tripe x cable
Outage | J.E.26.08.61574 | C001903568 | Jermaine Williams | Clarendon | Completed | Load_261428 | May Pen - 210 | 2026-08-28 11:42 | 2026-08-28 11:43 | 2026-08-28 11:56 | 2026-08-28 11:57 | 2026-08-28 12:47 | 2026-08-28 13:32 | 2026-08-28 13:31 | 2026-08-28 13:31 |  | Y | Fair | No | Cct loading, 10kva xfmr supplying approximately 40 customers. Xfmr upgrade needed, refer to Devon Brown. Simon Jackson was advised.
Outage | J.E.26.08.61398 | C001903580 | Donald Cunningham | St.Catherine | Completed | Load_245608 | Twickenham - 210 | 2026-08-28 11:45 | 2026-08-28 11:46 | 2026-08-28 13:43 | 2026-08-28 13:43 | 2026-08-28 14:30 | 2026-08-28 14:42 | 2026-08-28 14:43 | 2026-08-28 14:43 |  |  | Fair | No | Refer to mr Ellison customer unable to add credit
Outage | J.E.26.08.61593 | C001903606 | Selvin White | St.Elizabeth | Completed | Load_249016 | Maggotty - 110 | 2026-08-28 11:57 | 2026-08-28 11:59 | 2026-08-28 12:40 | 2026-08-28 12:40 | 2026-08-28 13:58 | 2026-08-28 14:05 | 2026-08-28 14:17 | 2026-08-28 14:17 |  |  | Fair | No | Please refer to Jessie Morales and C. Johnson at the field service department as call is hurricane Melissa related.
Outage | J.E.26.08.61103 | C001903613 | Moses Elliston | St.Catherine | Completed | Load_557184 | Tredegar - 410 | 2026-08-28 12:11 | 2026-08-28 12:12 | 2026-08-28 12:18 | 2026-08-28 12:19 | 2026-08-28 12:18 | 2026-08-28 10:55 | 2026-08-28 12:21 | 2026-08-28 12:21 |  |  | Fair | No | Credit added to prepaid account
Outage | J.E.26.08.61356 | C001903614 | Moses Elliston | St.Catherine | Completed | Load_557299 | Tredegar - 410 | 2026-08-28 12:11 | 2026-08-28 12:12 | 2026-08-28 12:15 | 2026-08-28 12:15 | 2026-08-28 12:15 | 2026-08-28 12:10 | 2026-08-28 12:16 | 2026-08-28 12:16 |  |  | Fair | No | Credit added to prepaid account
Non-Outage | J.E.26.08.36075 | C001903647 | Daniel Francis | St.Ann | Completed | Load_259886 | Upper White River - 110 | 2026-08-28 12:28 | 2026-08-28 12:29 | 2026-08-28 15:25 | 2026-08-28 15:25 | 2026-08-28 15:25 | 2026-08-28 15:28 | 2026-08-28 15:28 | 2026-08-28 15:28 |  |  | Fair | No | Found jumper break we work on it use 2 one bolt clamp power restored
Non-Outage | J.E.26.08.30491 | C001903648 | Daniel Francis | St.Ann | Completed | Load_259886 | Upper White River - 110 | 2026-08-28 12:29 | 2026-08-28 12:29 | 2026-08-28 14:16 | 2026-08-28 14:16 | 2026-08-28 14:50 | 2026-08-28 14:29 | 2026-08-28 15:25 | 2026-08-28 15:25 |  |  | Fair | No | Customer not answering phone
Non-Outage | J.E.26.08.61721 | C001903671 | Richard Samuda | Manchester | Completed | Load_302217 | Spur Tree - 310 | 2026-08-28 12:46 | 2026-08-29 07:13 | 2026-08-29 09:14 | 2026-08-29 09:18 | 2026-08-29 09:25 | 2026-08-29 09:34 | 2026-08-29 09:34 | 2026-08-29 09:34 |  |  | Fair | No | Found ok voltage 114, 114 228
Non-Outage | J.E.26.08.61612 | C001903681 | Horace Malcolm |  | Completed |  |  | 2026-08-28 12:48 | 2026-08-28 20:03 | 2026-08-29 00:53 | 2026-08-29 00:54 | 2026-08-29 00:53 | 2026-08-29 01:43 | 2026-08-29 01:44 | 2026-08-29 01:44 | BrokenWire |  | Fair | No | Unable to locate which of the hexing box in area have damaged wire in the report this call would refer to field service
Outage | J.E.26.08.61641 | C001903680 | Romeo Brissett | St.James | Completed | Load_292555 | Bogue - 310 | 2026-08-28 12:48 | 2026-08-28 12:49 | 2026-08-28 15:53 | 2026-08-28 15:53 | 2026-08-28 16:55 | 2026-08-28 19:00 | 2026-08-28 19:18 | 2026-08-28 19:18 | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Cut and removed tree limbs, spliced and retention 2 span of secondary, replaced (1)8amps junction
Outage | J.E.26.08.61842 | C001903682 | Derrick Dawkins | St.James | Completed | Load_249352 | Queens Drive - 710 | 2026-08-28 12:50 | 2026-08-28 23:08 | 2026-08-28 23:41 | 2026-08-29 00:59 | 2026-08-29 00:58 | 2026-08-29 00:42 | 2026-08-29 01:08 | 2026-08-29 01:08 |  |  | Fair | No | Only customer with out lights customer says no one at the premises at the moment
Outage | J.E.26.08.62018 | C001903699 | Tyrese Williams | St.Ann | Completed | Load_258093 | Roaring River - 410 | 2026-08-28 13:00 | 2026-08-28 13:07 | 2026-08-28 14:18 | 2026-08-28 14:22 | 2026-08-28 14:22 | 2026-08-28 14:25 | 2026-08-28 14:26 | 2026-08-28 14:26 |  |  | Fair | No | Premises found ok call related to the 25amp junction fuse at pole
Outage | J.E.26.08.62025 | C001903701 | Tyrese Williams | St.Ann | Completed | Load_259493 | Roaring River - 410 | 2026-08-28 13:02 | 2026-08-28 13:07 | 2026-08-28 13:19 | 2026-08-28 13:19 | 2026-08-28 13:57 | 2026-08-28 14:22 | 2026-08-28 14:22 | 2026-08-28 14:22 |  |  | Fair | No | Replace a 20 amp junction fuse at pole
Outage | J.E.26.08.62046 | C001903718 | Cliton Henry | St.Mary | Completed | Load_266827 | Oracabessa - 210 | 2026-08-28 13:08 | 2026-08-28 13:08 | 2026-08-28 14:08 | 2026-08-28 14:09 | 2026-08-28 15:09 | 2026-08-28 15:09 | 2026-08-28 15:10 | 2026-08-28 15:10 | Fire |  | Fair | No | No fire seen in the area as reported.
Outage | J.E.26.08.62109 | C001903742 | Hartley Chin | Clarendon | Completed | Load_259178 | Parnassus - 310 | 2026-08-28 13:31 | 2026-08-28 17:00 | 2026-08-28 17:34 | 2026-08-28 19:30 | 2026-08-28 19:29 | 2026-08-28 19:30 | 2026-08-28 19:30 | 2026-08-28 19:30 | BrokenWire |  | Fair | No | Call related to job # 62870
Outage | J.E.26.08.61007 | C001903752 | Christopher Edwards | KSAN | Completed | Load_242072 | Constant Spring - 310 | 2026-08-28 13:34 | 2026-08-28 13:35 | 2026-08-28 14:11 | 2026-08-28 14:12 | 2026-08-28 14:43 | 2026-08-28 16:08 | 2026-08-28 16:08 | 2026-08-28 16:08 |  |  | Fair | No | Splice and retention damage # 6 service wire Using (60ft #6 service wire(3) one bolt clamps
Outage | J.E.26.08.61875 | C001903764 | Derrick Grubb | St.Thomas | Completed | Load_326016 | Lysson - 410 | 2026-08-28 13:40 | 2026-08-28 15:08 | 2026-08-28 16:11 | 2026-08-28 16:12 | 2026-08-28 16:43 | 2026-08-28 17:11 | 2026-08-28 17:11 | 2026-08-28 17:11 | BrokenWire |  | Fair | No | Splice and retention one pole span of open secondary lower phase using approximately 10ft of #2aaa wire, two automatic splicing sleeve and a one bolt clamp. Voltage readings when leaving 117v, 118v, 233v.
Outage | J.E.26.08.62194 | C001903794 | Floyd Taylor | Trelawny | Completed | Load_268589 | Greenwood - 110 | 2026-08-28 14:12 | 2026-08-28 14:28 | 2026-08-28 15:35 | 2026-08-28 15:35 | 2026-08-28 17:09 | 2026-08-28 19:08 | 2026-08-28 19:08 | 2026-08-28 19:08 | BrokenWire |  | Fair | No | Isolated 25kva transformer,splice and retention 3span of secondary conductor using 40ft of #2aac and 4 pg clamps, voltage reading 116,118,234
Outage | J.E.26.08.62283 | C001903796 | Floyd Taylor | Trelawny | Completed | Load_239446 | Greenwood - 210 | 2026-08-28 14:16 | 2026-08-28 16:22 | 2026-08-28 19:53 | 2026-08-28 23:07 | 2026-08-28 23:07 | 2026-08-28 23:07 | 2026-08-28 23:08 | 2026-08-28 23:08 | Fire |  | Fair | No | Found ok , contacted customer and was informed report was made last week and their connection was restored
Non-Outage | J.E.26.08.61670 | C001903861 | Derrick Grubb | St.Thomas | Completed | Load_326016 | Lysson - 410 | 2026-08-28 15:05 | 2026-08-28 15:07 | 2026-08-28 17:12 | 2026-08-28 17:12 | 2026-08-28 17:12 | 2026-08-28 17:13 | 2026-08-28 17:13 | 2026-08-28 17:13 |  |  | Fair | No | Duplicate.
Non-Outage | J.E.26.08.61769 | C001903860 | Derrick Grubb | St.Thomas | Completed | Load_577267 | Good Year - 210 | 2026-08-28 15:05 | 2026-08-28 15:07 | 2026-08-28 17:24 | 2026-08-28 17:25 | 2026-08-28 18:54 | 2026-08-28 19:36 | 2026-08-28 19:36 | 2026-08-28 19:36 |  |  | Fair | No | Customer meter pothead covered with vines. Daylight attention required.
Non-Outage | J.E.26.08.61166 | C001903863 | Derrick Grubb | St.Thomas | Completed | Load_252054 | Good Year - 210 | 2026-08-28 15:06 | 2026-08-28 15:07 | 2026-08-28 20:19 | 2026-08-28 20:19 | 2026-08-28 20:20 | 2026-08-28 20:49 | 2026-08-28 20:49 | 2026-08-28 20:49 |  |  | Fair | No | Troubleshoot and clear corrosion at pole using a one bolt clamp. Voltage reading when leaving 117v, 118v, 236v.
Non-Outage | J.E.26.08.61666 | C001903862 | Derrick Grubb | St.Thomas | Completed | Load_348616 | Good Year - 210 | 2026-08-28 15:06 | 2026-08-28 15:07 | 2026-08-28 19:43 | 2026-08-28 19:44 | 2026-08-28 19:49 | 2026-08-28 20:16 | 2026-08-28 20:16 | 2026-08-28 20:16 |  |  | Fair | No | Troubleshoot and found customer meter defective. Replaced customer meter. Meter information was sent to field service technician Odeaney Brown.
Non-Outage | J.E.26.08.62693 | C001903880 | Damion Reid |  | Completed |  |  | 2026-08-28 15:22 | 2026-08-29 07:14 | 2026-08-29 09:22 | 2026-08-29 09:23 | 2026-08-29 10:20 | 2026-08-29 10:39 | 2026-08-29 10:40 | 2026-08-29 10:40 |  |  | Fair | No | Area found ok
Outage | J.E.26.08.61773 | C001903888 | Richard Samuda | Manchester | Completed | Load_295289 | Spur Tree - 310 | 2026-08-28 15:26 | 2026-08-29 07:13 | 2026-08-29 09:35 | 2026-08-29 10:00 | 2026-08-29 10:11 | 2026-08-29 11:12 | 2026-08-29 11:12 | 2026-08-29 11:12 | BrokenWire |  | Fair | No | Changed customer service wire that was defective using 25feet of #4 service wire and two 1bolt clamps voltage 116/118/234 customer back to normal
Outage | J.E.26.08.62255 | C001903889 | Christopher Edwards | KSAN | Completed | Load_292076 | Constant Spring - 310 | 2026-08-28 15:26 | 2026-08-28 15:41 | 2026-08-28 16:08 | 2026-08-28 17:36 | 2026-08-28 18:32 | 2026-08-28 19:03 | 2026-08-28 19:04 | 2026-08-28 19:04 |  |  | Fair | No | Reset 25 kva transformer
Outage | J.E.26.08.62559 | C001903887 | Barnett Brown | Manchester | Completed | Load_258254 | Spur Tree - 310 | 2026-08-28 15:26 | 2026-08-28 15:27 | 2026-08-28 16:29 | 2026-08-28 16:29 | 2026-08-28 17:28 | 2026-08-28 18:36 | 2026-08-28 18:39 | 2026-08-28 18:39 |  |  | Fair | No | Remade service joints at secondary line, voltage 115 116 231
Outage | J.E.26.08.61634 | C001903895 | Rochaine Palmer | KSAN | Completed | Load_242220 | Constant Spring - 210 | 2026-08-28 15:27 | 2026-08-28 15:40 | 2026-08-28 18:45 | 2026-08-28 18:45 | 2026-08-28 19:01 | 2026-08-28 19:10 | 2026-08-28 19:11 | 2026-08-28 19:11 | BrokenPole |  | Fair | No | Broken pole is customer private meter pole customer advised to get on electrician.
Outage | J.E.26.08.59187 | C001903904 | Rusean Allen | KSAS | Completed | Load_238333 | Greenwich - 510 | 2026-08-28 15:29 | 2026-08-28 15:30 | 2026-08-28 20:10 | 2026-08-28 20:11 | 2026-08-28 20:13 | 2026-08-28 20:14 | 2026-08-28 20:14 | 2026-08-28 20:14 | BrokenPole |  | Fair | No | Premises okay
Outage | J.E.26.08.61400 | C001903905 | Rusean Allen | KSAS | Completed | Load_262127 | Greenwich - 410 | 2026-08-28 15:29 | 2026-08-28 15:30 | 2026-08-28 19:24 | 2026-08-28 19:24 | 2026-08-28 19:24 | 2026-08-28 19:28 | 2026-08-28 19:28 | 2026-08-28 19:28 |  |  | Fair | No | Found okay
Outage | J.E.26.08.61633 | C001903909 | Rusean Allen | KSAS | Completed | Load_262254 | Greenwich - 310 | 2026-08-28 15:29 | 2026-08-28 15:30 | 2026-08-28 19:24 | 2026-08-28 19:29 | 2026-08-28 19:36 | 2026-08-28 19:36 | 2026-08-28 19:37 | 2026-08-28 19:37 |  |  | Fair | No | Not located
Outage | J.E.26.08.61956 | C001903910 | Lancelot Brown | Hanover | Completed | Load_576848 | Orange Bay - 310 | 2026-08-28 15:29 | 2026-08-28 15:33 | 2026-08-28 15:44 | 2026-08-28 18:45 | 2026-08-28 18:59 | 2026-08-28 19:10 | 2026-08-28 19:10 | 2026-08-28 19:10 |  |  | Rains | No | Found 25kva fuse blown cause by lightning and rain replace 1-2amps fuse at 25kva no pole number supply restore
Outage | J.E.26.08.62047 | C001903908 | Lancelot Brown | Hanover | Completed | Load_254006 | Orange Bay - 210 | 2026-08-28 15:29 | 2026-08-28 15:33 | 2026-08-28 15:44 | 2026-08-28 19:12 | 2026-08-28 19:57 | 2026-08-28 20:09 | 2026-08-28 20:09 | 2026-08-28 20:09 |  |  | Rains | No | Found junction fuse blown cause by lightning and rain replace 1-15amps junction fuse no pole number supply restore
Outage | J.E.26.08.62334 | C001903903 | Rusean Allen | KSAS | Completed | Load_261329 | Greenwich - 510 | 2026-08-28 15:29 | 2026-08-28 15:30 | 2026-08-28 19:37 | 2026-08-28 19:38 | 2026-08-28 19:42 | 2026-08-28 20:10 | 2026-08-28 20:10 | 2026-08-28 20:10 |  |  | Fair | No | Burnt clamp found at pole, clamp was changed.
Outage | J.E.26.08.62402 | C001903906 | Lancelot Brown | Hanover | Completed | Load_247084 | Orange Bay - 310 | 2026-08-28 15:29 | 2026-08-28 15:33 | 2026-08-28 15:44 | 2026-08-28 16:52 | 2026-08-28 17:27 | 2026-08-28 17:34 | 2026-08-28 17:34 | 2026-08-28 17:34 |  |  | Rains | No | Found 25kva fuse blown patroll found nothing customer said lightning flash and supply went replace 1-3amps fuse at 25kva no pole number supply restore
Outage | J.E.26.08.62694 | C001903902 | Lancelot Brown | Hanover | Completed | Load_252053 | Orange Bay - 210 | 2026-08-28 15:29 | 2026-08-28 15:39 | 2026-08-28 15:44 | 2026-08-28 20:57 | 2026-08-28 20:56 | 2026-08-28 20:57 | 2026-08-28 20:57 | 2026-08-28 20:57 |  |  | Rains | No | This call related to 20amps junction fuse no pole number supply restore
Outage | J.E.26.08.62848 | C001903900 | Rusean Allen | KSAS | Completed | Load_289826 | Greenwich - 510 | 2026-08-28 15:29 | 2026-08-28 15:30 | 2026-08-28 17:11 | 2026-08-28 17:26 | 2026-08-28 18:09 | 2026-08-28 18:37 | 2026-08-28 18:37 | 2026-08-28 18:37 |  |  | Fair | No | 1x 40amp fuse found 1x 40amp fuse replaced.1x 20amp fuse found 1x 20amp fuse replaced.1x 2amp fuse found 1x 2amp fuse replaced.
Non-Outage | J.E.26.08.57642 | C001903912 | Lancelot Brown |  | Completed |  |  | 2026-08-28 15:30 | 2026-08-28 15:33 | 2026-08-28 15:44 | 2026-08-28 16:48 | 2026-08-28 16:48 | 2026-08-28 16:48 | 2026-08-28 16:49 | 2026-08-28 16:49 |  |  | Rains | No | This call related to 3amps fuse at 25kva supply restore
Outage | J.E.26.08.62732 | C001903911 | Andre Smith | KSAS | Completed | Load_266609 | Cane River - 310 | 2026-08-28 15:30 | 2026-08-28 15:33 | 2026-08-28 21:35 | 2026-08-28 21:35 | 2026-08-28 21:41 | 2026-08-28 21:41 | 2026-08-28 21:41 | 2026-08-28 21:41 |  |  | Fair | No | Replace blown junction fuse 5A supply restored
Outage | J.E.26.08.54818 | C001903913 | Horace Malcolm | Hanover | Completed | Load_244447 | Orange Bay - 310 | 2026-08-28 15:32 | 2026-08-28 20:03 | 2026-08-28 23:50 | 2026-08-28 23:50 | 2026-08-28 23:59 | 2026-08-29 00:09 | 2026-08-29 00:09 | 2026-08-29 00:09 |  |  | Fair | No | Check and found plaza with supply voltage at pothead 114-115-229
Outage | J.E.26.08.57689 | C001903927 | Andre Smith | KSAS | Completed | Load_243276 | Cane River - 610 | 2026-08-28 15:33 | 2026-08-28 15:34 | 2026-08-28 20:20 | 2026-08-28 20:20 | 2026-08-28 21:05 | 2026-08-28 21:34 | 2026-08-28 21:35 | 2026-08-28 21:35 |  |  | Fair | No | Premises found okay supply restored already transformer replace
Outage | J.E.26.08.61815 | C001903928 | Andre Smith | KSAS | Completed | Load_248877 | Cane River - 610 | 2026-08-28 15:33 | 2026-08-28 15:34 | 2026-08-28 17:54 | 2026-08-28 17:55 | 2026-08-28 18:08 | 2026-08-28 20:19 | 2026-08-28 20:19 | 2026-08-28 20:19 |  |  | Fair | No | Replace defective 25kva transformer supply restored
Outage | J.E.26.08.61260 | C001903933 | Marlon Authors | St.Elizabeth | Completed | Load_265728 | Maggotty - 110 | 2026-08-28 15:36 | 2026-08-28 15:38 | 2026-08-28 20:33 | 2026-08-28 20:34 | 2026-08-28 20:33 | 2026-08-28 20:35 | 2026-08-28 20:38 | 2026-08-28 20:38 |  |  | Fair | No | Customer said a JPS personnel called her today to verify status of supply.
Outage | J.E.26.08.61746 | C001903929 | Marlon Authors | St.Elizabeth | Completed | Load_258200 | Maggotty - 110 | 2026-08-28 15:36 | 2026-08-28 15:38 | 2026-08-28 21:21 | 2026-08-28 21:22 | 2026-08-28 21:21 | 2026-08-28 21:23 | 2026-08-28 21:23 | 2026-08-28 21:23 | BrokenWire |  | Fair | No | Unable to locate and customer is not answering the phone.
Outage | J.E.26.08.62102 | C001903932 | Lancelot Brown | Hanover | Completed | Load_302837 | Orange Bay - 310 | 2026-08-28 15:36 | 2026-08-28 15:37 | 2026-08-28 15:44 | 2026-08-28 17:43 | 2026-08-28 18:11 | 2026-08-28 18:25 | 2026-08-28 18:26 | 2026-08-28 18:26 |  |  | Rains | No | Found junction fuse blown patroll found palm lim contact with primary line cut and remove palm lim from primary line replace 1-15amps junction fuse no pole number supply restore
Outage | J.E.26.08.62226 | C001903930 | Marlon Authors | Manchester | Completed | Load_240173 | Spur Tree - 210 | 2026-08-28 15:36 | 2026-08-28 15:38 | 2026-08-28 19:04 | 2026-08-28 19:04 | 2026-08-28 19:33 | 2026-08-28 19:37 | 2026-08-28 19:42 | 2026-08-28 19:42 | BrokenWire |  | Fair | No | Supply check and found working okay reading 110v, 107v and cross phase 217volts.
Outage | J.E.26.08.62350 | C001903931 | Marlon Authors | St.Elizabeth | Completed | Load_292028 | Maggotty - 110 | 2026-08-28 15:36 | 2026-08-28 15:38 | 2026-08-28 22:06 | 2026-08-28 22:07 | 2026-08-28 22:06 | 2026-08-28 22:09 | 2026-08-28 22:09 | 2026-08-28 22:09 |  |  | Fair | No | Please refer this call to the field services department.
Outage | J.E.26.08.61672 | C001903946 | Derrick Dawkins | St.James | Completed | Load_251737 | Queens Drive - 810 | 2026-08-28 15:41 | 2026-08-28 23:34 | 2026-08-28 23:58 | 2026-08-28 23:59 | 2026-08-29 00:40 | 2026-08-29 23:56 | 2026-08-29 00:45 | 2026-08-29 00:45 |  |  | Fair | Yes | Check and found area ok and found premises closed
Outage | J.E.26.08.62343 | C001903944 | Romeo Brissett | St.James | Completed | Load_260155 | Queens Drive - 710 | 2026-08-28 15:41 | 2026-08-28 15:43 | 2026-08-28 20:18 | 2026-08-28 20:18 | 2026-08-28 20:51 | 2026-08-28 22:00 | 2026-08-28 22:11 | 2026-08-28 22:11 |  |  | Fair | No | Isolated (1)25 kva transformer fuse, removed illegal connections repaired transformer drop lead.
Outage | J.E.26.08.62617 | C001903943 | Romeo Brissett | St.James | Completed | Load_257840 | Queens Drive - 710 | 2026-08-28 15:41 | 2026-08-28 15:43 | 2026-08-29 17:13 | 2026-08-29 17:14 | 2026-08-29 17:33 | 2026-08-29 17:40 | 2026-08-29 17:44 | 2026-08-29 17:44 | LeaningPole |  | Fair | No | Team member suan miller stated he just went on this call and already send a report about the leaning pole.
Outage | J.E.26.08.62946 | C001903942 | Romeo Brissett | St.James | Completed | Load_256979 | Bogue - 310 | 2026-08-28 15:41 | 2026-08-28 15:43 | 2026-08-28 19:18 | 2026-08-28 19:18 | 2026-08-28 20:07 | 2026-08-28 20:10 | 2026-08-28 20:17 | 2026-08-28 20:17 |  |  | Fair | No | Found customer service wire dislodged and missing due to hurricane Melissa, need 250ft of #6 and junction switch need to be connected for the transformer circuit. Please send to field service department to install service wire and send to emergency bucket truck team to reconnect switch need 5ft of copper..
Outage | J.E.26.08.61498 | C001903947 | Derrick Dawkins | St.James | Completed | Load_266792 | Queens Drive - 710 | 2026-08-28 15:42 | 2026-08-28 23:06 | 2026-08-28 23:41 | 2026-08-29 03:51 | 2026-08-29 03:50 | 2026-08-29 03:54 | 2026-08-29 03:55 | 2026-08-29 03:55 |  |  | Fair | No | Can’t locate customer
Outage | J.E.26.08.61843 | C001903954 | Floyd Taylor | Trelawny | Completed | Load_249410 | Greenwood - 210 | 2026-08-28 15:44 | 2026-08-28 15:45 | 2026-08-28 19:53 | 2026-08-28 23:00 | 2026-08-28 23:04 | 2026-08-28 23:05 | 2026-08-28 23:07 | 2026-08-28 23:07 |  |  | Fair | No | Found ok , contacted customer and was informed report was made last week and their connection was restored
Outage | J.E.26.08.60994 | C001903956 | Antony Levy | KSAS | Completed | Load_579135 | Duhaney - 310 | 2026-08-28 15:46 | 2026-08-28 15:50 | 2026-08-28 15:54 | 2026-08-28 16:19 | 2026-08-28 16:32 | 2026-08-28 16:39 | 2026-08-28 16:40 | 2026-08-28 16:40 |  |  | Fair | No | Premises closed
Outage | J.E.26.08.62636 | C001903963 | Tyrese Williams | St.Ann | Completed | Load_241608 | Cardiff Hall - 210 | 2026-08-28 15:51 | 2026-08-28 15:52 | 2026-08-28 19:41 | 2026-08-28 19:42 | 2026-08-28 20:33 | 2026-08-28 20:42 | 2026-08-28 20:42 | 2026-08-28 20:42 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.62659 | C001903964 | Tyrese Williams | St.Ann | Completed | Load_255328 | Cardiff Hall - 310 | 2026-08-28 15:51 | 2026-08-28 15:52 | 2026-08-28 17:25 | 2026-08-28 19:37 | 2026-08-28 19:39 | 2026-08-28 19:39 | 2026-08-28 19:40 | 2026-08-28 19:40 |  |  | Fair | No | Replace a 20amp junction fuse at pole
Outage | J.E.26.08.62855 | C001903965 | Tyrese Williams | St.Ann | Completed | Load_242962 | Cardiff Hall - 310 | 2026-08-28 15:51 | 2026-08-28 15:52 | 2026-08-28 17:25 | 2026-08-28 18:25 | 2026-08-28 19:32 | 2026-08-28 19:36 | 2026-08-28 19:36 | 2026-08-28 19:36 |  |  | Fair | No | Replace a 20amp junction fuse at pole
Outage | J.E.26.08.62884 | C001903973 | Raymond Lewis | St.Ann | Completed | Load_263588 | Roaring River - 210 | 2026-08-28 15:52 | 2026-08-28 15:53 | 2026-08-28 17:23 | 2026-08-28 17:24 | 2026-08-28 18:22 | 2026-08-28 18:23 | 2026-08-28 18:23 | 2026-08-28 18:23 |  |  | Fair | No | Premises found with supply
Outage | J.E.26.08.62923 | C001903967 | Raymond Lewis | St.Ann | Completed | Load_252446 | Roaring River - 410 | 2026-08-28 15:52 | 2026-08-28 15:53 | 2026-08-28 16:33 | 2026-08-28 16:34 | 2026-08-28 17:21 | 2026-08-28 17:23 | 2026-08-28 17:23 | 2026-08-28 17:23 |  |  | Fair | No | Supply restored
Outage | J.E.26.08.62979 | C001903975 | Marlon Authors | Manchester | Completed | Load_264334 | Spur Tree - 210 | 2026-08-28 15:53 | 2026-08-28 15:54 | 2026-08-28 16:07 | 2026-08-28 16:08 | 2026-08-28 16:18 | 2026-08-28 16:43 | 2026-08-28 16:44 | 2026-08-28 16:44 |  |  | Fair | No | Patrol and found clear. Replace one blown 10amp fuse that protects 100kva transformer in a back of three. Supply leave working okay.
Outage | J.E.26.08.62991 | C001903981 | Christopher Edwards | KSAN | Completed | Load_268197 | Constant Spring - 410 | 2026-08-28 15:59 | 2026-08-28 16:01 | 2026-08-28 19:35 | 2026-08-28 19:36 | 2026-08-28 19:35 | 2026-08-28 20:23 | 2026-08-28 20:23 | 2026-08-28 20:23 | BrokenWire |  | Fair | No | Remake burnt phase and neutral joint at pole Using (2) one bolt clamps Voltage:114,115,230v
Non-Outage | J.E.26.08.28911 | C001903986 | Radcliffe Coleman | St.Catherine | Completed | Load_255976 | Tredegar - 410 | 2026-08-28 16:05 | 2026-08-28 16:23 | 2026-08-28 21:10 | 2026-08-28 21:10 | 2026-08-28 22:07 | 2026-08-28 22:08 | 2026-08-28 22:08 | 2026-08-28 22:08 |  |  | Fair | No | Premises closed.
Non-Outage | J.E.26.08.28970 | C001903985 | Radcliffe Coleman | St.Catherine | Completed | Load_255976 | Tredegar - 410 | 2026-08-28 16:05 | 2026-08-28 16:23 | 2026-08-28 22:09 | 2026-08-28 22:09 | 2026-08-28 22:09 | 2026-08-28 22:09 | 2026-08-28 22:10 | 2026-08-28 22:10 |  |  | Fair | No | Premises closed
Outage | J.E.26.08.62329 | C001903990 | Javid Vernon | Westmoreland | Completed | Load_256472 | Paradise - 110 | 2026-08-28 16:11 | 2026-08-28 16:12 | 2026-08-28 16:43 | 2026-08-28 16:46 | 2026-08-28 18:18 | 2026-08-28 18:47 | 2026-08-28 18:47 | 2026-08-28 18:47 |  |  | Rains | No | Refuse one 8amp junction fuse
Outage | J.E.26.08.63096 | C001903991 | Richman Whyte | Westmoreland | Completed | Load_250446 | Paradise - 210 | 2026-08-28 16:11 | 2026-08-29 07:50 | 2026-08-29 10:10 | 2026-08-29 10:10 | 2026-08-29 10:39 | 2026-08-29 11:06 | 2026-08-29 11:07 | 2026-08-29 11:07 |  |  | Fair | No | Remake burn off secondary jumper use three one bolt clamps voltage 116 116 232
Outage | J.E.26.08.62561 | C001903992 | Donald Cunningham | St.Catherine | Completed | Load_264133 | New Michelton - 210 | 2026-08-28 16:12 | 2026-08-29 07:29 | 2026-08-29 10:44 | 2026-08-29 10:45 | 2026-08-29 11:33 | 2026-08-29 12:13 | 2026-08-29 12:15 | 2026-08-29 12:15 |  |  | Fair | No | Blown transformer fuse across from 62 king street bank of tree 50/100 kva replace 8 amp fuse
Non-Outage | J.E.26.08.61024 | C001904000 | Oshane Warren |  | Completed |  |  | 2026-08-28 16:13 | 2026-08-28 16:14 | 2026-08-28 17:20 | 2026-08-28 17:20 | 2026-08-28 18:24 | 2026-08-28 18:46 | 2026-08-28 18:47 | 2026-08-28 18:47 |  |  | Rains | No | Internal problem advice to fix voltage found on left 116 121 238
Non-Outage | J.E.26.08.56436 | C001904007 | Radcliffe Coleman | St.Catherine | Completed | Load_269394 | Rhodens Pen - 210 | 2026-08-28 16:18 | 2026-08-28 16:23 | 2026-08-28 17:52 | 2026-08-28 17:55 | 2026-08-28 18:54 | 2026-08-28 21:09 | 2026-08-28 21:09 | 2026-08-28 21:09 |  |  | Fair | No | Location found with a bank of two transformer giving low voltage. The line section was patrolled to see if there was any fault along the line. The bank was also isolated and the transformer checked to see whether it was defective. Closer check revealed that the transformer had tripped, it was then reset and the power restored. Voltage left at the location 117, 118, 205, 238, 234 and 235 (Voltage) respectively.
Outage | J.E.26.08.61041 | C001904008 | Raymond Carr | St.Mary | Completed | Load_240442 | Oracabessa - 210 | 2026-08-28 16:19 | 2026-08-28 16:20 | 2026-08-28 16:39 | 2026-08-28 16:39 | 2026-08-28 17:06 | 2026-08-28 02:00 | 2026-08-28 17:07 | 2026-08-28 17:07 |  |  | Fair | No | Customer reported that supply was restored earlier today.
Non-Outage | J.E.26.08.62605 | C001904009 | Evan Spaulding |  | Completed |  |  | 2026-08-28 16:20 | 2026-08-28 16:21 | 2026-08-28 18:54 | 2026-08-28 18:55 | 2026-08-28 18:54 | 2026-08-28 18:55 | 2026-08-28 18:56 | 2026-08-28 18:56 |  |  | Fair | No | Power was restored,there was a trip on the Annotto bay 310 feeder
Non-Outage | J.E.26.08.62774 | C001904010 | Evan Spaulding |  | Completed |  |  | 2026-08-28 16:20 | 2026-08-28 16:21 | 2026-08-28 18:56 | 2026-08-28 18:56 | 2026-08-28 18:56 | 2026-08-28 18:56 | 2026-08-28 18:58 | 2026-08-28 18:58 |  |  | Fair | No | Customer was restored,there on issue on the Annotto bay 310 feeder,operation team his still doing some patrol on it.
Non-Outage | J.E.26.08.62825 | C001904016 | Oshane Warren | Westmoreland | Completed | Load_239792 | Paradise - 310 | 2026-08-28 16:23 | 2026-08-28 16:24 | 2026-08-28 21:56 | 2026-08-28 21:57 | 2026-08-28 21:57 | 2026-08-28 21:57 | 2026-08-28 21:58 | 2026-08-28 21:58 |  |  | Fair | No | Customer stated power was restored
Outage | J.E.26.08.62106 | C001904015 | Wan Carlos Scarlett | Portmore | Completed | Load_259184 | Naggo Head - 510 | 2026-08-28 16:23 | 2026-08-28 16:25 | 2026-08-28 18:57 | 2026-08-28 18:57 | 2026-08-28 19:32 | 2026-08-28 20:35 | 2026-08-28 20:36 | 2026-08-28 20:36 |  |  | Fair | No | Reset customer breaker power supply has been restored
Outage | J.E.26.08.62147 | C001904017 | Wan Carlos Scarlett | St.Catherine | Completed | Load_1000333 | Twickenham - 210 | 2026-08-28 16:24 | 2026-08-28 16:25 | 2026-08-28 16:31 | 2026-08-28 16:32 | 2026-08-28 17:31 | 2026-08-28 18:55 | 2026-08-28 18:57 | 2026-08-28 18:57 | BrokenWire |  | Fair | No | Found customer service wire damage use 110ft of # 6 service wire use 3 one bolt clamps at pole use 3 Penn union at pothead reading 114-113-229
Non-Outage | J.E.26.08.49355 | C001904022 | Richard Samuda | Manchester | Completed | Load_255680 | Spur Tree - 310 | 2026-08-28 16:31 | 2026-08-29 07:13 | 2026-08-29 12:39 | 2026-08-29 12:45 | 2026-08-29 12:52 | 2026-08-29 12:56 | 2026-08-29 12:56 | 2026-08-29 12:56 |  |  | Fair | No | Customer has a damaged meter refer call to field service voltage 114, 114 228
Non-Outage | J.E.26.08.37701 | C001904023 | Shamour Haughton |  | Completed |  |  | 2026-08-28 16:32 | 2026-08-28 16:32 | 2026-08-28 18:42 | 2026-08-28 18:42 | 2026-08-28 18:42 | 2026-08-28 18:42 | 2026-08-28 18:44 | 2026-08-28 18:44 |  |  | Fair | No | Customer states that power was restored
Outage | J.E.26.08.63168 | C001904024 | Derrick Grubb | St.Thomas | Completed | Load_250144 | Good Year - 110 | 2026-08-28 16:34 | 2026-08-28 16:37 | 2026-08-28 17:21 | 2026-08-28 17:22 | 2026-08-28 17:22 | 2026-08-28 17:24 | 2026-08-28 17:24 | 2026-08-28 17:24 |  |  | Fair | No | Premises not located, several calls to customer phone went unanswered.
Outage | J.E.26.08.61398 | C001904025 | Moses Elliston | St.Catherine | Completed | Load_245608 | Twickenham - 210 | 2026-08-28 16:35 | 2026-08-28 16:36 | 2026-08-28 16:59 | 2026-08-28 17:00 | 2026-08-28 16:59 | 2026-08-28 13:10 | 2026-08-28 17:00 | 2026-08-28 17:00 |  |  | Fair | No | Credit added to previous account.
Outage | J.E.26.08.61691 | C001904026 | Wan Carlos Scarlett | Portmore | Completed | Load_239493 | Naggo Head - 610 | 2026-08-28 16:36 | 2026-08-28 16:37 | 2026-08-28 21:58 | 2026-08-28 21:58 | 2026-08-28 22:11 | 2026-08-28 22:11 | 2026-08-28 22:11 | 2026-08-28 22:11 |  |  | Fair | No | Customer not available at this time premises closed
Outage | J.E.26.08.63046 | C001904028 | Richard Samuda | Manchester | Completed | Load_238673 | Porus - 210 | 2026-08-28 16:36 | 2026-08-29 07:14 | 2026-08-29 07:24 | 2026-08-29 07:26 | 2026-08-29 07:52 | 2026-08-29 08:18 | 2026-08-29 08:18 | 2026-08-29 08:18 |  |  | Fair | No | 0204999 found 25kva transformer blown patrol line found nothing replaced fuse close line customer back to normal
Outage | J.E.26.08.63222 | C001904027 | Damion Reid | Manchester | Completed | Load_257798 | Kendal - 210 | 2026-08-28 16:36 | 2026-08-28 16:37 | 2026-08-28 19:02 | 2026-08-28 19:03 | 2026-08-28 19:45 | 2026-08-28 20:41 | 2026-08-28 20:42 | 2026-08-28 20:42 |  |  | Fair | No | Blown 20amp junction fuse found cause by lightning line patrol and replace blown fuse
Outage | J.E.26.08.63266 | C001904034 | Lancelot Brown | Westmoreland | Completed | Load_239066 | Paradise - 210 | 2026-08-28 16:42 | 2026-08-28 16:43 | 2026-08-28 19:11 | 2026-08-28 20:13 | 2026-08-28 20:25 | 2026-08-28 20:55 | 2026-08-28 20:56 | 2026-08-28 20:56 |  |  | Rains | No | Found junction fuse blown patroll found nothing caused by lightning and rain replace 1-20amps junction fuse no pole number supply restore
Outage | J.E.26.08.62870 | C001904042 | Hartley Chin | Clarendon | Completed | Load_1002600 | Parnassus - 310 | 2026-08-28 17:06 | 2026-08-28 17:08 | 2026-08-28 17:34 | 2026-08-28 17:39 | 2026-08-28 18:30 | 2026-08-28 19:22 | 2026-08-28 19:29 | 2026-08-28 19:29 |  |  | Fair | No | Isolate 25 KVA transformer @ pole # 0125582 due to broken open secondary neutral found , repair broken joint , change X2 drop lead clamp … re-energized transformer…
Non-Outage | J.E.26.08.35449 | C001904047 | Hartley Chin | Clarendon | Completed | Load_268922 | Parnassus - 310 | 2026-08-28 17:07 | 2026-08-28 17:08 | 2026-08-28 19:31 | 2026-08-28 19:32 | 2026-08-28 19:45 | 2026-08-28 19:53 | 2026-08-28 19:55 | 2026-08-28 19:55 | Fire |  | Fair | No | Premisis found ok. Customer stated that the issue was resolved.
Non-Outage | J.E.26.08.42628 | C001904045 | Hartley Chin | Clarendon | Completed | Load_263749 | Parnassus - 310 | 2026-08-28 17:07 | 2026-08-28 17:08 | 2026-08-28 22:26 | 2026-08-28 22:27 | 2026-08-28 22:52 | 2026-08-28 22:58 | 2026-08-28 23:05 | 2026-08-28 23:05 |  |  | Fair | No | Prem. Not found ,unable to contact customer with cu# provided…
Non-Outage | J.E.26.08.47962 | C001904046 | Hartley Chin | Clarendon | Completed | Load_257473 | Parnassus - 310 | 2026-08-28 17:07 | 2026-08-28 17:08 | 2026-08-28 19:31 | 2026-08-28 20:01 | 2026-08-28 21:07 | 2026-08-28 21:14 | 2026-08-28 21:19 | 2026-08-28 21:19 | LeaningPole |  | Fair | No | Ref to maintenance!!! Found leaning 35 ft pole with single phase Primary and 2/0 twisted.. pole foot is okay , pole only needs to be straighten … maintenance to repair… .
Non-Outage | J.E.26.08.62429 | C001904044 | Hartley Chin | Clarendon | Completed | Load_245721 | Parnassus - 310 | 2026-08-28 17:07 | 2026-08-28 17:08 | 2026-08-28 21:19 | 2026-08-28 21:20 | 2026-08-28 21:48 | 2026-08-28 22:05 | 2026-08-28 22:26 | 2026-08-28 22:26 |  |  | Fair | No | Found okay voltage read 111v , 113v ..
Non-Outage | J.E.26.08.63281 | C001904043 | Hartley Chin | Clarendon | Completed | Load_259178 | Parnassus - 310 | 2026-08-28 17:07 | 2026-08-28 17:08 | 2026-08-28 17:34 | 2026-08-28 19:31 | 2026-08-28 19:30 | 2026-08-28 19:31 | 2026-08-28 19:31 | 2026-08-28 19:31 |  |  | Fair | No | Call related to 62870 ..
Outage | J.E.26.08.63307 | C001904049 | Javid Vernon | Westmoreland | Completed | Load_241469 | Paradise - 210 | 2026-08-28 17:11 | 2026-08-28 17:12 | 2026-08-28 18:47 | 2026-08-28 18:47 | 2026-08-28 19:57 | 2026-08-28 21:06 | 2026-08-28 21:07 | 2026-08-28 21:07 | LowHangingWires,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Rains | No | Isolate one 50kva transformer to splice and retention one pole span secondary phase use 10feet #2 conductor ,two clamps and reclose transformer
Outage | J.E.26.08.63318 | C001904048 | Oshane Warren | Westmoreland | Completed | Load_239978 | Paradise - 310 | 2026-08-28 17:11 | 2026-08-28 17:11 | 2026-08-28 18:48 | 2026-08-28 18:48 | 2026-08-28 21:25 | 2026-08-28 21:39 | 2026-08-28 21:42 | 2026-08-28 21:42 |  | Y | Fair | No | Replace two 50amp and two 25amp junction fuse
Outage | J.E.26.08.63417 | C001904061 | Collin Robinson | Portland | Completed | Load_352475 | Port Antonio - 410 | 2026-08-28 17:30 | 2026-08-28 17:31 | 2026-08-28 18:09 | 2026-08-28 18:09 | 2026-08-28 19:40 | 2026-08-28 19:42 | 2026-08-28 19:42 | 2026-08-28 19:42 |  |  | Fair | No | Premises found with supply
Non-Outage | J.E.26.08.61942 | C001904065 | Collin Robinson | Portland | Completed | Load_248509 | Port Antonio - 410 | 2026-08-28 17:31 | 2026-08-28 17:32 | 2026-08-28 20:37 | 2026-08-28 20:37 | 2026-08-28 21:52 | 2026-08-28 22:15 | 2026-08-28 22:15 | 2026-08-28 22:15 |  |  | Fair | No | Change corroded grease nipple at pothead Voltage reading 115v 115v 230v
Non-Outage | J.E.26.08.62841 | C001904063 | Collin Robinson | Portland | Completed | Load_253764 | Port Antonio - 310 | 2026-08-28 17:31 | 2026-08-28 17:32 | 2026-08-28 19:44 | 2026-08-28 19:44 | 2026-08-28 20:28 | 2026-08-28 20:36 | 2026-08-28 20:36 | 2026-08-28 20:36 |  |  | Fair | No | Change two corroded one bolt clamp at pole Voltage reading 118v 118v 236v
Non-Outage | J.E.26.08.63452 | C001904064 | Collin Robinson | Portland | Completed | Load_350322 | Port Antonio - 310 | 2026-08-28 17:31 | 2026-08-28 17:32 | 2026-08-29 11:13 | 2026-08-29 11:14 | 2026-08-29 12:45 | 2026-08-29 12:53 | 2026-08-29 12:53 | 2026-08-29 12:53 |  |  | Fair | No | Change two corroded one bolt clamp at pothead Voltage reading 118v 117v 235v
Outage | J.E.26.08.63449 | C001904062 | Marlon Authors | Manchester | Completed | Load_247593 | Spur Tree - 210 | 2026-08-28 17:31 | 2026-08-28 17:32 | 2026-08-28 18:48 | 2026-08-28 18:49 | 2026-08-28 18:48 | 2026-08-28 18:58 | 2026-08-28 19:00 | 2026-08-28 19:00 |  |  | Fair | No | Patrol and found one broken 35ft TA wooden pole and secondary conductors banging. Isolate and close 25kva transformer circuit no pole # to retention secondary neutral. Restored supply okay. Please refer same to the maintenance department for replacement.
Outage | J.E.26.08.63416 | C001904069 | Oshane Warren | St.Elizabeth | Completed | Load_557819 | Maggotty - 110 | 2026-08-28 17:36 | 2026-08-28 17:37 | 2026-08-28 21:49 | 2026-08-28 21:49 | 2026-08-28 21:49 | 2026-08-28 21:49 | 2026-08-28 21:50 | 2026-08-28 21:50 |  |  | Fair | No | Unable to locate or contact customer
Outage | J.E.26.08.63422 | C001904068 | Oshane Warren | St.Elizabeth | Completed | Load_570225 | Maggotty - 110 | 2026-08-28 17:36 | 2026-08-28 17:37 | 2026-08-28 21:39 | 2026-08-28 22:01 | 2026-08-28 22:00 | 2026-08-28 22:01 | 2026-08-28 22:04 | 2026-08-28 22:04 |  |  | Fair | No | Hexing metering system customer got disconnected for none payment of bill however customer cleared the outstanding amount an request a reconnection
Outage | J.E.26.08.63517 | C001904076 | Rusean Allen | KSAS | Completed | Load_266848 | Greenwich - 510 | 2026-08-28 17:52 | 2026-08-28 17:52 | 2026-08-28 18:17 | 2026-08-28 18:38 | 2026-08-28 19:00 | 2026-08-28 19:19 | 2026-08-28 19:20 | 2026-08-28 19:20 |  |  | Fair | No | 1x 30amp fuse found 1x 30amp fuse replaced.1x 10amp fuse found 1x 10amp fuse replaced.
Outage | J.E.26.08.63532 | C001904077 | Rochaine Palmer | KSAN | Completed | Load_249412 | Constant Spring - 210 | 2026-08-28 17:52 | 2026-08-28 17:52 | 2026-08-28 19:11 | 2026-08-28 19:11 | 2026-08-28 20:19 | 2026-08-28 20:20 | 2026-08-28 20:25 | 2026-08-28 20:25 |  |  | Fair | No | Found one 30 amps junction fuse blown at pole #0011076. Refused using one 30 amps fuse and reclosed junction switch.
Outage | J.E.26.08.63655 | C001904083 | Christopher Edwards | KSAN | Completed | Load_258268 | Constant Spring - 410 | 2026-08-28 18:00 | 2026-08-28 18:01 | 2026-08-28 20:23 | 2026-08-28 20:24 | 2026-08-28 21:43 | 2026-08-28 22:20 | 2026-08-28 22:21 | 2026-08-28 22:21 |  |  | Fair | No | Remake burnt phase joint at pole Using (1) one bolt clamps
Non-Outage | J.E.26.08.63231 | C001904087 | Floyd Taylor | Trelawny | Completed | Load_244212 | Greenwood - 210 | 2026-08-28 18:23 | 2026-08-28 18:23 | 2026-08-28 19:55 | 2026-08-28 20:52 | 2026-08-28 21:05 | 2026-08-28 22:52 | 2026-08-28 22:54 | 2026-08-28 22:54 | BrokenWire |  | Fair | No | Isolated 25kva transformer and splice and retention 2 span of secondary conductor using 39ft of #2aac and 4pg clamps voltage readings left 115,113,230
Outage | J.E.26.08.63767 | C001904088 | Milton Charlton | KSAN | Completed | Load_255951 | Hope - 410 | 2026-08-28 18:32 | 2026-08-28 18:33 | 2026-08-28 18:37 | 2026-08-28 18:38 | 2026-08-28 18:57 | 2026-08-28 19:20 | 2026-08-28 19:03 | 2026-08-28 19:03 |  |  | Fair | No | Customer is fed from Hexing box and is getting no supply from the box. JPS escalation is unable to reconnect meter. Meter not responding. Refer to field service.
Outage | J.E.26.08.63507 | C001904090 | Floyd Taylor | Trelawny | Completed | Load_239446 | Greenwood - 210 | 2026-08-28 18:35 | 2026-08-28 18:36 | 2026-08-28 19:09 | 2026-08-28 19:10 | 2026-08-28 20:26 | 2026-08-28 20:27 | 2026-08-28 20:30 | 2026-08-28 20:30 | BrokenWire |  | Fair | No | Unable to locate customer
Outage | J.E.26.08.63311 | C001904091 | Derrick Grubb | St.Thomas | Completed | Load_326016 | Lysson - 410 | 2026-08-28 18:37 | 2026-08-28 18:43 | 2026-08-28 20:53 | 2026-08-28 20:54 | 2026-08-28 20:53 | 2026-08-28 20:55 | 2026-08-28 20:55 | 2026-08-28 20:55 |  |  | Fair | No | No directions in notes, several calls to customer phone went unanswered.
Outage | J.E.26.08.63802 | C001904092 | Horace Malcolm | St.James | Completed | Load_255565 | Bogue - 510 | 2026-08-28 18:44 | 2026-08-28 20:03 | 2026-08-28 21:23 | 2026-08-28 21:24 | 2026-08-28 22:01 | 2026-08-28 23:01 | 2026-08-28 23:01 | 2026-08-28 23:01 |  |  | Rains | No | Refused two 40amp junction fuses
Outage | J.E.26.08.63782 | C001904095 | Wan Carlos Scarlett | St.Catherine | Completed | Load_263723 | Twickenham - 210 | 2026-08-28 18:57 | 2026-08-28 18:58 | 2026-08-28 20:36 | 2026-08-28 20:36 | 2026-08-28 21:20 | 2026-08-28 21:57 | 2026-08-28 21:58 | 2026-08-28 21:58 | BrokenWire |  | Fair | No | Found customer 2 wire service at pole with the phase corroded use one bolt clamp at open secondary line phase reading 115
Outage | J.E.26.08.63915 | C001904097 | Andre Williams | Trelawny | Completed | Load_293051 | Greenwood - 210 | 2026-08-28 18:58 | 2026-08-29 07:56 | 2026-08-29 08:17 | 2026-08-29 08:24 | 2026-08-29 08:58 | 2026-08-29 09:10 | 2026-08-29 09:10 | 2026-08-29 09:10 | Fire |  | Fair | No | Splice and retention 20 ft broken #6 3 wire service conductor, voltage 115+113=228
Outage | J.E.26.08.63968 | C001904096 | Andre Williams | Trelawny | Completed | Load_262739 | Duncans - 210 | 2026-08-28 18:58 | 2026-08-29 07:56 | 2026-08-29 09:11 | 2026-08-29 09:20 | 2026-08-29 09:19 | 2026-08-29 09:20 | 2026-08-29 09:21 | 2026-08-29 09:21 |  |  | Fair | No | Unable to locate customer phone not answering and other # cast state they no longer live in Duncan’s hill
Outage | J.E.26.08.64085 | C001904099 | Floyd Taylor | Trelawny | Completed | Load_244212 | Greenwood - 210 | 2026-08-28 19:06 | 2026-08-28 22:48 | 2026-08-28 23:22 | 2026-08-28 23:22 | 2026-08-28 23:22 | 2026-08-28 23:29 | 2026-08-28 23:29 | 2026-08-28 23:29 | BrokenWire |  | Fair | No | Customer connection was restored, report was made while Issue was being fixed in the same area
Outage | J.E.26.08.63365 | C001904100 | Damion Reid | Manchester | Completed | Load_243578 | Kendal - 210 | 2026-08-28 19:08 | 2026-08-29 07:11 | 2026-08-29 07:42 | 2026-08-29 07:43 | 2026-08-29 09:08 | 2026-08-29 09:20 | 2026-08-29 09:20 | 2026-08-29 09:20 |  |  | Fair | No | Area found ok
Outage | J.E.26.08.64143 | C001904103 | Derrick Dawkins | St.James | Completed | Load_253128 | Queens Drive - 710 | 2026-08-28 19:17 | 2026-08-28 23:05 | 2026-08-28 23:41 | 2026-08-29 00:48 | 2026-08-29 00:47 | 2026-08-29 00:22 | 2026-08-29 00:56 | 2026-08-29 00:56 |  |  | Fair | No | Cannot locate customer
Outage | J.E.26.08.64203 | C001904104 | Milton Charlton | KSAN | Completed | Load_253380 | Hope - 410 | 2026-08-28 19:21 | 2026-08-28 19:22 | 2026-08-28 19:44 | 2026-08-28 21:02 | 2026-08-28 21:09 | 2026-08-28 21:05 | 2026-08-28 21:11 | 2026-08-28 21:11 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.64192 | C001904105 | Horace Malcolm | St.James | Completed | Load_250785 | Bogue - 510 | 2026-08-28 19:22 | 2026-08-28 20:03 | 2026-08-28 23:02 | 2026-08-28 23:02 | 2026-08-28 23:30 | 2026-08-28 23:49 | 2026-08-28 23:49 | 2026-08-28 23:49 | BrokenWire | Y | Rains | No | Splice and retention one pole span secondary nuetral used 40ft #2 conductor and two clamp
Non-Outage | J.E.26.08.64083 | C001904106 | Milton Charlton | KSAN | Completed | Load_247332 | Hope - 510 | 2026-08-28 19:23 | 2026-08-28 19:23 | 2026-08-28 22:24 | 2026-08-28 22:25 | 2026-08-28 22:25 | 2026-08-28 22:15 | 2026-08-28 22:26 | 2026-08-28 22:26 |  |  | Fair | No | Call duplicated.
Outage | J.E.26.08.64000 | C001904107 | Oshane Warren | Westmoreland | Completed | Load_239436 | Paradise - 310 | 2026-08-28 19:23 | 2026-08-28 19:25 | 2026-08-28 21:44 | 2026-08-28 21:45 | 2026-08-28 21:45 | 2026-08-28 21:45 | 2026-08-28 21:45 | 2026-08-28 21:45 |  |  | Fair | No | Check and found okay
Outage | J.E.26.08.63505 | C001904108 | Oshane Warren | Westmoreland | Completed | Load_253959 | Paradise - 310 | 2026-08-28 19:24 | 2026-08-28 19:25 | 2026-08-28 21:46 | 2026-08-28 21:46 | 2026-08-28 21:46 | 2026-08-28 21:46 | 2026-08-28 21:46 | 2026-08-28 21:46 |  |  | Fair | No | Customer stated that power was restored
Non-Outage | J.E.26.08.63171 | C001904113 | Raymond Carr | St.Mary | Completed | Load_260764 | Oracabessa - 110 | 2026-08-28 19:27 | 2026-08-28 19:28 | 2026-08-28 20:41 | 2026-08-28 20:41 | 2026-08-28 21:45 | 2026-08-28 21:46 | 2026-08-28 21:47 | 2026-08-28 21:47 |  |  | Fair | No | Several calls to contact number went unanswered. Customer couldn’t be contacted.
Non-Outage | J.E.26.08.63350 | C001904110 | Raymond Carr | St.Ann | Completed | Load_251915 | Upper White River - 110 | 2026-08-28 19:27 | 2026-08-28 19:28 | 2026-08-28 21:47 | 2026-08-28 21:47 | 2026-08-28 21:47 | 2026-08-28 21:48 | 2026-08-28 21:50 | 2026-08-28 21:50 |  |  | Fair | No | Premises already visited. A report was also sent.
Non-Outage | J.E.26.08.63702 | C001904109 | Raymond Carr | St.Mary | Completed | Load_246610 | Oracabessa - 110 | 2026-08-28 19:27 | 2026-08-28 19:28 | 2026-08-28 19:45 | 2026-08-28 19:46 | 2026-08-28 19:45 | 2026-08-28 19:28 | 2026-08-28 19:50 | 2026-08-28 19:50 |  |  | Fair | No | Voltage readings 114/116/230.
Outage | J.E.26.08.63632 | C001904111 | Oshane Warren | Westmoreland | Completed | Load_250712 | Paradise - 310 | 2026-08-28 19:27 | 2026-08-28 19:28 | 2026-08-28 21:58 | 2026-08-28 21:59 | 2026-08-28 21:59 | 2026-08-28 21:59 | 2026-08-28 22:00 | 2026-08-28 22:00 |  |  | Fair | No | Power was restored earlier
Outage | J.E.26.08.64343 | C001904119 | Milton Charlton | KSAN | Completed | Load_264252 | Hope - 510 | 2026-08-28 19:49 | 2026-08-28 19:51 | 2026-08-28 21:11 | 2026-08-28 21:12 | 2026-08-28 22:19 | 2026-08-28 22:15 | 2026-08-28 22:24 | 2026-08-28 22:24 |  |  | Fair | No | Customer service wire #6 triplex neutral burn off at pothead . Repair using 2ft #6 triplex phase and two 1-bolt clamps.Readings at pothead 115-116-231 volts.
Outage | J.E.26.08.64257 | C001904120 | Horace Malcolm | St.James | Completed | Load_265417 | Bogue - 610 | 2026-08-28 19:57 | 2026-08-28 21:07 | 2026-08-29 01:44 | 2026-08-29 01:44 | 2026-08-29 05:47 | 2026-08-29 05:47 | 2026-08-29 05:47 | 2026-08-29 05:47 |  |  | Fair | No | Check and found area ok
Outage | J.E.26.08.64541 | C001904122 | Javid Vernon | Westmoreland | Completed | Load_255934 | Paradise - 110 | 2026-08-28 19:59 | 2026-08-28 20:00 | 2026-08-28 21:07 | 2026-08-28 21:08 | 2026-08-28 21:46 | 2026-08-28 22:17 | 2026-08-28 22:20 | 2026-08-28 22:20 |  |  | Rains | No | After patrolling secondary and reclosing 25 kva transformer fuse hold for a couple seconds then blow oil and fire was coming from blow off valve transformer needs to be replaced urgently 15 to 20 customer are without power lasses are needed to remove illegal connections refer to maintenance
Outage | J.E.26.08.63645 | C001904127 | Tyrese Williams | St.Ann | Completed | Load_240837 | Cardiff Hall - 310 | 2026-08-28 20:15 | 2026-08-28 20:15 | 2026-08-28 20:26 | 2026-08-28 20:43 | 2026-08-28 21:26 | 2026-08-28 21:40 | 2026-08-28 21:40 | 2026-08-28 21:40 |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.08.64554 | C001904128 | Barnett Brown | Manchester | Completed | Load_254330 | Spur Tree - 310 | 2026-08-28 20:16 | 2026-08-28 20:17 | 2026-08-28 20:50 | 2026-08-28 20:51 | 2026-08-28 21:44 | 2026-08-29 01:00 | 2026-08-29 01:10 | 2026-08-29 01:10 |  |  | Fair | No | Open 25 kva transformer, remade joints at transformer drop lead
Outage | J.E.26.08.64351 | C001904130 | Evan Spaulding | St.Mary | Completed | Load_268674 | Annotto Bay - 310 | 2026-08-28 20:24 | 2026-08-28 20:25 | 2026-08-28 20:50 | 2026-08-28 20:51 | 2026-08-28 20:50 | 2026-08-28 20:50 | 2026-08-28 20:51 | 2026-08-28 20:51 |  |  | Fair | No | Customer says power was restored.
Outage | J.E.26.08.64367 | C001904131 | Evan Spaulding | St.Mary | Completed | Load_266590 | Annotto Bay - 310 | 2026-08-28 20:24 | 2026-08-28 20:25 | 2026-08-28 20:52 | 2026-08-28 20:52 | 2026-08-28 20:52 | 2026-08-28 20:52 | 2026-08-28 20:53 | 2026-08-28 20:53 |  |  | Fair | No | Customer says power was restored.
Outage | J.E.26.08.64809 | C001904133 | Damion Reid | Manchester | Completed | Load_251216 | Kendal - 210 | 2026-08-28 20:26 | 2026-08-28 20:26 | 2026-08-28 20:43 | 2026-08-28 20:44 | 2026-08-28 20:52 | 2026-08-28 21:50 | 2026-08-28 21:52 | 2026-08-28 21:52 | BrokenWire |  | Fair | No | One span of broken neutral conductor found cause by illegal connection open 25kva transformer fuse link splice an retention conductor using 20ft of #2 aluminum conductor one #2 preform two one bolt clamp and restore power
Outage | J.E.26.08.64351 | C001904137 | Evan Spaulding | St.Mary | Completed | Load_268674 | Annotto Bay - 310 | 2026-08-28 20:53 | 2026-08-28 20:54 | 2026-08-28 21:00 | 2026-08-28 21:01 | 2026-08-28 21:39 | 2026-08-28 21:52 | 2026-08-28 21:54 | 2026-08-28 21:54 |  |  | Fair | No | Use 2-1 bolt clamps at pole, voltage left 115v.
Outage | J.E.26.08.65222 | C001904144 | Andre Williams | Trelawny | Completed | Load_244212 | Greenwood - 210 | 2026-08-28 21:34 | 2026-08-29 07:56 | 2026-08-29 08:18 | 2026-08-29 08:20 | 2026-08-29 08:19 | 2026-08-29 08:20 | 2026-08-29 08:21 | 2026-08-29 08:21 |  |  | Fair | No | Power was restored to area lastnight, confirmed by call
Outage | J.E.26.08.65385 | C001904153 | Omar King | St.Ann | Completed | Load_242953 | Roaring River - 410 | 2026-08-28 22:46 | 2026-08-28 22:52 | 2026-08-28 23:05 | 2026-08-28 23:05 | 2026-08-29 00:20 | 2026-08-29 00:22 | 2026-08-29 00:24 | 2026-08-29 00:24 |  |  | Fair | No | Unable to find customer called customers several times however no answer
Outage | J.E.26.08.65473 | C001904152 | Omar King | St.Ann | Completed | Load_413061 | Roaring River - 410 | 2026-08-28 22:46 | 2026-08-28 22:52 | 2026-08-29 00:24 | 2026-08-29 00:24 | 2026-08-29 06:00 | 2026-08-29 06:06 | 2026-08-29 06:06 | 2026-08-29 06:06 |  |  | Fair | No | Customer meter centre that get supply from a underground circuit is single phasing please refer to SMD
Outage | J.E.26.08.65503 | C001904156 | Edward Royal | KSAN | Completed | Load_240425 | Washington Blvd - 810 | 2026-08-28 23:09 | 2026-08-28 23:11 | 2026-08-29 00:41 | 2026-08-29 00:41 | 2026-08-29 00:41 | 2026-08-29 00:41 | 2026-08-29 00:42 | 2026-08-29 00:42 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.65729 | C001904157 | Edward Royal | KSAN | Completed | Load_261791 | Hope - 510 | 2026-08-28 23:10 | 2026-08-28 23:11 | 2026-08-29 00:32 | 2026-08-29 00:36 | 2026-08-29 00:36 | 2026-08-29 00:37 | 2026-08-29 00:37 | 2026-08-29 00:37 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.63682 | C001904158 | Edward Royal | KSAS | Completed | Load_241096 | Duhaney - 410 | 2026-08-28 23:11 | 2026-08-28 23:12 | 2026-08-29 00:37 | 2026-08-29 00:38 | 2026-08-29 00:37 | 2026-08-29 00:39 | 2026-08-29 00:40 | 2026-08-29 00:40 |  |  | Fair | No | Call for st Mary department
Outage | J.E.26.08.63649 | C001904159 | Delano Gayle | St.Catherine | Completed | Load_253119 | New Michelton - 210 | 2026-08-28 23:12 | 2026-08-28 23:13 | 2026-08-29 02:20 | 2026-08-29 02:21 | 2026-08-29 03:22 | 2026-08-29 03:50 | 2026-08-29 03:50 | 2026-08-29 03:50 |  |  | Fair | No | Blown junction on main no pole#, patrolled line section and found okay for closure replace 20amps
Outage | J.E.26.08.65233 | C001904160 | Delano Gayle | St.Catherine | Completed | Load_255720 | Tredegar - 510 | 2026-08-28 23:13 | 2026-08-28 23:14 | 2026-08-29 01:29 | 2026-08-29 01:29 | 2026-08-29 01:49 | 2026-08-29 02:19 | 2026-08-29 02:20 | 2026-08-29 02:20 | Fire |  | Fair | No | Area found okay no fire seen
Outage | J.E.26.08.65898 | C001904162 | Wan Carlos Scarlett | St.Catherine | Completed | Load_267024 | Twickenham - 210 | 2026-08-28 23:16 | 2026-08-29 07:06 | 2026-08-29 07:17 | 2026-08-29 07:17 | 2026-08-29 08:36 | 2026-08-29 08:59 | 2026-08-29 09:04 | 2026-08-29 09:04 |  |  | Fair | No | Contact customer, customer unavailable at this time customer reschedule from Monday due to country visit also contact other customers, customers are not having any issues premises closed
Outage | J.E.26.08.65997 | C001904161 | Wan Carlos Scarlett | St.Catherine | Completed | Load_240110 | Twickenham - 210 | 2026-08-28 23:16 | 2026-08-29 09:44 | 2026-08-29 12:52 | 2026-08-29 12:53 | 2026-08-29 13:15 | 2026-08-29 14:16 | 2026-08-29 14:23 | 2026-08-29 14:23 |  |  | Fair | No | Found 1 span of open secondary neutral jumper burn out from one bolt clamps and transformer droplead both phase and neutral corroded use 10 one bolt clamps at open secondary line isolate and close 50 KVA transformer no pole # was found
Outage | J.E.26.08.63909 | C001904165 | Derrick Dawkins | St.James | Completed | Load_244479 | Queens Drive - 810 | 2026-08-28 23:32 | 2026-08-28 23:33 | 2026-08-29 03:47 | 2026-08-29 03:55 | 2026-08-29 03:59 | 2026-08-29 04:02 | 2026-08-29 04:02 | 2026-08-29 04:02 |  |  | Fair | No | Can’t locate customer
Outage | J.E.26.08.65745 | C001904166 | Derrick Dawkins | St.James | Completed | Load_266743 | Bogue - 310 | 2026-08-28 23:34 | 2026-08-28 23:35 | 2026-08-29 01:41 | 2026-08-29 01:42 | 2026-08-29 01:44 | 2026-08-29 02:44 | 2026-08-29 03:09 | 2026-08-29 03:09 |  |  | Fair | No | Found one span of secondary phase burnt down due to illegal connection open 50 kva transformer to carry out repairs used 4 pg clamp
Outage | J.E.26.08.66063 | C001904167 | Horace Malcolm | St.James | Completed | Load_250785 | Bogue - 510 | 2026-08-28 23:47 | 2026-08-28 23:48 | 2026-08-29 00:11 | 2026-08-29 00:11 | 2026-08-29 00:11 | 2026-08-29 00:13 | 2026-08-29 00:13 | 2026-08-29 00:13 |  |  | Fair | No | Related to call job number 63802
Outage | J.E.26.08.66431 | C001904174 | Daniel Francis | St.Ann | Completed | Load_242634 | Roaring River - 410 | 2026-08-29 02:23 | 2026-08-29 07:30 | 2026-08-29 08:22 | 2026-08-29 08:23 | 2026-08-29 08:33 | 2026-08-29 08:34 | 2026-08-29 08:37 | 2026-08-29 08:37 |  |  | Fair | No | Please refer to field service
Outage | J.E.26.08.65416 | C001904176 | Horace Malcolm | St.James | Completed | Load_252127 | Bogue - 510 | 2026-08-29 02:28 | 2026-08-29 07:39 | 2026-08-29 07:54 | 2026-08-29 07:54 | 2026-08-29 07:55 | 2026-08-29 07:56 | 2026-08-29 07:56 | 2026-08-29 07:56 |  |  | Fair | No | Supply was restored to area
Outage | J.E.26.08.63755 | C001904177 | Horace Malcolm | St.James | Completed | Load_242321 | Bogue - 510 | 2026-08-29 02:31 | 2026-08-29 07:39 | 2026-08-29 07:48 | 2026-08-29 07:49 | 2026-08-29 07:50 | 2026-08-29 07:53 | 2026-08-29 07:53 | 2026-08-29 07:53 |  |  | Fair | No | Check and found ok supply was restored to area
Outage | J.E.26.08.66045 | C001904179 | Edward Royal | KSAN | Completed | Load_567704 | Washington Blvd - 310 | 2026-08-29 02:36 | 2026-08-29 02:37 | 2026-08-29 03:30 | 2026-08-29 03:30 | 2026-08-29 03:30 | 2026-08-29 03:30 | 2026-08-29 03:31 | 2026-08-29 03:31 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.66239 | C001904180 | Edward Royal | KSAS | Completed | Load_240364 | Cane River - 410 | 2026-08-29 02:36 | 2026-08-29 02:38 | 2026-08-29 03:29 | 2026-08-29 03:29 | 2026-08-29 03:29 | 2026-08-29 03:29 | 2026-08-29 03:30 | 2026-08-29 03:30 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.63356 | C001904181 | Delano Gayle | St.Catherine | Completed | Load_244490 | New Michelton - 310 | 2026-08-29 02:40 | 2026-08-29 02:41 | 2026-08-29 03:50 | 2026-08-29 03:51 | 2026-08-29 04:15 | 2026-08-29 05:33 | 2026-08-29 05:33 | 2026-08-29 05:33 |  |  | Fair | No | Premises/ Area patrolled and found okay
Outage | J.E.26.08.66819 | C001904198 | Edward Royal | KSAN | Completed | Load_264781 | Washington Blvd - 310 | 2026-08-29 05:54 | 2026-08-29 10:03 | 2026-08-29 10:26 | 2026-08-29 10:27 | 2026-08-29 10:57 | 2026-08-29 11:23 | 2026-08-29 11:23 | 2026-08-29 11:23 |  |  | Fair | No | Replaced 15A junction fuse 2A transformer fuse
Outage | J.E.26.08.66600 | C001904200 | Ricky Hall | St.Catherine | Completed | Load_255156 | Tredegar - 210 | 2026-08-29 05:56 | 2026-08-29 07:29 | 2026-08-29 07:53 | 2026-08-29 10:20 | 2026-08-29 10:31 | 2026-08-29 10:32 | 2026-08-29 10:33 | 2026-08-29 10:33 |  |  | Fair | No | Internal Issue resolved by electrician
Outage | J.E.26.08.65457 | C001904215 | Derrick Dawkins | St.James | Completed | Load_262396 | Rose Hall - 210 | 2026-08-29 06:19 | 2026-08-29 06:21 | 2026-08-29 06:48 | 2026-08-29 07:14 | 2026-08-29 07:13 | 2026-08-29 07:03 | 2026-08-29 07:15 | 2026-08-29 07:15 |  |  | Fair | No | Found premises ok
Outage | J.E.26.08.65782 | C001904214 | Derrick Dawkins | St.James | Completed | Load_244260 | Rose Hall - 210 | 2026-08-29 06:19 | 2026-08-29 06:20 | 2026-08-29 06:26 | 2026-08-29 06:27 | 2026-08-29 06:48 | 2026-08-29 06:52 | 2026-08-29 07:13 | 2026-08-29 07:13 |  |  | Fair | No | Check and found premises ok
Outage | J.E.26.08.65785 | C001904340 | Wan Carlos Scarlett | Portmore | Completed | Load_254966 | Naggo Head - 610 | 2026-08-29 07:05 | 2026-08-29 07:06 | 2026-08-29 09:11 | 2026-08-29 10:16 | 2026-08-29 10:31 | 2026-08-29 10:45 | 2026-08-29 10:46 | 2026-08-29 10:46 |  |  | Fair | No | Found customer 3 wire service at pole with both phase and natural corroded use 3 one bolt clamp at pole readings 117 117 234
Outage | J.E.26.08.65899 | C001904341 | Wan Carlos Scarlett | St.Catherine | Completed | Load_249085 | Twickenham - 210 | 2026-08-29 07:05 | 2026-08-29 07:06 | 2026-08-29 07:17 | 2026-08-29 09:05 | 2026-08-29 09:05 | 2026-08-29 09:06 | 2026-08-29 09:10 | 2026-08-29 09:10 |  |  | Fair | No | Reach at location contact customer, customer is not available at this time customer will reschedule for an available time premises closed
Outage | J.E.26.08.65730 | C001904342 | Hartley Chin | Clarendon | Completed | Load_242606 | Monymusk - 210 | 2026-08-29 07:06 | 2026-08-29 07:08 | 2026-08-29 13:33 | 2026-08-29 13:33 | 2026-08-29 14:05 | 2026-08-29 14:27 | 2026-08-29 14:47 | 2026-08-29 14:47 |  |  | Fair | No | Prem not found … unable to contact customer with contact # provided…
Non-Outage | J.E.26.08.62602 | C001904346 | Hartley Chin |  | Completed |  |  | 2026-08-29 07:08 | 2026-08-29 07:10 | 2026-08-29 08:56 | 2026-08-29 08:57 | 2026-08-29 09:36 | 2026-08-29 09:37 | 2026-08-29 09:37 | 2026-08-29 09:37 | LeaningPole |  | Fair | No | Prem not found .. unable to contact customer with contact # provided… no Prem # or meter # available…
Non-Outage | J.E.26.08.62830 | C001904344 | Hartley Chin | Clarendon | Completed | Load_242606 | Monymusk - 210 | 2026-08-29 07:08 | 2026-08-29 07:09 | 2026-08-29 11:01 | 2026-08-29 11:49 | 2026-08-29 12:55 | 2026-08-29 13:32 | 2026-08-29 13:33 | 2026-08-29 13:33 |  |  | SevereWind | No | Found okay … voltage read 112v , 114v ..
Non-Outage | J.E.26.08.63636 | C001904347 | Wan Carlos Scarlett | Portmore | Completed | Load_259065 | Naggo Head - 510 | 2026-08-29 07:08 | 2026-08-29 07:10 | 2026-08-29 10:49 | 2026-08-29 10:50 | 2026-08-29 11:14 | 2026-08-29 12:06 | 2026-08-29 12:06 | 2026-08-29 12:06 | BrokenWire |  | Fair | No | Reach on location been calling customer got no answer premises closed
Non-Outage | J.E.26.08.63740 | C001904345 | Hartley Chin | Clarendon | Completed | Load_259178 | Parnassus - 310 | 2026-08-29 07:08 | 2026-08-29 07:09 | 2026-08-29 10:11 | 2026-08-29 10:12 | 2026-08-29 10:57 | 2026-08-29 11:01 | 2026-08-29 11:01 | 2026-08-29 11:01 |  |  | Fair | No | Call related to job # 62870
Non-Outage | J.E.26.08.65537 | C001904348 | Wan Carlos Scarlett | Portmore | Completed | Load_254966 | Naggo Head - 610 | 2026-08-29 07:08 | 2026-08-29 07:10 | 2026-08-29 09:11 | 2026-08-29 10:47 | 2026-08-29 10:46 | 2026-08-29 10:47 | 2026-08-29 10:49 | 2026-08-29 10:49 |  |  | Fair | No | Found customer 3 wire service at pole with both phase and natural corroded use 3 one bolt clamp at pole 117 117 234
Non-Outage | J.E.26.08.63171 | C001904350 | Cliton Henry | St.Mary | Completed | Load_260764 | Oracabessa - 110 | 2026-08-29 07:13 | 2026-08-29 07:14 | 2026-08-29 07:27 | 2026-08-29 07:27 | 2026-08-29 09:03 | 2026-08-29 09:07 | 2026-08-29 09:07 | 2026-08-29 09:07 |  |  | Fair | No | Premises lock, customer contact number provided went unanswered.
Outage | J.E.26.08.66358 | C001904351 | Richard Samuda | Manchester | Completed | Load_293058 | Spur Tree - 310 | 2026-08-29 07:14 | 2026-08-29 07:15 | 2026-08-29 08:20 | 2026-08-29 08:34 | 2026-08-29 08:56 | 2026-08-29 09:14 | 2026-08-29 09:14 | 2026-08-29 09:14 |  |  | Fair | No | Found okay 3047766 voltage 112, 113 225
Non-Outage | J.E.26.08.61269 | C001904352 | Raheem Ricketts | St.Elizabeth | Completed | Load_292464 | Maggotty - 210 | 2026-08-29 07:15 | 2026-08-29 07:16 | 2026-08-29 07:24 | 2026-08-29 07:27 | 2026-08-29 07:38 | 2026-08-29 07:38 | 2026-08-29 07:39 | 2026-08-29 07:39 |  |  | Fair | No | Unable to locate customer cell number went straight voicemail after several calls
Outage | J.E.26.08.60846 | C001904353 | Raheem Ricketts | St.Elizabeth | Completed | Load_266664 | Maggotty - 210 | 2026-08-29 07:15 | 2026-08-29 07:16 | 2026-08-29 07:24 | 2026-08-29 10:03 | 2026-08-29 10:14 | 2026-08-29 10:16 | 2026-08-29 10:16 | 2026-08-29 10:16 | Fire |  | Fair | No | Check and found okay
Non-Outage | J.E.26.08.57237 | C001904354 | Marlon Authors | St.Elizabeth | Completed | Load_249245 | Maggotty - 110 | 2026-08-29 07:17 | 2026-08-29 07:18 | 2026-08-29 12:53 | 2026-08-29 12:54 | 2026-08-29 12:53 | 2026-08-29 13:33 | 2026-08-29 13:33 | 2026-08-29 13:33 | LowHangingWires |  | Fair | No | Supply checked and found service wire hanging low across the road. Retention same using one linket. Supply leave working ok rdg 110v,107v and cross phased 217 volts
Non-Outage | J.E.26.08.50338 | C001904355 | Raheem Ricketts | St.Elizabeth | Completed | Load_1002276 | Maggotty - 210 | 2026-08-29 07:18 | 2026-08-29 07:19 | 2026-08-29 07:24 | 2026-08-29 08:10 | 2026-08-29 09:13 | 2026-08-29 10:02 | 2026-08-29 10:02 | 2026-08-29 10:02 |  |  | Fair | No | Check and found customer experiencing low voltage change 3 clamps at customer pothead and remake neutral joint at jps pole voltage left 110,110,220
Outage | J.E.26.08.65486 | C001904356 | Richman Whyte | Westmoreland | Completed | Load_260765 | Paradise - 110 | 2026-08-29 07:21 | 2026-08-29 07:22 | 2026-08-29 14:53 | 2026-08-29 14:53 | 2026-08-29 14:53 | 2026-08-29 14:53 | 2026-08-29 14:54 | 2026-08-29 14:54 |  |  | Fair | No | Customer stated that power was restored in the area and she is okay now
Outage | J.E.26.08.64091 | C001904358 | Rusean Allen | KSAS | Completed | Load_264427 | Greenwich - 310 | 2026-08-29 07:23 | 2026-08-29 07:56 | 2026-08-29 10:09 | 2026-08-29 10:09 | 2026-08-29 11:58 | 2026-08-29 12:20 | 2026-08-29 12:21 | 2026-08-29 12:21 |  |  | Fair | No | Breaker at rami enclosure found chipped, breaker reset was done.
Outage | J.E.26.08.66957 | C001904357 | Richman Whyte | Westmoreland | Completed | Load_241469 | Paradise - 210 | 2026-08-29 07:23 | 2026-08-29 07:23 | 2026-08-29 11:24 | 2026-08-29 11:25 | 2026-08-29 12:52 | 2026-08-29 12:56 | 2026-08-29 12:58 | 2026-08-29 12:58 |  |  | Fair | No | Open 100 kva transformer fuse and repair one span open secondary conductor top phase use 80 feet #2/0 aluminum conductor and six one bolt clamps voltage 117 117 234
Non-Outage | J.E.26.08.32085 | C001904359 | Marlon Authors | St.Elizabeth | Completed | Load_292293 | Maggotty - 110 | 2026-08-29 07:24 | 2026-08-29 07:25 | 2026-08-29 08:40 | 2026-08-29 08:40 | 2026-08-29 08:40 | 2026-08-29 08:41 | 2026-08-29 08:41 | 2026-08-29 08:41 |  |  | Fair | No | Customer said that the issue was resolved
Non-Outage | J.E.26.08.32065 | C001904360 | Marlon Authors | St.Elizabeth | Completed | Load_292293 | Maggotty - 110 | 2026-08-29 07:25 | 2026-08-29 07:25 | 2026-08-29 07:58 | 2026-08-29 07:59 | 2026-08-29 07:58 | 2026-08-29 07:59 | 2026-08-29 08:02 | 2026-08-29 08:02 |  |  | Fair | No | Customer said that the issue was resolved
Non-Outage | J.E.26.08.61233 | C001904361 | Marlon Authors | St.Elizabeth | Completed | Load_241383 | Maggotty - 110 | 2026-08-29 07:25 | 2026-08-29 07:27 | 2026-08-29 11:19 | 2026-08-29 11:20 | 2026-08-29 11:19 | 2026-08-29 11:35 | 2026-08-29 11:35 | 2026-08-29 11:35 |  |  | Fair | No | Supply checked and found meter and wires in meter socket burnt. Disconnect supply at pothead and advised customer to have same repaired
Outage | J.E.26.08.67037 | C001904362 | Hartley Chin | St.Catherine | Completed | Load_263189 | Rhodens Pen - 310 | 2026-08-29 07:26 | 2026-08-29 07:27 | 2026-08-29 09:09 | 2026-08-29 09:38 | 2026-08-29 09:44 | 2026-08-29 10:11 | 2026-08-29 10:11 | 2026-08-29 10:11 | BrokenWire |  | Fair | No | Isolate 25 KVA transformer @ pole # 0113215 due broken open secondary phase found in 1 span , broken joint repaired , CHNAGE X3 drop lead clamp , re-energized transformer…
Outage | J.E.26.08.66373 | C001904363 | Richard Nicholas | St.Catherine | Completed | Load_1000361 | Rhodens Pen - 410 | 2026-08-29 07:27 | 2026-08-29 07:28 | 2026-08-29 09:58 | 2026-08-29 09:58 | 2026-08-29 10:24 | 2026-08-29 10:43 | 2026-08-29 10:44 | 2026-08-29 10:44 |  |  | Fair | No | Premises found locked however 3w supply checked at meter socket,same found ok.voltage reading 116x2 and 232v.
Outage | J.E.26.08.66925 | C001904365 | Richard Nicholas | St.Catherine | Completed | Load_259990 | Rhodens Pen - 210 | 2026-08-29 07:27 | 2026-08-29 07:28 | 2026-08-29 07:54 | 2026-08-29 07:54 | 2026-08-29 09:15 | 2026-08-29 09:54 | 2026-08-29 09:57 | 2026-08-29 09:57 |  |  | Fair | No | Replaced blown 25kva transformer,5amp fuse.pole #011450.
Outage | J.E.26.08.66977 | C001904367 | Richard Nicholas | St.Catherine | Completed | Load_302295 | Rhodens Pen - 210 | 2026-08-29 07:27 | 2026-08-29 07:28 | 2026-08-29 10:45 | 2026-08-29 10:46 | 2026-08-29 11:20 | 2026-08-29 12:19 | 2026-08-29 12:20 | 2026-08-29 12:20 |  |  | Fair | No | Replaced blown 25amp junctions fuse on pole #0119531 and blown 8amp junctions on pole #584371.
Outage | J.E.26.08.66979 | C001904368 | Richard Nicholas | St.Catherine | Completed | Load_302291 | Rhodens Pen - 210 | 2026-08-29 07:27 | 2026-08-29 07:28 | 2026-08-29 12:21 | 2026-08-29 12:22 | 2026-08-29 12:27 | 2026-08-29 12:27 | 2026-08-29 12:28 | 2026-08-29 12:28 |  |  | Fair | No | Found ok
Outage | J.E.26.08.67052 | C001904369 | Richard Nicholas | St.Catherine | Completed | Load_302298 | Rhodens Pen - 210 | 2026-08-29 07:27 | 2026-08-29 07:28 | 2026-08-29 12:28 | 2026-08-29 12:28 | 2026-08-29 12:36 | 2026-08-29 12:36 | 2026-08-29 12:37 | 2026-08-29 12:37 |  |  | Fair | No | Found ok
Non-Outage | J.E.26.08.65956 | C001904371 | Ricky Hall | St.Catherine | Completed | Load_256498 | Tredegar - 310 | 2026-08-29 07:29 | 2026-08-29 07:30 | 2026-08-29 12:24 | 2026-08-29 12:25 | 2026-08-29 12:40 | 2026-08-29 12:41 | 2026-08-29 12:41 | 2026-08-29 12:41 | BangingWires |  | Fair | No | No banging wires seen
Non-Outage | J.E.26.08.67062 | C001904370 | Ricky Hall | St.Catherine | Completed | Load_570028 | Twickenham - 310 | 2026-08-29 07:29 | 2026-08-29 07:30 | 2026-08-29 12:01 | 2026-08-29 12:41 | 2026-08-29 13:27 | 2026-08-29 14:06 | 2026-08-29 14:06 | 2026-08-29 14:06 |  |  | Fair | No | Premises closed
Non-Outage | J.E.26.08.62304 | C001904372 | Ricky Hall | St.Catherine | Completed | Load_257507 | Tredegar - 210 | 2026-08-29 07:30 | 2026-08-29 07:30 | 2026-08-29 07:53 | 2026-08-29 10:09 | 2026-08-29 10:17 | 2026-08-29 10:19 | 2026-08-29 10:20 | 2026-08-29 10:20 |  |  | Fair | No | Premises closed
Non-Outage | J.E.26.08.63131 | C001904373 | Ricky Hall | St.Catherine | Completed | Load_258112 | Tredegar - 210 | 2026-08-29 07:30 | 2026-08-29 07:30 | 2026-08-29 07:53 | 2026-08-29 09:50 | 2026-08-29 10:02 | 2026-08-29 10:06 | 2026-08-29 10:06 | 2026-08-29 10:06 | BrokenWire |  | Fair | No | Incorrect information premises not found
Non-Outage | J.E.26.08.64087 | C001904375 | Donald Cunningham | St.Catherine | Completed | Load_252376 | New Michelton - 310 | 2026-08-29 07:30 | 2026-08-29 07:31 | 2026-08-29 12:16 | 2026-08-29 12:16 | 2026-08-29 13:00 | 2026-08-29 13:06 | 2026-08-29 13:06 | 2026-08-29 13:06 |  |  | Fair | No | Premises closed
Non-Outage | J.E.26.08.67007 | C001904374 | Donald Cunningham | St.Catherine | Completed | Load_249294 | New Michelton - 310 | 2026-08-29 07:30 | 2026-08-29 07:31 | 2026-08-29 13:06 | 2026-08-29 13:07 | 2026-08-29 13:43 | 2026-08-29 14:12 | 2026-08-29 14:13 | 2026-08-29 14:13 |  |  | Fair | No | Corroded phase and neural by pothead and pole corrected using 6 clamps voltage readings by meter socket 113/116/229 raining in area
Non-Outage | J.E.26.08.61277 | C001904381 | Cliton Henry | St.Ann | Completed | Load_245638 | Upper White River - 110 | 2026-08-29 07:32 | 2026-08-29 07:33 | 2026-08-29 11:16 | 2026-08-29 11:16 | 2026-08-29 12:12 | 2026-08-29 12:12 | 2026-08-29 12:13 | 2026-08-29 12:13 |  |  | Fair | No | Unable to locate customer, the customer contact number provided went unanswered.
Non-Outage | J.E.26.08.62406 | C001904378 | Romaine Roberts | St.Mary | Completed | Load_246409 | Annotto Bay - 310 | 2026-08-29 07:32 | 2026-08-29 10:44 | 2026-08-29 11:36 | 2026-08-29 11:36 | 2026-08-29 11:36 | 2026-08-29 11:37 | 2026-08-29 11:38 | 2026-08-29 11:38 |  |  | Fair | No | Found ok customer is now restore drew to feeder was out power is now restore
Non-Outage | J.E.26.08.62933 | C001904379 | Romaine Roberts | St.Mary | Completed | Load_251815 | Annotto Bay - 210 | 2026-08-29 07:32 | 2026-08-29 07:33 | 2026-08-29 11:40 | 2026-08-29 11:41 | 2026-08-29 12:49 | 2026-08-29 12:49 | 2026-08-29 12:49 | 2026-08-29 12:49 |  |  | Fair | No | Power restore
Outage | J.E.26.08.66009 | C001904384 | Collin Robinson | Portland | Completed | Load_255277 | Port Antonio - 410 | 2026-08-29 07:35 | 2026-08-29 07:35 | 2026-08-29 08:08 | 2026-08-29 08:08 | 2026-08-29 08:59 | 2026-08-29 09:36 | 2026-08-29 09:36 | 2026-08-29 09:36 |  |  | Fair | No | Remove tree limbs from primary conductor and replace 10 amps junction fuse
Non-Outage | J.E.26.08.32504 | C001904391 | Roxroy Needham | St.Ann | Completed | Load_251665 | Cardiff Hall - 310 | 2026-08-29 07:36 | 2026-08-29 07:38 | 2026-08-29 09:43 | 2026-08-29 09:44 | 2026-08-29 10:18 | 2026-08-29 10:36 | 2026-08-29 10:37 | 2026-08-29 10:37 |  |  | Fair | No | Remake joint at pole used 1 pg clamp voltage left at meter 114-115-227
Non-Outage | J.E.26.08.33478 | C001904390 | Roxroy Needham | St.Ann | Completed | Load_247889 | Cardiff Hall - 310 | 2026-08-29 07:36 | 2026-08-29 07:38 | 2026-08-29 10:37 | 2026-08-29 10:38 | 2026-08-29 11:37 | 2026-08-29 12:41 | 2026-08-29 12:41 | 2026-08-29 12:41 |  |  | Fair | No | Customer has internal issues and was advised to get an electrician
Non-Outage | J.E.26.08.50050 | C001904389 | Roxroy Needham | St.Ann | Completed | Load_249178 | Cardiff Hall - 310 | 2026-08-29 07:36 | 2026-08-29 07:38 | 2026-08-29 21:33 | 2026-08-29 21:33 | 2026-08-29 22:40 | 2026-08-29 22:40 | 2026-08-29 22:41 | 2026-08-29 22:41 |  |  | Fair | No | Premises not found not getting customer on phone
Non-Outage | J.E.26.08.54691 | C001904392 | Daniel Francis | St.Ann | Completed | Load_248837 | Ocho Rios - 510 | 2026-08-29 07:36 | 2026-08-29 07:38 | 2026-08-29 12:00 | 2026-08-29 12:00 | 2026-08-29 12:11 | 2026-08-29 12:11 | 2026-08-29 12:12 | 2026-08-29 12:12 |  |  | Fair | No | Not found customer not answering phone
Non-Outage | J.E.26.08.61372 | C001904386 | Roxroy Needham | St.Ann | Completed | Load_248462 | Cardiff Hall - 210 | 2026-08-29 07:36 | 2026-08-29 07:38 | 2026-08-29 09:19 | 2026-08-29 09:20 | 2026-08-29 09:41 | 2026-08-29 09:41 | 2026-08-29 09:43 | 2026-08-29 09:43 |  |  | Fair | No | Remake Joint at pole used 2 pg clamp voltage left at meter 114-112-219
Non-Outage | J.E.26.08.63003 | C001904385 | Roxroy Needham | St.Ann | Completed | Load_556920 | Cardiff Hall - 310 | 2026-08-29 07:36 | 2026-08-29 07:38 | 2026-08-29 12:42 | 2026-08-29 12:43 | 2026-08-29 13:07 | 2026-08-29 13:06 | 2026-08-29 13:08 | 2026-08-29 13:08 |  |  | Fair | No | Premises not found not getting customer on phone
Non-Outage | J.E.26.08.14321 | C001904398 | Daniel Francis | St.Ann | Completed | Load_245767 | Ocho Rios - 310 | 2026-08-29 07:37 | 2026-08-29 07:38 | 2026-08-29 11:28 | 2026-08-29 11:28 | 2026-08-29 11:35 | 2026-08-29 11:38 | 2026-08-29 11:38 | 2026-08-29 11:38 |  |  | Fair | No | Found okay customer say power restored from Sunday
Non-Outage | J.E.26.08.16269 | C001904397 | Daniel Francis | St.Ann | Completed | Load_257919 | Ocho Rios - 310 | 2026-08-29 07:37 | 2026-08-29 07:38 | 2026-08-29 11:39 | 2026-08-29 11:39 | 2026-08-29 11:57 | 2026-08-29 12:00 | 2026-08-29 12:00 | 2026-08-29 12:00 |  |  | Fair | No | Customer need to work on meter box also meter need to be replace
Non-Outage | J.E.26.08.17297 | C001904396 | Daniel Francis | St.Ann | Completed | Load_243179 | Ocho Rios - 310 | 2026-08-29 07:37 | 2026-08-29 07:38 | 2026-08-29 11:08 | 2026-08-29 11:08 | 2026-08-29 11:09 | 2026-08-29 11:10 | 2026-08-29 11:10 | 2026-08-29 11:10 |  |  | Fair | No | Not found customer not answering phone
Non-Outage | J.E.26.08.20844 | C001904393 | Daniel Francis | St.Ann | Completed | Load_251708 | Ocho Rios - 310 | 2026-08-29 07:37 | 2026-08-29 07:38 | 2026-08-29 11:11 | 2026-08-29 11:11 | 2026-08-29 11:14 | 2026-08-29 11:24 | 2026-08-29 11:26 | 2026-08-29 11:26 |  |  | Fair | No | Meter need to be replace found meter defective
Non-Outage | J.E.26.08.21614 | C001904394 | Daniel Francis | St.Ann | Completed | Load_268866 | Ocho Rios - 310 | 2026-08-29 07:37 | 2026-08-29 07:38 | 2026-08-29 10:54 | 2026-08-29 10:55 | 2026-08-29 11:06 | 2026-08-29 11:07 | 2026-08-29 11:07 | 2026-08-29 11:07 |  |  | Fair | No | Found okay
Non-Outage | J.E.26.08.24872 | C001904395 | Daniel Francis | St.Ann | Completed | Load_252506 | Ocho Rios - 310 | 2026-08-29 07:37 | 2026-08-29 07:38 | 2026-08-29 10:11 | 2026-08-29 10:12 | 2026-08-29 10:38 | 2026-08-29 10:51 | 2026-08-29 10:51 | 2026-08-29 10:51 |  |  | Fair | No | Change one bolt at pole 117 117 234 in all
Outage | J.E.26.08.63460 | C001904401 | Tajay Bernard | Hanover | Completed | Load_247084 | Orange Bay - 310 | 2026-08-29 07:49 | 2026-08-29 07:51 | 2026-08-29 09:24 | 2026-08-29 09:24 | 2026-08-29 09:24 | 2026-08-29 09:25 | 2026-08-29 09:25 | 2026-08-29 09:25 |  |  | Fair | No | Customer stated that power was restored
Outage | J.E.26.08.66635 | C001904399 | Tajay Bernard | Hanover | Completed | Load_1001399 | Orange Bay - 310 | 2026-08-29 07:49 | 2026-08-29 07:51 | 2026-08-29 08:04 | 2026-08-29 08:07 | 2026-08-29 09:05 | 2026-08-29 09:20 | 2026-08-29 09:23 | 2026-08-29 09:23 |  |  | Fair | No | Customer meter wasn’t reconnected. Customer power was restored
Outage | J.E.26.08.67161 | C001904400 | Javid Vernon | St.Elizabeth | Completed | Load_570225 | Maggotty - 110 | 2026-08-29 07:49 | 2026-08-29 07:50 | 2026-08-29 08:30 | 2026-08-29 08:31 | 2026-08-29 09:17 | 2026-08-29 09:27 | 2026-08-29 09:27 | 2026-08-29 09:27 |  |  | Fair | No | Rami failure no communication to customer meter in hexing box refers to field service
Outage | J.E.26.08.67198 | C001904402 | Rusean Allen | KSAS | Completed | Load_574672 | Cane River - 610 | 2026-08-29 07:49 | 2026-08-29 07:54 | 2026-08-29 14:15 | 2026-08-29 14:16 | 2026-08-29 14:21 | 2026-08-29 14:23 | 2026-08-29 14:24 | 2026-08-29 14:24 |  |  | Fair | No | Unable to gain access. Customer phone went unanswered.
Outage | J.E.26.08.61477 | C001904405 | Rusean Allen | KSAS | Completed | Load_245738 | Rockfort - 210 | 2026-08-29 07:50 | 2026-08-29 07:57 | 2026-08-29 14:24 | 2026-08-29 14:25 | 2026-08-29 14:26 | 2026-08-29 14:27 | 2026-08-29 14:27 | 2026-08-29 14:27 |  |  | Fair | No | Problem was already resolved
Outage | J.E.26.08.61530 | C001904406 | Rusean Allen | KSAS | Completed | Load_241894 | Up Park Camp - 510 | 2026-08-29 07:50 | 2026-08-29 07:57 | 2026-08-29 13:58 | 2026-08-29 13:58 | 2026-08-29 14:13 | 2026-08-29 14:15 | 2026-08-29 14:15 | 2026-08-29 14:15 |  |  | Fair | No | Rami failure, customer only one without power, refer to field service department.
Outage | J.E.26.08.66333 | C001904408 | Andre Williams | Trelawny | Completed | Load_237793 | Greenwood - 210 | 2026-08-29 07:55 | 2026-08-29 07:56 | 2026-08-29 09:53 | 2026-08-29 09:54 | 2026-08-29 09:53 | 2026-08-29 09:54 | 2026-08-29 09:54 | 2026-08-29 09:54 | BrokenPole |  | Fair | No | Reffer to Montego Bay emergency call is in flankers
Outage | J.E.26.08.63165 | C001904409 | Edward Royal | KSAS | Completed | Load_246514 | Rockfort - 410 | 2026-08-29 07:56 | 2026-08-29 08:09 | 2026-08-29 11:23 | 2026-08-29 11:24 | 2026-08-29 11:23 | 2026-08-29 11:24 | 2026-08-29 11:24 | 2026-08-29 11:24 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.67278 | C001904411 | Ricky Hall | St.Catherine | Completed | Load_267045 | Tredegar - 310 | 2026-08-29 08:00 | 2026-08-29 08:15 | 2026-08-29 11:49 | 2026-08-29 12:01 | 2026-08-29 12:07 | 2026-08-29 12:16 | 2026-08-29 12:16 | 2026-08-29 12:16 |  |  | Fair | No | Issue was resolved automatically (smart meter)
Outage | J.E.26.08.67050 | C001904413 | Christopher Edwards | KSAN | Completed | Load_240612 | Constant Spring - 410 | 2026-08-29 08:10 | 2026-08-29 08:11 | 2026-08-29 09:00 | 2026-08-29 09:13 | 2026-08-29 09:47 | 2026-08-29 11:06 | 2026-08-29 11:06 | 2026-08-29 11:06 |  | Y | Fair | No | Refuse blown junction fusesUsing (1) 25 amps1- 20 ampsClear bamboo off primary line
Outage | J.E.26.08.67221 | C001904414 | Romaine Roberts | St.Mary | Completed | Load_251815 | Annotto Bay - 210 | 2026-08-29 08:11 | 2026-08-29 08:11 | 2026-08-29 08:29 | 2026-08-29 08:30 | 2026-08-29 10:13 | 2026-08-29 10:37 | 2026-08-29 10:39 | 2026-08-29 10:39 |  |  | Fair | No | Outage related to 310 Annotto bay feeder that trip maintenance crew is on call
Outage | J.E.26.08.67323 | C001904415 | Milton Charlton | KSAN | Completed | Load_557675 | Hope - 410 | 2026-08-29 08:11 | 2026-08-29 08:14 | 2026-08-29 08:48 | 2026-08-29 08:48 | 2026-08-29 10:55 | 2026-08-29 09:40 | 2026-08-29 10:57 | 2026-08-29 10:57 |  |  | Fair | No | Found okay upon arrival. Customer confirm that the report was false.
Outage | J.E.26.08.67328 | C001904418 | Ricky Hall | St.Catherine | Completed | Load_253751 | Tredegar - 210 | 2026-08-29 08:14 | 2026-08-29 08:15 | 2026-08-29 08:40 | 2026-08-29 08:40 | 2026-08-29 09:21 | 2026-08-29 09:48 | 2026-08-29 09:49 | 2026-08-29 09:49 |  |  | Fair | No | Repair burnt off 3W service neutral at pole use 1 clamp 115*2/230
Outage | J.E.26.08.67346 | C001904419 | Rochaine Palmer | KSAN | Completed | Load_240736 | Washington Blvd - 710 | 2026-08-29 08:35 | 2026-08-29 10:15 | 2026-08-29 12:21 | 2026-08-29 12:22 | 2026-08-29 12:43 | 2026-08-29 12:45 | 2026-08-29 12:46 | 2026-08-29 12:46 |  |  | Fair | No | Reset customer circuit breaker.
Outage | J.E.26.08.67375 | C001904420 | Raheem Ricketts | St.Elizabeth | Completed | Load_252931 | Maggotty - 210 | 2026-08-29 08:37 | 2026-08-29 08:38 | 2026-08-29 11:12 | 2026-08-29 11:13 | 2026-08-29 12:38 | 2026-08-29 12:40 | 2026-08-29 12:40 | 2026-08-29 12:40 |  |  | Fair | No | Check and found okay customer made report regarding to light bill
Non-Outage | J.E.26.07.24843 | C001904421 | Eric Williams |  | Completed |  |  | 2026-08-29 08:42 | 2026-08-29 08:43 | 2026-08-29 09:32 | 2026-08-29 09:32 | 2026-08-29 10:00 | 2026-08-29 10:03 | 2026-08-29 10:03 | 2026-08-29 10:03 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.67337 | C001904423 | Cliton Henry | St.Mary | Completed | Load_351738 | Oracabessa - 110 | 2026-08-29 08:51 | 2026-08-29 08:53 | 2026-08-29 09:13 | 2026-08-29 09:14 | 2026-08-29 09:14 | 2026-08-29 10:45 | 2026-08-29 10:46 | 2026-08-29 10:46 |  |  | Fair | No | A blown 10 junction fuse found at Castle Garden pole #0013397 due to age fuse and salt air. Supply restored using 1- 15 amp fuse.
Non-Outage | J.E.26.08.61208 | C001904428 | Swon Miller | St.James | Completed | Load_246427 | Bogue - 310 | 2026-08-29 09:00 | 2026-08-29 09:03 | 2026-08-29 14:48 | 2026-08-29 14:48 | 2026-08-29 15:42 | 2026-08-18 03:52 | 2026-08-29 15:55 | 2026-08-29 15:55 |  |  | Fair | No | Unable to locate customer phone calls to customer went unanswered unable to locate the premises on humber avenue
Non-Outage | J.E.26.08.61539 | C001904430 | Swon Miller | St.James | Completed | Load_266792 | Queens Drive - 710 | 2026-08-29 09:00 | 2026-08-29 09:03 | 2026-08-29 10:47 | 2026-08-29 10:48 | 2026-08-29 10:54 | 2026-08-18 11:34 | 2026-08-29 11:43 | 2026-08-29 11:43 |  |  | Fair | No | Found customer single phasing voltage found 119 voltage left 119 box number EN 04440 please refer to field service/kadian mckniel
Non-Outage | J.E.26.08.61553 | C001904429 | Swon Miller | St.James | Completed | Load_251737 | Queens Drive - 810 | 2026-08-29 09:00 | 2026-08-29 09:03 | 2026-08-29 18:01 | 2026-08-29 18:02 | 2026-08-29 18:24 | 2026-08-25 06:35 | 2026-08-29 18:35 | 2026-08-29 18:35 |  |  | Fair | No | Found customer with low voltage voltage found on line side 105/105/210 load side 102/101/203 hundred kva transformer is at max the customer with the low voltage is at the end of the line recommend secondary circuit needs to be split please refer to maintenance/ kerron Frazier/ miss beckford Lincoln
Non-Outage | J.E.26.08.61698 | C001904426 | Swon Miller | St.James | Completed | Load_257288 | Queens Drive - 710 | 2026-08-29 09:00 | 2026-08-29 09:03 | 2026-08-29 13:13 | 2026-08-29 13:13 | 2026-08-29 13:46 | 2026-08-26 02:07 | 2026-08-29 14:09 | 2026-08-29 14:09 |  |  | Fair | No | Found customer single phasing due to defective meter voltage found voltage found on line side ofmeter l113/114/ 228 voltage left 114/113/228 please refer to field service/ kadian mckneil
Non-Outage | J.E.26.08.61731 | C001904427 | Swon Miller | St.James | Completed | Load_238546 | Queens Drive - 710 | 2026-08-29 09:00 | 2026-08-29 09:03 | 2026-08-29 15:56 | 2026-08-29 17:20 | 2026-08-29 17:55 | 2026-08-11 05:55 | 2026-08-29 18:01 | 2026-08-29 18:01 |  |  | Fair | No | Found premises closed customer states that he won’t be available until tomorrow
Non-Outage | J.E.26.08.61777 | C001904424 | Swon Miller | St.James | Completed | Load_242019 | Queens Drive - 710 | 2026-08-29 09:00 | 2026-08-29 09:03 | 2026-08-29 11:44 | 2026-08-29 11:45 | 2026-08-29 12:58 | 2026-08-29 13:08 | 2026-08-29 13:11 | 2026-08-29 13:11 |  |  | Fair | No | Found premises closed customer states that she is not available right now
Non-Outage | J.E.26.08.62132 | C001904425 | Swon Miller | St.James | Completed | Load_261444 | Queens Drive - 710 | 2026-08-29 09:00 | 2026-08-29 09:03 | 2026-08-29 09:31 | 2026-08-29 09:32 | 2026-08-29 09:43 | 2026-08-25 10:41 | 2026-08-29 10:47 | 2026-08-29 10:47 |  |  | Fair | No | Found customer voltage fluctuating cause by contamination at pothead clean and remake joints use 1 pg voltage found 101/105 voltage left 110/112/223
Non-Outage | J.E.26.08.56522 | C001904431 | Shamour Haughton | St.James | Completed | Load_303213 | Bogue - 310 | 2026-08-29 09:03 | 2026-08-29 09:10 | 2026-08-29 09:20 | 2026-08-29 09:20 | 2026-08-29 09:36 | 2026-08-29 09:37 | 2026-08-29 09:38 | 2026-08-29 09:38 |  |  | Fair | No | Customer is single phasing from box EN04510
Non-Outage | J.E.26.08.61506 | C001904439 | Richman Whyte | Westmoreland | Completed | Load_266056 | Paradise - 210 | 2026-08-29 09:08 | 2026-08-29 09:09 | 2026-08-29 11:20 | 2026-08-29 11:20 | 2026-08-29 11:20 | 2026-08-29 11:20 | 2026-08-29 11:23 | 2026-08-29 11:23 | LowHangingWires |  | Fair | No | Hexing area 30 feet wood pole with service wire on it leaning need crane truck to push it up also it need a guy on it
Non-Outage | J.E.26.08.67417 | C001904441 | Omar King |  | Completed |  |  | 2026-08-29 09:11 | 2026-08-30 07:16 | 2026-08-30 10:39 | 2026-08-30 10:39 | 2026-08-30 10:55 | 2026-08-30 10:56 | 2026-08-30 10:56 | 2026-08-30 10:56 | LowHangingWires |  | Fair | No | Unable to find customer call several times no answer directions not sufficient
Non-Outage | J.E.26.08.63697 | C001904442 | Horace Malcolm | St.James | Completed | Load_247495 | Bogue - 510 | 2026-08-29 09:12 | 2026-08-29 09:18 | 2026-08-30 10:12 | 2026-08-30 10:12 | 2026-08-30 10:50 | 2026-08-30 11:24 | 2026-08-30 11:24 | 2026-08-30 11:24 |  |  | Fair | No | Unable to locate customer or premises from direction given multiple calls to customer unavailable
Non-Outage | J.E.26.08.17176 | C001904445 | Horace Malcolm | St.James | Completed | Load_256374 | Bogue - 610 | 2026-08-29 09:17 | 2026-08-29 09:18 | 2026-08-29 13:25 | 2026-08-29 13:26 | 2026-08-29 14:53 | 2026-08-29 14:55 | 2026-08-29 14:55 | 2026-08-29 14:55 |  |  | Fair | No | Unable to locate customer or premises multiple calls to customer unavailable
Non-Outage | J.E.26.08.30248 | C001904444 | Horace Malcolm | St.James | Completed | Load_252070 | Bogue - 610 | 2026-08-29 09:17 | 2026-08-29 09:18 | 2026-08-29 10:43 | 2026-08-29 10:43 | 2026-08-29 11:02 | 2026-08-29 11:33 | 2026-08-29 11:33 | 2026-08-29 11:33 |  |  | Fair | No | Check and found customer having rami issue voltage reading at pothead and two joints at service wire and pole 114-019-114 field service required
Non-Outage | J.E.26.08.35385 | C001904443 | Horace Malcolm | St.James | Completed | Load_302124 | Bogue - 610 | 2026-08-29 09:17 | 2026-08-29 09:18 | 2026-08-29 11:34 | 2026-08-29 11:34 | 2026-08-29 11:49 | 2026-08-29 11:50 | 2026-08-29 11:51 | 2026-08-29 11:51 |  |  | Fair | No | Customer says issues was restored
Non-Outage | J.E.26.08.60777 | C001904449 | Richman Whyte | Westmoreland | Completed | Load_265891 | Paradise - 110 | 2026-08-29 09:30 | 2026-08-29 09:31 | 2026-08-29 14:45 | 2026-08-29 14:46 | 2026-08-29 14:45 | 2026-08-29 14:48 | 2026-08-29 14:51 | 2026-08-29 14:51 | BrokenWire |  | Fair | No | Change defective service wire use 55 feet #6 triplex service wire three one bolt clamps three service connectors voltage 112 113 226
Outage | J.E.26.08.67350 | C001904448 | Richard Samuda | Manchester | Completed | Load_258980 | Spur Tree - 310 | 2026-08-29 09:30 | 2026-08-29 09:30 | 2026-08-29 11:12 | 2026-08-29 11:16 | 2026-08-29 12:22 | 2026-08-29 00:39 | 2026-08-29 12:39 | 2026-08-29 12:39 |  |  | SevereWind | No | Found 25 kva transformer fuse blown patrol line found nothing replaced fuse customer back to normal
Outage | J.E.26.08.67463 | C001904450 | Raheem Ricketts |  | Completed | Load_254723 | Spur Tree - 210 | 2026-08-29 09:34 | 2026-08-29 09:35 | 2026-08-29 10:31 | 2026-08-29 10:31 | 2026-08-29 11:08 | 2026-08-29 11:12 | 2026-08-29 11:12 | 2026-08-29 11:12 |  |  | Fair | No | Unable to complete task customer meter is connected however customer doesn’t have any power unable to access meter because meter is barrel lock
Outage | J.E.26.08.67475 | C001904451 | Cliton Henry | St.Mary | Completed | Load_264013 | Blackstonedge - 110 | 2026-08-29 09:39 | 2026-08-29 09:44 | 2026-08-29 11:06 | 2026-08-29 11:08 | 2026-08-29 11:10 | 2026-08-29 11:12 | 2026-08-29 11:12 | 2026-08-29 11:12 |  |  | Fair | No | The customer stated that was restored.
Outage | J.E.26.08.67402 | C001904453 | Stephen Taylor | St.Thomas | Completed | Load_237781 | Good Year - 110 | 2026-08-29 09:40 | 2026-08-29 09:51 | 2026-08-29 11:38 | 2026-08-29 11:39 | 2026-08-29 12:41 | 2026-08-29 12:41 | 2026-08-29 12:55 | 2026-08-29 12:55 |  |  | Fair | No | See transformer link down patrol see nothing and close up back 25 kva transformer with a 3 amp fuse all customer is now okay
Outage | J.E.26.08.67418 | C001904454 | Christopher Edwards | KSAN | Completed | Load_258268 | Constant Spring - 410 | 2026-08-29 09:40 | 2026-08-29 09:50 | 2026-08-29 11:06 | 2026-08-29 11:07 | 2026-08-29 12:21 | 2026-08-29 13:30 | 2026-08-29 13:31 | 2026-08-29 13:31 | BrokenWire |  | Fair | No | Refuse blown transformer fuseUsing (1) 5 amps
Outage | J.E.26.08.67432 | C001904452 | Rochaine Palmer | KSAS | Completed | Load_247621 | Duhaney - 310 | 2026-08-29 09:40 | 2026-08-29 10:17 | 2026-08-29 13:07 | 2026-08-29 13:07 | 2026-08-29 13:51 | 2026-08-29 13:55 | 2026-08-29 14:03 | 2026-08-29 14:03 |  |  | Fair | No | Customer meter socket was tampered whit load side of meter was pulled out. Customer advised to get on electrician.
Outage | J.E.26.08.67487 | C001904456 | Ricky Hall | St.Catherine | Completed | Load_250859 | Tredegar - 210 | 2026-08-29 09:41 | 2026-08-29 09:43 | 2026-08-29 10:34 | 2026-08-29 10:35 | 2026-08-29 11:24 | 2026-08-29 11:48 | 2026-08-29 11:48 | 2026-08-29 11:48 | BrokenWire |  | Fair | No | Clear primary line replaced blown 20 amps junction fuse
Outage | J.E.26.08.67559 | C001904455 | Richard Nicholas | St.Catherine | Completed | Load_255329 | Rhodens Pen - 410 | 2026-08-29 09:41 | 2026-08-29 09:42 | 2026-08-29 14:43 | 2026-08-29 14:44 | 2026-08-29 15:05 | 2026-08-29 15:05 | 2026-08-29 15:05 | 2026-08-29 15:05 |  |  | Fair | No | Area found ok
Outage | J.E.26.08.67216 | C001904458 | Collin Robinson | Portland | Completed | Load_352999 | Port Antonio - 310 | 2026-08-29 09:44 | 2026-08-29 09:44 | 2026-08-29 10:32 | 2026-08-29 10:33 | 2026-08-29 10:47 | 2026-08-29 11:13 | 2026-08-29 11:13 | 2026-08-29 11:13 | BrokenWire |  | Fair | No | Replace 60 ft of # 6 twisted wire and six one bolt clamp Voltage reading 118v 118v 236v
Outage | J.E.26.08.67329 | C001904459 | Collin Robinson | Portland | Completed | Load_352475 | Port Antonio - 410 | 2026-08-29 09:44 | 2026-08-29 09:44 | 2026-08-29 12:56 | 2026-08-29 12:56 | 2026-08-29 14:22 | 2026-08-29 14:26 | 2026-08-29 14:27 | 2026-08-29 14:27 |  |  | Fair | No | Premises found with supply
Non-Outage | J.E.26.08.67164 | C001904461 | Stephen Taylor | St.Thomas | Completed | Load_267393 | Good Year - 210 | 2026-08-29 09:51 | 2026-08-29 09:52 | 2026-08-29 10:26 | 2026-08-29 10:27 | 2026-08-29 11:12 | 2026-08-29 11:12 | 2026-08-29 11:14 | 2026-08-29 11:14 | LowHangingWires |  | Fair | No | Retention low hanging wire customer is not okay
Outage | J.E.26.08.67542 | C001904462 | Richard Samuda | Manchester | Completed | Load_245137 | Spur Tree - 310 | 2026-08-29 09:53 | 2026-08-29 09:54 | 2026-08-29 13:20 | 2026-08-29 13:24 | 2026-08-29 13:27 | 2026-08-29 03:15 | 2026-08-29 15:15 | 2026-08-29 15:15 |  |  | Fair | No | Splice and reconnected customer one phase of customer service wire that was broken causing customer to experience single phasing voltage 116, 118 234
Non-Outage | J.E.26.08.41665 | C001904468 | Tajay Bernard | Hanover | Completed | Load_240604 | Orange Bay - 310 | 2026-08-29 09:54 | 2026-08-29 09:55 | 2026-08-29 17:59 | 2026-08-29 18:00 | 2026-08-29 18:32 | 2026-08-29 18:35 | 2026-08-29 18:36 | 2026-08-29 18:36 |  |  | Fair | No | Premises found, customer is not home and stated that she won’t be until Monday, no work can’t be done
Non-Outage | J.E.26.08.42624 | C001904467 | Tajay Bernard | Hanover | Completed | Load_240166 | Orange Bay - 310 | 2026-08-29 09:54 | 2026-08-29 09:55 | 2026-08-29 18:39 | 2026-08-29 18:40 | 2026-08-29 19:20 | 2026-08-29 19:38 | 2026-08-29 19:40 | 2026-08-29 19:40 |  |  | Fair | No | Check and found customer having low voltage on 1 phase, customer has a mid span connection so we are unable to carry out the task. A bucket ruck is needed to complete the workVoltage found 108/99/207
Non-Outage | J.E.26.08.50239 | C001904466 | Tajay Bernard | Hanover | Completed | Load_242231 | Orange Bay - 210 | 2026-08-29 09:54 | 2026-08-29 09:55 | 2026-08-29 10:04 | 2026-08-29 10:32 | 2026-08-29 10:32 | 2026-08-29 11:05 | 2026-08-29 11:06 | 2026-08-29 11:06 |  |  | Fair | No | Voltage found 236/230/227/391/408/402
Non-Outage | J.E.26.08.55945 | C001904465 | Tajay Bernard | Hanover | Completed | Load_263993 | Orange Bay - 210 | 2026-08-29 09:54 | 2026-08-29 09:55 | 2026-08-29 14:09 | 2026-08-29 14:10 | 2026-08-29 14:41 | 2026-08-29 15:25 | 2026-08-29 15:25 | 2026-08-29 15:25 |  |  | Fair | No | Premises check and found okay voltage found on jps pole 107/107/214Voltage left at customer pothead 107/107/214
Non-Outage | J.E.26.08.61144 | C001904464 | Tajay Bernard | Hanover | Completed | Load_260216 | Orange Bay - 210 | 2026-08-29 09:54 | 2026-08-29 09:55 | 2026-08-29 11:02 | 2026-08-29 11:07 | 2026-08-29 11:35 | 2026-08-29 13:54 | 2026-08-29 14:02 | 2026-08-29 14:02 |  |  | Fair | No | Isolate 1 25kva Transformer to clean and remake jumpers at jps pole and joints at customer pot head , and to retention 1 span of secondary twisted, 2 preform and 4 clamps was usedVoltage found 117/100/208Voltqge left 117/116/232
Non-Outage | J.E.26.08.64682 | C001904463 | Tajay Bernard | Hanover | Completed | Load_252500 | Orange Bay - 310 | 2026-08-29 09:54 | 2026-08-29 09:55 | 2026-08-29 15:26 | 2026-08-29 15:27 | 2026-08-29 16:37 | 2026-08-29 16:41 | 2026-08-29 16:41 | 2026-08-29 16:41 |  |  | Fair | No | Area check and found okay unable to locate customer on premises with directions given , multiple phone calls to customer number went unanswered
Outage | J.E.26.08.67312 | C001904472 | Rusean Allen | KSAS | Completed | Load_1002663 | Cane River - 310 | 2026-08-29 09:58 | 2026-08-29 17:12 | 2026-08-29 17:19 | 2026-08-29 17:19 | 2026-08-29 18:13 | 2026-08-29 18:37 | 2026-08-29 18:37 | 2026-08-29 18:37 |  |  | Fair | No | 1x 3amp fuse found 1x 3amp fuse replaced
Outage | J.E.26.08.67618 | C001904470 | Romaine Roberts | St.Mary | Completed | Load_248567 | Highgate -110 | 2026-08-29 09:58 | 2026-08-29 11:30 | 2026-08-29 19:03 | 2026-08-29 19:03 | 2026-08-29 21:29 | 2026-08-29 22:06 | 2026-08-29 22:47 | 2026-08-29 22:47 |  |  | Fair | No | Site close
Non-Outage | J.E.26.08.62638 | C001904475 | Daniel Francis | St.Ann | Completed | Load_251697 | Roaring River - 410 | 2026-08-29 10:11 | 2026-08-29 10:12 | 2026-08-29 12:12 | 2026-08-29 12:12 | 2026-08-29 12:28 | 2026-08-29 12:59 | 2026-08-29 12:59 | 2026-08-29 12:59 | BrokenWire |  | Fair | No | Splice and retention command neutral
Non-Outage | J.E.26.08.67541 | C001904477 | Wan Carlos Scarlett |  | Completed |  |  | 2026-08-29 10:12 | 2026-08-29 12:43 | 2026-08-29 17:34 | 2026-08-29 17:34 | 2026-08-29 18:19 | 2026-08-29 18:19 | 2026-08-29 18:23 | 2026-08-29 18:23 | Fire |  | Fair | No | Reach on location didn’t see any sign of fire on wire are on pole premises found okay
Outage | J.E.26.08.67691 | C001904478 | Rochaine Palmer | KSAS | Completed | Load_253791 | Greenwich - 510 | 2026-08-29 10:13 | 2026-08-29 10:15 | 2026-08-29 14:03 | 2026-08-29 14:03 | 2026-08-29 15:24 | 2026-08-29 16:40 | 2026-08-29 16:50 | 2026-08-29 16:50 |  |  | Fair | No | Bank of 1-167-100-100 kva transformers at pole #( no pole #) found 1-10 amps and 1-15 amps fuse blown. Reclosed using one 10 amps and one 15 amps fuse and reclosed transformer switches the 100 kva transformer fuse blow back . Removed transformer drop lead and reclosed 100 kva and it blow again. 100 kva transformer is Defective. Transformer is located between #58 halfway tree road and N.H.T building.
Outage | J.E.26.08.67685 | C001904479 | Richard Nicholas | St.Catherine | Completed | Load_238849 | Rhodens Pen - 210 | 2026-08-29 10:16 | 2026-08-29 10:19 | 2026-08-29 12:37 | 2026-08-29 12:38 | 2026-08-29 13:17 | 2026-08-29 13:43 | 2026-08-29 13:44 | 2026-08-29 13:44 | Fire |  | Fair | No | Premises found locked however no visible defects are fire seen at the premises.
Outage | J.E.26.08.67707 | C001904480 | Rochaine Palmer | KSAS | Completed | Load_264663 | Three Miles - 410 | 2026-08-29 10:16 | 2026-08-29 10:18 | 2026-08-29 10:43 | 2026-08-29 10:44 | 2026-08-29 12:17 | 2026-08-29 12:10 | 2026-08-29 12:21 | 2026-08-29 12:21 | BrokenWire |  | Fair | No | Isolate 50 kva transformer at pole #0022439 and repair broken open wire secondary neutral. Repaired using 70ft#2AA conductor and four 1- bolt clamps. Reclose transformer switch.
Non-Outage | J.E.26.08.63044 | C001904481 | Richard Samuda | Manchester | Completed | Load_244291 | Spur Tree - 310 | 2026-08-29 10:17 | 2026-08-29 10:17 | 2026-08-29 17:21 | 2026-08-29 17:22 | 2026-08-29 17:24 | 2026-08-29 05:24 | 2026-08-29 17:25 | 2026-08-29 17:25 |  |  | Fair | No | Found ok customer back to normal
Non-Outage | J.E.26.08.64152 | C001904484 | Richard Samuda | Manchester | Completed | Load_244291 | Spur Tree - 310 | 2026-08-29 10:17 | 2026-08-29 10:18 | 2026-08-29 16:21 | 2026-08-29 16:22 | 2026-08-29 16:35 | 2026-08-29 17:14 | 2026-08-29 17:15 | 2026-08-29 17:15 |  |  | SevereWind | No | Change burnt out 1blot clamp that was burnt out that was causing supply to be on and off in area using 1one bolt clamp voltage 115, 115, 230 customer back to normal
Outage | J.E.26.08.67600 | C001904482 | Richard Nicholas | St.Catherine | Completed | Load_253421 | Rhodens Pen - 210 | 2026-08-29 10:17 | 2026-08-29 10:19 | 2026-08-29 13:44 | 2026-08-29 13:45 | 2026-08-29 14:41 | 2026-08-29 14:41 | 2026-08-29 14:43 | 2026-08-29 14:43 |  |  | Fair | No | Area found ok
Outage | J.E.26.08.67633 | C001904486 | Clyde Brown | Clarendon | Completed | Load_568383 | May Pen - 110 | 2026-08-29 10:18 | 2026-08-29 10:19 | 2026-08-29 14:04 | 2026-08-29 14:05 | 2026-08-29 14:05 | 2026-08-29 13:54 | 2026-08-29 14:07 | 2026-08-29 14:07 |  | Y | Fair | No | Blown 8 amps junction fuse at Cross path caused by tree contact,line cleared and blown fuse replaced.
Outage | J.E.26.08.67634 | C001904487 | Clyde Brown | Clarendon | Completed | Load_253116 | May Pen - 110 | 2026-08-29 10:18 | 2026-08-29 10:19 | 2026-08-29 11:23 | 2026-08-29 11:24 | 2026-08-29 13:17 | 2026-08-29 13:53 | 2026-08-29 14:04 | 2026-08-29 14:04 |  | Y | Fair | No | Blown 8 amps junction fuse at Cross path caused by tree contact,line cleared and blown fuse replaced
Outage | J.E.26.08.67692 | C001904485 | Roxroy Needham | St.Ann | Completed | Load_1003806 | Cardiff Hall - 210 | 2026-08-29 10:18 | 2026-08-29 10:40 | 2026-08-29 13:06 | 2026-08-29 16:49 | 2026-08-29 18:28 | 2026-08-29 18:31 | 2026-08-29 18:31 | 2026-08-29 18:31 |  |  | Fair | No | Check and found ok
Outage | J.E.26.08.67698 | C001904488 | Roxroy Needham | St.Ann | Completed | Load_259466 | Cardiff Hall - 210 | 2026-08-29 10:18 | 2026-08-29 10:40 | 2026-08-29 13:06 | 2026-08-29 13:08 | 2026-08-29 16:46 | 2026-08-29 16:49 | 2026-08-29 16:49 | 2026-08-29 16:49 |  |  | Fair | No | Replace 3 amp fuse for 25 KVA transformer
Outage | J.E.26.08.67714 | C001904491 | Richman Whyte | Westmoreland | Completed | Load_293032 | Paradise - 110 | 2026-08-29 10:47 | 2026-08-29 10:48 | 2026-08-29 12:58 | 2026-08-29 12:59 | 2026-08-29 13:43 | 2026-08-29 13:44 | 2026-08-29 13:44 | 2026-08-29 13:44 |  |  | Fair | No | Unable to locate or contact customer on the phone direction is required
Outage | J.E.26.08.67847 | C001904494 | Rochaine Palmer | KSAS | Completed | Load_242712 | Duhaney - 410 | 2026-08-29 11:07 | 2026-08-29 11:20 | 2026-08-29 12:46 | 2026-08-29 12:47 | 2026-08-29 12:59 | 2026-08-29 13:05 | 2026-08-29 13:07 | 2026-08-29 13:07 |  |  | Fair | No | Unable to locate customer by telephone. Telephone number on the report going straight to voicemail
Outage | J.E.26.08.67871 | C001904493 | Edward Royal | KSAN | Completed | Load_253322 | Washington Blvd - 310 | 2026-08-29 11:07 | 2026-08-29 11:20 | 2026-08-29 13:38 | 2026-08-29 13:38 | 2026-08-29 13:38 | 2026-08-29 13:39 | 2026-08-29 13:39 | 2026-08-29 13:39 |  |  | Fair | No | Customer was related to fire at superior customer was disconnected from en box reffered to field service
Outage | J.E.26.08.67841 | C001904496 | Edward Royal | KSAN | Completed | Load_567705 | Washington Blvd - 310 | 2026-08-29 11:17 | 2026-08-29 11:20 | 2026-08-29 11:50 | 2026-08-29 11:50 | 2026-08-29 11:50 | 2026-08-29 11:51 | 2026-08-29 11:51 | 2026-08-29 11:51 |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.08.67924 | C001904500 | Omar King |  | Completed |  |  | 2026-08-29 11:30 | 2026-08-29 15:26 | 2026-08-29 16:18 | 2026-08-29 16:19 | 2026-08-29 17:41 | 2026-08-29 17:42 | 2026-08-29 17:42 | 2026-08-29 17:42 |  |  | Fair | No | Unable to find customer call several times no answer directions not sufficient
Outage | J.E.26.08.67848 | C001904501 | Richard Samuda | Manchester | Completed | Load_292612 | Spur Tree - 310 | 2026-08-29 11:30 | 2026-08-29 11:31 | 2026-08-29 13:01 | 2026-08-29 13:02 | 2026-08-29 13:02 | 2026-08-29 13:03 | 2026-08-29 13:03 | 2026-08-29 13:03 |  |  | Fair | No | Found ok customer said power was restored
Outage | J.E.26.08.67851 | C001904502 | Richard Samuda | Manchester | Completed | Load_254838 | Spur Tree - 310 | 2026-08-29 11:31 | 2026-08-29 11:32 | 2026-08-29 13:16 | 2026-08-29 16:20 | 2026-08-29 16:21 | 2026-08-29 16:22 | 2026-08-29 16:22 | 2026-08-29 16:22 |  |  | Fair | No | Premises not located and call to phone no answer
Non-Outage | J.E.26.08.61332 | C001904503 | Rusean Allen | KSAS | Completed | Load_238236 | Hunts Bay - 210 | 2026-08-29 11:35 | 2026-08-29 11:36 | 2026-08-29 13:24 | 2026-08-29 13:24 | 2026-08-29 13:54 | 2026-08-29 13:57 | 2026-08-29 13:57 | 2026-08-29 13:57 |  |  | Fair | No | Defective 100KVA transformer found at the intersection of princess street and Barry street. Refer to maintenance department.
Outage | J.E.26.08.68002 | C001904504 | Raheem Ricketts | Manchester | Completed | Load_269147 | Spur Tree - 210 | 2026-08-29 11:37 | 2026-08-29 11:39 | 2026-08-29 12:41 | 2026-08-29 12:53 | 2026-08-29 13:05 | 2026-08-29 13:21 | 2026-08-29 13:22 | 2026-08-29 13:22 |  |  | Fair | No | Check and found customer experiencing an internal problem
Outage | J.E.26.08.67615 | C001904505 | Rusean Allen | KSAS | Completed | Load_267192 | Rockfort - 410 | 2026-08-29 11:40 | 2026-08-29 17:12 | 2026-08-29 17:26 | 2026-08-29 18:49 | 2026-08-29 18:52 | 2026-08-29 18:53 | 2026-08-29 18:53 | 2026-08-29 18:53 |  |  | Fair | No | Premises okay
Outage | J.E.26.08.68029 | C001904507 | Eric Williams | KSAS | Completed | Load_567634 | Duhaney - 310 | 2026-08-29 12:05 | 2026-08-29 12:08 | 2026-08-29 12:15 | 2026-08-29 12:16 | 2026-08-29 12:25 | 2026-08-29 12:25 | 2026-08-29 12:25 | 2026-08-29 12:25 |  |  | Fair | No | Premises found okay
Outage | J.E.26.08.68113 | C001904506 | Milton Charlton | KSAN | Completed | Load_578851 | Hope - 510 | 2026-08-29 12:05 | 2026-08-29 12:09 | 2026-08-29 12:25 | 2026-08-29 12:26 | 2026-08-29 14:01 | 2026-08-29 13:25 | 2026-08-29 14:05 | 2026-08-29 14:05 |  |  | Fair | No | Customer service wire #6 duplex phase burn off at meter socket. Reconnect burnt off duplex phase. Reading at meter socket 116 volts.
Outage | J.E.26.08.67527 | C001904508 | Nickolas Rodriques | St.Catherine | Completed | Load_248418 | Tredegar - 310 | 2026-08-29 12:06 | 2026-08-29 15:16 | 2026-08-29 15:29 | 2026-08-29 15:33 | 2026-08-29 16:22 | 2026-08-29 16:49 | 2026-08-29 16:51 | 2026-08-29 16:51 |  |  | Fair | No | Found area with electricity. Customer confirmed that the power was restored.
Outage | J.E.26.08.67954 | C001904512 | Romaine Roberts | St.Mary | Completed | Load_241528 | Highgate -110 | 2026-08-29 12:08 | 2026-08-29 12:09 | 2026-08-29 15:34 | 2026-08-29 15:35 | 2026-08-29 18:56 | 2026-08-29 19:01 | 2026-08-29 19:01 | 2026-08-29 19:01 |  |  | Fair | No | Found junction fuse blown patrol line nothing found at the moment replace 10 amp no pole number power restore
Outage | J.E.26.08.68020 | C001904511 | Christopher Edwards | KSAN | Completed | Load_248755 | Constant Spring - 410 | 2026-08-29 12:08 | 2026-08-29 12:10 | 2026-08-29 13:32 | 2026-08-29 13:36 | 2026-08-29 13:35 | 2026-08-29 13:39 | 2026-08-29 13:40 | 2026-08-29 13:40 |  |  | Fair | No | Unable to reach customer by phoneUnable to locate premises
Outage | J.E.26.08.68024 | C001904510 | Romaine Roberts | St.Mary | Completed | Load_261204 | Highgate -110 | 2026-08-29 12:08 | 2026-08-29 12:09 | 2026-08-29 15:00 | 2026-08-29 15:01 | 2026-08-29 15:01 | 2026-08-29 15:02 | 2026-08-29 15:34 | 2026-08-29 15:34 | BrokenWire |  | Fair | No | Man cut tree on primary line cause pole to fall down CV construction also maintenance work needed primary jumper isolation 2 pole span away from fallen pole one transformer circuit is out replace 15 amp junction to restore supply to most customer
Non-Outage | J.E.26.08.68070 | C001904513 | Daniel Francis |  | Completed |  |  | 2026-08-29 12:15 | 2026-08-29 12:36 | 2026-08-29 12:59 | 2026-08-29 13:00 | 2026-08-29 13:18 | 2026-08-29 13:44 | 2026-08-29 13:47 | 2026-08-29 13:47 | Fire |  | Fair | No | Found secondary phase conducter dislodge and resting close to neutral conducter reposition and made safe
Outage | J.E.26.08.68143 | C001904515 | Christopher Edwards | KSAN | Completed | Load_258268 | Constant Spring - 410 | 2026-08-29 12:17 | 2026-08-29 12:21 | 2026-08-29 13:31 | 2026-08-29 13:31 | 2026-08-29 13:31 | 2026-08-29 13:31 | 2026-08-29 13:32 | 2026-08-29 13:32 |  |  | Fair | No | Related to previous call that was resolved
Outage | J.E.26.08.68149 | C001904514 | Stephen Taylor | St.Thomas | Completed | Load_252328 | Lysson - 410 | 2026-08-29 12:17 | 2026-08-29 12:37 | 2026-08-29 13:05 | 2026-08-29 13:05 | 2026-08-29 13:51 | 2026-08-29 01:00 | 2026-08-29 14:21 | 2026-08-29 14:21 |  |  | Fair | No | Patrol clear bush off line with switch stick and close up back junction with a 7 amp fuse safely a customer is now okay
Outage | J.E.26.08.68041 | C001904517 | Javid Vernon | St.Elizabeth | Completed | Load_557819 | Maggotty - 110 | 2026-08-29 12:29 | 2026-08-29 12:30 | 2026-08-29 12:38 | 2026-08-29 12:39 | 2026-08-29 13:21 | 2026-08-29 13:31 | 2026-08-29 13:37 | 2026-08-29 13:37 |  |  | Fair | No | Check and found 15 customer without power In hexing box #06599 customer needs urgent assistance refer to field service
Outage | J.E.26.08.68189 | C001904518 | Edward Royal | KSAN | Completed | Load_567705 | Washington Blvd - 310 | 2026-08-29 12:33 | 2026-08-29 12:34 | 2026-08-29 13:37 | 2026-08-29 13:37 | 2026-08-29 13:37 | 2026-08-29 13:37 | 2026-08-29 13:38 | 2026-08-29 13:38 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.68029 | C001904519 | Eric Williams | KSAS | Completed | Load_567634 | Duhaney - 310 | 2026-08-29 12:34 | 2026-08-29 13:34 | 2026-08-29 13:46 | 2026-08-29 13:46 | 2026-08-29 13:46 | 2026-08-29 14:26 | 2026-08-29 14:28 | 2026-08-29 14:28 |  |  | Fair | No | Blown 50amps, 30amps and 20amps junction fuse and 1 2amps transformer fuse found and replaced cause by bird
Outage | J.E.26.08.68049 | C001904520 | Wan Carlos Scarlett | St.Catherine | Completed | Load_253902 | Twickenham - 210 | 2026-08-29 12:35 | 2026-08-29 12:36 | 2026-08-29 14:23 | 2026-08-29 14:24 | 2026-08-29 15:00 | 2026-08-29 15:24 | 2026-08-29 15:28 | 2026-08-29 15:28 |  |  | Fair | No | Refuse a 100 KVA transformer with a 10 Amp fuse no pole # was found clear tree from line
Outage | J.E.26.08.68106 | C001904521 | Wan Carlos Scarlett | St.Catherine | Completed | Load_288801 | Twickenham - 210 | 2026-08-29 12:35 | 2026-08-29 12:36 | 2026-08-29 15:19 | 2026-08-29 15:28 | 2026-08-29 15:48 | 2026-08-29 16:14 | 2026-08-29 16:15 | 2026-08-29 16:15 |  |  | Fair | No | Found Customer getting supply from EG box customer experiencing single phase call refer to Moses
Outage | J.E.26.08.63176 | C001904525 | Nickolas Rodriques | St.Catherine | Completed | Load_241584 | Tredegar - 310 | 2026-08-29 12:41 | 2026-08-29 15:16 | 2026-08-29 16:52 | 2026-08-29 17:09 | 2026-08-29 17:56 | 2026-08-29 18:31 | 2026-08-29 18:33 | 2026-08-29 18:33 |  |  | Fair | No | Found customer with power. He confirmed that the issue was already resolved.
Outage | J.E.26.08.68252 | C001904527 | Delano Gayle | St.Catherine | Completed | Load_255316 | Rhodens Pen - 210 | 2026-08-29 12:50 | 2026-08-29 15:14 | 2026-08-29 19:18 | 2026-08-29 19:19 | 2026-08-29 19:19 | 2026-08-29 19:21 | 2026-08-29 19:21 | 2026-08-29 19:21 | Fire |  | Fair | No | Premises found okay related to call where burnt transformer neutral was repaired
Outage | J.E.26.08.62617 | C001904530 | Swon Miller | St.James | Completed | Load_257840 | Queens Drive - 710 | 2026-08-29 12:54 | 2026-08-29 12:55 | 2026-08-29 16:44 | 2026-08-29 16:44 | 2026-08-29 16:48 | 2026-08-29 17:16 | 2026-08-29 17:18 | 2026-08-29 17:18 | LeaningPole |  | Fair | No | Found 40ftclass6 wooden load bearing pole with single phase primary and 50 kva transformer leaning needs to be straight urgently plz refer to maintenance
Outage | J.E.26.08.67027 | C001904528 | Swon Miller | St.James | Completed | Load_293052 | Queens Drive - 310 | 2026-08-29 12:54 | 2026-08-29 17:42 | 2026-08-29 19:00 | 2026-08-29 19:00 | 2026-08-29 19:01 | 2026-08-29 19:27 | 2026-08-29 19:40 | 2026-08-29 19:40 | TreeContact |  | Fair | No | Check and found area okay
Outage | J.E.26.08.67790 | C001904529 | Swon Miller | St.James | Completed | Load_249352 | Queens Drive - 710 | 2026-08-29 12:54 | 2026-08-29 12:55 | 2026-08-29 14:10 | 2026-08-29 14:10 | 2026-08-29 14:21 | 2026-08-18 02:47 | 2026-08-29 14:48 | 2026-08-29 14:48 |  |  | Fair | No | Check and found customer meter defective contact customer care agent Lamar he stated that customer has been receiving estimated bills from last October customer meter is defective and needs to be replaced voltage found on line side 112/112/225 voltage left on line side 112/112/225 please refer to field service/kadian.mckneil
Outage | J.E.26.08.67728 | C001904531 | Andre Williams | Trelawny | Completed | Load_250145 | Duncans - 210 | 2026-08-29 12:59 | 2026-08-29 12:59 | 2026-08-29 13:11 | 2026-08-29 13:15 | 2026-08-29 13:14 | 2026-08-29 13:18 | 2026-08-29 13:18 | 2026-08-29 13:18 |  |  | Fair | No | Call in discovery bay , reffer to st Ann emergency
Outage | J.E.26.08.67739 | C001904534 | Raheem Ricketts | Manchester | Completed | Load_265673 | Spur Tree - 210 | 2026-08-29 13:09 | 2026-08-29 13:09 | 2026-08-29 13:23 | 2026-08-29 13:44 | 2026-08-29 14:14 | 2026-08-29 14:34 | 2026-08-29 14:34 | 2026-08-29 14:34 | TreeContact |  | Fair | No | Isolate 25kva to Cut an remove tree from wire an reconnect school wire using tree clamps then reclosed 25kva
Outage | J.E.26.08.68910 | C001904535 | Edward Royal | KSAN | Completed | Load_257312 | Washington Blvd - 310 | 2026-08-29 13:20 | 2026-08-29 13:33 | 2026-08-29 13:41 | 2026-08-29 13:42 | 2026-08-29 13:41 | 2026-08-29 13:42 | 2026-08-29 13:43 | 2026-08-29 13:43 |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.08.58953 | C001904536 | Donald Cunningham | St.Catherine | Completed | Load_249773 | New Michelton - 210 | 2026-08-29 13:27 | 2026-08-29 13:28 | 2026-08-29 14:47 | 2026-08-29 14:48 | 2026-08-29 15:19 | 2026-08-29 15:20 | 2026-08-29 15:26 | 2026-08-29 15:26 |  |  | Fair | No | Premises not located customer not reachable
Outage | J.E.26.08.68085 | C001904539 | Tajay Bernard | Hanover | Completed | Load_260216 | Orange Bay - 210 | 2026-08-29 13:40 | 2026-08-29 13:41 | 2026-08-29 14:03 | 2026-08-29 14:04 | 2026-08-29 14:04 | 2026-08-29 14:09 | 2026-08-29 14:09 | 2026-08-29 14:09 |  |  | Fair | No | Related to previous call job number 61144
Outage | J.E.26.08.69058 | C001904541 | Wan Carlos Scarlett | Portmore | Completed | Load_243335 | Naggo Head - 610 | 2026-08-29 13:55 | 2026-08-29 15:03 | 2026-08-29 16:15 | 2026-08-29 16:15 | 2026-08-29 17:10 | 2026-08-29 17:33 | 2026-08-29 17:34 | 2026-08-29 17:34 |  |  | Fair | No | Customer confirm that issue was resolved by a next JPS team
Outage | J.E.26.08.69057 | C001904544 | Andrew Powell | Manchester | Completed | Load_258370 | Spur Tree - 210 | 2026-08-29 14:04 | 2026-08-29 15:17 | 2026-08-29 15:36 | 2026-08-29 15:38 | 2026-08-29 15:49 | 2026-08-29 15:49 | 2026-08-29 15:53 | 2026-08-29 15:53 |  |  | Fair | No | Found customer disconnected due to out standing bill, which now settled no communication to meter please refer to field service department for assistance.
Non-Outage | J.E.26.08.67666 | C001904547 | Daniel Francis | St.Ann | Completed | Load_248002 | Roaring River - 210 | 2026-08-29 14:18 | 2026-08-29 14:18 | 2026-08-29 14:23 | 2026-08-29 14:24 | 2026-08-29 14:25 | 2026-08-29 15:06 | 2026-08-29 15:06 | 2026-08-29 15:06 |  |  | Fair | No | Change 3 one bolt clamp at transformer 112 112 224 in all
Outage | J.E.26.08.69151 | C001904548 | Christopher Edwards | KSAN | Completed | Load_265532 | Constant Spring - 410 | 2026-08-29 14:24 | 2026-08-29 14:27 | 2026-08-29 14:31 | 2026-08-29 15:20 | 2026-08-29 15:19 | 2026-08-29 15:20 | 2026-08-29 15:20 | 2026-08-29 15:20 |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Outage | J.E.26.08.68237 | C001904550 | Richard Samuda | Manchester | Completed | Load_1002353 | Spur Tree - 310 | 2026-08-29 14:35 | 2026-08-29 14:36 | 2026-08-29 15:15 | 2026-08-29 15:16 | 2026-08-29 15:33 | 2026-08-29 04:20 | 2026-08-29 16:20 | 2026-08-29 16:20 |  |  | Fair | No | 0204591 found 25kva transformer fuse blown patrol line found nothing replaced fuse customer back to normal
Outage | J.E.26.08.69196 | C001904549 | Delano Gayle | St.Catherine | Completed | Load_253958 | Tredegar - 210 | 2026-08-29 14:35 | 2026-08-29 15:15 | 2026-08-29 15:22 | 2026-08-29 15:23 | 2026-08-29 16:50 | 2026-08-29 17:19 | 2026-08-29 17:19 | 2026-08-29 17:19 |  |  | Fair | No | Premises found okay power was restored
Non-Outage | J.E.26.08.69170 | C001904551 | Barnett Brown | Manchester | Completed | Load_255496 | Kendal - 210 | 2026-08-29 14:38 | 2026-08-30 08:01 | 2026-08-30 13:04 | 2026-08-30 13:04 | 2026-08-30 14:22 | 2026-08-30 14:47 | 2026-08-30 14:48 | 2026-08-30 14:48 | BrokenWire |  | Fair | No | Premises found ok, light was restored from yesterday
Outage | J.E.26.08.69015 | C001904552 | Stephen Taylor | St.Thomas | Completed | Load_264343 | Lysson - 410 | 2026-08-29 14:41 | 2026-08-29 14:41 | 2026-08-29 16:25 | 2026-08-29 16:25 | 2026-08-29 16:25 | 2026-08-29 16:25 | 2026-08-29 16:26 | 2026-08-29 16:26 |  |  | Fair | No | Premese found okay check with customer and customer said power is back now
Outage | J.E.26.08.69230 | C001904553 | Damion Reid | Manchester | Completed | Load_255496 | Kendal - 210 | 2026-08-29 14:42 | 2026-08-29 14:42 | 2026-08-29 20:05 | 2026-08-29 20:06 | 2026-08-29 21:38 | 2026-08-29 23:40 | 2026-08-29 23:46 | 2026-08-29 23:46 | BrokenWire |  | Rains | No | One span of broken neutral conductor found cause by banging of secondary phase an neutral open 25kva transformer fuse link splice an retention conductor using 20ft of #2 aluminum conductor two one bolt clamp and restore power
Non-Outage | J.E.26.08.63389 | C001904554 | Delano Gayle |  | Completed |  |  | 2026-08-29 15:09 | 2026-08-29 15:11 | 2026-08-29 20:57 | 2026-08-29 20:57 | 2026-08-29 21:43 | 2026-08-29 21:54 | 2026-08-29 21:54 | 2026-08-29 21:54 | TreeContact |  | Fair | No | Premises not found
Non-Outage | J.E.26.08.69210 | C001904555 | Wayne Dillion |  | Completed |  |  | 2026-08-29 15:16 | 2026-08-29 15:17 | 2026-08-29 17:41 | 2026-08-29 17:41 | 2026-08-29 17:41 | 2026-08-29 18:30 | 2026-08-29 18:33 | 2026-08-29 18:33 |  |  | Fair | No | Supply check and found corrosion at pot head. Repair same using 3 linkets. Supply leave working okay reading 108v, 109v and cross phase 217v at the end of the line.
Outage | J.E.26.08.69203 | C001904557 | Oshane Warren | Westmoreland | Completed | Load_245618 | Paradise - 310 | 2026-08-29 15:18 | 2026-08-29 15:19 | 2026-08-29 15:32 | 2026-08-29 15:32 | 2026-08-29 17:58 | 2026-08-29 18:02 | 2026-08-29 18:02 | 2026-08-29 18:02 |  |  | Fair | No | Reset 25kva transformer
Outage | J.E.26.08.69206 | C001904558 | Neville Spencer | Clarendon | Completed | Load_268174 | May Pen - 110 | 2026-08-29 15:19 | 2026-08-29 15:20 | 2026-08-29 15:44 | 2026-08-29 15:44 | 2026-08-29 18:22 | 2026-08-29 18:22 | 2026-08-29 22:47 | 2026-08-29 22:47 |  |  | Fair | No | Renew blown 10 amp J/ fuse keep rejecting need daylight attention.
Outage | J.E.26.08.69308 | C001904560 | Damion Reid | Manchester | Completed | Load_267454 | Kendal - 210 | 2026-08-29 15:22 | 2026-08-29 15:22 | 2026-08-29 16:43 | 2026-08-29 16:44 | 2026-08-29 17:22 | 2026-08-29 18:00 | 2026-08-29 18:01 | 2026-08-29 18:01 |  |  | Rains | No | Remade burnt off neutral at transformer drop lead using two one bolt clamp
Outage | J.E.26.08.69348 | C001904559 | Damion Reid | Manchester | Completed | Load_303111 | Kendal - 210 | 2026-08-29 15:22 | 2026-08-29 15:22 | 2026-08-29 15:40 | 2026-08-29 15:41 | 2026-08-29 16:20 | 2026-08-29 16:42 | 2026-08-29 16:42 | 2026-08-29 16:42 |  |  | Rains | No | Customer say she did not make any report
Outage | J.E.26.08.69053 | C001904561 | Romeo Brissett | St.James | Completed | Load_248229 | Queens Drive - 710 | 2026-08-29 15:23 | 2026-08-29 15:24 | 2026-08-29 15:36 | 2026-08-29 15:36 | 2026-08-29 16:59 | 2026-08-29 18:00 | 2026-08-29 17:13 | 2026-08-29 17:13 |  |  | Fair | No | Check and found internal fault, customer was advised to get an electrician, V/R 108-111-220
Non-Outage | J.E.26.07.37679 | C001904568 | Omar King | St.Ann | Completed | Load_255970 | Cardiff Hall - 210 | 2026-08-29 15:27 | 2026-08-29 15:28 | 2026-08-29 17:44 | 2026-08-29 17:45 | 2026-08-29 19:10 | 2026-08-29 19:10 | 2026-08-29 19:11 | 2026-08-29 19:11 |  |  | Fair | No | Problem resolved
Non-Outage | J.E.26.07.37703 | C001904567 | Omar King | St.Ann | Completed | Load_413033 | Cardiff Hall - 210 | 2026-08-29 15:27 | 2026-08-29 15:28 | 2026-08-29 19:11 | 2026-08-29 19:11 | 2026-08-29 19:15 | 2026-08-29 19:16 | 2026-08-29 19:16 | 2026-08-29 19:16 |  |  | Fair | No | Problem as been resolved
Non-Outage | J.E.26.07.37727 | C001904565 | Omar King | St.Ann | Completed | Load_267596 | Cardiff Hall - 210 | 2026-08-29 15:27 | 2026-08-29 15:28 | 2026-08-29 19:18 | 2026-08-29 19:18 | 2026-08-29 20:03 | 2026-08-29 20:03 | 2026-08-29 20:03 | 2026-08-29 20:03 |  |  | Fair | No | Problem resolved
Non-Outage | J.E.26.08.63774 | C001904566 | Omar King | St.Ann | Completed | Load_267462 | Upper White River - 210 | 2026-08-29 15:27 | 2026-08-29 15:28 | 2026-08-29 20:03 | 2026-08-29 20:04 | 2026-08-29 21:51 | 2026-08-29 21:51 | 2026-08-29 21:52 | 2026-08-29 21:52 |  |  | Fair | No | Unable to find customer customer call several times no answer directions given
Outage | J.E.26.08.68992 | C001904562 | Omar King | St.Ann | Completed | Load_262635 | Upper White River - 210 | 2026-08-29 15:27 | 2026-08-29 15:28 | 2026-08-29 16:09 | 2026-08-29 16:09 | 2026-08-29 16:09 | 2026-08-29 16:17 | 2026-08-29 16:18 | 2026-08-29 16:18 |  |  | Fair | No | Customer said problem as been resolved
Outage | J.E.26.08.69316 | C001904563 | Tajay Bernard | Hanover | Completed | Load_264340 | Orange Bay - 310 | 2026-08-29 15:27 | 2026-08-29 15:28 | 2026-08-29 16:42 | 2026-08-29 16:51 | 2026-08-29 17:49 | 2026-08-29 17:58 | 2026-08-29 17:59 | 2026-08-29 17:59 |  |  | Fair | No | Refuse 1 25kva Transformer use 2amp fuse
Outage | J.E.26.08.65708 | C001904575 | Romeo Brissett | St.James | Completed | Load_1001321 | Bogue - 510 | 2026-08-29 15:28 | 2026-08-29 17:43 | 2026-08-29 18:49 | 2026-08-29 18:50 | 2026-08-29 19:15 | 2026-08-29 19:31 | 2026-08-29 19:47 | 2026-08-29 19:47 |  |  | Fair | No | Line patrolled and found power in the area.
Outage | J.E.26.08.67310 | C001904573 | Derrick Dawkins | St.James | Completed | Load_239760 | Bogue - 610 | 2026-08-29 15:28 | 2026-08-29 15:30 | 2026-08-29 18:02 | 2026-08-29 18:03 | 2026-08-29 18:16 | 2026-08-29 18:22 | 2026-08-29 18:22 | 2026-08-29 18:22 |  |  | Fair | No | Premises close
Outage | J.E.26.08.68145 | C001904574 | Derrick Dawkins | St.James | Completed | Load_288986 | Bogue - 310 | 2026-08-29 15:28 | 2026-08-29 15:30 | 2026-08-29 15:43 | 2026-08-29 15:44 | 2026-08-29 17:44 | 2026-08-29 17:57 | 2026-08-29 17:57 | 2026-08-29 17:57 |  |  | Fair | No | Found 15 kva transformer fuse blown 2 amp due to bird replace 2 amp fuse
Outage | J.E.26.08.69318 | C001904572 | Derrick Dawkins | St.James | Completed | Load_246246 | Bogue - 610 | 2026-08-29 15:28 | 2026-08-29 15:30 | 2026-08-29 19:51 | 2026-08-29 19:51 | 2026-08-29 20:12 | 2026-08-29 20:17 | 2026-08-29 20:13 | 2026-08-29 20:13 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.69319 | C001904571 | Derrick Dawkins | St.James | Completed | Load_248794 | Bogue - 610 | 2026-08-29 15:28 | 2026-08-29 15:30 | 2026-08-29 18:23 | 2026-08-29 18:24 | 2026-08-29 19:39 | 2026-08-29 19:48 | 2026-08-29 19:50 | 2026-08-29 19:50 |  |  | Fair | No | Found 50 kva transformer fuse blown due to lightning replaced 5 amp no pole # available
Non-Outage | J.E.26.08.67763 | C001904578 | Cliton Henry | St.Mary | Completed | Load_246610 | Oracabessa - 110 | 2026-08-29 15:29 | 2026-08-29 15:30 | 2026-08-29 16:04 | 2026-08-29 16:06 | 2026-08-29 16:21 | 2026-08-29 17:32 | 2026-08-29 17:36 | 2026-08-29 17:36 |  |  | Fair | No | The voltages found were 95-156/241 volts due a defective splicing sleeve. Corrective work done to jumper the splicing sleeve using 1 foot 2/0 insulated conductor and 2 one bolt clamps. Voltages left were 118-118/236 volts
Non-Outage | J.E.26.08.67996 | C001904577 | Cliton Henry | St.Mary | Completed | Load_351415 | Oracabessa - 210 | 2026-08-29 15:29 | 2026-08-29 15:30 | 2026-08-29 15:59 | 2026-08-29 15:59 | 2026-08-29 16:04 | 2026-08-29 16:06 | 2026-08-29 16:06 | 2026-08-29 16:06 |  |  | Fair | No | RAMI infrastructure, Kindly refer to Field Service Department for follow up
Outage | J.E.26.08.64352 | C001904576 | Romeo Brissett | St.James | Completed | Load_261533 | Bogue - 510 | 2026-08-29 15:29 | 2026-08-29 17:43 | 2026-08-29 19:47 | 2026-08-29 19:47 | 2026-08-29 20:00 | 2026-08-29 20:00 | 2026-08-29 20:11 | 2026-08-29 20:11 |  |  | Fair | No | Resi Stated power was restored from yesterday
Outage | J.E.26.08.68182 | C001904584 | Roxroy Needham | St.Ann | Completed | Load_245873 | Cardiff Hall - 210 | 2026-08-29 15:33 | 2026-08-29 15:34 | 2026-08-29 18:35 | 2026-08-29 18:36 | 2026-08-29 19:52 | 2026-08-29 20:26 | 2026-08-29 20:27 | 2026-08-29 20:27 |  |  | Fair | No | Replace 2 - 25 amp junction fuse
Outage | J.E.26.08.68183 | C001904581 | Roxroy Needham | St.Ann | Completed | Load_241258 | Cardiff Hall - 310 | 2026-08-29 15:33 | 2026-08-29 15:34 | 2026-08-29 20:31 | 2026-08-29 20:32 | 2026-08-29 20:32 | 2026-08-29 20:34 | 2026-08-29 20:34 | 2026-08-29 20:34 |  |  | Fair | No | Light was restored
Outage | J.E.26.08.68220 | C001904580 | Roxroy Needham | St.Ann | Completed | Load_261514 | Cardiff Hall - 310 | 2026-08-29 15:33 | 2026-08-29 15:34 | 2026-08-29 20:34 | 2026-08-29 20:35 | 2026-08-29 20:34 | 2026-08-29 20:37 | 2026-08-29 20:38 | 2026-08-29 20:38 |  |  | Fair | No | Light was restored
Outage | J.E.26.08.68258 | C001904582 | Roxroy Needham | St.Ann | Completed | Load_239011 | Cardiff Hall - 210 | 2026-08-29 15:33 | 2026-08-29 15:34 | 2026-08-29 20:29 | 2026-08-29 20:30 | 2026-08-29 20:30 | 2026-08-29 20:30 | 2026-08-29 20:31 | 2026-08-29 20:31 |  |  | Fair | No | Light was restored
Outage | J.E.26.08.68985 | C001904583 | Roxroy Needham | St.Ann | Completed | Load_556105 | Cardiff Hall - 210 | 2026-08-29 15:33 | 2026-08-29 15:34 | 2026-08-29 20:28 | 2026-08-29 20:28 | 2026-08-29 20:28 | 2026-08-29 20:29 | 2026-08-29 20:29 | 2026-08-29 20:29 |  |  | Fair | No | Light was restored
Outage | J.E.26.08.69116 | C001904579 | Roxroy Needham | St.Ann | Completed | Load_261111 | Cardiff Hall - 310 | 2026-08-29 15:33 | 2026-08-29 15:34 | 2026-08-29 20:39 | 2026-08-29 20:40 | 2026-08-29 20:39 | 2026-08-29 20:40 | 2026-08-29 20:40 | 2026-08-29 20:40 |  |  | Fair | No | Light was restored
Non-Outage | J.E.26.08.62717 | C001904589 | Collin Robinson | Portland | Completed | Load_350322 | Port Antonio - 310 | 2026-08-29 15:44 | 2026-08-29 15:45 | 2026-08-29 16:37 | 2026-08-29 16:38 | 2026-08-29 17:49 | 2026-08-29 17:51 | 2026-08-29 17:51 | 2026-08-29 17:51 |  |  | Fair | No | Information received from customer that issue was resolved earlier today
Non-Outage | J.E.26.08.67599 | C001904587 | Collin Robinson | Portland | Completed | Load_238055 | Port Antonio - 310 | 2026-08-29 15:44 | 2026-08-29 15:45 | 2026-08-29 21:06 | 2026-08-29 21:07 | 2026-08-29 22:44 | 2026-08-29 22:23 | 2026-08-29 22:46 | 2026-08-29 22:46 |  |  | Fair | No | Premises found okMeter socket voltage 118v 117v 235v
Non-Outage | J.E.26.08.68941 | C001904588 | Collin Robinson | Portland | Completed | Load_238174 | Port Antonio - 410 | 2026-08-29 15:44 | 2026-08-29 15:45 | 2026-08-29 17:52 | 2026-08-29 17:52 | 2026-08-29 20:09 | 2026-08-29 20:19 | 2026-08-29 20:20 | 2026-08-29 20:20 |  |  | Fair | No | Burn meter found at location refer to field service
Non-Outage | J.E.26.08.69288 | C001904586 | Collin Robinson | Portland | Completed | Load_241517 | Port Antonio - 410 | 2026-08-29 15:44 | 2026-08-29 15:45 | 2026-08-29 15:56 | 2026-08-29 15:56 | 2026-08-29 16:35 | 2026-08-29 16:37 | 2026-08-29 16:37 | 2026-08-29 16:37 |  |  | Fair | No | Information received from customer that issue was resolved
Outage | J.E.26.08.68206 | C001904592 | Antony Levy | KSAN | Completed | Load_267839 | Constant Spring - 210 | 2026-08-29 15:58 | 2026-08-29 15:59 | 2026-08-29 16:08 | 2026-08-29 19:50 | 2026-08-29 20:32 | 2026-08-29 20:35 | 2026-08-29 20:37 | 2026-08-29 20:37 |  |  | Fair | No | Customer has an internal issue customer advised.
Outage | J.E.26.08.68217 | C001904591 | Antony Levy | KSAN | Completed | Load_254297 | Constant Spring - 210 | 2026-08-29 15:58 | 2026-08-29 15:59 | 2026-08-29 16:08 | 2026-08-29 16:08 | 2026-08-29 17:47 | 2026-08-29 18:36 | 2026-08-29 18:37 | 2026-08-29 18:37 | BrokenWire |  | Fair | No | Broken service wire across rd way splice using 50 ft of no.triplex and 6 clamps then retention and connect...left a voltage reading of 114 113 224 v
Non-Outage | J.E.26.08.48525 | C001904596 | Christopher Edwards | KSAN | Completed | Load_265459 | Constant Spring - 210 | 2026-08-29 16:02 | 2026-08-29 16:03 | 2026-08-29 16:08 | 2026-08-29 16:52 | 2026-08-29 17:08 | 2026-08-29 17:45 | 2026-08-29 17:47 | 2026-08-29 17:47 |  |  | Fair | No | Remake corroded neutral joint atUsing (1) one bolt clamps Voltage:109,110,219v
Non-Outage | J.E.26.08.55531 | C001904595 | Christopher Edwards | KSAN | Completed | Load_301884 | Constant Spring - 210 | 2026-08-29 16:02 | 2026-08-29 16:03 | 2026-08-29 19:06 | 2026-08-29 19:06 | 2026-08-29 19:06 | 2026-08-29 19:13 | 2026-08-29 19:15 | 2026-08-29 19:15 |  |  | Fair | No | Customer was contacted and stated that the issue
Non-Outage | J.E.26.08.61117 | C001904594 | Christopher Edwards | KSAN | Completed | Load_242072 | Constant Spring - 310 | 2026-08-29 16:02 | 2026-08-29 16:03 | 2026-08-29 19:15 | 2026-08-29 19:17 | 2026-08-29 19:17 | 2026-08-29 19:17 | 2026-08-29 19:40 | 2026-08-29 19:40 |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Non-Outage | J.E.26.08.61980 | C001904593 | Christopher Edwards | KSAN | Completed | Load_557886 | Constant Spring - 210 | 2026-08-29 16:02 | 2026-08-29 16:03 | 2026-08-29 17:47 | 2026-08-29 17:48 | 2026-08-29 17:57 | 2026-08-29 19:05 | 2026-08-29 19:05 | 2026-08-29 19:05 |  |  | Fair | No | Neutral jumper joint is burnt Remake joint using (1) one bolt clamps Voltage:119,120,241v
Non-Outage | J.E.26.08.45169 | C001904597 | Antony Levy | KSAN | Completed | Load_248139 | Constant Spring - 210 | 2026-08-29 16:03 | 2026-08-29 16:04 | 2026-08-29 16:18 | 2026-08-29 18:38 | 2026-08-29 19:12 | 2026-08-29 19:47 | 2026-08-29 19:49 | 2026-08-29 19:49 |  |  | Fair | No | Burnt off phase wire repair using 2 clamps and left a voltage reading of 115 116 232.
Non-Outage | J.E.26.08.61040 | C001904598 | Antony Levy | KSAN | Completed | Load_263212 | Washington Blvd - 810 | 2026-08-29 16:03 | 2026-08-29 16:04 | 2026-08-29 16:19 | 2026-08-29 22:04 | 2026-08-29 22:37 | 2026-08-29 22:49 | 2026-08-29 22:50 | 2026-08-29 22:50 |  |  | Fair | No | Premises closed
Non-Outage | J.E.26.08.63228 | C001904601 | Milton Charlton | KSAN | Completed | Load_263286 | Hope - 410 | 2026-08-29 16:04 | 2026-08-29 16:05 | 2026-08-29 17:48 | 2026-08-29 17:49 | 2026-08-29 17:49 | 2026-08-29 18:05 | 2026-08-29 18:10 | 2026-08-29 18:10 |  |  | Fair | No | Unable to locate customer by telephone. Nobody answering the gate or the telephone .number.
Non-Outage | J.E.26.08.63268 | C001904599 | Milton Charlton | KSAN | Completed | Load_251127 | Hope - 410 | 2026-08-29 16:04 | 2026-08-29 16:05 | 2026-08-29 16:38 | 2026-08-29 16:39 | 2026-08-29 17:13 | 2026-08-29 17:05 | 2026-08-29 17:34 | 2026-08-29 17:34 |  |  | Fair | No | Customer service wire #6 triplex corroded at pothead. Repair using two 1- bolt clamps. Readings at pothead 119-117-238 volts.
Non-Outage | J.E.26.08.68874 | C001904600 | Milton Charlton | KSAN | Completed | Load_256502 | Hope - 410 | 2026-08-29 16:04 | 2026-08-29 16:05 | 2026-08-29 17:34 | 2026-08-29 17:35 | 2026-08-29 17:44 | 2026-08-29 17:35 | 2026-08-29 17:48 | 2026-08-29 17:48 |  |  | Fair | No | Fo okay upon arrival. Customer did not made a report to JPS. Nobody living at the premises by the name Troy Smith.
Outage | J.E.26.08.69498 | C001904603 | Damion Reid | Manchester | Completed | Load_242925 | Kendal - 210 | 2026-08-29 16:10 | 2026-08-29 16:19 | 2026-08-29 18:01 | 2026-08-29 18:02 | 2026-08-29 19:26 | 2026-08-29 19:58 | 2026-08-29 20:00 | 2026-08-29 20:00 |  |  | Fair | No | Remade burnt off phase in PMC box for 3 wire service voltage reading at meter after correction phase to neutral 111v-113v across phase 226v
Non-Outage | J.E.26.08.69296 | C001904604 | Oshane Warren |  | Completed |  |  | 2026-08-29 16:12 | 2026-08-29 16:14 | 2026-08-29 18:02 | 2026-08-29 18:03 | 2026-08-29 18:02 | 2026-08-29 18:02 | 2026-08-29 18:03 | 2026-08-29 18:03 | BrokenWire |  | Fair | No | Customer stated that power was restored
Non-Outage | J.E.26.08.69515 | C001904607 | Rochaine Palmer |  | Completed |  |  | 2026-08-29 16:22 | 2026-08-29 16:25 | 2026-08-29 16:38 | 2026-08-29 18:50 | 2026-08-29 18:49 | 2026-08-29 19:54 | 2026-08-29 20:03 | 2026-08-29 20:03 | Fire |  | Fair | No | Isolate 50kva transformer at pole #0095002 and reconnect twisted #2/0 secondary burnt up in Honda superior fire. Customer are back whit supply.
Outage | J.E.26.08.69164 | C001904608 | Rochaine Palmer | KSAN | Completed | Load_567705 | Washington Blvd - 310 | 2026-08-29 16:22 | 2026-08-29 16:24 | 2026-08-29 16:55 | 2026-08-29 16:56 | 2026-08-29 17:23 | 2026-08-29 18:37 | 2026-08-29 18:48 | 2026-08-29 18:48 |  |  | Fair | No | Were twisted secondary meet's open wire secondary copper line one of the phase leg corroded and burnt . Repaired using two 1- one bolt clamps. Readings at customer pothead 108-107-216 volts.
Outage | J.E.26.08.69522 | C001904606 | Rusean Allen | KSAS | Completed | Load_251134 | Cane River - 310 | 2026-08-29 16:22 | 2026-08-29 17:12 | 2026-08-29 18:39 | 2026-08-29 18:39 | 2026-08-29 18:40 | 2026-08-29 18:40 | 2026-08-29 18:40 | 2026-08-29 18:40 |  |  | Fair | No | Related
Outage | J.E.26.08.69540 | C001904605 | Rusean Allen | KSAS | Completed | Load_300839 | Cane River - 410 | 2026-08-29 16:22 | 2026-08-29 17:12 | 2026-08-29 18:37 | 2026-08-29 18:38 | 2026-08-29 18:38 | 2026-08-29 18:38 | 2026-08-29 18:39 | 2026-08-29 18:39 |  |  | Fair | No | Related
Outage | J.E.26.08.69542 | C001904609 | Wan Carlos Scarlett | St.Catherine | Completed | Load_237897 | Twickenham - 210 | 2026-08-29 16:23 | 2026-08-29 16:26 | 2026-08-29 18:23 | 2026-08-29 18:24 | 2026-08-29 18:52 | 2026-08-29 19:22 | 2026-08-29 19:23 | 2026-08-29 19:23 |  |  | Fair | No | Customer confirm that power supply has been restored
Outage | J.E.26.08.69360 | C001904612 | Nickolas Rodriques | St.Catherine | Completed | Load_248615 | New Michelton - 210 | 2026-08-29 16:30 | 2026-08-29 16:32 | 2026-08-29 18:33 | 2026-08-29 18:41 | 2026-08-29 19:58 | 2026-08-29 20:37 | 2026-08-29 20:40 | 2026-08-29 20:40 |  |  | Fair | No | Customer is requesting a team on Sunday August 30 to do repair as he is unable to accommodate the team.
Outage | J.E.26.08.69418 | C001904611 | Delano Gayle | St.Catherine | Completed | Load_259990 | Rhodens Pen - 210 | 2026-08-29 16:30 | 2026-08-29 16:33 | 2026-08-29 19:21 | 2026-08-29 19:22 | 2026-08-29 20:16 | 2026-08-29 20:56 | 2026-08-29 20:57 | 2026-08-29 20:57 |  |  | Fair | No | Blown 25kva transformer fuse no pole number, banging secondary phase and neutral in 2 span, space 2 span secondary phase and neutral, replace 5amps
Outage | J.E.26.08.69429 | C001904610 | Delano Gayle | St.Catherine | Completed | Load_255316 | Rhodens Pen - 210 | 2026-08-29 16:30 | 2026-08-29 16:33 | 2026-08-29 17:19 | 2026-08-29 17:20 | 2026-08-29 18:16 | 2026-08-29 19:17 | 2026-08-29 19:17 | 2026-08-29 19:17 |  |  | Fair | No | Banging secondary phase and neutral in 1 span, burnt 25kva transformer neutral lead, open 25kva transformer fuse no pole number, retention 1 span secondary phase and neutral, repair burnt transformer lead use 6ft #8pvc copper 2 clamps voltage readings 113-114-226
Outage | J.E.26.08.69603 | C001904617 | Oshane Warren | St.Elizabeth | Completed | Load_270053 | Maggotty - 110 | 2026-08-29 16:55 | 2026-08-29 16:55 | 2026-08-29 18:03 | 2026-08-29 18:04 | 2026-08-29 18:03 | 2026-08-29 18:06 | 2026-08-29 18:09 | 2026-08-29 18:09 |  |  | Fair | No | Hexing metering system customer got disconnected for none payment of bill customer pay the amount and requesting a reconnection
Non-Outage | J.E.26.08.69578 | C001904618 | Richard Samuda |  | Completed |  |  | 2026-08-29 16:56 | 2026-08-29 17:10 | 2026-08-29 17:17 | 2026-08-29 17:25 | 2026-08-29 17:49 | 2026-08-29 17:50 | 2026-08-29 17:50 | 2026-08-29 17:50 |  |  | Fair | No | Found ok customer back to normal
Non-Outage | J.E.26.08.55478 | C001904622 | Romeo Brissett | St.James | Completed | Load_255008 | Bogue - 510 | 2026-08-29 17:36 | 2026-08-29 17:41 | 2026-08-29 18:21 | 2026-08-29 18:21 | 2026-08-29 18:32 | 2026-08-29 18:43 | 2026-08-29 18:49 | 2026-08-29 18:49 |  |  | Fair | No | Check and found internal fault, voltage reading 120-120-240
Outage | J.E.26.08.51086 | C001904623 | Andre Smith | KSAN | Completed | Load_256666 | Washington Blvd - 710 | 2026-08-29 17:47 | 2026-08-29 17:48 | 2026-08-29 17:55 | 2026-08-29 17:56 | 2026-08-29 18:13 | 2026-08-29 18:56 | 2026-08-29 18:56 | 2026-08-29 18:56 |  |  | Fair | No | Premises found okay supply restored already
Outage | J.E.26.08.69635 | C001904624 | Milton Charlton | KSAN | Completed | Load_242063 | Hope - 410 | 2026-08-29 17:56 | 2026-08-29 17:57 | 2026-08-29 18:10 | 2026-08-29 18:10 | 2026-08-29 19:00 | 2026-08-29 18:45 | 2026-08-29 19:02 | 2026-08-29 19:02 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.08.70257 | C001904627 | Antony Levy | KSAS | Completed | Load_257773 | Duhaney - 310 | 2026-08-29 18:14 | 2026-08-29 18:15 | 2026-08-29 19:50 | 2026-08-29 20:38 | 2026-08-29 20:55 | 2026-08-29 21:12 | 2026-08-29 21:15 | 2026-08-29 21:15 |  |  | Fair | No | Blown 30 junction fuse found due to bird contact patrol and refuse junction...no pole number.
Outage | J.E.26.08.69678 | C001904630 | Roxroy Needham | St.Ann | Completed | Load_246511 | Cardiff Hall - 210 | 2026-08-29 18:18 | 2026-08-29 18:19 | 2026-08-29 20:42 | 2026-08-29 20:43 | 2026-08-29 21:17 | 2026-08-29 21:17 | 2026-08-29 21:32 | 2026-08-29 21:32 | Fire |  | Fair | No | Premises found ok customer say that JPS team come before
Outage | J.E.26.08.70597 | C001904631 | Marlon Brown | Trelawny | Completed | Load_239232 | Greenwood - 110 | 2026-08-29 18:22 | 2026-08-29 19:58 | 2026-08-29 20:04 | 2026-08-29 20:04 | 2026-08-29 20:04 | 2026-08-29 20:04 | 2026-08-29 20:04 | 2026-08-29 20:04 |  |  | Fair | No | St James call
Outage | J.E.26.08.69316 | C001904632 | Tajay Bernard | Hanover | Completed | Load_264340 | Orange Bay - 310 | 2026-08-29 18:24 | 2026-08-29 18:25 | 2026-08-29 19:41 | 2026-08-29 19:42 | 2026-08-29 19:42 | 2026-08-29 19:43 | 2026-08-29 19:43 | 2026-08-29 19:43 |  |  | Fair | No | Customer stated that power was restored
Outage | J.E.26.08.70551 | C001904633 | Tajay Bernard | Hanover | Completed | Load_256535 | Orange Bay - 310 | 2026-08-29 18:24 | 2026-08-29 18:26 | 2026-08-29 19:43 | 2026-08-29 19:44 | 2026-08-29 20:54 | 2026-08-29 21:36 | 2026-08-29 21:37 | 2026-08-29 21:37 |  |  | Fair | No | Clear banging wire and refuse 1 25kva transformer use 2amp fuse
Outage | J.E.26.08.70654 | C001904634 | Marlon Brown | Trelawny | Completed | Load_245327 | Duncans - 210 | 2026-08-29 18:26 | 2026-08-29 18:27 | 2026-08-29 18:30 | 2026-08-29 18:31 | 2026-08-29 18:30 | 2026-08-29 18:31 | 2026-08-29 18:31 | 2026-08-29 18:31 |  |  | Fair | No | St James call
Outage | J.E.26.08.70726 | C001904635 | Marlon Brown | Trelawny | Completed | Load_292745 | Greenwood - 110 | 2026-08-29 18:28 | 2026-08-29 19:58 | 2026-08-29 20:03 | 2026-08-29 20:03 | 2026-08-29 20:03 | 2026-08-29 20:03 | 2026-08-29 20:03 | 2026-08-29 20:03 |  |  | Fair | No | St James call
Outage | J.E.26.08.70347 | C001904636 | Derrick Dawkins | St.James | Completed | Load_244772 | Bogue - 610 | 2026-08-29 18:30 | 2026-08-29 18:39 | 2026-08-29 20:13 | 2026-08-29 20:14 | 2026-08-29 20:29 | 2026-08-29 20:34 | 2026-08-29 20:29 | 2026-08-29 20:29 |  |  | Fair | No | Cannot locate premises
Outage | J.E.26.08.70478 | C001904640 | Swon Miller | St.James | Completed | Load_244479 | Queens Drive - 810 | 2026-08-29 18:39 | 2026-08-29 18:40 | 2026-08-29 19:40 | 2026-08-29 19:40 | 2026-08-29 20:19 | 2026-08-29 20:46 | 2026-08-29 20:49 | 2026-08-29 20:49 |  |  | Fair | No | Check and found okay voltage found 114/115/231 voltage left 114/115/ customer states this is an old report
Outage | J.E.26.08.70740 | C001904639 | Derrick Dawkins | St.James | Completed | Load_240097 | Rose Hall - 210 | 2026-08-29 18:39 | 2026-08-30 08:00 | 2026-08-30 08:18 | 2026-08-30 09:24 | 2026-08-30 09:32 | 2026-08-30 09:02 | 2026-08-30 09:35 | 2026-08-30 09:35 |  |  | Fair | No | Found premises ok
Non-Outage | J.E.26.08.70334 | C001904643 | Andre Smith |  | Completed |  |  | 2026-08-29 18:42 | 2026-08-29 19:21 | 2026-08-29 21:05 | 2026-08-29 21:06 | 2026-08-29 21:54 | 2026-08-29 21:55 | 2026-08-29 21:55 | 2026-08-29 21:55 | Fire |  | Fair | No | Maintenance department replacing defective transformer
Outage | J.E.26.08.70281 | C001904641 | Rochaine Palmer | KSAN | Completed | Load_263228 | Washington Blvd - 710 | 2026-08-29 18:42 | 2026-08-29 18:43 | 2026-08-29 20:04 | 2026-08-29 20:04 | 2026-08-29 20:15 | 2026-08-29 20:25 | 2026-08-29 20:24 | 2026-08-29 20:24 |  |  | Fair | No | Customer fed from Y.P. Box # 03798 and getting a low voltage from the box readings 86-53-140 volts. Refer to field service.
Outage | J.E.26.08.70481 | C001904644 | Andre Smith | KSAS | Completed | Load_264427 | Greenwich - 310 | 2026-08-29 18:42 | 2026-08-29 19:21 | 2026-08-29 19:27 | 2026-08-29 19:27 | 2026-08-29 20:14 | 2026-08-29 21:05 | 2026-08-29 21:05 | 2026-08-29 21:05 |  |  | Fair | No | Reset breaker supply restored remove illegal connections in box
Outage | J.E.26.08.70289 | C001904646 | Tajay Bernard | St.James | Completed | Load_252666 | Bogue - 510 | 2026-08-29 18:45 | 2026-08-29 18:46 | 2026-08-29 19:40 | 2026-08-29 19:41 | 2026-08-29 19:40 | 2026-08-29 19:41 | 2026-08-29 19:41 | 2026-08-29 19:41 |  |  | Fair | No | This called belongs to st james
Outage | J.E.26.08.70594 | C001904649 | Romeo Brissett | St.James | Completed | Load_1001859 | Bogue - 610 | 2026-08-29 19:04 | 2026-08-29 19:06 | 2026-08-29 20:11 | 2026-08-29 20:12 | 2026-08-29 20:36 | 2026-08-29 20:45 | 2026-08-29 20:46 | 2026-08-29 20:46 |  |  | Fair | No | Patrolled and found maintenance team onsite DA switched is isolated at Tucker due to broken main line.
Outage | J.E.26.08.71247 | C001904653 | Rusean Allen | KSAS | Completed | Load_239287 | Rockfort - 210 | 2026-08-29 19:40 | 2026-08-29 19:43 | 2026-08-29 20:50 | 2026-08-29 21:34 | 2026-08-29 21:52 | 2026-08-29 22:07 | 2026-08-29 22:08 | 2026-08-29 22:08 | Fire |  | Fair | No | Burnt clamp found at pole, clamp was changed.
Outage | J.E.26.08.71105 | C001904654 | Wayne Dillion | St.Elizabeth | Completed | Load_267768 | Maggotty - 110 | 2026-08-29 19:42 | 2026-08-29 19:43 | 2026-08-29 19:50 | 2026-08-29 19:51 | 2026-08-29 19:50 | 2026-08-29 19:53 | 2026-08-29 19:53 | 2026-08-29 19:53 |  |  | Fair | No | Please refer this call to the field services department.
Outage | J.E.26.08.70945 | C001904658 | Marlon Brown | Trelawny | Completed | Load_1000587 | Greenwood - 110 | 2026-08-29 19:58 | 2026-08-29 20:02 | 2026-08-29 20:20 | 2026-08-29 20:21 | 2026-08-29 20:20 | 2026-08-29 20:21 | 2026-08-29 20:21 | 2026-08-29 20:21 |  |  | Fair | No | St James call
Outage | J.E.26.08.70966 | C001904660 | Marlon Brown | Trelawny | Completed | Load_1001713 | Greenwood - 110 | 2026-08-29 19:58 | 2026-08-29 20:02 | 2026-08-29 20:19 | 2026-08-29 20:20 | 2026-08-29 20:19 | 2026-08-29 20:20 | 2026-08-29 20:20 | 2026-08-29 20:20 |  |  | Fair | No | St James call
Outage | J.E.26.08.71230 | C001904657 | Marlon Brown | Trelawny | Completed | Load_265828 | Duncans - 110 | 2026-08-29 19:58 | 2026-08-29 20:02 | 2026-08-29 20:22 | 2026-08-29 20:22 | 2026-08-29 20:50 | 2026-08-29 20:51 | 2026-08-29 20:51 | 2026-08-29 20:51 |  |  | Fair | No | Customer says she didn’t make any report to jps and she has electricity and doesn’t have any issues with it.
Outage | J.E.26.08.71606 | C001904659 | Marlon Brown | Trelawny | Completed | Load_238650 | Greenwood - 110 | 2026-08-29 19:58 | 2026-08-29 20:02 | 2026-08-29 20:18 | 2026-08-29 20:19 | 2026-08-29 20:18 | 2026-08-29 20:19 | 2026-08-29 20:19 | 2026-08-29 20:19 |  |  | Fair | No | St James call
Outage | J.E.26.08.71581 | C001904661 | Wan Carlos Scarlett | St.Catherine | Completed | Load_267094 | Twickenham - 210 | 2026-08-29 20:01 | 2026-08-29 20:02 | 2026-08-29 20:07 | 2026-08-29 20:08 | 2026-08-29 20:49 | 2026-08-29 21:14 | 2026-08-29 21:16 | 2026-08-29 21:16 |  |  | Fair | No | Found customer 2 wire service at pole and pothead corroded use 2 Penn union and 2 one bolt clamps at pole and pothead reading 116
Outage | J.E.26.08.71040 | C001904662 | Tajay Bernard | Hanover | Completed | Load_264368 | Orange Bay - 310 | 2026-08-29 20:03 | 2026-08-29 20:07 | 2026-08-29 21:37 | 2026-08-29 21:38 | 2026-08-29 22:09 | 2026-08-29 22:13 | 2026-08-29 22:13 | 2026-08-29 22:13 | Fire |  | Fair | No | Area check and Found okay, no fire was found on the line. Multiple phone calls to customer number went unanswered
Outage | J.E.26.08.71086 | C001904663 | Tajay Bernard | Hanover | Completed | Load_264328 | Orange Bay - 310 | 2026-08-29 20:04 | 2026-08-29 20:07 | 2026-08-29 22:27 | 2026-08-29 22:28 | 2026-08-29 22:32 | 2026-08-29 22:33 | 2026-08-29 22:33 | 2026-08-29 22:33 |  |  | Fair | No | Area check and found okay customer stated that they didn’t made no report
Outage | J.E.26.08.71350 | C001904664 | Tajay Bernard | Hanover | Completed | Load_238848 | Orange Bay - 310 | 2026-08-29 20:04 | 2026-08-29 20:07 | 2026-08-29 22:14 | 2026-08-29 22:14 | 2026-08-29 22:25 | 2026-08-29 22:27 | 2026-08-29 22:27 | 2026-08-29 22:27 |  |  | Fair | No | Area check and found okay, customers stated they didn’t made a report
Outage | J.E.26.08.70837 | C001904667 | Swon Miller | St.James | Completed | Load_240373 | Queens Drive - 710 | 2026-08-29 20:11 | 2026-08-29 20:12 | 2026-08-29 20:52 | 2026-08-29 20:53 | 2026-08-29 22:04 | 2026-08-29 22:16 | 2026-08-29 22:24 | 2026-08-29 22:24 |  |  | Fair | No | Check and found area okay voltage found 117/116/234 centimeter states that power supply has been restored voltage left 117/116/234
Outage | J.E.26.08.70923 | C001904665 | Derrick Dawkins | St.James | Completed | Load_245170 | Queens Drive - 710 | 2026-08-29 20:11 | 2026-08-30 07:45 | 2026-08-30 08:16 | 2026-08-30 14:23 | 2026-08-30 14:26 | 2026-08-30 14:28 | 2026-08-30 14:28 | 2026-08-30 14:28 |  |  | Fair | No | Check and found customer ok
Outage | J.E.26.08.70976 | C001904666 | Derrick Dawkins | St.James | Completed | Load_237906 | Rose Hall - 210 | 2026-08-29 20:11 | 2026-08-30 08:00 | 2026-08-30 09:31 | 2026-08-30 13:09 | 2026-08-30 13:51 | 2026-08-30 13:52 | 2026-08-30 13:53 | 2026-08-30 13:53 |  |  | EarthMovement | No | Cannot locate customer
Outage | J.E.26.08.71623 | C001904669 | Lancelot Brown | Hanover | Completed | Load_268987 | Orange Bay - 310 | 2026-08-29 20:17 | 2026-08-30 07:27 | 2026-08-30 07:43 | 2026-08-30 11:02 | 2026-08-30 11:02 | 2026-08-30 11:04 | 2026-08-30 11:05 | 2026-08-30 11:05 |  |  | Fair | No | This call related to 25kva dropleed joint and secondary jumper
Outage | J.E.26.08.71611 | C001904670 | Rochaine Palmer | KSAN | Completed | Load_253322 | Washington Blvd - 310 | 2026-08-29 20:27 | 2026-08-29 20:28 | 2026-08-29 21:04 | 2026-08-29 21:05 | 2026-08-29 21:10 | 2026-08-29 21:10 | 2026-08-29 21:12 | 2026-08-29 21:12 |  |  | Fair | No | Matter was resolved.
Non-Outage | J.E.26.08.70896 | C001904671 | Stephen Taylor |  | Completed |  |  | 2026-08-29 20:40 | 2026-08-29 20:42 | 2026-08-29 21:20 | 2026-08-29 21:20 | 2026-08-29 21:20 | 2026-08-29 21:20 | 2026-08-29 21:21 | 2026-08-29 21:21 |  |  | Fair | No | Failed to locate customer several calls but no one answering the phone
Outage | J.E.26.08.68015 | C001904672 | Stephen Taylor | St.Thomas | Completed | Load_237781 | Good Year - 110 | 2026-08-29 20:40 | 2026-08-29 20:42 | 2026-08-29 20:46 | 2026-08-29 20:50 | 2026-08-29 20:49 | 2026-08-29 20:50 | 2026-08-29 20:51 | 2026-08-29 20:51 |  |  | Fair | No | Call to customer and customer said power is back now and okay
Outage | J.E.26.08.71927 | C001904673 | Richman Whyte | Westmoreland | Completed | Load_242128 | Paradise - 210 | 2026-08-29 20:40 | 2026-08-29 20:41 | 2026-08-29 21:10 | 2026-08-29 21:11 | 2026-08-29 23:34 | 2026-08-30 00:35 | 2026-08-30 00:35 | 2026-08-30 00:35 |  |  | Fair | No | Open fifty kva transformer fuse repair one span open secondary conductor top and lower phase use 8 one bolt clamps 40 feet 2/0 open aluminum conductor and one 2/0 splicing sleeve voltage 114 115 230
Outage | J.E.26.08.70289 | C001904675 | Horace Malcolm | St.James | Completed | Load_252666 | Bogue - 510 | 2026-08-29 21:50 | 2026-08-30 07:47 | 2026-08-30 09:20 | 2026-08-30 09:21 | 2026-08-30 09:55 | 2026-08-30 10:10 | 2026-08-30 10:10 | 2026-08-30 10:10 |  |  | Fair | No | Change burnt clamps on transformer drop lead used one clamps 117-120-237-208
Outage | J.E.26.08.73158 | C001904677 | Romeo Brissett | St.James | Completed | Load_556791 | Bogue - 310 | 2026-08-29 21:58 | 2026-08-29 21:59 | 2026-08-29 23:26 | 2026-08-29 23:27 | 2026-08-29 23:41 | 2026-08-30 12:14 | 2026-08-30 00:17 | 2026-08-30 00:17 |  |  | Fair | No | Removed bird and replaced (1)50kva transformer fuse.
Outage | J.E.26.08.73458 | C001904683 | Romeo Brissett | St.James | Completed | Load_301687 | Bogue - 310 | 2026-08-29 23:04 | 2026-08-29 23:08 | 2026-08-30 02:02 | 2026-08-30 05:02 | 2026-08-30 06:08 | 2026-08-30 07:00 | 2026-08-30 07:15 | 2026-08-30 07:15 | Fire |  | Fair | No | (1)25 transformer drop lead found burned of due to illegal connections repaired. Isolated (1)25KVA transformer, repaired drop lead.
Outage | J.E.26.08.72737 | C001904685 | Romeo Brissett | St.James | Completed | Load_253128 | Queens Drive - 710 | 2026-08-29 23:05 | 2026-08-29 23:08 | 2026-08-30 00:17 | 2026-08-30 00:18 | 2026-08-30 01:00 | 2026-08-30 02:00 | 2026-08-30 02:02 | 2026-08-30 02:02 |  |  | Fair | No | Line patrolled and found power in the area.
Outage | J.E.26.08.73431 | C001904684 | Romeo Brissett | St.James | Completed | Load_249465 | Queens Drive - 710 | 2026-08-29 23:05 | 2026-08-29 23:08 | 2026-08-30 02:03 | 2026-08-30 02:04 | 2026-08-30 03:03 | 2026-08-30 04:50 | 2026-08-30 05:02 | 2026-08-30 05:02 |  |  | Fair | No | Line patrolled and found power in the area.
Outage | J.E.26.08.72412 | C001904687 | Edward Royal | KSAN | Completed | Load_262237 | Washington Blvd - 310 | 2026-08-29 23:09 | 2026-08-29 23:12 | 2026-08-29 23:45 | 2026-08-29 23:46 | 2026-08-29 23:45 | 2026-08-29 23:46 | 2026-08-29 23:46 | 2026-08-29 23:46 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.72957 | C001904686 | Edward Royal | KSAS | Completed | Load_265849 | Rockfort - 210 | 2026-08-29 23:09 | 2026-08-29 23:12 | 2026-08-29 23:41 | 2026-08-29 23:42 | 2026-08-29 23:41 | 2026-08-29 23:42 | 2026-08-29 23:42 | 2026-08-29 23:42 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.71633 | C001904690 | Edward Royal | KSAN | Completed | Load_256666 | Washington Blvd - 710 | 2026-08-29 23:10 | 2026-08-29 23:12 | 2026-08-29 23:37 | 2026-08-29 23:38 | 2026-08-29 23:37 | 2026-08-29 23:38 | 2026-08-29 23:39 | 2026-08-29 23:39 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.71824 | C001904689 | Edward Royal | KSAN | Completed | Load_256666 | Washington Blvd - 710 | 2026-08-29 23:10 | 2026-08-29 23:12 | 2026-08-29 23:39 | 2026-08-29 23:40 | 2026-08-29 23:39 | 2026-08-29 23:40 | 2026-08-29 23:41 | 2026-08-29 23:41 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.72104 | C001904688 | Edward Royal | KSAS | Completed | Load_244355 | Hunts Bay - 210 | 2026-08-29 23:10 | 2026-08-29 23:12 | 2026-08-29 23:42 | 2026-08-29 23:43 | 2026-08-29 23:42 | 2026-08-29 23:45 | 2026-08-29 23:45 | 2026-08-29 23:45 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.73345 | C001904691 | Edward Royal | KSAS | Completed | Load_240364 | Cane River - 410 | 2026-08-29 23:10 | 2026-08-29 23:12 | 2026-08-29 23:34 | 2026-08-29 23:34 | 2026-08-29 23:34 | 2026-08-29 23:35 | 2026-08-29 23:35 | 2026-08-29 23:35 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.71417 | C001904694 | Delano Gayle | St.Catherine | Completed | Load_253958 | Tredegar - 210 | 2026-08-29 23:12 | 2026-08-29 23:17 | 2026-08-30 01:17 | 2026-08-30 01:17 | 2026-08-30 03:05 | 2026-08-30 03:06 | 2026-08-30 03:06 | 2026-08-30 03:06 |  |  | Fair | No | Premises found okay power was restored
Outage | J.E.26.08.72417 | C001904693 | Delano Gayle | St.Catherine | Completed | Load_260424 | Rhodens Pen - 410 | 2026-08-29 23:12 | 2026-08-29 23:17 | 2026-08-30 00:27 | 2026-08-30 00:27 | 2026-08-30 01:07 | 2026-08-30 01:16 | 2026-08-30 01:16 | 2026-08-30 01:16 |  |  | Fair | No | Premises not found no answer from customer phone, area patrolled and found okay
Outage | J.E.26.08.72857 | C001904692 | Delano Gayle | St.Catherine | Completed | Load_238240 | Rhodens Pen - 410 | 2026-08-29 23:12 | 2026-08-29 23:17 | 2026-08-29 23:20 | 2026-08-29 23:24 | 2026-08-30 00:15 | 2026-08-30 00:26 | 2026-08-30 00:27 | 2026-08-30 00:27 |  |  | Fair | No | Premises and area found okay
Outage | J.E.26.08.73474 | C001904695 | Delano Gayle | St.Catherine | Completed | Load_258281 | Tredegar - 510 | 2026-08-29 23:13 | 2026-08-29 23:17 | 2026-08-30 05:24 | 2026-08-30 05:24 | 2026-08-30 06:01 | 2026-08-30 07:27 | 2026-08-30 07:29 | 2026-08-30 07:29 |  |  | Fair | No | Premises found power was restored
Outage | J.E.26.08.71745 | C001904698 | Delano Gayle | St.Catherine | Completed | Load_261569 | Twickenham - 210 | 2026-08-29 23:17 | 2026-08-29 23:18 | 2026-08-30 03:06 | 2026-08-30 04:09 | 2026-08-30 04:37 | 2026-08-30 04:51 | 2026-08-30 04:51 | 2026-08-30 04:51 |  |  | Fair | No | Premises not found no answer from customer phone, area found okay
Non-Outage | J.E.26.08.73858 | C001904699 | Raymond Lewis |  | Completed |  |  | 2026-08-29 23:19 | 2026-08-29 23:20 | 2026-08-29 23:36 | 2026-08-29 23:36 | 2026-08-30 01:01 | 2026-08-30 13:12 | 2026-08-30 01:12 | 2026-08-30 01:12 | Fire |  | Flood | No | No fire seen
Outage | J.E.26.08.73915 | C001904707 | Delano Gayle | St.Catherine | Completed | Load_251909 | Twickenham - 210 | 2026-08-30 03:34 | 2026-08-30 03:35 | 2026-08-30 05:12 | 2026-08-30 05:13 | 2026-08-30 05:22 | 2026-08-30 05:23 | 2026-08-30 05:23 | 2026-08-30 05:23 |  |  | Fair | No | Premises found okay by phone call customer states no outage was in area
Outage | J.E.26.08.74339 | C001904710 | Ricky Hall | St.Catherine | Completed | Load_238876 | New Michelton - 210 | 2026-08-30 03:48 | 2026-08-30 07:43 | 2026-08-30 08:14 | 2026-08-30 11:06 | 2026-08-30 11:06 | 2026-08-30 11:06 | 2026-08-30 11:06 | 2026-08-30 11:06 |  |  | Fair | No | Call associated with outage #75127
Outage | J.E.26.08.74101 | C001904712 | Edward Royal | KSAN | Completed | Load_261791 | Hope - 510 | 2026-08-30 04:41 | 2026-08-30 04:45 | 2026-08-30 05:27 | 2026-08-30 05:28 | 2026-08-30 05:27 | 2026-08-30 05:28 | 2026-08-30 05:28 | 2026-08-30 05:28 |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.08.74921 | C001904716 | Edward Royal | KSAN | Completed | Load_249412 | Constant Spring - 210 | 2026-08-30 06:24 | 2026-08-30 06:27 | 2026-08-30 06:59 | 2026-08-30 07:00 | 2026-08-30 07:26 | 2026-08-30 07:36 | 2026-08-30 07:37 | 2026-08-30 07:37 |  |  | Fair | No | Replaced 25A junction fuse
Outage | J.E.26.08.74821 | C001904718 | Horace Malcolm | St.James | Completed | Load_262659 | Bogue - 610 | 2026-08-30 06:29 | 2026-08-30 07:47 | 2026-08-30 08:16 | 2026-08-30 08:17 | 2026-08-30 08:47 | 2026-08-30 09:13 | 2026-08-30 09:13 | 2026-08-30 09:13 |  |  | Fair | No | Ref two 30amp junction fuses
Outage | J.E.26.08.74941 | C001904719 | Horace Malcolm | St.James | Completed | Load_237694 | Bogue - 610 | 2026-08-30 06:30 | 2026-08-30 07:47 | 2026-08-30 09:19 | 2026-08-30 09:19 | 2026-08-30 09:19 | 2026-08-30 09:19 | 2026-08-30 09:19 | 2026-08-30 09:19 | BrokenWire |  | Fair | No | Call belongs to port Antonio
Outage | J.E.26.08.74172 | C001904720 | Roxroy Needham | St.Ann | Completed | Load_259577 | Cardiff Hall - 310 | 2026-08-30 07:09 | 2026-08-30 07:09 | 2026-08-30 09:19 | 2026-08-30 09:20 | 2026-08-30 09:21 | 2026-08-30 09:19 | 2026-08-30 09:22 | 2026-08-30 09:22 |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.08.74816 | C001904721 | Roxroy Needham | St.Ann | Completed | Load_1007080 | Cardiff Hall - 210 | 2026-08-30 07:10 | 2026-08-30 07:11 | 2026-08-30 09:15 | 2026-08-30 09:15 | 2026-08-30 09:15 | 2026-08-30 09:15 | 2026-08-30 09:16 | 2026-08-30 09:16 |  |  | Fair | No | Premises found ok call customer and customer say that the light is ok
Outage | J.E.26.08.69300 | C001904722 | Roxroy Needham | St.Ann | Completed | Load_265058 | Cardiff Hall - 210 | 2026-08-30 07:13 | 2026-08-30 07:29 | 2026-08-30 09:17 | 2026-08-30 09:18 | 2026-08-30 09:17 | 2026-08-30 09:18 | 2026-08-30 09:18 | 2026-08-30 09:18 |  |  | Fair | No | Premises found ok call customer and customer say that the light is back from yesterday
Outage | J.E.26.08.73852 | C001904723 | Javid Vernon | Westmoreland | Completed | Load_262638 | Paradise - 110 | 2026-08-30 07:15 | 2026-08-30 07:27 | 2026-08-30 09:19 | 2026-08-30 09:20 | 2026-08-30 09:47 | 2026-08-30 10:01 | 2026-08-30 10:01 | 2026-08-30 10:01 |  |  | Fair | No | Refuse one 15kva transformer use 2amp fuse
Outage | J.E.26.08.72230 | C001904724 | Omar King | St.Ann | Completed | Load_250016 | Ocho Rios - 510 | 2026-08-30 07:18 | 2026-08-30 07:19 | 2026-08-30 09:23 | 2026-08-30 09:24 | 2026-08-30 10:25 | 2026-08-30 10:29 | 2026-08-30 10:30 | 2026-08-30 10:30 |  |  | Fair | No | Problem resolved
Non-Outage | J.E.26.08.73546 | C001904727 | Collin Robinson |  | Completed |  |  | 2026-08-30 07:20 | 2026-08-30 07:21 | 2026-08-30 10:24 | 2026-08-30 10:24 | 2026-08-30 11:17 | 2026-08-30 12:09 | 2026-08-30 12:11 | 2026-08-30 12:11 |  |  | Rains | No | Clear bamboo from 2 phase of primary conductor and close two 30Amps trip saver
Outage | J.E.26.08.73098 | C001904729 | Raymond Carr | St.Mary | Completed | Load_251110 | Oracabessa - 110 | 2026-08-30 07:25 | 2026-08-30 07:26 | 2026-08-30 12:11 | 2026-08-30 12:11 | 2026-08-30 12:11 | 2026-08-23 | 2026-08-30 12:12 | 2026-08-30 12:12 |  |  | Fair | No | Fault was corrected, and supply was restored.
Outage | J.E.26.08.73938 | C001904728 | Javid Vernon | Westmoreland | Completed | Load_259530 | Paradise - 110 | 2026-08-30 07:25 | 2026-08-30 07:26 | 2026-08-30 10:06 | 2026-08-30 10:06 | 2026-08-30 10:17 | 2026-08-30 10:18 | 2026-08-30 10:18 | 2026-08-30 10:18 |  |  | Fair | No | Customer stated that the power was restored
Outage | J.E.26.08.74887 | C001904730 | Javid Vernon | Westmoreland | Completed | Load_412863 | Paradise - 210 | 2026-08-30 07:25 | 2026-08-30 07:26 | 2026-08-30 08:15 | 2026-08-30 08:16 | 2026-08-30 08:42 | 2026-08-30 09:16 | 2026-08-30 09:16 | 2026-08-30 09:16 |  |  | Fair | No | Refuse one 15amp junction fuse
Non-Outage | J.E.26.08.75025 | C001904735 | Raymond Carr |  | Completed |  |  | 2026-08-30 07:26 | 2026-08-30 07:27 | 2026-08-30 18:07 | 2026-08-30 18:07 | 2026-08-30 20:00 | 2026-08-30 19:48 | 2026-08-30 20:02 | 2026-08-30 20:02 | Fire |  | Fair | No | Several calls to contact number went unanswered.
Outage | J.E.26.08.73217 | C001904731 | Lancelot Brown | Hanover | Completed | Load_244715 | Orange Bay - 310 | 2026-08-30 07:26 | 2026-08-30 07:49 | 2026-08-30 11:11 | 2026-08-30 11:12 | 2026-08-30 11:11 | 2026-08-30 11:12 | 2026-08-30 11:12 | 2026-08-30 11:12 |  |  | Fair | No | Check and found ok customer said did not made a report
Outage | J.E.26.08.75049 | C001904733 | Raymond Carr | St.Mary | Completed | Load_254708 | Oracabessa - 210 | 2026-08-30 07:26 | 2026-08-30 07:26 | 2026-08-30 08:20 | 2026-08-30 08:21 | 2026-08-30 09:46 | 2026-08-30 10:00 | 2026-08-30 10:52 | 2026-08-30 10:52 |  |  | Fair | No | Line patrol and found primary jumper burnt off. Same was spliced and retention using two clamps and 10 ft#2aa. Supply was restored.
Outage | J.E.26.08.75007 | C001904737 | Raymond Carr | St.Mary | Completed | Load_269808 | Oracabessa - 110 | 2026-08-30 07:27 | 2026-08-30 07:28 | 2026-08-30 10:57 | 2026-08-30 10:58 | 2026-08-30 11:34 | 2026-08-30 12:00 | 2026-08-30 12:11 | 2026-08-30 12:11 |  |  | Fair | No | Burnt off transformer drop lead was reconnected, two clamps were used. Supply was restored.
Outage | J.E.26.08.75134 | C001904738 | Lancelot Brown | Hanover | Completed | Load_252500 | Orange Bay - 310 | 2026-08-30 07:27 | 2026-08-30 07:28 | 2026-08-30 07:43 | 2026-08-30 11:13 | 2026-08-30 12:51 | 2026-08-30 13:34 | 2026-08-30 13:35 | 2026-08-30 13:35 | Fire |  | Fair | No | Drop and splice and retention triplex service line used sixty feet #6 three connectors three pg clamps vl at pothead 114-115-230 supply restore also carry out bushing to replace service line
Outage | J.E.26.08.72634 | C001904740 | Floyd Taylor | Trelawny | Completed | Load_265828 | Duncans - 110 | 2026-08-30 07:28 | 2026-08-30 07:30 | 2026-08-30 12:52 | 2026-08-30 12:53 | 2026-08-30 13:43 | 2026-08-30 13:43 | 2026-08-30 13:44 | 2026-08-30 13:44 |  |  | Fair | No
Outage | J.E.26.08.73297 | C001904741 | Floyd Taylor | Trelawny | Completed | Load_556439 | Duncans - 210 | 2026-08-30 07:28 | 2026-08-30 07:29 | 2026-08-30 11:00 | 2026-08-30 11:01 | 2026-08-30 12:01 | 2026-08-30 12:02 | 2026-08-30 12:02 | 2026-08-30 12:02 |  |  | Fair | No
Outage | J.E.26.08.75128 | C001904739 | Raymond Carr | St.Mary | Completed | Load_261240 | Oracabessa - 210 | 2026-08-30 07:28 | 2026-08-30 07:28 | 2026-08-30 10:52 | 2026-08-30 10:53 | 2026-08-30 10:52 | 2026-08-30 10:00 | 2026-08-30 10:53 | 2026-08-30 10:53 |  |  | Fair | No | Supply was restored.
Outage | J.E.26.08.74707 | C001904742 | Floyd Taylor | Trelawny | Completed | Load_292773 | Greenwood - 110 | 2026-08-30 07:29 | 2026-08-30 07:30 | 2026-08-30 07:42 | 2026-08-30 07:43 | 2026-08-30 09:01 | 2026-08-30 10:27 | 2026-08-30 10:56 | 2026-08-30 10:56 |  |  | Fair | No | Cut tree off line and replace 25kva transformer blown fuse 1-3amp and also closed up trip saver in Wakefield square
Outage | J.E.26.08.73570 | C001904743 | Marlon Authors | Manchester | Completed | Load_567626 | Spur Tree - 210 | 2026-08-30 07:31 | 2026-08-30 07:33 | 2026-08-30 07:51 | 2026-08-30 07:51 | 2026-08-30 07:51 | 2026-08-30 07:54 | 2026-08-30 07:54 | 2026-08-30 07:54 |  |  | Fair | No | Customer said supply is okay
Outage | J.E.26.08.74693 | C001904744 | Marlon Authors | St.Elizabeth | Completed | Load_244058 | Maggotty - 110 | 2026-08-30 07:31 | 2026-08-30 07:33 | 2026-08-30 10:34 | 2026-08-30 10:35 | 2026-08-30 10:34 | 2026-08-30 11:01 | 2026-08-30 11:01 | 2026-08-30 11:01 |  |  | Fair | No | Patrol and found one 30 feet wooden overhead guy pole leaning and it causes the guy wire to pass inches away from the switch. Replace one blown 10 amp junction fuse no pole # restored supply okay. Please refer same to the maintenance department for further assistance
Outage | J.E.26.08.75140 | C001904745 | Barnett Brown | Manchester | Completed | Load_267716 | Kendal - 210 | 2026-08-30 07:33 | 2026-08-30 07:34 | 2026-08-30 07:59 | 2026-08-30 08:31 | 2026-08-30 11:45 | 2026-08-30 11:47 | 2026-08-30 13:04 | 2026-08-30 13:04 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.73654 | C001904746 | Floyd Taylor | Trelawny | Completed | Load_574709 | Greenwood - 210 | 2026-08-30 07:34 | 2026-08-30 07:35 | 2026-08-30 10:58 | 2026-08-30 10:59 | 2026-08-30 10:58 | 2026-08-30 10:59 | 2026-08-30 11:00 | 2026-08-30 11:00 |  |  | Fair | No | Call belong to montego bay
Non-Outage | J.E.26.08.75131 | C001904747 | Collin Robinson | Portland | Completed | Load_269688 | Port Antonio - 410 | 2026-08-30 07:35 | 2026-08-30 07:35 | 2026-08-30 07:47 | 2026-08-30 07:48 | 2026-08-30 09:09 | 2026-08-30 09:50 | 2026-08-30 09:50 | 2026-08-30 09:50 |  |  | Fair | No | Isolate 50KVA transformer to entangle and retention open secondary conductor
Outage | J.E.26.08.69206 | C001904748 | Neville Spencer | Clarendon | Completed | Load_268174 | May Pen - 110 | 2026-08-30 07:37 | 2026-08-30 07:38 | 2026-08-30 08:22 | 2026-08-30 08:23 | 2026-08-30 11:18 | 2026-08-30 13:55 | 2026-08-30 13:59 | 2026-08-30 13:59 |  | Y | Fair | No | Found dislodged primary phase Conductor at pole # 462698 attached same .Also cleaned bamboo from 13.8 kv line renew blown 10 amp j/ fuse area restored.
Outage | J.E.26.08.75127 | C001904749 | Ricky Hall | St.Catherine | Completed | Load_568200 | New Michelton - 210 | 2026-08-30 07:40 | 2026-08-30 07:42 | 2026-08-30 08:14 | 2026-08-30 08:42 | 2026-08-30 10:25 | 2026-08-30 11:04 | 2026-08-30 11:06 | 2026-08-30 11:06 |  |  | Fair | No | Replace blown 25 amps junction fuse
Outage | J.E.26.08.75048 | C001904750 | Derrick Dawkins | St.James | Completed | Load_244479 | Queens Drive - 810 | 2026-08-30 07:42 | 2026-08-30 07:43 | 2026-08-30 16:37 | 2026-08-30 22:28 | 2026-08-30 22:27 | 2026-08-30 10:39 | 2026-08-30 22:28 | 2026-08-30 22:28 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.74720 | C001904751 | Derrick Dawkins | St.James | Completed | Load_253128 | Queens Drive - 710 | 2026-08-30 07:43 | 2026-08-30 07:44 | 2026-08-30 07:50 | 2026-08-30 07:50 | 2026-08-30 07:50 | 2026-08-30 08:36 | 2026-08-30 09:19 | 2026-08-30 09:19 |  |  | Fair | No | Found premises ok
Outage | J.E.26.08.73407 | C001904753 | Derrick Dawkins | St.James | Completed | Load_244515 | Queens Drive - 710 | 2026-08-30 07:44 | 2026-08-30 07:45 | 2026-08-30 08:11 | 2026-08-30 09:19 | 2026-08-30 09:19 | 2026-08-30 09:22 | 2026-08-30 09:23 | 2026-08-30 09:23 |  |  | Fair | No | Check and found area ok customer says the light is back
Outage | J.E.26.08.73637 | C001904752 | Derrick Dawkins | St.James | Completed | Load_254244 | Queens Drive - 710 | 2026-08-30 07:44 | 2026-08-30 07:59 | 2026-08-30 12:38 | 2026-08-30 12:39 | 2026-08-30 13:02 | 2026-08-30 13:05 | 2026-08-30 13:06 | 2026-08-30 13:06 |  |  | Fair | No | Found premises and area ok
Non-Outage | J.E.26.08.70523 | C001904755 | Romaine Roberts |  | Completed |  |  | 2026-08-30 07:45 | 2026-08-30 07:46 | 2026-08-30 08:06 | 2026-08-30 08:06 | 2026-08-30 09:45 | 2026-08-30 09:45 | 2026-08-30 09:53 | 2026-08-30 09:53 | BrokenPole |  | Fair | No | Pole that fall down maintenance work carrying out c.Henry
Outage | J.E.26.08.73592 | C001904757 | Romaine Roberts | St.Mary | Completed | Load_241528 | Highgate -110 | 2026-08-30 07:46 | 2026-08-30 07:47 | 2026-08-30 11:57 | 2026-08-30 11:57 | 2026-08-30 13:07 | 2026-08-30 13:10 | 2026-08-30 13:31 | 2026-08-30 13:31 |  |  | Fair | No | Found 10 kva transformer fuse blow patrol line and clear vegetation from around transformer replace 3 amp fuse 611099
Outage | J.E.26.08.74814 | C001904756 | Horace Malcolm | St.James | Completed | Load_252935 | Bogue - 610 | 2026-08-30 07:46 | 2026-08-30 07:48 | 2026-08-30 09:15 | 2026-08-30 09:16 | 2026-08-30 09:15 | 2026-08-30 09:18 | 2026-08-30 09:18 | 2026-08-30 09:18 |  |  | Fair | No | Related to previous call job number 74821
Non-Outage | J.E.26.08.62770 | C001904762 | Richman Whyte | Westmoreland | Completed | Load_244225 | Paradise - 310 | 2026-08-30 07:48 | 2026-08-30 07:50 | 2026-08-30 13:09 | 2026-08-30 13:09 | 2026-08-30 13:09 | 2026-08-30 13:09 | 2026-08-30 13:10 | 2026-08-30 13:10 |  |  | Fair | No | Customer stated that the problem was resolved from last night
Non-Outage | J.E.26.08.70542 | C001904759 | Javid Vernon | Westmoreland | Completed | Load_248206 | Paradise - 110 | 2026-08-30 07:48 | 2026-08-30 17:34 | 2026-08-30 18:08 | 2026-08-30 18:09 | 2026-08-30 19:04 | 2026-08-30 19:51 | 2026-08-30 19:51 | 2026-08-30 19:51 | Fire |  | Rains | No | Reconnect customer service wire use one clamps voltage found 116 voltage left 116/115/231
Outage | J.E.26.08.67618 | C001904760 | Romaine Roberts | St.Mary | Completed | Load_248567 | Highgate -110 | 2026-08-30 07:48 | 2026-08-30 07:48 | 2026-08-30 16:59 | 2026-08-30 17:00 | 2026-08-30 18:02 | 2026-08-30 18:06 | 2026-08-30 18:07 | 2026-08-30 18:07 |  |  | Fair | No | Found premises close meter also is also enclose up and can’t be reach advise customer to have gate open so we can have entry to meter
Non-Outage | J.E.26.08.72963 | C001904763 | Romaine Roberts | St.Mary | Completed | Load_267478 | Highgate -110 | 2026-08-30 07:49 | 2026-08-30 07:49 | 2026-08-30 09:53 | 2026-08-30 09:54 | 2026-08-30 10:54 | 2026-08-30 11:54 | 2026-08-30 11:56 | 2026-08-30 11:56 |  |  | Fair | No | Open and close 25 kva transformer to splice and retention one span of secondary phase that burn off power restore
Outage | J.E.26.08.69360 | C001904775 | Ricky Hall | St.Catherine | Completed | Load_248615 | New Michelton - 210 | 2026-08-30 07:50 | 2026-08-30 07:51 | 2026-08-30 11:07 | 2026-08-30 11:07 | 2026-08-30 11:32 | 2026-08-30 11:59 | 2026-08-30 11:59 | 2026-08-30 11:59 |  |  | Fair | No | Repair slack 3 w service at pole use 2 clamps 117/116/233
Outage | J.E.26.08.73204 | C001904771 | Derrick Dawkins | St.James | Completed | Load_254099 | Bogue - 310 | 2026-08-30 07:50 | 2026-08-30 15:32 | 2026-08-30 16:37 | 2026-08-30 22:24 | 2026-08-30 22:23 | 2026-08-30 22:25 | 2026-08-30 22:25 | 2026-08-30 22:25 |  |  | Fair | No | Cannot locate customer
Outage | J.E.26.08.73232 | C001904770 | Derrick Dawkins | St.James | Completed | Load_239982 | Bogue - 310 | 2026-08-30 07:50 | 2026-08-30 15:32 | 2026-08-30 16:37 | 2026-08-30 21:28 | 2026-08-30 22:18 | 2026-08-30 22:19 | 2026-08-30 22:23 | 2026-08-30 22:23 |  |  | Fair | No | Cannot locate customer
Outage | J.E.26.08.73304 | C001904769 | Derrick Dawkins | St.James | Completed | Load_557002 | Bogue - 310 | 2026-08-30 07:50 | 2026-08-30 15:32 | 2026-08-30 16:28 | 2026-08-30 16:29 | 2026-08-30 16:41 | 2026-08-30 16:35 | 2026-08-30 16:43 | 2026-08-30 16:43 |  |  | Fair | No | Cannot locate customer
Outage | J.E.26.08.73732 | C001904768 | Derrick Dawkins | St.James | Completed | Load_576009 | Bogue - 310 | 2026-08-30 07:50 | 2026-08-30 16:34 | 2026-08-30 17:42 | 2026-08-30 22:25 | 2026-08-30 22:25 | 2026-08-30 18:53 | 2026-08-30 22:27 | 2026-08-30 22:27 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.74497 | C001904766 | Richard Nicholas | St.Catherine | Completed | Load_246714 | Tredegar - 210 | 2026-08-30 07:50 | 2026-08-30 07:50 | 2026-08-30 08:26 | 2026-08-30 08:26 | 2026-08-30 10:03 | 2026-08-30 10:50 | 2026-08-30 10:52 | 2026-08-30 10:52 |  |  | Fair | No | Cut and splice burnt 100kva transformer phase drop lead on pole #006421.2ft 4/0 pvc copper and 2 clamp.voltage reading 120x2 and 240v.
Outage | J.E.26.08.75003 | C001904767 | Derrick Dawkins | St.James | Completed | Load_1001919 | Bogue - 310 | 2026-08-30 07:50 | 2026-08-30 15:32 | 2026-08-30 16:35 | 2026-08-30 16:44 | 2026-08-30 17:39 | 2026-08-30 17:41 | 2026-08-30 17:41 | 2026-08-30 17:41 |  |  | Fair | No | Check and found premises ok
Outage | J.E.26.08.75017 | C001904772 | Rochaine Palmer | KSAS | Completed | Load_266562 | Hunts Bay - 310 | 2026-08-30 07:50 | 2026-08-30 07:54 | 2026-08-30 08:16 | 2026-08-30 08:17 | 2026-08-30 10:14 | 2026-08-30 10:05 | 2026-08-30 10:18 | 2026-08-30 10:18 | BrokenWire |  | Fair | No | #2/0 twisted secondary crystalize and burnt up in multiple spots . Need about 180ft of #2/0 twisted. Customers out of supply.
Outage | J.E.26.08.73319 | C001904776 | Neville Spencer | St.Ann | Completed | Load_255880 | Cardiff Hall - 310 | 2026-08-30 07:53 | 2026-08-30 09:23 | 2026-08-30 13:59 | 2026-08-30 13:59 | 2026-08-30 13:59 | 2026-08-30 13:59 | 2026-08-30 14:01 | 2026-08-30 14:01 |  | Y | Fair | No | Found dislodged primary phase Conductor at pole # 462698, attached same .Also cleaned bamboo from 13.8 kv line renew blown 10 amp j/ fuse area restored.
Non-Outage | J.E.26.08.75179 | C001904777 | Horace Malcolm |  | Completed |  |  | 2026-08-30 07:57 | 2026-08-30 07:58 | 2026-08-30 09:13 | 2026-08-30 09:14 | 2026-08-30 09:13 | 2026-08-30 09:15 | 2026-08-30 09:15 | 2026-08-30 09:15 | Fire |  | Fair | No | Related to previous call job number 74821
Outage | J.E.26.08.75233 | C001904778 | Roxroy Needham | St.Ann | Completed | Load_1003805 | Cardiff Hall - 210 | 2026-08-30 08:01 | 2026-08-30 08:06 | 2026-08-30 09:13 | 2026-08-30 09:14 | 2026-08-30 09:13 | 2026-08-30 09:10 | 2026-08-30 09:14 | 2026-08-30 09:14 |  |  | Fair | No | Premises found ok call customer and customer say that the light is ok
Outage | J.E.26.08.72322 | C001904783 | Stephen Taylor | Portland | Completed | Load_254637 | Port Antonio - 310 | 2026-08-30 08:18 | 2026-08-30 08:20 | 2026-08-30 10:33 | 2026-08-30 14:29 | 2026-08-30 14:28 | 2026-08-30 14:29 | 2026-08-30 14:30 | 2026-08-30 14:30 |  |  | Fair | No | Clean up single reading 111,112,224 customer is now okay
Outage | J.E.26.08.74541 | C001904779 | Christopher Edwards | KSAN | Completed | Load_261630 | Constant Spring - 210 | 2026-08-30 08:18 | 2026-08-30 08:30 | 2026-08-30 10:59 | 2026-08-30 11:26 | 2026-08-30 11:26 | 2026-08-30 12:09 | 2026-08-30 12:11 | 2026-08-30 12:11 |  |  | Fair | No | Customer was advised to go to bill express to buy credit and top up their account
Outage | J.E.26.08.75152 | C001904780 | Stephen Taylor | St.Thomas | Completed | Load_250144 | Good Year - 110 | 2026-08-30 08:18 | 2026-08-30 08:20 | 2026-08-30 13:25 | 2026-08-30 13:25 | 2026-08-30 13:25 | 2026-08-30 13:25 | 2026-08-30 13:27 | 2026-08-30 13:27 |  |  | Fair | No | Patrol the area power is in the area a lot of call to single customer no one answered the phone
Outage | J.E.26.08.75298 | C001904781 | Stephen Taylor | Portland | Completed | Load_256242 | Port Antonio - 310 | 2026-08-30 08:18 | 2026-08-30 08:20 | 2026-08-30 09:00 | 2026-08-30 09:01 | 2026-08-30 10:10 | 2026-08-30 10:11 | 2026-08-30 10:16 | 2026-08-30 10:16 |  |  | Fair | No | Patrol area and power is the area but several calls to single customer and no one answering the phone
Outage | J.E.26.08.75302 | C001904782 | Stephen Taylor | Portland | Completed | Load_263191 | Port Antonio - 310 | 2026-08-30 08:18 | 2026-08-30 08:20 | 2026-08-30 10:17 | 2026-08-30 10:17 | 2026-08-30 10:30 | 2026-08-30 10:30 | 2026-08-30 10:32 | 2026-08-30 10:32 |  |  | Fair | No | Clean up single phase line 3 clamps Rdg 112–113–225
Non-Outage | J.E.26.08.68921 | C001904786 | Stephen Taylor | Portland | Completed | Load_264343 | Lysson - 410 | 2026-08-30 08:23 | 2026-08-30 08:24 | 2026-08-30 11:14 | 2026-08-30 11:14 | 2026-08-30 11:14 | 2026-08-30 11:14 | 2026-08-30 11:15 | 2026-08-30 11:15 |  |  | Fair | No | Contact customer and customer say that power is restored and okay
Non-Outage | J.E.26.08.71989 | C001904787 | Stephen Taylor | Portland | Completed | Load_577160 | Port Antonio - 310 | 2026-08-30 08:23 | 2026-08-30 08:24 | 2026-08-30 11:04 | 2026-08-30 11:05 | 2026-08-30 11:07 | 2026-08-30 11:07 | 2026-08-30 11:08 | 2026-08-30 11:08 |  |  | Fair | No | Contact customer and customer say that power is restored and okay
Non-Outage | J.E.26.08.72949 | C001904785 | Stephen Taylor | Portland | Completed | Load_577165 | Port Antonio - 310 | 2026-08-30 08:23 | 2026-08-30 08:24 | 2026-08-30 11:15 | 2026-08-30 11:16 | 2026-08-30 11:16 | 2026-08-30 11:16 | 2026-08-30 11:16 | 2026-08-30 11:16 |  |  | Fair | No | Need more information a lot of call to customer no one answered the phone
Non-Outage | J.E.26.08.70350 | C001904788 | Christopher Edwards | KSAN | Completed | Load_241582 | Constant Spring - 210 | 2026-08-30 08:26 | 2026-08-30 08:28 | 2026-08-30 10:38 | 2026-08-30 10:39 | 2026-08-30 10:38 | 2026-08-30 10:58 | 2026-08-30 10:58 | 2026-08-30 10:58 |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Non-Outage | J.E.26.08.55038 | C001904791 | Christopher Edwards | KSAN | Completed | Load_263067 | Constant Spring - 210 | 2026-08-30 08:27 | 2026-08-31 08:13 | 2026-08-31 08:20 | 2026-08-31 08:21 | 2026-08-31 08:20 | 2026-08-31 08:21 | 2026-08-31 08:22 | 2026-08-31 08:22 |  |  | Fair | Yes | Customer is in the St Cathrine region
Non-Outage | J.E.26.08.61609 | C001904789 | Christopher Edwards | KSAN | Completed | Load_247023 | Constant Spring - 210 | 2026-08-30 08:27 | 2026-08-31 08:12 | 2026-08-31 08:19 | 2026-08-31 09:00 | 2026-08-31 09:08 | 2026-08-31 09:50 | 2026-08-31 09:51 | 2026-08-31 09:51 |  |  | Fair | No | Customer meter is burnt and needs to be replaced Customer currently having single phasing
Non-Outage | J.E.26.08.61836 | C001904790 | Christopher Edwards | KSAN | Completed | Load_247023 | Constant Spring - 210 | 2026-08-30 08:27 | 2026-08-30 08:28 | 2026-08-30 10:01 | 2026-08-30 10:01 | 2026-08-30 10:13 | 2026-08-30 10:37 | 2026-08-30 10:37 | 2026-08-30 10:37 |  |  | Fair | No | Remake corroded neutral joint at pole Using (1) one bolt clamps Voltage:115,114,230v
Non-Outage | J.E.26.08.62424 | C001904795 | Milton Charlton | KSAN | Completed | Load_247082 | West Kings House - 310 | 2026-08-30 08:28 | 2026-08-30 08:29 | 2026-08-30 09:31 | 2026-08-30 09:38 | 2026-08-30 09:45 | 2026-08-30 10:15 | 2026-08-30 09:49 | 2026-08-30 09:49 |  |  | Fair | No | Found okay upon arrival. Matter was resolved
Non-Outage | J.E.26.08.62600 | C001904793 | Milton Charlton | KSAN | Completed | Load_246866 | West Kings House - 310 | 2026-08-30 08:28 | 2026-08-30 08:29 | 2026-08-30 09:31 | 2026-08-30 12:34 | 2026-08-30 12:37 | 2026-08-30 12:25 | 2026-08-30 12:39 | 2026-08-30 12:39 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Non-Outage | J.E.26.08.62982 | C001904794 | Milton Charlton | KSAN | Completed | Load_557443 | West Kings House - 310 | 2026-08-30 08:28 | 2026-08-30 08:29 | 2026-08-30 09:31 | 2026-08-30 11:33 | 2026-08-30 12:32 | 2026-08-30 11:40 | 2026-08-30 12:34 | 2026-08-30 12:34 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Non-Outage | J.E.26.08.75021 | C001904796 | Milton Charlton | KSAN | Completed | Load_261910 | Washington Blvd - 410 | 2026-08-30 08:28 | 2026-08-30 08:29 | 2026-08-30 09:31 | 2026-08-30 09:50 | 2026-08-30 10:17 | 2026-08-30 10:55 | 2026-08-30 11:30 | 2026-08-30 11:30 |  |  | Fair | No | Customer meter #2581105 single phasing? Refer to field service.
Outage | J.E.26.08.75355 | C001904797 | Christopher Edwards | KSAS | Completed | Load_268579 | Duhaney - 310 | 2026-08-30 08:29 | 2026-08-30 08:30 | 2026-08-30 12:11 | 2026-08-30 12:25 | 2026-08-30 12:25 | 2026-08-30 13:15 | 2026-08-30 13:16 | 2026-08-30 13:16 |  |  | Fair | No | Remake burnt neutral joint Using (1) one bolt clamps Voltage :117,116,231v
Non-Outage | J.E.26.08.61617 | C001904799 | Edward Royal | KSAS | Completed | Load_265012 | Rockfort - 410 | 2026-08-30 08:31 | 2026-08-30 08:33 | 2026-08-30 10:33 | 2026-08-30 10:34 | 2026-08-30 10:33 | 2026-08-30 10:35 | 2026-08-30 10:38 | 2026-08-30 10:38 | Fire |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.08.74216 | C001904800 | Edward Royal | KSAS | Completed | Load_243276 | Cane River - 610 | 2026-08-30 08:31 | 2026-08-30 08:33 | 2026-08-30 10:25 | 2026-08-30 10:26 | 2026-08-30 10:25 | 2026-08-30 10:26 | 2026-08-30 10:27 | 2026-08-30 10:27 | Fire |  | Fair | No | Premises not found unable to communicate with customer
Outage | J.E.26.08.74148 | C001904798 | Edward Royal | KSAS | Completed | Load_249762 | Rockfort - 210 | 2026-08-30 08:31 | 2026-08-30 08:33 | 2026-08-30 10:38 | 2026-08-30 10:39 | 2026-08-30 10:38 | 2026-08-30 10:39 | 2026-08-30 10:39 | 2026-08-30 10:39 |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.08.58127 | C001904801 | Edward Royal | KSAS | Completed | Load_1002682 | Cane River - 410 | 2026-08-30 08:32 | 2026-08-30 08:33 | 2026-08-30 10:28 | 2026-08-30 10:29 | 2026-08-30 10:28 | 2026-08-30 10:30 | 2026-08-30 10:31 | 2026-08-30 10:31 | Fire |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.08.69689 | C001904802 | Hartley Chin | Clarendon | Completed | Load_243025 | May Pen - 110 | 2026-08-30 08:33 | 2026-08-31 07:32 | 2026-08-31 12:18 | 2026-08-31 12:29 | 2026-08-31 14:54 | 2026-08-31 14:44 | 2026-08-31 15:00 | 2026-08-31 15:00 | BrokenWire |  | Fair | No | Prem not found … unable to contact customer with contact # provided…
Non-Outage | J.E.26.08.69449 | C001904804 | Nickolas Rodriques | Portmore | Completed | Load_241653 | Naggo Head - 610 | 2026-08-30 08:35 | 2026-08-30 08:36 | 2026-08-30 12:42 | 2026-08-30 12:46 | 2026-08-30 13:20 | 2026-08-30 13:51 | 2026-08-30 13:54 | 2026-08-30 13:54 |  |  | Fair | No | Unable to locate or communicate with the customer after several attempts.
Non-Outage | J.E.26.08.71942 | C001904805 | Nickolas Rodriques | Portmore | Completed | Load_248667 | Naggo Head - 510 | 2026-08-30 08:35 | 2026-08-30 08:36 | 2026-08-30 09:14 | 2026-08-30 09:24 | 2026-08-30 09:55 | 2026-08-30 10:27 | 2026-08-30 10:35 | 2026-08-30 10:35 |  |  | Fair | No | Customer stated that she did not make any report and she is not having any electrical issues at her premises at 2 North.
Non-Outage | J.E.26.08.73054 | C001904806 | Nickolas Rodriques | Portmore | Completed | Load_260624 | Naggo Head - 610 | 2026-08-30 08:35 | 2026-08-30 08:36 | 2026-08-30 10:42 | 2026-08-30 10:44 | 2026-08-30 11:15 | 2026-08-30 12:38 | 2026-08-30 12:42 | 2026-08-30 12:42 |  |  | Fair | No | Checked and found customer single phasing (119) caused by broken service wire. Repaired by replacing four one-bolt clamps and two service sleeves. Current reading (120-119-239). The customer confirmed that all is well now.
Non-Outage | J.E.26.08.69555 | C001904811 | Donald Cunningham | St.Catherine | Completed | Load_238849 | Rhodens Pen - 210 | 2026-08-30 08:36 | 2026-08-30 08:37 | 2026-08-30 08:42 | 2026-08-30 08:42 | 2026-08-30 10:00 | 2026-08-30 10:01 | 2026-08-30 10:01 | 2026-08-30 10:01 | BrokenWire |  | Fair | No | Issues already resolved
Non-Outage | J.E.26.08.70662 | C001904812 | Donald Cunningham | St.Catherine | Completed | Load_259990 | Rhodens Pen - 210 | 2026-08-30 08:36 | 2026-08-30 08:37 | 2026-08-30 10:02 | 2026-08-30 10:04 | 2026-08-30 11:02 | 2026-08-30 11:14 | 2026-08-30 11:14 | 2026-08-30 11:14 |  |  | Fair | No | More info needed customer not reachable
Outage | J.E.26.08.75265 | C001904810 | Raheem Ricketts | Manchester | Completed | Load_302864 | Spur Tree - 210 | 2026-08-30 08:36 | 2026-08-30 08:37 | 2026-08-30 10:15 | 2026-08-30 11:33 | 2026-08-30 11:33 | 2026-08-30 11:35 | 2026-08-30 11:35 | 2026-08-30 11:35 |  |  | Fair | No | Unable to communicate with Customer cell number went unavailable after multiple calls however area has power no blown fuse was found
Outage | J.E.26.08.75393 | C001904809 | Raheem Ricketts | Manchester | Completed | Load_266064 | Spur Tree - 210 | 2026-08-30 08:36 | 2026-08-30 08:37 | 2026-08-30 10:15 | 2026-08-30 11:36 | 2026-08-30 11:36 | 2026-08-30 12:09 | 2026-08-30 12:09 | 2026-08-30 12:09 |  |  | Fair | No | Manchester call
Non-Outage | J.E.26.08.61560 | C001904814 | Neville Spencer | Clarendon | Completed | Load_266939 | Parnassus - 210 | 2026-08-30 08:38 | 2026-08-31 07:42 | 2026-08-31 09:07 | 2026-08-31 09:08 | 2026-08-31 10:08 | 2026-08-31 10:08 | 2026-08-31 10:09 | 2026-08-31 10:09 |  |  | Fair | No | Customer not located.
Non-Outage | J.E.26.08.69607 | C001904813 | Clyde Brown | Clarendon | Completed | Load_245256 | May Pen - 210 | 2026-08-30 08:38 | 2026-08-30 08:39 | 2026-08-30 08:59 | 2026-08-30 09:00 | 2026-08-30 09:26 | 2026-08-30 09:27 | 2026-08-30 09:30 | 2026-08-30 09:30 |  |  | Fair | No | Defective meter socket customer advised to get change
Outage | J.E.26.08.73503 | C001904815 | Floyd Taylor | Trelawny | Completed | Load_292409 | Greenwood - 210 | 2026-08-30 08:44 | 2026-08-30 08:44 | 2026-08-30 15:18 | 2026-08-30 15:18 | 2026-08-30 16:01 | 2026-08-30 16:01 | 2026-08-30 16:01 | 2026-08-30 16:01 |  |  | Fair | No
Outage | J.E.26.08.75398 | C001904816 | Rochaine Palmer | KSAN | Completed | Load_254673 | Washington Blvd - 710 | 2026-08-30 08:45 | 2026-08-30 08:50 | 2026-08-30 11:16 | 2026-08-30 11:17 | 2026-08-30 11:50 | 2026-08-30 12:05 | 2026-08-30 12:04 | 2026-08-30 12:04 |  |  | Fair | No | Reset customer circuit breakers found tripped.
Outage | J.E.26.08.75373 | C001904817 | Raymond Carr | St.Ann | Completed | Load_243161 | Upper White River - 110 | 2026-08-30 08:50 | 2026-08-30 10:04 | 2026-08-30 12:17 | 2026-08-30 12:18 | 2026-08-30 13:15 | 2026-08-30 17:36 | 2026-08-30 16:44 | 2026-08-30 16:44 | BrokenWire |  | Fair | No | Spliced and retention two spans of broken secondary conductors using 150ft#2aa, 6 one bolt clamps, 6#2 splicing sleeves, 6 #2 preforms. Supply was restored.
Outage | J.E.26.08.75495 | C001904818 | Javid Vernon | Westmoreland | Completed | Load_292237 | Paradise - 110 | 2026-08-30 09:01 | 2026-08-30 09:03 | 2026-08-30 10:21 | 2026-08-30 10:22 | 2026-08-30 10:21 | 2026-08-30 10:21 | 2026-08-30 10:22 | 2026-08-30 10:22 |  |  | Fair | No | Customer stated that the power was restored
Outage | J.E.26.08.75484 | C001904819 | Javid Vernon | Westmoreland | Completed | Load_292222 | Paradise - 210 | 2026-08-30 09:03 | 2026-08-30 09:03 | 2026-08-30 10:23 | 2026-08-30 10:24 | 2026-08-30 10:23 | 2026-08-30 10:23 | 2026-08-30 10:24 | 2026-08-30 10:24 |  |  | Fair | No | Customer stated that the power was restored
Outage | J.E.26.08.75495 | C001904821 | Javid Vernon | Westmoreland | Completed | Load_292237 | Paradise - 110 | 2026-08-30 09:03 | 2026-08-30 09:04 | 2026-08-30 10:21 | 2026-08-30 10:21 | 2026-08-30 10:21 | 2026-08-30 10:21 | 2026-08-30 10:21 | 2026-08-30 10:21 |  |  | Fair | No | Customer stated that the power was restored
Outage | J.E.26.08.75514 | C001904820 | Romaine Roberts | St.Mary | Completed | Load_269235 | Annotto Bay - 310 | 2026-08-30 09:03 | 2026-08-30 09:04 | 2026-08-30 13:46 | 2026-08-30 13:46 | 2026-08-30 15:10 | 2026-08-30 15:15 | 2026-08-30 15:17 | 2026-08-30 15:17 |  |  | Fair | No | Found 3-bank of 3 transformer fuse blown checks carryout nothing found rep,ace 3-5amp fuse no pole number power restore
Outage | J.E.26.08.75505 | C001904822 | Javid Vernon | Westmoreland | Completed | Load_262638 | Paradise - 110 | 2026-08-30 09:04 | 2026-08-30 09:08 | 2026-08-30 10:02 | 2026-08-30 10:02 | 2026-08-30 10:02 | 2026-08-30 10:02 | 2026-08-30 10:02 | 2026-08-30 10:02 |  |  | Fair | No | Related to previous call job # 73852
Outage | J.E.26.08.75408 | C001904825 | Derrick Dawkins | St.James | Completed | Load_270029 | Bogue - 310 | 2026-08-30 09:18 | 2026-08-30 09:19 | 2026-08-30 11:26 | 2026-08-30 11:27 | 2026-08-30 11:38 | 2026-08-30 12:34 | 2026-08-30 12:35 | 2026-08-30 12:35 |  |  | Fair | No | Found 3 junction fuse blown and one 50 kva transformer fuse blown also due to banging secondary replace one 25amp /one 15amp /one 8amp / on 5amp no pole number available for the 25amp junction
Outage | J.E.26.08.74941 | C001904828 | Collin Robinson | St.James | Completed | Load_237694 | Bogue - 610 | 2026-08-30 09:22 | 2026-08-30 09:23 | 2026-08-30 19:13 | 2026-08-30 19:14 | 2026-08-30 19:29 | 2026-08-30 19:31 | 2026-08-30 19:31 | 2026-08-30 19:31 | BrokenWire |  | Fair | No | Information received from customer that issue was resolve
Outage | J.E.26.08.75550 | C001904827 | Raheem Ricketts | Manchester | Completed | Load_292347 | Spur Tree - 210 | 2026-08-30 09:22 | 2026-08-30 09:23 | 2026-08-30 10:15 | 2026-08-30 10:20 | 2026-08-30 11:12 | 2026-08-30 11:14 | 2026-08-30 11:14 | 2026-08-30 11:14 |  |  | Fair | No | Check and found 25 kva fuse blown refuse 25kva
Non-Outage | J.E.26.08.70759 | C001904829 | Derrick Dawkins |  | Completed |  |  | 2026-08-30 09:23 | 2026-08-30 09:24 | 2026-08-30 13:53 | 2026-08-30 13:54 | 2026-08-30 14:21 | 2026-08-30 14:23 | 2026-08-30 14:23 | 2026-08-30 14:23 |  |  | Fair | No | Cannot locate customer
Outage | J.E.26.08.66333 | C001904831 | Swon Miller | Trelawny | Completed | Load_237793 | Greenwood - 210 | 2026-08-30 09:25 | 2026-08-30 15:34 | 2026-08-30 15:50 | 2026-08-30 15:50 | 2026-08-30 16:57 | 2026-08-25 05:30 | 2026-08-30 17:44 | 2026-08-30 17:44 | BrokenPole |  | Fair | No | Found 35ft class6 retired pole breken at the base .customers are using the pole as a intermediate pole
Outage | J.E.26.08.72730 | C001904830 | Derrick Dawkins | St.James | Completed | Load_242949 | Queens Drive - 710 | 2026-08-30 09:25 | 2026-08-30 09:25 | 2026-08-30 13:10 | 2026-08-30 14:30 | 2026-08-30 15:17 | 2026-08-30 16:20 | 2026-08-30 16:28 | 2026-08-30 16:28 |  |  | Fair | No | Cannot locate customer
Non-Outage | J.E.26.08.75531 | C001904832 | Raymond Carr |  | Completed |  |  | 2026-08-30 09:27 | 2026-08-30 10:15 | 2026-08-30 16:45 | 2026-08-30 16:46 | 2026-08-30 16:45 | 2026-08-30 16:32 | 2026-08-30 16:47 | 2026-08-30 16:47 | BrokenWire |  | Fair | No | Supply was restored.
Outage | J.E.26.08.75650 | C001904833 | Ryan Richards | Manchester | Completed | Load_257952 | Spur Tree - 310 | 2026-08-30 09:38 | 2026-08-30 09:46 | 2026-08-30 09:57 | 2026-08-30 10:08 | 2026-08-30 10:30 | 2026-08-30 10:51 | 2026-08-30 10:51 | 2026-08-30 10:51 |  |  | Fair | No | Area found ok customer said that there was no power outage in the area
Outage | J.E.26.08.75622 | C001904834 | Christopher Edwards | KSAS | Completed | Load_255994 | Duhaney - 310 | 2026-08-30 09:40 | 2026-08-30 09:41 | 2026-08-30 13:16 | 2026-08-30 13:34 | 2026-08-30 13:33 | 2026-08-30 14:43 | 2026-08-30 14:43 | 2026-08-30 14:43 | BrokenWire |  | Fair | No | Remake burnt phase joint Using (1) one bolt clamps
Outage | J.E.26.08.70654 | C001904838 | Floyd Taylor | Trelawny | Completed | Load_245327 | Duncans - 210 | 2026-08-30 09:42 | 2026-08-30 09:43 | 2026-08-30 10:57 | 2026-08-30 10:58 | 2026-08-30 10:57 | 2026-08-30 10:58 | 2026-08-30 10:58 | 2026-08-30 10:58 |  |  | Fair | No | Call belong to montego bay
Outage | J.E.26.08.75672 | C001904837 | Richard Nicholas | St.Catherine | Completed | Load_238911 | Tredegar - 210 | 2026-08-30 09:42 | 2026-08-30 09:43 | 2026-08-30 10:52 | 2026-08-30 10:52 | 2026-08-30 11:21 | 2026-08-30 12:26 | 2026-08-30 12:30 | 2026-08-30 12:30 |  | Y | Fair | No | Spot bushing done.retention 1 span of saggy and low hanging single phase primary.replaced blown 40amp junctions near to pole #0076307,and blown 25amp at pole #0076053 and blown 15amp junctions near to pole #012570.
Non-Outage | J.E.26.08.75275 | C001904839 | Lancelot Brown |  | Completed |  |  | 2026-08-30 09:46 | 2026-08-30 09:47 | 2026-08-30 13:35 | 2026-08-30 13:36 | 2026-08-30 13:35 | 2026-08-30 13:36 | 2026-08-30 13:36 | 2026-08-30 13:36 | Fire |  | Fair | No | Please pass on this call to st James crew
Outage | J.E.26.08.75582 | C001904840 | Javid Vernon | Westmoreland | Completed | Load_254537 | Paradise - 110 | 2026-08-30 09:47 | 2026-08-30 09:49 | 2026-08-30 10:18 | 2026-08-30 10:18 | 2026-08-30 10:18 | 2026-08-30 10:18 | 2026-08-30 10:19 | 2026-08-30 10:19 |  |  | Fair | No | Customer stated that the power was restored
Non-Outage | J.E.26.08.75549 | C001904842 | Marlon Authors |  | Completed |  |  | 2026-08-30 09:53 | 2026-08-30 09:55 | 2026-08-30 11:04 | 2026-08-30 11:04 | 2026-08-30 11:28 | 2026-08-30 13:01 | 2026-08-30 13:01 | 2026-08-30 13:01 | BrokenWire |  | Fair | No | Patrol and found one pole span of secondary neutral burnt off caused by vehicle accident. Splice and retention same using 15 feet of #2 conductor two #2 preforms, three clamps, one #2 splicing sleeve and replace one blown 2 amp fuse that protects 25 kva transformer circuit no pole #. Restored supply okay
Outage | J.E.26.08.75765 | C001904844 | Omar King | St.Ann | Completed | Load_240435 | Roaring River - 410 | 2026-08-30 10:12 | 2026-08-30 10:12 | 2026-08-30 10:56 | 2026-08-30 10:57 | 2026-08-30 11:46 | 2026-08-30 11:47 | 2026-08-30 11:47 | 2026-08-30 11:47 |  |  | Fair | No | Unable to find customer customer call several times no answer directions not sufficient
Outage | J.E.26.08.75790 | C001904846 | Omar King | St.Ann | Completed | Load_250016 | Ocho Rios - 510 | 2026-08-30 10:12 | 2026-08-30 10:13 | 2026-08-30 10:31 | 2026-08-30 10:31 | 2026-08-30 10:31 | 2026-08-30 10:31 | 2026-08-30 10:31 | 2026-08-30 10:31 |  |  | Fair | No | Problem as been resolved
Non-Outage | J.E.26.08.67874 | C001904849 | Rochaine Palmer | KSAN | Completed | Load_258733 | Washington Blvd - 310 | 2026-08-30 10:14 | 2026-08-30 10:15 | 2026-08-30 10:22 | 2026-08-30 10:22 | 2026-08-30 10:46 | 2026-08-30 11:15 | 2026-08-30 11:16 | 2026-08-30 11:16 |  |  | Fair | No | Customer service wire #6 triplex phase corroded at pothead. Repair using one 1- bolt clamp. Readings at pothead 114-115-230 volts
Non-Outage | J.E.26.08.68215 | C001904848 | Rochaine Palmer | KSAS | Completed | Load_261146 | Greenwich - 510 | 2026-08-30 10:14 | 2026-08-30 10:15 | 2026-08-30 13:14 | 2026-08-30 13:14 | 2026-08-30 13:53 | 2026-08-30 13:55 | 2026-08-30 13:58 | 2026-08-30 13:58 |  |  | Fair | No | Customer service wire #6 triplex phase and neutral corroded at pothead. Repair using two 1- bolt clamps. Readings at meter socket 113-114-228 volts.
Outage | J.E.26.08.75810 | C001904852 | Raheem Ricketts | Manchester | Completed | Load_246143 | Spur Tree - 210 | 2026-08-30 10:18 | 2026-08-30 10:21 | 2026-08-30 12:09 | 2026-08-30 12:10 | 2026-08-30 12:40 | 2026-08-30 14:09 | 2026-08-30 14:09 | 2026-08-30 14:09 |  |  | Fair | No | Isolate 25kva to cut an remove tree from secondary splice an retention 40 ft of bout nurtured an bottom phase using 4,clamps 2 splicing sleeve 2,#2 preform and reclosed 25kva
Outage | J.E.26.08.68106 | C001904854 | Moses Elliston | St.Catherine | Completed | Load_288801 | Twickenham - 210 | 2026-08-30 10:24 | 2026-08-30 10:24 | 2026-08-31 15:10 | 2026-08-31 15:11 | 2026-08-31 15:10 | 2026-08-31 15:10 | 2026-08-31 15:14 | 2026-08-31 15:14 |  |  | Fair | No | Unable to work due to outage in area
Outage | J.E.26.08.75619 | C001904858 | Floyd Taylor | Trelawny | Completed | Load_237728 | Duncans - 210 | 2026-08-30 10:35 | 2026-08-30 10:36 | 2026-08-30 12:02 | 2026-08-30 12:03 | 2026-08-30 12:42 | 2026-08-30 12:52 | 2026-08-30 12:52 | 2026-08-30 12:52 | Fire |  | Fair | No | Isolated 50kva transformer retention secondary line voltage readings left 114,113,230.
Outage | J.E.26.08.75959 | C001904861 | Javid Vernon | Westmoreland | Completed | Load_265484 | Paradise - 110 | 2026-08-30 10:57 | 2026-08-30 10:59 | 2026-08-30 11:30 | 2026-08-30 11:30 | 2026-08-30 11:30 | 2026-08-30 11:31 | 2026-08-30 11:31 | 2026-08-30 11:31 |  |  | Fair | No | Customer stated that the power was restored
Outage | J.E.26.08.75963 | C001904862 | Javid Vernon | Westmoreland | Completed | Load_254537 | Paradise - 110 | 2026-08-30 10:57 | 2026-08-30 10:59 | 2026-08-30 11:27 | 2026-08-30 11:28 | 2026-08-30 11:27 | 2026-08-30 11:27 | 2026-08-30 11:28 | 2026-08-30 11:28 |  |  | Fair | No | Customer stated that the power was restored
Outage | J.E.26.08.75979 | C001904865 | Richard Nicholas | St.Catherine | Completed | Load_246714 | Tredegar - 210 | 2026-08-30 11:04 | 2026-08-30 11:05 | 2026-08-30 12:30 | 2026-08-30 12:30 | 2026-08-30 13:18 | 2026-08-30 14:27 | 2026-08-30 14:29 | 2026-08-30 14:29 |  |  | Fair | No | Cut and splice damaged 3w service wire at mid span.2 clamp was used to complete the repair.
Outage | J.E.26.08.75314 | C001904867 | Stephen Taylor | St.Thomas | Completed | Load_264234 | Port Antonio - 310 | 2026-08-30 11:19 | 2026-08-30 11:23 | 2026-08-30 15:08 | 2026-08-30 15:08 | 2026-08-30 15:52 | 2026-08-30 15:53 | 2026-08-30 15:53 | 2026-08-30 15:53 |  |  | Fair | No | Patrol the area power is in the area a lot of lot of call to single customer no one answered the phone
Outage | J.E.26.08.76064 | C001904868 | Collin Robinson | Portland | Completed | Load_250602 | Port Antonio - 410 | 2026-08-30 11:20 | 2026-08-30 15:42 | 2026-08-30 17:49 | 2026-08-30 17:49 | 2026-08-30 19:06 | 2026-08-30 19:12 | 2026-08-30 19:12 | 2026-08-30 19:12 |  |  | Fair | No | Premises found with supply Voltage reading 117v 118v 235v
Outage | J.E.26.08.76068 | C001904869 | Collin Robinson | Portland | Completed | Load_352475 | Port Antonio - 410 | 2026-08-30 11:21 | 2026-08-30 11:22 | 2026-08-30 16:28 | 2026-08-30 16:29 | 2026-08-30 17:46 | 2026-08-30 17:49 | 2026-08-30 17:49 | 2026-08-30 17:49 |  |  | Fair | No | Premises found with supply Meter socket voltage 119v 120v 239v
Outage | J.E.26.08.76133 | C001904871 | Roxroy Needham | St.Ann | Completed | Load_241195 | Cardiff Hall - 310 | 2026-08-30 11:32 | 2026-08-30 11:32 | 2026-08-30 12:37 | 2026-08-30 12:38 | 2026-08-30 12:41 | 2026-08-30 00:40 | 2026-08-30 12:42 | 2026-08-30 12:42 |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.08.76052 | C001904873 | Edward Royal | KSAS | Completed | Load_267192 | Rockfort - 410 | 2026-08-30 11:34 | 2026-08-30 11:37 | 2026-08-30 11:50 | 2026-08-30 11:51 | 2026-08-30 12:20 | 2026-08-30 12:39 | 2026-08-30 12:40 | 2026-08-30 12:40 |  |  | Fair | No | Premises found ok. Voltage reading 118v 119v 236.9v
Outage | J.E.26.08.76121 | C001904872 | Edward Royal | KSAS | Completed | Load_240364 | Cane River - 410 | 2026-08-30 11:34 | 2026-08-30 11:37 | 2026-08-30 12:52 | 2026-08-30 12:53 | 2026-08-30 12:52 | 2026-08-30 13:50 | 2026-08-30 13:52 | 2026-08-30 13:52 |  |  | Fair | No | Premises found ok voltage reading 112v 113 v 223v
Outage | J.E.26.08.76008 | C001904876 | Javid Vernon | Westmoreland | Completed | Load_292222 | Paradise - 210 | 2026-08-30 11:37 | 2026-08-30 11:38 | 2026-08-30 12:28 | 2026-08-30 12:29 | 2026-08-30 12:28 | 2026-08-30 12:31 | 2026-08-30 12:31 | 2026-08-30 12:31 |  |  | Fair | No | Customer stated that the power was restored
Non-Outage | J.E.26.08.63791 | C001904878 | Rochaine Palmer | KSAS | Completed | Load_289416 | Greenwich - 510 | 2026-08-30 11:38 | 2026-08-30 11:40 | 2026-08-30 13:59 | 2026-08-30 14:00 | 2026-08-30 14:21 | 2026-08-30 14:25 | 2026-08-30 14:22 | 2026-08-30 14:22 |  |  | Fair | No | Premises closed. Customer states no body is at premises.
Non-Outage | J.E.26.08.62285 | C001904879 | Rochaine Palmer | KSAN | Completed | Load_266737 | Washington Blvd - 310 | 2026-08-30 11:39 | 2026-08-30 11:40 | 2026-08-30 13:09 | 2026-08-30 13:10 | 2026-08-30 13:12 | 2026-08-30 13:15 | 2026-08-30 13:14 | 2026-08-30 13:14 |  |  | Fair | No | Premises closed.
Non-Outage | J.E.26.08.62369 | C001904880 | Rochaine Palmer | KSAN | Completed | Load_259412 | Washington Blvd - 310 | 2026-08-30 11:39 | 2026-08-30 11:40 | 2026-08-30 12:05 | 2026-08-30 12:05 | 2026-08-30 12:57 | 2026-08-30 12:55 | 2026-08-30 13:03 | 2026-08-30 13:03 |  |  | Fair | No | Customer fed from E.N box and getting a low voltage on one of the phase leg coming from the box. Refer to field
Non-Outage | J.E.26.08.76307 | C001904884 | Ryan Richards |  | Completed |  |  | 2026-08-30 11:57 | 2026-08-30 11:57 | 2026-08-30 12:04 | 2026-08-30 12:05 | 2026-08-30 13:55 | 2026-08-30 14:59 | 2026-08-30 14:59 | 2026-08-30 14:59 | BrokenWire |  | Fair | No | Banging secondary phase and neutral found open 25 kva transformer retention secondary top phase and reclose transformer fuse all customers are now with supply
Non-Outage | J.E.26.08.76250 | C001904885 | Collin Robinson | Portland | Completed | Load_248323 | Port Antonio - 410 | 2026-08-30 11:58 | 2026-08-30 11:59 | 2026-08-30 12:18 | 2026-08-30 12:19 | 2026-08-30 13:47 | 2026-08-30 13:59 | 2026-08-30 14:00 | 2026-08-30 14:00 |  |  | Fair | No | Issue was resolved earlier today
Outage | J.E.26.08.76187 | C001904886 | Collin Robinson | Portland | Completed | Load_575971 | Port Antonio - 310 | 2026-08-30 12:03 | 2026-08-30 12:04 | 2026-08-30 14:00 | 2026-08-30 14:01 | 2026-08-30 15:34 | 2026-08-30 15:37 | 2026-08-30 15:37 | 2026-08-30 15:37 |  |  | Fair | No | Change two corroded one bolt clamp at meter pole Voltage reading 119v 120v 239v
Outage | J.E.26.08.75393 | C001904887 | Kenroy Dale | Manchester | Completed | Load_266064 | Spur Tree - 210 | 2026-08-30 12:07 | 2026-08-31 08:08 | 2026-08-31 13:47 | 2026-08-31 13:55 | 2026-08-31 14:31 | 2026-08-31 14:45 | 2026-08-31 14:46 | 2026-08-31 14:46 |  |  | Fair | No | Effort to contact customer multiple times was unsuccessful, area visited and still not found
Outage | J.E.26.08.76365 | C001904888 | Edward Royal | KSAS | Completed | Load_264861 | Rockfort - 210 | 2026-08-30 12:08 | 2026-08-30 12:48 | 2026-08-30 13:53 | 2026-08-30 13:54 | 2026-08-30 14:06 | 2026-08-30 15:11 | 2026-08-30 15:12 | 2026-08-30 15:12 | BrokenWire |  | Fair | No | Reconnected service #6 cable using one bolt clamp
Outage | J.E.26.08.73171 | C001904889 | Floyd Taylor | Trelawny | Completed | Load_262802 | Greenwood - 210 | 2026-08-30 12:09 | 2026-08-30 12:10 | 2026-08-30 13:44 | 2026-08-30 13:44 | 2026-08-30 14:03 | 2026-08-30 15:15 | 2026-08-30 15:18 | 2026-08-30 15:18 |  |  | Fair | No | Unable to contact customer light was found in the area
Outage | J.E.26.08.70839 | C001904890 | Horace Malcolm | St.James | Completed | Load_269746 | Bogue - 610 | 2026-08-30 12:14 | 2026-08-30 12:15 | 2026-08-30 12:24 | 2026-08-30 12:24 | 2026-08-30 12:25 | 2026-08-30 12:26 | 2026-08-30 12:26 | 2026-08-30 12:26 |  |  | Fair | No | Customer says supply restored
Outage | J.E.26.08.70946 | C001904891 | Lancelot Brown | St.James | Completed | Load_260871 | Bogue - 510 | 2026-08-30 12:14 | 2026-08-30 13:51 | 2026-08-30 18:45 | 2026-08-30 18:47 | 2026-08-30 18:47 | 2026-08-30 18:48 | 2026-08-30 18:48 | 2026-08-30 18:48 |  |  | Fair | No | Please pass on this call to st James crew direction is to Porto hello
Outage | J.E.26.08.77111 | C001904893 | Milton Charlton | KSAN | Completed | Load_261791 | Hope - 510 | 2026-08-30 12:38 | 2026-08-30 12:39 | 2026-08-30 12:52 | 2026-08-30 12:53 | 2026-08-30 14:32 | 2026-08-30 13:35 | 2026-08-30 14:34 | 2026-08-30 14:34 |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Non-Outage | J.E.26.08.76012 | C001904894 | Raymond Carr | St.Mary | Completed | Load_263198 | Oracabessa - 210 | 2026-08-30 12:44 | 2026-08-30 12:44 | 2026-08-30 18:05 | 2026-08-30 18:06 | 2026-08-30 18:05 | 2026-08-30 18:00 | 2026-08-30 18:06 | 2026-08-30 18:06 |  |  | Fair | No | Single phase condition was rectified.
Non-Outage | J.E.26.08.76155 | C001904895 | Raymond Carr | St.Mary | Completed | Load_263198 | Oracabessa - 210 | 2026-08-30 12:44 | 2026-08-30 12:45 | 2026-08-30 16:48 | 2026-08-30 16:48 | 2026-08-30 17:36 | 2026-08-30 17:59 | 2026-08-30 18:05 | 2026-08-30 18:05 |  |  | Fair | No | Defective clamp was replaced at transformer drop lead. Single phase condition rectified.
Outage | J.E.26.08.77520 | C001904896 | Roxroy Needham | St.Ann | Completed | Load_257202 | Cardiff Hall - 210 | 2026-08-30 12:45 | 2026-08-30 12:45 | 2026-08-30 13:19 | 2026-08-30 13:20 | 2026-08-30 14:37 | 2026-08-30 14:40 | 2026-08-30 14:43 | 2026-08-30 14:43 |  |  | Fair | No | Premises found ok
Outage | J.E.26.08.77655 | C001904897 | Marlon Authors | St.Elizabeth | Completed | Load_258035 | Maggotty - 110 | 2026-08-30 12:58 | 2026-08-30 13:01 | 2026-08-30 13:21 | 2026-08-30 13:22 | 2026-08-30 13:38 | 2026-08-30 13:41 | 2026-08-30 13:41 | 2026-08-30 13:41 |  |  | Fair | No | Unable to reach customer on the phone # provided
Outage | J.E.26.08.77676 | C001904898 | Ryan Richards | Manchester | Completed | Load_250166 | Spur Tree - 310 | 2026-08-30 13:00 | 2026-08-30 13:01 | 2026-08-30 16:02 | 2026-08-30 16:02 | 2026-08-30 16:11 | 2026-08-30 17:12 | 2026-08-30 17:12 | 2026-08-30 17:12 | Fire |  | Fair | No | Corroded neutral jumper found and corrected phase and neutral found at pothead and pole remade jumper using 1 one bolt clamp remade service wire for 3 w meter using 3 penunion and 3 one bolt clamps voltage 115/117/232 volts
Outage | J.E.26.08.77905 | C001904904 | Daniel Francis | St.Ann | Completed | Load_242574 | Cardiff Hall - 310 | 2026-08-30 13:42 | 2026-08-30 15:23 | 2026-08-30 19:34 | 2026-08-30 19:34 | 2026-08-30 19:34 | 2026-08-30 19:35 | 2026-08-30 19:37 | 2026-08-30 19:37 |  |  | Fair | No | Power restored
Outage | J.E.26.08.77796 | C001904908 | Ryan Richards | Manchester | Completed | Load_258296 | Kendal - 310 | 2026-08-30 13:51 | 2026-08-30 13:53 | 2026-08-30 14:59 | 2026-08-30 15:00 | 2026-08-30 15:38 | 2026-08-30 16:01 | 2026-08-30 16:01 | 2026-08-30 16:01 |  |  | Fair | No | Area found ok same as the other
Outage | J.E.26.08.77887 | C001904909 | Swon Miller | St.James | Completed | Load_251270 | Queens Drive - 710 | 2026-08-30 13:51 | 2026-08-30 15:34 | 2026-08-30 17:45 | 2026-08-30 17:45 | 2026-08-30 18:04 | 2026-08-18 18:20 | 2026-08-30 18:26 | 2026-08-30 18:26 |  |  | Fair | No | Check and found area okay voltage found 114/113/228 customer states that power supply has been restored voltage left 114/113/228
Non-Outage | J.E.26.08.68980 | C001904911 | Horace Malcolm | St.James | Completed | Load_246135 | Bogue - 610 | 2026-08-30 13:52 | 2026-08-30 13:53 | 2026-08-30 14:50 | 2026-08-30 14:51 | 2026-08-30 14:50 | 2026-08-30 14:55 | 2026-08-30 14:55 | 2026-08-30 14:55 | BrokenPole |  | Fair | No | Customer says issue resolved no broken pole no hanging wires
Non-Outage | J.E.26.08.77666 | C001904914 | Stephen Taylor | St.Thomas | Completed | Load_240234 | Lysson - 410 | 2026-08-30 13:57 | 2026-08-30 14:11 | 2026-08-30 15:56 | 2026-08-30 15:56 | 2026-08-30 15:56 | 2026-08-30 15:56 | 2026-08-30 15:57 | 2026-08-30 15:57 |  |  | Fair | Yes | Clean up single phase reading 111,112,224 customer is now okay
Outage | J.E.26.08.77982 | C001904915 | Horace Malcolm | St.James | Completed | Load_249611 | Bogue - 610 | 2026-08-30 13:58 | 2026-08-30 14:17 | 2026-08-30 14:41 | 2026-08-30 14:41 | 2026-08-30 14:48 | 2026-08-30 14:50 | 2026-08-30 14:50 | 2026-08-30 14:50 |  |  | Fair | No | Customer says supply restored issue resolved
Outage | J.E.26.08.78069 | C001904916 | Javid Vernon | Westmoreland | Completed | Load_557380 | Paradise - 210 | 2026-08-30 14:06 | 2026-08-30 14:25 | 2026-08-30 14:48 | 2026-08-30 14:48 | 2026-08-30 16:25 | 2026-08-30 16:45 | 2026-08-30 16:45 | 2026-08-30 16:45 |  |  | Rains | No | Reclose one 25kva transformer use one 3amp fuse
Outage | J.E.26.08.78236 | C001904918 | Collin Robinson | Portland | Completed | Load_255204 | Port Antonio - 310 | 2026-08-30 14:27 | 2026-08-30 14:28 | 2026-08-30 15:48 | 2026-08-30 15:49 | 2026-08-30 16:14 | 2026-08-30 16:20 | 2026-08-30 16:20 | 2026-08-30 16:20 | Fire |  | Fair | No | Repair burn joint at pothead Use 1 one bolt clamp Voltage reading 118v 118v 236v
Outage | J.E.26.08.75134 | C001904920 | Lancelot Brown | Hanover | Completed | Load_252500 | Orange Bay - 310 | 2026-08-30 14:46 | 2026-08-30 14:46 | 2026-08-30 18:37 | 2026-08-30 18:41 | 2026-08-30 18:41 | 2026-08-30 18:41 | 2026-08-30 18:41 | 2026-08-30 18:41 | Fire |  | Fair | No | This call was corrected
Outage | J.E.26.08.78305 | C001904921 | Milton Charlton | KSAN | Completed | Load_252653 | West Kings House - 310 | 2026-08-30 14:53 | 2026-08-30 14:53 | 2026-08-30 15:16 | 2026-08-30 15:16 | 2026-08-30 15:52 | 2026-08-30 15:50 | 2026-08-30 15:54 | 2026-08-30 15:54 |  |  | Fair | No | Found okay upon arrival. Customer has an internal problem.
Outage | J.E.26.08.77971 | C001904924 | Rusean Allen | KSAN | Completed | Load_240875 | Constant Spring - 410 | 2026-08-30 15:12 | 2026-08-30 15:13 | 2026-08-30 17:20 | 2026-08-30 17:20 | 2026-08-30 19:00 | 2026-08-30 19:29 | 2026-08-30 19:29 | 2026-08-30 19:29 |  |  | Fair | No | 1x 3amp fuse found 1x 3amp fuse replaced.
Outage | J.E.26.08.78020 | C001904923 | Rusean Allen | KSAN | Completed | Load_241209 | Constant Spring - 410 | 2026-08-30 15:12 | 2026-08-30 15:13 | 2026-08-30 15:34 | 2026-08-30 15:38 | 2026-08-30 16:34 | 2026-08-30 16:35 | 2026-08-30 16:35 | 2026-08-30 16:35 |  |  | Fair | No
Outage | J.E.26.08.78399 | C001904925 | Rusean Allen | KSAS | Completed | Load_268579 | Duhaney - 310 | 2026-08-30 15:12 | 2026-08-30 15:13 | 2026-08-30 16:35 | 2026-08-30 16:36 | 2026-08-30 17:07 | 2026-08-30 17:10 | 2026-08-30 17:17 | 2026-08-30 17:17 |  |  | Fair | No | Line side of meter socket found okay, customer was advised to contact electrician.
Outage | J.E.26.08.78086 | C001904930 | Lancelot Brown | Hanover | Completed | Load_261941 | Orange Bay - 210 | 2026-08-30 15:19 | 2026-08-30 15:20 | 2026-08-30 18:45 | 2026-08-30 18:50 | 2026-08-30 19:34 | 2026-08-30 19:53 | 2026-08-30 19:53 | 2026-08-30 19:53 |  |  | Fair | No | Found junction fuse blown patroll found vegetation grow on to riser pole caused junction fuse blown cut and remove vegetation from riser pole replace 1-30amps junction fuse no pole number supply restore
Non-Outage | J.E.26.07.34671 | C001904931 | Daniel Francis | St.Ann | Completed | Load_262615 | Cardiff Hall - 310 | 2026-08-30 15:20 | 2026-08-30 15:21 | 2026-08-30 20:30 | 2026-08-30 20:30 | 2026-08-30 20:53 | 2026-08-30 20:54 | 2026-08-30 20:54 | 2026-08-30 20:54 |  |  | Fair | No | Not found customer not answering phone
Non-Outage | J.E.26.08.06909 | C001904934 | Daniel Francis | St.Ann | Completed | Load_260537 | Cardiff Hall - 310 | 2026-08-30 15:20 | 2026-08-30 15:21 | 2026-08-30 19:48 | 2026-08-30 19:49 | 2026-08-30 19:59 | 2026-08-30 20:13 | 2026-08-30 20:14 | 2026-08-30 20:14 | LeaningPole |  | Fair | No | Found 30/c6 pole 100% decay open secondary 45% leaning conducter holding pole
Non-Outage | J.E.26.08.22692 | C001904933 | Daniel Francis | St.Ann | Completed | Load_256738 | Cardiff Hall - 310 | 2026-08-30 15:20 | 2026-08-30 15:21 | 2026-08-30 20:54 | 2026-08-30 20:55 | 2026-08-30 20:55 | 2026-08-30 20:55 | 2026-08-30 20:55 | 2026-08-30 20:55 |  |  | Fair | No | Not found
Non-Outage | J.E.26.08.43370 | C001904932 | Daniel Francis | St.Ann | Completed | Load_268140 | Cardiff Hall - 310 | 2026-08-30 15:20 | 2026-08-30 15:21 | 2026-08-30 20:15 | 2026-08-30 20:15 | 2026-08-30 20:27 | 2026-08-30 20:27 | 2026-08-30 20:29 | 2026-08-30 20:29 |  |  | Fair | No | Unable to locate customer not answering
Outage | J.E.26.08.78481 | C001904935 | Daniel Francis | St.Ann | Completed | Load_241195 | Cardiff Hall - 310 | 2026-08-30 15:24 | 2026-08-30 15:24 | 2026-08-30 17:05 | 2026-08-30 17:05 | 2026-08-30 19:07 | 2026-08-30 19:28 | 2026-08-30 19:32 | 2026-08-30 19:32 |  |  | Fair | No | Found 50 kva fuse blown patrol and re move connections
Non-Outage | J.E.26.08.78457 | C001904940 | Raymond Lewis |  | Completed |  |  | 2026-08-30 15:25 | 2026-08-30 15:26 | 2026-08-30 17:48 | 2026-08-30 17:49 | 2026-08-30 17:48 | 2026-08-30 17:49 | 2026-08-30 17:49 | 2026-08-30 17:49 |  |  | Fair | No | Supply restored
Outage | J.E.26.08.76070 | C001904936 | Raymond Lewis | St.Ann | Completed | Load_262212 | Roaring River - 210 | 2026-08-30 15:25 | 2026-08-30 15:26 | 2026-08-30 16:16 | 2026-08-30 16:17 | 2026-08-30 16:17 | 2026-08-30 16:20 | 2026-08-30 16:20 | 2026-08-30 16:20 |  |  | Fair | No | Phone turn off
Outage | J.E.26.08.78286 | C001904939 | Raymond Lewis | St.Ann | Completed | Load_241493 | Roaring River - 210 | 2026-08-30 15:25 | 2026-08-30 15:26 | 2026-08-30 17:47 | 2026-08-30 17:47 | 2026-08-30 17:47 | 2026-08-30 17:48 | 2026-08-30 17:48 | 2026-08-30 17:48 |  |  | Fair | No | Supply restored
Outage | J.E.26.08.78333 | C001904937 | Raymond Lewis | St.Ann | Completed | Load_269789 | Roaring River - 410 | 2026-08-30 15:25 | 2026-08-30 15:26 | 2026-08-30 16:23 | 2026-08-30 16:23 | 2026-08-30 16:48 | 2026-08-30 17:40 | 2026-08-30 17:41 | 2026-08-30 17:41 |  |  | Fair | No | Remove vegetables from x former pole and refuse and close 10 amp junction and 15 kva x former
Outage | J.E.26.08.78451 | C001904938 | Raymond Lewis | St.Ann | Completed | Load_237943 | Roaring River - 210 | 2026-08-30 15:25 | 2026-08-30 15:26 | 2026-08-30 17:43 | 2026-08-30 17:44 | 2026-08-30 17:43 | 2026-08-30 17:45 | 2026-08-30 17:45 | 2026-08-30 17:45 |  |  | Fair | No | Supply restored
Non-Outage | J.E.26.08.17555 | C001904947 | Raymond Lewis | St.Ann | Completed | Load_245542 | Roaring River - 410 | 2026-08-30 15:30 | 2026-08-30 15:31 | 2026-08-30 18:02 | 2026-08-30 18:02 | 2026-08-30 18:02 | 2026-08-30 18:03 | 2026-08-30 18:03 | 2026-08-30 18:03 |  |  | Fair | No | Supply restored
Non-Outage | J.E.26.08.24552 | C001904948 | Raymond Lewis | St.Ann | Completed | Load_242742 | Roaring River - 410 | 2026-08-30 15:30 | 2026-08-30 15:31 | 2026-08-30 17:58 | 2026-08-30 17:59 | 2026-08-30 17:58 | 2026-08-30 18:00 | 2026-08-30 18:00 | 2026-08-30 18:00 |  |  | Fair | No | Supply restored
Non-Outage | J.E.26.08.24720 | C001904945 | Raymond Lewis | St.Ann | Completed | Load_256279 | Roaring River - 410 | 2026-08-30 15:30 | 2026-08-30 15:31 | 2026-08-30 17:54 | 2026-08-30 17:55 | 2026-08-30 17:54 | 2026-08-30 17:55 | 2026-08-30 17:55 | 2026-08-30 17:55 |  |  | Fair | No | Phone not answering
Non-Outage | J.E.26.08.25095 | C001904946 | Raymond Lewis | St.Ann | Completed | Load_253335 | Roaring River - 410 | 2026-08-30 15:30 | 2026-08-30 15:31 | 2026-08-30 18:07 | 2026-08-30 18:08 | 2026-08-30 18:07 | 2026-08-30 18:08 | 2026-08-30 18:08 | 2026-08-30 18:08 |  |  | Fair | No | Phone not answering
Non-Outage | J.E.26.08.25328 | C001904944 | Raymond Lewis | St.Ann | Completed | Load_246811 | Roaring River - 410 | 2026-08-30 15:30 | 2026-08-30 15:31 | 2026-08-30 18:28 | 2026-08-30 18:28 | 2026-08-30 18:29 | 2026-08-30 18:30 | 2026-08-30 18:30 | 2026-08-30 18:30 |  |  | Fair | No | Supply restored
Non-Outage | J.E.26.08.27304 | C001904943 | Raymond Lewis | St.Ann | Completed | Load_267559 | Roaring River - 410 | 2026-08-30 15:30 | 2026-08-30 15:31 | 2026-08-30 18:10 | 2026-08-30 18:11 | 2026-08-30 18:26 | 2026-08-30 18:27 | 2026-08-30 18:27 | 2026-08-30 18:27 |  |  | Fair | No | Supply restored
Non-Outage | J.E.26.08.78315 | C001904952 | Ricky Hall |  | Completed |  |  | 2026-08-30 15:38 | 2026-08-30 15:40 | 2026-08-30 16:50 | 2026-08-30 16:50 | 2026-08-30 17:41 | 2026-08-30 18:08 | 2026-08-30 18:09 | 2026-08-30 18:09 | Fire |  | Fair | No | No fire seen
Outage | J.E.26.08.78429 | C001904953 | Nickolas Rodriques | St.Catherine | Completed | Load_267024 | Twickenham - 210 | 2026-08-30 15:40 | 2026-08-30 15:42 | 2026-08-30 16:16 | 2026-08-30 16:24 | 2026-08-30 17:04 | 2026-08-30 17:22 | 2026-08-30 17:26 | 2026-08-30 17:26 |  |  | Fair | No | Area was patrolled and no noticeable outage was found.
Outage | J.E.26.08.78491 | C001904954 | Nickolas Rodriques | St.Catherine | Completed | Load_249085 | Twickenham - 210 | 2026-08-30 15:40 | 2026-08-30 15:42 | 2026-08-30 17:26 | 2026-08-30 17:44 | 2026-08-30 18:05 | 2026-08-30 18:12 | 2026-08-30 18:14 | 2026-08-30 18:14 |  |  | Fair | No | Found area with electricity.
Outage | J.E.26.08.78582 | C001904958 | Ricky Hall | St.Catherine | Completed | Load_240657 | New Michelton - 210 | 2026-08-30 15:42 | 2026-08-30 15:43 | 2026-08-30 16:49 | 2026-08-30 18:09 | 2026-08-30 18:09 | 2026-08-30 18:09 | 2026-08-30 18:09 | 2026-08-30 18:09 |  |  | Fair | No | Replaced blown 20 amps junction fuse
Outage | J.E.26.08.78584 | C001904959 | Ricky Hall | St.Catherine | Completed | Load_265416 | New Michelton - 210 | 2026-08-30 15:42 | 2026-08-30 17:08 | 2026-08-30 18:09 | 2026-08-30 18:10 | 2026-08-30 18:10 | 2026-08-30 18:10 | 2026-08-30 18:10 | 2026-08-30 18:10 |  |  | Fair | No | Call associated with outage #78315
Outage | J.E.26.08.75890 | C001904961 | Derrick Dawkins | St.James | Completed | Load_256979 | Bogue - 310 | 2026-08-30 15:44 | 2026-08-30 16:00 | 2026-08-30 16:37 | 2026-08-30 20:44 | 2026-08-30 20:44 | 2026-08-30 21:21 | 2026-08-30 21:27 | 2026-08-30 21:27 |  |  | Fair | No | Found premises ok
Outage | J.E.26.08.78384 | C001904960 | Derrick Dawkins | St.James | Completed | Load_269249 | Bogue - 310 | 2026-08-30 15:44 | 2026-08-30 16:00 | 2026-08-30 16:31 | 2026-08-30 17:43 | 2026-08-30 18:13 | 2026-08-30 20:36 | 2026-08-30 20:43 | 2026-08-30 20:43 |  |  | Fair | No | Found 1 span of secondary phase and neutral burnt down due to vehicle accident open 25kva transformer to carry out repairs splice and retention use 40ft of #2 aluminum conductor 4 pg clamp
Non-Outage | J.E.26.08.78515 | C001904965 | Error Coore | Manchester | Completed | Load_248551 | Spur Tree - 310 | 2026-08-30 16:05 | 2026-08-31 08:55 | 2026-08-31 10:10 | 2026-08-31 10:12 | 2026-08-31 10:45 | 2026-08-31 11:05 | 2026-08-31 11:06 | 2026-08-31 11:06 | Fire |  | Fair | No | Premises found ok no fire seen in area
Outage | J.E.26.08.78501 | C001904964 | Wayne Dillion | St.Elizabeth | Completed | Load_250315 | Maggotty - 110 | 2026-08-30 16:05 | 2026-08-30 16:07 | 2026-08-30 16:35 | 2026-08-30 16:35 | 2026-08-30 17:42 | 2026-08-30 18:28 | 2026-08-30 18:29 | 2026-08-30 18:29 |  |  | Fair | No | Patrol and found one blown 1.5amp fuse fuse that protects chip type transformer size not visible. Replace same and supply restored okay.
Outage | J.E.26.08.78486 | C001904966 | Wayne Dillion | St.Elizabeth | Completed | Load_255127 | Maggotty - 110 | 2026-08-30 16:06 | 2026-08-30 16:08 | 2026-08-30 18:30 | 2026-08-30 18:30 | 2026-08-30 18:30 | 2026-08-30 17:58 | 2026-08-30 18:32 | 2026-08-30 18:32 |  |  | Fair | No | Patrol and found one blown 3amp fuse that protects 25kva transformer circuit no pole #. Replace same and supply restored okay.
Non-Outage | J.E.26.08.62581 | C001904968 | Ryan Richards | Manchester | Completed | Load_258254 | Spur Tree - 310 | 2026-08-30 16:12 | 2026-08-30 16:14 | 2026-08-30 21:17 | 2026-08-30 21:18 | 2026-08-31 06:53 | 2026-08-31 06:54 | 2026-08-31 06:54 | 2026-08-31 06:54 |  |  | Fair | No | Corroded neutral found at pole remade corroded neutral using 1 one bolt clamp voltage 112/115/227 volts
Non-Outage | J.E.26.08.60941 | C001904970 | Ryan Richards | Manchester | Completed | Load_1002354 | Spur Tree - 310 | 2026-08-30 16:13 | 2026-08-30 16:14 | 2026-08-30 17:12 | 2026-08-30 17:13 | 2026-08-30 18:13 | 2026-08-30 18:18 | 2026-08-30 18:19 | 2026-08-30 18:19 | BrokenPole |  | Fair | No | Leaning 35-6 ta pole found rotten at base leaning toward customer house pole needs to replace asap
Non-Outage | J.E.26.08.61775 | C001904969 | Ryan Richards | Manchester | Completed | Load_263980 | Spur Tree - 310 | 2026-08-30 16:13 | 2026-08-30 16:14 | 2026-08-30 18:19 | 2026-08-30 18:20 | 2026-08-30 18:56 | 2026-08-30 19:56 | 2026-08-30 19:56 | 2026-08-30 19:56 |  |  | Fair | Yes | Defective service wire found rotten cause by sea air replaced 60ft#6 triplex 3 penunion 3 one bolt clamps voltage 113/109/222 volts
Non-Outage | J.E.26.08.78756 | C001904972 | Stephen Taylor | St.Thomas | Completed | Load_252412 | Lysson - 410 | 2026-08-30 16:22 | 2026-08-30 16:23 | 2026-08-30 16:40 | 2026-08-30 16:41 | 2026-08-30 17:20 | 2026-08-30 17:20 | 2026-08-30 17:21 | 2026-08-30 17:21 |  |  | Fair | No | Clean up single phase line 2 clamps Rdg 113–112–225
Outage | J.E.26.08.78932 | C001904975 | Rusean Allen | KSAN | Completed | Load_268840 | Constant Spring - 410 | 2026-08-30 17:00 | 2026-08-30 17:01 | 2026-08-30 20:42 | 2026-08-30 20:47 | 2026-08-30 21:23 | 2026-08-30 21:30 | 2026-08-30 21:30 | 2026-08-30 21:30 |  |  | Fair | No | Internal issue, customer already contacted electrician
Outage | J.E.26.08.78589 | C001904979 | Hartley Chin | Clarendon | Completed | Load_267347 | May Pen - 110 | 2026-08-30 17:06 | 2026-08-30 17:07 | 2026-08-30 19:00 | 2026-08-30 19:34 | 2026-08-30 19:34 | 2026-08-30 20:49 | 2026-08-30 20:53 | 2026-08-30 20:53 |  |  | Fair | No | Found blown 15 amp junction fuse @ pole # 0202742 due to contact, cut tree from line , refused junction..
Outage | J.E.26.08.78840 | C001904978 | Hartley Chin | Clarendon | Completed | Load_268174 | May Pen - 110 | 2026-08-30 17:06 | 2026-08-30 17:07 | 2026-08-30 21:47 | 2026-08-30 21:50 | 2026-08-30 23:01 | 2026-08-30 23:14 | 2026-08-30 23:28 | 2026-08-30 23:28 |  |  | Fair | No | Found okay … voltage read 113v , 114v …
Outage | J.E.26.08.78884 | C001904977 | Hartley Chin | Clarendon | Completed | Load_255040 | May Pen - 110 | 2026-08-30 17:06 | 2026-08-30 17:07 | 2026-08-30 20:53 | 2026-08-30 20:54 | 2026-08-30 21:08 | 2026-08-30 21:46 | 2026-08-30 21:46 | 2026-08-30 21:46 |  |  | Fair | No | Found blown 20 amp junction fuse (no pole #) line patrolled and found okay , junction refused…
Outage | J.E.26.08.78952 | C001904986 | Ryan Richards | Manchester | Completed | Load_292136 | Spur Tree - 310 | 2026-08-30 17:26 | 2026-08-30 17:27 | 2026-08-30 19:58 | 2026-08-30 19:58 | 2026-08-30 21:01 | 2026-08-30 21:17 | 2026-08-30 21:17 | 2026-08-30 21:17 |  |  | Fair | No | Premises found ok customer having internal problems customer has been advised voltage 111/113/224 volts
Outage | J.E.26.08.78901 | C001904989 | Andrew Powell | St.Elizabeth | Completed | Load_252414 | Maggotty - 210 | 2026-08-30 17:29 | 2026-08-30 17:31 | 2026-08-30 17:41 | 2026-08-30 17:41 | 2026-08-30 18:54 | 2026-08-30 19:57 | 2026-08-30 19:59 | 2026-08-30 19:59 |  |  | Fair | No | Clear vegetation from secondary line. Tension two pole span of sagging secondary neutral conductor using one preform. Burnt 25 kva transformer can’t tied in approximately 21 customers affected, please refer to Mr Delroy crew for replacement.
Outage | J.E.26.08.78924 | C001904988 | Wayne Dillion | St.Elizabeth | Completed | Load_250315 | Maggotty - 110 | 2026-08-30 17:29 | 2026-08-30 17:32 | 2026-08-30 18:32 | 2026-08-30 18:32 | 2026-08-30 18:32 | 2026-08-30 18:33 | 2026-08-30 18:33 | 2026-08-30 18:33 |  |  | Fair | No | Supply restored to the area.
Non-Outage | J.E.26.08.67621 | C001904992 | Javid Vernon | Westmoreland | Completed | Load_255934 | Paradise - 110 | 2026-08-30 17:33 | 2026-08-30 17:34 | 2026-08-30 19:51 | 2026-08-30 19:53 | 2026-08-30 20:56 | 2026-08-30 21:28 | 2026-08-30 21:29 | 2026-08-30 21:29 |  |  | Fair | No | Area check and found okay unable to locate customer and and premises phone calls to customer number went unanswered and good direction was given
Non-Outage | J.E.26.08.78448 | C001904990 | Javid Vernon | Westmoreland | Completed | Load_255047 | Paradise - 210 | 2026-08-30 17:33 | 2026-08-30 17:34 | 2026-08-31 09:44 | 2026-08-31 09:44 | 2026-08-31 10:48 | 2026-08-31 11:05 | 2026-08-31 11:05 | 2026-08-31 11:05 | LeaningPole |  | Fair | No | Check and found one 35feet class 6 wooden pole leaning with single phase and primary and secondary that needs to be straightened refer to maintenance
Non-Outage | J.E.26.08.78695 | C001904991 | Javid Vernon | Westmoreland | Completed | Load_255047 | Paradise - 210 | 2026-08-30 17:33 | 2026-08-30 17:34 | 2026-08-30 21:31 | 2026-08-30 21:31 | 2026-08-30 22:39 | 2026-08-30 22:52 | 2026-08-30 22:58 | 2026-08-30 22:58 | LeaningPole |  | Fair | No | Area check and found okay no leaning pole
Non-Outage | J.E.26.08.78894 | C001904993 | Error Coore | Manchester | Completed | Load_1002530 | Kendal - 310 | 2026-08-30 17:36 | 2026-08-31 08:57 | 2026-08-31 11:59 | 2026-08-31 11:59 | 2026-08-31 12:21 | 2026-08-31 12:23 | 2026-08-31 12:27 | 2026-08-31 12:27 | BrokenPole |  | Fair | No | Found a 35 ft T pole rotten at base need some attention
Outage | J.E.26.08.79041 | C001904995 | Nickolas Rodriques | Portmore | Completed | Load_412907 | Naggo Head - 510 | 2026-08-30 17:53 | 2026-08-30 17:55 | 2026-08-30 18:14 | 2026-08-30 18:19 | 2026-08-30 18:54 | 2026-08-30 20:25 | 2026-08-30 20:33 | 2026-08-30 20:33 |  |  | Fair | No | Checked and found four junction fuses blown (40 amp, 15 amp and two 30 amp) caused by bird. Repaired by replacing the fuses and a fuse holder after completing patrol. After closing up, two sets of bank of three transformers were seen sparking over the apartment side. Further checks revealed that a fuse holder is missing from one of the three phase lines which feeds that section. To address this issue, the missing fuse holder was replaced with a 15 amp junction fuse. After replacing the fuse holder, no sparking was seen. The customers over that side that were experiencing unstable voltage due to the sparking, all confirmed that the issue has since been resolved.
Outage | J.E.26.08.78995 | C001904996 | Nickolas Rodriques | Portmore | Completed | Load_556669 | Naggo Head - 510 | 2026-08-30 17:54 | 2026-08-30 17:55 | 2026-08-30 20:33 | 2026-08-30 20:34 | 2026-08-30 20:40 | 2026-08-30 21:02 | 2026-08-30 21:05 | 2026-08-30 21:05 |  |  | Fair | No | Power restored. Call relates to the junction fuses that were replaced.
Outage | J.E.26.08.75345 | C001904997 | Wayne Dillion | St.Elizabeth | Completed | Load_241578 | Maggotty - 110 | 2026-08-30 17:55 | 2026-08-30 17:56 | 2026-08-30 18:40 | 2026-08-30 18:40 | 2026-08-30 20:21 | 2026-08-30 20:33 | 2026-08-30 20:33 | 2026-08-30 20:33 | BrokenPole |  | Fair | No | Patrol and found one broken 35ft wooden T pole caused by vehicle accident. Primary is dislodged from broken pole however secondary conductors still attached. All lines are energized and all customers have supply however conductors are hanging low no big unit cannot pass. Please refer this call to the maintenance department to have this critical matter dealt with urgent in the morning.
Non-Outage | J.E.26.08.79053 | C001904999 | Raymond Carr | St.Mary | Completed | Load_353347 | Oracabessa - 210 | 2026-08-30 18:04 | 2026-08-30 18:05 | 2026-08-30 20:02 | 2026-08-30 20:03 | 2026-08-30 21:12 | 2026-08-30 21:00 | 2026-08-30 21:14 | 2026-08-30 21:14 | Fire |  | Fair | No | Customer couldn’t be contacted.
Outage | J.E.26.08.79110 | C001905000 | Collin Robinson | Portland | Completed | Load_248393 | Port Antonio - 310 | 2026-08-30 18:07 | 2026-08-30 18:09 | 2026-08-30 19:31 | 2026-08-30 19:32 | 2026-08-30 21:03 | 2026-08-30 21:17 | 2026-08-30 21:17 | 2026-08-30 21:17 |  |  | Fair | No | Patrol and found Area with supply
Non-Outage | J.E.26.08.79351 | C001905002 | Error Coore | Manchester | Completed | Load_238080 | Spur Tree - 310 | 2026-08-30 18:36 | 2026-08-31 08:56 | 2026-08-31 12:29 | 2026-08-31 12:29 | 2026-08-31 13:23 | 2026-08-31 13:47 | 2026-08-31 13:48 | 2026-08-31 13:48 |  |  | Fair | No | Premises found locked not getting customer on phone unable to access meter
Outage | J.E.26.08.78852 | C001905005 | Rochaine Palmer | KSAS | Completed | Load_249762 | Rockfort - 210 | 2026-08-30 18:44 | 2026-08-30 19:11 | 2026-08-30 19:28 | 2026-08-30 19:29 | 2026-08-30 20:13 | 2026-08-30 20:15 | 2026-08-30 20:36 | 2026-08-30 20:36 |  |  | Fair | No | Found okay upon arrival. States they didn’t report any problem supply is normal. No one is at the premises but customer check there cameras and it’s working.
Outage | J.E.26.08.79027 | C001905009 | Nickolas Rodriques | Portmore | Completed | Load_243335 | Naggo Head - 610 | 2026-08-30 18:47 | 2026-08-30 18:48 | 2026-08-30 21:05 | 2026-08-30 21:08 | 2026-08-30 21:41 | 2026-08-30 21:56 | 2026-08-30 22:03 | 2026-08-30 22:03 |  |  | Fair | No | Unable to reach Deloris Wilson via the contact number/address provided. Daniel Chowfen was contacted and stated that he does not occupy that premises.
Outage | J.E.26.08.79373 | C001905013 | Wan Carlos Scarlett | St.Catherine | Completed | Load_258407 | New Michelton - 310 | 2026-08-30 18:53 | 2026-08-30 18:55 | 2026-08-30 19:00 | 2026-08-30 19:00 | 2026-08-30 20:22 | 2026-08-30 21:41 | 2026-08-30 21:44 | 2026-08-30 21:44 | Fire |  | Fair | No | Refuse 15amp junction no pole # was found suspect lightning take out the power supply
Outage | J.E.26.08.79450 | C001905015 | Stephen Taylor | St.Thomas | Completed | Load_254225 | Lysson - 410 | 2026-08-30 18:58 | 2026-08-30 19:01 | 2026-08-30 19:53 | 2026-08-30 19:53 | 2026-08-30 20:26 | 2026-08-30 20:26 | 2026-08-30 21:08 | 2026-08-30 21:08 |  |  | Fair | No | Clean up single phase line 3 clamps Rdg 113–114–226
Outage | J.E.26.08.79497 | C001905017 | Richard Nicholas | St.Catherine | Completed | Load_260217 | Rhodens Pen - 210 | 2026-08-30 19:01 | 2026-08-30 19:02 | 2026-08-30 19:33 | 2026-08-30 19:33 | 2026-08-30 20:48 | 2026-08-30 21:14 | 2026-08-30 21:15 | 2026-08-30 21:15 |  |  | Fair | No | Area found ok
Outage | J.E.26.08.79506 | C001905019 | Ricky Hall | St.Catherine | Completed | Load_265416 | New Michelton - 210 | 2026-08-30 19:04 | 2026-08-30 19:05 | 2026-08-30 19:14 | 2026-08-30 19:14 | 2026-08-30 20:02 | 2026-08-30 21:13 | 2026-08-30 21:48 | 2026-08-30 21:48 |  |  | Fair | No | Disconnect defective lightening arresterfor 50 kva xfmr replaced 5 amp fuse for the same Lao 25 amp junction fuse
Non-Outage | J.E.26.08.79601 | C001905049 | Hopeton Henry | St.Thomas | Completed | Load_249841 | Good Year - 210 | 2026-08-30 20:13 | 2026-08-31 08:06 | 2026-08-31 09:40 | 2026-08-31 11:12 | 2026-08-31 11:11 | 2026-08-31 11:48 | 2026-08-31 11:50 | 2026-08-31 11:50 | Fire |  | Fair | No | Found ok , no spark found
Non-Outage | J.E.26.08.80383 | C001905052 | Raymond Carr | St.Mary | Completed | Load_353347 | Oracabessa - 210 | 2026-08-30 20:34 | 2026-08-30 20:35 | 2026-08-30 21:14 | 2026-08-30 21:15 | 2026-08-30 21:25 | 2026-08-30 23:00 | 2026-08-30 22:58 | 2026-08-30 22:58 |  |  | Fair | No | Four defective clamps were replaced at transformer drop.Supply was restored.
Outage | J.E.26.08.80235 | C001905053 | Nickolas Rodriques | St.Catherine | Completed | Load_255965 | Twickenham - 210 | 2026-08-30 20:35 | 2026-08-30 20:36 | 2026-08-31 14:06 | 2026-08-31 14:07 | 2026-08-31 14:44 | 2026-08-31 14:56 | 2026-08-31 14:58 | 2026-08-31 14:58 |  |  | Fair | No | Customer confirmed that the area outage was restored.
Outage | J.E.26.08.80013 | C001905054 | Rochaine Palmer | KSAS | Completed | Load_259841 | Rockfort - 210 | 2026-08-30 20:36 | 2026-08-30 20:37 | 2026-08-30 21:09 | 2026-08-30 21:13 | 2026-08-30 22:16 | 2026-08-30 22:20 | 2026-08-30 22:24 | 2026-08-30 22:24 |  |  | Fair | No | Found one 25 amps junction fuse blown at pole #600535 and one fuse blown at pole #( no pole#). Refused and reclose the 25 amps junction switch. Unable to patrol the next line section properly to close the next switch. Need daylight attention line section of to be patrol on foot. No a motor vehicle road. Day light attention line section.
Outage | J.E.26.08.80454 | C001905058 | Richard Nicholas | St.Catherine | Completed | Load_1000328 | Tredegar - 210 | 2026-08-30 20:41 | 2026-08-30 20:42 | 2026-08-30 21:15 | 2026-08-30 21:36 | 2026-08-30 21:41 | 2026-08-30 21:58 | 2026-08-30 22:00 | 2026-08-30 22:00 |  |  | Fair | No | Reset tripped 10kva transformer that is located on pole #006610
Outage | J.E.26.08.80729 | C001905059 | Richard Nicholas | St.Catherine | Completed | Load_238376 | Twickenham - 310 | 2026-08-30 20:49 | 2026-08-30 20:50 | 2026-08-30 22:00 | 2026-08-30 22:00 | 2026-08-30 22:27 | 2026-08-30 22:48 | 2026-08-30 22:50 | 2026-08-30 22:50 |  | Y | Fair | No | Bushing required.replaced blown 15amp junctions fuse on 2phase T-off to garbally dr.
Outage | J.E.26.08.79021 | C001905060 | Horace Malcolm | St.James | Completed | Load_268384 | Bogue - 610 | 2026-08-30 20:52 | 2026-08-30 21:05 | 2026-08-30 22:01 | 2026-08-30 22:02 | 2026-08-30 22:33 | 2026-08-30 22:52 | 2026-08-30 22:53 | 2026-08-30 22:53 |  |  | Rains | No | Clean and remake joints at pole used 1clamp voltage 113-115-228
Non-Outage | J.E.26.08.79244 | C001905063 | Lancelot Brown | Hanover | Completed | Load_243282 | Orange Bay - 210 | 2026-08-30 21:04 | 2026-08-30 21:05 | 2026-08-30 21:48 | 2026-08-30 21:48 | 2026-08-30 22:03 | 2026-08-30 22:46 | 2026-08-30 22:46 | 2026-08-30 22:46 |  |  | Rains | No | Splice and retention triplex service line used thirty feet #6 three connectors two pg clamps vl at meter socket 114-113-228
Outage | J.E.26.08.80916 | C001905067 | Stephen Taylor | St.Thomas | Completed | Load_240594 | Good Year - 210 | 2026-08-30 21:19 | 2026-08-30 21:27 | 2026-08-31 18:20 | 2026-08-31 18:21 | 2026-08-31 18:20 | 2026-08-31 18:21 | 2026-08-31 18:22 | 2026-08-31 18:22 |  |  | Fair | No | Check with customer and customer said power is back now okay
Outage | J.E.26.08.80946 | C001905068 | Romeo Brissett | St.James | Completed | Load_263658 | Bogue - 610 | 2026-08-30 21:19 | 2026-08-31 00:14 | 2026-08-31 03:57 | 2026-08-31 03:57 | 2026-08-31 04:38 | 2026-08-31 06:00 | 2026-08-31 06:08 | 2026-08-31 06:08 | Fire |  | Fair | No | Found (1)10KVA transformer fuse blow due to customer defective pothead, Disconnected defective pothead replaced (1)10KVA transformer fuse, V/R 119-120-240. Customer was advised to get an electrician.
Non-Outage | J.E.26.08.70656 | C001905075 | Horace Malcolm |  | Completed |  |  | 2026-08-30 22:09 | 2026-08-31 08:03 | 2026-08-31 09:57 | 2026-08-31 09:58 | 2026-08-31 10:31 | 2026-08-31 10:45 | 2026-08-31 10:46 | 2026-08-31 10:46 |  |  | Fair | No | Check and found no found area ok unable to locate customer multiple calls to customer unavailable
Outage | J.E.26.08.81026 | C001905079 | Lancelot Brown | Hanover | Completed | Load_261941 | Orange Bay - 210 | 2026-08-30 22:39 | 2026-08-30 22:40 | 2026-08-30 22:47 | 2026-08-30 22:47 | 2026-08-30 22:47 | 2026-08-30 19:53 | 2026-08-30 22:54 | 2026-08-30 22:54 |  |  | Rains | No | Found junction fuse blown patroll found vegetation grow on riser pole cut and remove vegetation from riser pole replace 1-30amps junction fuse no pole number further checks found out 50kva pad mount transformer diffective need to replace please pass on to maintenance department at Bogue need ergent attention
Outage | J.E.26.08.80330 | C001905082 | Delano Gayle | St.Catherine | Completed | Load_555922 | Twickenham - 210 | 2026-08-30 23:57 | 2026-08-30 23:59 | 2026-08-31 04:17 | 2026-08-31 04:18 | 2026-08-31 04:36 | 2026-08-31 05:16 | 2026-08-31 05:16 | 2026-08-31 05:16 |  |  | Fair | No | Blown junction on main no pole#, patrolled line section and found okay for closure replace 30amps
Outage | J.E.26.08.80282 | C001905084 | Delano Gayle | St.Catherine | Completed | Load_267782 | Twickenham - 210 | 2026-08-30 23:58 | 2026-08-30 23:59 | 2026-08-31 05:17 | 2026-08-31 05:17 | 2026-08-31 05:21 | 2026-08-31 05:21 | 2026-08-31 05:21 | 2026-08-31 05:21 |  |  | Fair | No | Premises found okay related to call where 30amps junction fuse was replaced
Outage | J.E.26.08.80327 | C001905083 | Delano Gayle | St.Catherine | Completed | Load_237824 | Tredegar - 210 | 2026-08-30 23:58 | 2026-08-30 23:59 | 2026-08-31 00:24 | 2026-08-31 03:40 | 2026-08-31 03:59 | 2026-08-31 04:05 | 2026-08-31 04:06 | 2026-08-31 04:06 |  |  | Fair | No | Area patrolled and found okay