## sheet1
Detail
Job Type | Job | Order No. | Crew | Parish | Order Status | Device | Feeder | Creation Time | Assigned Time | Acknowlege Time | Enroute Time | On-Site Time | Actual Comp. Time | Comp. Time | Final Comp. Time | Hazard List | Tree Contact | Weather Condition | Phase Change | Technician Notes
Outage | J.E.26.07.40229 | C001871414 | Edward Royal | KSAS | Completed | Load_258805 | Greenwich - 510 | Jul 31, 2026 11:58pm | Jul 31, 2026 11:59pm | Aug 1, 2026 10:46am | Aug 1, 2026 10:46am | Aug 1, 2026 10:46am | Aug 1, 2026 10:49am | Aug 1, 2026 10:50am | Aug 1, 2026 10:50am |  |  | Fair | No | Replaced 3 one bolt clamps on the pothead voltage reading 120v 119v 238.7v
Outage | J.E.26.07.40254 | C001871413 | Edward Royal | KSAS | Completed | Load_241234 | Duhaney - 310 | Jul 31, 2026 11:55pm | Jul 31, 2026 11:59pm | Aug 1, 2026 2:01am | Aug 1, 2026 2:01am | Aug 1, 2026 2:01am | Aug 1, 2026 2:02am | Aug 1, 2026 2:02am | Aug 1, 2026 2:02am |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.07.40251 | C001871412 | Delano Gayle | St.Catherine | Completed | Load_261448 | Tredegar - 210 | Jul 31, 2026 11:49pm | Jul 31, 2026 11:50pm | Aug 1, 2026 1:47am | Aug 1, 2026 1:47am | Aug 1, 2026 2:14am | Aug 1, 2026 2:44am | Aug 1, 2026 2:44am | Aug 1, 2026 2:44am | Fire |  | Fair | No | Found okay at meter voltage readings 112-113-226 on load test advised customer
Outage | J.E.26.07.39659 | C001871411 | Shamour Haughton | St.James | Completed | Load_293417 | Queens Drive - 310 | Jul 31, 2026 11:46pm | Jul 31, 2026 11:50pm | Aug 1, 2026 1:42am | Aug 1, 2026 1:42am | Aug 1, 2026 1:42am | Aug 1, 2026 1:42am | Aug 1, 2026 1:44am | Aug 1, 2026 1:44am |  |  | Fair | No | Customer stated that power was restored
Outage | J.E.26.07.40143 | C001871410 | Shamour Haughton | St.James | Completed | Load_302407 | Bogue - 610 | Jul 31, 2026 11:45pm | Jul 31, 2026 11:50pm | Aug 1, 2026 6:26am | Aug 1, 2026 6:26am | Aug 1, 2026 8:25am | Aug 1, 2026 8:25am | Aug 1, 2026 8:28am | Aug 1, 2026 8:28am |  |  | Fair | No | Found 1,50amp junction fuse blown, refuse 50amp junction
Outage | J.E.26.07.40172 | C001871409 | Shamour Haughton | St.James | Completed | Load_246802 | Bogue - 610 | Jul 31, 2026 11:26pm | Jul 31, 2026 11:36pm | Aug 1, 2026 8:29am | Aug 1, 2026 8:29am | Aug 1, 2026 8:29am | Aug 1, 2026 8:29am | Aug 1, 2026 8:30am | Aug 1, 2026 8:30am |  |  | Fair | No | Related to previous call
Outage | J.E.26.07.40241 | C001871408 | Shamour Haughton | St.James | Completed | Load_243530 | Bogue - 610 | Jul 31, 2026 11:26pm | Jul 31, 2026 11:36pm | Aug 1, 2026 8:28am | Aug 1, 2026 8:28am | Aug 1, 2026 8:28am | Aug 1, 2026 8:28am | Aug 1, 2026 8:28am | Aug 1, 2026 8:28am |  |  | Fair | No | Related to previous call
Outage | J.E.26.07.39473 | C001871407 | Shamour Haughton | St.James | Completed | Load_266674 | Bogue - 410 | Jul 31, 2026 11:01pm | Jul 31, 2026 11:03pm | Jul 31, 2026 11:15pm | Jul 31, 2026 11:15pm | Aug 1, 2026 12:17am | Aug 1, 2026 12:25am | Aug 1, 2026 12:51am | Aug 1, 2026 12:51am | Fire |  | Fair | No | At the time of visit no fire was found, customer states they made a report because electricity went, power was found on the property, voltage left 227,229,229,409,413,413
Outage | J.E.26.07.40069 | C001871406 | Delano Gayle | St.Catherine | Completed | Load_248875 | Tredegar - 510 | Jul 31, 2026 10:51pm | Jul 31, 2026 11:03pm | Jul 31, 2026 11:59pm | Jul 31, 2026 11:59pm | Jul 31, 2026 11:59pm | Aug 1, 2026 12:00am | Aug 1, 2026 12:00am | Aug 1, 2026 12:00am |  |  | Fair | No | Premises found okay, power restored
Outage | J.E.26.07.40193 | C001871405 | Edward Royal | KSAN | Completed | Load_268847 | Constant Spring - 310 | Jul 31, 2026 10:43pm | Jul 31, 2026 10:48pm | Aug 1, 2026 2:03am | Aug 1, 2026 2:03am | Aug 1, 2026 3:41am | Aug 1, 2026 3:43am | Aug 1, 2026 3:43am | Aug 1, 2026 3:43am |  |  | Fair | No | Spliced and reconnected service cable using 30ft number 2 cable and 6 single bolt clamp
Outage | J.E.26.07.40211 | C001871404 | Edward Royal | KSAN | Completed | Load_262366 | Constant Spring - 410 | Jul 31, 2026 10:43pm | Jul 31, 2026 10:48pm | Aug 1, 2026 2:01am | Aug 1, 2026 2:01am | Aug 1, 2026 2:01am | Aug 1, 2026 2:01am | Aug 1, 2026 2:01am | Aug 1, 2026 2:01am |  |  | Fair | No | Premises found ok related to outage
Non-Outage | J.E.26.07.39992 | C001871403 | Edward Royal | null | Completed | null | null | Jul 31, 2026 10:42pm | Jul 31, 2026 10:50pm | Aug 1, 2026 10:25am | Aug 1, 2026 10:25am | Aug 1, 2026 10:25am | Aug 1, 2026 9:31am | Aug 1, 2026 10:27am | Aug 1, 2026 10:27am | Fire |  | Fair | No | Contact customer by phone customer said the problem was resolved
Non-Outage | J.E.26.07.40201 | C001871402 | Edward Royal | null | Completed | null | null | Jul 31, 2026 10:42pm | Jul 31, 2026 10:49pm | Aug 1, 2026 12:47am | Aug 1, 2026 2:02am | Aug 1, 2026 2:02am | Aug 1, 2026 2:03am | Aug 1, 2026 2:03am | Aug 1, 2026 2:03am | BrokenWire |  | Fair | No | When contacted customer by phone customer said that the power was restored
Outage | J.E.26.07.40191 | C001871400 | Delano Gayle | Portmore | Completed | Load_557221 | Naggo Head - 610 | Jul 31, 2026 9:42pm | Jul 31, 2026 10:53pm | Aug 1, 2026 4:31am | Aug 1, 2026 4:31am | Aug 1, 2026 5:29am | Aug 1, 2026 5:34am | Aug 1, 2026 5:34am | Aug 1, 2026 5:34am | Fire |  | Fair | No | Single customer premises not found y
Outage | J.E.26.07.40176 | C001871396 | Edward Royal | KSAS | Completed | Load_256910 | Duhaney - 310 | Jul 31, 2026 9:37pm | Jul 31, 2026 10:57pm | Aug 1, 2026 1:08am | Aug 1, 2026 1:08am | Aug 1, 2026 1:08am | Aug 1, 2026 2:00am | Aug 1, 2026 2:01am | Aug 1, 2026 2:01am |  |  | Fair | No | Replaced 3A transformer fuse
Non-Outage | J.E.26.07.40163 | C001871392 | Hartley Chin | null | Completed | null | null | Jul 31, 2026 9:20pm | Aug 1, 2026 7:21am | Aug 1, 2026 1:39pm | Aug 1, 2026 2:04pm | Aug 1, 2026 2:04pm | Aug 1, 2026 2:04pm | Aug 1, 2026 2:06pm | Aug 1, 2026 2:06pm | BrokenWire |  | Fair | No | Call related to job # 39377
Outage | J.E.26.07.40120 | C001871393 | Hartley Chin | Clarendon | Completed | Load_251474 | Parnassus - 210 | Jul 31, 2026 9:20pm | Aug 1, 2026 7:20am | Aug 1, 2026 9:21am | Aug 1, 2026 12:17pm | Aug 1, 2026 12:53pm | Aug 1, 2026 1:02pm | Aug 1, 2026 1:05pm | Aug 1, 2026 1:05pm |  |  | Fair | No | Premisis found ok. Voltage readings v113-v115
Non-Outage | J.E.26.07.40149 | C001871391 | Tajay Bernard | St.James | Completed | Load_575056 | Bogue - 510 | Jul 31, 2026 9:16pm | Aug 1, 2026 10:28am | Aug 1, 2026 3:44pm | Aug 1, 2026 3:44pm | Aug 1, 2026 3:44pm | Aug 1, 2026 3:44pm | Aug 1, 2026 3:45pm | Aug 1, 2026 3:45pm |  |  | Fair | No | Customer stated that the issue has been resolved
Non-Outage | J.E.26.07.39915 | C001871390 | Omar King | null | Completed | null | null | Jul 31, 2026 9:08pm | Jul 31, 2026 11:40pm | Aug 1, 2026 12:43am | Aug 1, 2026 12:43am | Aug 1, 2026 3:06am | Aug 1, 2026 3:06am | Aug 1, 2026 3:06am | Aug 1, 2026 3:06am |  |  | Fair | No | Unable to find customer call several times no answer directions not sufficient
Outage | J.E.26.07.40158 | C001871389 | Antony Levy | KSAN | Completed | Load_265225 | Constant Spring - 210 | Jul 31, 2026 8:59pm | Jul 31, 2026 9:01pm | Jul 31, 2026 9:06pm | Jul 31, 2026 9:06pm | Jul 31, 2026 10:14pm | Jul 31, 2026 10:15pm | Jul 31, 2026 10:17pm | Jul 31, 2026 10:17pm | Fire |  | Fair | No | Cx stated power only 1 leg of power in home........... 1 phase burned on twisted 3 plex found ... burnt leg spliced using clamp ... power restored
Outage | J.E.26.07.40145 | C001871383 | Rusean Allen | KSAS | Completed | Load_258805 | Greenwich - 510 | Jul 31, 2026 8:38pm | Jul 31, 2026 8:42pm | Aug 1, 2026 10:05am | Aug 1, 2026 10:26am | Aug 1, 2026 10:32am | Aug 1, 2026 10:34am | Aug 1, 2026 10:35am | Aug 1, 2026 10:35am | Fire |  | Fair | No | Premises locked
Outage | J.E.26.07.39928 | C001871381 | Clyde Brown | Clarendon | Completed | Load_238532 | May Pen - 110 | Jul 31, 2026 8:37pm | Jul 31, 2026 8:37pm | Jul 31, 2026 8:57pm | Jul 31, 2026 8:57pm | Jul 31, 2026 9:41pm | Jul 31, 2026 10:56pm | Jul 31, 2026 11:01pm | Jul 31, 2026 11:01pm |  |  | Fair | No | 25kva transformer phase lead burnt off at connection to secondary line ,open transformer and repair burnt off lead to secondary line ,voltage left 114/114 and 228V,
Outage | J.E.26.07.40144 | C001871380 | Cliton Henry | St.Mary | Completed | Load_238956 | Highgate - 210 | Jul 31, 2026 8:36pm | Aug 1, 2026 7:17am | Aug 1, 2026 7:43am | Aug 1, 2026 7:43am | Aug 1, 2026 8:52am | Aug 1, 2026 8:54am | Aug 1, 2026 9:44am | Aug 1, 2026 9:44am |  |  | Fair | No | The customer stated that the supply was restored.
Outage | J.E.26.07.40052 | C001871377 | Delano Gayle | St.Catherine | Completed | Load_261379 | Tredegar - 510 | Jul 31, 2026 8:27pm | Jul 31, 2026 10:31pm | Jul 31, 2026 11:17pm | Jul 31, 2026 11:17pm | Jul 31, 2026 11:49pm | Jul 31, 2026 11:58pm | Jul 31, 2026 11:58pm | Jul 31, 2026 11:58pm |  |  | Fair | No | Trip 10kva transformer no pole#, patrolled line section and found okay, reset transformer
Outage | J.E.26.07.40067 | C001871372 | Delano Gayle | St.Catherine | Completed | Load_260421 | Tredegar - 310 | Jul 31, 2026 8:00pm | Jul 31, 2026 10:31pm | Aug 1, 2026 12:04am | Aug 1, 2026 12:04am | Aug 1, 2026 12:32am | Aug 1, 2026 12:51am | Aug 1, 2026 12:51am | Aug 1, 2026 12:51am | BrokenPole |  | Fair | No | Premises not found no answer from customer phone
Non-Outage | J.E.26.07.40073 | C001871368 | Evan Spaulding | null | Completed | null | null | Jul 31, 2026 7:46pm | Jul 31, 2026 7:58pm | Jul 31, 2026 8:35pm | Jul 31, 2026 8:35pm | Jul 31, 2026 9:09pm | Jul 31, 2026 10:20pm | Jul 31, 2026 10:22pm | Jul 31, 2026 10:22pm | Fire |  | Fair | No | Use 2-1 bolt clamps on Transformer neutral,voltage left 116v,117v,233v.
Outage | J.E.26.07.40055 | C001871366 | Cliton Henry | St.Mary | Completed | Load_254695 | Annotto Bay - 310 | Jul 31, 2026 7:46pm | Aug 1, 2026 7:17am | Aug 1, 2026 9:44am | Aug 1, 2026 9:44am | Aug 1, 2026 9:54am | Aug 1, 2026 10:30am | Aug 1, 2026 10:31am | Aug 1, 2026 10:31am |  |  | Fair | No | A blown 2 amp fuse found for a 25 kva transformer due illegal connection. The illegal connection was removed. Supply restored using 1-2 amp fuse.
Outage | J.E.26.07.40090 | C001871367 | Raymond Carr | St.Mary | Completed | Load_239762 | Oracabessa - 210 | Jul 31, 2026 7:46pm | Jul 31, 2026 7:54pm | Jul 31, 2026 8:13pm | Jul 31, 2026 8:13pm | Jul 31, 2026 8:43pm | Jul 31, 2026 8:50pm | Jul 31, 2026 8:58pm | Jul 31, 2026 8:58pm |  |  | Fair | No | Blown 10 kva transformer fuse found, line patrol and found okay. A 2 amp fuse was used to renew supply was restored.
Outage | J.E.26.07.39913 | C001871365 | Swon Miller | St.James | Completed | Load_241873 | Queens Drive - 710 | Jul 31, 2026 7:41pm | Jul 31, 2026 7:42pm | Jul 31, 2026 8:04pm | Jul 31, 2026 8:05pm | Jul 31, 2026 9:05pm | Jul 28, 2026 9:20am | Jul 31, 2026 9:21pm | Jul 31, 2026 9:21pm | BrokenWire |  | Fair | No | Found customer service wire down cause by truck voltage found 0.000 needs about 80ft#6 triplex to carry out repairs voltage left 0.000
Outage | J.E.26.07.40044 | C001871363 | Omar King | St.Ann | Completed | Load_318637 | Roaring River - 410 | Jul 31, 2026 7:34pm | Jul 31, 2026 7:35pm | Jul 31, 2026 10:16pm | Jul 31, 2026 10:16pm | Jul 31, 2026 11:43pm | Aug 1, 2026 12:42am | Aug 1, 2026 12:42am | Aug 1, 2026 12:42am |  |  | Fair | No | Found a 25 KVA transformer defective please refer
Outage | J.E.26.07.40040 | C001871354 | Rusean Allen | KSAS | Completed | Load_257291 | Rockfort - 210 | Jul 31, 2026 7:10pm | Jul 31, 2026 7:12pm | Jul 31, 2026 8:16pm | Jul 31, 2026 8:16pm | Jul 31, 2026 9:48pm | Jul 31, 2026 10:43pm | Jul 31, 2026 10:43pm | Jul 31, 2026 10:43pm | BrokenWire |  | Fair | No | Broken service wire found, wire was spliced retention and reconnected.
Outage | J.E.26.07.40057 | C001871355 | Andrew Powell | St.Elizabeth | Completed | Load_1002213 | Maggotty - 210 | Jul 31, 2026 7:10pm | Jul 31, 2026 7:17pm | Jul 31, 2026 8:14pm | Jul 31, 2026 8:14pm | Jul 31, 2026 9:12pm | Jul 31, 2026 9:43pm | Jul 31, 2026 9:45pm | Jul 31, 2026 9:45pm |  |  | Fair | No | Patrol and found clear, replace one blown 10 amp junction fuse, two 5 amp fuse protect bank of three 50 kva transformer circuit, no pole number by switch location, restore supply okay.
Outage | J.E.26.07.39993 | C001871353 | Milton Charlton | KSAN | Completed | Load_238530 | Hope - 410 | Jul 31, 2026 7:09pm | Jul 31, 2026 7:09pm | Jul 31, 2026 7:22pm | Jul 31, 2026 7:22pm | Jul 31, 2026 8:52pm | Jul 31, 2026 8:50pm | Jul 31, 2026 8:57pm | Jul 31, 2026 8:57pm | Fire |  | Fair | No | Customer service wire #6 triplex crystalize and caught fire. Charge service wire using 50ft #6 triplex and six 1- bolt clamps. Readings at meter socket 113-114-227 volts.
Outage | J.E.26.07.40022 | C001871349 | Romeo Brissett | St.James | Completed | Load_239941 | Bogue - 610 | Jul 31, 2026 6:58pm | Jul 31, 2026 6:59pm | Jul 31, 2026 7:36pm | Jul 31, 2026 7:36pm | Jul 31, 2026 8:11pm | Jul 31, 2026 9:30pm | Jul 31, 2026 9:34pm | Jul 31, 2026 9:34pm | Fire |  | Fair | No | Isolated (1)25KVA transformer, removed illegal connections, spliced and retention 2 span of secondary. V/R 110+111-221.
Outage | J.E.26.07.40028 | C001871351 | Shamour Haughton | St.James | Completed | Load_302141 | Bogue - 510 | Jul 31, 2026 6:58pm | Aug 1, 2026 7:26am | Aug 1, 2026 8:41am | Aug 1, 2026 8:41am | Aug 1, 2026 10:19am | Aug 1, 2026 10:35am | Aug 1, 2026 10:41am | Aug 1, 2026 10:41am |  |  | Fair | No | Found customer experiencing internal issue, voltage left 112,113,226
Outage | J.E.26.07.39951 | C001871343 | Javid Vernon | Westmoreland | Completed | Load_238966 | Paradise - 210 | Jul 31, 2026 6:47pm | Jul 31, 2026 7:24pm | Jul 31, 2026 7:51pm | Jul 31, 2026 7:51pm | Jul 31, 2026 8:37pm | Jul 31, 2026 9:19pm | Jul 31, 2026 9:23pm | Jul 31, 2026 9:23pm |  |  | Fair | No | Reattach secondary phase to d-iron spool and reset one 10kva transformer
Outage | J.E.26.07.39986 | C001871339 | Damion Reid | Manchester | Completed | Load_263063 | Kendal - 210 | Jul 31, 2026 6:31pm | Jul 31, 2026 6:33pm | Jul 31, 2026 7:03pm | Jul 31, 2026 7:03pm | Jul 31, 2026 8:23pm | Jul 31, 2026 8:30pm | Jul 31, 2026 8:33pm | Jul 31, 2026 8:33pm |  |  | Fair | No | Premises found ok voltage at meter socket phase to neutral 114v-115v across phase 231v
Outage | J.E.26.07.39979 | C001871338 | Evan Spaulding | St.Mary | Completed | Load_238956 | Highgate - 210 | Jul 31, 2026 6:28pm | Jul 31, 2026 6:29pm | Jul 31, 2026 7:50pm | Jul 31, 2026 7:50pm | Jul 31, 2026 8:25pm | Jul 31, 2026 8:33pm | Jul 31, 2026 8:34pm | Jul 31, 2026 8:34pm |  |  | Fair | No | Reset 25kva Transformer at pole number 0010783.
Outage | J.E.26.07.39918 | C001871331 | Hopeton Henry | St.Thomas | Completed | Load_240667 | Good Year - 110 | Jul 31, 2026 6:17pm | Aug 1, 2026 7:47am | Aug 1, 2026 9:02am | Aug 1, 2026 12:10pm | Aug 1, 2026 12:11pm | Aug 1, 2026 12:13pm | Aug 1, 2026 12:14pm | Aug 1, 2026 12:14pm |  |  | Fair | No | Found ok ,issue resolved yesterday
Outage | J.E.26.07.39961 | C001871328 | Rusean Allen | KSAS | Completed | Load_243254 | Cane River - 610 | Jul 31, 2026 6:13pm | Jul 31, 2026 6:27pm | Jul 31, 2026 10:46pm | Jul 31, 2026 10:46pm | Jul 31, 2026 10:46pm | Jul 31, 2026 10:46pm | Jul 31, 2026 10:46pm | Jul 31, 2026 10:46pm | BrokenWire |  | Fair | No | Premises okay
Outage | J.E.26.07.39962 | C001871329 | Rusean Allen | KSAS | Completed | Load_258423 | Three Miles - 410 | Jul 31, 2026 6:13pm | Jul 31, 2026 6:27pm | Jul 31, 2026 9:26pm | Jul 31, 2026 10:43pm | Jul 31, 2026 10:43pm | Jul 31, 2026 10:45pm | Jul 31, 2026 10:46pm | Jul 31, 2026 10:46pm | Fire |  | Fair | No | Burnt meter and burnt meter socket found, wire was disconnected at pole.Customer was advised to contact electrician.
Non-Outage | J.E.26.07.38720 | C001871316 | Romeo Brissett | St.James | Completed | Load_569956 | Bogue - 410 | Jul 31, 2026 5:52pm | Jul 31, 2026 5:52pm | Jul 31, 2026 5:57pm | Jul 31, 2026 5:57pm | Jul 31, 2026 6:19pm | Jul 31, 2026 6:52pm | Jul 31, 2026 6:55pm | Jul 31, 2026 6:55pm |  |  | Fair | No | Replaced (1)50kva transformer kva,
Outage | J.E.26.07.39459 | C001871320 | Horace Malcolm | St.James | Completed | Load_557020 | Bogue - 310 | Jul 31, 2026 5:52pm | Aug 1, 2026 7:26am | Aug 1, 2026 9:08am | Aug 1, 2026 9:08am | Aug 1, 2026 9:08am | Aug 1, 2026 9:10am | Aug 1, 2026 9:10am | Aug 1, 2026 9:10am | BrokenWire |  | Fair | No | Check and found ok related to previous call job number 39459 voltage 114-116-230
Outage | J.E.26.07.39726 | C001871319 | Romeo Brissett | St.James | Completed | Load_575159 | Bogue - 310 | Jul 31, 2026 5:52pm | Jul 31, 2026 5:52pm | Jul 31, 2026 9:37pm | Jul 31, 2026 9:37pm | Jul 31, 2026 10:59pm | Jul 31, 2026 11:13pm | Jul 31, 2026 11:14pm | Jul 31, 2026 11:14pm |  |  | Fair | No | Check and found HX box no power coming from box to service wire, please send to field service.
Outage | J.E.26.07.39896 | C001871318 | Horace Malcolm | St.James | Completed | Load_259029 | Bogue - 310 | Jul 31, 2026 5:52pm | Aug 1, 2026 7:26am | Aug 1, 2026 9:11am | Aug 1, 2026 9:11am | Aug 1, 2026 9:11am | Aug 1, 2026 9:15am | Aug 1, 2026 9:15am | Aug 1, 2026 9:15am |  |  | Fair | No | Check and found ok supply restored
Outage | J.E.26.07.39943 | C001871317 | Raymond Lewis | St.Ann | Completed | Load_246878 | Cardiff Hall - 310 | Jul 31, 2026 5:52pm | Jul 31, 2026 5:52pm | Jul 31, 2026 8:20pm | Jul 31, 2026 8:20pm | Jul 31, 2026 10:48pm | Jul 31, 2026 11:38pm | Jul 31, 2026 11:39pm | Jul 31, 2026 11:39pm |  |  | Fair | No | Remove primary jumper from pole refuse and close 15 A junction fuse
Non-Outage | J.E.26.07.39303 | C001871315 | Shamour Haughton | St.James | Completed | Load_245672 | Bogue - 510 | Jul 31, 2026 5:51pm | Aug 1, 2026 7:26am | Aug 1, 2026 10:41am | Aug 1, 2026 10:41am | Aug 1, 2026 10:41am | Aug 1, 2026 10:41am | Aug 1, 2026 10:52am | Aug 1, 2026 10:52am |  |  | Fair | No | Check and found okay, customer state that power was restored
Non-Outage | J.E.26.07.39630 | C001871313 | Romeo Brissett | St.James | Completed | Load_242717 | Bogue - 310 | Jul 31, 2026 5:51pm | Jul 31, 2026 5:52pm | Jul 31, 2026 6:55pm | Jul 31, 2026 6:55pm | Jul 31, 2026 7:34pm | Jul 31, 2026 7:30pm | Jul 31, 2026 7:35pm | Jul 31, 2026 7:35pm |  |  | Fair | No | Premises was checked and customer stated issue was resolved
Non-Outage | J.E.26.07.39751 | C001871314 | Romeo Brissett | St.James | Completed | Load_239941 | Bogue - 610 | Jul 31, 2026 5:51pm | Jul 31, 2026 5:52pm | Jul 31, 2026 9:35pm | Jul 31, 2026 9:35pm | Jul 31, 2026 9:35pm | Jul 31, 2026 9:34pm | Jul 31, 2026 9:36pm | Jul 31, 2026 9:36pm |  |  | Fair | No | Check and found ok
Outage | J.E.26.07.39905 | C001871310 | Antony Levy | KSAN | Completed | Load_254418 | Constant Spring - 310 | Jul 31, 2026 5:42pm | Jul 31, 2026 5:43pm | Jul 31, 2026 10:21pm | Jul 31, 2026 10:21pm | Jul 31, 2026 10:21pm | Jul 31, 2026 10:21pm | Jul 31, 2026 10:21pm | Jul 31, 2026 10:21pm |  |  | Fair | No
Outage | J.E.26.07.39881 | C001871308 | Antony Levy | KSAN | Completed | Load_574750 | Constant Spring - 410 | Jul 31, 2026 5:41pm | Jul 31, 2026 5:44pm | Jul 31, 2026 7:31pm | Jul 31, 2026 7:31pm | Jul 31, 2026 8:42pm | Jul 31, 2026 9:01pm | Jul 31, 2026 9:02pm | Jul 31, 2026 9:02pm |  |  | EarthMovement | No | Premises found okay
Outage | J.E.26.07.39897 | C001871302 | Denton Williams | Portland | Completed | Load_265583 | Port Antonio - 410 | Jul 31, 2026 5:29pm | Jul 31, 2026 5:29pm | Jul 31, 2026 6:03pm | Jul 31, 2026 6:03pm | Jul 31, 2026 6:13pm | Jul 31, 2026 6:54pm | Jul 31, 2026 6:55pm | Jul 31, 2026 6:55pm |  |  | Fair | No | Site found ok, 118118/236 volts
Outage | J.E.26.07.39909 | C001871301 | Clyde Brown | Clarendon | Completed | Load_239018 | May Pen - 110 | Jul 31, 2026 5:29pm | Jul 31, 2026 5:30pm | Jul 31, 2026 7:10pm | Aug 1, 2026 10:23am | Aug 1, 2026 11:55am | Aug 1, 2026 2:28pm | Aug 1, 2026 2:38pm | Aug 1, 2026 2:38pm | BrokenWire | Y | Fair | No | Broken 3-span secondary phase and 2 span secondary neutral,open 25kva transformer and repaired with 10ft-#2/0 conductor,6ft-#2 conductor,3- preform 4splicing sleeve and 3- one bolt clamp.
Outage | J.E.26.07.39916 | C001871304 | Neville Spencer | Clarendon | Completed | Load_261428 | May Pen - 210 | Jul 31, 2026 5:29pm | Jul 31, 2026 5:31pm | Jul 31, 2026 7:17pm | Jul 31, 2026 7:17pm | Jul 31, 2026 11:57pm | Jul 31, 2026 11:57pm | Jul 31, 2026 11:58pm | Jul 31, 2026 11:58pm |  |  | Fair | No | Call resolved this morning.
Outage | J.E.26.07.39863 | C001871298 | Omar King | St.Ann | Completed | Load_259047 | Upper White River - 110 | Jul 31, 2026 5:27pm | Jul 31, 2026 5:27pm | Jul 31, 2026 8:18pm | Jul 31, 2026 10:15pm | Jul 31, 2026 10:15pm | Jul 31, 2026 10:16pm | Jul 31, 2026 10:16pm | Jul 31, 2026 10:16pm |  |  | Fair | No | Found a15 amp junction fuse blow cause by vegetation fuse as been replaced area is now with supply
Outage | J.E.26.07.39879 | C001871299 | Omar King | St.Ann | Completed | Load_351915 | Upper White River - 110 | Jul 31, 2026 5:27pm | Jul 31, 2026 5:27pm | Jul 31, 2026 8:18pm | Jul 31, 2026 8:18pm | Jul 31, 2026 9:34pm | Jul 31, 2026 10:15pm | Jul 31, 2026 10:15pm | Jul 31, 2026 10:15pm |  |  | Fair | No | Found a15 amp junction fuse blow cause by vegetation fuse as been replaced area is now with supply
Outage | J.E.26.07.39858 | C001871297 | Raymond Carr | St.Mary | Completed | Load_239762 | Oracabessa - 210 | Jul 31, 2026 5:23pm | Jul 31, 2026 5:23pm | Jul 31, 2026 5:31pm | Jul 31, 2026 5:31pm | Jul 31, 2026 6:43pm | Jul 31, 2026 6:28pm | Jul 31, 2026 6:44pm | Jul 31, 2026 6:44pm |  |  | Fair | No | Several calls to contact number went straight to voicemail.
Outage | J.E.26.07.39899 | C001871296 | Andrew Powell | St.Elizabeth | Completed | Load_267466 | Maggotty - 210 | Jul 31, 2026 5:23pm | Jul 31, 2026 5:23pm | Jul 31, 2026 5:43pm | Jul 31, 2026 5:44pm | Jul 31, 2026 5:58pm | Jul 31, 2026 6:00pm | Jul 31, 2026 6:02pm | Jul 31, 2026 6:02pm |  |  | Fair | No | Customer reported sparks on insulator due night cause from contamination.
Outage | J.E.26.07.39335 | C001871284 | Hartley Chin | Clarendon | Completed | Load_239043 | Parnassus - 310 | Jul 31, 2026 4:51pm | Aug 1, 2026 7:20am | Aug 1, 2026 8:12am | Aug 1, 2026 10:06am | Aug 1, 2026 10:42am | Aug 1, 2026 10:57am | Aug 1, 2026 11:12am | Aug 1, 2026 11:12am | LeaningPole |  | Fair | No | Ref to maintenance !!! Found leaning 35ft T/pole with single phase primary and #2 secondary twisted .. pole foot is okay .. pole only needs to be straighten… Note : customer supply is okay …
Outage | J.E.26.07.39377 | C001871283 | Hartley Chin | Clarendon | Completed | Load_247306 | Monymusk - 410 | Jul 31, 2026 4:51pm | Aug 1, 2026 7:20am | Aug 1, 2026 1:06pm | Aug 1, 2026 1:06pm | Aug 1, 2026 1:39pm | Aug 1, 2026 1:58pm | Aug 1, 2026 2:03pm | Aug 1, 2026 2:03pm |  |  | Fair | No | Found blown 2 amp fuse for 15 KVA transformer at pole # 0210789. Line patrolled and found ok, Transformer refused.
Outage | J.E.26.07.39847 | C001871282 | Javid Vernon | Westmoreland | Completed | Load_246713 | Paradise - 110 | Jul 31, 2026 4:51pm | Jul 31, 2026 4:51pm | Jul 31, 2026 9:23pm | Jul 31, 2026 9:23pm | Jul 31, 2026 10:39pm | Jul 31, 2026 10:50pm | Jul 31, 2026 10:50pm | Jul 31, 2026 10:50pm |  |  | Fair | No | Premises check and found okay customer stated that the power was restored
Outage | J.E.26.07.39506 | C001871281 | Hartley Chin | Clarendon | Completed | Load_245510 | May Pen - 210 | Jul 31, 2026 4:50pm | Aug 1, 2026 7:20am | Aug 1, 2026 8:08am | Aug 1, 2026 8:08am | Aug 1, 2026 9:13am | Aug 1, 2026 9:19am | Aug 1, 2026 9:20am | Aug 1, 2026 9:20am |  |  | Fair | No | Found okay .., voltage read 111v , 113v .. customer has internal issue…
Outage | J.E.26.07.39551 | C001871279 | Clyde Brown | Clarendon | Completed | Load_255025 | May Pen - 110 | Jul 31, 2026 4:50pm | Jul 31, 2026 4:58pm | Jul 31, 2026 5:22pm | Jul 31, 2026 7:10pm | Jul 31, 2026 8:37pm | Jul 31, 2026 8:42pm | Jul 31, 2026 8:47pm | Jul 31, 2026 8:47pm |  |  | Fair | No | Broken secondary neutral caused by truck,open 25 kva transformer and repaired with 8ft-#2/0 conductor,2-splicing sleeve ,2- preform and 2- clamp.
Outage | J.E.26.07.39657 | C001871280 | Neville Spencer | Clarendon | Completed | Load_406102 | Parnassus - 210 | Jul 31, 2026 4:50pm | Jul 31, 2026 4:57pm | Jul 31, 2026 7:06pm | Jul 31, 2026 7:06pm | Jul 31, 2026 7:06pm | Jul 31, 2026 7:06pm | Jul 31, 2026 7:10pm | Jul 31, 2026 7:10pm |  |  | Fair | No | Cleared creeper from pole renew blown 10 amp j/ fuse at pole # 562875 supply restored.
Outage | J.E.26.07.39709 | C001871278 | Hartley Chin | Clarendon | Completed | Load_263678 | May Pen - 210 | Jul 31, 2026 4:50pm | Aug 1, 2026 7:20am | Aug 1, 2026 2:06pm | Aug 1, 2026 2:06pm | Aug 1, 2026 3:19pm | Aug 1, 2026 3:10pm | Aug 1, 2026 3:22pm | Aug 1, 2026 3:22pm |  |  | SevereWind | No | Found blown 7 amp fuse on 100KVA transformer @ pole # 0098891 line patrolled and found okay, transformer refused…
Outage | J.E.26.07.39771 | C001871277 | Clyde Brown | Clarendon | Completed | Load_238532 | May Pen - 110 | Jul 31, 2026 4:50pm | Jul 31, 2026 4:58pm | Jul 31, 2026 5:22pm | Jul 31, 2026 5:22pm | Jul 31, 2026 5:29pm | Jul 31, 2026 7:04pm | Jul 31, 2026 7:10pm | Jul 31, 2026 7:10pm |  |  | Fair | No | Broken secondary phase open 25 kva transformer and repaired with 5ft-#2/0 conductor,1- preform and 1- clamp.
Outage | J.E.26.07.39789 | C001871276 | Clyde Brown | Clarendon | Completed | Load_250685 | May Pen - 110 | Jul 31, 2026 4:50pm | Jul 31, 2026 4:58pm | Jul 31, 2026 5:22pm | Jul 31, 2026 11:01pm | Jul 31, 2026 11:01pm | Jul 31, 2026 8:42pm | Jul 31, 2026 11:04pm | Jul 31, 2026 11:04pm |  |  | Fair | No | Broken secondary neutral caused by truck,open 25 kva transformer and repaired with 6ft-#2 conductor,2-splicing sleeve,1- preform and 1- clamp.
Outage | J.E.26.07.39851 | C001871275 | Neville Spencer | Clarendon | Completed | Load_406102 | Parnassus - 210 | Jul 31, 2026 4:50pm | Jul 31, 2026 4:57pm | Jul 31, 2026 5:41pm | Jul 31, 2026 5:42pm | Jul 31, 2026 6:30pm | Jul 31, 2026 7:02pm | Jul 31, 2026 7:05pm | Jul 31, 2026 7:05pm |  |  | Fair | No | Cleared creeper from pole renew blown 10 amp j/ fuse at pole # 562875 area restored.
Outage | J.E.26.07.39834 | C001871270 | Milton Charlton | KSAN | Completed | Load_265054 | Washington Blvd - 710 | Jul 31, 2026 4:46pm | Jul 31, 2026 5:10pm | Jul 31, 2026 5:54pm | Jul 31, 2026 5:54pm | Jul 31, 2026 6:29pm | Jul 31, 2026 6:30pm | Jul 31, 2026 6:37pm | Jul 31, 2026 6:37pm | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | 35ft wooden pole#( no pole #) broken in motor vehicle accident by trailer L.C # CT6151 and pole resting on car L.C # 3412HQ. Pole has on open wire secondary D.E three way and telephone cables. Need crane truck to remove pole off car and cables off truck to clear road way because the road is blocked. Isolate 50kva transformer feeding open secondary.
Outage | J.E.26.07.38919 | C001871267 | Wan Carlos Scarlett | St.Catherine | Completed | Load_266244 | Rhodens Pen - 410 | Jul 31, 2026 4:31pm | Jul 31, 2026 4:33pm | Jul 31, 2026 4:43pm | Jul 31, 2026 4:43pm | Jul 31, 2026 6:42pm | Jul 31, 2026 7:55pm | Jul 31, 2026 7:56pm | Jul 31, 2026 7:56pm |  |  | Fair | No | Reset 50 KVA transformer no pole # was found nothing was found on secondary line power supply has been restored
Outage | J.E.26.07.39263 | C001871266 | Wan Carlos Scarlett | St.Catherine | Completed | Load_245267 | Rhodens Pen - 410 | Jul 31, 2026 4:31pm | Jul 31, 2026 4:32pm | Jul 31, 2026 6:35pm | Jul 31, 2026 7:56pm | Jul 31, 2026 7:56pm | Jul 31, 2026 7:57pm | Jul 31, 2026 7:57pm | Jul 31, 2026 7:57pm |  |  | Fair | No | Call related to reset transformer customer confirmed that power supply has been restored
Non-Outage | J.E.26.07.39294 | C001871265 | Donald Cunningham | null | Completed | null | null | Jul 31, 2026 4:30pm | Aug 1, 2026 8:09am | Aug 1, 2026 10:27am | Aug 1, 2026 10:27am | Aug 1, 2026 11:43am | Aug 1, 2026 11:43am | Aug 1, 2026 11:44am | Aug 1, 2026 11:44am |  |  | Fair | No | Premises closed
Outage | J.E.26.07.39351 | C001871264 | Donald Cunningham | St.Catherine | Completed | Load_240706 | Twickenham - 310 | Jul 31, 2026 4:30pm | Aug 1, 2026 4:33pm | Aug 1, 2026 5:02pm | Aug 1, 2026 5:02pm | Aug 1, 2026 6:04pm | Aug 1, 2026 6:05pm | Aug 1, 2026 6:05pm | Aug 1, 2026 6:05pm |  |  | Fair | No | Premises closed
Outage | J.E.26.07.39362 | C001871263 | Wan Carlos Scarlett | St.Catherine | Completed | Load_261866 | Tredegar - 510 | Jul 31, 2026 4:30pm | Jul 31, 2026 4:32pm | Jul 31, 2026 7:18pm | Jul 31, 2026 7:58pm | Jul 31, 2026 8:47pm | Jul 31, 2026 9:00pm | Jul 31, 2026 9:01pm | Jul 31, 2026 9:01pm |  |  | Fair | No | Reset customer breaker power supply has been restored
Outage | J.E.26.07.39737 | C001871261 | Delano Gayle | St.Catherine | Completed | Load_265271 | Tredegar - 310 | Jul 31, 2026 4:28pm | Jul 31, 2026 10:53pm | Aug 1, 2026 12:54am | Aug 1, 2026 12:54am | Aug 1, 2026 1:37am | Aug 1, 2026 1:47am | Aug 1, 2026 1:47am | Aug 1, 2026 1:47am |  |  | Fair | No | Premises not found no answer from customer phone, hexing system installed in area
Outage | J.E.26.07.39812 | C001871262 | Delano Gayle | St.Catherine | Completed | Load_238023 | Twickenham - 310 | Jul 31, 2026 4:28pm | Jul 31, 2026 10:53pm | Aug 1, 2026 2:44am | Aug 1, 2026 2:44am | Aug 1, 2026 4:22am | Aug 1, 2026 4:30am | Aug 1, 2026 4:30am | Aug 1, 2026 4:30am |  |  | Fair | No | Premises not found
Outage | J.E.26.07.39850 | C001871260 | Nickolas Rodriques | St.Catherine | Completed | Load_293144 | Twickenham - 310 | Jul 31, 2026 4:28pm | Jul 31, 2026 5:13pm | Jul 31, 2026 8:34pm | Jul 31, 2026 8:34pm | Jul 31, 2026 9:15pm | Jul 31, 2026 9:30pm | Jul 31, 2026 9:49pm | Jul 31, 2026 9:49pm | BrokenPole |  | Fair | No | Checked and found a 30 ft wooden pole broken and resting on a truck located in a garage. The pole consists of only customer service wire which was isolated for safety. Only one customer and a streetlight is affected by this. Refer to maintenance.
Non-Outage | J.E.26.07.39829 | C001871246 | Andrew Powell | null | Completed | null | null | Jul 31, 2026 4:13pm | Jul 31, 2026 6:09pm | Jul 31, 2026 6:28pm | Jul 31, 2026 6:28pm | Jul 31, 2026 7:07pm | Jul 31, 2026 7:58pm | Jul 31, 2026 8:02pm | Jul 31, 2026 8:02pm |  |  | Fair | No | Disconnect #6 triplex service wire from secondary line due to burnt up service entry wire repair work required at customer premises , no meter found at location. Retention two pole span of sagging secondary neutral conductor and replace burnt up fuse holder 3 amp fuse protect 25 kva transformer circuit by pole number 038222, restored supply okay.
Outage | J.E.26.07.39489 | C001871247 | Nickolas Rodriques | Portmore | Completed | Load_261381 | Naggo Head - 610 | Jul 31, 2026 4:13pm | Jul 31, 2026 4:23pm | Jul 31, 2026 5:17pm | Jul 31, 2026 5:40pm | Jul 31, 2026 6:14pm | Jul 31, 2026 7:04pm | Jul 31, 2026 7:13pm | Jul 31, 2026 7:13pm | LeaningPole |  | Fair | No | Checked and found old abandoned wooden pole rotten and leaning towards customer’s house. Pole consists of two guy wire and FLOW cables. Refer to maintenance.
Outage | J.E.26.07.39838 | C001871243 | Damion Reid | Manchester | Completed | Load_243942 | Kendal - 210 | Jul 31, 2026 4:11pm | Jul 31, 2026 4:11pm | Jul 31, 2026 8:37pm | Jul 31, 2026 8:37pm | Jul 31, 2026 9:02pm | Jul 31, 2026 11:27pm | Jul 31, 2026 11:29pm | Jul 31, 2026 11:29pm | BrokenWire |  | Fair | No | Two span of broken secondary phase conductor found cause by vehicle accident open 25kva transformer fuse link splice an retention conductor using 30ft of 2/0 aluminum conductor two 2/0 preform 3 one bolt clamp and restore power
Outage | J.E.26.07.39456 | C001871240 | Nickolas Rodriques | St.Catherine | Completed | Load_291212 | Twickenham - 210 | Jul 31, 2026 4:07pm | Jul 31, 2026 4:23pm | Jul 31, 2026 9:49pm | Jul 31, 2026 9:55pm | Jul 31, 2026 10:25pm | Jul 31, 2026 11:25pm | Jul 31, 2026 11:26pm | Jul 31, 2026 11:26pm |  |  | Fair | No | Customer is reporting a defective streetlight. Refer to streetlight department.
Outage | J.E.26.07.39808 | C001871241 | Omar King | St.Ann | Completed | Load_257505 | Ocho Rios - 310 | Jul 31, 2026 4:07pm | Jul 31, 2026 4:08pm | Jul 31, 2026 4:56pm | Jul 31, 2026 6:41pm | Jul 31, 2026 7:46pm | Jul 31, 2026 8:16pm | Jul 31, 2026 8:18pm | Jul 31, 2026 8:18pm |  |  | Fair | No | Found a 25 KVA transformer fuse blow cause by vegetation customer is now with supply
Non-Outage | J.E.26.07.39811 | C001871237 | Evan Spaulding | null | Completed | null | null | Jul 31, 2026 4:05pm | Jul 31, 2026 4:06pm | Jul 31, 2026 5:28pm | Jul 31, 2026 5:28pm | Jul 31, 2026 7:21pm | Jul 31, 2026 7:21pm | Jul 31, 2026 7:33pm | Jul 31, 2026 7:33pm |  |  | Fair | No | Bank of three Transformers (1-100 kva and 2-50kva) feeding the whole Town center,100 kva max out voltage A-N= 96v,B-N=100v,C-N=200v,A-B=119v,A-C=229v,B-C=220v,The operation department is a ware of the issue a 167kva Transformer was brought over from Kingston to replace the 100kva , but it is not yet put up.
Outage | J.E.26.07.39772 | C001871234 | Richman Whyte | Westmoreland | Completed | Load_268022 | Paradise - 310 | Jul 31, 2026 4:02pm | Aug 1, 2026 7:23am | Aug 1, 2026 10:48am | Aug 1, 2026 10:48am | Aug 1, 2026 10:48am | Aug 1, 2026 10:48am | Aug 1, 2026 10:49am | Aug 1, 2026 10:49am | BrokenWire |  | Fair | No | Premises demolished
Outage | J.E.26.07.39820 | C001871233 | Damion Reid | Manchester | Completed | Load_265405 | Kendal - 210 | Jul 31, 2026 4:01pm | Jul 31, 2026 4:04pm | Jul 31, 2026 4:26pm | Jul 31, 2026 4:26pm | Jul 31, 2026 5:54pm | Jul 31, 2026 7:01pm | Jul 31, 2026 7:02pm | Jul 31, 2026 7:02pm |  |  | Fair | No | Blown 15amp junction fuse and blown 3amp fuse found for 25kva transformer line patrol nothing was found blown fuse replace
Outage | J.E.26.07.39827 | C001871232 | Richard Nicholas | St.Catherine | Completed | Load_262168 | New Michelton - 210 | Jul 31, 2026 4:01pm | Jul 31, 2026 4:04pm | Jul 31, 2026 7:14pm | Jul 31, 2026 7:14pm | Jul 31, 2026 7:43pm | Jul 31, 2026 7:51pm | Jul 31, 2026 7:52pm | Jul 31, 2026 7:52pm |  |  | EarthMovement | No | Area found ok
Outage | J.E.26.07.39818 | C001871229 | Richard Nicholas | St.Catherine | Completed | Load_253596 | New Michelton - 210 | Jul 31, 2026 3:57pm | Jul 31, 2026 4:04pm | Jul 31, 2026 8:56pm | Jul 31, 2026 8:56pm | Jul 31, 2026 9:59pm | Jul 31, 2026 10:42pm | Jul 31, 2026 10:44pm | Jul 31, 2026 10:44pm |  |  | Fair | No | Supply found disconnected remotely at smart meter for nonpayment of bill.customer advised.
Outage | J.E.26.07.39821 | C001871228 | Richman Whyte | Westmoreland | Completed | Load_263342 | Paradise - 310 | Jul 31, 2026 3:56pm | Jul 31, 2026 8:25pm | Jul 31, 2026 8:38pm | Jul 31, 2026 8:38pm | Jul 31, 2026 8:39pm | Jul 31, 2026 8:39pm | Jul 31, 2026 8:40pm | Jul 31, 2026 8:40pm |  |  | Fair | No | Replace three amp twenty fifty kva transformer fuse
Outage | J.E.26.07.39612 | C001871224 | Richard Nicholas | St.Catherine | Completed | Load_250877 | New Michelton - 210 | Jul 31, 2026 3:53pm | Jul 31, 2026 3:55pm | Jul 31, 2026 7:53pm | Jul 31, 2026 7:53pm | Jul 31, 2026 7:58pm | Jul 31, 2026 7:58pm | Jul 31, 2026 7:59pm | Jul 31, 2026 7:59pm |  |  | Fair | No | Found ok
Outage | J.E.26.07.39601 | C001871223 | Richard Nicholas | St.Catherine | Completed | Load_267187 | New Michelton - 210 | Jul 31, 2026 3:51pm | Jul 31, 2026 3:55pm | Jul 31, 2026 8:22pm | Jul 31, 2026 8:22pm | Jul 31, 2026 8:22pm | Jul 31, 2026 8:22pm | Jul 31, 2026 8:23pm | Jul 31, 2026 8:23pm |  |  | Fair | No | Area found ok
Outage | J.E.26.07.39644 | C001871222 | Richard Nicholas | St.Catherine | Completed | Load_250324 | New Michelton - 210 | Jul 31, 2026 3:51pm | Jul 31, 2026 3:55pm | Jul 31, 2026 8:16pm | Jul 31, 2026 8:16pm | Jul 31, 2026 8:21pm | Jul 31, 2026 8:21pm | Jul 31, 2026 8:22pm | Jul 31, 2026 8:22pm |  |  | Fair | No | Areafound ok
Outage | J.E.26.07.39646 | C001871221 | Richard Nicholas | St.Catherine | Completed | Load_255656 | New Michelton - 210 | Jul 31, 2026 3:51pm | Jul 31, 2026 3:55pm | Jul 31, 2026 8:23pm | Jul 31, 2026 8:23pm | Jul 31, 2026 8:23pm | Jul 31, 2026 8:23pm | Jul 31, 2026 8:23pm | Jul 31, 2026 8:23pm |  |  | Fair | No | Area found ok
Outage | J.E.26.07.39649 | C001871220 | Richard Nicholas | St.Catherine | Completed | Load_413079 | New Michelton - 210 | Jul 31, 2026 3:51pm | Jul 31, 2026 3:55pm | Jul 31, 2026 8:25pm | Jul 31, 2026 8:25pm | Jul 31, 2026 8:45pm | Jul 31, 2026 1:00am | Jul 31, 2026 8:56pm | Jul 31, 2026 8:56pm |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.07.39782 | C001871216 | Andrew Powell | null | Completed | null | null | Jul 31, 2026 3:50pm | Aug 1, 2026 7:31am | Aug 1, 2026 7:37am | Aug 1, 2026 7:46am | Aug 1, 2026 7:46am | Aug 1, 2026 7:46am | Aug 1, 2026 7:47am | Aug 1, 2026 7:47am |  |  | Fair | No | Premises not located inadequately direction contact customer by telephone unsuccessful.
Outage | J.E.26.07.39653 | C001871218 | Richard Nicholas | St.Catherine | Completed | Load_302041 | New Michelton - 210 | Jul 31, 2026 3:50pm | Jul 31, 2026 3:55pm | Jul 31, 2026 8:24pm | Jul 31, 2026 8:24pm | Jul 31, 2026 8:24pm | Jul 31, 2026 8:24pm | Jul 31, 2026 8:24pm | Jul 31, 2026 8:24pm |  |  | Fair | No | Area found ok
Outage | J.E.26.07.39746 | C001871219 | Richard Nicholas | St.Catherine | Completed | Load_240447 | New Michelton - 210 | Jul 31, 2026 3:50pm | Jul 31, 2026 3:55pm | Jul 31, 2026 4:31pm | Jul 31, 2026 4:31pm | Jul 31, 2026 6:16pm | Jul 31, 2026 7:12pm | Jul 31, 2026 7:13pm | Jul 31, 2026 7:13pm |  |  | Fair | No | Replaced blown 65amp junctions fuse on pole #0060371 and blown 65amp junctions fuse on pole #0130719.
Outage | J.E.26.07.39793 | C001871215 | Andrew Powell | St.Elizabeth | Completed | Load_292082 | Maggotty - 210 | Jul 31, 2026 3:50pm | Aug 1, 2026 11:21am | Aug 1, 2026 12:17pm | Aug 1, 2026 12:17pm | Aug 1, 2026 1:28pm | Aug 1, 2026 2:48pm | Aug 1, 2026 2:50pm | Aug 1, 2026 2:50pm |  |  | Fair | No | Replace defective service wire using 100 feet #6 triplex, three clamps and three service sleeves, voltage reading 109v-109v phase to neutral 218v cross phase, meter #2606328.
Outage | J.E.26.07.39798 | C001871217 | Richard Nicholas | St.Catherine | Completed | Load_241509 | New Michelton - 210 | Jul 31, 2026 3:50pm | Jul 31, 2026 3:55pm | Jul 31, 2026 8:24pm | Jul 31, 2026 8:24pm | Jul 31, 2026 8:25pm | Jul 31, 2026 8:25pm | Jul 31, 2026 8:25pm | Jul 31, 2026 8:25pm |  |  | Fair | No | Area found ok
Outage | J.E.26.07.39800 | C001871214 | Richard Nicholas | St.Catherine | Completed | Load_242473 | New Michelton - 410 | Jul 31, 2026 3:50pm | Jul 31, 2026 3:55pm | Jul 31, 2026 7:59pm | Jul 31, 2026 7:59pm | Jul 31, 2026 8:14pm | Jul 31, 2026 8:15pm | Jul 31, 2026 8:16pm | Jul 31, 2026 8:16pm |  |  | Fair | No | This call is for the st.mary crew and not st.catherine.
Non-Outage | J.E.26.07.39337 | C001871212 | Denton Williams | Portland | Completed | Load_412887 | Port Antonio - 410 | Jul 31, 2026 3:48pm | Jul 31, 2026 3:48pm | Jul 31, 2026 4:14pm | Jul 31, 2026 4:14pm | Jul 31, 2026 4:33pm | Jul 31, 2026 4:33pm | Jul 31, 2026 4:35pm | Jul 31, 2026 4:35pm |  |  | Fair | No | Pad mounted transformer need to top up. Low voltage. Refer to Dwayne Peart
Non-Outage | J.E.26.07.38506 | C001871203 | Andrew Powell | St.Elizabeth | Completed | Load_253891 | Maggotty - 210 | Jul 31, 2026 3:43pm | Jul 31, 2026 3:44pm | Jul 31, 2026 3:54pm | Jul 31, 2026 3:54pm | Jul 31, 2026 5:09pm | Jul 31, 2026 5:37pm | Jul 31, 2026 5:39pm | Jul 31, 2026 5:39pm | Fire |  | Fair | No | Splice and tension two broken service wire at secondary line using 10 feet #6 triplex and three clamps, voltage reading 110v-112v phase to neutral 222v cross phase.
Outage | J.E.26.07.39723 | C001871200 | Ryan Richards | Manchester | Completed | Load_258254 | Spur Tree - 310 | Jul 31, 2026 3:42pm | Jul 31, 2026 3:42pm | Jul 31, 2026 8:52pm | Jul 31, 2026 8:52pm | Jul 31, 2026 9:30pm | Aug 1, 2026 12:00am | Aug 1, 2026 12:01am | Aug 1, 2026 12:01am |  |  | Fair | No | Premises found lock multiple efforts made to contact customer but unsuccessful
Outage | J.E.26.07.39784 | C001871202 | Ryan Richards | Manchester | Completed | Load_268244 | Kendal - 310 | Jul 31, 2026 3:42pm | Jul 31, 2026 3:42pm | Jul 31, 2026 7:06pm | Jul 31, 2026 7:06pm | Jul 31, 2026 8:00pm | Jul 31, 2026 8:45pm | Jul 31, 2026 8:45pm | Jul 31, 2026 8:45pm |  |  | Fair | No | Corroded phase and neutral found at pothead remade pothead using 3 penunion Voltage 110/115/225 volts
Outage | J.E.26.07.39715 | C001871197 | Milton Charlton | KSAS | Completed | Load_247564 | Up Park Camp - 410 | Jul 31, 2026 3:38pm | Jul 31, 2026 3:53pm | Jul 31, 2026 6:38pm | Jul 31, 2026 6:38pm | Jul 31, 2026 7:17pm | Jul 31, 2026 7:25pm | Jul 31, 2026 7:22pm | Jul 31, 2026 7:22pm |  |  | Fair | No | Reconnect customer meter #2374410 that was disconnected reconnect done by J.P.S.Escalation.
Outage | J.E.26.07.39788 | C001871196 | Antony Levy | KSAN | Completed | Load_257522 | Constant Spring - 210 | Jul 31, 2026 3:38pm | Jul 31, 2026 3:52pm | Jul 31, 2026 9:02pm | Jul 31, 2026 9:02pm | Jul 31, 2026 9:04pm | Jul 31, 2026 9:05pm | Jul 31, 2026 9:05pm | Jul 31, 2026 9:05pm |  |  | Fair | No | Premises found okay with power cx called confirm has power
Non-Outage | J.E.26.07.38614 | C001871192 | Swon Miller | St.James | Completed | Load_268070 | Bogue - 510 | Jul 31, 2026 3:29pm | Jul 31, 2026 3:30pm | Jul 31, 2026 3:36pm | Jul 31, 2026 5:03pm | Jul 31, 2026 5:40pm | Jul 29, 2026 6:49pm | Jul 31, 2026 6:55pm | Jul 31, 2026 6:55pm |  |  | Fair | No | Found customers service wires burnt off due to illegal connections voltage found 0.000 remove illegal connections from service wire and use about 35ft#6 triplex to carry out repairs voltage left 114/115/231
Non-Outage | J.E.26.07.38814 | C001871190 | Swon Miller | St.James | Completed | Load_250754 | Queens Drive - 310 | Jul 31, 2026 3:29pm | Jul 31, 2026 3:30pm | Jul 31, 2026 3:36pm | Jul 31, 2026 4:13pm | Jul 31, 2026 4:31pm | Jul 20, 2026 5:01am | Jul 31, 2026 5:01pm | Jul 31, 2026 5:01pm |  |  | Fair | No | Found customer meter pole defective voltage found 109/111/221 voltage left 109/111 221 advise customer to get meter pole replace
Non-Outage | J.E.26.07.39273 | C001871189 | Swon Miller | St.James | Completed | Load_247261 | Bogue - 310 | Jul 31, 2026 3:29pm | Jul 31, 2026 3:30pm | Jul 31, 2026 3:35pm | Jul 31, 2026 9:21pm | Jul 31, 2026 10:26pm | Jul 28, 2026 10:49pm | Jul 31, 2026 10:54pm | Jul 31, 2026 10:54pm |  |  | Fair | No | Check and found okay customer states that problem has been rectified voltage found 116/115/232 voltage left 116/115/232
Non-Outage | J.E.26.07.39467 | C001871187 | Swon Miller | St.James | Completed | Load_267568 | Queens Drive - 710 | Jul 31, 2026 3:29pm | Jul 31, 2026 3:30pm | Jul 31, 2026 3:35pm | Jul 31, 2026 3:35pm | Jul 31, 2026 3:48pm | Jul 29, 2026 4:10am | Jul 31, 2026 4:12pm | Jul 31, 2026 4:12pm |  |  | Fair | No | Check and found okay voltage found 114/116/231 voltage left 114/116/231
Non-Outage | J.E.26.07.39541 | C001871188 | Swon Miller | St.James | Completed | Load_251737 | Queens Drive - 810 | Jul 31, 2026 3:29pm | Jul 31, 2026 3:30pm | Jul 31, 2026 3:35pm | Jul 31, 2026 6:56pm | Jul 31, 2026 7:24pm | Jul 31, 2026 7:48pm | Jul 31, 2026 8:02pm | Jul 31, 2026 8:02pm |  |  | Fair | No | Customer at the end of the circuit is experiencing low voltage voltage found line side 105/105/210 load side 101/102/202 this is an ongoing issue it was referred to field service
Outage | J.E.26.07.39740 | C001871186 | Raymond Carr | St.Mary | Completed | Load_247017 | Oracabessa - 110 | Jul 31, 2026 3:28pm | Jul 31, 2026 3:31pm | Jul 31, 2026 5:27pm | Jul 31, 2026 5:27pm | Jul 31, 2026 5:27pm | Jul 31, 2026 5:04pm | Jul 31, 2026 5:28pm | Jul 31, 2026 5:28pm |  |  | Fair | No | Related to defective transformer at Galina.
Outage | J.E.26.07.39720 | C001871184 | Denton Williams | Portland | Completed | Load_250952 | Port Antonio - 310 | Jul 31, 2026 3:27pm | Jul 31, 2026 3:28pm | Jul 31, 2026 6:57pm | Jul 31, 2026 6:57pm | Jul 31, 2026 6:57pm | Jul 31, 2026 6:57pm | Jul 31, 2026 6:59pm | Jul 31, 2026 6:59pm | BrokenWire |  | Fair | Yes | Customer states that power was already sorted out by a JPS crew
Outage | J.E.26.07.39747 | C001871185 | Denton Williams | Portland | Completed | Load_268759 | Port Antonio - 410 | Jul 31, 2026 3:27pm | Jul 31, 2026 3:28pm | Jul 31, 2026 4:54pm | Jul 31, 2026 4:54pm | Jul 31, 2026 5:09pm | Jul 31, 2026 5:57pm | Jul 31, 2026 6:03pm | Jul 31, 2026 6:03pm |  |  | Fair | No | Vehicle broke down customer service line. Use 100 feet of #6 wire and three clamps n three nipples. 114/115/230 volts
Outage | J.E.26.07.39719 | C001871183 | Tajay Bernard | Hanover | Completed | Load_262264 | Orange Bay - 210 | Jul 31, 2026 3:26pm | Jul 31, 2026 3:26pm | Jul 31, 2026 7:15pm | Jul 31, 2026 7:17pm | Jul 31, 2026 7:40pm | Jul 31, 2026 7:41pm | Jul 31, 2026 7:41pm | Jul 31, 2026 7:41pm |  |  | Fair | No | Area check and found okay unable to locate customer on premises multiple phone call to customer number went unanswered
Outage | J.E.26.07.39745 | C001871182 | Tajay Bernard | Hanover | Completed | Load_265709 | Orange Bay - 210 | Jul 31, 2026 3:26pm | Jul 31, 2026 3:26pm | Jul 31, 2026 6:46pm | Jul 31, 2026 6:47pm | Jul 31, 2026 6:54pm | Jul 31, 2026 7:13pm | Jul 31, 2026 7:15pm | Jul 31, 2026 7:15pm |  |  | Fair | No | Customer requesting reconnection for a ct meter, refer to field service. Customer stated that he’s without electricity for 11 months
Non-Outage | J.E.26.07.19144 | C001871181 | Tajay Bernard | St.James | Completed | Load_244774 | Orange Bay - 310 | Jul 31, 2026 3:25pm | Jul 31, 2026 3:25pm | Jul 31, 2026 6:40pm | Jul 31, 2026 6:41pm | Jul 31, 2026 6:41pm | Jul 31, 2026 6:43pm | Jul 31, 2026 6:43pm | Jul 31, 2026 6:43pm |  |  | Fair | No | Customer stated that the issue has resolved
Non-Outage | J.E.26.07.30162 | C001871180 | Tajay Bernard | St.James | Completed | Load_253839 | Orange Bay - 310 | Jul 31, 2026 3:25pm | Jul 31, 2026 3:25pm | Jul 31, 2026 7:41pm | Jul 31, 2026 7:41pm | Jul 31, 2026 9:51pm | Jul 31, 2026 10:09pm | Jul 31, 2026 10:09pm | Jul 31, 2026 10:09pm |  |  | Fair | No | Premises check and found customer has internal problems voltage reading 112/110/222
Non-Outage | J.E.26.07.37613 | C001871179 | Tajay Bernard | St.James | Completed | Load_258790 | Orange Bay - 310 | Jul 31, 2026 3:25pm | Jul 31, 2026 3:25pm | Jul 31, 2026 3:56pm | Jul 31, 2026 3:56pm | Jul 31, 2026 5:18pm | Jul 31, 2026 5:46pm | Jul 31, 2026 5:48pm | Jul 31, 2026 5:48pm |  |  | Fair | No | Clean and remake joints at customer pothead use 2 clampsVoltage before 115Voltage left 115/117/232
Non-Outage | J.E.26.07.37967 | C001871177 | Tajay Bernard | St.James | Completed | Load_244774 | Orange Bay - 310 | Jul 31, 2026 3:25pm | Jul 31, 2026 3:25pm | Jul 31, 2026 3:44pm | Jul 31, 2026 5:48pm | Jul 31, 2026 6:03pm | Jul 31, 2026 6:40pm | Jul 31, 2026 6:40pm | Jul 31, 2026 6:40pm |  |  | Fair | No | Premises check and found okay voltage found 113/113/226
Outage | J.E.26.07.38478 | C001871172 | Richard Watson | Manchester | Completed | Load_302835 | Spur Tree - 210 | Jul 31, 2026 3:24pm | Jul 31, 2026 3:24pm | Jul 31, 2026 3:48pm | Jul 31, 2026 3:48pm | Jul 31, 2026 4:08pm | Jul 31, 2026 4:20pm | Jul 31, 2026 4:21pm | Jul 31, 2026 4:21pm |  |  | Fair | No | Location was visited yesterday but however customer was not present at time of visit, customer was contacted by phone and told to get an electrician to effect repairs to pothead and conduit and call back for reconnection.
Non-Outage | J.E.26.07.38749 | C001871171 | Tajay Bernard | St.James | Completed | Load_252500 | Bogue - 510 | Jul 31, 2026 3:23pm | Aug 1, 2026 10:27am | Aug 1, 2026 10:51am | Aug 1, 2026 10:51am | Aug 1, 2026 12:33pm | Aug 1, 2026 12:54pm | Aug 1, 2026 12:56pm | Aug 1, 2026 12:56pm |  |  | Fair | No | Clean and remake jumpers at jps pole use 2 clamps Voltage found 112Voltage left 114/115/230
Non-Outage | J.E.26.07.38992 | C001871168 | Andrew Powell | null | Completed | null | null | Jul 31, 2026 3:20pm | Jul 31, 2026 3:22pm | Jul 31, 2026 8:04pm | Jul 31, 2026 8:04pm | Jul 31, 2026 8:04pm | Jul 31, 2026 8:04pm | Jul 31, 2026 8:04pm | Jul 31, 2026 8:04pm |  |  | Fair | No | Premises found okay customer stated that supply restored.
Outage | J.E.26.07.38726 | C001871170 | Andrew Powell | St.Elizabeth | Completed | Load_262261 | Maggotty - 210 | Jul 31, 2026 3:20pm | Jul 31, 2026 3:22pm | Jul 31, 2026 3:47pm | Jul 31, 2026 3:47pm | Jul 31, 2026 3:47pm | Jul 31, 2026 3:48pm | Jul 31, 2026 3:48pm | Jul 31, 2026 3:48pm |  |  | Fair | No | Premises found okay customer stated that fault resolved supply restored.
Outage | J.E.26.07.39232 | C001871169 | Andrew Powell | St.Elizabeth | Completed | Load_1002241 | Maggotty - 210 | Jul 31, 2026 3:20pm | Jul 31, 2026 3:22pm | Jul 31, 2026 3:38pm | Jul 31, 2026 3:38pm | Jul 31, 2026 3:38pm | Jul 31, 2026 3:39pm | Jul 31, 2026 3:40pm | Jul 31, 2026 3:40pm |  |  | Fair | No | Called related to burnt 25 kva transformer in Back Flagaman.
Outage | J.E.26.07.39340 | C001871165 | Andrew Powell | St.Elizabeth | Completed | Load_248429 | Maggotty - 210 | Jul 31, 2026 3:20pm | Jul 31, 2026 3:22pm | Jul 31, 2026 6:09pm | Jul 31, 2026 6:09pm | Jul 31, 2026 6:22pm | Jul 31, 2026 6:22pm | Jul 31, 2026 6:23pm | Jul 31, 2026 6:23pm |  |  | Fair | No | Premises found okay customer stated that supply restored.
Outage | J.E.26.07.39363 | C001871166 | Andrew Powell | St.Elizabeth | Completed | Load_250259 | Maggotty - 210 | Jul 31, 2026 3:20pm | Jul 31, 2026 3:22pm | Jul 31, 2026 9:45pm | Jul 31, 2026 9:45pm | Jul 31, 2026 10:51pm | Jul 31, 2026 10:55pm | Jul 31, 2026 10:56pm | Jul 31, 2026 10:56pm |  |  | Fair | Yes | Premises not located contact customer by telephone unsuccessful.
Outage | J.E.26.07.39404 | C001871167 | Andrew Powell | Manchester | Completed | Load_259417 | Spur Tree - 210 | Jul 31, 2026 3:20pm | Jul 31, 2026 3:22pm | Jul 31, 2026 3:35pm | Jul 31, 2026 3:35pm | Jul 31, 2026 3:35pm | Jul 31, 2026 3:35pm | Jul 31, 2026 3:36pm | Jul 31, 2026 3:36pm |  |  | Fair | No | Premises found okay customer stated that supply restored.
Outage | J.E.26.07.39602 | C001871164 | Andrew Powell | St.Elizabeth | Completed | Load_242009 | Maggotty - 210 | Jul 31, 2026 3:20pm | Jul 31, 2026 3:22pm | Jul 31, 2026 3:28pm | Jul 31, 2026 3:28pm | Jul 31, 2026 3:30pm | Jul 31, 2026 3:31pm | Jul 31, 2026 3:31pm | Jul 31, 2026 3:31pm |  |  | Fair | No | Called related to burnt 25 kva transformer in back Flagaman.
Outage | J.E.26.07.39663 | C001871163 | Andrew Powell | St.Elizabeth | Completed | Load_265170 | Maggotty - 210 | Jul 31, 2026 3:20pm | Aug 1, 2026 11:22am | Aug 1, 2026 2:53pm | Aug 1, 2026 2:53pm | Aug 1, 2026 2:53pm | Aug 1, 2026 2:53pm | Aug 1, 2026 2:54pm | Aug 1, 2026 2:54pm |  |  | Fair | No | Premises not located inadequately direction contact customer by telephone unsuccessful.
Non-Outage | J.E.26.07.39674 | C001871150 | Raymond Lewis | null | Completed | null | null | Jul 31, 2026 3:18pm | Jul 31, 2026 3:18pm | Jul 31, 2026 3:27pm | Jul 31, 2026 8:17pm | Jul 31, 2026 8:17pm | Jul 31, 2026 8:16pm | Jul 31, 2026 8:20pm | Jul 31, 2026 8:20pm |  |  | Fair | No | Open 25 kva x former to splice and retention 3 span secondary
Outage | J.E.26.07.39496 | C001871149 | Javid Vernon | Westmoreland | Completed | Load_257353 | Paradise - 110 | Jul 31, 2026 3:17pm | Jul 31, 2026 3:18pm | Jul 31, 2026 4:08pm | Jul 31, 2026 4:08pm | Jul 31, 2026 4:52pm | Jul 31, 2026 5:13pm | Jul 31, 2026 5:13pm | Jul 31, 2026 5:13pm |  |  | Fair | No | Refuse one 25kva transformer use 3amp fuse
Outage | J.E.26.07.39552 | C001871146 | Javid Vernon | Westmoreland | Completed | Load_249422 | Paradise - 210 | Jul 31, 2026 3:17pm | Jul 31, 2026 3:18pm | Jul 31, 2026 5:15pm | Jul 31, 2026 5:22pm | Jul 31, 2026 5:22pm | Jul 31, 2026 5:22pm | Jul 31, 2026 5:22pm | Jul 31, 2026 5:22pm |  |  | Fair | No | Customer stated that the power was restored
Outage | J.E.26.07.39576 | C001871145 | Javid Vernon | Westmoreland | Completed | Load_292673 | Paradise - 210 | Jul 31, 2026 3:17pm | Jul 31, 2026 3:18pm | Jul 31, 2026 5:23pm | Jul 31, 2026 5:23pm | Jul 31, 2026 6:44pm | Jul 31, 2026 7:11pm | Jul 31, 2026 7:11pm | Jul 31, 2026 7:11pm | BrokenWire |  | Fair | No | Retention and reconnect customer service wire use three clamps voltage reading 111/110/221
Outage | J.E.26.07.39666 | C001871147 | Javid Vernon | Westmoreland | Completed | Load_251332 | Paradise - 210 | Jul 31, 2026 3:17pm | Jul 31, 2026 3:18pm | Jul 31, 2026 7:12pm | Jul 31, 2026 7:12pm | Jul 31, 2026 7:36pm | Jul 31, 2026 7:45pm | Jul 31, 2026 7:51pm | Jul 31, 2026 7:51pm |  |  | Fair | No | Check and found meter defective after doing my checks meter is showing connected but there is no power going through the meter needs to be replaced urgently refer to field service voltage reading 108/114/223
Outage | J.E.26.07.39670 | C001871144 | Oshane Warren | Westmoreland | Completed | Load_292088 | Paradise - 210 | Jul 31, 2026 3:17pm | Aug 1, 2026 7:24am | Aug 1, 2026 8:46am | Aug 1, 2026 8:46am | Aug 1, 2026 10:34am | Aug 1, 2026 10:34am | Aug 1, 2026 10:35am | Aug 1, 2026 10:35am |  |  | Fair | No | Unable to locate or contact customer need direction
Non-Outage | J.E.26.07.37142 | C001871143 | Richard Watson | St.Elizabeth | Completed | Load_263224 | Maggotty - 110 | Jul 31, 2026 3:16pm | Jul 31, 2026 3:17pm | Jul 31, 2026 7:33pm | Jul 31, 2026 7:33pm | Jul 31, 2026 8:22pm | Jul 31, 2026 8:28pm | Jul 31, 2026 8:30pm | Jul 31, 2026 8:30pm | Fire |  | Fair | No | Found okay, supply restored from yesterday.
Non-Outage | J.E.26.07.39604 | C001871139 | Hopeton Henry | St.Thomas | Completed | Load_265545 | Lysson - 410 | Jul 31, 2026 3:14pm | Jul 31, 2026 3:14pm | Jul 31, 2026 4:32pm | Jul 31, 2026 4:32pm | Jul 31, 2026 5:10pm | Jul 31, 2026 6:50pm | Jul 31, 2026 6:52pm | Jul 31, 2026 6:52pm |  |  | Fair | No | Customer not located cell phone went unanswered, driving directions not correct
Outage | J.E.26.07.39656 | C001871140 | Tyrese Williams | St.Ann | Completed | Load_248846 | Cardiff Hall - 310 | Jul 31, 2026 3:14pm | Jul 31, 2026 3:24pm | Jul 31, 2026 5:03pm | Jul 31, 2026 7:33pm | Jul 31, 2026 8:02pm | Jul 31, 2026 8:20pm | Jul 31, 2026 8:20pm | Jul 31, 2026 8:20pm |  |  | Fair | No | Replace 15 amp junction fuse at pole
Outage | J.E.26.07.39721 | C001871141 | Tyrese Williams | St.Ann | Completed | Load_261435 | Cardiff Hall - 310 | Jul 31, 2026 3:14pm | Jul 31, 2026 3:24pm | Jul 31, 2026 5:03pm | Jul 31, 2026 5:04pm | Jul 31, 2026 5:45pm | Jul 31, 2026 5:49pm | Jul 31, 2026 5:49pm | Jul 31, 2026 5:49pm |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.07.39237 | C001871138 | Richard Watson | St.Elizabeth | Completed | Load_238611 | Maggotty - 110 | Jul 31, 2026 3:12pm | Jul 31, 2026 3:13pm | Jul 31, 2026 9:13pm | Jul 31, 2026 9:13pm | Jul 31, 2026 9:40pm | Jul 31, 2026 9:47pm | Jul 31, 2026 9:48pm | Jul 31, 2026 9:48pm |  |  | Fair | No | Customer without electricity since the passage of hurricane Melissa, however premises is not yet ready to receive electricity, as roofing is incomplete, customer advised to call back for reconnection once work is completed.
Outage | J.E.26.07.39447 | C001871136 | Richman Whyte | St.Elizabeth | Completed | Load_244141 | Maggotty - 110 | Jul 31, 2026 3:12pm | Jul 31, 2026 3:13pm | Jul 31, 2026 8:29pm | Jul 31, 2026 8:29pm | Jul 31, 2026 8:29pm | Jul 31, 2026 8:29pm | Jul 31, 2026 8:38pm | Jul 31, 2026 8:38pm |  |  | Fair | No | Customer stated that her house was destroyed by the hurricane and she has connection but she is still getting bills
Outage | J.E.26.07.39647 | C001871137 | Richard Watson | St.Elizabeth | Completed | Load_254694 | Maggotty - 110 | Jul 31, 2026 3:12pm | Jul 31, 2026 3:13pm | Jul 31, 2026 8:59pm | Jul 31, 2026 8:59pm | Jul 31, 2026 9:07pm | Jul 31, 2026 9:09pm | Jul 31, 2026 9:13pm | Jul 31, 2026 9:13pm |  |  | Fair | No | Unable to reach customer by phone or locate customer premises.
Outage | J.E.26.07.39699 | C001871104 | Antony Levy | KSAN | Completed | Load_260317 | Constant Spring - 310 | Jul 31, 2026 2:40pm | Jul 31, 2026 3:50pm | Jul 31, 2026 10:20pm | Jul 31, 2026 10:20pm | Jul 31, 2026 10:20pm | Jul 31, 2026 10:20pm | Jul 31, 2026 10:20pm | Jul 31, 2026 10:20pm |  |  | Fair | No
Outage | J.E.26.07.39710 | C001871106 | Antony Levy | KSAN | Completed | Load_248079 | Constant Spring - 310 | Jul 31, 2026 2:40pm | Jul 31, 2026 3:50pm | Jul 31, 2026 10:22pm | Jul 31, 2026 10:22pm | Jul 31, 2026 10:22pm | Jul 31, 2026 10:22pm | Jul 31, 2026 10:22pm | Jul 31, 2026 10:22pm |  |  | Fair | No
Non-Outage | J.E.26.07.39061 | C001871102 | Moses Elliston | Portmore | Completed | Load_293953 | Naggo Head - 510 | Jul 31, 2026 2:39pm | Jul 31, 2026 2:44pm | Jul 31, 2026 3:24pm | Jul 31, 2026 3:24pm | Jul 31, 2026 5:16pm | Jul 31, 2026 5:16pm | Jul 31, 2026 5:18pm | Jul 31, 2026 5:18pm |  |  | EarthMovement | No | Sixty feet burnt #6 triplex changed using 4 linkets,and 3 clamps.118-118-236 volts
Outage | J.E.26.07.39704 | C001871097 | Moses Elliston | St.Catherine | Completed | Load_568559 | Tredegar - 510 | Jul 31, 2026 2:29pm | Jul 31, 2026 2:30pm | Aug 1, 2026 10:40am | Aug 1, 2026 10:40am | Aug 1, 2026 10:40am | Aug 1, 2026 10:15am | Aug 1, 2026 10:41am | Aug 1, 2026 10:41am |  |  | Fair | No | Credit added to prepaid account.
Non-Outage | J.E.26.07.39714 | C001871096 | Antony Levy | null | Completed | null | null | Jul 31, 2026 2:27pm | Jul 31, 2026 4:02pm | Jul 31, 2026 10:23pm | Jul 31, 2026 10:23pm | Jul 31, 2026 10:38pm | Jul 31, 2026 10:38pm | Jul 31, 2026 10:39pm | Jul 31, 2026 10:39pm | BrokenPole |  | Fair | No | Not jps pole ...flow pole and wires
Outage | J.E.26.07.39687 | C001871080 | Antony Levy | KSAN | Completed | Load_246886 | Constant Spring - 310 | Jul 31, 2026 2:23pm | Jul 31, 2026 3:50pm | Jul 31, 2026 3:58pm | Jul 31, 2026 3:58pm | Jul 31, 2026 5:03pm | Jul 31, 2026 5:44pm | Jul 31, 2026 5:46pm | Jul 31, 2026 5:46pm |  |  | Fair | No | 20 amp junction fuse found blown,Tree fell on primary clear tre then refuse junction at pole 0000458.
Outage | J.E.26.07.39682 | C001871079 | Antony Levy | KSAN | Completed | Load_266632 | Constant Spring - 310 | Jul 31, 2026 2:21pm | Jul 31, 2026 4:01pm | Jul 31, 2026 10:19pm | Jul 31, 2026 10:19pm | Jul 31, 2026 10:19pm | Jul 31, 2026 10:19pm | Jul 31, 2026 10:20pm | Jul 31, 2026 10:20pm |  |  | Fair | No
Outage | J.E.26.07.39689 | C001871077 | Antony Levy | KSAN | Completed | Load_294382 | Constant Spring - 310 | Jul 31, 2026 2:21pm | Jul 31, 2026 4:01pm | Jul 31, 2026 10:18pm | Jul 31, 2026 10:18pm | Jul 31, 2026 10:19pm | Jul 31, 2026 10:19pm | Jul 31, 2026 10:19pm | Jul 31, 2026 10:19pm |  |  | Fair | No
Outage | J.E.26.07.39631 | C001871068 | Royston Montague | St.Catherine | Completed | Load_265050 | Tredegar - 410 | Jul 31, 2026 2:11pm | Jul 31, 2026 2:11pm | Jul 31, 2026 3:52pm | Jul 31, 2026 4:10pm | Jul 31, 2026 5:15pm | Jul 31, 2026 5:19pm | Jul 31, 2026 5:19pm | Jul 31, 2026 5:19pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.39676 | C001871066 | Milton Charlton | KSAN | Completed | Load_557824 | Hope - 410 | Jul 31, 2026 2:07pm | Jul 31, 2026 2:13pm | Jul 31, 2026 9:00pm | Jul 31, 2026 9:08pm | Jul 31, 2026 9:08pm | Jul 31, 2026 9:15pm | Jul 31, 2026 9:10pm | Jul 31, 2026 9:10pm | LowHangingWires |  | Fair | No | Unable to locate customer by telephone. Number on the report going straight to voicemail.
Outage | J.E.26.07.39691 | C001871064 | Christopher Edwards | KSAN | Completed | Load_244359 | Constant Spring - 310 | Jul 31, 2026 2:07pm | Jul 31, 2026 2:14pm | Jul 31, 2026 2:25pm | Jul 31, 2026 2:25pm | Jul 31, 2026 2:42pm | Jul 31, 2026 5:06pm | Jul 31, 2026 5:06pm | Jul 31, 2026 5:06pm | Fire |  | Fair | No | Splice and retention broken open secondary wireUsing:50ft #2 AA conductor (2) #2 preform (3) one bolt clamps Refuse blown 25 kva transformer Using (1) 3 amps
Outage | J.E.26.07.39648 | C001871054 | Hopeton Henry | St.Thomas | Completed | Load_270158 | Lysson - 410 | Jul 31, 2026 1:48pm | Jul 31, 2026 3:13pm | Jul 31, 2026 4:32pm | Jul 31, 2026 6:52pm | Jul 31, 2026 6:52pm | Jul 31, 2026 6:52pm | Jul 31, 2026 6:53pm | Jul 31, 2026 6:53pm |  |  | Fair | No | Customer not located
Non-Outage | J.E.26.07.39634 | C001871048 | Raymond Carr | null | Completed | null | null | Jul 31, 2026 1:39pm | Jul 31, 2026 3:31pm | Jul 31, 2026 5:29pm | Jul 31, 2026 5:29pm | Jul 31, 2026 5:29pm | Jul 31, 2026 5:17pm | Jul 31, 2026 5:30pm | Jul 31, 2026 5:30pm | Fire |  | Fair | No | Related to defective transformer at Galina.
Outage | J.E.26.07.39639 | C001871047 | Raymond Carr | St.Mary | Completed | Load_243605 | Oracabessa - 110 | Jul 31, 2026 1:39pm | Jul 31, 2026 3:31pm | Jul 31, 2026 3:57pm | Jul 31, 2026 3:57pm | Jul 31, 2026 5:16pm | Jul 31, 2026 5:16pm | Jul 31, 2026 5:27pm | Jul 31, 2026 5:27pm | Fire |  | Fair | No | Defective 50kva transformer found. Kindly refer refer to maintenance department for replacement. About forty five customers are affected.
Outage | J.E.26.07.39614 | C001871041 | Antony Levy | KSAN | Completed | Load_268626 | Constant Spring - 210 | Jul 31, 2026 1:23pm | Jul 31, 2026 3:58pm | Jul 31, 2026 7:03pm | Jul 31, 2026 7:03pm | Jul 31, 2026 7:03pm | Jul 31, 2026 7:03pm | Jul 31, 2026 7:04pm | Jul 31, 2026 7:04pm | TreeContact |  | Fair | No | Premises locked
Outage | J.E.26.07.39557 | C001871033 | Cliton Henry | St.Ann | Completed | Load_245285 | Upper White River - 110 | Jul 31, 2026 1:16pm | Jul 31, 2026 1:17pm | Jul 31, 2026 1:22pm | Jul 31, 2026 1:22pm | Jul 31, 2026 2:19pm | Jul 31, 2026 2:39pm | Jul 31, 2026 2:39pm | Jul 31, 2026 2:39pm |  |  | Fair | No | No stanchion in place to anchor the service wire hence the customer was not connect. The customer was advised.
Outage | J.E.26.07.39457 | C001871032 | Jowayne Newmans | Portland | Completed | Load_243638 | Port Antonio - 410 | Jul 31, 2026 1:15pm | Jul 31, 2026 1:15pm | Jul 31, 2026 2:51pm | Jul 31, 2026 2:51pm | Jul 31, 2026 2:51pm | Jul 31, 2026 2:53pm | Jul 31, 2026 2:54pm | Jul 31, 2026 2:54pm |  |  | Fair | No | Customer meter is damaged and need to be replaced, refer call to field service so that meter can be changed.
Outage | J.E.26.07.39532 | C001871031 | Jowayne Newmans | Portland | Completed | Load_246728 | Port Antonio - 410 | Jul 31, 2026 1:15pm | Jul 31, 2026 1:15pm | Jul 31, 2026 1:50pm | Jul 31, 2026 1:50pm | Jul 31, 2026 2:47pm | Jul 31, 2026 2:51pm | Jul 31, 2026 2:51pm | Jul 31, 2026 2:51pm | BrokenWire |  | Fair | No | Patrol and found customer service wire torn down cause by passing truck, disconnected service wire because customer service entrance is damaged. Customer is left without supply until repairs are completed to their system.
Outage | J.E.26.07.39613 | C001871030 | Andre Williams | Trelawny | Completed | Load_302355 | Duncans - 110 | Jul 31, 2026 1:11pm | Jul 31, 2026 1:12pm | Jul 31, 2026 3:41pm | Jul 31, 2026 3:41pm | Jul 31, 2026 3:46pm | Jul 31, 2026 3:49pm | Jul 31, 2026 3:49pm | Jul 31, 2026 3:49pm |  |  | Fair | No | Customer reconnected with the help meter center.
Outage | J.E.26.07.39605 | C001871028 | Andre Williams | Trelawny | Completed | Load_250742 | Duncans - 210 | Jul 31, 2026 1:05pm | Jul 31, 2026 1:06pm | Jul 31, 2026 1:16pm | Jul 31, 2026 1:23pm | Jul 31, 2026 3:37pm | Jul 31, 2026 3:39pm | Jul 31, 2026 3:40pm | Jul 31, 2026 3:40pm |  |  | Fair | No | Patrol line section remove top face that was resting on bracket back into spool insulator re fuse and close 3 amp on 25 kva transformer
Non-Outage | J.E.26.06.13489 | C001871023 | Derrick Dawkins | null | Completed | null | null | Jul 31, 2026 1:01pm | Jul 31, 2026 1:01pm | Jul 31, 2026 2:34pm | Jul 31, 2026 2:34pm | Jul 31, 2026 2:34pm | Jul 31, 2026 2:38pm | Jul 31, 2026 3:02pm | Jul 31, 2026 3:02pm |  |  | Fair | No | Cannot locate customer
Outage | J.E.26.07.39571 | C001871022 | Andrew Powell | Manchester | Completed | Load_241218 | Spur Tree - 210 | Jul 31, 2026 12:59pm | Aug 1, 2026 11:22am | Aug 1, 2026 2:52pm | Aug 1, 2026 2:52pm | Aug 1, 2026 2:52pm | Aug 1, 2026 2:52pm | Aug 1, 2026 2:53pm | Aug 1, 2026 2:53pm | BrokenWire |  | Fair | No | Premises not located inadequately direction contact customer by telephone unsuccessful.
Non-Outage | J.E.26.07.36409 | C001871021 | Odeanie Davis | KSAS | Completed | Load_256836 | Up Park Camp - 510 | Jul 31, 2026 12:57pm | Jul 31, 2026 1:00pm | Jul 31, 2026 1:12pm | Jul 31, 2026 1:16pm | Jul 31, 2026 1:16pm | Jul 31, 2026 2:05pm | Jul 31, 2026 2:04pm | Jul 31, 2026 2:04pm |  |  | Fair | No | 73v/115v at arrival, open circuit at secondary corrected, 3 one bolt clamps, 117v/115v & 232v after correction
Non-Outage | J.E.26.07.39578 | C001871007 | Rusean Allen | null | Completed | null | null | Jul 31, 2026 12:47pm | Jul 31, 2026 12:49pm | Jul 31, 2026 1:34pm | Jul 31, 2026 1:34pm | Jul 31, 2026 2:02pm | Jul 31, 2026 2:41pm | Jul 31, 2026 2:41pm | Jul 31, 2026 2:41pm |  |  | Fair | No | Stoplight needs to be checked. Voltage 120v
Outage | J.E.26.07.39561 | C001871008 | Rusean Allen | KSAS | Completed | Load_569195 | Cane River - 610 | Jul 31, 2026 12:47pm | Jul 31, 2026 12:49pm | Jul 31, 2026 1:18pm | Jul 31, 2026 3:25pm | Jul 31, 2026 3:29pm | Jul 31, 2026 3:29pm | Jul 31, 2026 3:29pm | Jul 31, 2026 3:29pm |  |  | Fair | No | Premises okay
Outage | J.E.26.07.39491 | C001871005 | Eric Williams | KSAN | Completed | Load_240096 | West Kings House - 410 | Jul 31, 2026 12:46pm | Jul 31, 2026 12:57pm | Jul 31, 2026 1:28pm | Jul 31, 2026 1:28pm | Jul 31, 2026 2:08pm | Jul 31, 2026 2:09pm | Jul 31, 2026 2:09pm | Jul 31, 2026 2:09pm |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.39562 | C001871006 | Elvis Trowers | KSAS | Completed | Load_250744 | Duhaney - 310 | Jul 31, 2026 12:46pm | Jul 31, 2026 12:56pm | Jul 31, 2026 2:03pm | Jul 31, 2026 2:03pm | Jul 31, 2026 2:46pm | Jul 31, 2026 2:51pm | Jul 31, 2026 2:51pm | Jul 31, 2026 2:51pm |  |  | Fair | Yes | Happened to be a disconnection and was reconnected with the assistant of escalation service department.
Outage | J.E.26.07.39563 | C001871004 | Elvis Trowers | KSAS | Completed | Load_245614 | Duhaney - 310 | Jul 31, 2026 12:46pm | Jul 31, 2026 1:00pm | Jul 31, 2026 1:15pm | Jul 31, 2026 1:15pm | Jul 31, 2026 2:01pm | Jul 31, 2026 2:03pm | Jul 31, 2026 2:03pm | Jul 31, 2026 2:03pm |  |  | Fair | Yes | Premises checked and found ok upon arrival customer was also spoken with, however he said that the power supply was restored.
Non-Outage | J.E.26.07.36826 | C001870980 | Rusean Allen | KSAS | Completed | Load_269395 | Hunts Bay - 510 | Jul 31, 2026 12:25pm | Jul 31, 2026 12:26pm | Jul 31, 2026 1:07pm | Jul 31, 2026 1:07pm | Jul 31, 2026 1:24pm | Jul 31, 2026 1:25pm | Jul 31, 2026 1:25pm | Jul 31, 2026 1:25pm |  |  | Fair | No | Internal problems, customer was advised to contact electrician
Outage | J.E.26.07.39509 | C001870979 | Romaine Roberts | St.Mary | Completed | Load_246693 | Highgate - 210 | Jul 31, 2026 12:25pm | Jul 31, 2026 12:25pm | Jul 31, 2026 12:57pm | Jul 31, 2026 12:57pm | Jul 31, 2026 12:57pm | Jul 31, 2026 1:10pm | Jul 31, 2026 1:11pm | Jul 31, 2026 1:11pm |  |  | Fair | No | Truck burst down one customer service mine replace 125 foot number 6 triplex 3 clamp and 3 penunion also customer meter defective on one side meter number 2872844
Non-Outage | J.E.26.07.18818 | C001870978 | Daniel Francis | St.Ann | Completed | Load_239487 | Roaring River - 210 | Jul 31, 2026 12:24pm | Jul 31, 2026 12:25pm | Jul 31, 2026 1:11pm | Jul 31, 2026 1:11pm | Jul 31, 2026 2:09pm | Jul 31, 2026 2:23pm | Jul 31, 2026 2:23pm | Jul 31, 2026 2:23pm |  |  | Fair | No | Pole #0070943 found 25kva transformer power defective banker 2
Outage | J.E.26.07.39526 | C001870973 | Dwayne Samuels | Trelawny | Completed | Load_575541 | Greenwood - 210 | Jul 31, 2026 12:22pm | Jul 31, 2026 12:24pm | Jul 31, 2026 1:09pm | Jul 31, 2026 1:40pm | Jul 31, 2026 2:20pm | Jul 31, 2026 2:41pm | Jul 31, 2026 2:42pm | Jul 31, 2026 2:42pm | BrokenWire |  | Fair | No | Customer is connected to hexing box hex-05304/hx-22655589 refer to field service
Outage | J.E.26.07.39508 | C001870971 | Marlon Brown | Trelawny | Completed | Load_238383 | Greenwood - 110 | Jul 31, 2026 12:15pm | Jul 31, 2026 3:22pm | Jul 31, 2026 4:46pm | Jul 31, 2026 4:46pm | Jul 31, 2026 7:12pm | Jul 31, 2026 8:10pm | Jul 31, 2026 8:10pm | Jul 31, 2026 8:10pm |  |  | Fair | No | Change defective service wire 100ft #6, 3 linkers & 3 pg clamps Voltage found at pothead noneVoltage leaving at pothead 106/108=214v.
Outage | J.E.26.07.39399 | C001870964 | Barnett Brown | Manchester | Completed | Load_250282 | Kendal - 210 | Jul 31, 2026 12:10pm | Jul 31, 2026 3:47pm | Jul 31, 2026 3:50pm | null | Jul 31, 2026 3:50pm | Jul 31, 2026 4:06pm | Jul 31, 2026 4:20pm | Jul 31, 2026 4:20pm | Fire |  | Fair | No | Leaking 25 kva transformer needs to be replaced, approximately 30 customers are out.
Outage | J.E.26.07.39497 | C001870955 | Ricky Hall | St.Catherine | Completed | Load_250877 | New Michelton - 210 | Jul 31, 2026 12:05pm | Jul 31, 2026 12:06pm | Jul 31, 2026 12:12pm | Jul 31, 2026 12:12pm | Jul 31, 2026 12:13pm | Jul 31, 2026 12:24pm | Jul 31, 2026 12:25pm | Jul 31, 2026 12:25pm |  |  | Fair | No | Replaced blown 65 amps junction fuse
Outage | J.E.26.07.39459 | C001870947 | Horace Malcolm | St.James | Completed | Load_557020 | Bogue - 310 | Jul 31, 2026 11:58am | Aug 1, 2026 7:32am | Aug 1, 2026 7:41am | Aug 1, 2026 7:41am | Aug 1, 2026 8:09am | Aug 1, 2026 9:07am | Aug 1, 2026 9:08am | Aug 1, 2026 9:08am | BrokenWire |  | Fair | No | Splice and retention customer service wire used 10ft #6 triplex wire and 1clamp voltage 114-116-230
Outage | J.E.26.07.39473 | C001870948 | Michael Christian | St.James | Completed | Load_266674 | Bogue - 410 | Jul 31, 2026 11:58am | Jul 31, 2026 1:27pm | Jul 31, 2026 1:32pm | Jul 31, 2026 1:32pm | Jul 31, 2026 1:53pm | Jul 31, 2026 3:08pm | Jul 31, 2026 3:09pm | Jul 31, 2026 3:09pm | Fire |  | Fair | No | Needed to give to 11 pm men work it’s and fire cause by slack at secondary line line transformer needed to open customer working call mer bell at # 252 6263 clamp at # 2 wire and 2/0 with the red wire needed to work and
Outage | J.E.26.07.39460 | C001870932 | Rusean Allen | KSAS | Completed | Load_245738 | Rockfort - 210 | Jul 31, 2026 11:47am | Jul 31, 2026 11:47am | Jul 31, 2026 12:34pm | Jul 31, 2026 12:50pm | Jul 31, 2026 1:02pm | Jul 31, 2026 1:04pm | Jul 31, 2026 1:04pm | Jul 31, 2026 1:04pm | BrokenWire |  | Fair | No | Broken secondary wire found, wire was spliced retention and reconnected.
Outage | J.E.26.07.39461 | C001870931 | Neville Spencer | Clarendon | Completed | Load_252773 | Monymusk - 410 | Jul 31, 2026 11:46am | Jul 31, 2026 11:47am | Jul 31, 2026 4:35pm | Jul 31, 2026 4:35pm | Jul 31, 2026 5:05pm | Jul 31, 2026 5:38pm | Jul 31, 2026 5:41pm | Jul 31, 2026 5:41pm | BrokenWire |  | Fair | No | Open 25 kva xmfr remade burnt out clamp on phase drop leads used 3, clamps voltage reading 114 116/ 232 supply restored.
Outage | J.E.26.07.39454 | C001870928 | Antony Levy | KSAN | Completed | Load_269276 | Washington Blvd - 410 | Jul 31, 2026 11:43am | Jul 31, 2026 3:57pm | Jul 31, 2026 7:08pm | Jul 31, 2026 7:08pm | Jul 31, 2026 7:27pm | Jul 31, 2026 7:28pm | Jul 31, 2026 7:28pm | Jul 31, 2026 7:28pm |  |  | Fair | No | Premises closed
Outage | J.E.26.07.39420 | C001870926 | Ricky Hall | St.Catherine | Completed | Load_255656 | New Michelton - 210 | Jul 31, 2026 11:40am | Jul 31, 2026 11:40am | Jul 31, 2026 12:12pm | Jul 31, 2026 12:25pm | Jul 31, 2026 12:25pm | Jul 31, 2026 12:25pm | Jul 31, 2026 12:26pm | Jul 31, 2026 12:26pm |  |  | Fair | No | Call associated with outage #39497
Outage | J.E.26.07.39429 | C001870922 | Selvin White | St.Elizabeth | Completed | Load_256735 | Maggotty - 210 | Jul 31, 2026 11:38am | Jul 31, 2026 11:38am | Jul 31, 2026 1:21pm | Jul 31, 2026 1:31pm | Jul 31, 2026 1:49pm | Jul 31, 2026 2:10pm | Jul 31, 2026 2:13pm | Jul 31, 2026 2:13pm | BrokenWire |  | SevereWind | No | Splice and retention approximately 10 ft of number six triplex service wire neutral conductor that burnt due to contact with secondary phase conductor caused by heavy wind. Supply restored with voltage readings of 221,110,111 volts.
Outage | J.E.26.07.39407 | C001870921 | Marlon Authors | Manchester | Completed | Load_254759 | Spur Tree - 210 | Jul 31, 2026 11:37am | Jul 31, 2026 11:38am | Jul 31, 2026 1:02pm | Jul 31, 2026 1:02pm | Jul 31, 2026 1:31pm | Jul 31, 2026 2:39pm | Jul 31, 2026 2:40pm | Jul 31, 2026 2:40pm | BrokenWire |  | Fair | No | Supply checked and found insulation burnt from service wire. Isolate and close 50 kva transformer circuit at pole #028218. To repair same using 5 feet of 2/0 conductor and four clamps . Supply leave working ok
Non-Outage | J.E.26.07.39384 | C001870920 | Rusean Allen | KSAS | Completed | Load_258204 | Cane River - 610 | Jul 31, 2026 11:35am | Jul 31, 2026 1:00pm | Jul 31, 2026 2:41pm | Jul 31, 2026 2:41pm | Jul 31, 2026 3:23pm | Jul 31, 2026 3:25pm | Jul 31, 2026 3:25pm | Jul 31, 2026 3:25pm |  |  | Fair | No | No directions, customer phone went unanswered
Outage | J.E.26.07.39326 | C001870919 | Wan Carlos Scarlett | St.Catherine | Completed | Load_246714 | Tredegar - 210 | Jul 31, 2026 11:35am | Jul 31, 2026 11:38am | Jul 31, 2026 12:44pm | Jul 31, 2026 12:44pm | Jul 31, 2026 1:53pm | Jul 31, 2026 2:20pm | Jul 31, 2026 2:25pm | Jul 31, 2026 2:25pm | BrokenWire |  | Fair | No | Found 100 KVA transformer with lower phase droplead to open secondary line burn out from the one bolt clamp pole #006421 use 2 one bolt clamps on line Readings 117 117 234 power supply has been restored
Non-Outage | J.E.26.07.39285 | C001870916 | Oshane Warren | Westmoreland | Completed | Load_249880 | Paradise - 210 | Jul 31, 2026 11:33am | Jul 31, 2026 11:33am | Jul 31, 2026 2:19pm | Jul 31, 2026 2:19pm | Jul 31, 2026 2:19pm | Jul 31, 2026 2:19pm | Jul 31, 2026 2:20pm | Jul 31, 2026 2:20pm |  |  | Fair | No | Splice and reconnect back conductor used 2 pg clamps
Non-Outage | J.E.26.07.39417 | C001870904 | Rusean Allen | null | Completed | null | null | Jul 31, 2026 11:23am | Jul 31, 2026 11:23am | Jul 31, 2026 11:56am | Jul 31, 2026 1:05pm | Jul 31, 2026 1:05pm | Jul 31, 2026 1:05pm | Jul 31, 2026 1:05pm | Jul 31, 2026 1:05pm | Fire |  | Fair | No | Related
Outage | J.E.26.07.39311 | C001870909 | Roxroy Needham | St.Ann | Completed | Load_260245 | Cardiff Hall - 310 | Jul 31, 2026 11:23am | Jul 31, 2026 11:24am | Jul 31, 2026 1:03pm | Jul 31, 2026 1:04pm | Jul 31, 2026 1:26pm | Jul 31, 2026 1:31pm | Jul 31, 2026 1:31pm | Jul 31, 2026 1:31pm | BrokenWire |  | Fair | No | Customer need to plan intermediate pole
Outage | J.E.26.07.39353 | C001870910 | Daniel Francis | St.Ann | Completed | Load_241512 | Ocho Rios - 310 | Jul 31, 2026 11:23am | Jul 31, 2026 11:24am | Jul 31, 2026 2:23pm | Jul 31, 2026 2:23pm | Jul 31, 2026 2:51pm | Jul 31, 2026 3:01pm | Jul 31, 2026 3:03pm | Jul 31, 2026 3:03pm |  |  | Fair | No | Found junction blown at pole 0010354 20amp replace
Outage | J.E.26.07.39367 | C001870911 | Omar King | St.Ann | Completed | Load_258977 | Ocho Rios - 310 | Jul 31, 2026 11:23am | Jul 31, 2026 3:13pm | Jul 31, 2026 3:25pm | Jul 31, 2026 3:25pm | Jul 31, 2026 4:33pm | Jul 31, 2026 4:55pm | Jul 31, 2026 4:56pm | Jul 31, 2026 4:56pm |  |  | Fair | No | Found customer meter not making any communication please refer to field service voltage reading 115-116-232 V
Outage | J.E.26.07.39403 | C001870880 | Dean- Smith | Hanover | Completed | Load_265709 | Orange Bay - 210 | Jul 31, 2026 11:03am | Jul 31, 2026 11:04am | Jul 31, 2026 12:31pm | Jul 31, 2026 12:31pm | Jul 31, 2026 1:58pm | Jul 31, 2026 1:58pm | Jul 31, 2026 2:12pm | Jul 31, 2026 2:12pm |  |  | Fair | No | Customer complaint of primary voltage low on one phase, customer was advised of our additional loading since restoration on both orange bay feeders .their pad mounted transformer is also private, they could try regular the voltage from the transformer.
Outage | J.E.26.07.39378 | C001870878 | Milton Charlton | KSAN | Completed | Load_257858 | Hope - 510 | Jul 31, 2026 11:02am | Jul 31, 2026 11:02am | Jul 31, 2026 1:38pm | Jul 31, 2026 1:38pm | Jul 31, 2026 1:48pm | Jul 31, 2026 2:00pm | Jul 31, 2026 2:00pm | Jul 31, 2026 2:00pm |  |  | Fair | No | Found okay upon arrival. Customer has on internal problem. Customer need to change meter socket. Readings at pothead and meter socket 15 volts.
Outage | J.E.26.07.39361 | C001870873 | Kenroy Dale | Manchester | Completed | Load_261230 | Kendal - 310 | Jul 31, 2026 10:56am | Jul 31, 2026 10:56am | Jul 31, 2026 11:22am | Jul 31, 2026 11:22am | Jul 31, 2026 12:40pm | Jul 31, 2026 1:00pm | Jul 31, 2026 1:01pm | Jul 31, 2026 1:01pm | LeakingTransformer |  | Fair | No | Rotten guy pole found badly leaning which caused customer to use rope to anchor on their wall. Maintenance is required
Outage | J.E.26.07.39355 | C001870870 | Cliton Henry | St.Mary | Completed | Load_256364 | Oracabessa - 110 | Jul 31, 2026 10:54am | Jul 31, 2026 10:54am | Jul 31, 2026 11:09am | Jul 31, 2026 11:09am | Jul 31, 2026 11:52am | Jul 31, 2026 12:09pm | Jul 31, 2026 12:14pm | Jul 31, 2026 12:14pm |  |  | Fair | No | The voltages found at the customer’s pothead were 119-119/238 volts. The customer was advised to get a licensed electrician to check internally. Kindly refer to Field Service Department to open the locking band at the meter to allow an electrician to check inside the meter socket
Outage | J.E.26.07.39376 | C001870871 | Cliton Henry | St.Mary | Completed | Load_250203 | Oracabessa - 110 | Jul 31, 2026 10:54am | Jul 31, 2026 10:54am | Jul 31, 2026 12:14pm | Jul 31, 2026 12:14pm | Jul 31, 2026 12:30pm | Jul 31, 2026 12:58pm | Jul 31, 2026 12:59pm | Jul 31, 2026 12:59pm |  |  | Fair | No | A burnt off secondary jumper found at pole # 0194485. A 25 kva transformer was de energized at pole #0013343 to carryout repairs. Corrective work done reconnected the secondary jumper using 1- one bolt clamp. Supply restored to energized the 25 kva transformer at pole #0013343
Outage | J.E.26.07.39366 | C001870852 | Andre Williams | Trelawny | Completed | Load_292431 | Duncans - 210 | Jul 31, 2026 10:40am | Jul 31, 2026 10:43am | Jul 31, 2026 11:35am | Jul 31, 2026 11:39am | Jul 31, 2026 11:51am | Jul 31, 2026 12:51am | Jul 31, 2026 11:52am | Jul 31, 2026 11:52am |  |  | Fair | No | Customers says didn’t make any report to Jps stating we have the wrong number
Outage | J.E.26.07.39339 | C001870835 | Neville Spencer | Clarendon | Completed | Load_269238 | Parnassus - 310 | Jul 31, 2026 10:21am | Jul 31, 2026 10:21am | Jul 31, 2026 11:05am | Jul 31, 2026 11:05am | Jul 31, 2026 11:54am | Jul 31, 2026 11:55am | Jul 31, 2026 12:00pm | Jul 31, 2026 12:00pm |  |  | Fair | No | Found secondary phase and neutral conductor entangled cleared renew blown 3 amp fuse protecting 25 kva xmfr at pole # 0119742 supply restored.
Outage | J.E.26.07.39352 | C001870834 | Andre Williams | Trelawny | Completed | Load_257206 | Martha Brae - 210 | Jul 31, 2026 10:19am | Jul 31, 2026 10:21am | Jul 31, 2026 10:36am | Jul 31, 2026 11:29am | Jul 31, 2026 11:29am | Jul 31, 2026 11:30am | Jul 31, 2026 11:34am | Jul 31, 2026 11:34am |  |  | Fair | No | Customer disconnected for none payment
Outage | J.E.26.07.39343 | C001870825 | Dwayne Samuels | St.James | Completed | Load_247847 | Queens Drive - 710 | Jul 31, 2026 10:15am | Jul 31, 2026 10:17am | Jul 31, 2026 11:09am | Jul 31, 2026 12:55pm | Jul 31, 2026 12:55pm | Jul 31, 2026 12:56pm | Jul 31, 2026 1:07pm | Jul 31, 2026 1:07pm |  |  | Fair | No | Check and found working ok call is related to 10kva tripped transformer that was reset today
Non-Outage | J.E.26.04.18191 | C001870822 | Horace Malcolm | null | Completed | null | null | Jul 31, 2026 10:14am | Jul 31, 2026 10:14am | Jul 31, 2026 12:57pm | Jul 31, 2026 12:57pm | Jul 31, 2026 1:53pm | Jul 31, 2026 2:11pm | Jul 31, 2026 2:11pm | Jul 31, 2026 2:11pm | Fire |  | Fair | No | Check and found premises ok no fire seen on pole
Non-Outage | J.E.26.06.02318 | C001870824 | Horace Malcolm | null | Completed | null | null | Jul 31, 2026 10:14am | Jul 31, 2026 10:14am | Jul 31, 2026 2:12pm | Jul 31, 2026 2:12pm | Jul 31, 2026 2:23pm | Jul 31, 2026 2:27pm | Jul 31, 2026 2:27pm | Jul 31, 2026 2:27pm | LeaningPole |  | Fair | No | Found one 40ft wooden pole with single phase primary and open span secondary lines leaning on customer fencing wall
Non-Outage | J.E.26.03.15654 | C001870820 | Horace Malcolm | null | Completed | null | null | Jul 31, 2026 10:13am | Jul 31, 2026 10:14am | Jul 31, 2026 10:26am | Jul 31, 2026 10:26am | Jul 31, 2026 11:35am | Jul 31, 2026 11:56am | Jul 31, 2026 11:56am | Jul 31, 2026 11:56am | Fire |  | Fair | No | Check an found service wire clamp slack causing sparks retighten back clamp
Non-Outage | J.E.26.03.28769 | C001870821 | Horace Malcolm | null | Completed | null | null | Jul 31, 2026 10:13am | Jul 31, 2026 10:14am | Jul 31, 2026 11:56am | Jul 31, 2026 11:56am | Jul 31, 2026 12:37pm | Jul 31, 2026 12:57pm | Jul 31, 2026 12:57pm | Jul 31, 2026 12:57pm | BrokenWire |  | Fair | No | Check and found no broken
Outage | J.E.26.07.39217 | C001870812 | Dean- Smith | St.James | Completed | Load_251941 | Bogue - 510 | Jul 31, 2026 10:12am | Jul 31, 2026 10:12am | Jul 31, 2026 10:22am | Jul 31, 2026 10:22am | Jul 31, 2026 11:22am | Jul 31, 2026 11:22am | Jul 31, 2026 12:31pm | Jul 31, 2026 12:31pm |  |  | Fair | No | Cut and remove vegetation, replace 2amp 25kva transformer fuse. Pole number ( 552856 )
Outage | J.E.26.07.39079 | C001870780 | Richman Whyte | St.Elizabeth | Completed | Load_265987 | Maggotty - 110 | Jul 31, 2026 9:52am | Jul 31, 2026 4:52pm | Jul 31, 2026 5:15pm | Jul 31, 2026 5:15pm | Jul 31, 2026 5:15pm | Jul 31, 2026 5:15pm | Jul 31, 2026 5:16pm | Jul 31, 2026 5:16pm |  |  | Fair | No | Customer get disconnect there is a problem with the meter refer to field service
Outage | J.E.26.07.39299 | C001870779 | Michael Christian | St.James | Completed | Load_575159 | Bogue - 310 | Jul 31, 2026 9:49am | Jul 31, 2026 9:55am | Jul 31, 2026 10:43am | Jul 31, 2026 10:43am | Jul 31, 2026 10:45am | Jul 31, 2026 10:48am | Jul 31, 2026 10:48am | Jul 31, 2026 10:48am |  |  | Fair | No | Found disconnection and reconnection
Non-Outage | J.E.26.02.05296 | C001870776 | Derrick Dawkins | null | Completed | null | null | Jul 31, 2026 9:46am | Jul 31, 2026 9:47am | Jul 31, 2026 3:02pm | Jul 31, 2026 3:02pm | Jul 31, 2026 4:43pm | Jul 31, 2026 3:15pm | Jul 31, 2026 4:59pm | Jul 31, 2026 4:59pm | LeaningPole |  | Fair | No | Cannot locate customer
Non-Outage | J.E.26.02.27631 | C001870775 | Derrick Dawkins | null | Completed | null | null | Jul 31, 2026 9:46am | Jul 31, 2026 9:47am | Jul 31, 2026 11:56am | Jul 31, 2026 1:26pm | Jul 31, 2026 1:27pm | Jul 31, 2026 1:30pm | Jul 31, 2026 1:32pm | Jul 31, 2026 1:32pm | LowHangingWires |  | Fair | No | Found several customers service wire hanging low from the en box needs to retention refer to field service
Non-Outage | J.E.26.02.30363 | C001870777 | Derrick Dawkins | null | Completed | null | null | Jul 31, 2026 9:46am | Jul 31, 2026 9:47am | Jul 31, 2026 11:54am | Jul 31, 2026 12:51pm | Jul 31, 2026 1:14pm | Jul 31, 2026 1:18pm | Jul 31, 2026 1:22pm | Jul 31, 2026 1:22pm | LowHangingWires |  | Fair | No | Found several customers service wire hanging low from the en box needs to retention refer to field service
Non-Outage | J.E.26.03.13190 | C001870774 | Derrick Dawkins | St.James | Completed | Load_556952 | Bogue - 310 | Jul 31, 2026 9:46am | Jul 31, 2026 9:47am | Jul 31, 2026 11:57am | Jul 31, 2026 1:36pm | Jul 31, 2026 1:50pm | Jul 31, 2026 1:53pm | Jul 31, 2026 1:54pm | Jul 31, 2026 1:54pm | LowHangingWires |  | Fair | No | Found several customers service wire hanging low from the hexing box refer to field service urgent attention
Non-Outage | J.E.26.06.19404 | C001870764 | Derrick Dawkins | null | Completed | null | null | Jul 31, 2026 9:38am | Jul 31, 2026 9:40am | Jul 31, 2026 11:58am | Jul 31, 2026 11:59am | Jul 31, 2026 12:00pm | Jul 31, 2026 11:53am | Jul 31, 2026 12:03pm | Jul 31, 2026 12:03pm | LeaningPole |  | Fair | No | Customer complained about street light not working
Non-Outage | J.E.26.07.05759 | C001870766 | Romeo Brissett | St.James | Completed | Load_266068 | Queens Drive - 710 | Jul 31, 2026 9:38am | Aug 1, 2026 7:53am | Aug 1, 2026 9:49am | Aug 1, 2026 9:49am | Aug 1, 2026 11:22am | Aug 1, 2026 11:00am | Aug 1, 2026 11:30am | Aug 1, 2026 11:30am | LeaningPole |  | Fair | No | Spliced and retention customer service due to leaning pole, Found (1)40ft pole severely leaning urgently need to straighten. Please send to maintenance.
Non-Outage | J.E.26.07.07137 | C001870769 | Derrick Dawkins | null | Completed | null | null | Jul 31, 2026 9:38am | Jul 31, 2026 9:40am | Jul 31, 2026 11:57am | Jul 31, 2026 12:40pm | Jul 31, 2026 12:40pm | Jul 31, 2026 12:19pm | Jul 31, 2026 12:42pm | Jul 31, 2026 12:42pm | LeaningPole |  | Fair | No | Check and found pole ok
Non-Outage | J.E.26.07.07765 | C001870770 | Derrick Dawkins | St.James | Completed | Load_254951 | Queens Drive - 710 | Jul 31, 2026 9:38am | Jul 31, 2026 9:40am | Jul 31, 2026 9:45am | Jul 31, 2026 9:45am | Jul 31, 2026 11:43am | Jul 31, 2026 11:36am | Jul 31, 2026 11:54am | Jul 31, 2026 11:54am | LeaningPole |  | Fair | No | Found 30 ft pole rotten at the base secondary line only need urgent attention refer to maintenance z
Outage | J.E.26.07.39297 | C001870758 | Ricky Hall | St.Catherine | Completed | Load_266283 | New Michelton - 210 | Jul 31, 2026 9:32am | Jul 31, 2026 9:33am | Jul 31, 2026 12:26pm | Jul 31, 2026 12:27pm | Jul 31, 2026 1:02pm | Jul 31, 2026 1:09pm | Jul 31, 2026 1:09pm | Jul 31, 2026 1:09pm | Fire |  | Fair | No | Splice and reconnect 3 w service mid span
Non-Outage | J.E.26.07.20230 | C001870753 | Royston Montague | St.Catherine | Completed | Load_255349 | Rhodens Pen - 410 | Jul 31, 2026 9:28am | Jul 31, 2026 9:28am | Jul 31, 2026 9:46am | Jul 31, 2026 11:41am | Jul 31, 2026 12:18pm | Jul 31, 2026 12:35pm | Jul 31, 2026 12:35pm | Jul 31, 2026 12:35pm |  |  | Fair | No | Faulty joints at customer take off point. Same corrected. Voltage found 114v voltage after job completion are 220v 109v 110v
Non-Outage | J.E.26.07.31028 | C001870751 | Junior Scarlett | St.James | Completed | Load_251354 | Bogue - 510 | Jul 31, 2026 9:25am | Jul 31, 2026 9:25am | Jul 31, 2026 9:31am | Jul 31, 2026 11:36am | Jul 31, 2026 12:04pm | Jul 31, 2026 12:05pm | Jul 31, 2026 12:06pm | Jul 31, 2026 12:06pm | LeaningPole |  | Fair | No | Check and found okVoltage found 114v 114v 228vVoltage leave 114v 114v 228v
Non-Outage | J.E.26.07.35252 | C001870749 | Junior Scarlett | St.James | Completed | Load_302358 | Bogue - 510 | Jul 31, 2026 9:24am | Jul 31, 2026 9:25am | Jul 31, 2026 9:31am | Jul 31, 2026 10:32am | Jul 31, 2026 11:24am | Jul 31, 2026 11:24am | Jul 31, 2026 11:26am | Jul 31, 2026 11:26am |  |  | Fair | No | Check and found okVoltage found 115v 115v 230v
Non-Outage | J.E.26.07.39183 | C001870744 | Junior Scarlett | St.James | Completed | Load_292389 | Bogue - 610 | Jul 31, 2026 9:23am | Jul 31, 2026 9:25am | Jul 31, 2026 9:31am | Jul 31, 2026 1:37pm | Jul 31, 2026 1:37pm | Jul 31, 2026 1:38pm | Jul 31, 2026 1:39pm | Jul 31, 2026 1:39pm |  |  | Fair | No | Refer to emergency team the whole are facing single faceVoltage found 114v 67v 220v
Non-Outage | J.E.26.07.39223 | C001870746 | Junior Scarlett | St.James | Completed | Load_249034 | Bogue - 610 | Jul 31, 2026 9:23am | Jul 31, 2026 9:25am | Jul 31, 2026 9:31am | Jul 31, 2026 2:51pm | Jul 31, 2026 3:05pm | Jul 31, 2026 3:20pm | Jul 31, 2026 3:20pm | Jul 31, 2026 3:20pm |  |  | Fair | No | Check and found okVoltage found 113v 113v 226vIllegal connections at night causes voltage drop
Non-Outage | J.E.26.07.24847 | C001870740 | Nicholas Dillon | St.Elizabeth | Completed | Load_244429 | Maggotty - 210 | Jul 31, 2026 9:22am | Jul 31, 2026 9:45am | Jul 31, 2026 10:53am | Jul 31, 2026 3:38pm | Jul 31, 2026 3:38pm | Jul 31, 2026 3:38pm | Jul 31, 2026 3:43pm | Jul 31, 2026 3:43pm | BrokenPole |  | Fair | Yes | Check voltage before at meter 107 99 phase to phase 206 . Clean joint at pothead and use 3 pen union before I left voltage is 110 104 phase to phase 214
Non-Outage | J.E.26.07.10244 | C001870735 | Andrae Dawkins | St.James | Completed | Load_576009 | Bogue - 310 | Jul 31, 2026 9:19am | Jul 31, 2026 9:22am | Jul 31, 2026 3:29pm | Jul 31, 2026 3:29pm | Jul 31, 2026 3:29pm | Jul 31, 2026 2:46pm | Jul 31, 2026 3:30pm | Jul 31, 2026 3:30pm |  |  | Fair | No | Customer experiencing on and off supply from EN box refer back to fieldservice
Non-Outage | J.E.26.07.10250 | C001870736 | Andrae Dawkins | St.James | Completed | Load_576009 | Bogue - 310 | Jul 31, 2026 9:19am | Jul 31, 2026 9:22am | Jul 31, 2026 1:51pm | Jul 31, 2026 3:16pm | Jul 31, 2026 3:16pm | Jul 31, 2026 2:46pm | Jul 31, 2026 3:29pm | Jul 31, 2026 3:29pm |  |  | Fair | No | Customer experiencing on and off supply from EN box refer back to field service
Non-Outage | J.E.26.07.10630 | C001870737 | Derrick Dawkins | St.James | Completed | Load_266579 | Bogue - 310 | Jul 31, 2026 9:19am | Jul 31, 2026 9:40am | Jul 31, 2026 11:57am | Jul 31, 2026 12:43pm | Jul 31, 2026 12:43pm | Jul 31, 2026 12:34pm | Jul 31, 2026 12:50pm | Jul 31, 2026 12:50pm | LeaningPole |  | Fair | No | Found 30 ft pole rotten at the base customer service wire holding the pole form falling down secondary line and street lights only need urgent attention refer to maintenance
Non-Outage | J.E.26.07.11354 | C001870739 | Andrae Dawkins | St.James | Completed | Load_292055 | Bogue - 310 | Jul 31, 2026 9:19am | Jul 31, 2026 9:22am | Jul 31, 2026 11:18am | Jul 31, 2026 3:31pm | Jul 31, 2026 3:31pm | Jul 31, 2026 11:21am | Jul 31, 2026 3:33pm | Jul 31, 2026 3:33pm | BrokenWire |  | Fair | No | Customer complained about cable wires hanging on wire
Non-Outage | J.E.26.07.38255 | C001870738 | Rochaine Hussey | KSAN | Completed | Load_572016 | Constant Spring - 310 | Jul 31, 2026 9:19am | Jul 31, 2026 9:20am | Jul 31, 2026 9:59am | Jul 31, 2026 2:43pm | Jul 31, 2026 2:43pm | Jul 31, 2026 2:44pm | Jul 31, 2026 2:46pm | Jul 31, 2026 2:46pm |  |  | Fair | No | Customer said issue was already resolved
Non-Outage | J.E.26.07.06631 | C001870713 | Andrae Dawkins | St.James | Completed | Load_574653 | Bogue - 310 | Jul 31, 2026 9:18am | Jul 31, 2026 9:22am | Jul 31, 2026 11:44am | Jul 31, 2026 1:27pm | Jul 31, 2026 1:27pm | Jul 31, 2026 10:17am | Jul 31, 2026 1:31pm | Jul 31, 2026 1:31pm |  |  | Fair | No | Unable to Locate customer cannot reach customer phone
Non-Outage | J.E.26.07.06702 | C001870715 | Andrae Dawkins | St.James | Completed | Load_576009 | Bogue - 310 | Jul 31, 2026 9:18am | Jul 31, 2026 9:22am | Jul 31, 2026 1:51pm | Jul 31, 2026 3:15pm | Jul 31, 2026 3:15pm | Jul 31, 2026 2:09pm | Jul 31, 2026 3:16pm | Jul 31, 2026 3:16pm |  |  | Fair | No | Cannot locate unable to reach customer phone
Non-Outage | J.E.26.07.07338 | C001870719 | Andrae Dawkins | St.James | Completed | Load_246427 | Bogue - 310 | Jul 31, 2026 9:18am | Jul 31, 2026 9:22am | Jul 31, 2026 3:14pm | Jul 31, 2026 3:14pm | Jul 31, 2026 3:14pm | Jul 31, 2026 1:33pm | Jul 31, 2026 3:14pm | Jul 31, 2026 3:14pm |  |  | Fair | No | Unable to locate customer
Non-Outage | J.E.26.07.07847 | C001870720 | Andrae Dawkins | St.James | Completed | Load_1001899 | Bogue - 310 | Jul 31, 2026 9:18am | Jul 31, 2026 9:22am | Jul 31, 2026 1:36pm | Jul 31, 2026 2:15pm | Jul 31, 2026 2:15pm | Jul 31, 2026 12:31pm | Jul 31, 2026 2:18pm | Jul 31, 2026 2:18pm |  |  | Fair | No | Cannot locate customer unable to reach customer phone
Non-Outage | J.E.26.07.09212 | C001870732 | Andrae Dawkins | St.James | Completed | Load_245438 | Queens Drive - 710 | Jul 31, 2026 9:18am | Jul 31, 2026 9:22am | Jul 31, 2026 1:37pm | Jul 31, 2026 1:37pm | Jul 31, 2026 1:51pm | Jul 31, 2026 12:07pm | Jul 31, 2026 1:54pm | Jul 31, 2026 1:54pm |  |  | Fair | No | Check and found ok customer said that they didn’t make any report and that there is no issue with the light
Non-Outage | J.E.26.07.09510 | C001870734 | Derrick Dawkins | St.James | Completed | Load_556954 | Bogue - 310 | Jul 31, 2026 9:18am | Jul 31, 2026 9:40am | Jul 31, 2026 1:23pm | Jul 31, 2026 1:55pm | Jul 31, 2026 2:07pm | Jul 31, 2026 2:13pm | Jul 31, 2026 2:14pm | Jul 31, 2026 2:14pm | LeaningPole |  | Fair | No | Found secondary pole leaning need to straighten refer to maintenance
Non-Outage | J.E.26.07.34918 | C001870716 | Rochaine Hussey | KSAN | Completed | Load_249723 | Constant Spring - 410 | Jul 31, 2026 9:18am | Jul 31, 2026 9:20am | Jul 31, 2026 1:00pm | Jul 31, 2026 1:04pm | Jul 31, 2026 1:04pm | Jul 31, 2026 2:39pm | Jul 31, 2026 2:40pm | Jul 31, 2026 2:40pm |  |  | Fair | No | Corrosion was found at the drop lead of the transformer which was causing low voltage , 25 kva transformer was isolated and clamps were changed , issue resolved 5 clamp used 122/117/239v
Non-Outage | J.E.26.07.35152 | C001870718 | Rochaine Hussey | KSAN | Completed | Load_241807 | Constant Spring - 410 | Jul 31, 2026 9:18am | Jul 31, 2026 9:21am | Jul 31, 2026 12:58pm | Jul 31, 2026 12:58pm | Jul 31, 2026 12:58pm | Jul 31, 2026 12:59pm | Jul 31, 2026 1:00pm | Jul 31, 2026 1:00pm |  |  | Fair | No | Unable to locate Customer was called multiple times
Non-Outage | J.E.26.07.36155 | C001870733 | Nicholas Dillon | St.Elizabeth | Completed | Load_291982 | Maggotty - 210 | Jul 31, 2026 9:18am | Jul 31, 2026 9:45am | Jul 31, 2026 10:53am | Jul 31, 2026 11:34am | Jul 31, 2026 12:04pm | Jul 31, 2026 12:04pm | Jul 31, 2026 12:05pm | Jul 31, 2026 12:05pm |  |  | Fair | Yes | Check and found corrosion at pole clean joint and use 2 one bolt clamp before I left voltage is 117 116 phase to phase 233
Non-Outage | J.E.26.07.37199 | C001870727 | Rochaine Hussey | KSAN | Completed | Load_244510 | Constant Spring - 410 | Jul 31, 2026 9:18am | Jul 31, 2026 9:20am | Jul 31, 2026 4:30pm | Jul 31, 2026 4:30pm | Jul 31, 2026 4:30pm | Jul 31, 2026 4:31pm | Jul 31, 2026 4:31pm | Jul 31, 2026 4:31pm |  |  | Fair | No | Customer was called multiple no answer Unable to locate
Non-Outage | J.E.26.07.38972 | C001870728 | Nicholas Dillon | Manchester | Completed | Load_302937 | Spur Tree - 210 | Jul 31, 2026 9:18am | Jul 31, 2026 9:45am | Jul 31, 2026 10:53am | Jul 31, 2026 1:04pm | Jul 31, 2026 1:12pm | Jul 31, 2026 1:12pm | Jul 31, 2026 2:08pm | Jul 31, 2026 2:08pm |  |  | Fair | No | Check and found corrosion at pole clean joint and use 1 one bolt clamp before I left voltage is 114 116 phase to phase 230
Non-Outage | J.E.26.07.39019 | C001870717 | Nicholas Dillon | Manchester | Completed | Load_302937 | Spur Tree - 210 | Jul 31, 2026 9:18am | Jul 31, 2026 9:45am | Jul 31, 2026 10:53am | Jul 31, 2026 2:08pm | Jul 31, 2026 3:31pm | Jul 31, 2026 3:31pm | Jul 31, 2026 3:32pm | Jul 31, 2026 3:32pm |  |  | Fair | Yes | Check and found corrosion at pole clean joint and use 2 one bolt clamp before I left voltage is 117 116 phase to phase 234
Non-Outage | J.E.26.07.05827 | C001870707 | Andrae Dawkins | St.James | Completed | Load_249900 | Bogue - 310 | Jul 31, 2026 9:17am | Jul 31, 2026 9:22am | Jul 31, 2026 10:20am | Jul 31, 2026 11:19am | Jul 31, 2026 11:19am | Jul 31, 2026 10:04am | Jul 31, 2026 11:21am | Jul 31, 2026 11:21am |  |  | Fair | No | Check and found ok customer said that they don’t have any issue there with the light
Non-Outage | J.E.26.07.06192 | C001870708 | Andrae Dawkins | St.James | Completed | Load_258690 | Bogue - 310 | Jul 31, 2026 9:17am | Jul 31, 2026 9:22am | Jul 31, 2026 3:33pm | Jul 31, 2026 3:33pm | Jul 31, 2026 3:33pm | Jul 31, 2026 3:23pm | Jul 31, 2026 3:34pm | Jul 31, 2026 3:34pm |  |  | Fair | No | Cannot locate customer unable to reach customer mobile
Non-Outage | J.E.26.07.06335 | C001870709 | Andrae Dawkins | St.James | Completed | Load_237885 | Queens Drive - 710 | Jul 31, 2026 9:17am | Jul 31, 2026 9:22am | Jul 31, 2026 2:18pm | Jul 31, 2026 2:18pm | Jul 31, 2026 3:10pm | Jul 31, 2026 1:03pm | Jul 31, 2026 3:13pm | Jul 31, 2026 3:13pm |  |  | Fair | No | Customer said the report was about a claim and someone already came a check now she waiting for them to reply
Non-Outage | J.E.26.07.06468 | C001870710 | Andrae Dawkins | St.James | Completed | Load_245438 | Queens Drive - 710 | Jul 31, 2026 9:17am | Jul 31, 2026 9:22am | Jul 31, 2026 10:17am | Jul 31, 2026 11:23am | Jul 31, 2026 11:39am | Jul 31, 2026 10:14am | Jul 31, 2026 11:41am | Jul 31, 2026 11:41am |  |  | Fair | No | Cannot locate customer unable to reach customer mobile
Non-Outage | J.E.26.07.34458 | C001870711 | Rochaine Hussey | KSAN | Completed | Load_264814 | Constant Spring - 410 | Jul 31, 2026 9:17am | Jul 31, 2026 9:20am | Jul 31, 2026 12:28pm | Jul 31, 2026 3:00pm | Jul 31, 2026 3:00pm | Jul 31, 2026 3:01pm | Jul 31, 2026 3:01pm | Jul 31, 2026 3:01pm | LeaningPole |  | Fair | No | Customer said issue was already resolved
Outage | J.E.26.07.39234 | C001870695 | Elvis Trowers | KSAS | Completed | Load_267829 | Duhaney - 310 | Jul 31, 2026 9:13am | Jul 31, 2026 9:13am | Jul 31, 2026 10:14am | Jul 31, 2026 10:15am | Jul 31, 2026 10:41am | Jul 31, 2026 10:47am | Jul 31, 2026 10:47am | Jul 31, 2026 10:47am |  |  | Fair | Yes | Premises found closed upon arrival and when customer was contacted he said that he or his wife isn’t home just now but at work, and won’t be home until after 3:00 PM.
Outage | J.E.26.07.39262 | C001870694 | Eric Williams | KSAN | Completed | Load_263587 | Washington Blvd - 610 | Jul 31, 2026 9:13am | Jul 31, 2026 11:12am | Jul 31, 2026 1:24pm | Jul 31, 2026 1:24pm | Jul 31, 2026 1:24pm | Jul 31, 2026 1:25pm | Jul 31, 2026 1:28pm | Jul 31, 2026 1:28pm |  |  | Fair | No | 1 Blown 30amps junction fuse and 1 3amps transformer fuse found and replace
Outage | J.E.26.07.39249 | C001870693 | Rusean Allen | KSAS | Completed | Load_238276 | Up Park Camp - 510 | Jul 31, 2026 9:11am | Jul 31, 2026 9:11am | Jul 31, 2026 10:35am | Jul 31, 2026 11:56am | Jul 31, 2026 12:43pm | Jul 31, 2026 12:47pm | Jul 31, 2026 12:47pm | Jul 31, 2026 12:47pm | BrokenWire |  | Fair | No | Broken secondary wire found, wire was spliced retention and reconnected.
Outage | J.E.26.07.39245 | C001870691 | Marlon Brown | Trelawny | Completed | Load_255143 | Greenwood - 110 | Jul 31, 2026 9:10am | Jul 31, 2026 3:22pm | Jul 31, 2026 3:35pm | Jul 31, 2026 3:35pm | Jul 31, 2026 4:14pm | Jul 31, 2026 4:44pm | Jul 31, 2026 4:45pm | Jul 31, 2026 4:45pm |  |  | Fair | No | Replaced service wire after hurricane Melissa damagesUse 10ft #6 triplex, 3 linkers & 3 pg clamps Voltage found noneVoltage leaving @ meter socket 104/108=212v
Outage | J.E.26.07.39264 | C001870692 | Dwayne Samuels | Trelawny | Completed | Load_292876 | Greenwood - 210 | Jul 31, 2026 9:10am | Jul 31, 2026 9:15am | Jul 31, 2026 9:25am | Jul 31, 2026 9:39am | Jul 31, 2026 10:25am | Jul 31, 2026 11:02am | Jul 31, 2026 11:02am | Jul 31, 2026 11:02am |  |  | Fair | No | Patrol secondary to find 1 tripped 10 kiva transformer complete line patrol before resetting tripped 10amp transformer at same
Non-Outage | J.E.26.07.25188 | C001870690 | Edward Royal | KSAN | Completed | Load_257312 | Washington Blvd - 310 | Jul 31, 2026 9:08am | Jul 31, 2026 9:08am | Jul 31, 2026 12:45pm | Jul 31, 2026 12:45pm | Jul 31, 2026 12:45pm | Jul 31, 2026 12:55pm | Jul 31, 2026 1:01pm | Jul 31, 2026 1:01pm |  |  | Fair | No | Defective meter need to be change reffered to field service
Non-Outage | J.E.26.07.27819 | C001870689 | Edward Royal | KSAN | Completed | Load_265970 | Washington Blvd - 310 | Jul 31, 2026 9:08am | Jul 31, 2026 9:08am | Jul 31, 2026 1:16pm | Jul 31, 2026 1:16pm | Jul 31, 2026 1:16pm | Jul 31, 2026 1:17pm | Jul 31, 2026 1:17pm | Jul 31, 2026 1:17pm |  |  | Fair | No | When contacted customer said that no one is at home
Non-Outage | J.E.26.07.30536 | C001870688 | Edward Royal | KSAN | Completed | Load_246286 | Washington Blvd - 310 | Jul 31, 2026 9:08am | Jul 31, 2026 9:08am | Jul 31, 2026 1:46pm | Jul 31, 2026 1:46pm | Jul 31, 2026 1:46pm | Jul 31, 2026 1:46pm | Jul 31, 2026 1:46pm | Jul 31, 2026 1:46pm |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.07.37825 | C001870687 | Edward Royal | KSAN | Completed | Load_265180 | Washington Blvd - 310 | Jul 31, 2026 9:08am | Jul 31, 2026 9:08am | Jul 31, 2026 1:38pm | Jul 31, 2026 1:38pm | Jul 31, 2026 1:38pm | Jul 31, 2026 1:43pm | Jul 31, 2026 1:43pm | Jul 31, 2026 1:43pm |  |  | Fair | No | En box need to be check reffered to field service box #EN 04722pole#0025240
Outage | J.E.26.07.39261 | C001870686 | Michael Christian | St.James | Completed | Load_254506 | Queens Drive - 310 | Jul 31, 2026 9:06am | Jul 31, 2026 10:18am | Jul 31, 2026 11:44am | Jul 31, 2026 11:44am | Jul 31, 2026 11:44am | Jul 31, 2026 11:45am | Jul 31, 2026 11:46am | Jul 31, 2026 11:46am |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.07.38475 | C001870681 | Hopeton Henry | St.Thomas | Completed | Load_248874 | Good Year - 210 | Jul 31, 2026 9:05am | Jul 31, 2026 9:06am | Jul 31, 2026 9:27am | Jul 31, 2026 2:12pm | Jul 31, 2026 2:12pm | Jul 31, 2026 2:32pm | Jul 31, 2026 2:34pm | Jul 31, 2026 2:34pm |  |  | Fair | No | Found corrosion use 120-119-240volts
Non-Outage | J.E.26.07.38504 | C001870682 | Hopeton Henry | St.Thomas | Completed | Load_243194 | Good Year - 210 | Jul 31, 2026 9:05am | Jul 31, 2026 9:06am | Jul 31, 2026 9:27am | Jul 31, 2026 9:30am | Jul 31, 2026 10:25am | Jul 31, 2026 10:52am | Jul 31, 2026 10:54am | Jul 31, 2026 10:54am | LeaningPole |  | Fair | No | No leaning pole found , customer supply as been restored yesterday
Non-Outage | J.E.26.07.38667 | C001870683 | Hopeton Henry | St.Thomas | Completed | Load_266155 | Good Year - 210 | Jul 31, 2026 9:05am | Jul 31, 2026 9:06am | Jul 31, 2026 9:27am | Jul 31, 2026 6:53pm | Jul 31, 2026 8:52pm | Aug 1, 2026 12:09pm | Aug 1, 2026 12:10pm | Aug 1, 2026 12:10pm |  |  | Fair | No | Check pole and pot head no problem found 113-111-224 volts
Non-Outage | J.E.26.07.39084 | C001870685 | Hopeton Henry | St.Thomas | Completed | Load_252161 | Good Year - 110 | Jul 31, 2026 9:05am | Jul 31, 2026 9:06am | Jul 31, 2026 9:27am | Jul 31, 2026 10:54am | Jul 31, 2026 11:22am | Jul 31, 2026 11:46am | Jul 31, 2026 11:46am | Jul 31, 2026 11:46am |  |  | Fair | No | Found ok
Outage | J.E.26.07.39251 | C001870676 | Stephen Taylor | St.Thomas | Completed | Load_265545 | Lysson - 410 | Jul 31, 2026 9:02am | Jul 31, 2026 9:02am | Jul 31, 2026 10:00am | Jul 31, 2026 10:00am | Jul 31, 2026 10:07am | Jul 31, 2026 10:07am | Jul 31, 2026 10:09am | Jul 31, 2026 10:09am | BrokenWire |  | Fair | No | Patrol the area power is in the area a lot of call to the customer no one answered the phone
Non-Outage | J.E.26.07.39248 | C001870674 | Antony Levy | KSAS | Completed | Load_267829 | Duhaney - 310 | Jul 31, 2026 9:01am | Jul 31, 2026 3:58pm | Jul 31, 2026 6:03pm | Jul 31, 2026 6:03pm | Jul 31, 2026 6:50pm | Jul 31, 2026 7:01pm | Jul 31, 2026 7:01pm | Jul 31, 2026 7:01pm |  |  | Fair | No | Premises locked
Outage | J.E.26.07.39071 | C001870673 | Hartley Chin | Clarendon | Completed | Load_253290 | Parnassus - 310 | Jul 31, 2026 9:01am | Aug 1, 2026 7:20am | Aug 1, 2026 11:12am | Aug 1, 2026 11:13am | Aug 1, 2026 11:46am | Aug 1, 2026 12:14pm | Aug 1, 2026 12:17pm | Aug 1, 2026 12:17pm |  |  | Fair | No | Premisis not found. Unable to contact customer with the number provided.
Non-Outage | J.E.26.07.39260 | C001870671 | Locksley Allen | St.Mary | Completed | Load_239016 | Highgate - 210 | Jul 31, 2026 8:59am | Jul 31, 2026 8:59am | Jul 31, 2026 10:10am | Jul 31, 2026 10:51am | Jul 31, 2026 10:52am | Jul 31, 2026 10:56am | Jul 31, 2026 10:53am | Jul 31, 2026 10:53am |  |  | Fair | No | Need better direction and phone number
Non-Outage | J.E.26.07.38440 | C001870666 | Odeanie Davis | KSAS | Completed | Load_248538 | Rockfort - 210 | Jul 31, 2026 8:56am | Jul 31, 2026 8:56am | Jul 31, 2026 9:00am | Jul 31, 2026 11:05am | Jul 31, 2026 11:08am | Jul 31, 2026 11:25am | Jul 31, 2026 11:32am | Jul 31, 2026 11:32am |  |  | Fair | No | 115v/118v & 234v at location, customer stated that their electrician resolved issue.
Non-Outage | J.E.26.07.38511 | C001870667 | Odeanie Davis | KSAS | Completed | Load_261603 | Rockfort - 410 | Jul 31, 2026 8:56am | Jul 31, 2026 8:56am | Jul 31, 2026 9:00am | Jul 31, 2026 9:04am | Jul 31, 2026 9:15am | Jul 31, 2026 10:00am | Jul 31, 2026 9:57am | Jul 31, 2026 9:57am |  |  | Fair | No | 101v/126v at arrival, open circuit at pothead corrected, 2 penn union & 1 one bolt clamp, 108v/118v & 227v after correction
Outage | J.E.26.07.39255 | C001870668 | Hartley Chin | Clarendon | Completed | Load_1003527 | Parnassus - 310 | Jul 31, 2026 8:56am | Aug 1, 2026 7:20am | Aug 1, 2026 8:12am | Aug 1, 2026 9:20am | Aug 1, 2026 10:01am | Aug 1, 2026 10:05am | Aug 1, 2026 10:06am | Aug 1, 2026 10:06am | BrokenWire |  | Fair | No | Found okay … customer stated issue was resolved last night …
Non-Outage | J.E.26.07.36411 | C001870665 | Odeanie Davis | KSAS | Completed | Load_237713 | Rockfort - 410 | Jul 31, 2026 8:55am | Jul 31, 2026 8:56am | Jul 31, 2026 9:00am | Jul 31, 2026 10:04am | Jul 31, 2026 10:06am | Jul 31, 2026 11:05am | Jul 31, 2026 11:05am | Jul 31, 2026 11:05am |  |  | Fair | No | 118v/118v arrival arrival, customer defective meter socket, customer was advised to contact their electrician, open circuit at pothead and secondary corrected, 3 one bolt clamps and 1 penn union, 118v/118v &237v after correction.
Non-Outage | J.E.26.07.38579 | C001870663 | Odaine Johnson | Clarendon | Completed | Load_569771 | Parnassus - 210 | Jul 31, 2026 8:55am | Jul 31, 2026 8:55am | Jul 31, 2026 9:29am | Jul 31, 2026 10:43am | Jul 31, 2026 12:15pm | Jul 31, 2026 12:15pm | Jul 31, 2026 12:15pm | Jul 31, 2026 12:15pm |  |  | Fair | No | Contacted customer and customer stated that the issue was resolved already
Non-Outage | J.E.26.07.39057 | C001870660 | Odaine Johnson | Clarendon | Completed | Load_265906 | May Pen - 210 | Jul 31, 2026 8:55am | Jul 31, 2026 8:55am | Jul 31, 2026 9:29am | Jul 31, 2026 10:23am | Jul 31, 2026 10:23am | Jul 31, 2026 10:23am | Jul 31, 2026 10:23am | Jul 31, 2026 10:23am |  |  | Fair | No | Contacted customer and customer stated that the issue was resolved already
Non-Outage | J.E.26.07.39064 | C001870661 | Neville Spencer | Clarendon | Completed | Load_301251 | Monymusk - 410 | Jul 31, 2026 8:55am | Jul 31, 2026 9:55am | Jul 31, 2026 12:00pm | Jul 31, 2026 12:01pm | Jul 31, 2026 12:50pm | Jul 31, 2026 4:34pm | Jul 31, 2026 4:35pm | Jul 31, 2026 4:35pm |  |  | Fair | No | Patrolled 12 kv line nothing found .
Non-Outage | J.E.26.07.39197 | C001870658 | Odaine Johnson | Clarendon | Completed | Load_238965 | Parnassus - 210 | Jul 31, 2026 8:55am | Jul 31, 2026 8:55am | Jul 31, 2026 9:29am | Jul 31, 2026 1:12pm | Jul 31, 2026 1:34pm | Jul 31, 2026 1:35pm | Jul 31, 2026 1:35pm | Jul 31, 2026 1:35pm |  |  | Fair | No | Premises found okay voltage reading 109/110/220 volts
Non-Outage | J.E.26.07.39240 | C001870659 | Odaine Johnson | Clarendon | Completed | Load_351851 | May Pen - 210 | Jul 31, 2026 8:55am | Jul 31, 2026 8:55am | Jul 31, 2026 9:29am | Jul 31, 2026 12:18pm | Jul 31, 2026 1:08pm | Jul 31, 2026 1:10pm | Jul 31, 2026 1:11pm | Jul 31, 2026 1:11pm |  |  | Fair | No | Burn off phase found at pole remade connection using 1 one bolt clamp voltage reading 119/119/239 volts
Outage | J.E.26.07.39236 | C001870648 | Kenroy Dale | Manchester | Completed | Load_557412 | Spur Tree - 310 | Jul 31, 2026 8:48am | Jul 31, 2026 8:49am | Jul 31, 2026 1:01pm | Jul 31, 2026 1:01pm | Jul 31, 2026 1:59pm | Jul 31, 2026 2:26pm | Jul 31, 2026 2:29pm | Jul 31, 2026 2:29pm |  |  | Fair | No | Customer has internal problems, customer was advised to get an electrician to check the premises. Voltage reading 110/112/222
Non-Outage | J.E.26.07.39024 | C001870639 | Andre Williams | Trelawny | Completed | Load_302572 | Martha Brae - 110 | Jul 31, 2026 8:39am | Jul 31, 2026 8:40am | Jul 31, 2026 8:50am | Jul 31, 2026 9:24am | Jul 31, 2026 9:24am | Jul 31, 2026 9:31am | Jul 31, 2026 9:31am | Jul 31, 2026 9:31am |  |  | Fair | No | Customer with supply, confirm by customer appliances working ok.
Non-Outage | J.E.26.07.39137 | C001870640 | Fredrick Hamilton | null | Completed | null | null | Jul 31, 2026 8:39am | Jul 31, 2026 8:40am | Jul 31, 2026 8:47am | Jul 31, 2026 8:57am | Jul 31, 2026 8:57am | Jul 31, 2026 8:59am | Jul 31, 2026 8:59am | Jul 31, 2026 8:59am | LeaningPole |  | Fair | No | Please assign to emergency
Outage | J.E.26.07.39238 | C001870642 | Jowayne Newmans | Portland | Completed | Load_263585 | Port Antonio - 410 | Jul 31, 2026 8:39am | Jul 31, 2026 8:39am | Jul 31, 2026 11:23am | Jul 31, 2026 11:23am | Jul 31, 2026 11:53am | Jul 31, 2026 12:01pm | Jul 31, 2026 12:01pm | Jul 31, 2026 12:01pm |  |  | Fair | No | Customer stated that they were without supply however did a voltage test at meter socket voltage reading was 118v, 119v, 238v. Advise customer to get an electrician to check their system.
Non-Outage | J.E.26.07.38517 | C001870637 | Fredrick Hamilton | KSAS | Completed | Load_258580 | Duhaney - 310 | Jul 31, 2026 8:38am | Jul 31, 2026 8:39am | Jul 31, 2026 8:47am | Jul 31, 2026 10:33am | Jul 31, 2026 10:37am | Jul 31, 2026 10:39am | Jul 31, 2026 10:39am | Jul 31, 2026 10:39am |  |  | Fair | No | Customer contacted and stated power was restored fully yesterday Premises is ok
Non-Outage | J.E.26.07.39051 | C001870638 | Fredrick Hamilton | KSAS | Completed | Load_254408 | Duhaney - 310 | Jul 31, 2026 8:38am | Jul 31, 2026 8:39am | Jul 31, 2026 8:47am | Jul 31, 2026 9:28am | Jul 31, 2026 9:52am | Jul 31, 2026 10:18am | Jul 31, 2026 10:18am | Jul 31, 2026 10:18am |  |  | Fair | No | Customer defect detected at premises customer advised 236v/119v/118v obtained Corrosion detected at customer pothead
Non-Outage | J.E.26.07.38576 | C001870636 | Fredrick Hamilton | KSAN | Completed | Load_252180 | Constant Spring - 210 | Jul 31, 2026 8:37am | Jul 31, 2026 8:39am | Jul 31, 2026 8:47am | Jul 31, 2026 10:42am | Jul 31, 2026 10:48am | Jul 31, 2026 11:17am | Jul 31, 2026 11:17am | Jul 31, 2026 11:17am |  |  | Fair | No | Corrosion detected at pothead same was corrected 3 penunion usedPremises is now ok
Non-Outage | J.E.26.07.37685 | C001870629 | Edward Royal | KSAN | Completed | Load_268605 | Washington Blvd - 710 | Jul 31, 2026 8:31am | Jul 31, 2026 8:31am | Jul 31, 2026 1:46pm | Jul 31, 2026 1:46pm | Jul 31, 2026 1:46pm | Jul 31, 2026 1:47pm | Jul 31, 2026 1:47pm | Jul 31, 2026 1:47pm | BrokenWire |  | Fair | No | Premises found ok customer was referring about 3rd party cable
Non-Outage | J.E.26.07.38384 | C001870628 | Edward Royal | KSAS | Completed | Load_263810 | Greenwich - 710 | Jul 31, 2026 8:31am | Jul 31, 2026 8:31am | Jul 31, 2026 9:10am | Jul 31, 2026 12:38pm | Jul 31, 2026 12:39pm | Jul 31, 2026 12:39pm | Jul 31, 2026 12:39pm | Jul 31, 2026 12:39pm |  |  | Fair | No | Meter not responding meter need to be check reffered to field service
Non-Outage | J.E.26.07.38461 | C001870627 | Edward Royal | KSAN | Completed | Load_253996 | Washington Blvd - 710 | Jul 31, 2026 8:31am | Jul 31, 2026 8:31am | Jul 31, 2026 11:28am | Jul 31, 2026 11:28am | Jul 31, 2026 11:28am | Jul 31, 2026 12:05pm | Jul 31, 2026 12:05pm | Jul 31, 2026 12:05pm |  |  | Fair | No | Meter not responding meter need to be check reffered to field service pole #0064837
Non-Outage | J.E.26.07.38669 | C001870626 | Edward Royal | KSAN | Completed | Load_243339 | Washington Blvd - 710 | Jul 31, 2026 8:30am | Jul 31, 2026 8:31am | Jul 31, 2026 8:59am | Jul 31, 2026 8:59am | Jul 31, 2026 8:59am | Jul 31, 2026 9:00am | Jul 31, 2026 9:00am | Jul 31, 2026 9:00am |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.07.38955 | C001870616 | Edward Royal | KSAN | Completed | Load_263228 | Washington Blvd - 710 | Jul 31, 2026 8:24am | Jul 31, 2026 8:25am | Jul 31, 2026 8:55am | Jul 31, 2026 8:55am | Jul 31, 2026 8:55am | Jul 31, 2026 8:57am | Jul 31, 2026 8:58am | Jul 31, 2026 8:58am |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.07.39141 | C001870615 | Rusean Allen | KSAS | Completed | Load_255768 | Hunts Bay - 310 | Jul 31, 2026 8:24am | Jul 31, 2026 8:28am | Jul 31, 2026 1:26pm | Jul 31, 2026 1:26pm | Jul 31, 2026 1:33pm | Jul 31, 2026 1:34pm | Jul 31, 2026 1:34pm | Jul 31, 2026 1:34pm |  |  | Fair | No | Premises found locked
Non-Outage | J.E.26.07.37611 | C001870614 | Milton Charlton | KSAN | Completed | Load_254899 | Hope - 410 | Jul 31, 2026 8:23am | Jul 31, 2026 8:24am | Jul 31, 2026 8:57am | Jul 31, 2026 8:57am | Jul 31, 2026 10:21am | Jul 31, 2026 10:20am | Jul 31, 2026 10:23am | Jul 31, 2026 10:23am |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Non-Outage | J.E.26.07.39203 | C001870612 | Christopher Edwards | KSAN | Completed | Load_243251 | Constant Spring - 410 | Jul 31, 2026 8:22am | Jul 31, 2026 8:24am | Jul 31, 2026 9:36am | Jul 31, 2026 10:09am | Jul 31, 2026 10:09am | Jul 31, 2026 11:38am | Jul 31, 2026 11:42am | Jul 31, 2026 11:42am |  | Y | Fair | No | Clear bamboo off secondary wires That was causing wire to bang
Outage | J.E.26.07.39212 | C001870610 | Michael Christian | St.James | Completed | Load_248368 | Queens Drive - 310 | Jul 31, 2026 8:15am | Jul 31, 2026 8:16am | Jul 31, 2026 11:46am | Jul 31, 2026 11:46am | Jul 31, 2026 11:46am | Jul 31, 2026 11:46am | Jul 31, 2026 11:47am | Jul 31, 2026 11:47am |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.38530 | C001870609 | Michael Christian | St.James | Completed | Load_302531 | Queens Drive - 310 | Jul 31, 2026 8:14am | Jul 31, 2026 8:16am | Jul 31, 2026 11:03am | Jul 31, 2026 11:03am | Jul 31, 2026 11:36am | Jul 31, 2026 11:44am | Jul 31, 2026 11:44am | Jul 31, 2026 11:44am |  |  | Fair | No | Found 1 15 kava out replace 1 2 amp in no pole #
Outage | J.E.26.07.38690 | C001870607 | Michael Christian | St.James | Completed | Load_302104 | Queens Drive - 710 | Jul 31, 2026 8:14am | Jul 31, 2026 8:16am | Jul 31, 2026 11:47am | Jul 31, 2026 11:47am | Jul 31, 2026 12:28pm | Jul 31, 2026 1:04pm | Jul 31, 2026 1:04pm | Jul 31, 2026 1:04pm |  |  | Fair | No | Found customer disconnection and found 2 defective pole and regularly cause customer not to connections and illegal connections send to field service
Non-Outage | J.E.26.07.20509 | C001870604 | Royston Montague | St.Catherine | Completed | Load_1001612 | Tredegar - 310 | Jul 31, 2026 8:10am | Jul 31, 2026 8:10am | Jul 31, 2026 8:26am | Jul 31, 2026 2:14pm | Jul 31, 2026 3:52pm | Jul 31, 2026 3:52pm | Jul 31, 2026 3:52pm | Jul 31, 2026 3:52pm |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.07.36882 | C001870606 | Cliton Henry | St.Mary | Completed | Load_258469 | Oracabessa - 210 | Jul 31, 2026 8:10am | Jul 31, 2026 8:10am | Jul 31, 2026 9:09am | Jul 31, 2026 9:09am | Jul 31, 2026 10:31am | Jul 31, 2026 10:36am | Jul 31, 2026 10:38am | Jul 31, 2026 10:38am | LowHangingWires |  | Fair | No | Two broken 30-c6 wood pole found with 2/0 triplex secondary conductors hang low. Kindly refer to St.Mary Operations for these replacement.
Non-Outage | J.E.26.07.38563 | C001870605 | Neckell Ormsby | St.Mary | Completed | Load_247233 | Highgate -110 | Jul 31, 2026 8:10am | Jul 31, 2026 8:10am | Jul 31, 2026 10:10am | Jul 31, 2026 10:10am | Jul 31, 2026 10:44am | Jul 31, 2026 12:00am | Jul 31, 2026 11:07am | Jul 31, 2026 11:07am | Fire |  | Fair | No | The issue was resolved yesterday by another team
Non-Outage | J.E.26.07.24269 | C001870600 | Royston Montague | St.Catherine | Completed | Load_253958 | Tredegar - 210 | Jul 31, 2026 8:09am | Jul 31, 2026 8:10am | Jul 31, 2026 8:26am | Jul 31, 2026 8:55am | Jul 31, 2026 10:22am | Jul 31, 2026 11:40am | Jul 31, 2026 11:40am | Jul 31, 2026 11:40am |  |  | Fair | No | Faulty jumper joints. 25kva transformer fuse open to do repair. Voltage found 210v 103v 105v voltage after job completion are 219v 108v 109v
Non-Outage | J.E.26.07.25602 | C001870601 | Royston Montague | St.Catherine | Completed | Load_262367 | Tredegar - 210 | Jul 31, 2026 8:09am | Jul 31, 2026 8:10am | Jul 31, 2026 8:26am | Jul 31, 2026 12:45pm | Jul 31, 2026 2:03pm | Jul 31, 2026 2:12pm | Jul 31, 2026 2:12pm | Jul 31, 2026 2:12pm |  |  | Fair | No | Customer issue is with an over growth tree at premises. Same seeking assistance to cut tree. Please inform maintenance department thanks.
Non-Outage | J.E.26.07.39022 | C001870598 | Locksley Allen | St.Mary | Completed | Load_264570 | Highgate - 210 | Jul 31, 2026 8:07am | Jul 31, 2026 8:07am | Jul 31, 2026 9:14am | Jul 31, 2026 9:19am | Jul 31, 2026 9:19am | Jul 31, 2026 10:12am | Jul 31, 2026 10:09am | Jul 31, 2026 10:09am |  |  | Fair | No | Neutral service wire at the pole burst,connect wire. Voltage at meter socket phase to phase 216v. Phase to neutral 108&109vMeter left working okay
Non-Outage | J.E.26.07.39026 | C001870599 | Locksley Allen | St.Mary | Completed | Load_258412 | Oracabessa - 210 | Jul 31, 2026 8:07am | Jul 31, 2026 8:07am | Jul 31, 2026 1:10pm | Jul 31, 2026 2:04pm | Jul 31, 2026 2:06pm | Jul 31, 2026 2:11pm | Jul 31, 2026 2:09pm | Jul 31, 2026 2:09pm |  |  | Fair | No | Customer said JPS corrected the problem yesterday Voltage at meter socket phase to phase 238v. Phase to neutral 116&119vMeter working okay
Non-Outage | J.E.26.07.37883 | C001870596 | Locksley Allen | St.Mary | Completed | Load_254255 | Oracabessa - 210 | Jul 31, 2026 8:06am | Jul 31, 2026 8:07am | Jul 31, 2026 10:54am | Jul 31, 2026 12:28pm | Jul 31, 2026 12:28pm | Jul 31, 2026 1:05pm | Jul 31, 2026 1:08pm | Jul 31, 2026 1:08pm |  |  | Fair | No | No low voltage problem found at premises. Clean up connectors at pole Voltage at meter socket phase to phase 240v. Phase to neutral 120&120vMeter left working
Non-Outage | J.E.26.07.37889 | C001870597 | Locksley Allen | St.Mary | Completed | Load_254708 | Oracabessa - 210 | Jul 31, 2026 8:06am | Jul 31, 2026 8:07am | Jul 31, 2026 2:09pm | Jul 31, 2026 2:25pm | Jul 31, 2026 2:25pm | Jul 31, 2026 2:32pm | Jul 31, 2026 2:30pm | Jul 31, 2026 2:30pm |  |  | Fair | No | No on and off problem found at premises. Since light comes back yesterday,she doesn’t have any problem. Voltage at meter socket phase to phase 220v.Phase to neutral 109&113vMeter working okay
Non-Outage | J.E.26.07.38984 | C001870593 | Wan Carlos Scarlett | St.Catherine | Completed | Load_569977 | Twickenham - 210 | Jul 31, 2026 8:04am | Jul 31, 2026 8:06am | Jul 31, 2026 2:25pm | Jul 31, 2026 2:25pm | Jul 31, 2026 3:04pm | Jul 31, 2026 3:23pm | Jul 31, 2026 3:28pm | Jul 31, 2026 3:28pm | BrokenPole |  | Fair | No | Found customer private meter pole defective pole broken advised customer to contact a licensed electrician to fix the problem isolated customer service wire
Non-Outage | J.E.26.07.36844 | C001870591 | Error Coore | Manchester | Completed | Load_244922 | Porus - 310 | Jul 31, 2026 8:03am | Jul 31, 2026 8:04am | Jul 31, 2026 11:22am | Jul 31, 2026 11:22am | Jul 31, 2026 11:57am | Jul 31, 2026 12:16pm | Jul 31, 2026 12:22pm | Jul 31, 2026 12:22pm |  |  | Fair | No | Premises found ok customer have internal problem voltage reading 115/115/230 volts
Non-Outage | J.E.26.07.37115 | C001870590 | Error Coore | Manchester | Completed | Load_240786 | Kendal - 310 | Jul 31, 2026 8:03am | Jul 31, 2026 8:04am | Jul 31, 2026 12:24pm | Jul 31, 2026 12:24pm | Jul 31, 2026 1:19pm | Jul 31, 2026 1:30pm | Jul 31, 2026 1:31pm | Jul 31, 2026 1:31pm |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.38571 | C001870584 | Error Coore | Manchester | Completed | Load_266810 | Spur Tree - 310 | Jul 31, 2026 8:03am | Jul 31, 2026 8:04am | Jul 31, 2026 8:21am | Jul 31, 2026 8:22am | Jul 31, 2026 8:36am | Jul 31, 2026 11:18am | Jul 31, 2026 11:21am | Jul 31, 2026 11:21am |  |  | Fair | No | Found customer with wrap connection at pothead remade wrap connection using 9 service sleeve however secondary line and pole need bushing customer have light inside of the premises but the meter do not have any display
Non-Outage | J.E.26.07.38751 | C001870592 | Orville Lee | St.Catherine | Completed | Load_248053 | Twickenham - 210 | Jul 31, 2026 8:03am | Jul 31, 2026 8:04am | Jul 31, 2026 8:21am | Jul 31, 2026 2:31pm | Jul 31, 2026 2:59pm | Jul 31, 2026 3:41pm | Jul 31, 2026 3:42pm | Jul 31, 2026 3:42pm | Fire |  | Fair | No | Premises found ok upon arrival 117v118v220v
Non-Outage | J.E.26.07.38784 | C001870589 | Orville Lee | St.Catherine | Completed | Load_247799 | Twickenham - 210 | Jul 31, 2026 8:03am | Jul 31, 2026 8:04am | Jul 31, 2026 8:21am | Jul 31, 2026 9:48am | Jul 31, 2026 10:02am | Jul 31, 2026 10:08am | Jul 31, 2026 10:09am | Jul 31, 2026 10:09am | BrokenWire |  | Fair | No | Customer was reporting low hanging telephone wireIncorrect procedure
Non-Outage | J.E.26.07.39028 | C001870588 | Nickolas Rodriques | Portmore | Completed | Load_268319 | Naggo Head - 610 | Jul 31, 2026 8:03am | Jul 31, 2026 8:06am | Jul 31, 2026 4:50pm | Jul 31, 2026 4:50pm | Jul 31, 2026 4:56pm | Jul 31, 2026 5:14pm | Jul 31, 2026 5:17pm | Jul 31, 2026 5:17pm | Fire |  | Fair | No | Checked and found customer service wire phase and neutral broken. Repaired by splice and re-tension wire using one service sleeve and two one-bolt clamps. Current reading (120-118-238). Also, no fire was seen upon arrival.
Outage | J.E.26.07.39217 | C001870585 | Dean Smith | St.James | Completed | Load_251941 | Bogue - 510 | Jul 31, 2026 8:03am | Jul 31, 2026 8:08am | Jul 31, 2026 10:12am | Jul 31, 2026 10:12am | Jul 31, 2026 10:12am | Jul 31, 2026 10:12am | Jul 31, 2026 10:13am | Jul 31, 2026 10:13am |  |  | Fair | No | Area was restored
Non-Outage | J.E.26.07.34676 | C001870582 | Dwain Samuels | Westmoreland | Completed | Load_259282 | Paradise - 210 | Jul 31, 2026 8:02am | Jul 31, 2026 8:02am | Jul 31, 2026 8:31am | Jul 31, 2026 9:13am | Jul 31, 2026 9:28am | Jul 31, 2026 9:47am | Jul 31, 2026 9:48am | Jul 31, 2026 9:48am |  |  | Fair | No | Corrosion Found at 3 wire pole. Voltage check 108-103-211. Corrosion clear use 3 one bolt clamp. Voltage check 121-120-241
Non-Outage | J.E.26.07.35760 | C001870578 | Dwain Samuels | Westmoreland | Completed | Load_292200 | Paradise - 110 | Jul 31, 2026 8:01am | Jul 31, 2026 8:02am | Jul 31, 2026 8:31am | Jul 31, 2026 9:49am | Jul 31, 2026 9:49am | Jul 31, 2026 9:50am | Jul 31, 2026 9:51am | Jul 31, 2026 9:51am |  |  | Fair | No | Area affected by low voltage due to transformer failure leaking oil. Needs urgent attention
Non-Outage | J.E.26.07.35828 | C001870576 | Dwain Samuels | Westmoreland | Completed | Load_260662 | Paradise - 210 | Jul 31, 2026 8:01am | Jul 31, 2026 8:02am | Jul 31, 2026 8:31am | Jul 31, 2026 11:36am | Jul 31, 2026 11:36am | Jul 31, 2026 11:37am | Jul 31, 2026 11:37am | Jul 31, 2026 11:37am |  |  | Fair | No | Called customer said supply was restored
Non-Outage | J.E.26.07.36157 | C001870574 | Dwain Samuels | Westmoreland | Completed | Load_251332 | Paradise - 210 | Jul 31, 2026 8:01am | Jul 31, 2026 8:02am | Jul 31, 2026 8:31am | Jul 31, 2026 11:42am | Jul 31, 2026 12:10pm | Jul 31, 2026 1:14pm | Jul 31, 2026 1:17pm | Jul 31, 2026 1:17pm |  |  | Fair | No | Corrosion found at 3 wire pole. Voltage check 105-111-216. Corrosion clear use 3 one bolt clamp. Voltage check 112-113-225
Non-Outage | J.E.26.07.36429 | C001870572 | Dwain Samuels | Westmoreland | Completed | Load_242624 | Paradise - 110 | Jul 31, 2026 8:01am | Jul 31, 2026 8:02am | Jul 31, 2026 8:31am | Jul 31, 2026 3:03pm | Jul 31, 2026 3:03pm | Jul 31, 2026 3:32pm | Jul 31, 2026 3:34pm | Jul 31, 2026 3:34pm |  |  | Fair | No | Found working okay. Voltage check 119-118-237
Non-Outage | J.E.26.07.38159 | C001870580 | Milton Charlton | KSAN | Completed | Load_255111 | Hope - 510 | Jul 31, 2026 8:01am | Jul 31, 2026 8:03am | Jul 31, 2026 12:12pm | Jul 31, 2026 12:13pm | Jul 31, 2026 12:35pm | Jul 31, 2026 12:40pm | Jul 31, 2026 12:39pm | Jul 31, 2026 12:39pm |  |  | Fair | No | Customer service wire #6 triplex phase corroded at pothead. Repair using one 1- bolt clamp. Readings at pothead 112-114-226. A lot of illegal connections connect to customer pothead customer problems.refer to R.D.P
Non-Outage | J.E.26.07.38282 | C001870577 | Milton Charlton | KSAN | Completed | Load_245385 | Hope - 410 | Jul 31, 2026 8:01am | Jul 31, 2026 8:03am | Jul 31, 2026 2:01pm | Jul 31, 2026 2:01pm | Jul 31, 2026 5:12pm | Jul 31, 2026 5:00pm | Jul 31, 2026 5:13pm | Jul 31, 2026 5:13pm |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Non-Outage | J.E.26.07.38509 | C001870575 | Milton Charlton | KSAN | Completed | Load_261550 | Hope - 510 | Jul 31, 2026 8:01am | Jul 31, 2026 8:03am | Jul 31, 2026 12:40pm | Jul 31, 2026 1:36pm | Jul 31, 2026 1:36pm | Jul 31, 2026 1:35pm | Jul 31, 2026 1:38pm | Jul 31, 2026 1:38pm |  |  | Fair | No | Call related to call at Craig’s Hill District.
Non-Outage | J.E.26.07.38961 | C001870573 | Milton Charlton | KSAN | Completed | Load_261550 | Hope - 510 | Jul 31, 2026 8:01am | Jul 31, 2026 8:03am | Jul 31, 2026 9:23am | Jul 31, 2026 10:23am | Jul 31, 2026 11:14am | Jul 31, 2026 12:05pm | Jul 31, 2026 12:09pm | Jul 31, 2026 12:09pm |  |  | Fair | No | Isolate 25 kva transformer at pole # 0112880 and repair broken open wire secondary phase. Repair using three 1- bolt clamps, one #2 preform and 20ft #2AA conductor. And reclosed transformer switch.
Non-Outage | J.E.26.07.36802 | C001870570 | Dwain Samuels | Westmoreland | Completed | Load_268696 | Paradise - 210 | Jul 31, 2026 8:00am | Jul 31, 2026 8:02am | Jul 31, 2026 8:31am | Jul 31, 2026 11:15am | Jul 31, 2026 11:15am | Jul 31, 2026 11:18am | Jul 31, 2026 11:20am | Jul 31, 2026 11:20am |  |  | Fair | No | In house team onsite. Dispatch error
Non-Outage | J.E.26.07.38444 | C001870569 | Oshane Warren | Westmoreland | Completed | Load_246713 | Paradise - 110 | Jul 31, 2026 8:00am | Jul 31, 2026 10:15am | Jul 31, 2026 11:04am | Jul 31, 2026 11:04am | Jul 31, 2026 1:40pm | Jul 31, 2026 2:15pm | Jul 31, 2026 2:19pm | Jul 31, 2026 2:19pm |  |  | Fair | No | Splice and reconnect back conductor used 2 pg clamps
Non-Outage | J.E.26.07.39032 | C001870571 | Milton Charlton | KSAN | Completed | Load_261550 | Hope - 510 | Jul 31, 2026 8:00am | Jul 31, 2026 8:04am | Jul 31, 2026 12:40pm | Jul 31, 2026 12:40pm | Jul 31, 2026 1:34pm | Jul 31, 2026 1:35pm | Jul 31, 2026 1:36pm | Jul 31, 2026 1:36pm |  |  | Fair | No | Call related to call at Craig’s Hill District.
Non-Outage | J.E.26.07.39135 | C001870566 | Dwain Samuels | Westmoreland | Completed | Load_256472 | Paradise - 110 | Jul 31, 2026 8:00am | Jul 31, 2026 8:02am | Jul 31, 2026 8:31am | Jul 31, 2026 1:52pm | Jul 31, 2026 2:38pm | Jul 31, 2026 2:44pm | Jul 31, 2026 2:45pm | Jul 31, 2026 2:45pm |  |  | Fair | No | Corrosion found at 3 wire pole . Voltage check 110-90-200. Corrosion clear use 2 one bolt clamp. Voltage check 110-111-221
Non-Outage | J.E.26.07.39173 | C001870568 | Milton Charlton | KSAN | Completed | Load_261550 | Hope - 510 | Jul 31, 2026 8:00am | Jul 31, 2026 8:05am | Jul 31, 2026 9:23am | Jul 31, 2026 12:09pm | Jul 31, 2026 12:10pm | Jul 31, 2026 12:10pm | Jul 31, 2026 12:10pm | Jul 31, 2026 12:10pm |  |  | Fair | No | Call related to call at Craig hill district.
Non-Outage | J.E.26.07.38336 | C001870562 | Andrae Clarke | Portland | Completed | Load_247317 | Port Antonio - 410 | Jul 31, 2026 7:59am | Jul 31, 2026 8:01am | Jul 31, 2026 4:18pm | Jul 31, 2026 4:18pm | Jul 31, 2026 4:18pm | Jul 31, 2026 4:18pm | Jul 31, 2026 4:19pm | Jul 31, 2026 4:19pm |  |  | Fair | No | Refer to Emergency Crew to check transformer
Non-Outage | J.E.26.07.38845 | C001870563 | Andrae Clarke | Portland | Completed | Load_254849 | Port Antonio - 310 | Jul 31, 2026 7:59am | Jul 31, 2026 8:01am | Jul 31, 2026 11:28am | Jul 31, 2026 12:20pm | Jul 31, 2026 12:32pm | Jul 31, 2026 12:37pm | Jul 31, 2026 12:35pm | Jul 31, 2026 12:35pm |  |  | Fair | No | Check voltage 237/120/117Customer needs to get an electrician to check
Non-Outage | J.E.26.07.38963 | C001870564 | Andrae Clarke | Portland | Completed | Load_241296 | Port Antonio - 410 | Jul 31, 2026 7:59am | Jul 31, 2026 8:01am | Jul 31, 2026 11:03am | Jul 31, 2026 11:03am | Jul 31, 2026 11:23am | Jul 31, 2026 11:39am | Jul 31, 2026 11:27am | Jul 31, 2026 11:27am |  |  | Fair | No | .check voltage 247/123/124Meter defective Meter needs to be replaced Refer to field service
Non-Outage | J.E.26.07.39112 | C001870561 | Elvis Trowers | null | Completed | null | null | Jul 31, 2026 7:59am | Jul 31, 2026 10:12am | Jul 31, 2026 10:48am | Jul 31, 2026 10:48am | Jul 31, 2026 11:12am | Jul 31, 2026 11:37am | Jul 31, 2026 11:37am | Jul 31, 2026 11:37am |  |  | Fair | Yes | Happened to be a disconnection when checked with escalation service department, was reconnected with the assistant of escalation service department.
Outage | J.E.26.07.37830 | C001870565 | Horace Malcolm | null | Completed | Load_246939 | Bogue - 610 | Jul 31, 2026 7:59am | Jul 31, 2026 8:00am | Jul 31, 2026 9:08am | Jul 31, 2026 9:08am | Jul 31, 2026 9:16am | Jul 31, 2026 9:43am | Jul 31, 2026 9:43am | Jul 31, 2026 9:43am |  |  | Fair | No | Check and found customer not getting no supply from meter coming from hexing box call to call center LOC is on meter referred to field service
Outage | J.E.26.07.39096 | C001870560 | Dean Smith | St.James | Completed | Load_253569 | Bogue - 510 | Jul 31, 2026 7:58am | Jul 31, 2026 8:10am | Jul 31, 2026 10:15am | Jul 31, 2026 10:15am | Jul 31, 2026 10:15am | Jul 31, 2026 10:15am | Jul 31, 2026 10:15am | Jul 31, 2026 10:15am |  |  | Fair | No | Area was restored.
Non-Outage | J.E.26.07.35981 | C001870559 | Oshane Warren | Westmoreland | Completed | Load_238229 | Paradise - 310 | Jul 31, 2026 7:57am | Jul 31, 2026 7:59am | Jul 31, 2026 9:18am | Jul 31, 2026 9:18am | Jul 31, 2026 9:46am | Jul 31, 2026 9:47am | Jul 31, 2026 9:47am | Jul 31, 2026 9:47am |  |  | Fair | No | Customer reporting high bill
Non-Outage | J.E.26.07.39216 | C001870558 | Oshane Warren | Westmoreland | Completed | Load_247850 | Paradise - 310 | Jul 31, 2026 7:57am | Jul 31, 2026 7:59am | Jul 31, 2026 9:48am | Jul 31, 2026 9:48am | Jul 31, 2026 10:14am | Jul 31, 2026 10:14am | Jul 31, 2026 10:16am | Jul 31, 2026 10:16am |  |  | Fair | No | Change defective clamps at secondary line voltage left 117 117 234
Outage | J.E.26.07.39090 | C001870556 | Dwayne Samuels | Trelawny | Completed | Load_292058 | Greenwood - 110 | Jul 31, 2026 7:56am | Jul 31, 2026 7:58am | Jul 31, 2026 8:31am | Jul 31, 2026 9:06am | Jul 31, 2026 9:36am | Jul 31, 2026 9:37am | Jul 31, 2026 9:39am | Jul 31, 2026 9:39am |  |  | Fair | No | Check and found working ok voltage found 119v/118v/237v
Outage | J.E.26.07.39110 | C001870555 | Dwayne Samuels | Trelawny | Completed | Load_302315 | Greenwood - 210 | Jul 31, 2026 7:56am | Jul 31, 2026 7:58am | Jul 31, 2026 11:12am | Jul 31, 2026 11:55am | Jul 31, 2026 12:50pm | Jul 31, 2026 12:55pm | Jul 31, 2026 12:55pm | Jul 31, 2026 12:55pm |  |  | Fair | No | Check and found working ok call is related to 10kva tripped transformer that was reset today
Outage | J.E.26.07.39144 | C001870557 | Dwayne Samuels | Trelawny | Completed | Load_1001498 | Duncans - 110 | Jul 31, 2026 7:56am | Jul 31, 2026 7:58am | Jul 31, 2026 8:33am | Jul 31, 2026 8:33am | Jul 31, 2026 9:00am | Jul 31, 2026 9:04am | Jul 31, 2026 9:06am | Jul 31, 2026 9:06am |  |  | Fair | No | Unable to locate customer premises check and found power was restored in area
Non-Outage | J.E.26.07.38694 | C001870551 | Kenroy Dale | null | Completed | null | null | Jul 31, 2026 7:54am | Jul 31, 2026 7:54am | Jul 31, 2026 8:12am | Jul 31, 2026 8:19am | Jul 31, 2026 9:00am | Jul 31, 2026 9:27am | Jul 31, 2026 9:27am | Jul 31, 2026 9:27am | BrokenPole |  | Fair | No | Area checked and found with supply, customer also confirmed that supply was restored from yesterday
Outage | J.E.26.07.39087 | C001870552 | Kenroy Dale | Manchester | Completed | Load_255646 | Kendal - 310 | Jul 31, 2026 7:54am | Jul 31, 2026 7:54am | Jul 31, 2026 9:27am | Jul 31, 2026 9:43am | Jul 31, 2026 10:55am | Jul 31, 2026 11:11am | Jul 31, 2026 11:13am | Jul 31, 2026 11:13am |  |  | Fair | No | Customer meter was disconnected for non-payment. Bill was paid call center contacted and supply was restored
Outage | J.E.26.07.39214 | C001870554 | Omar King | St.Ann | Completed | Load_260937 | Roaring River - 210 | Jul 31, 2026 7:54am | Jul 31, 2026 11:40pm | Aug 1, 2026 3:06am | Aug 1, 2026 3:06am | Aug 1, 2026 4:54am | Aug 1, 2026 4:54am | Aug 1, 2026 4:55am | Aug 1, 2026 4:55am |  |  | Fair | No | Unable to find customer call several times no answer directions not sufficient
Outage | J.E.26.07.39218 | C001870553 | Kenroy Dale | Manchester | Completed | Load_254581 | Spur Tree - 310 | Jul 31, 2026 7:54am | Jul 31, 2026 7:54am | Jul 31, 2026 2:29pm | Jul 31, 2026 2:46pm | Jul 31, 2026 3:10pm | Jul 31, 2026 3:22pm | Jul 31, 2026 3:23pm | Jul 31, 2026 3:23pm |  |  | Fair | No | Security state that no one is at premises and customer is overseas
Outage | J.E.26.07.38830 | C001870550 | Michael Paterson | Westmoreland | Completed | Load_250137 | Paradise - 110 | Jul 31, 2026 7:49am | Jul 31, 2026 7:50am | Jul 31, 2026 12:38pm | Jul 31, 2026 12:38pm | Jul 31, 2026 12:40pm | Jul 31, 2026 3:01pm | Jul 31, 2026 3:01pm | Jul 31, 2026 3:01pm |  |  | Fair | No | Found 25kva xfmr fuse blown as a result of motor vehicle accident, third party pole broken, also, splice and retention four span of secondary, using three 2/0 preform, four clamps, 60ft # 2 AA conductor, replace 2amps fuse, supply restored, voltage readings 117v, 119v, 236v.
Non-Outage | J.E.26.07.38974 | C001870548 | Michael Paterson | null | Completed | null | null | Jul 31, 2026 7:47am | Jul 31, 2026 7:49am | Jul 31, 2026 11:00am | Jul 31, 2026 11:00am | Jul 31, 2026 11:00am | Jul 31, 2026 11:01am | Jul 31, 2026 11:03am | Jul 31, 2026 11:03am | BrokenWire |  | Fair | No | Cut creeper, upgrade fuse size from 10amp to 20amp, supply restore.
Outage | J.E.26.07.39113 | C001870545 | Javid Vernon | Westmoreland | Completed | Load_265324 | Paradise - 210 | Jul 31, 2026 7:43am | Jul 31, 2026 4:41pm | Jul 31, 2026 5:15pm | Jul 31, 2026 5:21pm | Jul 31, 2026 5:21pm | Jul 31, 2026 5:21pm | Jul 31, 2026 5:22pm | Jul 31, 2026 5:22pm |  |  | Fair | No | Customer stated that the power was restored
Outage | J.E.26.07.39117 | C001870544 | Michael Paterson | Westmoreland | Completed | Load_292718 | Paradise - 210 | Jul 31, 2026 7:43am | Jul 31, 2026 7:49am | Jul 31, 2026 8:21am | Jul 31, 2026 8:21am | Jul 31, 2026 9:25am | Jul 31, 2026 10:58am | Jul 31, 2026 10:58am | Jul 31, 2026 10:58am |  | Y | Fair | No | Found junction fuse blown at pole #621630, cut and remove creamer from line, up grade fuse side from 10amp to 20amp, supply restore.
Outage | J.E.26.07.38849 | C001870543 | Marlon Authors | St.Elizabeth | Completed | Load_246963 | Maggotty - 210 | Jul 31, 2026 7:41am | Jul 31, 2026 7:41am | Jul 31, 2026 12:16pm | Jul 31, 2026 12:16pm | Jul 31, 2026 12:16pm | Jul 31, 2026 12:26pm | Jul 31, 2026 12:26pm | Jul 31, 2026 12:26pm |  |  | Fair | No | Customer supply was disconnected for none payment
Outage | J.E.26.07.38907 | C001870542 | Marlon Authors | Manchester | Completed | Load_556608 | Spur Tree - 210 | Jul 31, 2026 7:40am | Jul 31, 2026 7:41am | Jul 31, 2026 7:55am | Jul 31, 2026 7:56am | Jul 31, 2026 7:56am | Jul 31, 2026 7:57am | Jul 31, 2026 7:57am | Jul 31, 2026 7:57am |  |  | Fair | No | Customer said supply was restored
Outage | J.E.26.07.39035 | C001870540 | Marlon Authors | Manchester | Completed | Load_259417 | Spur Tree - 210 | Jul 31, 2026 7:40am | Jul 31, 2026 7:41am | Jul 31, 2026 8:57am | Jul 31, 2026 8:57am | Jul 31, 2026 9:28am | Jul 31, 2026 9:46am | Jul 31, 2026 9:46am | Jul 31, 2026 9:46am |  |  | Fair | No | Patrol and found illegal connection banging the secondary neutral and lower phase together. Remove same and reset trip type transformer circuit at pole #531019. Restored supply okay
Outage | J.E.26.07.39040 | C001870541 | Marlon Authors | Manchester | Completed | Load_251338 | Spur Tree - 210 | Jul 31, 2026 7:40am | Jul 31, 2026 7:41am | Jul 31, 2026 10:12am | Jul 31, 2026 10:12am | Jul 31, 2026 10:24am | Jul 31, 2026 10:26am | Jul 31, 2026 10:26am | Jul 31, 2026 10:26am |  |  | Fair | No | Unable to locate and the customer not answering the phone
Outage | J.E.26.07.39080 | C001870539 | Marlon Authors | Manchester | Completed | Load_248909 | Spur Tree - 210 | Jul 31, 2026 7:40am | Jul 31, 2026 7:41am | Jul 31, 2026 9:52am | Jul 31, 2026 9:52am | Jul 31, 2026 9:52am | Jul 31, 2026 9:54am | Jul 31, 2026 9:54am | Jul 31, 2026 9:54am |  |  | Fair | No | Supply restored to the area
Outage | J.E.26.07.38836 | C001870535 | Richard Nicholas | St.Catherine | Completed | Load_261641 | Tredegar - 310 | Jul 31, 2026 7:39am | Aug 1, 2026 8:08am | Aug 1, 2026 8:56am | Aug 1, 2026 8:56am | Aug 1, 2026 10:21am | Aug 1, 2026 11:04am | Aug 1, 2026 11:04am | Aug 1, 2026 11:04am |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.38897 | C001870536 | Wayne Dillion | Manchester | Completed | Load_262167 | Spur Tree - 210 | Jul 31, 2026 7:39am | Aug 1, 2026 7:46am | Aug 1, 2026 10:29am | Aug 1, 2026 10:29am | Aug 1, 2026 10:29am | Aug 1, 2026 10:30am | Aug 1, 2026 10:30am | Aug 1, 2026 10:30am |  |  | Fair | No | Customer said supply ok
Outage | J.E.26.07.39190 | C001870538 | Horace Malcolm | St.James | Completed | Load_242883 | Bogue - 610 | Jul 31, 2026 7:39am | Jul 31, 2026 7:44am | Jul 31, 2026 7:53am | Jul 31, 2026 7:53am | Jul 31, 2026 8:17am | Jul 31, 2026 9:07am | Jul 31, 2026 9:07am | Jul 31, 2026 9:07am |  |  | Fair | No | Refused one 15amp junction fuse
Outage | J.E.26.07.39206 | C001870534 | Tyrese Williams | St.Ann | Completed | Load_248334 | Cardiff Hall - 310 | Jul 31, 2026 7:38am | Jul 31, 2026 3:24pm | Jul 31, 2026 5:03pm | Jul 31, 2026 5:49pm | Jul 31, 2026 7:14pm | Jul 31, 2026 7:32pm | Jul 31, 2026 7:33pm | Jul 31, 2026 7:33pm | BrokenWire |  | Fair | No | Splice and retention service wire neutral
Outage | J.E.26.07.38892 | C001870533 | Richard Watson | St.Elizabeth | Completed | Load_262758 | Maggotty - 110 | Jul 31, 2026 7:37am | Jul 31, 2026 3:15pm | Jul 31, 2026 6:16pm | Jul 31, 2026 6:17pm | Jul 31, 2026 7:21pm | Jul 31, 2026 7:28pm | Jul 31, 2026 7:33pm | Jul 31, 2026 7:33pm |  |  | Fair | No | Customer requires reconnection after the passage of hurricane Melissa, however customer is to be connected to Hexing system, please refer to Field Service Department for reconnection.
Non-Outage | J.E.26.07.35281 | C001870531 | Dwayne Samuels | null | Completed | null | null | Jul 31, 2026 7:36am | Jul 31, 2026 10:16am | Jul 31, 2026 1:03pm | Jul 31, 2026 1:10pm | Jul 31, 2026 1:38pm | Jul 31, 2026 1:40pm | Jul 31, 2026 1:40pm | Jul 31, 2026 1:40pm |  |  | Fair | No | Check and found working ok voltage found 114v/114v/228v
Outage | J.E.26.07.38920 | C001870532 | Richard Watson | St.Elizabeth | Completed | Load_238344 | Maggotty - 110 | Jul 31, 2026 7:36am | Jul 31, 2026 3:15pm | Jul 31, 2026 5:31pm | Jul 31, 2026 5:31pm | Jul 31, 2026 5:47pm | Jul 31, 2026 5:54pm | Jul 31, 2026 6:00pm | Jul 31, 2026 6:00pm |  |  | Fair | No | Customer disconnected for outstanding balance, customer advised to clear outstanding balance and call in receipt for re-connection.
Outage | J.E.26.07.39078 | C001870529 | Richard Watson | St.Elizabeth | Completed | Load_240962 | Maggotty - 110 | Jul 31, 2026 7:33am | Jul 31, 2026 3:15pm | Jul 31, 2026 8:31pm | Jul 31, 2026 8:31pm | Jul 31, 2026 8:55pm | Jul 31, 2026 8:59pm | Jul 31, 2026 8:59pm | Jul 31, 2026 8:59pm |  |  | Fair | No | Customer contacted by phone and stated that the supply was restored from last night.
Outage | J.E.26.07.39088 | C001870528 | Selvin White | St.Elizabeth | Completed | Load_252931 | Maggotty - 210 | Jul 31, 2026 7:32am | Jul 31, 2026 7:33am | Jul 31, 2026 8:07am | Jul 31, 2026 8:10am | Jul 31, 2026 8:17am | Jul 31, 2026 8:19am | Jul 31, 2026 8:19am | Jul 31, 2026 8:19am |  |  | Fair | No | Customer was contacted and said supply was restored from yesterday evening by the emergency crew.
Outage | J.E.26.07.39095 | C001870525 | Stephen Taylor | St.Thomas | Completed | Load_251372 | Good Year - 210 | Jul 31, 2026 7:31am | Jul 31, 2026 9:04am | Jul 31, 2026 12:52pm | Jul 31, 2026 12:52pm | Jul 31, 2026 12:52pm | Jul 31, 2026 12:52pm | Jul 31, 2026 12:54pm | Jul 31, 2026 12:54pm |  |  | Fair | No | Check with customer and say power is back from last night
Outage | J.E.26.07.39128 | C001870524 | Stephen Taylor | St.Thomas | Completed | Load_240667 | Good Year - 110 | Jul 31, 2026 7:31am | Jul 31, 2026 9:04am | Jul 31, 2026 10:26am | Jul 31, 2026 10:26am | Jul 31, 2026 11:13am | Jul 31, 2026 11:13am | Jul 31, 2026 11:23am | Jul 31, 2026 11:23am |  |  | Fair | No | Patrol and clean secondary wire and close up back transformer safely all customer is now okay
Outage | J.E.26.07.39188 | C001870527 | Michael Christian | St.James | Completed | Load_240373 | Queens Drive - 710 | Jul 31, 2026 7:31am | Jul 31, 2026 7:35am | Jul 31, 2026 7:39am | Jul 31, 2026 7:39am | Jul 31, 2026 8:24am | Jul 31, 2026 8:28am | Jul 31, 2026 8:28am | Jul 31, 2026 8:28am | LowHangingWires |  | Fair | No | Found leaning pole pole needed urgent attention pole needed guys
Non-Outage | J.E.26.07.39122 | C001870523 | Jowayne Newmans | null | Completed | null | null | Jul 31, 2026 7:28am | Jul 31, 2026 7:28am | Jul 31, 2026 8:21am | Jul 31, 2026 8:26am | Jul 31, 2026 9:42am | Jul 31, 2026 10:01am | Jul 31, 2026 10:01am | Jul 31, 2026 10:01am |  |  | Fair | No | Patrol and found 25kva transformer trip cause by motor vehicle accident however all conductors are still intact. Repair by resetting transformer, customer now has electricity.
Outage | J.E.26.07.38927 | C001870521 | Nickolas Rodriques | Portmore | Completed | Load_256469 | Naggo Head - 610 | Jul 31, 2026 7:24am | Jul 31, 2026 7:24am | Jul 31, 2026 10:14am | Jul 31, 2026 10:17am | Jul 31, 2026 11:04am | Jul 31, 2026 11:19am | Jul 31, 2026 11:22am | Jul 31, 2026 11:22am |  |  | Fair | No | Found customer with electricity. He confirmed that he had an issue with his prepaid box which was subsequently resolved.
Outage | J.E.26.07.38942 | C001870522 | Nickolas Rodriques | Portmore | Completed | Load_263555 | Naggo Head - 510 | Jul 31, 2026 7:24am | Jul 31, 2026 7:24am | Jul 31, 2026 8:12am | Jul 31, 2026 8:17am | Jul 31, 2026 9:04am | Jul 31, 2026 10:12am | Jul 31, 2026 10:14am | Jul 31, 2026 10:14am |  |  | Fair | No | Checked and found customer single phasing (118) caused by broken service wire at pole. Repaired by connecting the wire using one clamp. Current reading (120-119-239). Customer confirmed that all is well now.
Outage | J.E.26.07.38957 | C001870519 | Nickolas Rodriques | Portmore | Completed | Load_1003656 | Naggo Head - 610 | Jul 31, 2026 7:24am | Jul 31, 2026 7:24am | Jul 31, 2026 11:22am | Jul 31, 2026 11:30am | Jul 31, 2026 12:30pm | Jul 31, 2026 12:44pm | Jul 31, 2026 12:47pm | Jul 31, 2026 12:47pm |  |  | Fair | No | Customer confirmed that the power was restored.
Outage | J.E.26.07.39034 | C001870518 | Nickolas Rodriques | Portmore | Completed | Load_266484 | Naggo Head - 610 | Jul 31, 2026 7:24am | Jul 31, 2026 7:24am | Jul 31, 2026 12:49pm | Jul 31, 2026 12:54pm | Jul 31, 2026 1:20pm | Jul 31, 2026 1:57pm | Jul 31, 2026 2:10pm | Jul 31, 2026 2:10pm |  |  | Fair | No | Checked and found customer with unstable voltage caused by corroded connections. Repaired by placing three one-bolt clamps at pole. Current reading (116-114-230)
Outage | J.E.26.07.38621 | C001870515 | Hartley Chin | Clarendon | Completed | Load_242744 | May Pen - 110 | Jul 31, 2026 7:22am | Jul 31, 2026 7:23am | Jul 31, 2026 12:29pm | Jul 31, 2026 12:29pm | Jul 31, 2026 1:36pm | Jul 31, 2026 1:37pm | Jul 31, 2026 1:40pm | Jul 31, 2026 1:40pm | BangingWires |  | Fair | No | Premisis not found .unable to contact customer
Outage | J.E.26.07.38682 | C001870517 | Neville Spencer | Clarendon | Completed | Load_247919 | Parnassus - 310 | Jul 31, 2026 7:22am | Jul 31, 2026 7:23am | Jul 31, 2026 9:57am | Jul 31, 2026 9:57am | Jul 31, 2026 10:21am | Jul 31, 2026 10:21am | Jul 31, 2026 11:05am | Jul 31, 2026 11:05am |  |  | Fair | No | Found defective 2, wire service installed 90 ft #6 triplex, 2 clamps, 2, 6/6 sleeves voltage reading 116 supply restored.
Outage | J.E.26.07.39008 | C001870516 | Hartley Chin | Clarendon | Completed | Load_249266 | May Pen - 110 | Jul 31, 2026 7:22am | Jul 31, 2026 7:24am | Jul 31, 2026 1:40pm | Jul 31, 2026 1:40pm | Jul 31, 2026 1:57pm | Jul 31, 2026 2:35pm | Jul 31, 2026 2:43pm | Jul 31, 2026 2:43pm |  |  | Fair | No | Found blown 3 amp fuse for 25 KVA transformer at pole # 0106040 . Line patrolled and found ok. Transformer refused.
Outage | J.E.26.07.39131 | C001870514 | Hartley Chin | Clarendon | Completed | Load_262103 | May Pen - 110 | Jul 31, 2026 7:22am | Jul 31, 2026 7:23am | Jul 31, 2026 7:58am | Jul 31, 2026 7:58am | Jul 31, 2026 11:56am | Jul 31, 2026 12:18pm | Jul 31, 2026 12:29pm | Jul 31, 2026 12:29pm |  |  | SevereWind | No | Found blown 20 amp junction fuse @ pole # 0155414 line patrolled and found okay , junction refused..
Outage | J.E.26.07.39146 | C001870512 | Roxroy Needham | St.Ann | Completed | Load_253998 | Cardiff Hall - 210 | Jul 31, 2026 7:22am | Jul 31, 2026 7:23am | Jul 31, 2026 11:22am | Jul 31, 2026 11:22am | Jul 31, 2026 12:36pm | Jul 31, 2026 12:56pm | Jul 31, 2026 12:58pm | Jul 31, 2026 12:58pm |  | Y | Fair | No | Cute tree from line and replace a 8 amps junction fuse at pole
Outage | J.E.26.07.39161 | C001870513 | Roxroy Needham | St.Ann | Completed | Load_246183 | Cardiff Hall - 210 | Jul 31, 2026 7:22am | Jul 31, 2026 7:23am | Jul 31, 2026 8:13am | Jul 31, 2026 8:13am | Jul 31, 2026 10:24am | Jul 31, 2026 11:20am | Jul 31, 2026 11:21am | Jul 31, 2026 11:21am | BrokenWire |  | Fair | No | Isolate 25 KVA transformer carry out spot bushing splice and retention 2 spans of secondary neutral and phase used 60 ft of No# 2 aa conductor, splice and retention 2- 3 wire service used 3 one bolt clamps
Outage | J.E.26.07.38941 | C001870510 | Wan Carlos Scarlett | St.Catherine | Completed | Load_294354 | Twickenham - 210 | Jul 31, 2026 7:12am | Jul 31, 2026 7:12am | Jul 31, 2026 10:03am | Jul 31, 2026 10:03am | Jul 31, 2026 10:23am | Jul 31, 2026 10:34am | Jul 31, 2026 10:36am | Jul 31, 2026 10:36am |  |  | Fair | No | Customer got reconnected by escalation department reset customer breaker power supply has been restored reading 115 116 231
Outage | J.E.26.07.38810 | C001870509 | Nickolas Rodriques | Portmore | Completed | Load_268319 | Naggo Head - 610 | Jul 31, 2026 7:09am | Jul 31, 2026 7:22am | Jul 31, 2026 3:02pm | Jul 31, 2026 3:10pm | Jul 31, 2026 3:48pm | Jul 31, 2026 4:35pm | Jul 31, 2026 4:50pm | Jul 31, 2026 4:50pm | BrokenWire |  | Fair | No | Checked and found customer service wire phase and neutral broken. Repaired by splice and re-tension wire using one service sleeve and two one-bolt clamps. Current reading (120-118-238)
Outage | J.E.26.07.38952 | C001870508 | Wan Carlos Scarlett | KSAS | Completed | Load_254412 | Duhaney - 210 | Jul 31, 2026 7:09am | Jul 31, 2026 7:10am | Jul 31, 2026 7:25am | Jul 31, 2026 7:25am | Jul 31, 2026 9:55am | Jul 31, 2026 9:56am | Jul 31, 2026 10:03am | Jul 31, 2026 10:03am | BrokenWire |  | Fair | No | Found transformer droplead supplying #2 twisted wire with phase and neutral burn off replaced 30 ft #2 triplex conductor use 6 one bolt clamps 3 Penn union readings 116 116 232 power supply has been restored
Outage | J.E.26.07.38970 | C001870507 | Nickolas Rodriques | Portmore | Completed | Load_265851 | Naggo Head - 610 | Jul 31, 2026 7:08am | Jul 31, 2026 7:22am | Jul 31, 2026 2:10pm | Jul 31, 2026 2:12pm | Jul 31, 2026 2:29pm | Jul 31, 2026 2:58pm | Jul 31, 2026 3:00pm | Jul 31, 2026 3:00pm | BrokenWire |  | Fair | No | Checked and found customer service wire disconnected to facilitate repair on customer side. Repaired by connecting wire using three service sleeves and one clamp. Current reading (117-116-233)
Outage | J.E.26.07.39180 | C001870506 | Wan Carlos Scarlett | St.Catherine | Completed | Load_250366 | Twickenham - 210 | Jul 31, 2026 7:08am | Jul 31, 2026 7:10am | Jul 31, 2026 11:26am | Jul 31, 2026 11:26am | Jul 31, 2026 12:04pm | Jul 31, 2026 12:41pm | Jul 31, 2026 12:44pm | Jul 31, 2026 12:44pm | BrokenWire |  | Fair | No | Found customer 2 wire service with neutral and phase corroded at pothead and pole use 2 Penn union 2 one bolt clamps readings
Outage | J.E.26.07.38689 | C001870502 | Neville Spencer | Clarendon | Completed | Load_238890 | Parnassus - 210 | Jul 31, 2026 7:05am | Jul 31, 2026 7:06am | Jul 31, 2026 9:28am | Jul 31, 2026 9:28am | Jul 31, 2026 9:46am | Jul 31, 2026 9:48am | Jul 31, 2026 9:48am | Jul 31, 2026 9:48am |  |  | Fair | No | Unable to locate customer.
Outage | J.E.26.07.38825 | C001870504 | Neville Spencer | Clarendon | Completed | Load_406117 | Parnassus - 210 | Jul 31, 2026 7:05am | Jul 31, 2026 7:06am | Jul 31, 2026 9:49am | Jul 31, 2026 9:49am | Jul 31, 2026 9:54am | Jul 31, 2026 9:54am | Jul 31, 2026 9:56am | Jul 31, 2026 9:56am |  |  | Fair | No | Found ok call resolved yesterday.
Outage | J.E.26.07.38925 | C001870503 | Neville Spencer | Clarendon | Completed | Load_406102 | Parnassus - 210 | Jul 31, 2026 7:05am | Jul 31, 2026 7:06am | Jul 31, 2026 8:31am | Jul 31, 2026 8:31am | Jul 31, 2026 9:01am | Jul 31, 2026 9:25am | Jul 31, 2026 9:27am | Jul 31, 2026 9:27am |  |  | Fair | No | Cleared bird from xmfr pole renew blown 15 amp j/ fuse at pole #=562875 area restored.
Outage | J.E.26.07.39089 | C001870505 | Neville Spencer | Clarendon | Completed | Load_261428 | May Pen - 210 | Jul 31, 2026 7:05am | Jul 31, 2026 7:06am | Jul 31, 2026 7:39am | Jul 31, 2026 7:39am | Jul 31, 2026 8:12am | Jul 31, 2026 8:12am | Jul 31, 2026 8:29am | Jul 31, 2026 8:29am |  |  | Fair | No | Reset trip 10 kva xmfr at pole # 0123609; supply restored. Xmf need to upgrade to 25 kva xmfr feeding approximately 45 customers.
Outage | J.E.26.07.39145 | C001870460 | Shamour Haughton | St.James | Completed | Load_241438 | Queens Drive - 710 | Jul 31, 2026 5:35am | Jul 31, 2026 5:43am | Jul 31, 2026 7:15am | Jul 31, 2026 7:15am | Jul 31, 2026 7:15am | Jul 31, 2026 7:15am | Jul 31, 2026 7:18am | Jul 31, 2026 7:18am | Fire |  | Fair | No | Found secondary banging, isolate 25kva to retention secondary using 1, 2/0 preform and reclose 25kva
Outage | J.E.26.07.39141 | C001870455 | Edward Royal | KSAS | Completed | Load_255768 | Hunts Bay - 310 | Jul 31, 2026 3:14am | Jul 31, 2026 3:15am | Jul 31, 2026 3:40am | Jul 31, 2026 3:40am | Jul 31, 2026 3:40am | Jul 31, 2026 3:41am | Jul 31, 2026 3:41am | Jul 31, 2026 3:41am |  |  | Fair | No | Premises found close
Non-Outage | J.E.26.07.38681 | C001870454 | Michael Christian | null | Completed | null | null | Jul 31, 2026 2:25am | Jul 31, 2026 7:36am | Jul 31, 2026 8:59am | Jul 31, 2026 8:59am | Jul 31, 2026 10:22am | Jul 31, 2026 10:35am | Jul 31, 2026 10:35am | Jul 31, 2026 10:35am |  |  | Fair | No | Replace 1 clamp at customer service wire at pole voltage 110 109 221 at pole
Outage | J.E.26.07.38827 | C001870453 | Shamour Haughton | St.James | Completed | Load_261827 | Queens Drive - 710 | Jul 31, 2026 2:25am | Jul 31, 2026 2:26am | Jul 31, 2026 2:30am | Jul 31, 2026 2:30am | Jul 31, 2026 2:30am | Jul 31, 2026 2:31am | Jul 31, 2026 3:19am | Jul 31, 2026 3:19am |  |  | Fair | No | Found 1,100kva fuse blown, refuse 1,100kva fuse using 1,10amp fuse
Outage | J.E.26.07.38975 | C001870451 | Dean Smith | St.James | Completed | Load_267822 | Bogue - 510 | Jul 31, 2026 2:23am | Jul 31, 2026 8:11am | Jul 31, 2026 8:24am | Jul 31, 2026 8:25am | Jul 31, 2026 10:06am | Jul 31, 2026 10:06am | Jul 31, 2026 10:08am | Jul 31, 2026 10:08am |  |  | Fair | No | Cut and remove tree limb from primary conductor, replace 2amp transformer fuse. Pole number n/a
Outage | J.E.26.07.39125 | C001870452 | Shamour Haughton | St.James | Completed | Load_301723 | Bogue - 310 | Jul 31, 2026 2:23am | Jul 31, 2026 2:24am | Jul 31, 2026 3:25am | Jul 31, 2026 3:25am | Jul 31, 2026 3:54am | Jul 31, 2026 3:54am | Jul 31, 2026 4:05am | Jul 31, 2026 4:05am |  |  | Fair | No | Customer experiencing internal issues,voltage left 112,114,226
Outage | J.E.26.07.39109 | C001870433 | Delano Gayle | St.Catherine | Completed | Load_259734 | Tredegar - 510 | Jul 31, 2026 12:25am | Jul 31, 2026 12:26am | Jul 31, 2026 5:52am | Jul 31, 2026 5:52am | Jul 31, 2026 6:20am | Jul 31, 2026 7:34am | Jul 31, 2026 7:34am | Jul 31, 2026 7:34am | Fire |  | Fair | No | Broken secondary neutral in 1 span, banging open secondary in other span, burnt 10kva transformer phase lead, burnt #6 triplex, open 10kva transformer fuse no pole number, splice and retention secondary neutral use 20ft #2aa, 1 #2 splicing sleeve, 1 clamps, space 1 span open secondary use 3 clamps, splice and retention burnt #6 triplex use 10ft #6 3 clamps 3 linkets, repair burnt transformer phase lead use 6ft pvc copper 2 clamps, close transformer fuse voltage readings 114-115-230
Outage | J.E.26.07.39116 | C001870430 | Edward Royal | KSAN | Completed | Load_269745 | Constant Spring - 310 | Jul 30, 2026 11:40pm | Jul 31, 2026 12:26am | Jul 31, 2026 2:09am | Jul 31, 2026 2:09am | Jul 31, 2026 2:27am | Jul 31, 2026 2:46am | Jul 31, 2026 2:47am | Jul 31, 2026 2:47am |  |  | Fair | No | Reset 25kva transformer
Non-Outage | J.E.26.07.39055 | C001870419 | Shamour Haughton | null | Completed | null | null | Jul 30, 2026 10:51pm | Jul 30, 2026 10:52pm | Jul 31, 2026 1:36am | Jul 31, 2026 1:36am | Jul 31, 2026 2:11am | Jul 31, 2026 2:12am | Jul 31, 2026 2:14am | Jul 31, 2026 2:14am | Fire |  | Fair | No | Check and found areaokay, customer number keep going voicemail, after directions was fallowed, area found with light, no fire was seen
Non-Outage | J.E.26.07.39059 | C001870418 | Shamour Haughton | null | Completed | null | null | Jul 30, 2026 10:47pm | Jul 30, 2026 11:01pm | Jul 31, 2026 2:14am | Jul 31, 2026 2:14am | Jul 31, 2026 2:14am | Jul 31, 2026 2:15am | Jul 31, 2026 2:16am | Jul 31, 2026 2:16am | Fire |  | Fair | No | Related to previous report
Outage | J.E.26.07.39092 | C001870417 | Shamour Haughton | St.James | Completed | Load_237881 | Bogue - 610 | Jul 30, 2026 10:41pm | Jul 30, 2026 11:00pm | Jul 31, 2026 1:26am | Jul 31, 2026 1:26am | Jul 31, 2026 1:33am | Jul 31, 2026 1:33am | Jul 31, 2026 1:34am | Jul 31, 2026 1:34am |  |  | Fair | No | Customer states that power was restored, area found okay
Outage | J.E.26.07.38943 | C001870416 | Shamour Haughton | St.James | Completed | Load_250693 | Bogue - 310 | Jul 30, 2026 10:39pm | Jul 30, 2026 11:00pm | Jul 31, 2026 2:18am | Jul 31, 2026 2:18am | Jul 31, 2026 2:18am | Jul 31, 2026 2:21am | Jul 31, 2026 2:25am | Jul 31, 2026 2:25am |  |  | Fair | No | Customer said power was restored
Outage | J.E.26.07.39062 | C001870415 | Shamour Haughton | St.James | Completed | Load_241438 | Queens Drive - 710 | Jul 30, 2026 10:39pm | Jul 30, 2026 10:51pm | Jul 31, 2026 2:16am | Jul 31, 2026 2:16am | Jul 31, 2026 2:16am | Jul 31, 2026 2:16am | Jul 31, 2026 2:16am | Jul 31, 2026 2:16am | Fire |  | Fair | No | Related to previous reports
Outage | J.E.26.07.39076 | C001870414 | Roxroy Needham | St.Ann | Completed | Load_246878 | Cardiff Hall - 310 | Jul 30, 2026 10:38pm | Jul 31, 2026 7:24am | Jul 31, 2026 1:32pm | Jul 31, 2026 1:33pm | Jul 31, 2026 2:30pm | Jul 31, 2026 2:51pm | Jul 31, 2026 2:55pm | Jul 31, 2026 2:55pm |  | Y | Fair | No | Reset a 10 KVA transformer at pole
Outage | J.E.26.07.39007 | C001870413 | Delano Gayle | St.Catherine | Completed | Load_239692 | Tredegar - 310 | Jul 30, 2026 10:37pm | Jul 30, 2026 10:59pm | Jul 31, 2026 3:15am | Jul 31, 2026 3:15am | Jul 31, 2026 4:40am | Jul 31, 2026 4:43am | Jul 31, 2026 4:43am | Jul 31, 2026 4:43am |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.39098 | C001870412 | Delano Gayle | St.Catherine | Completed | Load_294424 | Tredegar - 510 | Jul 30, 2026 10:37pm | Jul 30, 2026 10:59pm | Jul 31, 2026 12:01am | Jul 31, 2026 12:01am | Jul 31, 2026 1:48am | Jul 31, 2026 3:14am | Jul 31, 2026 3:15am | Jul 31, 2026 3:15am |  |  | Fair | No | Meter found disconnected, reconnected with assistance from call center representative
Non-Outage | J.E.26.07.38913 | C001870410 | Delano Gayle | null | Completed | null | null | Jul 30, 2026 10:36pm | Jul 30, 2026 11:01pm | Jul 31, 2026 4:45am | Jul 31, 2026 4:45am | Jul 31, 2026 5:22am | Jul 31, 2026 5:38am | Jul 31, 2026 5:38am | Jul 31, 2026 5:38am | Fire |  | Fair | No | Premises not found no answer from customer phone, no fire seen
Outage | J.E.26.07.39046 | C001870409 | Delano Gayle | St.Catherine | Completed | Load_252716 | Tredegar - 510 | Jul 30, 2026 10:36pm | Jul 30, 2026 11:00pm | Jul 30, 2026 11:04pm | Jul 30, 2026 11:04pm | Jul 30, 2026 11:50pm | Jul 31, 2026 12:00am | Jul 31, 2026 12:00am | Jul 31, 2026 12:00am |  |  | Fair | No | Premises not found no answer from customer phone, hexing area, area found okay
Outage | J.E.26.07.38862 | C001870408 | Edward Royal | KSAS | Completed | Load_255623 | Greenwich - 510 | Jul 30, 2026 10:35pm | Jul 30, 2026 11:39pm | Jul 31, 2026 2:07am | Jul 31, 2026 2:08am | Jul 31, 2026 2:08am | Jul 31, 2026 2:08am | Jul 31, 2026 2:09am | Jul 31, 2026 2:09am |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.07.38955 | C001870407 | Edward Royal | KSAN | Completed | Load_263228 | Washington Blvd - 710 | Jul 30, 2026 10:35pm | Jul 30, 2026 11:39pm | Jul 31, 2026 3:41am | Jul 31, 2026 3:41am | Jul 31, 2026 3:41am | Jul 31, 2026 3:41am | Jul 31, 2026 3:41am | Jul 31, 2026 3:41am |  |  | Fair | No | Premises found close
Non-Outage | J.E.26.07.23060 | C001870403 | Moses Elliston | St.Catherine | Completed | Load_269355 | Tredegar - 210 | Jul 30, 2026 10:03pm | Jul 30, 2026 10:03pm | Jul 31, 2026 11:01am | Jul 31, 2026 11:01am | Jul 31, 2026 11:01am | Jul 31, 2026 11:01am | Jul 31, 2026 11:02am | Jul 31, 2026 11:02am |  |  | Fair | No | Supply ok at premises.
Outage | J.E.26.07.39069 | C001870399 | Neckell Ormsby | St.Mary | Completed | Load_567730 | Highgate - 210 | Jul 30, 2026 9:38pm | Jul 31, 2026 7:29am | Jul 31, 2026 8:02am | Jul 31, 2026 8:02am | Jul 31, 2026 9:28am | Jul 31, 2026 10:04am | Jul 31, 2026 10:08am | Jul 31, 2026 10:08am |  |  | Fair | No | Found defective meter voltage in socket 115v 114v 230v please refer to field service to have the meter changed urgently due to guests at property
Outage | J.E.26.07.39000 | C001870397 | Romeo Brissett | St.James | Completed | Load_237651 | Bogue - 510 | Jul 30, 2026 8:50pm | Jul 30, 2026 9:00pm | Jul 30, 2026 9:57pm | Jul 30, 2026 9:57pm | Jul 30, 2026 10:14pm | Jul 30, 2026 10:38pm | Jul 30, 2026 10:39pm | Jul 30, 2026 10:39pm | Fire |  | Fair | No | Spliced and retention customer service wire.
Non-Outage | J.E.26.07.38605 | C001870395 | Moses Elliston | null | Completed | null | null | Jul 30, 2026 8:49pm | Jul 30, 2026 8:49pm | Jul 31, 2026 2:46pm | Jul 31, 2026 2:46pm | Jul 31, 2026 2:47pm | Jul 31, 2026 1:50pm | Jul 31, 2026 2:49pm | Jul 31, 2026 2:49pm |  |  | Fair | No | Prepaid account reconnected
Non-Outage | J.E.26.07.38561 | C001870392 | Elvis Trowers | KSAS | Completed | Load_267072 | Duhaney - 310 | Jul 30, 2026 8:41pm | Jul 31, 2026 8:41am | Jul 31, 2026 11:38am | Jul 31, 2026 11:38am | Jul 31, 2026 1:07pm | Jul 31, 2026 1:14pm | Jul 31, 2026 1:14pm | Jul 31, 2026 1:14pm | BrokenWire |  | Fair | Yes | Areas checked and found ok upon arrival, all broken wires are belonging to C/W, not to JPS.
Non-Outage | J.E.26.07.38702 | C001870393 | Kaydon Taylor | KSAN | Completed | Load_264378 | Constant Spring - 210 | Jul 30, 2026 8:41pm | Jul 30, 2026 8:42pm | Jul 30, 2026 9:05pm | Jul 30, 2026 9:06pm | Jul 30, 2026 9:33pm | Jul 30, 2026 9:37pm | Jul 30, 2026 9:37pm | Jul 30, 2026 9:37pm | BrokenWire |  | Fair | No | Telecommunication broken wire remove wire off the customer gate.
Non-Outage | J.E.26.07.38885 | C001870390 | Christopher Edwards | KSAN | Completed | Load_255114 | Constant Spring - 410 | Jul 30, 2026 8:41pm | Jul 30, 2026 8:41pm | Jul 30, 2026 9:11pm | Jul 30, 2026 9:11pm | Jul 30, 2026 9:23pm | Jul 30, 2026 9:58pm | Jul 30, 2026 9:59pm | Jul 30, 2026 9:59pm |  |  | Fair | No | Remake corroded neutral joint At pole using (2) one bolt clamps Voltage:115,114,230v
Non-Outage | J.E.26.07.38999 | C001870391 | Christopher Edwards | KSAN | Completed | Load_267312 | Constant Spring - 310 | Jul 30, 2026 8:41pm | Jul 30, 2026 8:41pm | Jul 30, 2026 9:59pm | Jul 31, 2026 8:29am | Jul 31, 2026 8:51am | Jul 31, 2026 9:35am | Jul 31, 2026 9:35am | Jul 31, 2026 9:35am |  |  | Fair | No | Remake corroded neutral joint at poleUsing (1) one bolt clamps Voltage:116,115,230v
Outage | J.E.26.07.38956 | C001870384 | Hopeton Henry | St.Thomas | Completed | Load_265545 | Lysson - 410 | Jul 30, 2026 8:37pm | Jul 30, 2026 8:39pm | Jul 30, 2026 9:12pm | Jul 30, 2026 11:36pm | Jul 30, 2026 11:36pm | Jul 31, 2026 12:15am | Jul 31, 2026 12:16am | Jul 31, 2026 12:16am |  |  | Fair | No | Found corrosion at pole and pot head 113-117-230 volts
Outage | J.E.26.07.39037 | C001870385 | Hopeton Henry | St.Thomas | Completed | Load_260487 | Lysson - 410 | Jul 30, 2026 8:37pm | Jul 30, 2026 8:39pm | Jul 30, 2026 9:12pm | Jul 30, 2026 9:45pm | Jul 30, 2026 10:38pm | Jul 30, 2026 11:35pm | Jul 30, 2026 11:36pm | Jul 30, 2026 11:36pm |  |  | Fair | No | Refuse 25 kva with 3 amp
Outage | J.E.26.07.39047 | C001870383 | Jowayne Newmans | Portland | Completed | Load_265513 | Port Antonio - 410 | Jul 30, 2026 8:34pm | Jul 30, 2026 8:34pm | Jul 30, 2026 9:07pm | Jul 30, 2026 9:07pm | Jul 30, 2026 10:26pm | Jul 30, 2026 10:30pm | Jul 30, 2026 10:30pm | Jul 30, 2026 10:30pm | BrokenWire |  | Fair | No | Patrol and found 25kva transformer trip cause by motor vehicle accident, however no damage was done to conductor. Repair by resetting 25kva transformer. Customers now have electricity.
Outage | J.E.26.07.38950 | C001870382 | Tyrese Williams | St.Ann | Completed | Load_305062 | Cardiff Hall - 210 | Jul 30, 2026 8:31pm | Jul 30, 2026 8:31pm | Jul 30, 2026 8:54pm | Jul 30, 2026 8:59pm | Jul 30, 2026 8:59pm | Jul 30, 2026 9:04pm | Jul 30, 2026 9:05pm | Jul 30, 2026 9:05pm |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.07.39013 | C001870380 | Omar King | St.Ann | Completed | Load_260937 | Roaring River - 210 | Jul 30, 2026 8:29pm | Jul 30, 2026 11:54pm | Jul 31, 2026 2:13am | Jul 31, 2026 2:14am | Jul 31, 2026 3:25am | Jul 31, 2026 3:26am | Jul 31, 2026 3:26am | Jul 31, 2026 3:26am |  |  | Fair | No | Call several times no answer directions not sufficient
Outage | J.E.26.07.39039 | C001870379 | Tyrese Williams | St.Ann | Completed | Load_246183 | Cardiff Hall - 210 | Jul 30, 2026 8:26pm | Jul 30, 2026 8:31pm | Jul 30, 2026 8:42pm | Jul 30, 2026 9:28pm | Jul 30, 2026 9:28pm | Jul 30, 2026 9:34pm | Jul 30, 2026 9:34pm | Jul 30, 2026 9:34pm | BrokenWire |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.07.38871 | C001870376 | Tyrese Williams | St.Ann | Completed | Load_575948 | Cardiff Hall - 210 | Jul 30, 2026 8:17pm | Jul 30, 2026 8:18pm | Jul 30, 2026 8:30pm | Jul 30, 2026 8:30pm | Jul 30, 2026 8:30pm | Jul 30, 2026 8:34pm | Jul 30, 2026 8:34pm | Jul 30, 2026 8:34pm |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.07.38948 | C001870375 | Selvin White | St.Elizabeth | Completed | Load_248429 | Maggotty - 210 | Jul 30, 2026 8:17pm | Jul 31, 2026 7:35am | Jul 31, 2026 8:30am | Jul 31, 2026 8:31am | Jul 31, 2026 9:12am | Jul 31, 2026 9:41am | Jul 31, 2026 9:41am | Jul 31, 2026 9:41am |  |  | Fair | No | Replace a defective 2 amp fuse for a 15 KVA transformer circuit at pole number 0187381 after patrolling secondary circuit.. supply restored to the area. Defective was found to be the cause.Fuse was separated from the housing.
Outage | J.E.26.07.39004 | C001870377 | Selvin White | St.Elizabeth | Completed | Load_1002211 | Maggotty - 210 | Jul 30, 2026 8:17pm | Jul 31, 2026 7:34am | Jul 31, 2026 10:30am | Jul 31, 2026 10:30am | Jul 31, 2026 10:41am | Jul 31, 2026 11:33am | Jul 31, 2026 11:33am | Jul 31, 2026 11:33am |  |  | SevereWind | No | Replace a blown 3 amp fuse for a 50 KVA transformer circuit after clearing banging secondary conductors coming into contact with customer’s service wire due to heavy wind and leaning 40 ft wooden pole. A section of the secondary conductor’s needs to be transferred from old pole and a section to be replaced by 2/0 twisted. Please advise the maintenance department. Supply restored to all the affected customers.
Outage | J.E.26.07.39014 | C001870378 | Andrew Powell | Manchester | Completed | Load_260938 | Spur Tree - 210 | Jul 30, 2026 8:17pm | Jul 30, 2026 8:23pm | Jul 30, 2026 10:19pm | Jul 30, 2026 10:19pm | Jul 30, 2026 10:49pm | Jul 30, 2026 11:05pm | Jul 30, 2026 11:10pm | Jul 30, 2026 11:10pm |  |  | Fair | No | Patrol and found clear, reset tripped 10 kva transformer circuit breaker by pole number 023300, restored supply okay.
Outage | J.E.26.07.38572 | C001870371 | Clyde Brown | Clarendon | Completed | Load_251382 | May Pen - 210 | Jul 30, 2026 7:39pm | Jul 30, 2026 7:39pm | Jul 30, 2026 7:52pm | Jul 30, 2026 7:52pm | Jul 30, 2026 8:36pm | Jul 30, 2026 8:36pm | Jul 30, 2026 8:45pm | Jul 30, 2026 8:45pm | TreeContact |  | Fair | No | Big guango tree in next door property and leaning over customer premises and near secondary line,customer advise.
Outage | J.E.26.07.38978 | C001870369 | Tyrese Williams | St.Ann | Completed | Load_269771 | Cardiff Hall - 310 | Jul 30, 2026 7:30pm | Jul 30, 2026 7:30pm | Jul 30, 2026 7:44pm | Jul 30, 2026 7:44pm | Jul 30, 2026 8:10pm | Jul 30, 2026 8:21pm | Jul 30, 2026 8:21pm | Jul 30, 2026 8:21pm |  |  | Fair | No | Replace a 20amp junction fuse at pole
Non-Outage | J.E.26.07.38986 | C001870368 | Wan Carlos Scarlett | St.Catherine | Completed | Load_569977 | Twickenham - 210 | Jul 30, 2026 7:29pm | Jul 30, 2026 7:29pm | Jul 30, 2026 7:44pm | Jul 30, 2026 7:44pm | Jul 30, 2026 8:26pm | Jul 30, 2026 9:13pm | Jul 30, 2026 9:24pm | Jul 30, 2026 9:24pm | BrokenPole |  | Fair | No | Found customer private meter pole rotten and fell and damaged customer vehicle advised customer that it is a internal issue advised customer to how to resolve the issue isolated customer service wire until repair is made contact back Jps for a reconnection
Outage | J.E.26.07.38747 | C001870366 | Richman Whyte | Westmoreland | Completed | Load_266710 | Paradise - 310 | Jul 30, 2026 7:28pm | Jul 30, 2026 7:31pm | Jul 30, 2026 8:34pm | Jul 30, 2026 8:34pm | Jul 30, 2026 8:34pm | Jul 30, 2026 8:35pm | Jul 30, 2026 8:35pm | Jul 30, 2026 8:35pm | LeaningPole |  | Fair | No | Hanover call
Outage | J.E.26.07.38782 | C001870365 | Richman Whyte | Westmoreland | Completed | Load_243915 | Paradise - 310 | Jul 30, 2026 7:28pm | Jul 30, 2026 7:31pm | Jul 30, 2026 8:36pm | Jul 30, 2026 8:36pm | Jul 30, 2026 8:36pm | Jul 30, 2026 8:36pm | Jul 30, 2026 8:37pm | Jul 30, 2026 8:37pm |  |  | Fair | No | Customer need a new meter refer to field service
Outage | J.E.26.07.38835 | C001870367 | Richman Whyte | Westmoreland | Completed | Load_249479 | Paradise - 310 | Jul 30, 2026 7:28pm | Jul 30, 2026 7:31pm | Jul 30, 2026 8:33pm | Jul 30, 2026 8:34pm | Jul 30, 2026 8:34pm | Jul 30, 2026 8:34pm | Jul 30, 2026 8:34pm | Jul 30, 2026 8:34pm |  |  | Fair | No | Hanover call
Outage | J.E.26.07.38947 | C001870364 | Shamour Haughton | St.James | Completed | Load_246347 | Queens Drive - 710 | Jul 30, 2026 7:21pm | Jul 30, 2026 10:55pm | Jul 31, 2026 1:16am | Jul 31, 2026 1:16am | Jul 31, 2026 1:16am | Jul 31, 2026 1:16am | Jul 31, 2026 1:19am | Jul 31, 2026 1:19am | Fire |  | Fair | No | Customer states that power was restored
Outage | J.E.26.07.38089 | C001870362 | Marlon Brown | null | Completed | Load_257118 | Greenwood - 110 | Jul 30, 2026 7:00pm | Jul 30, 2026 7:12pm | Jul 30, 2026 8:44pm | Jul 30, 2026 8:44pm | Jul 30, 2026 9:57pm | Jul 30, 2026 9:58pm | Jul 30, 2026 9:58pm | Jul 30, 2026 9:58pm |  |  | Fair | No | Premises Closed, customer not at home.
Outage | J.E.26.07.38940 | C001870360 | Devon Grant | KSAN | Completed | Load_250646 | Constant Spring - 210 | Jul 30, 2026 6:59pm | Jul 30, 2026 6:59pm | Jul 30, 2026 9:01pm | Jul 30, 2026 9:01pm | Jul 30, 2026 9:44pm | Jul 30, 2026 10:07pm | Jul 30, 2026 10:09pm | Jul 30, 2026 10:09pm |  |  | Fair | No | Reconnect customer by the meter socket.
Outage | J.E.26.07.38954 | C001870361 | Devon Grant | KSAN | Completed | Load_253684 | Constant Spring - 210 | Jul 30, 2026 6:59pm | Jul 30, 2026 6:59pm | Jul 30, 2026 10:09pm | Jul 30, 2026 10:37pm | Jul 30, 2026 10:37pm | Jul 30, 2026 10:23pm | Jul 30, 2026 10:38pm | Jul 30, 2026 10:38pm |  |  | Fair | No | Can’t locate customer premises, calls to customer went unanswered.
Outage | J.E.26.07.38949 | C001870359 | Andre Williams | Trelawny | Completed | Load_294543 | Duncans - 110 | Jul 30, 2026 6:56pm | Jul 30, 2026 7:08pm | Jul 30, 2026 7:41pm | Jul 30, 2026 7:41pm | Jul 30, 2026 7:58pm | Jul 30, 2026 8:00pm | Jul 30, 2026 8:00pm | Jul 30, 2026 8:00pm |  |  | Fair | No | Customer meter socket defective ,customer was advice to carry out repairs
Outage | J.E.26.07.38935 | C001870357 | Tyrese Williams | St.Ann | Completed | Load_1003802 | Cardiff Hall - 210 | Jul 30, 2026 6:36pm | Jul 30, 2026 6:36pm | Jul 30, 2026 7:21pm | Jul 30, 2026 7:40pm | Jul 30, 2026 7:40pm | Jul 30, 2026 7:41pm | Jul 30, 2026 7:41pm | Jul 30, 2026 7:41pm | BrokenWire |  | Fair | No | Call isn’t for st.ann team
Outage | J.E.26.07.38918 | C001870348 | Kaydon Taylor | KSAS | Completed | Load_579134 | Duhaney - 310 | Jul 30, 2026 5:56pm | Jul 30, 2026 5:56pm | Jul 30, 2026 6:35pm | Jul 30, 2026 6:37pm | Jul 30, 2026 7:37pm | Jul 30, 2026 7:39pm | Jul 30, 2026 7:39pm | Jul 30, 2026 7:39pm | BrokenWire |  | Fair | No | One clamp at pole v 116
Outage | J.E.26.07.38926 | C001870345 | Tajay Bernard | St.James | Completed | Load_269071 | Bogue - 510 | Jul 30, 2026 5:52pm | Jul 30, 2026 6:32pm | Jul 30, 2026 6:51pm | Jul 30, 2026 6:52pm | Jul 30, 2026 7:41pm | Jul 30, 2026 8:07pm | Jul 30, 2026 8:07pm | Jul 30, 2026 8:07pm |  |  | Fair | No | Reconnect customer service wire that was burnt off use 1 clamp voltage reading 112Cause (illegal connection was at the customer joint)
Outage | J.E.26.07.38868 | C001870338 | Nickolas Rodriques | St.Catherine | Completed | Load_260982 | Tredegar - 510 | Jul 30, 2026 5:39pm | Jul 30, 2026 5:39pm | Jul 30, 2026 7:25pm | Jul 30, 2026 7:25pm | Jul 30, 2026 8:22pm | Jul 30, 2026 8:45pm | Jul 30, 2026 8:45pm | Jul 30, 2026 8:45pm |  |  | Fair | No | Power restored. Customer confirmed that the power outage was restored.
Outage | J.E.26.07.38906 | C001870339 | Nickolas Rodriques | St.Catherine | Completed | Load_257427 | Tredegar - 510 | Jul 30, 2026 5:39pm | Jul 30, 2026 5:39pm | Jul 30, 2026 8:46pm | Jul 30, 2026 8:53pm | Jul 30, 2026 9:07pm | Jul 30, 2026 9:13pm | Jul 30, 2026 9:15pm | Jul 30, 2026 9:15pm |  |  | Fair | No | Found area with electricity. Customer confirmed that the power outage was later restored.
Outage | J.E.26.07.38899 | C001870335 | Omar King | St.Ann | Completed | Load_263941 | Upper White River - 210 | Jul 30, 2026 5:23pm | Jul 30, 2026 5:24pm | Jul 30, 2026 10:34pm | Jul 30, 2026 10:34pm | Jul 31, 2026 12:23am | Jul 31, 2026 1:28am | Jul 31, 2026 1:29am | Jul 31, 2026 1:29am |  |  | Fair | No | Found a10 amp junction fuse blow cause by vegetation fuse as been replaced area is now with supply
Outage | J.E.26.07.38905 | C001870334 | Tyrese Williams | St.Ann | Completed | Load_258385 | Cardiff Hall - 310 | Jul 30, 2026 5:23pm | Jul 30, 2026 5:23pm | Jul 30, 2026 5:33pm | Jul 30, 2026 5:33pm | Jul 30, 2026 6:00pm | Jul 30, 2026 6:04pm | Jul 30, 2026 6:04pm | Jul 30, 2026 6:04pm |  |  | Fair | No | Reset a 25 kva transformer at pole
Outage | J.E.26.07.38890 | C001870333 | Antony Levy | KSAN | Completed | Load_253062 | West Kings House - 410 | Jul 30, 2026 5:20pm | Jul 30, 2026 5:20pm | Jul 30, 2026 7:26pm | Jul 30, 2026 7:26pm | Jul 30, 2026 8:18pm | Jul 30, 2026 8:18pm | Jul 30, 2026 8:19pm | Jul 30, 2026 8:19pm |  |  | Fair | No | Call related to outage.
Outage | J.E.26.07.38364 | C001870332 | Tyrese Williams | St.Ann | Completed | Load_268647 | Cardiff Hall - 210 | Jul 30, 2026 5:17pm | Jul 30, 2026 5:18pm | Jul 30, 2026 5:35pm | Jul 30, 2026 6:04pm | Jul 30, 2026 7:16pm | Jul 30, 2026 7:32pm | Jul 30, 2026 7:32pm | Jul 30, 2026 7:32pm |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.07.38392 | C001870325 | Raymond Lewis | null | Completed | null | null | Jul 30, 2026 5:01pm | Jul 30, 2026 5:01pm | Jul 30, 2026 5:17pm | Jul 30, 2026 5:17pm | Jul 30, 2026 6:11pm | Jul 30, 2026 7:33pm | Jul 30, 2026 7:34pm | Jul 30, 2026 7:34pm |  | Y | Fair | No | Cut and remove tree from secondary line,remade neutral and phase on 25 kva x former,voltage 116/116/233
Outage | J.E.26.07.38450 | C001870324 | Tyrese Williams | St.Ann | Completed | Load_252510 | Cardiff Hall - 210 | Jul 30, 2026 5:01pm | Jul 30, 2026 5:01pm | Jul 30, 2026 5:15pm | Jul 30, 2026 5:15pm | Jul 30, 2026 5:16pm | Jul 30, 2026 5:16pm | Jul 30, 2026 5:17pm | Jul 30, 2026 5:17pm |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.07.38453 | C001870323 | Tyrese Williams | St.Ann | Completed | Load_254668 | Cardiff Hall - 310 | Jul 30, 2026 5:01pm | Jul 30, 2026 5:01pm | Jul 30, 2026 5:06pm | Jul 30, 2026 5:06pm | Jul 30, 2026 5:06pm | Jul 30, 2026 5:12pm | Jul 30, 2026 5:12pm | Jul 30, 2026 5:12pm |  |  | Fair | No | Premises found ok power was restored
Outage | J.E.26.07.38832 | C001870318 | Ryan Richards | Manchester | Completed | Load_265440 | Kendal - 210 | Jul 30, 2026 4:58pm | Jul 30, 2026 4:59pm | Jul 30, 2026 8:54pm | Jul 30, 2026 8:54pm | Jul 30, 2026 10:05pm | Jul 30, 2026 11:09pm | Jul 30, 2026 11:09pm | Jul 30, 2026 11:09pm |  |  | Fair | No | Corroded neutral found at pole remade corroded neutral using 1 one bolt clamps voltage 115/117/233 volts
Outage | J.E.26.07.38881 | C001870317 | Swon Miller | St.James | Completed | Load_238934 | Bogue - 310 | Jul 30, 2026 4:56pm | Jul 30, 2026 4:56pm | Jul 30, 2026 10:40pm | Jul 30, 2026 10:40pm | Jul 30, 2026 10:40pm | Jul 23, 2026 10:41pm | Jul 30, 2026 10:42pm | Jul 30, 2026 10:42pm |  |  | Fair | No | Call related to previous
Outage | J.E.26.07.38874 | C001870316 | Romeo Brissett | St.James | Completed | Load_256751 | Bogue - 610 | Jul 30, 2026 4:55pm | Jul 30, 2026 4:56pm | Jul 30, 2026 6:03pm | Jul 30, 2026 6:03pm | Jul 30, 2026 6:51pm | Jul 30, 2026 7:18pm | Jul 30, 2026 7:25pm | Jul 30, 2026 7:25pm |  |  | Fair | No | Removed several illegal connections and reset (1)10KVA transformer fuse.
Outage | J.E.26.07.37505 | C001870310 | Marlon Brown | Trelawny | Completed | Load_263936 | Greenwood - 210 | Jul 30, 2026 4:47pm | Jul 30, 2026 4:55pm | Jul 30, 2026 5:34pm | Jul 30, 2026 5:34pm | Jul 30, 2026 7:14pm | Jul 30, 2026 7:15pm | Jul 30, 2026 7:15pm | Jul 30, 2026 7:15pm |  |  | Fair | No | Found ok voltage leaving at meter socket 118/118=236Voltage found at meter socket 118/118=236
Outage | J.E.26.07.38518 | C001870304 | Richman Whyte | St.Elizabeth | Completed | Load_262537 | Maggotty - 110 | Jul 30, 2026 4:43pm | Jul 31, 2026 3:16pm | Jul 31, 2026 4:20pm | Jul 31, 2026 4:20pm | Jul 31, 2026 4:42pm | Jul 31, 2026 5:05pm | Jul 31, 2026 5:07pm | Jul 31, 2026 5:07pm | BrokenWire |  | Fair | No | Connect back burn off service wire at secondary line use 1 one bolt clamp voltage 109 110 220
Outage | J.E.26.07.38744 | C001870302 | Selvin White | St.Elizabeth | Completed | Load_570258 | Maggotty - 110 | Jul 30, 2026 4:43pm | Jul 31, 2026 7:30am | Jul 31, 2026 8:20am | Jul 31, 2026 2:13pm | Jul 31, 2026 3:19pm | Jul 31, 2026 3:20pm | Jul 31, 2026 3:22pm | Jul 31, 2026 3:22pm | BrokenWire |  | Fair | No | Escalation department was contacted and said customer meter was working okay however customer phone number is not working.
Outage | J.E.26.07.38752 | C001870303 | Richard Watson | St.Elizabeth | Completed | Load_255323 | Maggotty - 110 | Jul 30, 2026 4:43pm | Jul 31, 2026 3:13pm | Jul 31, 2026 4:21pm | Jul 31, 2026 4:21pm | Jul 31, 2026 5:12pm | Jul 31, 2026 5:30pm | Jul 31, 2026 5:30pm | Jul 31, 2026 5:30pm | BrokenWire |  | Fair | No | Replace approximately 70ft of defective #6 triplex service wire, also use one 1bolt clamp and three #6-#6 service sleeves, voltages left inside meter socket 110v, 112v, 222v.
Outage | J.E.26.07.38837 | C001870306 | Kaydon Taylor | KSAS | Completed | Load_579220 | Duhaney - 310 | Jul 30, 2026 4:43pm | Jul 30, 2026 4:44pm | Jul 30, 2026 5:24pm | Jul 30, 2026 5:50pm | Jul 30, 2026 5:50pm | Jul 30, 2026 5:52pm | Jul 30, 2026 5:52pm | Jul 30, 2026 5:52pm |  |  | Fair | No | Found okay
Outage | J.E.26.07.38842 | C001870301 | Antony Levy | KSAN | Completed | Load_266745 | West Kings House - 310 | Jul 30, 2026 4:43pm | Jul 30, 2026 5:20pm | Jul 30, 2026 5:26pm | Jul 30, 2026 5:26pm | Jul 30, 2026 6:43pm | Jul 30, 2026 7:24pm | Jul 30, 2026 7:25pm | Jul 30, 2026 7:25pm | Fire |  | Fair | No | West kings house 210 underground cable burnt load transfers to west kings house 410 all customers restored.
Outage | J.E.26.07.38843 | C001870305 | Kaydon Taylor | KSAS | Completed | Load_254965 | Duhaney - 310 | Jul 30, 2026 4:43pm | Jul 30, 2026 4:44pm | Jul 30, 2026 5:53pm | Jul 30, 2026 6:17pm | Jul 30, 2026 6:32pm | Jul 30, 2026 6:35pm | Jul 30, 2026 6:35pm | Jul 30, 2026 6:35pm | LowHangingWires |  | Fair | No | Telecommunication wire hanging low also defective 30’ wood at pole #050816
Outage | J.E.26.07.38863 | C001870307 | Swon Miller | St.James | Completed | Load_245091 | Bogue - 310 | Jul 30, 2026 4:43pm | Jul 30, 2026 4:46pm | Jul 30, 2026 10:42pm | Jul 30, 2026 10:42pm | Jul 30, 2026 10:42pm | Aug 6, 2026 10:43am | Jul 30, 2026 10:44pm | Jul 30, 2026 10:44pm |  |  | Fair | No
Outage | J.E.26.07.38869 | C001870300 | Swon Miller | St.James | Completed | Load_243690 | Bogue - 310 | Jul 30, 2026 4:43pm | Jul 30, 2026 4:46pm | Jul 30, 2026 9:18pm | Jul 30, 2026 9:18pm | Jul 30, 2026 9:38pm | Jul 22, 2026 10:33am | Jul 30, 2026 10:34pm | Jul 30, 2026 10:34pm |  |  | Fair | No | Check and area okay customer states that power was restored forty five minutes ago
Outage | J.E.26.07.38853 | C001870298 | Romeo Brissett | St.James | Completed | Load_556239 | Bogue - 610 | Jul 30, 2026 4:42pm | Jul 30, 2026 4:45pm | Jul 30, 2026 5:42pm | Jul 30, 2026 5:42pm | Jul 30, 2026 5:42pm | Jul 30, 2026 5:45pm | Jul 30, 2026 5:45pm | Jul 30, 2026 5:45pm |  |  | Fair | No | Check and found ok
Outage | J.E.26.07.38856 | C001870299 | Romeo Brissett | St.James | Completed | Load_556251 | Bogue - 610 | Jul 30, 2026 4:42pm | Jul 30, 2026 4:45pm | Jul 30, 2026 4:52pm | Jul 30, 2026 4:52pm | Jul 30, 2026 5:16pm | Jul 30, 2026 5:40pm | Jul 30, 2026 5:41pm | Jul 30, 2026 5:41pm |  |  | EarthMovement | No | Replaced (1)40qmps junction fuse. Switch need to change please send to maintenance.
Non-Outage | J.E.26.07.38873 | C001870297 | Wan Carlos Scarlett | null | Completed | null | null | Jul 30, 2026 4:41pm | Jul 30, 2026 4:41pm | Jul 30, 2026 7:41pm | Jul 30, 2026 7:41pm | Jul 30, 2026 7:42pm | Jul 30, 2026 7:43pm | Jul 30, 2026 7:44pm | Jul 30, 2026 7:44pm | BrokenWire |  | Fair | No | Call related to the broken wire outage earlier customer confirmed that power supply has been restored checked and found okay
Non-Outage | J.E.26.07.35737 | C001870296 | Andrew Powell | St.Elizabeth | Completed | Load_292854 | Maggotty - 210 | Jul 30, 2026 4:36pm | Jul 30, 2026 4:44pm | Jul 30, 2026 7:11pm | Jul 30, 2026 7:11pm | Jul 30, 2026 7:55pm | Jul 30, 2026 8:32pm | Jul 30, 2026 8:33pm | Jul 30, 2026 8:33pm |  |  | Fair | No | Remade corroded service wire joints at secondary line 3 wire using three clamps, voltage reading 112v-113v phase to neutral 225v cross phase.
Outage | J.E.26.07.37869 | C001870292 | Marlon Brown | Trelawny | Completed | Load_245255 | Greenwood - 110 | Jul 30, 2026 4:33pm | Jul 30, 2026 4:49pm | Jul 30, 2026 7:21pm | Jul 30, 2026 7:21pm | Jul 30, 2026 7:21pm | Jul 30, 2026 7:21pm | Jul 30, 2026 7:21pm | Jul 30, 2026 7:21pm |  |  | Fair | No | Streetlight issue.
Outage | J.E.26.07.38851 | C001870291 | Marlon Brown | Trelawny | Completed | Load_251586 | Greenwood - 110 | Jul 30, 2026 4:33pm | Jul 30, 2026 4:49pm | Jul 30, 2026 5:15pm | Jul 30, 2026 5:15pm | Jul 30, 2026 5:15pm | Jul 30, 2026 5:16pm | Jul 30, 2026 5:16pm | Jul 30, 2026 5:16pm |  |  | Fair | No | St James call
Outage | J.E.26.07.38724 | C001870290 | Marlon Brown | Trelawny | Completed | Load_1001692 | Greenwood - 210 | Jul 30, 2026 4:32pm | Jul 30, 2026 4:49pm | Jul 30, 2026 7:22pm | Jul 30, 2026 7:22pm | Jul 30, 2026 7:22pm | Jul 30, 2026 7:22pm | Jul 30, 2026 7:22pm | Jul 30, 2026 7:22pm |  |  | Fair | No | Customer says she didn’t make any report
Outage | J.E.26.07.38800 | C001870288 | Marlon Brown | Trelawny | Completed | Load_572265 | Martha Brae - 210 | Jul 30, 2026 4:32pm | Jul 30, 2026 4:49pm | Jul 30, 2026 7:23pm | Jul 30, 2026 7:23pm | Jul 30, 2026 7:23pm | Jul 30, 2026 7:24pm | Jul 30, 2026 7:24pm | Jul 30, 2026 7:24pm |  |  | Fair | No | Feeder issue
Outage | J.E.26.07.38839 | C001870289 | Andre Williams | Trelawny | Completed | Load_294599 | Duncans - 110 | Jul 30, 2026 4:32pm | Jul 30, 2026 4:54pm | Jul 30, 2026 8:20pm | Jul 30, 2026 8:20pm | Jul 30, 2026 8:46pm | Jul 30, 2026 8:48pm | Jul 30, 2026 8:48pm | Jul 30, 2026 8:48pm |  |  | Fair | No | Meter communicating confirm with supply by meter center.
Outage | J.E.26.07.38610 | C001870284 | Andrew Powell | St.Elizabeth | Completed | Load_242009 | Maggotty - 210 | Jul 30, 2026 4:26pm | Jul 30, 2026 4:26pm | Jul 30, 2026 5:52pm | Jul 30, 2026 5:52pm | Jul 30, 2026 6:16pm | Jul 30, 2026 7:02pm | Jul 30, 2026 7:05pm | Jul 30, 2026 7:05pm | Fire |  | Fair | No | Retention one pole span of sagging secondary upper phase conductor, burnt 25 kva transformer can’t tied in approximately 49 customers affected, please refer to Mr Delroy Crew for replacement.
Outage | J.E.26.07.38768 | C001870283 | Andrew Powell | Manchester | Completed | Load_268514 | Spur Tree - 210 | Jul 30, 2026 4:25pm | Jul 30, 2026 4:26pm | Jul 30, 2026 8:34pm | Jul 30, 2026 8:34pm | Jul 30, 2026 9:22pm | Jul 30, 2026 10:16pm | Jul 30, 2026 10:18pm | Jul 30, 2026 10:18pm |  |  | Fair | No | Splice and tension two pole span of broken secondary neutral conductor using two automatic splicing sleeves, replace blown 2 amp fuse protect 25 kva transformer circuit, no pole number by switch location, restore supply okay.
Outage | J.E.26.07.38829 | C001870282 | Andrew Powell | St.Elizabeth | Completed | Load_242009 | Maggotty - 210 | Jul 30, 2026 4:25pm | Jul 30, 2026 4:26pm | Jul 30, 2026 7:08pm | Jul 30, 2026 7:08pm | Jul 30, 2026 7:08pm | Jul 30, 2026 7:08pm | Jul 30, 2026 7:09pm | Jul 30, 2026 7:09pm |  |  | Fair | No | Called related to burnt transformer in Flagaman area leaves without supply.
Outage | J.E.26.07.38661 | C001870279 | Hopeton Henry | St.Thomas | Completed | Load_577217 | Good Year - 210 | Jul 30, 2026 4:23pm | Jul 30, 2026 5:02pm | Jul 30, 2026 5:06pm | Jul 30, 2026 5:06pm | Jul 30, 2026 8:11pm | Jul 30, 2026 8:11pm | Jul 30, 2026 8:16pm | Jul 30, 2026 8:16pm |  |  | Fair | No | Reset 10 kva transformer
Outage | J.E.26.07.38675 | C001870277 | Hopeton Henry | St.Thomas | Completed | Load_269555 | Good Year - 210 | Jul 30, 2026 4:22pm | Jul 30, 2026 5:02pm | Jul 30, 2026 5:06pm | Jul 30, 2026 8:17pm | Jul 30, 2026 9:12pm | Jul 30, 2026 9:31pm | Jul 30, 2026 9:33pm | Jul 30, 2026 9:33pm | Fire |  | Fair | No | No fire found
Outage | J.E.26.07.38769 | C001870278 | Hopeton Henry | St.Thomas | Completed | Load_253672 | Lysson - 410 | Jul 30, 2026 4:22pm | Jul 30, 2026 5:02pm | Jul 30, 2026 5:06pm | Jul 30, 2026 8:16pm | Jul 30, 2026 8:16pm | Jul 30, 2026 8:16pm | Jul 30, 2026 8:17pm | Jul 30, 2026 8:17pm |  |  | Fair | No | Reset 10kva transformer
Non-Outage | J.E.26.06.38227 | C001870272 | Fitzroy Turner | KSAS | Completed | Load_267729 | Rockfort - 410 | Jul 30, 2026 4:11pm | Jul 30, 2026 4:11pm | Jul 30, 2026 5:56pm | Jul 30, 2026 5:56pm | Jul 30, 2026 5:57pm | Jul 30, 2026 5:57pm | Jul 30, 2026 5:58pm | Jul 30, 2026 5:58pm |  |  | Fair | No | Customer premises found with electricity supply
Non-Outage | J.E.26.07.10971 | C001870271 | Fitzroy Turner | KSAS | Completed | Load_265849 | Rockfort - 210 | Jul 30, 2026 4:11pm | Jul 30, 2026 4:11pm | Jul 30, 2026 7:47pm | Jul 30, 2026 7:47pm | Jul 30, 2026 8:40pm | Jul 30, 2026 10:34pm | Jul 30, 2026 10:34pm | Jul 30, 2026 10:34pm |  |  | Fair | No | Customer premises found with electricity supply
Non-Outage | J.E.26.07.08283 | C001870267 | Fitzroy Turner | KSAS | Completed | Load_269212 | Rockfort - 410 | Jul 30, 2026 4:10pm | Jul 30, 2026 4:10pm | Jul 30, 2026 7:15pm | Jul 30, 2026 7:15pm | Jul 30, 2026 7:47pm | Jul 30, 2026 7:47pm | Jul 30, 2026 7:47pm | Jul 30, 2026 7:47pm |  |  | Fair | No | Customer premises found with electricity supply
Non-Outage | J.E.26.07.38790 | C001870269 | Daniel Francis | null | Completed | null | null | Jul 30, 2026 4:10pm | Jul 31, 2026 7:36am | Jul 31, 2026 8:50am | Jul 31, 2026 8:50am | Jul 31, 2026 9:43am | Jul 31, 2026 9:48am | Jul 31, 2026 9:48am | Jul 31, 2026 9:48am |  |  | Fair | No | Found ok
Outage | J.E.26.07.38828 | C001870268 | Evan Spaulding | St.Mary | Completed | Load_269725 | Highgate - 210 | Jul 30, 2026 4:10pm | Jul 30, 2026 4:11pm | Jul 30, 2026 7:01pm | Jul 30, 2026 7:01pm | Jul 30, 2026 7:51pm | Jul 30, 2026 8:24pm | Jul 30, 2026 8:25pm | Jul 30, 2026 8:25pm |  |  | Fair | No | Patrol line section no fault seen,replace 1-10 amps junction fuse at pole number 001076.
Outage | J.E.26.07.38831 | C001870270 | Jowayne Newmans | Portland | Completed | Load_260603 | Port Antonio - 410 | Jul 30, 2026 4:10pm | Jul 30, 2026 4:11pm | Jul 30, 2026 4:59pm | Jul 30, 2026 4:59pm | Jul 30, 2026 4:59pm | Jul 30, 2026 5:00pm | Jul 30, 2026 5:00pm | Jul 30, 2026 5:00pm |  |  | Fair | No | Customer got disconnected due to late bill payment.
Non-Outage | J.E.26.06.21613 | C001870256 | Fitzroy Turner | KSAS | Completed | Load_556758 | Cane River - 410 | Jul 30, 2026 4:09pm | Jul 30, 2026 4:10pm | Jul 30, 2026 6:02pm | Jul 30, 2026 6:02pm | Jul 30, 2026 6:02pm | Jul 30, 2026 6:05pm | Jul 30, 2026 6:20pm | Jul 30, 2026 6:20pm |  |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.07.36684 | C001870257 | Romeo Brissett | St.James | Completed | Load_242321 | Bogue - 510 | Jul 30, 2026 4:09pm | Jul 30, 2026 4:11pm | Jul 30, 2026 5:45pm | Jul 30, 2026 8:20pm | Jul 30, 2026 9:22pm | Jul 30, 2026 9:50pm | Jul 30, 2026 9:57pm | Jul 30, 2026 9:57pm |  |  | Fair | No | Replaced (1)8maps junction and (1)25KVA transformer fuse
Outage | J.E.26.07.38385 | C001870255 | Swon Miller | St.James | Completed | Load_268642 | Queens Drive - 310 | Jul 30, 2026 4:09pm | Jul 30, 2026 4:10pm | Jul 30, 2026 6:22pm | Jul 30, 2026 6:22pm | Jul 30, 2026 6:56pm | Jul 30, 2026 7:13pm | Jul 30, 2026 7:13pm | Jul 30, 2026 7:13pm |  |  | Fair | No | Check and found areas voltage found 117/117/234
Non-Outage | J.E.26.07.36826 | C001870251 | Fitzroy Turner | KSAS | Completed | Load_269395 | Hunts Bay - 510 | Jul 30, 2026 4:08pm | Jul 30, 2026 4:09pm | Jul 30, 2026 6:52pm | Jul 30, 2026 6:52pm | Jul 30, 2026 7:13pm | Jul 30, 2026 7:14pm | Jul 30, 2026 7:14pm | Jul 30, 2026 7:14pm |  |  | Fair | No | Premises close at this time
Outage | J.E.26.07.38607 | C001870252 | Fitzroy Turner | KSAS | Completed | Load_556657 | Cane River - 410 | Jul 30, 2026 4:08pm | Jul 30, 2026 4:09pm | Jul 30, 2026 5:49pm | Jul 30, 2026 6:21pm | Jul 30, 2026 6:47pm | Jul 30, 2026 6:48pm | Jul 30, 2026 6:49pm | Jul 30, 2026 6:49pm |  |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.07.38734 | C001870253 | Fitzroy Turner | KSAS | Completed | Load_239591 | Cane River - 610 | Jul 30, 2026 4:08pm | Jul 30, 2026 4:09pm | Jul 30, 2026 4:23pm | Jul 30, 2026 4:23pm | Jul 30, 2026 5:17pm | Jul 30, 2026 5:45pm | Jul 30, 2026 5:47pm | Jul 30, 2026 5:47pm |  |  | Fair | No | Found tree phase primary one phase blown cause by defective drop out switch.change one defective drop out switch and one 8 amps fuse supply restored to customer
Outage | J.E.26.07.38405 | C001870249 | Andre Smith | KSAS | Completed | Load_263810 | Greenwich - 710 | Jul 30, 2026 4:07pm | Jul 30, 2026 4:07pm | Jul 30, 2026 6:58pm | Jul 30, 2026 6:58pm | Jul 30, 2026 8:27pm | Jul 30, 2026 8:44pm | Jul 30, 2026 8:44pm | Jul 30, 2026 8:44pm |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.38592 | C001870246 | Andre Smith | KSAS | Completed | Load_244165 | Greenwich - 710 | Jul 30, 2026 4:07pm | Jul 30, 2026 4:07pm | Jul 30, 2026 6:38pm | Jul 30, 2026 6:38pm | Jul 30, 2026 6:49pm | Jul 30, 2026 6:57pm | Jul 30, 2026 6:57pm | Jul 30, 2026 6:57pm |  |  | Fair | No | Premises found okay supply restored already
Outage | J.E.26.07.38685 | C001870248 | Andre Smith | KSAS | Completed | Load_239090 | Up Park Camp - 310 | Jul 30, 2026 4:07pm | Jul 30, 2026 4:07pm | Jul 30, 2026 9:45pm | Jul 30, 2026 9:45pm | Jul 30, 2026 10:24pm | Jul 30, 2026 10:24pm | Jul 30, 2026 10:24pm | Jul 30, 2026 10:24pm |  |  | Fair | No | Premises found okay supply restored already
Outage | J.E.26.07.38801 | C001870250 | Andre Smith | KSAS | Completed | Load_242523 | Greenwich - 310 | Jul 30, 2026 4:07pm | Jul 30, 2026 4:07pm | Jul 30, 2026 8:44pm | Jul 30, 2026 8:44pm | Jul 30, 2026 9:44pm | Jul 30, 2026 9:45pm | Jul 30, 2026 9:45pm | Jul 30, 2026 9:45pm | BrokenWire |  | Fair | No | Repair broken secondary phase cause by illegal connections supply restored
Outage | J.E.26.07.38819 | C001870247 | Andre Smith | KSAN | Completed | Load_243339 | Washington Blvd - 710 | Jul 30, 2026 4:07pm | Jul 30, 2026 4:07pm | Jul 30, 2026 4:32pm | Jul 30, 2026 4:32pm | Jul 30, 2026 5:38pm | Jul 30, 2026 6:33pm | Jul 30, 2026 6:35pm | Jul 30, 2026 6:35pm | BrokenWire |  | Fair | No | Broken secondary phase cause by illegal connections repair using 4ft 2/0 aaa supply restored
Outage | J.E.26.07.38788 | C001870236 | Swon Miller | St.James | Completed | Load_266817 | Bogue - 310 | Jul 30, 2026 4:04pm | Jul 30, 2026 4:05pm | Jul 30, 2026 10:51pm | Jul 30, 2026 10:51pm | Jul 30, 2026 10:52pm | Jul 21, 2026 10:54am | Jul 30, 2026 10:56pm | Jul 30, 2026 10:56pm |  |  | Fair | No | Call related to previous
Outage | J.E.26.07.38797 | C001870235 | Romeo Brissett | St.James | Completed | Load_258600 | Bogue - 610 | Jul 30, 2026 4:04pm | Jul 30, 2026 4:06pm | Jul 30, 2026 7:25pm | Jul 30, 2026 7:25pm | Jul 30, 2026 7:50pm | Jul 30, 2026 8:20pm | Jul 30, 2026 8:20pm | Jul 30, 2026 8:20pm |  |  | Fair | No | Spliced and retention customer service wire. Used 20ft of #6 and 3 clamps V/R 113-112-226
Non-Outage | J.E.26.07.38547 | C001870232 | Swon Miller | null | Completed | null | null | Jul 30, 2026 4:02pm | Jul 30, 2026 4:06pm | Jul 30, 2026 7:14pm | Jul 30, 2026 7:14pm | Jul 30, 2026 7:47pm | Jul 29, 2026 8:05am | Jul 30, 2026 8:05pm | Jul 30, 2026 8:05pm | TreeContact |  | Fair | No | Found one span secondary lines overgrown with vegetation heavy bushing required plz refer to maintenance/k.Frazier voltage found 116/116/233 voltage left 116/116/233
Outage | J.E.26.07.38799 | C001870231 | Shamour Haughton | St.James | Completed | Load_243043 | Queens Drive - 710 | Jul 30, 2026 4:02pm | Jul 30, 2026 11:04pm | Jul 31, 2026 1:22am | Jul 31, 2026 1:22am | Jul 31, 2026 1:22am | Jul 31, 2026 1:22am | Jul 31, 2026 1:23am | Jul 31, 2026 1:23am |  |  | Fair | No | Customer states that power was restored
Non-Outage | J.E.26.07.26248 | C001870228 | Nickolas Rodriques | St.Catherine | Completed | Load_248862 | Tredegar - 510 | Jul 30, 2026 3:55pm | Jul 30, 2026 3:55pm | Jul 30, 2026 4:12pm | Jul 30, 2026 4:32pm | Jul 30, 2026 6:03pm | Jul 30, 2026 6:38pm | Jul 30, 2026 6:39pm | Jul 30, 2026 6:39pm |  |  | Fair | No | No noticeable fire was seen upon arrival. Customer stated that the issue was already resolved.
Non-Outage | J.E.26.07.26316 | C001870226 | Nickolas Rodriques | St.Catherine | Completed | Load_248862 | Tredegar - 510 | Jul 30, 2026 3:55pm | Jul 30, 2026 3:55pm | Jul 30, 2026 6:39pm | Jul 30, 2026 6:40pm | Jul 30, 2026 6:56pm | Jul 30, 2026 7:13pm | Jul 30, 2026 7:25pm | Jul 30, 2026 7:25pm |  |  | Fair | No | Unable to communicate with this specific customer, however, no fire/sparking was observed upon arrival.
Non-Outage | J.E.26.07.26651 | C001870225 | Nickolas Rodriques | St.Catherine | Completed | Load_269784 | Tredegar - 510 | Jul 30, 2026 3:55pm | Jul 30, 2026 3:55pm | Jul 30, 2026 10:33pm | Jul 30, 2026 10:34pm | Jul 30, 2026 11:03pm | Jul 30, 2026 11:06pm | Jul 30, 2026 11:09pm | Jul 30, 2026 11:09pm |  |  | Fair | No | Found customer with electricity. The customer confirmed that the issue was resolved by another team.
Non-Outage | J.E.26.07.27223 | C001870227 | Nickolas Rodriques | St.Catherine | Completed | Load_251832 | Tredegar - 510 | Jul 30, 2026 3:55pm | Jul 30, 2026 3:55pm | Jul 30, 2026 9:17pm | Jul 30, 2026 9:17pm | Jul 30, 2026 9:49pm | Jul 30, 2026 10:23pm | Jul 30, 2026 10:32pm | Jul 30, 2026 10:32pm |  |  | Fair | No | Customer stated that she is unable to accommodate the team at this time and is requesting a team on Saturday August 01, 2026.
Outage | J.E.26.07.36775 | C001870220 | Tajay Bernard | St.James | Completed | Load_242544 | Orange Bay - 310 | Jul 30, 2026 3:54pm | Jul 30, 2026 4:20pm | Jul 30, 2026 5:37pm | Jul 30, 2026 5:37pm | Jul 30, 2026 5:37pm | Jul 30, 2026 5:38pm | Jul 30, 2026 5:38pm | Jul 30, 2026 5:38pm |  |  | Fair | No | Customer stated that power was restored
Outage | J.E.26.07.38165 | C001870218 | Tajay Bernard | St.James | Completed | Load_252019 | Orange Bay - 310 | Jul 30, 2026 3:53pm | Jul 30, 2026 4:19pm | Jul 30, 2026 5:38pm | Jul 30, 2026 6:08pm | Jul 30, 2026 6:08pm | Jul 30, 2026 6:08pm | Jul 30, 2026 6:08pm | Jul 30, 2026 6:08pm |  |  | Fair | No | Customer stated that power was restored
Outage | J.E.26.07.38365 | C001870212 | Tajay Bernard | St.James | Completed | Load_250581 | Bogue - 510 | Jul 30, 2026 3:53pm | Jul 30, 2026 4:18pm | Jul 30, 2026 4:21pm | Jul 30, 2026 4:37pm | Jul 30, 2026 5:28pm | Jul 30, 2026 5:37pm | Jul 30, 2026 5:37pm | Jul 30, 2026 5:37pm |  |  | Fair | No | Premises check and found okay voltage found 117/117/234
Outage | J.E.26.07.38478 | C001870213 | Richard Watson | Manchester | Completed | Load_302835 | Spur Tree - 210 | Jul 30, 2026 3:53pm | Jul 30, 2026 4:28pm | Jul 30, 2026 7:18pm | Jul 30, 2026 7:18pm | Jul 30, 2026 7:34pm | Jul 30, 2026 7:49pm | Jul 30, 2026 7:50pm | Jul 30, 2026 7:50pm | BrokenWire |  | Fair | No | Service wire phase from secondary pole to meter pole, broken in mid-span, customer pothead and conduit damaged, service wire disconnected in midspan and taped off, service wire entanglement in cables, follow up with bucket truck required to disconnect service wire from secondary pole.
Outage | J.E.26.07.38481 | C001870215 | Richard Watson | St.Elizabeth | Completed | Load_239662 | Maggotty - 110 | Jul 30, 2026 3:53pm | Jul 30, 2026 4:28pm | Jul 30, 2026 8:06pm | Jul 30, 2026 8:06pm | Jul 30, 2026 8:59pm | Jul 30, 2026 9:12pm | Jul 30, 2026 9:20pm | Jul 30, 2026 9:20pm |  |  | Fair | No | Found fuse holder barrel down due to slack contact in slot, unscrew a portion of fuse holder barrel head, close switch and restore supply to area.
Outage | J.E.26.07.38555 | C001870214 | Richard Watson | Manchester | Completed | Load_573423 | Spur Tree - 210 | Jul 30, 2026 3:53pm | Jul 30, 2026 4:29pm | Jul 30, 2026 5:51pm | Jul 30, 2026 5:51pm | Jul 30, 2026 5:56pm | Jul 30, 2026 5:58pm | Jul 30, 2026 5:58pm | Jul 30, 2026 5:58pm |  |  | Fair | No | Area found with supply upon arrival.
Outage | J.E.26.07.38648 | C001870216 | Marlon Authors | Manchester | Completed | Load_244726 | Spur Tree - 210 | Jul 30, 2026 3:53pm | Jul 31, 2026 7:39am | Jul 31, 2026 7:48am | Jul 31, 2026 7:57am | Jul 31, 2026 7:57am | Jul 31, 2026 7:59am | Jul 31, 2026 7:59am | Jul 31, 2026 7:59am |  |  | Fair | No | Customer said supply was restored
Outage | J.E.26.07.38652 | C001870217 | Richard Watson | Manchester | Completed | Load_302821 | Spur Tree - 210 | Jul 30, 2026 3:53pm | Jul 30, 2026 4:29pm | Jul 30, 2026 6:18pm | Jul 30, 2026 6:18pm | Jul 30, 2026 6:23pm | Jul 30, 2026 6:28pm | Jul 30, 2026 6:28pm | Jul 30, 2026 6:28pm |  |  | Fair | No | Premises found okay.
Outage | J.E.26.07.38704 | C001870205 | Wan Carlos Scarlett | St.Catherine | Completed | Load_251991 | Twickenham - 210 | Jul 30, 2026 3:47pm | Jul 31, 2026 7:11am | Jul 31, 2026 10:37am | Jul 31, 2026 10:37am | Jul 31, 2026 11:08am | Jul 31, 2026 11:21am | Jul 31, 2026 11:26am | Jul 31, 2026 11:26am | Fire |  | Fair | No | Customer confirmed issue was resolved by a licensed electrician customer breaker was defective check and found okay reading 112 113 226
Outage | J.E.26.07.37969 | C001870204 | Wan Carlos Scarlett | Portmore | Completed | Load_248824 | Naggo Head - 510 | Jul 30, 2026 3:46pm | Jul 30, 2026 3:47pm | Jul 30, 2026 4:09pm | Jul 30, 2026 9:24pm | Jul 30, 2026 9:52pm | Jul 30, 2026 10:45pm | Jul 30, 2026 10:47pm | Jul 30, 2026 10:47pm |  |  | Fair | No | Found customer with internal problem customer service main defective advised customer to contact a licensed electrician to fix the issue
Outage | J.E.26.07.38738 | C001870199 | Wan Carlos Scarlett | St.Catherine | Completed | Load_248053 | Twickenham - 210 | Jul 30, 2026 3:46pm | Jul 30, 2026 3:47pm | Jul 30, 2026 4:10pm | Jul 30, 2026 4:12pm | Jul 30, 2026 4:12pm | Jul 30, 2026 7:30pm | Jul 30, 2026 7:40pm | Jul 30, 2026 7:40pm | BrokenWire |  | Fair | No | Found 6 span of open secondary top phase and neutral wire burn down by Jps bushing contractor use 200ft #2 aluminum wire 9 preform 7 splicing sleeve 12 one bolt clamps isolate and close 50 KVA transformer no pole # was found power supply has been restored
Outage | J.E.26.07.38785 | C001870184 | Neville Spencer | Clarendon | Completed | Load_267921 | May Pen - 110 | Jul 30, 2026 3:37pm | Jul 30, 2026 3:38pm | Jul 30, 2026 3:47pm | Jul 30, 2026 3:47pm | Jul 30, 2026 5:27pm | Jul 30, 2026 5:54pm | Jul 30, 2026 5:55pm | Jul 30, 2026 5:55pm | Fire |  | Fair | No | Open 25 kva xmf retention one span of secondary phase supply restored.
Outage | J.E.26.07.38786 | C001870183 | Raymond Carr | St.Mary | Completed | Load_258412 | Oracabessa - 210 | Jul 30, 2026 3:36pm | Jul 30, 2026 3:38pm | Jul 30, 2026 7:08pm | Jul 30, 2026 7:08pm | Jul 30, 2026 7:36pm | Jul 30, 2026 8:00pm | Jul 30, 2026 8:17pm | Jul 30, 2026 8:17pm | BrokenWire |  | SevereWind | No | One span of banged secondary conductors were cleared, due to heavy winds, supply restored to normal now.
Outage | J.E.26.07.38387 | C001870182 | Richard Nicholas | St.Catherine | Completed | Load_257986 | Tredegar - 210 | Jul 30, 2026 3:35pm | Jul 30, 2026 3:35pm | Jul 30, 2026 10:20pm | Jul 30, 2026 10:20pm | Jul 30, 2026 10:40pm | Jul 30, 2026 11:01pm | Jul 30, 2026 11:03pm | Jul 30, 2026 11:03pm |  |  | Fair | No | Rammy system in the area,premises found close however area is unsafe to work at night.pleaes refer to field service.
Outage | J.E.26.07.38791 | C001870180 | Richard Nicholas | St.Catherine | Completed | Load_265936 | Tredegar - 210 | Jul 30, 2026 3:34pm | Jul 30, 2026 3:34pm | Jul 30, 2026 7:23pm | Jul 30, 2026 7:23pm | Jul 30, 2026 8:18pm | Jul 30, 2026 9:20pm | Jul 30, 2026 9:21pm | Jul 30, 2026 9:21pm |  |  | Fair | No | Replaced blown 30amp x3 junctions fuse near to pole #0053480.
Outage | J.E.26.07.38421 | C001870178 | Richard Nicholas | St.Catherine | Completed | Load_1001442 | Tredegar - 210 | Jul 30, 2026 3:32pm | Jul 30, 2026 3:32pm | Jul 30, 2026 9:22pm | Jul 30, 2026 9:22pm | Jul 30, 2026 9:52pm | Jul 30, 2026 1:00am | Jul 30, 2026 10:20pm | Jul 30, 2026 10:20pm |  |  | Fair | No | Found ok
Outage | J.E.26.07.38406 | C001870176 | Richard Nicholas | St.Catherine | Completed | Load_246786 | Tredegar - 410 | Jul 30, 2026 3:30pm | Jul 30, 2026 3:30pm | Jul 30, 2026 6:55pm | Jul 30, 2026 6:55pm | Jul 30, 2026 7:14pm | Jul 30, 2026 7:22pm | Jul 30, 2026 7:23pm | Jul 30, 2026 7:23pm |  |  | Fair | No | Area found ok
Outage | J.E.26.07.38426 | C001870174 | Richard Nicholas | St.Catherine | Completed | Load_241062 | Tredegar - 410 | Jul 30, 2026 3:30pm | Jul 30, 2026 3:30pm | Jul 30, 2026 3:54pm | Jul 30, 2026 3:54pm | Jul 30, 2026 5:25pm | Jul 30, 2026 6:47pm | Jul 30, 2026 6:50pm | Jul 30, 2026 6:50pm |  |  | Fair | No | Replaced blown 30amp junctions fuse on pole #006728,blown 50amp junctions at the intersection of Adelaide st. And young st and blown 15kva transformer 2amp fuse on pole #600702.
Outage | J.E.26.07.38467 | C001870175 | Devon Grant | KSAN | Completed | Load_247559 | Constant Spring - 210 | Jul 30, 2026 3:30pm | Jul 30, 2026 3:30pm | Jul 30, 2026 5:49pm | Jul 30, 2026 5:49pm | Jul 30, 2026 6:19pm | Jul 30, 2026 6:27pm | Jul 30, 2026 6:28pm | Jul 30, 2026 6:28pm | BrokenWire |  | Fair | No | Premises closed
Non-Outage | J.E.26.07.38779 | C001870173 | Kaydon Taylor | null | Completed | null | null | Jul 30, 2026 3:29pm | Jul 30, 2026 3:33pm | Jul 30, 2026 4:11pm | Jul 30, 2026 4:46pm | Jul 30, 2026 5:22pm | Jul 30, 2026 5:23pm | Jul 30, 2026 5:23pm | Jul 30, 2026 5:23pm | Fire |  | Fair | No | Found okay
Outage | J.E.26.07.38644 | C001870168 | Devon Grant | KSAN | Completed | Load_557772 | Constant Spring - 210 | Jul 30, 2026 3:29pm | Jul 30, 2026 3:30pm | Jul 30, 2026 4:52pm | Jul 30, 2026 4:52pm | Jul 30, 2026 5:48pm | Jul 30, 2026 5:48pm | Jul 30, 2026 5:48pm | Jul 30, 2026 5:48pm |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.38692 | C001870170 | Devon Grant | KSAN | Completed | Load_258114 | Constant Spring - 210 | Jul 30, 2026 3:29pm | Jul 30, 2026 3:30pm | Jul 30, 2026 8:25pm | Jul 30, 2026 8:25pm | Jul 30, 2026 9:00pm | Jul 30, 2026 9:00pm | Jul 30, 2026 9:00pm | Jul 30, 2026 9:00pm |  |  | Fair | No | 3w open secondary circuit, repair broken neutral by using 7ft #2AA conductor and four onebolt clamps
Non-Outage | J.E.26.07.38424 | C001870167 | Ryan Richards | Manchester | Completed | Load_249671 | Kendal - 210 | Jul 30, 2026 3:27pm | Jul 30, 2026 3:28pm | Jul 30, 2026 3:34pm | Jul 30, 2026 3:34pm | Jul 30, 2026 5:14pm | Jul 30, 2026 6:12pm | Jul 30, 2026 6:22pm | Jul 30, 2026 6:22pm |  |  | Fair | No | Corroded phase and neutral found at pole and corroded neutral splicing sleeve found jumped splicing sleeve remade corroded phase using 2 one bolt clamps 110/109/220 volts
Outage | J.E.26.07.38672 | C001870165 | Ryan Richards | Manchester | Completed | Load_254977 | Kendal - 210 | Jul 30, 2026 3:26pm | Jul 30, 2026 3:28pm | Jul 30, 2026 6:28pm | Jul 30, 2026 6:39pm | Jul 30, 2026 7:48pm | Jul 30, 2026 8:53pm | Jul 30, 2026 8:54pm | Jul 30, 2026 8:54pm | BrokenWire |  | Fair | No | No service wire found at premises customer was disconnected from hurricane Melissa replaced 100ft#6 triplex 3 penunion 3 one bolt clamps voltage 113/116/229 volts
Non-Outage | J.E.26.07.37019 | C001870159 | Richman Whyte | Westmoreland | Completed | Load_259004 | Paradise - 310 | Jul 30, 2026 3:21pm | Jul 30, 2026 3:21pm | Jul 30, 2026 6:58pm | Jul 30, 2026 6:58pm | Jul 30, 2026 6:58pm | Jul 30, 2026 6:58pm | Jul 30, 2026 6:59pm | Jul 30, 2026 6:59pm |  |  | Fair | No | Same area same person clean corrosion on service wire at pothead and pole voltage 115 114 230
Outage | J.E.26.07.38502 | C001870160 | Moses Elliston | St.Catherine | Completed | Load_270150 | Twickenham - 410 | Jul 30, 2026 3:21pm | Jul 30, 2026 3:22pm | Jul 31, 2026 10:45am | Jul 31, 2026 10:45am | Jul 31, 2026 10:45am | Jul 31, 2026 10:45am | Jul 31, 2026 10:47am | Jul 31, 2026 10:47am |  |  | Fair | No | Credit added to prepaid account.
Non-Outage | J.E.26.07.36073 | C001870158 | Richman Whyte | Westmoreland | Completed | Load_249230 | Paradise - 310 | Jul 30, 2026 3:20pm | Jul 30, 2026 3:21pm | Jul 30, 2026 5:14pm | Jul 30, 2026 5:14pm | Jul 30, 2026 5:14pm | Jul 30, 2026 5:14pm | Jul 30, 2026 5:14pm | Jul 30, 2026 5:14pm |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.07.36362 | C001870155 | Richman Whyte | Westmoreland | Completed | Load_254517 | Paradise - 310 | Jul 30, 2026 3:20pm | Jul 30, 2026 3:21pm | Jul 30, 2026 5:10pm | Jul 30, 2026 5:10pm | Jul 30, 2026 5:10pm | Jul 30, 2026 5:11pm | Jul 30, 2026 5:11pm | Jul 30, 2026 5:11pm |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.07.38567 | C001870156 | Richman Whyte | Westmoreland | Completed | Load_266113 | Paradise - 310 | Jul 30, 2026 3:20pm | Jul 30, 2026 3:21pm | Jul 30, 2026 3:46pm | Jul 30, 2026 3:46pm | Jul 30, 2026 4:46pm | Jul 30, 2026 5:07pm | Jul 30, 2026 5:08pm | Jul 30, 2026 5:08pm |  |  | Fair | No | Customer have internal problem advise to fix voltage 111 110 220
Non-Outage | J.E.26.07.38569 | C001870157 | Richman Whyte | Westmoreland | Completed | Load_259004 | Paradise - 310 | Jul 30, 2026 3:20pm | Jul 30, 2026 3:21pm | Jul 30, 2026 6:56pm | Jul 30, 2026 6:56pm | Jul 30, 2026 6:57pm | Jul 30, 2026 6:57pm | Jul 30, 2026 6:58pm | Jul 30, 2026 6:58pm |  |  | Fair | No | Clean corrosion on service wire at pothead and pole use four one bolt clamps voltage 115 114 230
Outage | J.E.26.07.37552 | C001870146 | Marlon Brown | Trelawny | Completed | Load_292361 | Greenwood - 210 | Jul 30, 2026 3:19pm | Jul 30, 2026 6:54pm | Jul 30, 2026 7:15pm | Jul 30, 2026 7:15pm | Jul 30, 2026 7:15pm | Jul 30, 2026 7:16pm | Jul 30, 2026 7:16pm | Jul 30, 2026 7:16pm |  |  | Fair | No | Fixed by electrician
Outage | J.E.26.07.38706 | C001870149 | Moses Elliston | St.Catherine | Completed | Load_242360 | Tredegar - 510 | Jul 30, 2026 3:19pm | Jul 30, 2026 3:20pm | Jul 31, 2026 11:07am | Jul 31, 2026 11:07am | Jul 31, 2026 11:07am | Jul 31, 2026 11:08am | Jul 31, 2026 11:09am | Jul 31, 2026 11:09am |  |  | Fair | No | Pay as you go account reconnected
Outage | J.E.26.07.38777 | C001870145 | Evan Spaulding | St.Mary | Completed | Load_239455 | Highgate -110 | Jul 30, 2026 3:18pm | Jul 30, 2026 3:19pm | Jul 30, 2026 4:07pm | Jul 30, 2026 4:07pm | Jul 30, 2026 4:52pm | Jul 30, 2026 4:59pm | Jul 30, 2026 5:03pm | Jul 30, 2026 5:03pm | Fire |  | Fair | No | Sparks was coming from flow strand wire earlier today,but no sparks is there presently.
Outage | J.E.26.07.38402 | C001870138 | Andre Williams | Trelawny | Completed | Load_294596 | Duncans - 110 | Jul 30, 2026 3:17pm | Jul 30, 2026 4:51pm | Jul 30, 2026 5:21pm | Jul 30, 2026 8:06pm | Jul 30, 2026 8:18pm | Jul 30, 2026 8:19pm | Jul 30, 2026 8:20pm | Jul 30, 2026 8:20pm |  |  | Fair | No | Premises ok confirm by meter center communication establish with meter
Outage | J.E.26.07.38532 | C001870140 | Michael Paterson | Westmoreland | Completed | Load_250137 | Paradise - 110 | Jul 30, 2026 3:17pm | Jul 31, 2026 7:49am | Jul 31, 2026 3:01pm | Jul 31, 2026 3:01pm | Jul 31, 2026 3:01pm | Jul 31, 2026 3:02pm | Jul 31, 2026 3:02pm | Jul 31, 2026 3:02pm |  |  | Fair | No | Found 25kva xfmr fuse blown as a result of motor vehicle accident, third party pole broken, also, splice and retention four span of secondary, using three 2/0 preform, four clamps, 60ft # 2 AA conductor, replace 2amps fuse, supply restored, voltage readings 117v, 119v, 236v.
Outage | J.E.26.07.38580 | C001870141 | Michael Paterson | Westmoreland | Completed | Load_268696 | Paradise - 210 | Jul 30, 2026 3:17pm | Jul 31, 2026 7:49am | Jul 31, 2026 11:05am | Jul 31, 2026 11:21am | Jul 31, 2026 11:21am | Jul 31, 2026 11:46am | Jul 31, 2026 11:46am | Jul 31, 2026 11:46am |  |  | Fair | No | Check and found ok, voltage readings 105v, 108v, 213v, however, customer disputes getting high bills that are being estimated, communication issues, please refer to Claint Johnson at paradise to address problem.
Outage | J.E.26.07.38739 | C001870143 | Raymond Carr | St.Mary | Completed | Load_576544 | Oracabessa - 110 | Jul 30, 2026 3:17pm | Jul 30, 2026 3:18pm | Jul 30, 2026 3:37pm | Jul 30, 2026 3:37pm | Jul 30, 2026 4:51pm | Jul 23, 2026 6:25pm | Jul 30, 2026 6:48pm | Jul 30, 2026 6:48pm | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | SevereWind | No | Blown 25 kva transformer fuse found, line patrol and found 1 span of secondary phase dislodged, also two other sagging spans were tensioned. A 2 amp fuse was used to renew supply was restored.
Outage | J.E.26.07.38766 | C001870136 | Romeo Brissett | St.James | Completed | Load_302647 | Bogue - 410 | Jul 30, 2026 3:15pm | Jul 30, 2026 3:15pm | Jul 30, 2026 3:30pm | Jul 30, 2026 3:30pm | Jul 30, 2026 4:04pm | Jul 30, 2026 4:44pm | Jul 30, 2026 4:52pm | Jul 30, 2026 4:52pm |  |  | Fair | No | Replaced (1)50amps junction fuse and (1)100kva transformer fuse, used (1)8amps and (1)50amps
Non-Outage | J.E.26.07.38396 | C001870129 | Richard Grant | null | Completed | null | null | Jul 30, 2026 3:14pm | Jul 30, 2026 3:15pm | Jul 30, 2026 5:51pm | Jul 30, 2026 6:23pm | Jul 30, 2026 6:23pm | Jul 30, 2026 6:24pm | Jul 30, 2026 6:24pm | Jul 30, 2026 6:24pm | BrokenPole |  | Fair | No | 2 span of broken phase and neutral for opened secondary found caused by illegal connection. 2 #2 sleeves, 1 2/0 sleeve, 1 2/0 preform, 3 onebolt clamps, approximately 20ft #2 wire and approximately 80ft 2/0 wire used to retention line section. Supply restored and area left okay.
Outage | J.E.26.07.38690 | C001870127 | Swon Miller | St.James | Completed | Load_302104 | Queens Drive - 710 | Jul 30, 2026 3:13pm | Jul 30, 2026 3:13pm | Jul 30, 2026 8:07pm | Jul 30, 2026 8:07pm | Jul 30, 2026 8:49pm | Jul 15, 2026 9:05am | Jul 30, 2026 9:18pm | Jul 30, 2026 9:18pm |  |  | Fair | No | Unable to carry out repairs dues to interference from residents who wants the service wire to be removed from their yard daylight attention required
Outage | J.E.26.07.38730 | C001870126 | Swon Miller | St.James | Completed | Load_240235 | Queens Drive - 310 | Jul 30, 2026 3:13pm | Jul 30, 2026 3:13pm | Jul 30, 2026 3:24pm | Jul 30, 2026 3:24pm | Jul 30, 2026 3:48pm | Jul 20, 2026 6:45am | Jul 30, 2026 6:05pm | Jul 30, 2026 6:05pm |  |  | Fair | No | Check and found 25 kva transformer trip and customer meter socket burnt cause by severe winds which caused customer pothead to bang up and burnt isolate customers service wire and advise customer to get pothead and meter socket repair before power supply can be restored reset 25 kva transformer no pole available voltage found 0.000 voltage left 115/116/232
Non-Outage | J.E.26.07.38605 | C001870124 | Richard Grant | null | Completed | null | null | Jul 30, 2026 3:10pm | Jul 30, 2026 3:12pm | Jul 30, 2026 6:25pm | Jul 30, 2026 6:25pm | Jul 30, 2026 7:21pm | Jul 30, 2026 7:23pm | Jul 30, 2026 7:23pm | Jul 30, 2026 7:23pm |  |  | Fair | No | Customer has issue with prepaid meter. Kindly assign call to Moses.
Outage | J.E.26.07.37833 | C001870122 | Richard Grant | St.Catherine | Completed | Load_264873 | New Michelton - 210 | Jul 30, 2026 3:10pm | Jul 30, 2026 3:12pm | Jul 30, 2026 5:51pm | Jul 30, 2026 6:24pm | Jul 30, 2026 6:24pm | Jul 30, 2026 6:25pm | Jul 30, 2026 6:25pm | Jul 30, 2026 6:25pm | BrokenWire |  | Fair | No | 2 span of broken phase and neutral for opened secondary found caused by illegal connection. 2 #2 sleeves, 1 2/0 sleeve, 1 2/0 preform, 3 onebolt clamps, approximately 20ft #2 wire and approximately 80ft 2/0 wire used to retention line section. Supply restored and area left okay.
Outage | J.E.26.07.38665 | C001870123 | Richard Grant | St.Catherine | Completed | Load_264873 | New Michelton - 210 | Jul 30, 2026 3:10pm | Jul 30, 2026 3:12pm | Jul 30, 2026 3:37pm | Jul 30, 2026 3:37pm | Jul 30, 2026 5:11pm | Jul 30, 2026 6:23pm | Jul 30, 2026 6:23pm | Jul 30, 2026 6:23pm | BrokenWire |  | Fair | No | 2 span of broken phase and neutral for opened secondary found caused by illegal connection. 2 #2 sleeves, 1 2/0 sleeve, 1 2/0 preform, 3 onebolt clamps, approximately 20ft #2 wire and approximately 80ft 2/0 wire used to retention line section. Supply restored and area left okay.
Outage | J.E.26.07.38714 | C001870120 | Richard Grant | St.Catherine | Completed | Load_259021 | New Michelton - 210 | Jul 30, 2026 3:10pm | Jul 30, 2026 3:12pm | Jul 30, 2026 7:23pm | Jul 30, 2026 7:23pm | Jul 30, 2026 7:58pm | Jul 30, 2026 9:03pm | Jul 30, 2026 9:03pm | Jul 30, 2026 9:03pm |  | Y | Fair | No | 10amps fuse found blown at 2phase junction pole caused by coconut tree limb touching phase. Limb removed, 10amps fuse replaced with same and supply restored. Area left okay
Non-Outage | J.E.26.07.38499 | C001870109 | Derrick Dawkins | St.James | Completed | Load_268282 | Bogue - 610 | Jul 30, 2026 3:09pm | Jul 30, 2026 3:10pm | Jul 30, 2026 4:30pm | Jul 30, 2026 4:30pm | Jul 30, 2026 4:37pm | Jul 30, 2026 4:41pm | Jul 30, 2026 4:42pm | Jul 30, 2026 4:42pm |  |  | Fair | No | Found premises ok customer complain about high light bill
Outage | J.E.26.07.38727 | C001870108 | Derrick Dawkins | St.James | Completed | Load_262140 | Bogue - 610 | Jul 30, 2026 3:09pm | Jul 30, 2026 3:09pm | Jul 30, 2026 3:28pm | Jul 30, 2026 3:28pm | Jul 30, 2026 4:23pm | Jul 30, 2026 4:26pm | Jul 30, 2026 4:26pm | Jul 30, 2026 4:26pm |  |  | Fair | No | Check and found premises ok
Outage | J.E.26.07.38577 | C001870059 | Christopher Edwards | KSAN | Completed | Load_239178 | Constant Spring - 410 | Jul 30, 2026 2:37pm | Jul 30, 2026 2:39pm | Jul 30, 2026 2:45pm | Jul 30, 2026 2:57pm | Jul 30, 2026 3:01pm | Jul 30, 2026 7:45pm | Jul 30, 2026 7:45pm | Jul 30, 2026 7:45pm | BrokenWire | Y | Fair | No | Clear fallen bamboo off open secondary Reset 50 kva transformer
Outage | J.E.26.07.38697 | C001870039 | Raymond Carr | St.Mary | Completed | Load_269669 | Oracabessa - 110 | Jul 30, 2026 2:20pm | Jul 30, 2026 5:15pm | Jul 30, 2026 6:48pm | Jul 30, 2026 6:48pm | Jul 30, 2026 7:06pm | Jul 30, 2026 7:00pm | Jul 30, 2026 7:08pm | Jul 30, 2026 7:08pm | BrokenPole |  | Fair | No | Leaning pole. Refer to maintenance department.
Outage | J.E.26.07.38690 | C001870027 | Horace Malcolm | St.James | Completed | Load_302104 | Queens Drive - 710 | Jul 30, 2026 2:14pm | Jul 30, 2026 2:14pm | Jul 30, 2026 3:08pm | Jul 30, 2026 3:08pm | Jul 30, 2026 3:08pm | Jul 30, 2026 3:09pm | Jul 30, 2026 3:09pm | Jul 30, 2026 3:09pm |  |  | Fair | No | Crew shift end
Outage | J.E.26.07.38679 | C001870016 | Swon Miller | St.James | Completed | Load_254649 | Bogue - 310 | Jul 30, 2026 2:09pm | Jul 30, 2026 4:08pm | Jul 30, 2026 10:48pm | Jul 30, 2026 10:48pm | Jul 30, 2026 10:48pm | Jul 29, 2026 10:00am | Jul 30, 2026 10:50pm | Jul 30, 2026 10:50pm |  |  | Fair | No | Call related to previous
Outage | J.E.26.07.38684 | C001870015 | Swon Miller | St.James | Completed | Load_245091 | Bogue - 310 | Jul 30, 2026 2:09pm | Jul 30, 2026 4:08pm | Jul 30, 2026 10:44pm | Jul 30, 2026 10:44pm | Jul 30, 2026 10:45pm | Jul 14, 2026 10:48am | Jul 30, 2026 10:47pm | Jul 30, 2026 10:47pm |  |  | Fair | No | Call related to previous
Non-Outage | J.E.26.07.38559 | C001870008 | Jowayne Newmans | Portland | Completed | Load_354121 | Port Antonio - 410 | Jul 30, 2026 2:01pm | Jul 30, 2026 2:02pm | Jul 30, 2026 2:12pm | Jul 30, 2026 2:12pm | Jul 30, 2026 2:24pm | Jul 30, 2026 2:57pm | Jul 30, 2026 2:58pm | Jul 30, 2026 2:58pm | Fire |  | Fair | No | Patrol and found secondary upper phase and neutral conductor touching causing fire, repair by retention neutral conductor using 1 #2 preform. Customer has electricity.
Outage | J.E.26.07.38621 | C001869993 | Neville Spencer | Clarendon | Completed | Load_242744 | May Pen - 110 | Jul 30, 2026 1:51pm | Jul 30, 2026 3:38pm | Jul 30, 2026 6:36pm | Jul 30, 2026 6:36pm | Jul 30, 2026 7:24pm | Jul 30, 2026 7:24pm | Jul 30, 2026 7:28pm | Jul 30, 2026 7:28pm | BangingWires |  | Fair | No | Need daylight visit road bad.last pole now one at home.
Outage | J.E.26.07.38639 | C001869978 | Richard Samuda | Manchester | Completed | Load_249050 | Spur Tree - 310 | Jul 30, 2026 1:35pm | Jul 30, 2026 1:35pm | Jul 30, 2026 1:38pm | Jul 30, 2026 1:39pm | Jul 30, 2026 2:11pm | Jul 30, 2026 4:59am | Jul 30, 2026 5:00pm | Jul 30, 2026 5:00pm |  |  | SevereWind | No | Found 50kva transformer blown patrol line found tree banging out line Carried out spot bushing area replaced fuse customer back to normal
Non-Outage | J.E.26.07.38513 | C001869975 | Omar King | null | Completed | null | null | Jul 30, 2026 1:31pm | Jul 30, 2026 5:00pm | Jul 30, 2026 5:39pm | Jul 30, 2026 5:39pm | Jul 30, 2026 6:08pm | Jul 30, 2026 6:09pm | Jul 30, 2026 6:09pm | Jul 30, 2026 6:09pm | Fire |  | Fair | No | The problem has been resolved
Outage | J.E.26.07.38598 | C001869974 | Omar King | St.Ann | Completed | Load_268103 | Upper White River - 210 | Jul 30, 2026 1:31pm | Jul 30, 2026 4:33pm | Jul 31, 2026 1:29am | Jul 31, 2026 1:29am | Jul 31, 2026 1:56am | Jul 31, 2026 1:58am | Jul 31, 2026 2:00am | Jul 31, 2026 2:00am |  |  | Fair | No | Call several times no answer directions not sufficient premises not found
Outage | J.E.26.07.38622 | C001869973 | Daniel Francis | St.Ann | Completed | Load_246908 | Ocho Rios - 510 | Jul 30, 2026 1:31pm | Jul 30, 2026 1:31pm | Jul 30, 2026 1:46pm | Jul 30, 2026 1:46pm | Jul 30, 2026 1:59pm | Jul 30, 2026 2:33pm | Jul 30, 2026 2:42pm | Jul 30, 2026 2:42pm | BrokenPole |  | Fair | No | Meter need to be change one side of the meter is not working
Outage | J.E.26.07.38165 | C001869948 | Dean Smith | St.James | Completed | Load_252019 | Orange Bay - 310 | Jul 30, 2026 1:05pm | Jul 30, 2026 1:05pm | Jul 30, 2026 2:54pm | Jul 30, 2026 2:54pm | Jul 30, 2026 2:54pm | Jul 30, 2026 2:54pm | Jul 30, 2026 3:04pm | Jul 30, 2026 3:04pm |  |  | Fair | No | Area was restored, unable to return to the area to attend this power quality issue....Shift ended
Outage | J.E.26.07.38365 | C001869947 | Dean Smith | St.James | Completed | Load_250581 | Bogue - 510 | Jul 30, 2026 1:05pm | Jul 30, 2026 1:05pm | Jul 30, 2026 3:04pm | Jul 30, 2026 3:04pm | Jul 30, 2026 3:04pm | Jul 30, 2026 3:04pm | Jul 30, 2026 3:04pm | Jul 30, 2026 3:04pm |  |  | Fair | No | Shift ended
Outage | J.E.26.07.38588 | C001869940 | Clyde Brown | Clarendon | Completed | Load_579463 | Parnassus - 310 | Jul 30, 2026 1:04pm | Jul 30, 2026 1:04pm | Jul 30, 2026 1:24pm | Jul 30, 2026 10:07pm | Jul 30, 2026 10:07pm | Jul 30, 2026 10:08pm | Jul 30, 2026 10:13pm | Jul 30, 2026 10:13pm |  |  | Fair | No | Found secondary phase and neutral entangled same cleared and voltage now ok reading 111/112 and 223V
Non-Outage | J.E.26.07.38547 | C001869937 | Horace Malcolm | null | Completed | null | null | Jul 30, 2026 1:02pm | Jul 30, 2026 1:02pm | Jul 30, 2026 3:09pm | Jul 30, 2026 3:09pm | Jul 30, 2026 3:09pm | Jul 30, 2026 3:10pm | Jul 30, 2026 3:10pm | Jul 30, 2026 3:10pm | TreeContact |  | Fair | No | Crew shift end
Outage | J.E.26.07.38451 | C001869938 | Michael Christian | St.James | Completed | Load_301752 | Bogue - 310 | Jul 30, 2026 1:02pm | Jul 30, 2026 1:03pm | Jul 30, 2026 2:09pm | Jul 30, 2026 2:09pm | Jul 30, 2026 2:34pm | Jul 30, 2026 2:43pm | Jul 30, 2026 2:43pm | Jul 30, 2026 2:43pm |  |  | Fair | No | Check and found okay voltage 111 113 225 at pothead internal fault
Outage | J.E.26.07.38539 | C001869939 | Michael Christian | St.James | Completed | Load_249504 | Bogue - 310 | Jul 30, 2026 1:02pm | Jul 31, 2026 7:46am | Jul 31, 2026 10:50am | Jul 31, 2026 10:50am | Jul 31, 2026 11:01am | Jul 31, 2026 11:03am | Jul 31, 2026 11:03am | Jul 31, 2026 11:03am |  |  | Fair | No | Send to field service e n connections
Outage | J.E.26.07.38385 | C001869932 | Horace Malcolm | St.James | Completed | Load_268642 | Queens Drive - 310 | Jul 30, 2026 1:01pm | Jul 30, 2026 1:01pm | Jul 30, 2026 3:11pm | Jul 30, 2026 3:11pm | Jul 30, 2026 3:11pm | Jul 30, 2026 3:12pm | Jul 30, 2026 3:12pm | Jul 30, 2026 3:12pm |  |  | Fair | No | Crew shift end
Outage | J.E.26.07.38420 | C001869935 | Tyrese Williams | St.Ann | Completed | Load_261283 | Cardiff Hall - 310 | Jul 30, 2026 1:01pm | Jul 30, 2026 4:27pm | Jul 30, 2026 4:47pm | Jul 30, 2026 5:12pm | Jul 30, 2026 5:12pm | Jul 30, 2026 5:12pm | Jul 30, 2026 5:13pm | Jul 30, 2026 5:13pm |  |  | Fair | No | Premises found ok power was restored
Outage | J.E.26.07.38429 | C001869933 | Tyrese Williams | St.Ann | Completed | Load_259648 | Cardiff Hall - 310 | Jul 30, 2026 1:01pm | Jul 30, 2026 4:27pm | Jul 30, 2026 4:42pm | Jul 30, 2026 8:27pm | Jul 30, 2026 8:27pm | Jul 30, 2026 8:27pm | Jul 30, 2026 8:27pm | Jul 30, 2026 8:27pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.38454 | C001869931 | Tyrese Williams | St.Ann | Completed | Load_268052 | Cardiff Hall - 310 | Jul 30, 2026 1:01pm | Jul 30, 2026 4:27pm | Jul 30, 2026 4:36pm | Jul 30, 2026 4:36pm | Jul 30, 2026 4:37pm | Jul 30, 2026 4:37pm | Jul 30, 2026 4:38pm | Jul 30, 2026 4:38pm |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.07.38530 | C001869934 | Horace Malcolm | St.James | Completed | Load_302531 | Queens Drive - 310 | Jul 30, 2026 1:01pm | Jul 30, 2026 1:01pm | Jul 30, 2026 3:10pm | Jul 30, 2026 3:10pm | Jul 30, 2026 3:10pm | Jul 30, 2026 3:11pm | Jul 30, 2026 3:11pm | Jul 30, 2026 3:11pm |  |  | Fair | No | Crew shift end
Outage | J.E.26.07.38492 | C001869930 | Tyrese Williams | St.Ann | Completed | Load_264960 | Cardiff Hall - 310 | Jul 30, 2026 1:00pm | Jul 30, 2026 4:27pm | Jul 30, 2026 4:35pm | Jul 30, 2026 4:35pm | Jul 30, 2026 4:35pm | Jul 30, 2026 4:35pm | Jul 30, 2026 4:35pm | Jul 30, 2026 4:35pm |  |  | Fair | No | Premises found ok power was restored
Outage | J.E.26.07.38541 | C001869928 | Tyrese Williams | St.Ann | Completed | Load_262327 | Cardiff Hall - 310 | Jul 30, 2026 1:00pm | Jul 30, 2026 4:37pm | Jul 30, 2026 4:43pm | Jul 30, 2026 4:43pm | Jul 30, 2026 4:44pm | Jul 30, 2026 4:45pm | Jul 30, 2026 4:45pm | Jul 30, 2026 4:45pm |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.07.38556 | C001869929 | Tyrese Williams | St.Ann | Completed | Load_248961 | Cardiff Hall - 310 | Jul 30, 2026 1:00pm | Jul 30, 2026 4:27pm | Jul 30, 2026 4:31pm | Jul 30, 2026 4:31pm | Jul 30, 2026 4:32pm | Jul 30, 2026 4:33pm | Jul 30, 2026 4:33pm | Jul 30, 2026 4:33pm |  |  | Fair | No | Premises found ok customer said light was restored
Outage | J.E.26.07.38476 | C001869921 | Cliton Henry | St.Mary | Completed | Load_245479 | Blackstonedge - 110 | Jul 30, 2026 12:53pm | Jul 30, 2026 12:55pm | Jul 30, 2026 1:47pm | Jul 30, 2026 1:47pm | Jul 30, 2026 3:36pm | Jul 30, 2026 3:43pm | Jul 30, 2026 3:48pm | Jul 30, 2026 3:48pm | BrokenPole,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | A broken 30-c6 wood pole (over head guy pole) found leaning dangerously at approximately 45 degrees . Kindly refer to St. Mary Operations for replacement.
Outage | J.E.26.07.38552 | C001869920 | Neckell Ormsby | St.Mary | Completed | Load_567730 | Highgate - 210 | Jul 30, 2026 12:53pm | Jul 30, 2026 12:54pm | Jul 30, 2026 1:02pm | Jul 30, 2026 1:02pm | Jul 30, 2026 2:04pm | Jul 30, 2026 2:18pm | Jul 30, 2026 2:18pm | Jul 30, 2026 2:18pm |  |  | Fair | No | After making several calls and checks unable to locate customer
Non-Outage | J.E.26.07.35869 | C001869914 | Devon Grant | KSAN | Completed | Load_258114 | Constant Spring - 210 | Jul 30, 2026 12:49pm | Jul 30, 2026 5:04pm | Jul 30, 2026 8:07pm | Jul 30, 2026 8:07pm | Jul 30, 2026 8:24pm | Jul 30, 2026 8:25pm | Jul 30, 2026 8:25pm | Jul 30, 2026 8:25pm |  |  | Fair | No | 3w open secondary circuit, repair broken neutral by using 7ft #2AA conductor and four onebolt clamps.
Outage | J.E.26.07.38485 | C001869913 | Rusean Allen | KSAN | Completed | Load_243339 | Washington Blvd - 710 | Jul 30, 2026 12:48pm | Jul 30, 2026 12:49pm | Jul 30, 2026 1:02pm | Jul 30, 2026 1:02pm | Jul 30, 2026 1:14pm | Jul 30, 2026 1:14pm | Jul 30, 2026 1:19pm | Jul 30, 2026 1:19pm | BrokenWire |  | Fair | No | Excessive amount of illegal connections needs to be removed.Refer to RPD
Outage | J.E.26.07.38557 | C001869904 | Clyde Brown | Clarendon | Completed | Load_569771 | Parnassus - 210 | Jul 30, 2026 12:35pm | Jul 30, 2026 12:42pm | Jul 30, 2026 1:24pm | Jul 30, 2026 1:24pm | Jul 30, 2026 2:20pm | Jul 30, 2026 7:21pm | Jul 30, 2026 7:38pm | Jul 30, 2026 7:38pm | LeakingTransformer |  | SevereWind | No | Blown 3 amps fuse for 25 kva transformer caused by 5span open conductor broken caused by heavy wind in area,transformer isolated and blown 10 amps junction fuse on main road replaced,broken secondary phase and neutral 5 span repaired with 18 ft-#2 conductor,4-splicing sleeve,16ft-#2/0 conductor 6ft-2/0 conductor 6-preform and 8-one bolt clamp and blown 3 amps fuse replaced
Outage | J.E.26.07.38479 | C001869892 | Ricky Hall | St.Catherine | Completed | Load_255042 | Rhodens Pen - 210 | Jul 30, 2026 12:29pm | Jul 30, 2026 12:34pm | Jul 30, 2026 1:34pm | Jul 30, 2026 1:34pm | Jul 30, 2026 2:04pm | Jul 30, 2026 2:58pm | Jul 30, 2026 2:58pm | Jul 30, 2026 2:58pm |  |  | Fair | No | Replaced 2 blown 30 amps junction fuse
Non-Outage | J.E.26.07.37171 | C001869880 | Roemello Brown | Trelawny | Completed | Load_246936 | Duncans - 210 | Jul 30, 2026 12:15pm | Jul 30, 2026 12:16pm | Jul 30, 2026 12:26pm | Jul 30, 2026 12:26pm | Jul 30, 2026 1:08pm | Jul 30, 2026 1:08pm | Jul 30, 2026 1:33pm | Jul 30, 2026 1:33pm |  |  | Fair | No | Secondary line fluctuating customers in the area stated that lighting struck the transformer an there was an fire on it also affecting the whole community please send emergency team to check transformer please Voltage found 111/114/225Voltage leave 111/114/225
Non-Outage | J.E.26.07.37979 | C001869878 | Roemello Brown | Trelawny | Completed | Load_294320 | Greenwood - 110 | Jul 30, 2026 12:15pm | Jul 30, 2026 12:16pm | Jul 31, 2026 9:35am | Jul 31, 2026 9:35am | Jul 31, 2026 9:54am | Jul 31, 2026 9:54am | Jul 31, 2026 10:18am | Jul 31, 2026 10:18am |  |  | Fair | No | Premises found working okay when I arrive at the premises check voltage at the pothead an at pole side locking band on the meter so I don’t go in the meter socket Voltage found 116/116/232Voltage leave 116/116/232
Non-Outage | J.E.26.07.38144 | C001869877 | Roemello Brown | Trelawny | Completed | Load_262089 | Duncans - 110 | Jul 30, 2026 12:15pm | Jul 30, 2026 12:16pm | Jul 31, 2026 8:11am | Jul 31, 2026 8:13am | Jul 31, 2026 8:33am | Jul 31, 2026 8:34am | Jul 31, 2026 9:31am | Jul 31, 2026 9:31am |  |  | Fair | No | Corrosion at the pole an at the pothead have clamps change Voltage found 122/101/223Voltage leave 113/115/228
Non-Outage | J.E.26.07.38355 | C001869876 | Roemello Brown | Trelawny | Completed | Load_262457 | Greenwood - 110 | Jul 30, 2026 12:15pm | Jul 30, 2026 12:16pm | Jul 30, 2026 12:24pm | Jul 31, 2026 10:47am | Jul 31, 2026 11:14am | Jul 31, 2026 11:14am | Jul 31, 2026 11:21am | Jul 31, 2026 11:21am |  |  | Fair | No | Premises found working okay Voltage found 117/116/233Voltage leave 117/116/233
Non-Outage | J.E.26.07.38358 | C001869875 | Roemello Brown | Trelawny | Completed | Load_267437 | Greenwood - 110 | Jul 30, 2026 12:15pm | Jul 30, 2026 12:16pm | Jul 31, 2026 10:19am | Jul 31, 2026 10:19am | Jul 31, 2026 10:43am | Jul 31, 2026 10:43am | Jul 31, 2026 10:46am | Jul 31, 2026 10:46am |  |  | Fair | No | Premises found working okay when I arrive at the premises Voltage found 114/115/229Voltage leave 114/115/229
Non-Outage | J.E.26.07.38389 | C001869869 | Kenroy Dale | null | Completed | null | null | Jul 30, 2026 12:13pm | Jul 30, 2026 2:15pm | Jul 30, 2026 2:19pm | Jul 30, 2026 2:21pm | Jul 30, 2026 2:25pm | Jul 30, 2026 4:03pm | Jul 30, 2026 4:04pm | Jul 30, 2026 4:04pm | BrokenPole |  | Fair | No | Blown 2 amp transformer fuse found, line patrol three span of secondary neutral and one span of secondary phase found broken. Conductor was spliced and retention, blown fuse replaced. Area now with supply
Outage | J.E.26.07.38462 | C001869867 | Rayon Foster | Hanover | Completed | Load_267610 | Orange Bay - 210 | Jul 30, 2026 12:12pm | Jul 30, 2026 12:12pm | Jul 30, 2026 1:01pm | Jul 30, 2026 1:03pm | Jul 30, 2026 1:17pm | Jul 30, 2026 1:39pm | Jul 30, 2026 1:39pm | Jul 30, 2026 1:39pm | LowHangingWires |  | Fair | No | Customer’s service wires need to relocate form customer gate refer to (Clint Johnson) from the savanna mar deportment to visit location about 10 service wires hanging low across drive way
Outage | J.E.26.07.37550 | C001869865 | Marlon Brown | Trelawny | Completed | Load_268209 | Duncans - 110 | Jul 30, 2026 12:10pm | Jul 30, 2026 7:21pm | Jul 30, 2026 7:27pm | Jul 30, 2026 7:27pm | Jul 30, 2026 8:43pm | Jul 30, 2026 8:44pm | Jul 30, 2026 8:44pm | Jul 30, 2026 8:44pm |  |  | Fair | No | Unable to locate customer via telephone nor direction
Outage | J.E.26.07.38409 | C001869863 | Marlon Brown | Trelawny | Completed | Load_241826 | Martha Brae - 110 | Jul 30, 2026 12:10pm | Jul 30, 2026 3:16pm | Jul 30, 2026 7:25pm | Jul 30, 2026 7:26pm | Jul 30, 2026 7:26pm | Jul 30, 2026 7:26pm | Jul 30, 2026 7:26pm | Jul 30, 2026 7:26pm |  |  | Fair | No | Unable to locate customer via telephone nor direction
Outage | J.E.26.07.38410 | C001869866 | Marlon Brown | Trelawny | Completed | Load_261797 | Martha Brae - 210 | Jul 30, 2026 12:10pm | Jul 30, 2026 3:16pm | Jul 30, 2026 7:24pm | Jul 30, 2026 7:24pm | Jul 30, 2026 7:24pm | Jul 30, 2026 7:25pm | Jul 30, 2026 7:25pm | Jul 30, 2026 7:25pm |  |  | Fair | No | Feeder issue
Outage | J.E.26.07.38445 | C001869862 | Barnett Brown | Manchester | Completed | Load_268873 | Spur Tree - 310 | Jul 30, 2026 12:10pm | Jul 30, 2026 12:11pm | Jul 30, 2026 1:26pm | Jul 30, 2026 1:26pm | Jul 30, 2026 1:26pm | Jul 30, 2026 1:35pm | Jul 30, 2026 1:37pm | Jul 30, 2026 1:37pm | TreeContact |  | Fair | No | Found ok customer said he didn’t make any report
Outage | J.E.26.07.38490 | C001869864 | Richard Samuda | Manchester | Completed | Load_266540 | Spur Tree - 310 | Jul 30, 2026 12:10pm | Jul 30, 2026 1:01pm | Jul 30, 2026 1:09pm | Jul 30, 2026 1:09pm | Jul 30, 2026 1:09pm | Jul 30, 2026 1:11am | Jul 30, 2026 1:11pm | Jul 30, 2026 1:11pm |  |  | Fair | No | Found 25 transformer blown patrol line found nothing replaced fuse customer back to normal
Outage | J.E.26.07.38465 | C001869859 | Selvin White | St.Elizabeth | Completed | Load_1004201 | Maggotty - 110 | Jul 30, 2026 12:09pm | Jul 30, 2026 12:09pm | Jul 30, 2026 12:56pm | Jul 30, 2026 12:56pm | Jul 30, 2026 1:01pm | Jul 30, 2026 1:06pm | Jul 30, 2026 1:07pm | Jul 30, 2026 1:07pm |  |  | Fair | No | Please refer to Simone Bicarie and C. Johnson at the field service department for reconnecting .
Outage | J.E.26.07.36993 | C001869857 | Oshane Warren | St.Elizabeth | Completed | Load_265987 | Maggotty - 110 | Jul 30, 2026 12:06pm | Jul 30, 2026 12:08pm | Jul 30, 2026 1:22pm | Jul 30, 2026 1:22pm | Jul 30, 2026 1:22pm | Jul 30, 2026 1:22pm | Jul 30, 2026 1:23pm | Jul 30, 2026 1:23pm |  |  | Fair | No | Customer was disconnected for none payment of bill
Outage | J.E.26.07.38464 | C001869848 | Moses Elliston | St.Catherine | Completed | Load_244526 | Tredegar - 210 | Jul 30, 2026 11:58am | Jul 30, 2026 3:18pm | Jul 30, 2026 5:26pm | Jul 30, 2026 5:26pm | Jul 30, 2026 5:26pm | Jul 30, 2026 3:30pm | Jul 30, 2026 5:27pm | Jul 30, 2026 5:27pm |  |  | Fair | No | Credit added prepaid account.
Outage | J.E.26.07.36821 | C001869845 | Richard Watson | Manchester | Completed | Load_269147 | Spur Tree - 210 | Jul 30, 2026 11:57am | Jul 30, 2026 3:41pm | Jul 30, 2026 5:59pm | Jul 30, 2026 5:59pm | Jul 30, 2026 6:09pm | Jul 30, 2026 6:15pm | Jul 30, 2026 6:18pm | Jul 30, 2026 6:18pm |  |  | Fair | No | Found okay.
Outage | J.E.26.07.37594 | C001869847 | Marlon Authors | St.Elizabeth | Completed | Load_292198 | Maggotty - 210 | Jul 30, 2026 11:57am | Jul 30, 2026 11:58am | Jul 30, 2026 2:08pm | Jul 30, 2026 2:08pm | Jul 30, 2026 3:22pm | Jul 30, 2026 3:32pm | Jul 30, 2026 3:32pm | Jul 30, 2026 3:32pm |  |  | Fair | No | Patrol and found clear. Replace one blown 1 amp fuse that protects 15 kva transformer no pole #. Restored supply okay
Outage | J.E.26.07.38225 | C001869844 | Richard Watson | Manchester | Completed | Load_254709 | Spur Tree - 210 | Jul 30, 2026 11:57am | Jul 30, 2026 3:41pm | Jul 30, 2026 6:28pm | Jul 30, 2026 6:29pm | Jul 30, 2026 6:43pm | Jul 30, 2026 7:04pm | Jul 30, 2026 7:09pm | Jul 30, 2026 7:09pm |  |  | Fair | No | Replace blown 8amp junction fuse no pole#, also replace blown 2amp fuse for 25kva transformer no pole#, remove whist from transformer, supply restored.
Outage | J.E.26.07.38407 | C001869843 | Andrew Powell | Manchester | Completed | Load_251440 | Spur Tree - 210 | Jul 30, 2026 11:57am | Jul 30, 2026 4:27pm | Jul 30, 2026 4:38pm | Jul 30, 2026 4:38pm | Jul 30, 2026 4:38pm | Jul 30, 2026 4:38pm | Jul 30, 2026 4:39pm | Jul 30, 2026 4:39pm |  |  | Fair | No | Premises found okay customer stated that supply restored.
Outage | J.E.26.07.38452 | C001869842 | Richard Watson | Manchester | Completed | Load_1002209 | Spur Tree - 210 | Jul 30, 2026 11:56am | Jul 30, 2026 3:41pm | Jul 30, 2026 4:34pm | Jul 30, 2026 4:34pm | Jul 30, 2026 5:39pm | Jul 30, 2026 5:42pm | Jul 30, 2026 5:44pm | Jul 30, 2026 5:44pm |  |  | Fair | No | Supply found in area upon arrival.
Outage | J.E.26.07.38427 | C001869838 | Donald Cunningham | St.Catherine | Completed | Load_557323 | Twickenham - 410 | Jul 30, 2026 11:54am | Jul 30, 2026 12:31pm | Jul 30, 2026 12:41pm | Jul 30, 2026 12:41pm | Jul 30, 2026 1:11pm | Jul 30, 2026 2:07pm | Jul 30, 2026 2:10pm | Jul 30, 2026 2:10pm |  |  | Fair | No | Blown junction fuse by T/off to fellowship main road replace 30 amp and also replace 25 amp on compound
Outage | J.E.26.07.38448 | C001869829 | Rusean Allen | KSAS | Completed | Load_240053 | Duhaney - 410 | Jul 30, 2026 11:49am | Jul 30, 2026 11:51am | Jul 30, 2026 1:19pm | Jul 30, 2026 1:19pm | Jul 30, 2026 1:22pm | Jul 30, 2026 1:23pm | Jul 30, 2026 1:23pm | Jul 30, 2026 1:23pm |  |  | Fair | No | Power was restored
Outage | J.E.26.07.38449 | C001869828 | Rusean Allen | KSAS | Completed | Load_239644 | Duhaney - 410 | Jul 30, 2026 11:49am | Jul 30, 2026 11:51am | Jul 30, 2026 1:23pm | Jul 30, 2026 1:23pm | Jul 30, 2026 1:28pm | Jul 30, 2026 1:28pm | Jul 30, 2026 1:29pm | Jul 30, 2026 1:29pm |  |  | Fair | No | Premises okay
Outage | J.E.26.07.38463 | C001869827 | Michael Paterson | Westmoreland | Completed | Load_268703 | Paradise - 210 | Jul 30, 2026 11:48am | Jul 30, 2026 11:48am | Jul 30, 2026 2:32pm | Jul 30, 2026 2:32pm | Jul 31, 2026 7:06am | Jul 31, 2026 7:10am | Jul 31, 2026 7:10am | Jul 31, 2026 7:10am |  |  | Fair | No | Found premises ok volt’s reading at meter 115-114=229 volts
Non-Outage | J.E.26.07.38024 | C001869810 | Michael Paterson | Westmoreland | Completed | Load_244663 | Paradise - 110 | Jul 30, 2026 11:44am | Jul 31, 2026 10:03am | Jul 31, 2026 12:21pm | Jul 31, 2026 12:21pm | Jul 31, 2026 12:31pm | Jul 31, 2026 12:37pm | Jul 31, 2026 12:37pm | Jul 31, 2026 12:37pm |  |  | Fair | No | Visit location found supply ok customer advise crew that a team visit last night and resolved power
Non-Outage | J.E.26.07.38398 | C001869809 | Evan Spaulding | null | Completed | null | null | Jul 30, 2026 11:44am | Jul 30, 2026 3:37pm | Jul 30, 2026 5:04pm | Jul 30, 2026 5:04pm | Jul 30, 2026 5:25pm | Jul 30, 2026 5:59pm | Jul 30, 2026 6:01pm | Jul 30, 2026 6:01pm |  |  | Fair | No | Cut fallen bamboo from secondary conductors voltage left 114v,115v,229v.
Outage | J.E.26.07.34563 | C001869803 | Selvin White | St.Elizabeth | Completed | Load_230094 | Maggotty - 110 | Jul 30, 2026 11:44am | Jul 30, 2026 12:00pm | Jul 30, 2026 1:49pm | Jul 30, 2026 1:51pm | Jul 30, 2026 2:40pm | Jul 30, 2026 2:44pm | Jul 30, 2026 2:44pm | Jul 30, 2026 2:44pm |  |  | Fair | No | Escalation department says a location complaint order was already generated for the field service technician to visit the premises for inspection.
Outage | J.E.26.07.38288 | C001869796 | Omar King | St.Ann | Completed | Load_240910 | Ocho Rios - 310 | Jul 30, 2026 11:44am | Jul 30, 2026 4:30pm | Jul 30, 2026 5:22pm | Jul 30, 2026 5:22pm | Jul 30, 2026 5:35pm | Jul 30, 2026 5:36pm | Jul 30, 2026 5:37pm | Jul 30, 2026 5:37pm |  |  | Fair | No | Problem has been resolved
Outage | J.E.26.07.38368 | C001869795 | Daniel Francis | St.Ann | Completed | Load_262552 | Ocho Rios - 310 | Jul 30, 2026 11:44am | Jul 31, 2026 7:26am | Jul 31, 2026 1:08pm | Jul 31, 2026 1:08pm | Jul 31, 2026 1:08pm | Jul 31, 2026 1:09pm | Jul 31, 2026 1:10pm | Jul 31, 2026 1:10pm |  |  | Fair | No | Found okay 111 110 221 in all internal problem
Outage | J.E.26.07.38380 | C001869797 | Michael Paterson | Westmoreland | Completed | Load_258517 | Paradise - 210 | Jul 30, 2026 11:44am | Jul 30, 2026 11:45am | Jul 30, 2026 1:43pm | Jul 30, 2026 1:44pm | Jul 30, 2026 1:44pm | Jul 30, 2026 2:09pm | Jul 30, 2026 2:11pm | Jul 30, 2026 2:11pm | BrokenWire |  | Fair | No | Reconnection done at pole using three clamps, voltage readings, 116v, 114v, 230v.
Outage | J.E.26.07.38390 | C001869804 | Tyrese Williams | St.Ann | Completed | Load_248334 | Cardiff Hall - 310 | Jul 30, 2026 11:44am | Jul 30, 2026 4:27pm | Jul 30, 2026 4:50pm | Jul 30, 2026 4:50pm | Jul 30, 2026 4:50pm | Jul 30, 2026 4:50pm | Jul 30, 2026 4:51pm | Jul 30, 2026 4:51pm | BrokenWire |  | Fair | No | Premises not found not getting Customer on phone
Outage | J.E.26.07.38401 | C001869805 | Raymond Lewis | St.Ann | Completed | Load_241237 | Cardiff Hall - 210 | Jul 30, 2026 11:44am | Jul 30, 2026 4:30pm | Jul 30, 2026 7:34pm | Jul 30, 2026 7:34pm | Jul 30, 2026 8:06pm | Jul 30, 2026 8:08pm | Jul 30, 2026 8:08pm | Jul 30, 2026 8:08pm | BrokenWire |  | Fair | No | Need key to open meter socket
Outage | J.E.26.07.38403 | C001869812 | Devon Grant | KSAN | Completed | Load_575134 | Constant Spring - 210 | Jul 30, 2026 11:44am | Jul 30, 2026 3:32pm | Jul 30, 2026 4:44pm | Jul 30, 2026 6:28pm | Jul 30, 2026 7:02pm | Jul 30, 2026 7:06pm | Jul 30, 2026 7:07pm | Jul 30, 2026 7:07pm |  |  | Fair | No | Customer reconnected by call center representative.
Outage | J.E.26.07.38432 | C001869811 | Rusean Allen | KSAS | Completed | Load_255900 | Three Miles - 410 | Jul 30, 2026 11:44am | Jul 30, 2026 11:51am | Jul 30, 2026 3:22pm | Jul 30, 2026 3:22pm | Jul 30, 2026 3:22pm | Jul 30, 2026 3:23pm | Jul 30, 2026 3:23pm | Jul 30, 2026 3:23pm |  |  | Fair | No | Hexing failure, refer field service department.
Outage | J.E.26.07.38442 | C001869815 | Stephen Taylor | St.Thomas | Completed | Load_259921 | Lysson - 410 | Jul 30, 2026 11:44am | Jul 30, 2026 11:50am | Jul 30, 2026 12:17pm | Jul 30, 2026 12:17pm | Jul 30, 2026 5:02pm | Jul 30, 2026 5:03pm | Jul 30, 2026 5:06pm | Jul 30, 2026 5:06pm |  |  | Fair | No | Junction fuse out patrol the line nothing found and the line close up back with a 10ams fuse customer are now ok
Outage | J.E.26.07.38459 | C001869813 | Clyde Brown | Clarendon | Completed | Load_253849 | May Pen - 210 | Jul 30, 2026 11:44am | Jul 30, 2026 11:51am | Jul 30, 2026 12:09pm | Jul 30, 2026 12:09pm | Jul 30, 2026 12:58pm | Jul 30, 2026 12:50pm | Jul 30, 2026 1:08pm | Jul 30, 2026 1:08pm |  | Y | Fair | No | Blown 25 amps junction fuse near stop light caused by wist on line same cleared and blown fuse replaced
Outage | J.E.26.07.38020 | C001869595 | Michael Paterson | Westmoreland | Completed | Load_254102 | Paradise - 210 | Jul 30, 2026 9:49am | Jul 30, 2026 9:52am | Jul 30, 2026 12:25pm | Jul 30, 2026 12:25pm | Jul 30, 2026 12:56pm | Jul 30, 2026 1:24pm | Jul 30, 2026 1:24pm | Jul 30, 2026 1:24pm | Fire |  | Fair | No | Apartment complex, meter center has 5 meters, complainant meter found in in a different socket, team put meter in the right sockets, matter normalize. Meter # 3041519 found in socket #5 and Meter # 3041518 found in socket #2.
Outage | J.E.26.07.37822 | C001869594 | Michael Paterson | Westmoreland | Completed | Load_237660 | Paradise - 210 | Jul 30, 2026 9:48am | Jul 30, 2026 9:52am | Jul 30, 2026 10:39am | Jul 30, 2026 10:42am | Jul 30, 2026 11:13am | Jul 30, 2026 11:14am | Jul 30, 2026 11:14am | Jul 30, 2026 11:14am |  |  | Fair | No | Customer confirm ok via phone call.
Outage | J.E.26.07.36378 | C001869592 | Oshane Warren | Westmoreland | Completed | Load_245618 | Paradise - 310 | Jul 30, 2026 9:46am | Jul 30, 2026 10:05am | Jul 30, 2026 2:24pm | Jul 30, 2026 2:24pm | Jul 30, 2026 3:09pm | Jul 30, 2026 3:14pm | Jul 30, 2026 3:18pm | Jul 30, 2026 3:18pm |  |  | Fair | No | Customer is not ready for connection customer needs to carry out repair and meter is nowhere to be found refer to feel service
Outage | J.E.26.07.36684 | C001869587 | Rayon Foster | St.James | Completed | Load_242321 | Bogue - 510 | Jul 30, 2026 9:46am | Jul 30, 2026 9:46am | Jul 30, 2026 10:19am | Jul 30, 2026 10:20am | Jul 30, 2026 10:20am | Jul 30, 2026 10:21am | Jul 30, 2026 10:21am | Jul 30, 2026 10:21am |  |  | Fair | No | St James call
Outage | J.E.26.07.37367 | C001869588 | Oshane Warren | Westmoreland | Completed | Load_244556 | Paradise - 310 | Jul 30, 2026 9:46am | Jul 30, 2026 10:04am | Jul 30, 2026 12:23pm | Jul 30, 2026 12:23pm | Jul 30, 2026 12:23pm | Jul 30, 2026 1:18pm | Jul 30, 2026 1:19pm | Jul 30, 2026 1:19pm |  |  | Fair | No | Reconnect service wire at pathead and secondary line used 65ft of number 6 twisted wire uses 2 service connector voltage 110
Outage | J.E.26.07.37549 | C001869590 | Michael Paterson | Westmoreland | Completed | Load_251611 | Paradise - 310 | Jul 30, 2026 9:46am | Jul 30, 2026 11:55am | Jul 30, 2026 2:28pm | Jul 30, 2026 2:28pm | Jul 30, 2026 2:28pm | Jul 30, 2026 2:30pm | Jul 30, 2026 2:30pm | Jul 30, 2026 2:30pm |  |  | Fair | No | Unable to locate customer, however, customer is not responding to phone calls.
Outage | J.E.26.07.38327 | C001869593 | Horace Malcolm | St.James | Completed | Load_240235 | Queens Drive - 310 | Jul 30, 2026 9:46am | Jul 30, 2026 9:47am | Jul 30, 2026 10:21am | Jul 30, 2026 11:50am | Jul 30, 2026 11:50am | Jul 30, 2026 12:40pm | Jul 30, 2026 12:40pm | Jul 30, 2026 12:40pm |  |  | Fair | No | Refused one 25kva transformer used on 2amp fuse
Outage | J.E.26.07.38368 | C001869589 | Daniel Francis | St.Ann | Completed | Load_262552 | Ocho Rios - 310 | Jul 30, 2026 9:46am | Jul 30, 2026 9:56am | Jul 31, 2026 11:20am | Jul 31, 2026 11:20am | Jul 31, 2026 1:00pm | Jul 31, 2026 1:07pm | Jul 31, 2026 1:07pm | Jul 31, 2026 1:07pm |  |  | Fair | No | Found okay 111 110 221 in all internal problem
Outage | J.E.26.07.38369 | C001869591 | Roxroy Needham | St.Ann | Completed | Load_248846 | Cardiff Hall - 310 | Jul 30, 2026 9:46am | Jul 30, 2026 9:46am | Jul 30, 2026 10:17am | Jul 30, 2026 10:17am | Jul 30, 2026 12:02pm | Jul 30, 2026 12:04pm | Jul 30, 2026 12:05pm | Jul 30, 2026 12:05pm |  |  | Fair | No | Replace 5amp fuse for a 50kva transformer
Outage | J.E.26.07.38290 | C001869569 | Neckell Ormsby | St.Mary | Completed | Load_266601 | Highgate - 210 | Jul 30, 2026 9:30am | Jul 30, 2026 9:30am | Jul 30, 2026 11:34am | Jul 30, 2026 11:34am | Jul 30, 2026 12:13pm | Jul 30, 2026 12:28pm | Jul 30, 2026 12:34pm | Jul 30, 2026 12:34pm |  |  | Fair | No | Found damaged meter please refer to field service to have it changed meter #3012106
Outage | J.E.26.07.38334 | C001869570 | Neckell Ormsby | St.Mary | Completed | Load_248289 | Highgate -110 | Jul 30, 2026 9:30am | Jul 30, 2026 9:30am | Jul 30, 2026 10:17am | Jul 30, 2026 10:17am | Jul 30, 2026 11:06am | Jul 30, 2026 11:34am | Jul 30, 2026 11:34am | Jul 30, 2026 11:34am |  |  | Rains | No | Found junction fuse blown new pole # patrol and found bamboo on primary remove bamboo and replace 1- 10am fuse
Outage | J.E.26.07.38295 | C001869565 | Ricky Hall | St.Catherine | Completed | Load_253421 | Rhodens Pen - 210 | Jul 30, 2026 9:24am | Jul 30, 2026 9:31am | Jul 30, 2026 10:22am | Jul 30, 2026 10:22am | Jul 30, 2026 11:20am | Jul 30, 2026 11:50am | Jul 30, 2026 11:51am | Jul 30, 2026 11:51am |  |  | Fair | No | Clean and reconnect 3W service at pole use 1 clamp 18/118/236
Outage | J.E.26.07.38325 | C001869564 | Richard Nicholas | St.Catherine | Completed | Load_249338 | Tredegar - 410 | Jul 30, 2026 9:24am | Jul 30, 2026 3:29pm | Jul 30, 2026 6:51pm | Jul 30, 2026 6:51pm | Jul 30, 2026 6:51pm | Jul 30, 2026 6:51pm | Jul 30, 2026 6:55pm | Jul 30, 2026 6:55pm |  |  | Fair | No | Replaced blown 15kva transformer 2amp fuse on pole # 600702.
Outage | J.E.26.07.38297 | C001869558 | Wan Carlos Scarlett | Portmore | Completed | Load_1003660 | Naggo Head - 610 | Jul 30, 2026 9:17am | Jul 30, 2026 10:16am | Jul 30, 2026 10:23am | null | Jul 30, 2026 10:23am | Jul 30, 2026 2:22pm | Jul 30, 2026 2:25pm | Jul 30, 2026 2:25pm |  |  | SevereWind | No | Refuse 65 Amps junction no pole # was found also found bird between underground cable switch that caused the power outage, power supply has been restored
Outage | J.E.26.07.38280 | C001869554 | Eric Williams | KSAN | Completed | Load_239172 | Hope - 410 | Jul 30, 2026 9:10am | Jul 30, 2026 9:11am | Jul 30, 2026 9:20am | Jul 30, 2026 9:20am | Jul 30, 2026 10:48am | Jul 30, 2026 10:55am | Jul 30, 2026 10:57am | Jul 30, 2026 10:57am |  |  | Fair | No | 2 burnt hotline clamps found and replace
Outage | J.E.26.07.38082 | C001869543 | Edward Royal | KSAS | Completed | Load_242868 | Rockfort - 410 | Jul 30, 2026 8:54am | Jul 30, 2026 8:55am | Jul 30, 2026 11:35am | Jul 30, 2026 11:35am | Jul 30, 2026 11:35am | Jul 30, 2026 12:07pm | Jul 30, 2026 12:07pm | Jul 30, 2026 12:07pm |  |  | Fair | No | Spliced and reconnected service neutral using 1 single bolt clamp
Outage | J.E.26.07.38268 | C001869544 | Rusean Allen | KSAS | Completed | Load_269999 | Three Miles - 510 | Jul 30, 2026 8:54am | Jul 30, 2026 9:10am | Jul 30, 2026 10:15am | Jul 30, 2026 10:15am | Jul 30, 2026 10:21am | Jul 30, 2026 10:21am | Jul 30, 2026 10:21am | Jul 30, 2026 10:21am |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.38269 | C001869541 | Rusean Allen | KSAN | Completed | Load_243339 | Washington Blvd - 710 | Jul 30, 2026 8:54am | Jul 30, 2026 8:55am | Jul 30, 2026 9:58am | Jul 30, 2026 10:12am | Jul 30, 2026 10:12am | Jul 30, 2026 10:13am | Jul 30, 2026 10:13am | Jul 30, 2026 10:13am |  |  | Fair | No | Related to 8 cundall terrace
Outage | J.E.26.07.38271 | C001869542 | Rusean Allen | KSAN | Completed | Load_261902 | Washington Blvd - 710 | Jul 30, 2026 8:54am | Jul 30, 2026 8:55am | Jul 30, 2026 9:58am | Jul 30, 2026 10:11am | Jul 30, 2026 10:11am | Jul 30, 2026 10:12am | Jul 30, 2026 10:12am | Jul 30, 2026 10:12am |  |  | Fair | No | Related to 8 Cundall terrace
Outage | J.E.26.07.38273 | C001869539 | Roxroy Needham | St.Ann | Completed | Load_261435 | Cardiff Hall - 310 | Jul 30, 2026 8:53am | Jul 30, 2026 8:55am | Jul 30, 2026 12:05pm | Jul 30, 2026 12:06pm | Jul 30, 2026 1:04pm | Jul 30, 2026 1:00pm | Jul 30, 2026 1:13pm | Jul 30, 2026 1:13pm |  | Y | Fair | No | Retention a span of secondary service wire and remake joint used 2 pg clamp
Outage | J.E.26.07.38274 | C001869540 | Omar King | St.Ann | Completed | Load_574533 | Ocho Rios - 310 | Jul 30, 2026 8:53am | Jul 30, 2026 4:29pm | Jul 30, 2026 6:11pm | Jul 30, 2026 6:11pm | Jul 30, 2026 8:03pm | Jul 30, 2026 10:33pm | Jul 30, 2026 10:33pm | Jul 30, 2026 10:33pm | BrokenWire |  | Fair | No | Found four secondary neutral and phase broken cause illegal connection line section as been splice and retention customer is now with supply
Non-Outage | J.E.26.07.36422 | C001869534 | Andrae Clarke | Portland | Completed | Load_349987 | Port Antonio - 410 | Jul 30, 2026 8:48am | Jul 30, 2026 2:41pm | Jul 31, 2026 2:06pm | Jul 31, 2026 2:06pm | Jul 31, 2026 3:41pm | Jul 31, 2026 4:12pm | Jul 31, 2026 4:18pm | Jul 31, 2026 4:18pm |  |  | Fair | No | Check voltage at pole 100/112 214Refer to Emergency Crew to check transformer at pole number 0191119
Non-Outage | J.E.26.07.36432 | C001869533 | Andrae Clarke | Portland | Completed | Load_353091 | Port Antonio - 410 | Jul 30, 2026 8:48am | Jul 30, 2026 2:41pm | Jul 31, 2026 10:56am | Jul 31, 2026 10:56am | Jul 31, 2026 10:56am | Jul 31, 2026 10:16am | Jul 31, 2026 10:58am | Jul 31, 2026 10:58am |  |  | Fair | No | Made several phone calls to the customer and got no response
Non-Outage | J.E.26.07.36700 | C001869532 | Andrae Clarke | Portland | Completed | Load_354844 | Port Antonio - 410 | Jul 30, 2026 8:48am | Jul 30, 2026 2:41pm | Jul 31, 2026 12:36pm | Jul 31, 2026 12:36pm | Jul 31, 2026 2:04pm | Jul 31, 2026 2:11pm | Jul 31, 2026 2:05pm | Jul 31, 2026 2:05pm |  |  | Fair | No | Premises found okay Check voltage 115/117/232
Non-Outage | J.E.26.07.38264 | C001869522 | Neckell Ormsby | St.Mary | Completed | Load_269511 | Annotto Bay - 310 | Jul 30, 2026 8:41am | Jul 30, 2026 8:41am | Jul 30, 2026 8:47am | Jul 30, 2026 8:47am | Jul 30, 2026 9:57am | Jul 30, 2026 10:16am | Jul 30, 2026 10:17am | Jul 30, 2026 10:17am | Fire |  | Rains | No | Tree limb touching primary when it’s windy please refer to maintenance department to have the area bushed
Outage | J.E.26.07.38229 | C001869519 | Rayon Foster | Hanover | Completed | Load_247675 | Orange Bay - 210 | Jul 30, 2026 8:35am | Jul 30, 2026 8:35am | Jul 30, 2026 10:29am | Jul 30, 2026 10:29am | Jul 30, 2026 11:58am | Jul 30, 2026 1:03pm | Jul 30, 2026 1:03pm | Jul 30, 2026 1:03pm |  |  | Fair | No | Found working ok Voltage found on location when arrived 113/112AB225 bots
Outage | J.E.26.07.38135 | C001869506 | Michael Christian | St.James | Completed | Load_575140 | Bogue - 310 | Jul 30, 2026 8:26am | Jul 30, 2026 8:26am | Jul 30, 2026 9:11am | Jul 30, 2026 9:14am | Jul 30, 2026 10:11am | Jul 30, 2026 10:35am | Jul 30, 2026 10:35am | Jul 30, 2026 10:35am |  |  | Fair | No | Check and found okay voltage 111 113 224 at pothead
Outage | J.E.26.07.37563 | C001869498 | Devon Grant | KSAN | Completed | Load_258114 | Constant Spring - 210 | Jul 30, 2026 8:21am | Jul 30, 2026 3:31pm | Jul 30, 2026 7:07pm | Jul 30, 2026 7:07pm | Jul 30, 2026 7:31pm | Jul 30, 2026 8:04pm | Jul 30, 2026 8:07pm | Jul 30, 2026 8:07pm |  |  | Fair | No | 3w open secondary circuit, repair broken neutral by using 7ft #2AA conductor and four onebolt clamps.
Outage | J.E.26.07.38103 | C001869496 | Rusean Allen | KSAN | Completed | Load_243339 | Washington Blvd - 710 | Jul 30, 2026 8:19am | Jul 30, 2026 8:20am | Jul 30, 2026 8:52am | Jul 30, 2026 9:27am | Jul 30, 2026 9:56am | Jul 30, 2026 10:07am | Jul 30, 2026 10:07am | Jul 30, 2026 10:07am |  |  | Fair | No | 30amp fuse found 30amp fuse replaced.
Outage | J.E.26.07.38168 | C001869495 | Rusean Allen | KSAN | Completed | Load_243339 | Washington Blvd - 710 | Jul 30, 2026 8:19am | Jul 30, 2026 8:20am | Jul 30, 2026 9:57am | Jul 30, 2026 10:13am | Jul 30, 2026 10:14am | Jul 30, 2026 10:14am | Jul 30, 2026 10:14am | Jul 30, 2026 10:14am |  |  | Fair | No | Related to 8 Cundall Terrace
Outage | J.E.26.07.38051 | C001869491 | Milton Charlton | KSAN | Completed | Load_1006339 | Hope - 410 | Jul 30, 2026 8:17am | Jul 30, 2026 8:17am | Jul 30, 2026 9:39am | Jul 30, 2026 9:54am | Jul 30, 2026 11:30am | Jul 30, 2026 11:30am | Jul 30, 2026 11:31am | Jul 30, 2026 11:31am |  |  | Fair | No | Found okay upon arrival. Customer has an internal problem. Readings at meter socket 118-118-236 volts.
Outage | J.E.26.07.38074 | C001869489 | Milton Charlton | KSAN | Completed | Load_261433 | Hope - 410 | Jul 30, 2026 8:17am | Jul 30, 2026 8:17am | Jul 30, 2026 12:07pm | Jul 30, 2026 12:07pm | Jul 30, 2026 1:40pm | Jul 30, 2026 1:40pm | Jul 30, 2026 1:41pm | Jul 30, 2026 1:41pm |  |  | Fair | No | Found okay upon arrival.Matter was resolved.
Outage | J.E.26.07.38146 | C001869492 | Stephen Taylor | St.Thomas | Completed | Load_243194 | Good Year - 210 | Jul 30, 2026 8:17am | Jul 30, 2026 8:18am | Jul 30, 2026 11:49am | Jul 30, 2026 11:49am | Jul 30, 2026 11:49am | Jul 30, 2026 11:49am | Jul 30, 2026 11:50am | Jul 30, 2026 11:50am |  |  | Fair | No | Call to customer and customer said power is back and okay now
Outage | J.E.26.07.38214 | C001869490 | Milton Charlton | KSAN | Completed | Load_300523 | Hope - 510 | Jul 30, 2026 8:17am | Jul 30, 2026 8:17am | Jul 30, 2026 9:39am | Jul 30, 2026 9:39am | Jul 30, 2026 9:39am | Jul 30, 2026 9:40am | Jul 30, 2026 9:46am | Jul 30, 2026 9:46am |  |  | Fair | No | Switch top feeding Hope Gardens complex burn off in main line( Hope S/S 410. Need bucket truck to reconnect switch top burn off at Hot-line clamp.
Non-Outage | J.E.26.07.37227 | C001869488 | Andrae Dawkins | St.James | Completed | Load_262913 | Queens Drive - 310 | Jul 30, 2026 8:16am | Jul 30, 2026 8:16am | Jul 30, 2026 3:58pm | Jul 30, 2026 3:58pm | Jul 30, 2026 3:58pm | Jul 30, 2026 2:11pm | Jul 30, 2026 3:59pm | Jul 30, 2026 3:59pm |  |  | Fair | No | Check and found ok customer said that the problem was already resolved
Non-Outage | J.E.26.07.38233 | C001869486 | Daniel Francis | null | Completed | null | null | Jul 30, 2026 8:10am | Jul 30, 2026 8:12am | Jul 30, 2026 12:16pm | Jul 30, 2026 12:16pm | Jul 30, 2026 1:10pm | Jul 30, 2026 1:18pm | Jul 30, 2026 1:20pm | Jul 30, 2026 1:20pm |  |  | Fair | No | Found junction fuse blown at 0012604 20 amp
Non-Outage | J.E.26.07.36806 | C001869485 | Rayon Foster | Hanover | Completed | Load_575278 | Orange Bay - 310 | Jul 30, 2026 8:09am | Jul 30, 2026 8:12am | Jul 30, 2026 9:15am | Jul 30, 2026 9:16am | Jul 30, 2026 9:28am | Jul 30, 2026 10:19am | Jul 30, 2026 10:19am | Jul 30, 2026 10:19am |  |  | Fair | No | Corrosion on jps pole was the cause of low voltage remake joints using three one bolt clamp voltage after changing clamps 110/111AB221 bolts
Non-Outage | J.E.26.07.37153 | C001869478 | Junior Scarlett | Hanover | Completed | Load_245538 | Orange Bay - 310 | Jul 30, 2026 8:07am | Jul 30, 2026 8:08am | Jul 30, 2026 8:17am | Jul 30, 2026 10:59am | Jul 30, 2026 12:20pm | Jul 30, 2026 12:29pm | Jul 30, 2026 12:29pm | Jul 30, 2026 12:29pm |  |  | Fair | No | Check and found okVoltage found 115v 114v 229v
Non-Outage | J.E.26.07.37488 | C001869476 | Junior Scarlett | St.James | Completed | Load_301701 | Bogue - 310 | Jul 30, 2026 8:07am | Jul 30, 2026 8:08am | Jul 30, 2026 8:17am | Jul 30, 2026 8:36am | Jul 30, 2026 9:06am | Jul 30, 2026 9:30am | Jul 30, 2026 9:35am | Jul 30, 2026 9:35am | LeaningPole |  | Fair | No | Lean pole refer to maintenanceVoltage found 115v 115v 230v 205v
Non-Outage | J.E.26.07.38064 | C001869477 | Junior Scarlett | null | Completed | null | null | Jul 30, 2026 8:07am | Jul 30, 2026 8:08am | Jul 30, 2026 8:17am | Jul 30, 2026 12:34pm | Jul 30, 2026 2:07pm | Jul 30, 2026 2:25pm | Jul 30, 2026 2:25pm | Jul 30, 2026 2:25pm | LeaningPole |  | Fair | No | Check and found okVoltage 113v 115v 227v
Outage | J.E.26.07.38154 | C001869475 | Daniel Francis | St.Ann | Completed | Load_265774 | Cardiff Hall - 210 | Jul 30, 2026 8:07am | Jul 30, 2026 8:27am | Jul 30, 2026 11:26am | Jul 30, 2026 11:26am | Jul 30, 2026 11:32am | Jul 30, 2026 10:16am | Jul 30, 2026 11:34am | Jul 30, 2026 11:34am |  |  | Fair | No | Replace 70ft service wire Use 6 one bolt clamp
Outage | J.E.26.07.38185 | C001869481 | Daniel Francis | St.Ann | Completed | Load_574372 | Cardiff Hall - 210 | Jul 30, 2026 8:07am | Jul 30, 2026 8:12am | Jul 30, 2026 12:14pm | Jul 30, 2026 12:14pm | Jul 30, 2026 12:15pm | Jul 30, 2026 12:16pm | Jul 30, 2026 12:16pm | Jul 30, 2026 12:16pm |  |  | Fair | No | Not found customer not answering phone
Outage | J.E.26.07.38206 | C001869480 | Daniel Francis | St.Ann | Completed | Load_574262 | Cardiff Hall - 210 | Jul 30, 2026 8:07am | Jul 30, 2026 8:12am | Jul 30, 2026 11:38am | Jul 30, 2026 11:38am | Jul 30, 2026 11:56am | Jul 30, 2026 12:11pm | Jul 30, 2026 12:12pm | Jul 30, 2026 12:12pm |  |  | Fair | No | Change one 2amp fuse
Outage | J.E.26.07.38219 | C001869479 | Daniel Francis | St.Ann | Completed | Load_335846 | Cardiff Hall - 210 | Jul 30, 2026 8:07am | Jul 30, 2026 8:12am | Jul 30, 2026 12:12pm | Jul 30, 2026 12:12pm | Jul 30, 2026 12:12pm | Jul 30, 2026 12:14am | Jul 30, 2026 12:14pm | Jul 30, 2026 12:14pm |  |  | Fair | No | We call and customer say light come
Non-Outage | J.E.26.07.36721 | C001869472 | Andrae Dawkins | St.James | Completed | Load_240693 | Queens Drive - 710 | Jul 30, 2026 8:05am | Jul 30, 2026 8:06am | Jul 30, 2026 1:32pm | Jul 30, 2026 1:32pm | Jul 30, 2026 2:58pm | Jul 30, 2026 1:33pm | Jul 30, 2026 3:57pm | Jul 30, 2026 3:57pm | LeaningPole |  | Fair | No | Cannot locate customer unable to reach customer mobile
Non-Outage | J.E.26.07.37093 | C001869471 | Andrae Dawkins | St.James | Completed | Load_263743 | Queens Drive - 710 | Jul 30, 2026 8:05am | Jul 30, 2026 8:06am | Jul 30, 2026 8:25am | Jul 30, 2026 9:29am | Jul 30, 2026 9:33am | Jul 30, 2026 11:03am | Jul 30, 2026 11:08am | Jul 30, 2026 11:08am |  |  | Fair | No | Found customer experiencing low voltage due to slack connection clean and remade joints used one red to red linket voltage found 112/58/57 voltage left 114/113/227
Non-Outage | J.E.26.07.37234 | C001869470 | Andrae Dawkins | St.James | Completed | Load_249993 | Queens Drive - 710 | Jul 30, 2026 8:05am | Jul 30, 2026 8:06am | Jul 30, 2026 8:25am | Jul 30, 2026 11:09am | Jul 30, 2026 11:09am | Jul 30, 2026 9:16am | Jul 30, 2026 11:12am | Jul 30, 2026 11:12am |  |  | Fair | No | Cannot locate customer unable to reach customers mobile phome
Non-Outage | J.E.26.07.37313 | C001869473 | Andrae Dawkins | St.James | Completed | Load_245936 | Queens Drive - 710 | Jul 30, 2026 8:05am | Jul 30, 2026 8:06am | Jul 30, 2026 8:26am | Jul 30, 2026 12:11pm | Jul 30, 2026 12:11pm | Jul 30, 2026 1:02pm | Jul 30, 2026 1:15pm | Jul 30, 2026 1:15pm |  |  | Fair | No | Found multiple customers in the area experiencing low voltage voltage found at customer meter 107/99/207 voltage found at transformer 116/117/232 also found one leg of transformer lead burnt refer back to emergency crew
Non-Outage | J.E.26.07.38000 | C001869474 | Andrae Dawkins | St.James | Completed | Load_240194 | Queens Drive - 710 | Jul 30, 2026 8:05am | Jul 30, 2026 8:06am | Jul 30, 2026 3:57pm | Jul 30, 2026 3:57pm | Jul 30, 2026 3:57pm | Jul 30, 2026 1:59pm | Jul 30, 2026 3:58pm | Jul 30, 2026 3:58pm | LeaningPole |  | Fair | No | Cannot locate customer
Non-Outage | J.E.26.07.30151 | C001869469 | Orville Lee | St.Catherine | Completed | Load_253883 | Twickenham - 210 | Jul 30, 2026 8:04am | Jul 30, 2026 8:05am | Jul 30, 2026 8:47am | Jul 30, 2026 2:24pm | Jul 30, 2026 2:31pm | Jul 30, 2026 2:37pm | Jul 30, 2026 2:37pm | Jul 30, 2026 2:37pm |  |  | Fair | No | Premise closed Multiple calls to customer go to voicemail Voltage 115V116V231V
Non-Outage | J.E.26.07.31021 | C001869467 | Orville Lee | Portmore | Completed | Load_266551 | Naggo Head - 510 | Jul 30, 2026 8:04am | Jul 30, 2026 8:04am | Jul 31, 2026 8:21am | Jul 31, 2026 1:28pm | Jul 31, 2026 1:38pm | Jul 31, 2026 1:49pm | Jul 31, 2026 1:50pm | Jul 31, 2026 1:50pm |  |  | Fair | No | Premises found ok upon arrival Voltage 117v118v237v
Non-Outage | J.E.26.07.34551 | C001869466 | Orville Lee | Portmore | Completed | Load_1003655 | Naggo Head - 610 | Jul 30, 2026 8:04am | Jul 30, 2026 8:04am | Jul 31, 2026 8:21am | Jul 31, 2026 12:46pm | Jul 31, 2026 1:00pm | Jul 31, 2026 1:07pm | Jul 31, 2026 1:15pm | Jul 31, 2026 1:15pm |  |  | Fair | No | Premises found ok upon arrival116v117v234vCustomer mentioned that she was reporting outage in the area
Non-Outage | J.E.26.07.36444 | C001869464 | Orville Lee | Portmore | Completed | Load_579374 | Naggo Head - 610 | Jul 30, 2026 8:04am | Jul 30, 2026 8:04am | Jul 31, 2026 8:21am | Jul 31, 2026 11:52am | Jul 31, 2026 11:56am | Jul 31, 2026 12:10pm | Jul 31, 2026 12:45pm | Jul 31, 2026 12:45pm |  |  | Fair | No | Checks made and found pothead connection corroded Three pen union usedVoltage118v120v238v
Non-Outage | J.E.26.07.36792 | C001869465 | Orville Lee | Portmore | Completed | Load_241334 | Naggo Head - 510 | Jul 30, 2026 8:04am | Jul 30, 2026 8:04am | Jul 31, 2026 8:21am | Jul 31, 2026 10:26am | Jul 31, 2026 10:26am | Jul 31, 2026 10:45am | Jul 31, 2026 10:47am | Jul 31, 2026 10:47am |  |  | Fair | No | Checks made and found pothead corroded Three pen union used Voltage 112v112v224
Non-Outage | J.E.26.07.32008 | C001869458 | Odaine Johnson | Clarendon | Completed | Load_252773 | Monymusk - 410 | Jul 30, 2026 8:03am | Jul 30, 2026 8:03am | Jul 30, 2026 10:08am | Jul 30, 2026 10:14am | Jul 30, 2026 10:29am | Jul 30, 2026 10:29am | Jul 30, 2026 10:29am | Jul 30, 2026 10:29am |  |  | Fair | No | Burn off phase found at pole remade connection using 1 one bolt clamp voltage reading 112/114/227 volts
Non-Outage | J.E.26.07.37213 | C001869463 | Orville Lee | St.Catherine | Completed | Load_251909 | Twickenham - 210 | Jul 30, 2026 8:03am | Jul 30, 2026 8:04am | Jul 30, 2026 8:46am | Jul 30, 2026 12:54pm | Jul 30, 2026 1:06pm | Jul 30, 2026 2:19pm | Jul 30, 2026 2:20pm | Jul 30, 2026 2:20pm |  |  | Fair | No | Defective service wire changed Two pen union and two one 1 bolt clamp115v
Non-Outage | J.E.26.07.37865 | C001869461 | Orville Lee | KSAS | Completed | Load_302954 | Duhaney - 210 | Jul 30, 2026 8:03am | Jul 30, 2026 8:04am | Jul 31, 2026 8:21am | Jul 31, 2026 3:45pm | Jul 31, 2026 3:56pm | Jul 31, 2026 4:00pm | Jul 31, 2026 4:02pm | Jul 31, 2026 4:02pm |  |  | Fair | No | Costumer got an electrician to rectify the problem Voltage 117v118v235v
Non-Outage | J.E.26.07.38013 | C001869457 | Odaine Johnson | Clarendon | Completed | Load_244719 | Parnassus - 210 | Jul 30, 2026 8:03am | Jul 30, 2026 8:03am | Jul 30, 2026 10:09am | Jul 30, 2026 11:43am | Jul 30, 2026 12:13pm | Jul 30, 2026 12:33am | Jul 30, 2026 12:35pm | Jul 30, 2026 12:35pm |  |  | Fair | No | Corrosion was found at service pole 3 one bolt clamps was replaced and problem was fixed Voltage reading before A112 B109 AB221Voltage reading after A113 B110 AB224
Non-Outage | J.E.26.07.27482 | C001869448 | Odaine Johnson | Clarendon | Completed | Load_259064 | Parnassus - 310 | Jul 30, 2026 8:02am | Jul 30, 2026 8:03am | Jul 30, 2026 9:35am | Jul 30, 2026 9:35am | Jul 30, 2026 9:58am | Jul 30, 2026 9:58am | Jul 30, 2026 9:58am | Jul 30, 2026 9:58am |  |  | Fair | No | Premises found okay
Non-Outage | J.E.26.07.28017 | C001869450 | Odaine Johnson | Clarendon | Completed | Load_262066 | Parnassus - 310 | Jul 30, 2026 8:02am | Jul 30, 2026 8:03am | Jul 31, 2026 8:10am | Jul 31, 2026 8:10am | Jul 31, 2026 8:11am | Jul 31, 2026 8:11am | Jul 31, 2026 8:11am | Jul 31, 2026 8:11am |  |  | Fair | No | Contacted customer and customer stated that the issue was resolved already
Non-Outage | J.E.26.07.30232 | C001869451 | Odaine Johnson | Clarendon | Completed | Load_248793 | Parnassus - 310 | Jul 30, 2026 8:02am | Jul 30, 2026 8:03am | Jul 31, 2026 8:12am | Jul 31, 2026 8:12am | Jul 31, 2026 8:12am | Jul 31, 2026 8:13am | Jul 31, 2026 8:14am | Jul 31, 2026 8:14am |  |  | Fair | No | Premises was found working ok Voltage reading is A117 B117 AB234
Non-Outage | J.E.26.07.30235 | C001869449 | Odaine Johnson | Clarendon | Completed | Load_243883 | Parnassus - 310 | Jul 30, 2026 8:02am | Jul 30, 2026 8:03am | Jul 31, 2026 8:14am | Jul 31, 2026 8:14am | Jul 31, 2026 8:15am | Jul 31, 2026 8:15am | Jul 31, 2026 8:16am | Jul 31, 2026 8:16am |  |  | Fair | No | Premises was found working ok voltage reading is A113 B114 AB227
Non-Outage | J.E.26.07.31291 | C001869453 | Odaine Johnson | Clarendon | Completed | Load_254623 | Parnassus - 310 | Jul 30, 2026 8:02am | Jul 30, 2026 8:03am | Jul 30, 2026 9:59am | Jul 30, 2026 9:59am | Jul 30, 2026 10:05am | Jul 30, 2026 10:06am | Jul 30, 2026 10:06am | Jul 30, 2026 10:06am |  |  | Fair | No | Premises found okay
Non-Outage | J.E.26.07.35375 | C001869455 | Odaine Johnson | Clarendon | Completed | Load_255474 | Parnassus - 210 | Jul 30, 2026 8:02am | Jul 30, 2026 8:03am | Jul 30, 2026 10:08am | Jul 30, 2026 1:48pm | Jul 30, 2026 2:14pm | Jul 30, 2026 2:15pm | Jul 30, 2026 2:16pm | Jul 30, 2026 2:16pm |  |  | Fair | No | Meter damaged result in customer to be experiencing single phase, meter need to be replaced
Non-Outage | J.E.26.07.36334 | C001869456 | Odaine Johnson | Clarendon | Completed | Load_247720 | Parnassus - 210 | Jul 30, 2026 8:02am | Jul 30, 2026 8:03am | Jul 30, 2026 10:09am | Jul 30, 2026 12:36pm | Jul 30, 2026 12:48pm | Jul 30, 2026 12:48pm | Jul 30, 2026 12:48pm | Jul 30, 2026 12:48pm |  |  | Fair | No | Area experiencing low voltage voltage problem, emergency team needed
Non-Outage | J.E.26.07.36373 | C001869452 | Odaine Johnson | Clarendon | Completed | Load_248978 | Parnassus - 310 | Jul 30, 2026 8:02am | Jul 30, 2026 8:03am | Jul 30, 2026 10:08am | Jul 30, 2026 10:30am | Jul 30, 2026 11:01am | Jul 30, 2026 11:01am | Jul 30, 2026 11:02am | Jul 30, 2026 11:02am |  |  | Fair | No | Corroded neutral found at pole remade connection using 1 one bolt clamp voltage reading 115/116/232 volts
Non-Outage | J.E.26.07.36840 | C001869454 | Odaine Johnson | Clarendon | Completed | Load_264684 | Parnassus - 210 | Jul 30, 2026 8:02am | Jul 30, 2026 8:03am | Jul 30, 2026 10:09am | Jul 30, 2026 12:49pm | Jul 30, 2026 1:31pm | Jul 30, 2026 1:47pm | Jul 30, 2026 1:48pm | Jul 30, 2026 1:48pm |  |  | Fair | No | Burn off neutral wire found at pole remade connection using 1 one bolt clamp voltage reading 114/115/229 volts
Non-Outage | J.E.26.07.07752 | C001869445 | Royston Montague | St.Catherine | Completed | Load_1001269 | Twickenham - 410 | Jul 30, 2026 8:01am | Jul 30, 2026 8:01am | Jul 30, 2026 8:21am | Jul 30, 2026 9:17am | Jul 30, 2026 9:41am | Jul 30, 2026 10:16am | Jul 30, 2026 10:16am | Jul 30, 2026 10:16am |  |  | Fair | No | Customer confirmed her electrician corrected loose wire inside panel box.
Non-Outage | J.E.26.07.22977 | C001869446 | Royston Montague | St.Catherine | Completed | Load_266407 | Twickenham - 310 | Jul 30, 2026 8:01am | Jul 30, 2026 8:01am | Jul 30, 2026 8:21am | Jul 30, 2026 8:42am | Jul 30, 2026 9:11am | Jul 30, 2026 9:16am | Jul 30, 2026 9:17am | Jul 30, 2026 9:17am |  |  | Fair | No | Customer confirmed issue resolved please update thanks.
Non-Outage | J.E.26.07.37425 | C001869444 | Royston Montague | St.Catherine | Completed | Load_247080 | Twickenham - 310 | Jul 30, 2026 8:01am | Jul 30, 2026 8:01am | Jul 30, 2026 8:21am | Jul 30, 2026 10:59am | Jul 30, 2026 11:14am | Jul 30, 2026 12:53pm | Jul 30, 2026 12:53pm | Jul 30, 2026 12:53pm |  |  | Fair | No | Faulty joint at pothead, same corrected. Voltage 227v 113v 113v
Outage | J.E.26.07.38228 | C001869447 | Kemark Slue | St.Catherine | Completed | Load_568498 | Tredegar - 510 | Jul 30, 2026 8:01am | Jul 30, 2026 8:05am | Jul 30, 2026 10:46am | Jul 30, 2026 10:46am | Jul 30, 2026 11:42am | Jul 30, 2026 11:42am | Jul 30, 2026 2:23pm | Jul 30, 2026 2:23pm |  |  | Fair | No | Premises was checked and found okay.
Non-Outage | J.E.26.07.11094 | C001869443 | Royston Montague | St.Catherine | Completed | Load_238151 | Twickenham - 310 | Jul 30, 2026 8:00am | Jul 30, 2026 8:01am | Jul 30, 2026 8:21am | Jul 30, 2026 10:57am | Jul 30, 2026 10:58am | Jul 30, 2026 10:59am | Jul 30, 2026 10:59am | Jul 30, 2026 10:59am |  |  | Fair | No | Damage twisted wire, #6 , same repair, voltage found 114v voltage after job completion are 229v 114v 113v
Non-Outage | J.E.26.07.20424 | C001869442 | Royston Montague | St.Catherine | Completed | Load_238583 | Twickenham - 310 | Jul 30, 2026 8:00am | Jul 30, 2026 8:01am | Jul 30, 2026 8:21am | Jul 30, 2026 10:16am | Jul 30, 2026 10:36am | Jul 30, 2026 10:38am | Jul 30, 2026 10:38am | Jul 30, 2026 10:38am |  |  | Fair | No | Open phase at customer take off point corrected yesterday, please update thanks.
Outage | J.E.26.07.38046 | C001869441 | Clyde Brown | Clarendon | Completed | Load_243695 | Parnassus - 310 | Jul 30, 2026 7:59am | Jul 30, 2026 8:01am | Jul 30, 2026 8:52am | Jul 30, 2026 8:52am | Jul 30, 2026 9:33am | Jul 30, 2026 9:44am | Jul 30, 2026 9:51am | Jul 30, 2026 9:51am |  | Y | Fair | No | Blown 8 amps junction fuse on Chatteau Road cause by bushing crew cut tree on line ,line clear and blown fuse replaced
Outage | J.E.26.07.38099 | C001869439 | Clyde Brown | Clarendon | Completed | Load_239165 | Parnassus - 310 | Jul 30, 2026 7:56am | Jul 30, 2026 7:56am | Jul 30, 2026 10:54am | Jul 30, 2026 10:54am | Jul 30, 2026 10:54am | Jul 30, 2026 10:53am | Jul 30, 2026 11:01am | Jul 30, 2026 11:01am |  |  | Fair | No | Burnt off phase wire at secondary line connection remade with one clamp for 3 wire service,voltage left 113/112 and 225V
Outage | J.E.26.07.38218 | C001869438 | Clyde Brown | Clarendon | Completed | Load_253290 | Parnassus - 310 | Jul 30, 2026 7:56am | Jul 30, 2026 7:56am | Jul 30, 2026 9:51am | Jul 30, 2026 9:52am | Jul 30, 2026 9:59am | Jul 30, 2026 10:00am | Jul 30, 2026 10:06am | Jul 30, 2026 10:06am |  |  | Fair | No | Cannot be located.
Non-Outage | J.E.26.07.35171 | C001869433 | Rochaine Hussey | KSAN | Completed | Load_258268 | Constant Spring - 410 | Jul 30, 2026 7:52am | Jul 30, 2026 7:57am | Jul 30, 2026 12:03pm | Jul 30, 2026 12:03pm | Jul 30, 2026 12:21pm | Jul 30, 2026 12:33pm | Jul 30, 2026 12:34pm | Jul 30, 2026 12:34pm |  |  | Fair | No | Customer say the issue was resolved and power was restored
Non-Outage | J.E.26.07.37203 | C001869432 | Rochaine Hussey | null | Completed | null | null | Jul 30, 2026 7:52am | Jul 30, 2026 7:56am | Jul 30, 2026 9:00am | Jul 30, 2026 10:22am | Jul 30, 2026 10:22am | Jul 30, 2026 10:23am | Jul 30, 2026 10:23am | Jul 30, 2026 10:23am |  |  | Fair | No | customer say the issue was already resolved and power was restored
Non-Outage | J.E.26.07.36442 | C001869429 | Fredrick Hamilton | KSAN | Completed | Load_254870 | Constant Spring - 210 | Jul 30, 2026 7:50am | Jul 30, 2026 7:55am | Jul 30, 2026 8:11am | Jul 30, 2026 2:34pm | Jul 30, 2026 2:55pm | Jul 30, 2026 4:08pm | Jul 30, 2026 4:08pm | Jul 30, 2026 4:08pm |  |  | Fair | No | Customer has defective meter socket at location customer advised
Non-Outage | J.E.26.07.37192 | C001869428 | Fredrick Hamilton | KSAN | Completed | Load_267514 | Constant Spring - 210 | Jul 30, 2026 7:50am | Jul 30, 2026 7:55am | Jul 30, 2026 8:11am | Jul 30, 2026 1:55pm | Jul 30, 2026 1:55pm | Jul 30, 2026 1:56pm | Jul 30, 2026 1:56pm | Jul 30, 2026 1:56pm |  |  | Fair | No | Single phase detected at pole same was corrected 1 clamp used
Non-Outage | J.E.26.07.37587 | C001869430 | Fredrick Hamilton | KSAN | Completed | Load_267514 | Constant Spring - 210 | Jul 30, 2026 7:50am | Jul 30, 2026 7:55am | Jul 30, 2026 8:11am | Jul 30, 2026 1:30pm | Jul 30, 2026 1:30pm | Jul 30, 2026 1:55pm | Jul 30, 2026 1:55pm | Jul 30, 2026 1:55pm |  |  | Fair | No | Single phase detected at pole same was corrected 1 clamp used235v/117v/118v obtained
Non-Outage | J.E.26.07.37905 | C001869431 | Fredrick Hamilton | KSAN | Completed | Load_264644 | Constant Spring - 210 | Jul 30, 2026 7:50am | Jul 30, 2026 7:55am | Jul 30, 2026 8:11am | Jul 30, 2026 9:25am | Jul 30, 2026 9:41am | Jul 30, 2026 10:23am | Jul 30, 2026 10:23am | Jul 30, 2026 10:23am |  |  | Fair | No | 3 penunions installed at pothead,pole checked customer had electrician Changed breakers and did maintenance however customer is still affected by low voltage when load is applied Please have emergency check hexing box232v/117v/118.3v obtained Pole#0155675
Non-Outage | J.E.26.07.14656 | C001869427 | Fredrick Hamilton | KSAN | Completed | Load_241917 | Washington Blvd - 310 | Jul 30, 2026 7:49am | Jul 30, 2026 7:55am | Jul 30, 2026 8:11am | Jul 31, 2026 11:56am | Jul 31, 2026 12:30pm | Jul 31, 2026 12:59pm | Jul 31, 2026 12:59pm | Jul 31, 2026 12:59pm |  |  | Fair | No | Please have emergency check hexing box connection no issues detected At pothead 236v/119v/118v obtained Corrosion detectedPole#0025209Low voltage affecting customer with and without load
Non-Outage | J.E.26.06.34761 | C001869418 | Odeanie Davis | KSAS | Completed | Load_257993 | Three Miles - 410 | Jul 30, 2026 7:48am | Jul 30, 2026 7:49am | Jul 30, 2026 10:45am | Jul 30, 2026 12:29pm | Jul 30, 2026 12:29pm | Jul 30, 2026 11:44am | Jul 30, 2026 12:30pm | Jul 30, 2026 12:30pm |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.07.04801 | C001869420 | Odeanie Davis | KSAS | Completed | Load_261195 | Hunts Bay - 810 | Jul 30, 2026 7:48am | Jul 30, 2026 7:49am | Jul 30, 2026 8:41am | Jul 30, 2026 8:42am | Jul 30, 2026 8:42am | Jul 30, 2026 8:43am | Jul 30, 2026 8:43am | Jul 30, 2026 8:43am |  |  | Fair | No | Customer stated that this issue was resolved by us
Non-Outage | J.E.26.07.05247 | C001869421 | Odeanie Davis | KSAS | Completed | Load_255943 | Three Miles - 510 | Jul 30, 2026 7:48am | Jul 30, 2026 7:49am | Jul 30, 2026 11:46am | Jul 30, 2026 1:25pm | Jul 30, 2026 1:25pm | Jul 30, 2026 1:49pm | Jul 30, 2026 4:29pm | Jul 30, 2026 4:29pm |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.07.05354 | C001869423 | Odeanie Davis | KSAS | Completed | Load_255943 | Three Miles - 510 | Jul 30, 2026 7:48am | Jul 30, 2026 7:49am | Jul 30, 2026 11:43am | Jul 30, 2026 1:24pm | Jul 30, 2026 1:24pm | Jul 30, 2026 1:31pm | Jul 30, 2026 1:25pm | Jul 30, 2026 1:25pm |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.07.11113 | C001869424 | Odeanie Davis | KSAN | Completed | Load_252305 | Washington Blvd - 310 | Jul 30, 2026 7:48am | Jul 30, 2026 7:49am | Jul 30, 2026 10:13am | Jul 30, 2026 10:13am | Jul 30, 2026 10:17am | Jul 30, 2026 10:43am | Jul 30, 2026 10:43am | Jul 30, 2026 10:43am |  |  | Fair | No | 43v/119v at location, rammi team needed
Non-Outage | J.E.26.07.11194 | C001869425 | Odeanie Davis | KSAN | Completed | Load_247699 | Washington Blvd - 310 | Jul 30, 2026 7:48am | Jul 30, 2026 7:49am | Jul 30, 2026 10:52am | Jul 30, 2026 11:02am | Jul 30, 2026 11:02am | Jul 30, 2026 11:36am | Jul 30, 2026 11:36am | Jul 30, 2026 11:36am |  |  | Fair | No | Customer stated that lights dimming in the night, no issue found at pothead or where twisted connected to secondary, 113v/114v & 227v at location, customer is the last customer on secondary line.
Non-Outage | J.E.26.07.14548 | C001869426 | Odeanie Davis | KSAS | Completed | Load_268383 | Three Miles - 510 | Jul 30, 2026 7:48am | Jul 30, 2026 7:49am | Jul 30, 2026 8:46am | Jul 30, 2026 8:46am | Jul 30, 2026 8:46am | Jul 30, 2026 8:53am | Jul 30, 2026 8:53am | Jul 30, 2026 8:53am |  |  | Fair | No | Customer stated that they didn’t report any issue
Outage | J.E.26.07.38209 | C001869415 | Wan Carlos Scarlett | St.Catherine | Completed | Load_246545 | Twickenham - 210 | Jul 30, 2026 7:45am | Jul 31, 2026 7:11am | Jul 31, 2026 3:28pm | Jul 31, 2026 3:28pm | Jul 31, 2026 3:52pm | Jul 31, 2026 3:54pm | Jul 31, 2026 3:59pm | Jul 31, 2026 3:59pm |  |  | Fair | No | Customer reporting street light not working
Outage | J.E.26.07.37956 | C001869408 | Dean Smith | Hanover | Completed | Load_295102 | Orange Bay - 310 | Jul 30, 2026 7:37am | Jul 30, 2026 7:39am | Jul 30, 2026 10:37am | Jul 30, 2026 10:38am | Jul 30, 2026 10:38am | Jul 30, 2026 10:38am | Jul 30, 2026 10:38am | Jul 30, 2026 10:38am |  |  | Fair | No | Check and found ok
Outage | J.E.26.07.38163 | C001869411 | Dean Smith | Hanover | Completed | Load_255828 | Orange Bay - 310 | Jul 30, 2026 7:37am | Jul 30, 2026 7:39am | Jul 30, 2026 9:20am | Jul 30, 2026 10:47am | Jul 30, 2026 12:16pm | Jul 30, 2026 12:16pm | Jul 30, 2026 12:17pm | Jul 30, 2026 12:17pm |  |  | Rains | No | Replace 15amp junction fuse
Outage | J.E.26.07.38204 | C001869410 | Dean Smith | Hanover | Completed | Load_302811 | Orange Bay - 310 | Jul 30, 2026 7:37am | Jul 30, 2026 7:39am | Jul 30, 2026 10:38am | Jul 30, 2026 10:38am | Jul 30, 2026 10:38am | Jul 30, 2026 10:38am | Jul 30, 2026 10:47am | Jul 30, 2026 10:47am |  |  | Fair | No | Cut and remove vegetation, replace 8amp junction fuse. Pole number n/a
Non-Outage | J.E.26.07.36426 | C001869407 | Hopeton Henry | St.Thomas | Completed | Load_249913 | Good Year - 110 | Jul 30, 2026 7:36am | Jul 31, 2026 9:07am | Jul 31, 2026 9:27am | Jul 31, 2026 11:47am | Jul 31, 2026 2:02pm | Jul 31, 2026 2:02pm | Jul 31, 2026 2:04pm | Jul 31, 2026 2:04pm |  |  | Fair | No | Reconnect service at pole 117volts
Non-Outage | J.E.26.07.36591 | C001869406 | Hopeton Henry | St.Thomas | Completed | Load_249913 | Good Year - 110 | Jul 30, 2026 7:36am | Jul 30, 2026 7:36am | Jul 30, 2026 8:41am | Jul 30, 2026 2:13pm | Jul 30, 2026 2:13pm | Jul 30, 2026 2:13pm | Jul 30, 2026 2:14pm | Jul 30, 2026 2:14pm |  |  | Fair | No | Check and found ok , issue was related to a previous outage
Non-Outage | J.E.26.07.36757 | C001869405 | Hopeton Henry | St.Thomas | Completed | Load_249913 | Good Year - 110 | Jul 30, 2026 7:36am | Jul 30, 2026 7:36am | Jul 30, 2026 8:41am | Jul 30, 2026 12:26pm | Jul 30, 2026 2:10pm | Jul 30, 2026 2:11pm | Jul 30, 2026 2:13pm | Jul 30, 2026 2:13pm |  |  | Fair | No | Found banging conductors, cut tree from secondary 111-113-224 volts
Non-Outage | J.E.26.07.36777 | C001869402 | Hopeton Henry | St.Thomas | Completed | Load_253956 | Good Year - 210 | Jul 30, 2026 7:36am | Jul 30, 2026 7:36am | Jul 30, 2026 8:41am | Jul 31, 2026 2:35pm | Jul 31, 2026 2:35pm | Jul 31, 2026 2:39pm | Jul 31, 2026 2:39pm | Jul 31, 2026 2:39pm |  |  | Fair | No | Customer not located
Non-Outage | J.E.26.07.37219 | C001869404 | Hopeton Henry | St.Thomas | Completed | Load_245745 | Good Year - 210 | Jul 30, 2026 7:36am | Jul 30, 2026 7:36am | Jul 30, 2026 8:41am | Jul 30, 2026 8:53am | Jul 30, 2026 8:53am | Jul 30, 2026 8:53am | Jul 30, 2026 8:54am | Jul 30, 2026 8:54am |  |  | Fair | No | Found defective meter , refer to field service
Non-Outage | J.E.26.07.37244 | C001869403 | Hopeton Henry | St.Thomas | Completed | Load_248874 | Good Year - 210 | Jul 30, 2026 7:36am | Jul 30, 2026 7:36am | Jul 30, 2026 8:41am | Jul 30, 2026 4:41pm | Jul 30, 2026 4:41pm | Jul 30, 2026 4:43pm | Jul 30, 2026 4:43pm | Jul 30, 2026 4:43pm |  |  | Fair | No | Found ok , issue was resolved
Outage | J.E.26.07.38174 | C001869401 | Elvis Trowers | KSAS | Completed | Load_248351 | Duhaney - 410 | Jul 30, 2026 7:32am | Jul 30, 2026 7:34am | Jul 30, 2026 10:14am | Jul 30, 2026 10:14am | Jul 30, 2026 10:36am | Jul 30, 2026 11:31am | Jul 30, 2026 11:31am | Jul 30, 2026 11:31am |  |  | Fair | Yes | Areas found without electricity supply when checked, and 2 blown junction fuses were at separate locations and was replaced after patrol was completed at pole #058660– 1/10 amp and 1/25 amp at pole #0126912.
Non-Outage | J.E.26.07.37136 | C001869398 | Wan Carlos Scarlett | null | Completed | null | null | Jul 30, 2026 7:28am | Jul 30, 2026 7:44am | Jul 30, 2026 7:51am | Jul 30, 2026 7:51am | Jul 30, 2026 8:39am | Jul 30, 2026 9:02am | Jul 30, 2026 9:07am | Jul 30, 2026 9:07am |  |  | Fair | No | Reach on location been calling customer but got no answer didn’t see any sign of wire broken are hanging low premises found okay
Outage | J.E.26.07.37858 | C001869396 | Kemark Slue | St.Catherine | Completed | Load_252716 | Tredegar - 510 | Jul 30, 2026 7:28am | Jul 30, 2026 7:59am | Jul 30, 2026 9:38am | Jul 30, 2026 9:38am | Jul 30, 2026 10:20am | Jul 30, 2026 10:46am | Jul 30, 2026 10:46am | Jul 30, 2026 10:46am |  |  | Fair | No | Premises check and found ok
Outage | J.E.26.07.37940 | C001869395 | Kemark Slue | St.Catherine | Completed | Load_574647 | Rhodens Pen - 210 | Jul 30, 2026 7:28am | Jul 30, 2026 7:55am | Jul 30, 2026 8:31am | Jul 30, 2026 8:31am | Jul 30, 2026 9:33am | Jul 30, 2026 9:35am | Jul 30, 2026 9:38am | Jul 30, 2026 9:38am |  |  | Fair | No | Unable to locate customer. Calls to number went unanswered.
Non-Outage | J.E.26.07.38167 | C001869392 | Stephen Taylor | null | Completed | null | null | Jul 30, 2026 7:26am | Jul 30, 2026 7:27am | Jul 30, 2026 11:50am | Jul 30, 2026 11:50am | Jul 30, 2026 11:50am | Jul 30, 2026 11:50am | Jul 30, 2026 11:52am | Jul 30, 2026 11:52am |  |  | Fair | No | Call to customer and customer say power is back and everything is ok
Outage | J.E.26.07.38137 | C001869393 | Stephen Taylor | St.Thomas | Completed | Load_250741 | Lysson - 410 | Jul 30, 2026 7:26am | Jul 30, 2026 7:28am | Jul 30, 2026 7:56am | Jul 30, 2026 7:56am | Jul 30, 2026 8:36am | Jul 30, 2026 8:37am | Jul 30, 2026 8:40am | Jul 30, 2026 8:40am | Fire |  | Fair | No | Drop switch and bracket defective and need to replace urgent by the jps maintenance team
Non-Outage | J.E.26.07.36037 | C001869390 | Christopher Edwards | null | Completed | null | null | Jul 30, 2026 7:25am | Jul 30, 2026 7:27am | Jul 30, 2026 9:59am | Jul 30, 2026 10:13am | Jul 30, 2026 10:36am | Jul 30, 2026 11:53am | Jul 30, 2026 11:53am | Jul 30, 2026 11:53am |  |  | Fair | No
Outage | J.E.26.07.36298 | C001869391 | Christopher Edwards | KSAN | Completed | Load_249915 | Constant Spring - 410 | Jul 30, 2026 7:25am | Jul 31, 2026 8:06am | Jul 31, 2026 9:40am | Jul 31, 2026 9:40am | Jul 31, 2026 9:40am | Jul 31, 2026 9:40am | Jul 31, 2026 9:41am | Jul 31, 2026 9:41am |  |  | Fair | No | Customer is in the st Cathrine region
Non-Outage | J.E.26.07.36665 | C001869386 | Jowayne Newmans | null | Completed | null | null | Jul 30, 2026 7:17am | Jul 30, 2026 7:19am | Jul 30, 2026 8:09am | Jul 30, 2026 8:09am | Jul 30, 2026 8:18am | Jul 30, 2026 8:19am | Jul 30, 2026 8:19am | Jul 30, 2026 8:19am |  |  | Fair | No | Jps representative stated that the cell site got back electricity from yesterday.
Outage | J.E.26.07.37279 | C001869384 | Jowayne Newmans | Portland | Completed | Load_260238 | Port Antonio - 410 | Jul 30, 2026 7:17am | Jul 30, 2026 7:19am | Jul 30, 2026 10:00am | Jul 30, 2026 10:00am | Jul 30, 2026 11:14am | Jul 30, 2026 1:27pm | Jul 30, 2026 1:27pm | Jul 30, 2026 1:27pm | BrokenWire |  | Fair | No | Patrol and found 1 pole span of neutral conductor burn down cause by overgrown tree through secondary conductor, repair by removing overgrown trees, splice and retention conductor using 10ft of #2 aluminum conductor and 4 one bolt clamps. Customers now have electricity.
Outage | J.E.26.07.38021 | C001869385 | Jowayne Newmans | Portland | Completed | Load_252444 | Port Antonio - 410 | Jul 30, 2026 7:17am | Jul 30, 2026 7:19am | Jul 30, 2026 8:19am | Jul 30, 2026 8:19am | Jul 30, 2026 9:54am | Jul 30, 2026 10:00am | Jul 30, 2026 10:00am | Jul 30, 2026 10:00am | BrokenWire |  | Fair | No | Patrol and found customer without electricity cause by burnt connection at secondary conductor, repair by reconnecting service wire to secondary conductor using 1 one bolt clamp. Voltage reading after repair 111v.
Outage | J.E.26.07.38184 | C001869383 | Cliton Henry | St.Mary | Completed | Load_261367 | Oracabessa - 210 | Jul 30, 2026 7:14am | Jul 30, 2026 7:15am | Jul 30, 2026 7:24am | Jul 30, 2026 7:24am | Jul 30, 2026 8:20am | Jul 30, 2026 10:48am | Jul 30, 2026 10:58am | Jul 30, 2026 10:58am |  |  | Fair | No | A blown 25 amp junction fuse at Ramble square at pole # 0013524 due to a dislodged insulator found cross country. The insulated was disconnected and spot bushing carryout to cut branches. Supply restored using 1-25 amp fuse.
Outage | J.E.26.07.38083 | C001869282 | Roxroy Needham | St.Ann | Completed | Load_265383 | Cardiff Hall - 210 | Jul 30, 2026 1:17am | Jul 30, 2026 7:48am | Jul 30, 2026 8:18am | Jul 30, 2026 8:18am | Jul 30, 2026 9:56am | Jul 30, 2026 10:07am | Jul 30, 2026 10:07am | Jul 30, 2026 10:07am |  |  | Fair | No | Line open for maintenance work
Outage | J.E.26.07.38031 | C001869279 | Roxroy Needham | St.Ann | Completed | Load_265383 | Cardiff Hall - 210 | Jul 30, 2026 12:15am | Jul 30, 2026 7:48am | Jul 30, 2026 10:08am | Jul 30, 2026 10:15am | Jul 30, 2026 10:15am | Jul 30, 2026 10:15am | Jul 30, 2026 10:16am | Jul 30, 2026 10:16am |  |  | Fair | No | Line open for maintenance work
Outage | J.E.26.07.38069 | C001869280 | Roxroy Needham | St.Ann | Completed | Load_243651 | Cardiff Hall - 310 | Jul 30, 2026 12:15am | Jul 30, 2026 7:48am | Jul 30, 2026 10:08am | Jul 30, 2026 10:12am | Jul 30, 2026 10:12am | Jul 30, 2026 10:14am | Jul 30, 2026 10:15am | Jul 30, 2026 10:15am |  |  | Fair | No | Line open for maintenance work
Outage | J.E.26.07.38015 | C001869262 | Shamour Haughton | St.James | Completed | Load_253389 | Bogue - 310 | Jul 29, 2026 11:09pm | Jul 29, 2026 11:12pm | Jul 30, 2026 12:16am | Jul 30, 2026 12:16am | Jul 30, 2026 1:48am | Jul 30, 2026 2:00am | Jul 30, 2026 2:01am | Jul 30, 2026 2:01am |  | Y | Fair | No | Found 2,20amp junction fuse blown caused by tree limb, cut and remove tree limb from primary and reclose 2,20amp junction at pole number 057164
Outage | J.E.26.07.38010 | C001869256 | Shamour Haughton | St.James | Completed | Load_247579 | Bogue - 310 | Jul 29, 2026 10:27pm | Jul 29, 2026 11:12pm | Jul 30, 2026 2:01am | Jul 30, 2026 2:01am | Jul 30, 2026 2:01am | Jul 30, 2026 2:01am | Jul 30, 2026 2:02am | Jul 30, 2026 2:02am |  |  | Fair | No | Related to previous call
Outage | J.E.26.07.38009 | C001869251 | Stephen Taylor | St.Thomas | Completed | Load_575858 | Good Year - 110 | Jul 29, 2026 10:08pm | Jul 30, 2026 7:26am | Jul 30, 2026 10:05am | Jul 30, 2026 10:05am | Jul 30, 2026 10:24am | Jul 30, 2026 10:25am | Jul 30, 2026 10:52am | Jul 30, 2026 10:52am |  |  | Fair | No | Patrol clean line with switch stick and close up back junction with a 7 amp fuse safely customer is now okay
Outage | J.E.26.07.38016 | C001869252 | Stephen Taylor | St.Thomas | Completed | Load_265020 | Good Year - 110 | Jul 29, 2026 10:08pm | Jul 30, 2026 7:26am | Jul 30, 2026 12:07pm | Jul 30, 2026 12:07pm | Jul 30, 2026 12:07pm | Jul 30, 2026 12:08pm | Jul 30, 2026 12:09pm | Jul 30, 2026 12:09pm |  |  | Fair | No | Patrol line and close up junction with 10ams fuses customer are now ok
Non-Outage | J.E.26.07.37943 | C001869240 | Denton Williams | null | Completed | null | null | Jul 29, 2026 9:21pm | Jul 29, 2026 9:21pm | Jul 29, 2026 9:32pm | Jul 29, 2026 9:32pm | Jul 29, 2026 9:44pm | Jul 29, 2026 10:21pm | Jul 29, 2026 10:26pm | Jul 29, 2026 10:26pm | Fire |  | Fair | No | Banging open secondary wires, cause by slack span. Retention two span of conductors to restore area to normalcy.
Non-Outage | J.E.26.07.37838 | C001869230 | Daniel Francis | St.Ann | Completed | Load_246587 | Ocho Rios - 310 | Jul 29, 2026 9:03pm | Jul 30, 2026 7:47am | Jul 30, 2026 1:24pm | Jul 30, 2026 1:24pm | Jul 30, 2026 1:30pm | Jul 30, 2026 1:45pm | Jul 30, 2026 1:45pm | Jul 30, 2026 1:45pm |  |  | Fair | No | Pole # 0180299 change two 2amp fuse power restored
Non-Outage | J.E.26.07.37777 | C001869228 | Andrew Powell | St.Elizabeth | Completed | Load_1002215 | Maggotty - 210 | Jul 29, 2026 8:57pm | Jul 29, 2026 8:58pm | Jul 30, 2026 4:41pm | Jul 30, 2026 4:41pm | Jul 30, 2026 5:12pm | Jul 30, 2026 5:49pm | Jul 30, 2026 5:51pm | Jul 30, 2026 5:51pm |  |  | Fair | No | Replace defective service wire using 30 feet #6 triplex, three clamps and three service sleeves, voltage reading 114v-115v phase to neutral 229v cross phase, meter #2851430.
Outage | J.E.26.07.37918 | C001869227 | Swon Miller | St.James | Completed | Load_262913 | Queens Drive - 310 | Jul 29, 2026 8:54pm | Jul 29, 2026 8:55pm | Jul 29, 2026 9:17pm | Jul 29, 2026 9:17pm | Jul 29, 2026 9:59pm | Jul 29, 2026 10:19pm | Jul 29, 2026 10:20pm | Jul 29, 2026 10:20pm |  |  | Fair | No | Check and found area okay unable to locate customer phone calls to customer number went unanswered
Outage | J.E.26.07.37829 | C001869226 | Wan Carlos Scarlett | St.Catherine | Completed | Load_248920 | Twickenham - 210 | Jul 29, 2026 8:51pm | Jul 29, 2026 8:52pm | Jul 29, 2026 9:06pm | Jul 29, 2026 9:06pm | Jul 29, 2026 9:46pm | Jul 29, 2026 9:57pm | Jul 29, 2026 10:05pm | Jul 29, 2026 10:05pm | BrokenWire |  | Fair | No | Customer report streetlight not working no sign of broken wire found in the area
Outage | J.E.26.07.32659 | C001869225 | Moses Elliston | Portmore | Completed | Load_269641 | Naggo Head - 510 | Jul 29, 2026 8:50pm | Jul 29, 2026 8:51pm | Jul 30, 2026 5:35pm | Jul 30, 2026 5:35pm | Jul 30, 2026 5:35pm | Jul 30, 2026 5:35pm | Jul 30, 2026 5:37pm | Jul 30, 2026 5:37pm |  |  | Fair | No | Slack linket on 3 wire service phase at pothead changed,
Outage | J.E.26.07.37862 | C001869224 | Javid Vernon | Westmoreland | Completed | Load_247636 | Paradise - 210 | Jul 29, 2026 8:48pm | Jul 29, 2026 8:49pm | Jul 29, 2026 9:02pm | Jul 29, 2026 9:03pm | Jul 29, 2026 9:32pm | Jul 29, 2026 9:49pm | Jul 29, 2026 9:49pm | Jul 29, 2026 9:49pm |  |  | Fair | No | Refuse one 25kva transformer use 4amp fuse
Non-Outage | J.E.26.07.37650 | C001869222 | Milton Charlton | KSAN | Completed | Load_240114 | Hope - 410 | Jul 29, 2026 8:46pm | Jul 29, 2026 9:13pm | Jul 30, 2026 11:32am | Jul 30, 2026 11:32am | Jul 30, 2026 12:04pm | Jul 30, 2026 12:10pm | Jul 30, 2026 12:07pm | Jul 30, 2026 12:07pm | LeakingTransformer |  | Fair | No | 50 kva transformer at pole #0007316 leaking oil but customer feeding from bank of 3-50 kva have supply. The lighting transformer leaking oil.
Non-Outage | J.E.26.07.36798 | C001869220 | Damion Reid | Manchester | Completed | Load_238024 | Kendal - 210 | Jul 29, 2026 8:42pm | Jul 29, 2026 8:49pm | Jul 29, 2026 9:17pm | Jul 29, 2026 9:17pm | Jul 29, 2026 10:48pm | Jul 29, 2026 11:04pm | Jul 29, 2026 11:05pm | Jul 29, 2026 11:05pm |  |  | Fair | No | Remade corroded phase at secondary jumper using one 1 bolt clamp
Outage | J.E.26.07.37859 | C001869219 | Barnett Brown | Manchester | Completed | Load_250583 | Spur Tree - 310 | Jul 29, 2026 8:42pm | Jul 30, 2026 10:44am | Jul 30, 2026 1:57pm | Jul 30, 2026 1:57pm | Jul 30, 2026 2:21pm | Jul 30, 2026 2:22pm | Jul 30, 2026 2:26pm | Jul 30, 2026 2:26pm |  |  | Fair | No | Premises found ok, customer said she didn’t make any report
Non-Outage | J.E.26.07.37843 | C001869214 | Tyrese Williams | null | Completed | null | null | Jul 29, 2026 8:27pm | Jul 29, 2026 8:28pm | Jul 29, 2026 8:42pm | Jul 29, 2026 8:42pm | Jul 29, 2026 9:28pm | Jul 29, 2026 9:31pm | Jul 29, 2026 9:31pm | Jul 29, 2026 9:31pm | BrokenWire |  | Fair | No | Premises found ok internet wire seen burst down
Outage | J.E.26.07.37085 | C001869213 | Tyrese Williams | St.Ann | Completed | Load_256510 | Cardiff Hall - 210 | Jul 29, 2026 8:27pm | Jul 29, 2026 8:28pm | Jul 29, 2026 8:42pm | Jul 29, 2026 9:31pm | Jul 29, 2026 10:04pm | Jul 29, 2026 10:21pm | Jul 29, 2026 10:21pm | Jul 29, 2026 10:21pm | BrokenWire |  | Fair | No | Remade neutral jumper use 1 pg clamp
Outage | J.E.26.07.33467 | C001869195 | Raymond Lewis | St.Ann | Completed | Load_258103 | Roaring River - 410 | Jul 29, 2026 7:45pm | Jul 29, 2026 7:45pm | Jul 29, 2026 7:49pm | Jul 29, 2026 7:49pm | Jul 29, 2026 7:49pm | Jul 29, 2026 7:57pm | Jul 29, 2026 7:58pm | Jul 29, 2026 7:58pm |  |  | Fair | No | 30 class 6 wood pole rotten out(DE pole with service wire and 1street light 2 span need to retention
Outage | J.E.26.07.37835 | C001869191 | Romeo Brissett | St.James | Completed | Load_238926 | Bogue - 610 | Jul 29, 2026 7:32pm | Jul 29, 2026 7:32pm | Jul 29, 2026 10:10pm | Jul 29, 2026 10:11pm | Jul 29, 2026 10:11pm | Jul 29, 2026 10:10pm | Jul 29, 2026 10:12pm | Jul 29, 2026 10:12pm |  |  | Fair | No | Check and found ok
Outage | J.E.26.07.37792 | C001869190 | Richard Nicholas | St.Catherine | Completed | Load_269823 | Tredegar - 410 | Jul 29, 2026 7:19pm | Jul 29, 2026 7:21pm | Jul 29, 2026 8:10pm | Jul 29, 2026 8:10pm | Jul 29, 2026 9:13pm | Jul 29, 2026 10:47pm | Jul 29, 2026 10:48pm | Jul 29, 2026 10:48pm |  |  | Fair | No | Replaced blown 30amp x2 junctions fuse on pole #008104.
Outage | J.E.26.07.35802 | C001869188 | Romeo Brissett | Trelawny | Completed | Load_239272 | Greenwood - 210 | Jul 29, 2026 7:15pm | Jul 29, 2026 7:16pm | Jul 29, 2026 7:45pm | Jul 29, 2026 7:45pm | Jul 29, 2026 7:46pm | Jul 29, 2026 8:00pm | Jul 29, 2026 8:04pm | Jul 29, 2026 8:04pm |  |  | Fair | No | Check and found ok related to #37239
Outage | J.E.26.07.37775 | C001869187 | Omar King | St.Ann | Completed | Load_243386 | Ocho Rios - 410 | Jul 29, 2026 7:13pm | Jul 29, 2026 7:14pm | Jul 29, 2026 8:58pm | Jul 29, 2026 8:58pm | Jul 29, 2026 8:59pm | Jul 29, 2026 9:37pm | Jul 29, 2026 9:37pm | Jul 29, 2026 9:37pm |  |  | Fair | No | Found 100 KVA transformer fuse blown and switch defective temporary work as been carry out customer is now with supply
Outage | J.E.26.07.37806 | C001869185 | Tajay Bernard | Hanover | Completed | Load_264233 | Orange Bay - 310 | Jul 29, 2026 7:13pm | Jul 29, 2026 7:13pm | Jul 29, 2026 7:43pm | Jul 29, 2026 7:43pm | Jul 29, 2026 8:12pm | Jul 29, 2026 8:26pm | Jul 29, 2026 8:27pm | Jul 29, 2026 8:27pm |  |  | Fair | No | Refuse 1 50kva Transformer use 5amp fuse
Non-Outage | J.E.26.07.36688 | C001869182 | Hopeton Henry | St.Thomas | Completed | Load_248874 | Good Year - 210 | Jul 29, 2026 6:49pm | Jul 29, 2026 6:50pm | Jul 29, 2026 7:23pm | Jul 30, 2026 2:15pm | Jul 30, 2026 2:23pm | Jul 30, 2026 4:40pm | Jul 30, 2026 4:41pm | Jul 30, 2026 4:41pm |  |  | Fair | No | Found corrosion at pole and pot head , use 12 clamps 119-120-240 volts
Outage | J.E.26.07.37733 | C001869180 | Edward Royal | KSAS | Completed | Load_246165 | Greenwich - 410 | Jul 29, 2026 6:47pm | Jul 29, 2026 6:51pm | Jul 29, 2026 8:07pm | Jul 29, 2026 8:07pm | Jul 29, 2026 8:07pm | Jul 29, 2026 8:41pm | Jul 29, 2026 8:42pm | Jul 29, 2026 8:42pm | Fire |  | Fair | No | Spliced and reconnected secondary phase jumper using 2 single bolt clamp
Outage | J.E.26.07.37660 | C001869177 | Edward Royal | KSAS | Completed | Load_289600 | Greenwich - 510 | Jul 29, 2026 6:40pm | Jul 29, 2026 6:51pm | Jul 29, 2026 9:38pm | Jul 29, 2026 9:38pm | Jul 29, 2026 9:38pm | Jul 29, 2026 9:39pm | Jul 29, 2026 9:39pm | Jul 29, 2026 9:39pm |  |  | Fair | No | Meter not responding meter need to be check reffered to field service
Outage | J.E.26.07.37367 | C001869176 | Richman Whyte | Westmoreland | Completed | Load_244556 | Paradise - 310 | Jul 29, 2026 6:35pm | Jul 29, 2026 6:35pm | Jul 29, 2026 7:34pm | Jul 29, 2026 7:34pm | Jul 29, 2026 7:34pm | Jul 29, 2026 7:34pm | Jul 29, 2026 7:35pm | Jul 29, 2026 7:35pm |  |  | Fair | No | Customer is requesting a daylight visit
Non-Outage | J.E.26.07.34578 | C001869173 | Andrew Powell | St.Elizabeth | Completed | Load_1002276 | Maggotty - 210 | Jul 29, 2026 6:12pm | Jul 29, 2026 6:13pm | Jul 29, 2026 11:00pm | Jul 29, 2026 11:00pm | Jul 29, 2026 11:01pm | Jul 29, 2026 11:01pm | Jul 29, 2026 11:02pm | Jul 29, 2026 11:02pm |  |  | Fair | No | Premises not located inadequately direction contact customer by telephone unsuccessful.
Non-Outage | J.E.26.07.35164 | C001869171 | Andrew Powell | Manchester | Completed | Load_302753 | Spur Tree - 210 | Jul 29, 2026 6:12pm | Jul 29, 2026 6:13pm | Jul 29, 2026 7:07pm | Jul 29, 2026 7:07pm | Jul 29, 2026 7:43pm | Jul 29, 2026 8:08pm | Jul 29, 2026 8:11pm | Jul 29, 2026 8:11pm |  |  | Fair | No | Remade corroded service wire phase joint at meter pothead 3 wire using one service sleeves, voltage reading 117v-117v phase to neutral 234v cross phase.
Non-Outage | J.E.26.07.36794 | C001869172 | Andrew Powell | St.Elizabeth | Completed | Load_254148 | Maggotty - 210 | Jul 29, 2026 6:12pm | Jul 29, 2026 6:13pm | Jul 29, 2026 8:11pm | Jul 29, 2026 8:11pm | Jul 29, 2026 10:57pm | Jul 29, 2026 10:00pm | Jul 29, 2026 11:00pm | Jul 29, 2026 11:00pm |  |  | Fair | No | Clear vegetation and replace defective service wire using 100 feet #6 triplex, three clamps and three service sleeves, voltage reading 108v-109v phase to neutral 217v cross phase, meter #2966742.
Non-Outage | J.E.26.07.37299 | C001869170 | Andrew Powell | null | Completed | null | null | Jul 29, 2026 6:10pm | Jul 29, 2026 6:10pm | Jul 29, 2026 6:13pm | Jul 29, 2026 6:14pm | Jul 29, 2026 6:35pm | Jul 29, 2026 6:40pm | Jul 29, 2026 6:42pm | Jul 29, 2026 6:42pm |  |  | Fair | No | Close three drop out switches protect 750 kva pod mounted transformer, no pole number by switch location, restore supply okay.
Outage | J.E.26.07.37147 | C001869168 | Rayon Foster | Hanover | Completed | Load_245538 | Orange Bay - 310 | Jul 29, 2026 6:05pm | Jul 29, 2026 6:09pm | Jul 30, 2026 8:11am | Jul 30, 2026 8:11am | Jul 30, 2026 8:52am | Jul 30, 2026 9:11am | Jul 30, 2026 9:12am | Jul 30, 2026 9:12am | LeaningPole |  | Fair | No | Unable to locate customer or reach on cellphone (to be revisit )
Outage | J.E.26.07.37590 | C001869167 | Rayon Foster | Hanover | Completed | Load_258804 | Orange Bay - 310 | Jul 29, 2026 6:03pm | Jul 29, 2026 6:04pm | Jul 29, 2026 8:28pm | Jul 29, 2026 9:05pm | Jul 29, 2026 9:05pm | Jul 29, 2026 9:14pm | Jul 29, 2026 9:16pm | Jul 29, 2026 9:16pm |  |  | Fair | No | Patrol primary line to find 1 blown 10 amp junction fuse carry complete line patrol and carry out bushing before replacing 1 10amp junction at same and close
Non-Outage | J.E.26.07.36449 | C001869165 | Evan Spaulding | St.Mary | Completed | Load_269511 | Annotto Bay - 310 | Jul 29, 2026 5:55pm | Jul 29, 2026 5:55pm | Jul 29, 2026 6:06pm | Jul 29, 2026 6:06pm | Jul 29, 2026 6:48pm | Jul 29, 2026 7:14pm | Jul 29, 2026 7:15pm | Jul 29, 2026 7:15pm |  |  | Fair | No | Replace 1-8 amps junction fuse at pole number 0005246.
Non-Outage | J.E.26.07.37392 | C001869161 | Richard Grant | null | Completed | null | null | Jul 29, 2026 5:32pm | Jul 29, 2026 5:32pm | Jul 29, 2026 6:44pm | Jul 29, 2026 6:44pm | Jul 29, 2026 7:32pm | Jul 29, 2026 7:35pm | Jul 29, 2026 7:36pm | Jul 29, 2026 7:36pm | LowHangingWires |  | Fair | No | Full opened secondary T off has low hanging wires. Kindly send email to A Murray to have line section assess and rectify.
Non-Outage | J.E.26.07.36396 | C001869160 | Nickolas Rodriques | St.Catherine | Completed | Load_268720 | Tredegar - 510 | Jul 29, 2026 5:30pm | Jul 29, 2026 5:30pm | Jul 29, 2026 6:41pm | Jul 29, 2026 7:22pm | Jul 29, 2026 8:19pm | Jul 29, 2026 9:28pm | Jul 29, 2026 9:32pm | Jul 29, 2026 9:32pm |  |  | Fair | No | Customer stated that she is unable to accommodate the team at this time. She stated that she will make back a report whenever she is available.
Outage | J.E.26.07.37554 | C001869159 | Hartley Chin | Clarendon | Completed | Load_250569 | Monymusk - 210 | Jul 29, 2026 5:29pm | Jul 29, 2026 5:30pm | Jul 29, 2026 8:48pm | Jul 29, 2026 8:48pm | Jul 29, 2026 9:38pm | Jul 29, 2026 10:52pm | Jul 29, 2026 10:52pm | Jul 29, 2026 10:52pm | Fire |  | Fair | No | Isolate 25KVA transformer @ pole # 0129570 due to broken open secondary phase found , broken joint repaired, re-energized transformer…
Outage | J.E.26.07.37545 | C001869157 | Edward Royal | KSAS | Completed | Load_1003016 | Three Miles - 410 | Jul 29, 2026 5:24pm | Jul 29, 2026 5:24pm | Jul 29, 2026 6:09pm | Jul 29, 2026 6:09pm | Jul 29, 2026 6:09pm | Jul 29, 2026 6:18pm | Jul 29, 2026 6:18pm | Jul 29, 2026 6:18pm |  |  | Fair | No | Contact customer by phone customer said he have difficulty adding credit when I contacted escalation the agent said it must referred to field service team.
Outage | J.E.26.07.37344 | C001869155 | Hartley Chin | Clarendon | Completed | Load_249022 | May Pen - 210 | Jul 29, 2026 5:18pm | Jul 29, 2026 5:18pm | Jul 29, 2026 8:42pm | Jul 29, 2026 8:42pm | Jul 29, 2026 8:42pm | Jul 29, 2026 8:47pm | Jul 29, 2026 8:48pm | Jul 29, 2026 8:48pm | BrokenPole |  | Fair | No | Ref to maintenance!!!! Found leaning/rotten 30 ft pole with open secondary circuit .. pole requires immediate attention due to it leaning over customers house … pole foot is 100% rotten … note: customer supply is okay .
Outage | J.E.26.07.37411 | C001869152 | Fitzroy Turner | KSAS | Completed | Load_290055 | Hunts Bay - 810 | Jul 29, 2026 5:14pm | Jul 29, 2026 5:16pm | Jul 29, 2026 6:01pm | Jul 29, 2026 6:04pm | Jul 29, 2026 6:04pm | Jul 29, 2026 6:04pm | Jul 29, 2026 6:05pm | Jul 29, 2026 6:05pm |  |  | Fair | No | Customer needs to reconnect in hexing box
Outage | J.E.26.07.37385 | C001869149 | Denton Williams | Portland | Completed | Load_261020 | Port Antonio - 410 | Jul 29, 2026 5:08pm | Jul 29, 2026 5:08pm | Jul 29, 2026 5:12pm | Jul 29, 2026 5:12pm | Jul 29, 2026 5:19pm | Jul 29, 2026 5:38pm | Jul 29, 2026 5:39pm | Jul 29, 2026 5:39pm |  |  | Fair | No | Defective 50kva transformer, also leaking oil. A replacement is needed. Please refer to the Portland maintenance team.
Non-Outage | J.E.26.07.17290 | C001869147 | Tyrese Williams | St.Ann | Completed | Load_248442 | Cardiff Hall - 310 | Jul 29, 2026 5:01pm | Jul 29, 2026 5:09pm | Jul 29, 2026 8:05pm | Jul 29, 2026 8:06pm | Jul 29, 2026 8:06pm | Jul 29, 2026 8:07pm | Jul 29, 2026 8:07pm | Jul 29, 2026 8:07pm |  |  | Fair | No | Premises not found not getting customer on phone
Non-Outage | J.E.26.07.37406 | C001869146 | Andre Williams | null | Completed | null | null | Jul 29, 2026 5:00pm | Jul 30, 2026 12:03pm | Jul 30, 2026 12:17pm | Jul 30, 2026 12:17pm | Jul 30, 2026 1:52pm | Jul 30, 2026 5:05pm | Jul 30, 2026 5:06pm | Jul 30, 2026 5:06pm | BrokenWire |  | Fair | No | Splice and retention 3 span open secondary,open 25 kva transformer remake jumper that was open customers now with supply
Outage | J.E.26.07.37380 | C001869143 | Andre Williams | Trelawny | Completed | Load_303159 | Duncans - 210 | Jul 29, 2026 5:00pm | Jul 30, 2026 4:51pm | Jul 30, 2026 5:15pm | Jul 30, 2026 5:15pm | Jul 30, 2026 5:15pm | Jul 30, 2026 5:17pm | Jul 30, 2026 5:17pm | Jul 30, 2026 5:17pm |  |  | Fair | No | Premises ok power was restored from yesterday
Outage | J.E.26.07.37382 | C001869144 | Marlon Brown | Trelawny | Completed | Load_240708 | Duncans - 210 | Jul 29, 2026 5:00pm | Jul 29, 2026 5:01pm | Jul 29, 2026 5:16pm | Jul 29, 2026 5:16pm | Jul 29, 2026 7:12pm | Jul 29, 2026 11:48pm | Jul 29, 2026 11:51pm | Jul 29, 2026 11:51pm |  |  | Fair | No | Tree fell on line resulting in the braking of primary phase and secondary circuit. Primary was replaced along with some of the secondary, however approximately 7 customers were left out. Requires about 250ft #2 triplex or 4 sets of D- iron crevice and approximately 200ft #2 AAC to complete the repair of circuit. See permit number 11032 For details, 1 20amps junction fuse, 6 pg clamps, 5 preforms 2 sets of D- iron crevice.
Outage | J.E.26.07.37322 | C001869142 | Romeo Brissett | St.James | Completed | Load_241352 | Bogue - 610 | Jul 29, 2026 4:58pm | Jul 29, 2026 4:59pm | Jul 29, 2026 7:39pm | Jul 29, 2026 8:04pm | Jul 29, 2026 9:03pm | Jul 29, 2026 10:08pm | Jul 29, 2026 10:10pm | Jul 29, 2026 10:10pm |  |  | Fair | No | Removed tree limbs replaced (1)10amps junction fuse.
Outage | J.E.26.07.37360 | C001869141 | Elvis Trowers | KSAN | Completed | Load_248139 | Constant Spring - 210 | Jul 29, 2026 4:58pm | Jul 30, 2026 7:33am | Jul 30, 2026 9:38am | Jul 30, 2026 9:38am | Jul 30, 2026 10:02am | Jul 30, 2026 10:09am | Jul 30, 2026 10:09am | Jul 30, 2026 10:09am |  |  | Fair | Yes | Premises found closed upon arrival and customer could not be contacted by telephone either after several calls, even though areas was checked and found with regular electricity supply.
Outage | J.E.26.07.37382 | C001869138 | Andre Williams | Trelawny | Completed | Load_240708 | Duncans - 210 | Jul 29, 2026 4:58pm | Jul 30, 2026 4:51pm | Jul 30, 2026 5:08pm | Jul 30, 2026 5:08pm | Jul 30, 2026 5:08pm | Jul 30, 2026 5:09pm | Jul 30, 2026 5:10pm | Jul 30, 2026 5:10pm |  |  | Fair | No | Job completed since evening area with supply
Outage | J.E.26.07.37398 | C001869139 | Milton Charlton | KSAN | Completed | Load_238547 | Washington Blvd - 610 | Jul 29, 2026 4:58pm | Jul 29, 2026 5:01pm | Jul 29, 2026 7:09pm | Jul 29, 2026 7:13pm | Jul 29, 2026 7:13pm | Jul 29, 2026 7:15pm | Jul 29, 2026 7:14pm | Jul 29, 2026 7:14pm |  |  | Fair | No | Call related to call at East King House Road.
Outage | J.E.26.07.37279 | C001869127 | Denton Williams | Portland | Completed | Load_260238 | Port Antonio - 410 | Jul 29, 2026 4:44pm | Jul 29, 2026 5:08pm | Jul 29, 2026 6:02pm | Jul 29, 2026 6:02pm | Jul 29, 2026 6:02pm | Jul 29, 2026 6:05pm | Jul 29, 2026 6:11pm | Jul 29, 2026 6:11pm | BrokenWire |  | Fair | No | Crew is unable to respond to call due to our vehicle is a truck. A small pickup van is needed to respond to this power outage.
Outage | J.E.26.07.36892 | C001869124 | Hopeton Henry | St.Thomas | Completed | Load_263983 | Good Year - 210 | Jul 29, 2026 4:41pm | Jul 29, 2026 4:56pm | Jul 29, 2026 5:04pm | Jul 29, 2026 8:43pm | Jul 29, 2026 8:54pm | Jul 29, 2026 9:01pm | Jul 29, 2026 9:01pm | Jul 29, 2026 9:01pm |  |  | Fair | No | Refresh connections at pole and pot head 115-112-227 v
Outage | J.E.26.07.36351 | C001869114 | Wan Carlos Scarlett | St.Catherine | Completed | Load_244322 | Twickenham - 210 | Jul 29, 2026 4:27pm | Jul 29, 2026 4:28pm | Jul 29, 2026 6:23pm | Jul 29, 2026 6:23pm | Jul 29, 2026 7:43pm | Jul 29, 2026 7:44pm | Jul 29, 2026 7:45pm | Jul 29, 2026 7:45pm |  |  | Fair | No | Refuse 10amp junction no pole # was found suspect bird take out the power supply
Outage | J.E.26.07.37348 | C001869113 | Tajay Bernard | Hanover | Completed | Load_252358 | Orange Bay - 310 | Jul 29, 2026 4:27pm | Jul 29, 2026 4:28pm | Jul 29, 2026 4:32pm | Jul 29, 2026 4:32pm | Jul 29, 2026 5:43pm | Jul 29, 2026 6:50pm | Jul 29, 2026 6:52pm | Jul 29, 2026 6:52pm |  |  | Fair | No | Splice and retention 2 pole span of secondary phase and neutral and refuse 1 25kva Transformer use a 3amp fuse, 4 #2 preform and 2 clamps
Outage | J.E.26.07.37317 | C001869112 | Tajay Bernard | Hanover | Completed | Load_247675 | Orange Bay - 210 | Jul 29, 2026 4:26pm | Jul 29, 2026 4:28pm | Jul 29, 2026 4:32pm | Jul 29, 2026 6:52pm | Jul 29, 2026 7:31pm | Jul 29, 2026 7:43pm | Jul 29, 2026 7:43pm | Jul 29, 2026 7:43pm |  |  | Fair | No | Area check and found okay unable to locate customer on premises multiple phone call to customer number went unanswered
Outage | J.E.26.07.37310 | C001869110 | Javid Vernon | Westmoreland | Completed | Load_254355 | Paradise - 210 | Jul 29, 2026 4:23pm | Jul 29, 2026 4:23pm | Jul 29, 2026 6:09pm | Jul 29, 2026 8:42pm | Jul 29, 2026 8:42pm | Jul 29, 2026 8:42pm | Jul 29, 2026 8:43pm | Jul 29, 2026 8:43pm | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Related to previous call job #37138
Outage | J.E.26.07.37339 | C001869111 | Richman Whyte | Westmoreland | Completed | Load_263806 | Paradise - 310 | Jul 29, 2026 4:23pm | Jul 29, 2026 4:24pm | Jul 29, 2026 6:30pm | Jul 29, 2026 6:30pm | Jul 29, 2026 6:30pm | Jul 29, 2026 6:31pm | Jul 29, 2026 6:32pm | Jul 29, 2026 6:32pm |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.36733 | C001869097 | Raymond Lewis | St.Ann | Completed | Load_248565 | Cardiff Hall - 210 | Jul 29, 2026 4:08pm | Jul 29, 2026 4:08pm | Jul 29, 2026 5:17pm | Jul 29, 2026 5:17pm | Jul 29, 2026 5:46pm | Jul 29, 2026 5:48pm | Jul 29, 2026 5:48pm | Jul 29, 2026 5:48pm | LeaningPole |  | Fair | No | Pole ok
Outage | J.E.26.07.32659 | C001869096 | Richard Nicholas | Portmore | Completed | Load_269641 | Naggo Head - 510 | Jul 29, 2026 4:04pm | Jul 29, 2026 4:05pm | Jul 29, 2026 6:57pm | Jul 29, 2026 6:57pm | Jul 29, 2026 7:40pm | Jul 29, 2026 8:08pm | Jul 29, 2026 8:10pm | Jul 29, 2026 8:10pm |  |  | Fair | No | Rammy system failure,customer experiencing single phasing that is detected at the rammy box.
Non-Outage | J.E.26.07.01265 | C001869089 | Wan Carlos Scarlett | Portmore | Completed | Load_260088 | Naggo Head - 510 | Jul 29, 2026 4:02pm | Jul 29, 2026 4:02pm | Jul 29, 2026 4:21pm | Jul 29, 2026 4:21pm | Jul 29, 2026 4:59pm | Jul 29, 2026 6:22pm | Jul 29, 2026 6:23pm | Jul 29, 2026 6:23pm |  |  | Fair | No | Found customer 3 wire service at pole with one of the phase corroded use 2 one bolt clamps at secondary line phase readings 116-114-231
Non-Outage | J.E.26.07.30916 | C001869090 | Wan Carlos Scarlett | Portmore | Completed | Load_261913 | Naggo Head - 510 | Jul 29, 2026 4:02pm | Jul 29, 2026 4:02pm | Jul 29, 2026 7:45pm | Jul 29, 2026 7:45pm | Jul 29, 2026 8:41pm | Jul 29, 2026 9:04pm | Jul 29, 2026 9:06pm | Jul 29, 2026 9:06pm |  |  | Fair | No | Found customer 3 wire service at pole with one of the phase corroded use one bolt clamp at secondary line phase readings 114-113-229
Outage | J.E.26.07.37275 | C001869088 | Richman Whyte | Westmoreland | Completed | Load_252258 | Paradise - 310 | Jul 29, 2026 3:58pm | Jul 29, 2026 3:59pm | Jul 29, 2026 4:09pm | Jul 29, 2026 4:09pm | Jul 29, 2026 4:10pm | Jul 29, 2026 4:10pm | Jul 29, 2026 4:10pm | Jul 29, 2026 4:10pm |  |  | Fair | No | Replace 5amp junction fuse
Outage | J.E.26.07.36745 | C001869083 | Andrew Powell | St.Elizabeth | Completed | Load_241225 | Maggotty - 210 | Jul 29, 2026 3:56pm | Jul 30, 2026 4:27pm | Jul 30, 2026 4:35pm | Jul 30, 2026 4:35pm | Jul 30, 2026 4:35pm | Jul 30, 2026 4:35pm | Jul 30, 2026 4:36pm | Jul 30, 2026 4:36pm |  |  | Fair | No | Premises found okay customer stated that fault resolved supply restored.
Outage | J.E.26.07.36822 | C001869082 | Richard Watson | St.Elizabeth | Completed | Load_238591 | Maggotty - 110 | Jul 29, 2026 3:55pm | Jul 29, 2026 3:56pm | Jul 29, 2026 7:59pm | Jul 29, 2026 8:05pm | Jul 29, 2026 8:23pm | Jul 29, 2026 9:19pm | Jul 29, 2026 9:26pm | Jul 29, 2026 9:26pm | BrokenWire |  | Fair | No | Splice and retention one span of broken secondary common neutral, also retention one span of top and lower secondary phase, use approximately 30ft of #2 aluminum conductor, one 1bolt clamp and one #2 splicing sleeve.
Outage | J.E.26.07.37097 | C001869080 | Richard Watson | St.Elizabeth | Completed | Load_263224 | Maggotty - 110 | Jul 29, 2026 3:55pm | Jul 29, 2026 3:56pm | Jul 29, 2026 5:50pm | Jul 29, 2026 5:51pm | Jul 29, 2026 6:50pm | Jul 29, 2026 7:35pm | Jul 29, 2026 7:56pm | Jul 29, 2026 7:56pm | TreeContact | Y | Fair | No | Replace blown 15amp junction fuse no pole# one pole span from St. Paul’s square cause by defective 25kva transformer at Medina no pole#, transformer leaking a lot of oil, oil spill bag required, huge tree fell on open wire secondary breaking all three conductors (one span), transformer d/o switch needs to replace urgently. Approximately 20 customers are without supply please refer to Mr Delroy Crew for replacement.
Outage | J.E.26.07.37103 | C001869079 | Marlon Authors | St.Elizabeth | Completed | Load_305159 | Maggotty - 210 | Jul 29, 2026 3:54pm | Jul 30, 2026 10:20am | Jul 30, 2026 11:38am | Jul 30, 2026 12:09pm | Jul 30, 2026 12:32pm | Jul 30, 2026 1:52pm | Jul 30, 2026 1:59pm | Jul 30, 2026 1:59pm |  |  | Fair | No | Patrol and found clear. Replace one blown 15 amp junction fuse no pole #. Restored supply ok
Outage | J.E.26.07.36751 | C001869069 | Selvin White | St.Elizabeth | Completed | Load_574151 | Maggotty - 110 | Jul 29, 2026 3:50pm | Jul 30, 2026 10:40am | Jul 30, 2026 11:17am | Jul 30, 2026 11:17am | Jul 30, 2026 12:08pm | Jul 30, 2026 12:13pm | Jul 30, 2026 12:13pm | Jul 30, 2026 12:13pm |  |  | Fair | No | Premises found damaged and is under reconstruction. Customer says damaged was done during hurricane Melissa. No meter or service wire found at location.
Outage | J.E.26.07.36773 | C001869068 | Andrew Powell | St.Elizabeth | Completed | Load_1002241 | Maggotty - 210 | Jul 29, 2026 3:50pm | Jul 29, 2026 3:51pm | Jul 29, 2026 4:16pm | Jul 29, 2026 4:16pm | Jul 29, 2026 4:49pm | Jul 29, 2026 5:06pm | Jul 29, 2026 5:11pm | Jul 29, 2026 5:11pm |  |  | Fair | No | Found customer disconnected by error due to meter displacement, meter #2932373 and #2858409 customer leaves without supply please refer to field service department for correction.
Outage | J.E.26.07.37046 | C001869067 | Andrew Powell | St.Elizabeth | Completed | Load_240230 | Maggotty - 210 | Jul 29, 2026 3:50pm | Jul 29, 2026 3:51pm | Jul 29, 2026 5:14pm | Jul 29, 2026 5:14pm | Jul 29, 2026 5:44pm | Jul 29, 2026 6:04pm | Jul 29, 2026 6:11pm | Jul 29, 2026 6:11pm |  |  | Fair | No | Found defective 3 wire AMI smart meter #2964608 no supply passing through meter customer leaves with out supply, voltage reading 107v-109v phase to neutral 216v cross phase inside meter socket, please refer to field service department for replacement.
Non-Outage | J.E.26.07.33796 | C001869060 | Nickolas Rodriques | null | Completed | null | null | Jul 29, 2026 3:46pm | Jul 29, 2026 3:46pm | Jul 29, 2026 4:10pm | Jul 29, 2026 4:22pm | Jul 29, 2026 4:48pm | Jul 29, 2026 4:55pm | Jul 29, 2026 4:56pm | Jul 29, 2026 4:56pm |  |  | Fair | No | Customer confirmed that the power outage was already restored.
Outage | J.E.26.07.37207 | C001869058 | Ryan Richards | Manchester | Completed | Load_256152 | Spur Tree - 310 | Jul 29, 2026 3:43pm | Jul 29, 2026 3:44pm | Jul 29, 2026 4:28pm | Jul 29, 2026 4:28pm | Jul 29, 2026 6:31pm | Jul 29, 2026 7:14pm | Jul 29, 2026 7:15pm | Jul 29, 2026 7:15pm | BrokenWire |  | Fair | No | 4 broken service wires also supply found wires where feeding 15 meters all meters where affected cause by bushing team splice and retention using 150ft#6 triplex 12 penunion Voltage 116/117/234 volts
Non-Outage | J.E.26.07.36404 | C001869056 | Hartley Chin | null | Completed | null | null | Jul 29, 2026 3:41pm | Jul 29, 2026 3:41pm | Jul 29, 2026 3:48pm | Jul 29, 2026 3:53pm | Jul 29, 2026 3:54pm | Jul 29, 2026 3:54pm | Jul 29, 2026 3:54pm | Jul 29, 2026 3:54pm |  |  | SevereWind | No | Call related to job # 36345 ..
Non-Outage | J.E.26.07.30980 | C001869054 | Richard Grant | St.Catherine | Completed | Load_238048 | New Michelton - 410 | Jul 29, 2026 3:40pm | Jul 29, 2026 3:40pm | Jul 29, 2026 5:33pm | Jul 29, 2026 5:33pm | Jul 29, 2026 6:42pm | Jul 29, 2026 6:44pm | Jul 29, 2026 6:44pm | Jul 29, 2026 6:44pm |  |  | Fair | No | 115 115 230 208 235 236 voltages found at premises. Premises found okay
Outage | J.E.26.07.36683 | C001869053 | Richard Grant | St.Catherine | Completed | Load_252376 | New Michelton - 410 | Jul 29, 2026 3:40pm | Jul 29, 2026 3:40pm | Jul 29, 2026 3:49pm | Jul 29, 2026 4:01pm | Jul 29, 2026 5:31pm | Jul 29, 2026 5:32pm | Jul 29, 2026 5:33pm | Jul 29, 2026 5:33pm |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.37239 | C001869055 | Romeo Brissett | St.James | Completed | Load_252604 | Bogue - 610 | Jul 29, 2026 3:40pm | Jul 29, 2026 4:23pm | Jul 29, 2026 5:30pm | Jul 29, 2026 5:30pm | Jul 29, 2026 6:47pm | Jul 29, 2026 7:30pm | Jul 29, 2026 7:38pm | Jul 29, 2026 7:38pm |  |  | Fair | No | Isolated (1)15KVA transformer repair transformer switch bottom
Outage | J.E.26.07.36378 | C001869047 | Richman Whyte | Westmoreland | Completed | Load_245618 | Paradise - 310 | Jul 29, 2026 3:37pm | Jul 29, 2026 9:35pm | Jul 29, 2026 10:30pm | Jul 29, 2026 10:30pm | Jul 29, 2026 10:30pm | Jul 29, 2026 10:31pm | Jul 29, 2026 10:32pm | Jul 29, 2026 10:32pm |  |  | Fair | Yes | Customer required connection after hurricane need daylight attention
Outage | J.E.26.07.36808 | C001869045 | Fitzroy Turner | KSAN | Completed | Load_265571 | West Kings House - 310 | Jul 29, 2026 3:36pm | Jul 29, 2026 3:38pm | Jul 29, 2026 5:58pm | Jul 29, 2026 5:58pm | Jul 29, 2026 5:59pm | Jul 29, 2026 6:02pm | Jul 29, 2026 6:04pm | Jul 29, 2026 6:04pm |  |  | Fair | No | Supply restored after replace defective drop out switch at the intersection of Marcus Garvey drive and bell rd
Outage | J.E.26.07.37132 | C001869044 | Kaydon Taylor | KSAN | Completed | Load_244070 | Constant Spring - 210 | Jul 29, 2026 3:36pm | Jul 29, 2026 3:38pm | Jul 29, 2026 8:33pm | Jul 29, 2026 8:33pm | Jul 29, 2026 8:56pm | Jul 29, 2026 8:58pm | Jul 29, 2026 8:58pm | Jul 29, 2026 8:58pm | LeaningPole |  | Fair | No | Several attempts calling the customer no answer
Outage | J.E.26.07.36385 | C001869043 | Kaydon Taylor | KSAS | Completed | Load_267072 | Duhaney - 310 | Jul 29, 2026 3:35pm | Jul 29, 2026 3:38pm | Jul 29, 2026 5:25pm | Jul 29, 2026 5:25pm | Jul 29, 2026 5:26pm | Jul 29, 2026 1:00am | Jul 29, 2026 5:27pm | Jul 29, 2026 5:27pm |  |  | Fair | No | Found okay
Outage | J.E.26.07.37101 | C001869042 | Kaydon Taylor | KSAN | Completed | Load_253397 | Constant Spring - 210 | Jul 29, 2026 3:35pm | Jul 29, 2026 3:38pm | Jul 29, 2026 9:03pm | Jul 29, 2026 9:03pm | Jul 29, 2026 9:57pm | Jul 29, 2026 10:43pm | Jul 29, 2026 10:43pm | Jul 29, 2026 10:43pm | Fire | Y | Fair | No | Secondary bushings requires preferably in the morning period
Outage | J.E.26.07.37229 | C001869040 | Kaydon Taylor | KSAN | Completed | Load_260500 | Constant Spring - 210 | Jul 29, 2026 3:35pm | Jul 29, 2026 3:38pm | Jul 29, 2026 5:35pm | Jul 29, 2026 5:35pm | Jul 29, 2026 7:11pm | Jul 29, 2026 8:33pm | Jul 29, 2026 8:33pm | Jul 29, 2026 8:33pm |  |  | Fair | No | Customer is disconnected
Outage | J.E.26.07.37238 | C001869041 | Elvis Trowers | KSAS | Completed | Load_238539 | Duhaney - 310 | Jul 29, 2026 3:35pm | Jul 30, 2026 7:33am | Jul 30, 2026 11:34am | Jul 30, 2026 11:34am | Jul 30, 2026 12:08pm | Jul 30, 2026 12:19pm | Jul 30, 2026 12:19pm | Jul 30, 2026 12:19pm | TreeContact | Y | Fair | Yes | Major secondary bushings that is required for this location, trees are growing up into secondary lines.
Outage | J.E.26.07.36465 | C001869028 | Raymond Carr | St.Mary | Completed | Load_260418 | Oracabessa - 110 | Jul 29, 2026 3:27pm | Jul 29, 2026 3:28pm | Jul 29, 2026 3:44pm | Jul 29, 2026 3:44pm | Jul 29, 2026 4:07pm | Jul 29, 2026 3:48pm | Jul 29, 2026 4:08pm | Jul 29, 2026 4:08pm |  |  | Fair | No | Customer reported that supply was restored.
Outage | J.E.26.07.36548 | C001869029 | Raymond Carr | St.Mary | Completed | Load_256987 | Oracabessa - 110 | Jul 29, 2026 3:27pm | Jul 29, 2026 3:28pm | Jul 29, 2026 4:08pm | Jul 29, 2026 4:09pm | Jul 29, 2026 4:42pm | Jul 29, 2026 4:31pm | Jul 29, 2026 4:43pm | Jul 29, 2026 4:43pm |  |  | Fair | No | Supply was restored.
Outage | J.E.26.07.37231 | C001869026 | Edward Royal | KSAN | Completed | Load_244711 | Washington Blvd - 710 | Jul 29, 2026 3:24pm | Jul 29, 2026 3:33pm | Jul 29, 2026 4:21pm | Jul 29, 2026 4:21pm | Jul 29, 2026 4:26pm | Jul 29, 2026 4:32pm | Jul 29, 2026 4:32pm | Jul 29, 2026 4:32pm | BrokenWire |  | Fair | No | Customer have internal problems advice customer to get a electrician to fix the pothead before power can be restored
Outage | J.E.26.07.36944 | C001869024 | Tyrese Williams | St.Ann | Completed | Load_242202 | Cardiff Hall - 310 | Jul 29, 2026 3:23pm | Jul 29, 2026 3:25pm | Jul 29, 2026 3:40pm | Jul 29, 2026 6:16pm | Jul 29, 2026 8:03pm | Jul 29, 2026 8:05pm | Jul 29, 2026 8:05pm | Jul 29, 2026 8:05pm |  |  | Fair | No | Remade service wire joint at pole use 1 pg clamp unable to capture voltage due to power outage in area
Outage | J.E.26.07.37230 | C001869025 | Tyrese Williams | St.Ann | Completed | Load_238811 | Cardiff Hall - 310 | Jul 29, 2026 3:23pm | Jul 29, 2026 3:25pm | Jul 29, 2026 3:34pm | Jul 29, 2026 4:12pm | Jul 29, 2026 5:59pm | Jul 29, 2026 6:16pm | Jul 29, 2026 6:16pm | Jul 29, 2026 6:16pm |  |  | Fair | No | Refer to field service team customer meter in hexing box
Non-Outage | J.E.26.07.36581 | C001869020 | Edward Royal | null | Completed | null | null | Jul 29, 2026 3:21pm | Jul 29, 2026 3:31pm | Jul 29, 2026 4:05pm | Jul 29, 2026 4:05pm | Jul 29, 2026 4:10pm | Jul 29, 2026 4:12pm | Jul 29, 2026 4:13pm | Jul 29, 2026 4:13pm |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.07.36813 | C001869018 | Edward Royal | null | Completed | null | null | Jul 29, 2026 3:21pm | Jul 29, 2026 3:31pm | Jul 29, 2026 4:13pm | Jul 29, 2026 4:13pm | Jul 29, 2026 4:19pm | Jul 29, 2026 4:20pm | Jul 29, 2026 4:20pm | Jul 29, 2026 4:20pm |  |  | Fair | No | Yp box was on fire need to be change reffered to field service
Non-Outage | J.E.26.07.36831 | C001869017 | Edward Royal | null | Completed | null | null | Jul 29, 2026 3:21pm | Jul 29, 2026 3:31pm | Jul 29, 2026 3:36pm | Jul 29, 2026 3:36pm | Jul 29, 2026 3:36pm | Jul 29, 2026 3:36pm | Jul 29, 2026 3:36pm | Jul 29, 2026 3:36pm |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.07.36811 | C001869019 | Fitzroy Turner | KSAS | Completed | Load_269999 | Three Miles - 510 | Jul 29, 2026 3:21pm | Jul 29, 2026 3:42pm | Jul 29, 2026 5:53pm | Jul 29, 2026 5:54pm | Jul 29, 2026 5:54pm | Jul 29, 2026 5:54pm | Jul 29, 2026 5:56pm | Jul 29, 2026 5:56pm |  |  | Fair | No | Found defective drop out switch at the intersection of bell road and Marcus Garvey drive have one switch change and close up line supply restored to the area
Non-Outage | J.E.26.07.37127 | C001869015 | Edward Royal | null | Completed | null | null | Jul 29, 2026 3:20pm | Jul 29, 2026 3:31pm | Jul 29, 2026 4:04pm | Jul 29, 2026 4:04pm | Jul 29, 2026 4:04pm | Jul 29, 2026 4:05pm | Jul 29, 2026 4:05pm | Jul 29, 2026 4:05pm | Fire |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.07.37194 | C001869014 | Milton Charlton | null | Completed | null | null | Jul 29, 2026 3:20pm | Jul 29, 2026 3:43pm | Jul 29, 2026 4:44pm | Jul 29, 2026 4:44pm | Jul 29, 2026 7:09pm | Jul 29, 2026 7:10pm | Jul 29, 2026 7:13pm | Jul 29, 2026 7:13pm | Fire |  | Fair | No | Open wire secondary phase and neutral come intact and cause transformer to blow 3 amps fuse at pole #( no pole #) . Entangle both wires and add spacers and reclosed 3 amps transformer switch .
Outage | J.E.26.07.36857 | C001869016 | Fitzroy Turner | KSAS | Completed | Load_257326 | Cane River - 610 | Jul 29, 2026 3:20pm | Jul 29, 2026 3:44pm | Jul 29, 2026 6:38pm | Jul 29, 2026 6:38pm | Jul 29, 2026 6:41pm | Jul 29, 2026 6:41pm | Jul 29, 2026 6:42pm | Jul 29, 2026 6:42pm |  |  | Fair | Yes | Customer premises found with electricity supply
Outage | J.E.26.07.37007 | C001869010 | Romeo Brissett | St.James | Completed | Load_302249 | Bogue - 510 | Jul 29, 2026 3:14pm | Jul 29, 2026 3:14pm | Jul 29, 2026 5:17pm | Jul 29, 2026 5:17pm | Jul 29, 2026 5:20pm | Jul 29, 2026 5:20pm | Jul 29, 2026 5:21pm | Jul 29, 2026 5:21pm |  |  | Fair | No | Check and found ok
Outage | J.E.26.07.37037 | C001869007 | Romeo Brissett | St.James | Completed | Load_266148 | Bogue - 510 | Jul 29, 2026 3:13pm | Jul 29, 2026 3:14pm | Jul 29, 2026 3:17pm | Jul 29, 2026 3:17pm | Jul 29, 2026 3:52pm | Jul 29, 2026 4:24pm | Jul 29, 2026 4:40pm | Jul 29, 2026 4:40pm |  |  | Fair | No | Cut and removed vegetation, replaced (1)15amps junction fuse
Outage | J.E.26.07.37108 | C001869008 | Romeo Brissett | St.James | Completed | Load_240574 | Bogue - 510 | Jul 29, 2026 3:13pm | Jul 29, 2026 3:14pm | Jul 29, 2026 4:40pm | Jul 29, 2026 4:40pm | Jul 29, 2026 4:40pm | Jul 29, 2026 5:13pm | Jul 29, 2026 5:17pm | Jul 29, 2026 5:17pm |  |  | Fair | No | Removed vegetation and replaced (1)25 kva transformer fuse line need bushing and maintenance.
Outage | J.E.26.07.37147 | C001869009 | Romeo Brissett | Hanover | Completed | Load_245538 | Orange Bay - 310 | Jul 29, 2026 3:13pm | Jul 29, 2026 4:59pm | Jul 29, 2026 5:25pm | Jul 29, 2026 5:25pm | Jul 29, 2026 5:25pm | Jul 29, 2026 5:29pm | Jul 29, 2026 5:29pm | Jul 29, 2026 5:29pm | LeaningPole |  | Fair | No | Hanover call
Non-Outage | J.E.26.07.37138 | C001869004 | Javid Vernon | null | Completed | null | null | Jul 29, 2026 3:12pm | Jul 29, 2026 3:13pm | Jul 29, 2026 6:07pm | Jul 29, 2026 6:07pm | Jul 29, 2026 7:08pm | Jul 29, 2026 8:42pm | Jul 29, 2026 8:42pm | Jul 29, 2026 8:42pm | BrokenWire |  | Fair | No | Isolate one 25 kva transformer to splice and retention one pole span of secondary phase and neutral use 30ft #2 conductor and 4 clamp and reclose 25kva transformer voltage reading 116/117/234
Outage | J.E.26.07.36972 | C001869002 | Javid Vernon | Westmoreland | Completed | Load_259036 | Paradise - 210 | Jul 29, 2026 3:12pm | Jul 29, 2026 3:13pm | Jul 29, 2026 8:43pm | Jul 29, 2026 8:43pm | Jul 29, 2026 10:06pm | Jul 29, 2026 10:25pm | Jul 29, 2026 10:25pm | Jul 29, 2026 10:25pm |  |  | Fair | No | Premises check and found okay voltage reading 113/115/228 customer meter found defective needs to be replaced urgently refer to field service
Outage | J.E.26.07.37098 | C001869003 | Javid Vernon | Westmoreland | Completed | Load_248839 | Paradise - 210 | Jul 29, 2026 3:12pm | Jul 29, 2026 3:13pm | Jul 29, 2026 10:26pm | Jul 29, 2026 10:26pm | Jul 29, 2026 10:26pm | Jul 29, 2026 10:29pm | Jul 29, 2026 10:29pm | Jul 29, 2026 10:29pm |  |  | Fair | No | Customer stated that the power was restored
Outage | J.E.26.07.36740 | C001869000 | Javid Vernon | Westmoreland | Completed | Load_251045 | Paradise - 210 | Jul 29, 2026 3:11pm | Jul 29, 2026 3:13pm | Jul 29, 2026 3:40pm | Jul 29, 2026 3:40pm | Jul 29, 2026 4:04pm | Jul 29, 2026 4:14pm | Jul 29, 2026 4:15pm | Jul 29, 2026 4:15pm |  |  | Fair | No | Premises found okay voltage reading 115/115/230 customer got disconnected for none payments
Outage | J.E.26.07.36775 | C001868998 | Rayon Foster | Hanover | Completed | Load_242544 | Orange Bay - 310 | Jul 29, 2026 3:11pm | Jul 29, 2026 3:12pm | Jul 29, 2026 10:09pm | Jul 29, 2026 10:09pm | Jul 29, 2026 10:09pm | Jul 29, 2026 10:12pm | Jul 29, 2026 10:35pm | Jul 29, 2026 10:35pm |  |  | Fair | No | When spoke customers they requested that for technicians to return in the morning gates to the premises are currently closed resend to technicians tomorrow morning
Outage | J.E.26.07.36888 | C001869001 | Michael Paterson | Westmoreland | Completed | Load_245695 | Paradise - 210 | Jul 29, 2026 3:11pm | Jul 30, 2026 9:56am | Jul 30, 2026 11:14am | Jul 30, 2026 11:15am | Jul 30, 2026 12:00pm | Jul 30, 2026 12:01pm | Jul 30, 2026 12:05pm | Jul 30, 2026 12:05pm |  |  | Fair | No | Customer confirm ok via phone call
Outage | J.E.26.07.37195 | C001868999 | Javid Vernon | Westmoreland | Completed | Load_239491 | Paradise - 110 | Jul 29, 2026 3:11pm | Jul 29, 2026 3:13pm | Jul 29, 2026 4:16pm | Jul 29, 2026 4:16pm | Jul 29, 2026 5:29pm | Jul 29, 2026 5:51pm | Jul 29, 2026 6:04pm | Jul 29, 2026 6:04pm | Fire |  | Fair | No | Check and found customer meter and service wire defective needs to be replaced customer needs urgent assistance refer to field service
Non-Outage | J.E.26.07.36829 | C001868988 | Neville Spencer | Clarendon | Completed | Load_241326 | May Pen - 110 | Jul 29, 2026 3:07pm | Jul 29, 2026 3:07pm | Jul 29, 2026 6:04pm | Jul 29, 2026 6:04pm | Jul 29, 2026 7:11pm | Jul 29, 2026 7:11pm | Jul 29, 2026 7:12pm | Jul 29, 2026 7:12pm |  |  | Fair | No | Unable to locate customer.
Non-Outage | J.E.26.07.37089 | C001868987 | Rayon Foster | null | Completed | null | null | Jul 29, 2026 3:06pm | Jul 29, 2026 3:12pm | Jul 29, 2026 4:39pm | Jul 29, 2026 4:39pm | Jul 29, 2026 4:40pm | Jul 29, 2026 5:17pm | Jul 29, 2026 5:26pm | Jul 29, 2026 5:26pm |  |  | Rains | No | Blow 100 kva transformer fuse remove fuse holder patrol secondary line line was clear replace with 10 amps fuse after patrolling secondary line and close
Outage | J.E.26.07.37146 | C001868986 | Rayon Foster | Hanover | Completed | Load_256907 | Orange Bay - 310 | Jul 29, 2026 3:06pm | Jul 29, 2026 3:12pm | Jul 29, 2026 3:53pm | Jul 29, 2026 3:53pm | Jul 29, 2026 3:53pm | Jul 29, 2026 4:12pm | Jul 29, 2026 4:14pm | Jul 29, 2026 4:14pm |  |  | Rains | No | Leaking 25 kva transformer 25kva transformer feeding over 39 customers recommending transformer change and up grade to a 50 kva ergently
Outage | J.E.26.07.37149 | C001868984 | Richman Whyte | Westmoreland | Completed | Load_256660 | Paradise - 310 | Jul 29, 2026 3:05pm | Jul 29, 2026 3:33pm | Jul 29, 2026 3:44pm | Jul 29, 2026 3:44pm | Jul 29, 2026 3:44pm | Jul 29, 2026 3:46pm | Jul 29, 2026 3:46pm | Jul 29, 2026 3:46pm |  |  | Fair | No | 35 class #6 wood pole with primary and secondary D V construction broken down need to replace 10amp junction fuse out as well
Outage | J.E.26.07.36907 | C001868974 | Selvin White | St.Elizabeth | Completed | Load_292979 | Maggotty - 110 | Jul 29, 2026 2:43pm | Jul 29, 2026 2:43pm | Jul 29, 2026 4:00pm | Jul 29, 2026 4:00pm | Jul 29, 2026 4:11pm | Jul 29, 2026 4:16pm | Jul 29, 2026 4:16pm | Jul 29, 2026 4:16pm |  |  | Fair | No | Replace a blown 15 amp junction fuse at Luana Housing Scheme after patrolling 2 phase primary line. Supply restored to the affected customers.
Non-Outage | J.E.26.07.32882 | C001868968 | Moses Elliston | Portmore | Completed | Load_557242 | Naggo Head - 510 | Jul 29, 2026 2:39pm | Jul 30, 2026 8:11am | Jul 30, 2026 12:49pm | Jul 30, 2026 12:49pm | Jul 30, 2026 12:49pm | Jul 30, 2026 12:49pm | Jul 30, 2026 12:54pm | Jul 30, 2026 12:54pm |  |  | Fair | No | Burnt 3 wire service phase at pole repaired with 1 linket .116-116-232 volts.
Outage | J.E.26.07.33401 | C001868963 | Eric Williams | KSAN | Completed | Load_259753 | Constant Spring - 410 | Jul 29, 2026 2:31pm | Jul 29, 2026 2:31pm | Jul 29, 2026 5:37pm | Jul 29, 2026 5:37pm | Jul 29, 2026 5:56pm | Jul 29, 2026 6:56pm | Jul 29, 2026 7:49pm | Jul 29, 2026 7:49pm |  |  | Fair | No | Defective 25kva transformer found and replaced and also blown 3 amp found and replaced
Outage | J.E.26.07.37156 | C001868950 | Denton Williams | Portland | Completed | Load_352469 | Port Antonio - 410 | Jul 29, 2026 2:19pm | Jul 29, 2026 3:39pm | Jul 29, 2026 3:43pm | Jul 29, 2026 3:43pm | Jul 29, 2026 5:04pm | Jul 29, 2026 5:11pm | Jul 29, 2026 5:11pm | Jul 29, 2026 5:11pm | Fire |  | Fair | No | Visited location and we didn’t observe any fire or notice anything abnormal. Customer okay.
Outage | J.E.26.07.36519 | C001868944 | Cliton Henry | St.Mary | Completed | Load_349590 | Oracabessa - 110 | Jul 29, 2026 2:10pm | Jul 29, 2026 2:10pm | Jul 29, 2026 2:22pm | Jul 29, 2026 2:22pm | Jul 29, 2026 2:33pm | Jul 29, 2026 2:36pm | Jul 29, 2026 2:37pm | Jul 29, 2026 2:37pm |  |  | Fair | No | This reported outage in Galina is part of a planned outage confirm by Morando McKenzie Operations Manager.
Non-Outage | J.E.26.07.37112 | C001868939 | Damion Reid | null | Completed | null | null | Jul 29, 2026 2:07pm | Jul 29, 2026 3:43pm | Jul 29, 2026 6:08pm | Jul 29, 2026 6:08pm | Jul 29, 2026 7:19pm | Jul 29, 2026 8:02pm | Jul 29, 2026 8:03pm | Jul 29, 2026 8:03pm | BrokenWire |  | Fair | No | Blown 20amp junction fuse found cause by vehicle accident line patrol and replace blown fuse
Outage | J.E.26.07.37085 | C001868937 | Neville Spencer | St.Ann | Completed | Load_256510 | Cardiff Hall - 210 | Jul 29, 2026 2:05pm | Jul 29, 2026 3:20pm | Jul 29, 2026 7:17pm | Jul 29, 2026 7:17pm | Jul 29, 2026 7:17pm | Jul 29, 2026 7:17pm | Jul 29, 2026 7:17pm | Jul 29, 2026 7:17pm | BrokenWire |  | Fair | No | Call belong to ST Ann’s.
Non-Outage | J.E.26.07.37049 | C001868919 | Ryan Richards | null | Completed | null | null | Jul 29, 2026 1:53pm | Jul 29, 2026 3:48pm | Jul 29, 2026 7:15pm | Jul 29, 2026 7:15pm | Jul 29, 2026 8:55pm | Jul 29, 2026 9:44pm | Jul 29, 2026 9:44pm | Jul 29, 2026 9:44pm |  |  | Fair | No | Burn up customer service entry found customer as been advised to carry out repair
Outage | J.E.26.07.36959 | C001868893 | Hartley Chin | Clarendon | Completed | Load_572086 | Parnassus - 310 | Jul 29, 2026 1:19pm | Jul 29, 2026 1:25pm | Jul 29, 2026 1:37pm | Jul 29, 2026 1:37pm | Jul 29, 2026 1:48pm | Jul 29, 2026 2:21pm | Jul 29, 2026 2:27pm | Jul 29, 2026 2:27pm |  |  | Fair | No | Found blown 30 AMP junction fuse at pole # 0183780. Line patrolled and refused.
Non-Outage | J.E.26.07.37045 | C001868892 | Swon Miller | null | Completed | null | null | Jul 29, 2026 1:18pm | Jul 29, 2026 3:23pm | Jul 29, 2026 4:19pm | Jul 29, 2026 4:19pm | Jul 29, 2026 4:20pm | Jul 29, 2026 4:28am | Jul 29, 2026 4:32pm | Jul 29, 2026 4:32pm | BrokenWire |  | Fair | No | Found two customers service wires broken cause by truck voltage found 0.000 advise customer to repair stanchion before repairs can be carried out voltage left 0.000
Outage | J.E.26.07.37034 | C001868884 | Derrick Dawkins | St.James | Completed | Load_257601 | Bogue - 610 | Jul 29, 2026 1:14pm | Jul 29, 2026 1:14pm | Jul 29, 2026 1:41pm | Jul 29, 2026 1:41pm | Jul 29, 2026 1:42pm | Jul 29, 2026 1:42pm | Jul 29, 2026 1:43pm | Jul 29, 2026 1:43pm |  |  | Fair | No | Checked and found ok, customer stated light is restored
Outage | J.E.26.07.36855 | C001868876 | Milton Charlton | KSAS | Completed | Load_239182 | Up Park Camp - 410 | Jul 29, 2026 1:10pm | Jul 29, 2026 1:11pm | Jul 29, 2026 4:06pm | Jul 29, 2026 4:06pm | Jul 29, 2026 4:34pm | Jul 29, 2026 4:35pm | Jul 29, 2026 4:44pm | Jul 29, 2026 4:44pm | LowHangingWires |  | Fair | No | 30ft wooden pole at the corner of Seymour Ave and Upper Montrose Road. Pole broken in motor vehicle accident posting treat to large vehicle. Pole has on open wire secondary on 8ft crossarm on the next pole 5ft crossarm whit 3- wire secondary broken also. Need immediate attention.
Outage | J.E.26.07.36940 | C001868869 | Damion Reid | Manchester | Completed | Load_248693 | Kendal - 210 | Jul 29, 2026 1:03pm | Jul 29, 2026 3:43pm | Jul 29, 2026 8:04pm | Jul 29, 2026 8:04pm | Jul 29, 2026 8:45pm | Jul 29, 2026 9:11pm | Jul 29, 2026 9:13pm | Jul 29, 2026 9:13pm |  |  | Fair | No | Call related to one done at belcarries earlier
Outage | J.E.26.07.36984 | C001868865 | Marlon Brown | Trelawny | Completed | Load_250805 | Greenwood - 110 | Jul 29, 2026 1:00pm | Jul 29, 2026 3:18pm | Jul 29, 2026 3:34pm | Jul 29, 2026 3:34pm | Jul 29, 2026 4:31pm | Jul 29, 2026 5:12pm | Jul 29, 2026 5:12pm | Jul 29, 2026 5:12pm | BrokenWire |  | Fair | No | 100ft #6 triplex 2 pg clamps and 2 linkers Voltage found noneVoltage leaving at pothead 114v. Hurricane Melissa damage service wire, no service wire seen at premises b
Non-Outage | J.E.26.07.27938 | C001868856 | Odaine Johnson | Clarendon | Completed | Load_264303 | Parnassus - 310 | Jul 29, 2026 12:54pm | Jul 29, 2026 12:55pm | Jul 29, 2026 2:21pm | Jul 29, 2026 2:21pm | Jul 29, 2026 2:32pm | Jul 29, 2026 2:32pm | Jul 29, 2026 2:33pm | Jul 29, 2026 2:33pm |  |  | Fair | No | Premises found okay
Non-Outage | J.E.26.07.29795 | C001868855 | Odaine Johnson | Clarendon | Completed | Load_257464 | Parnassus - 310 | Jul 29, 2026 12:54pm | Jul 29, 2026 12:55pm | Jul 29, 2026 2:33pm | Jul 29, 2026 2:33pm | Jul 30, 2026 9:30am | Jul 30, 2026 9:31am | Jul 30, 2026 9:31am | Jul 30, 2026 9:31am |  |  | Fair | No | Premises found okay
Non-Outage | J.E.26.07.30325 | C001868854 | Odaine Johnson | Clarendon | Completed | Load_256822 | Parnassus - 310 | Jul 29, 2026 12:54pm | Jul 29, 2026 12:55pm | Jul 30, 2026 9:32am | Jul 30, 2026 9:32am | Jul 30, 2026 9:35am | Jul 30, 2026 9:35am | Jul 30, 2026 9:35am | Jul 30, 2026 9:35am |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.36557 | C001868767 | Jowayne Newmans | Portland | Completed | Load_268045 | Port Antonio - 410 | Jul 29, 2026 12:36pm | Jul 29, 2026 12:37pm | Jul 29, 2026 1:06pm | Jul 29, 2026 1:06pm | Jul 29, 2026 1:58pm | Jul 29, 2026 2:12pm | Jul 29, 2026 2:12pm | Jul 29, 2026 2:12pm |  |  | Fair | No | Customer stated that they were without supply however did a voltage test at meter socket voltage reading was 116v, 118v, 234v. Advise customer to get an electrician to check their system.
Outage | J.E.26.07.36450 | C001868745 | Kenroy Dale | Manchester | Completed | Load_263292 | Kendal - 210 | Jul 29, 2026 12:21pm | Jul 29, 2026 12:21pm | Jul 29, 2026 12:35pm | Jul 29, 2026 12:39pm | Jul 29, 2026 12:49pm | Jul 29, 2026 12:50pm | Jul 29, 2026 12:57pm | Jul 29, 2026 12:57pm |  |  | Fair | No | Customer requesting barrel lock to remove from meter socket, in order to carry out repairs to defective meter socket (field service required)
Outage | J.E.26.07.36678 | C001868738 | Michael Christian | St.James | Completed | Load_254901 | Queens Drive - 810 | Jul 29, 2026 12:17pm | Jul 29, 2026 12:19pm | Jul 29, 2026 12:27pm | Jul 29, 2026 12:27pm | Jul 29, 2026 12:29pm | Jul 29, 2026 12:40pm | Jul 29, 2026 12:40pm | Jul 29, 2026 12:40pm |  |  | Fair | No | Check and found outage
Non-Outage | J.E.26.07.36842 | C001868737 | Rusean Allen | KSAS | Completed | Load_239977 | Up Park Camp - 510 | Jul 29, 2026 12:15pm | Jul 29, 2026 12:16pm | Jul 29, 2026 12:25pm | Jul 29, 2026 12:31pm | Jul 29, 2026 1:25pm | Jul 29, 2026 2:13pm | Jul 29, 2026 2:14pm | Jul 29, 2026 2:14pm |  |  | Fair | No | Defective service wire found .120ft #6 service wire was disconnected and reinstalled.
Outage | J.E.26.07.36755 | C001868736 | Derrick Dawkins | St.James | Completed | Load_262825 | Bogue - 610 | Jul 29, 2026 12:13pm | Jul 29, 2026 12:14pm | Jul 29, 2026 2:10pm | Jul 29, 2026 2:10pm | Jul 29, 2026 2:20pm | Jul 29, 2026 2:28pm | Jul 29, 2026 2:29pm | Jul 29, 2026 2:29pm |  |  | Fair | No | Checked and found ok
Outage | J.E.26.07.36814 | C001868730 | Derrick Dawkins | St.James | Completed | Load_260918 | Bogue - 610 | Jul 29, 2026 12:13pm | Jul 29, 2026 12:13pm | Jul 29, 2026 1:45pm | Jul 29, 2026 1:45pm | Jul 29, 2026 2:04pm | Jul 29, 2026 2:05pm | Jul 29, 2026 2:06pm | Jul 29, 2026 2:06pm |  |  | Fair | No | Calls to customer went unanswered cannot locate premises
Outage | J.E.26.07.36834 | C001868729 | Horace Malcolm | St.James | Completed | Load_270234 | Queens Drive - 710 | Jul 29, 2026 12:12pm | Jul 29, 2026 12:12pm | Jul 29, 2026 1:35pm | Jul 29, 2026 1:35pm | Jul 29, 2026 2:14pm | Jul 29, 2026 2:46pm | Jul 29, 2026 2:46pm | Jul 29, 2026 2:46pm | BrokenWire |  | Fair | No | Splice customer service wire nuetral used 10ft #6 triplex wire and two clamps voltage 113-115-228
Outage | J.E.26.07.36752 | C001868719 | Wan Carlos Scarlett | St.Catherine | Completed | Load_259973 | Twickenham - 210 | Jul 29, 2026 12:06pm | Jul 29, 2026 12:07pm | Jul 29, 2026 3:46pm | Jul 29, 2026 3:46pm | Jul 29, 2026 4:17pm | Jul 29, 2026 4:20pm | Jul 29, 2026 4:21pm | Jul 29, 2026 4:21pm |  |  | Fair | No | Found customer with internal problem advised customer to get a licensed electrician to fix the problem.customer breaker defective
Outage | J.E.26.07.36807 | C001868718 | Moses Elliston | KSAS | Completed | Load_1000996 | Duhaney - 210 | Jul 29, 2026 12:06pm | Jul 29, 2026 12:07pm | Jul 29, 2026 2:13pm | Jul 29, 2026 2:13pm | Jul 29, 2026 2:13pm | Jul 29, 2026 2:13pm | Jul 29, 2026 2:17pm | Jul 29, 2026 2:17pm |  |  | Fair | No | Defective collector # 17473731,box # 2832 to be change.Customer without supply.Refer to Paulstan Francis
Non-Outage | J.E.26.07.35320 | C001868716 | Donald Cunningham | null | Completed | null | null | Jul 29, 2026 12:03pm | Jul 29, 2026 12:05pm | Jul 29, 2026 12:35pm | Jul 29, 2026 12:35pm | Jul 29, 2026 1:30pm | Jul 29, 2026 1:31pm | Jul 29, 2026 1:36pm | Jul 29, 2026 1:36pm |  |  | Fair | No | Need more directions customer reachable
Non-Outage | J.E.26.07.36676 | C001868714 | Moses Elliston | null | Completed | null | null | Jul 29, 2026 12:03pm | Jul 29, 2026 12:04pm | Jul 29, 2026 1:37pm | Jul 29, 2026 1:37pm | Jul 29, 2026 1:37pm | Jul 29, 2026 1:17pm | Jul 29, 2026 1:38pm | Jul 29, 2026 1:38pm |  |  | Fair | No | Credit added to prepaid account
Outage | J.E.26.07.33799 | C001868717 | Nickolas Rodriques | St.Catherine | Completed | Load_262226 | Tredegar - 210 | Jul 29, 2026 12:03pm | Jul 29, 2026 12:04pm | Jul 29, 2026 1:48pm | Jul 29, 2026 1:57pm | Jul 29, 2026 2:42pm | Jul 29, 2026 2:57pm | Jul 29, 2026 2:57pm | Jul 29, 2026 2:57pm |  |  | Fair | No | Found customer with electricity. The customer stated that she did not make any report and she is not having any issues with her power supply.
Outage | J.E.26.07.36566 | C001868715 | Nickolas Rodriques | St.Catherine | Completed | Load_262771 | Tredegar - 310 | Jul 29, 2026 12:03pm | Jul 29, 2026 12:04pm | Jul 29, 2026 12:22pm | Jul 29, 2026 12:24pm | Jul 29, 2026 1:17pm | Jul 29, 2026 1:23pm | Jul 29, 2026 1:48pm | Jul 29, 2026 1:48pm |  |  | Fair | No | Customer was located and confirmed that the area outage was restored.
Outage | J.E.26.07.36808 | C001868708 | Milton Charlton | KSAN | Completed | Load_265571 | West Kings House - 310 | Jul 29, 2026 12:00pm | Jul 29, 2026 12:01pm | Jul 29, 2026 1:05pm | Jul 29, 2026 1:05pm | Jul 29, 2026 3:08pm | Jul 29, 2026 2:30pm | Jul 29, 2026 3:15pm | Jul 29, 2026 3:15pm |  |  | Fair | No | Corner of Bell road and Marcus Garvey Drive defective switch on 40ft concrete pole #( no pole#) fed from main line three phase primary middle switch defective.. Need immediate attention customer out of supply mostly factory.
Outage | J.E.26.07.36771 | C001868702 | Michael Christian | St.James | Completed | Load_556952 | Bogue - 310 | Jul 29, 2026 11:57am | Jul 29, 2026 11:57am | Jul 29, 2026 12:48pm | Jul 29, 2026 12:48pm | Jul 29, 2026 1:17pm | Jul 29, 2026 1:26pm | Jul 29, 2026 1:26pm | Jul 29, 2026 1:26pm | LowHangingWires |  | Fair | No | Need 1 30 ft pole for secondary life
Non-Outage | J.E.26.07.36725 | C001868701 | Wan Carlos Scarlett | Portmore | Completed | Load_257303 | Naggo Head - 510 | Jul 29, 2026 11:54am | Jul 29, 2026 11:54am | Jul 29, 2026 12:39pm | Jul 29, 2026 12:39pm | Jul 29, 2026 1:00pm | Jul 29, 2026 1:07pm | Jul 29, 2026 1:27pm | Jul 29, 2026 1:27pm |  |  | Fair | No | Found 50KVA transformer X1 lug burn out and found transformer casing ground to neutral burn off 50KVA transformer supplying HEXING service box HEXIN 04218 pole 0028037 transformer single phase going in and out voltage and high voltage because of the transformer casing ground burn off also
Outage | J.E.26.07.36583 | C001868700 | Derrick Dawkins | St.James | Completed | Load_257601 | Bogue - 610 | Jul 29, 2026 11:53am | Jul 29, 2026 12:00pm | Jul 29, 2026 12:15pm | Jul 29, 2026 12:16pm | Jul 29, 2026 12:44pm | Jul 29, 2026 1:40pm | Jul 29, 2026 1:40pm | Jul 29, 2026 1:40pm | BrokenWire |  | Fair | No | Found 1 span secondary phase burn down due to vegetation open a 50 kva transformer to carry out repairs removed vegetation splice and retention used 2 pg clam
Outage | J.E.26.07.36754 | C001868683 | Neville Spencer | Clarendon | Completed | Load_254385 | May Pen - 110 | Jul 29, 2026 11:44am | Jul 29, 2026 3:07pm | Jul 29, 2026 3:22pm | Jul 29, 2026 3:22pm | Jul 29, 2026 5:31pm | Jul 29, 2026 5:31pm | Jul 29, 2026 6:03pm | Jul 29, 2026 6:03pm |  |  | Fair | Yes | Remade burnt off netural in meter socket voltage reading 116 supply restored.
Outage | J.E.26.07.36746 | C001868671 | Barnett Brown | Manchester | Completed | Load_256152 | Spur Tree - 310 | Jul 29, 2026 11:42am | Jul 29, 2026 11:43am | Jul 30, 2026 10:56am | Jul 30, 2026 1:50pm | Jul 30, 2026 1:51pm | Jul 30, 2026 1:56pm | Jul 30, 2026 1:57pm | Jul 30, 2026 1:57pm |  |  | Fair | No | Balance 1 span secondary line
Outage | J.E.26.07.36747 | C001868672 | Barnett Brown | Manchester | Completed | Load_1002521 | Kendal - 310 | Jul 29, 2026 11:42am | Jul 29, 2026 11:43am | Jul 29, 2026 12:13pm | Jul 29, 2026 12:13pm | Jul 29, 2026 12:52pm | Jul 29, 2026 1:05pm | Jul 29, 2026 1:27pm | Jul 29, 2026 1:27pm |  |  | Fair | No | Remade joint at secondary jumper
Outage | J.E.26.07.36526 | C001868669 | Christopher Edwards | KSAN | Completed | Load_292076 | Constant Spring - 310 | Jul 29, 2026 11:39am | Jul 29, 2026 11:50am | Jul 29, 2026 12:28pm | Jul 29, 2026 12:34pm | Jul 29, 2026 12:34pm | Jul 29, 2026 1:33pm | Jul 29, 2026 1:35pm | Jul 29, 2026 1:35pm |  |  | Fair | No | Refuse blown junction fuseUsing (1) 20 ampsAlso clear vegetation off primary line
Outage | J.E.26.07.34760 | C001868661 | Elvis Trowers | KSAN | Completed | Load_244977 | Constant Spring - 210 | Jul 29, 2026 11:36am | Jul 29, 2026 11:40am | Jul 29, 2026 3:17pm | Jul 29, 2026 3:17pm | Jul 29, 2026 3:17pm | Jul 29, 2026 3:20pm | Jul 29, 2026 3:20pm | Jul 29, 2026 3:20pm |  |  | Fair | Yes | Premises checked and found ok, customer was also spoken with however she suggested that the power supply was restored from earlier.
Outage | J.E.26.07.36577 | C001868653 | Stephen Taylor | St.Thomas | Completed | Load_251945 | Good Year - 110 | Jul 29, 2026 11:28am | Jul 29, 2026 11:29am | Jul 30, 2026 8:41am | Jul 30, 2026 8:42am | Jul 30, 2026 10:02am | Jul 30, 2026 10:02am | Jul 30, 2026 10:03am | Jul 30, 2026 10:03am |  |  | Fair | No | Check with customer and customer said power was restored from yesterday and okay now
Outage | J.E.26.07.36728 | C001868654 | Stephen Taylor | St.Thomas | Completed | Load_249913 | Good Year - 110 | Jul 29, 2026 11:28am | Jul 29, 2026 11:29am | Jul 29, 2026 12:15pm | Jul 29, 2026 12:16pm | Jul 29, 2026 12:56pm | Jul 29, 2026 12:56pm | Jul 29, 2026 1:11pm | Jul 29, 2026 1:11pm |  |  | Fair | No | Clean up single phase use 3 clamps reading 111,112,224 customer is now okay
Non-Outage | J.E.26.06.33944 | C001868648 | Fitzroy Turner | KSAS | Completed | Load_267297 | Hunts Bay - 310 | Jul 29, 2026 11:25am | Jul 29, 2026 4:59pm | Jul 29, 2026 6:23pm | Jul 29, 2026 6:23pm | Jul 29, 2026 6:36pm | Jul 29, 2026 6:36pm | Jul 29, 2026 6:37pm | Jul 29, 2026 6:37pm |  |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.07.34176 | C001868621 | Moses Elliston | St.Catherine | Completed | Load_260976 | Tredegar - 210 | Jul 29, 2026 11:14am | Jul 29, 2026 11:14am | Jul 29, 2026 11:32am | Jul 29, 2026 11:32am | Jul 29, 2026 11:32am | Jul 29, 2026 11:10am | Jul 29, 2026 11:35am | Jul 29, 2026 11:35am |  |  | Fair | No | Defective 15 kva,13.8 kv transformer with yp meters to be change.Refer to Roy Brown.
Outage | J.E.26.07.36663 | C001868605 | Daniel Francis | St.Ann | Completed | Load_267500 | Ocho Rios - 310 | Jul 29, 2026 11:07am | Jul 29, 2026 11:09am | Jul 29, 2026 11:37am | Jul 29, 2026 11:37am | Jul 29, 2026 12:09pm | Jul 29, 2026 3:35pm | Jul 29, 2026 3:46pm | Jul 29, 2026 3:46pm | Fire |  | Fair | No | Found secondary nuetral broken close to Berger king and post off ocho rios splic and retention also replaced drop lead for transformer 00681019
Outage | J.E.26.07.36671 | C001868604 | Roxroy Needham | St.Ann | Completed | Load_245352 | Cardiff Hall - 310 | Jul 29, 2026 11:07am | Jul 29, 2026 11:08am | Jul 29, 2026 12:28pm | Jul 29, 2026 12:28pm | Jul 29, 2026 12:28pm | Jul 29, 2026 12:29pm | Jul 29, 2026 12:29pm | Jul 29, 2026 12:29pm | BrokenWire |  | Fair | No | Issue was resolved
Non-Outage | J.E.26.07.36706 | C001868597 | Orville Lee | Portmore | Completed | Load_244905 | Naggo Head - 610 | Jul 29, 2026 10:58am | Jul 29, 2026 11:01am | Jul 30, 2026 12:11pm | Jul 30, 2026 12:11pm | Jul 30, 2026 12:11pm | Jul 30, 2026 12:11pm | Jul 30, 2026 12:14pm | Jul 30, 2026 12:14pm | BrokenWire |  | Fair | No | Pole 110015 badly lean causing secondary line hanging extremely low and touching when heavy windPole is T ConstructedPole construction of street light, 3 take off to customers 3 primary and a junction connection Refer to maintenance
Outage | J.E.26.07.36689 | C001868588 | Donald Cunningham | St.Catherine | Completed | Load_290839 | Rhodens Pen - 210 | Jul 29, 2026 10:58am | Jul 29, 2026 11:00am | Jul 29, 2026 1:36pm | Jul 29, 2026 1:36pm | Jul 29, 2026 2:13pm | Jul 29, 2026 2:31pm | Jul 29, 2026 2:34pm | Jul 29, 2026 2:34pm |  |  | Fair | No | Defective rami box transformer need to replace 15 kva leaking oil
Outage | J.E.26.07.36667 | C001868577 | Ricky Hall | St.Catherine | Completed | Load_238048 | New Michelton - 410 | Jul 29, 2026 10:44am | Jul 29, 2026 10:44am | Jul 29, 2026 11:02am | Jul 29, 2026 11:02am | Jul 29, 2026 11:58am | Jul 29, 2026 12:13pm | Jul 29, 2026 12:14pm | Jul 29, 2026 12:14pm |  |  | Rains | No | Replaced burnt out fuse holder and 15 amps fuse
Outage | J.E.26.07.36589 | C001868576 | Ricky Hall | St.Catherine | Completed | Load_258128 | New Michelton - 410 | Jul 29, 2026 10:43am | Jul 29, 2026 10:44am | Jul 29, 2026 1:06pm | Jul 29, 2026 1:07pm | Jul 29, 2026 2:01pm | Jul 29, 2026 2:56pm | Jul 29, 2026 2:57pm | Jul 29, 2026 2:57pm |  |  | Fair | No | Reconnect 3W service via call centre 115/118/233
Non-Outage | J.E.26.07.24146 | C001868519 | Wan Carlos Scarlett | St.Catherine | Completed | Load_262410 | Twickenham - 210 | Jul 29, 2026 10:22am | Jul 29, 2026 10:25am | Jul 29, 2026 11:07am | Jul 29, 2026 11:07am | Jul 29, 2026 11:40am | Jul 29, 2026 12:03pm | Jul 29, 2026 12:07pm | Jul 29, 2026 12:07pm | BrokenPole |  | Fair | No | Found 30ft pole with dead end open secondary line and guy wire pole leaning towards the road pole rotten from the foot of the pole. No pole # was found
Non-Outage | J.E.26.07.25413 | C001868518 | Donald Cunningham | St.Catherine | Completed | Load_243946 | Rhodens Pen - 410 | Jul 29, 2026 10:20am | Jul 29, 2026 10:21am | Jul 29, 2026 10:58am | Jul 29, 2026 10:58am | Jul 29, 2026 12:28pm | Jul 29, 2026 12:28pm | Jul 29, 2026 12:33pm | Jul 29, 2026 12:33pm |  |  | Fair | No | Premises closed customer requests Sunday visit no one at home in the week
Non-Outage | J.E.26.07.34591 | C001868486 | Elvis Trowers | null | Completed | null | null | Jul 29, 2026 9:58am | Jul 29, 2026 9:59am | Jul 29, 2026 11:44am | Jul 29, 2026 11:44am | Jul 29, 2026 11:52am | Jul 29, 2026 11:56am | Jul 29, 2026 11:56am | Jul 29, 2026 11:56am |  |  | Fair | Yes | Customer was contacted by telephone and when spoken with he said that the situation was resolved but he just wanted to know what was the issue for the power to be going away so often.
Non-Outage | J.E.26.07.36464 | C001868479 | Swon Miller | null | Completed | null | null | Jul 29, 2026 9:54am | Jul 29, 2026 4:29pm | Jul 29, 2026 4:33pm | Jul 29, 2026 4:33pm | Jul 29, 2026 5:49pm | Jul 14, 2026 6:25pm | Jul 29, 2026 6:26pm | Jul 29, 2026 6:26pm | LowHangingWires |  | Fair | No | Premises not found clearer direction required the gentleman that I spoke to on the phone is also not familia with the area
Outage | J.E.26.07.35018 | C001868471 | Eric Williams | KSAS | Completed | Load_300873 | Cane River - 410 | Jul 29, 2026 9:51am | Jul 29, 2026 9:51am | Jul 29, 2026 10:25am | Jul 29, 2026 10:25am | Jul 29, 2026 11:16am | Jul 29, 2026 1:53pm | Jul 29, 2026 1:56pm | Jul 29, 2026 1:56pm |  |  | SaltSprays | No | Defective 10KVA transformer found and replaced, also replaced 1 2amps transformer fuse in bank of 3 transformer, voltage reading 239,240,240,416,416,417
Non-Outage | J.E.26.07.36201 | C001868470 | Edward Royal | null | Completed | null | null | Jul 29, 2026 9:50am | Jul 29, 2026 9:51am | Jul 29, 2026 12:33pm | Jul 29, 2026 12:33pm | Jul 29, 2026 12:33pm | Jul 29, 2026 12:33pm | Jul 29, 2026 12:33pm | Jul 29, 2026 12:33pm |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.07.36387 | C001868469 | Edward Royal | KSAS | Completed | Load_268518 | Hunts Bay - 810 | Jul 29, 2026 9:50am | Jul 29, 2026 9:51am | Jul 29, 2026 3:35pm | Jul 29, 2026 3:35pm | Jul 29, 2026 3:35pm | Jul 29, 2026 3:35pm | Jul 29, 2026 3:35pm | Jul 29, 2026 3:35pm | Fire |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.07.36414 | C001868468 | Edward Royal | KSAS | Completed | Load_238088 | Hunts Bay - 510 | Jul 29, 2026 9:50am | Jul 29, 2026 9:51am | Jul 29, 2026 4:32pm | Jul 29, 2026 4:32pm | Jul 29, 2026 4:43pm | Jul 29, 2026 4:54pm | Jul 29, 2026 4:55pm | Jul 29, 2026 4:55pm |  |  | Fair | No | Premises found ok voltage reading 238 119 119 v
Outage | J.E.26.07.35780 | C001868462 | Andrew Powell | Manchester | Completed | Load_268017 | Spur Tree - 210 | Jul 29, 2026 9:46am | Jul 29, 2026 3:53pm | Jul 29, 2026 6:43pm | Jul 29, 2026 6:43pm | Jul 29, 2026 7:06pm | Jul 29, 2026 7:06pm | Jul 29, 2026 7:07pm | Jul 29, 2026 7:07pm |  |  | Fair | No | Premises not located inadequately direction contact customer by telephone unsuccessful.
Outage | J.E.26.07.36450 | C001868445 | Kenroy Dale | Manchester | Completed | Load_263292 | Kendal - 210 | Jul 29, 2026 9:37am | Jul 29, 2026 9:38am | Jul 29, 2026 10:18am | Jul 29, 2026 10:18am | Jul 29, 2026 11:31am | Jul 29, 2026 11:47am | Jul 29, 2026 11:47am | Jul 29, 2026 11:47am |  |  | Fair | No | Customer requested barrel lock to be removed
Outage | J.E.26.07.36454 | C001868444 | Horace Malcolm | St.James | Completed | Load_262913 | Queens Drive - 310 | Jul 29, 2026 9:37am | Jul 29, 2026 9:37am | Jul 29, 2026 10:52am | Jul 29, 2026 10:52am | Jul 29, 2026 10:52am | Jul 29, 2026 10:54am | Jul 29, 2026 10:54am | Jul 29, 2026 10:54am |  |  | Fair | No | Check and found ok related to previous call job number 36406
Outage | J.E.26.07.34176 | C001868443 | Moses Elliston | St.Catherine | Completed | Load_260976 | Tredegar - 210 | Jul 29, 2026 9:33am | Jul 29, 2026 9:34am | Jul 29, 2026 11:08am | Jul 29, 2026 11:08am | Jul 29, 2026 11:08am | Jul 29, 2026 10:50am | Jul 29, 2026 11:10am | Jul 29, 2026 11:10am |  |  | Fair | No | Defective 15 kva 13.8 kv transformer with YP meters to be change.
Outage | J.E.26.07.36170 | C001868442 | Donald Cunningham | St.Catherine | Completed | Load_568622 | Tredegar - 510 | Jul 29, 2026 9:33am | Jul 29, 2026 9:34am | Jul 29, 2026 9:49am | Jul 29, 2026 9:49am | Jul 29, 2026 10:38am | Jul 29, 2026 10:45am | Jul 29, 2026 10:46am | Jul 29, 2026 10:46am |  |  | Fair | No | Premises not located customer not reachable
Non-Outage | J.E.26.07.33994 | C001868436 | Barnett Brown | Manchester | Completed | Load_292850 | Kendal - 310 | Jul 29, 2026 9:31am | Jul 29, 2026 9:32am | Jul 29, 2026 10:51am | Jul 29, 2026 10:51am | Jul 29, 2026 11:32am | Jul 29, 2026 11:56am | Jul 29, 2026 12:08pm | Jul 29, 2026 12:08pm |  |  | Fair | No | Open 25 kva transformer, pole number 0120456, remade transformer drop lead, however, burnt 25 kva needs to be replaced. Over 35 customers are on tied in circuit
Non-Outage | J.E.26.07.33479 | C001868435 | Damion Reid | Manchester | Completed | Load_242198 | Kendal - 210 | Jul 29, 2026 9:30am | Jul 29, 2026 3:43pm | Jul 29, 2026 4:40pm | Jul 29, 2026 4:40pm | Jul 29, 2026 5:25pm | Jul 29, 2026 6:02pm | Jul 29, 2026 6:03pm | Jul 29, 2026 6:03pm |  |  | Fair | No | Unable to contact or locate customer
Outage | J.E.26.07.36415 | C001868403 | Kenroy Dale | Manchester | Completed | Load_240219 | Porus - 310 | Jul 29, 2026 9:13am | Jul 29, 2026 9:14am | Jul 29, 2026 11:48am | Jul 29, 2026 12:57pm | Jul 29, 2026 12:57pm | Jul 29, 2026 2:36pm | Jul 29, 2026 2:43pm | Jul 29, 2026 2:43pm |  |  | Fair | No | Open 25 kva transformer to de-bush tree that fall on line, services wire was also splice and retention. Transformer was re-closed and area now with supply
Non-Outage | J.E.26.07.36067 | C001868395 | Andre Williams | Trelawny | Completed | Load_246936 | Duncans - 210 | Jul 29, 2026 9:12am | Jul 29, 2026 9:13am | Jul 29, 2026 9:16am | Jul 29, 2026 9:19am | Jul 29, 2026 10:24am | Jul 29, 2026 10:59am | Jul 29, 2026 10:59am | Jul 29, 2026 10:59am |  |  | Fair | No | Remake burnt off jumper leading into lane and clean coroded neutral voltage voltage on line 119+119=238
Non-Outage | J.E.26.07.36329 | C001868394 | Marlon Authors | St.Elizabeth | Completed | Load_265559 | Maggotty - 210 | Jul 29, 2026 9:12am | Jul 29, 2026 9:33am | Jul 29, 2026 12:49pm | Jul 29, 2026 12:49pm | Jul 29, 2026 12:49pm | Jul 29, 2026 12:53pm | Jul 29, 2026 12:53pm | Jul 29, 2026 12:53pm |  |  | Fair | No | Supply checked and found defective meter socket and meter also burnt rdg 110v,112v and cross phased 223 volts. Customer was advised to have meter socket repaired. Please refer same to the field services department for meter replacement
Non-Outage | J.E.26.07.25855 | C001868386 | Andrae Dawkins | St.James | Completed | Load_248976 | Queens Drive - 710 | Jul 29, 2026 9:05am | Jul 29, 2026 9:06am | Jul 29, 2026 11:12am | Jul 29, 2026 11:12am | Jul 29, 2026 11:12am | Jul 29, 2026 11:16am | Jul 29, 2026 11:17am | Jul 29, 2026 11:17am |  |  | Fair | No | Found customer single phasing from EG box 00518 refer back to field service kaydian
Non-Outage | J.E.26.07.31239 | C001868387 | Andrae Dawkins | St.James | Completed | Load_270006 | Queens Drive - 810 | Jul 29, 2026 9:05am | Jul 29, 2026 9:06am | Jul 29, 2026 3:03pm | Jul 29, 2026 3:03pm | Jul 29, 2026 3:30pm | Jul 29, 2026 1:50pm | Jul 29, 2026 3:50pm | Jul 29, 2026 3:50pm |  |  | Fair | No | Found multiple customers experiencing low referrals back to emergency crew
Non-Outage | J.E.26.07.36406 | C001868385 | Horace Malcolm | St.James | Completed | Load_262913 | Queens Drive - 310 | Jul 29, 2026 9:04am | Jul 29, 2026 9:05am | Jul 29, 2026 9:25am | Jul 29, 2026 9:25am | Jul 29, 2026 10:08am | Jul 29, 2026 10:52am | Jul 29, 2026 10:52am | Jul 29, 2026 10:52am |  |  | Fair | No | Isolate two 25kva transformer to repair burnt off transformer phase drop lead used 1clamp voltage 115-117-232
Outage | J.E.26.07.36398 | C001868375 | Jowayne Newmans | Portland | Completed | Load_243638 | Port Antonio - 410 | Jul 29, 2026 8:59am | Jul 29, 2026 9:00am | Jul 29, 2026 9:34am | Jul 29, 2026 9:34am | Jul 29, 2026 10:09am | Jul 29, 2026 10:12am | Jul 29, 2026 10:12am | Jul 29, 2026 10:12am |  |  | Fair | No | Patrol and found customer meter single phasing and need to be replaced, refer call to field service to replace damaged meter. Voltage reading left at meter socket 110v, 112v, 221v.
Outage | J.E.26.07.36382 | C001868374 | Daniel Francis | St.Ann | Completed | Load_265774 | Cardiff Hall - 210 | Jul 29, 2026 8:58am | Jul 29, 2026 9:38am | Jul 29, 2026 9:58am | Jul 29, 2026 9:58am | Jul 29, 2026 10:04am | Jul 29, 2026 10:12am | Jul 29, 2026 10:13am | Jul 29, 2026 10:13am |  |  | Fair | No | Pole #0089281 change one 2amp fuse
Outage | J.E.26.07.36321 | C001868369 | Richard Nicholas | St.Catherine | Completed | Load_305203 | Tredegar - 210 | Jul 29, 2026 8:54am | Jul 29, 2026 3:51pm | Jul 29, 2026 5:44pm | Jul 29, 2026 5:44pm | Jul 29, 2026 6:30pm | Jul 29, 2026 6:55pm | Jul 29, 2026 6:57pm | Jul 29, 2026 6:57pm | TreeContact | Y | Fair | No | Bushing required
Outage | J.E.26.07.36371 | C001868344 | Ricky Hall | St.Catherine | Completed | Load_256195 | New Michelton - 410 | Jul 29, 2026 8:43am | Jul 29, 2026 8:43am | Jul 29, 2026 12:14pm | Jul 29, 2026 12:15pm | Jul 29, 2026 12:38pm | Jul 29, 2026 12:59pm | Jul 29, 2026 12:59pm | Jul 29, 2026 12:59pm |  |  | Rains | No | Replaced blown 50 amps junction fuse
Outage | J.E.26.07.36390 | C001868343 | Ricky Hall | St.Catherine | Completed | Load_267869 | New Michelton - 410 | Jul 29, 2026 8:43am | Jul 29, 2026 8:43am | Jul 29, 2026 12:59pm | Jul 29, 2026 12:59pm | Jul 29, 2026 12:59pm | Jul 29, 2026 1:06pm | Jul 29, 2026 1:06pm | Jul 29, 2026 1:06pm |  |  | Fair | No | Customer not located
Non-Outage | J.E.26.07.36377 | C001868342 | Rayon Foster | null | Completed | null | null | Jul 29, 2026 8:42am | Jul 29, 2026 8:44am | Jul 29, 2026 7:19pm | Jul 29, 2026 9:17pm | Jul 29, 2026 10:00pm | Jul 29, 2026 10:00pm | Jul 29, 2026 10:08pm | Jul 29, 2026 10:08pm |  |  | Fair | No | When called mr garnet he said that power was restored at the cell site
Outage | J.E.26.07.36370 | C001868319 | Oshane Warren | Westmoreland | Completed | Load_260892 | Paradise - 310 | Jul 29, 2026 8:30am | Jul 29, 2026 8:42am | Jul 29, 2026 8:54am | Jul 29, 2026 8:54am | Jul 29, 2026 11:17am | Jul 29, 2026 11:39am | Jul 29, 2026 11:41am | Jul 29, 2026 11:41am |  |  | Fair | No | Reconnect back server wire at pathead and secondary line used 60 ft #6 twisted wire and 3 service connector 3 1 bolt clamps voltage 115 115 230
Non-Outage | J.E.26.07.35768 | C001868318 | Andrae Clarke | Portland | Completed | Load_262425 | Port Antonio - 410 | Jul 29, 2026 8:29am | Jul 29, 2026 9:27am | Jul 29, 2026 11:33am | Jul 29, 2026 11:33am | Jul 29, 2026 12:07pm | Jul 29, 2026 12:09pm | Jul 29, 2026 12:09pm | Jul 29, 2026 12:09pm |  |  | Fair | No | Premises found okay Check voltage 117/119/236
Non-Outage | J.E.26.07.35890 | C001868317 | Andrae Clarke | Portland | Completed | Load_262425 | Port Antonio - 410 | Jul 29, 2026 8:29am | Jul 29, 2026 9:27am | Jul 29, 2026 11:21am | Jul 29, 2026 11:21am | Jul 29, 2026 11:31am | Jul 29, 2026 11:45am | Jul 29, 2026 11:33am | Jul 29, 2026 11:33am |  |  | Fair | No | Premises found okay Check voltage 118/116/234
Non-Outage | J.E.26.07.36375 | C001868316 | Andrae Clarke | Portland | Completed | Load_263585 | Port Antonio - 410 | Jul 29, 2026 8:29am | Jul 29, 2026 9:27am | Jul 29, 2026 10:58am | Jul 29, 2026 10:58am | Jul 29, 2026 10:58am | Jul 29, 2026 10:24am | Jul 29, 2026 11:21am | Jul 29, 2026 11:21am |  |  | Fair | No | Premises found okay check voltage 122/114/236
Outage | J.E.26.07.36331 | C001868295 | Selvin White | St.Elizabeth | Completed | Load_255988 | Maggotty - 110 | Jul 29, 2026 8:18am | Jul 29, 2026 8:42am | Jul 29, 2026 9:29am | Jul 29, 2026 9:29am | Jul 29, 2026 9:41am | Jul 29, 2026 9:54am | Jul 29, 2026 9:54am | Jul 29, 2026 9:54am |  |  | Fair | No | Meter found blank with no connections from JPS supply. Customer states that that’s from the last hurricane.. meter #2968927 and 2968925 are both barrel locked with conduit damaged. Please refer to C. Johnson and Simone Bicarie for follow up investigation as customer says the accounts are still being billed.
Outage | J.E.26.07.36351 | C001868294 | Wan Carlos Scarlett | St.Catherine | Completed | Load_244322 | Twickenham - 210 | Jul 29, 2026 8:18am | Jul 29, 2026 8:19am | Jul 29, 2026 9:48am | Jul 29, 2026 1:34pm | Jul 29, 2026 3:07pm | Jul 29, 2026 3:45pm | Jul 29, 2026 3:46pm | Jul 29, 2026 3:46pm |  |  | Fair | No | Customer confirm that power supply has been restored
Non-Outage | J.E.26.07.34851 | C001868282 | Oraine Minto | St.Ann | Completed | Load_266511 | Cardiff Hall - 310 | Jul 29, 2026 8:17am | Jul 29, 2026 8:19am | Jul 29, 2026 12:48pm | Jul 29, 2026 1:32pm | Jul 29, 2026 1:32pm | Jul 29, 2026 1:38pm | Jul 29, 2026 1:38pm | Jul 29, 2026 1:38pm |  |  | Fair | No | Refer to maintenance Transformer output is 214 at the transformer 100kva Pole #0010479Customer having low voltage issues at night
Non-Outage | J.E.26.07.35001 | C001868283 | Oraine Minto | St.Ann | Completed | Load_266408 | Cardiff Hall - 210 | Jul 29, 2026 8:17am | Jul 29, 2026 8:19am | Jul 29, 2026 8:33am | Jul 29, 2026 9:00am | Jul 29, 2026 9:00am | Jul 29, 2026 9:01am | Jul 29, 2026 9:01am | Jul 29, 2026 9:01am |  |  | Fair | No | Power was restored
Non-Outage | J.E.26.07.35042 | C001868281 | Oraine Minto | St.Ann | Completed | Load_263632 | Cardiff Hall - 210 | Jul 29, 2026 8:17am | Jul 29, 2026 8:19am | Jul 30, 2026 11:47am | Jul 30, 2026 12:11pm | Jul 30, 2026 12:11pm | Jul 30, 2026 12:12pm | Jul 30, 2026 12:15pm | Jul 30, 2026 12:15pm |  |  | Fair | No | Refer to maintenance Transformer output at the PICA plaza and the plaza next to it voltage is low 207v Pole#085367
Non-Outage | J.E.26.07.35546 | C001868279 | Oraine Minto | St.Ann | Completed | Load_244783 | Ocho Rios - 310 | Jul 29, 2026 8:17am | Jul 29, 2026 8:19am | Jul 30, 2026 10:29am | Jul 30, 2026 10:30am | Jul 30, 2026 10:30am | Jul 30, 2026 10:30am | Jul 30, 2026 10:31am | Jul 30, 2026 10:31am |  |  | Fair | No | Customer states that issue was resolved
Non-Outage | J.E.26.07.35876 | C001868280 | Oraine Minto | St.Ann | Completed | Load_251108 | Cardiff Hall - 310 | Jul 29, 2026 8:17am | Jul 29, 2026 8:19am | Jul 29, 2026 9:50am | Jul 29, 2026 9:50am | Jul 29, 2026 10:55am | Jul 29, 2026 10:55am | Jul 29, 2026 11:02am | Jul 29, 2026 11:02am |  |  | Fair | No | 2 one bolt clamp was used 220v 108v 113v
Outage | J.E.26.07.36354 | C001868278 | Ricky Hall | St.Catherine | Completed | Load_249743 | New Michelton - 410 | Jul 29, 2026 8:16am | Jul 29, 2026 8:17am | Jul 29, 2026 8:20am | Jul 29, 2026 9:21am | Jul 29, 2026 10:28am | Jul 29, 2026 11:01am | Jul 29, 2026 11:02am | Jul 29, 2026 11:02am |  |  | Fair | No | Retention banging secondary lines replaced blown 2 amps junction fus 10 kva xfmr
Outage | J.E.26.07.35796 | C001868276 | Daniel Francis | Trelawny | Completed | Load_252380 | Duncans - 210 | Jul 29, 2026 8:15am | Jul 29, 2026 8:15am | Jul 29, 2026 9:06am | Jul 29, 2026 9:06am | Jul 29, 2026 9:06am | Jul 29, 2026 9:07am | Jul 29, 2026 9:10am | Jul 29, 2026 9:10am |  |  | Fair | No | Customer says power is restored
Non-Outage | J.E.26.07.18606 | C001868259 | Locksley Allen | St.Ann | Completed | Load_254437 | Upper White River - 210 | Jul 29, 2026 8:13am | Jul 29, 2026 8:15am | Jul 30, 2026 2:52pm | Jul 30, 2026 3:47pm | Jul 30, 2026 3:47pm | Jul 30, 2026 3:55pm | Jul 30, 2026 4:00pm | Jul 30, 2026 4:00pm |  |  | Fair | No | Meter found blank. Clean up connectors at pole Voltage at meter socket phase to phase 250v. Phase to neutral 125&125vMeter left
Non-Outage | J.E.26.07.20370 | C001868260 | Locksley Allen | St.Ann | Completed | Load_246188 | Blackstonedge - 110 | Jul 29, 2026 8:13am | Jul 29, 2026 8:15am | Jul 30, 2026 9:09am | Jul 30, 2026 10:05am | Jul 30, 2026 10:05am | Jul 30, 2026 10:14am | Jul 30, 2026 10:17am | Jul 30, 2026 10:17am |  |  | Fair | No | No on and off problem found at premises at present Voltage at meter socket phase to phase 230v. Phase to neutral 117&119Meter left working
Non-Outage | J.E.26.07.20638 | C001868261 | Locksley Allen | St.Mary | Completed | Load_248495 | Blackstonedge - 110 | Jul 29, 2026 8:13am | Jul 29, 2026 8:14am | Jul 30, 2026 10:18am | Jul 30, 2026 11:34am | Jul 30, 2026 11:34am | Jul 30, 2026 11:48am | Jul 30, 2026 11:52am | Jul 30, 2026 11:52am |  |  | Fair | No | Connectors found corroded, clean up connectors Voltage at meter socket phase to phase 238v. Phase to neutral 118&119vMeter left working okay
Non-Outage | J.E.26.07.32596 | C001868274 | Clyde Brown | Clarendon | Completed | Load_251856 | May Pen - 110 | Jul 29, 2026 8:13am | Jul 29, 2026 8:13am | Jul 29, 2026 10:27am | Jul 29, 2026 10:28am | Jul 29, 2026 11:48am | Jul 29, 2026 1:25pm | Jul 29, 2026 1:32pm | Jul 29, 2026 1:32pm |  |  | Fair | No | Defective 3 wire service for 2wire connection same spliced and retention with 70ft-#6 triplex service wire voltage left 112V
Non-Outage | J.E.26.07.35084 | C001868263 | Locksley Allen | St.Mary | Completed | Load_242748 | Oracabessa - 210 | Jul 29, 2026 8:13am | Jul 29, 2026 8:14am | Jul 29, 2026 2:28pm | Jul 29, 2026 2:29pm | Jul 29, 2026 2:29pm | Jul 29, 2026 3:09pm | Jul 29, 2026 3:11pm | Jul 29, 2026 3:11pm |  |  | Fair | No | Duplicate. Defective meter socket,customer was advised to get it change
Non-Outage | J.E.26.07.35181 | C001868265 | Locksley Allen | St.Mary | Completed | Load_259924 | Highgate -110 | Jul 29, 2026 8:13am | Jul 29, 2026 8:14am | Jul 29, 2026 9:50am | Jul 29, 2026 10:06am | Jul 29, 2026 10:06am | Jul 29, 2026 10:37am | Jul 29, 2026 10:40am | Jul 29, 2026 10:40am |  |  | Fair | No | Pothead found corroded. Clean up pothead Voltage at meter socket phase to phase 231v.Phase to neutral 116&114v.Meter left working
Non-Outage | J.E.26.07.35286 | C001868272 | Locksley Allen | St.Mary | Completed | Load_242748 | Oracabessa - 210 | Jul 29, 2026 8:13am | Jul 29, 2026 8:14am | Jul 29, 2026 1:26pm | Jul 29, 2026 2:25pm | Jul 29, 2026 2:25pm | Jul 29, 2026 1:25pm | Jul 29, 2026 2:28pm | Jul 29, 2026 2:28pm |  |  | Fair | No | Meter socket defective and needs to change urgently.Voltage at meter socket phase to phase 240v. Phase to neutral 120&117vCustomer was advised to change meter socket urgently
Non-Outage | J.E.26.07.35487 | C001868273 | Locksley Allen | St.Mary | Completed | Load_354128 | Oracabessa - 110 | Jul 29, 2026 8:13am | Jul 29, 2026 8:14am | Jul 29, 2026 12:12pm | Jul 29, 2026 12:46pm | Jul 29, 2026 12:46pm | Jul 29, 2026 1:12pm | Jul 29, 2026 1:15pm | Jul 29, 2026 1:15pm |  |  | Fair | No | Meter socket defective and needs to change Voltage at meter socket phase to phase 242v. Phase to neutral 120&117vMeter working okay
Non-Outage | J.E.26.07.36113 | C001868275 | Locksley Allen | St.Mary | Completed | Load_252159 | Highgate - 210 | Jul 29, 2026 8:13am | Jul 29, 2026 8:15am | Jul 29, 2026 10:41am | Jul 29, 2026 11:51am | Jul 29, 2026 11:51am | Jul 29, 2026 12:07pm | Jul 29, 2026 12:10pm | Jul 29, 2026 12:10pm |  |  | Fair | No | Pothead found corroded,clean up pothead.Voltage at meter socket phase to phase 225v. Phase to neutral 111&114vMeter left working
Outage | J.E.26.07.35645 | C001868264 | Rayon Foster | Hanover | Completed | Load_240310 | Orange Bay - 310 | Jul 29, 2026 8:13am | Jul 29, 2026 8:13am | Jul 29, 2026 2:21pm | Jul 29, 2026 3:47pm | Jul 29, 2026 3:47pm | Jul 29, 2026 2:42am | Jul 29, 2026 3:51pm | Jul 29, 2026 3:51pm |  |  | Rains | No | Found working ok customer said she made a report for a friend in a next community
Non-Outage | J.E.26.07.05966 | C001868255 | Locksley Allen | St.Ann | Completed | Load_270210 | Blackstonedge - 110 | Jul 29, 2026 8:12am | Jul 29, 2026 8:15am | Jul 30, 2026 1:31pm | Jul 30, 2026 1:31pm | Jul 30, 2026 1:31pm | Jul 30, 2026 1:37pm | Jul 30, 2026 1:34pm | Jul 30, 2026 1:34pm |  |  | Fair | No | Unable to locate meter. Waiting on customer to return call to get directions
Non-Outage | J.E.26.07.08605 | C001868257 | Locksley Allen | St.Ann | Completed | Load_354886 | Blackstonedge - 110 | Jul 29, 2026 8:12am | Jul 29, 2026 8:15am | Jul 30, 2026 2:23pm | Jul 30, 2026 2:29pm | Jul 30, 2026 2:29pm | Jul 30, 2026 2:34pm | Jul 30, 2026 2:31pm | Jul 30, 2026 2:31pm |  |  | Fair | No | Customer said JPS corrected the problem about two weeks ago
Non-Outage | J.E.26.07.08741 | C001868258 | Locksley Allen | St.Ann | Completed | Load_248758 | Blackstonedge - 110 | Jul 29, 2026 8:12am | Jul 29, 2026 8:15am | Jul 30, 2026 11:52am | Jul 30, 2026 12:32pm | Jul 30, 2026 12:33pm | Jul 30, 2026 12:46pm | Jul 30, 2026 12:50pm | Jul 30, 2026 12:50pm |  |  | Fair | No | No low voltage problem found at the premises at present Voltage at meter socket phase to phase 238v. Phase to neutral 119&113The transformer that is near the end of the secondary line,the switch is open and it is not connected to the secondary line. The neighbor has the same problem at times. Check the transformer
Non-Outage | J.E.26.07.33942 | C001868253 | Clyde Brown | Clarendon | Completed | Load_568437 | May Pen - 110 | Jul 29, 2026 8:12am | Jul 29, 2026 8:13am | Jul 29, 2026 8:44am | Jul 29, 2026 8:44am | Jul 29, 2026 9:59am | Jul 29, 2026 10:00am | Jul 29, 2026 10:02am | Jul 29, 2026 10:02am | BrokenWire |  | Fair | No | Found ok
Non-Outage | J.E.26.07.35165 | C001868256 | Odaine Johnson | Clarendon | Completed | Load_267981 | Parnassus - 310 | Jul 29, 2026 8:12am | Jul 29, 2026 8:14am | Jul 29, 2026 9:41am | Jul 29, 2026 10:47am | Jul 29, 2026 11:12am | Jul 29, 2026 11:13am | Jul 29, 2026 11:15am | Jul 29, 2026 11:15am |  |  | Fair | No | Corrosion was found at pothead 3 pen union was replaced and problem was fixed Voltage reading A115 B115 AB230
Non-Outage | J.E.26.07.35240 | C001868254 | Odaine Johnson | Clarendon | Completed | Load_261044 | Parnassus - 210 | Jul 29, 2026 8:12am | Jul 29, 2026 9:09am | Jul 29, 2026 9:41am | Jul 29, 2026 1:28pm | Jul 29, 2026 2:19pm | Jul 29, 2026 2:19pm | Jul 29, 2026 2:20pm | Jul 29, 2026 2:20pm |  |  | Fair | No | Corroded phase found at pole remade connection using 1 one bolt clamp voltage reading 115/115/231 volts
Non-Outage | J.E.26.07.20440 | C001868249 | Royston Montague | St.Catherine | Completed | Load_238583 | Twickenham - 310 | Jul 29, 2026 8:10am | Jul 29, 2026 8:11am | Jul 29, 2026 8:30am | Jul 29, 2026 9:55am | Jul 29, 2026 10:04am | Jul 29, 2026 10:35am | Jul 29, 2026 10:36am | Jul 29, 2026 10:36am |  |  | Fair | No | Faulty joint at customer take off point. Same corrected, voltage found 114v 97v voltage after job completion are 229v 115v 113v
Non-Outage | J.E.26.07.20474 | C001868250 | Royston Montague | St.Catherine | Completed | Load_263708 | Twickenham - 310 | Jul 29, 2026 8:10am | Jul 29, 2026 8:11am | Jul 29, 2026 8:30am | Jul 29, 2026 12:07pm | Jul 29, 2026 12:20pm | Jul 29, 2026 12:21pm | Jul 29, 2026 12:21pm | Jul 29, 2026 12:21pm |  |  | Fair | No | Customer confirmed issue resolved, please update thanks.
Non-Outage | J.E.26.07.20902 | C001868248 | Royston Montague | St.Catherine | Completed | Load_238583 | Twickenham - 310 | Jul 29, 2026 8:10am | Jul 29, 2026 8:11am | Jul 29, 2026 8:30am | Jul 29, 2026 10:36am | Jul 29, 2026 10:36am | Jul 29, 2026 10:38am | Jul 29, 2026 10:38am | Jul 29, 2026 10:38am |  |  | Fair | No | Faulty joint at customer take off point. Same corrected, voltage found 97v 115v voltage after job completion are 229v 115v 113v
Non-Outage | J.E.26.07.25526 | C001868251 | Royston Montague | St.Catherine | Completed | Load_241538 | Twickenham - 310 | Jul 29, 2026 8:10am | Jul 29, 2026 8:11am | Jul 29, 2026 8:30am | Jul 29, 2026 8:41am | Jul 29, 2026 9:52am | Jul 29, 2026 9:54am | Jul 29, 2026 9:54am | Jul 29, 2026 9:54am | LeakingTransformer |  | Fair | No | Transformer seems in good condition.
Non-Outage | J.E.26.07.22737 | C001868246 | Royston Montague | St.Catherine | Completed | Load_238151 | Twickenham - 310 | Jul 29, 2026 8:09am | Jul 29, 2026 8:11am | Jul 29, 2026 8:30am | Jul 30, 2026 10:39am | Jul 30, 2026 10:56am | Jul 30, 2026 10:57am | Jul 30, 2026 10:57am | Jul 30, 2026 10:57am |  |  | Fair | No | Broken twisted wire #6 same repair, voltage found 114v voltage after job completion are 229v 113v 114v
Non-Outage | J.E.26.07.23001 | C001868245 | Royston Montague | St.Catherine | Completed | Load_247309 | Twickenham - 310 | Jul 29, 2026 8:09am | Jul 29, 2026 8:11am | Jul 29, 2026 8:30am | Jul 29, 2026 12:22pm | Jul 29, 2026 12:31pm | Jul 29, 2026 12:32pm | Jul 29, 2026 12:32pm | Jul 29, 2026 12:32pm |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.07.24664 | C001868247 | Royston Montague | St.Catherine | Completed | Load_257089 | Twickenham - 310 | Jul 29, 2026 8:09am | Jul 29, 2026 8:11am | Jul 29, 2026 8:30am | Jul 29, 2026 10:38am | Jul 29, 2026 10:46am | Jul 29, 2026 11:16am | Jul 29, 2026 11:18am | Jul 29, 2026 11:18am |  |  | Fair | No | Open neutral at customer take off point . Same corrected, voltage found 125v 87v voltage after job completion are 227v 113v 113v
Non-Outage | J.E.26.07.27643 | C001868244 | Royston Montague | St.Catherine | Completed | Load_246503 | Twickenham - 310 | Jul 29, 2026 8:09am | Jul 29, 2026 8:11am | Jul 29, 2026 8:30am | Jul 29, 2026 1:13pm | Jul 29, 2026 3:11pm | Jul 29, 2026 3:20pm | Jul 29, 2026 3:22pm | Jul 29, 2026 3:22pm |  |  | Fair | No | Customer asked to get an electrician to check load side. Also observed pothead wires need to change, customer informed. Voltage 230v 114v 114v
Non-Outage | J.E.26.07.31576 | C001868241 | Royston Montague | St.Catherine | Completed | Load_254160 | Twickenham - 310 | Jul 29, 2026 8:09am | Jul 29, 2026 8:11am | Jul 29, 2026 8:30am | Jul 29, 2026 11:39am | Jul 29, 2026 11:44am | Jul 29, 2026 11:46am | Jul 29, 2026 11:47am | Jul 29, 2026 11:47am |  |  | Fair | No | Main gate lock to enter scheme. Multiple calls to customer phone go without answer.
Non-Outage | J.E.26.07.31657 | C001868242 | Royston Montague | St.Catherine | Completed | Load_254160 | Twickenham - 310 | Jul 29, 2026 8:09am | Jul 29, 2026 8:11am | Jul 29, 2026 8:30am | Jul 29, 2026 11:47am | Jul 29, 2026 11:47am | Jul 29, 2026 11:47am | Jul 29, 2026 11:48am | Jul 29, 2026 11:48am |  |  | Fair | No | Main gate lock to enter scheme. Multiple calls to customer phone go without answer.
Non-Outage | J.E.26.07.32830 | C001868240 | Royston Montague | St.Catherine | Completed | Load_294520 | Twickenham - 310 | Jul 29, 2026 8:09am | Jul 29, 2026 8:11am | Jul 29, 2026 8:30am | Jul 29, 2026 12:00pm | Jul 29, 2026 12:06pm | Jul 29, 2026 12:07pm | Jul 29, 2026 12:07pm | Jul 29, 2026 12:07pm |  |  | Fair | No | Defective breakers , customer confirmed electrician corrected same. Voltage 230v 114v 114v
Non-Outage | J.E.26.07.32976 | C001868238 | Royston Montague | St.Catherine | Completed | Load_254160 | Twickenham - 310 | Jul 29, 2026 8:09am | Jul 29, 2026 8:11am | Jul 29, 2026 8:30am | Jul 29, 2026 11:53am | Jul 29, 2026 11:53am | Jul 29, 2026 11:54am | Jul 29, 2026 11:54am | Jul 29, 2026 11:54am |  |  | Fair | No | Main gate lock to enter scheme. Multiple calls to customer phone go without answer.
Non-Outage | J.E.26.07.34273 | C001868239 | Royston Montague | St.Catherine | Completed | Load_1004021 | Twickenham - 310 | Jul 29, 2026 8:09am | Jul 29, 2026 8:11am | Jul 29, 2026 8:30am | Jul 29, 2026 11:22am | Jul 29, 2026 11:22am | Jul 29, 2026 11:23am | Jul 29, 2026 11:23am | Jul 29, 2026 11:23am |  |  | Fair | No | Customer confirmed issue resolved. Please update thanks.
Non-Outage | J.E.26.07.34737 | C001868231 | Royston Montague | St.Catherine | Completed | Load_240706 | Twickenham - 310 | Jul 29, 2026 8:08am | Jul 29, 2026 8:08am | Jul 29, 2026 8:30am | Jul 29, 2026 12:35pm | Jul 29, 2026 12:43pm | Jul 29, 2026 1:07pm | Jul 29, 2026 1:08pm | Jul 29, 2026 1:08pm |  |  | Fair | No | Open phase at customer take off point. Same corrected. Voltage found 115v voltage after job completion are 232v 115v 114v
Non-Outage | J.E.26.07.34634 | C001868230 | Rayon Foster | Hanover | Completed | Load_269922 | Orange Bay - 310 | Jul 29, 2026 8:07am | Jul 29, 2026 8:07am | Jul 29, 2026 5:36pm | Jul 29, 2026 5:36pm | Jul 29, 2026 6:28pm | Jul 29, 2026 7:18pm | Jul 29, 2026 7:18pm | Jul 29, 2026 7:18pm |  |  | Fair | No | Damaged 120v meter refer to field service to have meter changed voltage found at new meter socket install 115v/112v/227v
Outage | J.E.26.07.36306 | C001868229 | Roxroy Needham | St.Ann | Completed | Load_245352 | Cardiff Hall - 310 | Jul 29, 2026 8:07am | Jul 29, 2026 8:21am | Jul 29, 2026 9:42am | Jul 29, 2026 9:42am | Jul 29, 2026 11:36am | Jul 29, 2026 12:22pm | Jul 29, 2026 12:27pm | Jul 29, 2026 12:27pm | BrokenWire |  | Fair | No | Isolate 25 KVA transformer splice and retention 1 span of secondary neutral used 40 ft of No# 2 aa conductor voltage readings left 114,116,230
Non-Outage | J.E.26.07.34161 | C001868224 | Rochaine Hussey | KSAN | Completed | Load_241480 | Constant Spring - 410 | Jul 29, 2026 8:06am | Jul 29, 2026 8:06am | Jul 29, 2026 1:12pm | Jul 29, 2026 1:12pm | Jul 29, 2026 1:12pm | Jul 29, 2026 2:49pm | Jul 29, 2026 3:29pm | Jul 29, 2026 3:29pm |  |  | Fair | No | One bolt clamp was changed due to corrosion and issue was resolved 120/119/239v
Non-Outage | J.E.26.07.35511 | C001868225 | Rochaine Hussey | KSAN | Completed | Load_264247 | Constant Spring - 410 | Jul 29, 2026 8:06am | Jul 29, 2026 8:06am | Jul 29, 2026 11:02am | Jul 29, 2026 11:02am | Jul 29, 2026 12:43pm | Jul 29, 2026 12:44pm | Jul 29, 2026 12:45pm | Jul 29, 2026 12:45pm |  |  | Fair | No | Visit location customer not answering Unable to locate
Non-Outage | J.E.26.07.36290 | C001868223 | Rochaine Hussey | KSAN | Completed | Load_240017 | Constant Spring - 410 | Jul 29, 2026 8:06am | Jul 29, 2026 8:06am | Jul 29, 2026 11:48am | Jul 29, 2026 12:46pm | Jul 29, 2026 12:46pm | Jul 29, 2026 12:48pm | Jul 29, 2026 1:12pm | Jul 29, 2026 1:12pm |  |  | Fair | No | Pothead was corroded 2clamp used112/113/225vIssue resolved
Outage | J.E.26.07.36053 | C001868228 | Rayon Foster | Hanover | Completed | Load_260966 | Orange Bay - 310 | Jul 29, 2026 8:06am | Jul 29, 2026 8:06am | Jul 29, 2026 11:20am | Jul 29, 2026 11:20am | Jul 29, 2026 12:52pm | Jul 29, 2026 1:24pm | Jul 29, 2026 1:24pm | Jul 29, 2026 1:24pm |  |  | Fair | No | Blow 10kva transformer fuse remove fuse holder patrol secondary line line was clear lighting suspected to be the cause replace with 1amp and reclose
Non-Outage | J.E.26.07.34631 | C001868221 | Roemello Brown | Trelawny | Completed | Load_257998 | Greenwood - 110 | Jul 29, 2026 8:05am | Jul 29, 2026 8:06am | Jul 29, 2026 2:05pm | Jul 29, 2026 2:05pm | Jul 29, 2026 3:12pm | Jul 29, 2026 3:13pm | Jul 29, 2026 3:26pm | Jul 29, 2026 3:26pm |  |  | Fair | No | This is a hexing box also this size 2 service wire to the premises one is given 119/119/238 volt reading an the next line given no supply also no one is at the premises also try calling the number on the order to talk to the customer got no answer so Can you send field service personnel to check in the hexing box please Hex#06877Hx#27121840
Non-Outage | J.E.26.07.34828 | C001868222 | Roemello Brown | Trelawny | Completed | Load_251727 | Greenwood - 110 | Jul 29, 2026 8:05am | Jul 29, 2026 8:06am | Jul 29, 2026 9:27am | Jul 29, 2026 9:33am | Jul 29, 2026 11:20am | Jul 29, 2026 11:20am | Jul 29, 2026 12:00pm | Jul 29, 2026 12:00pm |  |  | Fair | No | Secondary line fluctuating needs emergency team to assist problem affecting a section of the community please assist as soon as possible thank you Voltage found 100/114/214Voltage leave 100/114/214
Non-Outage | J.E.26.07.34969 | C001868220 | Orville Lee | St.Catherine | Completed | Load_239521 | Twickenham - 210 | Jul 29, 2026 8:05am | Jul 29, 2026 8:06am | Jul 29, 2026 10:46am | Jul 29, 2026 10:50am | Jul 29, 2026 11:58am | Jul 29, 2026 11:59am | Jul 29, 2026 11:59am | Jul 29, 2026 11:59am |  |  | Fair | No | Changed defective service wire2 Penn union, 2 one bolt clamps and 80ft #6 service wire usedVoltage 116V
Non-Outage | J.E.26.07.35494 | C001868219 | Orville Lee | Portmore | Completed | Load_243335 | Naggo Head - 610 | Jul 29, 2026 8:05am | Jul 29, 2026 8:06am | Jul 29, 2026 10:46am | Jul 30, 2026 11:41am | Jul 30, 2026 11:46am | Jul 30, 2026 11:49am | Jul 30, 2026 11:50am | Jul 30, 2026 11:50am | Fire |  | Fair | No | Issue was solved by technician
Non-Outage | J.E.26.07.35849 | C001868218 | Orville Lee | Portmore | Completed | Load_259252 | Naggo Head - 510 | Jul 29, 2026 8:05am | Jul 29, 2026 8:06am | Jul 29, 2026 10:46am | Jul 29, 2026 11:59am | Jul 29, 2026 12:24pm | Jul 29, 2026 12:29pm | Jul 29, 2026 12:30pm | Jul 29, 2026 12:30pm |  |  | Fair | No | Customer reported seeing sparks at post Upon arrival no sparks was seen
Non-Outage | J.E.26.07.36079 | C001868217 | Orville Lee | St.Catherine | Completed | Load_251909 | Twickenham - 210 | Jul 29, 2026 8:05am | Jul 29, 2026 8:05am | Jul 29, 2026 10:46am | Jul 30, 2026 2:21pm | Jul 30, 2026 2:21pm | Jul 30, 2026 2:22pm | Jul 30, 2026 2:24pm | Jul 30, 2026 2:24pm |  |  | Fair | No | Defective service wire changedTwo pen union, one 1bolt clamp and 80ft #6 service wire used115v
Non-Outage | J.E.26.07.36118 | C001868215 | Orville Lee | Portmore | Completed | Load_244905 | Naggo Head - 610 | Jul 29, 2026 8:05am | Jul 29, 2026 8:05am | Jul 29, 2026 10:46am | Jul 30, 2026 11:52am | Jul 30, 2026 12:00pm | Jul 30, 2026 12:06pm | Jul 30, 2026 12:08pm | Jul 30, 2026 12:08pm | Fire |  | Fair | No | Pole 110015 badly lean causing wires to hang extremely low, sagging and touching each other Pole consist of street light, 3 take off to customers, 3 primary and a junction Pole is T constructed Refer to maintenance
Non-Outage | J.E.26.07.36121 | C001868216 | Orville Lee | Portmore | Completed | Load_570096 | Naggo Head - 610 | Jul 29, 2026 8:05am | Jul 29, 2026 8:05am | Jul 29, 2026 10:46am | Jul 29, 2026 4:38pm | Jul 29, 2026 4:49pm | Jul 29, 2026 5:06pm | Jul 29, 2026 5:15pm | Jul 29, 2026 5:15pm |  |  | Fair | No | Checks made and found pothead corroded Three pen union usedVoltage118v119v
Non-Outage | J.E.26.07.36161 | C001868214 | Orville Lee | Portmore | Completed | Load_255598 | Naggo Head - 510 | Jul 29, 2026 8:04am | Jul 29, 2026 8:05am | Jul 29, 2026 8:57am | Jul 29, 2026 8:57am | Jul 29, 2026 9:52am | Jul 29, 2026 10:45am | Jul 29, 2026 10:46am | Jul 29, 2026 10:46am |  |  | Fair | No | Premises found ok upon arrival 120v120v240v
Non-Outage | J.E.26.07.36231 | C001868213 | Orville Lee | Portmore | Completed | Load_238237 | Naggo Head - 610 | Jul 29, 2026 8:04am | Jul 29, 2026 8:05am | Jul 29, 2026 10:46am | Jul 30, 2026 11:08am | Jul 30, 2026 11:19am | Jul 30, 2026 11:39am | Jul 30, 2026 11:40am | Jul 30, 2026 11:40am | Fire |  | Fair | No | Costumer as reporting seeing sparks at junction connection
Non-Outage | J.E.26.07.36233 | C001868212 | Orville Lee | Portmore | Completed | Load_259464 | Naggo Head - 510 | Jul 29, 2026 8:04am | Jul 29, 2026 8:05am | Jul 29, 2026 10:46am | Jul 30, 2026 12:15pm | Jul 30, 2026 12:46pm | Jul 30, 2026 12:52pm | Jul 30, 2026 12:54pm | Jul 30, 2026 12:54pm |  |  | Fair | No | Premises closedVoltage 119v120v237vCustomer was advised to make a report when they are available
Non-Outage | J.E.26.07.34157 | C001868208 | Fredrick Hamilton | KSAS | Completed | Load_258580 | Duhaney - 310 | Jul 29, 2026 8:03am | Jul 29, 2026 8:05am | Jul 29, 2026 8:14am | Jul 29, 2026 9:47am | Jul 29, 2026 9:49am | Jul 29, 2026 10:53am | Jul 29, 2026 10:53am | Jul 29, 2026 10:53am |  |  | Fair | No | Corrosion detected at pole at pothead same was corrected 2 clamp and 2 penunion 122v obtained
Non-Outage | J.E.26.07.33570 | C001868196 | Fredrick Hamilton | KSAN | Completed | Load_251467 | Constant Spring - 210 | Jul 29, 2026 8:02am | Jul 29, 2026 8:03am | Jul 29, 2026 8:14am | Jul 30, 2026 2:29pm | Jul 30, 2026 2:30pm | Jul 30, 2026 2:31pm | Jul 30, 2026 2:31pm | Jul 30, 2026 2:31pm |  |  | Fair | No | Customer contacted and stated that issue was resolved previously Premises is ok
Non-Outage | J.E.26.07.33791 | C001868198 | Fredrick Hamilton | KSAN | Completed | Load_262126 | Constant Spring - 210 | Jul 29, 2026 8:02am | Jul 29, 2026 8:03am | Jul 29, 2026 8:14am | Jul 30, 2026 2:17pm | Jul 30, 2026 2:26pm | Jul 30, 2026 2:27pm | Jul 30, 2026 2:27pm | Jul 30, 2026 2:27pm |  |  | Fair | No | Please have emergency check transformer multiple customers affected by fluctuating voltage 233v/118v/117v obtained
Non-Outage | J.E.26.07.34016 | C001868200 | Fredrick Hamilton | KSAN | Completed | Load_243485 | Constant Spring - 210 | Jul 29, 2026 8:02am | Jul 29, 2026 8:03am | Jul 29, 2026 8:14am | Jul 30, 2026 1:10pm | Jul 30, 2026 1:12pm | Jul 30, 2026 1:16pm | Jul 30, 2026 1:16pm | Jul 30, 2026 1:16pm |  |  | Fair | No | Premises found ok at time of visit customer states that power was restored fully
Non-Outage | J.E.26.07.34486 | C001868199 | Fredrick Hamilton | KSAN | Completed | Load_264644 | Constant Spring - 210 | Jul 29, 2026 8:02am | Jul 29, 2026 8:03am | Jul 29, 2026 8:14am | Jul 29, 2026 12:44pm | Jul 29, 2026 12:52pm | Jul 29, 2026 1:15pm | Jul 29, 2026 1:15pm | Jul 29, 2026 1:15pm |  |  | Fair | No | Premises found locked at time of visit Customer not available
Non-Outage | J.E.26.07.35184 | C001868206 | Fredrick Hamilton | KSAS | Completed | Load_240844 | Duhaney - 310 | Jul 29, 2026 8:02am | Jul 29, 2026 8:05am | Jul 29, 2026 8:14am | Jul 29, 2026 8:49am | Jul 29, 2026 9:11am | Jul 29, 2026 9:42am | Jul 29, 2026 9:42am | Jul 29, 2026 9:42am |  |  | Fair | No | 116.9v corrosion detected at pothead same was corrected 2 penunion used
Non-Outage | J.E.26.07.35284 | C001868201 | Fredrick Hamilton | KSAN | Completed | Load_265159 | Constant Spring - 210 | Jul 29, 2026 8:02am | Jul 29, 2026 8:03am | Jul 29, 2026 8:14am | Jul 29, 2026 11:47am | Jul 29, 2026 11:53am | Jul 29, 2026 12:33pm | Jul 29, 2026 12:33pm | Jul 29, 2026 12:33pm |  |  | Fair | No | 2 clamps installed at pole 2 penunion installed at pothead 237v/118v/119v obtained
Non-Outage | J.E.26.07.35788 | C001868205 | Fredrick Hamilton | KSAS | Completed | Load_265194 | Duhaney - 310 | Jul 29, 2026 8:02am | Jul 29, 2026 8:05am | Jul 29, 2026 8:14am | Jul 29, 2026 10:53am | Jul 29, 2026 10:57am | Jul 29, 2026 11:44am | Jul 29, 2026 11:44am | Jul 29, 2026 11:44am |  |  | Fair | No | Corrosion detected at pole 170v obtained same was corrected 237v117v/118v now obtained 2 penunion 2 clamps used
Non-Outage | J.E.26.07.35905 | C001868203 | Fredrick Hamilton | KSAS | Completed | Load_246988 | Duhaney - 310 | Jul 29, 2026 8:02am | Jul 29, 2026 8:05am | Jul 29, 2026 8:14am | Jul 29, 2026 1:49pm | Jul 29, 2026 1:57pm | Jul 29, 2026 2:25pm | Jul 29, 2026 2:25pm | Jul 29, 2026 2:25pm |  |  | Fair | No | Customers meter found disconnected a CRR was contacted and supply was restored Premises is now ok
Outage | J.E.26.07.36345 | C001868194 | Hartley Chin | Clarendon | Completed | Load_258028 | Monymusk - 210 | Jul 29, 2026 8:00am | Jul 29, 2026 8:00am | Jul 29, 2026 8:55am | Jul 29, 2026 3:42pm | Jul 29, 2026 3:42pm | Jul 29, 2026 3:53pm | Jul 29, 2026 3:53pm | Jul 29, 2026 3:53pm |  |  | SevereWind | No | Found blown 3 amp fuse on 25 KVA transformer @ pole # 0129637 line patrolled and found okay , transformer refused …
Outage | J.E.26.07.35137 | C001868187 | Selvin White | St.Elizabeth | Completed | Load_247271 | Maggotty - 110 | Jul 29, 2026 7:58am | Jul 29, 2026 7:58am | Jul 29, 2026 9:55am | Jul 29, 2026 9:55am | Jul 29, 2026 10:24am | Jul 29, 2026 10:31am | Jul 29, 2026 10:31am | Jul 29, 2026 10:31am |  |  | Fair | No | Supply found okay at the time of visit. Customer says problem was resolved from last night.
Outage | J.E.26.07.36085 | C001868191 | Selvin White | St.Elizabeth | Completed | Load_259083 | Maggotty - 110 | Jul 29, 2026 7:58am | Jul 29, 2026 7:58am | Jul 29, 2026 8:19am | Jul 29, 2026 8:20am | Jul 29, 2026 8:42am | Jul 29, 2026 9:28am | Jul 29, 2026 9:28am | Jul 29, 2026 9:28am |  |  | Fair | No | Meter #297247 was found in customer’s meter socket and was found to be disconnected for non payment. Escalation department was contacted and said the field service department would visit the location to verify and rectify the issue.
Outage | J.E.26.07.36178 | C001868192 | Richard Watson | St.Elizabeth | Completed | Load_248804 | Maggotty - 110 | Jul 29, 2026 7:58am | Jul 29, 2026 3:54pm | Jul 29, 2026 9:31pm | Jul 29, 2026 9:31pm | Jul 29, 2026 9:36pm | Jul 29, 2026 9:47pm | Jul 29, 2026 9:48pm | Jul 29, 2026 9:48pm |  |  | Fair | No | Escalation department contacted and they stated that the meter is on however the customer is still without supply, please refer to field service department for further checks.
Outage | J.E.26.07.36319 | C001868193 | Richard Watson | St.Elizabeth | Completed | Load_292945 | Maggotty - 110 | Jul 29, 2026 7:58am | Jul 29, 2026 3:54pm | Jul 29, 2026 4:53pm | Jul 29, 2026 4:53pm | Jul 29, 2026 5:11pm | Jul 29, 2026 5:42pm | Jul 29, 2026 5:49pm | Jul 29, 2026 5:49pm |  |  | Fair | No | Replace blown 10amp junction fuse no pole#, also replace 1amp fuse for 10kva transformer no pole#, after completing patrol no visible fault found, supply restored to affected area.
Non-Outage | J.E.26.06.30919 | C001868183 | Odeanie Davis | KSAS | Completed | Load_251977 | Hunts Bay - 710 | Jul 29, 2026 7:57am | Jul 29, 2026 7:58am | Jul 29, 2026 8:59am | Jul 29, 2026 10:40am | Jul 29, 2026 10:40am | Jul 29, 2026 10:56am | Jul 29, 2026 10:41am | Jul 29, 2026 10:41am |  |  | Fair | No | Customer stated that issue was resolved by Jps
Non-Outage | J.E.26.07.00180 | C001868180 | Odeanie Davis | KSAS | Completed | Load_290138 | Greenwich - 710 | Jul 29, 2026 7:57am | Jul 29, 2026 7:58am | Jul 29, 2026 8:59am | Jul 29, 2026 9:40am | Jul 29, 2026 9:43am | Jul 29, 2026 10:30am | Jul 29, 2026 10:30am | Jul 29, 2026 10:30am |  |  | Fair | No | 118v/0V at arrival, open circuit at secondary corrected, 4 penn union, 119v/119v & 238v after correction
Non-Outage | J.E.26.07.02228 | C001868181 | Odeanie Davis | KSAS | Completed | Load_243805 | Greenwich - 710 | Jul 29, 2026 7:57am | Jul 29, 2026 7:58am | Jul 29, 2026 8:59am | Jul 29, 2026 10:31am | Jul 29, 2026 10:33am | Jul 29, 2026 10:37am | Jul 29, 2026 10:34am | Jul 29, 2026 10:34am |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.07.14766 | C001868182 | Odeanie Davis | KSAS | Completed | Load_241818 | Greenwich - 410 | Jul 29, 2026 7:57am | Jul 29, 2026 7:58am | Jul 29, 2026 8:59am | Jul 29, 2026 10:57am | Jul 29, 2026 11:00am | Jul 29, 2026 11:15am | Jul 29, 2026 11:12am | Jul 29, 2026 11:12am |  |  | Fair | No | Meter found burnt and defective on one side, customer was advised to contact their electrician to rectify issue on their end, 115v/116v & 231v at location, 17.6 amp & 29.3 amp
Non-Outage | J.E.26.07.34750 | C001868184 | Odeanie Davis | KSAS | Completed | Load_293236 | Hunts Bay - 310 | Jul 29, 2026 7:57am | Jul 29, 2026 7:58am | Jul 29, 2026 8:59am | Jul 29, 2026 9:05am | Jul 29, 2026 9:05am | Jul 29, 2026 9:21am | Jul 29, 2026 9:21am | Jul 29, 2026 9:21am |  |  | Fair | No | 104v/132v at arrival, open neutral on customer line corrected, 1 one bolt clamp, 119v/118v & 237v after correction
Outage | J.E.26.07.36346 | C001868185 | Selvin White | St.Elizabeth | Completed | Load_251307 | Maggotty - 110 | Jul 29, 2026 7:57am | Jul 29, 2026 7:58am | Jul 29, 2026 10:31am | Jul 29, 2026 10:31am | Jul 29, 2026 11:23am | Jul 29, 2026 2:05pm | Jul 29, 2026 2:15pm | Jul 29, 2026 2:15pm |  |  | SevereWind | No | Install drop leads and also install approximately 30 ft of number six triplex service wire to supply customer. Also energized 10 KVA transformer that supply 3 customers. Supply restored.
Non-Outage | J.E.26.06.39068 | C001868179 | Odeanie Davis | KSAS | Completed | Load_249339 | Greenwich - 410 | Jul 29, 2026 7:56am | Jul 29, 2026 7:58am | Jul 29, 2026 9:00am | Jul 29, 2026 1:57pm | Jul 29, 2026 1:57pm | Jul 29, 2026 2:46pm | Jul 29, 2026 2:46pm | Jul 29, 2026 2:46pm |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.07.10572 | C001868174 | Odeanie Davis | KSAS | Completed | Load_262483 | Cane River - 410 | Jul 29, 2026 7:56am | Jul 29, 2026 7:58am | Jul 29, 2026 11:20am | Jul 29, 2026 1:21pm | Jul 29, 2026 1:56pm | Jul 29, 2026 2:04pm | Jul 29, 2026 1:57pm | Jul 29, 2026 1:57pm |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.07.12337 | C001868176 | Odeanie Davis | KSAS | Completed | Load_267551 | Cane River - 410 | Jul 29, 2026 7:56am | Jul 29, 2026 7:58am | Jul 29, 2026 11:20am | Jul 29, 2026 11:20am | Jul 29, 2026 11:22am | Jul 29, 2026 11:28am | Jul 29, 2026 11:25am | Jul 29, 2026 11:25am |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.07.12497 | C001868177 | Odeanie Davis | KSAS | Completed | Load_254152 | Cane River - 410 | Jul 29, 2026 7:56am | Jul 29, 2026 7:58am | Jul 29, 2026 11:20am | Jul 29, 2026 11:31am | Jul 29, 2026 11:31am | Jul 29, 2026 11:59am | Jul 29, 2026 11:57am | Jul 29, 2026 11:57am |  |  | Fair | No | 117v/122v at arrival, open neutral at secondary corrected, 1 one bolt clamp, 119v/120v & 240v after correction.
Non-Outage | J.E.26.07.13049 | C001868175 | Odeanie Davis | KSAS | Completed | Load_259334 | Cane River - 610 | Jul 29, 2026 7:56am | Jul 29, 2026 7:58am | Jul 29, 2026 11:20am | Jul 29, 2026 12:01pm | Jul 29, 2026 12:27pm | Jul 29, 2026 12:36pm | Jul 29, 2026 1:05pm | Jul 29, 2026 1:05pm |  |  | Fair | No | 117v/0V at arrival, open circuit at secondary corrected, 2 penn union & 2 one bolt clamps, 118v/117v & 236v after correction.
Non-Outage | J.E.26.07.35007 | C001868178 | Edward Royal | KSAS | Completed | Load_294227 | Greenwich - 310 | Jul 29, 2026 7:56am | Jul 29, 2026 7:58am | Jul 29, 2026 3:37pm | Jul 29, 2026 3:39pm | Jul 29, 2026 3:39pm | Jul 29, 2026 3:40pm | Jul 29, 2026 3:40pm | Jul 29, 2026 3:40pm |  |  | Fair | No | Premises found ok related to outage
Non-Outage | J.E.26.07.35860 | C001868172 | Hopeton Henry | St.Thomas | Completed | Load_251945 | Good Year - 110 | Jul 29, 2026 7:54am | Jul 29, 2026 7:55am | Jul 29, 2026 8:55am | Jul 29, 2026 12:34pm | Jul 29, 2026 1:41pm | Jul 29, 2026 2:01pm | Jul 29, 2026 2:02pm | Jul 29, 2026 2:02pm |  |  | Fair | No | Found defective 10 kva transformer. Pole 037000 Customer left single phasing
Non-Outage | J.E.26.07.36339 | C001868173 | Hopeton Henry | St.Thomas | Completed | Load_249913 | Good Year - 110 | Jul 29, 2026 7:54am | Jul 29, 2026 7:55am | Jul 29, 2026 8:55am | Jul 29, 2026 10:00am | Jul 29, 2026 11:00am | Jul 29, 2026 11:58am | Jul 29, 2026 11:59am | Jul 29, 2026 11:59am |  |  | Fair | No | Found bang conductor, cut tree from secondary reading 110-117-228 v
Outage | J.E.26.07.35099 | C001868171 | Oshane Warren | Westmoreland | Completed | Load_248237 | Paradise - 310 | Jul 29, 2026 7:54am | Jul 29, 2026 7:54am | Jul 29, 2026 11:42am | Jul 29, 2026 11:43am | Jul 29, 2026 1:29pm | Jul 29, 2026 2:08pm | Jul 29, 2026 2:09pm | Jul 29, 2026 2:09pm |  |  | Fair | No | Reconnect back service wire at pathead and secondary line used 3service connector and used 100 ft number 6 twisted wire
Non-Outage | J.E.26.07.35845 | C001868170 | Michael Paterson | null | Completed | null | null | Jul 29, 2026 7:53am | Jul 29, 2026 7:56am | Jul 29, 2026 8:49am | Jul 29, 2026 8:49am | Jul 29, 2026 9:44am | Jul 29, 2026 9:44am | Jul 29, 2026 9:45am | Jul 29, 2026 9:45am |  |  | Fair | No | Customer confirm ok via phone call.
Non-Outage | J.E.26.07.36337 | C001868165 | Wan Carlos Scarlett | Portmore | Completed | Load_1004106 | Naggo Head - 510 | Jul 29, 2026 7:53am | Jul 29, 2026 7:53am | Jul 29, 2026 10:09am | Jul 29, 2026 10:09am | Jul 29, 2026 10:38am | Jul 29, 2026 10:57am | Jul 29, 2026 11:07am | Jul 29, 2026 11:07am | LowHangingWires |  | Fair | No | Found single phase primary line dislodged from out from insulator return primary line back in to insulator isolate and close single phase primary line junction no pole # was found
Outage | J.E.26.07.36124 | C001868169 | Oshane Warren | Westmoreland | Completed | Load_265538 | Paradise - 310 | Jul 29, 2026 7:53am | Jul 29, 2026 7:54am | Jul 29, 2026 11:42am | Jul 29, 2026 11:42am | Jul 29, 2026 11:42am | Jul 29, 2026 11:42am | Jul 29, 2026 11:43am | Jul 29, 2026 11:43am |  |  | Fair | No | Customer states that the power was restored
Outage | J.E.26.07.36150 | C001868164 | Fitzroy Turner | KSAS | Completed | Load_238088 | Hunts Bay - 510 | Jul 29, 2026 7:52am | Jul 29, 2026 3:45pm | Jul 29, 2026 3:50pm | Jul 29, 2026 6:06pm | Jul 29, 2026 6:21pm | Jul 29, 2026 6:22pm | Jul 29, 2026 6:22pm | Jul 29, 2026 6:22pm |  |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.07.36209 | C001868163 | Rayon Foster | Hanover | Completed | Load_292318 | Orange Bay - 310 | Jul 29, 2026 7:52am | Jul 29, 2026 7:55am | Jul 29, 2026 2:03pm | Jul 29, 2026 2:03pm | Jul 29, 2026 3:44pm | Jul 29, 2026 9:34am | Jul 29, 2026 3:47pm | Jul 29, 2026 3:47pm |  |  | Fair | No | Found working ok when arrived on location power was in the area
Non-Outage | J.E.26.07.35862 | C001868162 | Rayon Foster | Hanover | Completed | Load_573351 | Orange Bay - 310 | Jul 29, 2026 7:50am | Jul 29, 2026 7:55am | Jul 29, 2026 8:34am | Jul 29, 2026 8:34am | Jul 29, 2026 9:40am | Jul 29, 2026 11:10am | Jul 29, 2026 11:11am | Jul 29, 2026 11:11am |  |  | Fair | No | Open one 25 kva transformer to do repair corroded joints on jps pole using 9 one bolt clamps and reclose voltage after closing 114/115AB229 volts
Outage | J.E.26.07.36169 | C001868161 | Edward Royal | KSAN | Completed | Load_255789 | Washington Blvd - 310 | Jul 29, 2026 7:50am | Jul 29, 2026 7:51am | Jul 29, 2026 10:40am | Jul 29, 2026 10:42am | Jul 29, 2026 10:42am | Jul 29, 2026 12:30pm | Jul 29, 2026 12:32pm | Jul 29, 2026 12:32pm |  |  | Fair | No | Spliced and reconnected secondary phase using 40ft 2 north conductor 6 single bolt clamp replaced transformer drop lead using 5 ampack
Non-Outage | J.E.26.07.36110 | C001868156 | Derrick Dawkins | St.James | Completed | Load_268752 | Bogue - 610 | Jul 29, 2026 7:46am | Jul 29, 2026 7:49am | Jul 29, 2026 11:37am | Jul 29, 2026 11:44am | Jul 29, 2026 11:52am | Jul 29, 2026 12:05pm | Jul 29, 2026 12:11pm | Jul 29, 2026 12:11pm |  |  | Fair | No | Found customer meter socket defective advised customer to get an electrician voltage 119/119=239
Non-Outage | J.E.26.07.35865 | C001868155 | Horace Malcolm | null | Completed | null | null | Jul 29, 2026 7:43am | Jul 29, 2026 7:43am | Jul 29, 2026 7:56am | Jul 29, 2026 7:56am | Jul 29, 2026 7:56am | Jul 29, 2026 7:57am | Jul 29, 2026 7:57am | Jul 29, 2026 7:57am |  |  | Fair | No | This call belongs to trelawny
Non-Outage | J.E.26.07.35998 | C001868153 | Derrick Dawkins | null | Completed | null | null | Jul 29, 2026 7:43am | Jul 29, 2026 7:44am | Jul 29, 2026 10:20am | Jul 29, 2026 10:40am | Jul 29, 2026 11:02am | Jul 29, 2026 11:02am | Jul 29, 2026 11:04am | Jul 29, 2026 11:04am |  |  | Fair | No | Only customer without electricity from the en box
Outage | J.E.26.07.36278 | C001868154 | Derrick Dawkins | St.James | Completed | Load_567780 | Bogue - 610 | Jul 29, 2026 7:43am | Jul 29, 2026 7:44am | Jul 29, 2026 11:32am | Jul 29, 2026 2:06pm | Jul 29, 2026 2:06pm | Jul 29, 2026 2:07pm | Jul 29, 2026 2:07pm | Jul 29, 2026 2:07pm |  |  | Fair | No | Checked and found ok
Non-Outage | J.E.26.07.34641 | C001868149 | Michael Christian | St.James | Completed | Load_301719 | Bogue - 310 | Jul 29, 2026 7:41am | Jul 29, 2026 7:41am | Jul 29, 2026 7:56am | Jul 29, 2026 7:56am | Jul 29, 2026 9:13am | Jul 29, 2026 9:23am | Jul 29, 2026 9:23am | Jul 29, 2026 9:23am |  |  | Fair | No | EN box send to field service
Non-Outage | J.E.26.07.35242 | C001868150 | Derrick Dawkins | St.James | Completed | Load_292048 | Bogue - 310 | Jul 29, 2026 7:41am | Jul 29, 2026 7:52am | Jul 29, 2026 9:21am | Jul 29, 2026 11:04am | Jul 29, 2026 11:04am | Jul 29, 2026 11:31am | Jul 29, 2026 11:31am | Jul 29, 2026 11:31am |  |  | Fair | No | Only customer out the en box single phasing refer back to kadian field service
Outage | J.E.26.07.35541 | C001868148 | Horace Malcolm | St.James | Completed | Load_268569 | Bogue - 310 | Jul 29, 2026 7:39am | Jul 29, 2026 7:53am | Jul 29, 2026 7:57am | Jul 29, 2026 7:57am | Jul 29, 2026 7:57am | Jul 29, 2026 7:58am | Jul 29, 2026 7:58am | Jul 29, 2026 7:58am |  |  | Fair | No | This call belongs to trelawny
Outage | J.E.26.07.34082 | C001868146 | Edward Royal | KSAS | Completed | Load_260949 | Three Miles - 410 | Jul 29, 2026 7:38am | Jul 29, 2026 7:39am | Jul 29, 2026 10:34am | Jul 29, 2026 10:34am | Jul 29, 2026 10:34am | Jul 10, 2026 9:23am | Jul 29, 2026 10:39am | Jul 29, 2026 10:39am |  |  | Fair | No | Power was restored by escalation
Outage | J.E.26.07.34884 | C001868147 | Edward Royal | KSAS | Completed | Load_293205 | Three Miles - 410 | Jul 29, 2026 7:38am | Jul 29, 2026 7:39am | Jul 29, 2026 2:33pm | Jul 29, 2026 2:33pm | Jul 29, 2026 2:33pm | Jul 29, 2026 2:47pm | Jul 29, 2026 2:48pm | Jul 29, 2026 2:48pm |  |  | Fair | No | Meter need to be check meter not responding reffered to field service
Outage | J.E.26.07.36183 | C001868141 | Donald Cunningham | St.Catherine | Completed | Load_288492 | Rhodens Pen - 210 | Jul 29, 2026 7:37am | Jul 29, 2026 7:38am | Jul 29, 2026 8:01am | Jul 29, 2026 8:01am | Jul 29, 2026 9:29am | Jul 29, 2026 9:47am | Jul 29, 2026 9:48am | Jul 29, 2026 9:48am |  |  | Fair | No | Burnt up fuse holder replace with 2 amp fuse for 15 kva transformer
Outage | J.E.26.07.35776 | C001868140 | Christopher Edwards | KSAN | Completed | Load_260676 | Constant Spring - 410 | Jul 29, 2026 7:36am | Jul 29, 2026 7:39am | Jul 29, 2026 10:03am | Jul 29, 2026 10:58am | Jul 29, 2026 11:47am | Jul 29, 2026 12:19pm | Jul 29, 2026 12:28pm | Jul 29, 2026 12:28pm |  |  | Fair | No | Clear bird nest off transformer Refuse blown 15 kva transformer Using (1)2 amps
Outage | J.E.26.07.36215 | C001868139 | Wan Carlos Scarlett | St.Catherine | Completed | Load_259973 | Twickenham - 210 | Jul 29, 2026 7:35am | Jul 29, 2026 7:51am | Jul 29, 2026 8:02am | Jul 29, 2026 8:02am | Jul 29, 2026 9:12am | Jul 29, 2026 10:06am | Jul 29, 2026 10:09am | Jul 29, 2026 10:09am |  |  | Fair | No | Reach on location been calling customer but got no answer premises closed reading at pole readings 116 116 232
Non-Outage | J.E.26.07.32671 | C001868134 | Horace Malcolm | St.James | Completed | Load_259452 | Queens Drive - 310 | Jul 29, 2026 7:34am | Jul 29, 2026 7:34am | Jul 29, 2026 12:09pm | Jul 29, 2026 12:09pm | Jul 29, 2026 1:17pm | Jul 29, 2026 1:28pm | Jul 29, 2026 1:29pm | Jul 29, 2026 1:29pm |  |  | Fair | No | Check and found premises ok voltage 112-115-227
Non-Outage | J.E.26.07.35473 | C001868136 | Horace Malcolm | St.James | Completed | Load_267952 | Rose Hall - 210 | Jul 29, 2026 7:34am | Jul 29, 2026 7:34am | Jul 29, 2026 1:32pm | Jul 29, 2026 1:32pm | Jul 29, 2026 1:32pm | Jul 29, 2026 1:34pm | Jul 29, 2026 1:34pm | Jul 29, 2026 1:34pm |  |  | Fair | No | Unable to locate customer or premises from directions given multiple calls to customer unavailable
Non-Outage | J.E.26.07.35593 | C001868135 | Horace Malcolm | St.James | Completed | Load_254051 | Queens Drive - 310 | Jul 29, 2026 7:34am | Jul 29, 2026 7:34am | Jul 29, 2026 10:55am | Jul 29, 2026 10:55am | Jul 29, 2026 11:42am | Jul 29, 2026 12:08pm | Jul 29, 2026 12:08pm | Jul 29, 2026 12:08pm |  |  | Fair | No | Isolate one 25kva transformer to clean transformer drop leads voltage 115-116-231
Non-Outage | J.E.26.07.35871 | C001868137 | Horace Malcolm | St.James | Completed | Load_248812 | Queens Drive - 310 | Jul 29, 2026 7:34am | Jul 29, 2026 7:34am | Jul 29, 2026 8:10am | Jul 29, 2026 8:10am | Jul 29, 2026 9:00am | Jul 29, 2026 9:25am | Jul 29, 2026 9:25am | Jul 29, 2026 9:25am |  |  | Fair | No | Clean and remake joints at customer used 2clamps voltage 115-116-231
Non-Outage | J.E.26.07.36177 | C001868131 | Michael Paterson | null | Completed | null | null | Jul 29, 2026 7:32am | Jul 29, 2026 7:45am | Jul 29, 2026 9:52am | Jul 29, 2026 9:52am | Jul 29, 2026 9:52am | Jul 29, 2026 9:53am | Jul 29, 2026 9:54am | Jul 29, 2026 9:54am |  |  | Fair | No | Customer disconnected for overdue bill balance.
Outage | J.E.26.07.35892 | C001868128 | Michael Paterson | Westmoreland | Completed | Load_257353 | Paradise - 110 | Jul 29, 2026 7:31am | Jul 29, 2026 7:43am | Jul 29, 2026 9:43am | Jul 29, 2026 9:46am | Jul 29, 2026 9:46am | Jul 29, 2026 9:46am | Jul 29, 2026 9:47am | Jul 29, 2026 9:47am |  |  | Fair | No | Customer confirm ok via phone call.
Outage | J.E.26.07.35978 | C001868129 | Michael Paterson | Westmoreland | Completed | Load_254866 | Paradise - 210 | Jul 29, 2026 7:31am | Jul 29, 2026 7:43am | Jul 29, 2026 10:24am | Jul 29, 2026 10:24am | Jul 29, 2026 2:31pm | Jul 29, 2026 2:32pm | Jul 29, 2026 2:35pm | Jul 29, 2026 2:35pm |  |  | Fair | No | Top on connection found at location, customer now connect directly to main, connection done using approximately 80ft #6 triplex, three linkets and three clamps, voltage readings 107v, 108v, 215v.
Outage | J.E.26.07.36125 | C001868130 | Michael Paterson | Westmoreland | Completed | Load_261865 | Paradise - 110 | Jul 29, 2026 7:31am | Jul 29, 2026 7:43am | Jul 29, 2026 2:35pm | Jul 29, 2026 2:35pm | Jul 29, 2026 5:19pm | Jul 29, 2026 5:22pm | Jul 29, 2026 5:22pm | Jul 29, 2026 5:22pm |  |  | Fair | No | Check and found premises ok, customer has internal problem, advise to fix,voltage readings, 109v,115v, 224v,
Outage | J.E.26.07.36148 | C001868122 | Hartley Chin | Clarendon | Completed | Load_237758 | May Pen - 110 | Jul 29, 2026 7:25am | Jul 30, 2026 9:16am | Jul 30, 2026 10:13am | Jul 30, 2026 10:13am | Jul 30, 2026 12:06pm | Jul 30, 2026 12:26pm | Jul 30, 2026 12:28pm | Jul 30, 2026 12:28pm |  |  | SevereWind | No | Found okay … voltage read 113v , 111v ..
Outage | J.E.26.07.36093 | C001868119 | Hartley Chin | Clarendon | Completed | Load_244719 | Parnassus - 210 | Jul 29, 2026 7:22am | Jul 29, 2026 7:23am | Jul 29, 2026 5:50pm | Jul 29, 2026 5:50pm | Jul 29, 2026 6:49pm | Jul 29, 2026 7:23pm | Jul 29, 2026 7:24pm | Jul 29, 2026 7:24pm | TreeContact |  | Fair | No | Prem not found … unable to contact customer upon reaching Reid’s Mocho …area patrolled and found okay … unable to find customer meter …
Outage | J.E.26.07.36214 | C001868120 | Hartley Chin | Clarendon | Completed | Load_1000625 | May Pen - 210 | Jul 29, 2026 7:22am | Jul 29, 2026 7:23am | Jul 29, 2026 9:31am | Jul 29, 2026 12:03pm | Jul 29, 2026 12:03pm | Jul 29, 2026 12:03pm | Jul 29, 2026 12:03pm | Jul 29, 2026 12:03pm |  |  | Fair | No | Call related to job # 36237 ..
Outage | J.E.26.07.36237 | C001868121 | Hartley Chin | Clarendon | Completed | Load_572195 | Parnassus - 310 | Jul 29, 2026 7:22am | Jul 29, 2026 7:23am | Jul 29, 2026 9:31am | Jul 29, 2026 10:40am | Jul 29, 2026 10:41am | Jul 29, 2026 11:49am | Jul 29, 2026 12:02pm | Jul 29, 2026 12:02pm |  |  | Fair | No | Found blown 20 amp junction fuse @ pole # 617220 line patrolled and found blown 8 amp junction fuse , line patrolled and found blown 2 amp fuse on 15 KVA transformer @ pole # 0107932 on throat transformer supplying HX 26552518 … junctions refused , transformer fuse blew after refusing … Ref to field service !!!! 15KVA @ pole # 0107932 is still without service..
Non-Outage | J.E.26.07.35821 | C001868117 | Shamour Haughton | St.James | Completed | Load_260722 | Queens Drive - 710 | Jul 29, 2026 6:38am | Jul 29, 2026 6:38am | Jul 29, 2026 7:37am | Jul 29, 2026 7:37am | Jul 29, 2026 7:37am | Jul 29, 2026 7:37am | Jul 29, 2026 7:39am | Jul 29, 2026 7:39am |  |  | Fair | No | Found customer pothead corroded, clean and remake joint at pothead, voltage left 117,117,235
Outage | J.E.26.07.36169 | C001868088 | Christopher Edwards | KSAN | Completed | Load_255789 | Washington Blvd - 310 | Jul 29, 2026 12:16am | Jul 29, 2026 12:24am | Jul 29, 2026 12:37am | Jul 29, 2026 12:57am | Jul 29, 2026 12:57am | Jul 29, 2026 4:33am | Jul 29, 2026 4:36am | Jul 29, 2026 4:36am |  |  | Fair | No | Broken open secondary phaseUnable to splice and retention broken wireDue to vehicles park directly under pole and also resident build a shop around the pole50 kva transformer is isolated Required daylight attention
Outage | J.E.26.07.32605 | C001868086 | Raymond Lewis | St.Ann | Completed | Load_412973 | Cardiff Hall - 210 | Jul 28, 2026 11:10pm | Jul 28, 2026 11:10pm | Jul 28, 2026 11:44pm | Jul 28, 2026 11:44pm | Jul 29, 2026 1:06am | Jul 29, 2026 1:12pm | Jul 29, 2026 1:14am | Jul 29, 2026 1:14am | Fire |  | Fair | No | Trelawny call also need Jamaican number
Non-Outage | J.E.26.07.36130 | C001868085 | Shamour Haughton | St.James | Completed | Load_302735 | Queens Drive - 310 | Jul 28, 2026 11:08pm | Jul 28, 2026 11:08pm | Jul 29, 2026 3:29am | Jul 29, 2026 3:29am | Jul 29, 2026 3:47am | Jul 29, 2026 4:18am | Jul 29, 2026 4:21am | Jul 29, 2026 4:21am |  |  | Fair | No | Found 1,40amp padmount fuse blown refuse 100kva, refuse 40amp
Non-Outage | J.E.26.07.34183 | C001868083 | Delano Gayle | null | Completed | null | null | Jul 28, 2026 11:05pm | Jul 28, 2026 11:06pm | Jul 29, 2026 4:26am | Jul 29, 2026 4:26am | Jul 29, 2026 5:03am | Jul 29, 2026 5:04am | Jul 29, 2026 5:04am | Jul 29, 2026 5:04am | BrokenWire |  | Fair | No | Premises not found no answer from customer phone
Outage | J.E.26.07.35507 | C001868082 | Delano Gayle | St.Catherine | Completed | Load_250865 | Rhodens Pen - 210 | Jul 28, 2026 11:05pm | Jul 28, 2026 11:06pm | Jul 29, 2026 3:50am | Jul 29, 2026 3:50am | Jul 29, 2026 4:11am | Jul 29, 2026 4:24am | Jul 29, 2026 4:25am | Jul 29, 2026 4:25am | BrokenWire |  | Fair | No | Premises found okay, area patrolled and found okay no fire seen
Outage | J.E.26.07.35891 | C001868081 | Delano Gayle | Portmore | Completed | Load_268319 | Naggo Head - 610 | Jul 28, 2026 11:05pm | Jul 28, 2026 11:06pm | Jul 29, 2026 5:04am | Jul 29, 2026 5:04am | Jul 29, 2026 5:05am | Jul 29, 2026 5:06am | Jul 29, 2026 5:06am | Jul 29, 2026 5:06am | BrokenWire |  | Fair | No | Premises locked, area found okay no broken wire seen
Outage | J.E.26.07.36126 | C001868084 | Christopher Edwards | KSAN | Completed | Load_241807 | Constant Spring - 410 | Jul 28, 2026 11:05pm | Jul 28, 2026 11:06pm | Jul 29, 2026 6:40am | Jul 29, 2026 6:40am | Jul 29, 2026 7:51am | Jul 29, 2026 8:04am | Jul 29, 2026 8:05am | Jul 29, 2026 8:05am | BrokenWire |  | Fair | No | Check and found okNo broken wires found in areaSupply is in the area
Non-Outage | J.E.26.07.33714 | C001868080 | Christopher Edwards | null | Completed | null | null | Jul 28, 2026 11:04pm | Jul 28, 2026 11:04pm | Jul 28, 2026 11:10pm | Jul 28, 2026 11:22pm | Jul 28, 2026 11:22pm | Jul 28, 2026 11:30pm | Jul 28, 2026 11:31pm | Jul 28, 2026 11:31pm | Fire |  | Fair | No | Customer was contacted and stated that the issue was resolved
Outage | J.E.26.07.35249 | C001868074 | Christopher Edwards | KSAS | Completed | Load_267072 | Duhaney - 310 | Jul 28, 2026 11:03pm | Jul 28, 2026 11:04pm | Jul 28, 2026 11:47pm | Jul 28, 2026 11:47pm | Jul 28, 2026 11:47pm | Jul 29, 2026 12:00am | Jul 29, 2026 12:01am | Jul 29, 2026 12:01am |  |  | Fair | No | Premises closedUnable to reach customer by phone
Outage | J.E.26.07.35250 | C001868073 | Christopher Edwards | KSAS | Completed | Load_249073 | Duhaney - 410 | Jul 28, 2026 11:03pm | Jul 28, 2026 11:04pm | Jul 29, 2026 4:48am | Jul 29, 2026 4:48am | Jul 29, 2026 4:48am | Jul 29, 2026 4:55am | Jul 29, 2026 4:56am | Jul 29, 2026 4:56am |  |  | Fair | No | Check and found okSupply is in the area
Outage | J.E.26.07.35295 | C001868076 | Elvis Trowers | KSAS | Completed | Load_250509 | Greenwich - 710 | Jul 28, 2026 11:03pm | Jul 29, 2026 7:40am | Jul 29, 2026 9:37am | Jul 29, 2026 9:37am | Jul 29, 2026 10:23am | Jul 29, 2026 11:01am | Jul 29, 2026 11:02am | Jul 29, 2026 11:02am |  |  | Fair | Yes | Customer was found having fluctuating voltage when checked and corroded joints was found at pat head where 3 one bolt clamps was used, voltage when checked was left at 118+118=236 volt.
Outage | J.E.26.07.35774 | C001868075 | Christopher Edwards | KSAN | Completed | Load_243339 | Washington Blvd - 710 | Jul 28, 2026 11:03pm | Jul 28, 2026 11:04pm | Jul 28, 2026 11:35pm | Jul 28, 2026 11:35pm | Jul 28, 2026 11:35pm | Jul 28, 2026 11:46pm | Jul 28, 2026 11:46pm | Jul 28, 2026 11:46pm |  |  | Fair | No | Customer was contacted and said that the issue was resolved
Outage | J.E.26.07.35799 | C001868077 | Christopher Edwards | KSAS | Completed | Load_1002674 | Cane River - 410 | Jul 28, 2026 11:03pm | Jul 28, 2026 11:04pm | Jul 28, 2026 11:19pm | Jul 29, 2026 12:01am | Jul 29, 2026 12:01am | Jul 29, 2026 12:37am | Jul 29, 2026 12:37am | Jul 29, 2026 12:37am |  |  | Fair | No | Check and found okSupply is at the premises
Outage | J.E.26.07.36090 | C001868070 | Delano Gayle | St.Catherine | Completed | Load_254199 | Tredegar - 210 | Jul 28, 2026 10:45pm | Jul 28, 2026 10:47pm | Jul 28, 2026 11:18pm | Jul 28, 2026 11:18pm | Jul 29, 2026 3:36am | Jul 29, 2026 3:45am | Jul 29, 2026 3:46am | Jul 29, 2026 3:46am | Fire |  | Fair | No | Defective 10kva hexing transformer, transformer spraying oil, send call to maintenance/ field services to replace
Outage | J.E.26.07.36101 | C001868071 | Shamour Haughton | St.James | Completed | Load_261827 | Queens Drive - 710 | Jul 28, 2026 10:45pm | Jul 28, 2026 11:00pm | Jul 29, 2026 1:12am | Jul 29, 2026 1:12am | Jul 29, 2026 1:19am | Jul 29, 2026 1:20am | Jul 29, 2026 1:23am | Jul 29, 2026 1:23am |  |  | Fair | No | Found 1,100kva fuse blown refuse 100kva use 1,10amp fuse
Outage | J.E.26.07.35502 | C001868065 | Edward Royal | KSAN | Completed | Load_574897 | Washington Blvd - 610 | Jul 28, 2026 10:08pm | Jul 28, 2026 10:13pm | Jul 28, 2026 10:23pm | Jul 28, 2026 10:23pm | Jul 28, 2026 10:23pm | Jul 28, 2026 10:26pm | Jul 28, 2026 10:26pm | Jul 28, 2026 10:26pm |  |  | Fair | No | Remove tree from primary line and Replaced 4 junction fuse 2 30A 215A fuse
Outage | J.E.26.07.35155 | C001868064 | Moses Elliston | St.Catherine | Completed | Load_266236 | Tredegar - 210 | Jul 28, 2026 10:07pm | Jul 28, 2026 10:07pm | Jul 29, 2026 11:17am | Jul 29, 2026 11:17am | Jul 29, 2026 11:17am | Jul 29, 2026 11:17am | Jul 29, 2026 11:18am | Jul 29, 2026 11:18am |  |  | Fair | No | Supply ok at premises
Non-Outage | J.E.26.07.36100 | C001868063 | Marlon Brown | Trelawny | Completed | Load_292409 | Greenwood - 210 | Jul 28, 2026 9:50pm | Jul 28, 2026 9:51pm | Jul 28, 2026 9:54pm | Jul 28, 2026 9:55pm | Jul 28, 2026 10:39pm | Jul 28, 2026 11:26pm | Jul 28, 2026 11:29pm | Jul 28, 2026 11:29pm |  |  | Fair | No | Isolated 50kva transformer to repair drop lead, use 2 pg clamps and 8ft 2/0 cu Voltage found 90Voltage leaving 1t9/109=232.
Outage | J.E.26.07.36040 | C001868059 | Nickolas Rodriques | St.Catherine | Completed | Load_265602 | Tredegar - 510 | Jul 28, 2026 9:35pm | Jul 29, 2026 8:56am | Jul 29, 2026 11:00am | Jul 29, 2026 11:02am | Jul 29, 2026 11:54am | Jul 29, 2026 12:06pm | Jul 29, 2026 12:20pm | Jul 29, 2026 12:20pm | LowHangingWires |  | Fair | No | Upon arrival, found FLOW wire broken. No JPS wire was found broken. (Area has electricity).
Non-Outage | J.E.26.07.35079 | C001868058 | Moses Elliston | null | Completed | null | null | Jul 28, 2026 9:31pm | Jul 28, 2026 9:31pm | Jul 29, 2026 3:35pm | Jul 29, 2026 3:39pm | Jul 29, 2026 3:39pm | Jul 29, 2026 3:40pm | Jul 29, 2026 3:41pm | Jul 29, 2026 3:41pm |  |  | Fair | No | Credit added to prepaid account
Outage | J.E.26.07.36034 | C001868057 | Hartley Chin | Clarendon | Completed | Load_405727 | Parnassus - 210 | Jul 28, 2026 9:30pm | Jul 29, 2026 8:01am | Jul 29, 2026 12:13pm | Jul 29, 2026 12:13pm | Jul 29, 2026 1:07pm | Jul 29, 2026 1:22pm | Jul 29, 2026 1:23pm | Jul 29, 2026 1:23pm |  |  | SevereWind | No | Found okay … voltage read 119v , 119v , 206v ..
Outage | J.E.26.07.36049 | C001868048 | Milton Charlton | KSAN | Completed | Load_250228 | West Kings House - 310 | Jul 28, 2026 9:04pm | Jul 28, 2026 9:05pm | Jul 28, 2026 9:14pm | Jul 28, 2026 9:16pm | Jul 28, 2026 9:58pm | Jul 28, 2026 9:20pm | Jul 28, 2026 10:03pm | Jul 28, 2026 10:03pm |  |  | Fair | No | New customer and she don’t know the location of her meter. She was unable to locate the landlord.
Outage | J.E.26.07.36033 | C001868046 | Milton Charlton | KSAN | Completed | Load_263454 | Washington Blvd - 610 | Jul 28, 2026 8:56pm | Jul 29, 2026 11:51am | Jul 29, 2026 3:16pm | Jul 29, 2026 3:16pm | Jul 29, 2026 3:52pm | Jul 29, 2026 3:40pm | Jul 29, 2026 3:59pm | Jul 29, 2026 3:59pm |  |  | Fair | No | Customer service wire #6 triplex phase corroded at pothead. Repair using one 1- bolt clamp. Readings at meter socket and pothead 121-120-241 volts.
Outage | J.E.26.07.36032 | C001868041 | Richman Whyte | Westmoreland | Completed | Load_246958 | Paradise - 310 | Jul 28, 2026 8:50pm | Jul 28, 2026 8:51pm | Jul 28, 2026 10:18pm | Jul 28, 2026 10:18pm | Jul 28, 2026 10:18pm | Jul 28, 2026 10:20pm | Jul 28, 2026 10:20pm | Jul 28, 2026 10:20pm |  |  | Fair | No | Close back knife switch at waterworks after Donald Williams trip feeder 3-1-0 at paradise substation also replace 8amp junction at waterworks
Non-Outage | J.E.26.07.36023 | C001868040 | Swon Miller | St.James | Completed | Load_250164 | Queens Drive - 310 | Jul 28, 2026 8:43pm | Jul 28, 2026 8:43pm | Jul 28, 2026 9:06pm | Jul 28, 2026 9:06pm | Jul 28, 2026 9:35pm | Jul 21, 2026 9:50am | Jul 28, 2026 9:52pm | Jul 28, 2026 9:52pm |  |  | Fair | No | Found 1,50 amp junction fuse blown cause by lightning replace 50 amp junction fuse voltage found 115/114 voltage left 115/114/113
Non-Outage | J.E.26.07.35821 | C001868035 | Shamour Haughton | St.James | Completed | Load_260722 | Queens Drive - 710 | Jul 28, 2026 8:12pm | Jul 28, 2026 11:00pm | Jul 29, 2026 12:28am | Jul 29, 2026 12:28am | Jul 29, 2026 12:55am | Jul 29, 2026 12:55am | Jul 29, 2026 12:58am | Jul 29, 2026 12:58am |  |  | Fair | No | Check and found customer experiencing internal issue
Outage | J.E.26.07.32430 | C001868034 | Nickolas Rodriques | St.Catherine | Completed | Load_556034 | Tredegar - 510 | Jul 28, 2026 8:11pm | Jul 29, 2026 12:58pm | Jul 29, 2026 2:57pm | Jul 29, 2026 3:12pm | Jul 29, 2026 3:46pm | Jul 29, 2026 4:06pm | Jul 29, 2026 4:09pm | Jul 29, 2026 4:09pm |  |  | Fair | No | Power restored. Customer confirmed that the area outage was restored.
Outage | J.E.26.07.35922 | C001868033 | Andrew Powell | St.Elizabeth | Completed | Load_305176 | Maggotty - 210 | Jul 28, 2026 8:09pm | Jul 28, 2026 9:05pm | Jul 28, 2026 10:08pm | Jul 28, 2026 10:08pm | Jul 28, 2026 10:08pm | Jul 28, 2026 10:09pm | Jul 28, 2026 10:09pm | Jul 28, 2026 10:09pm |  |  | Fair | No | Premises found okay customer stated that supply restored.
Outage | J.E.26.07.35891 | C001868027 | Wan Carlos Scarlett | Portmore | Completed | Load_268319 | Naggo Head - 610 | Jul 28, 2026 7:45pm | Jul 28, 2026 7:45pm | Jul 28, 2026 9:49pm | Jul 28, 2026 9:49pm | Jul 28, 2026 11:31pm | Jul 29, 2026 7:51am | Jul 29, 2026 7:52am | Jul 29, 2026 7:52am | BrokenWire |  | Fair | No | Found span of open secondary line phase jumper burn out from the one clamp use 2 one bolt clamps at pole readings 116-116-234
Outage | J.E.26.07.35727 | C001868026 | Shamour Haughton | St.James | Completed | Load_247534 | Queens Drive - 710 | Jul 28, 2026 7:39pm | Jul 28, 2026 11:00pm | Jul 29, 2026 1:31am | Jul 29, 2026 1:31am | Jul 29, 2026 2:04am | Jul 29, 2026 2:04am | Jul 29, 2026 2:06am | Jul 29, 2026 2:06am |  |  | Fair | No | Check and found okay,customer states power was restored
Outage | J.E.26.07.35757 | C001868024 | Shamour Haughton | St.James | Completed | Load_260359 | Queens Drive - 710 | Jul 28, 2026 7:39pm | Jul 28, 2026 11:00pm | Jul 29, 2026 2:06am | Jul 29, 2026 2:06am | Jul 29, 2026 2:37am | Jul 29, 2026 2:37am | Jul 29, 2026 2:40am | Jul 29, 2026 2:40am |  |  | Fair | No | Unable to locate customer, cell number went voicemail
Outage | J.E.26.07.35623 | C001868023 | Romeo Brissett | St.James | Completed | Load_302847 | Bogue - 610 | Jul 28, 2026 7:38pm | Jul 28, 2026 7:38pm | Jul 28, 2026 10:35pm | Jul 28, 2026 10:35pm | Jul 28, 2026 11:33pm | Jul 28, 2026 11:48pm | Jul 28, 2026 11:50pm | Jul 28, 2026 11:50pm |  |  | Fair | No | Replaced (1)10KVA transformer fuse.
Outage | J.E.26.07.35778 | C001868022 | Derrick Dawkins | St.James | Completed | Load_239431 | Bogue - 610 | Jul 28, 2026 7:38pm | Jul 29, 2026 9:02am | Jul 29, 2026 2:07pm | Jul 29, 2026 2:07pm | Jul 29, 2026 2:07pm | Jul 29, 2026 2:10pm | Jul 29, 2026 2:10pm | Jul 29, 2026 2:10pm |  |  | Fair | No | Customer stated the electricity is back
Outage | J.E.26.07.35786 | C001868021 | Shamour Haughton | St.James | Completed | Load_260918 | Bogue - 610 | Jul 28, 2026 7:37pm | Jul 28, 2026 11:00pm | Jul 28, 2026 11:55pm | Jul 28, 2026 11:55pm | Jul 29, 2026 12:19am | Jul 29, 2026 12:22am | Jul 29, 2026 12:23am | Jul 29, 2026 12:23am |  |  | Fair | No | Check and found okay, customer’s state that power was restored
Non-Outage | J.E.26.07.35880 | C001868018 | Fitzroy Turner | null | Completed | null | null | Jul 28, 2026 7:33pm | Jul 28, 2026 7:37pm | Jul 28, 2026 8:17pm | Jul 28, 2026 8:17pm | Jul 28, 2026 8:17pm | Jul 28, 2026 8:38pm | Jul 28, 2026 8:41pm | Jul 28, 2026 8:41pm | BrokenWire |  | Fair | No | Found #2 quad burnt mid span use 15ft of 2# triplex to splice and retention using 6 one bolt clamps and one preform to carry out repair supply restored to customer
Outage | J.E.26.07.35833 | C001868015 | Andrew Powell | Manchester | Completed | Load_302912 | Spur Tree - 210 | Jul 28, 2026 7:29pm | Jul 28, 2026 7:31pm | Jul 28, 2026 10:13pm | Jul 28, 2026 10:13pm | Jul 28, 2026 10:13pm | Jul 28, 2026 10:13pm | Jul 28, 2026 10:15pm | Jul 28, 2026 10:15pm |  |  | Fair | No | Premises not located inadequately direction contact number in report incorrect.
Outage | J.E.26.07.35853 | C001868014 | Andrew Powell | St.Elizabeth | Completed | Load_250403 | Maggotty - 210 | Jul 28, 2026 7:29pm | Jul 28, 2026 7:31pm | Jul 28, 2026 8:10pm | Jul 28, 2026 8:10pm | Jul 28, 2026 8:11pm | Jul 28, 2026 8:12pm | Jul 28, 2026 8:13pm | Jul 28, 2026 8:13pm |  |  | Fair | No | Premises not located unable to reach customer due to over seas contact number only.
Outage | J.E.26.07.35854 | C001868008 | Denton Williams | Portland | Completed | Load_262425 | Port Antonio - 410 | Jul 28, 2026 7:23pm | Jul 28, 2026 7:58pm | Jul 28, 2026 8:19pm | Jul 28, 2026 8:20pm | Jul 28, 2026 9:07pm | Jul 28, 2026 9:07pm | Jul 28, 2026 9:11pm | Jul 28, 2026 9:11pm |  |  | Fair | No | Phone ringing without am answer. No driving direction
Outage | J.E.26.07.35212 | C001868002 | Moses Elliston | St.Catherine | Completed | Load_268179 | Tredegar - 310 | Jul 28, 2026 7:06pm | Jul 29, 2026 8:55am | Jul 29, 2026 3:16pm | Jul 29, 2026 3:16pm | Jul 29, 2026 3:16pm | Jul 29, 2026 3:16pm | Jul 29, 2026 3:17pm | Jul 29, 2026 3:17pm |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.07.35556 | C001868001 | Richard Watson | St.Elizabeth | Completed | Load_292979 | Maggotty - 110 | Jul 28, 2026 7:06pm | Jul 28, 2026 7:06pm | Jul 28, 2026 10:35pm | Jul 28, 2026 10:35pm | Jul 28, 2026 11:08pm | Jul 28, 2026 11:22pm | Jul 28, 2026 11:27pm | Jul 28, 2026 11:27pm |  |  | Fair | No | Replace blown 15amp junction fuse at pole#0104961, after completing patrol no visible fault found, supply restored to area.
Outage | J.E.26.07.35758 | C001867996 | Tyrese Williams | St.Ann | Completed | Load_251360 | Cardiff Hall - 310 | Jul 28, 2026 6:59pm | Jul 28, 2026 7:00pm | Jul 28, 2026 7:05pm | Jul 28, 2026 7:05pm | Jul 28, 2026 7:10pm | Jul 28, 2026 7:10pm | Jul 28, 2026 7:10pm | Jul 28, 2026 7:10pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.35818 | C001867995 | Fitzroy Turner | KSAS | Completed | Load_250310 | Greenwich - 510 | Jul 28, 2026 6:58pm | Jul 28, 2026 6:59pm | Jul 28, 2026 8:41pm | Jul 28, 2026 8:41pm | Jul 28, 2026 8:42pm | Jul 28, 2026 8:42pm | Jul 28, 2026 8:43pm | Jul 28, 2026 8:43pm |  |  | Fair | No | Supply restored to customer after repair was carry out repairs service wire using 15ft triplex and 6 one bolt clamps
Outage | J.E.26.07.35781 | C001867992 | Wan Carlos Scarlett | Portmore | Completed | Load_258305 | Twickenham - 210 | Jul 28, 2026 6:52pm | Jul 28, 2026 6:54pm | Jul 28, 2026 7:47pm | Jul 28, 2026 7:47pm | Jul 28, 2026 7:47pm | Jul 28, 2026 7:48pm | Jul 28, 2026 7:50pm | Jul 28, 2026 7:50pm |  |  | Fair | No | Found one span of open secondary line phase and neutral touching on each other tension one span of open secondary line phase and neutral use 3 one bolt clamps at pole isolate and close 50KVA transformer no pole # was found
Outage | J.E.26.07.35800 | C001867987 | Fitzroy Turner | KSAS | Completed | Load_259549 | Rockfort - 210 | Jul 28, 2026 6:44pm | Jul 28, 2026 6:46pm | Jul 28, 2026 6:50pm | Jul 28, 2026 6:50pm | Jul 28, 2026 7:00pm | Jul 28, 2026 7:13pm | Jul 28, 2026 7:28pm | Jul 28, 2026 7:28pm | BrokenWire |  | Fair | No | Found tree wire open secondary phase and neutral cut down cause by tree cut and line splice and retention using 5ft of #4 copper and 6 one bolt clamps to carry out repair supply restored to areas
Outage | J.E.26.07.35765 | C001867985 | Andrew Powell | Manchester | Completed | Load_262926 | Spur Tree - 210 | Jul 28, 2026 6:39pm | Jul 28, 2026 6:40pm | Jul 28, 2026 8:14pm | Jul 28, 2026 8:14pm | Jul 28, 2026 8:14pm | Jul 28, 2026 8:15pm | Jul 28, 2026 8:15pm | Jul 28, 2026 8:15pm |  |  | Fair | No | Premises found okay customer stated that supply restored.
Outage | J.E.26.07.35773 | C001867984 | Richard Watson | St.Elizabeth | Completed | Load_258532 | Maggotty - 110 | Jul 28, 2026 6:39pm | Jul 28, 2026 6:41pm | Jul 28, 2026 9:56pm | Jul 28, 2026 9:57pm | Jul 28, 2026 10:20pm | Jul 28, 2026 10:32pm | Jul 28, 2026 10:32pm | Jul 28, 2026 10:32pm |  |  | Rains | No | Entire cedar spring area patrolled and electricity found in all areas of the community.
Outage | J.E.26.07.35784 | C001867983 | Marlon Authors | Manchester | Completed | Load_268609 | Spur Tree - 210 | Jul 28, 2026 6:39pm | Jul 29, 2026 9:44am | Jul 29, 2026 11:11am | Jul 29, 2026 11:11am | Jul 29, 2026 11:11am | Jul 29, 2026 11:50am | Jul 29, 2026 11:51am | Jul 29, 2026 11:51am |  |  | Fair | No | Unable to locate and the customer not answering the phone
Outage | J.E.26.07.35775 | C001867977 | Milton Charlton | KSAN | Completed | Load_239630 | Hope - 510 | Jul 28, 2026 6:30pm | Jul 28, 2026 6:31pm | Jul 28, 2026 7:50pm | Jul 28, 2026 7:50pm | Jul 28, 2026 8:17pm | Jul 28, 2026 8:20pm | Jul 28, 2026 8:19pm | Jul 28, 2026 8:19pm |  |  | Fair | No | Reset 25 kva transformer at pole# 0110378 found tripped.
Non-Outage | J.E.26.07.35752 | C001867976 | Raymond Lewis | null | Completed | null | null | Jul 28, 2026 6:24pm | Jul 28, 2026 6:24pm | Jul 28, 2026 7:42pm | Jul 28, 2026 7:42pm | Jul 28, 2026 8:42pm | Jul 28, 2026 9:25pm | Jul 28, 2026 9:25pm | Jul 28, 2026 9:25pm | Fire |  | Fair | No | Vehicle accident
Outage | J.E.26.07.35762 | C001867975 | Marlon Brown | Trelawny | Completed | Load_292447 | Greenwood - 110 | Jul 28, 2026 6:24pm | Jul 28, 2026 6:24pm | Jul 28, 2026 6:50pm | Jul 28, 2026 6:50pm | Jul 28, 2026 7:15pm | Jul 28, 2026 7:42pm | Jul 28, 2026 7:42pm | Jul 28, 2026 7:42pm |  |  | Fair | No | Replaced 5amps 50kva Transformer fuse and fuse holder. Fuse holder burnt out.
Outage | J.E.26.07.35740 | C001867970 | Tyrese Williams | St.Ann | Completed | Load_255926 | Cardiff Hall - 310 | Jul 28, 2026 6:11pm | Jul 28, 2026 6:12pm | Jul 28, 2026 7:00pm | Jul 28, 2026 7:14pm | Jul 28, 2026 7:16pm | Jul 28, 2026 7:17pm | Jul 28, 2026 7:18pm | Jul 28, 2026 7:18pm | BrokenWire |  | Fair | No | Customer said she didn’t make any report
Outage | J.E.26.07.35657 | C001867969 | Raymond Carr | St.Mary | Completed | Load_238939 | Blackstonedge - 110 | Jul 28, 2026 6:08pm | Jul 28, 2026 6:08pm | Jul 28, 2026 7:15pm | Jul 28, 2026 7:15pm | Jul 28, 2026 7:15pm | Jul 28, 2026 7:11pm | Jul 28, 2026 7:17pm | Jul 28, 2026 7:17pm |  |  | Fair | No | Customer reported that she had an electrician fixed fault.
Outage | J.E.26.07.35048 | C001867967 | Richard Grant | St.Catherine | Completed | Load_240274 | New Michelton - 410 | Jul 28, 2026 6:00pm | Jul 28, 2026 6:00pm | Jul 28, 2026 8:03pm | Jul 28, 2026 9:38pm | Jul 28, 2026 9:38pm | Jul 28, 2026 9:38pm | Jul 28, 2026 9:38pm | Jul 28, 2026 9:38pm |  |  | Rains | No | Area and premises found with supply. Premises found okay
Outage | J.E.26.07.34925 | C001867965 | Clyde Brown | Clarendon | Completed | Load_354364 | May Pen - 110 | Jul 28, 2026 5:54pm | Jul 28, 2026 5:54pm | Jul 28, 2026 7:28pm | Jul 28, 2026 7:28pm | Jul 28, 2026 8:53pm | Jul 28, 2026 8:52pm | Jul 28, 2026 9:02pm | Jul 28, 2026 9:02pm | Fire |  | Fair | No | Blown 15 amps junction fuse at Forte George line patrolled this was caused by Freak storm and lightning ,blown fuse replaced.
Outage | J.E.26.07.35258 | C001867962 | Swon Miller | St.James | Completed | Load_259518 | Queens Drive - 710 | Jul 28, 2026 5:49pm | Jul 28, 2026 5:57pm | Jul 28, 2026 6:57pm | Jul 28, 2026 6:57pm | Jul 28, 2026 7:18pm | Jul 21, 2026 7:29am | Jul 28, 2026 7:36pm | Jul 28, 2026 7:36pm |  |  | Fair | No | Found 1,30 amp junction fuse blown cause by lightning replace 30 amp junction fuse at pole number 215405 voltage found 0.000 voltage left 117/117/234
Outage | J.E.26.07.35566 | C001867958 | Swon Miller | St.James | Completed | Load_269643 | Queens Drive - 310 | Jul 28, 2026 5:47pm | Jul 28, 2026 5:49pm | Jul 28, 2026 9:54pm | Jul 28, 2026 9:54pm | Jul 28, 2026 10:27pm | Jul 28, 2026 10:37pm | Jul 28, 2026 10:37pm | Jul 28, 2026 10:37pm |  |  | Fair | No | Check and found areas okay voltage found 117/118/236 customer states that power supply has been restored voltage left 117/118/236
Outage | J.E.26.07.35652 | C001867960 | Swon Miller | St.James | Completed | Load_261958 | Queens Drive - 710 | Jul 28, 2026 5:47pm | Jul 28, 2026 5:49pm | Jul 28, 2026 6:04pm | Jul 28, 2026 6:04pm | Jul 28, 2026 6:05pm | Jul 28, 2026 6:06am | Jul 28, 2026 6:06pm | Jul 28, 2026 6:06pm |  |  | Fair | No | Call related to previous
Outage | J.E.26.07.35658 | C001867959 | Swon Miller | St.James | Completed | Load_406000 | Queens Drive - 310 | Jul 28, 2026 5:47pm | Jul 28, 2026 5:49pm | Jul 28, 2026 6:03pm | Jul 28, 2026 6:09pm | Jul 28, 2026 6:28pm | Jul 21, 2026 6:40am | Jul 28, 2026 6:42pm | Jul 28, 2026 6:42pm |  |  | Fair | No | Check and found okay voltage found 115/115/231 voltage left 115/115/231
Non-Outage | J.E.26.07.35559 | C001867951 | Neville Spencer | null | Completed | null | null | Jul 28, 2026 5:38pm | Jul 28, 2026 5:38pm | Jul 28, 2026 6:15pm | Jul 28, 2026 6:15pm | Jul 28, 2026 6:34pm | Jul 28, 2026 7:46pm | Jul 28, 2026 7:57pm | Jul 28, 2026 7:57pm |  |  | Fair | No | Open 25 kva xmfr in bank of 3, splice and retention broken secondary phase Conductor used 30 ft wire, 2, clamps,2, preform Also renew blown 3 amp fuse protecting 25 kva xmfr supply restored.
Outage | J.E.26.07.34789 | C001867948 | Edward Royal | KSAN | Completed | Load_243339 | Washington Blvd - 710 | Jul 28, 2026 5:36pm | Jul 28, 2026 5:36pm | Jul 28, 2026 6:49pm | Jul 28, 2026 6:49pm | Jul 28, 2026 6:49pm | Jul 28, 2026 6:50pm | Jul 28, 2026 6:50pm | Jul 28, 2026 6:50pm |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.07.35635 | C001867947 | Raymond Lewis | St.Ann | Completed | Load_244869 | Ocho Rios - 510 | Jul 28, 2026 5:35pm | Jul 28, 2026 5:35pm | Jul 28, 2026 9:26pm | Jul 28, 2026 9:26pm | Jul 28, 2026 9:26pm | Jul 28, 2026 9:27pm | Jul 28, 2026 9:27pm | Jul 28, 2026 9:27pm |  |  | Fair | No | Supply restored
Outage | J.E.26.07.35620 | C001867930 | Tajay Bernard | Hanover | Completed | Load_573360 | Orange Bay - 310 | Jul 28, 2026 5:25pm | Jul 28, 2026 8:09pm | Jul 28, 2026 8:14pm | Jul 28, 2026 10:19pm | Jul 28, 2026 10:19pm | Jul 28, 2026 10:34pm | Jul 28, 2026 10:35pm | Jul 28, 2026 10:35pm |  |  | Fair | No | Refuse 1 15amp junction fuse
Non-Outage | J.E.26.07.33896 | C001867928 | Andre Williams | Trelawny | Completed | Load_241073 | Duncans - 210 | Jul 28, 2026 5:19pm | Jul 28, 2026 5:21pm | Jul 28, 2026 6:55pm | Jul 28, 2026 7:02pm | Jul 28, 2026 7:02pm | Jul 28, 2026 7:02pm | Jul 28, 2026 7:02pm | Jul 28, 2026 7:02pm |  |  | Fair | No | Customer side of pothead coroded customer was advice, voltage on Jps side 118+119=237
Non-Outage | J.E.26.07.33923 | C001867927 | Andre Williams | Trelawny | Completed | Load_241073 | Duncans - 210 | Jul 28, 2026 5:19pm | Jul 28, 2026 5:21pm | Jul 28, 2026 6:10pm | Jul 28, 2026 6:10pm | Jul 28, 2026 6:53pm | Jul 28, 2026 6:54pm | Jul 28, 2026 6:55pm | Jul 28, 2026 6:55pm |  |  | Fair | No | Customer side of pothead coroded customer was advice, voltage on Jps side 118+119=237
Non-Outage | J.E.26.07.35570 | C001867924 | Kenroy Dale | null | Completed | null | null | Jul 28, 2026 5:15pm | Jul 29, 2026 7:38am | Jul 29, 2026 7:48am | Jul 29, 2026 7:57am | Jul 29, 2026 8:47am | Jul 29, 2026 9:09am | Jul 29, 2026 9:15am | Jul 29, 2026 9:15am |  |  | Fair | No | Meter defective and need to be replaced, (electrician on-site carry out repairs on customers end)
Outage | J.E.26.07.35551 | C001867918 | Clyde Brown | Clarendon | Completed | Load_351243 | May Pen - 110 | Jul 28, 2026 5:03pm | Jul 29, 2026 7:59am | Jul 29, 2026 10:02am | Jul 29, 2026 10:03am | Jul 29, 2026 10:11am | Jul 29, 2026 10:08am | Jul 29, 2026 10:18am | Jul 29, 2026 10:18am |  |  | Fair | No | Found ok
Outage | J.E.26.07.35555 | C001867919 | Clyde Brown | Clarendon | Completed | Load_1003520 | May Pen - 110 | Jul 28, 2026 5:03pm | Jul 29, 2026 7:57am | Jul 29, 2026 10:18am | Jul 29, 2026 10:18am | Jul 29, 2026 10:18am | Jul 29, 2026 10:15am | Jul 29, 2026 10:25am | Jul 29, 2026 10:25am |  |  | Fair | No | Customer said she did not make call to JPS
Outage | J.E.26.07.35294 | C001867917 | Romeo Brissett | St.James | Completed | Load_252604 | Bogue - 610 | Jul 28, 2026 5:00pm | Jul 28, 2026 5:00pm | Jul 28, 2026 6:13pm | Jul 28, 2026 6:13pm | Jul 28, 2026 7:01pm | Jul 28, 2026 7:00pm | Jul 28, 2026 7:04pm | Jul 28, 2026 7:04pm |  |  | Fair | No | Customer was connected by escalation. Frequent outages due HX box issue please send to field service.
Outage | J.E.26.07.35499 | C001867916 | Romeo Brissett | St.James | Completed | Load_260332 | Bogue - 610 | Jul 28, 2026 4:59pm | Jul 28, 2026 5:00pm | Jul 28, 2026 9:53pm | Jul 28, 2026 9:53pm | Jul 28, 2026 10:32pm | Jul 28, 2026 10:29pm | Jul 28, 2026 10:34pm | Jul 28, 2026 10:34pm |  |  | Fair | No | Unable to locate customer
Outage | J.E.26.07.35540 | C001867915 | Romeo Brissett | St.James | Completed | Load_239375 | Bogue - 610 | Jul 28, 2026 4:59pm | Jul 28, 2026 5:00pm | Jul 28, 2026 7:05pm | Jul 28, 2026 7:05pm | Jul 28, 2026 7:41pm | Jul 28, 2026 9:40pm | Jul 28, 2026 9:52pm | Jul 28, 2026 9:52pm |  |  | Fair | No | Line patrolled, found clear and safe,, the 50 kva transformer was tested closed and found defective, circuit unable to tie.13 Customer found without supply, recommending (1)25KVA transformer due to the amount of the customers. Please send to maintenance.
Outage | J.E.26.07.35518 | C001867913 | Rayon Foster | Hanover | Completed | Load_244864 | Orange Bay - 310 | Jul 28, 2026 4:56pm | Jul 28, 2026 4:56pm | Jul 28, 2026 6:09pm | Jul 28, 2026 6:09pm | Jul 28, 2026 6:43pm | Jul 28, 2026 10:32pm | Jul 28, 2026 10:32pm | Jul 28, 2026 10:32pm |  |  | Rains | No | Defective 100kva transformer rewire back up transformer to become edesion transformer voltage after rewireing 118/118AB 236 volts
Outage | J.E.26.07.35503 | C001867911 | Tajay Bernard | Hanover | Completed | Load_252053 | Orange Bay - 210 | Jul 28, 2026 4:55pm | Jul 28, 2026 4:55pm | Jul 28, 2026 6:28pm | Jul 28, 2026 6:29pm | Jul 28, 2026 6:29pm | Jul 28, 2026 6:30pm | Jul 28, 2026 6:32pm | Jul 28, 2026 6:32pm | BrokenWire |  | Fair | No | Related to previous call job # 35519
Outage | J.E.26.07.35519 | C001867912 | Tajay Bernard | Hanover | Completed | Load_258609 | Orange Bay - 210 | Jul 28, 2026 4:55pm | Jul 28, 2026 4:55pm | Jul 28, 2026 6:05pm | Jul 28, 2026 6:05pm | Jul 28, 2026 6:27pm | Jul 28, 2026 6:28pm | Jul 28, 2026 6:28pm | Jul 28, 2026 6:28pm |  |  | Fair | No | Customer stated that power was restored
Non-Outage | J.E.26.07.35501 | C001867910 | Swon Miller | St.James | Completed | Load_243926 | Queens Drive - 810 | Jul 28, 2026 4:54pm | Jul 28, 2026 4:54pm | Jul 28, 2026 7:37pm | Jul 28, 2026 7:37pm | Jul 28, 2026 7:58pm | Jul 21, 2026 8:18am | Jul 28, 2026 8:19pm | Jul 28, 2026 8:19pm |  |  | Fair | No | Found 1,50 amp junction fuse blown cause by lightning replace 1,50 amp junction fuse at pole number 058319
Non-Outage | J.E.26.07.35524 | C001867902 | Milton Charlton | KSAN | Completed | Load_263454 | Washington Blvd - 610 | Jul 28, 2026 4:53pm | Jul 28, 2026 4:59pm | Jul 28, 2026 7:16pm | Jul 28, 2026 7:19pm | Jul 28, 2026 7:27pm | Jul 28, 2026 7:30pm | Jul 28, 2026 7:29pm | Jul 28, 2026 7:29pm |  |  | Fair | No | Found okay upon arrival. Customer has an internal problem customer meter socket defective on need to be change. Readings at meter socket 120-119-240 volts.
Outage | J.E.26.07.35093 | C001867909 | Michael Christian | St.James | Completed | Load_249682 | Bogue - 310 | Jul 28, 2026 4:53pm | Jul 29, 2026 12:12pm | Jul 29, 2026 1:26pm | Jul 29, 2026 1:26pm | Jul 29, 2026 2:27pm | Jul 29, 2026 2:29pm | Jul 29, 2026 2:30pm | Jul 29, 2026 2:30pm |  |  | Fair | No | Found locked
Outage | J.E.26.07.35302 | C001867905 | Swon Miller | St.James | Completed | Load_293364 | Queens Drive - 310 | Jul 28, 2026 4:53pm | Jul 28, 2026 4:53pm | Jul 28, 2026 5:01pm | Jul 28, 2026 5:01pm | Jul 28, 2026 5:18pm | Jul 21, 2026 5:57am | Jul 28, 2026 5:58pm | Jul 28, 2026 5:58pm |  |  | Fair | No | Found 1,30 amp junction fuse blown cause by lightning replace 30 amp junction fuse at pole number 520592 voltage left 0.000 voltage 115/114/230
Outage | J.E.26.07.35325 | C001867908 | Swon Miller | St.James | Completed | Load_249916 | Bogue - 310 | Jul 28, 2026 4:53pm | Jul 28, 2026 4:53pm | Jul 28, 2026 5:11pm | Jul 28, 2026 5:58pm | Jul 28, 2026 5:59pm | Jul 28, 2026 6:03am | Jul 28, 2026 6:03pm | Jul 28, 2026 6:03pm |  |  | Fair | No | Call is related to previous
Outage | J.E.26.07.35327 | C001867907 | Swon Miller | St.James | Completed | Load_575863 | Bogue - 410 | Jul 28, 2026 4:53pm | Jul 28, 2026 4:53pm | Jul 28, 2026 5:07pm | Jul 28, 2026 10:37pm | Jul 28, 2026 10:57pm | Jul 28, 2026 11:01pm | Jul 28, 2026 11:01pm | Jul 28, 2026 11:01pm |  |  | Fair | No | Check and found area okay customer states that power supply has been restored
Outage | J.E.26.07.35344 | C001867903 | Swon Miller | St.James | Completed | Load_302615 | Queens Drive - 310 | Jul 28, 2026 4:53pm | Jul 28, 2026 4:53pm | Jul 28, 2026 6:14pm | Jul 28, 2026 6:43pm | Jul 28, 2026 6:49pm | Jul 28, 2026 6:54am | Jul 28, 2026 6:57pm | Jul 28, 2026 6:57pm |  |  | Fair | No | Check and found areas okay voltage found 116/115/232 customer states that power supply has been restored voltage left 115/116/232
Outage | J.E.26.07.35526 | C001867906 | Swon Miller | St.James | Completed | Load_294428 | Bogue - 410 | Jul 28, 2026 4:53pm | Jul 28, 2026 4:53pm | Jul 28, 2026 8:21pm | Jul 28, 2026 8:21pm | Jul 28, 2026 8:22pm | Jul 29, 2026 8:50am | Jul 28, 2026 9:05pm | Jul 28, 2026 9:05pm |  |  | Fair | No | Found 1;25 kva transformer fuse blown cause by lightning replace 3 amp in 25 kva transformer voltage found 0.000 voltage left 115/115/231
Non-Outage | J.E.26.07.35528 | C001867901 | Fitzroy Turner | null | Completed | null | null | Jul 28, 2026 4:51pm | Jul 28, 2026 4:58pm | Jul 28, 2026 8:45pm | Jul 28, 2026 8:45pm | Jul 28, 2026 9:41pm | Jul 28, 2026 9:42pm | Jul 28, 2026 9:43pm | Jul 28, 2026 9:43pm | Fire |  | Fair | No | Tree branch remove from tree phase open secondary areas is now safe
Outage | J.E.26.07.35525 | C001867897 | Javid Vernon | Westmoreland | Completed | Load_239066 | Paradise - 210 | Jul 28, 2026 4:47pm | Jul 28, 2026 4:48pm | Jul 28, 2026 4:56pm | Jul 28, 2026 4:56pm | Jul 28, 2026 5:51pm | Jul 28, 2026 6:25pm | Jul 28, 2026 6:25pm | Jul 28, 2026 6:25pm |  |  | Fair | No | Cut and remove vegetation and refuse one 15amp junction fuse
Outage | J.E.26.07.35411 | C001867895 | Richard Watson | St.Elizabeth | Completed | Load_248131 | Maggotty - 110 | Jul 28, 2026 4:46pm | Jul 28, 2026 4:48pm | Jul 28, 2026 6:47pm | Jul 28, 2026 6:47pm | Jul 28, 2026 7:48pm | Jul 28, 2026 9:47pm | Jul 28, 2026 9:56pm | Jul 28, 2026 9:56pm |  |  | Rains | No | Replace blown 50amp junction fuse at Emma Thompson basic school at pole#0181308, also replace blown 30amp junction fuse at elderslie no pole# and blown 15amp junction fuse at Niagara square, after completing patrol suspected cause lightning, supply restored to affected areas.
Non-Outage | J.E.26.07.34562 | C001867890 | Hopeton Henry | St.Thomas | Completed | Load_266529 | Good Year - 210 | Jul 28, 2026 4:40pm | Jul 28, 2026 4:41pm | Jul 29, 2026 8:55am | Jul 29, 2026 9:10am | Jul 29, 2026 9:16am | Jul 29, 2026 9:55am | Jul 29, 2026 9:56am | Jul 29, 2026 9:56am |  |  | Fair | Yes | Internal problem, customer advised 113-113-226 volts
Non-Outage | J.E.26.07.34657 | C001867891 | Derrick Grubb | St.Thomas | Completed | Load_262086 | Good Year - 110 | Jul 28, 2026 4:40pm | Jul 28, 2026 7:05pm | Jul 28, 2026 10:22pm | Jul 28, 2026 10:22pm | Jul 28, 2026 10:39pm | Jul 28, 2026 10:39pm | Jul 28, 2026 10:48pm | Jul 28, 2026 10:48pm |  |  | Fair | No | Premises not located and several calls to customer went unanswered
Non-Outage | J.E.26.07.34924 | C001867892 | Derrick Grubb | St.Thomas | Completed | Load_245745 | Good Year - 210 | Jul 28, 2026 4:40pm | Jul 28, 2026 7:04pm | Jul 28, 2026 9:28pm | Jul 28, 2026 9:28pm | Jul 28, 2026 10:19pm | Jul 28, 2026 10:21pm | Jul 28, 2026 10:22pm | Jul 28, 2026 10:22pm |  |  | Fair | No | Premises closed
Outage | J.E.26.07.35496 | C001867883 | Milton Charlton | KSAN | Completed | Load_256049 | Hope - 510 | Jul 28, 2026 4:34pm | Jul 28, 2026 4:35pm | Jul 28, 2026 8:19pm | Jul 28, 2026 8:19pm | Jul 28, 2026 8:19pm | Jul 28, 2026 8:25pm | Jul 28, 2026 8:22pm | Jul 28, 2026 8:22pm |  |  | Fair | No | Call related to call at #318 Hope flat.
Outage | J.E.26.07.35502 | C001867884 | Edward Royal | KSAN | Completed | Load_574897 | Washington Blvd - 610 | Jul 28, 2026 4:34pm | Jul 28, 2026 6:48pm | Jul 28, 2026 7:33pm | Jul 28, 2026 7:33pm | Jul 28, 2026 7:33pm | Jul 28, 2026 9:36pm | Jul 28, 2026 9:36pm | Jul 28, 2026 9:36pm |  |  | Fair | No | Defective 100 kva transformer needs be change over by kings house I am asking for second opinion by in-house crew
Outage | J.E.26.07.35454 | C001867876 | Andrew Powell | Manchester | Completed | Load_1002269 | Spur Tree - 210 | Jul 28, 2026 4:33pm | Jul 28, 2026 4:43pm | Jul 28, 2026 8:26pm | Jul 28, 2026 8:27pm | Jul 28, 2026 9:49pm | Jul 28, 2026 9:50pm | Jul 28, 2026 9:53pm | Jul 28, 2026 9:53pm |  |  | Fair | No | Found customer disconnected due to meter wrongly displaced in meter socket, customer leaves without supply, please refer to field service department for correction.
Non-Outage | J.E.26.07.34602 | C001867874 | Neville Spencer | null | Completed | null | null | Jul 28, 2026 4:30pm | Jul 28, 2026 4:30pm | Jul 28, 2026 7:58pm | Jul 28, 2026 7:58pm | Jul 28, 2026 8:26pm | Jul 28, 2026 8:26pm | Jul 28, 2026 8:29pm | Jul 28, 2026 8:29pm | Fire |  | Fair | No | Found supply at location illegal connection need to removed REF TO FIELD SERVICE.
Outage | J.E.26.07.35401 | C001867869 | Marlon Authors | St.Elizabeth | Completed | Load_292512 | Maggotty - 210 | Jul 28, 2026 4:26pm | Jul 29, 2026 9:45am | Jul 29, 2026 12:01pm | Jul 29, 2026 12:01pm | Jul 29, 2026 12:15pm | Jul 29, 2026 12:19pm | Jul 29, 2026 12:19pm | Jul 29, 2026 12:19pm |  |  | Fair | No | Unable to locate and the customer not answering the phone
Outage | J.E.26.07.34058 | C001867859 | Neville Spencer | Clarendon | Completed | Load_255380 | May Pen - 110 | Jul 28, 2026 4:22pm | Jul 28, 2026 5:55pm | Jul 28, 2026 8:29pm | Jul 28, 2026 8:29pm | Jul 28, 2026 8:53pm | Jul 28, 2026 8:54pm | Jul 28, 2026 9:13pm | Jul 28, 2026 9:13pm |  |  | Fair | No | Found defective meter socket temporary repair voltage reading 116 customer advised.
Outage | J.E.26.07.34370 | C001867858 | Neville Spencer | Clarendon | Completed | Load_405727 | Parnassus - 210 | Jul 28, 2026 4:22pm | Jul 28, 2026 4:57pm | Jul 28, 2026 5:31pm | Jul 28, 2026 5:31pm | Jul 28, 2026 6:10pm | Jul 28, 2026 6:12pm | Jul 28, 2026 6:13pm | Jul 28, 2026 6:13pm |  |  | Fair | No | Found ok call resolved last night.
Non-Outage | J.E.26.07.33208 | C001867854 | Christopher Edwards | null | Completed | null | null | Jul 28, 2026 4:21pm | Jul 29, 2026 11:16am | Jul 29, 2026 1:35pm | Jul 29, 2026 1:46pm | Jul 29, 2026 1:46pm | Jul 29, 2026 2:02pm | Jul 29, 2026 2:03pm | Jul 29, 2026 2:03pm | Fire |  | Fair | No | Check and found okCable pole head was cut to provide clearance from open secondary wires
Non-Outage | J.E.26.07.35309 | C001867857 | Denton Williams | null | Completed | null | null | Jul 28, 2026 4:21pm | Jul 28, 2026 4:22pm | Jul 28, 2026 8:18pm | Jul 28, 2026 8:18pm | Jul 28, 2026 8:18pm | Jul 28, 2026 8:18pm | Jul 28, 2026 8:19pm | Jul 28, 2026 8:19pm |  |  | Fair | No | Tree fall on line and clear it self, caused a 10 amp tripsaver to operate, close 10 amp tripsaver, all customers are .
Outage | J.E.26.07.32997 | C001867855 | Milton Charlton | KSAN | Completed | Load_579157 | Washington Blvd - 610 | Jul 28, 2026 4:21pm | Jul 28, 2026 4:34pm | Jul 28, 2026 6:50pm | Jul 28, 2026 7:30pm | Jul 28, 2026 7:48pm | Jul 28, 2026 7:50pm | Jul 28, 2026 7:50pm | Jul 28, 2026 7:50pm |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.07.35246 | C001867856 | Denton Williams | Portland | Completed | Load_266550 | Port Antonio - 410 | Jul 28, 2026 4:21pm | Jul 28, 2026 4:22pm | Jul 28, 2026 7:06pm | Jul 28, 2026 7:06pm | Jul 28, 2026 8:02pm | Jul 28, 2026 8:12pm | Jul 28, 2026 8:18pm | Jul 28, 2026 8:18pm |  | Y | Fair | No | Tree fall on line and clear it self, caused a 10 amp tripsaver to operate, close 10 amp tripsaver, all customers are .
Outage | J.E.26.07.34462 | C001867845 | Clyde Brown | Clarendon | Completed | Load_249430 | May Pen - 110 | Jul 28, 2026 4:18pm | Jul 28, 2026 4:20pm | Jul 28, 2026 5:10pm | Jul 28, 2026 5:10pm | Jul 28, 2026 5:43pm | Jul 28, 2026 5:50pm | Jul 28, 2026 6:06pm | Jul 28, 2026 6:06pm |  |  | Fair | No | Blown 10 amps junction fuse at Colonel Ridge,line patrolled and no fault seen,blown fuse replaced.
Outage | J.E.26.07.34954 | C001867843 | Hartley Chin | Clarendon | Completed | Load_242961 | Parnassus - 210 | Jul 28, 2026 4:17pm | Jul 29, 2026 8:00am | Jul 29, 2026 4:00pm | Jul 29, 2026 4:00pm | Jul 29, 2026 5:39pm | Jul 29, 2026 5:39pm | Jul 29, 2026 5:39pm | Jul 29, 2026 5:39pm |  |  | Fair | No | Prem not found … unable to contact customer with contact # provided..
Outage | J.E.26.07.34970 | C001867844 | Neville Spencer | Clarendon | Completed | Load_254385 | May Pen - 110 | Jul 28, 2026 4:17pm | Jul 28, 2026 4:20pm | Jul 28, 2026 9:13pm | Jul 28, 2026 9:13pm | Jul 28, 2026 11:45pm | Jul 28, 2026 11:45pm | Jul 28, 2026 11:47pm | Jul 28, 2026 11:47pm |  |  | Fair | No | Unable to locate customer.
Outage | J.E.26.07.33368 | C001867833 | Clyde Brown | Clarendon | Completed | Load_244375 | May Pen - 110 | Jul 28, 2026 4:06pm | Jul 28, 2026 4:19pm | Jul 28, 2026 6:07pm | Jul 28, 2026 6:07pm | Jul 28, 2026 6:07pm | Jul 28, 2026 5:49pm | Jul 28, 2026 6:10pm | Jul 28, 2026 6:10pm |  |  | Fair | No | Blown 10 amps junction fuse at colonel Ridge,line patrolled and no fault seen,blown fuse replaced.
Outage | J.E.26.07.34508 | C001867831 | Clyde Brown | Clarendon | Completed | Load_266472 | May Pen - 110 | Jul 28, 2026 4:05pm | Jul 28, 2026 4:20pm | Jul 28, 2026 6:16pm | Jul 28, 2026 6:16pm | Jul 28, 2026 7:17pm | Jul 28, 2026 7:20pm | Jul 28, 2026 7:27pm | Jul 28, 2026 7:27pm |  |  | Rains | No | Blown 3 amps fuse for 25 kva transformer,line patrolled,lightning suspected and blown fuse replaced
Outage | J.E.26.07.35197 | C001867830 | Clyde Brown | Clarendon | Completed | Load_242669 | May Pen - 110 | Jul 28, 2026 4:05pm | Jul 28, 2026 4:27pm | Jul 28, 2026 6:10pm | Jul 28, 2026 6:10pm | Jul 28, 2026 6:10pm | Jul 28, 2026 5:50pm | Jul 28, 2026 6:12pm | Jul 28, 2026 6:12pm |  |  | Fair | No | Blown 10 amps junction fuse at Colonel Ridge,line patrolled and no fault seen,blown fuse replaced.
Non-Outage | J.E.26.07.34784 | C001867821 | Omar King | St.Ann | Completed | Load_252272 | Cardiff Hall - 210 | Jul 28, 2026 4:02pm | Jul 28, 2026 4:02pm | Jul 28, 2026 8:19pm | Jul 28, 2026 8:19pm | Jul 28, 2026 8:56pm | Jul 28, 2026 8:56pm | Jul 28, 2026 8:56pm | Jul 28, 2026 8:56pm |  |  | Fair | No | Unable to find customer call several times no answer directions not sufficient
Outage | J.E.26.07.35291 | C001867822 | Andrew Powell | St.Elizabeth | Completed | Load_269899 | Maggotty - 210 | Jul 28, 2026 4:02pm | Jul 28, 2026 4:03pm | Jul 28, 2026 5:50pm | Jul 28, 2026 5:50pm | Jul 28, 2026 5:50pm | Jul 28, 2026 5:50pm | Jul 28, 2026 5:51pm | Jul 28, 2026 5:51pm |  |  | Fair | No | Found okay customer stated that supply at the premises.
Non-Outage | J.E.26.07.35161 | C001867820 | Omar King | St.Ann | Completed | Load_325650 | Cardiff Hall - 210 | Jul 28, 2026 4:01pm | Jul 28, 2026 4:02pm | Jul 28, 2026 7:09pm | Jul 28, 2026 7:09pm | Jul 28, 2026 7:53pm | Jul 28, 2026 8:17pm | Jul 28, 2026 8:19pm | Jul 28, 2026 8:19pm |  |  | Fair | No | System low voltage
Outage | J.E.26.07.35195 | C001867812 | Rayon Foster | Hanover | Completed | Load_292318 | Orange Bay - 310 | Jul 28, 2026 3:56pm | Jul 28, 2026 3:56pm | Jul 28, 2026 4:36pm | Jul 28, 2026 5:49pm | Jul 28, 2026 5:49pm | Jul 28, 2026 6:01pm | Jul 28, 2026 6:01pm | Jul 28, 2026 6:01pm |  |  | Rains | No | Blow 10 amps junction fuse remove fuse holder patrol primary line line was clear replace with 15 amps junction fuse and close after communicating with dispatcher
Non-Outage | J.E.26.07.26561 | C001867809 | Tajay Bernard | Hanover | Completed | Load_305016 | Orange Bay - 210 | Jul 28, 2026 3:55pm | Jul 28, 2026 3:55pm | Jul 28, 2026 4:16pm | Jul 28, 2026 4:16pm | Jul 28, 2026 5:45pm | Jul 28, 2026 6:04pm | Jul 28, 2026 6:04pm | Jul 28, 2026 6:04pm |  |  | Fair | No | Clean and remake joints at customer pothead, 2 clamps was usedVoltage found 104/110/214Voltage left 109/110/219
Non-Outage | J.E.26.07.31418 | C001867808 | Tajay Bernard | Hanover | Completed | Load_241441 | Orange Bay - 210 | Jul 28, 2026 3:54pm | Jul 28, 2026 3:55pm | Jul 28, 2026 6:32pm | Jul 28, 2026 6:32pm | Jul 28, 2026 6:32pm | Jul 28, 2026 6:33pm | Jul 28, 2026 6:34pm | Jul 28, 2026 6:34pm |  |  | Fair | No | Customer stated that power is at the premises
Non-Outage | J.E.26.07.35274 | C001867802 | Ryan Richards | null | Completed | null | null | Jul 28, 2026 3:52pm | Jul 28, 2026 3:52pm | Jul 28, 2026 7:30pm | Jul 28, 2026 7:30pm | Jul 28, 2026 8:39pm | Jul 28, 2026 11:46pm | Jul 28, 2026 11:46pm | Jul 28, 2026 11:46pm |  |  | Fair | No | Corroded phase and neutral drop lead found for 25 kva transformer open 25 kva transformer remade using 3 one bolt clamps and reclose transformer all customers are now with supply voltage 119/120/240 volts
Outage | J.E.26.07.35276 | C001867794 | Javid Vernon | Westmoreland | Completed | Load_262801 | Paradise - 110 | Jul 28, 2026 3:44pm | Jul 28, 2026 3:49pm | Jul 28, 2026 4:09pm | Jul 28, 2026 4:10pm | Jul 28, 2026 4:10pm | Jul 28, 2026 4:16pm | Jul 28, 2026 4:18pm | Jul 28, 2026 4:18pm |  |  | Fair | No | Customer got disconnected for none payment but customer got reconnect after paying bill
Outage | J.E.26.07.35247 | C001867789 | Andrew Powell | St.Elizabeth | Completed | Load_270016 | Maggotty - 210 | Jul 28, 2026 3:43pm | Jul 28, 2026 3:44pm | Jul 28, 2026 6:46pm | Jul 28, 2026 6:46pm | Jul 28, 2026 6:52pm | Jul 28, 2026 6:54pm | Jul 28, 2026 6:56pm | Jul 28, 2026 6:56pm | BrokenPole |  | Fair | No | Premises not located inadequately direction contact customer by telephone unsuccessful.
Non-Outage | J.E.26.07.35079 | C001867785 | Richard Nicholas | null | Completed | null | null | Jul 28, 2026 3:42pm | Jul 28, 2026 3:48pm | Jul 28, 2026 8:09pm | Jul 28, 2026 8:09pm | Jul 28, 2026 8:54pm | Jul 28, 2026 9:15pm | Jul 28, 2026 9:16pm | Jul 28, 2026 9:16pm |  |  | Fair | No | Rammy system prepaid failure.
Non-Outage | J.E.26.07.35103 | C001867786 | Richard Nicholas | null | Completed | null | null | Jul 28, 2026 3:42pm | Jul 29, 2026 3:50pm | Jul 29, 2026 3:55pm | Jul 29, 2026 3:55pm | Jul 29, 2026 5:42pm | Jul 29, 2026 5:42pm | Jul 29, 2026 5:44pm | Jul 29, 2026 5:44pm | Fire |  | Fair | No | Cannot locate,premises is in Kingston and not st.catherine.
Outage | J.E.26.07.35154 | C001867787 | Clyde Brown | St.Ann | Completed | Load_292830 | Cardiff Hall - 310 | Jul 28, 2026 3:42pm | Jul 28, 2026 3:51pm | Jul 28, 2026 4:03pm | Jul 28, 2026 4:03pm | Jul 28, 2026 4:03pm | Jul 28, 2026 3:51pm | Jul 28, 2026 4:10pm | Jul 28, 2026 4:10pm |  |  | Fair | No | Customer said supply was restored
Outage | J.E.26.07.35134 | C001867784 | Damion Reid | Manchester | Completed | Load_263292 | Kendal - 210 | Jul 28, 2026 3:41pm | Jul 28, 2026 3:41pm | Jul 28, 2026 4:55pm | Jul 28, 2026 4:55pm | Jul 28, 2026 5:47pm | Jul 28, 2026 5:55pm | Jul 28, 2026 5:56pm | Jul 28, 2026 5:56pm |  |  | Fair | No | Unable to contact or locate customer
Outage | J.E.26.07.35194 | C001867783 | Damion Reid | Manchester | Completed | Load_244809 | Kendal - 210 | Jul 28, 2026 3:41pm | Jul 28, 2026 3:41pm | Jul 28, 2026 5:59pm | Jul 28, 2026 5:59pm | Jul 28, 2026 6:30pm | Jul 28, 2026 7:29pm | Jul 28, 2026 7:32pm | Jul 28, 2026 7:32pm |  |  | Fair | No | One span of broken secondary phase conductor found cause by tree cut on secondary line open 25kva transformer fuse link splice an retention conductor using 20ft of #2 aluminum conductor one #2 preform one 2/0 preform one 1 bolt clamp and restore power
Outage | J.E.26.07.34796 | C001867782 | Fitzroy Turner | KSAS | Completed | Load_240280 | Rockfort - 410 | Jul 28, 2026 3:39pm | Jul 28, 2026 3:39pm | Jul 28, 2026 6:15pm | Jul 28, 2026 9:49pm | Jul 28, 2026 10:01pm | Jul 23, 2026 1:00am | Jul 28, 2026 11:15pm | Jul 28, 2026 11:15pm | Fire |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.07.34965 | C001867781 | Fitzroy Turner | KSAS | Completed | Load_244079 | Greenwich - 310 | Jul 28, 2026 3:39pm | Jul 28, 2026 3:39pm | Jul 28, 2026 9:41pm | Jul 28, 2026 9:43pm | Jul 28, 2026 9:43pm | Jul 28, 2026 9:45pm | Jul 28, 2026 9:48pm | Jul 28, 2026 9:48pm |  |  | EarthMovement | No | Found two 30 amps junction fuse found blown cause bagging primary line remove insulator to carry issue replaced two 30amps fuses supply restored to the areas
Outage | J.E.26.07.33467 | C001867780 | Raymond Lewis | St.Ann | Completed | Load_258103 | Roaring River - 410 | Jul 28, 2026 3:38pm | Jul 29, 2026 4:08pm | Jul 29, 2026 5:49pm | Jul 29, 2026 5:49pm | Jul 29, 2026 6:05pm | Jul 29, 2026 6:22pm | Jul 29, 2026 6:22pm | Jul 29, 2026 6:22pm | LeaningPole |  | Fair | No | 30 classes 6 hood DE pole number 113898 rotten out open secondary with straight and service wire
Outage | J.E.26.07.35018 | C001867763 | Fitzroy Turner | KSAS | Completed | Load_300873 | Cane River - 410 | Jul 28, 2026 3:37pm | Jul 28, 2026 3:38pm | Jul 28, 2026 5:01pm | Jul 28, 2026 5:01pm | Jul 28, 2026 5:25pm | Jul 28, 2026 6:10pm | Jul 28, 2026 6:11pm | Jul 28, 2026 6:11pm |  |  | Fair | No | Found defective 5 kva transformer in a bank of three 5kva transformer one defective
Outage | J.E.26.07.35117 | C001867766 | Tyrese Williams | St.Ann | Completed | Load_262864 | Cardiff Hall - 310 | Jul 28, 2026 3:37pm | Jul 28, 2026 3:38pm | Jul 28, 2026 4:31pm | Jul 28, 2026 4:31pm | Jul 28, 2026 5:52pm | Jul 28, 2026 6:04pm | Jul 28, 2026 6:05pm | Jul 28, 2026 6:05pm |  |  | Rains | No | Reset a 25kva transformer at pole
Outage | J.E.26.07.35121 | C001867768 | Fitzroy Turner | KSAS | Completed | Load_556650 | Cane River - 410 | Jul 28, 2026 3:37pm | Jul 28, 2026 3:39pm | Jul 28, 2026 6:20pm | Jul 28, 2026 6:20pm | Jul 28, 2026 6:41pm | Jul 28, 2026 6:47pm | Jul 28, 2026 6:49pm | Jul 28, 2026 6:49pm | BrokenWire |  | Fair | No | Found tree wire services neutral broken mid span splice and retention using one clamp supply restored to customer
Outage | J.E.26.07.35150 | C001867765 | Richard Nicholas | St.Catherine | Completed | Load_261113 | Tredegar - 310 | Jul 28, 2026 3:37pm | Jul 28, 2026 3:38pm | Jul 28, 2026 7:03pm | Jul 28, 2026 7:03pm | Jul 28, 2026 7:42pm | Jul 28, 2026 8:03pm | Jul 28, 2026 8:04pm | Jul 28, 2026 8:04pm |  |  | Fair | No | Area found ok
Outage | J.E.26.07.35155 | C001867769 | Richard Nicholas | St.Catherine | Completed | Load_266236 | Tredegar - 210 | Jul 28, 2026 3:37pm | Jul 28, 2026 3:38pm | Jul 28, 2026 9:17pm | Jul 28, 2026 9:17pm | Jul 28, 2026 9:40pm | Jul 28, 2026 9:53pm | Jul 28, 2026 9:54pm | Jul 28, 2026 9:54pm |  |  | Fair | No | Prepaid rammy failure
Outage | J.E.26.07.35215 | C001867771 | Romeo Brissett | St.James | Completed | Load_255565 | Bogue - 510 | Jul 28, 2026 3:37pm | Jul 28, 2026 3:38pm | Jul 28, 2026 4:12pm | Jul 28, 2026 4:12pm | Jul 28, 2026 4:51pm | Jul 28, 2026 5:40pm | Jul 28, 2026 5:52pm | Jul 28, 2026 5:52pm |  |  | Rains | No | Replaced (1)25amps junction fuse and (1)40amps junction fuse.
Outage | J.E.26.07.34779 | C001867762 | Nickolas Rodriques | St.Catherine | Completed | Load_270195 | Tredegar - 410 | Jul 28, 2026 3:36pm | Jul 29, 2026 8:57am | Jul 29, 2026 9:07am | Jul 29, 2026 9:12am | Jul 29, 2026 10:32am | Jul 29, 2026 10:41am | Jul 29, 2026 10:58am | Jul 29, 2026 10:58am |  |  | Fair | No | Power restored. Customer confirmed that the area outage was later restored.
Outage | J.E.26.07.34785 | C001867760 | Richard Nicholas | St.Catherine | Completed | Load_238911 | Tredegar - 210 | Jul 28, 2026 3:36pm | Jul 28, 2026 3:38pm | Jul 28, 2026 9:55pm | Jul 28, 2026 9:55pm | Jul 28, 2026 10:15pm | Jul 28, 2026 10:29pm | Jul 28, 2026 10:31pm | Jul 28, 2026 10:31pm |  |  | Fair | No | Area found ok
Outage | J.E.26.07.34897 | C001867759 | Fitzroy Turner | KSAS | Completed | Load_261859 | Hunts Bay - 210 | Jul 28, 2026 3:36pm | Jul 28, 2026 3:38pm | Jul 28, 2026 3:57pm | Jul 28, 2026 3:57pm | Jul 28, 2026 4:03pm | Jul 28, 2026 4:35pm | Jul 28, 2026 4:59pm | Jul 28, 2026 4:59pm | BrokenWire | Y | EarthMovement | No | Found bank of three transformer neutral drop leads corroded at pole use two one bolt clamps to carry out repair supply restored to the areas
Outage | J.E.26.07.35053 | C001867758 | Fitzroy Turner | KSAS | Completed | Load_248008 | Rockfort - 410 | Jul 28, 2026 3:36pm | Jul 28, 2026 3:38pm | Jul 28, 2026 6:16pm | Jul 28, 2026 7:33pm | Jul 28, 2026 8:11pm | Jul 28, 2026 8:15pm | Jul 28, 2026 8:17pm | Jul 28, 2026 8:17pm | TreeContact |  | Fair | No | Tree needs to cut from single phase line soon as possible.please send email to bushing department
Outage | J.E.26.07.35090 | C001867757 | Edward Royal | KSAS | Completed | Load_268518 | Hunts Bay - 810 | Jul 28, 2026 3:36pm | Jul 29, 2026 7:49am | Jul 29, 2026 3:01pm | Jul 29, 2026 3:02pm | Jul 29, 2026 3:02pm | Jul 29, 2026 3:35pm | Jul 29, 2026 3:35pm | Jul 29, 2026 3:35pm | Fire |  | Fair | No | Replaced hotline clamp to primary line
Non-Outage | J.E.26.07.35036 | C001867755 | Andrew Powell | null | Completed | null | null | Jul 28, 2026 3:34pm | Jul 28, 2026 3:37pm | Jul 28, 2026 9:55pm | Jul 28, 2026 9:55pm | Jul 28, 2026 9:55pm | Jul 28, 2026 9:56pm | Jul 28, 2026 9:57pm | Jul 28, 2026 9:57pm |  |  | Fair | No | Premises found okay customer stated that supply restored.
Outage | J.E.26.07.31847 | C001867752 | Richard Grant | St.Catherine | Completed | Load_266826 | New Michelton - 410 | Jul 28, 2026 3:33pm | Jul 28, 2026 3:34pm | Jul 28, 2026 4:21pm | Jul 28, 2026 4:21pm | Jul 28, 2026 5:50pm | Jul 28, 2026 5:51pm | Jul 28, 2026 5:51pm | Jul 28, 2026 5:51pm |  |  | Rains | No | Premises found okay.
Outage | J.E.26.07.34781 | C001867753 | Richard Grant | St.Catherine | Completed | Load_240992 | New Michelton - 210 | Jul 28, 2026 3:33pm | Jul 28, 2026 3:34pm | Jul 28, 2026 5:52pm | Jul 28, 2026 5:52pm | Jul 28, 2026 6:28pm | Jul 28, 2026 8:02pm | Jul 28, 2026 8:03pm | Jul 28, 2026 8:03pm |  |  | Rains | No | 25amps and 3amps fuse found blown at 3phase junction pole and for 25kva transformer, respectively, caused by bird contact. 25amps and 3amps fuse replaced with same size fuse and placed back at respective switches. Supply restored and area left okay
Outage | J.E.26.07.35048 | C001867754 | Richard Grant | St.Catherine | Completed | Load_240274 | New Michelton - 410 | Jul 28, 2026 3:33pm | Jul 28, 2026 3:34pm | Jul 28, 2026 8:03pm | Jul 28, 2026 8:04pm | Jul 28, 2026 9:36pm | Jul 28, 2026 9:38pm | Jul 28, 2026 9:38pm | Jul 28, 2026 9:38pm |  |  | Rains | No | Area and premises found with supply. Premises found okay
Outage | J.E.26.07.34664 | C001867741 | Nickolas Rodriques | St.Catherine | Completed | Load_240706 | Twickenham - 310 | Jul 28, 2026 3:31pm | Jul 28, 2026 3:32pm | Jul 28, 2026 3:45pm | Jul 28, 2026 3:56pm | Jul 28, 2026 4:59pm | Jul 28, 2026 5:10pm | Jul 28, 2026 5:11pm | Jul 28, 2026 5:11pm |  |  | Fair | No | Found premises with electricity. Customer stated that the power was restored.
Outage | J.E.26.07.35135 | C001867740 | Andrew Powell | St.Elizabeth | Completed | Load_1002241 | Maggotty - 210 | Jul 28, 2026 3:30pm | Jul 28, 2026 3:32pm | Jul 28, 2026 4:50pm | Jul 28, 2026 4:50pm | Jul 28, 2026 5:15pm | Jul 28, 2026 5:39pm | Jul 28, 2026 5:41pm | Jul 28, 2026 5:41pm |  |  | Fair | No | Remade corroded service wire joints at secondary line 3 wire using three clamps, voltage reading 107v-107v phase to neutral 214v cross phase.
Outage | J.E.26.07.34963 | C001867737 | Andrew Powell | St.Elizabeth | Completed | Load_1002274 | Maggotty - 210 | Jul 28, 2026 3:29pm | Jul 28, 2026 3:30pm | Jul 28, 2026 3:49pm | Jul 28, 2026 3:49pm | Jul 28, 2026 4:30pm | Jul 28, 2026 4:31pm | Jul 28, 2026 4:36pm | Jul 28, 2026 4:36pm |  |  | Fair | No | Found 3 wire meter and 100 feet #6 triplex service wire required to connect customer leaves without supply, please refer to field service department for replacement, meter #2660674.
Outage | J.E.26.07.35203 | C001867739 | Andrew Powell | St.Elizabeth | Completed | Load_265089 | Maggotty - 210 | Jul 28, 2026 3:29pm | Jul 28, 2026 3:31pm | Jul 28, 2026 6:57pm | Jul 28, 2026 6:57pm | Jul 28, 2026 7:33pm | Jul 28, 2026 8:04pm | Jul 28, 2026 8:06pm | Jul 28, 2026 8:06pm |  |  | Fair | No | Disconnection due to outstanding bills, customer leaves without supply.
Outage | J.E.26.07.35214 | C001867738 | Andrew Powell | St.Elizabeth | Completed | Load_242373 | Maggotty - 210 | Jul 28, 2026 3:29pm | Jul 28, 2026 3:31pm | Jul 28, 2026 5:54pm | Jul 28, 2026 5:54pm | Jul 28, 2026 6:33pm | Jul 28, 2026 6:41pm | Jul 28, 2026 6:43pm | Jul 28, 2026 6:43pm |  |  | Fair | No | Premises found okay customer stated that it was internal issues, voltage reading 112v-113v phase to neutral 225v cross phase inside meter socket 3 wire.
Non-Outage | J.E.26.07.35015 | C001867732 | Edward Royal | KSAN | Completed | Load_239823 | Washington Blvd - 710 | Jul 28, 2026 3:28pm | Jul 28, 2026 3:30pm | Jul 28, 2026 9:38pm | Jul 28, 2026 9:38pm | Jul 28, 2026 9:38pm | Jul 28, 2026 9:39pm | Jul 28, 2026 9:40pm | Jul 28, 2026 9:40pm | BrokenWire |  | Fair | No | Premises found ok customer was referring about 3rd party cable
Outage | J.E.26.07.34503 | C001867727 | Nickolas Rodriques | St.Catherine | Completed | Load_302901 | Rhodens Pen - 210 | Jul 28, 2026 3:27pm | Jul 28, 2026 3:28pm | Jul 28, 2026 7:56pm | Jul 28, 2026 8:00pm | Jul 28, 2026 8:54pm | Jul 28, 2026 9:22pm | Jul 28, 2026 9:26pm | Jul 28, 2026 9:26pm |  |  | Fair | No | Found customer with electricity. The customer stated that she had a breaker issue which was resolved by her Electrician.
Outage | J.E.26.07.35130 | C001867725 | Richman Whyte | St.Elizabeth | Completed | Load_265987 | Maggotty - 110 | Jul 28, 2026 3:27pm | Jul 28, 2026 3:28pm | Jul 28, 2026 6:24pm | Jul 28, 2026 6:24pm | Jul 28, 2026 6:25pm | Jul 28, 2026 6:27pm | Jul 28, 2026 6:27pm | Jul 28, 2026 6:27pm |  |  | Fair | No | Customer got disconnected for none payment of bill referral already sent to field service
Outage | J.E.26.07.35033 | C001867722 | Denton Williams | Portland | Completed | Load_267293 | Port Antonio - 310 | Jul 28, 2026 3:26pm | Jul 28, 2026 3:26pm | Jul 28, 2026 9:11pm | Jul 28, 2026 9:11pm | Jul 28, 2026 10:09pm | Jul 28, 2026 10:10pm | Jul 28, 2026 10:17pm | Jul 28, 2026 10:17pm |  |  | Fair | No | The customer informed us that they have a service wire break that’s located beyond the meter. Customer was advised to consult a licensed electrician to evaluate and fix the issue.
Outage | J.E.26.07.35122 | C001867723 | Denton Williams | Portland | Completed | Load_243585 | Port Antonio - 410 | Jul 28, 2026 3:26pm | Jul 28, 2026 3:26pm | Jul 28, 2026 3:57pm | Jul 28, 2026 3:57pm | Jul 28, 2026 4:53pm | Jul 28, 2026 7:03pm | Jul 28, 2026 7:06pm | Jul 28, 2026 7:06pm | BrokenWire |  | Fair | No | Use seven clamps to change connections on service line and transformer drop leads. 119/119/239 volts, at transformer point
Outage | J.E.26.07.34846 | C001867720 | Derrick Grubb | St.Thomas | Completed | Load_269308 | Good Year - 210 | Jul 28, 2026 3:25pm | Jul 28, 2026 3:25pm | Jul 28, 2026 4:49pm | Jul 28, 2026 4:49pm | Jul 28, 2026 4:49pm | Jul 28, 2026 5:36pm | Jul 28, 2026 5:37pm | Jul 28, 2026 5:37pm | BrokenWire |  | Fair | No | Premises closed, customer advised to call when someone is at premises
Outage | J.E.26.07.34964 | C001867719 | Derrick Grubb | St.Thomas | Completed | Load_242327 | Good Year - 210 | Jul 28, 2026 3:25pm | Jul 28, 2026 3:25pm | Jul 28, 2026 5:37pm | Jul 28, 2026 5:56pm | Jul 28, 2026 6:04pm | Jul 28, 2026 6:06pm | Jul 28, 2026 6:07pm | Jul 28, 2026 6:07pm | TreeContact | Y | Fair | No | Tree contact with open secondary
Non-Outage | J.E.26.07.16993 | C001867715 | Andrae Dawkins | St.James | Completed | Load_266001 | Queens Drive - 310 | Jul 28, 2026 3:24pm | Jul 29, 2026 9:08am | Jul 29, 2026 12:59pm | Jul 29, 2026 12:59pm | Jul 29, 2026 12:59pm | Jul 29, 2026 12:04pm | Jul 29, 2026 1:21pm | Jul 29, 2026 1:21pm |  |  | Fair | No | Kingston call customer complained about a post that has been broken in two
Non-Outage | J.E.26.07.34986 | C001867718 | Derrick Grubb | null | Completed | null | null | Jul 28, 2026 3:24pm | Jul 28, 2026 3:25pm | Jul 28, 2026 5:37pm | Jul 28, 2026 5:38pm | Jul 28, 2026 5:51pm | Jul 28, 2026 5:52pm | Jul 28, 2026 5:56pm | Jul 28, 2026 5:56pm | BrokenPole |  | Fair | No | Broken 30 class six wooden pole broken pole belong to flow however number twisted triplex on pole , refer to maintenance
Outage | J.E.26.07.35104 | C001867716 | Ryan Richards | Manchester | Completed | Load_256152 | Spur Tree - 310 | Jul 28, 2026 3:24pm | Jul 28, 2026 3:39pm | Jul 28, 2026 4:28pm | Jul 28, 2026 4:28pm | Jul 28, 2026 5:36pm | Jul 28, 2026 5:55pm | Jul 28, 2026 5:55pm | Jul 28, 2026 5:55pm | BrokenWire |  | Fair | No | Rotten service wire found rotten service wires also supply 2 o the meter with power replaced 70ft#6 triplex 3 penunion 3 one bolt clamps voltage leave with customer 113/114/228 volts
Outage | J.E.26.07.35123 | C001867717 | Derrick Grubb | St.Thomas | Completed | Load_249679 | Lysson - 410 | Jul 28, 2026 3:24pm | Jul 28, 2026 3:25pm | Jul 28, 2026 6:07pm | Jul 28, 2026 6:07pm | Jul 28, 2026 8:31pm | Jul 28, 2026 8:34pm | Jul 28, 2026 8:47pm | Jul 28, 2026 8:47pm |  |  | Fair | No | Reset 10 kva transformer at pole number 0004988, area needs urgent bushings
Non-Outage | J.E.26.07.12869 | C001867713 | Andrae Dawkins | St.James | Completed | Load_290408 | Queens Drive - 310 | Jul 28, 2026 3:23pm | Jul 29, 2026 9:09am | Jul 29, 2026 3:02pm | Jul 29, 2026 3:02pm | Jul 29, 2026 3:02pm | Jul 29, 2026 12:19pm | Jul 29, 2026 3:03pm | Jul 29, 2026 3:03pm |  |  | Fair | No | Unable to reach customer mobile cannot locate customer due to no directions
Non-Outage | J.E.26.07.11486 | C001867703 | Swon Miller | St.James | Completed | Load_248507 | Queens Drive - 710 | Jul 28, 2026 3:22pm | Jul 28, 2026 3:23pm | Jul 28, 2026 3:34pm | Jul 28, 2026 3:34pm | Jul 28, 2026 4:31pm | Jul 29, 2026 4:44am | Jul 28, 2026 4:46pm | Jul 28, 2026 4:46pm |  |  | Fair | No | Check and found area okay voltage found 116/116/233 voltage left 116/116/233
Outage | J.E.26.07.35099 | C001867700 | Richman Whyte | Westmoreland | Completed | Load_248237 | Paradise - 310 | Jul 28, 2026 3:22pm | Jul 28, 2026 3:26pm | Jul 28, 2026 8:28pm | Jul 28, 2026 8:28pm | Jul 28, 2026 8:28pm | Jul 28, 2026 8:29pm | Jul 28, 2026 8:29pm | Jul 28, 2026 8:29pm |  |  | Fair | No | Reconnection required need 100ft service wire
Outage | J.E.26.07.35200 | C001867701 | Damion Reid | Manchester | Completed | Load_245396 | Kendal - 210 | Jul 28, 2026 3:22pm | Jul 28, 2026 3:40pm | Jul 28, 2026 7:32pm | Jul 28, 2026 7:32pm | Jul 28, 2026 7:51pm | Jul 28, 2026 8:59pm | Jul 28, 2026 9:00pm | Jul 28, 2026 9:00pm |  |  | Fair | No | Blown 30amp junction fuse found cause by tree limb remove limb and replace blown fuse
Outage | J.E.26.07.35129 | C001867699 | Raymond Carr | St.Mary | Completed | Load_351803 | Oracabessa - 110 | Jul 28, 2026 3:21pm | Jul 28, 2026 3:22pm | Jul 28, 2026 3:36pm | Jul 28, 2026 3:36pm | Jul 28, 2026 4:31pm | Jul 28, 2026 4:17pm | Jul 28, 2026 4:50pm | Jul 28, 2026 4:50pm |  |  | Fair | No | Blown junction fuse found , line patrol and found okay however tree contact was suspected.A 40 amp fuse fuse was used to renew supply was restored.
Outage | J.E.26.07.34698 | C001867691 | Christopher Edwards | KSAN | Completed | Load_1001097 | Constant Spring - 410 | Jul 28, 2026 3:15pm | Jul 29, 2026 7:48am | Jul 29, 2026 8:05am | Jul 29, 2026 8:05am | Jul 29, 2026 8:26am | Jul 29, 2026 8:58am | Jul 29, 2026 9:00am | Jul 29, 2026 9:00am |  |  | Fair | No | Clear bamboo off open secondary wiresThat was causing wire to bang
Outage | J.E.26.07.35044 | C001867687 | Kaydon Taylor | KSAN | Completed | Load_262628 | Constant Spring - 410 | Jul 28, 2026 3:15pm | Jul 28, 2026 3:24pm | Jul 28, 2026 8:48pm | Jul 28, 2026 8:48pm | Jul 28, 2026 11:25pm | Jul 28, 2026 11:28pm | Jul 28, 2026 11:28pm | Jul 28, 2026 11:28pm | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Rains | No | 15 amp junction fuse found blown n replace at pole #0001447
Outage | J.E.26.07.35136 | C001867689 | Christopher Edwards | KSAN | Completed | Load_239622 | Constant Spring - 410 | Jul 28, 2026 3:15pm | Jul 29, 2026 7:48am | Jul 29, 2026 9:00am | Jul 29, 2026 9:00am | Jul 29, 2026 9:31am | Jul 29, 2026 10:01am | Jul 29, 2026 10:02am | Jul 29, 2026 10:02am | TreeContact | Y | Fair | No | Clear vegetation off transformer Refuse blown 25 kva transformer Using (1) 2 amps
Outage | J.E.26.07.34881 | C001867680 | Edward Royal | KSAN | Completed | Load_293752 | Washington Blvd - 710 | Jul 28, 2026 3:12pm | Jul 28, 2026 3:13pm | Jul 28, 2026 3:43pm | Jul 28, 2026 6:50pm | Jul 28, 2026 6:50pm | Jul 28, 2026 6:51pm | Jul 28, 2026 6:51pm | Jul 28, 2026 6:51pm |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.07.35142 | C001867679 | Edward Royal | KSAN | Completed | Load_293751 | Washington Blvd - 710 | Jul 28, 2026 3:12pm | Jul 28, 2026 3:13pm | Jul 28, 2026 5:25pm | Jul 28, 2026 5:25pm | Jul 28, 2026 5:25pm | Jul 28, 2026 5:33pm | Jul 28, 2026 5:34pm | Jul 28, 2026 5:34pm |  |  | Fair | No | Replaced 2A transformer fuse
Outage | J.E.26.07.35144 | C001867682 | Edward Royal | KSAN | Completed | Load_293753 | Washington Blvd - 710 | Jul 28, 2026 3:12pm | Jul 28, 2026 3:13pm | Jul 28, 2026 5:34pm | Jul 28, 2026 5:34pm | Jul 28, 2026 5:34pm | Jul 28, 2026 5:35pm | Jul 28, 2026 5:35pm | Jul 28, 2026 5:35pm |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.07.35192 | C001867681 | Edward Royal | KSAN | Completed | Load_266051 | Washington Blvd - 710 | Jul 28, 2026 3:12pm | Jul 28, 2026 3:13pm | Jul 28, 2026 5:36pm | Jul 28, 2026 5:36pm | Jul 28, 2026 5:58pm | Jul 28, 2026 6:39pm | Jul 28, 2026 6:49pm | Jul 28, 2026 6:49pm |  |  | Fair | No | Spliced and reconnected secondary neutral using 2 single bolt clamp
Outage | J.E.26.07.34702 | C001867677 | Edward Royal | KSAN | Completed | Load_257365 | Washington Blvd - 310 | Jul 28, 2026 3:10pm | Jul 28, 2026 3:13pm | Jul 28, 2026 4:31pm | Jul 28, 2026 4:31pm | Jul 28, 2026 4:31pm | Jul 28, 2026 5:07pm | Jul 28, 2026 5:16pm | Jul 28, 2026 5:16pm | BrokenWire |  | Fair | No | Spliced and reconnected services cable using 60ft service cables 4 single bolt clamp pole #0167171
Outage | J.E.26.07.34878 | C001867678 | Edward Royal | KSAS | Completed | Load_248863 | Greenwich - 710 | Jul 28, 2026 3:10pm | Jul 29, 2026 7:40am | Jul 29, 2026 3:57pm | Jul 29, 2026 3:57pm | Jul 29, 2026 3:57pm | Jul 29, 2026 4:04pm | Jul 29, 2026 4:04pm | Jul 29, 2026 4:04pm |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.07.34978 | C001867614 | Moses Elliston | St.Catherine | Completed | Load_238151 | Twickenham - 310 | Jul 28, 2026 2:28pm | Jul 28, 2026 2:28pm | Jul 29, 2026 10:15am | Jul 29, 2026 10:15am | Jul 29, 2026 10:15am | Jul 29, 2026 10:16am | Jul 29, 2026 10:16am | Jul 29, 2026 10:16am |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.07.34620 | C001867612 | Neville Spencer | Clarendon | Completed | Load_240258 | Parnassus - 210 | Jul 28, 2026 2:25pm | Jul 28, 2026 2:25pm | Jul 28, 2026 2:39pm | Jul 28, 2026 2:39pm | Jul 28, 2026 3:10pm | Jul 28, 2026 3:10pm | Jul 28, 2026 3:11pm | Jul 28, 2026 3:11pm | BrokenWire |  | Fair | No | Unable to locate customer.
Outage | J.E.26.07.35111 | C001867613 | Andre Williams | Trelawny | Completed | Load_249194 | Duncans - 110 | Jul 28, 2026 2:25pm | Jul 28, 2026 2:26pm | Jul 28, 2026 2:33pm | Jul 28, 2026 2:33pm | Jul 28, 2026 3:12pm | Jul 28, 2026 4:08pm | Jul 28, 2026 4:08pm | Jul 28, 2026 4:08pm |  |  | Rains | No | Patrol line section re fuse and close 15 amp junction and 4 amp on 50 kva transformer.
Non-Outage | J.E.26.07.34867 | C001867589 | Romaine Roberts | St.Mary | Completed | Load_243466 | Highgate -110 | Jul 28, 2026 2:06pm | Jul 28, 2026 2:06pm | Jul 28, 2026 2:34pm | Jul 28, 2026 2:34pm | Jul 28, 2026 2:34pm | Jul 28, 2026 2:35pm | Jul 28, 2026 2:35pm | Jul 28, 2026 2:35pm | BrokenWire |  | Fair | No | Illegal connections burn down 2 span of secondary phase and neutral open and close 25 kva to splice and retention conductor power restore
Non-Outage | J.E.26.07.35021 | C001867572 | Derrick Dawkins | null | Completed | null | null | Jul 28, 2026 1:58pm | Jul 28, 2026 2:21pm | Jul 28, 2026 3:16pm | Jul 28, 2026 3:16pm | Jul 28, 2026 3:27pm | Jul 28, 2026 4:09pm | Jul 28, 2026 4:10pm | Jul 28, 2026 4:10pm |  |  | Rains | No | Sanction need to be repaired before making connection customer advised to get an electrician
Outage | J.E.26.07.34984 | C001867571 | Andre Williams | Trelawny | Completed | Load_249842 | Duncans - 210 | Jul 28, 2026 1:56pm | Jul 28, 2026 1:56pm | Jul 28, 2026 4:10pm | Jul 28, 2026 4:10pm | Jul 28, 2026 4:47pm | Jul 28, 2026 4:48pm | Jul 28, 2026 4:49pm | Jul 28, 2026 4:49pm |  |  | Rains | No | Premises found ok and with supply voltage at meter 118+118=236
Outage | J.E.26.07.34858 | C001867567 | Moses Elliston | St.Catherine | Completed | Load_557179 | Tredegar - 410 | Jul 28, 2026 1:50pm | Jul 28, 2026 1:54pm | Jul 29, 2026 1:32pm | Jul 29, 2026 1:32pm | Jul 29, 2026 1:32pm | Jul 29, 2026 1:32pm | Jul 29, 2026 1:37pm | Jul 29, 2026 1:37pm |  |  | Fair | No | Defective collector to be change .Refer to Paulstan Francis.By Mother Fuller Church .Badly Leaning pole ,and urgent bushings.Refer to Roy Brown.
Outage | J.E.26.07.34798 | C001867557 | Wan Carlos Scarlett | Portmore | Completed | Load_245046 | Naggo Head - 610 | Jul 28, 2026 1:42pm | Jul 28, 2026 1:54pm | Jul 28, 2026 2:12pm | Jul 28, 2026 4:21pm | Jul 28, 2026 5:52pm | Jul 28, 2026 5:55pm | Jul 28, 2026 5:56pm | Jul 28, 2026 5:56pm |  |  | Fair | No | Customer confirm that power supply has been restored
Outage | J.E.26.07.34710 | C001867552 | Nickolas Rodriques | St.Catherine | Completed | Load_266075 | Twickenham - 210 | Jul 28, 2026 1:38pm | Jul 28, 2026 3:25pm | Jul 28, 2026 3:43pm | Jul 28, 2026 5:12pm | Jul 28, 2026 7:21pm | Jul 28, 2026 7:40pm | Jul 28, 2026 7:42pm | Jul 28, 2026 7:42pm |  |  | Fair | No | Unable to locate or communicate with the customer after several attempts. Need proper directions.
Outage | J.E.26.07.34808 | C001867553 | Wan Carlos Scarlett | St.Catherine | Completed | Load_251909 | Twickenham - 210 | Jul 28, 2026 1:38pm | Jul 28, 2026 1:54pm | Jul 28, 2026 7:56pm | Jul 28, 2026 7:56pm | Jul 28, 2026 8:55pm | Jul 28, 2026 9:48pm | Jul 28, 2026 9:49pm | Jul 28, 2026 9:49pm |  |  | Fair | No | Found customer 3 wire service at pole with one of the phase corroded use 2 one bolt clamps at open secondary line phase readings 114-113-229
Outage | J.E.26.07.34999 | C001867551 | Daniel Francis | St.Ann | Completed | Load_269408 | Ocho Rios - 310 | Jul 28, 2026 1:37pm | Jul 28, 2026 1:37pm | Jul 28, 2026 2:00pm | Jul 28, 2026 2:00pm | Jul 28, 2026 2:41pm | Jul 28, 2026 2:47pm | Jul 28, 2026 2:48pm | Jul 28, 2026 2:48pm |  |  | Fair | No | Pole #0098830 change one 2amp fuse
Non-Outage | J.E.26.07.34973 | C001867543 | Edward Royal | null | Completed | null | null | Jul 28, 2026 1:33pm | Jul 28, 2026 1:33pm | Jul 28, 2026 1:54pm | Jul 28, 2026 1:54pm | Jul 28, 2026 2:41pm | Jul 28, 2026 2:44pm | Jul 28, 2026 2:44pm | Jul 28, 2026 2:44pm | Fire |  | Fair | No | Defective 100kva transformer need to be change reffered to maintenance it a bank of 3 transformer and the power transformer caught on fire
Outage | J.E.26.07.34959 | C001867542 | Denton Williams | Portland | Completed | Load_249793 | Port Antonio - 310 | Jul 28, 2026 1:30pm | Jul 28, 2026 3:27pm | Jul 28, 2026 3:49pm | Jul 28, 2026 3:49pm | Jul 28, 2026 3:49pm | Jul 28, 2026 3:49pm | Jul 28, 2026 3:52pm | Jul 28, 2026 3:52pm |  |  | Fair | No | Customer was on disconnection, customer is now connected with the aid of customer service.
Outage | J.E.26.07.34955 | C001867541 | Jowayne Newmans | Portland | Completed | Load_241254 | Port Antonio - 310 | Jul 28, 2026 1:29pm | Jul 28, 2026 1:30pm | Jul 28, 2026 1:35pm | Jul 28, 2026 1:35pm | Jul 28, 2026 1:56pm | Jul 28, 2026 2:53pm | Jul 28, 2026 2:53pm | Jul 28, 2026 2:53pm |  |  | Fair | No | Patrol and found 2 20 amp junction fuses blown cause by overgrown vegetation on insulated primary conductor, remove vegetation off primary conductor and replace 2 20 amp fuses. However extensive bushing is required to clear primary conductor from vegetation refer call to maintenance for follow up. Customer now has electricity.
Non-Outage | J.E.26.07.34674 | C001867534 | Andre Williams | Trelawny | Completed | Load_269738 | Duncans - 210 | Jul 28, 2026 1:25pm | Jul 28, 2026 1:25pm | Jul 28, 2026 5:55pm | Jul 28, 2026 6:10pm | Jul 28, 2026 6:10pm | Jul 28, 2026 6:10pm | Jul 28, 2026 6:10pm | Jul 28, 2026 6:10pm |  |  | Fair | No | Customer phone not responding unable to locate
Non-Outage | J.E.26.07.34904 | C001867535 | Andre Williams | Trelawny | Completed | Load_267170 | Duncans - 210 | Jul 28, 2026 1:25pm | Jul 28, 2026 1:25pm | Jul 28, 2026 2:24pm | Jul 28, 2026 4:53pm | Jul 28, 2026 5:52pm | Jul 28, 2026 5:54pm | Jul 28, 2026 5:54pm | Jul 28, 2026 5:54pm |  |  | Fair | No | No low voltage detected, voltage at pothead 115+119=234
Outage | J.E.26.07.34383 | C001867511 | Neville Spencer | Clarendon | Completed | Load_267245 | Parnassus - 210 | Jul 28, 2026 12:58pm | Jul 28, 2026 12:58pm | Jul 28, 2026 3:11pm | Jul 28, 2026 3:11pm | Jul 28, 2026 4:18pm | Jul 28, 2026 4:18pm | Jul 28, 2026 4:20pm | Jul 28, 2026 4:20pm |  |  | Fair | No | Unable to locate customer.
Outage | J.E.26.07.34765 | C001867510 | Neville Spencer | Clarendon | Completed | Load_262277 | May Pen - 210 | Jul 28, 2026 12:56pm | Jul 28, 2026 12:56pm | Jul 28, 2026 4:20pm | Jul 28, 2026 4:20pm | Jul 28, 2026 5:28pm | Jul 28, 2026 5:30pm | Jul 28, 2026 5:31pm | Jul 28, 2026 5:31pm |  |  | Fair | No | Premises closed.
Non-Outage | J.E.26.07.34912 | C001867505 | Wayne Dillion | null | Completed | null | null | Jul 28, 2026 12:54pm | Jul 28, 2026 12:57pm | Jul 28, 2026 1:59pm | Jul 28, 2026 1:59pm | Jul 28, 2026 1:59pm | Jul 28, 2026 2:00pm | Jul 28, 2026 2:00pm | Jul 28, 2026 2:00pm |  |  | Fair | No | Customer said problem has been resolved from yesterday evening
Outage | J.E.26.07.34889 | C001867508 | Andrew Powell | St.Elizabeth | Completed | Load_246963 | Maggotty - 210 | Jul 28, 2026 12:54pm | Jul 28, 2026 3:30pm | Jul 28, 2026 3:39pm | Jul 28, 2026 8:18pm | Jul 28, 2026 8:18pm | Jul 28, 2026 8:18pm | Jul 28, 2026 8:18pm | Jul 28, 2026 8:18pm |  |  | Fair | No | Premises found okay customer stated that supply restored.
Outage | J.E.26.07.34909 | C001867507 | Richard Watson | St.Elizabeth | Completed | Load_1002147 | Maggotty - 110 | Jul 28, 2026 12:54pm | Jul 28, 2026 4:26pm | Jul 28, 2026 5:02pm | Jul 28, 2026 5:02pm | Jul 28, 2026 5:29pm | Jul 28, 2026 6:32pm | Jul 28, 2026 6:36pm | Jul 28, 2026 6:36pm |  |  | Fair | No | Replace approximately 60ft of #6 triplex service wire, also use three #6-#6 service sleeves and three 1bolt clamps, cause by the passage of hurricane Melissa, voltage left 110v, 110v, 220v.
Outage | J.E.26.07.32949 | C001867495 | Donald Cunningham | St.Catherine | Completed | Load_238478 | New Michelton - 410 | Jul 28, 2026 12:46pm | Jul 28, 2026 12:56pm | Jul 28, 2026 1:15pm | Jul 28, 2026 1:15pm | Jul 28, 2026 2:06pm | Jul 28, 2026 2:14pm | Jul 28, 2026 2:20pm | Jul 28, 2026 2:20pm |  |  | Fair | No | Premises found ok supply restored
Outage | J.E.26.07.34920 | C001867494 | Gregory Grossett | Portland | Completed | Load_251129 | Port Antonio - 410 | Jul 28, 2026 12:46pm | Jul 28, 2026 12:50pm | Jul 28, 2026 12:53pm | Jul 28, 2026 12:53pm | Jul 28, 2026 1:45pm | Jul 28, 2026 2:45pm | Jul 28, 2026 2:47pm | Jul 28, 2026 2:47pm |  | Y | Fair | No | 8amps junction fuse blown cause by tree fall on primary conductor cut and removed tree then restore supply to the area.
Outage | J.E.26.07.34829 | C001867493 | Richard Samuda | Manchester | Completed | Load_1002467 | Kendal - 210 | Jul 28, 2026 12:44pm | Jul 28, 2026 12:59pm | Jul 28, 2026 1:04pm | Jul 28, 2026 1:04pm | Jul 28, 2026 1:41pm | Jul 28, 2026 2:10am | Jul 28, 2026 2:10pm | Jul 28, 2026 2:10pm | BrokenWire |  | Fair | No | Pole number: 042292 Found 8 amp junction blown patrol line found nothing fuse customer back to normal
Outage | J.E.26.07.33764 | C001867460 | Derrick Dawkins | Hanover | Completed | Load_254647 | Orange Bay - 310 | Jul 28, 2026 12:11pm | Jul 28, 2026 12:12pm | Jul 28, 2026 1:37pm | Jul 28, 2026 1:49pm | Jul 28, 2026 2:40pm | Jul 28, 2026 2:03pm | Jul 28, 2026 2:43pm | Jul 28, 2026 2:43pm |  |  | Rains | No | Customer stated she did not make a report
Outage | J.E.26.07.34854 | C001867452 | Romaine Roberts | St.Mary | Completed | Load_243466 | Highgate -110 | Jul 28, 2026 12:08pm | Jul 28, 2026 12:09pm | Jul 28, 2026 1:12pm | Jul 28, 2026 1:12pm | Jul 28, 2026 2:10pm | Jul 28, 2026 2:33pm | Jul 28, 2026 2:34pm | Jul 28, 2026 2:34pm | BrokenWire |  | Fair | No | Illegal connections burn down 2 span of secondary phase and neutral open and close 25 kva to splice and retention conductor power restore
Non-Outage | J.E.26.07.34811 | C001867424 | Michael Paterson | null | Completed | null | null | Jul 28, 2026 11:33am | Jul 28, 2026 11:34am | Jul 28, 2026 12:51pm | Jul 28, 2026 12:53pm | Jul 28, 2026 12:53pm | Jul 28, 2026 12:54pm | Jul 28, 2026 12:55pm | Jul 28, 2026 12:55pm |  |  | Fair | No | Customer confirm ok via phone call.
Non-Outage | J.E.26.07.34795 | C001867419 | Neville Spencer | Clarendon | Completed | Load_243509 | Parnassus - 210 | Jul 28, 2026 11:30am | Jul 28, 2026 11:30am | Jul 28, 2026 12:51pm | Jul 28, 2026 12:52pm | Jul 28, 2026 2:01pm | Jul 28, 2026 2:01pm | Jul 28, 2026 2:38pm | Jul 28, 2026 2:38pm |  |  | Fair | No | Remade burnt out clamps at pothead on 4 wire service used 2. Clamps voltage reading 112. 113 196 224 227 228 supply restored..
Outage | J.E.26.07.34703 | C001867421 | Evan Spaulding | St.Mary | Completed | Load_263045 | Highgate - 210 | Jul 28, 2026 11:30am | Jul 28, 2026 3:19pm | Jul 28, 2026 7:28pm | Jul 28, 2026 7:28pm | Jul 28, 2026 7:28pm | Jul 28, 2026 7:28pm | Jul 28, 2026 7:29pm | Jul 28, 2026 7:29pm |  |  | Fair | No | Premises found lock
Outage | J.E.26.07.34800 | C001867420 | Wayne Dillion | St.Elizabeth | Completed | Load_248132 | Maggotty - 210 | Jul 28, 2026 11:30am | Jul 28, 2026 11:31am | Jul 28, 2026 12:04pm | Jul 28, 2026 12:04pm | Jul 28, 2026 12:04pm | Jul 28, 2026 12:06pm | Jul 28, 2026 12:06pm | Jul 28, 2026 12:06pm |  |  | Fair | No | Customer said supply was restored.
Non-Outage | J.E.26.07.01795 | C001867416 | Odeanie Davis | KSAS | Completed | Load_261609 | Three Miles - 410 | Jul 28, 2026 11:29am | Jul 28, 2026 11:29am | Jul 28, 2026 3:16pm | Jul 29, 2026 2:46pm | Jul 29, 2026 2:46pm | Jul 29, 2026 3:00pm | Jul 29, 2026 2:47pm | Jul 29, 2026 2:47pm |  |  | Fair | No | Loses team needed at location
Outage | J.E.26.07.34766 | C001867418 | Jowayne Newmans | Portland | Completed | Load_349991 | Port Antonio - 310 | Jul 28, 2026 11:29am | Jul 28, 2026 11:30am | Jul 28, 2026 11:35am | Jul 28, 2026 11:35am | Jul 28, 2026 12:01pm | Jul 28, 2026 12:31pm | Jul 28, 2026 12:31pm | Jul 28, 2026 12:31pm |  |  | Fair | No | Patrol and found 15and 10 amp junction fuses blown cause by wild life, repair by replace 10 and 15 amp fuses.customers now have electricity.
Outage | J.E.26.07.34769 | C001867394 | Selvin White | St.Elizabeth | Completed | Load_292676 | Maggotty - 110 | Jul 28, 2026 11:17am | Jul 28, 2026 11:19am | Jul 28, 2026 1:59pm | Jul 28, 2026 1:59pm | Jul 28, 2026 2:33pm | Jul 28, 2026 2:54pm | Jul 28, 2026 2:54pm | Jul 28, 2026 2:54pm |  |  | Fair | No | Replace a defective 8 amp junction fuse at the entrance to the lane opposite the cemetery after patrolling single phase primary at Comfort Hall district. Supply restored to the affected customers.
Outage | J.E.26.07.34790 | C001867393 | Wayne Dillion | Manchester | Completed | Load_252998 | Spur Tree - 210 | Jul 28, 2026 11:17am | Jul 28, 2026 11:18am | Jul 28, 2026 11:59am | Jul 28, 2026 11:59am | Jul 28, 2026 11:59am | Jul 28, 2026 12:03pm | Jul 28, 2026 12:04pm | Jul 28, 2026 12:04pm |  |  | Fair | No | Customer has been disconnected due to none payment of bill.
Outage | J.E.26.07.34546 | C001867386 | Eric Williams | KSAS | Completed | Load_239591 | Cane River - 610 | Jul 28, 2026 11:09am | Jul 28, 2026 11:10am | Jul 28, 2026 12:21pm | Jul 28, 2026 12:21pm | Jul 28, 2026 2:06pm | Jul 28, 2026 3:01pm | Jul 28, 2026 3:01pm | Jul 28, 2026 3:01pm | BrokenWire |  | Fair | No | Switch bottom jumper burnt at one bolt clamp joint, same corrected with 3 ft #4 bear copper, customer left with power supply.
Non-Outage | J.E.26.07.33767 | C001867340 | Odeanie Davis | KSAS | Completed | Load_260329 | Rockfort - 210 | Jul 28, 2026 10:51am | Jul 28, 2026 10:51am | Jul 28, 2026 2:35pm | Jul 28, 2026 2:35pm | Jul 28, 2026 2:52pm | Jul 28, 2026 3:21pm | Jul 28, 2026 3:15pm | Jul 28, 2026 3:15pm |  |  | Fair | No | 102v/115v at arrival, open circuit at pothead corrected, 3 pen union, 114v/115v & 229v afternoon correction,
Non-Outage | J.E.26.07.33049 | C001867339 | Odeanie Davis | KSAS | Completed | Load_251700 | Hunts Bay - 510 | Jul 28, 2026 10:50am | Jul 28, 2026 10:51am | Jul 28, 2026 12:42pm | Jul 28, 2026 12:42pm | Jul 28, 2026 12:52pm | Jul 28, 2026 2:02pm | Jul 28, 2026 2:02pm | Jul 28, 2026 2:02pm |  |  | Fair | No | 234v at arrival no neutral, open circuit at pothead corrected, open neutral at secondary corrected, 1 one bolt clamp & 3 penn union, 117v/116v & 234v after correction.
Outage | J.E.26.07.34699 | C001867320 | Selvin White | St.Elizabeth | Completed | Load_292398 | Maggotty - 110 | Jul 28, 2026 10:40am | Jul 28, 2026 10:40am | Jul 28, 2026 12:28pm | Jul 28, 2026 12:37pm | Jul 28, 2026 12:56pm | Jul 28, 2026 1:27pm | Jul 28, 2026 1:27pm | Jul 28, 2026 1:27pm |  |  | Fair | No | Replace a blown 10 amp junction fuse at the entrance to Center Road at pole number 621163 after patrolling single phase primary line. Lightning strike was said to be the cause yesterday evening.
Non-Outage | J.E.26.07.34721 | C001867317 | Dean Smith | null | Completed | null | null | Jul 28, 2026 10:33am | Jul 28, 2026 10:34am | Jul 28, 2026 2:52pm | Jul 28, 2026 2:52pm | Jul 28, 2026 2:52pm | Jul 28, 2026 2:52pm | Jul 28, 2026 2:53pm | Jul 28, 2026 2:53pm |  |  | Rains | No | Unable to locate
Outage | J.E.26.07.25581 | C001867312 | Derrick Dawkins | Westmoreland | Completed | Load_244752 | Paradise - 310 | Jul 28, 2026 10:33am | Jul 28, 2026 10:35am | Jul 28, 2026 11:18am | Jul 28, 2026 11:18am | Jul 28, 2026 11:54am | Jul 28, 2026 11:55am | Jul 28, 2026 11:55am | Jul 28, 2026 11:55am |  |  | Fair | No | Checked and found ok
Outage | J.E.26.07.34680 | C001867313 | Swon Miller | Trelawny | Completed | Load_255673 | Greenwood - 210 | Jul 28, 2026 10:33am | Jul 29, 2026 3:39pm | Jul 29, 2026 3:55pm | Jul 29, 2026 3:56pm | Jul 29, 2026 3:56pm | Jul 14, 2026 4:19am | Jul 29, 2026 4:19pm | Jul 29, 2026 4:19pm |  |  | Fair | No | Found two customers service wires down cause by truck voltage found 0.000 advise customer to repair stanchion before repairs can be carried out voltage left 0.000
Outage | J.E.26.07.34718 | C001867310 | Derrick Dawkins | St.James | Completed | Load_292578 | Bogue - 610 | Jul 28, 2026 10:32am | Jul 28, 2026 10:32am | Jul 28, 2026 2:43pm | Jul 28, 2026 2:43pm | Jul 28, 2026 3:14pm | Jul 28, 2026 3:15pm | Jul 28, 2026 3:16pm | Jul 28, 2026 3:16pm |  |  | Rains | No | Checked and found ok
Outage | J.E.26.07.34649 | C001867307 | Horace Malcolm | St.James | Completed | Load_244366 | Queens Drive - 710 | Jul 28, 2026 10:31am | Jul 28, 2026 10:31am | Jul 28, 2026 10:59am | Jul 28, 2026 10:59am | Jul 28, 2026 11:31am | Jul 28, 2026 11:43am | Jul 28, 2026 11:43am | Jul 28, 2026 11:43am |  |  | Fair | No | Check and found customer disconnected got customer reconnected
Outage | J.E.26.07.34685 | C001867308 | Horace Malcolm | St.James | Completed | Load_238899 | Queens Drive - 310 | Jul 28, 2026 10:31am | Jul 28, 2026 10:31am | Jul 28, 2026 1:22pm | Jul 28, 2026 1:22pm | Jul 28, 2026 1:40pm | Jul 28, 2026 2:22pm | Jul 28, 2026 2:22pm | Jul 28, 2026 2:22pm |  |  | Fair | No | Check and found customer having single phase coming from meter EG 02289 referred to field service voltage 113
Outage | J.E.26.07.34708 | C001867309 | Oshane Warren | Westmoreland | Completed | Load_240487 | Paradise - 310 | Jul 28, 2026 10:31am | Jul 28, 2026 10:34am | Jul 28, 2026 11:25am | Jul 28, 2026 11:25am | Jul 28, 2026 12:11pm | Jul 28, 2026 12:18pm | Jul 28, 2026 12:21pm | Jul 28, 2026 12:21pm |  |  | Fair | No | Customer was disconnected for none payment of bill however there is a light pole torn down from hurricane leaning on customer building need to be removed customer is carrying out repair
Outage | J.E.26.07.34619 | C001867306 | Derrick Dawkins | St.James | Completed | Load_302247 | Bogue - 510 | Jul 28, 2026 10:30am | Jul 28, 2026 10:31am | Jul 28, 2026 11:57am | Jul 28, 2026 11:57am | Jul 28, 2026 1:14pm | Jul 28, 2026 1:36pm | Jul 28, 2026 1:36pm | Jul 28, 2026 1:36pm | BrokenWire |  | Fair | No | Customer not ready for connection advise customer to gar an electrician
Outage | J.E.26.07.34688 | C001867284 | Michael Paterson | Westmoreland | Completed | Load_250910 | Paradise - 210 | Jul 28, 2026 10:17am | Jul 28, 2026 10:19am | Jul 28, 2026 12:59pm | Jul 28, 2026 12:59pm | Jul 28, 2026 1:45pm | Jul 28, 2026 1:45pm | Jul 28, 2026 1:47pm | Jul 28, 2026 1:47pm |  |  | Fair | No | Customer account is disconnected due to outstanding bills owing.
Outage | J.E.26.07.34677 | C001867283 | Clyde Brown | St.Ann | Completed | Load_264080 | Cardiff Hall - 310 | Jul 28, 2026 10:15am | Jul 28, 2026 3:42pm | Jul 28, 2026 4:16pm | Jul 28, 2026 4:16pm | Jul 28, 2026 4:16pm | Jul 28, 2026 4:11pm | Jul 28, 2026 4:18pm | Jul 28, 2026 4:18pm | BrokenWire |  | Fair | No | Found ok,customer said supply was restored
Outage | J.E.26.07.34546 | C001867279 | Rusean Allen | KSAS | Completed | Load_239591 | Cane River - 610 | Jul 28, 2026 10:11am | Jul 28, 2026 10:11am | Jul 28, 2026 10:33am | Jul 28, 2026 10:34am | Jul 28, 2026 11:02am | Jul 28, 2026 11:05am | Jul 28, 2026 11:06am | Jul 28, 2026 11:06am | BrokenWire |  | Fair | No | Switch bottom burnt off in main line, refer to in-house team
Outage | J.E.26.07.34614 | C001867272 | Roxroy Needham | St.Ann | Completed | Load_252213 | Cardiff Hall - 310 | Jul 28, 2026 10:08am | Jul 28, 2026 10:09am | Jul 28, 2026 11:41am | Jul 28, 2026 1:52pm | Jul 29, 2026 8:45am | Jul 28, 2026 2:56pm | Jul 29, 2026 8:46am | Jul 29, 2026 8:46am |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.34643 | C001867268 | Daniel Francis | St.Ann | Completed | Load_246929 | Ocho Rios - 410 | Jul 28, 2026 10:08am | Jul 28, 2026 10:08am | Jul 28, 2026 10:33am | Jul 28, 2026 10:33am | Jul 28, 2026 10:39am | Jul 28, 2026 11:16am | Jul 28, 2026 11:20am | Jul 28, 2026 11:20am |  |  | Fair | No | Change one 15amp and one 10amp fuse it’s 2 junction fuse at Hermosa cove
Outage | J.E.26.07.34650 | C001867269 | Daniel Francis | St.Ann | Completed | Load_257505 | Ocho Rios - 310 | Jul 28, 2026 10:08am | Jul 28, 2026 10:08am | Jul 28, 2026 10:32am | Jul 28, 2026 10:32am | Jul 28, 2026 10:32am | Jul 28, 2026 10:30am | Jul 28, 2026 10:33am | Jul 28, 2026 10:33am |  |  | Fair | No | We call customer she say light is back
Outage | J.E.26.07.34607 | C001867267 | Richard Samuda | Manchester | Completed | Load_269453 | Kendal - 210 | Jul 28, 2026 10:07am | Jul 28, 2026 10:10am | Jul 28, 2026 10:20am | Jul 28, 2026 10:34am | Jul 28, 2026 11:00am | Jul 28, 2026 11:13am | Jul 28, 2026 11:13am | Jul 28, 2026 11:13am |  |  | Fair | No | Found ok power in meter cannot check voltage premises located
Outage | J.E.26.07.34653 | C001867266 | Kenroy Dale | Manchester | Completed | Load_265696 | Spur Tree - 310 | Jul 28, 2026 10:07am | Jul 28, 2026 10:08am | Jul 28, 2026 1:35pm | Jul 28, 2026 1:35pm | Jul 28, 2026 2:03pm | Jul 28, 2026 2:05pm | Jul 28, 2026 2:07pm | Jul 28, 2026 2:07pm | BrokenPole |  | Fair | No | Dead secondary pole found badly rooting at base. Pole need urgent attention
Non-Outage | J.E.26.07.27842 | C001867236 | Rochaine Hussey | KSAN | Completed | Load_244974 | Constant Spring - 210 | Jul 28, 2026 9:48am | Jul 28, 2026 9:49am | Jul 28, 2026 12:51pm | Jul 28, 2026 1:22pm | Jul 28, 2026 1:25pm | Jul 28, 2026 1:52pm | Jul 28, 2026 1:54pm | Jul 28, 2026 1:54pm | Fire |  | Fair | No | Rotten pole #180896Bushing was done at pothead 121/121/242v
Outage | J.E.26.07.34611 | C001867233 | Selvin White | St.Elizabeth | Completed | Load_293025 | Maggotty - 110 | Jul 28, 2026 9:44am | Jul 28, 2026 9:46am | Jul 28, 2026 1:27pm | Jul 28, 2026 1:27pm | Jul 28, 2026 1:57pm | Jul 28, 2026 1:59pm | Jul 28, 2026 1:59pm | Jul 28, 2026 1:59pm |  |  | Fair | No | Supply was found okay at the time of visit. Customer has some internal issues and was advised.
Outage | J.E.26.07.34519 | C001867227 | Wan Carlos Scarlett | St.Catherine | Completed | Load_267949 | Twickenham - 210 | Jul 28, 2026 9:43am | Jul 28, 2026 9:44am | Jul 28, 2026 1:59pm | Jul 28, 2026 1:59pm | Jul 28, 2026 2:53pm | Jul 28, 2026 4:19pm | Jul 28, 2026 4:20pm | Jul 28, 2026 4:20pm |  |  | Fair | No | Found customer 3 wire service at pole with one of the phase corroded use 2 one bolt clamps at open secondary line readings 114-115-230
Outage | J.E.26.07.34504 | C001867225 | Wan Carlos Scarlett | Portmore | Completed | Load_248531 | Naggo Head - 610 | Jul 28, 2026 9:42am | Jul 28, 2026 9:44am | Jul 28, 2026 10:11am | Jul 28, 2026 10:11am | Jul 28, 2026 10:31am | Jul 28, 2026 10:41am | Jul 28, 2026 10:42am | Jul 28, 2026 10:42am |  |  | Fair | No | Customer confirm that power supply has been restored
Outage | J.E.26.07.34529 | C001867224 | Wan Carlos Scarlett | Portmore | Completed | Load_570097 | Naggo Head - 610 | Jul 28, 2026 9:42am | Jul 28, 2026 9:44am | Jul 28, 2026 10:42am | Jul 28, 2026 10:42am | Jul 28, 2026 12:18pm | Jul 28, 2026 1:57pm | Jul 28, 2026 1:59pm | Jul 28, 2026 1:59pm |  |  | Fair | No | Refuse 15 Amps junction no pole # was found nothing was found on primary line
Outage | J.E.26.07.34637 | C001867226 | Eric Williams | KSAN | Completed | null | null | Jul 28, 2026 9:42am | Jul 28, 2026 9:42am | Jul 28, 2026 9:51am | Jul 28, 2026 9:51am | Jul 28, 2026 9:51am | Jul 28, 2026 10:34am | Jul 28, 2026 10:36am | Jul 28, 2026 10:36am |  |  | Fair | No | Open 2 trip saver and 1 drop out switch, and install short & ground Frazier crescent, for engineering work
Non-Outage | J.E.26.07.34556 | C001867222 | Richard Nicholas | null | Completed | null | null | Jul 28, 2026 9:40am | Jul 28, 2026 3:54pm | Jul 28, 2026 4:43pm | Jul 28, 2026 4:43pm | Jul 28, 2026 6:42pm | Jul 28, 2026 7:02pm | Jul 28, 2026 7:02pm | Jul 28, 2026 7:02pm | BrokenWire |  | Fair | No | Area found ok
Outage | J.E.26.07.34215 | C001867221 | Rodclif Dawkins | St.Catherine | Completed | Load_249355 | Tredegar - 310 | Jul 28, 2026 9:39am | Jul 28, 2026 9:40am | Jul 28, 2026 9:49am | Jul 28, 2026 9:49am | Jul 28, 2026 10:22am | Jul 28, 2026 12:43pm | Jul 28, 2026 12:43pm | Jul 28, 2026 12:43pm |  |  | Fair | No | At the give location crew 1-blown fuse on 3ph T-off line section patrol and found defective wooden cross arm and dislodged phase . Line section patrol was isolated and short and ground to effect repairs. 1-heavy duty T-arm, 3-post type polymers, 3-long studs and 2-16” machine bolts and spring washers were all used to effect repairs. Line section patrol was has now been fully restored. All customers Normalize.
Non-Outage | J.E.26.07.32796 | C001867208 | Fredrick Hamilton | KSAN | Completed | Load_245853 | Constant Spring - 310 | Jul 28, 2026 9:35am | Jul 28, 2026 9:35am | Jul 28, 2026 10:52am | Jul 28, 2026 11:18am | Jul 28, 2026 11:19am | Jul 28, 2026 11:20am | Jul 28, 2026 11:21am | Jul 28, 2026 11:21am |  |  | Fair | No | Customer contacted and stated issue was a customer defect which was rectified by her electrician Premises is ok
Non-Outage | J.E.26.07.32845 | C001867209 | Fredrick Hamilton | KSAN | Completed | Load_245871 | Constant Spring - 310 | Jul 28, 2026 9:35am | Jul 28, 2026 9:35am | Jul 28, 2026 10:52am | Jul 28, 2026 10:55am | Jul 28, 2026 11:00am | Jul 28, 2026 11:15am | Jul 28, 2026 11:15am | Jul 28, 2026 11:15am |  |  | Fair | No | 237v/118v/117v obtained no issues detected on JPS supply
Non-Outage | J.E.26.07.34297 | C001867210 | Fredrick Hamilton | KSAN | Completed | Load_265159 | Constant Spring - 210 | Jul 28, 2026 9:35am | Jul 28, 2026 9:35am | Jul 28, 2026 10:52am | Jul 28, 2026 12:51pm | Jul 28, 2026 1:42pm | Jul 28, 2026 2:00pm | Jul 28, 2026 2:00pm | Jul 28, 2026 2:00pm |  |  | Fair | No | 243.9v/122v/121.8v obtained no issues detected on JPS supply Premises is ok
Non-Outage | J.E.26.07.32773 | C001867207 | Fredrick Hamilton | KSAN | Completed | Load_264247 | Constant Spring - 410 | Jul 28, 2026 9:34am | Jul 28, 2026 9:35am | Jul 28, 2026 10:52am | Jul 28, 2026 12:17pm | Jul 28, 2026 12:17pm | Jul 28, 2026 12:43pm | Jul 28, 2026 12:43pm | Jul 28, 2026 12:43pm |  |  | Fair | No | 203v/107.4v/96v obtained low voltage detected affecting multiple customers please have emergency check transformer
Non-Outage | J.E.26.07.33863 | C001867204 | Fredrick Hamilton | KSAN | Completed | Load_264612 | Constant Spring - 410 | Jul 28, 2026 9:34am | Jul 28, 2026 9:35am | Jul 28, 2026 10:52am | Jul 28, 2026 11:24am | Jul 28, 2026 11:24am | Jul 28, 2026 11:25am | Jul 28, 2026 11:26am | Jul 28, 2026 11:26am |  |  | Fair | No | Multiple calls to customer went unanswered
Non-Outage | J.E.26.07.33876 | C001867206 | Fredrick Hamilton | KSAN | Completed | Load_264247 | Constant Spring - 410 | Jul 28, 2026 9:34am | Jul 28, 2026 9:35am | Jul 28, 2026 10:52am | Jul 28, 2026 12:44pm | Jul 28, 2026 12:44pm | Jul 28, 2026 12:47pm | Jul 28, 2026 12:47pm | Jul 28, 2026 12:47pm |  |  | Fair | No | 207v/96v/107v obtained low voltage detected and affecting multiple customers Please have emergency check transformer
Non-Outage | J.E.26.07.34416 | C001867205 | Fredrick Hamilton | KSAN | Completed | Load_243332 | Constant Spring - 410 | Jul 28, 2026 9:34am | Jul 28, 2026 9:35am | Jul 28, 2026 10:52am | Jul 28, 2026 12:00pm | Jul 28, 2026 12:07pm | Jul 28, 2026 12:12pm | Jul 28, 2026 12:13pm | Jul 28, 2026 12:13pm |  |  | Fair | No | 223v/109v/113v obtained low voltage detected Bushing required Bucket truck required
Non-Outage | J.E.26.07.34623 | C001867191 | Andre Williams | null | Completed | null | null | Jul 28, 2026 9:31am | Jul 28, 2026 9:32am | Jul 28, 2026 10:09am | Jul 28, 2026 10:37am | Jul 28, 2026 11:16am | Jul 28, 2026 11:17am | Jul 28, 2026 11:18am | Jul 28, 2026 11:18am | LeaningPole |  | Fair | No | Unable to locate unable to locate need more directions
Non-Outage | J.E.26.06.25235 | C001867187 | Kenroy Dale | Manchester | Completed | Load_257142 | Spur Tree - 310 | Jul 28, 2026 9:28am | Jul 28, 2026 9:29am | Jul 28, 2026 2:59pm | Jul 28, 2026 3:00pm | Jul 28, 2026 3:16pm | Jul 28, 2026 3:16pm | Jul 28, 2026 3:21pm | Jul 28, 2026 3:21pm |  |  | Fair | No | Open 25 kva transformer to remade corroded drop leads, connections was remade using 3 one bolt clamp transformer re-closed voltage reading 112/112/224
Non-Outage | J.E.26.07.24737 | C001867170 | Elvis Trowers | KSAN | Completed | Load_264383 | Constant Spring - 210 | Jul 28, 2026 9:23am | Jul 29, 2026 11:58am | Jul 29, 2026 12:44pm | Jul 29, 2026 12:44pm | Jul 29, 2026 1:21pm | Jul 29, 2026 3:06pm | Jul 29, 2026 3:06pm | Jul 29, 2026 3:06pm |  |  | Fair | Yes | Happened to be internal when checked corroded meter socket found customer was also advised to contact an electrician, voltage when checked was at 116+117=233, transformer topped changed is at B-2.
Outage | J.E.26.07.34595 | C001867169 | Horace Malcolm | St.James | Completed | Load_270006 | Queens Drive - 810 | Jul 28, 2026 9:20am | Jul 28, 2026 9:21am | Jul 28, 2026 10:13am | Jul 28, 2026 10:13am | Jul 28, 2026 10:13am | Jul 28, 2026 10:15am | Jul 28, 2026 10:15am | Jul 28, 2026 10:15am |  |  | Fair | No | Check and found ok related to previous call 34100
Non-Outage | J.E.26.06.34213 | C001867156 | Elvis Trowers | KSAN | Completed | Load_244977 | Constant Spring - 210 | Jul 28, 2026 9:17am | Jul 28, 2026 9:17am | Jul 28, 2026 1:33pm | Jul 28, 2026 1:33pm | Jul 28, 2026 2:09pm | Jul 28, 2026 2:16pm | Jul 28, 2026 2:16pm | Jul 28, 2026 2:16pm | LeaningPole |  | Fair | Yes | Checked out and found ok, nothing to do with JPS but with C/W both pole and cables.
Non-Outage | J.E.26.07.32923 | C001867162 | Roemello Brown | Trelawny | Completed | Load_259972 | Greenwood - 210 | Jul 28, 2026 9:17am | Jul 28, 2026 9:18am | Jul 28, 2026 11:51am | Jul 28, 2026 1:40pm | Jul 28, 2026 1:58pm | Jul 28, 2026 1:58pm | Jul 28, 2026 2:31pm | Jul 28, 2026 2:31pm |  |  | Fair | No | Premises found working okay Voltage found 115/116/231Voltage leave 115/116/231
Non-Outage | J.E.26.07.32981 | C001867161 | Roemello Brown | Trelawny | Completed | Load_292258 | Greenwood - 210 | Jul 28, 2026 9:17am | Jul 28, 2026 9:18am | Jul 28, 2026 11:51am | Jul 28, 2026 2:32pm | Jul 28, 2026 2:42pm | Jul 28, 2026 2:43pm | Jul 28, 2026 2:48pm | Jul 28, 2026 2:48pm |  |  | Fair | No | Premises found working okay Voltage found 116/116/232Voltage leave 116/116/232
Non-Outage | J.E.26.07.33151 | C001867160 | Roemello Brown | Trelawny | Completed | Load_259972 | Greenwood - 210 | Jul 28, 2026 9:17am | Jul 28, 2026 9:18am | Jul 28, 2026 11:49am | Jul 28, 2026 12:58pm | Jul 28, 2026 1:20pm | Jul 28, 2026 1:20pm | Jul 28, 2026 1:40pm | Jul 28, 2026 1:40pm |  |  | Fair | No | Premises found working okay Voltage found 115/116/231Voltage found 115/116/231
Non-Outage | J.E.26.07.33544 | C001867157 | Roemello Brown | Trelawny | Completed | Load_260052 | Greenwood - 110 | Jul 28, 2026 9:17am | Jul 28, 2026 9:18am | Jul 28, 2026 10:05am | Jul 28, 2026 10:20am | Jul 28, 2026 10:46am | Jul 28, 2026 10:46am | Jul 28, 2026 11:40am | Jul 28, 2026 11:40am |  |  | Fair | No | Corrosion at the pothead have clamps change Voltage found 117/117/234Voltage leave 116/117/234
Non-Outage | J.E.26.07.34300 | C001867159 | Roemello Brown | Trelawny | Completed | Load_261832 | Greenwood - 110 | Jul 28, 2026 9:17am | Jul 28, 2026 9:18am | Jul 29, 2026 3:34pm | Jul 29, 2026 3:34pm | Jul 29, 2026 3:39pm | Jul 29, 2026 3:39pm | Jul 29, 2026 3:52pm | Jul 29, 2026 3:52pm |  |  | Fair | No | Premises found working okay customer was reporting a noise from the fuse Voltage found 120/121/241Voltage leave 120121/241
Non-Outage | J.E.26.07.18743 | C001867154 | Elvis Trowers | KSAN | Completed | Load_240569 | Constant Spring - 210 | Jul 28, 2026 9:16am | Jul 28, 2026 9:17am | Jul 28, 2026 12:09pm | Jul 28, 2026 12:09pm | Jul 28, 2026 12:50pm | Jul 28, 2026 1:25pm | Jul 28, 2026 1:26pm | Jul 28, 2026 1:26pm | BangingWires |  | Fair | Yes | Removed telephone strand wire out of secondary wire to prevent sparking.
Non-Outage | J.E.26.07.32689 | C001867140 | Oraine Minto | St.Ann | Completed | Load_240435 | Roaring River - 410 | Jul 28, 2026 9:09am | Jul 28, 2026 9:10am | Jul 29, 2026 4:02pm | Jul 29, 2026 4:02pm | Jul 29, 2026 4:03pm | Jul 29, 2026 4:03pm | Jul 29, 2026 4:04pm | Jul 29, 2026 4:04pm |  |  | Fair | No | Power was restored
Non-Outage | J.E.26.07.33593 | C001867142 | Oraine Minto | St.Ann | Completed | Load_556003 | Roaring River - 410 | Jul 28, 2026 9:09am | Jul 28, 2026 9:10am | Jul 28, 2026 1:03pm | Jul 28, 2026 1:10pm | Jul 28, 2026 1:10pm | Jul 28, 2026 1:11pm | Jul 28, 2026 1:11pm | Jul 28, 2026 1:11pm |  |  | Fair | No | Refer to emergency
Non-Outage | J.E.26.07.33908 | C001867146 | Oraine Minto | St.Ann | Completed | Load_265383 | Cardiff Hall - 210 | Jul 28, 2026 9:09am | Jul 28, 2026 9:10am | Jul 28, 2026 12:11pm | Jul 28, 2026 12:12pm | Jul 28, 2026 12:12pm | Jul 28, 2026 12:12pm | Jul 28, 2026 12:13pm | Jul 28, 2026 12:13pm |  |  | Fair | No | Unable to connect customer number not Jamaican
Non-Outage | J.E.26.07.34018 | C001867145 | Oraine Minto | St.Ann | Completed | Load_247718 | Cardiff Hall - 210 | Jul 28, 2026 9:09am | Jul 28, 2026 9:10am | Jul 28, 2026 12:51pm | Jul 28, 2026 12:51pm | Jul 28, 2026 12:51pm | Jul 28, 2026 12:52pm | Jul 28, 2026 12:55pm | Jul 28, 2026 12:55pm |  |  | Fair | No | Refer to emergency
Non-Outage | J.E.26.07.34047 | C001867147 | Oraine Minto | St.Ann | Completed | Load_248752 | Cardiff Hall - 210 | Jul 28, 2026 9:09am | Jul 28, 2026 9:10am | Jul 28, 2026 12:10pm | Jul 28, 2026 12:10pm | Jul 28, 2026 12:10pm | Jul 28, 2026 12:10pm | Jul 28, 2026 12:11pm | Jul 28, 2026 12:11pm |  |  | Fair | No | Issue resolved
Non-Outage | J.E.26.07.34073 | C001867144 | Oraine Minto | St.Ann | Completed | Load_267137 | Cardiff Hall - 210 | Jul 28, 2026 9:09am | Jul 28, 2026 9:10am | Jul 28, 2026 12:57pm | Jul 28, 2026 12:57pm | Jul 28, 2026 12:57pm | Jul 28, 2026 12:58pm | Jul 28, 2026 12:59pm | Jul 28, 2026 12:59pm |  |  | Fair | No | Issue was resolved
Non-Outage | J.E.26.07.34389 | C001867143 | Oraine Minto | St.Ann | Completed | Load_246641 | Cardiff Hall - 310 | Jul 28, 2026 9:09am | Jul 28, 2026 9:10am | Jul 29, 2026 2:37pm | Jul 29, 2026 2:37pm | Jul 29, 2026 2:37pm | Jul 29, 2026 2:38pm | Jul 29, 2026 2:38pm | Jul 29, 2026 2:38pm |  |  | Fair | No | Issue was resolved
Non-Outage | J.E.26.07.33115 | C001867133 | Locksley Allen | St.Mary | Completed | Load_250666 | Oracabessa - 110 | Jul 28, 2026 9:06am | Jul 28, 2026 9:07am | Jul 28, 2026 12:44pm | Jul 28, 2026 12:57pm | Jul 28, 2026 12:57pm | Jul 28, 2026 12:03pm | Jul 28, 2026 1:00pm | Jul 28, 2026 1:00pm |  |  | Fair | No | Meter burn up. Voltage at meter socket phase to phase 234vPhase to neutral 119&114v. Please change meter ur
Non-Outage | J.E.26.07.32461 | C001867129 | Derrick Dawkins | St.James | Completed | Load_268145 | Bogue - 610 | Jul 28, 2026 9:02am | Jul 28, 2026 9:03am | Jul 28, 2026 11:11am | Jul 28, 2026 11:11am | Jul 28, 2026 11:11am | Jul 28, 2026 11:12am | Jul 28, 2026 11:13am | Jul 28, 2026 11:13am |  |  | Fair | No | Calls to customer went unanswered unable to locate
Non-Outage | J.E.26.07.33410 | C001867126 | Derrick Dawkins | St.James | Completed | Load_261201 | Bogue - 610 | Jul 28, 2026 9:02am | Jul 28, 2026 9:02am | Jul 28, 2026 11:14am | Jul 28, 2026 11:14am | Jul 28, 2026 11:16am | Jul 28, 2026 11:17am | Jul 28, 2026 11:17am | Jul 28, 2026 11:17am |  |  | Fair | No | Checked and found ok
Outage | J.E.26.07.34564 | C001867128 | Michael Paterson | Westmoreland | Completed | Load_266673 | Paradise - 110 | Jul 28, 2026 9:02am | Jul 28, 2026 9:43am | Jul 28, 2026 10:21am | Jul 28, 2026 10:21am | Jul 28, 2026 12:10pm | Jul 28, 2026 12:11pm | Jul 28, 2026 12:35pm | Jul 28, 2026 12:35pm |  |  | Fair | No | Check and found premise ok, voltage reading up to meter socket, 113v, 110v, 223v, customer has inter Issues , advise to fix.
Outage | J.E.26.07.34568 | C001867127 | Oshane Warren | Westmoreland | Completed | Load_254235 | Paradise - 310 | Jul 28, 2026 9:02am | Jul 28, 2026 9:44am | Jul 28, 2026 10:00am | Jul 28, 2026 10:00am | Jul 28, 2026 10:01am | Jul 28, 2026 10:02am | Jul 28, 2026 10:02am | Jul 28, 2026 10:02am |  |  | Fair | No | Restore from yesterday
Outage | J.E.26.07.34423 | C001867125 | Derrick Dawkins | St.James | Completed | Load_267503 | Bogue - 510 | Jul 28, 2026 8:58am | Jul 28, 2026 8:59am | Jul 28, 2026 1:37pm | Jul 28, 2026 1:37pm | Jul 28, 2026 1:48pm | Jul 28, 2026 1:49pm | Jul 28, 2026 1:49pm | Jul 28, 2026 1:49pm |  |  | Rains | No | Premises ok
Non-Outage | J.E.26.07.32900 | C001867112 | Elvis Trowers | KSAN | Completed | Load_239951 | Washington Blvd - 410 | Jul 28, 2026 8:57am | Jul 28, 2026 8:57am | Jul 28, 2026 9:17am | Jul 28, 2026 9:17am | Jul 28, 2026 10:07am | Jul 28, 2026 10:23am | Jul 28, 2026 10:23am | Jul 28, 2026 10:23am |  |  | Fair | Yes | Premises checked and found ok upon arrival, customer was assisted by resetting his breaker.
Non-Outage | J.E.26.07.33375 | C001867113 | Elvis Trowers | KSAN | Completed | Load_261467 | Washington Blvd - 410 | Jul 28, 2026 8:57am | Jul 28, 2026 8:57am | Jul 28, 2026 10:26am | Jul 28, 2026 10:27am | Jul 28, 2026 10:56am | Jul 28, 2026 11:08am | Jul 28, 2026 11:08am | Jul 28, 2026 11:08am |  |  | Fair | Yes | Happened to be internal when checked, defective 3 wire meter socket found wires burnt out, complete meter socket needs to be changed.
Non-Outage | J.E.26.07.34000 | C001867111 | Elvis Trowers | KSAN | Completed | Load_268661 | Washington Blvd - 510 | Jul 28, 2026 8:57am | Jul 28, 2026 8:57am | Jul 28, 2026 11:28am | Jul 28, 2026 11:29am | Jul 28, 2026 11:50am | Jul 28, 2026 11:57am | Jul 28, 2026 11:58am | Jul 28, 2026 11:58am |  |  | Fair | Yes | Places check and found ok, no sparks or fire was seen upon arrival.
Non-Outage | J.E.26.07.32640 | C001867105 | Locksley Allen | St.Mary | Completed | Load_264113 | Oracabessa - 210 | Jul 28, 2026 8:51am | Jul 28, 2026 8:59am | Jul 28, 2026 1:47pm | Jul 28, 2026 2:09pm | Jul 28, 2026 2:09pm | Jul 28, 2026 2:09pm | Jul 28, 2026 2:12pm | Jul 28, 2026 2:12pm |  |  | Fair | No | Voltage at meter socket phase to phase 241v. Phase to neutral 121&121vVoltage at panel inside 241v and 121&121v. No problem found Meter left working
Non-Outage | J.E.26.07.32644 | C001867104 | Locksley Allen | St.Mary | Completed | Load_349785 | Oracabessa - 210 | Jul 28, 2026 8:51am | Jul 28, 2026 8:59am | Jul 28, 2026 2:17pm | Jul 28, 2026 3:05pm | Jul 28, 2026 3:05pm | Jul 28, 2026 3:10pm | Jul 28, 2026 3:14pm | Jul 28, 2026 3:14pm | BrokenWire |  | Fair | No | No problem found at premises.Voltage at meter socket phase to phase 240v. Phase to neutral 120&119vAs of the 30/7/26 the small gate will be open, so that the meter can be change . Please refer to field service Meter 1137253—-rdg—-6254
Non-Outage | J.E.26.07.32994 | C001867102 | Romaine Roberts | St.Mary | Completed | Load_265726 | Highgate -110 | Jul 28, 2026 8:51am | Jul 28, 2026 8:59am | Jul 28, 2026 11:43am | Jul 28, 2026 11:43am | Jul 28, 2026 12:22pm | Jul 28, 2026 1:06pm | Jul 28, 2026 1:10pm | Jul 28, 2026 1:10pm |  |  | Fair | No | Bamboo bang and burn down one span of secondary neutral open and close 25 kva transformer to splice and retention conductor to restore supply
Non-Outage | J.E.26.07.33412 | C001867103 | Locksley Allen | St.Mary | Completed | Load_350817 | Oracabessa - 110 | Jul 28, 2026 8:51am | Jul 28, 2026 8:59am | Jul 28, 2026 12:17pm | Jul 28, 2026 12:27pm | Jul 28, 2026 12:27pm | Jul 28, 2026 12:28pm | Jul 28, 2026 12:30pm | Jul 28, 2026 12:30pm |  |  | Fair | No | Voltage at meter socket phase to phase 196v. Phase to neutral 116&81vThe problem is on the pole,but the base of the pole is rotten and not safe to climb. Bucket truck is needed
Non-Outage | J.E.26.07.33448 | C001867101 | Locksley Allen | St.Mary | Completed | Load_350817 | Oracabessa - 110 | Jul 28, 2026 8:51am | Jul 28, 2026 8:59am | Jul 28, 2026 11:52am | Jul 28, 2026 12:40pm | Jul 28, 2026 12:40pm | Jul 28, 2026 12:46pm | Jul 28, 2026 12:43pm | Jul 28, 2026 12:43pm |  |  | Fair | No | Gate lock and customer is not answering their phone
Non-Outage | J.E.26.07.34042 | C001867100 | Locksley Allen | St.Mary | Completed | Load_243893 | Oracabessa - 210 | Jul 28, 2026 8:51am | Jul 28, 2026 8:59am | Jul 28, 2026 1:01pm | Jul 28, 2026 1:44pm | Jul 28, 2026 1:44pm | Jul 28, 2026 1:50pm | Jul 28, 2026 1:47pm | Jul 28, 2026 1:47pm | Fire |  | Fair | No | JPS corrected the problem from yesterday Voltage at meter socket phase to phase 121,121,&208Meter left working
Non-Outage | J.E.26.07.34543 | C001867099 | Romaine Roberts | St.Mary | Completed | Load_259431 | Highgate -110 | Jul 28, 2026 8:51am | Jul 28, 2026 8:59am | Jul 28, 2026 10:01am | Jul 28, 2026 10:01am | Jul 28, 2026 10:54am | Jul 28, 2026 11:43am | Jul 28, 2026 11:43am | Jul 28, 2026 11:43am |  | Y | Fair | No | Bamboo fall on second line and cause conductor to bang up open and close 25 kva to clear line and restore supply
Non-Outage | J.E.26.07.32811 | C001867097 | Locksley Allen | St.Mary | Completed | Load_245218 | Oracabessa - 110 | Jul 28, 2026 8:50am | Jul 28, 2026 8:59am | Jul 28, 2026 3:15pm | Jul 28, 2026 3:15pm | Jul 28, 2026 3:15pm | Jul 28, 2026 3:14pm | Jul 28, 2026 3:17pm | Jul 28, 2026 3:17pm |  |  | Fair | No | No problem found at premises. JPS corrected the problem from last week
Non-Outage | J.E.26.07.32828 | C001867098 | Locksley Allen | St.Mary | Completed | Load_349522 | Oracabessa - 110 | Jul 28, 2026 8:50am | Jul 28, 2026 8:59am | Jul 28, 2026 9:54am | Jul 28, 2026 10:58am | Jul 28, 2026 10:58am | Jul 28, 2026 11:41am | Jul 28, 2026 11:51am | Jul 28, 2026 11:51am |  |  | Fair | No | Voltage at meter socket phase to phase 240v. Phase to neutral 116&116vPothead found corroded,clean up pothead.Meter left working
Outage | J.E.26.07.34565 | C001867090 | Cliton Henry | St.Mary | Completed | Load_245218 | Oracabessa - 110 | Jul 28, 2026 8:48am | Jul 28, 2026 8:49am | Jul 28, 2026 10:52am | Jul 28, 2026 12:19pm | Jul 28, 2026 12:19pm | Jul 28, 2026 12:27pm | Jul 28, 2026 12:27pm | Jul 28, 2026 12:27pm |  |  | Fair | No | The customer supply found ok, Voltages at the metering point were 119-119/239 volts. The customer stated that the supply was disconnected for debt.
Outage | J.E.26.07.34571 | C001867089 | Cliton Henry | St.Mary | Completed | Load_353382 | Oracabessa - 110 | Jul 28, 2026 8:48am | Jul 28, 2026 12:17pm | Jul 28, 2026 12:27pm | Jul 28, 2026 12:27pm | Jul 28, 2026 12:43pm | Jul 28, 2026 1:19pm | Jul 28, 2026 1:46pm | Jul 28, 2026 1:46pm |  |  | Fair | No | The wrapped joints found at the customer’s pothead were reconnected using 2 #2-#2 penunions. Voltage left was 115 volts. The 2w meter found to be defective, kindly refer to field service departments for a meter replacement.
Non-Outage | J.E.26.06.37171 | C001867077 | Nicholas Dillon | St.Elizabeth | Completed | Load_259959 | Maggotty - 210 | Jul 28, 2026 8:36am | Jul 28, 2026 8:38am | Jul 28, 2026 10:03am | Jul 28, 2026 10:03am | Jul 28, 2026 10:07am | Jul 28, 2026 10:07am | Jul 28, 2026 10:08am | Jul 28, 2026 10:08am |  |  | Fair | Yes | Check and found corrosion at pole clean joint and use 1 one bolt clamp before I left voltage is 112 113 phase to phase 226
Non-Outage | J.E.26.06.38298 | C001867081 | Nicholas Dillon | Manchester | Completed | Load_257398 | Spur Tree - 210 | Jul 28, 2026 8:36am | Jul 28, 2026 8:38am | Jul 29, 2026 5:03pm | Jul 29, 2026 5:03pm | Jul 29, 2026 5:04pm | Jul 29, 2026 5:04pm | Jul 29, 2026 5:08pm | Jul 29, 2026 5:08pm |  |  | Fair | No | Check voltage before at meter 98 103 phase to phase 201. Whole area experiencing low voltage
Non-Outage | J.E.26.06.36921 | C001867075 | Nicholas Dillon | Manchester | Completed | Load_245643 | Spur Tree - 210 | Jul 28, 2026 8:35am | Jul 28, 2026 8:38am | Jul 29, 2026 9:52am | Jul 29, 2026 9:52am | Jul 29, 2026 9:52am | Jul 29, 2026 9:52am | Jul 29, 2026 9:55am | Jul 29, 2026 9:55am |  |  | Fair | No | Premises not found. Not getting customer by phone
Non-Outage | J.E.26.06.37091 | C001867076 | Nicholas Dillon | Manchester | Completed | Load_239027 | Spur Tree - 210 | Jul 28, 2026 8:35am | Jul 28, 2026 8:38am | Jul 29, 2026 9:57am | Jul 29, 2026 9:57am | Jul 29, 2026 10:14am | Jul 29, 2026 10:15am | Jul 29, 2026 10:17am | Jul 29, 2026 10:17am |  |  | Flood | Yes | Check and found corrosion at pole clean joint and use 2 one bolt clamp before I left voltage is 116 115 phase to phase 231
Outage | J.E.26.07.34520 | C001867073 | Wayne Dillion | Manchester | Completed | Load_245543 | Spur Tree - 210 | Jul 28, 2026 8:30am | Jul 28, 2026 8:33am | Jul 28, 2026 10:40am | Jul 28, 2026 10:40am | Jul 28, 2026 10:40am | Jul 28, 2026 10:45am | Jul 28, 2026 10:45am | Jul 28, 2026 10:45am |  |  | Fair | No | Supply check and found one side of the meter damaged. Please refer same to the field services department for replacement.
Outage | J.E.26.07.34522 | C001867072 | Selvin White | St.Elizabeth | Completed | Load_242242 | Maggotty - 210 | Jul 28, 2026 8:30am | Jul 28, 2026 9:30am | Jul 28, 2026 10:54am | Jul 28, 2026 10:54am | Jul 28, 2026 11:41am | Jul 28, 2026 12:13pm | Jul 28, 2026 12:13pm | Jul 28, 2026 12:13pm |  |  | Fair | No | Replace approximately 60 ft of number six triplex service wire that was damaged and removed after the recent hurricane. Supply restored to the affected customer. Voltage readings left at customer’s pothead are 227,113,114 volts.
Non-Outage | J.E.26.07.33977 | C001867066 | Evan Spaulding | null | Completed | null | null | Jul 28, 2026 8:27am | Jul 28, 2026 3:19pm | Jul 28, 2026 5:47pm | Jul 28, 2026 5:47pm | Jul 28, 2026 5:47pm | Jul 28, 2026 5:48pm | Jul 28, 2026 5:48pm | Jul 28, 2026 5:48pm |  |  | Fair | No | Issue was resolved from last night
Non-Outage | J.E.26.07.34535 | C001867065 | Andrae Clarke | null | Completed | null | null | Jul 28, 2026 8:25am | Jul 28, 2026 8:25am | Jul 28, 2026 10:34am | Jul 28, 2026 10:34am | Jul 28, 2026 11:43am | Jul 28, 2026 12:13pm | Jul 28, 2026 12:08pm | Jul 28, 2026 12:08pm |  | Y | Fair | No | Balance service wire Line needs bushings
Outage | J.E.26.07.33838 | C001867060 | Tyrese Williams | St.Ann | Completed | Load_247903 | Cardiff Hall - 310 | Jul 28, 2026 8:23am | Jul 28, 2026 3:36pm | Jul 28, 2026 6:05pm | Jul 28, 2026 6:30pm | Jul 28, 2026 6:59pm | Jul 28, 2026 7:00pm | Jul 28, 2026 7:00pm | Jul 28, 2026 7:00pm |  |  | Fair | No | Replace a 20amp junction fuse at pole #0185932
Outage | J.E.26.07.33488 | C001867057 | Tyrese Williams | St.Ann | Completed | Load_246072 | Cardiff Hall - 310 | Jul 28, 2026 8:22am | Jul 28, 2026 3:36pm | Jul 28, 2026 6:05pm | Jul 28, 2026 6:27pm | Jul 28, 2026 6:27pm | Jul 28, 2026 6:27pm | Jul 28, 2026 6:28pm | Jul 28, 2026 6:28pm |  |  | Fair | No | Call related to 3 amp fuse was replaced
Outage | J.E.26.07.34021 | C001867058 | Tyrese Williams | St.Ann | Completed | Load_246072 | Cardiff Hall - 310 | Jul 28, 2026 8:22am | Jul 28, 2026 3:36pm | Jul 28, 2026 6:05pm | Jul 28, 2026 6:28pm | Jul 28, 2026 6:28pm | Jul 28, 2026 6:29pm | Jul 28, 2026 6:30pm | Jul 28, 2026 6:30pm |  |  | Rains | No | Call related to 3 amp fuse was replaced
Outage | J.E.26.07.34400 | C001867059 | Tyrese Williams | St.Ann | Completed | Load_246072 | Cardiff Hall - 310 | Jul 28, 2026 8:22am | Jul 28, 2026 3:36pm | Jul 28, 2026 6:05pm | Jul 28, 2026 6:05pm | Jul 28, 2026 6:19pm | Jul 28, 2026 6:26pm | Jul 28, 2026 6:26pm | Jul 28, 2026 6:26pm |  |  | Fair | No | Replace a 25 kva transformer fuse with a 3 amp at pole
Outage | J.E.26.07.33602 | C001867053 | Roxroy Needham | St.Ann | Completed | Load_251752 | Cardiff Hall - 310 | Jul 28, 2026 8:20am | Jul 28, 2026 8:21am | Jul 28, 2026 9:46am | Jul 28, 2026 11:25am | Jul 28, 2026 11:34am | Jul 28, 2026 12:37pm | Jul 28, 2026 12:40pm | Jul 28, 2026 12:40pm |  |  | Fair | No | Open 25 KVA transformer splice and retention 2 spans of secondary neutral used 60 ft of No# 2 aa conductor
Outage | J.E.26.07.33808 | C001867056 | Roxroy Needham | St.Ann | Completed | Load_258564 | Roaring River - 410 | Jul 28, 2026 8:20am | Jul 28, 2026 9:00am | Jul 28, 2026 9:38am | Jul 28, 2026 1:12pm | Jul 28, 2026 1:50pm | Jul 28, 2026 1:51pm | Jul 28, 2026 1:51pm | Jul 28, 2026 1:51pm |  |  | Fair | No | Replace 10 amp junction fuse at pole
Outage | J.E.26.07.34187 | C001867055 | Roxroy Needham | St.Ann | Completed | Load_263642 | Cardiff Hall - 310 | Jul 28, 2026 8:20am | Jul 28, 2026 8:21am | Jul 28, 2026 8:37am | Jul 28, 2026 8:37am | Jul 28, 2026 11:21am | Jul 28, 2026 11:21am | Jul 28, 2026 11:22am | Jul 28, 2026 11:22am |  |  | Fair | No | Replace 8 amp junction fuse
Outage | J.E.26.07.34198 | C001867054 | Roxroy Needham | St.Ann | Completed | Load_239752 | Cardiff Hall - 310 | Jul 28, 2026 8:20am | Jul 28, 2026 8:21am | Jul 28, 2026 9:39am | Jul 28, 2026 12:41pm | Jul 28, 2026 1:11pm | Jul 28, 2026 1:11pm | Jul 28, 2026 1:11pm | Jul 28, 2026 1:11pm |  |  | Fair | No | Customer say light is back
Non-Outage | J.E.26.01.36837 | C001867037 | Dwain Samuels | null | Completed | null | null | Jul 28, 2026 8:15am | Jul 28, 2026 8:17am | Jul 28, 2026 8:45am | Jul 28, 2026 12:20pm | Jul 28, 2026 12:26pm | Jul 28, 2026 12:39pm | Jul 28, 2026 12:41pm | Jul 28, 2026 12:41pm |  |  | Fair | No | Corrosion found at 3 wire pole. Voltage check 115-0-115. Corrosion clear use 3 one bolt clamp 115-114-229
Non-Outage | J.E.26.02.06865 | C001867038 | Dwain Samuels | Westmoreland | Completed | Load_249621 | Orange Bay - 210 | Jul 28, 2026 8:15am | Jul 28, 2026 8:16am | Jul 28, 2026 8:45am | Jul 28, 2026 12:47pm | Jul 28, 2026 12:54pm | Jul 28, 2026 12:57pm | Jul 28, 2026 12:58pm | Jul 28, 2026 12:58pm |  |  | Fair | No | Found working okay. Voltage check 114-116-230
Non-Outage | J.E.26.02.07104 | C001867039 | Dwain Samuels | null | Completed | null | null | Jul 28, 2026 8:15am | Jul 28, 2026 8:17am | Jul 28, 2026 8:45am | Jul 28, 2026 12:41pm | Jul 28, 2026 12:41pm | Jul 28, 2026 12:41pm | Jul 28, 2026 12:42pm | Jul 28, 2026 12:42pm |  |  | Fair | No | Corrosion found at 3 wire pole. Voltage check 115-0-115. Corrosion clear use 3 one bolt clamp. Voltage check 115-114-229
Non-Outage | J.E.26.02.16059 | C001867040 | Dwain Samuels | Westmoreland | Completed | Load_237679 | Paradise - 210 | Jul 28, 2026 8:15am | Jul 28, 2026 8:16am | Jul 28, 2026 8:45am | Jul 28, 2026 8:54am | Jul 28, 2026 9:17am | Jul 28, 2026 9:23am | Jul 28, 2026 9:23am | Jul 28, 2026 9:23am |  |  | Fair | No
Non-Outage | J.E.26.02.16383 | C001867041 | Dwain Samuels | Westmoreland | Completed | Load_570273 | Orange Bay - 310 | Jul 28, 2026 8:15am | Jul 28, 2026 8:16am | Jul 28, 2026 8:45am | Jul 29, 2026 11:49am | Jul 29, 2026 12:40pm | Jul 29, 2026 12:47pm | Jul 29, 2026 12:47pm | Jul 29, 2026 12:47pm |  |  | Fair | No | Corrosion found at 3 wire pole. Voltage check 115-92-207. Corrosion clear use 3 one bolt clamp. Voltage check 115-114-229
Non-Outage | J.E.26.02.19510 | C001867042 | Dwain Samuels | Westmoreland | Completed | Load_263858 | Orange Bay - 310 | Jul 28, 2026 8:15am | Jul 28, 2026 8:16am | Jul 28, 2026 8:45am | Jul 29, 2026 10:49am | Jul 29, 2026 10:57am | Jul 29, 2026 10:58am | Jul 29, 2026 11:01am | Jul 29, 2026 11:01am |  |  | Fair | No | Called and customer said supply is fine maybe an old report
Non-Outage | J.E.26.01.27084 | C001867032 | Dwain Samuels | Westmoreland | Completed | Load_248892 | Orange Bay - 310 | Jul 28, 2026 8:14am | Jul 28, 2026 8:16am | Jul 28, 2026 8:45am | Jul 29, 2026 11:12am | Jul 29, 2026 11:12am | Jul 29, 2026 11:13am | Jul 29, 2026 11:14am | Jul 29, 2026 11:14am |  |  | Fair | No | Called customer states he has no problems with the electricity only internet
Non-Outage | J.E.26.01.27094 | C001867034 | Dwain Samuels | Westmoreland | Completed | Load_265484 | Orange Bay - 310 | Jul 28, 2026 8:14am | Jul 28, 2026 8:16am | Jul 28, 2026 8:45am | Jul 29, 2026 11:02am | Jul 29, 2026 11:04am | Jul 29, 2026 11:08am | Jul 29, 2026 11:08am | Jul 29, 2026 11:08am |  |  | Fair | No | Found working okay. Voltage check 114-113-227
Non-Outage | J.E.26.01.28529 | C001867033 | Dwain Samuels | Westmoreland | Completed | Load_265484 | Orange Bay - 310 | Jul 28, 2026 8:14am | Jul 28, 2026 8:16am | Jul 28, 2026 8:45am | Jul 29, 2026 11:15am | Jul 29, 2026 11:19am | Jul 29, 2026 11:27am | Jul 29, 2026 11:24am | Jul 29, 2026 11:24am |  |  | Fair | No | Found working okay. Voltage check 114-114-224
Non-Outage | J.E.26.01.31569 | C001867035 | Dwain Samuels | Westmoreland | Completed | Load_253063 | Orange Bay - 310 | Jul 28, 2026 8:14am | Jul 28, 2026 8:16am | Jul 28, 2026 8:45am | Jul 29, 2026 10:24am | Jul 29, 2026 10:25am | Jul 29, 2026 10:29am | Jul 29, 2026 10:31am | Jul 29, 2026 10:31am |  |  | Fair | No | Found working okay. Voltage check 116-115-231
Non-Outage | J.E.26.07.23969 | C001867018 | Junior Scarlett | St.James | Completed | Load_556943 | Bogue - 310 | Jul 28, 2026 8:14am | Jul 28, 2026 8:14am | Jul 28, 2026 8:42am | Jul 28, 2026 10:27am | Jul 28, 2026 10:54am | Jul 28, 2026 11:32am | Jul 28, 2026 11:32am | Jul 28, 2026 11:32am |  |  | Fair | No | Refer to field serviceEG system EG number hex 02256Voltage found 115v 44v 221v
Non-Outage | J.E.26.07.23983 | C001867015 | Junior Scarlett | St.James | Completed | Load_574653 | Bogue - 310 | Jul 28, 2026 8:14am | Jul 28, 2026 8:14am | Jul 28, 2026 8:42am | Jul 28, 2026 1:15pm | Jul 28, 2026 1:43pm | Jul 28, 2026 1:43pm | Jul 28, 2026 1:44pm | Jul 28, 2026 1:44pm |  |  | Fair | No | Check and found ok115v 113v 226v
Non-Outage | J.E.26.04.29990 | C001867002 | Stephen Taylor | null | Completed | null | null | Jul 28, 2026 8:13am | Jul 28, 2026 8:14am | Jul 28, 2026 10:47am | Jul 28, 2026 11:42am | Jul 28, 2026 11:51am | Jul 28, 2026 11:51am | Jul 28, 2026 11:53am | Jul 28, 2026 11:53am |  |  | Fair | No | Premise found okay Rdg 113–112-225
Non-Outage | J.E.26.05.20813 | C001867001 | Stephen Taylor | null | Completed | null | null | Jul 28, 2026 8:13am | Jul 28, 2026 8:14am | Jul 28, 2026 9:48am | Jul 28, 2026 9:48am | Jul 28, 2026 9:49am | Jul 28, 2026 9:49am | Jul 28, 2026 9:51am | Jul 28, 2026 9:51am |  |  | Fair | No | Contact customer and customer sat the she needs a billing charge was advise to visit the office
Non-Outage | J.E.26.07.24436 | C001867008 | Junior Scarlett | St.James | Completed | Load_264461 | Bogue - 310 | Jul 28, 2026 8:13am | Jul 28, 2026 8:14am | Jul 28, 2026 8:42am | Jul 28, 2026 9:43am | Jul 28, 2026 10:01am | Jul 28, 2026 10:25am | Jul 28, 2026 10:25am | Jul 28, 2026 10:25am |  |  | Fair | No | Check and found okVoltage found 112v 111v 221v
Non-Outage | J.E.26.07.25260 | C001867006 | Junior Scarlett | St.James | Completed | Load_269651 | Bogue - 310 | Jul 28, 2026 8:13am | Jul 28, 2026 8:14am | Jul 28, 2026 8:42am | Jul 29, 2026 9:56am | Jul 29, 2026 10:19am | Jul 29, 2026 11:03am | Jul 29, 2026 11:03am | Jul 29, 2026 11:03am |  |  | Fair | No | Check and found okVoltage found 114v 115v 228v
Non-Outage | J.E.26.07.25499 | C001867004 | Junior Scarlett | St.James | Completed | Load_239360 | Bogue - 310 | Jul 28, 2026 8:13am | Jul 28, 2026 8:14am | Jul 28, 2026 8:42am | Jul 28, 2026 8:59am | Jul 28, 2026 9:10am | Jul 28, 2026 9:26am | Jul 28, 2026 9:26am | Jul 28, 2026 9:26am |  |  | Fair | No | Check and found okVoltage found 115v 115v 230v
Non-Outage | J.E.26.07.31024 | C001867003 | Junior Scarlett | St.James | Completed | Load_266770 | Bogue - 310 | Jul 28, 2026 8:13am | Jul 28, 2026 8:14am | Jul 28, 2026 8:42am | Jul 29, 2026 11:44am | Jul 29, 2026 12:12pm | Jul 29, 2026 1:46pm | Jul 29, 2026 1:57pm | Jul 29, 2026 1:57pm |  |  | Fair | No | Reattach neutral Install two clampVoltage found 115v 137v 230vVoltage leave 115v 115v 230vJob completed
Non-Outage | J.E.26.07.32905 | C001867000 | Junior Scarlett | St.James | Completed | Load_242526 | Bogue - 310 | Jul 28, 2026 8:13am | Jul 28, 2026 8:15am | Jul 28, 2026 8:42am | Jul 29, 2026 8:40am | Jul 29, 2026 8:51am | Jul 29, 2026 9:45am | Jul 29, 2026 9:45am | Jul 29, 2026 9:45am |  |  | Fair | No | Neutral broken Install clampReattach wireVoltage found 101v 137v 230Voltage leave 115v 115v 230v Job completed
Non-Outage | J.E.26.07.33754 | C001866998 | Junior Scarlett | St.James | Completed | Load_1003264 | Bogue - 310 | Jul 28, 2026 8:13am | Jul 28, 2026 8:15am | Jul 28, 2026 8:42am | Jul 28, 2026 1:50pm | Jul 28, 2026 2:06pm | Jul 28, 2026 2:40am | Jul 28, 2026 2:42pm | Jul 28, 2026 2:42pm |  |  | Rains | No | Customer meter socket defective advise customer to fix her meter socket Voltage found 114v 114v 228vVoltage leave 114v 114v228v
Non-Outage | J.E.26.05.01717 | C001866972 | Hopeton Henry | St.Thomas | Completed | Load_270128 | Good Year - 110 | Jul 28, 2026 8:07am | Jul 28, 2026 8:07am | Jul 28, 2026 11:51am | Jul 28, 2026 12:17pm | Jul 28, 2026 12:22pm | Jul 28, 2026 12:24pm | Jul 28, 2026 12:25pm | Jul 28, 2026 12:25pm |  |  | Fair | No | Found defective meter , refer to feild service
Non-Outage | J.E.26.05.11418 | C001866971 | Hopeton Henry | St.Thomas | Completed | Load_262983 | Good Year - 110 | Jul 28, 2026 8:07am | Jul 28, 2026 8:07am | Jul 28, 2026 11:51am | Jul 28, 2026 11:57am | Jul 28, 2026 12:13pm | Jul 28, 2026 12:15pm | Jul 28, 2026 12:17pm | Jul 28, 2026 12:17pm |  |  | Fair | No | Reconnect service at pole 114volts
Non-Outage | J.E.26.06.02195 | C001866970 | Hopeton Henry | St.Thomas | Completed | Load_264837 | Good Year - 110 | Jul 28, 2026 8:07am | Jul 28, 2026 8:07am | Jul 28, 2026 11:51am | Jul 29, 2026 9:58am | Jul 29, 2026 9:58am | Jul 29, 2026 9:58am | Jul 29, 2026 9:59am | Jul 29, 2026 9:59am |  |  | Fair | No | Bucket truck required
Non-Outage | J.E.26.06.19767 | C001866969 | Hopeton Henry | St.Thomas | Completed | Load_264991 | Good Year - 110 | Jul 28, 2026 8:07am | Jul 28, 2026 8:07am | Jul 28, 2026 11:51am | Jul 29, 2026 9:59am | Jul 29, 2026 9:59am | Jul 29, 2026 9:59am | Jul 29, 2026 10:00am | Jul 29, 2026 10:00am |  |  | Fair | No | Bucket truck required
Non-Outage | J.E.26.06.20905 | C001866968 | Hopeton Henry | St.Thomas | Completed | Load_261867 | Good Year - 110 | Jul 28, 2026 8:06am | Jul 28, 2026 8:07am | Jul 28, 2026 11:51am | Jul 28, 2026 2:06pm | Jul 28, 2026 2:32pm | Jul 28, 2026 2:32pm | Jul 28, 2026 2:42pm | Jul 28, 2026 2:42pm |  |  | Fair | No | Customer not located
Non-Outage | J.E.26.06.21471 | C001866967 | Hopeton Henry | St.Thomas | Completed | Load_256512 | Good Year - 110 | Jul 28, 2026 8:06am | Jul 28, 2026 8:07am | Jul 28, 2026 11:51am | Jul 28, 2026 12:27pm | Jul 28, 2026 1:20pm | Jul 28, 2026 2:04pm | Jul 28, 2026 2:05pm | Jul 28, 2026 2:05pm |  |  | Fair | No | Found ok117 115-232
Non-Outage | J.E.26.06.26678 | C001866966 | Hopeton Henry | St.Thomas | Completed | Load_577197 | Good Year - 110 | Jul 28, 2026 8:06am | Jul 28, 2026 8:07am | Jul 28, 2026 11:51am | Jul 28, 2026 2:42pm | Jul 28, 2026 2:43pm | Jul 28, 2026 2:43pm | Jul 28, 2026 3:12pm | Jul 28, 2026 3:12pm |  |  | Fair | No | Check and found ok
Non-Outage | J.E.26.06.26758 | C001866965 | Hopeton Henry | St.Thomas | Completed | Load_269125 | Good Year - 110 | Jul 28, 2026 8:06am | Jul 28, 2026 8:07am | Jul 28, 2026 11:51am | Jul 29, 2026 11:59am | Jul 29, 2026 12:13pm | Jul 29, 2026 12:33pm | Jul 29, 2026 12:33pm | Jul 29, 2026 12:33pm |  |  | Fair | No | Customer not located
Non-Outage | J.E.26.07.33387 | C001866963 | Hopeton Henry | St.Thomas | Completed | Load_238504 | Good Year - 210 | Jul 28, 2026 8:06am | Jul 28, 2026 8:07am | Jul 28, 2026 11:51am | Jul 28, 2026 3:13pm | Jul 28, 2026 3:43pm | Jul 28, 2026 3:43pm | Jul 28, 2026 3:44pm | Jul 28, 2026 3:44pm |  |  | Fair | No | Found defective meter, refer to field service
Non-Outage | J.E.26.07.34240 | C001866961 | Hopeton Henry | St.Thomas | Completed | Load_266529 | Good Year - 210 | Jul 28, 2026 8:06am | Jul 28, 2026 8:07am | Jul 28, 2026 11:51am | Jul 28, 2026 3:44pm | Jul 28, 2026 3:56pm | Jul 28, 2026 5:03pm | Jul 28, 2026 5:04pm | Jul 28, 2026 5:04pm |  |  | Fair | No | Found corrosion at pot head , use 3 connectors 113-113-226 volts
Outage | J.E.26.07.34130 | C001866952 | Michael Christian | St.James | Completed | Load_1002429 | Bogue - 310 | Jul 28, 2026 8:02am | Jul 28, 2026 8:02am | Jul 28, 2026 9:11am | Jul 28, 2026 9:11am | Jul 28, 2026 10:28am | Jul 28, 2026 10:37am | Jul 28, 2026 10:37am | Jul 28, 2026 10:37am |  |  | Fair | No | Check and found voltage 110 109 221 at pothead
Outage | J.E.26.07.34527 | C001866951 | Michael Christian | St.James | Completed | Load_255304 | Bogue - 310 | Jul 28, 2026 8:02am | Jul 28, 2026 8:02am | Jul 28, 2026 10:28am | Jul 28, 2026 10:37am | Jul 28, 2026 12:31pm | Jul 28, 2026 12:39pm | Jul 28, 2026 12:39pm | Jul 28, 2026 12:39pm |  |  | Fair | No | Premises not found call customer available send to field service
Non-Outage | J.E.26.07.00309 | C001866949 | Odeanie Davis | KSAS | Completed | Load_237939 | Hunts Bay - 310 | Jul 28, 2026 8:01am | Jul 28, 2026 8:01am | Jul 28, 2026 10:13am | Jul 28, 2026 11:05am | Jul 28, 2026 11:05am | Jul 28, 2026 11:40am | Jul 28, 2026 11:32am | Jul 28, 2026 11:32am |  |  | Fair | No | 101v at arrival, open circuit at secondary corrected, 1 one bolt clamp, 118v after correction Customer is in the process of upgrading their service from 110v to 220v. Customer was advised to contact jps when this is completed.
Non-Outage | J.E.26.07.00386 | C001866946 | Odeanie Davis | KSAS | Completed | Load_267297 | Hunts Bay - 310 | Jul 28, 2026 8:01am | Jul 28, 2026 8:01am | Jul 28, 2026 8:41am | Jul 28, 2026 9:24am | Jul 28, 2026 9:26am | Jul 28, 2026 9:27am | Jul 28, 2026 9:29am | Jul 28, 2026 9:29am |  |  | Fair | No | Customer stated that they don’t have any power issue
Non-Outage | J.E.26.07.04988 | C001866950 | Odeanie Davis | KSAS | Completed | Load_1002954 | Hunts Bay - 210 | Jul 28, 2026 8:01am | Jul 28, 2026 8:01am | Jul 28, 2026 8:40am | Jul 28, 2026 9:06am | Jul 28, 2026 9:06am | Jul 28, 2026 9:15am | Jul 28, 2026 9:15am | Jul 28, 2026 9:15am |  |  | Fair | No | Customer stated that they didn’t report an issue
Non-Outage | J.E.26.07.10845 | C001866947 | Odeanie Davis | KSAS | Completed | Load_245309 | Hunts Bay - 310 | Jul 28, 2026 8:01am | Jul 28, 2026 8:01am | Jul 28, 2026 10:11am | Jul 28, 2026 2:03pm | Jul 28, 2026 2:03pm | Jul 28, 2026 2:11pm | Jul 28, 2026 2:04pm | Jul 28, 2026 2:04pm |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.07.10988 | C001866948 | Odeanie Davis | KSAS | Completed | Load_246463 | Hunts Bay - 310 | Jul 28, 2026 8:01am | Jul 28, 2026 8:01am | Jul 28, 2026 8:42am | Jul 28, 2026 8:46am | Jul 28, 2026 8:46am | Jul 28, 2026 8:55am | Jul 28, 2026 8:56am | Jul 28, 2026 8:56am |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.07.11047 | C001866945 | Odeanie Davis | KSAS | Completed | Load_260970 | Hunts Bay - 310 | Jul 28, 2026 8:00am | Jul 28, 2026 8:01am | Jul 28, 2026 8:41am | Jul 28, 2026 11:47am | Jul 28, 2026 12:39pm | Jul 28, 2026 12:42pm | Jul 28, 2026 12:42pm | Jul 28, 2026 12:42pm |  |  | Fair | No | 83v/111v at from secondary, multiple wrap on seen on secondary line from transformer, emergency team needed.
Non-Outage | J.E.26.07.11055 | C001866944 | Odeanie Davis | KSAS | Completed | Load_266530 | Hunts Bay - 310 | Jul 28, 2026 8:00am | Jul 28, 2026 8:01am | Jul 28, 2026 8:41am | Jul 28, 2026 9:21am | Jul 28, 2026 9:21am | Jul 28, 2026 9:25am | Jul 28, 2026 9:22am | Jul 28, 2026 9:22am |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.07.11578 | C001866943 | Odeanie Davis | KSAS | Completed | Load_258629 | Hunts Bay - 310 | Jul 28, 2026 8:00am | Jul 28, 2026 8:01am | Jul 28, 2026 10:36am | Jul 28, 2026 10:40am | Jul 28, 2026 10:40am | Jul 28, 2026 10:46am | Jul 28, 2026 10:43am | Jul 28, 2026 10:43am |  |  | Fair | No | Customer stated that they didn’t make a report
Non-Outage | J.E.26.07.14629 | C001866942 | Odeanie Davis | KSAS | Completed | Load_255768 | Hunts Bay - 310 | Jul 28, 2026 8:00am | Jul 28, 2026 8:01am | Jul 28, 2026 10:45am | Jul 28, 2026 10:45am | Jul 28, 2026 10:45am | Jul 28, 2026 11:02am | Jul 28, 2026 11:02am | Jul 28, 2026 11:02am |  |  | Fair | No | 122v/123v & 246v at location, customer stated that they are receiving high voltage up to 248v. Field service team needed.
Non-Outage | J.E.26.07.19105 | C001866941 | Odeanie Davis | KSAS | Completed | Load_263277 | Hunts Bay - 310 | Jul 28, 2026 8:00am | Jul 28, 2026 8:01am | Jul 28, 2026 8:40am | Jul 28, 2026 9:32am | Jul 28, 2026 9:36am | Jul 28, 2026 10:02am | Jul 28, 2026 10:02am | Jul 28, 2026 10:02am |  |  | Fair | No | 121v/121v & 242v, 211v on 190 phase, no power issue found At location
Non-Outage | J.E.26.07.25628 | C001866940 | Odeanie Davis | KSAS | Completed | Load_248613 | Hunts Bay - 310 | Jul 28, 2026 8:00am | Jul 28, 2026 8:01am | Jul 28, 2026 10:37am | Jul 28, 2026 11:42am | Jul 28, 2026 11:42am | Jul 28, 2026 11:50am | Jul 28, 2026 11:47am | Jul 28, 2026 11:47am |  |  | Fair | No | Customer stated that they don’t have any power issues
Non-Outage | J.E.26.07.25660 | C001866939 | Odeanie Davis | KSAS | Completed | Load_248818 | Hunts Bay - 310 | Jul 28, 2026 8:00am | Jul 28, 2026 8:01am | Jul 28, 2026 10:06am | Jul 28, 2026 10:07am | Jul 28, 2026 10:07am | Jul 28, 2026 10:11am | Jul 28, 2026 10:08am | Jul 28, 2026 10:08am |  |  | Fair | No | Customer stated that issue was resolved by Jps
Non-Outage | J.E.26.07.26026 | C001866938 | Odeanie Davis | KSAS | Completed | Load_247544 | Hunts Bay - 310 | Jul 28, 2026 8:00am | Jul 28, 2026 8:01am | Jul 28, 2026 10:22am | Jul 28, 2026 10:22am | Jul 28, 2026 10:27am | Jul 28, 2026 10:36am | Jul 28, 2026 10:36am | Jul 28, 2026 10:36am |  |  | Fair | No | 119v/117v & 237v at location, no power issues found
Non-Outage | J.E.26.07.27008 | C001866933 | Odaine Johnson | Clarendon | Completed | Load_250759 | Parnassus - 310 | Jul 28, 2026 8:00am | Jul 28, 2026 8:00am | Jul 28, 2026 8:21am | Jul 29, 2026 10:01am | Jul 29, 2026 10:44am | Jul 29, 2026 10:46am | Jul 29, 2026 10:46am | Jul 29, 2026 10:46am |  |  | Fair | No | Premises found okay voltage reading 112/113/225 volts
Non-Outage | J.E.26.07.27013 | C001866936 | Odaine Johnson | Clarendon | Completed | Load_247245 | Parnassus - 310 | Jul 28, 2026 8:00am | Jul 28, 2026 8:00am | Jul 28, 2026 8:21am | Jul 28, 2026 1:14pm | Jul 28, 2026 1:29pm | Jul 28, 2026 1:29pm | Jul 28, 2026 1:29pm | Jul 28, 2026 1:29pm |  |  | Fair | No | Premises found okay
Non-Outage | J.E.26.07.27019 | C001866935 | Odaine Johnson | Clarendon | Completed | Load_239411 | Parnassus - 310 | Jul 28, 2026 8:00am | Jul 28, 2026 8:00am | Jul 28, 2026 8:21am | Jul 29, 2026 1:18pm | Jul 29, 2026 1:26pm | Jul 29, 2026 1:26pm | Jul 29, 2026 1:27pm | Jul 29, 2026 1:27pm |  |  | Fair | No | Loose connection found at pole, and retention voltage reading 117/115/233 volts
Non-Outage | J.E.26.07.27028 | C001866937 | Odaine Johnson | Clarendon | Completed | Load_248618 | Parnassus - 310 | Jul 28, 2026 8:00am | Jul 28, 2026 8:00am | Jul 28, 2026 8:21am | Jul 28, 2026 12:41pm | Jul 28, 2026 1:13pm | Jul 28, 2026 1:14pm | Jul 28, 2026 1:14pm | Jul 28, 2026 1:14pm |  |  | Fair | No | Premises found okay voltage reading 115/115/230 volts
Non-Outage | J.E.26.07.26522 | C001866928 | Odaine Johnson | Clarendon | Completed | Load_241314 | Parnassus - 210 | Jul 28, 2026 7:59am | Jul 28, 2026 8:00am | Jul 28, 2026 8:21am | Jul 28, 2026 1:30pm | Jul 28, 2026 3:28pm | Jul 28, 2026 3:28pm | Jul 28, 2026 3:29pm | Jul 28, 2026 3:29pm |  |  | Fair | No | Contacted customer but no one answer and follow direction given and still did not find location
Non-Outage | J.E.26.07.26525 | C001866929 | Odaine Johnson | Clarendon | Completed | Load_249822 | Parnassus - 310 | Jul 28, 2026 7:59am | Jul 28, 2026 8:00am | Jul 28, 2026 8:21am | Jul 28, 2026 12:16pm | Jul 28, 2026 12:40pm | Jul 28, 2026 12:40pm | Jul 28, 2026 12:41pm | Jul 28, 2026 12:41pm |  |  | Fair | No | Premises was found working ok voltage reading A116 B116 AB232
Non-Outage | J.E.26.07.26576 | C001866931 | Odaine Johnson | Clarendon | Completed | Load_263080 | Parnassus - 310 | Jul 28, 2026 7:59am | Jul 28, 2026 8:00am | Jul 28, 2026 8:21am | Jul 28, 2026 11:30am | Jul 28, 2026 12:08pm | Jul 28, 2026 12:08pm | Jul 28, 2026 12:09pm | Jul 28, 2026 12:09pm |  |  | Fair | No | Premises found okay voltage reading 115/114/230 volts
Non-Outage | J.E.26.07.26999 | C001866932 | Odaine Johnson | Clarendon | Completed | Load_249822 | Parnassus - 310 | Jul 28, 2026 7:59am | Jul 28, 2026 8:00am | Jul 28, 2026 8:21am | Jul 28, 2026 12:11pm | Jul 28, 2026 12:15pm | Jul 28, 2026 12:15pm | Jul 28, 2026 12:16pm | Jul 28, 2026 12:16pm |  |  | Fair | No | Premises found okay voltage reading A115 B116 AB231
Non-Outage | J.E.26.07.32648 | C001866923 | Horace Malcolm | St.James | Completed | Load_259518 | Queens Drive - 710 | Jul 28, 2026 7:57am | Jul 28, 2026 7:58am | Jul 28, 2026 10:17am | Jul 28, 2026 10:17am | Jul 28, 2026 10:44am | Jul 28, 2026 10:51am | Jul 28, 2026 10:51am | Jul 28, 2026 10:51am |  |  | Fair | No
Non-Outage | J.E.26.07.34100 | C001866924 | Horace Malcolm | St.James | Completed | Load_270006 | Queens Drive - 810 | Jul 28, 2026 7:57am | Jul 28, 2026 7:58am | Jul 28, 2026 8:30am | Jul 28, 2026 8:30am | Jul 28, 2026 9:01am | Jul 28, 2026 10:12am | Jul 28, 2026 10:12am | Jul 28, 2026 10:12am |  |  | Fair | No | Isolate two 50kva transformer to repair nuetral jumper and change transformer drop lead used 3ft #2 conductor 4ft 2/0 copper wire and 4clamps voltage 114-115-229
Non-Outage | J.E.26.07.34514 | C001866922 | Derrick Dawkins | St.James | Completed | Load_240027 | Bogue - 610 | Jul 28, 2026 7:56am | Jul 28, 2026 9:00am | Jul 28, 2026 9:22am | Jul 28, 2026 9:22am | Jul 28, 2026 11:04am | Jul 28, 2026 11:04am | Jul 28, 2026 11:06am | Jul 28, 2026 11:06am | BrokenWire |  | Fair | No | Premises ok 117/118=236
Non-Outage | J.E.26.07.26221 | C001866914 | Royston Montague | St.Catherine | Completed | Load_241890 | Rhodens Pen - 210 | Jul 28, 2026 7:55am | Jul 28, 2026 7:56am | Jul 28, 2026 8:04am | Jul 28, 2026 11:37am | Jul 28, 2026 11:45am | Jul 28, 2026 11:51am | Jul 28, 2026 12:00pm | Jul 28, 2026 12:00pm |  |  | Fair | No | Slack meter in socket. Same corrected. Voltage 228v 112v 113v
Non-Outage | J.E.26.07.28033 | C001866911 | Royston Montague | St.Catherine | Completed | Load_265913 | Rhodens Pen - 410 | Jul 28, 2026 7:55am | Jul 28, 2026 7:56am | Jul 28, 2026 8:04am | Jul 28, 2026 11:29am | Jul 28, 2026 11:36am | Jul 28, 2026 11:36am | Jul 28, 2026 11:37am | Jul 28, 2026 11:37am |  |  | Fair | No | Customer confirmed issue resolved.please update thanks.
Non-Outage | J.E.26.07.28271 | C001866908 | Royston Montague | St.Catherine | Completed | Load_568186 | Rhodens Pen - 410 | Jul 28, 2026 7:55am | Jul 28, 2026 7:56am | Jul 28, 2026 8:04am | Jul 28, 2026 1:14pm | Jul 28, 2026 1:14pm | Jul 28, 2026 1:16pm | Jul 28, 2026 1:16pm | Jul 28, 2026 1:16pm |  |  | Fair | No | Premises found ok, 228v 113v 112v , not seeing anyone at home.multiple calls to customer phone go without answer.
Non-Outage | J.E.26.07.28809 | C001866909 | Royston Montague | St.Catherine | Completed | Load_1001536 | Tredegar - 510 | Jul 28, 2026 7:55am | Jul 28, 2026 7:56am | Jul 28, 2026 8:04am | Jul 28, 2026 1:16pm | Jul 28, 2026 4:48pm | Jul 28, 2026 4:48pm | Jul 28, 2026 4:48pm | Jul 28, 2026 4:48pm |  |  | Fair | No | Rami system in area, multiple calls to customer phone go without answer.
Non-Outage | J.E.26.07.28866 | C001866910 | Royston Montague | St.Catherine | Completed | Load_268950 | Tredegar - 510 | Jul 28, 2026 7:55am | Jul 28, 2026 7:56am | Jul 28, 2026 8:04am | Jul 28, 2026 4:50pm | Jul 28, 2026 4:50pm | Jul 28, 2026 4:51pm | Jul 28, 2026 4:52pm | Jul 28, 2026 4:52pm |  |  | Fair | No | Not locating this premises. Phone number on job order not correct.
Non-Outage | J.E.26.07.33185 | C001866921 | Andrae Clarke | Portland | Completed | Load_265666 | Port Antonio - 310 | Jul 28, 2026 7:55am | Jul 28, 2026 7:56am | Jul 28, 2026 8:09am | Jul 28, 2026 8:16am | Jul 28, 2026 10:32am | Jul 28, 2026 10:24am | Jul 28, 2026 10:34am | Jul 28, 2026 10:34am |  |  | Fair | No | Repair broken wire use one one bolt clamp Check voltage 114/118/232
Non-Outage | J.E.26.07.34314 | C001866920 | Rusean Allen | null | Completed | null | null | Jul 28, 2026 7:55am | Jul 28, 2026 7:55am | Jul 28, 2026 8:22am | Jul 28, 2026 8:22am | Jul 28, 2026 8:49am | Jul 28, 2026 8:54am | Jul 28, 2026 8:54am | Jul 28, 2026 8:54am |  |  | Fair | No | Excessive illegal connections needs to be removed, refer to RPD….
Non-Outage | J.E.26.07.34339 | C001866919 | Rusean Allen | null | Completed | null | null | Jul 28, 2026 7:55am | Jul 28, 2026 7:55am | Jul 28, 2026 8:49am | Jul 28, 2026 8:54am | Jul 28, 2026 8:54am | Jul 28, 2026 8:55am | Jul 28, 2026 8:55am | Jul 28, 2026 8:55am |  |  | Fair | No | Related
Non-Outage | J.E.26.07.34343 | C001866918 | Rusean Allen | null | Completed | null | null | Jul 28, 2026 7:55am | Jul 28, 2026 7:55am | Jul 28, 2026 8:50am | Jul 28, 2026 9:03am | Jul 28, 2026 9:03am | Jul 28, 2026 9:05am | Jul 28, 2026 9:05am | Jul 28, 2026 9:05am | Fire |  | Fair | No | Related to excessive illegal connections
Non-Outage | J.E.26.07.34525 | C001866912 | Dwain Samuels | Westmoreland | Completed | Load_292188 | Paradise - 210 | Jul 28, 2026 7:55am | Jul 28, 2026 7:55am | Jul 28, 2026 8:45am | Jul 28, 2026 2:13pm | Jul 28, 2026 2:13pm | Jul 28, 2026 2:13pm | Jul 28, 2026 2:14pm | Jul 28, 2026 2:14pm |  |  | Fair | No | Called customer said it’s an old report
Outage | J.E.26.07.33715 | C001866917 | Rusean Allen | KSAS | Completed | Load_251825 | Cane River - 310 | Jul 28, 2026 7:55am | Jul 28, 2026 7:55am | Jul 28, 2026 9:07am | Jul 28, 2026 9:07am | Jul 28, 2026 9:10am | Jul 28, 2026 9:12am | Jul 28, 2026 9:13am | Jul 28, 2026 9:13am | LowHangingWires |  | Fair | No | Customer reports street light not working.
Outage | J.E.26.07.33904 | C001866916 | Rusean Allen | KSAS | Completed | Load_556650 | Cane River - 410 | Jul 28, 2026 7:55am | Jul 28, 2026 7:55am | Jul 28, 2026 9:14am | Jul 28, 2026 9:14am | Jul 28, 2026 9:27am | Jul 28, 2026 9:28am | Jul 28, 2026 9:29am | Jul 28, 2026 9:29am | BrokenWire |  | Fair | No | Directions needed, customer phone went unanswered.
Outage | J.E.26.07.34140 | C001866913 | Rusean Allen | KSAS | Completed | Load_257463 | Cane River - 610 | Jul 28, 2026 7:55am | Jul 28, 2026 7:55am | Jul 28, 2026 9:29am | Jul 28, 2026 9:29am | Jul 28, 2026 10:13am | Jul 28, 2026 10:30am | Jul 28, 2026 10:30am | Jul 28, 2026 10:30am |  |  | Fair | No | Corroded clamps found at pole, clamps were changed.
Non-Outage | J.E.26.07.29476 | C001866907 | Royston Montague | St.Catherine | Completed | Load_1000822 | Rhodens Pen - 210 | Jul 28, 2026 7:54am | Jul 28, 2026 7:56am | Jul 28, 2026 8:04am | Jul 28, 2026 12:00pm | Jul 28, 2026 1:04pm | Jul 28, 2026 1:14pm | Jul 28, 2026 1:14pm | Jul 28, 2026 1:14pm |  |  | Fair | No | Customer confirmed issue resolved, please update thanks.
Non-Outage | J.E.26.07.30276 | C001866906 | Odaine Johnson | St.Catherine | Completed | Load_244798 | Rhodens Pen - 310 | Jul 28, 2026 7:54am | Jul 28, 2026 7:56am | Jul 28, 2026 8:21am | Jul 28, 2026 10:16am | Jul 28, 2026 11:12am | Jul 28, 2026 11:13am | Jul 28, 2026 11:14am | Jul 28, 2026 11:14am |  |  | Fair | No | Corrosion was found at service pole one bolt clamps was replaced and problem was fixed Voltage reading is A112 B112 AB224
Non-Outage | J.E.26.07.30329 | C001866904 | Odaine Johnson | St.Catherine | Completed | Load_265946 | Rhodens Pen - 310 | Jul 28, 2026 7:54am | Jul 28, 2026 7:56am | Jul 28, 2026 8:21am | Jul 28, 2026 10:09am | Jul 28, 2026 10:15am | Jul 28, 2026 10:15am | Jul 28, 2026 10:15am | Jul 28, 2026 10:15am |  |  | Fair | No | Contacted customer and customer stated that the issue was resolved already
Non-Outage | J.E.26.07.30724 | C001866905 | Royston Montague | St.Catherine | Completed | Load_243374 | Rhodens Pen - 410 | Jul 28, 2026 7:54am | Jul 28, 2026 7:56am | Jul 28, 2026 8:04am | Jul 28, 2026 10:31am | Jul 28, 2026 11:14am | Jul 28, 2026 11:25am | Jul 28, 2026 11:25am | Jul 28, 2026 11:25am |  |  | Fair | No | Open phase at customers take off point. Same corrected. Voltage found 114v voltage after job completion are 229v 114v 114v
Non-Outage | J.E.26.07.32942 | C001866901 | Dean Smith | Hanover | Completed | Load_257160 | Orange Bay - 310 | Jul 28, 2026 7:53am | Jul 28, 2026 7:53am | Jul 28, 2026 12:02pm | Jul 28, 2026 12:02pm | Jul 28, 2026 12:49pm | Jul 28, 2026 12:49pm | Jul 28, 2026 12:50pm | Jul 28, 2026 12:50pm |  |  | Fair | No | Clean corrosion at customer meter pole, voltage left 120v,120v,240v.
Outage | J.E.26.07.32852 | C001866898 | Eric Williams | KSAN | Completed | Load_245203 | Constant Spring - 210 | Jul 28, 2026 7:52am | Jul 28, 2026 8:56am | Jul 28, 2026 10:37am | Jul 28, 2026 10:37am | Jul 28, 2026 11:13am | Jul 28, 2026 12:18pm | Jul 28, 2026 12:21pm | Jul 28, 2026 12:21pm | BrokenWire |  | Fair | No | Broken #2 twisted repaired used 2 - one bolt clamp. 30ft cl6 secondary pole defective and leaning toward road way. Sent to maintenance to have same corrected.
Non-Outage | J.E.26.07.32882 | C001866897 | Orville Lee | Portmore | Completed | Load_557242 | Naggo Head - 510 | Jul 28, 2026 7:51am | Jul 28, 2026 7:55am | Jul 28, 2026 8:12am | Jul 29, 2026 12:30pm | Jul 29, 2026 1:01pm | Jul 29, 2026 1:19pm | Jul 29, 2026 1:22pm | Jul 29, 2026 1:22pm |  |  | Fair | No | Refer to MosesCustomer connected to EG02408Voltage35V116V
Non-Outage | J.E.26.07.32919 | C001866894 | Orville Lee | Portmore | Completed | Load_238610 | Naggo Head - 510 | Jul 28, 2026 7:51am | Jul 28, 2026 7:51am | Jul 28, 2026 8:12am | Jul 28, 2026 1:30pm | Jul 28, 2026 1:35pm | Jul 28, 2026 1:57pm | Jul 28, 2026 2:00pm | Jul 28, 2026 2:00pm |  |  | Fair | No | Checks made and found secondary line connection corroded Three one bolt clamp usedVoltage116v117v233v
Non-Outage | J.E.26.07.33124 | C001866893 | Orville Lee | Portmore | Completed | Load_245046 | Naggo Head - 610 | Jul 28, 2026 7:51am | Jul 28, 2026 7:51am | Jul 28, 2026 8:12am | Jul 28, 2026 10:47am | Jul 28, 2026 11:03am | Jul 28, 2026 11:48am | Jul 28, 2026 11:50am | Jul 28, 2026 11:50am |  |  | Fair | No | Clear tree from secondary line reconnect customer to secondary lineVoltage120v120v240v
Non-Outage | J.E.26.07.33464 | C001866895 | Orville Lee | St.Catherine | Completed | Load_265320 | Twickenham - 210 | Jul 28, 2026 7:51am | Jul 28, 2026 7:51am | Jul 28, 2026 8:12am | Jul 28, 2026 2:04pm | Jul 28, 2026 3:44pm | Jul 28, 2026 3:44pm | Jul 28, 2026 3:48pm | Jul 28, 2026 3:48pm |  |  | Fair | No | Checks made and found service wire defective 70ft #6 service wire changed Two pen union and three one bolt clamp used Voltage109110229v
Non-Outage | J.E.26.07.33377 | C001866888 | Andre Williams | Trelawny | Completed | Load_570268 | Greenwood - 110 | Jul 28, 2026 7:50am | Jul 28, 2026 7:50am | Jul 28, 2026 9:33am | Jul 28, 2026 9:33am | Jul 28, 2026 9:33am | Jul 28, 2026 9:35am | Jul 28, 2026 9:34am | Jul 28, 2026 9:34am | LowHangingWires |  | Fair | No | Unable to locate phone number not in use
Non-Outage | J.E.26.07.33443 | C001866887 | Andre Williams | Trelawny | Completed | Load_245993 | Martha Brae - 210 | Jul 28, 2026 7:50am | Jul 28, 2026 7:50am | Jul 28, 2026 8:49am | Jul 28, 2026 8:50am | Jul 28, 2026 9:13am | Jul 28, 2026 9:30am | Jul 28, 2026 9:32am | Jul 28, 2026 9:32am |  |  | Fair | No | Clean coroded joints at Jps pole on customer #6 wire voltage 116+114=232
Non-Outage | J.E.26.07.33798 | C001866892 | Orville Lee | St.Catherine | Completed | Load_259899 | Twickenham - 210 | Jul 28, 2026 7:50am | Jul 28, 2026 7:51am | Jul 28, 2026 8:12am | Jul 28, 2026 3:50pm | Jul 28, 2026 5:03pm | Jul 28, 2026 5:03pm | Jul 28, 2026 5:06pm | Jul 28, 2026 5:06pm |  |  | Fair | No | Checks made and found pothead and secondary corroded Four pen union and five one bolt clamp used114v115v230v
Non-Outage | J.E.26.07.34492 | C001866891 | Orville Lee | Portmore | Completed | Load_239685 | Naggo Head - 610 | Jul 28, 2026 7:50am | Jul 28, 2026 7:51am | Jul 28, 2026 8:12am | Jul 28, 2026 11:53am | Jul 28, 2026 12:08pm | Jul 28, 2026 12:37pm | Jul 28, 2026 12:39pm | Jul 28, 2026 12:39pm |  |  | Fair | No | Checks made and found pothead corroded Three pen union used Voltage117v117v236v
Non-Outage | J.E.26.07.34496 | C001866890 | Orville Lee | Portmore | Completed | Load_264402 | Naggo Head - 510 | Jul 28, 2026 7:50am | Jul 28, 2026 7:51am | Jul 28, 2026 8:12am | Jul 28, 2026 12:40pm | Jul 28, 2026 1:09pm | Jul 28, 2026 1:20pm | Jul 28, 2026 1:24pm | Jul 28, 2026 1:24pm |  |  | Fair | No | Checks made and found meter socket terminal and meter terminal burnMeter change recommended Customer was advised to get defective meter socket repaired Voltage 121V121V242VMeter 2226554
Non-Outage | J.E.26.07.34506 | C001866889 | Milton Charlton | null | Completed | null | null | Jul 28, 2026 7:50am | Jul 29, 2026 7:52am | Jul 29, 2026 9:26am | Jul 29, 2026 9:26am | Jul 29, 2026 10:45am | Jul 29, 2026 10:50am | Jul 29, 2026 11:06am | Jul 29, 2026 11:06am |  |  | Fair | No | Primary and secondary bushing is required urgently. Tree limb touching Primary conductor causing fire.
Non-Outage | J.E.26.07.34037 | C001866886 | Edward Royal | null | Completed | null | null | Jul 28, 2026 7:49am | Jul 28, 2026 7:50am | Jul 28, 2026 5:16pm | Jul 28, 2026 5:16pm | Jul 28, 2026 5:16pm | Jul 28, 2026 5:17pm | Jul 28, 2026 5:17pm | Jul 28, 2026 5:17pm | Fire |  | Fair | No | When arrived at location there no fire identified
Non-Outage | J.E.26.07.34341 | C001866882 | Gregory Grossett | null | Completed | null | null | Jul 28, 2026 7:47am | Jul 28, 2026 7:47am | Jul 28, 2026 7:58am | Jul 28, 2026 7:58am | Jul 28, 2026 8:16am | Jul 28, 2026 8:37am | Jul 28, 2026 8:37am | Jul 28, 2026 8:37am | BrokenWire |  | Fair | No | After calling the customer we could not reach out to the customer however we say a broken 110 service wire on the road and dislodge pothead disconnect service wire to make area safe.
Outage | J.E.26.07.34365 | C001866883 | Gregory Grossett | Portland | Completed | Load_263585 | Port Antonio - 410 | Jul 28, 2026 7:47am | Jul 28, 2026 7:47am | Jul 28, 2026 8:37am | Jul 28, 2026 8:37am | Jul 28, 2026 8:43am | Jul 28, 2026 8:45am | Jul 28, 2026 8:45am | Jul 28, 2026 8:45am |  |  | Fair | No | Customer meter socket is defective however we could not get to the customer on phone to advise them to have it changed voltage reading 119v.
Outage | J.E.26.07.34024 | C001866881 | Oshane Warren | Westmoreland | Completed | Load_253169 | Paradise - 310 | Jul 28, 2026 7:46am | Jul 28, 2026 7:48am | Jul 28, 2026 8:11am | Jul 28, 2026 8:11am | Jul 28, 2026 9:53am | Jul 28, 2026 9:57am | Jul 28, 2026 10:00am | Jul 28, 2026 10:00am |  |  | Fair | No | Customer is requesting disconnection however customer is not connected back to the grid as yet and no meter is found at the location for the customer
Non-Outage | J.E.26.07.33540 | C001866878 | Hartley Chin | null | Completed | null | null | Jul 28, 2026 7:45am | Jul 28, 2026 7:46am | Jul 28, 2026 10:58am | Jul 28, 2026 10:58am | Jul 28, 2026 11:49am | Jul 28, 2026 12:03pm | Jul 28, 2026 12:04pm | Jul 28, 2026 12:04pm | BrokenWire | Y | Fair | No | Found 20 amp trip saver open @ 0138322 line patrolled found bamboo on line removed and close trip saver
Non-Outage | J.E.26.07.33772 | C001866875 | Milton Charlton | KSAN | Completed | Load_247088 | Hope - 510 | Jul 28, 2026 7:45am | Jul 28, 2026 7:46am | Jul 28, 2026 11:14am | Jul 28, 2026 12:22pm | Jul 28, 2026 12:22pm | Jul 28, 2026 12:10pm | Jul 28, 2026 12:25pm | Jul 28, 2026 12:25pm |  |  | Fair | No | Call related to other call at 23 Tavern Drive.
Non-Outage | J.E.26.07.33776 | C001866876 | Milton Charlton | KSAN | Completed | Load_579201 | Hope - 510 | Jul 28, 2026 7:45am | Jul 28, 2026 7:46am | Jul 28, 2026 11:14am | Jul 28, 2026 12:18pm | Jul 28, 2026 12:18pm | Jul 28, 2026 12:10pm | Jul 28, 2026 12:22pm | Jul 28, 2026 12:22pm |  |  | Fair | No | Found okay upon arrival. Readings at pothead and meter socket 118-118-236 volts. Readings at pothead and meter 118-118-236 volts.
Non-Outage | J.E.26.07.33781 | C001866877 | Milton Charlton | KSAN | Completed | Load_247088 | Hope - 510 | Jul 28, 2026 7:45am | Jul 28, 2026 7:46am | Jul 28, 2026 11:14am | Jul 28, 2026 11:14am | Jul 28, 2026 12:14pm | Jul 28, 2026 12:15pm | Jul 28, 2026 12:17pm | Jul 28, 2026 12:17pm |  |  | Fair | No | Found okay upon arrival. Customer has on internal problem. Readings at pothead 118-118-236 volts.
Non-Outage | J.E.26.07.33889 | C001866879 | Hartley Chin | null | Completed | null | null | Jul 28, 2026 7:45am | Jul 28, 2026 7:46am | Jul 28, 2026 10:25am | Jul 28, 2026 10:29am | Jul 28, 2026 10:29am | Jul 28, 2026 10:30am | Jul 28, 2026 10:33am | Jul 28, 2026 10:33am | BrokenWire |  | Fair | No | Premisis found ok. Customer stated the issue was resolved .
Outage | J.E.26.07.33456 | C001866880 | Neville Spencer | Clarendon | Completed | Load_265466 | Parnassus - 210 | Jul 28, 2026 7:45am | Jul 28, 2026 7:46am | Jul 28, 2026 10:57am | Jul 28, 2026 10:57am | Jul 28, 2026 12:49pm | Jul 28, 2026 12:50pm | Jul 28, 2026 12:51pm | Jul 28, 2026 12:51pm |  |  | Fair | No | Unable to locate customer.
Non-Outage | J.E.26.07.33585 | C001866874 | Oshane Warren | Westmoreland | Completed | Load_259238 | Paradise - 310 | Jul 28, 2026 7:43am | Jul 28, 2026 7:47am | Jul 28, 2026 8:11am | Jul 28, 2026 11:23am | Jul 28, 2026 11:23am | Jul 28, 2026 11:25am | Jul 28, 2026 11:25am | Jul 28, 2026 11:25am | Fire |  | Fair | No | Check and find ok
Non-Outage | J.E.26.07.34480 | C001866871 | Milton Charlton | null | Completed | null | null | Jul 28, 2026 7:43am | Jul 28, 2026 7:43am | Jul 28, 2026 12:25pm | Jul 28, 2026 12:25pm | Jul 28, 2026 12:29pm | Jul 28, 2026 12:35pm | Jul 28, 2026 12:31pm | Jul 28, 2026 12:31pm | BrokenWire |  | Fair | No | Found okay upon arrival. Matter was resolved.
Non-Outage | J.E.26.07.27783 | C001866869 | Rayon Foster | Hanover | Completed | Load_259314 | Orange Bay - 310 | Jul 28, 2026 7:41am | Jul 28, 2026 7:42am | Jul 28, 2026 9:24am | Jul 28, 2026 11:11am | Jul 28, 2026 11:28am | Jul 28, 2026 12:25pm | Jul 28, 2026 12:27pm | Jul 28, 2026 12:27pm |  |  | Rains | No | Voltage check when arrived on location 46/94 volts meter was blank damage #6 service wire splice and retention 50 feet of #6 service wire voltage check after repair 110/111AB221 volts
Non-Outage | J.E.26.07.32655 | C001866870 | Rayon Foster | Hanover | Completed | Load_1001376 | Orange Bay - 310 | Jul 28, 2026 7:41am | Jul 28, 2026 7:42am | Jul 28, 2026 9:24am | Jul 28, 2026 2:33pm | Jul 28, 2026 2:43pm | Jul 28, 2026 3:05pm | Jul 28, 2026 3:05pm | Jul 28, 2026 3:05pm |  |  | Rains | No | Voltage found on location 118/118AB 236volts customer had on internal issue witch was dealt with by her electrician
Non-Outage | J.E.26.07.33028 | C001866867 | Rayon Foster | Hanover | Completed | Load_254929 | Orange Bay - 310 | Jul 28, 2026 7:41am | Jul 28, 2026 7:42am | Jul 28, 2026 9:24am | Jul 28, 2026 12:31pm | Jul 28, 2026 12:31pm | Jul 28, 2026 2:21pm | Jul 28, 2026 2:22pm | Jul 28, 2026 2:22pm |  |  | Rains | No | Corrosion on jps pole was the cause of low voltage Debush an troubleshoot line and change clamp voltage after repair 110volts 120 supply from jps
Outage | J.E.26.07.34116 | C001866860 | Hartley Chin | Clarendon | Completed | Load_269906 | May Pen - 110 | Jul 28, 2026 7:40am | Jul 28, 2026 7:41am | Jul 28, 2026 9:36am | Jul 28, 2026 10:33am | Jul 28, 2026 10:36am | Jul 28, 2026 10:41am | Jul 28, 2026 10:43am | Jul 28, 2026 10:43am |  |  | Fair | No | Premisis found ok.
Outage | J.E.26.07.34454 | C001866866 | Milton Charlton | KSAN | Completed | Load_238164 | Hope - 510 | Jul 28, 2026 7:40am | Jul 28, 2026 7:41am | Jul 28, 2026 12:35pm | Jul 28, 2026 12:35pm | Jul 28, 2026 2:10pm | Jul 28, 2026 2:05pm | Jul 28, 2026 2:14pm | Jul 28, 2026 2:14pm |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.07.34468 | C001866865 | Milton Charlton | KSAN | Completed | Load_265279 | Hope - 510 | Jul 28, 2026 7:40am | Jul 28, 2026 7:41am | Jul 28, 2026 10:47am | Jul 28, 2026 11:10am | Jul 28, 2026 11:10am | Jul 28, 2026 10:40am | Jul 28, 2026 11:12am | Jul 28, 2026 11:12am | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Call related to call at 234 River Side Drive.
Outage | J.E.26.07.34472 | C001866864 | Milton Charlton | KSAN | Completed | Load_252799 | Hope - 510 | Jul 28, 2026 7:40am | Jul 28, 2026 7:41am | Jul 28, 2026 10:47am | Jul 28, 2026 11:08am | Jul 28, 2026 11:08am | Jul 28, 2026 10:40am | Jul 28, 2026 11:10am | Jul 28, 2026 11:10am |  |  | Fair | No | Call related to call at Hope River Street.
Outage | J.E.26.07.34477 | C001866862 | Milton Charlton | KSAN | Completed | Load_240360 | Hope - 510 | Jul 28, 2026 7:40am | Jul 28, 2026 7:41am | Jul 28, 2026 10:47am | Jul 28, 2026 11:06am | Jul 28, 2026 11:06am | Jul 28, 2026 10:40am | Jul 28, 2026 11:08am | Jul 28, 2026 11:08am |  |  | Fair | No | Call related to call at Hope River Street.
Outage | J.E.26.07.34501 | C001866861 | Milton Charlton | KSAN | Completed | Load_259172 | Hope - 510 | Jul 28, 2026 7:40am | Jul 28, 2026 7:41am | Jul 28, 2026 10:10am | Jul 28, 2026 10:10am | Jul 28, 2026 11:02am | Jul 28, 2026 10:40am | Jul 28, 2026 11:06am | Jul 28, 2026 11:06am |  |  | Fair | No | Refused and reclosed 25 amps junction switch at pole #0035502 using one 25 amps fuse.
Outage | J.E.26.07.34507 | C001866859 | Hartley Chin | St.Ann | Completed | Load_265251 | Cardiff Hall - 310 | Jul 28, 2026 7:39am | Jul 28, 2026 7:41am | Jul 28, 2026 10:43am | Jul 28, 2026 12:05pm | Jul 28, 2026 1:55pm | Jul 28, 2026 1:56pm | Jul 28, 2026 1:58pm | Jul 28, 2026 1:58pm |  |  | Fair | No | Found 2 of 3 30 amp Tripsaver open @ 0188634 (cave valley to James hill) line patrolled and closed. Suspect freak storm yesterday was the fault.
Outage | J.E.26.07.34411 | C001866858 | Richard Samuda | Manchester | Completed | Load_238677 | Kendal - 210 | Jul 28, 2026 7:38am | Jul 28, 2026 8:24am | Jul 28, 2026 11:18am | Jul 28, 2026 11:18am | Jul 28, 2026 12:22pm | Jul 28, 2026 12:23pm | Jul 28, 2026 12:23pm | Jul 28, 2026 12:23pm |  |  | Fair | No | Customer said power was restored
Outage | J.E.26.07.34459 | C001866857 | Richard Samuda | Manchester | Completed | Load_246179 | Kendal - 210 | Jul 28, 2026 7:38am | Jul 28, 2026 8:23am | Jul 28, 2026 8:41am | Jul 28, 2026 8:41am | Jul 28, 2026 10:02am | Jul 28, 2026 10:19am | Jul 28, 2026 10:20am | Jul 28, 2026 10:20am | BrokenWire |  | Fair | No | Found 25 kva transformer blown patrol line found nothing replaced fuse customer back to normal
Non-Outage | J.E.26.07.32439 | C001866850 | Edward Royal | KSAS | Completed | Load_267072 | Duhaney - 310 | Jul 28, 2026 7:37am | Jul 28, 2026 7:48am | Jul 28, 2026 11:15am | Jul 28, 2026 11:15am | Jul 28, 2026 11:15am | Jul 28, 2026 11:15am | Jul 28, 2026 11:15am | Jul 28, 2026 11:15am |  |  | Fair | No | Call related
Non-Outage | J.E.26.07.32686 | C001866847 | Edward Royal | KSAS | Completed | Load_267072 | Duhaney - 310 | Jul 28, 2026 7:37am | Jul 28, 2026 7:48am | Jul 28, 2026 11:25am | Jul 28, 2026 11:25am | Jul 28, 2026 11:25am | Jul 28, 2026 11:26am | Jul 28, 2026 11:26am | Jul 28, 2026 11:26am |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.07.32724 | C001866848 | Edward Royal | KSAS | Completed | Load_267072 | Duhaney - 310 | Jul 28, 2026 7:37am | Jul 28, 2026 7:48am | Jul 28, 2026 11:14am | Jul 28, 2026 11:14am | Jul 28, 2026 11:14am | Jul 28, 2026 11:14am | Jul 28, 2026 11:15am | Jul 28, 2026 11:15am |  |  | Fair | No | Call related
Non-Outage | J.E.26.07.32916 | C001866846 | Edward Royal | KSAS | Completed | Load_269132 | Duhaney - 310 | Jul 28, 2026 7:37am | Jul 28, 2026 7:48am | Jul 28, 2026 11:39am | Jul 28, 2026 11:39am | Jul 28, 2026 11:51am | Jul 28, 2026 11:52am | Jul 28, 2026 11:53am | Jul 28, 2026 11:53am | LeakingTransformer |  | Fair | No | 25kva transformer leaking transformer still engerize and working properly
Outage | J.E.26.07.32718 | C001866844 | Edward Royal | KSAS | Completed | Load_267072 | Duhaney - 310 | Jul 28, 2026 7:36am | Jul 28, 2026 7:48am | Jul 28, 2026 11:13am | Jul 28, 2026 11:13am | Jul 28, 2026 11:13am | Jul 28, 2026 11:13am | Jul 28, 2026 11:14am | Jul 28, 2026 11:14am |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.07.32998 | C001866843 | Edward Royal | KSAS | Completed | Load_246988 | Duhaney - 310 | Jul 28, 2026 7:36am | Jul 28, 2026 7:48am | Jul 28, 2026 11:16am | Jul 28, 2026 11:16am | Jul 28, 2026 11:21am | Jul 28, 2026 11:21am | Jul 28, 2026 11:22am | Jul 28, 2026 11:22am |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.07.33143 | C001866845 | Edward Royal | KSAS | Completed | Load_241282 | Duhaney - 310 | Jul 28, 2026 7:36am | Jul 28, 2026 7:48am | Jul 28, 2026 11:29am | Jul 28, 2026 11:29am | Jul 28, 2026 11:29am | Jul 28, 2026 11:38am | Jul 28, 2026 11:38am | Jul 28, 2026 11:38am |  |  | Fair | No | Customer was reconnected by escalation
Outage | J.E.26.07.33059 | C001866834 | Moses Elliston | St.Catherine | Completed | Load_294308 | Twickenham - 310 | Jul 28, 2026 7:34am | Jul 28, 2026 7:35am | Jul 28, 2026 11:25am | Jul 28, 2026 11:25am | Jul 28, 2026 11:25am | Jul 28, 2026 11:46am | Jul 28, 2026 11:48am | Jul 28, 2026 11:48am |  |  | Fair | No | Meter changed to # 3026259 due to credit adding issues .
Outage | J.E.26.07.33135 | C001866832 | Donald Cunningham | St.Catherine | Completed | Load_239409 | New Michelton - 210 | Jul 28, 2026 7:34am | Jul 28, 2026 8:25am | Jul 28, 2026 11:48am | Jul 28, 2026 11:48am | Jul 28, 2026 12:55pm | Jul 28, 2026 12:55pm | Jul 28, 2026 1:12pm | Jul 28, 2026 1:12pm |  |  | Fair | No | Slack and corroded phase by pole corrected using one clamp voltage readings 117
Outage | J.E.26.07.33393 | C001866831 | Neville Spencer | St.Catherine | Completed | Load_250129 | Rhodens Pen - 310 | Jul 28, 2026 7:34am | Jul 28, 2026 7:35am | Jul 28, 2026 8:01am | Jul 28, 2026 8:01am | Jul 28, 2026 10:21am | Jul 28, 2026 10:56am | Jul 28, 2026 10:57am | Jul 28, 2026 10:57am | Fire |  | Fair | No | Remade slack phase joints at secondary on 3, wire service used 2 clamps voltage reading 114 114 227 .
Outage | J.E.26.07.33819 | C001866836 | Donald Cunningham | St.Catherine | Completed | Load_265022 | New Michelton - 410 | Jul 28, 2026 7:34am | Jul 28, 2026 8:25am | Jul 28, 2026 10:03am | Jul 28, 2026 10:03am | Jul 28, 2026 11:46am | Jul 28, 2026 11:47am | Jul 28, 2026 11:48am | Jul 28, 2026 11:48am |  |  | Fair | No | Premises closed
Outage | J.E.26.07.34146 | C001866835 | Nickolas Rodriques | St.Catherine | Completed | Load_238100 | Tredegar - 510 | Jul 28, 2026 7:34am | Jul 29, 2026 9:35am | Jul 29, 2026 4:56pm | Jul 29, 2026 5:25pm | Jul 29, 2026 5:36pm | Jul 29, 2026 6:35pm | Jul 29, 2026 6:40pm | Jul 29, 2026 6:40pm |  |  | Fair | No | Customer confirmed that the power was later restored.
Outage | J.E.26.07.34329 | C001866842 | Nickolas Rodriques | St.Catherine | Completed | Load_251090 | Rhodens Pen - 410 | Jul 28, 2026 7:34am | Jul 28, 2026 3:28pm | Jul 28, 2026 9:26pm | Jul 28, 2026 9:30pm | Jul 28, 2026 10:03pm | Jul 28, 2026 10:34pm | Jul 28, 2026 10:40pm | Jul 28, 2026 10:40pm |  |  | Fair | No | Customer stated that he is single phasing. Reading found at meter (115-112-227). Checks were done which revealed that the customer is having internal issues. Customer was advised to consult an Electrician to do repairs.
Outage | J.E.26.07.33105 | C001866829 | Christopher Edwards | KSAN | Completed | Load_246942 | Constant Spring - 410 | Jul 28, 2026 7:33am | Jul 28, 2026 7:33am | Jul 28, 2026 7:56am | Jul 28, 2026 9:44am | Jul 28, 2026 10:33am | Jul 28, 2026 11:15am | Jul 28, 2026 11:15am | Jul 28, 2026 11:15am |  |  | Fair | No | Refuse blown junction fuseUsing (1) 20 amps
Outage | J.E.26.07.33611 | C001866825 | Christopher Edwards | KSAN | Completed | Load_252598 | Constant Spring - 410 | Jul 28, 2026 7:33am | Jul 28, 2026 7:33am | Jul 28, 2026 11:16am | Jul 28, 2026 11:21am | Jul 28, 2026 11:21am | Jul 28, 2026 11:21am | Jul 28, 2026 11:21am | Jul 28, 2026 11:21am |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Outage | J.E.26.07.33695 | C001866824 | Christopher Edwards | KSAN | Completed | Load_241480 | Constant Spring - 410 | Jul 28, 2026 7:33am | Jul 29, 2026 7:48am | Jul 29, 2026 10:03am | Jul 29, 2026 10:03am | Jul 29, 2026 10:41am | Jul 29, 2026 10:56am | Jul 29, 2026 10:56am | Jul 29, 2026 10:56am |  |  | Fair | No | Remake burnt phase joint at poleUsing (2) one bolt clamps Voltage:115,114,230v
Outage | J.E.26.07.34473 | C001866823 | Christopher Edwards | KSAN | Completed | Load_262984 | Constant Spring - 410 | Jul 28, 2026 7:33am | Jul 28, 2026 7:33am | Jul 28, 2026 11:15am | Jul 28, 2026 11:21am | Jul 28, 2026 12:00pm | Jul 28, 2026 12:50pm | Jul 28, 2026 12:51pm | Jul 28, 2026 12:51pm |  |  | Fair | No | Clear fallen bamboo off primary lineRefuse blown junction fuse using (1) 20 amps
Outage | J.E.26.07.32929 | C001866819 | Selvin White | St.Elizabeth | Completed | Load_265047 | Maggotty - 110 | Jul 28, 2026 7:24am | Jul 28, 2026 7:36am | Jul 28, 2026 7:47am | Jul 28, 2026 10:32am | Jul 28, 2026 10:32am | Jul 28, 2026 10:38am | Jul 28, 2026 10:40am | Jul 28, 2026 10:40am |  |  | Fair | No | Replace approximately 70 ft of number six triplex service that was damaged after the storm. Supply restored with voltage readings of 224 ,112,111 volts.
Non-Outage | J.E.26.07.33817 | C001866816 | Junior Scarlett | St.James | Completed | Load_556941 | Bogue - 310 | Jul 28, 2026 7:20am | Jul 28, 2026 9:01am | Jul 28, 2026 11:30am | Jul 28, 2026 11:32am | Jul 28, 2026 11:50am | Jul 28, 2026 12:24am | Jul 28, 2026 12:24pm | Jul 28, 2026 12:24pm | LeaningPole |  | Fair | No | Lean pole putting strain on customer pothead Pole need to straighten Pole shift from it original position Voltage found 115v 115v 230v
Non-Outage | J.E.26.07.34111 | C001866815 | Horace Malcolm | null | Completed | null | null | Jul 28, 2026 7:20am | Jul 28, 2026 8:06am | Jul 28, 2026 11:43am | Jul 28, 2026 11:43am | Jul 28, 2026 12:42pm | Jul 28, 2026 1:22pm | Jul 28, 2026 1:22pm | Jul 28, 2026 1:22pm | Fire |  | Fair | No | Check and found noise coming from transformer and no sparks voltage 119-120-239-208
Outage | J.E.26.07.33768 | C001866809 | Wan Carlos Scarlett | St.Catherine | Completed | Load_557293 | Twickenham - 210 | Jul 28, 2026 7:09am | Jul 28, 2026 7:09am | Jul 28, 2026 9:01am | Jul 28, 2026 9:01am | Jul 28, 2026 9:32am | Jul 28, 2026 10:09am | Jul 28, 2026 10:10am | Jul 28, 2026 10:10am |  |  | Fair | No | Customer was reconnected from escalation department
Outage | J.E.26.07.34331 | C001866806 | Wan Carlos Scarlett | St.Catherine | Completed | Load_253883 | Twickenham - 210 | Jul 28, 2026 7:09am | Jul 28, 2026 7:09am | Jul 28, 2026 7:35am | Jul 28, 2026 8:38am | Jul 28, 2026 8:38am | Jul 28, 2026 8:59am | Jul 28, 2026 9:00am | Jul 28, 2026 9:00am |  |  | Fair | No | Found one span of open secondary line phase jumper burn out from the one bolt clamp use 2 one bolt clamps at pole readings 116-117-234
Outage | J.E.26.07.34426 | C001866803 | Hartley Chin | Clarendon | Completed | Load_350804 | May Pen - 110 | Jul 28, 2026 6:45am | Jul 28, 2026 7:31am | Jul 28, 2026 12:04pm | Jul 28, 2026 12:04pm | Jul 28, 2026 12:04pm | Jul 28, 2026 12:04pm | Jul 28, 2026 12:05pm | Jul 28, 2026 12:05pm |  |  | Fair | No | Call related to job 33540
Outage | J.E.26.07.34188 | C001866775 | Daniel Francis | St.Ann | Completed | Load_256334 | Ocho Rios - 310 | Jul 27, 2026 11:49pm | Jul 28, 2026 8:19am | Jul 28, 2026 9:03am | Jul 28, 2026 9:03am | Jul 28, 2026 9:33am | Jul 28, 2026 10:20am | Jul 28, 2026 10:25am | Jul 28, 2026 10:25am |  |  | Fair | No | Found junction brown at pole 0010354 cut tree limb from line and renew fuse
Outage | J.E.26.07.34184 | C001866774 | Rusean Allen | KSAN | Completed | Load_243339 | Washington Blvd - 710 | Jul 27, 2026 11:32pm | Jul 27, 2026 11:33pm | Jul 28, 2026 1:16am | Jul 28, 2026 1:16am | Jul 28, 2026 1:56am | Jul 28, 2026 1:57am | Jul 28, 2026 1:57am | Jul 28, 2026 1:57am | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Premises okay
Outage | J.E.26.07.34264 | C001866770 | Kenroy Dale | Manchester | Completed | Load_269460 | Porus - 310 | Jul 27, 2026 9:50pm | Jul 28, 2026 8:27am | Jul 28, 2026 11:16am | Jul 28, 2026 11:29am | Jul 28, 2026 12:24pm | Jul 28, 2026 1:29pm | Jul 28, 2026 1:35pm | Jul 28, 2026 1:35pm |  |  | Fair | No | Corrected phase found in mid-span connection was remade and customer now with supply voltage reading 114/115/230
Outage | J.E.26.07.34170 | C001866768 | Rusean Allen | KSAS | Completed | Load_254801 | Greenwich - 510 | Jul 27, 2026 9:28pm | Jul 27, 2026 11:33pm | Jul 28, 2026 1:02am | Jul 28, 2026 1:02am | Jul 28, 2026 1:10am | Jul 28, 2026 1:15am | Jul 28, 2026 1:15am | Jul 28, 2026 1:15am | BrokenWire |  | Fair | No | Line side found okay
Non-Outage | J.E.26.07.34166 | C001866766 | Cliton Henry | null | Completed | null | null | Jul 27, 2026 9:27pm | Jul 28, 2026 7:51am | Jul 28, 2026 8:43am | Jul 28, 2026 8:43am | Jul 28, 2026 8:52am | Jul 28, 2026 8:52am | Jul 28, 2026 8:54am | Jul 28, 2026 8:54am |  |  | Fair | No | The customer stated that the supply was restored from last night.
Outage | J.E.26.07.34081 | C001866767 | Rusean Allen | KSAN | Completed | Load_241594 | Washington Blvd - 310 | Jul 27, 2026 9:27pm | Jul 27, 2026 11:33pm | Jul 27, 2026 11:51pm | Jul 28, 2026 12:21am | Jul 28, 2026 12:59am | Jul 28, 2026 1:01am | Jul 28, 2026 1:02am | Jul 28, 2026 1:02am |  |  | Fair | No | Light seen at premises.
Outage | J.E.26.07.34153 | C001866765 | Cliton Henry | St.Ann | Completed | Load_257387 | Upper White River - 110 | Jul 27, 2026 9:26pm | Jul 28, 2026 7:51am | Jul 28, 2026 8:56am | Jul 28, 2026 9:57am | Jul 28, 2026 9:57am | Jul 28, 2026 10:26am | Jul 28, 2026 10:50am | Jul 28, 2026 10:50am |  |  | Fair | No | The supply found ok, Voltages found 118-119/237
Outage | J.E.26.07.34242 | C001866764 | Evan Spaulding | St.Mary | Completed | Load_251374 | Highgate - 210 | Jul 27, 2026 9:26pm | Jul 28, 2026 3:19pm | Jul 28, 2026 3:49pm | Jul 28, 2026 3:49pm | Jul 28, 2026 5:18pm | Jul 28, 2026 5:42pm | Jul 28, 2026 5:43pm | Jul 28, 2026 5:43pm | BrokenWire |  | Fair | No | Use 1 -1 bolt. Clamp at pot head, voltage left 113v,114v,227v.
Outage | J.E.26.07.34274 | C001866762 | Rayon Foster | Hanover | Completed | Load_259314 | Orange Bay - 310 | Jul 27, 2026 9:01pm | Jul 28, 2026 7:36am | Jul 28, 2026 9:06am | Jul 28, 2026 9:06am | Jul 28, 2026 10:53am | Jul 28, 2026 10:14am | Jul 28, 2026 11:10am | Jul 28, 2026 11:10am | BangingWires |  | Fair | No | Damage cross harm customer reported on 40 feet concrete pole with secondary wires attached to pole refer to maintenance team to rectify
Non-Outage | J.E.26.07.34203 | C001866760 | Andre Williams | Trelawny | Completed | Load_250973 | Greenwood - 110 | Jul 27, 2026 8:50pm | Jul 27, 2026 8:51pm | Jul 27, 2026 9:44pm | Jul 27, 2026 9:44pm | Jul 27, 2026 9:53pm | Jul 27, 2026 9:55pm | Jul 27, 2026 9:55pm | Jul 27, 2026 9:55pm |  |  | Fair | No | Technician at plant resolving issue on there end switching phases from inside there panel
Non-Outage | J.E.26.07.34149 | C001866759 | Andrew Powell | St.Elizabeth | Completed | Load_267008 | Maggotty - 210 | Jul 27, 2026 8:45pm | Jul 27, 2026 8:45pm | Jul 27, 2026 8:50pm | Jul 27, 2026 8:54pm | Jul 27, 2026 9:25pm | Jul 27, 2026 9:45pm | Jul 27, 2026 9:46pm | Jul 27, 2026 9:46pm |  |  | Fair | No | Remade corroded service wire joints at secondary line 3 wire using two clamps, voltage reading 112v-113v phase to neutral 225v cross phase.
Non-Outage | J.E.26.07.31905 | C001866755 | Wayne Dillion | St.Elizabeth | Completed | Load_249486 | Maggotty - 110 | Jul 27, 2026 8:43pm | Jul 27, 2026 8:44pm | Jul 27, 2026 9:49pm | Jul 27, 2026 9:49pm | Jul 27, 2026 9:49pm | Jul 27, 2026 9:54pm | Jul 27, 2026 10:01pm | Jul 27, 2026 10:01pm | LeaningPole |  | Fair | No | Patrol and found one badly leaning 35ft wooden T pole no pole#. Please refer same to the maintenance department for replacement.
Outage | J.E.26.07.34215 | C001866758 | Donald Cunningham | St.Catherine | Completed | Load_249355 | Tredegar - 310 | Jul 27, 2026 8:43pm | Jul 27, 2026 8:44pm | Jul 27, 2026 10:23pm | Jul 27, 2026 10:23pm | Jul 27, 2026 10:42pm | Jul 27, 2026 10:42pm | Jul 27, 2026 10:48pm | Jul 27, 2026 10:48pm |  |  | Fair | No | Premises closed
Outage | J.E.26.07.34243 | C001866756 | Donald Cunningham | St.Catherine | Completed | Load_262408 | Tredegar - 310 | Jul 27, 2026 8:43pm | Jul 27, 2026 8:44pm | Jul 27, 2026 9:57pm | Jul 27, 2026 9:57pm | Jul 27, 2026 10:20pm | Jul 27, 2026 10:22pm | Jul 27, 2026 10:23pm | Jul 27, 2026 10:23pm |  |  | Fair | No | 1-20amp j/fuse blown found defective cross arm. needs daylight attention and bucket truck to replace, A Murray advised
Outage | J.E.26.07.34258 | C001866757 | Donald Cunningham | St.Catherine | Completed | Load_257259 | Tredegar - 310 | Jul 27, 2026 8:43pm | Jul 27, 2026 8:44pm | Jul 27, 2026 10:48pm | Jul 27, 2026 10:48pm | Jul 27, 2026 11:08pm | Jul 27, 2026 11:09pm | Jul 27, 2026 11:09pm | Jul 27, 2026 11:09pm |  |  | Fair | No | Premises not found
Non-Outage | J.E.26.07.33532 | C001866753 | Wayne Dillion | Manchester | Completed | Load_244017 | Spur Tree - 210 | Jul 27, 2026 8:42pm | Jul 27, 2026 8:44pm | Jul 28, 2026 10:06am | Jul 28, 2026 10:06am | Jul 28, 2026 10:14am | Jul 28, 2026 10:30am | Jul 28, 2026 10:33am | Jul 28, 2026 10:33am | BrokenPole |  | Fair | No | Patrol and found one broken 35ft wooden pole no pole #. Please refer same to the maintenance department for replacement.
Non-Outage | J.E.26.07.33970 | C001866752 | Wayne Dillion | St.Elizabeth | Completed | Load_238591 | Maggotty - 110 | Jul 27, 2026 8:42pm | Jul 27, 2026 8:44pm | Jul 27, 2026 10:13pm | Jul 27, 2026 10:13pm | Jul 27, 2026 10:13pm | Jul 27, 2026 10:14pm | Jul 27, 2026 10:15pm | Jul 27, 2026 10:15pm | BrokenWire |  | Fair | No | Unable to locate and customer not answering the phone.
Outage | J.E.26.07.34251 | C001866754 | Donald Cunningham | St.Catherine | Completed | Load_268172 | Tredegar - 310 | Jul 27, 2026 8:42pm | Jul 27, 2026 8:44pm | Jul 27, 2026 8:53pm | Jul 27, 2026 8:53pm | Jul 27, 2026 9:51pm | Jul 27, 2026 9:52pm | Jul 27, 2026 9:53pm | Jul 27, 2026 9:53pm |  |  | Fair | No | Broken and defective 8 feet cross arm need to replace refer to maintenance
Non-Outage | J.E.26.07.16560 | C001866751 | Andrew Powell | St.Elizabeth | Completed | Load_292854 | Spur Tree - 210 | Jul 27, 2026 8:40pm | Jul 27, 2026 8:44pm | Jul 27, 2026 9:47pm | Jul 27, 2026 9:47pm | Jul 27, 2026 10:25pm | Jul 27, 2026 10:26pm | Jul 27, 2026 10:27pm | Jul 27, 2026 10:27pm |  |  | Fair | No | Premises not located inadequately direction contact customer by telephone unsuccessful.
Outage | J.E.26.07.34078 | C001866748 | Marlon Brown | Trelawny | Completed | Load_257998 | Greenwood - 110 | Jul 27, 2026 8:20pm | Jul 27, 2026 8:39pm | Jul 27, 2026 10:23pm | Jul 27, 2026 10:23pm | Jul 28, 2026 3:27pm | Jul 28, 2026 3:27pm | Jul 28, 2026 3:28pm | Jul 28, 2026 3:28pm |  |  | Fair | No | Field service
Outage | J.E.26.07.33830 | C001866746 | Devon Grant | KSAN | Completed | Load_270129 | Constant Spring - 210 | Jul 27, 2026 7:54pm | Jul 27, 2026 7:55pm | Jul 27, 2026 10:16pm | Jul 27, 2026 10:16pm | Jul 27, 2026 10:16pm | Jul 27, 2026 10:16pm | Jul 27, 2026 10:16pm | Jul 27, 2026 10:16pm |  |  | Fair | No | Refuse blown 40amps junction by Fraser Cres.
Outage | J.E.26.07.34035 | C001866747 | Devon Grant | KSAN | Completed | Load_266238 | Constant Spring - 210 | Jul 27, 2026 7:54pm | Jul 27, 2026 7:55pm | Jul 27, 2026 8:26pm | Jul 27, 2026 8:26pm | Jul 27, 2026 9:12pm | Jul 27, 2026 10:15pm | Jul 27, 2026 10:16pm | Jul 27, 2026 10:16pm |  |  | Fair | No | Refuse blown 40amps junction by Fraser Cres.
Outage | J.E.26.07.34038 | C001866739 | Fitzroy Turner | KSAS | Completed | Load_300784 | Greenwich - 510 | Jul 27, 2026 7:36pm | Jul 27, 2026 7:36pm | Jul 27, 2026 8:44pm | Jul 27, 2026 8:44pm | Jul 27, 2026 9:14pm | Jul 27, 2026 9:18pm | Jul 27, 2026 9:21pm | Jul 27, 2026 9:21pm |  |  | Fair | No | Found 8amps junction fuse blown cause by bird replaced one 8amp fuse supply restored to customer
Outage | J.E.26.07.34062 | C001866736 | Javid Vernon | Westmoreland | Completed | Load_291994 | Paradise - 110 | Jul 27, 2026 7:30pm | Jul 27, 2026 7:53pm | Jul 27, 2026 8:13pm | Jul 27, 2026 8:13pm | Jul 27, 2026 8:13pm | Jul 27, 2026 8:13pm | Jul 27, 2026 8:15pm | Jul 27, 2026 8:15pm |  |  | Fair | No | Unable to locate customer and premises customer phone number is not ringing and no directions was given
Outage | J.E.26.07.34101 | C001866737 | Javid Vernon | Westmoreland | Completed | Load_262557 | Paradise - 210 | Jul 27, 2026 7:30pm | Jul 27, 2026 7:53pm | Jul 27, 2026 8:01pm | Jul 27, 2026 8:01pm | Jul 27, 2026 8:01pm | Jul 27, 2026 8:01pm | Jul 27, 2026 8:03pm | Jul 27, 2026 8:03pm |  |  | Fair | No | Customer stated that power was restored to the area and her premises
Outage | J.E.26.07.33982 | C001866734 | Romeo Brissett | St.James | Completed | Load_412840 | Bogue - 310 | Jul 27, 2026 7:29pm | Jul 27, 2026 7:29pm | Jul 27, 2026 7:34pm | Jul 27, 2026 10:21pm | Jul 27, 2026 10:21pm | Jul 27, 2026 10:31pm | Jul 27, 2026 10:33pm | Jul 27, 2026 10:33pm |  |  | Fair | No | Customer stated they reach home and power restored.
Outage | J.E.26.07.34133 | C001866733 | Swon Miller | St.James | Completed | Load_267503 | Bogue - 510 | Jul 27, 2026 7:28pm | Jul 27, 2026 7:29pm | Jul 27, 2026 10:39pm | Jul 27, 2026 10:39pm | Jul 27, 2026 11:01pm | Jul 27, 2026 11:11pm | Jul 27, 2026 11:13pm | Jul 27, 2026 11:13pm |  |  | Fair | No | Found customer service disconnected for nonpayment of bill voltage found 0.000 plz refer to field service voltage left 0.000
Non-Outage | J.E.26.07.34056 | C001866682 | Andre Williams | Trelawny | Completed | Load_260629 | Duncans - 110 | Jul 27, 2026 7:16pm | Jul 27, 2026 7:17pm | Jul 27, 2026 8:10pm | Jul 27, 2026 8:10pm | Jul 27, 2026 8:39pm | Jul 27, 2026 8:39pm | Jul 27, 2026 8:41pm | Jul 27, 2026 8:41pm |  |  | Fair | No | Phase rotation issue resolved by technician, premises ok
Outage | J.E.26.07.33988 | C001866666 | Swon Miller | St.James | Completed | Load_302188 | Bogue - 610 | Jul 27, 2026 6:46pm | Jul 27, 2026 6:52pm | Jul 27, 2026 8:28pm | Jul 27, 2026 8:28pm | Jul 27, 2026 8:40pm | Jul 14, 2026 10:23am | Jul 27, 2026 10:28pm | Jul 27, 2026 10:28pm |  |  | Fair | No | Found 1,8 amp and 1,10 amp junction fuse blown cause by contamination replace 8 amp and 10 amp junction fuse voltage found 0.000 voltage left 115/115/230
Non-Outage | J.E.26.07.33990 | C001866665 | Raymond Carr | null | Completed | null | null | Jul 27, 2026 6:43pm | Jul 27, 2026 6:43pm | Jul 27, 2026 6:57pm | Jul 27, 2026 6:57pm | Jul 27, 2026 7:29pm | Jul 27, 2026 7:50pm | Jul 27, 2026 8:00pm | Jul 27, 2026 8:00pm | Fire |  | Fair | No | 100kva transformer Tripp switch found operated. Line patrol and found okay, Tripp switch reset and supply was restored.
Outage | J.E.26.07.34019 | C001866663 | Richman Whyte | Westmoreland | Completed | Load_251790 | Paradise - 310 | Jul 27, 2026 6:43pm | Jul 27, 2026 6:43pm | Jul 27, 2026 7:43pm | Jul 27, 2026 7:43pm | Jul 27, 2026 8:28pm | Jul 27, 2026 9:18pm | Jul 27, 2026 9:18pm | Jul 27, 2026 9:18pm |  |  | Rains | No | Replace twenty amp junction fuse
Outage | J.E.26.07.34024 | C001866664 | Richman Whyte | Westmoreland | Completed | Load_253169 | Paradise - 310 | Jul 27, 2026 6:43pm | Jul 27, 2026 6:43pm | Jul 27, 2026 9:38pm | Jul 27, 2026 9:38pm | Jul 27, 2026 9:38pm | Jul 27, 2026 9:39pm | Jul 27, 2026 9:43pm | Jul 27, 2026 9:43pm |  |  | Rains | No | Customer is requesting disconnection her house was damaged in the hurricane and she is still getting a bill she need it to stop
Outage | J.E.26.07.34026 | C001866662 | Wayne Dillion | St.Elizabeth | Completed | Load_251996 | Maggotty - 110 | Jul 27, 2026 6:42pm | Jul 27, 2026 6:42pm | Jul 27, 2026 7:18pm | Jul 27, 2026 7:19pm | Jul 27, 2026 7:19pm | Jul 27, 2026 7:40pm | Jul 27, 2026 7:40pm | Jul 27, 2026 7:40pm |  |  | Fair | No | Patrol and found 10kva transformer primary bushing broken. Approximately 15 customers are without supply. Please refer same to the maintenance department for further assistance.
Outage | J.E.26.07.33586 | C001866661 | Jowayne Newmans | Portland | Completed | Load_249013 | Port Antonio - 310 | Jul 27, 2026 6:38pm | Jul 28, 2026 7:23am | Jul 28, 2026 7:55am | Jul 28, 2026 8:48am | Jul 28, 2026 8:49am | Jul 28, 2026 8:59am | Jul 28, 2026 8:59am | Jul 28, 2026 8:59am |  |  | Fair | No | Patrol and found customer without supply cause by burnt off service wire at secondary conductor, repair by reconnecting service wire using 1 one bolt clamp. Voltage reading after repair 112v. Customer has a 110v supply.
Outage | J.E.26.07.33762 | C001866659 | Denton Williams | Portland | Completed | Load_255140 | Port Antonio - 410 | Jul 27, 2026 6:38pm | Jul 27, 2026 6:38pm | Jul 27, 2026 8:53pm | Jul 27, 2026 8:55pm | Jul 27, 2026 9:10pm | Jul 27, 2026 9:25pm | Jul 27, 2026 9:28pm | Jul 27, 2026 9:28pm |  |  | Fair | No | 10amps junction fuse found blown. Suspect tree contact caused outage. Replace 10amps fuse to restore power supply at this location.
Outage | J.E.26.07.33134 | C001866658 | Tyrese Williams | St.Ann | Completed | Load_256510 | Cardiff Hall - 210 | Jul 27, 2026 6:35pm | Jul 27, 2026 6:36pm | Jul 27, 2026 7:09pm | Jul 27, 2026 7:11pm | Jul 27, 2026 7:12pm | Jul 27, 2026 7:13pm | Jul 27, 2026 7:13pm | Jul 27, 2026 7:13pm | Fire |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.07.33672 | C001866653 | Tyrese Williams | St.Ann | Completed | Load_242301 | Cardiff Hall - 210 | Jul 27, 2026 6:28pm | Jul 27, 2026 6:29pm | Jul 27, 2026 7:09pm | Jul 27, 2026 7:16pm | Jul 27, 2026 7:51pm | Jul 27, 2026 7:57pm | Jul 27, 2026 7:57pm | Jul 27, 2026 7:57pm |  |  | Fair | No | Premises found ok voltage found ok as well
Outage | J.E.26.07.33684 | C001866654 | Tyrese Williams | St.Ann | Completed | Load_412864 | Cardiff Hall - 210 | Jul 27, 2026 6:28pm | Jul 27, 2026 6:29pm | Jul 27, 2026 7:09pm | Jul 27, 2026 8:59pm | Jul 27, 2026 8:59pm | Jul 27, 2026 8:59pm | Jul 27, 2026 9:00pm | Jul 27, 2026 9:00pm |  |  | Fair | No | Premises found ok power was restored
Outage | J.E.26.07.33731 | C001866657 | Tyrese Williams | St.Ann | Completed | Load_248752 | Cardiff Hall - 210 | Jul 27, 2026 6:28pm | Jul 27, 2026 6:29pm | Jul 27, 2026 7:09pm | Jul 27, 2026 9:01pm | Jul 27, 2026 9:01pm | Jul 27, 2026 9:03pm | Jul 27, 2026 9:03pm | Jul 27, 2026 9:03pm |  |  | Fair | No | Premises found ok power was restored
Outage | J.E.26.07.33760 | C001866656 | Tyrese Williams | St.Ann | Completed | Load_263221 | Cardiff Hall - 210 | Jul 27, 2026 6:28pm | Jul 27, 2026 6:29pm | Jul 27, 2026 7:09pm | Jul 27, 2026 9:00pm | Jul 27, 2026 9:00pm | Jul 27, 2026 9:01pm | Jul 27, 2026 9:01pm | Jul 27, 2026 9:01pm |  |  | Fair | No | Premises found ok power was restored
Outage | J.E.26.07.33974 | C001866655 | Tyrese Williams | St.Ann | Completed | Load_243874 | Cardiff Hall - 210 | Jul 27, 2026 6:28pm | Jul 27, 2026 6:29pm | Jul 27, 2026 7:09pm | Jul 27, 2026 7:58pm | Jul 27, 2026 8:56pm | Jul 27, 2026 8:57pm | Jul 27, 2026 8:57pm | Jul 27, 2026 8:57pm |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.07.33878 | C001866649 | Daniel Francis | St.Ann | Completed | Load_305076 | Cardiff Hall - 210 | Jul 27, 2026 6:22pm | Jul 27, 2026 6:22pm | Jul 27, 2026 6:32pm | Jul 27, 2026 10:06pm | Jul 27, 2026 10:06pm | Jul 27, 2026 10:07pm | Jul 27, 2026 10:10pm | Jul 27, 2026 10:10pm |  |  | Fair | No | Power restored after switching was completed
Outage | J.E.26.07.33662 | C001866648 | Kaydon Taylor | KSAN | Completed | Load_249614 | Constant Spring - 410 | Jul 27, 2026 6:21pm | Jul 27, 2026 6:21pm | Jul 27, 2026 6:31pm | Jul 27, 2026 6:33pm | Jul 27, 2026 7:51pm | Jul 27, 2026 10:02pm | Jul 27, 2026 10:02pm | Jul 27, 2026 10:02pm |  | Y | Rains | No | Remove bamboo off line section
Outage | J.E.26.07.33720 | C001866646 | Richman Whyte | Westmoreland | Completed | Load_265538 | Paradise - 310 | Jul 27, 2026 6:20pm | Jul 27, 2026 6:25pm | Jul 27, 2026 9:19pm | Jul 27, 2026 9:19pm | Jul 27, 2026 9:32pm | Jul 27, 2026 9:33pm | Jul 27, 2026 9:33pm | Jul 27, 2026 9:33pm |  |  | Rains | No | Check and found okay
Outage | J.E.26.07.33747 | C001866647 | Romeo Brissett | St.James | Completed | Load_256402 | Bogue - 310 | Jul 27, 2026 6:20pm | Jul 27, 2026 6:35pm | Jul 27, 2026 7:32pm | Jul 27, 2026 7:32pm | Jul 27, 2026 7:32pm | Jul 27, 2026 7:28pm | Jul 27, 2026 7:34pm | Jul 27, 2026 7:34pm |  |  | Fair | Yes | Check and found ok
Outage | J.E.26.07.33936 | C001866645 | Swon Miller | St.James | Completed | Load_266451 | Bogue - 610 | Jul 27, 2026 6:19pm | Jul 27, 2026 6:20pm | Jul 27, 2026 6:50pm | Jul 27, 2026 6:50pm | Jul 27, 2026 8:00pm | Jul 21, 2026 8:25pm | Jul 27, 2026 8:28pm | Jul 27, 2026 8:28pm |  |  | Fair | No | Unable to locate customer
Outage | J.E.26.07.33802 | C001866644 | Daniel Francis | St.Ann | Completed | Load_575875 | Cardiff Hall - 210 | Jul 27, 2026 6:15pm | Jul 27, 2026 6:16pm | Jul 27, 2026 6:32pm | Jul 27, 2026 6:52pm | Jul 27, 2026 7:02pm | Jul 27, 2026 9:44pm | Jul 27, 2026 9:54pm | Jul 27, 2026 9:54pm |  |  | Fair | No | Found pole mount recloser open at Lcb6-1049 after patrol and found nothing close from control
Outage | J.E.26.07.33147 | C001866643 | Devon Grant | KSAS | Completed | Load_267072 | Duhaney - 310 | Jul 27, 2026 6:13pm | Jul 27, 2026 6:14pm | Jul 27, 2026 7:22pm | Jul 27, 2026 7:22pm | Jul 27, 2026 7:33pm | Jul 27, 2026 7:33pm | Jul 27, 2026 7:34pm | Jul 27, 2026 7:34pm |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.32437 | C001866642 | Devon Grant | KSAS | Completed | Load_246988 | Duhaney - 310 | Jul 27, 2026 6:11pm | Jul 27, 2026 6:11pm | Jul 27, 2026 6:52pm | Jul 27, 2026 6:52pm | Jul 27, 2026 7:22pm | Jul 27, 2026 7:22pm | Jul 27, 2026 7:22pm | Jul 27, 2026 7:22pm | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Premises found okay
Outage | J.E.26.07.33854 | C001866641 | Damion Reid | Manchester | Completed | Load_249671 | Kendal - 210 | Jul 27, 2026 6:03pm | Jul 27, 2026 6:05pm | Jul 27, 2026 7:45pm | Jul 27, 2026 7:45pm | Jul 27, 2026 8:31pm | Jul 27, 2026 8:59pm | Jul 27, 2026 8:59pm | Jul 27, 2026 8:59pm |  |  | Fair | No | Area found ok
Outage | J.E.26.07.33911 | C001866640 | Andre Williams | Trelawny | Completed | Load_292095 | Duncans - 210 | Jul 27, 2026 6:02pm | Jul 27, 2026 6:11pm | Jul 27, 2026 8:07pm | Jul 27, 2026 8:09pm | Jul 27, 2026 8:09pm | Jul 27, 2026 8:09pm | Jul 27, 2026 8:10pm | Jul 27, 2026 8:10pm |  |  | Fair | No | Unable to locate need more directions # not working
Outage | J.E.26.07.33925 | C001866638 | Omar King | St.Ann | Completed | Load_257615 | Ocho Rios - 510 | Jul 27, 2026 5:59pm | Jul 27, 2026 5:59pm | Jul 27, 2026 6:24pm | Jul 27, 2026 6:24pm | Jul 27, 2026 7:03pm | Jul 27, 2026 7:08pm | Jul 27, 2026 7:08pm | Jul 27, 2026 7:08pm | Fire |  | Fair | No | Found two (2) 50 amp junction fuse blow I observed that two other junction as blown at private property in the say area unable to do assessment at the property area is close with no one to assist me with access to pole.
Outage | J.E.26.07.33877 | C001866637 | Michael Christian | St.James | Completed | Load_263504 | Bogue - 310 | Jul 27, 2026 5:49pm | Jul 28, 2026 8:03am | Jul 28, 2026 8:17am | Jul 28, 2026 8:17am | Jul 28, 2026 9:06am | Jul 28, 2026 9:11am | Jul 28, 2026 9:11am | Jul 28, 2026 9:11am |  |  | Fair | No | Check and found okay voltage 110 113 224 at pothead internal fault
Non-Outage | J.E.26.07.25588 | C001866631 | Edward Royal | KSAS | Completed | Load_254739 | Cane River - 610 | Jul 27, 2026 5:15pm | Jul 27, 2026 5:16pm | Jul 27, 2026 6:46pm | Jul 27, 2026 6:46pm | Jul 27, 2026 6:46pm | Jul 27, 2026 7:02pm | Jul 27, 2026 7:02pm | Jul 27, 2026 7:02pm |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.07.25737 | C001866630 | Edward Royal | KSAS | Completed | Load_556074 | Hunts Bay - 410 | Jul 27, 2026 5:15pm | Jul 27, 2026 5:16pm | Jul 27, 2026 8:39pm | Jul 27, 2026 8:39pm | Jul 27, 2026 8:39pm | Jul 27, 2026 8:40pm | Jul 27, 2026 8:40pm | Jul 27, 2026 8:40pm |  |  | Fair | No | Premises was found with supply
Non-Outage | J.E.26.07.33020 | C001866629 | Edward Royal | KSAS | Completed | Load_241353 | Rockfort - 410 | Jul 27, 2026 5:15pm | Jul 27, 2026 5:16pm | Jul 27, 2026 7:37pm | Jul 27, 2026 7:37pm | Jul 27, 2026 7:52pm | Jul 27, 2026 8:17pm | Jul 27, 2026 8:22pm | Jul 27, 2026 8:22pm |  |  | Fair | No | Spliced and reconnected service phase using 2 single bolt clamp voltage reading 222 112 113v
Non-Outage | J.E.26.07.33049 | C001866627 | Edward Royal | KSAS | Completed | Load_251700 | Hunts Bay - 510 | Jul 27, 2026 5:15pm | Jul 27, 2026 5:16pm | Jul 27, 2026 7:05pm | Jul 27, 2026 7:05pm | Jul 27, 2026 7:05pm | Jul 27, 2026 7:06pm | Jul 27, 2026 7:06pm | Jul 27, 2026 7:06pm |  |  | Fair | No | Premises found close
Non-Outage | J.E.26.07.33520 | C001866628 | Edward Royal | KSAS | Completed | Load_239084 | Three Miles - 410 | Jul 27, 2026 5:15pm | Jul 27, 2026 5:16pm | Jul 27, 2026 8:41pm | Jul 27, 2026 8:41pm | Jul 27, 2026 8:53pm | Jul 27, 2026 9:18pm | Jul 27, 2026 9:19pm | Jul 27, 2026 9:19pm |  |  | Fair | No | Defective hex meter need change box # 00428. People’s in the community is stealing power from the school it look like a community is on the school light that is what caused the meter to burn .referred to field service
Non-Outage | J.E.26.07.33767 | C001866626 | Edward Royal | KSAS | Completed | Load_260329 | Rockfort - 210 | Jul 27, 2026 5:15pm | Jul 27, 2026 5:16pm | Jul 27, 2026 7:33pm | Jul 27, 2026 7:33pm | Jul 27, 2026 7:33pm | Jul 27, 2026 7:36pm | Jul 27, 2026 7:36pm | Jul 27, 2026 7:36pm |  |  | Fair | No | Premises found close
Non-Outage | J.E.26.07.32940 | C001866625 | Omar King | St.Ann | Completed | Load_575757 | Roaring River - 410 | Jul 27, 2026 5:13pm | Jul 27, 2026 6:07pm | Jul 27, 2026 7:08pm | Jul 27, 2026 7:08pm | Jul 27, 2026 9:04pm | Jul 27, 2026 9:10pm | Jul 27, 2026 9:10pm | Jul 27, 2026 9:10pm |  |  | Fair | No | System low voltage
Outage | J.E.26.07.33487 | C001866624 | Tyrese Williams | St.Ann | Completed | Load_267655 | Cardiff Hall - 310 | Jul 27, 2026 5:12pm | Jul 27, 2026 5:13pm | Jul 27, 2026 5:16pm | Jul 27, 2026 5:16pm | Jul 27, 2026 5:27pm | Jul 27, 2026 4:41pm | Jul 27, 2026 5:28pm | Jul 27, 2026 5:28pm |  |  | Fair | No | Replace a 8 amp junction fuse at pole
Outage | J.E.26.07.33388 | C001866623 | Wayne Dillion | St.Elizabeth | Completed | Load_260299 | Maggotty - 110 | Jul 27, 2026 5:09pm | Jul 27, 2026 5:09pm | Jul 27, 2026 5:29pm | Jul 27, 2026 5:29pm | Jul 27, 2026 5:29pm | Jul 27, 2026 6:03pm | Jul 27, 2026 6:03pm | Jul 27, 2026 6:03pm |  |  | Fair | No | Patrol and found one 65amp operate no pole # caused by a freak storm. Re-close and supply was restored to the areas.
Outage | J.E.26.07.33764 | C001866621 | Tajay Bernard | Hanover | Completed | Load_254647 | Orange Bay - 310 | Jul 27, 2026 5:00pm | Jul 27, 2026 5:01pm | Jul 27, 2026 10:12pm | Jul 27, 2026 10:12pm | Jul 27, 2026 10:12pm | Jul 27, 2026 10:13pm | Jul 27, 2026 10:13pm | Jul 27, 2026 10:13pm |  |  | Fair | No | This Call belongs to st james
Outage | J.E.26.07.33440 | C001866619 | Ryan Richards | Manchester | Completed | Load_244314 | Spur Tree - 210 | Jul 27, 2026 4:55pm | Jul 27, 2026 4:55pm | Jul 27, 2026 7:14pm | Jul 27, 2026 7:14pm | Jul 27, 2026 8:12pm | Jul 27, 2026 9:11pm | Jul 27, 2026 9:12pm | Jul 27, 2026 9:12pm |  |  | Fair | No | Premises found ok customer change over switch defective voltage 239/240/240/416 volts customer electrician was advised
Outage | J.E.26.07.33561 | C001866617 | Wayne Dillion | St.Elizabeth | Completed | Load_243652 | Maggotty - 110 | Jul 27, 2026 4:54pm | Jul 27, 2026 4:55pm | Jul 27, 2026 6:04pm | Jul 27, 2026 6:05pm | Jul 27, 2026 6:20pm | Jul 27, 2026 6:35pm | Jul 27, 2026 6:37pm | Jul 27, 2026 6:37pm |  |  | Fair | No | Patrol and found one blown 10amp junction fuse no pole#. Replace same and restored supply okay.
Outage | J.E.26.07.33689 | C001866604 | Devon Grant | KSAN | Completed | Load_245203 | Constant Spring - 210 | Jul 27, 2026 4:38pm | Jul 27, 2026 5:05pm | Jul 27, 2026 7:34pm | Jul 27, 2026 7:34pm | Jul 27, 2026 8:22pm | Jul 27, 2026 8:23pm | Jul 27, 2026 8:25pm | Jul 27, 2026 8:25pm | Fire |  | Fair | No | One 50kva transformer needed at location
Non-Outage | J.E.26.07.26877 | C001866596 | Clyde Brown | Clarendon | Completed | Load_243509 | Parnassus - 210 | Jul 27, 2026 4:36pm | Jul 27, 2026 4:36pm | Jul 27, 2026 5:37pm | Jul 27, 2026 5:37pm | Jul 27, 2026 5:37pm | Jul 27, 2026 5:28pm | Jul 27, 2026 5:40pm | Jul 27, 2026 5:40pm |  |  | Fair | No | Corroded phase at pothead connection remade with one clamp,voltage left 198/115/114 phase to neutral and 237/232/235V
Outage | J.E.26.07.33182 | C001866595 | Neville Spencer | Clarendon | Completed | Load_266472 | May Pen - 110 | Jul 27, 2026 4:35pm | Jul 27, 2026 4:35pm | Jul 27, 2026 9:45pm | Jul 27, 2026 9:45pm | Jul 27, 2026 9:45pm | Jul 27, 2026 11:16pm | Jul 27, 2026 11:16pm | Jul 27, 2026 11:16pm | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Renew blown 3 amp fuse protecting 25 , kva xmfr at pole #01064643 & blown 40 amp j/ fuse area restored.
Outage | J.E.26.07.33189 | C001866594 | Neville Spencer | Clarendon | Completed | Load_241202 | May Pen - 110 | Jul 27, 2026 4:35pm | Jul 27, 2026 4:35pm | Jul 27, 2026 7:41pm | Jul 27, 2026 7:41pm | Jul 27, 2026 7:41pm | Jul 27, 2026 7:41pm | Jul 27, 2026 9:45pm | Jul 27, 2026 9:45pm |  | Y | Fair | No | Open trip saver at pole # 0138322 cleared bamboo from 24 kv line . Also splice and retention broken primary phase Conductor used 50 ft#2AA conductor, 2 clamps, 2, preform area restored.
Outage | J.E.26.07.32633 | C001866574 | Swon Miller | St.James | Completed | Load_253840 | Bogue - 610 | Jul 27, 2026 4:20pm | Jul 27, 2026 4:21pm | Jul 27, 2026 4:27pm | Jul 27, 2026 4:27pm | Jul 27, 2026 5:43pm | Jul 28, 2026 6:34am | Jul 27, 2026 6:34pm | Jul 27, 2026 6:34pm |  |  | Fair | No | Check and found okay customer states that power supply was restored voltage found 116/115/231 voltage left 116/115/231
Outage | J.E.26.07.33654 | C001866575 | Romeo Brissett | St.James | Completed | Load_556983 | Bogue - 310 | Jul 27, 2026 4:20pm | Jul 27, 2026 4:26pm | Jul 27, 2026 8:47pm | Jul 27, 2026 8:47pm | Jul 27, 2026 8:47pm | Jul 27, 2026 10:00pm | Jul 27, 2026 10:21pm | Jul 27, 2026 10:21pm |  |  | Fair | No | Bank of (2)15KVA transformer found with lighting transformer fuse blown, transformer was tested closed and blown, once service wire is connected transformer not holding, service wire is suspected defective, it’s over a hundred (100ft) feet of #2 quad twisted. V/R 117-117-209-234-236-238. Transformers circuit was left energized and service wire isolated from transformer lead, please send to field service.
Outage | J.E.26.07.33529 | C001866557 | Derrick Grubb | St.Thomas | Completed | Load_245249 | Lysson - 410 | Jul 27, 2026 4:10pm | Jul 27, 2026 4:17pm | Jul 27, 2026 4:32pm | Jul 27, 2026 4:32pm | Jul 27, 2026 5:22pm | Jul 27, 2026 5:50pm | Jul 27, 2026 5:50pm | Jul 27, 2026 5:50pm | BrokenWire |  | Fair | No | Clear branch from line and refuse 7amp junction. No number on pole. Power restored.
Outage | J.E.26.07.33558 | C001866558 | Tajay Bernard | Hanover | Completed | Load_244685 | Orange Bay - 310 | Jul 27, 2026 4:10pm | Jul 27, 2026 4:29pm | Jul 27, 2026 5:26pm | Jul 27, 2026 8:08pm | Jul 27, 2026 9:10pm | Jul 27, 2026 10:11pm | Jul 27, 2026 10:12pm | Jul 27, 2026 10:12pm |  | Y | Fair | No | Remove vegetation on single phase primary line and refuse 1 15amp junction fuse, and also splice and retention 1 pole span of secondary neutral use 1 pre form and 1 clamp
Outage | J.E.26.07.33601 | C001866560 | Damion Reid | Manchester | Completed | Load_245396 | Kendal - 210 | Jul 27, 2026 4:10pm | Jul 27, 2026 4:10pm | Jul 27, 2026 5:55pm | Jul 27, 2026 5:55pm | Jul 27, 2026 6:20pm | Jul 27, 2026 6:41pm | Jul 27, 2026 6:42pm | Jul 27, 2026 6:42pm |  |  | Fair | No | Blown 30amp junction fuse found cause by contamination line patrol and replace blown fuse
Outage | J.E.26.07.32991 | C001866534 | Marlon Brown | Trelawny | Completed | Load_572266 | Martha Brae - 210 | Jul 27, 2026 4:01pm | Jul 27, 2026 4:12pm | Jul 27, 2026 4:15pm | Jul 27, 2026 4:15pm | Jul 27, 2026 4:19pm | Jul 27, 2026 4:20pm | Jul 27, 2026 4:20pm | Jul 27, 2026 4:20pm |  |  | Rains | No | Feeder issue, customer supply was restored.
Outage | J.E.26.07.33537 | C001866533 | Andre Williams | Trelawny | Completed | Load_249194 | Duncans - 110 | Jul 27, 2026 4:01pm | Jul 27, 2026 4:01pm | Jul 27, 2026 4:16pm | Jul 27, 2026 5:28pm | Jul 27, 2026 7:03pm | Jul 27, 2026 7:33pm | Jul 27, 2026 7:34pm | Jul 27, 2026 7:34pm |  |  | Rains | No | Patrol line section re fuse and close 15 amp main junctand one 5 amp on 50 kva transformer area now with supply
Outage | J.E.26.07.33541 | C001866532 | Richman Whyte | Westmoreland | Completed | Load_249908 | Paradise - 310 | Jul 27, 2026 4:00pm | Jul 27, 2026 4:00pm | Jul 27, 2026 7:15pm | Jul 27, 2026 7:17pm | Jul 27, 2026 7:17pm | Jul 27, 2026 7:18pm | Jul 27, 2026 7:19pm | Jul 27, 2026 7:19pm |  |  | Rains | No | Reclosed trip saver after removing bamboo
Outage | J.E.26.07.33401 | C001866528 | Christopher Edwards | KSAN | Completed | Load_259753 | Constant Spring - 410 | Jul 27, 2026 3:59pm | Jul 28, 2026 7:31am | Jul 28, 2026 12:52pm | Jul 28, 2026 12:52pm | Jul 28, 2026 1:45pm | Jul 28, 2026 3:16pm | Jul 28, 2026 3:19pm | Jul 28, 2026 3:19pm |  |  | Rains | No | Refuse blown junction fuseUsing (1) 20 ampsRefuse blown 25 kva transformer Using (1) 2 ampsDefective 25 kva transformer Defective transformer is the second transformer on mount Matthew’s road
Outage | J.E.26.07.33406 | C001866529 | Kaydon Taylor | KSAN | Completed | Load_268220 | Constant Spring - 410 | Jul 27, 2026 3:59pm | Jul 27, 2026 4:00pm | Jul 27, 2026 4:06pm | Jul 27, 2026 4:06pm | Jul 27, 2026 5:12pm | Jul 27, 2026 6:28pm | Jul 27, 2026 6:28pm | Jul 27, 2026 6:28pm |  |  | Rains | No | 30 Amp junction fuse found blown and replace atPole #0011767
Outage | J.E.26.07.33506 | C001866530 | Christopher Edwards | KSAN | Completed | Load_262984 | Constant Spring - 410 | Jul 27, 2026 3:59pm | Jul 28, 2026 7:31am | Jul 28, 2026 11:21am | Jul 28, 2026 12:51pm | Jul 28, 2026 12:51pm | Jul 28, 2026 12:51pm | Jul 28, 2026 12:51pm | Jul 28, 2026 12:51pm |  |  | Fair | No | Related to previous call that was resolved
Outage | J.E.26.07.33511 | C001866524 | Horace Malcolm | St.James | Completed | Load_252345 | Queens Drive - 310 | Jul 27, 2026 3:58pm | Jul 28, 2026 7:56am | Jul 28, 2026 2:23pm | Jul 28, 2026 2:23pm | Jul 28, 2026 2:39pm | Jul 28, 2026 2:50pm | Jul 28, 2026 2:50pm | Jul 28, 2026 2:50pm |  |  | Fair | No | Check and found premises ok supply restored
Outage | J.E.26.07.30183 | C001866514 | Ryan Richards | Manchester | Completed | Load_269460 | Porus - 310 | Jul 27, 2026 3:55pm | Jul 27, 2026 3:55pm | Jul 27, 2026 4:17pm | Jul 27, 2026 4:18pm | Jul 27, 2026 5:10pm | Jul 27, 2026 5:47pm | Jul 27, 2026 5:47pm | Jul 27, 2026 5:47pm |  |  | Fair | No | Slack transformer secondary bushing and corroded open 25 kva transformer remade slack bushing and reclose transformer customers are now with supply
Outage | J.E.26.07.33026 | C001866505 | Romeo Brissett | St.James | Completed | Load_266817 | Bogue - 310 | Jul 27, 2026 3:53pm | Jul 27, 2026 4:14pm | Jul 27, 2026 4:27pm | Jul 27, 2026 4:27pm | Jul 27, 2026 5:59pm | Jul 27, 2026 7:20pm | Jul 27, 2026 7:32pm | Jul 27, 2026 7:32pm |  |  | Fair | No | Found clearance breach, clear primary from customer service wire, replaced (1)30amps junction fuse. Recommending an intermediate pole to permanently clear breach. At spring mount 6 pole from junction pole.
Outage | J.E.26.07.33380 | C001866496 | Nickolas Rodriques | St.Catherine | Completed | Load_259014 | Tredegar - 210 | Jul 27, 2026 3:47pm | Jul 27, 2026 3:48pm | Jul 27, 2026 5:09pm | Jul 27, 2026 5:11pm | Jul 27, 2026 6:42pm | Jul 27, 2026 7:33pm | Jul 27, 2026 7:41pm | Jul 27, 2026 7:41pm | BrokenWire |  | Fair | No | Checked and found one pole span of secondary phase down caused by slack connection. Isolate a 50 KVA transformer for safety to repair. Repaired by splice and retention wire using 15 ft of 2-north aluminum, one splicing sleeve, two clamps and replaced the fuse after completing patrol.
Non-Outage | J.E.26.07.33142 | C001866494 | Clyde Brown | Clarendon | Completed | Load_243509 | Parnassus - 210 | Jul 27, 2026 3:46pm | Jul 27, 2026 3:47pm | Jul 27, 2026 4:06pm | Jul 27, 2026 4:06pm | Jul 27, 2026 4:44pm | Jul 27, 2026 5:28pm | Jul 27, 2026 5:34pm | Jul 27, 2026 5:34pm |  |  | Fair | No | Corroded pothead on 190 leg phase ,clamp change voltage left 198/115/114 phase and neutral and 237/232/235 on phase to phase.
Outage | J.E.26.07.33494 | C001866495 | Milton Charlton | KSAN | Completed | Load_263286 | Hope - 410 | Jul 27, 2026 3:46pm | Jul 27, 2026 3:47pm | Jul 27, 2026 4:22pm | Jul 27, 2026 4:31pm | Jul 27, 2026 5:51pm | Jul 27, 2026 5:50pm | Jul 27, 2026 5:55pm | Jul 27, 2026 5:55pm |  |  | Fair | No | Customers meter #2462625 and meter #2642625 at #6 violet avenue is not on the premises meters are stolen customers are whiteout supply. Refer to field service.
Outage | J.E.26.07.33516 | C001866493 | Richman Whyte | Westmoreland | Completed | Load_259377 | Paradise - 310 | Jul 27, 2026 3:46pm | Jul 27, 2026 3:48pm | Jul 27, 2026 6:17pm | Jul 27, 2026 6:17pm | Jul 27, 2026 7:15pm | Jul 27, 2026 7:16pm | Jul 27, 2026 7:17pm | Jul 27, 2026 7:17pm |  |  | Rains | No | Removed several bamboos from line and reclosed 3 30amp trip saver
Outage | J.E.26.07.33089 | C001866484 | Marlon Brown | Trelawny | Completed | Load_259972 | Greenwood - 210 | Jul 27, 2026 3:42pm | Jul 27, 2026 3:43pm | Jul 27, 2026 8:16pm | Jul 27, 2026 8:16pm | Jul 27, 2026 9:05pm | Jul 27, 2026 10:15pm | Jul 27, 2026 10:15pm | Jul 27, 2026 10:15pm | BrokenWire |  | Fair | No | Isolated 25kva transformer to repair 1 span secondary neutral conductor, clear tree limb from line, use 50ft #2 AAC, 2 #2 preforms and 1 pg clamp.
Outage | J.E.26.07.33454 | C001866485 | Marlon Brown | Trelawny | Completed | Load_259574 | Greenwood - 110 | Jul 27, 2026 3:42pm | Jul 27, 2026 3:43pm | Jul 27, 2026 4:30pm | Jul 27, 2026 4:30pm | Jul 27, 2026 6:20pm | Jul 27, 2026 8:16pm | Jul 27, 2026 8:16pm | Jul 27, 2026 8:16pm | BrokenWire |  | Fair | No | Tree cut on line by citizens cause secondary phase and neutral to brake, use 50ft AAC, 3 preforms and 3 pg clamps. 50kva transformer was isolated to effect repairs.
Non-Outage | J.E.26.07.33435 | C001866481 | Evan Spaulding | null | Completed | null | null | Jul 27, 2026 3:41pm | Jul 27, 2026 3:41pm | Jul 27, 2026 6:45pm | Jul 27, 2026 6:45pm | Jul 27, 2026 6:45pm | Jul 27, 2026 6:45pm | Jul 27, 2026 6:50pm | Jul 27, 2026 6:50pm |  |  | Fair | No | This issue was brought to the attention of the operation department and a 167 kva Transformer was bring over from Kingston but not yet installed, refer it again to the operations department
Outage | J.E.26.07.33072 | C001866482 | Evan Spaulding | St.Mary | Completed | Load_265580 | Highgate - 210 | Jul 27, 2026 3:41pm | Jul 27, 2026 3:41pm | Jul 27, 2026 4:10pm | Jul 27, 2026 4:10pm | Jul 27, 2026 5:14pm | Jul 27, 2026 5:30pm | Jul 27, 2026 5:31pm | Jul 27, 2026 5:31pm | Fire |  | Fair | No | Reattach broken neutral conductor using 1-1 bolt clamp,voltage left 112v,111v,223v.
Outage | J.E.26.07.33468 | C001866483 | Marlon Brown | Trelawny | Completed | Load_575490 | Greenwood - 210 | Jul 27, 2026 3:41pm | Jul 27, 2026 3:43pm | Jul 27, 2026 10:22pm | Jul 27, 2026 10:22pm | Jul 27, 2026 10:22pm | Jul 27, 2026 10:22pm | Jul 27, 2026 10:22pm | Jul 27, 2026 10:22pm | BrokenWire |  | Fair | No | Customer not at home.
Outage | J.E.26.07.33491 | C001866480 | Derrick Grubb | St.Thomas | Completed | Load_263983 | Good Year - 210 | Jul 27, 2026 3:40pm | Jul 27, 2026 3:41pm | Jul 27, 2026 6:25pm | Jul 27, 2026 6:25pm | Jul 27, 2026 7:25pm | Jul 27, 2026 7:27pm | Jul 27, 2026 7:27pm | Jul 27, 2026 7:27pm |  |  | Fair | No | Premises not found, several calls to customer phone went unanswered.
Non-Outage | J.E.26.07.33493 | C001866470 | Devon Grant | null | Completed | null | null | Jul 27, 2026 3:37pm | Jul 27, 2026 4:29pm | Jul 27, 2026 6:13pm | Jul 27, 2026 6:13pm | Jul 27, 2026 6:13pm | Jul 27, 2026 6:13pm | Jul 27, 2026 6:14pm | Jul 27, 2026 6:14pm | BrokenWire |  | Fair | No | 3w open secondary, Repair burnt jumper by using 2ft of #2AA wire
Non-Outage | J.E.26.07.33502 | C001866468 | Devon Grant | null | Completed | null | null | Jul 27, 2026 3:37pm | Jul 27, 2026 4:29pm | Jul 27, 2026 5:05pm | Jul 27, 2026 5:05pm | Jul 27, 2026 5:28pm | Jul 27, 2026 6:08pm | Jul 27, 2026 6:11pm | Jul 27, 2026 6:11pm | Fire |  | Fair | No | Burnt jumper found and corrected customer back to normal
Outage | J.E.26.07.32760 | C001866469 | Fitzroy Turner | KSAN | Completed | Load_293845 | Washington Blvd - 710 | Jul 27, 2026 3:37pm | Jul 27, 2026 3:37pm | Jul 27, 2026 4:52pm | Jul 27, 2026 4:52pm | Jul 27, 2026 5:01pm | Jul 27, 2026 5:10pm | Jul 27, 2026 5:11pm | Jul 27, 2026 5:11pm |  |  | Fair | No | Unable to communicate with customer meter please send email to field service department to check YPP box
Outage | J.E.26.07.33206 | C001866467 | Nickolas Rodriques | St.Catherine | Completed | Load_1000748 | Rhodens Pen - 210 | Jul 27, 2026 3:36pm | Jul 27, 2026 3:37pm | Jul 27, 2026 3:45pm | Jul 27, 2026 3:50pm | Jul 27, 2026 5:00pm | Jul 27, 2026 5:07pm | Jul 27, 2026 5:09pm | Jul 27, 2026 5:09pm |  |  | Fair | No | Unable to communicate with the customer to gain access to the gated community after several attempts.
Outage | J.E.26.07.33393 | C001866466 | Nickolas Rodriques | St.Catherine | Completed | Load_250129 | Rhodens Pen - 310 | Jul 27, 2026 3:36pm | Jul 27, 2026 3:37pm | Jul 27, 2026 7:41pm | Jul 27, 2026 7:52pm | Jul 27, 2026 8:25pm | Jul 27, 2026 8:42pm | Jul 27, 2026 8:46pm | Jul 27, 2026 8:46pm | Fire |  | Fair | No | Clarendon call
Outage | J.E.26.07.33507 | C001866465 | Tajay Bernard | Hanover | Completed | Load_302747 | Orange Bay - 310 | Jul 27, 2026 3:36pm | Jul 27, 2026 3:38pm | Jul 27, 2026 3:52pm | Jul 27, 2026 3:52pm | Jul 27, 2026 5:09pm | Jul 27, 2026 5:19pm | Jul 27, 2026 5:22pm | Jul 27, 2026 5:22pm |  |  | Fair | No | Refuse 1 25kva Transformer use 3amp fuse Transformer was found leaking oil and we are also recommending the transformer to be upgraded to a 50kva transformer
Outage | J.E.26.07.32855 | C001866462 | Donald Cunningham | St.Catherine | Completed | Load_262532 | Twickenham - 310 | Jul 27, 2026 3:35pm | Jul 27, 2026 3:36pm | Jul 27, 2026 7:06pm | Jul 27, 2026 7:06pm | Jul 27, 2026 8:13pm | Jul 27, 2026 8:14pm | Jul 27, 2026 8:16pm | Jul 27, 2026 8:16pm |  |  | Fair | No | Not located customer can’t be reach base on contact given
Outage | J.E.26.07.32936 | C001866461 | Donald Cunningham | St.Catherine | Completed | Load_269686 | Tredegar - 410 | Jul 27, 2026 3:35pm | Jul 27, 2026 3:36pm | Jul 27, 2026 4:55pm | Jul 27, 2026 4:55pm | Jul 27, 2026 5:43pm | Jul 27, 2026 5:43pm | Jul 27, 2026 5:55pm | Jul 27, 2026 5:55pm |  |  | Fair | No | Premises found ok customer section breaker trip same reset
Outage | J.E.26.07.33006 | C001866463 | Tajay Bernard | Hanover | Completed | Load_269776 | Orange Bay - 310 | Jul 27, 2026 3:35pm | Jul 27, 2026 3:37pm | Jul 27, 2026 5:29pm | Jul 27, 2026 5:30pm | Jul 27, 2026 6:51pm | Jul 27, 2026 8:07pm | Jul 27, 2026 8:08pm | Jul 27, 2026 8:08pm | LowHangingWires |  | Fair | No | Isolate 1 20amp junction fuse to splice and retention 1 pole span of secondary phase and neutral
Outage | J.E.26.07.33059 | C001866464 | Donald Cunningham | St.Catherine | Completed | Load_294308 | Twickenham - 310 | Jul 27, 2026 3:35pm | Jul 27, 2026 3:36pm | Jul 27, 2026 5:56pm | Jul 27, 2026 5:56pm | Jul 27, 2026 7:01pm | Jul 27, 2026 7:02pm | Jul 27, 2026 7:05pm | Jul 27, 2026 7:05pm |  |  | Fair | No | Customer unable to add credit refer to mr Ellison
Outage | J.E.26.07.33110 | C001866459 | Raymond Carr | St.Mary | Completed | Load_257423 | Blackstonedge - 110 | Jul 27, 2026 3:34pm | Jul 27, 2026 3:35pm | Jul 27, 2026 5:27pm | Jul 27, 2026 5:27pm | Jul 27, 2026 5:27pm | Jul 27, 2026 5:21pm | Jul 27, 2026 5:28pm | Jul 27, 2026 5:28pm |  |  | Fair | No | Supply was restored.
Outage | J.E.26.07.33117 | C001866460 | Donald Cunningham | St.Catherine | Completed | Load_264169 | Tredegar - 510 | Jul 27, 2026 3:34pm | Jul 27, 2026 3:36pm | Jul 27, 2026 3:52pm | Jul 27, 2026 3:52pm | Jul 27, 2026 4:53pm | Jul 27, 2026 4:53pm | Jul 27, 2026 4:54pm | Jul 27, 2026 4:54pm |  |  | Fair | No | Defective 25 kva transformer preparing for change
Outage | J.E.26.07.33445 | C001866458 | Raymond Carr | St.Mary | Completed | Load_264013 | Blackstonedge - 110 | Jul 27, 2026 3:34pm | Jul 27, 2026 3:35pm | Jul 27, 2026 3:48pm | Jul 27, 2026 3:49pm | Jul 27, 2026 5:10pm | Jul 27, 2026 5:00pm | Jul 27, 2026 5:26pm | Jul 27, 2026 5:26pm |  |  | Fair | No | Blown junction fuse found, line patrol and found okay, however unable to ascertain, cause of outage. A 20 amp fuse was used to renew, supply was restored.
Outage | J.E.26.07.33378 | C001866450 | Javid Vernon | Westmoreland | Completed | Load_268242 | Paradise - 110 | Jul 27, 2026 3:23pm | Jul 27, 2026 3:24pm | Jul 27, 2026 3:59pm | Jul 27, 2026 4:00pm | Jul 27, 2026 4:01pm | Jul 27, 2026 4:43pm | Jul 27, 2026 4:43pm | Jul 27, 2026 4:43pm |  |  | Fair | No | Splice and retention customer service wire use 5ft #6 triplex wire and three clamps voltage reading 117/114/231
Outage | J.E.26.07.33233 | C001866440 | Wayne Dillion | St.Elizabeth | Completed | Load_292638 | Maggotty - 110 | Jul 27, 2026 3:18pm | Jul 27, 2026 3:19pm | Jul 27, 2026 4:17pm | Jul 27, 2026 4:17pm | Jul 27, 2026 4:30pm | Jul 27, 2026 5:11pm | Jul 27, 2026 5:17pm | Jul 27, 2026 5:17pm |  |  | Fair | No | Patrol and found three 40amp chip savers operate no pole # caused by a freak storm. Re-close all three and supply was restored to the areas.
Outage | J.E.26.07.33341 | C001866433 | Richard Grant | St.Catherine | Completed | Load_256974 | New Michelton - 210 | Jul 27, 2026 3:18pm | Jul 27, 2026 3:20pm | Jul 27, 2026 3:56pm | Jul 27, 2026 6:55pm | Jul 27, 2026 6:55pm | Jul 27, 2026 6:55pm | Jul 27, 2026 6:55pm | Jul 27, 2026 6:55pm |  | Y | Rains | No | 15a fuse found blown for single phase primary caused by coconut tree limb fallen onto line. Bushing conducted to remove limb and push back tree away from line. 15a fuse replaced with same size fuse and supply restored. Area left okay.
Outage | J.E.26.07.33345 | C001866432 | Richard Grant | St.Catherine | Completed | Load_253596 | New Michelton - 210 | Jul 27, 2026 3:18pm | Jul 27, 2026 3:20pm | Jul 27, 2026 3:56pm | Jul 27, 2026 6:56pm | Jul 27, 2026 6:56pm | Jul 27, 2026 6:57pm | Jul 27, 2026 6:57pm | Jul 27, 2026 6:57pm |  | Y | Rains | No | 15a fuse found blown for single phase primary caused by coconut tree limb fallen onto line. Bushing conducted to remove limb and push back tree away from line. 15a fuse replaced with same size fuse and supply restored. Area left okay.
Outage | J.E.26.07.33418 | C001866435 | Richard Grant | St.Catherine | Completed | Load_238478 | New Michelton - 410 | Jul 27, 2026 3:18pm | Jul 27, 2026 3:20pm | Jul 27, 2026 6:57pm | Jul 27, 2026 6:57pm | Jul 27, 2026 7:24pm | Jul 27, 2026 7:56pm | Jul 27, 2026 7:56pm | Jul 27, 2026 7:56pm |  |  | Rains | No | Defective service wire found at location. 3 onebolt clamps, 3 penunions and approximately 100ft service wire used to change out defective wire. Supply restored and premises left okay
Outage | J.E.26.07.33439 | C001866434 | Richard Grant | St.Catherine | Completed | Load_264929 | New Michelton - 210 | Jul 27, 2026 3:18pm | Jul 27, 2026 3:20pm | Jul 27, 2026 3:56pm | Jul 27, 2026 4:12pm | Jul 27, 2026 5:41pm | Jul 27, 2026 6:52pm | Jul 27, 2026 6:54pm | Jul 27, 2026 6:54pm |  | Y | Rains | No | 15a fuse found blown for single phase primary caused by coconut tree limb fallen onto line. Bushing conducted to remove limb and push back tree away from line. 15a fuse replaced with same size fuse and supply restored. Area left okay.
Non-Outage | J.E.26.07.33001 | C001866431 | Damion Reid | null | Completed | null | null | Jul 27, 2026 3:17pm | Jul 27, 2026 3:18pm | Jul 27, 2026 3:35pm | Jul 27, 2026 3:36pm | Jul 27, 2026 4:40pm | Jul 27, 2026 5:44pm | Jul 27, 2026 5:47pm | Jul 27, 2026 5:47pm |  |  | Fair | No | Dislodge guy wire found banging against cable strand open 25kva transformer fuse link secure guy wire and restore power
Outage | J.E.26.07.33153 | C001866429 | Denton Williams | Portland | Completed | Load_248103 | Port Antonio - 410 | Jul 27, 2026 3:15pm | Jul 27, 2026 6:40pm | Jul 27, 2026 7:02pm | Jul 27, 2026 7:19pm | Jul 27, 2026 8:41pm | Jul 27, 2026 8:46pm | Jul 27, 2026 8:53pm | Jul 27, 2026 8:53pm | BrokenWire |  | Fair | No | The customer stated that a truck pass by and pull down service line. Upon reaching the location we had to disconnect service line to make area safe. However, we’re unable to reconnect customer because the customer stantion is bent and the meter pole is across road way about 15ft high which is below standard. Advised customer to contact a licensed electrician to carry out repairs.
Outage | J.E.26.07.32611 | C001866428 | Wan Carlos Scarlett | Portmore | Completed | Load_265520 | Naggo Head - 510 | Jul 27, 2026 3:13pm | Jul 27, 2026 3:20pm | Jul 27, 2026 4:05pm | Jul 27, 2026 6:20pm | Jul 27, 2026 6:43pm | Jul 27, 2026 7:25pm | Jul 27, 2026 7:27pm | Jul 27, 2026 7:27pm |  |  | Fair | No | Found 25KVA transformer drop lead wire to secondary line phase and neutral corroded use 3 one bolt clamps at pole readings 117-116-234
Outage | J.E.26.07.32678 | C001866426 | Wan Carlos Scarlett | Portmore | Completed | Load_242899 | Naggo Head - 510 | Jul 27, 2026 3:13pm | Jul 27, 2026 3:20pm | Jul 27, 2026 10:16pm | Jul 27, 2026 10:17pm | Jul 27, 2026 10:40pm | Jul 28, 2026 7:34am | Jul 28, 2026 7:34am | Jul 28, 2026 7:34am |  |  | Fair | No | Customer confirm that power supply has been restored
Outage | J.E.26.07.32808 | C001866418 | Wan Carlos Scarlett | Portmore | Completed | Load_239416 | Naggo Head - 510 | Jul 27, 2026 3:12pm | Jul 27, 2026 3:20pm | Jul 27, 2026 5:23pm | Jul 27, 2026 7:27pm | Jul 27, 2026 7:57pm | Jul 27, 2026 9:05pm | Jul 27, 2026 9:06pm | Jul 27, 2026 9:06pm |  |  | Fair | No | Found one span of open secondary line phase jumper burn from the one bolt clamp use 2 one bolt clamps at pole readings 117-116-234
Outage | J.E.26.07.32851 | C001866417 | Wan Carlos Scarlett | Portmore | Completed | Load_259464 | Naggo Head - 510 | Jul 27, 2026 3:12pm | Jul 27, 2026 3:20pm | Jul 27, 2026 4:24pm | Jul 27, 2026 5:25pm | Jul 27, 2026 5:46pm | Jul 27, 2026 6:19pm | Jul 27, 2026 6:20pm | Jul 27, 2026 6:20pm | BrokenWire |  | Fair | No | Found customer 3 wire service at pole with the neutral broken off use one bolt clamp at open secondary line neutral readings 115-114-230
Outage | J.E.26.07.32930 | C001866416 | Wan Carlos Scarlett | St.Catherine | Completed | Load_289883 | Twickenham - 210 | Jul 27, 2026 3:12pm | Jul 27, 2026 3:20pm | Jul 27, 2026 4:26pm | Jul 27, 2026 9:07pm | Jul 27, 2026 9:45pm | Jul 27, 2026 10:15pm | Jul 27, 2026 10:16pm | Jul 27, 2026 10:16pm |  |  | Fair | No | Found customer 3 wire service at pole with one of the phase broken off use one bolt clamp at pole readings 115-117-232
Outage | J.E.26.07.33453 | C001866415 | Moses Elliston | St.Catherine | Completed | Load_556892 | Twickenham - 210 | Jul 27, 2026 3:12pm | Jul 27, 2026 3:20pm | Jul 28, 2026 10:38am | Jul 28, 2026 10:38am | Jul 28, 2026 10:38am | Jul 28, 2026 10:38am | Jul 28, 2026 10:39am | Jul 28, 2026 10:39am |  |  | Fair | No | Supply ok at premises
Outage | J.E.26.07.33075 | C001866413 | Rayon Foster | Hanover | Completed | Load_292864 | Orange Bay - 310 | Jul 27, 2026 3:09pm | Jul 27, 2026 3:37pm | Jul 27, 2026 4:44pm | Jul 27, 2026 4:44pm | Jul 27, 2026 5:50pm | Jul 27, 2026 7:07pm | Jul 27, 2026 7:07pm | Jul 27, 2026 7:07pm |  |  | Rains | No | Blow 20 a,ps junction fuse remove fuse holder patrol primary line line was clear refuse with same 20amps fuse reclose after finishing patrolling
Outage | J.E.26.07.33175 | C001866362 | Milton Charlton | KSAN | Completed | Load_243364 | Hope - 510 | Jul 27, 2026 2:35pm | Jul 27, 2026 2:35pm | Jul 27, 2026 2:40pm | Jul 27, 2026 3:06pm | Jul 27, 2026 4:07pm | Jul 27, 2026 4:05pm | Jul 27, 2026 4:15pm | Jul 27, 2026 4:15pm |  |  | Fair | No | Customer service wire #6 duplex phase burn off at pole. Repair using one 1 bolt clamp.
Non-Outage | J.E.26.07.32657 | C001866355 | Fredrick Hamilton | KSAN | Completed | Load_573987 | Washington Blvd - 410 | Jul 27, 2026 2:28pm | Jul 27, 2026 2:28pm | Jul 28, 2026 8:16am | Jul 28, 2026 8:48am | Jul 28, 2026 9:21am | Jul 28, 2026 9:32am | Jul 28, 2026 9:32am | Jul 28, 2026 9:32am |  |  | Fair | No | Single phase condition detected at pole same was corrected 1 clamp used
Non-Outage | J.E.26.07.32669 | C001866354 | Fredrick Hamilton | KSAN | Completed | Load_251210 | Washington Blvd - 610 | Jul 27, 2026 2:28pm | Jul 27, 2026 2:28pm | Jul 28, 2026 8:16am | Jul 28, 2026 9:37am | Jul 28, 2026 9:43am | Jul 28, 2026 10:52am | Jul 28, 2026 10:52am | Jul 28, 2026 10:52am |  |  | Fair | No | 232v/110v/120v obtained corrosion detected at pole same was corrected 3 penunion used
Non-Outage | J.E.26.07.33003 | C001866349 | Fredrick Hamilton | KSAN | Completed | Load_239622 | Constant Spring - 410 | Jul 27, 2026 2:28pm | Jul 27, 2026 2:28pm | Jul 28, 2026 8:16am | Jul 28, 2026 12:48pm | Jul 28, 2026 12:48pm | Jul 28, 2026 12:49pm | Jul 28, 2026 12:49pm | Jul 28, 2026 12:49pm |  |  | Fair | No | Multiple calls to customer went straight to voicemail
Outage | J.E.26.07.33116 | C001866343 | Javid Vernon | Westmoreland | Completed | Load_249451 | Paradise - 110 | Jul 27, 2026 2:22pm | Jul 27, 2026 3:25pm | Jul 27, 2026 5:25pm | Jul 27, 2026 5:26pm | Jul 27, 2026 5:39pm | Jul 27, 2026 5:47pm | Jul 27, 2026 5:52pm | Jul 27, 2026 5:52pm | BrokenWire |  | Fair | No | Premises check and found okay customer reporting internet wire they want to be remove from infront her gate not related to JPS
Outage | J.E.26.07.33016 | C001866341 | Moses Elliston | St.Catherine | Completed | Load_263708 | Twickenham - 310 | Jul 27, 2026 2:18pm | Jul 27, 2026 2:21pm | Jul 27, 2026 3:57pm | Jul 27, 2026 3:58pm | Jul 27, 2026 3:58pm | Jul 27, 2026 2:52pm | Jul 27, 2026 4:00pm | Jul 27, 2026 4:00pm |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.07.33088 | C001866331 | Edward Royal | KSAS | Completed | Load_300847 | Cane River - 410 | Jul 27, 2026 2:11pm | Jul 27, 2026 2:11pm | Jul 27, 2026 2:42pm | Jul 27, 2026 2:42pm | Jul 27, 2026 2:42pm | Jul 27, 2026 2:43pm | Jul 27, 2026 2:54pm | Jul 27, 2026 2:54pm |  |  | Fair | No | Meter not responding meter need to be check reffered to field service
Outage | J.E.26.07.33061 | C001866323 | Derrick Grubb | St.Thomas | Completed | Load_262773 | Lysson - 410 | Jul 27, 2026 2:03pm | Jul 27, 2026 3:41pm | Jul 27, 2026 5:50pm | Jul 27, 2026 5:50pm | Jul 27, 2026 6:02pm | Jul 27, 2026 6:25pm | Jul 27, 2026 6:25pm | Jul 27, 2026 6:25pm | BrokenWire |  | Fair | No | Reconnect customer neutral wire using a one bolt clamp. Voltage readings when leaving 114v, 115v, 230v.
Non-Outage | J.E.26.07.31356 | C001866322 | Fredrick Hamilton | KSAN | Completed | Load_263165 | Constant Spring - 210 | Jul 27, 2026 2:01pm | Jul 27, 2026 2:02pm | Jul 27, 2026 2:20pm | Jul 27, 2026 2:29pm | Jul 27, 2026 3:12pm | Jul 27, 2026 3:32pm | Jul 27, 2026 3:32pm | Jul 27, 2026 3:32pm |  |  | Fair | No | 247.7v/122.9v/124v obtained high voltage detected affecting multiple customers Please have emergency check transformer
Outage | J.E.26.07.33039 | C001866316 | Cliton Henry | St.Mary | Completed | Load_250773 | Highgate - 210 | Jul 27, 2026 1:57pm | Jul 27, 2026 2:01pm | Jul 27, 2026 2:04pm | Jul 27, 2026 2:04pm | Jul 27, 2026 3:18pm | Jul 27, 2026 3:52pm | Jul 27, 2026 3:53pm | Jul 27, 2026 3:53pm |  |  | Fair | No | A blown 15 amp junction fuse found at pole #0167963 and a blown 2 amp fuse for a 25 kva at pole #034088. Supply restored using 1-15 amp fuse at pole #0167963 and 1-3 amp at pole #034088 respectively.
Outage | J.E.26.07.33060 | C001866302 | Damion Reid | Manchester | Completed | Load_269943 | Kendal - 210 | Jul 27, 2026 1:46pm | Jul 27, 2026 3:21pm | Jul 27, 2026 6:44pm | Jul 27, 2026 6:44pm | Jul 27, 2026 7:08pm | Jul 27, 2026 7:44pm | Jul 27, 2026 7:45pm | Jul 27, 2026 7:45pm |  |  | Fair | No | Unable to contact or locate customer
Outage | J.E.26.07.32992 | C001866297 | Rayon Foster | Hanover | Completed | Load_264368 | Orange Bay - 310 | Jul 27, 2026 1:38pm | Jul 27, 2026 1:39pm | Jul 27, 2026 4:08pm | Jul 27, 2026 4:08pm | Jul 27, 2026 4:08pm | Jul 27, 2026 4:17pm | Jul 27, 2026 4:17pm | Jul 27, 2026 4:17pm |  |  | Rains | No | Coon jps pole remake joints using two clamps voltage after changing clamps 110/109AB19
Outage | J.E.26.07.33006 | C001866298 | Dean Smith | Hanover | Completed | Load_269776 | Orange Bay - 310 | Jul 27, 2026 1:38pm | Jul 27, 2026 1:40pm | Jul 27, 2026 3:17pm | Jul 27, 2026 3:17pm | Jul 27, 2026 3:17pm | Jul 27, 2026 3:17pm | Jul 27, 2026 3:18pm | Jul 27, 2026 3:18pm | LowHangingWires |  | Fair | No | Shift ended
Non-Outage | J.E.26.07.33056 | C001866293 | Dwain Samuels | Westmoreland | Completed | Load_255148 | Paradise - 210 | Jul 27, 2026 1:37pm | Jul 27, 2026 1:37pm | Jul 27, 2026 3:03pm | Jul 28, 2026 9:30am | Jul 28, 2026 10:02am | Jul 28, 2026 10:33am | Jul 28, 2026 10:35am | Jul 28, 2026 10:35am |  |  | Fair | No | Corrosion found at 3 wire pole. Voltage check 122-0-122. Corrosion clear use 2 one bolt clamp. Voltage check 122-120-242
Non-Outage | J.E.26.07.33035 | C001866292 | Derrick Dawkins | St.James | Completed | Load_260404 | Bogue - 610 | Jul 27, 2026 1:36pm | Jul 27, 2026 1:37pm | Jul 27, 2026 2:04pm | Jul 27, 2026 2:04pm | Jul 27, 2026 2:54pm | Jul 27, 2026 3:09pm | Jul 27, 2026 3:09pm | Jul 27, 2026 3:09pm |  |  | Fair | No | Found a 50 kva transfer fuse blown replace a 5 amp junction fuse voltage 241/232/229 412/405/401
Outage | J.E.26.07.33026 | C001866280 | Shamour Haughton | St.James | Completed | Load_245091 | Bogue - 310 | Jul 27, 2026 1:21pm | Jul 27, 2026 1:21pm | Jul 27, 2026 1:28pm | Jul 27, 2026 1:29pm | Jul 27, 2026 3:12pm | Jul 27, 2026 3:12pm | Jul 27, 2026 3:54pm | Jul 27, 2026 3:54pm |  |  | Fair | No | Found 30amp junction fuse blown, patrolled and test closed, area still without power, please refer to 3pm crew
Non-Outage | J.E.26.07.33025 | C001866279 | Andre Smith | KSAS | Completed | Load_254801 | Greenwich - 510 | Jul 27, 2026 1:20pm | Jul 27, 2026 1:20pm | Jul 27, 2026 2:30pm | Jul 27, 2026 2:30pm | Jul 27, 2026 2:58pm | Jul 27, 2026 2:59pm | Jul 27, 2026 2:59pm | Jul 27, 2026 2:59pm | BrokenWire |  | Fair | No | Customer meter found burnt and defective field service department required to replace meter
Non-Outage | J.E.26.07.32927 | C001866271 | Andre Williams | Trelawny | Completed | Load_292657 | Duncans - 110 | Jul 27, 2026 1:15pm | Jul 27, 2026 1:15pm | Jul 27, 2026 1:21pm | Jul 27, 2026 1:21pm | Jul 27, 2026 1:53pm | Jul 27, 2026 1:55pm | Jul 27, 2026 1:55pm | Jul 27, 2026 1:55pm |  |  | Fair | No | Internal issue phases where switch internally, technician was advised to set back in correct order
Non-Outage | J.E.26.07.27822 | C001866256 | Edward Royal | KSAS | Completed | Load_268029 | Cane River - 410 | Jul 27, 2026 1:08pm | Jul 27, 2026 1:08pm | Jul 27, 2026 1:13pm | Jul 27, 2026 1:13pm | Jul 27, 2026 1:24pm | Jul 27, 2026 1:25pm | Jul 27, 2026 1:25pm | Jul 27, 2026 1:25pm |  |  | Fair | No | When contacted customer by phone customer said that nobody is at home
Non-Outage | J.E.26.07.32962 | C001866255 | Odeanie Davis | KSAN | Completed | Load_241775 | Washington Blvd - 310 | Jul 27, 2026 1:03pm | Jul 27, 2026 1:04pm | Jul 27, 2026 1:24pm | Jul 27, 2026 2:28pm | Jul 27, 2026 2:28pm | Jul 27, 2026 2:31pm | Jul 27, 2026 2:33pm | Jul 27, 2026 2:33pm |  |  | Fair | No | 117v/0.4v One phasing from meter in rammi box Customer has partial supply
Non-Outage | J.E.26.07.13254 | C001866244 | Nicholas Dillon | Manchester | Completed | Load_239279 | Spur Tree - 210 | Jul 27, 2026 12:51pm | Jul 27, 2026 12:52pm | Jul 27, 2026 1:48pm | Jul 27, 2026 1:48pm | Jul 27, 2026 1:48pm | Jul 27, 2026 1:50pm | Jul 27, 2026 1:51pm | Jul 27, 2026 1:51pm |  |  | Fair | Yes | Check and found corrosion at pole clean corrosion use 1 one bolt clamp before I left voltage is 120 120 phase to phase 241
Outage | J.E.26.07.32950 | C001866240 | Michael Christian | St.James | Completed | Load_246542 | Bogue - 310 | Jul 27, 2026 12:46pm | Jul 27, 2026 12:49pm | Jul 27, 2026 1:09pm | Jul 27, 2026 1:09pm | Jul 27, 2026 1:43pm | Jul 27, 2026 2:41pm | Jul 27, 2026 2:41pm | Jul 27, 2026 2:41pm | BrokenWire |  | Fair | No | F round broken secondary line replace use 2 clamps voltage 111 113 at pothead
Outage | J.E.26.07.32963 | C001866241 | Michael Christian | St.James | Completed | Load_555842 | Bogue - 310 | Jul 27, 2026 12:46pm | Jul 27, 2026 12:49pm | Jul 27, 2026 2:41pm | Jul 27, 2026 2:42pm | Jul 27, 2026 2:57pm | Jul 27, 2026 3:05pm | Jul 27, 2026 3:05pm | Jul 27, 2026 3:05pm |  |  | Fair | No
Outage | J.E.26.07.32771 | C001866239 | Marlon Brown | Trelawny | Completed | Load_292497 | Greenwood - 210 | Jul 27, 2026 12:44pm | Jul 27, 2026 9:51pm | Jul 27, 2026 10:15pm | Jul 27, 2026 10:16pm | Jul 27, 2026 10:16pm | Jul 27, 2026 10:21pm | Jul 27, 2026 10:21pm | Jul 27, 2026 10:21pm | Fire |  | Fair | No | Same as call number 33089.
Outage | J.E.26.07.32903 | C001866235 | Andre Williams | Trelawny | Completed | Load_247321 | Duncans - 110 | Jul 27, 2026 12:41pm | Jul 28, 2026 7:35am | Jul 28, 2026 7:45am | Jul 28, 2026 7:48am | Jul 28, 2026 8:28am | Jul 28, 2026 8:45am | Jul 28, 2026 8:47am | Jul 28, 2026 8:47am |  |  | Fair | No | Switch phases at pothead to resolve customer rotation issue voltage on bothe phase 112+115=227/. 206volts
Outage | J.E.26.07.32985 | C001866234 | Andre Williams | Trelawny | Completed | Load_252012 | Duncans - 210 | Jul 27, 2026 12:41pm | Jul 27, 2026 1:19pm | Jul 27, 2026 7:34pm | Jul 27, 2026 7:34pm | Jul 27, 2026 7:56pm | Jul 27, 2026 7:58pm | Jul 27, 2026 7:59pm | Jul 27, 2026 7:59pm |  |  | Rains | No | Reconnect broken phase on customer #6 three wire service
Outage | J.E.26.07.32692 | C001866230 | Andre Williams | Trelawny | Completed | Load_256637 | Duncans - 110 | Jul 27, 2026 12:40pm | Jul 27, 2026 12:42pm | Jul 27, 2026 1:16pm | Jul 27, 2026 1:17pm | Jul 27, 2026 1:17pm | Jul 27, 2026 1:21pm | Jul 27, 2026 1:21pm | Jul 27, 2026 1:21pm | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Switch phase at customer pothead to fix rotation is on two 120 phase No fire on wire
Outage | J.E.26.07.32779 | C001866231 | Andre Williams | Trelawny | Completed | Load_246434 | Greenwood - 110 | Jul 27, 2026 12:40pm | Jul 27, 2026 12:42pm | Jul 27, 2026 1:56pm | Jul 27, 2026 3:29pm | Jul 27, 2026 3:29pm | Jul 27, 2026 4:15pm | Jul 27, 2026 4:16pm | Jul 27, 2026 4:16pm | Fire |  | Fair | No | Splice and retention broken #6 conductor on 3 wire service
Non-Outage | J.E.26.07.32334 | C001866228 | Hopeton Henry | St.Thomas | Completed | Load_266044 | Good Year - 210 | Jul 27, 2026 12:38pm | Jul 27, 2026 12:38pm | Jul 27, 2026 1:18pm | Jul 27, 2026 2:09pm | Jul 27, 2026 2:26pm | Jul 27, 2026 2:57pm | Jul 27, 2026 2:59pm | Jul 27, 2026 2:59pm |  |  | Fair | No | Refresh connections at pole and pot head 111-111-222volts
Non-Outage | J.E.26.07.32770 | C001866229 | Stephen Taylor | St.Thomas | Completed | Load_255607 | Lysson - 410 | Jul 27, 2026 12:38pm | Jul 27, 2026 12:51pm | Jul 28, 2026 8:07am | Jul 28, 2026 8:19am | Jul 28, 2026 9:27am | Jul 28, 2026 9:28am | Jul 28, 2026 9:29am | Jul 28, 2026 9:29am |  |  | Fair | No | Patrol area and power is in the area but several calls to single customer and no one answering the phones failed to locate customer
Outage | J.E.26.07.32970 | C001866220 | Stephen Taylor | St.Thomas | Completed | Load_240330 | Good Year - 210 | Jul 27, 2026 12:38pm | Jul 27, 2026 12:38pm | Jul 27, 2026 12:43pm | Jul 27, 2026 12:45pm | Jul 27, 2026 12:49pm | Jul 27, 2026 1:13pm | Jul 27, 2026 1:24pm | Jul 27, 2026 1:24pm | BrokenWire |  | Fair | No | Retention service wire customer is now okay reading 111,112
Outage | J.E.26.07.32983 | C001866219 | Andre Smith | KSAN | Completed | Load_248819 | Washington Blvd - 310 | Jul 27, 2026 12:35pm | Jul 27, 2026 12:35pm | Jul 27, 2026 1:09pm | Jul 27, 2026 1:09pm | Jul 27, 2026 1:57pm | Jul 27, 2026 2:29pm | Jul 27, 2026 2:29pm | Jul 27, 2026 2:29pm |  |  | Fair | No | Repair burnt phase at pothead supply restored 118 v
Outage | J.E.26.07.32957 | C001866204 | Romaine Roberts | St.Mary | Completed | Load_250415 | Annotto Bay - 210 | Jul 27, 2026 12:25pm | Jul 27, 2026 12:27pm | Jul 27, 2026 2:05pm | Jul 27, 2026 2:05pm | Jul 27, 2026 2:05pm | Jul 27, 2026 2:06pm | Jul 27, 2026 2:06pm | Jul 27, 2026 2:06pm |  |  | Fair | No | Junction fuse found blown patrol line nothing was found replace 30 amp no pole number found power restore
Outage | J.E.26.07.32972 | C001866199 | Romaine Roberts | St.Mary | Completed | Load_352260 | Annotto Bay - 210 | Jul 27, 2026 12:23pm | Jul 27, 2026 12:27pm | Jul 27, 2026 2:02pm | Jul 27, 2026 2:02pm | Jul 27, 2026 2:02pm | Jul 27, 2026 2:02pm | Jul 27, 2026 2:04pm | Jul 27, 2026 2:04pm |  |  | Fair | No | Junction fuse found blown patrol line nothing was found replace 30 amp no pole number found power restore
Outage | J.E.26.07.32888 | C001866198 | Christopher Edwards | KSAN | Completed | Load_247395 | Constant Spring - 410 | Jul 27, 2026 12:19pm | Jul 27, 2026 12:20pm | Jul 27, 2026 12:25pm | Jul 27, 2026 12:31pm | Jul 27, 2026 12:31pm | Jul 27, 2026 12:31pm | Jul 27, 2026 12:32pm | Jul 27, 2026 12:32pm |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Outage | J.E.26.07.32955 | C001866188 | Daniel Francis | St.Ann | Completed | Load_249772 | Roaring River - 410 | Jul 27, 2026 12:11pm | Jul 27, 2026 12:17pm | Jul 27, 2026 1:00pm | Jul 27, 2026 1:00pm | Jul 27, 2026 1:07pm | Jul 27, 2026 2:02pm | Jul 27, 2026 2:02pm | Jul 27, 2026 2:02pm |  |  | Fair | No | Patrol and found junction blown at 044970 patrol and renew 2 30amp
Non-Outage | J.E.26.07.32893 | C001866187 | Javid Vernon | Westmoreland | Completed | Load_260069 | Paradise - 210 | Jul 27, 2026 12:09pm | Jul 27, 2026 3:25pm | Jul 27, 2026 4:47pm | Jul 27, 2026 4:47pm | Jul 27, 2026 5:08pm | Jul 27, 2026 5:25pm | Jul 27, 2026 5:25pm | Jul 27, 2026 5:25pm |  |  | Fair | No | Area check and found okay unable to locate customer and premises customer phone number is not ringing
Outage | J.E.26.07.32925 | C001866182 | Barnett Brown | Manchester | Completed | Load_259080 | Spur Tree - 310 | Jul 27, 2026 12:07pm | Jul 27, 2026 12:09pm | Jul 27, 2026 1:21pm | Jul 27, 2026 1:21pm | Jul 27, 2026 2:38pm | Jul 27, 2026 2:39pm | Jul 27, 2026 4:20pm | Jul 27, 2026 4:20pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.32947 | C001866181 | Daniel Francis | St.Ann | Completed | Load_249244 | Roaring River - 410 | Jul 27, 2026 12:05pm | Jul 27, 2026 12:08pm | Jul 27, 2026 2:03pm | Jul 27, 2026 2:03pm | Jul 27, 2026 2:03pm | Jul 27, 2026 2:04pm | Jul 27, 2026 2:05pm | Jul 27, 2026 2:05pm |  |  | Fair | No | Power restored
Non-Outage | J.E.26.07.23657 | C001866179 | Daniel Francis | St.Ann | Completed | Load_262327 | Cardiff Hall - 310 | Jul 27, 2026 12:02pm | Jul 27, 2026 12:11pm | Jul 27, 2026 3:11pm | Jul 27, 2026 3:11pm | Jul 27, 2026 3:11pm | Jul 27, 2026 3:12pm | Jul 27, 2026 3:12pm | Jul 27, 2026 3:12pm |  |  | Fair | No | Customer not answering phone
Non-Outage | J.E.26.07.32703 | C001866178 | Rayon Foster | null | Completed | null | null | Jul 27, 2026 12:01pm | Jul 27, 2026 12:02pm | Jul 27, 2026 12:55pm | Jul 27, 2026 1:17pm | Jul 27, 2026 2:22pm | Jul 27, 2026 2:42pm | Jul 27, 2026 2:42pm | Jul 27, 2026 2:42pm | LowHangingWires |  | Fair | No | Observed No secondary JPS wires hanging low observed cable wire hanging low no meter was number attach to report unable to reach on cell phone
Outage | J.E.26.07.32917 | C001866175 | Daniel Francis | St.Ann | Completed | Load_259099 | Ocho Rios - 310 | Jul 27, 2026 11:57am | Jul 27, 2026 12:06pm | Jul 27, 2026 6:32pm | Jul 28, 2026 11:23am | Jul 28, 2026 12:31pm | Jul 28, 2026 1:32pm | Jul 28, 2026 1:32pm | Jul 28, 2026 1:32pm | BrokenWire |  | Fair | No | Found D iron dislodge along with secondary phase conducter replace d iron complete and re anchor conductors
Outage | J.E.26.07.32932 | C001866174 | Daniel Francis | St.Ann | Completed | Load_255970 | Cardiff Hall - 210 | Jul 27, 2026 11:57am | Jul 27, 2026 12:16pm | Jul 27, 2026 2:05pm | Jul 27, 2026 2:05pm | Jul 27, 2026 2:05pm | Jul 27, 2026 2:12pm | Jul 27, 2026 2:12pm | Jul 27, 2026 2:12pm |  |  | Fair | No | Found okay customer say light come
Outage | J.E.26.07.32938 | C001866173 | Daniel Francis | St.Ann | Completed | Load_574268 | Roaring River - 210 | Jul 27, 2026 11:56am | Jul 27, 2026 12:06pm | Jul 27, 2026 12:30pm | Jul 27, 2026 12:30pm | Jul 27, 2026 12:59pm | Jul 27, 2026 1:00pm | Jul 27, 2026 1:00pm | Jul 27, 2026 1:00pm |  |  | Fair | No | Premises lock
Outage | J.E.26.07.32843 | C001866158 | Clyde Brown | Clarendon | Completed | Load_248180 | Monymusk - 210 | Jul 27, 2026 11:44am | Jul 27, 2026 11:44am | Jul 27, 2026 12:28pm | Jul 27, 2026 12:28pm | Jul 27, 2026 1:04pm | Jul 27, 2026 1:45pm | Jul 27, 2026 1:57pm | Jul 27, 2026 1:57pm |  |  | Fair | No | Defective meter socket customer advised to change
Non-Outage | J.E.26.07.32737 | C001866151 | Andrae Clarke | Portland | Completed | Load_248592 | Port Antonio - 310 | Jul 27, 2026 11:39am | Jul 27, 2026 12:05pm | Jul 27, 2026 12:14pm | Jul 27, 2026 12:15pm | Jul 27, 2026 12:45pm | Jul 27, 2026 12:35pm | Jul 27, 2026 12:49pm | Jul 27, 2026 12:49pm |  |  | Fair | No | Customer meter defective meter needs to be changed Check voltage 116/119/235Refer to field service
Outage | J.E.26.07.32854 | C001866130 | Roxroy Needham | St.Ann | Completed | Load_252832 | Cardiff Hall - 210 | Jul 27, 2026 11:31am | Jul 27, 2026 11:37am | Jul 27, 2026 1:41pm | Jul 27, 2026 1:41pm | Jul 27, 2026 2:50pm | Jul 27, 2026 2:50pm | Jul 27, 2026 2:52pm | Jul 27, 2026 2:52pm | LowHangingWires |  | Fair | No | Customer has internal issues and was advised to get an electrician
Non-Outage | J.E.26.07.32458 | C001866127 | Richard Nicholas | St.Catherine | Completed | Load_251951 | Tredegar - 510 | Jul 27, 2026 11:29am | Jul 27, 2026 11:29am | Jul 27, 2026 1:16pm | Jul 27, 2026 1:16pm | Jul 27, 2026 2:16pm | Jul 27, 2026 2:55pm | Jul 27, 2026 2:57pm | Jul 27, 2026 2:57pm |  |  | Fair | No | Meter socket found defective with incorrect meter socket cover,fault pointed out to the customer however supply left working temporary.voltage reading 117,116 and 233v.
Outage | J.E.26.07.32832 | C001866105 | Wayne Dillion | St.Elizabeth | Completed | Load_1002127 | Maggotty - 110 | Jul 27, 2026 11:12am | Jul 27, 2026 4:06pm | Jul 27, 2026 6:37pm | Jul 27, 2026 7:41pm | Jul 27, 2026 8:55pm | Jul 27, 2026 9:12pm | Jul 27, 2026 9:21pm | Jul 27, 2026 9:21pm |  |  | Fair | No | Supply check and found working okay reading 111v, 111v cross phased 223volts and 190volts. The school breaker is off. Customer was advised to get an electrician to carry out further checks.
Outage | J.E.26.07.32848 | C001866103 | Edward Royal | KSAS | Completed | Load_239591 | Cane River - 610 | Jul 27, 2026 11:08am | Jul 27, 2026 11:09am | Jul 27, 2026 11:28am | Jul 27, 2026 11:28am | Jul 27, 2026 11:28am | Jul 27, 2026 12:50pm | Jul 27, 2026 12:51pm | Jul 27, 2026 12:51pm | BrokenWire |  | Fair | No | Spliced and reconnected secondary phase using 3 single bolt clamp
Non-Outage | J.E.26.07.21854 | C001866087 | Andre Smith | KSAS | Completed | Load_262444 | Hunts Bay - 310 | Jul 27, 2026 11:05am | Jul 27, 2026 11:07am | Jul 27, 2026 11:41am | Jul 27, 2026 11:41am | Jul 27, 2026 12:15pm | Jul 27, 2026 12:19pm | Jul 27, 2026 12:19pm | Jul 27, 2026 12:19pm |  |  | Fair | No | Defective 100kva transformer found in bank of three maintenance department required
Outage | J.E.26.07.32777 | C001866091 | Romeo Brissett | St.James | Completed | Load_270234 | Queens Drive - 710 | Jul 27, 2026 11:05am | Jul 27, 2026 11:06am | Jul 27, 2026 2:19pm | Jul 27, 2026 2:19pm | Jul 27, 2026 3:19pm | Jul 27, 2026 4:14pm | Jul 27, 2026 4:26pm | Jul 27, 2026 4:26pm | BrokenWire |  | Rains | No | Spliced and retention customer service wire.
Outage | J.E.26.07.32814 | C001866090 | Derrick Dawkins | St.James | Completed | Load_268830 | Bogue - 610 | Jul 27, 2026 11:05am | Jul 27, 2026 11:06am | Jul 27, 2026 11:27am | Jul 27, 2026 11:27am | Jul 27, 2026 1:15pm | Jul 27, 2026 2:01pm | Jul 27, 2026 2:04pm | Jul 27, 2026 2:04pm |  |  | Fair | No | Found customer service wire disconnected due to hurricane Reconnected customer service wire voltage left 118/119=237
Outage | J.E.26.07.32823 | C001866089 | Romeo Brissett | St.James | Completed | Load_294708 | Queens Drive - 710 | Jul 27, 2026 11:05am | Jul 27, 2026 11:06am | Jul 27, 2026 11:43am | Jul 27, 2026 11:43am | Jul 27, 2026 12:50pm | Jul 27, 2026 1:08pm | Jul 27, 2026 1:10pm | Jul 27, 2026 1:10pm |  |  | Fair | No | Found meter disconnected please send to field service.
Outage | J.E.26.07.32818 | C001866029 | Daniel Francis | St.Ann | Completed | Load_256006 | Ocho Rios - 310 | Jul 27, 2026 10:45am | Jul 27, 2026 10:46am | Jul 27, 2026 2:44pm | Jul 27, 2026 2:44pm | Jul 27, 2026 3:08pm | Jul 27, 2026 3:10pm | Jul 27, 2026 3:11pm | Jul 27, 2026 3:11pm |  |  | Fair | No | Found okay customer say she get back light
Outage | J.E.26.07.32815 | C001866018 | Daniel Francis | St.Ann | Completed | Load_263848 | Cardiff Hall - 310 | Jul 27, 2026 10:43am | Jul 27, 2026 12:11pm | Jul 27, 2026 2:13pm | Jul 27, 2026 2:13pm | Jul 27, 2026 2:42pm | Jul 27, 2026 2:43pm | Jul 27, 2026 2:44pm | Jul 27, 2026 2:44pm |  |  | Fair | No | Customer say light come found okay
Non-Outage | J.E.26.07.32817 | C001866017 | Daniel Francis | null | Completed | null | null | Jul 27, 2026 10:42am | Jul 27, 2026 10:46am | Jul 27, 2026 11:44am | Jul 27, 2026 11:44am | Jul 27, 2026 12:22pm | Jul 27, 2026 12:23pm | Jul 27, 2026 12:24pm | Jul 27, 2026 12:24pm |  |  | Fair | No | Found ok customer had problems adding credit but resolved now
Outage | J.E.26.07.32806 | C001866001 | Wayne Dillion | St.Elizabeth | Completed | Load_256104 | Maggotty - 210 | Jul 27, 2026 10:33am | Jul 27, 2026 10:40am | Jul 27, 2026 12:49pm | Jul 27, 2026 12:49pm | Jul 27, 2026 12:49pm | Jul 27, 2026 1:32pm | Jul 27, 2026 1:33pm | Jul 27, 2026 1:33pm | Fire |  | Fair | No | Supply check and found customers having low voltage reading 107v, 109v and cross phase 216volts from transformer. Transformer is on tap 5. Please refer same to the maintenance department for further assistance.
Non-Outage | J.E.26.07.32443 | C001865986 | Richard Nicholas | null | Completed | null | null | Jul 27, 2026 10:28am | Jul 27, 2026 10:29am | Jul 27, 2026 12:46pm | Jul 27, 2026 12:46pm | Jul 27, 2026 1:15pm | Jul 27, 2026 1:15pm | Jul 27, 2026 1:16pm | Jul 27, 2026 1:16pm |  |  | Fair | No | Area found ok
Outage | J.E.26.07.32768 | C001865968 | Kemark Slue | St.Catherine | Completed | Load_249992 | New Michelton - 210 | Jul 27, 2026 10:28am | Jul 27, 2026 10:29am | Jul 27, 2026 11:16am | Jul 27, 2026 11:17am | Jul 27, 2026 12:37pm | Jul 27, 2026 12:00pm | Jul 27, 2026 1:28pm | Jul 27, 2026 1:28pm | TreeContact | Y | Fair | No | Upon arrival at the location the crew discovered that a large Star apple tree and Ackee tree limbs are overhanging and making contact with open secondary please refer to maintenance to have trees cut.
Outage | J.E.26.07.32800 | C001865969 | Richard Nicholas | St.Catherine | Completed | Load_254199 | Tredegar - 210 | Jul 27, 2026 10:28am | Jul 27, 2026 10:29am | Jul 27, 2026 11:55am | Jul 27, 2026 11:55am | Jul 27, 2026 12:22pm | Jul 27, 2026 12:40pm | Jul 27, 2026 12:44pm | Jul 27, 2026 12:44pm |  |  | Fair | No | 10kva transformer with YP enclosure installed.box # 05153, pole #0063862.transformer found defective and recommended to replace.
Outage | J.E.26.07.32752 | C001865956 | Roxroy Needham | St.Ann | Completed | Load_266401 | Cardiff Hall - 210 | Jul 27, 2026 10:20am | Jul 27, 2026 10:27am | Jul 27, 2026 10:43am | Jul 27, 2026 10:43am | Jul 27, 2026 11:31am | Jul 27, 2026 12:06pm | Jul 27, 2026 12:08pm | Jul 27, 2026 12:08pm |  |  | Fair | No | Customer has internal issues and was advised to get an electrician
Outage | J.E.26.07.32758 | C001865942 | Kenroy Dale | Manchester | Completed | Load_263292 | Kendal - 210 | Jul 27, 2026 10:16am | Jul 27, 2026 10:19am | Jul 27, 2026 1:38pm | Jul 27, 2026 1:38pm | Jul 27, 2026 2:23pm | Jul 27, 2026 2:39pm | Jul 27, 2026 2:39pm | Jul 27, 2026 2:39pm |  |  | Fair | No | Customer paying bill on wrong account, landlord was advised to provide customer with correct meter number
Non-Outage | J.E.26.07.30784 | C001865941 | Selvin White | St.Elizabeth | Completed | Load_300464 | Maggotty - 110 | Jul 27, 2026 10:14am | Jul 27, 2026 10:14am | Jul 27, 2026 10:36am | Jul 27, 2026 10:36am | Jul 27, 2026 11:47am | Jul 27, 2026 1:27pm | Jul 27, 2026 1:27pm | Jul 27, 2026 1:27pm |  |  | Fair | No | Replace 2 blown 20 amp junction fuses along with three 3 amp fuses for a bank of three 50 KVA transformers at Niagara district that supply the NWC pump after patrolling 3 phase primary line. Supply restored.
Outage | J.E.26.07.32733 | C001865922 | Oshane Warren | Westmoreland | Completed | Load_241436 | Paradise - 310 | Jul 27, 2026 10:08am | Jul 27, 2026 10:08am | Jul 28, 2026 8:11am | Jul 28, 2026 10:04am | Jul 28, 2026 10:04am | Jul 28, 2026 10:04am | Jul 28, 2026 10:07am | Jul 28, 2026 10:07am |  |  | Fair | No | Restore from yesterday
Outage | J.E.26.07.32645 | C001865911 | Romeo Brissett | St.James | Completed | Load_244260 | Queens Drive - 310 | Jul 27, 2026 9:58am | Jul 27, 2026 10:03am | Jul 27, 2026 1:10pm | Jul 27, 2026 1:11pm | Jul 27, 2026 1:53pm | Jul 27, 2026 2:16pm | Jul 27, 2026 2:19pm | Jul 27, 2026 2:19pm |  |  | Rains | No | Line patrolled and found power in the area,resident stated power was restored last night.
Outage | J.E.26.07.32761 | C001865904 | Neckell Ormsby | St.Mary | Completed | Load_254414 | Highgate - 210 | Jul 27, 2026 9:57am | Jul 27, 2026 9:58am | Jul 27, 2026 11:18am | Jul 27, 2026 11:18am | Jul 27, 2026 11:35am | Jul 27, 2026 12:01pm | Jul 27, 2026 12:01pm | Jul 27, 2026 12:01pm | BrokenPole |  | Fair | No | Found broken intermediate pole caused by motor vehicle accident 30 class 6 please refer to maintenance department only 1- service wire on it
Non-Outage | J.E.26.07.32239 | C001865894 | Rusean Allen | null | Completed | null | null | Jul 27, 2026 9:53am | Jul 27, 2026 9:53am | Jul 27, 2026 12:50pm | Jul 27, 2026 12:50pm | Jul 27, 2026 1:46pm | Jul 27, 2026 1:47pm | Jul 27, 2026 1:47pm | Jul 27, 2026 1:47pm |  |  | Fair | No | Not found
Non-Outage | J.E.26.07.32732 | C001865903 | Romaine Roberts | null | Completed | null | null | Jul 27, 2026 9:53am | Jul 27, 2026 9:54am | Jul 27, 2026 11:25am | Jul 27, 2026 11:25am | Jul 27, 2026 12:54pm | Jul 27, 2026 2:01pm | Jul 27, 2026 2:02pm | Jul 27, 2026 2:02pm | BrokenWire |  | Fair | No | Customer 3 wire service was disconnected from drawing the storm however call and checks was made to the call center wher the meter in confirm active so a reconnection was carry out
Non-Outage | J.E.26.07.32709 | C001865893 | Edward Royal | KSAS | Completed | Load_245025 | Cane River - 410 | Jul 27, 2026 9:52am | Jul 27, 2026 9:52am | Jul 27, 2026 12:51pm | Jul 27, 2026 12:51pm | Jul 27, 2026 12:56pm | Jul 27, 2026 1:07pm | Jul 27, 2026 1:08pm | Jul 27, 2026 1:08pm |  |  | Fair | No | Customer have internal problems customer have faulty wiring advise customer to get a electrician to fix the problem voltage reading 116 v
Non-Outage | J.E.26.07.32265 | C001865892 | Andre Smith | KSAN | Completed | Load_293687 | Washington Blvd - 710 | Jul 27, 2026 9:51am | Jul 27, 2026 9:51am | Jul 27, 2026 10:10am | Jul 27, 2026 10:10am | Jul 27, 2026 10:21am | Jul 27, 2026 10:38am | Jul 27, 2026 10:38am | Jul 27, 2026 10:38am | Fire |  | Fair | No | Burnt Defective ypp box field service department required
Outage | J.E.26.07.32735 | C001865891 | Edward Royal | KSAS | Completed | Load_254594 | Up Park Camp - 510 | Jul 27, 2026 9:50am | Jul 27, 2026 1:10pm | Jul 27, 2026 1:37pm | Jul 27, 2026 1:37pm | Jul 27, 2026 1:44pm | Jul 27, 2026 2:00pm | Jul 27, 2026 2:01pm | Jul 27, 2026 2:01pm |  |  | Fair | No | Customer have internal problems customer have faulty wiring advise customer to get a electrician to fix the problem voltage reading 240 121 121 v
Outage | J.E.26.07.32607 | C001865889 | Michael Christian | St.James | Completed | Load_1002051 | Bogue - 310 | Jul 27, 2026 9:49am | Jul 27, 2026 9:49am | Jul 27, 2026 10:53am | Jul 27, 2026 10:53am | Jul 27, 2026 11:46am | Jul 27, 2026 12:03pm | Jul 27, 2026 12:04pm | Jul 27, 2026 12:04pm |  |  | Fair | No | Found 1 25 kava transformer out replace 1 2 amp in 25 no pole #
Outage | J.E.26.07.32632 | C001865890 | Michael Christian | St.James | Completed | Load_557020 | Bogue - 310 | Jul 27, 2026 9:49am | Jul 27, 2026 9:49am | Jul 27, 2026 10:54am | Jul 27, 2026 12:04pm | Jul 27, 2026 1:05pm | Jul 27, 2026 1:08pm | Jul 27, 2026 1:08pm | Jul 27, 2026 1:08pm | LowHangingWires |  | Fair | No | Check and found okay
Outage | J.E.26.07.32658 | C001865888 | Michael Christian | St.James | Completed | Load_253346 | Bogue - 410 | Jul 27, 2026 9:49am | Jul 27, 2026 9:49am | Jul 27, 2026 9:54am | Jul 27, 2026 9:54am | Jul 27, 2026 10:31am | Jul 27, 2026 10:53am | Jul 27, 2026 10:53am | Jul 27, 2026 10:53am |  |  | Fair | No | Replace 2 clamps at customer service wire at pothead voltage 113 115 229 at meter
Outage | J.E.26.07.29213 | C001865879 | Error Coore | Manchester | Completed | Load_254977 | Kendal - 210 | Jul 27, 2026 9:47am | Jul 27, 2026 9:47am | Jul 27, 2026 11:59am | Jul 27, 2026 11:59am | Jul 27, 2026 1:46pm | Jul 27, 2026 2:03pm | Jul 27, 2026 2:05pm | Jul 27, 2026 2:05pm |  |  | Fair | No | Premise not found unable to locate customer not getting customer on phone
Outage | J.E.26.07.32613 | C001865878 | Roxroy Needham | St.Ann | Completed | Load_250632 | Cardiff Hall - 310 | Jul 27, 2026 9:45am | Jul 27, 2026 9:47am | Jul 27, 2026 10:04am | Jul 27, 2026 10:31am | Jul 27, 2026 10:31am | Jul 27, 2026 10:32am | Jul 27, 2026 10:33am | Jul 27, 2026 10:33am |  |  | Fair | No | Found premises ok
Outage | J.E.26.07.32704 | C001865863 | Kenroy Dale | Manchester | Completed | Load_268909 | Kendal - 210 | Jul 27, 2026 9:35am | Jul 27, 2026 9:37am | Jul 27, 2026 11:47am | Jul 27, 2026 11:52am | Jul 27, 2026 12:58pm | Jul 27, 2026 1:30pm | Jul 27, 2026 1:30pm | Jul 27, 2026 1:30pm |  |  | Fair | No | Supply found okay voltage reading 110 customers have internal issues
Outage | J.E.26.07.32687 | C001865820 | Ricky Hall | St.Catherine | Completed | Load_251081 | Tredegar - 310 | Jul 27, 2026 9:21am | Jul 27, 2026 9:23am | Jul 27, 2026 10:24am | Jul 27, 2026 10:25am | Jul 27, 2026 10:38am | Jul 27, 2026 10:38am | Jul 27, 2026 10:53am | Jul 27, 2026 10:53am |  |  | Fair | No | Customer disconnected for nonpayment of bill c4 advised
Outage | J.E.26.07.32467 | C001865817 | Rusean Allen | KSAS | Completed | Load_241188 | Three Miles - 410 | Jul 27, 2026 9:20am | Jul 27, 2026 9:21am | Jul 27, 2026 12:30pm | Jul 27, 2026 12:30pm | Jul 27, 2026 12:47pm | Jul 27, 2026 12:49pm | Jul 27, 2026 12:49pm | Jul 27, 2026 12:49pm |  |  | Fair | No | Hexing failure, customer unable to top up. Refer to field service department.
Outage | J.E.26.07.32690 | C001865818 | Rusean Allen | KSAS | Completed | Load_238838 | Hunts Bay - 710 | Jul 27, 2026 9:20am | Jul 27, 2026 9:21am | Jul 27, 2026 2:21pm | Jul 27, 2026 2:21pm | Jul 27, 2026 11:47pm | Jul 27, 2026 11:49pm | Jul 27, 2026 11:49pm | Jul 27, 2026 11:49pm |  |  | Fair | No | Prepaid customer have top issues
Non-Outage | J.E.26.07.32663 | C001865816 | Daniel Francis | null | Completed | null | null | Jul 27, 2026 9:19am | Jul 27, 2026 9:39am | Jul 27, 2026 10:40am | Jul 27, 2026 10:40am | Jul 27, 2026 11:36am | Jul 27, 2026 11:41am | Jul 27, 2026 11:41am | Jul 27, 2026 11:41am |  |  | Fair | No | Found. Ok not JPS. Internal circuit breaker switch off
Outage | J.E.26.07.32677 | C001865815 | Andre Smith | KSAS | Completed | Load_254801 | Greenwich - 510 | Jul 27, 2026 9:19am | Jul 27, 2026 9:19am | Jul 27, 2026 10:38am | Jul 27, 2026 10:38am | Jul 27, 2026 11:22am | Jul 27, 2026 11:40am | Jul 27, 2026 11:41am | Jul 27, 2026 11:41am |  |  | Fair | No | Premises found okay internal problems
Non-Outage | J.E.26.07.32631 | C001865796 | Roxroy Needham | null | Completed | null | null | Jul 27, 2026 9:18am | Jul 27, 2026 9:40am | Jul 27, 2026 10:11am | Jul 27, 2026 10:33am | Jul 27, 2026 10:33am | Jul 27, 2026 10:34am | Jul 27, 2026 10:34am | Jul 27, 2026 10:34am | BrokenWire |  | Fair | No | Found premises ok
Outage | J.E.26.07.32615 | C001865814 | Roxroy Needham | St.Ann | Completed | Load_240073 | Cardiff Hall - 210 | Jul 27, 2026 9:18am | Jul 27, 2026 9:20am | Jul 27, 2026 12:13pm | Jul 27, 2026 12:15pm | Jul 27, 2026 1:20pm | Jul 27, 2026 1:39pm | Jul 27, 2026 1:40pm | Jul 27, 2026 1:40pm |  |  | Fair | No | Customer was advised to get an electrician to retention her wire
Outage | J.E.26.07.32618 | C001865798 | Edward Royal | KSAS | Completed | Load_257412 | Rockfort - 410 | Jul 27, 2026 9:18am | Jul 27, 2026 9:19am | Jul 27, 2026 9:29am | Jul 27, 2026 9:29am | Jul 27, 2026 10:05am | Jul 27, 2026 11:07am | Jul 27, 2026 11:08am | Jul 27, 2026 11:08am |  |  | Fair | No | Replaced 100ft service cable with 6 single bolt clamp
Outage | J.E.26.07.32651 | C001865813 | Daniel Francis | St.Ann | Completed | Load_269868 | Roaring River - 210 | Jul 27, 2026 9:18am | Jul 27, 2026 9:21am | Jul 27, 2026 9:43am | Jul 27, 2026 9:43am | Jul 27, 2026 9:44am | Jul 27, 2026 9:45am | Jul 27, 2026 9:45am | Jul 27, 2026 9:45am |  |  | Fair | No | Not found customer not answering look like the not working
Outage | J.E.26.07.32664 | C001865797 | Roxroy Needham | St.Ann | Completed | Load_304967 | Cardiff Hall - 310 | Jul 27, 2026 9:18am | Jul 27, 2026 9:20am | Jul 27, 2026 10:02am | Jul 27, 2026 10:02am | Jul 27, 2026 10:11am | Jul 27, 2026 10:21am | Jul 27, 2026 10:29am | Jul 27, 2026 10:29am |  |  | Fair | No | Replace 1- 7amp transformer fuse for a 100 KVA
Non-Outage | J.E.26.07.14653 | C001865794 | Daniel Francis | St.Ann | Completed | Load_242953 | Roaring River - 410 | Jul 27, 2026 9:16am | Jul 27, 2026 9:17am | Jul 27, 2026 9:41am | Jul 27, 2026 9:41am | Jul 27, 2026 9:42am | Jul 27, 2026 9:42am | Jul 27, 2026 9:43am | Jul 27, 2026 9:43am |  |  | Fair | No | Not found
Outage | J.E.26.07.32586 | C001865789 | Ricky Hall | St.Catherine | Completed | Load_250219 | Tredegar - 310 | Jul 27, 2026 9:14am | Jul 27, 2026 9:15am | Jul 27, 2026 9:29am | Jul 27, 2026 9:29am | Jul 27, 2026 10:00am | Jul 27, 2026 10:10am | Jul 27, 2026 10:10am | Jul 27, 2026 10:10am | BrokenPole |  | Fair | No | Not located insufficient information
Outage | J.E.26.07.32636 | C001865790 | Ricky Hall | St.Catherine | Completed | Load_254399 | Tredegar - 310 | Jul 27, 2026 9:14am | Jul 27, 2026 9:15am | Jul 27, 2026 10:11am | Jul 27, 2026 10:20am | Jul 27, 2026 10:23am | Jul 27, 2026 10:23am | Jul 27, 2026 10:24am | Jul 27, 2026 10:24am |  |  | Fair | No | Defective service line customer advised
Outage | J.E.26.07.32678 | C001865791 | Ricky Hall | Portmore | Completed | Load_242899 | Naggo Head - 510 | Jul 27, 2026 9:14am | Jul 27, 2026 10:26am | Jul 27, 2026 1:05pm | Jul 27, 2026 1:06pm | Jul 27, 2026 2:00pm | Jul 27, 2026 3:31pm | Jul 27, 2026 3:32pm | Jul 27, 2026 3:32pm |  |  | Fair | No | Repair burnt 4w service at pole in bank of 3*25 kva use 1 clamp (240*3)(418/419/420)
Outage | J.E.26.07.32672 | C001865772 | Javid Vernon | Westmoreland | Completed | Load_250735 | Paradise - 210 | Jul 27, 2026 9:07am | Jul 27, 2026 3:25pm | Jul 27, 2026 5:53pm | Jul 27, 2026 5:53pm | Jul 27, 2026 5:53pm | Jul 27, 2026 5:54pm | Jul 27, 2026 5:54pm | Jul 27, 2026 5:54pm |  |  | Fair | No | Customer stated that the power was restored
Non-Outage | J.E.26.07.32623 | C001865771 | Oshane Warren | Westmoreland | Completed | Load_556532 | Paradise - 310 | Jul 27, 2026 9:04am | Jul 27, 2026 12:05pm | Jul 27, 2026 12:59pm | Jul 27, 2026 12:59pm | Jul 27, 2026 1:21pm | Jul 27, 2026 1:25pm | Jul 27, 2026 1:25pm | Jul 27, 2026 1:25pm |  |  | Fair | No | Replace 40amp junction fuse
Non-Outage | J.E.26.07.32594 | C001865722 | Roemello Brown | Trelawny | Completed | Load_259972 | Greenwood - 210 | Jul 27, 2026 8:33am | Jul 28, 2026 9:24am | Jul 28, 2026 11:53am | Jul 28, 2026 12:03pm | Jul 28, 2026 12:39pm | Jul 28, 2026 12:39pm | Jul 28, 2026 12:58pm | Jul 28, 2026 12:58pm |  |  | Fair | No | Premises check premises found working okVoltage found 115/114/229Voltage leave 115/114/229
Non-Outage | J.E.26.07.32168 | C001865721 | Roemello Brown | Trelawny | Completed | Load_264891 | Duncans - 110 | Jul 27, 2026 8:32am | Jul 27, 2026 8:32am | Jul 27, 2026 12:59pm | Jul 27, 2026 1:18pm | Jul 27, 2026 1:37pm | Jul 27, 2026 1:37pm | Jul 27, 2026 1:46pm | Jul 27, 2026 1:46pm |  |  | Fair | No | Premises check premises found working okay Voltage found 116/117/233Voltage leave 116/117/233
Non-Outage | J.E.26.07.26645 | C001865720 | Rusean Allen | KSAS | Completed | Load_245415 | Hunts Bay - 210 | Jul 27, 2026 8:31am | Jul 27, 2026 8:34am | Jul 27, 2026 9:33am | Jul 27, 2026 10:01am | Jul 27, 2026 11:17am | Jul 27, 2026 12:25pm | Jul 27, 2026 12:25pm | Jul 27, 2026 12:25pm |  |  | Fair | No | Defective fuse barrel found, fuse barrel was changed.1x 15amp fuse found 1x 15amp fuse replaced.
Outage | J.E.26.07.32610 | C001865717 | Milton Charlton | KSAN | Completed | Load_578921 | Hope - 510 | Jul 27, 2026 8:27am | Jul 27, 2026 8:27am | Jul 27, 2026 1:52pm | Jul 27, 2026 1:53pm | Jul 27, 2026 2:03pm | Jul 27, 2026 3:10pm | Jul 27, 2026 2:10pm | Jul 27, 2026 2:10pm | BrokenPole |  | Fair | No | 40ft wooden pole at 18B August Town Road rotten at the foot and held up by 3 phase conductors and telephone cables. Pole has on 3 phase primary, street light and a quantity of service wires coming from Hexing box. Need immediate attention.
Non-Outage | J.E.26.07.05723 | C001865716 | Error Coore | Manchester | Completed | Load_261060 | Spur Tree - 310 | Jul 27, 2026 8:25am | Jul 27, 2026 8:27am | Jul 28, 2026 11:24am | Jul 28, 2026 11:24am | Jul 28, 2026 12:00pm | Jul 28, 2026 12:07pm | Jul 28, 2026 12:08pm | Jul 28, 2026 12:08pm |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.15030 | C001865713 | Error Coore | Manchester | Completed | Load_302243 | Spur Tree - 310 | Jul 27, 2026 8:25am | Jul 27, 2026 8:25am | Jul 28, 2026 9:54am | Jul 28, 2026 9:54am | Jul 28, 2026 10:35am | Jul 28, 2026 11:22am | Jul 28, 2026 11:23am | Jul 28, 2026 11:23am |  |  | Fair | No | Found customer with wrap connection at pothead remade wrap connection using 2 service sleeve voltage reading 118/117/235 volts
Non-Outage | J.E.26.07.15326 | C001865714 | Error Coore | Manchester | Completed | Load_238520 | Spur Tree - 310 | Jul 27, 2026 8:25am | Jul 27, 2026 8:25am | Jul 27, 2026 2:05pm | Jul 27, 2026 2:06pm | Jul 27, 2026 3:32pm | Jul 27, 2026 3:45pm | Jul 27, 2026 3:47pm | Jul 27, 2026 3:47pm |  |  | Fair | No | Premise found ok voltage reading 115/117/232 volts
Non-Outage | J.E.26.07.16928 | C001865712 | Error Coore | Manchester | Completed | Load_265696 | Spur Tree - 310 | Jul 27, 2026 8:25am | Jul 27, 2026 8:25am | Jul 28, 2026 12:09pm | Jul 28, 2026 12:09pm | Jul 28, 2026 12:31pm | Jul 28, 2026 12:53pm | Jul 28, 2026 12:54pm | Jul 28, 2026 12:54pm |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.23972 | C001865708 | Ryan Richards | Manchester | Completed | Load_267897 | Spur Tree - 310 | Jul 27, 2026 8:24am | Jul 27, 2026 3:27pm | Jul 27, 2026 5:51pm | Jul 27, 2026 5:52pm | Jul 27, 2026 6:49pm | Jul 27, 2026 7:13pm | Jul 27, 2026 7:14pm | Jul 27, 2026 7:14pm |  |  | Fair | No | Rotten service found at premises replaced 80ft#6 triplex 3 penunion 3 one bolt clamps voltage 113/115/229 volts
Non-Outage | J.E.26.07.24195 | C001865711 | Error Coore | Manchester | Completed | Load_268919 | Spur Tree - 310 | Jul 27, 2026 8:24am | Jul 27, 2026 8:25am | Jul 27, 2026 9:03am | Jul 27, 2026 9:03am | Jul 27, 2026 9:52am | Jul 27, 2026 10:56am | Jul 27, 2026 10:58am | Jul 27, 2026 10:58am |  |  | Fair | No | Found customer with corroded phase and neutral at pothead remade corroded phase and neutral using 3 service sleeve voltage reading 117/117/234 volts
Non-Outage | J.E.26.07.29531 | C001865707 | Error Coore | Manchester | Completed | Load_237916 | Spur Tree - 310 | Jul 27, 2026 8:23am | Jul 28, 2026 8:28am | Jul 28, 2026 12:55pm | Jul 28, 2026 12:55pm | Jul 28, 2026 1:27pm | Jul 28, 2026 1:31pm | Jul 28, 2026 1:31pm | Jul 28, 2026 1:31pm |  |  | Fair | No | Premise not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.30290 | C001865705 | Barnett Brown | Manchester | Completed | Load_256433 | Spur Tree - 310 | Jul 27, 2026 8:23am | Jul 27, 2026 8:24am | Jul 27, 2026 12:34pm | Jul 27, 2026 12:34pm | Jul 27, 2026 1:00pm | Jul 27, 2026 1:19pm | Jul 27, 2026 1:20pm | Jul 27, 2026 1:20pm |  |  | Fair | No | Customer did not make any report
Non-Outage | J.E.26.07.31137 | C001865706 | Barnett Brown | Manchester | Completed | Load_254646 | Spur Tree - 310 | Jul 27, 2026 8:23am | Jul 27, 2026 8:24am | Jul 27, 2026 10:03am | Jul 27, 2026 10:04am | Jul 27, 2026 12:08pm | Jul 27, 2026 12:12pm | Jul 27, 2026 12:21pm | Jul 27, 2026 12:21pm |  |  | Fair | No | Customer has internal problem, voltage 113 114 227
Non-Outage | J.E.26.07.23332 | C001865694 | Dwain Samuels | Westmoreland | Completed | Load_242128 | Paradise - 210 | Jul 27, 2026 8:21am | Jul 27, 2026 8:22am | Jul 27, 2026 8:46am | Jul 27, 2026 9:56am | Jul 27, 2026 9:56am | Jul 27, 2026 10:02am | Jul 27, 2026 10:02am | Jul 27, 2026 10:02am |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.07.23951 | C001865697 | Dwain Samuels | Westmoreland | Completed | Load_255314 | Paradise - 210 | Jul 27, 2026 8:21am | Jul 27, 2026 8:22am | Jul 27, 2026 8:46am | Jul 27, 2026 10:17am | Jul 27, 2026 10:17am | Jul 27, 2026 10:23am | Jul 27, 2026 10:26am | Jul 27, 2026 10:26am |  |  | Fair | No | Customer say the complaint was the electricity coming on and off during the day time … and is okay now
Non-Outage | J.E.26.07.24287 | C001865695 | Dwain Samuels | Westmoreland | Completed | Load_260662 | Paradise - 210 | Jul 27, 2026 8:21am | Jul 27, 2026 8:22am | Jul 27, 2026 8:46am | Jul 27, 2026 10:42am | Jul 27, 2026 10:42am | Jul 27, 2026 10:48am | Jul 27, 2026 10:48am | Jul 27, 2026 10:48am |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.07.26616 | C001865696 | Dwain Samuels | Westmoreland | Completed | Load_243368 | Paradise - 210 | Jul 27, 2026 8:21am | Jul 27, 2026 8:22am | Jul 27, 2026 8:46am | Jul 27, 2026 10:33am | Jul 27, 2026 10:33am | Jul 27, 2026 10:33am | Jul 27, 2026 10:34am | Jul 27, 2026 10:34am |  |  | Fair | No | Need a proper directions and contact information called but no answer
Non-Outage | J.E.26.07.26915 | C001865698 | Dwain Samuels | Westmoreland | Completed | Load_295374 | Paradise - 210 | Jul 27, 2026 8:21am | Jul 27, 2026 8:22am | Jul 27, 2026 8:46am | Jul 27, 2026 9:36am | Jul 27, 2026 9:45am | Jul 27, 2026 9:53am | Jul 27, 2026 9:54am | Jul 27, 2026 9:54am |  |  | Fair | No | Customer has internal problems. Voltage check 113-113-226
Non-Outage | J.E.26.07.30400 | C001865699 | Dwain Samuels | Westmoreland | Completed | Load_250735 | Paradise - 210 | Jul 27, 2026 8:21am | Jul 27, 2026 8:22am | Jul 27, 2026 8:46am | Jul 27, 2026 10:57am | Jul 27, 2026 11:00am | Jul 27, 2026 11:35am | Jul 27, 2026 11:36am | Jul 27, 2026 11:36am |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.07.31840 | C001865693 | Odeanie Davis | KSAS | Completed | Load_1002850 | Greenwich - 710 | Jul 27, 2026 8:20am | Jul 27, 2026 8:20am | Jul 27, 2026 11:58am | Jul 27, 2026 11:58am | Jul 27, 2026 11:58am | Jul 27, 2026 12:16pm | Jul 27, 2026 12:06pm | Jul 27, 2026 12:06pm |  |  | Fair | No | 115v/0V at arrival, open circuit at secondary and on twisted wire corrected, 2 one bolt clamps and 1 penn union, 121v/120v & 241v after correction.
Non-Outage | J.E.26.07.30687 | C001865689 | Edward Royal | KSAS | Completed | Load_257412 | Rockfort - 410 | Jul 27, 2026 8:19am | Jul 27, 2026 9:30am | Jul 27, 2026 10:05am | Jul 27, 2026 11:08am | Jul 27, 2026 11:09am | Jul 27, 2026 11:10am | Jul 27, 2026 11:10am | Jul 27, 2026 11:10am |  |  | Fair | No | Call related
Non-Outage | J.E.26.07.31056 | C001865688 | Odeanie Davis | KSAS | Completed | Load_258629 | Hunts Bay - 310 | Jul 27, 2026 8:19am | Jul 27, 2026 8:20am | Jul 27, 2026 12:07pm | Jul 27, 2026 12:25pm | Jul 27, 2026 12:25pm | Jul 27, 2026 12:59pm | Jul 27, 2026 1:04pm | Jul 27, 2026 1:04pm |  |  | Fair | No | 102v at arrival, open circuit at secondary corrected. 3 one bolt clamps, 111v after correction.
Non-Outage | J.E.26.07.31300 | C001865691 | Odeanie Davis | KSAS | Completed | Load_256836 | Up Park Camp - 510 | Jul 27, 2026 8:19am | Jul 27, 2026 8:20am | Jul 27, 2026 10:25am | Jul 27, 2026 10:25am | Jul 27, 2026 10:30am | Jul 27, 2026 10:44am | Jul 27, 2026 10:44am | Jul 27, 2026 10:44am |  |  | Fair | No | Unable to contact customer via phone number, lock gate.
Non-Outage | J.E.26.07.31379 | C001865692 | Odeanie Davis | KSAS | Completed | Load_1002850 | Greenwich - 710 | Jul 27, 2026 8:19am | Jul 27, 2026 8:20am | Jul 27, 2026 10:47am | Jul 27, 2026 10:47am | Jul 27, 2026 11:51am | Jul 27, 2026 12:07pm | Jul 27, 2026 11:58am | Jul 27, 2026 11:58am |  |  | Fair | No | 115v/0V at arrival, open circuit at secondary and on twisted wire corrected, 2 one bolt clamps and 1 penn union, 121v/120v & 241v after correction.
Non-Outage | J.E.26.07.32133 | C001865690 | Odeanie Davis | KSAS | Completed | Load_243254 | Cane River - 610 | Jul 27, 2026 8:19am | Jul 27, 2026 8:20am | Jul 27, 2026 9:10am | Jul 27, 2026 9:10am | Jul 27, 2026 9:39am | Jul 27, 2026 9:58am | Jul 27, 2026 9:58am | Jul 27, 2026 9:58am |  |  | Fair | No | 113v/114v & 227v at location, loose connection from transformer, transformer seen leaking, transformer needs to be checked and/or replaced.
Outage | J.E.26.07.32588 | C001865686 | Jowayne Newmans | Portland | Completed | Load_245474 | Port Antonio - 410 | Jul 27, 2026 8:19am | Jul 27, 2026 8:19am | Jul 27, 2026 8:44am | Jul 27, 2026 8:45am | Jul 27, 2026 10:35am | Jul 27, 2026 11:33am | Jul 27, 2026 11:33am | Jul 27, 2026 11:33am |  |  | Fair | No | Patrol and 10amp junction fuse blown pole# 046539 cause by tree touching primary conductor, repair by removing tree off primary conductor and replace 10 amp fuse. Customers now have electricity.
Non-Outage | J.E.26.07.32015 | C001865676 | Roemello Brown | Trelawny | Completed | Load_555930 | Martha Brae - 210 | Jul 27, 2026 8:16am | Jul 27, 2026 8:18am | Jul 27, 2026 10:17am | Jul 27, 2026 1:46pm | Jul 27, 2026 2:04pm | Jul 27, 2026 2:04pm | Jul 27, 2026 3:13pm | Jul 27, 2026 3:13pm |  |  | Fair | No | Service wire defective have it replaced Voltage found 103/36/139Voltage leave 105/107/212
Non-Outage | J.E.26.07.32017 | C001865677 | Andre Williams | Trelawny | Completed | Load_572265 | Martha Brae - 210 | Jul 27, 2026 8:16am | Jul 27, 2026 11:20am | Jul 27, 2026 11:32am | Jul 27, 2026 11:32am | Jul 27, 2026 12:40pm | Jul 27, 2026 12:51pm | Jul 27, 2026 12:51pm | Jul 27, 2026 12:51pm |  |  | Fair | Yes | Open two 100 kva transformer switch phase back to original position, rotation issue now resolve
Non-Outage | J.E.26.07.32560 | C001865678 | Andre Williams | Trelawny | Completed | Load_256637 | Duncans - 110 | Jul 27, 2026 8:16am | Jul 27, 2026 11:20am | Jul 27, 2026 12:53pm | Jul 27, 2026 1:12pm | Jul 27, 2026 1:12pm | Jul 27, 2026 1:14pm | Jul 27, 2026 1:16pm | Jul 27, 2026 1:16pm |  |  | Fair | No | Switch phase at customer pothead to fix rotation is on two 120 phase
Non-Outage | J.E.26.07.31985 | C001865675 | Roemello Brown | Trelawny | Completed | Load_294543 | Duncans - 110 | Jul 27, 2026 8:15am | Jul 27, 2026 8:18am | Jul 27, 2026 3:15pm | Jul 27, 2026 3:15pm | Jul 27, 2026 3:46pm | Jul 27, 2026 3:46pm | Jul 27, 2026 3:57pm | Jul 27, 2026 3:57pm |  |  | Fair | No | Customer meter socket shorts out an burn up the wires in the meter socket no one was not home to inform them about it I tried calling the number provided went straight to voicemails the rain came down same time so I didn’t see anyone to leave an message for the person Voltage found 116/115/231Voltage leave 116/115/231
Non-Outage | J.E.26.07.32174 | C001865674 | Roemello Brown | Trelawny | Completed | Load_1001488 | Duncans - 210 | Jul 27, 2026 8:15am | Jul 27, 2026 8:18am | Jul 27, 2026 10:10am | Jul 27, 2026 11:47am | Jul 27, 2026 12:27pm | Jul 27, 2026 12:27pm | Jul 27, 2026 12:57pm | Jul 27, 2026 12:57pm |  |  | Fair | No | Corrosion at pothead have clamps changeVoltage found 118/113/204/231Voltage leave 118/119/204/237
Non-Outage | J.E.26.07.25950 | C001865670 | Andrae Dawkins | St.James | Completed | Load_249993 | Queens Drive - 710 | Jul 27, 2026 8:11am | Jul 27, 2026 8:26am | Jul 27, 2026 10:29am | Jul 27, 2026 10:29am | Jul 27, 2026 10:29am | Jul 27, 2026 9:56am | Jul 27, 2026 10:33am | Jul 27, 2026 10:33am |  |  | Fair | No | Cannot locate customer due to no proper directions also unable to reach customer phone
Non-Outage | J.E.26.07.31233 | C001865669 | Andrae Dawkins | St.James | Completed | Load_265743 | Queens Drive - 710 | Jul 27, 2026 8:09am | Jul 27, 2026 8:10am | Jul 27, 2026 9:44am | Jul 27, 2026 9:44am | Jul 27, 2026 9:48am | Jul 27, 2026 9:42am | Jul 27, 2026 9:50am | Jul 27, 2026 9:50am |  |  | Fair | No | Check and found ok customer said the problem was already resolved
Non-Outage | J.E.26.07.31336 | C001865668 | Andrae Dawkins | St.James | Completed | Load_269852 | Queens Drive - 710 | Jul 27, 2026 8:09am | Jul 27, 2026 8:10am | Jul 27, 2026 2:32pm | Jul 27, 2026 2:32pm | Jul 27, 2026 2:33pm | Jul 27, 2026 2:57pm | Jul 27, 2026 2:57pm | Jul 27, 2026 2:57pm |  |  | Fair | No | Found customer single phasing due to one leg of customer service wire burnt due to slack connection cleaned and remade joints used one pg clamp voltage left 110/117/227
Non-Outage | J.E.26.07.32420 | C001865667 | Andrae Dawkins | St.James | Completed | Load_247453 | Queens Drive - 710 | Jul 27, 2026 8:09am | Jul 27, 2026 8:10am | Jul 28, 2026 10:55am | Jul 28, 2026 10:55am | Jul 28, 2026 10:55am | Jul 28, 2026 11:50am | Jul 28, 2026 11:53am | Jul 28, 2026 11:53am |  |  | Fair | No | Found multiple customer experiencing low voltage voltage found on secondary line 100/104/205 refer back to emergency crew
Non-Outage | J.E.26.07.32494 | C001865664 | Andrae Dawkins | St.James | Completed | Load_237816 | Queens Drive - 310 | Jul 27, 2026 8:09am | Jul 27, 2026 8:10am | Jul 27, 2026 3:12pm | Jul 27, 2026 3:12pm | Jul 27, 2026 3:50pm | Jul 27, 2026 3:51pm | Jul 27, 2026 3:53pm | Jul 27, 2026 3:53pm |  |  | Fair | No | Found customer experiencing low voltage due to contamination at pothead clean and remade joints voltage eft 118/118/237
Non-Outage | J.E.26.07.32519 | C001865665 | Romeo Brissett | St.James | Completed | Load_250164 | Queens Drive - 310 | Jul 27, 2026 8:09am | Jul 27, 2026 8:19am | Jul 27, 2026 8:37am | Jul 27, 2026 8:37am | Jul 27, 2026 9:20am | Jul 27, 2026 9:25am | Jul 27, 2026 9:28am | Jul 27, 2026 9:28am |  |  | Fair | No | Replaced (1)50amps junction fuse.
Non-Outage | J.E.26.07.32567 | C001865666 | Andrae Dawkins | St.James | Completed | Load_257587 | Queens Drive - 710 | Jul 27, 2026 8:09am | Jul 27, 2026 8:10am | Jul 27, 2026 8:47am | Jul 27, 2026 11:21am | Jul 27, 2026 11:30am | Jul 27, 2026 11:49am | Jul 27, 2026 12:27pm | Jul 27, 2026 12:27pm |  |  | Fair | No | Found customer experiencing high voltage due to customer neutral wire corroded cleaned and remade joint used one pg clamp left 116/117/233
Outage | J.E.26.07.32456 | C001865662 | Oshane Warren | Westmoreland | Completed | Load_241436 | Paradise - 310 | Jul 27, 2026 8:09am | Jul 27, 2026 10:02am | Jul 27, 2026 10:36am | Jul 27, 2026 10:36am | Jul 27, 2026 12:25pm | Jul 27, 2026 12:28pm | Jul 27, 2026 12:55pm | Jul 27, 2026 12:55pm |  |  | Fair | No | 25kva xformer defective needs to be changed 64 customer is connected suspected 25 kva transformer is under size advised to replace a 50 kva transformer and more customer is carrying out repairs to get reconnected advise in the future to split the circuit and added a 25 kva transformer refer to maintenance
Outage | J.E.26.07.32524 | C001865663 | Javid Vernon | Westmoreland | Completed | Load_241092 | Paradise - 110 | Jul 27, 2026 8:09am | Jul 27, 2026 3:25pm | Jul 27, 2026 3:32pm | Jul 27, 2026 4:43pm | Jul 27, 2026 4:43pm | Jul 27, 2026 4:44pm | Jul 27, 2026 4:45pm | Jul 27, 2026 4:45pm | BrokenPole |  | Fair | No | Customers stated that the issue has been resolved and power was restored
Non-Outage | J.E.26.07.08522 | C001865657 | Neckell Ormsby | St.Mary | Completed | Load_247804 | Blackstonedge - 110 | Jul 27, 2026 8:07am | Jul 27, 2026 8:17am | Jul 27, 2026 8:27am | Jul 27, 2026 8:27am | Jul 27, 2026 9:25am | Jul 27, 2026 9:32am | Jul 27, 2026 9:33am | Jul 27, 2026 9:33am | Fire |  | Fair | No | No fire found customer says the issue was resolved about 2- weeks now
Non-Outage | J.E.26.07.09326 | C001865655 | Locksley Allen | St.Mary | Completed | Load_245218 | Oracabessa - 110 | Jul 27, 2026 8:07am | Jul 27, 2026 8:09am | Jul 27, 2026 3:27pm | Jul 27, 2026 3:51pm | Jul 27, 2026 3:51pm | Jul 27, 2026 3:54pm | Jul 27, 2026 3:58pm | Jul 27, 2026 3:58pm |  |  | Fair | No | No low voltage problem found at premises. Voltage at meter socket phase to phase 242v. Phase to neutral 121&120vCustomer said her appliances were damage on the 9/7/26. Several other customers are complaining about damage appliances during that time.Secondary line is sla
Non-Outage | J.E.26.07.09912 | C001865656 | Neckell Ormsby | St.Mary | Completed | Load_245479 | Blackstonedge - 110 | Jul 27, 2026 8:07am | Jul 27, 2026 8:17am | Jul 27, 2026 9:33am | Jul 27, 2026 9:33am | Jul 27, 2026 10:12am | Jul 27, 2026 10:14am | Jul 27, 2026 10:14am | Jul 27, 2026 10:14am | BrokenPole |  | Fair | No | No broken pole seen in area also unable to locate customer after several calls
Non-Outage | J.E.26.07.10450 | C001865654 | Locksley Allen | St.Mary | Completed | Load_260379 | Oracabessa - 110 | Jul 27, 2026 8:06am | Jul 27, 2026 8:10am | Jul 27, 2026 2:23pm | Jul 27, 2026 2:47pm | Jul 27, 2026 2:47pm | Jul 27, 2026 2:58pm | Jul 27, 2026 2:57pm | Jul 27, 2026 2:57pm |  |  | Fair | No | Customer said JPS corrected the problem from last week. Meter socket lock up
Non-Outage | J.E.26.07.10794 | C001865653 | Locksley Allen | St.Mary | Completed | Load_256780 | Blackstonedge - 110 | Jul 27, 2026 8:06am | Jul 27, 2026 8:09am | Jul 27, 2026 9:22am | Jul 27, 2026 10:15am | Jul 27, 2026 10:15am | Jul 27, 2026 10:51am | Jul 27, 2026 10:54am | Jul 27, 2026 10:54am |  |  | Fair | No | Meter found blank and low voltage problem found at premises. Pothead and pole found corroded. Clean up pothead and pole Voltage at meter socket phase to phase 231v. Phase to neutral 113&119vMeter left working
Non-Outage | J.E.26.07.11206 | C001865652 | Locksley Allen | St.Mary | Completed | Load_261425 | Oracabessa - 210 | Jul 27, 2026 8:06am | Jul 27, 2026 8:09am | Jul 27, 2026 12:23pm | Jul 27, 2026 2:13pm | Jul 27, 2026 2:13pm | Jul 27, 2026 2:22pm | Jul 27, 2026 2:22pm | Jul 27, 2026 2:22pm |  |  | Fair | No | Pothead found corroded . Clean up pothead Voltage at meter socket phase to phase 230v. Phase to neutral 120&114vMeter left working
Non-Outage | J.E.26.07.11965 | C001865651 | Neckell Ormsby | St.Mary | Completed | Load_262034 | Blackstonedge - 110 | Jul 27, 2026 8:05am | Jul 27, 2026 8:17am | Jul 27, 2026 10:15am | Jul 27, 2026 10:15am | Jul 27, 2026 10:21am | Jul 27, 2026 10:27am | Jul 27, 2026 10:28am | Jul 27, 2026 10:28am | BrokenWire |  | Fair | No | No directions also unable to locate customer after several calls
Non-Outage | J.E.26.07.12475 | C001865646 | Locksley Allen | St.Mary | Completed | Load_248681 | Blackstonedge - 110 | Jul 27, 2026 8:04am | Jul 27, 2026 8:09am | Jul 28, 2026 9:50am | Jul 28, 2026 9:50am | Jul 28, 2026 9:50am | Jul 28, 2026 9:50am | Jul 28, 2026 9:53am | Jul 28, 2026 9:53am |  |  | Fair | No | Customer has supply,but her meter is blank. She was advised by the technician that JPS will change the meter soon
Non-Outage | J.E.26.07.14133 | C001865642 | Locksley Allen | St.Mary | Completed | Load_260379 | Oracabessa - 110 | Jul 27, 2026 8:04am | Jul 27, 2026 8:09am | Jul 27, 2026 2:58pm | Jul 27, 2026 2:58pm | Jul 27, 2026 2:58pm | Jul 27, 2026 3:01pm | Jul 27, 2026 3:00pm | Jul 27, 2026 3:00pm |  |  | Fair | No | Duplicated . JPS corrected the problem
Non-Outage | J.E.26.07.19071 | C001865638 | Locksley Allen | St.Mary | Completed | Load_269770 | Blackstonedge - 110 | Jul 27, 2026 8:04am | Jul 27, 2026 8:11am | Jul 27, 2026 11:47am | Jul 27, 2026 11:47am | Jul 27, 2026 11:47am | Jul 27, 2026 11:47am | Jul 27, 2026 11:51am | Jul 27, 2026 11:51am |  |  | Fair | No | Meter burn up,same premisesdup
Non-Outage | J.E.26.07.31356 | C001865647 | Fredrick Hamilton | KSAN | Completed | Load_263165 | Constant Spring - 210 | Jul 27, 2026 8:04am | Jul 27, 2026 8:05am | Jul 27, 2026 8:07am | Jul 27, 2026 10:26am | Jul 27, 2026 10:27am | Jul 27, 2026 10:30am | Jul 27, 2026 10:30am | Jul 27, 2026 10:30am |  |  | Fair | No | Multiple calls to customer went straight to voicemail Proper directions required
Non-Outage | J.E.26.07.31490 | C001865649 | Fredrick Hamilton | KSAN | Completed | Load_250523 | Constant Spring - 210 | Jul 27, 2026 8:04am | Jul 27, 2026 8:05am | Jul 27, 2026 8:08am | Jul 27, 2026 11:48am | Jul 27, 2026 11:50am | Jul 27, 2026 12:01pm | Jul 27, 2026 12:01pm | Jul 27, 2026 12:01pm |  |  | Fair | No | Defective meter socket at location burnt wires and burnt lug Customer advised
Non-Outage | J.E.26.07.31615 | C001865648 | Fredrick Hamilton | KSAN | Completed | Load_257446 | Constant Spring - 210 | Jul 27, 2026 8:04am | Jul 27, 2026 8:05am | Jul 27, 2026 8:07am | Jul 27, 2026 11:19am | Jul 27, 2026 11:28am | Jul 27, 2026 11:43am | Jul 27, 2026 11:43am | Jul 27, 2026 11:43am |  |  | Fair | No | 236.4v/117.7v/118.4v obtained Corrosion detected in meter socket on customer neutral Same was corrected
Non-Outage | J.E.26.07.32241 | C001865645 | Milton Charlton | KSAN | Completed | Load_245238 | West Kings House - 410 | Jul 27, 2026 8:04am | Jul 27, 2026 8:05am | Jul 27, 2026 9:11am | Jul 27, 2026 2:10pm | Jul 27, 2026 2:55pm | Jul 27, 2026 9:20pm | Jul 27, 2026 3:00pm | Jul 27, 2026 3:00pm | BrokenWire |  | Fair | No | Customer service wire #6 triplex phase burn off at pole . Reconnect triplex phase using one1- bolt clamp
Non-Outage | J.E.26.07.32393 | C001865643 | Fredrick Hamilton | KSAN | Completed | Load_240328 | Washington Blvd - 510 | Jul 27, 2026 8:04am | Jul 27, 2026 8:05am | Jul 27, 2026 8:07am | Jul 27, 2026 10:41am | Jul 27, 2026 11:09am | Jul 27, 2026 11:14am | Jul 27, 2026 11:15am | Jul 27, 2026 11:15am |  |  | Fair | No | Premises found locked at time of visit Customer not available at time of visit
Non-Outage | J.E.26.07.32535 | C001865640 | Edward Royal | KSAS | Completed | Load_267072 | Duhaney - 310 | Jul 27, 2026 8:04am | Jul 28, 2026 7:48am | Jul 28, 2026 9:55am | Jul 28, 2026 9:55am | Jul 28, 2026 10:10am | Jul 28, 2026 11:12am | Jul 28, 2026 11:12am | Jul 28, 2026 11:12am |  |  | Fair | No | Spliced and reconnected secondary neutral using 10ft number 2 conductor and 2 single bolt clamp voltage reading 224 112 112 v
Non-Outage | J.E.26.07.19247 | C001865637 | Locksley Allen | St.Mary | Completed | Load_243446 | Oracabessa - 110 | Jul 27, 2026 8:03am | Jul 27, 2026 8:11am | Jul 27, 2026 3:01pm | Jul 27, 2026 3:22pm | Jul 27, 2026 3:22pm | Jul 27, 2026 3:24pm | Jul 27, 2026 3:27pm | Jul 27, 2026 3:27pm |  |  | Fair | No | No low voltage problem found at premises Voltage at meter socket phase to phase 235v. Phase to neutral 114&121vThe voltage is slightly high and several customers in this street is having the same problem. Check transformer
Non-Outage | J.E.26.07.20252 | C001865636 | Locksley Allen | St.Mary | Completed | Load_261325 | Blackstonedge - 110 | Jul 27, 2026 8:03am | Jul 27, 2026 8:11am | Jul 27, 2026 12:13pm | Jul 27, 2026 12:13pm | Jul 27, 2026 12:13pm | Jul 27, 2026 12:16pm | Jul 27, 2026 12:15pm | Jul 27, 2026 12:15pm |  |  | Fair | No | Customer said JPS corrected the problem from last week
Non-Outage | J.E.26.07.20264 | C001865635 | Locksley Allen | St.Mary | Completed | Load_259005 | Blackstonedge - 110 | Jul 27, 2026 8:03am | Jul 27, 2026 8:11am | Jul 27, 2026 12:02pm | Jul 27, 2026 12:02pm | Jul 27, 2026 12:02pm | Jul 27, 2026 12:07pm | Jul 27, 2026 12:06pm | Jul 27, 2026 12:06pm |  |  | Fair | No | Customer said JPS corrected the problem last week. Unable to check the voltage because the gate lock and customer is not at home
Non-Outage | J.E.26.07.20675 | C001865632 | Locksley Allen | St.Mary | Completed | Load_269770 | Blackstonedge - 110 | Jul 27, 2026 8:03am | Jul 27, 2026 8:11am | Jul 27, 2026 11:08am | Jul 27, 2026 11:33am | Jul 27, 2026 11:33am | Jul 27, 2026 11:40am | Jul 27, 2026 11:46am | Jul 27, 2026 11:46am |  |  | Fair | No | Meter burn up. Meter needs to change urgently Voltage at meter socket phase to phase 220v. Phase to neutral 113&106vSocket found bridge out
Non-Outage | J.E.26.07.32348 | C001865631 | Andrae Clarke | Portland | Completed | Load_255121 | Port Antonio - 310 | Jul 27, 2026 7:59am | Jul 27, 2026 8:00am | Jul 27, 2026 8:06am | Jul 27, 2026 10:50am | Jul 27, 2026 10:50am | Jul 27, 2026 10:41am | Jul 27, 2026 10:53am | Jul 27, 2026 10:53am |  |  | Fair | No | Repair corroded wires use two one bolt clamp Check voltage 17/119/236
Non-Outage | J.E.26.07.32388 | C001865630 | Andrae Clarke | Portland | Completed | Load_240419 | Port Antonio - 410 | Jul 27, 2026 7:58am | Jul 27, 2026 8:00am | Jul 27, 2026 10:53am | Jul 27, 2026 10:53am | Jul 27, 2026 10:53am | Jul 27, 2026 11:36am | Jul 27, 2026 11:32am | Jul 27, 2026 11:32am |  |  | Fair | No | Made check found voltage low refer to Emergency Crew with bucket truckBucket Truck needed
Outage | J.E.26.07.31380 | C001865623 | Dean Smith | Hanover | Completed | Load_239009 | Orange Bay - 310 | Jul 27, 2026 7:54am | Jul 27, 2026 7:54am | Jul 27, 2026 12:49pm | Jul 27, 2026 12:49pm | Jul 27, 2026 12:49pm | Jul 27, 2026 12:49pm | Jul 27, 2026 12:52pm | Jul 27, 2026 12:52pm | BrokenWire |  | Fair | No | Customer said truck took his wire, please forward to field service to replace service wire.
Outage | J.E.26.07.32562 | C001865625 | Dean Smith | Hanover | Completed | Load_248363 | Orange Bay - 210 | Jul 27, 2026 7:54am | Jul 27, 2026 7:55am | Jul 27, 2026 9:15am | Jul 27, 2026 9:15am | Jul 27, 2026 9:15am | Jul 27, 2026 9:42am | Jul 27, 2026 9:43am | Jul 27, 2026 9:43am |  |  | Fair | No | Check and found ok, 115v,115v,230v.
Outage | J.E.26.07.32543 | C001865616 | Derrick Dawkins | St.James | Completed | Load_264499 | Bogue - 610 | Jul 27, 2026 7:53am | Jul 27, 2026 8:05am | Jul 27, 2026 10:52am | Jul 27, 2026 10:52am | Jul 27, 2026 10:53am | Jul 27, 2026 10:53am | Jul 27, 2026 10:53am | Jul 27, 2026 10:53am |  |  | Fair | No | Prem found ok
Outage | J.E.26.07.32553 | C001865617 | Derrick Dawkins | St.James | Completed | Load_253101 | Bogue - 610 | Jul 27, 2026 7:53am | Jul 27, 2026 8:05am | Jul 27, 2026 10:36am | Jul 27, 2026 10:36am | Jul 27, 2026 10:51am | Jul 27, 2026 10:51am | Jul 27, 2026 10:52am | Jul 27, 2026 10:52am |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.32578 | C001865618 | Derrick Dawkins | St.James | Completed | Load_247962 | Bogue - 610 | Jul 27, 2026 7:53am | Jul 27, 2026 8:05am | Jul 27, 2026 10:52am | Jul 27, 2026 10:52am | Jul 27, 2026 10:52am | Jul 27, 2026 10:52am | Jul 27, 2026 10:52am | Jul 27, 2026 10:52am |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.32525 | C001865615 | Derrick Dawkins | St.James | Completed | Load_262774 | Bogue - 610 | Jul 27, 2026 7:52am | Jul 27, 2026 8:05am | Jul 27, 2026 8:31am | Jul 27, 2026 8:31am | Jul 27, 2026 10:34am | Jul 27, 2026 10:34am | Jul 27, 2026 10:35am | Jul 27, 2026 10:35am |  |  | Fair | No | Premises checked and found ok
Outage | J.E.26.07.32531 | C001865614 | Michael Christian | St.James | Completed | Load_1002386 | Bogue - 310 | Jul 27, 2026 7:52am | Jul 27, 2026 8:04am | Jul 27, 2026 8:08am | Jul 27, 2026 8:08am | Jul 27, 2026 8:35am | Jul 27, 2026 9:33am | Jul 27, 2026 9:33am | Jul 27, 2026 9:33am |  |  | Fair | No | Premises not found
Non-Outage | J.E.26.07.14592 | C001865608 | Kenroy Dale | Manchester | Completed | Load_268909 | Kendal - 210 | Jul 27, 2026 7:49am | Jul 27, 2026 7:49am | Jul 27, 2026 1:31pm | Jul 27, 2026 1:31pm | Jul 27, 2026 1:37pm | Jul 27, 2026 1:37pm | Jul 27, 2026 1:38pm | Jul 27, 2026 1:38pm |  |  | Fair | No | Duplicate service order
Non-Outage | J.E.26.07.17044 | C001865610 | Damion Reid | Manchester | Completed | Load_242926 | Kendal - 210 | Jul 27, 2026 7:49am | Jul 27, 2026 3:21pm | Jul 27, 2026 9:01pm | Jul 27, 2026 9:01pm | Jul 27, 2026 9:54pm | Jul 27, 2026 10:12pm | Jul 27, 2026 10:15pm | Jul 27, 2026 10:15pm |  |  | Fair | No | Remade corroded service phase at secondary pole for 3 wire service using one 1 bolt clamp voltage reading at meter socket phase to neutral 113v-114v across phase 229v
Non-Outage | J.E.26.07.17085 | C001865609 | Kenroy Dale | Manchester | Completed | Load_262533 | Kendal - 210 | Jul 27, 2026 7:49am | Jul 27, 2026 7:49am | Jul 27, 2026 9:45am | Jul 27, 2026 9:45am | Jul 27, 2026 9:46am | Jul 27, 2026 9:47am | Jul 27, 2026 9:49am | Jul 27, 2026 9:49am |  |  | Fair | No | Area checked and found with supply, customer also confirmed that supply was restored voltage reading 115/116/231
Non-Outage | J.E.26.07.31261 | C001865612 | Kenroy Dale | Manchester | Completed | Load_303063 | Kendal - 210 | Jul 27, 2026 7:49am | Jul 27, 2026 7:49am | Jul 27, 2026 9:00am | Jul 27, 2026 9:49am | Jul 27, 2026 10:30am | Jul 27, 2026 11:33am | Jul 27, 2026 11:47am | Jul 27, 2026 11:47am |  |  | Fair | No | Opened 5 kva transformer for clearance to remade burned off phase at pole and retention 2/0 triplex, connection was remade, conductor retention and transformer re-closed. voltage reading 113/115/228
Non-Outage | J.E.26.07.32545 | C001865601 | Milton Charlton | null | Completed | null | null | Jul 27, 2026 7:44am | Jul 27, 2026 7:45am | Jul 27, 2026 1:50pm | Jul 27, 2026 1:50pm | Jul 27, 2026 1:50pm | Jul 27, 2026 1:50pm | Jul 27, 2026 1:52pm | Jul 27, 2026 1:52pm |  |  | Fair | No | Call related to call at #6 May Lane August Town.
Outage | J.E.26.07.32537 | C001865600 | Milton Charlton | KSAN | Completed | Load_578940 | Hope - 510 | Jul 27, 2026 7:44am | Jul 27, 2026 7:45am | Jul 27, 2026 1:52pm | Jul 27, 2026 1:52pm | Jul 27, 2026 1:52pm | Jul 27, 2026 1:55pm | Jul 27, 2026 1:53pm | Jul 27, 2026 1:53pm |  |  | Fair | No | Call related to call at #6 May Lane August Town.
Outage | J.E.26.07.32557 | C001865603 | Milton Charlton | KSAN | Completed | Load_578935 | Hope - 510 | Jul 27, 2026 7:44am | Jul 27, 2026 7:45am | Jul 27, 2026 12:00pm | Jul 27, 2026 12:00pm | Jul 27, 2026 1:43pm | Jul 27, 2026 1:40pm | Jul 27, 2026 1:50pm | Jul 27, 2026 1:50pm |  |  | Fair | No | Found one 30 amps junction fuse blown at pole#0119228.refused using one 30 amps fuse and reclosed junction switch.
Outage | J.E.26.07.32563 | C001865597 | Christopher Edwards | KSAN | Completed | Load_266471 | Constant Spring - 410 | Jul 27, 2026 7:42am | Jul 27, 2026 7:44am | Jul 27, 2026 7:49am | Jul 27, 2026 8:34am | Jul 27, 2026 8:34am | Jul 27, 2026 10:11am | Jul 27, 2026 10:12am | Jul 27, 2026 10:12am |  |  | Fair | No | Customer meter is defective and needs to be replaced Went to this location multiple times
Non-Outage | J.E.26.07.29770 | C001865596 | Royston Montague | St.Catherine | Completed | Load_252376 | New Michelton - 410 | Jul 27, 2026 7:35am | Jul 27, 2026 7:36am | Jul 27, 2026 8:19am | Jul 27, 2026 4:17pm | Jul 27, 2026 6:13pm | Jul 27, 2026 6:17pm | Jul 27, 2026 6:17pm | Jul 27, 2026 6:17pm |  |  | Fair | No | Not locating this premises. GPS coordinate on job not working.
Non-Outage | J.E.26.07.31198 | C001865595 | Royston Montague | St.Catherine | Completed | Load_238626 | Tredegar - 310 | Jul 27, 2026 7:35am | Jul 27, 2026 7:36am | Jul 27, 2026 8:19am | Jul 27, 2026 9:15am | Jul 27, 2026 10:16am | Jul 27, 2026 10:35am | Jul 27, 2026 10:35am | Jul 27, 2026 10:35am |  |  | Fair | No | Box number 01244, customer only getting one hot leg. Voltage 114v please assign this job to sir Moses thanks.
Non-Outage | J.E.26.07.32280 | C001865594 | Royston Montague | St.Catherine | Completed | Load_258753 | New Michelton - 210 | Jul 27, 2026 7:35am | Jul 27, 2026 7:36am | Jul 27, 2026 8:19am | Jul 28, 2026 4:49pm | Jul 28, 2026 4:49pm | Jul 28, 2026 4:49pm | Jul 28, 2026 4:49pm | Jul 28, 2026 4:49pm |  |  | Fair | No | Rami system in area.
Non-Outage | J.E.26.07.32038 | C001865592 | Orville Lee | null | Completed | null | null | Jul 27, 2026 7:33am | Jul 27, 2026 9:23am | Jul 27, 2026 11:56am | Jul 27, 2026 11:58am | Jul 27, 2026 11:59am | Jul 27, 2026 12:00pm | Jul 27, 2026 12:01pm | Jul 27, 2026 12:01pm | Fire |  | Fair | No | Secondary line was patrolled and no fire, arching or banging line seen.
Outage | J.E.26.07.32572 | C001865591 | Ricky Hall | Portmore | Completed | Load_1003660 | Naggo Head - 610 | Jul 27, 2026 7:32am | Jul 27, 2026 10:26am | Jul 27, 2026 11:26am | Jul 27, 2026 11:28am | Jul 27, 2026 12:25pm | Jul 27, 2026 1:03pm | Jul 27, 2026 1:04pm | Jul 27, 2026 1:04pm |  |  | Fair | No | Replaced 2 blown junction fuse
Non-Outage | J.E.26.07.31114 | C001865588 | Orville Lee | Portmore | Completed | Load_268692 | Naggo Head - 610 | Jul 27, 2026 7:30am | Jul 27, 2026 7:31am | Jul 27, 2026 8:28am | Jul 27, 2026 10:33am | Jul 27, 2026 10:43am | Jul 27, 2026 10:45am | Jul 27, 2026 10:47am | Jul 27, 2026 10:47am |  |  | Fair | No | Customer mentioned that the telephone number is incorrect and they did not make a report Unable to get inside gated community without customer informed security personnel at the entrance gate
Non-Outage | J.E.26.07.32042 | C001865587 | Orville Lee | Portmore | Completed | Load_243960 | Naggo Head - 510 | Jul 27, 2026 7:30am | Jul 27, 2026 7:31am | Jul 27, 2026 8:28am | Jul 27, 2026 11:33am | Jul 27, 2026 11:42am | Jul 27, 2026 11:51am | Jul 27, 2026 11:56am | Jul 27, 2026 11:56am | Fire |  | Fair | No | Secondary line was patrolled and no visible fire seen or banging line seen
Non-Outage | J.E.26.07.32236 | C001865589 | Orville Lee | Portmore | Completed | Load_251292 | Naggo Head - 510 | Jul 27, 2026 7:30am | Jul 27, 2026 7:31am | Jul 27, 2026 8:28am | Jul 27, 2026 10:48am | Jul 27, 2026 10:57am | Jul 27, 2026 11:29am | Jul 27, 2026 11:31am | Jul 27, 2026 11:31am |  |  | Fair | No | 30ft service wire was changed Three pen union and two one bolt clamp usedVoltage116v
Non-Outage | J.E.26.07.32256 | C001865590 | Orville Lee | Portmore | Completed | Load_243615 | Naggo Head - 510 | Jul 27, 2026 7:30am | Jul 27, 2026 7:31am | Jul 27, 2026 8:28am | Jul 27, 2026 8:29am | Jul 27, 2026 9:57am | Jul 27, 2026 10:31am | Jul 27, 2026 10:33am | Jul 27, 2026 10:33am |  |  | Fair | No | Checks made and found pothead and secondary line corroded Three pen union and two one 1bolt clamp usedVoltage 120v120v240v
Outage | J.E.26.07.32455 | C001865586 | Dean Smith | Hanover | Completed | Load_243282 | Orange Bay - 210 | Jul 27, 2026 7:28am | Jul 27, 2026 7:53am | Jul 27, 2026 9:43am | Jul 27, 2026 9:43am | Jul 27, 2026 10:45am | Jul 27, 2026 10:46am | Jul 27, 2026 10:47am | Jul 27, 2026 10:47am |  |  | Fair | No | Check and found ok, customer meter socket burnt, advised to fix
Outage | J.E.26.07.32564 | C001865584 | Roxroy Needham | St.Ann | Completed | Load_269661 | Cardiff Hall - 310 | Jul 27, 2026 7:28am | Jul 27, 2026 7:28am | Jul 27, 2026 8:15am | Jul 27, 2026 8:16am | Jul 27, 2026 9:35am | Jul 27, 2026 9:55am | Jul 27, 2026 9:58am | Jul 27, 2026 9:58am |  | Y | Fair | No | Replace a 20 amps junction fuse at pole
Outage | J.E.26.07.32551 | C001865583 | Roxroy Needham | St.Ann | Completed | Load_245585 | Cardiff Hall - 310 | Jul 27, 2026 7:26am | Jul 27, 2026 7:28am | Jul 27, 2026 9:59am | Jul 27, 2026 9:59am | Jul 27, 2026 9:59am | Jul 27, 2026 9:59am | Jul 27, 2026 10:00am | Jul 27, 2026 10:00am |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.32452 | C001865580 | Richard Nicholas | St.Catherine | Completed | Load_266292 | Tredegar - 310 | Jul 27, 2026 7:25am | Jul 27, 2026 7:31am | Jul 27, 2026 8:11am | Jul 27, 2026 8:11am | Jul 27, 2026 9:18am | Jul 27, 2026 9:41am | Jul 27, 2026 9:41am | Jul 27, 2026 9:41am |  |  | Fair | No | Area found ok
Outage | J.E.26.07.32454 | C001865582 | Clyde Brown | Clarendon | Completed | Load_405727 | Parnassus - 210 | Jul 27, 2026 7:25am | Jul 27, 2026 7:26am | Jul 27, 2026 9:37am | Jul 27, 2026 9:37am | Jul 27, 2026 9:37am | Jul 27, 2026 9:31am | Jul 27, 2026 9:39am | Jul 27, 2026 9:39am |  |  | Fair | No | Found ok
Outage | J.E.26.07.32516 | C001865581 | Moses Elliston | St.Catherine | Completed | Load_242257 | Tredegar - 410 | Jul 27, 2026 7:25am | Jul 27, 2026 7:26am | Jul 27, 2026 2:40pm | Jul 27, 2026 2:40pm | Jul 27, 2026 2:40pm | Jul 27, 2026 1:30pm | Jul 27, 2026 2:42pm | Jul 27, 2026 2:42pm |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.07.32464 | C001865579 | Moses Elliston | St.Catherine | Completed | Load_568941 | Twickenham - 310 | Jul 27, 2026 7:24am | Jul 27, 2026 7:26am | Jul 27, 2026 11:14am | Jul 27, 2026 11:14am | Jul 27, 2026 11:14am | Jul 27, 2026 11:20am | Jul 27, 2026 11:20am | Jul 27, 2026 11:20am |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.07.32375 | C001865575 | Wayne Dillion | Manchester | Completed | Load_292993 | Spur Tree - 210 | Jul 27, 2026 7:21am | Jul 27, 2026 7:21am | Jul 27, 2026 9:01am | Jul 27, 2026 9:01am | Jul 27, 2026 9:01am | Jul 27, 2026 9:02am | Jul 27, 2026 9:02am | Jul 27, 2026 9:02am |  |  | Fair | No | Customer said supply ok problem has been resolved
Outage | J.E.26.07.32430 | C001865576 | Kemark Slue | St.Catherine | Completed | Load_556034 | Tredegar - 510 | Jul 27, 2026 7:21am | Jul 27, 2026 7:23am | Jul 27, 2026 7:53am | Jul 27, 2026 10:51am | Jul 27, 2026 10:51am | Jul 27, 2026 11:13am | Jul 27, 2026 11:16am | Jul 27, 2026 11:16am |  |  | Fair | No | Upon arrival at the location the crew discovered that a 25 kva 13.8 kv transformer fuse is blown, further observation revealed that the transformer had been checked by another crew and is defective, please refer to A. Murray to have said transformer upgrade to a 50 kva 13.8 kv transformer as approximately 35 legitimate customers were counted.
Outage | J.E.26.07.32360 | C001865544 | Horace Malcolm | St.James | Completed | Load_263530 | Queens Drive - 310 | Jul 26, 2026 11:27pm | Jul 26, 2026 11:35pm | Jul 27, 2026 6:18am | Jul 27, 2026 6:18am | Jul 27, 2026 6:18am | Jul 27, 2026 6:19am | Jul 27, 2026 6:19am | Jul 27, 2026 6:19am |  |  | Fair | No | Check and found ok supply restored to area
Outage | J.E.26.07.32426 | C001865545 | Horace Malcolm | St.James | Completed | Load_269969 | Bogue - 310 | Jul 26, 2026 11:27pm | Jul 26, 2026 11:35pm | Jul 27, 2026 2:59am | Jul 27, 2026 2:59am | Jul 27, 2026 4:15am | Jul 27, 2026 6:18am | Jul 27, 2026 6:18am | Jul 27, 2026 6:18am |  |  | Fair | No | Splice and retention one three pole span secondary phase and nuetral used 90ft #2 conductor (3) #2 preforms 3clamps and refuse one 25kva used (1) 2amp fuse
Outage | J.E.26.07.32425 | C001865543 | Delano Gayle | St.Catherine | Completed | Load_262632 | Tredegar - 210 | Jul 26, 2026 11:23pm | Jul 26, 2026 11:24pm | Jul 27, 2026 1:43am | Jul 27, 2026 1:43am | Jul 27, 2026 1:55am | Jul 27, 2026 2:00am | Jul 27, 2026 2:01am | Jul 27, 2026 2:01am |  |  | Fair | No | Power restored to McVickers lane and sections of cromarty when 30amps junction fuse and 25amps junction fuse was replaced, however 1 10kva hexing transformer circuit remains out as fire was reportedly seen coming from box, approximately 10customers remain out,send call to Moses to check box
Outage | J.E.26.07.32432 | C001865542 | Delano Gayle | St.Catherine | Completed | Load_265584 | Tredegar - 510 | Jul 26, 2026 11:23pm | Jul 26, 2026 11:24pm | Jul 27, 2026 2:02am | Jul 27, 2026 2:02am | Jul 27, 2026 3:47am | Jul 27, 2026 4:35am | Jul 27, 2026 4:35am | Jul 27, 2026 4:35am |  |  | Fair | No | Blown 25kva transformer fuse no pole number, patrolled and found line section okay for closure replace 3amps fuse and upon closure fuse exploded, remove drop lead and test close once more and upon closure fuse exploded once more and oil was spraying from Drop lead bushing ,Conclusion:Defective 25kva transformer no pole number, send call to maintenance
Outage | J.E.26.07.32410 | C001865535 | Delano Gayle | St.Catherine | Completed | Load_238911 | Tredegar - 210 | Jul 26, 2026 10:09pm | Jul 26, 2026 11:23pm | Jul 26, 2026 11:30pm | Jul 26, 2026 11:30pm | Jul 27, 2026 12:40am | Jul 27, 2026 1:43am | Jul 27, 2026 1:43am | Jul 27, 2026 1:43am | Fire |  | Fair | No | Blown 30amps junction on main no pole number, blown junction no pole number, patrolled line section and found okay for closure replace 30amps at main and 25amps at other blown junction leading into cromarty
Outage | J.E.26.07.32404 | C001865534 | Fitzroy Turner | KSAS | Completed | Load_250955 | Three Miles - 410 | Jul 26, 2026 10:06pm | Jul 26, 2026 10:07pm | Jul 26, 2026 10:34pm | Jul 26, 2026 10:34pm | Jul 26, 2026 10:34pm | Jul 26, 2026 10:56pm | Jul 26, 2026 10:59pm | Jul 26, 2026 10:59pm | Fire |  | Fair | No | Found tree wire open secondary phase and neutral coming contact with each other cause fire use 4ft of #2 conductors to space wire areas is now safe
Non-Outage | J.E.26.07.31551 | C001865533 | Jowayne Newmans | Portland | Completed | Load_249013 | Port Antonio - 310 | Jul 26, 2026 10:00pm | Jul 26, 2026 10:00pm | Jul 26, 2026 10:32pm | Jul 26, 2026 10:32pm | Jul 26, 2026 10:32pm | Jul 26, 2026 10:33pm | Jul 26, 2026 10:34pm | Jul 26, 2026 10:34pm | Fire |  | Fair | No | Customer stated that issue was resolved from last night
Outage | J.E.26.07.32396 | C001865530 | Christopher Edwards | KSAN | Completed | Load_262938 | Constant Spring - 210 | Jul 26, 2026 9:51pm | Jul 26, 2026 11:13pm | Jul 26, 2026 11:19pm | Jul 26, 2026 11:34pm | Jul 26, 2026 11:52pm | Jul 27, 2026 12:16am | Jul 27, 2026 12:17am | Jul 27, 2026 12:17am |  |  | Fair | No | Refuse blown 50:kva transformer using (1) 5 amps
Non-Outage | J.E.26.07.32401 | C001865528 | Daniel Francis | null | Completed | null | null | Jul 26, 2026 9:41pm | Jul 26, 2026 9:42pm | Jul 26, 2026 10:27pm | Jul 26, 2026 10:27pm | Jul 26, 2026 10:28pm | Jul 26, 2026 10:28pm | Jul 26, 2026 10:30pm | Jul 26, 2026 10:30pm | Fire |  | Fair | No | No fire seen now
Outage | J.E.26.07.32299 | C001865529 | Daniel Francis | St.Ann | Completed | Load_264221 | Ocho Rios - 310 | Jul 26, 2026 9:41pm | Jul 26, 2026 9:42pm | Jul 26, 2026 9:49pm | Jul 26, 2026 9:49pm | Jul 26, 2026 10:17pm | Jul 26, 2026 10:23pm | Jul 26, 2026 10:26pm | Jul 26, 2026 10:26pm |  |  | Fair | No | No fire seen at the moment residents pointing to insulator on transmission lines pole #0180292
Outage | J.E.26.07.32342 | C001865524 | Milton Charlton | KSAN | Completed | Load_568475 | Hope - 510 | Jul 26, 2026 9:14pm | Jul 26, 2026 9:15pm | Jul 27, 2026 9:36am | Jul 27, 2026 9:36am | Jul 27, 2026 11:45am | Jul 27, 2026 11:55am | Jul 27, 2026 11:59am | Jul 27, 2026 11:59am |  |  | Fair | No | Found one 3 amps transformer fuse blown at pole #( no pole#). Refused using one 3 amps fuse and reclosed transformer switch
Non-Outage | J.E.26.07.32330 | C001865523 | Kaydon Taylor | null | Completed | null | null | Jul 26, 2026 9:13pm | Jul 27, 2026 9:16am | Jul 27, 2026 9:34am | Jul 27, 2026 9:43am | Jul 27, 2026 9:43am | Jul 27, 2026 9:44am | Jul 27, 2026 9:44am | Jul 27, 2026 9:44am |  |  | Fair | No | Found okay
Outage | J.E.26.07.32376 | C001865522 | Christopher Edwards | KSAN | Completed | Load_264054 | Constant Spring - 410 | Jul 26, 2026 9:10pm | Jul 27, 2026 7:45am | Jul 27, 2026 10:12am | Jul 27, 2026 10:39am | Jul 27, 2026 10:39am | Jul 27, 2026 11:52am | Jul 27, 2026 11:54am | Jul 27, 2026 11:54am |  |  | Fair | No | Isolate 100kva transformer To remake burnt secondary jumper joint Using (2) one bolt clamps Voltage:115,114,230v
Outage | J.E.26.07.32384 | C001865521 | Oshane Warren | Westmoreland | Completed | Load_292176 | Paradise - 110 | Jul 26, 2026 9:08pm | Jul 26, 2026 9:08pm | Jul 26, 2026 9:17pm | Jul 26, 2026 9:17pm | Jul 26, 2026 9:52pm | Jul 26, 2026 9:54pm | Jul 26, 2026 9:55pm | Jul 26, 2026 9:55pm |  |  | Rains | No | Replace 8amp junction fuse
Outage | J.E.26.07.32299 | C001865519 | Omar King | St.Ann | Completed | Load_264221 | Ocho Rios - 310 | Jul 26, 2026 8:31pm | Jul 26, 2026 8:31pm | Jul 27, 2026 4:31pm | Jul 27, 2026 4:31pm | Jul 27, 2026 5:40pm | Jul 27, 2026 5:40pm | Jul 27, 2026 5:41pm | Jul 27, 2026 5:41pm |  |  | Fair | No | Unable to find customer customer call several times no answer directions not sufficient
Outage | J.E.26.07.32317 | C001865518 | Raymond Carr | St.Mary | Completed | Load_269124 | Oracabessa - 210 | Jul 26, 2026 8:30pm | Jul 26, 2026 8:30pm | Jul 26, 2026 9:21pm | Jul 26, 2026 9:21pm | Jul 26, 2026 10:01pm | Jul 26, 2026 10:20pm | Jul 26, 2026 10:03pm | Jul 26, 2026 10:03pm |  |  | Fair | No | Customer reported that her breaker tripped.
Outage | J.E.26.07.32353 | C001865515 | Horace Malcolm | St.James | Completed | Load_256186 | Queens Drive - 310 | Jul 26, 2026 8:19pm | Jul 26, 2026 11:26pm | Jul 27, 2026 12:24am | Jul 27, 2026 12:24am | Jul 27, 2026 1:10am | Jul 27, 2026 2:58am | Jul 27, 2026 2:58am | Jul 27, 2026 2:58am |  |  | Fair | No | Check and found defective lightening arrester disconnect arrester and replace one 30amp junction fuse
Outage | J.E.26.07.32345 | C001865514 | Horace Malcolm | St.James | Completed | Load_244260 | Queens Drive - 310 | Jul 26, 2026 8:18pm | Jul 26, 2026 11:26pm | Jul 27, 2026 6:19am | Jul 27, 2026 6:19am | Jul 27, 2026 6:19am | Jul 27, 2026 6:20am | Jul 27, 2026 6:21am | Jul 27, 2026 6:21am |  |  | Fair | No | Check and found ok supply restored to area
Outage | J.E.26.07.32351 | C001865513 | Horace Malcolm | St.James | Completed | Load_239852 | Queens Drive - 310 | Jul 26, 2026 8:18pm | Jul 26, 2026 11:26pm | Jul 27, 2026 6:21am | Jul 27, 2026 6:21am | Jul 27, 2026 6:21am | Jul 27, 2026 6:24am | Jul 27, 2026 6:24am | Jul 27, 2026 6:24am |  |  | Fair | No | Check and found area ok supply restored
Outage | J.E.26.07.32271 | C001865511 | Wayne Dillion | Manchester | Completed | Load_292993 | Spur Tree - 210 | Jul 26, 2026 8:17pm | Jul 26, 2026 8:17pm | Jul 26, 2026 10:48pm | Jul 26, 2026 10:48pm | Jul 26, 2026 10:48pm | Jul 26, 2026 11:00pm | Jul 26, 2026 11:10pm | Jul 26, 2026 11:10pm |  |  | Fair | No | Patrol and found one blown 2amp junction fuse that protects 25kva transformer circuit no pole #. Replace same and supply restored okay.
Outage | J.E.26.07.32349 | C001865510 | Wayne Dillion | St.Elizabeth | Completed | Load_260786 | Maggotty - 110 | Jul 26, 2026 8:10pm | Jul 26, 2026 8:10pm | Jul 26, 2026 8:58pm | Jul 26, 2026 8:58pm | Jul 26, 2026 9:19pm | Jul 26, 2026 9:47pm | Jul 26, 2026 9:47pm | Jul 26, 2026 9:47pm |  |  | Fair | No | Patrol and found one blown 40amp junction fuse no pole #. Replace same and supply restored okay.
Non-Outage | J.E.26.07.26003 | C001865509 | Ryan Richards | null | Completed | null | null | Jul 26, 2026 8:05pm | Jul 26, 2026 8:05pm | Jul 26, 2026 8:21pm | Jul 26, 2026 8:21pm | Jul 26, 2026 9:47pm | Jul 26, 2026 10:11pm | Jul 26, 2026 10:11pm | Jul 26, 2026 10:11pm | LowHangingWires,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Customer standtion bend an broken cause by rubbish truck customer as been advised to carry out repair
Non-Outage | J.E.26.05.34917 | C001865508 | Wayne Dillion | null | Completed | null | null | Jul 26, 2026 8:03pm | Jul 26, 2026 8:04pm | Jul 27, 2026 9:28am | Jul 27, 2026 9:28am | Jul 27, 2026 9:31am | Jul 27, 2026 9:33am | Jul 27, 2026 9:36am | Jul 27, 2026 9:36am | LeaningPole |  | Fair | No | One badly leaning 35 feet wooden pole with a 25 kva transformer leaning on customer wall customer said the are afraid the pole mite fall on there house an car please refer to maintenance to have the matter resolved
Non-Outage | J.E.26.07.04481 | C001865507 | Wayne Dillion | null | Completed | null | null | Jul 26, 2026 8:03pm | Jul 26, 2026 8:04pm | Jul 27, 2026 9:43am | Jul 27, 2026 9:43am | Jul 27, 2026 9:43am | Jul 27, 2026 9:44am | Jul 27, 2026 9:45am | Jul 27, 2026 9:45am | BrokenPole |  | Fair | No | Customer said problem has been resolved
Non-Outage | J.E.26.07.32177 | C001865506 | Michael Christian | null | Completed | null | null | Jul 26, 2026 7:58pm | Jul 26, 2026 7:58pm | Jul 26, 2026 8:03pm | Jul 26, 2026 8:03pm | Jul 26, 2026 8:44pm | Jul 26, 2026 10:57pm | Jul 26, 2026 10:57pm | Jul 26, 2026 10:57pm | BrokenWire |  | Fair | No | Found broken wire men work and the line cut bamboo offs lines time for me my time is up
Outage | J.E.26.07.32091 | C001865505 | Marlon Brown | Trelawny | Completed | Load_254068 | Duncans - 210 | Jul 26, 2026 7:57pm | Jul 26, 2026 8:19pm | Jul 26, 2026 8:55pm | Jul 26, 2026 8:55pm | Jul 26, 2026 8:57pm | Jul 26, 2026 8:57pm | Jul 26, 2026 8:57pm | Jul 26, 2026 8:57pm |  |  | Fair | No | Feeder issue
Outage | J.E.26.07.32250 | C001865504 | Marlon Brown | Trelawny | Completed | Load_268209 | Duncans - 110 | Jul 26, 2026 7:57pm | Jul 26, 2026 8:19pm | Jul 26, 2026 10:17pm | Jul 26, 2026 10:17pm | Jul 26, 2026 10:26pm | Jul 26, 2026 10:48pm | Jul 26, 2026 10:48pm | Jul 26, 2026 10:48pm |  |  | Fair | No | Electricity in area, not able to locate customer.
Non-Outage | J.E.26.07.32340 | C001865503 | Marlon Brown | null | Completed | null | null | Jul 26, 2026 7:55pm | Jul 26, 2026 8:20pm | Jul 26, 2026 8:59pm | Jul 26, 2026 8:59pm | Jul 26, 2026 9:04pm | Jul 26, 2026 9:05pm | Jul 26, 2026 9:05pm | Jul 26, 2026 9:05pm | Fire |  | Fair | No | Cable wires not a jps conductor.
Non-Outage | J.E.26.06.19164 | C001865500 | Andrew Powell | null | Completed | null | null | Jul 26, 2026 7:26pm | Jul 26, 2026 7:28pm | Jul 26, 2026 8:31pm | Jul 26, 2026 8:31pm | Jul 26, 2026 8:53pm | Jul 26, 2026 8:54pm | Jul 26, 2026 8:55pm | Jul 26, 2026 8:55pm | BrokenPole |  | Fair | No | Premises not located inadequately direction contact customer by telephone unsuccessful.
Non-Outage | J.E.26.06.34546 | C001865499 | Andrew Powell | null | Completed | null | null | Jul 26, 2026 7:26pm | Jul 26, 2026 7:28pm | Jul 26, 2026 7:46pm | Jul 26, 2026 7:46pm | Jul 26, 2026 7:46pm | Jul 26, 2026 7:46pm | Jul 26, 2026 7:47pm | Jul 26, 2026 7:47pm | BrokenWire |  | Fair | No | Premises found okay customer stated that fault resolved supply restored.
Non-Outage | J.E.26.01.22622 | C001865496 | Selvin White | null | Completed | null | null | Jul 26, 2026 7:25pm | Jul 27, 2026 9:51am | Jul 27, 2026 1:28pm | Jul 27, 2026 1:29pm | Jul 27, 2026 2:16pm | Jul 27, 2026 2:32pm | Jul 27, 2026 2:32pm | Jul 27, 2026 2:32pm | BrokenPole |  | Rains | No | Supply found okay with no broken pole found at location.
Non-Outage | J.E.26.03.13319 | C001865497 | Andrew Powell | null | Completed | null | null | Jul 26, 2026 7:25pm | Jul 26, 2026 7:28pm | Jul 26, 2026 7:41pm | Jul 26, 2026 7:41pm | Jul 26, 2026 7:41pm | Jul 26, 2026 7:42pm | Jul 26, 2026 7:43pm | Jul 26, 2026 7:43pm | LeaningPole |  | Fair | No | Premises found okay customer stated that fault resolved.
Non-Outage | J.E.26.05.34310 | C001865498 | Andrew Powell | null | Completed | null | null | Jul 26, 2026 7:25pm | Jul 26, 2026 7:28pm | Jul 26, 2026 7:36pm | Jul 26, 2026 7:36pm | Jul 26, 2026 7:36pm | Jul 26, 2026 7:37pm | Jul 26, 2026 7:37pm | Jul 26, 2026 7:37pm | BrokenPole |  | Fair | No | Premises found okay customer stated that fault resolved.
Outage | J.E.26.07.32309 | C001865494 | Andrew Powell | Manchester | Completed | Load_256830 | Spur Tree - 210 | Jul 26, 2026 7:21pm | Jul 26, 2026 7:22pm | Jul 26, 2026 7:27pm | Jul 26, 2026 7:29pm | Jul 26, 2026 7:30pm | Jul 26, 2026 7:30pm | Jul 26, 2026 7:31pm | Jul 26, 2026 7:31pm |  |  | Fair | No | Premises found okay customer stated that supply restored.
Outage | J.E.26.07.32310 | C001865495 | Andrew Powell | Manchester | Completed | Load_247501 | Spur Tree - 210 | Jul 26, 2026 7:21pm | Jul 26, 2026 7:22pm | Jul 26, 2026 7:31pm | Jul 26, 2026 7:31pm | Jul 26, 2026 7:31pm | Jul 26, 2026 7:32pm | Jul 26, 2026 7:32pm | Jul 26, 2026 7:32pm |  |  | Fair | No | Premises found okay customer stated that supply restored.
Non-Outage | J.E.26.07.32308 | C001865493 | Barnett Brown | null | Completed | null | null | Jul 26, 2026 7:20pm | Jul 27, 2026 7:28am | Jul 27, 2026 7:57am | Jul 27, 2026 7:59am | Jul 27, 2026 9:39am | Jul 27, 2026 9:47am | Jul 27, 2026 9:51am | Jul 27, 2026 9:51am |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.07.32305 | C001865492 | Barnett Brown | null | Completed | null | null | Jul 26, 2026 7:19pm | Jul 27, 2026 7:28am | Jul 27, 2026 9:51am | Jul 27, 2026 9:51am | Jul 27, 2026 10:01am | Jul 27, 2026 10:02am | Jul 27, 2026 10:03am | Jul 27, 2026 10:03am |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.07.32297 | C001865490 | Fitzroy Turner | null | Completed | null | null | Jul 26, 2026 7:10pm | Jul 26, 2026 7:10pm | Jul 26, 2026 8:34pm | Jul 26, 2026 8:34pm | Jul 26, 2026 8:34pm | Jul 26, 2026 8:35pm | Jul 26, 2026 8:36pm | Jul 26, 2026 8:36pm | Fire |  | Fair | No | Found defective YPP box burnt up cause by illegal construction please send email to field service department to check box
Outage | J.E.26.07.32292 | C001865480 | Javid Vernon | Westmoreland | Completed | Load_255234 | Paradise - 310 | Jul 26, 2026 6:57pm | Jul 26, 2026 6:57pm | Jul 26, 2026 8:41pm | Jul 26, 2026 8:41pm | Jul 26, 2026 8:41pm | Jul 26, 2026 8:41pm | Jul 26, 2026 8:42pm | Jul 26, 2026 8:42pm | Fire |  | Fair | No | Related to previous call job #32120
Non-Outage | J.E.26.07.32275 | C001865473 | Fitzroy Turner | null | Completed | null | null | Jul 26, 2026 6:48pm | Jul 26, 2026 7:10pm | Jul 26, 2026 8:37pm | Jul 26, 2026 8:37pm | Jul 26, 2026 8:39pm | Jul 26, 2026 9:05pm | Jul 26, 2026 9:07pm | Jul 26, 2026 9:07pm | Fire |  | Fair | No | Defective defective YPP box cause 30amps junction fuse to blown replaced 30 amp fuse supply restored to areas
Outage | J.E.26.07.32269 | C001865465 | Fitzroy Turner | KSAN | Completed | Load_293471 | Washington Blvd - 710 | Jul 26, 2026 6:37pm | Jul 26, 2026 6:39pm | Jul 26, 2026 9:44pm | Jul 26, 2026 9:45pm | Jul 26, 2026 9:45pm | Jul 26, 2026 9:55pm | Jul 26, 2026 9:56pm | Jul 26, 2026 9:56pm |  |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.07.32270 | C001865468 | Fitzroy Turner | KSAS | Completed | Load_293524 | Three Miles - 410 | Jul 26, 2026 6:37pm | Jul 26, 2026 6:39pm | Jul 26, 2026 9:08pm | Jul 26, 2026 9:08pm | Jul 26, 2026 9:27pm | Jul 26, 2026 9:27pm | Jul 26, 2026 9:28pm | Jul 26, 2026 9:28pm | LeakingTransformer |  | Fair | No | Supply restored after replace blown fuse
Outage | J.E.26.07.32272 | C001865467 | Fitzroy Turner | KSAS | Completed | Load_240971 | Three Miles - 410 | Jul 26, 2026 6:37pm | Jul 26, 2026 6:39pm | Jul 26, 2026 7:29pm | Jul 26, 2026 7:29pm | Jul 26, 2026 8:00pm | Jul 26, 2026 8:26pm | Jul 26, 2026 8:34pm | Jul 26, 2026 8:34pm | Fire |  | Fair | No | Found defective YPP box burnt up cause 30amps junction fuse blown at four fourty drive replaced blown 30 junction fuses supply restored to the areas
Outage | J.E.26.07.32283 | C001865466 | Fitzroy Turner | KSAN | Completed | Load_293318 | Washington Blvd - 710 | Jul 26, 2026 6:37pm | Jul 26, 2026 6:39pm | Jul 26, 2026 9:29pm | Jul 26, 2026 9:42pm | Jul 26, 2026 9:42pm | Jul 26, 2026 9:43pm | Jul 26, 2026 9:43pm | Jul 26, 2026 9:43pm |  |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.07.32242 | C001865464 | Milton Charlton | KSAN | Completed | Load_242558 | Hope - 410 | Jul 26, 2026 6:36pm | Jul 26, 2026 6:36pm | Jul 26, 2026 7:28pm | Jul 26, 2026 7:28pm | Jul 26, 2026 8:21pm | Jul 26, 2026 8:30pm | Jul 26, 2026 8:26pm | Jul 26, 2026 8:26pm |  |  | Fair | No | Found one 20 amps junction fuse blown at pole#. 0001575 And one 3 amps transformer fuse blown at pole # 0007002. Refuse using one 20 amp fuse and one 3 amps fuse and reclosed junction and transformer switches.
Outage | J.E.26.07.32282 | C001865461 | Richard Nicholas | St.Catherine | Completed | Load_245090 | Tredegar - 210 | Jul 26, 2026 6:30pm | Jul 26, 2026 6:32pm | Jul 26, 2026 7:42pm | Jul 26, 2026 7:42pm | Jul 26, 2026 8:22pm | Jul 26, 2026 8:59pm | Jul 26, 2026 9:00pm | Jul 26, 2026 9:00pm |  |  | Fair | No | Premises found ok,customer circuit breaker was tripped same was reset.
Outage | J.E.26.07.32260 | C001865459 | Moses Elliston | St.Catherine | Completed | Load_288641 | Twickenham - 210 | Jul 26, 2026 6:27pm | Jul 26, 2026 6:29pm | Jul 27, 2026 2:44pm | Jul 27, 2026 2:44pm | Jul 27, 2026 2:44pm | Jul 27, 2026 11:49am | Jul 27, 2026 2:46pm | Jul 27, 2026 2:46pm |  |  | Fair | No | Customer said supply ok in area.
Outage | J.E.26.07.32271 | C001865457 | Wayne Dillion | Manchester | Completed | Load_292993 | Spur Tree - 210 | Jul 26, 2026 6:19pm | Jul 26, 2026 6:20pm | Jul 26, 2026 7:20pm | Jul 26, 2026 7:20pm | Jul 26, 2026 7:20pm | Jul 26, 2026 7:24pm | Jul 26, 2026 7:25pm | Jul 26, 2026 7:25pm |  |  | Fair | No | Unable to locate and customer not answering the phone.
Outage | J.E.26.07.32259 | C001865451 | Oshane Warren | Westmoreland | Completed | Load_292176 | Paradise - 110 | Jul 26, 2026 6:01pm | Jul 26, 2026 6:02pm | Jul 26, 2026 7:48pm | Jul 26, 2026 7:48pm | Jul 26, 2026 9:14pm | Jul 26, 2026 9:15pm | Jul 26, 2026 9:15pm | Jul 26, 2026 9:15pm |  |  | Rains | No | Unable to locate or contact customer on the phone need direction
Outage | J.E.26.07.32254 | C001865450 | Javid Vernon | Westmoreland | Completed | Load_261456 | Paradise - 310 | Jul 26, 2026 6:00pm | Jul 26, 2026 6:02pm | Jul 26, 2026 8:40pm | Jul 26, 2026 8:40pm | Jul 26, 2026 8:40pm | Jul 26, 2026 8:40pm | Jul 26, 2026 8:41pm | Jul 26, 2026 8:41pm |  |  | Fair | No | Related to previous call job #32120
Outage | J.E.26.07.27832 | C001865434 | Moses Elliston | St.Catherine | Completed | Load_290732 | Twickenham - 210 | Jul 26, 2026 5:35pm | Jul 26, 2026 5:35pm | Jul 27, 2026 6:31am | Jul 27, 2026 6:31am | Jul 27, 2026 6:31am | Jul 26, 2026 6:00pm | Jul 27, 2026 6:32am | Jul 27, 2026 6:32am |  |  | Fair | No | Supply reconnected
Non-Outage | J.E.26.07.31414 | C001865432 | Neville Spencer | Clarendon | Completed | Load_255474 | Parnassus - 210 | Jul 26, 2026 5:30pm | Jul 26, 2026 5:30pm | Jul 26, 2026 7:33pm | Jul 26, 2026 7:34pm | Jul 27, 2026 5:04pm | Jul 27, 2026 5:04pm | Jul 27, 2026 5:05pm | Jul 27, 2026 5:05pm |  |  | Fair | No | Not found.
Non-Outage | J.E.26.07.30807 | C001865430 | Neville Spencer | Clarendon | Completed | Load_238006 | Parnassus - 210 | Jul 26, 2026 5:29pm | Jul 26, 2026 5:30pm | Jul 26, 2026 5:39pm | Jul 26, 2026 5:39pm | Jul 26, 2026 5:59pm | Jul 26, 2026 5:59pm | Jul 26, 2026 7:31pm | Jul 26, 2026 7:31pm |  |  | Fair | No | Found 180 ft 2 wire service burnt up feeding meter # 2256085 wire need to replace
Non-Outage | J.E.26.07.20068 | C001865428 | Rayon Foster | Hanover | Completed | Load_251176 | Orange Bay - 310 | Jul 26, 2026 5:18pm | Jul 26, 2026 5:18pm | Jul 27, 2026 10:08am | Jul 27, 2026 10:08am | Jul 27, 2026 10:19am | Jul 27, 2026 10:25am | Jul 27, 2026 10:25am | Jul 27, 2026 10:25am |  |  | Fair | No | Customer said her issue was resolved weeks ago by by a jps team
Non-Outage | J.E.26.07.20116 | C001865427 | Rayon Foster | Hanover | Completed | Load_292525 | Orange Bay - 310 | Jul 26, 2026 5:18pm | Jul 26, 2026 5:18pm | Jul 27, 2026 10:27am | Jul 27, 2026 10:27am | Jul 27, 2026 11:08am | Jul 27, 2026 11:35am | Jul 27, 2026 11:36am | Jul 27, 2026 11:36am |  |  | Fair | No | Voltage check in meter socket 109/106 AB215 low voltage cause from voltage drop one 25 kva transformer feeding entry community redundant 25 kva transformer need to reinstall to rectify the low voltage issue curcuit was tied out in the hurricane refer to maintenance to split curcuit to resolve issue
Non-Outage | J.E.26.07.24450 | C001865426 | Rayon Foster | Hanover | Completed | Load_292700 | Orange Bay - 310 | Jul 26, 2026 5:18pm | Jul 26, 2026 5:18pm | Jul 27, 2026 9:24am | Jul 27, 2026 9:24am | Jul 27, 2026 10:00am | Jul 27, 2026 10:07am | Jul 27, 2026 10:08am | Jul 27, 2026 10:08am |  |  | Fair | No | When reach on location customer said he got his electrician to rectify the issue voltage in area 113/113AB226
Non-Outage | J.E.26.07.30381 | C001865425 | Rayon Foster | Hanover | Completed | Load_302748 | Orange Bay - 310 | Jul 26, 2026 5:18pm | Jul 26, 2026 5:18pm | Jul 26, 2026 7:02pm | Jul 26, 2026 7:02pm | Jul 26, 2026 7:52pm | Jul 26, 2026 7:58pm | Jul 26, 2026 8:01pm | Jul 26, 2026 8:01pm |  |  | Fair | No | Damage service wire and corroded joints was the cause of customer low voltage use about 25 feet of number 6 service wire, 3 linkets and 3 one bolt clamps for repair voltage left 113v/113v/226v
Non-Outage | J.E.26.07.31629 | C001865424 | Rayon Foster | Hanover | Completed | Load_264368 | Orange Bay - 310 | Jul 26, 2026 5:17pm | Jul 26, 2026 5:18pm | Jul 27, 2026 3:29pm | Jul 27, 2026 3:29pm | Jul 27, 2026 3:29pm | Jul 27, 2026 4:06pm | Jul 27, 2026 4:07pm | Jul 27, 2026 4:07pm |  |  | Rains | No | Corrosion on jps pole remake joints using two clamps voltage after changing clamps 110/109AB219
Non-Outage | J.E.26.07.32055 | C001865423 | Rayon Foster | Hanover | Completed | Load_265958 | Orange Bay - 310 | Jul 26, 2026 5:17pm | Jul 26, 2026 5:18pm | Jul 27, 2026 11:07am | Jul 27, 2026 1:05pm | Jul 27, 2026 1:05pm | Jul 27, 2026 1:17pm | Jul 27, 2026 1:17pm | Jul 27, 2026 1:17pm |  |  | Fair | No | Found working ok voltage check on meter up on arrival 113/113AB226 volts
Outage | J.E.26.07.32197 | C001865422 | Jowayne Newmans | Portland | Completed | Load_247147 | Port Antonio - 410 | Jul 26, 2026 5:05pm | Jul 26, 2026 5:07pm | Jul 26, 2026 5:40pm | Jul 26, 2026 5:40pm | Jul 26, 2026 6:58pm | Jul 26, 2026 8:35pm | Jul 26, 2026 8:36pm | Jul 26, 2026 8:36pm |  |  | Fair | No | Patrol and found cell site without electricity cause by burnt down 2 north twisted service wire, repair by splicing and retention conductor using 15ft of twisted service wire and 6 one bolt clamps. Cell site now has electricity.
Non-Outage | J.E.26.07.32219 | C001865421 | Fitzroy Turner | KSAS | Completed | Load_265686 | Greenwich - 410 | Jul 26, 2026 5:02pm | Jul 26, 2026 5:09pm | Jul 26, 2026 5:52pm | Jul 26, 2026 5:52pm | Jul 26, 2026 5:52pm | Jul 26, 2026 5:53pm | Jul 26, 2026 5:54pm | Jul 26, 2026 5:54pm |  |  | Fair | No | Found bank of three 25kva transformer one fuse blown replace with one 3 amps fuse supply restored to customer
Non-Outage | J.E.26.07.32089 | C001865416 | Milton Charlton | KSAN | Completed | Load_248033 | Washington Blvd - 610 | Jul 26, 2026 4:29pm | Jul 26, 2026 4:30pm | Jul 26, 2026 4:54pm | Jul 26, 2026 4:54pm | Jul 26, 2026 5:17pm | Jul 26, 2026 5:20pm | Jul 26, 2026 5:19pm | Jul 26, 2026 5:19pm |  |  | Fair | No | Customer meter #2444983 burnt on one side and single phasing. Meter need to be changed. Refer to field service.
Outage | J.E.26.07.32187 | C001865415 | Milton Charlton | KSAN | Completed | Load_265279 | Hope - 510 | Jul 26, 2026 4:29pm | Jul 26, 2026 4:30pm | Jul 26, 2026 5:17pm | Jul 26, 2026 5:19pm | Jul 26, 2026 6:28pm | Jul 26, 2026 6:35pm | Jul 26, 2026 6:31pm | Jul 26, 2026 6:31pm |  |  | Fair | No | Customer service wire #6 duplex phase corroded at pole. Repair using one 1- bolt clamp. Readings at pothead 117 volts.
Non-Outage | J.E.26.07.30996 | C001865414 | Edward Royal | KSAN | Completed | Load_244974 | Constant Spring - 210 | Jul 26, 2026 4:26pm | Jul 26, 2026 4:29pm | Jul 26, 2026 8:13pm | Jul 26, 2026 8:13pm | Jul 26, 2026 8:13pm | Jul 26, 2026 8:14pm | Jul 26, 2026 8:14pm | Jul 26, 2026 8:14pm |  |  | Fair | No | Premises found close call related
Non-Outage | J.E.26.07.31087 | C001865413 | Edward Royal | KSAN | Completed | Load_257446 | Constant Spring - 210 | Jul 26, 2026 4:26pm | Jul 26, 2026 4:29pm | Jul 26, 2026 8:56pm | Jul 26, 2026 8:56pm | Jul 26, 2026 8:56pm | Jul 26, 2026 8:59pm | Jul 26, 2026 8:59pm | Jul 26, 2026 8:59pm |  |  | Fair | No | Premises found ok voltage reading 236 118 119 v
Outage | J.E.26.07.32180 | C001865412 | Nickolas Rodriques | St.Catherine | Completed | Load_240388 | Twickenham - 210 | Jul 26, 2026 4:12pm | Jul 26, 2026 4:13pm | Jul 26, 2026 4:17pm | Jul 26, 2026 4:35pm | Jul 26, 2026 5:01pm | Jul 26, 2026 6:04pm | Jul 26, 2026 6:15pm | Jul 26, 2026 6:15pm | Fire |  | Fair | No | No fire was seen upon arrival. Customer stated that she is without power, reading found at meter (118). Checks were done and it was found that the customer meter socket is defective. Customer was advised to consult an Electrician to do repairs.
Outage | J.E.26.07.32175 | C001865411 | Kemark Slue | St.Catherine | Completed | Load_252776 | Tredegar - 510 | Jul 26, 2026 4:11pm | Jul 27, 2026 7:21am | Jul 27, 2026 7:53am | Jul 27, 2026 7:53am | Jul 27, 2026 9:47am | Jul 27, 2026 8:41am | Jul 27, 2026 10:51am | Jul 27, 2026 10:51am |  |  | Fair | No | Upon arrival at the location the crew discovered that 10 kva 13.8 kv transformer fuse was blown resulting from creepers that had came in contact with switch bottom, cut and remove creepers from pole, refuse link and re-energized circuit.
Non-Outage | J.E.26.07.31652 | C001865410 | Edward Royal | KSAN | Completed | Load_255830 | Constant Spring - 210 | Jul 26, 2026 4:05pm | Jul 26, 2026 4:29pm | Jul 26, 2026 8:11pm | Jul 26, 2026 8:11pm | Jul 26, 2026 8:11pm | Jul 26, 2026 8:13pm | Jul 26, 2026 8:13pm | Jul 26, 2026 8:13pm |  |  | Fair | No | When contacted customer said that the time is too late and she want to go to bed requesting daylight visit
Outage | J.E.26.07.32163 | C001865407 | Edward Royal | KSAN | Completed | Load_239951 | Washington Blvd - 410 | Jul 26, 2026 4:01pm | Jul 26, 2026 4:01pm | Jul 26, 2026 7:18pm | Jul 26, 2026 8:10pm | Jul 26, 2026 8:10pm | Jul 26, 2026 8:10pm | Jul 26, 2026 8:11pm | Jul 26, 2026 8:11pm |  |  | Fair | No | When contacted customer said that the premises is close
Outage | J.E.26.07.32147 | C001865405 | Fitzroy Turner | KSAS | Completed | Load_255198 | Three Miles - 510 | Jul 26, 2026 4:00pm | Jul 26, 2026 4:01pm | Jul 26, 2026 5:10pm | Jul 26, 2026 5:54pm | Jul 26, 2026 6:31pm | Jul 26, 2026 7:25pm | Jul 26, 2026 7:26pm | Jul 26, 2026 7:26pm |  |  | Fair | No | 611157 pole found bank of two transformer one 100kva and one 50kva drop lead burnt off cause fuse to blown and illegal connections use one clamp and one 10amps fuse to carry out repair supply restored to areas
Outage | J.E.26.07.32153 | C001865404 | Marlon Brown | Trelawny | Completed | Load_251614 | Martha Brae - 210 | Jul 26, 2026 4:00pm | Jul 26, 2026 4:01pm | Jul 26, 2026 4:50pm | Jul 26, 2026 4:50pm | Jul 26, 2026 4:50pm | Jul 26, 2026 4:51pm | Jul 26, 2026 4:51pm | Jul 26, 2026 4:51pm |  |  | Fair | No | Feeder issue
Outage | J.E.26.07.32165 | C001865406 | Marlon Brown | Trelawny | Completed | Load_264891 | Duncans - 110 | Jul 26, 2026 4:00pm | Jul 26, 2026 4:01pm | Jul 26, 2026 4:14pm | Jul 26, 2026 4:14pm | Jul 26, 2026 4:49pm | Jul 26, 2026 4:49pm | Jul 26, 2026 4:49pm | Jul 26, 2026 4:49pm |  |  | Fair | No | Feeder issue
Outage | J.E.26.07.32157 | C001865402 | Fitzroy Turner | KSAS | Completed | Load_289968 | Hunts Bay - 410 | Jul 26, 2026 3:59pm | Jul 26, 2026 4:01pm | Jul 26, 2026 7:26pm | Jul 26, 2026 7:26pm | Jul 26, 2026 7:27pm | Jul 26, 2026 7:28pm | Jul 26, 2026 7:29pm | Jul 26, 2026 7:29pm |  |  | Fair | No | Supply restored after replace blown 10amps fuse in 100kva transformer
Outage | J.E.26.07.32164 | C001865403 | Marlon Brown | Trelawny | Completed | Load_239800 | Greenwood - 210 | Jul 26, 2026 3:59pm | Jul 26, 2026 4:01pm | Jul 26, 2026 4:51pm | Jul 26, 2026 4:51pm | Jul 26, 2026 5:35pm | Jul 26, 2026 6:11pm | Jul 26, 2026 6:11pm | Jul 26, 2026 6:11pm | BrokenWire |  | Fair | No | Refer to maintenance personnel, maintenance are aware of situation.
Outage | J.E.26.07.32131 | C001865399 | Fitzroy Turner | KSAS | Completed | Load_253227 | Cane River - 610 | Jul 26, 2026 3:54pm | Jul 26, 2026 3:57pm | Jul 26, 2026 4:01pm | Jul 26, 2026 4:01pm | Jul 26, 2026 4:56pm | Jul 26, 2026 5:02pm | Jul 26, 2026 5:05pm | Jul 26, 2026 5:05pm |  |  | Fair | No | Found switches top jumper burnt off at underground cables switches # LAB412 have switch top remade using one 2/0 to 2/0 ampact to carry out repair supply restored to areas
Outage | J.E.26.07.32138 | C001865400 | Fitzroy Turner | KSAS | Completed | Load_244455 | Cane River - 610 | Jul 26, 2026 3:54pm | Jul 26, 2026 3:57pm | Jul 26, 2026 5:02pm | Jul 26, 2026 5:08pm | Jul 26, 2026 5:08pm | Jul 26, 2026 5:08pm | Jul 26, 2026 5:10pm | Jul 26, 2026 5:10pm |  |  | Fair | No | Supply restored to the areas after remake switches top jumper at LAB 6 -412
Outage | J.E.26.07.32152 | C001865401 | Fitzroy Turner | KSAS | Completed | Load_254610 | Cane River - 610 | Jul 26, 2026 3:54pm | Jul 26, 2026 3:57pm | Jul 26, 2026 5:01pm | Jul 26, 2026 5:05pm | Jul 26, 2026 5:05pm | Jul 26, 2026 5:05pm | Jul 26, 2026 5:08pm | Jul 26, 2026 5:08pm |  |  | Fair | No | Supply restored to port royal after repairs was carried out by switch pole LAB 6-412 repair burnt off jumper at cable pole
Outage | J.E.26.07.32120 | C001865396 | Javid Vernon | Westmoreland | Completed | Load_292670 | Paradise - 310 | Jul 26, 2026 3:40pm | Jul 26, 2026 4:57pm | Jul 26, 2026 5:01pm | Jul 26, 2026 5:03pm | Jul 26, 2026 7:14pm | Jul 26, 2026 8:39pm | Jul 26, 2026 8:40pm | Jul 26, 2026 8:40pm |  |  | Fair | No | Cut and remove tree limb on single phase primary line and refuse 1 20amp junction fuse
Outage | J.E.26.07.32079 | C001865394 | Ryan Richards | Manchester | Completed | Load_254646 | Spur Tree - 310 | Jul 26, 2026 3:36pm | Jul 26, 2026 3:37pm | Jul 26, 2026 3:47pm | Jul 26, 2026 3:47pm | Jul 26, 2026 4:44pm | Jul 26, 2026 5:51pm | Jul 26, 2026 5:52pm | Jul 26, 2026 5:52pm |  |  | Fair | No | Corroded phase and neutral found at pothead and pole remade phase using 3 one bolt clamps and 3 penunion voltage 111/114/229 volts
Outage | J.E.26.07.32137 | C001865395 | Ryan Richards | Manchester | Completed | Load_260683 | Kendal - 310 | Jul 26, 2026 3:36pm | Jul 26, 2026 3:37pm | Jul 26, 2026 5:52pm | Jul 26, 2026 5:52pm | Jul 26, 2026 7:09pm | Jul 26, 2026 8:18pm | Jul 26, 2026 8:18pm | Jul 26, 2026 8:18pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.32060 | C001865393 | Wayne Dillion | St.Elizabeth | Completed | Load_292295 | Maggotty - 110 | Jul 26, 2026 3:31pm | Jul 26, 2026 3:35pm | Jul 26, 2026 5:02pm | Jul 26, 2026 5:03pm | Jul 26, 2026 5:03pm | Jul 26, 2026 5:33pm | Jul 26, 2026 5:40pm | Jul 26, 2026 5:40pm |  |  | Fair | No | Supply check and found no service wire. Connect same using 100ft of #6 triplex service wire, 3 clamps and 3 linkets. Supply leave working okay reading 110v, 111v and cross phase 222volts.
Outage | J.E.26.07.32154 | C001865392 | Andrew Powell | St.Elizabeth | Completed | Load_256294 | Maggotty - 210 | Jul 26, 2026 3:31pm | Jul 26, 2026 3:35pm | Jul 26, 2026 3:53pm | Jul 26, 2026 3:56pm | Jul 26, 2026 4:15pm | Jul 26, 2026 4:37pm | Jul 26, 2026 4:41pm | Jul 26, 2026 4:41pm |  |  | Fair | No | Remade corroded service wire neutral joint at secondary line 3 wire using one clamp, voltage reading 108v-108v phase to neutral 216v cross phase.
Non-Outage | J.E.26.06.06931 | C001865386 | Hartley Chin | St.Catherine | Completed | Load_556346 | Rhodens Pen - 210 | Jul 26, 2026 3:30pm | Jul 26, 2026 3:32pm | Jul 26, 2026 5:59pm | Jul 26, 2026 7:13pm | Jul 26, 2026 7:42pm | Jul 26, 2026 7:42pm | Jul 26, 2026 7:46pm | Jul 26, 2026 7:46pm |  |  | Fair | No | Customer stated she didn’t made any report…
Non-Outage | J.E.26.06.08654 | C001865387 | Hartley Chin | St.Catherine | Completed | Load_302298 | Rhodens Pen - 210 | Jul 26, 2026 3:30pm | Jul 26, 2026 3:32pm | Jul 26, 2026 10:11pm | Jul 26, 2026 10:11pm | Jul 26, 2026 11:01pm | Jul 26, 2026 11:01pm | Jul 26, 2026 11:22pm | Jul 26, 2026 11:22pm |  |  | Fair | No | Found okay …voltage read 114v , 112v ..
Non-Outage | J.E.26.06.08702 | C001865388 | Hartley Chin | St.Catherine | Completed | Load_256389 | Rhodens Pen - 210 | Jul 26, 2026 3:30pm | Jul 26, 2026 3:32pm | Jul 26, 2026 7:46pm | Jul 26, 2026 7:46pm | Jul 26, 2026 7:46pm | Jul 26, 2026 7:46pm | Jul 26, 2026 7:47pm | Jul 26, 2026 7:47pm |  |  | Fair | No | Customer stated issue was resolved…
Non-Outage | J.E.26.06.08814 | C001865389 | Hartley Chin | St.Catherine | Completed | Load_260217 | Rhodens Pen - 210 | Jul 26, 2026 3:30pm | Jul 26, 2026 3:32pm | Jul 26, 2026 9:29pm | Jul 26, 2026 9:29pm | Jul 26, 2026 10:09pm | Jul 26, 2026 10:10pm | Jul 26, 2026 10:11pm | Jul 26, 2026 10:11pm |  |  | Fair | No | Customer stated she did make any report…
Non-Outage | J.E.26.06.09863 | C001865390 | Hartley Chin | St.Catherine | Completed | Load_247071 | Rhodens Pen - 210 | Jul 26, 2026 3:30pm | Jul 26, 2026 3:32pm | Jul 26, 2026 7:51pm | Jul 26, 2026 7:52pm | Jul 26, 2026 7:52pm | Jul 26, 2026 7:53pm | Jul 26, 2026 7:53pm | Jul 26, 2026 7:53pm |  |  | Fair | No | Found okay , voltage read 112v , 114v
Non-Outage | J.E.26.06.11741 | C001865391 | Hartley Chin | St.Catherine | Completed | Load_302294 | Rhodens Pen - 210 | Jul 26, 2026 3:30pm | Jul 26, 2026 3:32pm | Jul 26, 2026 7:50pm | Jul 26, 2026 7:56pm | Jul 26, 2026 9:26pm | Jul 26, 2026 9:26pm | Jul 26, 2026 9:29pm | Jul 26, 2026 9:29pm |  |  | Fair | No | Prem not found … unable to contact customer with contact # provided …
Non-Outage | J.E.26.06.05204 | C001865385 | Hartley Chin | St.Catherine | Completed | Load_252474 | Rhodens Pen - 210 | Jul 26, 2026 3:29pm | Jul 26, 2026 3:32pm | Jul 26, 2026 5:59pm | Jul 26, 2026 5:59pm | Jul 26, 2026 7:12pm | Jul 26, 2026 7:13pm | Jul 26, 2026 7:13pm | Jul 26, 2026 7:13pm |  |  | Fair | No | Found okay .. customer stated that supply was restored…
Non-Outage | J.E.26.03.27305 | C001865383 | Ricky Hall | null | Completed | null | null | Jul 26, 2026 3:26pm | Jul 26, 2026 3:27pm | Jul 26, 2026 3:53pm | Jul 26, 2026 4:43pm | Jul 26, 2026 5:55pm | Jul 26, 2026 7:18pm | Jul 26, 2026 7:20pm | Jul 26, 2026 7:20pm |  |  | Fair | No | Make jumper for corroded marriage joint on upper phase use 2 clamps( customer also advised to carry out or on load side of line as defects were pointed out)1120/120/240 in meter socket
Outage | J.E.26.07.32096 | C001865382 | Marlon Brown | St.James | Completed | Load_247261 | Bogue - 310 | Jul 26, 2026 3:24pm | Jul 26, 2026 4:01pm | Jul 26, 2026 4:49pm | Jul 26, 2026 4:49pm | Jul 26, 2026 4:49pm | Jul 26, 2026 4:50pm | Jul 26, 2026 4:50pm | Jul 26, 2026 4:50pm |  |  | Fair | No | Feeder issue
Outage | J.E.26.07.32151 | C001865381 | Michael Christian | St.James | Completed | Load_1002485 | Bogue - 310 | Jul 26, 2026 3:24pm | Jul 26, 2026 3:25pm | Jul 26, 2026 7:14pm | Jul 26, 2026 7:14pm | Jul 26, 2026 7:14pm | Jul 26, 2026 7:19pm | Jul 26, 2026 7:20pm | Jul 26, 2026 7:20pm |  |  | Rains | No | Internal fault voltage 110 109 222 at pothead
Non-Outage | J.E.26.07.27918 | C001865379 | Nickolas Rodriques | null | Completed | null | null | Jul 26, 2026 3:13pm | Jul 26, 2026 3:16pm | Jul 26, 2026 7:48pm | Jul 26, 2026 8:00pm | Jul 26, 2026 8:35pm | Jul 26, 2026 10:18pm | Jul 26, 2026 10:20pm | Jul 26, 2026 10:20pm | BrokenPole |  | Fair | No | Customer is reporting a defective streetlight. Refer to streetlight department.
Non-Outage | J.E.26.07.29154 | C001865380 | Wan Carlos Scarlett | null | Completed | null | null | Jul 26, 2026 3:13pm | Jul 26, 2026 3:16pm | Jul 26, 2026 9:48pm | Jul 26, 2026 9:48pm | Jul 26, 2026 10:59pm | Jul 27, 2026 3:18pm | Jul 27, 2026 3:18pm | Jul 27, 2026 3:18pm |  |  | Fair | No | Customer was reconnected from escalation department power supply has been restored
Outage | J.E.26.07.31199 | C001865376 | Rayon Foster | Hanover | Completed | Load_253619 | Orange Bay - 310 | Jul 26, 2026 2:37pm | Jul 26, 2026 2:37pm | Jul 26, 2026 2:49pm | Jul 26, 2026 3:09pm | Jul 26, 2026 3:49pm | Jul 26, 2026 4:20pm | Jul 26, 2026 4:21pm | Jul 26, 2026 4:21pm |  |  | Rains | No | Corrosion on jps pole was the cause of no supply remake joints on pole using two clamps voltage after repair 113/113AB227volts
Outage | J.E.26.07.32109 | C001865373 | Raymond Carr | St.Mary | Completed | Load_251110 | Oracabessa - 110 | Jul 26, 2026 2:26pm | Jul 26, 2026 2:26pm | Jul 26, 2026 2:47pm | Jul 26, 2026 2:47pm | Jul 26, 2026 2:54pm | Jul 26, 2026 2:49pm | Jul 26, 2026 3:01pm | Jul 26, 2026 3:01pm |  |  | Fair | No | Supply found okay.
Non-Outage | J.E.26.03.39246 | C001865370 | Hartley Chin | St.Catherine | Completed | Load_573724 | Rhodens Pen - 310 | Jul 26, 2026 2:16pm | Jul 26, 2026 2:18pm | Jul 26, 2026 2:42pm | Jul 26, 2026 2:44pm | Jul 26, 2026 4:24pm | Jul 26, 2026 4:42pm | Jul 26, 2026 4:43pm | Jul 26, 2026 4:43pm | LeaningPole |  | Fair | No | Ref to maintenance !!! Found leaning 40ft T/D/E pole with 3 phase Primary and neutral , pole foot is okay , customer only needs pole to be straighten … Note : customer supply is okay …
Non-Outage | J.E.26.07.20448 | C001865367 | Hartley Chin | null | Completed | null | null | Jul 26, 2026 2:04pm | Jul 26, 2026 2:18pm | Jul 26, 2026 4:44pm | Jul 26, 2026 4:44pm | Jul 26, 2026 5:19pm | Jul 26, 2026 5:58pm | Jul 26, 2026 5:59pm | Jul 26, 2026 5:59pm | LowHangingWires |  | Fair | No | Prem not found … unable to contact customer with contact # provided…
Non-Outage | J.E.26.04.18443 | C001865365 | Richard Nicholas | St.Catherine | Completed | Load_249307 | Tredegar - 510 | Jul 26, 2026 2:01pm | Jul 26, 2026 2:01pm | Jul 26, 2026 3:35pm | Jul 26, 2026 3:35pm | Jul 26, 2026 4:13pm | Jul 26, 2026 4:41pm | Jul 26, 2026 4:42pm | Jul 26, 2026 4:42pm | BrokenPole |  | Fair | No | Area found ok,no broken pole seen.
Non-Outage | J.E.26.07.20422 | C001865363 | Richard Nicholas | St.Catherine | Completed | Load_264044 | Tredegar - 210 | Jul 26, 2026 2:00pm | Jul 26, 2026 2:00pm | Jul 26, 2026 4:43pm | Jul 26, 2026 6:13pm | Jul 26, 2026 7:11pm | Jul 26, 2026 7:40pm | Jul 26, 2026 7:42pm | Jul 26, 2026 7:42pm | BrokenPole |  | Fair | No | Found ok,no broken pole seen.
Non-Outage | J.E.26.07.22527 | C001865364 | Richard Nicholas | St.Catherine | Completed | Load_260421 | Tredegar - 310 | Jul 26, 2026 2:00pm | Jul 26, 2026 2:00pm | Jul 27, 2026 9:41am | Jul 27, 2026 9:41am | Jul 27, 2026 10:59am | Jul 27, 2026 11:49am | Jul 27, 2026 11:52am | Jul 27, 2026 11:52am | BrokenPole |  | Fair | No | 40ft class 6 T- construction with open secondary and single phase primary,found broken in the half of the pole.pole also need to relocate from the location because it is presently on private property.follow up required.
Non-Outage | J.E.26.03.37079 | C001865362 | Richard Nicholas | null | Completed | null | null | Jul 26, 2026 1:59pm | Jul 26, 2026 2:00pm | Jul 26, 2026 4:45pm | Jul 26, 2026 4:45pm | Jul 26, 2026 6:12pm | Jul 26, 2026 6:12pm | Jul 26, 2026 6:13pm | Jul 26, 2026 6:13pm | BrokenPole |  | Fair | No | Area found ok,broken pole was replaced more than a month ago
Outage | J.E.26.07.32098 | C001865361 | Jowayne Newmans | Portland | Completed | Load_252048 | Port Antonio - 410 | Jul 26, 2026 1:59pm | Jul 26, 2026 2:01pm | Jul 26, 2026 2:20pm | Jul 26, 2026 2:20pm | Jul 26, 2026 2:21pm | Jul 26, 2026 2:21pm | Jul 26, 2026 2:21pm | Jul 26, 2026 2:21pm |  |  | Fair | No | Customer stated that they have supply.
Non-Outage | J.E.26.07.27282 | C001865359 | Richard Nicholas | St.Catherine | Completed | Load_254602 | Tredegar - 310 | Jul 26, 2026 1:57pm | Jul 26, 2026 1:57pm | Jul 26, 2026 9:00pm | Jul 26, 2026 9:00pm | Jul 26, 2026 9:52pm | Jul 26, 2026 10:58pm | Jul 26, 2026 11:00pm | Jul 26, 2026 11:00pm | BrokenWire |  | EarthMovement | No | Cut and splice defective # triplex Rammy service wire.2 clamp and 4linket was used.voltage reading 118x2 and 236v.
Non-Outage | J.E.26.07.31890 | C001865360 | Oshane Warren | Westmoreland | Completed | Load_244663 | Paradise - 110 | Jul 26, 2026 1:57pm | Jul 26, 2026 1:58pm | Jul 26, 2026 2:04pm | Jul 26, 2026 2:04pm | Jul 26, 2026 2:04pm | Jul 26, 2026 2:11pm | Jul 26, 2026 2:12pm | Jul 26, 2026 2:12pm |  |  | Fair | No | Replace 15amp junction fuse voltage 228 233 247 408 426 391
Non-Outage | J.E.26.07.22501 | C001865358 | Neville Spencer | St.Catherine | Completed | Load_268479 | Rhodens Pen - 310 | Jul 26, 2026 1:56pm | Jul 26, 2026 1:57pm | Jul 26, 2026 3:31pm | Jul 26, 2026 3:31pm | Jul 26, 2026 4:26pm | Jul 26, 2026 4:28pm | Jul 26, 2026 4:28pm | Jul 26, 2026 4:28pm | Fire |  | Fair | No | Unable to locate customer.
Non-Outage | J.E.26.07.29205 | C001865357 | Neville Spencer | St.Catherine | Completed | Load_252011 | Rhodens Pen - 310 | Jul 26, 2026 1:56pm | Jul 26, 2026 1:57pm | Jul 26, 2026 2:35pm | Jul 26, 2026 2:35pm | Jul 26, 2026 3:04pm | Jul 26, 2026 3:04pm | Jul 26, 2026 3:31pm | Jul 26, 2026 3:31pm | Fire |  | Fair | No | Remade burnt out clamp on phase joint at secondary on 3, wire service used 2, clamps voltage reading 114 117 232 supply restored.
Non-Outage | J.E.26.07.30943 | C001865354 | Milton Charlton | KSAN | Completed | Load_256996 | Washington Blvd - 510 | Jul 26, 2026 1:48pm | Jul 26, 2026 1:48pm | Jul 26, 2026 3:43pm | Jul 26, 2026 3:48pm | Jul 26, 2026 3:48pm | Jul 26, 2026 4:50pm | Jul 26, 2026 4:50pm | Jul 26, 2026 4:50pm |  |  | Fair | No | Customer service wire #6 triplex phase and neutral burn off at pole . Repair using 10ft #6 triplex and three 1- bolt clamps. Readings at meter socket 118-118-236 volts.
Non-Outage | J.E.26.07.31334 | C001865355 | Edward Royal | KSAN | Completed | Load_256996 | Washington Blvd - 510 | Jul 26, 2026 1:48pm | Jul 26, 2026 4:29pm | Jul 26, 2026 8:41pm | Jul 26, 2026 8:41pm | Jul 26, 2026 8:41pm | Jul 26, 2026 8:42pm | Jul 26, 2026 8:42pm | Jul 26, 2026 8:42pm |  |  | Fair | No | Premises found ok voltage reading 238 119 119 v
Non-Outage | J.E.26.07.32023 | C001865353 | Edward Royal | null | Completed | null | null | Jul 26, 2026 1:40pm | Jul 26, 2026 1:40pm | Jul 26, 2026 2:37pm | Jul 26, 2026 2:37pm | Jul 26, 2026 3:21pm | Jul 26, 2026 3:38pm | Jul 26, 2026 3:38pm | Jul 26, 2026 3:38pm | Fire |  | Fair | No | Customer have internal problems customer have faulty wiring advise customer to get a electrician to fix the problem voltage reading 116 v
Non-Outage | J.E.26.07.32053 | C001865352 | Edward Royal | KSAS | Completed | Load_258629 | Hunts Bay - 310 | Jul 26, 2026 1:40pm | Jul 26, 2026 1:40pm | Jul 26, 2026 3:38pm | Jul 26, 2026 3:38pm | Jul 26, 2026 3:38pm | Jul 26, 2026 3:39pm | Jul 26, 2026 3:39pm | Jul 26, 2026 3:39pm | Fire |  | Fair | No | Call related
Outage | J.E.26.07.32074 | C001865351 | Edward Royal | KSAN | Completed | Load_575335 | Washington Blvd - 710 | Jul 26, 2026 1:31pm | Jul 26, 2026 1:32pm | Jul 26, 2026 2:00pm | Jul 26, 2026 2:00pm | Jul 26, 2026 2:00pm | Jul 26, 2026 2:03pm | Jul 26, 2026 2:03pm | Jul 26, 2026 2:03pm |  |  | Fair | No | Meter not responding meter need to be check reffered to field service
Non-Outage | J.E.26.07.06688 | C001865348 | Hopeton Henry | St.Thomas | Completed | Load_568168 | Good Year - 110 | Jul 26, 2026 1:27pm | Jul 26, 2026 1:27pm | Jul 26, 2026 2:51pm | Jul 26, 2026 2:51pm | Jul 26, 2026 3:51pm | Jul 26, 2026 6:40pm | Jul 26, 2026 6:41pm | Jul 26, 2026 6:41pm |  |  | Fair | Yes | Splice broken service wire 113-110-223
Non-Outage | J.E.26.07.07177 | C001865349 | Hopeton Henry | St.Thomas | Completed | Load_252941 | Good Year - 110 | Jul 26, 2026 1:27pm | Jul 26, 2026 1:28pm | Jul 26, 2026 6:45pm | Jul 27, 2026 12:36pm | Jul 27, 2026 12:37pm | Jul 27, 2026 12:37pm | Jul 27, 2026 12:43pm | Jul 27, 2026 12:43pm |  |  | Fair | No | Check and found ok , customer confirmed
Non-Outage | J.E.26.07.08653 | C001865350 | Hopeton Henry | St.Thomas | Completed | Load_263661 | Good Year - 110 | Jul 26, 2026 1:27pm | Jul 26, 2026 1:28pm | Jul 26, 2026 6:45pm | Jul 26, 2026 6:45pm | Jul 26, 2026 6:45pm | Jul 26, 2026 6:45pm | Jul 26, 2026 6:47pm | Jul 26, 2026 6:47pm | LeaningPole |  | Fair | No | Check and found rotten secondary pole 35 ft open secondary refer to maintenance customer as supply
Non-Outage | J.E.26.07.14800 | C001865347 | Hopeton Henry | St.Thomas | Completed | Load_264983 | Good Year - 210 | Jul 26, 2026 1:27pm | Jul 26, 2026 1:27pm | Jul 26, 2026 6:45pm | Jul 26, 2026 9:52pm | Jul 26, 2026 9:52pm | Jul 26, 2026 9:52pm | Jul 26, 2026 9:52pm | Jul 26, 2026 9:52pm |  |  | Fair | No | Customer not located
Outage | J.E.26.07.32062 | C001865346 | Oshane Warren | Westmoreland | Completed | Load_246407 | Paradise - 110 | Jul 26, 2026 1:21pm | Jul 26, 2026 1:22pm | Jul 26, 2026 2:13pm | Jul 26, 2026 2:13pm | Jul 26, 2026 2:13pm | Jul 26, 2026 2:40pm | Jul 26, 2026 2:41pm | Jul 26, 2026 2:41pm | Fire |  | Fair | No | Change defective clamps from service wire at secondary line
Outage | J.E.26.07.32019 | C001865345 | Nickolas Rodriques | St.Catherine | Completed | Load_241449 | Twickenham - 210 | Jul 26, 2026 1:13pm | Jul 26, 2026 1:15pm | Jul 26, 2026 6:18pm | Jul 26, 2026 6:27pm | Jul 26, 2026 7:18pm | Jul 26, 2026 7:46pm | Jul 26, 2026 7:47pm | Jul 26, 2026 7:47pm |  |  | Fair | No | Customer stated that she is without power supply. Reading found (114-113-227). Checks were done which revealed that the customer is having internal issues. The customer was advised to consult an Electrician to do repairs.
Outage | J.E.26.07.32045 | C001865343 | Wan Carlos Scarlett | Portmore | Completed | Load_269641 | Naggo Head - 510 | Jul 26, 2026 1:12pm | Jul 26, 2026 1:13pm | Jul 26, 2026 5:07pm | Jul 26, 2026 7:03pm | Jul 26, 2026 7:29pm | Jul 26, 2026 7:32pm | Jul 26, 2026 7:32pm | Jul 26, 2026 7:32pm | Fire |  | Fair | No | Customer confirm that power supply has been restored
Outage | J.E.26.07.32058 | C001865344 | Wan Carlos Scarlett | Portmore | Completed | Load_256866 | Naggo Head - 510 | Jul 26, 2026 1:12pm | Jul 26, 2026 1:13pm | Jul 26, 2026 4:31pm | Jul 26, 2026 4:31pm | Jul 26, 2026 4:31pm | Jul 26, 2026 6:59pm | Jul 26, 2026 7:03pm | Jul 26, 2026 7:03pm |  |  | Fair | No | Found 2 span of open secondary line phase and neutral burn down use 250ft of # 2 loom wire use 2 splicing sleeve 6 one bolt clamps at pole refuse 25kVA transformer with a 3amp fuse pole # 015506
Outage | J.E.26.07.32040 | C001865341 | Edward Royal | KSAS | Completed | Load_244079 | Greenwich - 310 | Jul 26, 2026 12:41pm | Jul 26, 2026 12:43pm | Jul 26, 2026 3:39pm | Jul 26, 2026 3:39pm | Jul 26, 2026 7:51pm | Jul 26, 2026 8:09pm | Jul 26, 2026 8:10pm | Jul 26, 2026 8:10pm |  |  | Fair | No | Replaced 2 30A junction fuse
Non-Outage | J.E.26.07.29377 | C001865338 | Javid Vernon | Westmoreland | Completed | Load_245673 | Paradise - 310 | Jul 26, 2026 12:36pm | Jul 26, 2026 12:37pm | Jul 26, 2026 1:28pm | Jul 26, 2026 1:28pm | Jul 26, 2026 1:28pm | Jul 26, 2026 1:31pm | Jul 26, 2026 1:32pm | Jul 26, 2026 1:32pm |  |  | Fair | No | Unable to locate are contact customer phone number is not ringing and no directions was given
Non-Outage | J.E.26.07.32010 | C001865335 | Jowayne Newmans | Portland | Completed | Load_248592 | Port Antonio - 310 | Jul 26, 2026 12:18pm | Jul 26, 2026 12:22pm | Jul 26, 2026 1:03pm | Jul 26, 2026 1:03pm | Jul 26, 2026 2:01pm | Jul 26, 2026 2:01pm | Jul 26, 2026 2:19pm | Jul 26, 2026 2:19pm |  |  | Fair | No | Patrol and found customer meter single phasing and need to be replaced, refer call to field service for meter to be changed. Voltage reading at meter socket 118v, 119v, 239v.
Non-Outage | J.E.26.07.31943 | C001865333 | Michael Christian | St.James | Completed | Load_250412 | Bogue - 310 | Jul 26, 2026 12:09pm | Jul 26, 2026 12:09pm | Jul 26, 2026 1:16pm | Jul 26, 2026 1:16pm | Jul 26, 2026 1:37pm | Jul 26, 2026 1:42pm | Jul 26, 2026 1:42pm | Jul 26, 2026 1:42pm |  |  | Rains | No | Found 1 100 kava out cause by lightning replace 1 10 amp in 100 kava
Outage | J.E.26.07.32002 | C001865332 | Elvis Trowers | KSAN | Completed | Load_261630 | Constant Spring - 210 | Jul 26, 2026 11:52am | Jul 26, 2026 11:59am | Jul 26, 2026 12:24pm | Jul 26, 2026 12:24pm | Jul 26, 2026 12:43pm | Jul 26, 2026 2:05pm | Jul 26, 2026 2:05pm | Jul 26, 2026 2:05pm | BrokenWire |  | Fair | Yes | Customer was found having single phasing when checked and defective twisted wire found about 40’ was used for splice and reconnect, voltage when check was left at 119+119=238 volts.
Outage | J.E.26.07.31952 | C001865331 | Ricky Hall | St.Catherine | Completed | Load_244765 | New Michelton - 410 | Jul 26, 2026 11:47am | Jul 26, 2026 11:49am | Jul 26, 2026 11:53am | Jul 26, 2026 11:53am | Jul 26, 2026 11:54am | Jul 26, 2026 11:55am | Jul 26, 2026 11:56am | Jul 26, 2026 11:56am |  |  | Fair | No | Replace blown15 amp junction fuse
Non-Outage | J.E.26.07.31988 | C001865330 | Neville Spencer | null | Completed | null | null | Jul 26, 2026 11:44am | Jul 26, 2026 11:51am | Jul 26, 2026 12:28pm | Jul 26, 2026 12:28pm | Jul 26, 2026 12:59pm | Jul 26, 2026 12:59pm | Jul 26, 2026 1:03pm | Jul 26, 2026 1:03pm |  |  | Fair | No | Found pump working.
Outage | J.E.26.07.31961 | C001865328 | Marlon Brown | Trelawny | Completed | Load_302607 | Martha Brae - 210 | Jul 26, 2026 11:30am | Jul 26, 2026 11:31am | Jul 26, 2026 2:40pm | Jul 26, 2026 2:41pm | Jul 26, 2026 3:32pm | Jul 26, 2026 3:34pm | Jul 26, 2026 3:34pm | Jul 26, 2026 3:34pm |  |  | Fair | No | Unable to locate customer via telephone nor direction
Outage | J.E.26.07.31970 | C001865329 | Marlon Brown | Trelawny | Completed | Load_1001505 | Duncans - 110 | Jul 26, 2026 11:30am | Jul 26, 2026 11:31am | Jul 26, 2026 1:45pm | Jul 26, 2026 1:45pm | Jul 26, 2026 2:31pm | Jul 26, 2026 2:40pm | Jul 26, 2026 2:40pm | Jul 26, 2026 2:40pm |  |  | Fair | No | Found ok, feeder issue. 120/120=240v.
Non-Outage | J.E.26.07.31344 | C001865324 | Michael Christian | St.James | Completed | Load_265743 | Queens Drive - 710 | Jul 26, 2026 11:24am | Jul 26, 2026 11:25am | Jul 26, 2026 11:46am | Jul 26, 2026 11:46am | Jul 26, 2026 1:07pm | Jul 26, 2026 1:16pm | Jul 26, 2026 1:16pm | Jul 26, 2026 1:16pm |  |  | Fair | No | Check and found okay voltage 111 114 227 at pothead
Non-Outage | J.E.26.07.31593 | C001865323 | Michael Christian | St.James | Completed | Load_1002045 | Queens Drive - 710 | Jul 26, 2026 11:24am | Jul 26, 2026 11:25am | Jul 26, 2026 12:02pm | Jul 26, 2026 3:03pm | Jul 26, 2026 3:25pm | Jul 26, 2026 3:27pm | Jul 26, 2026 3:27pm | Jul 26, 2026 3:27pm |  |  | Fair | No | Premises not found
Non-Outage | J.E.26.07.31884 | C001865326 | Michael Christian | St.James | Completed | Load_269852 | Queens Drive - 710 | Jul 26, 2026 11:24am | Jul 26, 2026 11:25am | Jul 26, 2026 1:42pm | Jul 26, 2026 1:42pm | Jul 26, 2026 2:39pm | Jul 26, 2026 3:00pm | Jul 26, 2026 3:00pm | Jul 26, 2026 3:00pm |  |  | Fair | No | Use 3 clamps at pole at customs services wires at pole voltage 109 107 225 at pothead
Non-Outage | J.E.26.07.31954 | C001865322 | Jowayne Newmans | Portland | Completed | Load_256293 | Port Antonio - 310 | Jul 26, 2026 11:21am | Jul 26, 2026 11:59am | Jul 26, 2026 2:21pm | Jul 26, 2026 2:21pm | Jul 26, 2026 3:06pm | Jul 26, 2026 3:25pm | Jul 26, 2026 3:26pm | Jul 26, 2026 3:26pm |  |  | Fair | No | Customer stated that they were having low voltage however did a voltage test at meter socket voltage reading was 118v, 118v, 236v. Advise customer to get an electrician to check their system.
Outage | J.E.26.07.31971 | C001865321 | Romaine Roberts | St.Mary | Completed | Load_245223 | Highgate - 210 | Jul 26, 2026 11:21am | Jul 26, 2026 11:22am | Jul 26, 2026 11:51am | Jul 26, 2026 11:51am | Jul 26, 2026 11:51am | Jul 26, 2026 12:38pm | Jul 26, 2026 12:38pm | Jul 26, 2026 12:38pm |  | Y | Fair | No | Open and close 25 kva transformer to splice and retention conductor also carryout bushing power restore
Outage | J.E.26.07.31976 | C001865320 | Elvis Trowers | KSAS | Completed | Load_578717 | Duhaney - 310 | Jul 26, 2026 11:19am | Jul 26, 2026 11:20am | Jul 26, 2026 2:06pm | Jul 26, 2026 2:06pm | Jul 26, 2026 2:46pm | Jul 26, 2026 3:03pm | Jul 26, 2026 3:03pm | Jul 26, 2026 3:03pm | BrokenWire |  | Fair | Yes | Reconnect dislodged twisted wire phase on pole with one, one bolt clamp voltage when checked was left at 117 +118=235 volts.
Non-Outage | J.E.26.07.31441 | C001865319 | Neville Spencer | Clarendon | Completed | Load_243848 | Monymusk - 210 | Jul 26, 2026 11:05am | Jul 26, 2026 11:05am | Jul 26, 2026 1:20pm | Jul 26, 2026 1:20pm | Jul 26, 2026 1:27pm | Jul 26, 2026 1:27pm | Jul 26, 2026 1:29pm | Jul 26, 2026 1:29pm |  |  | Fair | No | Renew blown 3 amp fuse protecting 25 kva xmf at pole # 0107501 supply restored.
Non-Outage | J.E.26.07.29417 | C001865316 | Neville Spencer | Clarendon | Completed | Load_241776 | Monymusk - 210 | Jul 26, 2026 11:04am | Jul 26, 2026 11:05am | Jul 26, 2026 1:29pm | Jul 26, 2026 1:29pm | Jul 26, 2026 2:04pm | Jul 26, 2026 2:04pm | Jul 26, 2026 2:33pm | Jul 26, 2026 2:33pm |  |  | Fair | No | Remade corrded phase joints at secondary on 3, wire service used 2 clamps voltage reading 118 119 237 supply restored,
Non-Outage | J.E.26.07.29430 | C001865318 | Neville Spencer | Clarendon | Completed | Load_248180 | Monymusk - 210 | Jul 26, 2026 11:04am | Jul 26, 2026 11:05am | Jul 26, 2026 1:04pm | Jul 26, 2026 1:04pm | Jul 26, 2026 1:18pm | Jul 26, 2026 1:18pm | Jul 26, 2026 1:20pm | Jul 26, 2026 1:20pm |  |  | Fair | No | Premises closed.
Outage | J.E.26.07.31877 | C001865317 | Ryan Richards | Manchester | Completed | Load_247000 | Spur Tree - 210 | Jul 26, 2026 11:04am | Jul 26, 2026 11:08am | Jul 26, 2026 12:45pm | Jul 26, 2026 1:13pm | Jul 26, 2026 2:06pm | Jul 26, 2026 3:42pm | Jul 26, 2026 3:42pm | Jul 26, 2026 3:42pm |  |  | Fair | No | Blown 10 amp junction fuse found line patrol nothing found lighting suspected to be the cause site now with supply
Non-Outage | J.E.26.07.29351 | C001865314 | Neville Spencer | Clarendon | Completed | Load_243507 | May Pen - 210 | Jul 26, 2026 11:03am | Jul 26, 2026 11:04am | Jul 26, 2026 11:12am | Jul 26, 2026 11:12am | Jul 26, 2026 12:24pm | Jul 26, 2026 12:25pm | Jul 26, 2026 12:25pm | Jul 26, 2026 12:25pm |  |  | Fair | No | Call resolved.
Outage | J.E.26.07.31935 | C001865313 | Shamour Haughton | St.James | Completed | Load_302425 | Bogue - 610 | Jul 26, 2026 11:03am | Jul 26, 2026 11:04am | Jul 26, 2026 11:24am | Jul 26, 2026 11:24am | Jul 26, 2026 12:25pm | Jul 26, 2026 1:30pm | Jul 26, 2026 1:34pm | Jul 26, 2026 1:34pm | BrokenWire |  | Fair | No | Found 2 pole span of secondary broken, isolate 2,25kva to splice and retention secondary using 40ft #2 conductor 3 clamps and 2#2 preform and reclose 2,25kva
Outage | J.E.26.07.31960 | C001865315 | Wayne Dillion | Manchester | Completed | Load_266329 | Spur Tree - 210 | Jul 26, 2026 11:03am | Jul 26, 2026 12:35pm | Jul 26, 2026 2:35pm | Jul 26, 2026 2:35pm | Jul 26, 2026 2:35pm | Jul 26, 2026 3:21am | Jul 26, 2026 3:23pm | Jul 26, 2026 3:23pm |  |  | Fair | No | Supply check and found contamination at pole. Repair same using 2 clamps. Supply leave working okay reading 116v, 116v and cross phase 232volts. Further checks reveals that customer meter is defective. Please refer same to the field service for a meter change.
Outage | J.E.26.07.31949 | C001865309 | Ricky Hall | St.Catherine | Completed | Load_252376 | New Michelton - 410 | Jul 26, 2026 10:47am | Jul 26, 2026 10:47am | Jul 26, 2026 11:21am | Jul 26, 2026 11:21am | Jul 26, 2026 11:21am | Jul 26, 2026 11:21am | Jul 26, 2026 11:22am | Jul 26, 2026 11:22am | Fire |  | Fair | No | Call associated with outage #31950
Outage | J.E.26.07.31950 | C001865310 | Ricky Hall | St.Catherine | Completed | Load_266826 | New Michelton - 410 | Jul 26, 2026 10:47am | Jul 26, 2026 10:47am | Jul 26, 2026 11:07am | Jul 26, 2026 11:08am | Jul 26, 2026 11:19am | Jul 26, 2026 11:20am | Jul 26, 2026 11:20am | Jul 26, 2026 11:20am | Fire |  | Fair | No | Replaced blown 25 amps junction fuse
Non-Outage | J.E.26.07.05012 | C001865307 | Stephen Taylor | St.Thomas | Completed | Load_261497 | Lysson - 410 | Jul 26, 2026 10:28am | Jul 26, 2026 10:28am | Jul 26, 2026 11:02am | Jul 26, 2026 11:02am | Jul 26, 2026 11:02am | Jul 26, 2026 11:02am | Jul 26, 2026 11:04am | Jul 26, 2026 11:04am | LeaningPole |  | Fair | No | Jps secondary pole leaning down and need to straighten by the jps maintenance team urgent
Non-Outage | J.E.26.07.07179 | C001865305 | Stephen Taylor | St.Thomas | Completed | Load_241688 | Lysson - 410 | Jul 26, 2026 10:28am | Jul 26, 2026 10:28am | Jul 26, 2026 1:26pm | Jul 26, 2026 1:26pm | Jul 26, 2026 2:31pm | Jul 26, 2026 2:31pm | Jul 26, 2026 2:34pm | Jul 26, 2026 2:34pm |  |  | Fair | No | Clean up single phase use 3 one bolt clamp customer is now ok
Non-Outage | J.E.26.07.07276 | C001865306 | Stephen Taylor | St.Thomas | Completed | Load_249385 | Lysson - 410 | Jul 26, 2026 10:28am | Jul 26, 2026 10:28am | Jul 26, 2026 11:18am | Jul 26, 2026 11:18am | Jul 26, 2026 11:18am | Jul 26, 2026 11:30am | Jul 26, 2026 11:32am | Jul 26, 2026 11:32am |  |  | Fair | No | Patrol area and power is in the area but several calls to single customer and no one answering the phone need more information to locate customer
Non-Outage | J.E.26.07.08014 | C001865304 | Stephen Taylor | St.Thomas | Completed | Load_239111 | Lysson - 410 | Jul 26, 2026 10:28am | Jul 26, 2026 10:28am | Jul 26, 2026 11:09am | Jul 26, 2026 11:09am | Jul 26, 2026 11:09am | Jul 26, 2026 11:09am | Jul 26, 2026 11:10am | Jul 26, 2026 11:10am |  |  | Fair | No | Contact customer and customer said power is back now and okay
Non-Outage | J.E.26.07.31677 | C001865303 | Stephen Taylor | St.Thomas | Completed | Load_237738 | Lysson - 410 | Jul 26, 2026 10:28am | Jul 26, 2026 10:28am | Jul 26, 2026 12:02pm | Jul 26, 2026 12:02pm | Jul 26, 2026 12:42pm | Jul 26, 2026 1:21pm | Jul 26, 2026 1:25pm | Jul 26, 2026 1:25pm |  |  | Fair | No | Clear up single phase use 2 one bolts clamp rdg 112-113-225 customer is now okay
Outage | J.E.26.07.31934 | C001865302 | Clyde Brown | Clarendon | Completed | Load_246973 | May Pen - 110 | Jul 26, 2026 10:27am | Jul 26, 2026 10:28am | Jul 26, 2026 11:44am | Jul 26, 2026 12:17pm | Jul 26, 2026 12:17pm | Jul 26, 2026 12:02pm | Jul 26, 2026 12:24pm | Jul 26, 2026 12:24pm |  |  | Fair | No | Disconnection
Outage | J.E.26.07.31853 | C001865301 | Clyde Brown | Clarendon | Completed | Load_244344 | May Pen - 110 | Jul 26, 2026 10:22am | Jul 26, 2026 10:22am | Jul 26, 2026 10:31am | Jul 26, 2026 11:45am | Jul 26, 2026 11:45am | Jul 26, 2026 11:42am | Jul 26, 2026 11:53am | Jul 26, 2026 11:53am |  |  | Fair | No | 10kva transformer tripped caused by truck caused secondary conductors to touched together ,line cleared and transformer reset.
Outage | J.E.26.07.31764 | C001865299 | Ricky Hall | St.Catherine | Completed | Load_241810 | New Michelton - 410 | Jul 26, 2026 10:18am | Jul 26, 2026 10:19am | Jul 26, 2026 10:47am | Jul 26, 2026 10:47am | Jul 26, 2026 10:47am | Jul 26, 2026 11:05am | Jul 26, 2026 11:07am | Jul 26, 2026 11:07am |  |  | Fair | No | Defective 25 kva xfmr plz refer to relevant personel(xfmr leaking)
Outage | J.E.26.07.31540 | C001865297 | Kaydon Taylor | KSAN | Completed | Load_255903 | Constant Spring - 210 | Jul 26, 2026 10:16am | Jul 27, 2026 9:16am | Jul 27, 2026 9:45am | Jul 27, 2026 10:04am | Jul 27, 2026 12:54pm | Jul 27, 2026 2:17pm | Jul 27, 2026 2:17pm | Jul 27, 2026 2:17pm |  |  | Rains | No | Two clamps at pothead
Outage | J.E.26.07.31929 | C001865296 | Hartley Chin | St.Catherine | Completed | Load_237883 | Rhodens Pen - 210 | Jul 26, 2026 10:13am | Jul 26, 2026 10:14am | Jul 26, 2026 10:19am | Jul 26, 2026 10:29am | Jul 26, 2026 12:06pm | Jul 26, 2026 12:20pm | Jul 26, 2026 12:24pm | Jul 26, 2026 12:24pm | Fire |  | Fair | No | Ref to field service!!! Customer is the only person currently without supply . Customer is receiving supply from HX 26552542 … no voltage read found @ customer pot bead … requires urgent attention… premises is a shop …
Outage | J.E.26.07.27335 | C001865293 | Moses Elliston | St.Catherine | Completed | Load_576120 | Twickenham - 210 | Jul 26, 2026 10:02am | Jul 26, 2026 10:02am | Jul 27, 2026 6:32am | Jul 27, 2026 6:32am | Jul 27, 2026 6:32am | Jul 26, 2026 6:00pm | Jul 27, 2026 6:34am | Jul 27, 2026 6:34am |  |  | Fair | No | Supply reconnected at meter 117-117-234 volts
Outage | J.E.26.07.29500 | C001865294 | Nickolas Rodriques | St.Catherine | Completed | Load_270044 | Twickenham - 210 | Jul 26, 2026 10:02am | Jul 26, 2026 10:10am | Jul 26, 2026 12:48pm | Jul 26, 2026 12:49pm | Jul 26, 2026 12:54pm | Jul 26, 2026 1:13pm | Jul 26, 2026 1:14pm | Jul 26, 2026 1:14pm |  |  | Fair | No | Customer was located and confirmed that the issue was resolved.
Non-Outage | J.E.26.07.30282 | C001865291 | Ryan Richards | Manchester | Completed | Load_574872 | Kendal - 310 | Jul 26, 2026 9:54am | Jul 26, 2026 9:54am | Jul 26, 2026 10:18am | Jul 26, 2026 10:18am | Jul 26, 2026 11:15am | Jul 26, 2026 12:05pm | Jul 26, 2026 12:05pm | Jul 26, 2026 12:05pm |  |  | Fair | No | Burn off phase found at pole remade burn off phase using one 1 bolt clamps voltage 113/115 229 volts
Outage | J.E.26.07.31849 | C001865290 | Wan Carlos Scarlett | Portmore | Completed | Load_1003656 | Naggo Head - 610 | Jul 26, 2026 9:54am | Jul 26, 2026 9:54am | Jul 26, 2026 10:26am | Jul 26, 2026 3:14pm | Jul 26, 2026 3:45pm | Jul 26, 2026 4:30pm | Jul 26, 2026 4:31pm | Jul 26, 2026 4:31pm |  |  | Fair | No | Call related to outage earlier customer confirmed that power supply has been restored
Outage | J.E.26.07.31852 | C001865292 | Wan Carlos Scarlett | Portmore | Completed | Load_1003655 | Naggo Head - 610 | Jul 26, 2026 9:54am | Jul 26, 2026 9:54am | Jul 26, 2026 11:00am | Jul 26, 2026 11:01am | Jul 26, 2026 11:33am | Jul 26, 2026 12:01pm | Jul 26, 2026 12:03pm | Jul 26, 2026 12:03pm |  |  | SevereWind | No | Refuse 15 Amps junction no pole # was found nothing was found on primary line
Non-Outage | J.E.26.07.31697 | C001865288 | Oshane Warren | Westmoreland | Completed | Load_292178 | Paradise - 110 | Jul 26, 2026 9:53am | Jul 26, 2026 9:53am | Jul 26, 2026 10:22am | Jul 26, 2026 10:22am | Jul 26, 2026 11:53am | Jul 26, 2026 12:26pm | Jul 26, 2026 12:26pm | Jul 26, 2026 12:26pm |  |  | Fair | No | Change defective clamps from xformer drop leads
Outage | J.E.26.07.31476 | C001865289 | Wan Carlos Scarlett | Portmore | Completed | Load_263269 | Naggo Head - 510 | Jul 26, 2026 9:53am | Jul 26, 2026 9:54am | Jul 26, 2026 10:02am | Jul 26, 2026 10:02am | Jul 26, 2026 10:02am | Jul 26, 2026 10:52am | Jul 26, 2026 10:54am | Jul 26, 2026 10:54am |  |  | Fair | No | Found customer service wire damage use 40ft of # service wire use 3 one bolt clamps at pole use 3 Penn union at pothead service wire reading 115-116-231
Outage | J.E.26.07.30233 | C001865286 | Wan Carlos Scarlett | Portmore | Completed | Load_242899 | Naggo Head - 510 | Jul 26, 2026 9:52am | Jul 26, 2026 9:53am | Jul 26, 2026 12:03pm | Jul 26, 2026 12:03pm | Jul 26, 2026 12:21pm | Jul 26, 2026 12:48pm | Jul 26, 2026 12:50pm | Jul 26, 2026 12:50pm |  |  | Fair | No | Refuse 50KVA transformer with a 5amp fuse no pole # was found nothing was found on the secondary line
Outage | J.E.26.07.31848 | C001865287 | Wan Carlos Scarlett | Portmore | Completed | Load_265520 | Naggo Head - 510 | Jul 26, 2026 9:52am | Jul 26, 2026 9:53am | Jul 26, 2026 8:25pm | Jul 26, 2026 8:25pm | Jul 26, 2026 9:22pm | Jul 26, 2026 9:46pm | Jul 26, 2026 9:48pm | Jul 26, 2026 9:48pm | BrokenWire |  | Fair | No | Found customer 3 wire service at pothead with one of the phase corroded use 2 one bolt clamps at service wire phase and neutral readings 114-115-230
Non-Outage | J.E.26.07.31387 | C001865284 | Christopher Edwards | KSAN | Completed | Load_244510 | Constant Spring - 410 | Jul 26, 2026 9:40am | Jul 26, 2026 9:40am | Jul 26, 2026 9:52am | Jul 26, 2026 9:52am | Jul 26, 2026 10:20am | Jul 26, 2026 11:21am | Jul 26, 2026 11:22am | Jul 26, 2026 11:22am |  |  | Fair | No | Remake corroded phase joint At pole using (1) one bolt clamps Voltage:112,110,219v
Non-Outage | J.E.26.07.30365 | C001865283 | Milton Charlton | KSAN | Completed | Load_256784 | West Kings House - 410 | Jul 26, 2026 9:38am | Jul 26, 2026 9:39am | Jul 26, 2026 11:31am | Jul 26, 2026 11:32am | Jul 26, 2026 12:27pm | Jul 26, 2026 12:30pm | Jul 26, 2026 12:29pm | Jul 26, 2026 12:29pm |  |  | Fair | No | Found okay upon arrival. No fire seen on location.
Non-Outage | J.E.26.07.31365 | C001865281 | Milton Charlton | KSAN | Completed | Load_246577 | Hope - 410 | Jul 26, 2026 9:38am | Jul 26, 2026 9:39am | Jul 26, 2026 12:54pm | Jul 26, 2026 12:54pm | Jul 26, 2026 1:44pm | Jul 26, 2026 1:30pm | Jul 26, 2026 1:48pm | Jul 26, 2026 1:48pm |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Non-Outage | J.E.26.07.31895 | C001865280 | Elvis Trowers | null | Completed | null | null | Jul 26, 2026 9:38am | Jul 26, 2026 9:39am | Jul 26, 2026 10:21am | Jul 26, 2026 10:21am | Jul 26, 2026 10:39am | Jul 26, 2026 11:17am | Jul 26, 2026 11:17am | Jul 26, 2026 11:17am | BrokenWire |  | Fair | Yes | Broken secondary neutral was found, during patrol splice reconnect and removed telephone strand wire out of secondary wire.
Outage | J.E.26.07.31856 | C001865282 | Jowayne Newmans | Portland | Completed | Load_255200 | Port Antonio - 410 | Jul 26, 2026 9:38am | Jul 26, 2026 9:41am | Jul 26, 2026 9:49am | Jul 26, 2026 9:49am | Jul 26, 2026 10:06am | Jul 26, 2026 10:36am | Jul 26, 2026 10:36am | Jul 26, 2026 10:36am |  |  | Fair | No | Customer was without supply cause by corroded one bolt connection on secondary conductor, repair by reconnecting service wire on secondary conductor using 2 one bolt clamps. Voltage reading before repair 10v, 0.7v voltage reading after repair 110v, 112v, 221v.
Outage | J.E.26.07.31892 | C001865279 | Edward Royal | KSAS | Completed | Load_300827 | Cane River - 410 | Jul 26, 2026 9:37am | Jul 26, 2026 9:39am | Jul 26, 2026 1:54pm | Jul 26, 2026 1:54pm | Jul 26, 2026 1:54pm | Jul 26, 2026 1:54pm | Jul 26, 2026 1:54pm | Jul 26, 2026 1:54pm | BrokenWire |  | Fair | No | Call related
Outage | J.E.26.07.31896 | C001865278 | Milton Charlton | null | Completed | Load_267533 | Washington Blvd - 610 | Jul 26, 2026 9:37am | Jul 26, 2026 9:39am | Jul 26, 2026 12:30pm | Jul 26, 2026 12:30pm | Jul 26, 2026 12:40pm | Jul 26, 2026 12:50pm | Jul 26, 2026 12:50pm | Jul 26, 2026 12:50pm |  |  | Fair | No | Reconnect customer meter #2795868 by J.P.S. Escalation.
Non-Outage | J.E.26.07.10478 | C001865276 | Hopeton Henry | St.Thomas | Completed | Load_252941 | Good Year - 110 | Jul 26, 2026 9:35am | Jul 26, 2026 9:37am | Jul 26, 2026 9:51am | Jul 26, 2026 1:03pm | Jul 26, 2026 1:14pm | Jul 26, 2026 1:17pm | Jul 26, 2026 1:18pm | Jul 26, 2026 1:18pm |  |  | Fair | No | Customer states the issue was resolved 2 weeks ago
Non-Outage | J.E.26.07.11162 | C001865275 | Hopeton Henry | null | Completed | null | null | Jul 26, 2026 9:35am | Jul 26, 2026 9:38am | Jul 26, 2026 9:51am | Jul 26, 2026 2:49pm | Jul 26, 2026 2:49pm | Jul 26, 2026 2:49pm | Jul 26, 2026 2:50pm | Jul 26, 2026 2:50pm |  |  | Fair | No | Check and found ok
Non-Outage | J.E.26.07.11373 | C001865277 | Hopeton Henry | St.Thomas | Completed | Load_255249 | Good Year - 110 | Jul 26, 2026 9:35am | Jul 26, 2026 9:37am | Jul 26, 2026 9:51am | Jul 26, 2026 1:18pm | Jul 26, 2026 1:22pm | Jul 26, 2026 2:45pm | Jul 26, 2026 2:47pm | Jul 26, 2026 2:47pm |  |  | Fair | No | Change defective service wire 35 ft #6 triplex 3 clamps 3 connector 119-120-240 volts
Non-Outage | J.E.26.07.12335 | C001865274 | Hopeton Henry | St.Thomas | Completed | Load_256439 | Good Year - 110 | Jul 26, 2026 9:35am | Jul 26, 2026 9:37am | Jul 26, 2026 9:51am | Jul 26, 2026 12:19pm | Jul 26, 2026 12:21pm | Jul 26, 2026 12:21pm | Jul 26, 2026 12:22pm | Jul 26, 2026 12:22pm |  |  | Fair | No | Found ok , customer said the issue was resolved
Non-Outage | J.E.26.07.12815 | C001865273 | Hopeton Henry | St.Thomas | Completed | Load_268960 | Good Year - 110 | Jul 26, 2026 9:35am | Jul 26, 2026 9:37am | Jul 26, 2026 9:51am | Jul 26, 2026 12:55pm | Jul 26, 2026 12:55pm | Jul 26, 2026 1:02pm | Jul 26, 2026 1:03pm | Jul 26, 2026 1:03pm |  |  | Fair | No | Internal problem, customer advised
Non-Outage | J.E.26.07.13650 | C001865271 | Hopeton Henry | St.Thomas | Completed | Load_269125 | Good Year - 110 | Jul 26, 2026 9:35am | Jul 26, 2026 9:37am | Jul 26, 2026 9:51am | Jul 27, 2026 9:58am | Jul 27, 2026 11:13am | Jul 27, 2026 11:27am | Jul 27, 2026 11:29am | Jul 27, 2026 11:29am |  |  | Fair | Yes | Fix corrosion problem at pot head , 113-110-223 volts
Non-Outage | J.E.26.07.13816 | C001865272 | Hopeton Henry | St.Thomas | Completed | Load_263676 | Good Year - 110 | Jul 26, 2026 9:35am | Jul 26, 2026 9:37am | Jul 26, 2026 9:51am | Jul 26, 2026 12:22pm | Jul 26, 2026 12:22pm | Jul 26, 2026 12:51pm | Jul 26, 2026 12:52pm | Jul 26, 2026 12:52pm |  |  | Fair | No | Issue resolved by in-house crew
Non-Outage | J.E.26.07.17346 | C001865270 | Hopeton Henry | null | Completed | null | null | Jul 26, 2026 9:35am | Jul 26, 2026 9:39am | Jul 26, 2026 9:51am | Jul 26, 2026 10:49am | Jul 26, 2026 10:49am | Jul 26, 2026 10:50am | Jul 26, 2026 10:50am | Jul 26, 2026 10:50am | BrokenPole |  | Fair | No | Customer not located, broken pole not found
Non-Outage | J.E.26.07.17774 | C001865268 | Hopeton Henry | St.Thomas | Completed | Load_353390 | Good Year - 110 | Jul 26, 2026 9:35am | Jul 26, 2026 9:37am | Jul 26, 2026 9:51am | Jul 26, 2026 12:04pm | Jul 26, 2026 12:04pm | Jul 26, 2026 12:16pm | Jul 26, 2026 12:17pm | Jul 26, 2026 12:17pm |  |  | Fair | No | Internal problem, customer advised
Non-Outage | J.E.26.07.31846 | C001865269 | Hopeton Henry | St.Thomas | Completed | Load_262086 | Good Year - 110 | Jul 26, 2026 9:35am | Jul 26, 2026 9:37am | Jul 26, 2026 9:51am | Jul 27, 2026 11:30am | Jul 27, 2026 11:44am | Jul 27, 2026 12:23pm | Jul 27, 2026 12:25pm | Jul 27, 2026 12:25pm |  |  | Fair | Yes | Use 1 clamp at pole 115-120-235 volts
Outage | J.E.26.07.31091 | C001865266 | Oshane Warren | Westmoreland | Completed | Load_292666 | Paradise - 110 | Jul 26, 2026 9:35am | Jul 26, 2026 9:37am | Jul 26, 2026 3:09pm | Jul 26, 2026 3:09pm | Jul 26, 2026 4:10pm | Jul 26, 2026 4:12pm | Jul 26, 2026 4:12pm | Jul 26, 2026 4:12pm |  |  | Fair | No | Check and find ok voltage 119 119 237
Outage | J.E.26.07.31881 | C001865267 | Oshane Warren | Westmoreland | Completed | Load_244638 | Paradise - 210 | Jul 26, 2026 9:35am | Jul 26, 2026 9:37am | Jul 26, 2026 12:27pm | Jul 26, 2026 12:27pm | Jul 26, 2026 12:46pm | Jul 26, 2026 12:58pm | Jul 26, 2026 12:59pm | Jul 26, 2026 12:59pm |  |  | Rains | No | Replace 3amps 25kva xformer fuse
Outage | J.E.26.07.31581 | C001865263 | Stephen Taylor | St.Thomas | Completed | Load_265149 | Lysson - 410 | Jul 26, 2026 9:34am | Jul 26, 2026 9:34am | Jul 26, 2026 3:38pm | Jul 26, 2026 3:38pm | Jul 26, 2026 4:36pm | Jul 26, 2026 4:37pm | Jul 26, 2026 4:39pm | Jul 26, 2026 4:39pm |  |  | Fair | No | Check with customer and customer say power is back and everything is ok
Outage | J.E.26.07.31816 | C001865261 | Stephen Taylor | St.Thomas | Completed | Load_267646 | Lysson - 410 | Jul 26, 2026 9:34am | Jul 26, 2026 9:34am | Jul 26, 2026 11:11am | Jul 26, 2026 11:11am | Jul 26, 2026 11:11am | Jul 26, 2026 11:11am | Jul 26, 2026 11:13am | Jul 26, 2026 11:13am |  |  | Fair | No | Went into and power is in the area but several calls to single customer and no one answering the phone need more information to locate customer
Outage | J.E.26.07.31850 | C001865262 | Christopher Edwards | KSAN | Completed | Load_263999 | Constant Spring - 410 | Jul 26, 2026 9:34am | Jul 26, 2026 9:34am | Jul 26, 2026 9:51am | Jul 26, 2026 9:51am | Jul 26, 2026 9:51am | Jul 26, 2026 9:51am | Jul 26, 2026 9:52am | Jul 26, 2026 9:52am |  |  | Fair | No | Related to previous call that was rectified
Outage | J.E.26.07.31851 | C001865264 | Elvis Trowers | KSAN | Completed | Load_267820 | Constant Spring - 210 | Jul 26, 2026 9:34am | Jul 26, 2026 9:34am | Jul 26, 2026 11:20am | Jul 26, 2026 11:20am | Jul 26, 2026 12:07pm | Jul 26, 2026 12:11pm | Jul 26, 2026 12:11pm | Jul 26, 2026 12:11pm |  |  | Fair | Yes | Premises checked and found ok upon arrival customer was also spoken with, however she suggested that the power supply was restored.
Outage | J.E.26.07.31858 | C001865265 | Christopher Edwards | KSAN | Completed | Load_264085 | Constant Spring - 410 | Jul 26, 2026 9:34am | Jul 26, 2026 9:34am | Jul 26, 2026 9:49am | Jul 26, 2026 9:49am | Jul 26, 2026 9:49am | Jul 26, 2026 9:49am | Jul 26, 2026 9:51am | Jul 26, 2026 9:51am |  | Y | Fair | No | Clear fallen bamboo off primary lineReclose 15 amps trip saver
Outage | J.E.26.07.31679 | C001865260 | Marlon Brown | Trelawny | Completed | Load_257527 | Greenwood - 210 | Jul 26, 2026 9:33am | Jul 26, 2026 9:34am | Jul 26, 2026 3:34pm | Jul 26, 2026 3:34pm | Jul 26, 2026 3:34pm | Jul 26, 2026 3:35pm | Jul 26, 2026 3:35pm | Jul 26, 2026 3:35pm |  |  | Fair | No | Refer to Field Service Department as customer meter is defective.
Outage | J.E.26.07.31751 | C001865255 | Damion Reid | Manchester | Completed | Load_268999 | Kendal - 210 | Jul 26, 2026 9:33am | Jul 26, 2026 9:34am | Jul 26, 2026 9:56am | Jul 26, 2026 9:56am | Jul 26, 2026 10:45am | Jul 26, 2026 11:29am | Jul 26, 2026 11:31am | Jul 26, 2026 11:31am | Fire |  | Fair | No | Blown 3amp fuse found for 25kva transformer cause by banging secondary phase an neutral conductor balance conductor and replace blown fuse
Outage | J.E.26.07.31878 | C001865256 | Edward Royal | KSAS | Completed | Load_266364 | Three Miles - 510 | Jul 26, 2026 9:33am | Jul 26, 2026 9:35am | Jul 26, 2026 11:30am | Jul 26, 2026 11:30am | Jul 26, 2026 11:30am | Jul 26, 2026 11:31am | Jul 26, 2026 11:32am | Jul 26, 2026 11:32am |  |  | Fair | No | Customer have internal problems customer have faulty wiring advise customer to get a electrician to fix the problem voltage reading 240 120 120 v
Outage | J.E.26.07.31880 | C001865253 | Rayon Foster | Hanover | Completed | Load_241495 | Orange Bay - 310 | Jul 26, 2026 9:33am | Jul 26, 2026 9:33am | Jul 26, 2026 10:13am | Jul 26, 2026 10:13am | Jul 26, 2026 11:04am | Jul 26, 2026 12:25pm | Jul 26, 2026 12:29pm | Jul 26, 2026 12:29pm |  |  | Fair | No | Patrol primary line to find 1 blown30amp junction complete line patrol before replacing 1 30amp junction at same and close line section is too long recommend mid junction switch added to line section to reduce range of outage
Outage | J.E.26.07.31882 | C001865254 | Rayon Foster | Hanover | Completed | Load_245507 | Orange Bay - 310 | Jul 26, 2026 9:33am | Jul 26, 2026 9:33am | Jul 26, 2026 10:13am | Jul 26, 2026 12:30pm | Jul 26, 2026 12:30pm | Jul 26, 2026 12:30pm | Jul 26, 2026 12:31pm | Jul 26, 2026 12:31pm |  |  | Fair | No | Patrol primary line to find 1 blown30amp junction complete line patrol before replacing 1 30amp junction at same and close line section is too long recommend mid junction switch added to line section to reduce range of outage
Outage | J.E.26.07.31885 | C001865257 | Edward Royal | KSAS | Completed | Load_1002652 | Cane River - 310 | Jul 26, 2026 9:33am | Jul 26, 2026 9:35am | Jul 26, 2026 2:03pm | Jul 26, 2026 2:03pm | Jul 26, 2026 2:34pm | Jul 26, 2026 2:36pm | Jul 26, 2026 2:37pm | Jul 26, 2026 2:37pm |  |  | Fair | No | Replaced 20A junction fuse
Outage | J.E.26.07.31860 | C001865252 | Rayon Foster | Hanover | Completed | Load_250192 | Orange Bay - 310 | Jul 26, 2026 9:32am | Jul 26, 2026 9:33am | Jul 26, 2026 12:31pm | Jul 26, 2026 12:31pm | Jul 26, 2026 1:03pm | Jul 26, 2026 1:08pm | Jul 26, 2026 1:08pm | Jul 26, 2026 1:08pm |  |  | EarthMovement | No | Customer stated that his power supply was already restored.
Outage | J.E.26.07.31876 | C001865251 | Andrew Powell | Manchester | Completed | Load_292150 | Spur Tree - 210 | Jul 26, 2026 9:32am | Jul 26, 2026 9:33am | Jul 26, 2026 10:44am | Jul 26, 2026 10:44am | Jul 26, 2026 11:53am | Jul 26, 2026 12:21pm | Jul 26, 2026 12:23pm | Jul 26, 2026 12:23pm |  |  | Fair | No | No service wire found at location. Replace broken service wire using 50 feet #6 triplex, three clamps and three service sleeves, voltage reading 114v-114v phase to neutral 228v cross phase, meter #2611098.
Outage | J.E.26.07.31877 | C001865250 | Andrew Powell | Manchester | Completed | Load_247000 | Spur Tree - 210 | Jul 26, 2026 9:32am | Jul 26, 2026 9:33am | Jul 26, 2026 10:41am | Jul 26, 2026 10:41am | Jul 26, 2026 10:41am | Jul 26, 2026 10:42am | Jul 26, 2026 10:42am | Jul 26, 2026 10:42am |  |  | Fair | No | Manchester called.
Outage | J.E.26.07.31320 | C001865244 | Andrew Powell | St.Elizabeth | Completed | Load_260561 | Maggotty - 210 | Jul 26, 2026 7:08am | Jul 26, 2026 7:08am | Jul 26, 2026 7:13am | Jul 26, 2026 7:15am | Jul 26, 2026 7:58am | Jul 26, 2026 8:01am | Jul 26, 2026 8:02am | Jul 26, 2026 8:02am | BrokenPole |  | Fair | No | Broken cable and wireless wooden pole not Jps equipment no customer affected.
Outage | J.E.26.07.31752 | C001865245 | Andrew Powell | Manchester | Completed | Load_239027 | Spur Tree - 210 | Jul 26, 2026 7:08am | Jul 26, 2026 7:08am | Jul 26, 2026 8:02am | Jul 26, 2026 8:02am | Jul 26, 2026 9:30am | Jul 26, 2026 10:29am | Jul 26, 2026 10:41am | Jul 26, 2026 10:41am |  |  | Fair | No | Found burnt 25 kva transformer at Pole number 526775 cause from overloading circuit, can’t tied in approximately 40 customers affected please refer to Mr Delroy Crew replacement.
Outage | J.E.26.07.31091 | C001865243 | Andrew Powell | Westmoreland | Completed | Load_292666 | Paradise - 110 | Jul 26, 2026 7:07am | Jul 26, 2026 7:07am | Jul 26, 2026 7:11am | Jul 26, 2026 7:11am | Jul 26, 2026 7:11am | Jul 26, 2026 7:12am | Jul 26, 2026 7:12am | Jul 26, 2026 7:12am |  |  | Fair | No | Westmoreland called.
Outage | J.E.26.07.31191 | C001865242 | Oshane Warren | Westmoreland | Completed | Load_238992 | Paradise - 110 | Jul 26, 2026 7:06am | Jul 26, 2026 1:21pm | Jul 26, 2026 2:46pm | Jul 26, 2026 2:46pm | Jul 26, 2026 2:46pm | Jul 26, 2026 3:02pm | Jul 26, 2026 3:08pm | Jul 26, 2026 3:08pm |  |  | Fair | No | Change defective clamps from service wire at secondary line
Outage | J.E.26.07.31253 | C001865241 | Oshane Warren | Westmoreland | Completed | Load_255924 | Paradise - 210 | Jul 26, 2026 7:05am | Jul 26, 2026 7:06am | Jul 26, 2026 9:25am | Jul 26, 2026 9:25am | Jul 26, 2026 9:25am | Jul 26, 2026 9:26am | Jul 26, 2026 9:33am | Jul 26, 2026 9:33am |  |  | Fair | No | Customer reporting getting estimates bill and do not receive any power as yet due to building under construction
Outage | J.E.26.07.31661 | C001865240 | Oshane Warren | Westmoreland | Completed | Load_256594 | Paradise - 110 | Jul 26, 2026 7:05am | Jul 26, 2026 7:06am | Jul 26, 2026 9:00am | Jul 26, 2026 9:00am | Jul 26, 2026 9:00am | Jul 26, 2026 9:01am | Jul 26, 2026 9:01am | Jul 26, 2026 9:01am |  |  | Fair | No | Unable to locate or contact customer on the phone need direction
Outage | J.E.26.07.31763 | C001865239 | Oshane Warren | Westmoreland | Completed | Load_292178 | Paradise - 110 | Jul 26, 2026 7:05am | Jul 26, 2026 7:06am | Jul 26, 2026 8:49am | Jul 26, 2026 8:49am | Jul 26, 2026 8:58am | Jul 26, 2026 8:59am | Jul 26, 2026 9:00am | Jul 26, 2026 9:00am |  |  | Fair | No | Unable to locate or contact customer on the phone need direction
Non-Outage | J.E.26.07.31781 | C001865237 | Edward Royal | KSAS | Completed | Load_300827 | Cane River - 410 | Jul 26, 2026 4:45am | Jul 26, 2026 9:40am | Jul 26, 2026 1:08pm | Jul 26, 2026 1:08pm | Jul 26, 2026 1:09pm | Jul 26, 2026 1:52pm | Jul 26, 2026 1:53pm | Jul 26, 2026 1:53pm | BrokenWire |  | Fair | No | Unable to identify customers service line reffered to field service box #HEX 01217
Outage | J.E.26.07.31785 | C001865220 | Christopher Edwards | KSAN | Completed | Load_244974 | Constant Spring - 210 | Jul 26, 2026 1:48am | Jul 26, 2026 1:49am | Jul 26, 2026 1:53am | Jul 26, 2026 5:32am | Jul 26, 2026 6:26am | Jul 26, 2026 7:19am | Jul 26, 2026 7:21am | Jul 26, 2026 7:21am |  |  | Fair | No | Splice and retention broken open secondary wireUsing (50ft #2 AA conductor (2) #2 preform 4 one bolt clamps Refuse blown 25 kva transformer Using (1) 3 amps
Outage | J.E.26.07.31768 | C001865218 | Horace Malcolm | St.James | Completed | Load_270006 | Queens Drive - 810 | Jul 26, 2026 1:46am | Jul 26, 2026 1:46am | Jul 26, 2026 6:23am | Jul 26, 2026 6:23am | Jul 26, 2026 6:44am | Jul 26, 2026 6:46am | Jul 26, 2026 6:46am | Jul 26, 2026 6:46am |  |  | Fair | No | Check and found ok supply restored to area
Outage | J.E.26.07.31771 | C001865217 | Horace Malcolm | St.James | Completed | Load_239297 | Queens Drive - 810 | Jul 26, 2026 1:46am | Jul 26, 2026 1:46am | Jul 26, 2026 6:46am | Jul 26, 2026 6:46am | Jul 26, 2026 6:46am | Jul 26, 2026 6:47am | Jul 26, 2026 6:47am | Jul 26, 2026 6:47am |  |  | Fair | No | Check and found area ok supply restored
Outage | J.E.26.07.31787 | C001865219 | Christopher Edwards | KSAN | Completed | Load_264085 | Constant Spring - 410 | Jul 26, 2026 1:46am | Jul 26, 2026 1:47am | Jul 26, 2026 7:21am | Jul 26, 2026 7:21am | Jul 26, 2026 8:13am | Jul 26, 2026 9:27am | Jul 26, 2026 9:27am | Jul 26, 2026 9:27am |  |  | Fair | No | Clear fallen bamboo off primary LineReclose 15 amps trip saver
Outage | J.E.26.07.31775 | C001865216 | Horace Malcolm | St.James | Completed | Load_266148 | Bogue - 510 | Jul 26, 2026 1:45am | Jul 26, 2026 1:46am | Jul 26, 2026 3:49am | Jul 26, 2026 3:49am | Jul 26, 2026 4:51am | Jul 26, 2026 5:28am | Jul 26, 2026 5:29am | Jul 26, 2026 5:29am |  |  | Fair | No | Refused one 15amp junction fuse
Outage | J.E.26.07.31761 | C001865214 | Delano Gayle | Portmore | Completed | Load_570079 | Naggo Head - 610 | Jul 26, 2026 12:00am | Jul 26, 2026 12:01am | Jul 26, 2026 12:43am | Jul 26, 2026 2:07am | Jul 26, 2026 2:48am | Jul 26, 2026 2:52am | Jul 26, 2026 2:52am | Jul 26, 2026 2:52am | BrokenPole |  | Fair | No | Customer reporting defective street light
Outage | J.E.26.07.31025 | C001865213 | Edward Royal | KSAS | Completed | Load_252375 | Three Miles - 410 | Jul 25, 2026 11:17pm | Jul 26, 2026 9:33am | Jul 26, 2026 11:02am | Jul 26, 2026 11:02am | Jul 26, 2026 11:02am | Jul 26, 2026 11:05am | Jul 26, 2026 11:06am | Jul 26, 2026 11:06am | Fire |  | Fair | No | Contact customer by phone customer said a jps team come fix it last night
Outage | J.E.26.07.31519 | C001865210 | Horace Malcolm | St.James | Completed | Load_250208 | Queens Drive - 710 | Jul 25, 2026 11:14pm | Jul 25, 2026 11:14pm | Jul 26, 2026 5:29am | Jul 26, 2026 5:29am | Jul 26, 2026 5:53am | Jul 26, 2026 5:56am | Jul 26, 2026 5:56am | Jul 26, 2026 5:56am |  |  | Fair | No | Unable to carry out repairs due to customer load side service wire defective if repair is carried out customer would experiencing high voltage
Outage | J.E.26.07.31591 | C001865211 | Horace Malcolm | St.James | Completed | Load_269969 | Bogue - 310 | Jul 25, 2026 11:14pm | Jul 25, 2026 11:14pm | Jul 26, 2026 12:52am | Jul 26, 2026 12:52am | Jul 26, 2026 1:48am | Jul 26, 2026 3:48am | Jul 26, 2026 3:48am | Jul 26, 2026 3:48am |  |  | Fair | No | Splice and retention two pole span secondary nuetral used 50ft #2 conductor (2)#2 preforms clamp and refuse one 15kva transformer used (1)2 amp fuse
Non-Outage | J.E.26.07.31674 | C001865208 | Andre Williams | Trelawny | Completed | Load_260629 | Duncans - 110 | Jul 25, 2026 10:15pm | Jul 25, 2026 10:16pm | Jul 25, 2026 10:22pm | Jul 25, 2026 10:22pm | Jul 25, 2026 10:35pm | Jul 25, 2026 10:45pm | Jul 25, 2026 10:45pm | Jul 25, 2026 10:45pm |  |  | Fair | No | Patrol close 3 amp on 10 kva in bank of two transformer, ( technician not present to start up pump)
Outage | J.E.26.07.31332 | C001865206 | Ryan Richards | Manchester | Completed | Load_293050 | Kendal - 310 | Jul 25, 2026 10:08pm | Jul 26, 2026 9:33am | Jul 26, 2026 9:59am | Jul 26, 2026 9:59am | Jul 26, 2026 9:59am | Jul 26, 2026 10:18am | Jul 26, 2026 10:18am | Jul 26, 2026 10:18am |  |  | Fair | No | Burn up service wire found at the premises replaced 70ft#6 triplex 3 penunion 3 one bolts clamp voltage 115/117/233 volts
Outage | J.E.26.07.31724 | C001865205 | Christopher Edwards | KSAN | Completed | Load_253424 | West Kings House - 210 | Jul 25, 2026 10:06pm | Jul 25, 2026 10:59pm | Jul 25, 2026 11:08pm | Jul 25, 2026 11:19pm | Jul 25, 2026 11:31pm | Jul 25, 2026 11:44pm | Jul 25, 2026 11:45pm | Jul 25, 2026 11:45pm | Fire |  | Fair | No | Check and found okSupply is in the area
Non-Outage | J.E.26.07.31160 | C001865203 | Christopher Edwards | KSAN | Completed | Load_244468 | Hope - 410 | Jul 25, 2026 9:43pm | Jul 25, 2026 10:59pm | Jul 25, 2026 11:47pm | Jul 25, 2026 11:47pm | Jul 26, 2026 12:08am | Jul 26, 2026 12:37am | Jul 26, 2026 12:37am | Jul 26, 2026 12:37am |  |  | Fair | No | Premises closed Unable to reach customer by phone
Outage | J.E.26.07.27832 | C001865201 | Nickolas Rodriques | St.Catherine | Completed | Load_290732 | Twickenham - 210 | Jul 25, 2026 9:40pm | Jul 26, 2026 10:34am | Jul 26, 2026 2:25pm | Jul 26, 2026 2:31pm | Jul 26, 2026 3:39pm | Jul 26, 2026 3:47pm | Jul 26, 2026 4:12pm | Jul 26, 2026 4:12pm |  |  | Fair | No | Customer stated that she is currently without electricity. No noticeable fuse was found blown. Unable to proceed with checks because a small unit is required to access narrow lane.
Outage | J.E.26.07.31693 | C001865199 | Daniel Francis | St.Ann | Completed | Load_237943 | Roaring River - 210 | Jul 25, 2026 9:38pm | Jul 25, 2026 9:42pm | Jul 25, 2026 10:20pm | Jul 25, 2026 10:20pm | Jul 25, 2026 10:29pm | Jul 25, 2026 10:30pm | Jul 25, 2026 10:33pm | Jul 25, 2026 10:33pm |  |  | Fair | No | Please refer to field service department customer connect hexing box
Outage | J.E.26.07.31663 | C001865198 | Jowayne Newmans | Portland | Completed | Load_249256 | Port Antonio - 410 | Jul 25, 2026 9:31pm | Jul 25, 2026 9:31pm | Jul 25, 2026 10:32pm | Jul 25, 2026 10:32pm | Jul 25, 2026 10:33pm | Jul 25, 2026 10:34pm | Jul 25, 2026 10:34pm | Jul 25, 2026 10:34pm |  |  | Fair | No | Customer stated that they got back electricity.
Outage | J.E.26.07.31685 | C001865197 | Ricky Hall | St.Catherine | Completed | Load_266826 | New Michelton - 410 | Jul 25, 2026 9:30pm | Jul 25, 2026 9:31pm | Jul 25, 2026 9:37pm | Jul 25, 2026 9:37pm | Jul 25, 2026 9:42pm | Jul 25, 2026 10:21pm | Jul 25, 2026 10:21pm | Jul 25, 2026 10:21pm | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Conduct spot bushing replaced blow 10 amps junction junction fuse
Outage | J.E.26.07.31692 | C001865196 | Hartley Chin | St.Catherine | Completed | Load_252011 | Rhodens Pen - 310 | Jul 25, 2026 9:30pm | Jul 25, 2026 9:31pm | Jul 25, 2026 10:16pm | Jul 25, 2026 10:16pm | Jul 25, 2026 10:48pm | Jul 25, 2026 11:02pm | Jul 25, 2026 11:02pm | Jul 25, 2026 11:02pm | Fire |  | Fair | No | Found okay … voltage read 112v , 114v …
Outage | J.E.26.07.31682 | C001865195 | Swon Miller | St.James | Completed | Load_238073 | Queens Drive - 710 | Jul 25, 2026 9:07pm | Jul 25, 2026 9:07pm | Jul 25, 2026 10:26pm | Jul 25, 2026 10:26pm | Jul 25, 2026 10:26pm | Jul 25, 2026 10:58pm | Jul 25, 2026 11:03pm | Jul 25, 2026 11:03pm | Fire |  | Fair | No | Found 100kva transformer drop lead phase burnt off due to illegal connections voltage found 116 open 100 kva transformer to carry out repairs clean and remake transformer drop lead and retention two span of secondary phase and neutral use 1#2 preform 3 pg
Outage | J.E.26.07.31666 | C001865193 | Nickolas Rodriques | St.Catherine | Completed | Load_258234 | Twickenham - 210 | Jul 25, 2026 8:55pm | Jul 26, 2026 9:59am | Jul 26, 2026 10:47am | Jul 26, 2026 10:49am | Jul 26, 2026 11:19am | Jul 26, 2026 11:48am | Jul 26, 2026 11:49am | Jul 26, 2026 11:49am |  |  | Fair | No | Customer stated that she has no electricity. Reading found (118). Checks were done which revealed that the customer is having internal issues. The customer was advised to consult an electrician to do repairs.
Outage | J.E.26.07.31647 | C001865192 | Andre Williams | Trelawny | Completed | Load_245993 | Duncans - 110 | Jul 25, 2026 8:29pm | Jul 25, 2026 8:29pm | Jul 25, 2026 8:47pm | Jul 25, 2026 8:49pm | Jul 25, 2026 9:04pm | Jul 25, 2026 9:08pm | Jul 25, 2026 9:11pm | Jul 25, 2026 9:11pm | Fire |  | Fair | No | Customer says fire was seen on switch pole at queens street and duke street intersection during a power restoration on line section 3 nights back. No sparks or fire seen on pole upon visit (3phase t off on 3phase line heading queen street
Outage | J.E.26.07.31623 | C001865191 | Eric Williams | KSAN | Completed | Load_257446 | Constant Spring - 210 | Jul 25, 2026 8:24pm | Jul 25, 2026 8:31pm | Jul 25, 2026 8:59pm | Jul 25, 2026 8:59pm | Jul 25, 2026 9:43pm | Jul 25, 2026 9:43pm | Jul 25, 2026 9:44pm | Jul 25, 2026 9:44pm |  |  | Fair | No | Premises okay, customer stated power restored and everything okay
Outage | J.E.26.07.29707 | C001865189 | Moses Elliston | KSAS | Completed | Load_1001006 | Duhaney - 210 | Jul 25, 2026 8:21pm | Jul 25, 2026 8:21pm | Jul 26, 2026 11:18am | Jul 26, 2026 11:18am | Jul 26, 2026 11:18am | Jul 26, 2026 11:40am | Jul 26, 2026 12:03pm | Jul 26, 2026 12:03pm |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.07.31580 | C001865190 | Wan Carlos Scarlett | St.Catherine | Completed | Load_258305 | Twickenham - 210 | Jul 25, 2026 8:21pm | Jul 25, 2026 8:21pm | Jul 26, 2026 7:14am | Jul 26, 2026 7:14am | Jul 26, 2026 7:59am | Jul 26, 2026 8:26am | Jul 26, 2026 8:27am | Jul 26, 2026 8:27am |  |  | Fair | No | Reach on location been calling customer but got no answer premises closed
Outage | J.E.26.07.31624 | C001865188 | Kaydon Taylor | KSAS | Completed | Load_268029 | Cane River - 410 | Jul 25, 2026 8:15pm | Jul 25, 2026 8:17pm | Jul 25, 2026 8:32pm | Jul 25, 2026 8:32pm | Jul 25, 2026 8:56pm | Jul 25, 2026 9:22pm | Jul 25, 2026 9:22pm | Jul 25, 2026 9:22pm |  |  | Fair | No | Internal problem burn meter socket
Outage | J.E.26.07.31609 | C001865186 | Delano Gayle | St.Catherine | Completed | Load_305191 | Tredegar - 210 | Jul 25, 2026 8:13pm | Jul 25, 2026 8:17pm | Jul 25, 2026 8:47pm | Jul 25, 2026 8:47pm | Jul 25, 2026 9:04pm | Jul 25, 2026 9:09pm | Jul 25, 2026 9:09pm | Jul 25, 2026 9:09pm |  |  | Fair | No | Premises found okay related to call where 20amps junction fuse was replaced
Non-Outage | J.E.26.07.31483 | C001865184 | Andre Williams | Trelawny | Completed | Load_265886 | Duncans - 110 | Jul 25, 2026 8:06pm | Jul 25, 2026 8:07pm | Jul 25, 2026 8:11pm | Jul 25, 2026 8:11pm | Jul 25, 2026 8:23pm | Jul 25, 2026 8:45pm | Jul 25, 2026 8:46pm | Jul 25, 2026 8:46pm |  |  | Fair | No | Plant experiencing fluctuations on 3phase ,voltage 415/415/397( occasionally both showing 415 drop to 408 and back and reading showing 397 occasionally rise to 410 ) reffer to maintenance to follow up on issue
Outage | J.E.26.07.31573 | C001865180 | Daniel Francis | St.Ann | Completed | Load_556002 | Roaring River - 410 | Jul 25, 2026 7:27pm | Jul 25, 2026 8:11pm | Jul 25, 2026 9:25pm | Jul 25, 2026 9:25pm | Jul 25, 2026 10:16pm | Jul 25, 2026 10:19pm | Jul 25, 2026 10:19pm | Jul 25, 2026 10:19pm |  |  | Fair | No | Internal fault not JPS voltage 120 120/240
Outage | J.E.26.07.31572 | C001865178 | Delano Gayle | St.Catherine | Completed | Load_238652 | Tredegar - 210 | Jul 25, 2026 7:26pm | Jul 25, 2026 7:29pm | Jul 25, 2026 7:38pm | Jul 25, 2026 7:38pm | Jul 25, 2026 8:17pm | Jul 25, 2026 8:46pm | Jul 25, 2026 8:46pm | Jul 25, 2026 8:46pm |  |  | Fair | No | Blown junction on main no pole number, patrolled line section and found okay for closure replace 20amps
Outage | J.E.26.07.31578 | C001865179 | Hartley Chin | St.Catherine | Completed | Load_261086 | Rhodens Pen - 310 | Jul 25, 2026 7:26pm | Jul 25, 2026 7:30pm | Jul 25, 2026 7:35pm | Jul 25, 2026 7:35pm | Jul 25, 2026 9:51pm | Jul 25, 2026 10:05pm | Jul 25, 2026 10:16pm | Jul 25, 2026 10:16pm | BrokenPole |  | Fair | No | Ref to maintenance!! Found broken 30 ft pole with open secondary circuit, pole is broken in middle and is being supported by dead-end gye . Pole requires urgent attention!!!
Outage | J.E.26.07.31542 | C001865177 | Edward Royal | KSAN | Completed | Load_246286 | Washington Blvd - 310 | Jul 25, 2026 7:22pm | Jul 26, 2026 9:33am | Jul 26, 2026 11:32am | Jul 26, 2026 11:39am | Jul 26, 2026 11:39am | Jul 26, 2026 12:33pm | Jul 26, 2026 12:33pm | Jul 26, 2026 12:33pm |  |  | Fair | No | Spliced and reconnected service phase using 2 single bolt clamp voltage reading 240 120 121 v
Outage | J.E.26.07.31547 | C001865176 | Delano Gayle | St.Catherine | Completed | Load_251081 | Tredegar - 310 | Jul 25, 2026 7:11pm | Jul 25, 2026 7:11pm | Jul 26, 2026 12:14am | Jul 26, 2026 12:14am | Jul 26, 2026 12:39am | Jul 26, 2026 12:43am | Jul 26, 2026 12:43am | Jul 26, 2026 12:43am |  |  | Fair | No | Premises not found area found okay
Outage | J.E.26.07.31131 | C001865175 | Moses Elliston | St.Catherine | Completed | Load_256848 | Tredegar - 510 | Jul 25, 2026 7:10pm | Jul 25, 2026 7:11pm | Jul 26, 2026 3:28pm | Jul 26, 2026 3:28pm | Jul 26, 2026 3:28pm | Jul 26, 2026 3:32pm | Jul 26, 2026 3:32pm | Jul 26, 2026 3:32pm |  |  | Fair | No
Outage | J.E.26.07.31549 | C001865173 | Jowayne Newmans | Portland | Completed | Load_249256 | Port Antonio - 410 | Jul 25, 2026 7:06pm | Jul 25, 2026 7:07pm | Jul 25, 2026 7:24pm | Jul 25, 2026 7:24pm | Jul 25, 2026 7:53pm | Jul 25, 2026 8:19pm | Jul 25, 2026 8:20pm | Jul 25, 2026 8:20pm | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Patrol and found 25kva transformer fuse blown cause by neutral wire that run to earth breaching with lower secondary phase conductor, repair by clearing breach and replace 3 amp fuse. Customers now have electricity.
Outage | J.E.26.07.31507 | C001865170 | Jowayne Newmans | Portland | Completed | Load_249013 | Port Antonio - 310 | Jul 25, 2026 7:05pm | Jul 25, 2026 7:06pm | Jul 25, 2026 8:45pm | Jul 25, 2026 8:45pm | Jul 25, 2026 9:52pm | Jul 25, 2026 10:32pm | Jul 25, 2026 10:32pm | Jul 25, 2026 10:32pm |  |  | Fair | No | Patrol and found one pole span of secondary neutral conductor burn down, repair by splicing and retention conductor using 40ft of #2 aluminum conductor and 2 one bolt clamp. Customers now have electricity.
Outage | J.E.26.07.31527 | C001865171 | Jowayne Newmans | Portland | Completed | Load_351338 | Port Antonio - 410 | Jul 25, 2026 7:05pm | Jul 25, 2026 7:06pm | Jul 25, 2026 7:53pm | Jul 25, 2026 8:20pm | Jul 25, 2026 8:33pm | Jul 25, 2026 8:44pm | Jul 25, 2026 8:44pm | Jul 25, 2026 8:44pm | BrokenWire |  | Fair | No | Patrol and found 25kva transformer trip, repair by resetting transformer. Customers now have electricity.
Outage | J.E.26.07.31512 | C001865169 | Clyde Brown | Clarendon | Completed | Load_255025 | May Pen - 110 | Jul 25, 2026 7:04pm | Jul 25, 2026 7:05pm | Jul 25, 2026 7:26pm | Jul 25, 2026 7:26pm | Jul 25, 2026 8:50pm | Jul 25, 2026 8:49pm | Jul 25, 2026 8:57pm | Jul 25, 2026 8:57pm |  |  | Fair | No | Found ok,internal fault 110V at meter socket and pothead,customer advised to get electrician to check private 2wire service line .
Outage | J.E.26.07.31543 | C001865168 | Eric Williams | KSAN | Completed | Load_262366 | Washington Blvd - 510 | Jul 25, 2026 6:54pm | Jul 25, 2026 6:55pm | Jul 25, 2026 8:34pm | Jul 25, 2026 8:34pm | Jul 25, 2026 8:54pm | Jul 25, 2026 8:56pm | Jul 25, 2026 8:59pm | Jul 25, 2026 8:59pm |  |  | Fair | No | Blown 3amps transformer fuse found and replace
Outage | J.E.26.07.31538 | C001865167 | Eric Williams | KSAS | Completed | Load_256910 | Duhaney - 310 | Jul 25, 2026 6:51pm | Jul 25, 2026 6:52pm | Jul 25, 2026 6:55pm | Jul 25, 2026 6:55pm | Jul 25, 2026 7:26pm | Jul 25, 2026 8:27pm | Jul 25, 2026 8:34pm | Jul 25, 2026 8:34pm |  |  | Fair | No | Blown 3amps transformer fuse found and replace
Outage | J.E.26.07.31540 | C001865166 | Eric Williams | KSAN | Completed | Load_255903 | Constant Spring - 210 | Jul 25, 2026 6:51pm | Jul 25, 2026 6:52pm | Jul 25, 2026 9:44pm | Jul 25, 2026 9:44pm | Jul 25, 2026 10:46pm | Jul 25, 2026 10:46pm | Jul 25, 2026 10:47pm | Jul 25, 2026 10:47pm |  |  | Fair | No | Daylight attention required
Non-Outage | J.E.26.07.08551 | C001865165 | Stephen Taylor | St.Thomas | Completed | Load_256790 | Lysson - 410 | Jul 25, 2026 6:32pm | Jul 25, 2026 6:32pm | Jul 25, 2026 6:59pm | Jul 25, 2026 6:59pm | Jul 25, 2026 6:59pm | Jul 25, 2026 7:00pm | Jul 25, 2026 7:01pm | Jul 25, 2026 7:01pm |  |  | Fair | No | Contact customer and customer say that power was restored and now okay
Non-Outage | J.E.26.07.08566 | C001865163 | Stephen Taylor | St.Thomas | Completed | Load_270158 | Lysson - 410 | Jul 25, 2026 6:32pm | Jul 25, 2026 6:32pm | Jul 25, 2026 7:06pm | Jul 25, 2026 7:06pm | Jul 25, 2026 7:06pm | Jul 25, 2026 7:06pm | Jul 25, 2026 7:06pm | Jul 25, 2026 7:06pm |  |  | Fair | No | Contact customer and customer say that power was restored and now okay
Non-Outage | J.E.26.07.24930 | C001865164 | Stephen Taylor | St.Thomas | Completed | Load_238021 | Lysson - 410 | Jul 25, 2026 6:32pm | Jul 25, 2026 6:32pm | Jul 25, 2026 7:07pm | Jul 25, 2026 7:07pm | Jul 25, 2026 7:07pm | Jul 25, 2026 7:07pm | Jul 25, 2026 7:08pm | Jul 25, 2026 7:08pm |  |  | Fair | No | Contact customer and customer say that power was restored and now okay
Non-Outage | J.E.26.07.31322 | C001865162 | Stephen Taylor | St.Thomas | Completed | Load_248385 | Lysson - 410 | Jul 25, 2026 6:32pm | Jul 25, 2026 6:32pm | Jul 26, 2026 2:34pm | Jul 26, 2026 2:34pm | Jul 26, 2026 3:34pm | Jul 26, 2026 3:34pm | Jul 26, 2026 3:37pm | Jul 26, 2026 3:37pm |  |  | Fair | No | Patrol the area power is in the area and several call to customer and no one answer
Non-Outage | J.E.26.06.03359 | C001865160 | Hopeton Henry | St.Thomas | Completed | Load_269083 | Good Year - 210 | Jul 25, 2026 6:26pm | Jul 25, 2026 6:26pm | Jul 25, 2026 6:49pm | Jul 25, 2026 8:38pm | Jul 25, 2026 8:38pm | Jul 26, 2026 9:05am | Jul 26, 2026 9:06am | Jul 26, 2026 9:06am |  |  | Fair | No | Customer not located
Non-Outage | J.E.26.06.30526 | C001865161 | Hopeton Henry | St.Thomas | Completed | Load_246388 | Good Year - 210 | Jul 25, 2026 6:26pm | Jul 25, 2026 6:26pm | Jul 25, 2026 6:49pm | Jul 26, 2026 9:06am | Jul 26, 2026 10:06am | Jul 26, 2026 10:20am | Jul 26, 2026 10:22am | Jul 26, 2026 10:22am |  |  | Fair | No | Check and found ok , customer was having low voltage on the high voltage side
Non-Outage | J.E.26.07.11960 | C001865159 | Hopeton Henry | St.Thomas | Completed | Load_266684 | Good Year - 210 | Jul 25, 2026 6:26pm | Jul 25, 2026 6:26pm | Jul 25, 2026 6:49pm | Jul 25, 2026 7:34pm | Jul 25, 2026 8:09pm | Jul 25, 2026 8:35pm | Jul 25, 2026 8:37pm | Jul 25, 2026 8:37pm |  |  | Fair | No | Reconnect service at pole , 112-113-230 volts
Non-Outage | J.E.26.07.24012 | C001865156 | Kaydon Taylor | KSAS | Completed | Load_270073 | null | Jul 25, 2026 6:12pm | Jul 25, 2026 6:12pm | Jul 25, 2026 7:15pm | Jul 25, 2026 7:15pm | Jul 25, 2026 7:15pm | Jul 25, 2026 7:17pm | Jul 25, 2026 7:17pm | Jul 25, 2026 7:17pm | BrokenPole |  | Fair | No | Broken 30’ pole needs to retire from the line urgently before it falls
Non-Outage | J.E.26.07.31306 | C001865155 | Kaydon Taylor | null | Completed | null | null | Jul 25, 2026 6:12pm | Jul 25, 2026 6:12pm | Jul 25, 2026 7:18pm | Jul 25, 2026 7:18pm | Jul 25, 2026 8:23pm | Jul 25, 2026 8:30pm | Jul 25, 2026 8:30pm | Jul 25, 2026 8:30pm | BrokenPole |  | Fair | No | Found okay
Non-Outage | J.E.26.07.31416 | C001865153 | Wan Carlos Scarlett | null | Completed | null | null | Jul 25, 2026 6:04pm | Jul 25, 2026 6:05pm | Jul 25, 2026 6:44pm | Jul 25, 2026 6:44pm | Jul 25, 2026 6:59pm | Jul 25, 2026 7:31pm | Jul 25, 2026 7:32pm | Jul 25, 2026 7:32pm |  |  | Fair | No | Customer got reconnected by escalation department power supply has been restored
Outage | J.E.26.07.31282 | C001865149 | Swon Miller | St.James | Completed | Load_265743 | Queens Drive - 710 | Jul 25, 2026 6:04pm | Jul 25, 2026 6:04pm | Jul 25, 2026 6:23pm | Jul 25, 2026 6:23pm | Jul 25, 2026 7:24pm | Jul 14, 2026 7:33am | Jul 25, 2026 7:46pm | Jul 25, 2026 7:46pm |  |  | Fair | No | Check and found transformer drop lead burnt cause by slack connection open 100 kva transformer to carry out repairs use 3ft 2/o copper conductor and 2pg to carry out repairs voltage 115 voltage left 115/114/229
Outage | J.E.26.07.31325 | C001865151 | Horace Malcolm | St.James | Completed | Load_270006 | Queens Drive - 810 | Jul 25, 2026 6:04pm | Jul 25, 2026 10:43pm | Jul 26, 2026 12:01am | Jul 26, 2026 12:01am | Jul 26, 2026 12:14am | Jul 26, 2026 12:52am | Jul 26, 2026 12:52am | Jul 26, 2026 12:52am |  |  | Fair | No | Check and found lug on transformer drop lead slack retighten lug voltage 115-113-228
Outage | J.E.26.07.31449 | C001865150 | Horace Malcolm | St.James | Completed | Load_260155 | Queens Drive - 710 | Jul 25, 2026 6:04pm | Jul 25, 2026 10:43pm | Jul 26, 2026 5:56am | Jul 26, 2026 5:56am | Jul 26, 2026 6:15am | Jul 26, 2026 6:23am | Jul 26, 2026 6:23am | Jul 26, 2026 6:23am |  |  | Fair | No | Unable to locate customer premises cannot locate from directions given
Outage | J.E.26.07.31476 | C001865152 | Wan Carlos Scarlett | Portmore | Completed | Load_263269 | Naggo Head - 510 | Jul 25, 2026 6:04pm | Jul 25, 2026 6:05pm | Jul 25, 2026 6:20pm | Jul 25, 2026 9:05pm | Jul 25, 2026 9:40pm | Jul 25, 2026 10:03pm | Jul 25, 2026 10:04pm | Jul 25, 2026 10:04pm |  |  | Fair | No | Customer confirmed premises is closed at this time would like a request for a morning visit tomorrow premises closed
Non-Outage | J.E.26.07.31483 | C001865147 | Andre Williams | Trelawny | Completed | Load_265886 | Duncans - 110 | Jul 25, 2026 6:02pm | Jul 25, 2026 6:02pm | Jul 25, 2026 6:48pm | Jul 25, 2026 6:48pm | Jul 25, 2026 6:48pm | Jul 25, 2026 6:52pm | Jul 25, 2026 7:14pm | Jul 25, 2026 7:14pm |  |  | Fair | No | Low voltage stem from circulation on feeder in parish , maintenance aware of issue.
Outage | J.E.26.07.31493 | C001865148 | Delano Gayle | St.Catherine | Completed | Load_240550 | Tredegar - 210 | Jul 25, 2026 6:02pm | Jul 25, 2026 6:03pm | Jul 25, 2026 9:09pm | Jul 25, 2026 9:09pm | Jul 25, 2026 9:53pm | Jul 25, 2026 9:53pm | Jul 25, 2026 9:54pm | Jul 25, 2026 9:54pm |  |  | Fair | No | Premises found okay
Non-Outage | J.E.26.07.31431 | C001865146 | Cliton Henry | St.Mary | Completed | Load_242851 | Oracabessa - 110 | Jul 25, 2026 5:55pm | Jul 25, 2026 5:55pm | Jul 25, 2026 7:47pm | Jul 25, 2026 7:47pm | Jul 25, 2026 9:16pm | Jul 25, 2026 10:02pm | Jul 25, 2026 10:06pm | Jul 25, 2026 10:06pm |  |  | Fair | No | The customer service wire burnt off in mid span and required a longer reach bucket truck to correct. Kindly refer to St. Mary Operations to reconnect.
Outage | J.E.26.07.31363 | C001865145 | Stephen Taylor | St.Thomas | Completed | Load_265904 | Lysson - 410 | Jul 25, 2026 5:54pm | Jul 25, 2026 6:28pm | Jul 25, 2026 7:11pm | Jul 25, 2026 7:11pm | Jul 25, 2026 7:11pm | Jul 25, 2026 7:11pm | Jul 25, 2026 7:12pm | Jul 25, 2026 7:12pm |  |  | Fair | No | Contact customer and customer say that power was restored and now okay
Outage | J.E.26.07.31492 | C001865141 | Milton Charlton | KSAN | Completed | Load_265279 | Hope - 510 | Jul 25, 2026 5:47pm | Jul 25, 2026 5:47pm | Jul 25, 2026 6:22pm | Jul 25, 2026 6:22pm | Jul 25, 2026 7:52pm | Jul 25, 2026 7:55pm | Jul 25, 2026 8:01pm | Jul 25, 2026 8:01pm |  |  | Fair | No | Found okay upon arrival. Customer complaining that there is an illegal connection on his pothead which is causing his supply to flicker.
Non-Outage | J.E.26.07.31447 | C001865140 | Romaine Roberts | St.Mary | Completed | Load_265580 | Highgate - 210 | Jul 25, 2026 5:46pm | Jul 25, 2026 5:47pm | Jul 25, 2026 6:20pm | Jul 25, 2026 7:35pm | Jul 25, 2026 7:35pm | Jul 25, 2026 7:48pm | Jul 25, 2026 7:51pm | Jul 25, 2026 7:51pm |  |  | Fair | No | Found burn clamps on 25 kva transformer drop lead cause buy banging wire open and close 25 kva transformer to retention conductor and remake jumper on drop lead
Non-Outage | J.E.26.07.31457 | C001865139 | Romaine Roberts | St.Mary | Completed | Load_259090 | Highgate - 210 | Jul 25, 2026 5:46pm | Jul 25, 2026 5:47pm | Jul 25, 2026 7:52pm | Jul 25, 2026 7:52pm | Jul 25, 2026 9:21pm | Jul 25, 2026 9:45pm | Jul 25, 2026 9:49pm | Jul 25, 2026 9:49pm |  |  | Fair | No | 3 wire service Corrosion at pole and pothead clean and remake joints 113-114 227 3 penunion and 3 clamps
Non-Outage | J.E.26.07.31469 | C001865138 | Tajay Bernard | St.James | Completed | Load_256657 | Bogue - 510 | Jul 25, 2026 5:41pm | Jul 25, 2026 6:03pm | Jul 25, 2026 8:31pm | Jul 25, 2026 8:47pm | Jul 25, 2026 9:25pm | Jul 25, 2026 10:19pm | Jul 25, 2026 10:23pm | Jul 25, 2026 10:23pm |  |  | Fair | No | Remove vegetation and refuse 1 25amp junction fuse Voltage reading 235/235/238/415/415/417
Outage | J.E.26.07.31400 | C001865134 | Marlon Authors | St.Elizabeth | Completed | Load_244692 | Maggotty - 110 | Jul 25, 2026 5:38pm | Jul 25, 2026 5:38pm | Jul 25, 2026 9:14pm | Jul 25, 2026 9:14pm | Jul 25, 2026 9:14pm | Jul 25, 2026 9:15pm | Jul 25, 2026 9:15pm | Jul 25, 2026 9:15pm |  |  | Fair | No | Supply restored to the area
Outage | J.E.26.07.31401 | C001865137 | Marlon Authors | St.Elizabeth | Completed | Load_256896 | Maggotty - 110 | Jul 25, 2026 5:38pm | Jul 25, 2026 5:38pm | Jul 25, 2026 6:07pm | Jul 25, 2026 6:07pm | Jul 25, 2026 6:31pm | Jul 25, 2026 8:49pm | Jul 25, 2026 8:49pm | Jul 25, 2026 8:49pm |  |  | Fair | No | Patrol and found clear. Replace one blown 30 amp junction fuse no pole #. Restored supply okay
Outage | J.E.26.07.31427 | C001865135 | Marlon Authors | St.Elizabeth | Completed | Load_244450 | Maggotty - 110 | Jul 25, 2026 5:38pm | Jul 25, 2026 5:38pm | Jul 25, 2026 9:56pm | Jul 25, 2026 9:56pm | Jul 25, 2026 10:34pm | Jul 25, 2026 10:39pm | Jul 25, 2026 10:39pm | Jul 25, 2026 10:39pm |  |  | Fair | No | Patrol and found clear. Replace one blown 15 amp junction fuse no pole #. Restored supply okay
Outage | J.E.26.07.31458 | C001865136 | Marlon Authors | St.Elizabeth | Completed | Load_265998 | Maggotty - 110 | Jul 25, 2026 5:38pm | Jul 25, 2026 5:38pm | Jul 25, 2026 9:17pm | Jul 25, 2026 9:17pm | Jul 25, 2026 9:49pm | Jul 25, 2026 9:56pm | Jul 25, 2026 9:56pm | Jul 25, 2026 9:56pm |  |  | Fair | No | Patrol and found clear. Replace one blown 15 amp junction fuse no pole #. Restored supply okay
Outage | J.E.26.07.30659 | C001865133 | Moses Elliston | St.Catherine | Completed | Load_568118 | Rhodens Pen - 210 | Jul 25, 2026 5:29pm | Jul 25, 2026 5:29pm | Jul 26, 2026 12:41pm | Jul 26, 2026 12:41pm | Jul 26, 2026 12:41pm | Jul 26, 2026 12:42pm | Jul 26, 2026 12:43pm | Jul 26, 2026 12:43pm |  |  | Fair | No | Supply reconnected at meter 117-117-234 volts
Outage | J.E.26.07.31195 | C001865132 | Moses Elliston | St.Catherine | Completed | Load_579394 | Twickenham - 410 | Jul 25, 2026 5:24pm | Jul 25, 2026 5:24pm | Jul 26, 2026 12:03pm | Jul 26, 2026 12:03pm | Jul 26, 2026 12:03pm | Jul 26, 2026 10:31am | Jul 26, 2026 12:07pm | Jul 26, 2026 12:07pm |  |  | Fair | No | Supply reconnected at meter.
Non-Outage | J.E.26.07.30303 | C001865131 | Kaydon Taylor | null | Completed | null | null | Jul 25, 2026 4:52pm | Jul 25, 2026 4:52pm | Jul 25, 2026 5:46pm | Jul 25, 2026 5:47pm | Jul 25, 2026 6:00pm | Jul 25, 2026 7:13pm | Jul 25, 2026 7:13pm | Jul 25, 2026 7:13pm |  |  | Fair | No | Isolate bank of two transformer to carry out repair at pole #0068820 ( 100&25kva). 20’ of # 2 aaa conductor wire 4 clamps
Outage | J.E.26.07.27574 | C001865129 | Wan Carlos Scarlett | Portmore | Completed | Load_291189 | Naggo Head - 510 | Jul 25, 2026 4:41pm | Jul 25, 2026 4:42pm | Jul 25, 2026 9:06pm | Jul 25, 2026 10:04pm | Jul 25, 2026 10:40pm | Jul 25, 2026 10:54pm | Jul 25, 2026 10:55pm | Jul 25, 2026 10:55pm |  |  | Fair | No | Customer got reconnected from escalation department power supply has been restored check and found okay
Outage | J.E.26.07.27335 | C001865128 | Wan Carlos Scarlett | St.Catherine | Completed | Load_576120 | Twickenham - 210 | Jul 25, 2026 4:38pm | Jul 25, 2026 4:42pm | Jul 25, 2026 8:28pm | Jul 25, 2026 8:33pm | Jul 25, 2026 8:55pm | Jul 25, 2026 9:04pm | Jul 25, 2026 9:05pm | Jul 25, 2026 9:05pm |  |  | Fair | No | Customer not getting power supply from EG contact escalation for assistance escalation not getting any communication need field service assistance to complete work task
Outage | J.E.26.07.31294 | C001865127 | Delano Gayle | St.Catherine | Completed | Load_257201 | Tredegar - 310 | Jul 25, 2026 4:16pm | Jul 25, 2026 4:16pm | Jul 25, 2026 6:38pm | Jul 25, 2026 6:38pm | Jul 25, 2026 7:24pm | Jul 25, 2026 7:35pm | Jul 25, 2026 7:35pm | Jul 25, 2026 7:35pm |  |  | Fair | No | found okay at meter socket, voltage readings 112-113-225, customer breaker tripped reset breaker
Outage | J.E.26.07.31311 | C001865126 | Delano Gayle | St.Catherine | Completed | Load_264169 | Tredegar - 510 | Jul 25, 2026 4:16pm | Jul 25, 2026 4:16pm | Jul 25, 2026 4:55pm | Jul 25, 2026 4:55pm | Jul 25, 2026 4:55pm | Jul 25, 2026 4:56pm | Jul 25, 2026 4:56pm | Jul 25, 2026 4:56pm |  |  | Fair | No | Premises found okay related to call where 20amps fuse was replaced at blown junction
Non-Outage | J.E.26.07.31423 | C001865125 | Roxroy Needham | St.Ann | Completed | Load_1003801 | Cardiff Hall - 210 | Jul 25, 2026 4:15pm | Jul 25, 2026 4:40pm | Jul 25, 2026 5:10pm | Jul 25, 2026 5:12pm | Jul 25, 2026 5:15pm | Jul 25, 2026 5:46pm | Jul 25, 2026 5:51pm | Jul 25, 2026 5:51pm | LowHangingWires |  | Fair | No | Retention a span of service wire
Outage | J.E.26.07.31408 | C001865122 | Eric Williams | KSAS | Completed | Load_261930 | Duhaney - 310 | Jul 25, 2026 4:06pm | Jul 25, 2026 4:40pm | Jul 25, 2026 5:02pm | Jul 25, 2026 5:20pm | Jul 25, 2026 5:51pm | Jul 25, 2026 6:44pm | Jul 25, 2026 6:44pm | Jul 25, 2026 6:44pm |  |  | Fair | No | Wrap joints corroded at pot head, voltage readings 115/116/232volts, customers left with power supply.
Outage | J.E.26.07.26051 | C001865114 | Moses Elliston | St.Catherine | Completed | Load_246045 | Tredegar - 510 | Jul 25, 2026 4:00pm | Jul 25, 2026 4:00pm | Jul 26, 2026 10:08am | Jul 26, 2026 10:08am | Jul 26, 2026 10:08am | Jul 26, 2026 10:08am | Jul 26, 2026 10:09am | Jul 26, 2026 10:09am |  |  | Fair | No | Other meters at premises.Customer reported wrong account.
Outage | J.E.26.07.31268 | C001865112 | Kaydon Taylor | null | Completed | Load_270073 | null | Jul 25, 2026 3:41pm | Jul 25, 2026 3:41pm | Jul 25, 2026 4:29pm | Jul 25, 2026 4:31pm | Jul 25, 2026 4:52pm | Jul 25, 2026 5:13pm | Jul 25, 2026 5:14pm | Jul 25, 2026 5:14pm |  |  | Fair | No | 15kva transformer fuse found blown and replace 3 amp pole # 0175066
Outage | J.E.26.07.31250 | C001865109 | Kaydon Taylor | KSAN | Completed | Load_251805 | Washington Blvd - 310 | Jul 25, 2026 3:40pm | Jul 25, 2026 3:41pm | Jul 25, 2026 4:25pm | Jul 25, 2026 4:27pm | Jul 25, 2026 4:28pm | Jul 25, 2026 4:29pm | Jul 25, 2026 4:29pm | Jul 25, 2026 4:29pm |  |  | Fair | No | Found okay
Outage | J.E.26.07.31323 | C001865110 | Kaydon Taylor | KSAS | Completed | Load_1002860 | Rockfort - 410 | Jul 25, 2026 3:40pm | Jul 25, 2026 3:41pm | Jul 25, 2026 7:14pm | Jul 25, 2026 7:14pm | Jul 25, 2026 7:14pm | Jul 25, 2026 7:14pm | Jul 25, 2026 7:14pm | Jul 25, 2026 7:14pm | BrokenWire |  | Fair | No | Found okay
Outage | J.E.26.07.30975 | C001865108 | Wan Carlos Scarlett | St.Catherine | Completed | Load_267899 | Twickenham - 210 | Jul 25, 2026 3:35pm | Jul 25, 2026 3:35pm | Jul 25, 2026 8:28pm | Jul 26, 2026 8:27am | Jul 26, 2026 8:58am | Jul 26, 2026 9:07am | Jul 26, 2026 9:09am | Jul 26, 2026 9:09am |  |  | Fair | No | Reset customer breaker power supply has been restored reading at meter socket 115 115 231
Outage | J.E.26.07.31214 | C001865105 | Eric Williams | KSAN | Completed | Load_244958 | Constant Spring - 210 | Jul 25, 2026 3:20pm | Jul 25, 2026 3:29pm | Jul 25, 2026 3:48pm | Jul 25, 2026 4:46pm | Jul 25, 2026 5:01pm | Jul 25, 2026 5:01pm | Jul 25, 2026 5:02pm | Jul 25, 2026 5:02pm |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.31373 | C001865101 | Jowayne Newmans | Portland | Completed | Load_263453 | Port Antonio - 410 | Jul 25, 2026 3:17pm | Jul 25, 2026 3:18pm | Jul 25, 2026 3:23pm | Jul 25, 2026 3:23pm | Jul 25, 2026 3:43pm | Jul 25, 2026 4:08pm | Jul 25, 2026 4:09pm | Jul 25, 2026 4:09pm |  | Y | Fair | No | Patrol and found coconut tree fell on secondary conductor however transformer fuse wasn’t blown went ahead and isolate transformer to clear breach and replace 2 amp fuse. Customers now have electricity and breach has been cleared.
Outage | J.E.26.07.31319 | C001865099 | Delano Gayle | St.Catherine | Completed | Load_252599 | Tredegar - 510 | Jul 25, 2026 2:55pm | Jul 25, 2026 4:09pm | Jul 25, 2026 4:14pm | Jul 25, 2026 4:14pm | Jul 25, 2026 4:42pm | Jul 25, 2026 4:55pm | Jul 25, 2026 4:55pm | Jul 25, 2026 4:55pm | BrokenWire |  | Fair | No | 2 blown junction on main no pole number, truck hit pole causing 2 phase primary to bang, replace 1 20amps 1 15amps
Outage | J.E.26.07.31348 | C001865100 | Wan Carlos Scarlett | Portmore | Completed | Load_260602 | Naggo Head - 510 | Jul 25, 2026 2:55pm | Jul 25, 2026 2:56pm | Jul 25, 2026 3:46pm | Jul 25, 2026 4:11pm | Jul 25, 2026 4:26pm | Jul 25, 2026 4:39pm | Jul 25, 2026 4:45pm | Jul 25, 2026 4:45pm |  |  | Fair | No | Refuse 40 Amps junction no pole # was found nothing was found on primary line cause by lightning struck power supply has been restored
Non-Outage | J.E.26.07.31303 | C001865096 | Romeo Brissett | null | Completed | null | null | Jul 25, 2026 2:03pm | Jul 25, 2026 2:03pm | Jul 25, 2026 4:03pm | Jul 25, 2026 5:39pm | Jul 25, 2026 6:14pm | Jul 25, 2026 6:48pm | Jul 25, 2026 6:49pm | Jul 25, 2026 6:49pm | BrokenWire |  | Fair | No | Spliced and retention customer service wire, V/R before 118-35-123 after118-118-236
Non-Outage | J.E.26.06.29689 | C001865094 | Derrick Dawkins | St.James | Completed | Load_302381 | Bogue - 510 | Jul 25, 2026 1:59pm | Jul 25, 2026 1:59pm | Jul 25, 2026 3:27pm | Jul 25, 2026 3:27pm | Jul 25, 2026 5:15pm | Jul 25, 2026 5:19pm | Jul 25, 2026 5:19pm | Jul 25, 2026 5:19pm |  |  | Fair | No | Cannot locate customer
Non-Outage | J.E.26.07.21267 | C001865095 | Derrick Dawkins | St.James | Completed | Load_249158 | Bogue - 610 | Jul 25, 2026 1:59pm | Jul 25, 2026 1:59pm | Jul 25, 2026 2:23pm | Jul 25, 2026 2:23pm | Jul 25, 2026 3:22pm | Jul 25, 2026 3:27pm | Jul 25, 2026 3:27pm | Jul 25, 2026 3:27pm |  |  | Fair | No | Found premises ok
Non-Outage | J.E.26.02.32175 | C001865092 | Romeo Brissett | St.James | Completed | Load_266606 | Bogue - 310 | Jul 25, 2026 1:55pm | Jul 25, 2026 1:56pm | Jul 25, 2026 4:03pm | Jul 25, 2026 5:09pm | Jul 25, 2026 5:38pm | Jul 25, 2026 5:28pm | Jul 25, 2026 5:39pm | Jul 25, 2026 5:39pm |  |  | Fair | No | Customer stated issue was resolved
Non-Outage | J.E.26.07.31103 | C001865091 | Richard Samuda | null | Completed | null | null | Jul 25, 2026 1:51pm | Jul 25, 2026 1:51pm | Jul 25, 2026 2:44pm | Jul 25, 2026 3:59pm | Jul 25, 2026 3:59pm | Jul 25, 2026 5:00pm | Jul 25, 2026 5:00pm | Jul 25, 2026 5:00pm |  |  | Rains | No | Splice and reconnected customer service wire that was broken causing customer to experience single phase voltage 111/113/224
Outage | J.E.26.07.31285 | C001865090 | Andre Smith | KSAN | Completed | Load_246721 | Washington Blvd - 310 | Jul 25, 2026 1:47pm | Jul 25, 2026 1:48pm | Jul 25, 2026 2:21pm | Jul 25, 2026 2:21pm | Jul 25, 2026 2:42pm | Jul 25, 2026 2:42pm | Jul 25, 2026 2:45pm | Jul 25, 2026 2:45pm | BrokenWire |  | Fair | No | Replace blown transformer fuse 3A supply restored
Non-Outage | J.E.26.07.31271 | C001865089 | Hopeton Henry | null | Completed | null | null | Jul 25, 2026 1:46pm | Jul 25, 2026 1:47pm | Jul 25, 2026 3:08pm | Jul 25, 2026 5:02pm | Jul 25, 2026 6:49pm | Jul 25, 2026 6:50pm | Jul 25, 2026 6:54pm | Jul 25, 2026 6:54pm | Fire |  | Fair | No | Splice and retention service wire 120-120-240 volts
Outage | J.E.26.07.31293 | C001865088 | Daniel Francis | St.Ann | Completed | Load_246075 | Roaring River - 410 | Jul 25, 2026 1:43pm | Jul 25, 2026 3:51pm | Jul 25, 2026 4:24pm | Jul 25, 2026 5:43pm | Jul 25, 2026 6:59pm | Jul 25, 2026 8:26pm | Jul 25, 2026 9:21pm | Jul 25, 2026 9:21pm | LowHangingWires |  | Fair | No | Replace 100ft of #. 6 service wire also 6 one bolt clamp use
Outage | J.E.26.07.31262 | C001865087 | Derrick Dawkins | St.James | Completed | Load_268070 | Bogue - 510 | Jul 25, 2026 1:40pm | Jul 25, 2026 1:45pm | Jul 25, 2026 2:00pm | Jul 25, 2026 2:03pm | Jul 25, 2026 2:07pm | Jul 25, 2026 2:22pm | Jul 25, 2026 2:22pm | Jul 25, 2026 2:22pm | LowHangingWires |  | Fair | No | Cable wire hanging low across the road
Outage | J.E.26.07.31277 | C001865086 | Ricky Hall | St.Catherine | Completed | Load_250238 | New Michelton - 210 | Jul 25, 2026 1:37pm | Jul 25, 2026 1:38pm | Jul 25, 2026 8:20pm | Jul 25, 2026 8:24pm | Jul 25, 2026 9:20pm | Jul 25, 2026 9:21pm | Jul 25, 2026 9:22pm | Jul 25, 2026 9:22pm | BrokenWire |  | Fair | No | Broken 3W service beyond Jps metering point customer advised
Non-Outage | J.E.26.07.13051 | C001865084 | Edward Royal | KSAS | Completed | Load_259334 | Cane River - 610 | Jul 25, 2026 1:35pm | Jul 25, 2026 1:35pm | Jul 25, 2026 1:46pm | Jul 25, 2026 1:46pm | Jul 25, 2026 1:46pm | Jul 25, 2026 1:47pm | Jul 25, 2026 1:47pm | Jul 25, 2026 1:47pm |  |  | Fair | No | When contacted customer said that nobody is there
Non-Outage | J.E.26.07.25202 | C001865085 | Edward Royal | KSAS | Completed | Load_242988 | Cane River - 410 | Jul 25, 2026 1:35pm | Jul 25, 2026 1:35pm | Jul 25, 2026 1:51pm | Jul 25, 2026 1:51pm | Jul 25, 2026 1:52pm | Jul 25, 2026 1:52pm | Jul 25, 2026 1:52pm | Jul 25, 2026 1:52pm |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.07.26054 | C001865083 | Edward Royal | KSAS | Completed | Load_1002691 | Cane River - 410 | Jul 25, 2026 1:35pm | Jul 25, 2026 1:35pm | Jul 25, 2026 1:48pm | Jul 25, 2026 1:48pm | Jul 25, 2026 1:48pm | Jul 25, 2026 1:49pm | Jul 25, 2026 1:49pm | Jul 25, 2026 1:49pm | Fire |  | Fair | No | Premises found close
Outage | J.E.26.07.30479 | C001865079 | Wayne Dillion | St.Elizabeth | Completed | Load_261839 | Maggotty - 110 | Jul 25, 2026 1:31pm | Jul 26, 2026 9:32am | Jul 26, 2026 10:24am | Jul 26, 2026 10:24am | Jul 26, 2026 10:24am | Jul 26, 2026 10:50am | Jul 26, 2026 10:52am | Jul 26, 2026 10:52am |  |  | Fair | No | Supply check and found no service wire. Connect same using 70ft of #6 triplex service wire, 3 clamps and 3 linkets. Supply leave working okay reading 112v, 114v and cross phase 226volts.
Outage | J.E.26.07.30707 | C001865078 | Wayne Dillion | St.Elizabeth | Completed | Load_268564 | Maggotty - 110 | Jul 25, 2026 1:31pm | Jul 26, 2026 9:32am | Jul 26, 2026 11:04am | Jul 26, 2026 11:04am | Jul 26, 2026 11:20am | Jul 26, 2026 11:30am | Jul 26, 2026 11:31am | Jul 26, 2026 11:31am |  |  | Fair | No | Supply check and found one blown 1amp fuse that protects 5kva chip type transformer circuit no pole #. Replace same and supply restored okay.
Outage | J.E.26.07.31205 | C001865080 | Raheem Ricketts | St.Elizabeth | Completed | Load_269055 | Maggotty - 210 | Jul 25, 2026 1:31pm | Jul 25, 2026 2:54pm | Jul 25, 2026 3:04pm | Jul 25, 2026 3:32pm | Jul 25, 2026 6:00pm | Jul 25, 2026 6:20pm | Jul 25, 2026 6:20pm | Jul 25, 2026 6:20pm |  |  | Fair | No | Check and one 15 amp junction fuse blown replace junction fuse using one 15amp fuse
Outage | J.E.26.07.31256 | C001865081 | Marlon Authors | St.Elizabeth | Completed | Load_292676 | Maggotty - 110 | Jul 25, 2026 1:31pm | Jul 25, 2026 1:32pm | Jul 25, 2026 2:21pm | Jul 25, 2026 2:21pm | Jul 25, 2026 3:46pm | Jul 25, 2026 5:02pm | Jul 25, 2026 5:02pm | Jul 25, 2026 5:02pm |  |  | Rains | No | Patrol and found clear. Replace one blown 8 amp junction fuse no pole #. Restored supply ok
Non-Outage | J.E.26.07.30568 | C001865073 | Hartley Chin | null | Completed | null | null | Jul 25, 2026 1:09pm | Jul 25, 2026 1:09pm | Jul 25, 2026 2:07pm | Jul 25, 2026 2:07pm | Jul 25, 2026 2:42pm | Jul 25, 2026 2:47pm | Jul 25, 2026 2:47pm | Jul 25, 2026 2:47pm |  |  | Fair | No | Found okay , customer stated power was restored…
Non-Outage | J.E.26.07.25417 | C001865072 | Nickolas Rodriques | null | Completed | null | null | Jul 25, 2026 1:07pm | Jul 25, 2026 1:08pm | Jul 25, 2026 9:26pm | Jul 25, 2026 9:26pm | Jul 25, 2026 10:51pm | Jul 25, 2026 10:50pm | Jul 26, 2026 12:09am | Jul 26, 2026 12:09am |  |  | Fair | No | Customer confirmed that the issue with his prepaid box was already resolved.
Non-Outage | J.E.26.07.25458 | C001865070 | Nickolas Rodriques | null | Completed | null | null | Jul 25, 2026 1:07pm | Jul 25, 2026 1:08pm | Jul 25, 2026 5:25pm | Jul 25, 2026 5:26pm | Jul 25, 2026 5:55pm | Jul 25, 2026 6:28pm | Jul 25, 2026 6:35pm | Jul 25, 2026 6:35pm |  |  | Fair | No | Checked and found traffic lights without power due to broken service wire which was caused by illegal connection. Repaired by connecting the wire using one service sleeve. Current reading (118)
Non-Outage | J.E.26.07.26630 | C001865071 | Nickolas Rodriques | null | Completed | null | null | Jul 25, 2026 1:07pm | Jul 25, 2026 1:08pm | Jul 25, 2026 8:11pm | Jul 25, 2026 8:14pm | Jul 25, 2026 9:04pm | Jul 25, 2026 9:25pm | Jul 25, 2026 9:26pm | Jul 25, 2026 9:26pm |  |  | Fair | No | Found customer with electricity. The customer confirmed that the area outage was restored.
Outage | J.E.26.07.29707 | C001865069 | Nickolas Rodriques | KSAS | Completed | Load_1001006 | Duhaney - 210 | Jul 25, 2026 1:07pm | Jul 25, 2026 1:08pm | Jul 25, 2026 6:36pm | Jul 25, 2026 6:36pm | Jul 25, 2026 7:31pm | Jul 25, 2026 8:09pm | Jul 25, 2026 8:10pm | Jul 25, 2026 8:10pm |  |  | Fair | No | Found customer with electricity. However, the customer stated that he is having issues topping his prepaid box. Refer to field service.
Outage | J.E.26.07.31227 | C001865068 | Delano Gayle | St.Catherine | Completed | Load_247899 | Tredegar - 310 | Jul 25, 2026 1:07pm | Jul 25, 2026 4:09pm | Jul 25, 2026 4:57pm | Jul 25, 2026 4:57pm | Jul 25, 2026 6:09pm | Jul 25, 2026 6:10pm | Jul 25, 2026 6:11pm | Jul 25, 2026 6:11pm |  |  | Fair | No | Premises found okay power restored to premises
Non-Outage | J.E.26.07.25578 | C001865066 | Neville Spencer | null | Completed | null | null | Jul 25, 2026 1:03pm | Jul 25, 2026 1:04pm | Jul 25, 2026 1:38pm | Jul 25, 2026 1:38pm | Jul 25, 2026 1:38pm | Jul 25, 2026 1:39pm | Jul 25, 2026 1:39pm | Jul 25, 2026 1:39pm |  |  | Fair | No | Found ok.
Non-Outage | J.E.26.07.26357 | C001865064 | Neville Spencer | null | Completed | null | null | Jul 25, 2026 1:03pm | Jul 25, 2026 1:04pm | Jul 25, 2026 1:13pm | Jul 25, 2026 1:13pm | Jul 25, 2026 1:34pm | Jul 25, 2026 1:34pm | Jul 25, 2026 1:35pm | Jul 25, 2026 1:35pm |  |  | Fair | No | Found ok.
Non-Outage | J.E.26.07.29467 | C001865062 | Neville Spencer | null | Completed | null | null | Jul 25, 2026 1:03pm | Jul 25, 2026 1:04pm | Jul 25, 2026 3:29pm | Jul 25, 2026 3:29pm | Jul 25, 2026 4:01pm | Jul 25, 2026 4:01pm | Jul 25, 2026 4:02pm | Jul 25, 2026 4:02pm |  |  | Fair | No | Found ok call resolved yesterday.
Non-Outage | J.E.26.07.29565 | C001865061 | Neville Spencer | null | Completed | null | null | Jul 25, 2026 1:03pm | Jul 25, 2026 1:04pm | Jul 25, 2026 4:02pm | Jul 25, 2026 4:02pm | Jul 25, 2026 4:02pm | Jul 25, 2026 4:02pm | Jul 25, 2026 4:03pm | Jul 25, 2026 4:03pm |  |  | Fair | No | Found ok call resolved yesterday.
Non-Outage | J.E.26.07.30648 | C001865063 | Neville Spencer | null | Completed | null | null | Jul 25, 2026 1:03pm | Jul 25, 2026 1:04pm | Jul 25, 2026 4:03pm | Jul 25, 2026 4:03pm | Jul 25, 2026 4:58pm | Jul 25, 2026 4:59pm | Jul 25, 2026 5:01pm | Jul 25, 2026 5:01pm |  |  | Fair | No | Found ok call resolved last night.
Outage | J.E.26.07.26540 | C001865065 | Neville Spencer | Clarendon | Completed | Load_262171 | Monymusk - 410 | Jul 25, 2026 1:03pm | Jul 25, 2026 1:04pm | Jul 25, 2026 5:25pm | Jul 25, 2026 5:25pm | Jul 25, 2026 6:42pm | Jul 25, 2026 6:42pm | Jul 25, 2026 6:42pm | Jul 25, 2026 6:42pm |  |  | Fair | No | Found ok.
Outage | J.E.26.07.31263 | C001865060 | Neville Spencer | St.Catherine | Completed | Load_1000338 | Rhodens Pen - 410 | Jul 25, 2026 1:03pm | Jul 25, 2026 1:04pm | Jul 25, 2026 1:42pm | Jul 25, 2026 1:42pm | Jul 25, 2026 3:19pm | Jul 25, 2026 3:26pm | Jul 25, 2026 3:28pm | Jul 25, 2026 3:28pm |  |  | Fair | No | Cleared bird from xmfr pole renew blown 3 amp fuse protecting 25 kva xmfr supply restored voltage reading 116 118 235.
Non-Outage | J.E.26.07.30805 | C001865058 | Wan Carlos Scarlett | null | Completed | null | null | Jul 25, 2026 12:51pm | Jul 25, 2026 12:52pm | Jul 25, 2026 6:44pm | Jul 25, 2026 7:33pm | Jul 25, 2026 7:46pm | Jul 25, 2026 8:01pm | Jul 25, 2026 8:02pm | Jul 25, 2026 8:02pm |  |  | Fair | No | Reach on location been calling customer but got no answer premises closed
Outage | J.E.26.07.27335 | C001865057 | Wan Carlos Scarlett | St.Catherine | Completed | Load_576120 | Twickenham - 210 | Jul 25, 2026 12:51pm | Jul 25, 2026 12:52pm | Jul 25, 2026 12:59pm | Jul 25, 2026 12:59pm | Jul 25, 2026 1:22pm | Jul 25, 2026 1:44pm | Jul 25, 2026 1:46pm | Jul 25, 2026 1:46pm |  |  | Fair | No | Customer having issues with there power supply coming from EG box contact escalation for assistance escalation not getting any communication need field service assistance to complete work task
Outage | J.E.26.07.27767 | C001865056 | Wan Carlos Scarlett | Portmore | Completed | Load_252150 | Naggo Head - 610 | Jul 25, 2026 12:51pm | Jul 25, 2026 12:52pm | Jul 25, 2026 3:40pm | Jul 25, 2026 3:40pm | Jul 25, 2026 3:47pm | Jul 25, 2026 4:09pm | Jul 25, 2026 4:11pm | Jul 25, 2026 4:11pm |  |  | Fair | No | Found customer 2 wire service at pothead with phase wire burnt off use 1 Penn union at pothead reading 116
Outage | J.E.26.07.27856 | C001865055 | Wan Carlos Scarlett | Portmore | Completed | Load_579361 | Naggo Head - 610 | Jul 25, 2026 12:51pm | Jul 25, 2026 12:52pm | Jul 25, 2026 6:44pm | Jul 25, 2026 8:03pm | Jul 25, 2026 8:12pm | Jul 25, 2026 8:30pm | Jul 25, 2026 8:33pm | Jul 25, 2026 8:33pm |  |  | Fair | No | Customer has prepaid meter and made a request to change to a postpaid meter field service is already aware and schedule for it to be change in the coming week
Non-Outage | J.E.26.07.25335 | C001865052 | Wan Carlos Scarlett | null | Completed | null | null | Jul 25, 2026 12:50pm | Jul 25, 2026 12:52pm | Jul 25, 2026 1:08pm | Jul 25, 2026 4:49pm | Jul 25, 2026 5:22pm | Jul 25, 2026 5:50pm | Jul 25, 2026 5:53pm | Jul 25, 2026 5:53pm |  |  | Fair | No | Customer confirmed that issue was resolved by a next JPS crew check and found okay
Outage | J.E.26.07.26541 | C001865054 | Wan Carlos Scarlett | St.Catherine | Completed | Load_290732 | Twickenham - 210 | Jul 25, 2026 12:50pm | Jul 25, 2026 12:52pm | Jul 25, 2026 1:00pm | Jul 25, 2026 1:46pm | Jul 25, 2026 1:46pm | Jul 25, 2026 1:46pm | Jul 25, 2026 1:52pm | Jul 25, 2026 1:52pm |  |  | Fair | No | Customer not getting power supply from EG Box contact escalation team for assistance escalation department not getting any communication need field service assistance to complete work task
Outage | J.E.26.07.27102 | C001865053 | Wan Carlos Scarlett | Portmore | Completed | Load_253505 | Naggo Head - 510 | Jul 25, 2026 12:50pm | Jul 25, 2026 12:52pm | Jul 25, 2026 1:07pm | Jul 25, 2026 1:52pm | Jul 25, 2026 2:35pm | Jul 25, 2026 3:00pm | Jul 25, 2026 3:01pm | Jul 25, 2026 3:01pm |  |  | Fair | No | Customer confirmed that power supply has been restored check and found okay reading at pole115 115 230
Non-Outage | J.E.26.07.31209 | C001865048 | Elvis Trowers | null | Completed | null | null | Jul 25, 2026 12:46pm | Jul 25, 2026 12:53pm | Jul 25, 2026 2:04pm | Jul 25, 2026 2:04pm | Jul 25, 2026 2:38pm | Jul 25, 2026 2:42pm | Jul 25, 2026 2:42pm | Jul 25, 2026 2:42pm | BrokenPole |  | Fair | Yes | Premises checked and found ok, customer was also spoken with however he said that it’s the street lights that are not working he’s talking about.
Outage | J.E.26.07.31074 | C001865049 | Barnett Brown | Manchester | Completed | Load_244954 | Spur Tree - 310 | Jul 25, 2026 12:46pm | Jul 25, 2026 12:49pm | Jul 25, 2026 5:18pm | Jul 25, 2026 5:18pm | Jul 25, 2026 6:32pm | Jul 25, 2026 6:33pm | Jul 25, 2026 7:31pm | Jul 25, 2026 7:31pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.31120 | C001865050 | Barnett Brown | Manchester | Completed | Load_248597 | Spur Tree - 310 | Jul 25, 2026 12:46pm | Jul 25, 2026 12:49pm | Jul 25, 2026 9:35pm | Jul 25, 2026 9:35pm | Jul 25, 2026 10:28pm | Jul 25, 2026 10:29pm | Jul 25, 2026 10:30pm | Jul 25, 2026 10:30pm |  |  | Fair | No | Premises found ok premises found ok
Outage | J.E.26.07.31135 | C001865051 | Barnett Brown | Manchester | Completed | Load_254646 | Spur Tree - 310 | Jul 25, 2026 12:46pm | Jul 25, 2026 12:49pm | Jul 25, 2026 7:31pm | Jul 25, 2026 7:31pm | Jul 25, 2026 8:38pm | Jul 25, 2026 9:34pm | Jul 25, 2026 9:34pm | Jul 25, 2026 9:34pm |  |  | Fair | No | Remade service joint at secondary line
Outage | J.E.26.07.31241 | C001865047 | Tyrese Williams | St.Ann | Completed | Load_255932 | Cardiff Hall - 310 | Jul 25, 2026 12:11pm | Jul 25, 2026 12:14pm | Jul 25, 2026 1:03pm | Jul 25, 2026 1:08pm | Jul 25, 2026 2:29pm | Jul 25, 2026 2:40pm | Jul 25, 2026 2:40pm | Jul 25, 2026 2:40pm | BrokenWire |  | Fair | No | Splice and retention service wire neutral light left working ok at premise
Outage | J.E.26.07.31130 | C001865046 | Kaydon Taylor | KSAS | Completed | Load_240083 | Hunts Bay - 510 | Jul 25, 2026 11:58am | Jul 25, 2026 3:37pm | Jul 25, 2026 5:15pm | Jul 25, 2026 5:18pm | Jul 25, 2026 5:45pm | Jul 25, 2026 5:46pm | Jul 25, 2026 5:46pm | Jul 25, 2026 5:46pm |  |  | Fair | No | Found okay
Non-Outage | J.E.26.07.31219 | C001865045 | Cliton Henry | St.Mary | Completed | Load_268193 | Oracabessa - 110 | Jul 25, 2026 11:42am | Jul 25, 2026 11:48am | Jul 25, 2026 12:04pm | Jul 25, 2026 12:04pm | Jul 25, 2026 12:21pm | Jul 25, 2026 12:45pm | Jul 25, 2026 12:53pm | Jul 25, 2026 12:53pm |  |  | Fair | No | A burnt off service wire phase conductor found was reconnected using 1- one bolt clamp. Voltages left 116-117/233 volts.
Outage | J.E.26.07.31151 | C001865043 | Hartley Chin | St.Catherine | Completed | Load_239636 | Rhodens Pen - 310 | Jul 25, 2026 11:35am | Jul 25, 2026 11:36am | Jul 25, 2026 12:56pm | Jul 25, 2026 12:56pm | Jul 25, 2026 1:49pm | Jul 25, 2026 1:56pm | Jul 25, 2026 2:07pm | Jul 25, 2026 2:07pm |  |  | Fair | No | Found okay … customer stated issue was resolved…
Outage | J.E.26.07.31139 | C001865042 | Ricky Hall | St.Catherine | Completed | Load_253319 | New Michelton - 410 | Jul 25, 2026 11:34am | Jul 25, 2026 11:35am | Jul 25, 2026 12:00pm | Jul 25, 2026 12:00pm | Jul 25, 2026 12:17pm | Jul 25, 2026 12:17pm | Jul 25, 2026 12:18pm | Jul 25, 2026 12:18pm |  |  | Fair | No | Call associated with outage #31016
Outage | J.E.26.07.31141 | C001865041 | Derrick Dawkins | St.James | Completed | Load_261122 | Bogue - 510 | Jul 25, 2026 11:34am | Jul 25, 2026 11:34am | Jul 25, 2026 12:55pm | Jul 25, 2026 12:55pm | Jul 25, 2026 1:12pm | Jul 25, 2026 1:06pm | Jul 25, 2026 1:14pm | Jul 25, 2026 1:14pm |  |  | Fair | No | Customer stated that they didn’t make any report
Outage | J.E.26.07.31203 | C001865040 | Derrick Dawkins | St.James | Completed | Load_259585 | Bogue - 510 | Jul 25, 2026 11:34am | Jul 25, 2026 11:34am | Jul 25, 2026 1:12pm | Jul 25, 2026 1:14pm | Jul 25, 2026 1:14pm | Jul 25, 2026 1:31pm | Jul 25, 2026 1:31pm | Jul 25, 2026 1:31pm |  |  | Fair | No | Found 2 junction fuse blown 20 amp replaced 2 20 amp junction fuse no pole amp available
Outage | J.E.26.07.31089 | C001865037 | Delano Gayle | St.Catherine | Completed | Load_250219 | Tredegar - 310 | Jul 25, 2026 11:33am | Jul 25, 2026 4:09pm | Jul 25, 2026 9:54pm | Jul 25, 2026 9:54pm | Jul 25, 2026 11:02pm | Jul 25, 2026 11:03pm | Jul 25, 2026 11:04pm | Jul 25, 2026 11:04pm | Fire |  | Fair | No | Premises not found no answer from customer phone
Outage | J.E.26.07.31131 | C001865039 | Delano Gayle | St.Catherine | Completed | Load_256848 | Tredegar - 510 | Jul 25, 2026 11:33am | Jul 25, 2026 4:09pm | Jul 25, 2026 6:12pm | Jul 25, 2026 6:12pm | Jul 25, 2026 6:34pm | Jul 25, 2026 6:36pm | Jul 25, 2026 6:36pm | Jul 25, 2026 6:36pm |  |  | Fair | No | Hexing customer with CIU issues send call to Moses
Outage | J.E.26.07.31195 | C001865038 | Nickolas Rodriques | St.Catherine | Completed | Load_579394 | Twickenham - 410 | Jul 25, 2026 11:33am | Jul 25, 2026 11:33am | Jul 25, 2026 3:02pm | Jul 25, 2026 3:05pm | Jul 25, 2026 3:56pm | Jul 25, 2026 4:47pm | Jul 25, 2026 5:07pm | Jul 25, 2026 5:07pm |  |  | Fair | No | Checked and found customer without power. Checks were done which revealed that the issue is stemming from the hexing box (HEX 06534). Refer to field service.
Outage | J.E.26.07.31091 | C001865032 | Raheem Ricketts | Westmoreland | Completed | Load_292666 | Paradise - 110 | Jul 25, 2026 11:05am | Jul 25, 2026 11:07am | Jul 25, 2026 12:09pm | Jul 25, 2026 12:09pm | Jul 25, 2026 12:09pm | Jul 25, 2026 12:10pm | Jul 25, 2026 12:10pm | Jul 25, 2026 12:10pm |  |  | Fair | No | Westmoreland
Outage | J.E.26.07.31191 | C001865031 | Raheem Ricketts | Westmoreland | Completed | Load_238992 | Paradise - 110 | Jul 25, 2026 11:05am | Jul 25, 2026 11:07am | Jul 25, 2026 12:07pm | Jul 25, 2026 12:07pm | Jul 25, 2026 12:07pm | Jul 25, 2026 12:09pm | Jul 25, 2026 12:09pm | Jul 25, 2026 12:09pm |  |  | Fair | No | Westmoreland call
Non-Outage | J.E.26.07.30383 | C001865027 | Cliton Henry | St.Ann | Completed | Load_261992 | Upper White River - 110 | Jul 25, 2026 11:02am | Jul 25, 2026 11:03am | Jul 25, 2026 3:43pm | Jul 25, 2026 3:43pm | Jul 25, 2026 4:41pm | Jul 25, 2026 5:02pm | Jul 25, 2026 5:05pm | Jul 25, 2026 5:05pm |  |  | Fair | No | The premises found ok, Voltage found 108-119/228 volts
Outage | J.E.26.07.31053 | C001865026 | Richman Whyte | Westmoreland | Completed | Load_248686 | Paradise - 310 | Jul 25, 2026 11:00am | Jul 25, 2026 11:01am | Jul 25, 2026 11:27am | Jul 25, 2026 11:27am | Jul 25, 2026 11:27am | Jul 25, 2026 11:27am | Jul 25, 2026 11:29am | Jul 25, 2026 11:29am |  |  | Fair | No | Meter issue referr to field
Outage | J.E.26.07.31163 | C001865025 | Tajay Bernard | Hanover | Completed | Load_248803 | Orange Bay - 210 | Jul 25, 2026 11:00am | Jul 25, 2026 11:01am | Jul 25, 2026 11:21am | Jul 25, 2026 11:21am | Jul 25, 2026 12:38pm | Jul 25, 2026 12:59pm | Jul 25, 2026 1:02pm | Jul 25, 2026 1:02pm |  |  | Fair | No | Refuse 1 25amp junction fuse
Outage | J.E.26.07.31177 | C001865023 | Stephen Taylor | St.Thomas | Completed | Load_260086 | Lysson - 410 | Jul 25, 2026 10:51am | Jul 25, 2026 10:51am | Jul 25, 2026 3:07pm | Jul 25, 2026 3:07pm | Jul 25, 2026 3:41pm | Jul 25, 2026 1:00am | Jul 25, 2026 4:56pm | Jul 25, 2026 4:56pm |  |  | Fair | No | See junction link down no number on pole patrol clear line with switch stick and close up back junction with a 25 amp fuse all customer is now okay
Outage | J.E.26.07.31161 | C001865022 | Stephen Taylor | St.Thomas | Completed | Load_237738 | Lysson - 410 | Jul 25, 2026 10:36am | Jul 25, 2026 10:37am | Jul 25, 2026 1:24pm | Jul 25, 2026 1:24pm | Jul 25, 2026 2:50pm | Jul 25, 2026 2:50pm | Jul 25, 2026 3:07pm | Jul 25, 2026 3:07pm |  |  | Fair | No | Replace 25 kva transformer drop leads and close up 10 kva transformer safely customer is now okay
Non-Outage | J.E.26.07.31169 | C001865021 | Andre Smith | null | Completed | null | null | Jul 25, 2026 10:34am | Jul 25, 2026 10:36am | Jul 25, 2026 11:44am | Jul 25, 2026 11:44am | Jul 25, 2026 1:59pm | Jul 25, 2026 2:21pm | Jul 25, 2026 2:21pm | Jul 25, 2026 2:21pm | BrokenPole |  | Fair | No | 40ft broken tee pole found cause by vehicle accident maintenance department required
Outage | J.E.26.07.31143 | C001865020 | Christopher Edwards | KSAN | Completed | Load_259627 | Constant Spring - 310 | Jul 25, 2026 10:34am | Jul 25, 2026 10:35am | Jul 25, 2026 12:42pm | Jul 25, 2026 1:34pm | Jul 25, 2026 1:34pm | Jul 25, 2026 2:04pm | Jul 25, 2026 2:04pm | Jul 25, 2026 2:04pm |  |  | Fair | No | Check and found okSupply is at the premises
Outage | J.E.26.07.31138 | C001865016 | Hopeton Henry | St.Thomas | Completed | Load_255852 | Good Year - 210 | Jul 25, 2026 10:21am | Jul 25, 2026 10:22am | Jul 25, 2026 11:54am | Jul 25, 2026 11:56am | Jul 25, 2026 11:57am | Jul 25, 2026 11:57am | Jul 25, 2026 11:58am | Jul 25, 2026 11:58am | Fire |  | Fair | No | Issue resolved
Outage | J.E.26.07.31132 | C001865014 | Christopher Edwards | KSAN | Completed | Load_256191 | Constant Spring - 310 | Jul 25, 2026 10:05am | Jul 25, 2026 10:05am | Jul 25, 2026 11:45am | Jul 25, 2026 12:16pm | Jul 25, 2026 12:17pm | Jul 25, 2026 12:42pm | Jul 25, 2026 12:42pm | Jul 25, 2026 12:42pm |  |  | Fair | No | Customer meter pole is damaged Truck tore down customer service wireAnd damaged stanchion Customer was advised to fix stanchion before service can be connected
Non-Outage | J.E.26.07.30782 | C001865013 | Edward Royal | KSAS | Completed | Load_248244 | Cane River - 310 | Jul 25, 2026 9:59am | Jul 25, 2026 9:59am | Jul 25, 2026 10:57am | Jul 25, 2026 10:57am | Jul 25, 2026 10:57am | Jul 25, 2026 10:57am | Jul 25, 2026 10:57am | Jul 25, 2026 10:57am |  |  | Fair | No | Call related
Non-Outage | J.E.26.07.31080 | C001865008 | Daniel Francis | St.Ann | Completed | Load_245767 | Ocho Rios - 310 | Jul 25, 2026 9:51am | Jul 25, 2026 3:51pm | Jul 25, 2026 4:31pm | Jul 25, 2026 4:31pm | Jul 25, 2026 5:32pm | Jul 25, 2026 5:38pm | Jul 25, 2026 5:38pm | Jul 25, 2026 5:38pm |  |  | Fair | No | Found ok voltage 117/117/234
Outage | J.E.26.07.31095 | C001865010 | Andre Williams | Trelawny | Completed | Load_572266 | Duncans - 110 | Jul 25, 2026 9:51am | Jul 25, 2026 9:52am | Jul 25, 2026 10:04am | Jul 25, 2026 10:04am | Jul 25, 2026 10:04am | Jul 25, 2026 10:18am | Jul 25, 2026 10:19am | Jul 25, 2026 10:19am |  |  | Fair | No | Inspect secondary,re fuse and close blown 5 amp junction on 100 kva transformer (replace 5 amp with 10 amp
Outage | J.E.26.07.31098 | C001865011 | Andre Williams | Trelawny | Completed | Load_1001529 | Duncans - 110 | Jul 25, 2026 9:51am | Jul 25, 2026 9:52am | Jul 25, 2026 10:23am | Jul 25, 2026 10:53am | Jul 25, 2026 11:37am | Jul 25, 2026 12:04pm | Jul 25, 2026 12:04pm | Jul 25, 2026 12:04pm |  |  | Fair | No | Spice and retention damage #6twisted on customer 3 wire service voltage 113+113=226
Outage | J.E.26.07.31115 | C001865009 | Andre Williams | Trelawny | Completed | Load_572265 | Duncans - 110 | Jul 25, 2026 9:51am | Jul 25, 2026 9:52am | Jul 25, 2026 10:19am | Jul 25, 2026 10:19am | Jul 25, 2026 10:19am | Jul 25, 2026 10:22am | Jul 25, 2026 10:23am | Jul 25, 2026 10:23am |  |  | Fair | No | Inspect secondary,re fuse and close blown 5 amp junction on 100 kva transformer (replace 5 amp with 10 amp
Outage | J.E.26.07.30769 | C001865007 | Marlon Authors | Manchester | Completed | Load_292518 | Spur Tree - 210 | Jul 25, 2026 9:42am | Jul 25, 2026 9:42am | Jul 25, 2026 11:24am | Jul 25, 2026 11:24am | Jul 25, 2026 12:58pm | Jul 25, 2026 1:29pm | Jul 25, 2026 1:29pm | Jul 25, 2026 1:29pm | Fire |  | Fair | No | Patrol and found one pole span of secondary upper phase and neutral conductor bonded together caused by illegal connection . Retention same and replace one blown 3 amp fuse that protects 25 kva transformer circuit no pole #. Restored supply okay
Outage | J.E.26.07.31108 | C001865006 | Jowayne Newmans | Portland | Completed | Load_267978 | Port Antonio - 310 | Jul 25, 2026 9:41am | Jul 25, 2026 9:48am | Jul 25, 2026 11:57am | Jul 25, 2026 11:57am | Jul 25, 2026 12:33pm | Jul 25, 2026 12:58pm | Jul 25, 2026 12:58pm | Jul 25, 2026 12:58pm |  |  | Fair | No | Patrol and found 15 amp junction fuse blown cause by overgrown vegetation on transformer, repair by removing vegetation off transformer and replace 15 amp fuse. Customer now has electricity.
Non-Outage | J.E.26.07.30334 | C001865005 | Raheem Ricketts | null | Completed | null | null | Jul 25, 2026 9:40am | Jul 25, 2026 9:42am | Jul 25, 2026 10:07am | Jul 25, 2026 10:07am | Jul 25, 2026 10:07am | Jul 25, 2026 10:08am | Jul 25, 2026 10:08am | Jul 25, 2026 10:08am |  |  | Fair | No | Customer says power has been restored from yesterday
Outage | J.E.26.07.30699 | C001865004 | Raheem Ricketts | Manchester | Completed | Load_259751 | Spur Tree - 210 | Jul 25, 2026 9:40am | Jul 25, 2026 9:40am | Jul 25, 2026 10:03am | Jul 25, 2026 10:03am | Jul 25, 2026 10:06am | Jul 25, 2026 10:07am | Jul 25, 2026 10:07am | Jul 25, 2026 10:07am |  |  | Fair | No | Customer says power has been restored
Outage | J.E.26.07.31078 | C001865003 | Raheem Ricketts | St.Elizabeth | Completed | Load_259710 | Maggotty - 210 | Jul 25, 2026 9:40am | Jul 25, 2026 9:40am | Jul 25, 2026 12:10pm | Jul 25, 2026 12:10pm | Jul 25, 2026 12:15pm | Jul 25, 2026 12:17pm | Jul 25, 2026 12:17pm | Jul 25, 2026 12:17pm |  |  | Fair | No | Unable to locate customer cell phone went voicemail after several calls
Outage | J.E.26.07.31093 | C001865002 | Raheem Ricketts | Manchester | Completed | Load_244726 | Spur Tree - 210 | Jul 25, 2026 9:40am | Jul 25, 2026 9:40am | Jul 25, 2026 10:15am | Jul 25, 2026 10:15am | Jul 25, 2026 11:47am | Jul 25, 2026 12:07pm | Jul 25, 2026 12:07pm | Jul 25, 2026 12:07pm |  |  | Fair | No | Check on found one leg of customer service wire burn off at pole remake joint at pole using 1 clamp
Outage | J.E.26.07.27462 | C001864995 | Wan Carlos Scarlett | Portmore | Completed | Load_247524 | Naggo Head - 510 | Jul 25, 2026 9:12am | Jul 25, 2026 9:13am | Jul 25, 2026 10:19am | Jul 25, 2026 10:37am | Jul 25, 2026 11:00am | Jul 25, 2026 11:15am | Jul 25, 2026 11:16am | Jul 25, 2026 11:16am |  |  | Fair | No | Reach on location been calling customer but got no answer premises closed
Outage | J.E.26.07.31022 | C001864994 | Wan Carlos Scarlett | Portmore | Completed | Load_570289 | Naggo Head - 510 | Jul 25, 2026 9:12am | Jul 25, 2026 9:13am | Jul 25, 2026 10:17am | Jul 25, 2026 10:18am | Jul 25, 2026 10:18am | Jul 25, 2026 10:18am | Jul 25, 2026 10:19am | Jul 25, 2026 10:19am |  |  | Fair | No | Call related to outage earlier customer confirmed that power supply has been restored
Outage | J.E.26.07.31066 | C001864996 | Wan Carlos Scarlett | Portmore | Completed | Load_255016 | Naggo Head - 510 | Jul 25, 2026 9:12am | Jul 25, 2026 9:13am | Jul 25, 2026 9:54am | Jul 25, 2026 9:54am | Jul 25, 2026 10:13am | Jul 25, 2026 10:15am | Jul 25, 2026 10:17am | Jul 25, 2026 10:17am |  |  | Fair | No | Refuse 40 Amps junction pole# 016275 nothing was found on primary line cause by lightning strike
Outage | J.E.26.07.25372 | C001864990 | Nickolas Rodriques | St.Catherine | Completed | Load_568559 | Tredegar - 510 | Jul 25, 2026 8:54am | Jul 25, 2026 8:59am | Jul 25, 2026 11:22am | Jul 25, 2026 12:06pm | Jul 25, 2026 12:50pm | Jul 25, 2026 1:14pm | Jul 25, 2026 1:18pm | Jul 25, 2026 1:18pm |  |  | Fair | No | Unable to locate or communicate with the customer after several attempts. Need proper directions.
Outage | J.E.26.07.31016 | C001864989 | Ricky Hall | St.Catherine | Completed | Load_259788 | New Michelton - 410 | Jul 25, 2026 8:51am | Jul 25, 2026 8:53am | Jul 25, 2026 10:27am | Jul 25, 2026 10:27am | Jul 25, 2026 11:24am | Jul 25, 2026 11:58am | Jul 25, 2026 11:59am | Jul 25, 2026 11:59am |  |  | Rains | No | Replaced blown 10 amps junction fuse
Non-Outage | J.E.26.07.31037 | C001864985 | Jowayne Newmans | Portland | Completed | Load_245356 | Port Antonio - 310 | Jul 25, 2026 8:48am | Jul 25, 2026 8:55am | Jul 25, 2026 9:40am | Jul 25, 2026 9:40am | Jul 25, 2026 11:34am | Jul 25, 2026 11:55am | Jul 25, 2026 11:55am | Jul 25, 2026 11:55am |  |  | Fair | No | Customer was experiencing high voltage 118v, 125v cause by service wire neutral conductor broke. Repair by reconnecting neutral conductor using 2 one bolt clamps. Voltage reading after repair 118v, 118v, 236v.
Outage | J.E.26.07.28739 | C001864986 | Nickolas Rodriques | St.Catherine | Completed | Load_245504 | Twickenham - 310 | Jul 25, 2026 8:48am | Jul 25, 2026 8:50am | Jul 25, 2026 10:51am | Jul 25, 2026 10:59am | Jul 25, 2026 11:13am | Jul 25, 2026 11:16am | Jul 25, 2026 11:21am | Jul 25, 2026 11:21am |  |  | Fair | No | Power restored. Customer stated that there was an area outage which was later restored.
Outage | J.E.26.07.29079 | C001864987 | Nickolas Rodriques | St.Catherine | Completed | Load_248722 | Twickenham - 310 | Jul 25, 2026 8:48am | Jul 25, 2026 8:50am | Jul 25, 2026 8:59am | Jul 25, 2026 9:10am | Jul 25, 2026 10:24am | Jul 25, 2026 10:48am | Jul 25, 2026 10:50am | Jul 25, 2026 10:50am |  |  | Fair | No | Found customer with electricity. Customer confirmed that the area outage was restored.
Outage | J.E.26.07.29115 | C001864988 | Nickolas Rodriques | St.Catherine | Completed | Load_302299 | Rhodens Pen - 210 | Jul 25, 2026 8:48am | Jul 25, 2026 8:50am | Jul 25, 2026 1:18pm | Jul 25, 2026 1:21pm | Jul 25, 2026 2:15pm | Jul 25, 2026 2:39pm | Jul 25, 2026 2:40pm | Jul 25, 2026 2:40pm |  |  | Fair | No | Customer stated that the area outage was restored.
Outage | J.E.26.07.30909 | C001864984 | Hartley Chin | St.Catherine | Completed | Load_241586 | Rhodens Pen - 310 | Jul 25, 2026 8:45am | Jul 25, 2026 8:47am | Jul 25, 2026 8:54am | Jul 25, 2026 8:56am | Jul 25, 2026 9:42am | Jul 25, 2026 9:53am | Jul 25, 2026 9:54am | Jul 25, 2026 9:54am |  |  | Fair | No | Found okay … voltage read 114v , 115v ..
Non-Outage | J.E.26.07.26373 | C001864982 | Neville Spencer | null | Completed | null | null | Jul 25, 2026 8:44am | Jul 25, 2026 8:44am | Jul 25, 2026 10:42am | Jul 25, 2026 10:42am | Jul 25, 2026 11:33am | Jul 25, 2026 11:33am | Jul 25, 2026 11:34am | Jul 25, 2026 11:34am |  |  | Fair | No | Found ok.
Non-Outage | J.E.26.07.27032 | C001864980 | Neville Spencer | null | Completed | null | null | Jul 25, 2026 8:44am | Jul 25, 2026 8:44am | Jul 25, 2026 11:36am | Jul 25, 2026 11:36am | Jul 25, 2026 1:10pm | Jul 25, 2026 1:11pm | Jul 25, 2026 1:11pm | Jul 25, 2026 1:11pm |  |  | Fair | No | Unable to locate customer.
Non-Outage | J.E.26.07.29815 | C001864983 | Cliton Henry | null | Completed | null | null | Jul 25, 2026 8:44am | Jul 25, 2026 1:10pm | Jul 25, 2026 2:04pm | Jul 25, 2026 2:05pm | Jul 25, 2026 2:50pm | Jul 25, 2026 2:57pm | Jul 25, 2026 3:00pm | Jul 25, 2026 3:00pm | LowHangingWires |  | Fair | No | A low primary neutral conductor found cross country, two poles need to be straightened and the line bushing. Kindly refer to St. Mary Operations for maintenance work.
Non-Outage | J.E.26.07.30828 | C001864981 | Romaine Roberts | St.Mary | Completed | Load_265580 | Highgate - 210 | Jul 25, 2026 8:44am | Jul 25, 2026 8:46am | Jul 25, 2026 10:56am | Jul 25, 2026 10:56am | Jul 25, 2026 12:08pm | Jul 25, 2026 1:07pm | Jul 25, 2026 1:07pm | Jul 25, 2026 1:07pm |  |  | Fair | No | Premises not found
Outage | J.E.26.07.29708 | C001864977 | Neville Spencer | Clarendon | Completed | Load_260924 | May Pen - 210 | Jul 25, 2026 8:44am | Jul 25, 2026 8:44am | Jul 25, 2026 9:25am | Jul 25, 2026 9:25am | Jul 25, 2026 10:07am | Jul 25, 2026 10:32am | Jul 25, 2026 10:32am | Jul 25, 2026 10:32am |  |  | Fair | No | Removed defective lightning arrester from 5 kva xmf in bank of 3 at pole # 0125732 . Also renew 2 blown 2 amp fuse supply restored.
Outage | J.E.26.07.30248 | C001864978 | Neville Spencer | Clarendon | Completed | Load_245215 | Monymusk - 410 | Jul 25, 2026 8:44am | Jul 25, 2026 8:44am | Jul 25, 2026 10:41am | Jul 25, 2026 10:41am | Jul 25, 2026 10:41am | Jul 25, 2026 10:41am | Jul 25, 2026 10:42am | Jul 25, 2026 10:42am |  |  | Fair | No | Found ok.
Outage | J.E.26.07.30442 | C001864979 | Neville Spencer | Clarendon | Completed | Load_246356 | Parnassus - 310 | Jul 25, 2026 8:44am | Jul 25, 2026 8:44am | Jul 25, 2026 10:37am | Jul 25, 2026 10:37am | Jul 25, 2026 10:37am | Jul 25, 2026 10:37am | Jul 25, 2026 10:38am | Jul 25, 2026 10:38am |  |  | Fair | No | Found ok,
Outage | J.E.26.07.31054 | C001864976 | Elvis Trowers | KSAS | Completed | Load_261930 | Duhaney - 310 | Jul 25, 2026 8:40am | Jul 25, 2026 8:51am | Jul 25, 2026 1:36pm | Jul 25, 2026 1:36pm | Jul 25, 2026 1:57pm | Jul 25, 2026 2:02pm | Jul 25, 2026 2:02pm | Jul 25, 2026 2:02pm |  |  | Fair | Yes | Premises found closed upon arrival and when customer was contacted he said that he’s not at home just now but at work and won’t be home until later this evening.
Non-Outage | J.E.26.07.24918 | C001864975 | Stephen Taylor | St.Thomas | Completed | Load_577137 | Lysson - 410 | Jul 25, 2026 8:38am | Jul 25, 2026 8:40am | Jul 25, 2026 5:47pm | Jul 25, 2026 5:47pm | Jul 25, 2026 5:50pm | Jul 25, 2026 5:50pm | Jul 25, 2026 5:52pm | Jul 25, 2026 5:52pm |  |  | Fair | No | Need more information a lot of call to customer no one answered the phone
Non-Outage | J.E.26.07.25512 | C001864974 | Stephen Taylor | St.Thomas | Completed | Load_269349 | Lysson - 410 | Jul 25, 2026 8:38am | Jul 25, 2026 8:39am | Jul 25, 2026 7:08pm | Jul 25, 2026 7:08pm | Jul 25, 2026 7:08pm | Jul 25, 2026 7:09pm | Jul 25, 2026 7:09pm | Jul 25, 2026 7:09pm |  |  | Fair | No | When in the area power is in the area a lot of call to single customer no one answered the phone
Non-Outage | J.E.26.07.30216 | C001864973 | Stephen Taylor | St.Thomas | Completed | Load_238108 | Lysson - 410 | Jul 25, 2026 8:38am | Jul 25, 2026 8:39am | Jul 25, 2026 5:52pm | Jul 25, 2026 5:52pm | Jul 25, 2026 6:29pm | Jul 25, 2026 6:29pm | Jul 25, 2026 6:56pm | Jul 25, 2026 6:56pm |  |  | Fair | No | Clean up single use 2 clamps customer is now okay reading 111,112,223
Non-Outage | J.E.26.07.31052 | C001864972 | Stephen Taylor | St.Thomas | Completed | Load_248385 | Lysson - 410 | Jul 25, 2026 8:38am | Jul 25, 2026 8:39am | Jul 25, 2026 9:41am | Jul 25, 2026 9:41am | Jul 25, 2026 10:26am | Jul 25, 2026 10:26am | Jul 25, 2026 10:27am | Jul 25, 2026 10:27am |  |  | Fair | No | Clean up single reading 112 customer is now okay
Outage | J.E.26.07.31042 | C001864971 | Andre Smith | KSAN | Completed | Load_575407 | Washington Blvd - 710 | Jul 25, 2026 8:36am | Jul 25, 2026 8:39am | Jul 25, 2026 9:15am | Jul 25, 2026 9:15am | Jul 25, 2026 9:58am | Jul 25, 2026 10:12am | Jul 25, 2026 10:14am | Jul 25, 2026 10:14am |  |  | Fair | No | Replace blown junction fuses 15A/30A cause by birds making contact with conductor
Non-Outage | J.E.26.07.15379 | C001864970 | Hopeton Henry | St.Thomas | Completed | Load_259414 | Good Year - 210 | Jul 25, 2026 8:35am | Jul 25, 2026 8:36am | Jul 25, 2026 11:54am | Jul 25, 2026 12:29pm | Jul 25, 2026 12:29pm | Jul 25, 2026 3:09pm | Jul 25, 2026 3:10pm | Jul 25, 2026 3:10pm |  |  | Fair | No | Check and found low voltage at the end of the circuit 118-100-217 volts refer to maintenance to do detail patrol
Non-Outage | J.E.26.07.25415 | C001864969 | Hopeton Henry | St.Thomas | Completed | Load_263983 | Good Year - 210 | Jul 25, 2026 8:35am | Jul 25, 2026 8:35am | Jul 25, 2026 11:54am | Jul 25, 2026 3:11pm | Jul 25, 2026 3:11pm | Jul 25, 2026 3:11pm | Jul 25, 2026 3:11pm | Jul 25, 2026 3:11pm |  |  | Fair | No | Customer not located
Non-Outage | J.E.26.07.26101 | C001864967 | Hopeton Henry | St.Thomas | Completed | Load_246172 | Good Year - 110 | Jul 25, 2026 8:34am | Jul 25, 2026 8:35am | Jul 25, 2026 11:54am | Jul 25, 2026 4:57pm | Jul 25, 2026 5:01pm | Jul 25, 2026 5:01pm | Jul 25, 2026 5:02pm | Jul 25, 2026 5:02pm |  |  | Fair | No | Customer not located
Non-Outage | J.E.26.07.26867 | C001864966 | Hopeton Henry | St.Thomas | Completed | Load_252737 | Good Year - 110 | Jul 25, 2026 8:34am | Jul 25, 2026 8:35am | Jul 25, 2026 11:54am | Jul 25, 2026 3:12pm | Jul 25, 2026 4:31pm | Jul 25, 2026 4:33pm | Jul 25, 2026 4:35pm | Jul 25, 2026 4:35pm |  |  | Fair | No | Customer not located
Outage | J.E.26.07.31043 | C001864965 | Milton Charlton | KSAN | Completed | Load_243463 | Hope - 510 | Jul 25, 2026 8:26am | Jul 25, 2026 8:26am | Jul 25, 2026 5:08pm | Jul 25, 2026 5:09pm | Jul 25, 2026 5:36pm | Jul 25, 2026 5:40pm | Jul 25, 2026 5:37pm | Jul 25, 2026 5:37pm |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.07.31045 | C001864964 | Christopher Edwards | KSAN | Completed | Load_266471 | Constant Spring - 410 | Jul 25, 2026 8:26am | Jul 25, 2026 8:26am | Jul 25, 2026 10:29am | Jul 25, 2026 10:29am | Jul 25, 2026 10:29am | Jul 25, 2026 11:43am | Jul 25, 2026 11:44am | Jul 25, 2026 11:44am |  |  | Fair | No | Defective meter Meter is burnt and needs to be replaced
Non-Outage | J.E.26.07.27753 | C001864962 | Cliton Henry | null | Completed | null | null | Jul 25, 2026 8:20am | Jul 25, 2026 8:22am | Jul 25, 2026 9:07am | Jul 25, 2026 9:31am | Jul 25, 2026 10:14am | Jul 25, 2026 10:31am | Jul 25, 2026 10:33am | Jul 25, 2026 10:33am |  |  | Fair | No | A wrapped joint found at the customer pothead was reconnected using 1-#2-#2 pen unions. Voltages left 119-120/239 volts.
Non-Outage | J.E.26.07.29551 | C001864963 | Cliton Henry | St.Mary | Completed | Load_350817 | Oracabessa - 110 | Jul 25, 2026 8:20am | Jul 25, 2026 8:22am | Jul 25, 2026 10:34am | Jul 25, 2026 11:07am | Jul 25, 2026 11:47am | Jul 25, 2026 11:48am | Jul 25, 2026 12:03pm | Jul 25, 2026 12:03pm |  |  | Fair | No | A defective service wire was replaced using approximately 70 feet #6 triplex and 6- one bolt clamps. Voltages left 118-118/237 volts.
Non-Outage | J.E.26.07.29789 | C001864961 | Cliton Henry | null | Completed | null | null | Jul 25, 2026 8:16am | Jul 25, 2026 8:18am | Jul 25, 2026 10:33am | Jul 25, 2026 10:33am | Jul 25, 2026 10:33am | Jul 25, 2026 10:33am | Jul 25, 2026 10:34am | Jul 25, 2026 10:34am |  |  | Fair | No | Supply found ok, same as 29789
Non-Outage | J.E.26.07.16494 | C001864960 | Kenroy Dale | Manchester | Completed | Load_263892 | Porus - 210 | Jul 25, 2026 8:10am | Jul 25, 2026 8:12am | Jul 25, 2026 10:24am | Jul 25, 2026 10:24am | Jul 25, 2026 11:07am | Jul 25, 2026 12:06pm | Jul 25, 2026 12:14pm | Jul 25, 2026 12:14pm |  |  | Fair | No | Opened 25 kva transformer to retention secondary lower phase and remake connection at pole, conductor was retention and connection at pole remade using three 1bolt clamp. Transformer was re-closed and area now with supply
Non-Outage | J.E.26.07.23186 | C001864959 | Kenroy Dale | Manchester | Completed | Load_241025 | Porus - 310 | Jul 25, 2026 8:10am | Jul 25, 2026 8:12am | Jul 25, 2026 8:20am | Jul 25, 2026 8:20am | Jul 25, 2026 9:46am | Jul 25, 2026 10:23am | Jul 25, 2026 10:24am | Jul 25, 2026 10:24am | Fire |  | Fair | No | Low hanging service wire causing fire when there is heavy wind, service wire was retention and area now safe
Outage | J.E.26.07.30997 | C001864958 | Marlon Brown | Trelawny | Completed | Load_247929 | Greenwood - 110 | Jul 25, 2026 8:03am | Jul 26, 2026 9:34am | Jul 26, 2026 9:44am | Jul 26, 2026 1:39pm | Jul 26, 2026 1:39pm | Jul 26, 2026 1:42pm | Jul 26, 2026 1:42pm | Jul 26, 2026 1:42pm |  |  | Fair | No | Meter is burnt. Refer to Field Service Department
Non-Outage | J.E.26.07.30419 | C001864957 | Andre Williams | Trelawny | Completed | Load_295088 | Duncans - 110 | Jul 25, 2026 7:58am | Jul 25, 2026 7:58am | Jul 25, 2026 8:35am | Jul 25, 2026 8:38am | Jul 25, 2026 8:55am | Jul 25, 2026 8:56am | Jul 25, 2026 8:57am | Jul 25, 2026 8:57am |  |  | Fair | No | Issue resulting from problem with rotation on feeder section maintenance aware of pending issue
Non-Outage | J.E.26.07.31032 | C001864956 | Edward Royal | null | Completed | null | null | Jul 25, 2026 7:58am | Jul 25, 2026 8:15am | Jul 25, 2026 9:17am | Jul 25, 2026 9:17am | Jul 25, 2026 9:17am | Jul 25, 2026 10:26am | Jul 25, 2026 10:27am | Jul 25, 2026 10:27am | BrokenWire |  | Fair | No | Replaced secondary insulation to cross arm
Non-Outage | J.E.26.07.30208 | C001864954 | Elvis Trowers | KSAN | Completed | Load_238411 | West Kings House - 410 | Jul 25, 2026 7:55am | Jul 25, 2026 7:56am | Jul 25, 2026 11:51am | Jul 25, 2026 11:51am | Jul 25, 2026 12:29pm | Jul 25, 2026 12:37pm | Jul 25, 2026 12:37pm | Jul 25, 2026 12:37pm | BrokenPole |  | Fair | Yes | Happened to be internal when checked, customer was advised to contact an electrician to get the situation resolved, it’s their private pole.
Non-Outage | J.E.26.07.30332 | C001864951 | Milton Charlton | KSAN | Completed | Load_578935 | Hope - 510 | Jul 25, 2026 7:54am | Jul 25, 2026 7:55am | Jul 25, 2026 9:08am | Jul 25, 2026 9:08am | Jul 25, 2026 10:26am | Jul 25, 2026 9:35am | Jul 25, 2026 10:28am | Jul 25, 2026 10:28am |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Non-Outage | J.E.26.07.30746 | C001864949 | Milton Charlton | KSAN | Completed | Load_246577 | Hope - 410 | Jul 25, 2026 7:54am | Jul 25, 2026 7:55am | Jul 25, 2026 4:42pm | Jul 25, 2026 4:44pm | Jul 25, 2026 4:46pm | Jul 25, 2026 5:05pm | Jul 25, 2026 5:08pm | Jul 25, 2026 5:08pm |  |  | Fair | No | Change 1-bolt clamps on customer #6 triplex service wire using two 1- bolt clamps.
Non-Outage | J.E.26.07.30835 | C001864953 | Christopher Edwards | KSAN | Completed | Load_249915 | Constant Spring - 410 | Jul 25, 2026 7:54am | Jul 25, 2026 7:55am | Jul 25, 2026 8:03am | Jul 25, 2026 8:45am | Jul 25, 2026 8:45am | Jul 25, 2026 10:28am | Jul 25, 2026 10:29am | Jul 25, 2026 10:29am |  |  | Fair | No | Remake burnt open secondary neutral jumper joint Using (2) one bolt clamps Voltage:114,115,230v
Non-Outage | J.E.26.07.31004 | C001864950 | Elvis Trowers | KSAN | Completed | Load_256996 | Washington Blvd - 510 | Jul 25, 2026 7:54am | Jul 25, 2026 7:55am | Jul 25, 2026 11:24am | Jul 25, 2026 11:24am | Jul 25, 2026 11:43am | Jul 25, 2026 11:51am | Jul 25, 2026 11:51am | Jul 25, 2026 11:51am |  |  | Fair | Yes | Premises found closed upon arrival and customer could not be contacted by telephone either after several calls and was unable to leave a voice message.
Outage | J.E.26.07.30506 | C001864946 | Marlon Brown | Trelawny | Completed | Load_257854 | Greenwood - 110 | Jul 25, 2026 7:47am | Jul 26, 2026 9:34am | Jul 26, 2026 9:59am | Jul 26, 2026 9:59am | Jul 26, 2026 11:14am | Jul 26, 2026 1:38pm | Jul 26, 2026 1:39pm | Jul 26, 2026 1:39pm |  |  | Fair | No | Refer to maintenance.
Outage | J.E.26.07.30960 | C001864945 | Andre Smith | KSAS | Completed | Load_295258 | Hunts Bay - 710 | Jul 25, 2026 7:46am | Jul 25, 2026 7:46am | Jul 25, 2026 10:14am | Jul 25, 2026 10:14am | Jul 25, 2026 11:36am | Jul 25, 2026 11:44am | Jul 25, 2026 11:44am | Jul 25, 2026 11:44am |  |  | Fair | No | Supply restored with the assistance of callcenter
Outage | J.E.26.07.30970 | C001864944 | Kaydon Taylor | KSAS | Completed | Load_252375 | Three Miles - 410 | Jul 25, 2026 7:45am | Jul 25, 2026 3:37pm | Jul 25, 2026 9:32pm | Jul 25, 2026 9:35pm | Jul 25, 2026 10:04pm | Jul 25, 2026 11:07pm | Jul 25, 2026 11:07pm | Jul 25, 2026 11:07pm | Fire |  | Fair | No | Isolate bank of two transformer (100 n 25 kva) at pole #0022454 to carry out repairs. 5’of #2/0 wire 4 clamps
Non-Outage | J.E.26.07.29700 | C001864943 | Tajay Bernard | St.James | Completed | Load_1001216 | Bogue - 510 | Jul 25, 2026 7:44am | Jul 25, 2026 7:44am | Jul 25, 2026 8:06am | Jul 25, 2026 8:07am | Jul 25, 2026 8:07am | Jul 25, 2026 8:08am | Jul 25, 2026 8:09am | Jul 25, 2026 8:09am |  |  | Fair | No | Customer stated that the issue has been resolved
Non-Outage | J.E.26.05.07314 | C001864940 | Tajay Bernard | St.James | Completed | Load_260871 | Bogue - 510 | Jul 25, 2026 7:41am | Jul 25, 2026 7:43am | Jul 25, 2026 8:02am | Jul 25, 2026 11:01am | Jul 25, 2026 11:13am | Jul 25, 2026 11:13am | Jul 25, 2026 11:13am | Jul 25, 2026 11:13am |  |  | Fair | No | Customer stated that the issue has been resolved
Non-Outage | J.E.26.07.22306 | C001864939 | Tajay Bernard | Hanover | Completed | Load_245538 | Orange Bay - 310 | Jul 25, 2026 7:41am | Jul 25, 2026 7:43am | Jul 25, 2026 8:10am | Jul 25, 2026 8:11am | Jul 25, 2026 9:15am | Jul 25, 2026 9:28am | Jul 25, 2026 9:30am | Jul 25, 2026 9:30am |  |  | Fair | No | Customer has internal problems, problems has to be fixed before any work can be done
Non-Outage | J.E.26.07.30530 | C001864942 | Stephen Taylor | null | Completed | null | null | Jul 25, 2026 7:41am | Jul 25, 2026 7:42am | Jul 25, 2026 11:29am | Jul 25, 2026 11:29am | Jul 25, 2026 12:48pm | Jul 25, 2026 12:48pm | Jul 25, 2026 12:49pm | Jul 25, 2026 12:49pm | BrokenWire |  | Fair | No | Patrol see nothing and close up back 25 kva transformer with a 3 amp fuse all customer is now okay
Non-Outage | J.E.26.07.30913 | C001864941 | Hopeton Henry | null | Completed | null | null | Jul 25, 2026 7:41am | Jul 25, 2026 8:37am | Jul 25, 2026 9:44am | Jul 25, 2026 9:44am | Jul 25, 2026 9:44am | Jul 25, 2026 11:55am | Jul 25, 2026 11:56am | Jul 25, 2026 11:56am | Fire |  | Fair | No | Splice and retention secondary conductors
Non-Outage | J.E.26.02.41081 | C001864938 | Javid Vernon | Westmoreland | Completed | Load_248629 | Orange Bay - 310 | Jul 25, 2026 7:33am | Jul 25, 2026 7:33am | Jul 25, 2026 11:02am | Jul 25, 2026 11:02am | Jul 25, 2026 11:02am | Jul 25, 2026 11:02am | Jul 25, 2026 11:04am | Jul 25, 2026 11:04am |  |  | Fair | No | Unable to locate customer on premises phone calls to customer number went unanswered
Non-Outage | J.E.26.02.42129 | C001864937 | Javid Vernon | Westmoreland | Completed | Load_250890 | Paradise - 110 | Jul 25, 2026 7:33am | Jul 25, 2026 7:33am | Jul 25, 2026 8:19am | Jul 25, 2026 8:19am | Jul 25, 2026 8:19am | Jul 25, 2026 8:20am | Jul 25, 2026 8:20am | Jul 25, 2026 8:20am |  |  | Fair | No | Customer stated that the issue has been resolved
Non-Outage | J.E.26.02.42630 | C001864936 | Javid Vernon | Westmoreland | Completed | Load_239491 | Orange Bay - 310 | Jul 25, 2026 7:32am | Jul 25, 2026 7:33am | Jul 25, 2026 10:49am | Jul 25, 2026 10:49am | Jul 25, 2026 10:49am | Jul 25, 2026 10:50am | Jul 25, 2026 10:50am | Jul 25, 2026 10:50am |  |  | Fair | No | Customer stated that the issue has been resolved
Non-Outage | J.E.26.07.25083 | C001864935 | Tyrese Williams | St.Ann | Completed | Load_267649 | Cardiff Hall - 310 | Jul 25, 2026 7:31am | Jul 25, 2026 7:34am | Jul 25, 2026 8:18am | Jul 25, 2026 2:40pm | Jul 25, 2026 2:40pm | Jul 25, 2026 2:40pm | Jul 25, 2026 2:41pm | Jul 25, 2026 2:41pm | Fire |  | Fair | No | Premises not found not getting customer on phone
Non-Outage | J.E.26.07.25108 | C001864933 | Tyrese Williams | St.Ann | Completed | Load_304980 | Cardiff Hall - 310 | Jul 25, 2026 7:31am | Jul 25, 2026 7:34am | Jul 25, 2026 8:18am | Jul 25, 2026 10:24am | Jul 25, 2026 11:47am | Jul 25, 2026 11:54am | Jul 25, 2026 11:55am | Jul 25, 2026 11:55am |  |  | Fair | No | Remade service wire joint at pole use 1 pg clamp
Non-Outage | J.E.26.07.29751 | C001864932 | Javid Vernon | Westmoreland | Completed | Load_292085 | Paradise - 310 | Jul 25, 2026 7:31am | Jul 25, 2026 7:32am | Jul 25, 2026 9:33am | Jul 25, 2026 9:33am | Jul 25, 2026 10:07am | Jul 25, 2026 10:40am | Jul 25, 2026 10:40am | Jul 25, 2026 10:40am |  |  | Fair | No | Check and found customer having high voltage 122/122/244 isolate 25kva transformer to change tap from 3 to 1 after reclosing transformer voltage left 115/115/230
Non-Outage | J.E.26.07.29765 | C001864934 | Javid Vernon | Westmoreland | Completed | Load_246407 | Paradise - 110 | Jul 25, 2026 7:31am | Jul 25, 2026 7:32am | Jul 25, 2026 11:02am | Jul 25, 2026 11:04am | Jul 25, 2026 11:04am | Jul 25, 2026 11:05am | Jul 25, 2026 11:07am | Jul 25, 2026 11:07am |  |  | Fair | No | Unable to locate customer on premises phone calls to customer number went unanswered
Non-Outage | J.E.26.07.25559 | C001864930 | Tyrese Williams | St.Ann | Completed | Load_254196 | Cardiff Hall - 210 | Jul 25, 2026 7:30am | Jul 25, 2026 7:34am | Jul 25, 2026 8:18am | Jul 25, 2026 8:44am | Jul 25, 2026 9:33am | Jul 25, 2026 9:41am | Jul 25, 2026 9:43am | Jul 25, 2026 9:43am |  |  | Fair | No | Premises found ok at the time of visit
Non-Outage | J.E.26.07.29780 | C001864931 | Javid Vernon | Westmoreland | Completed | Load_292666 | Paradise - 110 | Jul 25, 2026 7:30am | Jul 25, 2026 7:32am | Jul 25, 2026 8:20am | Jul 25, 2026 8:24am | Jul 25, 2026 8:55am | Jul 25, 2026 9:28am | Jul 25, 2026 9:33am | Jul 25, 2026 9:33am |  |  | Fair | No | Check and found customer having high voltage 123/123/246 isolate one 25kva transformer to change the tap from 3 to 1 after reclosing transfer voltage left 117/117 234
Non-Outage | J.E.26.07.30170 | C001864929 | Tyrese Williams | St.Ann | Completed | Load_253323 | Cardiff Hall - 310 | Jul 25, 2026 7:30am | Jul 25, 2026 7:34am | Jul 25, 2026 8:18am | Jul 25, 2026 11:55am | Jul 25, 2026 12:48pm | Jul 25, 2026 1:02pm | Jul 25, 2026 1:03pm | Jul 25, 2026 1:03pm |  |  | Fair | No | Remade joint at pole use 1 pg clamp
Non-Outage | J.E.26.07.25089 | C001864928 | Raymond Lewis | St.Ann | Completed | Load_269408 | Ocho Rios - 310 | Jul 25, 2026 7:29am | Jul 25, 2026 7:29am | Jul 25, 2026 9:24am | Jul 25, 2026 9:24am | Jul 25, 2026 9:25am | Jul 25, 2026 9:43pm | Jul 25, 2026 9:44am | Jul 25, 2026 9:44am |  |  | Fair | No | Refuse and close 2 amp junction
Non-Outage | J.E.26.07.26014 | C001864924 | Raymond Lewis | St.Ann | Completed | Load_268866 | Ocho Rios - 310 | Jul 25, 2026 7:29am | Jul 25, 2026 7:29am | Jul 25, 2026 9:45am | Jul 25, 2026 9:45am | Jul 25, 2026 9:48am | Jul 25, 2026 9:50pm | Jul 25, 2026 9:50am | Jul 25, 2026 9:50am |  |  | Fair | No | Travis Brown say that supply restored
Non-Outage | J.E.26.07.26445 | C001864926 | Raymond Lewis | St.Ann | Completed | Load_268866 | Ocho Rios - 310 | Jul 25, 2026 7:29am | Jul 25, 2026 7:29am | Jul 25, 2026 9:51am | Jul 25, 2026 9:51am | Jul 25, 2026 9:51am | Jul 25, 2026 9:53am | Jul 25, 2026 9:54am | Jul 25, 2026 9:54am |  |  | Fair | No | Travis Brown say that supply restored
Non-Outage | J.E.26.07.30694 | C001864927 | Raymond Lewis | null | Completed | null | null | Jul 25, 2026 7:29am | Jul 25, 2026 7:29am | Jul 25, 2026 7:54am | Jul 25, 2026 7:54am | Jul 25, 2026 9:23am | Jul 25, 2026 9:24pm | Jul 25, 2026 9:24am | Jul 25, 2026 9:24am |  |  | Fair | No | Phone not answering
Outage | J.E.26.07.30814 | C001864925 | Richman Whyte | Westmoreland | Completed | Load_253169 | Paradise - 310 | Jul 25, 2026 7:29am | Jul 25, 2026 7:29am | Jul 25, 2026 9:39am | Jul 25, 2026 9:39am | Jul 25, 2026 9:39am | Jul 25, 2026 9:39am | Jul 25, 2026 9:40am | Jul 25, 2026 9:40am |  |  | Fair | No | Customer service issues
Non-Outage | J.E.26.03.11239 | C001864919 | Swon Miller | St.James | Completed | Load_242019 | Queens Drive - 710 | Jul 25, 2026 7:28am | Jul 25, 2026 7:29am | Jul 25, 2026 1:24pm | Jul 25, 2026 1:24pm | Jul 25, 2026 1:26pm | Jul 28, 2026 1:32am | Jul 25, 2026 1:35pm | Jul 25, 2026 1:35pm |  |  | Fair | No | Call related to previous both calls are the same
Non-Outage | J.E.26.05.11477 | C001864922 | Swon Miller | null | Completed | null | null | Jul 25, 2026 7:28am | Jul 25, 2026 7:29am | Jul 25, 2026 1:36pm | Jul 25, 2026 1:36pm | Jul 25, 2026 2:13pm | Jul 6, 2026 2:46pm | Jul 25, 2026 2:50pm | Jul 25, 2026 2:50pm | BrokenPole |  | Fair | No | Check and found okay no fire are broken pole found at location
Non-Outage | J.E.26.05.18379 | C001864920 | Swon Miller | St.James | Completed | Load_242019 | Queens Drive - 710 | Jul 25, 2026 7:28am | Jul 25, 2026 7:29am | Jul 25, 2026 12:37pm | Jul 25, 2026 12:37pm | Jul 25, 2026 12:43pm | Jul 15, 2026 1:20am | Jul 25, 2026 1:22pm | Jul 25, 2026 1:22pm |  |  | Fair | No | Check and found area okay unable to locate customer calls to customer went unanswered voltage found 111/110/221 voltage left 111/110/221
Non-Outage | J.E.26.07.17812 | C001864918 | Swon Miller | St.James | Completed | Load_259109 | Queens Drive - 710 | Jul 25, 2026 7:28am | Jul 25, 2026 7:29am | Jul 25, 2026 5:50pm | Jul 25, 2026 5:50pm | Jul 25, 2026 6:13pm | Jul 28, 2026 6:23am | Jul 25, 2026 6:23pm | Jul 25, 2026 6:23pm |  |  | Fair | No | Check and found okay customer states that the issue was resolved from last week
Non-Outage | J.E.26.07.21483 | C001864917 | Swon Miller | St.James | Completed | Load_238044 | Queens Drive - 710 | Jul 25, 2026 7:28am | Jul 25, 2026 7:29am | Jul 25, 2026 4:51pm | Jul 25, 2026 4:51pm | Jul 25, 2026 4:53pm | Jul 25, 2026 5:03pm | Jul 25, 2026 5:04pm | Jul 25, 2026 5:04pm |  |  | Fair | No | This call is related to the previous
Non-Outage | J.E.26.07.21549 | C001864915 | Swon Miller | St.James | Completed | Load_238044 | Queens Drive - 710 | Jul 25, 2026 7:28am | Jul 25, 2026 7:29am | Jul 25, 2026 3:30pm | Jul 25, 2026 3:30pm | Jul 25, 2026 4:30pm | Jul 25, 2026 4:48pm | Jul 25, 2026 4:51pm | Jul 25, 2026 4:51pm |  |  | Fair | No | Check and found area okay voltage found 115/114/232 customer states that this is an old report voltage left 115/114/231
Non-Outage | J.E.26.07.25152 | C001864914 | Swon Miller | St.James | Completed | Load_265675 | Queens Drive - 710 | Jul 25, 2026 7:28am | Jul 25, 2026 7:29am | Jul 25, 2026 10:44am | Jul 25, 2026 10:44am | Jul 25, 2026 11:09am | Jul 14, 2026 12:25am | Jul 25, 2026 12:35pm | Jul 25, 2026 12:35pm |  |  | Fair | No | Check and found customer single phasing cause by contamination at pole clean and remake joints use 1,pg voltage found 114voltage left 114/113/227
Non-Outage | J.E.26.07.30850 | C001864921 | Swon Miller | null | Completed | null | null | Jul 25, 2026 7:28am | Jul 25, 2026 7:29am | Jul 25, 2026 5:04pm | Jul 25, 2026 5:04pm | Jul 25, 2026 5:27pm | Jul 14, 2026 5:48am | Jul 25, 2026 5:50pm | Jul 25, 2026 5:50pm | Fire |  | Fair | No | Check and found okay no fire found
Non-Outage | J.E.26.07.30897 | C001864916 | Swon Miller | St.James | Completed | Load_247589 | Queens Drive - 710 | Jul 25, 2026 7:28am | Jul 25, 2026 7:29am | Jul 25, 2026 2:51pm | Jul 25, 2026 2:51pm | Jul 25, 2026 3:07pm | Jul 21, 2026 3:25am | Jul 25, 2026 3:26pm | Jul 25, 2026 3:26pm |  |  | Fair | No | Check and found okay please refer to field service
Outage | J.E.26.07.30684 | C001864923 | Richman Whyte | Westmoreland | Completed | Load_244545 | Paradise - 310 | Jul 25, 2026 7:28am | Jul 25, 2026 7:29am | Jul 25, 2026 11:04am | Jul 25, 2026 11:04am | Jul 25, 2026 11:04am | Jul 25, 2026 11:04am | Jul 25, 2026 11:05am | Jul 25, 2026 11:05am |  |  | Fair | No | Unable to locate or contact customer on the phone
Non-Outage | J.E.26.07.25794 | C001864913 | Swon Miller | St.James | Completed | Load_405862 | Rose Hall - 210 | Jul 25, 2026 7:27am | Jul 25, 2026 7:29am | Jul 25, 2026 10:02am | Jul 25, 2026 10:03am | Jul 25, 2026 10:26am | Jul 25, 2026 10:40am | Jul 25, 2026 10:44am | Jul 25, 2026 10:44am |  |  | Fair | No | Unable to locate customer phone calls to customer number went unanswered
Outage | J.E.26.07.30974 | C001864912 | Stephen Taylor | St.Thomas | Completed | Load_260086 | Lysson - 410 | Jul 25, 2026 7:25am | Jul 25, 2026 7:36am | Jul 25, 2026 7:42am | Jul 25, 2026 7:42am | Jul 25, 2026 9:01am | Jul 25, 2026 9:01am | Jul 25, 2026 9:41am | Jul 25, 2026 9:41am |  |  | Fair | No | Transformer fuse out patrol clear bush off line and close up 10 kva transformer 2 amp fuse safely customer is now okay
Non-Outage | J.E.26.02.24632 | C001864911 | Derrick Dawkins | St.James | Completed | Load_243693 | Bogue - 610 | Jul 25, 2026 7:24am | Jul 25, 2026 7:25am | Jul 25, 2026 10:13am | Jul 25, 2026 11:44am | Jul 25, 2026 11:47am | Jul 25, 2026 11:50am | Jul 25, 2026 11:50am | Jul 25, 2026 11:50am |  |  | Fair | No | Checked and found ok 118/117=236
Non-Outage | J.E.26.07.14538 | C001864910 | Derrick Dawkins | St.James | Completed | Load_249411 | Bogue - 610 | Jul 25, 2026 7:23am | Jul 25, 2026 7:24am | Jul 25, 2026 11:50am | Jul 25, 2026 11:53am | Jul 25, 2026 12:16pm | Jul 25, 2026 12:31pm | Jul 25, 2026 12:32pm | Jul 25, 2026 12:32pm |  |  | Fair | No | Checked and found ok
Non-Outage | J.E.26.07.22282 | C001864909 | Derrick Dawkins | St.James | Completed | Load_267492 | Bogue - 610 | Jul 25, 2026 7:23am | Jul 25, 2026 7:24am | Jul 25, 2026 10:23am | Jul 25, 2026 10:23am | Jul 25, 2026 10:41am | Jul 25, 2026 11:43am | Jul 25, 2026 11:43am | Jul 25, 2026 11:43am |  |  | Fair | No | Customer is getting low voltage because of the distance of the transformer and also multiple illegal connections. Voltage reading 112v/95v=206v tap changer is at position 3Tap changer moved to tap position 5 and the voltage reading at the Xfmr drop lead is 120v/120v/240v and the voltage reading at the end of the line is now at 113v/100v/213v
Non-Outage | J.E.26.07.25182 | C001864907 | Derrick Dawkins | St.James | Completed | Load_240027 | Bogue - 610 | Jul 25, 2026 7:23am | Jul 25, 2026 7:24am | Jul 25, 2026 8:10am | Jul 25, 2026 8:10am | Jul 25, 2026 10:21am | Jul 25, 2026 10:22am | Jul 25, 2026 10:22am | Jul 25, 2026 10:22am |  |  | Fair | No | Premises ok
Non-Outage | J.E.26.07.30158 | C001864908 | Derrick Dawkins | St.James | Completed | Load_241316 | Bogue - 610 | Jul 25, 2026 7:23am | Jul 25, 2026 7:24am | Jul 25, 2026 12:32pm | Jul 25, 2026 12:32pm | Jul 25, 2026 12:51pm | Jul 25, 2026 12:55pm | Jul 25, 2026 12:55pm | Jul 25, 2026 12:55pm |  |  | Fair | No | Premises not found calls to customer went unanswered
Non-Outage | J.E.26.07.17383 | C001864906 | Richard Samuda | Manchester | Completed | Load_303108 | Kendal - 210 | Jul 25, 2026 7:22am | Jul 25, 2026 7:22am | Jul 25, 2026 9:56am | Jul 25, 2026 9:56am | Jul 25, 2026 11:04am | Jul 25, 2026 11:06am | Jul 25, 2026 11:05am | Jul 25, 2026 11:05am |  |  | Fair | Yes | Found ok
Non-Outage | J.E.26.07.25096 | C001864904 | Richard Samuda | Manchester | Completed | Load_261299 | Kendal - 210 | Jul 25, 2026 7:22am | Jul 25, 2026 7:22am | Jul 25, 2026 7:46am | Jul 25, 2026 7:46am | Jul 25, 2026 8:24am | Jul 25, 2026 9:39am | Jul 25, 2026 9:42am | Jul 25, 2026 9:42am |  |  | Fair | No | Remake neutral jumper that was corroded causing customer to experience low voltage using two one bolt clamps and 5 ft of #2 aluminum wire voltage 111 /113/224
Non-Outage | J.E.26.07.26111 | C001864905 | Richard Samuda | Manchester | Completed | Load_261299 | Kendal - 210 | Jul 25, 2026 7:22am | Jul 25, 2026 7:22am | Jul 25, 2026 9:47am | Jul 25, 2026 9:48am | Jul 25, 2026 9:48am | Jul 25, 2026 9:49am | Jul 25, 2026 9:49am | Jul 25, 2026 9:49am |  |  | EarthMovement | No | Customer back to normal
Non-Outage | J.E.26.07.30318 | C001864903 | Richard Samuda | Manchester | Completed | Load_254593 | Kendal - 210 | Jul 25, 2026 7:22am | Jul 25, 2026 7:22am | Jul 25, 2026 11:51am | Jul 25, 2026 12:37pm | Jul 25, 2026 12:37pm | Jul 25, 2026 12:38pm | Jul 25, 2026 12:39pm | Jul 25, 2026 12:39pm |  |  | Fair | No | This call is for st Thomas
Non-Outage | J.E.26.07.30485 | C001864902 | Richard Samuda | Manchester | Completed | Load_238024 | Kendal - 210 | Jul 25, 2026 7:22am | Jul 25, 2026 7:22am | Jul 25, 2026 11:38am | Jul 25, 2026 11:38am | Jul 25, 2026 11:40am | Jul 25, 2026 11:50am | Jul 25, 2026 11:50am | Jul 25, 2026 11:50am |  |  | Fair | No | Over sea phone number no answer
Outage | J.E.26.07.25358 | C001864899 | Barnett Brown | Manchester | Completed | Load_252759 | Spur Tree - 310 | Jul 25, 2026 7:19am | Jul 25, 2026 7:20am | Jul 25, 2026 11:10am | Jul 25, 2026 11:10am | Jul 25, 2026 12:40pm | Jul 25, 2026 1:16pm | Jul 25, 2026 1:18pm | Jul 25, 2026 1:18pm |  |  | Fair | No | Remade service joints at secondary line, voltage 116 115 231
Outage | J.E.26.07.30743 | C001864900 | Barnett Brown | Manchester | Completed | Load_237916 | Spur Tree - 310 | Jul 25, 2026 7:19am | Jul 25, 2026 7:20am | Jul 25, 2026 1:24pm | Jul 25, 2026 1:24pm | Jul 25, 2026 4:21pm | Jul 25, 2026 5:13pm | Jul 25, 2026 5:16pm | Jul 25, 2026 5:16pm |  |  | Fair | No | Customer has internal fault, voltage 118 120 238
Outage | J.E.26.07.30958 | C001864897 | Barnett Brown | Manchester | Completed | Load_251145 | Spur Tree - 310 | Jul 25, 2026 7:19am | Jul 25, 2026 7:20am | Jul 25, 2026 8:47am | Jul 25, 2026 8:47am | Jul 25, 2026 9:18am | Jul 25, 2026 11:02am | Jul 25, 2026 11:06am | Jul 25, 2026 11:06am |  |  | Fair | No | Patrol line, clear primary jumper with switch stick, replace blown 15 amp junction fuse, pole number 041582
Outage | J.E.26.07.31009 | C001864898 | Barnett Brown | Manchester | Completed | Load_269851 | Spur Tree - 310 | Jul 25, 2026 7:19am | Jul 25, 2026 7:20am | Jul 25, 2026 11:06am | Jul 25, 2026 11:06am | Jul 25, 2026 11:06am | Jul 25, 2026 11:07am | Jul 25, 2026 11:08am | Jul 25, 2026 11:08am |  |  | Fair | No | Related to previous call where 15 amp fuse was replaced
Non-Outage | J.E.26.01.32574 | C001864896 | Romeo Brissett | St.James | Completed | Load_244365 | Bogue - 310 | Jul 25, 2026 7:16am | Jul 25, 2026 7:16am | Jul 25, 2026 10:45am | Jul 25, 2026 10:45am | Jul 25, 2026 10:45am | Jul 25, 2026 10:45pm | Jul 25, 2026 10:47am | Jul 25, 2026 10:47am |  |  | Fair | No | Customer returned call and stated power.
Non-Outage | J.E.26.01.34166 | C001864894 | Romeo Brissett | St.James | Completed | Load_1001893 | Bogue - 310 | Jul 25, 2026 7:16am | Jul 25, 2026 7:16am | Jul 25, 2026 12:48pm | Jul 25, 2026 12:48pm | Jul 25, 2026 1:07pm | Jul 25, 2026 1:04pm | Jul 25, 2026 1:09pm | Jul 25, 2026 1:09pm |  |  | Fair | No | Customer returned call and stated power restored
Non-Outage | J.E.26.01.35973 | C001864893 | Romeo Brissett | St.James | Completed | Load_261423 | Bogue - 310 | Jul 25, 2026 7:16am | Jul 25, 2026 7:16am | Jul 25, 2026 11:38am | Jul 25, 2026 11:38am | Jul 25, 2026 12:44pm | Jul 25, 2026 12:40pm | Jul 25, 2026 12:47pm | Jul 25, 2026 12:47pm |  |  | Fair | No | Spliced and retention customer service wire, used 10ft of #6. V/R 113-113-227
Non-Outage | J.E.26.01.36049 | C001864895 | Romeo Brissett | St.James | Completed | Load_244150 | Bogue - 310 | Jul 25, 2026 7:16am | Jul 25, 2026 7:16am | Jul 25, 2026 10:48am | Jul 25, 2026 10:48am | Jul 25, 2026 11:10am | Jul 25, 2026 11:33am | Jul 25, 2026 11:37am | Jul 25, 2026 11:37am |  |  | Fair | No | Used 2 clamps on pole V/R 113-113-200-226-228-230
Non-Outage | J.E.26.01.36804 | C001864892 | Romeo Brissett | St.James | Completed | Load_556938 | Bogue - 310 | Jul 25, 2026 7:15am | Jul 25, 2026 7:16am | Jul 25, 2026 1:09pm | Jul 25, 2026 1:09pm | Jul 25, 2026 1:09pm | Jul 25, 2026 1:10pm | Jul 25, 2026 1:10pm | Jul 25, 2026 1:10pm |  |  | Fair | No | Customer stated it’s an old report
Non-Outage | J.E.26.01.37552 | C001864891 | Romeo Brissett | St.James | Completed | Load_301730l | Bogue - 310 | Jul 25, 2026 7:15am | Jul 25, 2026 7:16am | Jul 25, 2026 1:10pm | Jul 25, 2026 1:10pm | Jul 25, 2026 1:10pm | Jul 25, 2026 1:11pm | Jul 25, 2026 1:11pm | Jul 25, 2026 1:11pm |  |  | Fair | No | Customer stated it’s an old report
Non-Outage | J.E.26.01.39562 | C001864889 | Romeo Brissett | St.James | Completed | Load_254292 | Bogue - 310 | Jul 25, 2026 7:15am | Jul 25, 2026 7:16am | Jul 25, 2026 10:42am | Jul 25, 2026 10:42am | Jul 25, 2026 10:42am | Jul 25, 2026 10:40am | Jul 25, 2026 10:44am | Jul 25, 2026 10:44am |  |  | Fair | No | Premises was checked and Mr you stated issue was resolved from last week
Non-Outage | J.E.26.01.39608 | C001864890 | Romeo Brissett | St.James | Completed | Load_238775 | Bogue - 310 | Jul 25, 2026 7:15am | Jul 25, 2026 7:16am | Jul 25, 2026 9:34am | Jul 25, 2026 9:34am | Jul 25, 2026 9:43am | Jul 25, 2026 10:25am | Jul 25, 2026 10:42am | Jul 25, 2026 10:42am |  |  | Fair | No | Meter was checked and found power V/R 114-114-229
Outage | J.E.26.07.30988 | C001864888 | Romeo Brissett | St.James | Completed | Load_556788 | Bogue - 310 | Jul 25, 2026 7:15am | Jul 25, 2026 7:16am | Jul 25, 2026 7:25am | Jul 25, 2026 7:25am | Jul 25, 2026 8:44am | Jul 25, 2026 8:30am | Jul 25, 2026 9:02am | Jul 25, 2026 9:02am |  |  | Fair | No | Line patrolled and found power in the area, Unable to locate customer.
Outage | J.E.26.07.30941 | C001864854 | Tyrese Williams | St.Ann | Completed | Load_239328 | Cardiff Hall - 210 | Jul 25, 2026 3:00am | Jul 25, 2026 7:30am | Jul 25, 2026 8:17am | Jul 25, 2026 9:43am | Jul 25, 2026 10:18am | Jul 25, 2026 10:24am | Jul 25, 2026 10:24am | Jul 25, 2026 10:24am |  |  | Fair | No | Premises found ok customer said the light came back
Outage | J.E.26.07.30837 | C001864853 | Swon Miller | St.James | Completed | Load_251817 | Queens Drive - 710 | Jul 25, 2026 2:59am | Jul 25, 2026 7:17am | Jul 25, 2026 7:27am | Jul 25, 2026 7:28am | Jul 25, 2026 7:59am | Jul 28, 2026 8:16am | Jul 25, 2026 8:17am | Jul 25, 2026 8:17am |  |  | Fair | No | Found 1,25 kva transformer fuse blown cause by contamination replace 3 amp in 25 kva transformer voltage found 0.000 voltage 115/114/229
Outage | J.E.26.07.30954 | C001864852 | Edward Royal | KSAN | Completed | Load_575405 | Washington Blvd - 710 | Jul 25, 2026 2:58am | Jul 25, 2026 2:58am | Jul 25, 2026 3:17am | Jul 25, 2026 3:17am | Jul 25, 2026 3:17am | Jul 25, 2026 3:26am | Jul 25, 2026 3:27am | Jul 25, 2026 3:27am |  |  | Fair | No | When contacted customer by phone customer said that they have no power l contacted escalation and they said meter not communicating they checked over meter in box and they are working referred to field service
Outage | J.E.26.07.30947 | C001864851 | Elvis Trowers | KSAN | Completed | Load_247096 | Washington Blvd - 510 | Jul 25, 2026 2:57am | Jul 25, 2026 7:39am | Jul 25, 2026 9:53am | Jul 25, 2026 9:53am | Jul 25, 2026 10:19am | Jul 25, 2026 11:09am | Jul 25, 2026 11:10am | Jul 25, 2026 11:10am |  |  | Fair | Yes | Customer was found without electricity supply when checked and corroded joints was found at pat head and 2 one bolt clamps was used.
Outage | J.E.26.07.30386 | C001864847 | Edward Royal | KSAN | Completed | Load_556768 | Washington Blvd - 610 | Jul 24, 2026 11:49pm | Jul 24, 2026 11:50pm | Jul 25, 2026 3:05am | Jul 25, 2026 3:05am | Jul 25, 2026 3:05am | Jul 25, 2026 3:06am | Jul 25, 2026 3:07am | Jul 25, 2026 3:07am |  |  | Fair | No | Contact customer by phone customer said the power was restored
Outage | J.E.26.07.30497 | C001864846 | Edward Royal | KSAN | Completed | Load_262358 | West Kings House - 410 | Jul 24, 2026 11:49pm | Jul 24, 2026 11:50pm | Jul 25, 2026 3:01am | Jul 25, 2026 3:01am | Jul 25, 2026 3:01am | Jul 25, 2026 3:04am | Jul 25, 2026 3:05am | Jul 25, 2026 3:05am |  |  | Fair | No | Contact customer by phone customer said the power was restored
Outage | J.E.26.07.29776 | C001864845 | Delano Gayle | St.Catherine | Completed | Load_579394 | Twickenham - 410 | Jul 24, 2026 11:00pm | Jul 24, 2026 11:04pm | Jul 25, 2026 3:43am | Jul 25, 2026 3:43am | Jul 25, 2026 3:54am | Jul 25, 2026 4:10am | Jul 25, 2026 4:10am | Jul 25, 2026 4:10am |  |  | Fair | No | Premises not found no answer from customer phone, patrolled scheme and found okay
Outage | J.E.26.07.29820 | C001864843 | Delano Gayle | St.Catherine | Completed | Load_258756 | Tredegar - 510 | Jul 24, 2026 11:00pm | Jul 24, 2026 11:04pm | Jul 24, 2026 11:10pm | Jul 24, 2026 11:10pm | Jul 25, 2026 3:03am | Jul 25, 2026 3:09am | Jul 25, 2026 3:09am | Jul 25, 2026 3:09am |  |  | Fair | No | Premises not found, area found okay
Outage | J.E.26.07.30330 | C001864844 | Delano Gayle | St.Catherine | Completed | Load_244050 | Tredegar - 410 | Jul 24, 2026 11:00pm | Jul 24, 2026 11:04pm | Jul 25, 2026 3:09am | Jul 25, 2026 3:09am | Jul 25, 2026 3:42am | Jul 25, 2026 3:43am | Jul 25, 2026 3:43am | Jul 25, 2026 3:43am |  |  | Fair | No | Premises found okay power was restored to area
Non-Outage | J.E.26.07.30818 | C001864833 | Milton Charlton | null | Completed | null | null | Jul 24, 2026 9:06pm | Jul 24, 2026 9:07pm | Jul 25, 2026 5:37pm | Jul 25, 2026 5:37pm | Jul 25, 2026 5:40pm | Jul 25, 2026 5:40pm | Jul 25, 2026 5:41pm | Jul 25, 2026 5:41pm | BrokenPole |  | Fair | No | Found okay upon arrival. Matter was resolved.
Non-Outage | J.E.26.07.30797 | C001864830 | Edward Royal | KSAS | Completed | Load_250673 | Rockfort - 410 | Jul 24, 2026 8:46pm | Jul 25, 2026 9:37am | Jul 25, 2026 10:36am | Jul 25, 2026 10:36am | Jul 25, 2026 10:36am | Jul 25, 2026 10:37am | Jul 25, 2026 10:37am | Jul 25, 2026 10:37am | Fire |  | Fair | No | Incorrect procedure advice customer to visit ruthven road
Outage | J.E.26.07.30795 | C001864831 | Edward Royal | KSAS | Completed | Load_248244 | Cane River - 310 | Jul 24, 2026 8:46pm | Jul 25, 2026 9:38am | Jul 25, 2026 10:37am | Jul 25, 2026 10:37am | Jul 25, 2026 10:51am | Jul 25, 2026 10:56am | Jul 25, 2026 10:56am | Jul 25, 2026 10:56am |  |  | Fair | No | Meter need to be check reffered to field service meter only give out single phase box #HEX01763 pole #018880
Outage | J.E.26.07.30630 | C001864827 | Andre Williams | Trelawny | Completed | Load_295089 | Duncans - 110 | Jul 24, 2026 8:45pm | Jul 24, 2026 8:46pm | Jul 24, 2026 8:58pm | Jul 24, 2026 8:58pm | Jul 24, 2026 9:11pm | Jul 24, 2026 9:12pm | Jul 24, 2026 9:12pm | Jul 24, 2026 9:12pm |  |  | Fair | No | Premises found with supply call related to earlier outage during day
Outage | J.E.26.07.30631 | C001864829 | Andre Williams | Trelawny | Completed | Load_295092 | Duncans - 110 | Jul 24, 2026 8:45pm | Jul 24, 2026 8:46pm | Jul 24, 2026 8:52pm | Jul 24, 2026 9:13pm | Jul 24, 2026 9:13pm | Jul 24, 2026 9:14pm | Jul 24, 2026 9:14pm | Jul 24, 2026 9:14pm |  |  | Fair | No | Area found with supply upon drive through
Outage | J.E.26.07.30632 | C001864828 | Andre Williams | Trelawny | Completed | Load_1001480 | Duncans - 110 | Jul 24, 2026 8:45pm | Jul 24, 2026 8:46pm | Jul 24, 2026 9:16pm | Jul 24, 2026 9:16pm | Jul 24, 2026 9:19pm | Jul 24, 2026 9:21pm | Jul 24, 2026 9:21pm | Jul 24, 2026 9:21pm |  |  | Fair | No | Premises found with supply upon drive through
Outage | J.E.26.07.30683 | C001864826 | Andrew Powell | St.Elizabeth | Completed | Load_262806 | Maggotty - 210 | Jul 24, 2026 8:39pm | Jul 24, 2026 8:39pm | Jul 24, 2026 8:52pm | Jul 24, 2026 8:52pm | Jul 24, 2026 9:45pm | Jul 24, 2026 10:38pm | Jul 24, 2026 10:41pm | Jul 24, 2026 10:41pm |  |  | Fair | No | Isolate and close 10 amp trip saver by pole number 034771 to repair burnt off primary drop lead at switch head using one clamp, restore supply okay.
Outage | J.E.26.07.30638 | C001864817 | Richman Whyte | Westmoreland | Completed | Load_292514 | Paradise - 110 | Jul 24, 2026 7:59pm | Jul 24, 2026 8:00pm | Jul 24, 2026 9:16pm | Jul 24, 2026 9:16pm | Jul 24, 2026 10:23pm | Jul 24, 2026 10:23pm | Jul 24, 2026 10:25pm | Jul 24, 2026 10:25pm |  |  | Fair | No | Reset twenty five kva transformer
Non-Outage | J.E.26.07.30515 | C001864816 | Elvis Trowers | KSAN | Completed | Load_257446 | Constant Spring - 210 | Jul 24, 2026 7:58pm | Jul 24, 2026 7:58pm | Jul 24, 2026 8:51pm | Jul 24, 2026 8:51pm | Jul 24, 2026 8:54pm | Jul 24, 2026 8:55pm | Jul 24, 2026 8:55pm | Jul 24, 2026 8:55pm |  |  | Fair | Yes | Premises checked and found okay customer was also spoken with.
Non-Outage | J.E.26.07.30655 | C001864815 | Elvis Trowers | KSAN | Completed | Load_257446 | Constant Spring - 210 | Jul 24, 2026 7:58pm | Jul 24, 2026 7:58pm | Jul 24, 2026 8:56pm | Jul 24, 2026 8:57pm | Jul 24, 2026 8:57pm | Jul 24, 2026 8:58pm | Jul 24, 2026 8:58pm | Jul 24, 2026 8:58pm |  |  | Fair | Yes | Call related, premises checked and found okay.
Outage | J.E.26.07.30757 | C001864813 | Roxroy Needham | St.Ann | Completed | Load_255932 | Cardiff Hall - 310 | Jul 24, 2026 7:54pm | Jul 24, 2026 7:54pm | Jul 24, 2026 8:07pm | Jul 24, 2026 8:08pm | Jul 24, 2026 9:25pm | Jul 24, 2026 9:26pm | Jul 24, 2026 9:26pm | Jul 24, 2026 9:26pm |  |  | Fair | No | Customer has internal issues and was advised to get an electrician
Outage | J.E.26.07.30386 | C001864808 | Milton Charlton | KSAN | Completed | Load_556768 | Washington Blvd - 610 | Jul 24, 2026 7:42pm | Jul 24, 2026 7:42pm | Jul 25, 2026 10:30am | Jul 25, 2026 10:30am | Jul 25, 2026 4:00pm | Jul 25, 2026 10:30am | Jul 25, 2026 4:03pm | Jul 25, 2026 4:03pm |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Non-Outage | J.E.26.07.30725 | C001864798 | Cliton Henry | St.Mary | Completed | Load_237637 | Blackstonedge - 110 | Jul 24, 2026 7:24pm | Jul 24, 2026 7:25pm | Jul 24, 2026 7:30pm | Jul 24, 2026 7:30pm | Jul 24, 2026 7:30pm | Jul 24, 2026 7:35pm | Jul 24, 2026 7:35pm | Jul 24, 2026 7:35pm |  |  | Fair | No | The customer service wire was disconnected due a defective meter socket and a burnt meter. The customer was advised to get a licensed electrician to carryout repairs. Kindly refer to Field Service Department for a meter replacement .
Outage | J.E.26.07.30719 | C001864797 | Ricky Hall | St.Catherine | Completed | Load_237949 | New Michelton - 410 | Jul 24, 2026 7:22pm | Jul 24, 2026 7:26pm | Jul 24, 2026 7:59pm | Jul 24, 2026 7:59pm | Jul 24, 2026 8:15pm | Jul 24, 2026 8:23pm | Jul 24, 2026 8:23pm | Jul 24, 2026 8:23pm |  |  | Fair | No | Call associated with outage #29772
Outage | J.E.26.07.27916 | C001864795 | Romaine Roberts | Portmore | Completed | Load_262775 | Naggo Head - 510 | Jul 24, 2026 7:20pm | Jul 24, 2026 7:22pm | Jul 24, 2026 8:50pm | Jul 24, 2026 8:50pm | Jul 24, 2026 8:50pm | Jul 24, 2026 9:28pm | Jul 24, 2026 9:28pm | Jul 24, 2026 9:28pm | BrokenWire |  | Fair | No | Found ok call was mad to customer who said they have supply
Non-Outage | J.E.26.07.30706 | C001864792 | Daniel Francis | null | Completed | null | null | Jul 24, 2026 7:10pm | Jul 24, 2026 7:10pm | Jul 24, 2026 8:48pm | Jul 24, 2026 8:48pm | Jul 24, 2026 9:05pm | Jul 24, 2026 9:05pm | Jul 24, 2026 9:06pm | Jul 24, 2026 9:06pm |  |  | Fair | No | Found okay
Outage | J.E.26.07.30675 | C001864790 | Cliton Henry | St.Mary | Completed | Load_245290 | Blackstonedge - 110 | Jul 24, 2026 7:08pm | Jul 24, 2026 7:09pm | Jul 24, 2026 8:56pm | Jul 24, 2026 8:56pm | Jul 24, 2026 8:56pm | Jul 24, 2026 9:10pm | Jul 24, 2026 9:08pm | Jul 24, 2026 9:08pm |  |  | Fair | No | The customer meter was reconnected with the assistance from escalation team.
Outage | J.E.26.07.30681 | C001864791 | Cliton Henry | St.Mary | Completed | Load_260951 | Oracabessa - 210 | Jul 24, 2026 7:08pm | Jul 24, 2026 7:09pm | Jul 24, 2026 9:09pm | Jul 24, 2026 9:09pm | Jul 24, 2026 10:34pm | Jul 24, 2026 10:44pm | Jul 24, 2026 10:59pm | Jul 24, 2026 10:59pm |  |  | Fair | No | A blown 2 amp fuse found for a 25 kva transformer at pole # 0055194 due to broken 30-c6 secondary dead pole.The broken pole was isolated at a secondary dead pole and supply restored using 1-3 amp fuse. Approximately 5 customers left without electricity supply. Kindly refer to St.Mary Operations for for a replacement.
Outage | J.E.26.07.30295 | C001864787 | Cliton Henry | St.Mary | Completed | Load_237637 | Blackstonedge - 110 | Jul 24, 2026 7:04pm | Jul 24, 2026 7:07pm | Jul 24, 2026 7:11pm | Jul 24, 2026 7:11pm | Jul 24, 2026 7:12pm | Jul 24, 2026 7:13pm | Jul 24, 2026 7:17pm | Jul 24, 2026 7:17pm | BrokenWire |  | Fair | No | A blown 20 amp junction fuse found at Woodside community center. Supply restored using 1-25 amp fuse.
Outage | J.E.26.07.29739 | C001864784 | Barnett Brown | Manchester | Completed | Load_270122 | Kendal - 210 | Jul 24, 2026 6:48pm | Jul 24, 2026 6:48pm | Jul 24, 2026 7:06pm | Jul 24, 2026 7:06pm | Jul 24, 2026 9:09pm | Jul 24, 2026 9:27pm | Jul 24, 2026 9:28pm | Jul 24, 2026 9:28pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.30672 | C001864779 | Daniel Francis | St.Ann | Completed | Load_246908 | Ocho Rios - 510 | Jul 24, 2026 6:39pm | Jul 24, 2026 6:39pm | Jul 24, 2026 7:43pm | Jul 24, 2026 7:43pm | Jul 24, 2026 7:46pm | Jul 24, 2026 8:00pm | Jul 24, 2026 8:00pm | Jul 24, 2026 8:00pm |  |  | Fair | No | Pole # 464666 change one 8amp fuse
Non-Outage | J.E.26.07.29713 | C001864777 | Rusean Allen | KSAS | Completed | Load_254508 | Hunts Bay - 310 | Jul 24, 2026 6:32pm | Jul 24, 2026 6:33pm | Jul 24, 2026 7:48pm | Jul 24, 2026 7:48pm | Jul 24, 2026 10:12pm | Jul 24, 2026 10:15pm | Jul 24, 2026 10:15pm | Jul 24, 2026 10:15pm |  |  | Fair | No | Defective 100KVA transformer needs to changed, refer to maintenance department.
Outage | J.E.26.07.30662 | C001864776 | Elvis Trowers | KSAN | Completed | Load_257446 | Constant Spring - 210 | Jul 24, 2026 6:30pm | Jul 24, 2026 6:42pm | Jul 24, 2026 7:42pm | Jul 24, 2026 7:42pm | Jul 24, 2026 8:19pm | Jul 24, 2026 8:50pm | Jul 24, 2026 8:50pm | Jul 24, 2026 8:50pm |  |  | Fair | Yes | Premises checked and found ok upon arrival customer was also spoken with, however they wanted to know why they were having the fluctuating issues, and since the power came back it’s normal.
Outage | J.E.26.07.30659 | C001864775 | Hartley Chin | St.Catherine | Completed | Load_568118 | Rhodens Pen - 210 | Jul 24, 2026 6:29pm | Jul 25, 2026 8:48am | Jul 25, 2026 9:54am | Jul 25, 2026 9:54am | Jul 25, 2026 11:19am | Jul 25, 2026 11:44am | Jul 25, 2026 11:47am | Jul 25, 2026 11:47am |  |  | Fair | No | Ref to field service !!! Customer is not receiving any supply … contacted escalation.. was told that they were unable to communicate with customer meter .. Note : area is hexing ..
Outage | J.E.26.07.30657 | C001864773 | Daniel Francis | St.Ann | Completed | Load_255837 | Roaring River - 210 | Jul 24, 2026 6:25pm | Jul 24, 2026 6:25pm | Jul 24, 2026 10:14pm | Jul 24, 2026 10:14pm | Jul 24, 2026 10:46pm | Jul 24, 2026 11:15pm | Jul 24, 2026 11:16pm | Jul 24, 2026 11:16pm |  |  | Fair | No | Change one 8amp fuse no pole #
Outage | J.E.26.07.30604 | C001864768 | Daniel Francis | St.Ann | Completed | Load_239077 | Ocho Rios - 310 | Jul 24, 2026 6:07pm | Jul 24, 2026 6:07pm | Jul 24, 2026 8:01pm | Jul 24, 2026 8:01pm | Jul 24, 2026 8:15pm | Jul 24, 2026 8:47pm | Jul 24, 2026 8:48pm | Jul 24, 2026 8:48pm |  |  | Fair | No | Change one 50 amp fuse pole # 0195537
Outage | J.E.26.07.30581 | C001864765 | Jermaine Williams | Clarendon | Completed | Load_247306 | Monymusk - 410 | Jul 24, 2026 5:47pm | Jul 24, 2026 5:48pm | Jul 24, 2026 6:02pm | Jul 24, 2026 6:02pm | Jul 24, 2026 6:21pm | Jul 24, 2026 7:24pm | Jul 24, 2026 7:06pm | Jul 24, 2026 7:06pm |  |  | Fair | No | Defective 10kva xfmr. Approximately 15 customers affected.
Outage | J.E.26.07.27837 | C001864764 | Nickolas Rodriques | Portmore | Completed | Load_256681 | Naggo Head - 510 | Jul 24, 2026 5:43pm | Jul 24, 2026 5:47pm | Jul 24, 2026 6:28pm | Jul 24, 2026 6:35pm | Jul 24, 2026 7:00pm | Jul 24, 2026 7:12pm | Jul 24, 2026 7:14pm | Jul 24, 2026 7:14pm |  |  | Fair | No | Customer is reporting a defective streetlight. Refer to streetlight department.
Outage | J.E.26.07.30296 | C001864760 | Nickolas Rodriques | Portmore | Completed | Load_240118 | Naggo Head - 610 | Jul 24, 2026 5:42pm | Jul 24, 2026 5:47pm | Jul 24, 2026 7:18pm | Jul 24, 2026 7:18pm | Jul 24, 2026 7:41pm | Jul 24, 2026 7:53pm | Jul 24, 2026 7:55pm | Jul 24, 2026 7:55pm |  |  | Fair | No | Found area with electricity. Customer confirmed that the area outage was restored.
Outage | J.E.26.07.29361 | C001864733 | Neville Spencer | Clarendon | Completed | Load_243507 | May Pen - 210 | Jul 24, 2026 5:17pm | Jul 24, 2026 5:18pm | Jul 24, 2026 6:46pm | Jul 24, 2026 6:46pm | Jul 24, 2026 6:46pm | Jul 24, 2026 6:46pm | Jul 24, 2026 6:48pm | Jul 24, 2026 6:48pm |  |  | Fair | No | Open 25 kva xmfr repair burnt out clamp on netural drop lead used 3, clamps voltage reading 126 118 235 .
Outage | J.E.26.07.30533 | C001864732 | Neville Spencer | Clarendon | Completed | Load_243507 | May Pen - 210 | Jul 24, 2026 5:17pm | Jul 24, 2026 5:18pm | Jul 24, 2026 5:23pm | Jul 24, 2026 5:23pm | Jul 24, 2026 6:01pm | Jul 24, 2026 6:40pm | Jul 24, 2026 6:46pm | Jul 24, 2026 6:46pm |  |  | Fair | No | Open 25 kva xmfr repair burnt out clamp on netural drop lead used 3, clamps voltage reading 116 118 235 .
Non-Outage | J.E.26.05.32041 | C001864731 | Richard Samuda | Manchester | Completed | Load_247867 | Spur Tree - 210 | Jul 24, 2026 5:12pm | Jul 24, 2026 5:13pm | Jul 24, 2026 7:50pm | Jul 24, 2026 7:50pm | Jul 24, 2026 7:58pm | Jul 24, 2026 7:58pm | Jul 24, 2026 7:58pm | Jul 24, 2026 7:58pm | BrokenWire |  | Fair | No | Found ok
Non-Outage | J.E.26.01.03462 | C001864728 | Richard Samuda | Manchester | Completed | Load_256206 | Spur Tree - 210 | Jul 24, 2026 5:09pm | Jul 24, 2026 5:10pm | Jul 24, 2026 9:18pm | Jul 24, 2026 9:18pm | Jul 24, 2026 9:48pm | Jul 24, 2026 10:26pm | Jul 24, 2026 10:26pm | Jul 24, 2026 10:26pm | BrokenWire |  | Fair | No | Found ok
Non-Outage | J.E.26.01.07480 | C001864727 | Richard Samuda | Manchester | Completed | Load_257074 | Spur Tree - 210 | Jul 24, 2026 5:09pm | Jul 24, 2026 5:10pm | Jul 24, 2026 7:13pm | Jul 24, 2026 7:13pm | Jul 24, 2026 7:47pm | Jul 24, 2026 7:49pm | Jul 24, 2026 7:49pm | Jul 24, 2026 7:49pm | BrokenWire |  | Fair | No | Customer say situation was resolved
Non-Outage | J.E.26.01.28859 | C001864729 | Richard Samuda | Manchester | Completed | Load_265815 | Spur Tree - 210 | Jul 24, 2026 5:09pm | Jul 24, 2026 5:10pm | Jul 24, 2026 9:03pm | Jul 24, 2026 9:03pm | Jul 24, 2026 9:04pm | Jul 24, 2026 9:18pm | Jul 24, 2026 9:18pm | Jul 24, 2026 9:18pm | BrokenWire |  | Fair | No | Found ok
Non-Outage | J.E.26.07.29700 | C001864726 | Shamour Haughton | St.James | Completed | Load_1001216 | Bogue - 510 | Jul 24, 2026 5:02pm | Jul 24, 2026 5:02pm | Jul 24, 2026 5:06pm | Jul 24, 2026 5:06pm | Jul 24, 2026 6:10pm | Jul 24, 2026 6:15pm | Jul 24, 2026 6:21pm | Jul 24, 2026 6:21pm |  |  | Fair | No | Found customer experiencing single phasing, clean corrosion at pothead using 3 clamps, voltage left 115,116,231
Outage | J.E.26.07.30554 | C001864725 | Richman Whyte | Westmoreland | Completed | Load_246813 | Paradise - 110 | Jul 24, 2026 4:57pm | Jul 24, 2026 4:58pm | Jul 24, 2026 5:52pm | Jul 24, 2026 5:52pm | Jul 24, 2026 6:02pm | Jul 24, 2026 6:02pm | Jul 24, 2026 6:03pm | Jul 24, 2026 6:03pm | Fire |  | Fair | No | Meter feeding customer burnt up disconnect for repair
Outage | J.E.26.07.30475 | C001864724 | Stephen Taylor | St.Thomas | Completed | Load_247145 | Good Year - 110 | Jul 24, 2026 4:52pm | Jul 24, 2026 4:53pm | Jul 24, 2026 6:04pm | Jul 24, 2026 6:04pm | Jul 24, 2026 7:35pm | Jul 24, 2026 7:35pm | Jul 24, 2026 8:19pm | Jul 24, 2026 8:19pm | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Splice and retention 2 span of secondary wire use 3 clamps and 60 foot of aluminum wire and close up back 25 kva transformer all customer is now okay
Non-Outage | J.E.26.07.26609 | C001864723 | Daniel Francis | St.Ann | Completed | Load_248392 | Roaring River - 210 | Jul 24, 2026 4:49pm | Jul 24, 2026 4:49pm | Jul 25, 2026 4:16pm | Jul 25, 2026 4:17pm | Jul 25, 2026 4:24pm | Jul 25, 2026 4:29pm | Jul 25, 2026 4:30pm | Jul 25, 2026 4:30pm |  |  | Fair | No | Customer did not make report
Non-Outage | J.E.26.07.29644 | C001864722 | Daniel Francis | St.Ann | Completed | Load_269031 | Ocho Rios - 510 | Jul 24, 2026 4:49pm | Jul 24, 2026 4:49pm | Jul 24, 2026 5:06pm | Jul 24, 2026 5:07pm | Jul 24, 2026 6:56pm | Jul 24, 2026 7:36pm | Jul 24, 2026 7:43pm | Jul 24, 2026 7:43pm |  |  | Fair | No | Use 3 one bolt clamp at pole 117 117 234 in all
Non-Outage | J.E.26.07.30170 | C001864721 | Roxroy Needham | St.Ann | Completed | Load_253323 | Cardiff Hall - 310 | Jul 24, 2026 4:49pm | Jul 24, 2026 4:49pm | Jul 24, 2026 6:23pm | Jul 24, 2026 6:23pm | Jul 24, 2026 6:24pm | Jul 24, 2026 6:26pm | Jul 24, 2026 6:26pm | Jul 24, 2026 6:26pm |  |  | Fair | No | Didn’t get customer on phone
Outage | J.E.26.07.30502 | C001864720 | Milton Charlton | KSAN | Completed | Load_265727 | Hope - 510 | Jul 24, 2026 4:25pm | Jul 24, 2026 4:47pm | Jul 24, 2026 7:53pm | Jul 24, 2026 7:54pm | Jul 24, 2026 9:44pm | Jul 24, 2026 9:40pm | Jul 24, 2026 9:48pm | Jul 24, 2026 9:48pm |  |  | Fair | No | Remove wisp and vines from the top of 25 kva transformer. Refused and reclosed transformer switch at pole #0110209 using one 3amps fuse.
Non-Outage | J.E.26.01.26815 | C001864719 | Richman Whyte | Westmoreland | Completed | Load_263345 | Orange Bay - 310 | Jul 24, 2026 4:23pm | Jul 24, 2026 4:23pm | Jul 24, 2026 6:07pm | Jul 24, 2026 6:07pm | Jul 24, 2026 6:08pm | Jul 24, 2026 6:08pm | Jul 24, 2026 6:08pm | Jul 24, 2026 6:08pm |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.01.26859 | C001864718 | Richman Whyte | Westmoreland | Completed | Load_265239 | Paradise - 110 | Jul 24, 2026 4:23pm | Jul 24, 2026 4:23pm | Jul 24, 2026 6:08pm | Jul 24, 2026 6:08pm | Jul 24, 2026 6:08pm | Jul 24, 2026 6:09pm | Jul 24, 2026 6:09pm | Jul 24, 2026 6:09pm |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.01.27032 | C001864717 | Richman Whyte | Westmoreland | Completed | Load_265710 | Orange Bay - 310 | Jul 24, 2026 4:23pm | Jul 24, 2026 4:23pm | Jul 24, 2026 6:10pm | Jul 24, 2026 6:10pm | Jul 24, 2026 6:10pm | Jul 24, 2026 6:10pm | Jul 24, 2026 6:11pm | Jul 24, 2026 6:11pm |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.01.27110 | C001864715 | Richman Whyte | Westmoreland | Completed | Load_250137 | Orange Bay - 310 | Jul 24, 2026 4:23pm | Jul 24, 2026 4:23pm | Jul 24, 2026 6:15pm | Jul 24, 2026 6:15pm | Jul 24, 2026 6:33pm | Jul 24, 2026 6:33pm | Jul 24, 2026 6:33pm | Jul 24, 2026 6:33pm |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.01.27143 | C001864716 | Richman Whyte | Westmoreland | Completed | Load_256009 | Paradise - 110 | Jul 24, 2026 4:23pm | Jul 24, 2026 4:23pm | Jul 24, 2026 6:09pm | Jul 24, 2026 6:09pm | Jul 24, 2026 6:09pm | Jul 24, 2026 6:09pm | Jul 24, 2026 6:10pm | Jul 24, 2026 6:10pm |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.01.31566 | C001864714 | Richman Whyte | Westmoreland | Completed | Load_253063 | Orange Bay - 310 | Jul 24, 2026 4:23pm | Jul 24, 2026 4:23pm | Jul 24, 2026 8:22pm | Jul 24, 2026 8:22pm | Jul 24, 2026 8:22pm | Jul 24, 2026 8:22pm | Jul 24, 2026 8:24pm | Jul 24, 2026 8:24pm |  |  | Fair | No | Open twenty five kva transformer fuse and change defective clamps on transformer drop Leeds use six one bolt clamps voltage 110 109 220
Non-Outage | J.E.26.02.20364 | C001864713 | Richman Whyte | Westmoreland | Completed | Load_250137 | Paradise - 110 | Jul 24, 2026 4:23pm | Jul 24, 2026 4:23pm | Jul 24, 2026 9:15pm | Jul 24, 2026 9:15pm | Jul 24, 2026 9:15pm | Jul 24, 2026 9:15pm | Jul 24, 2026 9:16pm | Jul 24, 2026 9:16pm |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.02.41722 | C001864712 | Richman Whyte | Westmoreland | Completed | Load_249867 | Orange Bay - 310 | Jul 24, 2026 4:23pm | Jul 24, 2026 4:23pm | Jul 24, 2026 8:30pm | Jul 24, 2026 8:30pm | Jul 24, 2026 8:30pm | Jul 24, 2026 8:31pm | Jul 24, 2026 8:31pm | Jul 24, 2026 8:31pm |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.07.30176 | C001864709 | Richman Whyte | Westmoreland | Completed | Load_251528 | Paradise - 110 | Jul 24, 2026 4:23pm | Jul 24, 2026 4:23pm | Jul 24, 2026 9:14pm | Jul 24, 2026 9:14pm | Jul 24, 2026 9:14pm | Jul 24, 2026 9:14pm | Jul 24, 2026 9:15pm | Jul 24, 2026 9:15pm |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.30499 | C001864707 | Eric Williams | KSAS | Completed | Load_254801 | Greenwich - 510 | Jul 24, 2026 4:21pm | Jul 24, 2026 4:23pm | Jul 24, 2026 5:31pm | Jul 24, 2026 6:24pm | Jul 24, 2026 6:34pm | Jul 24, 2026 6:35pm | Jul 24, 2026 6:36pm | Jul 24, 2026 6:36pm |  |  | Fair | No | Premises closed, customer requested a visit monday
Non-Outage | J.E.26.07.30201 | C001864701 | Michael Christian | null | Completed | null | null | Jul 24, 2026 4:19pm | Jul 24, 2026 8:11pm | Jul 24, 2026 9:14pm | Jul 24, 2026 9:14pm | Jul 24, 2026 9:15pm | Jul 24, 2026 9:16pm | Jul 24, 2026 9:16pm | Jul 24, 2026 9:16pm | TreeContact |  | Fair | No
Outage | J.E.26.07.30323 | C001864702 | Michael Christian | St.James | Completed | Load_269145 | Queens Drive - 710 | Jul 24, 2026 4:19pm | Jul 24, 2026 4:45pm | Jul 24, 2026 4:59pm | Jul 24, 2026 4:59pm | Jul 24, 2026 5:37pm | Jul 24, 2026 5:43pm | Jul 24, 2026 5:43pm | Jul 24, 2026 5:43pm |  |  | Fair | No | Voltage 110 112 223 at pothead
Outage | J.E.26.07.30427 | C001864704 | Michael Christian | St.James | Completed | Load_259581 | Bogue - 310 | Jul 24, 2026 4:19pm | Jul 24, 2026 4:45pm | Jul 24, 2026 4:59pm | Jul 24, 2026 7:11pm | Jul 24, 2026 7:11pm | Jul 24, 2026 7:13pm | Jul 24, 2026 7:14pm | Jul 24, 2026 7:14pm |  |  | Fair | No | Replace 1 30 amp junction no pole #
Outage | J.E.26.07.30471 | C001864703 | Oshane Warren | St.Elizabeth | Completed | Load_292665 | Maggotty - 110 | Jul 24, 2026 4:19pm | Jul 24, 2026 4:20pm | Jul 24, 2026 7:48pm | Jul 24, 2026 8:15pm | Jul 24, 2026 9:35pm | Jul 24, 2026 9:38pm | Jul 24, 2026 9:38pm | Jul 24, 2026 9:38pm |  |  | Fair | No | Customer reports street light not working
Outage | J.E.26.07.30427 | C001864700 | Michael Christian | St.James | Completed | Load_259581 | Bogue - 310 | Jul 24, 2026 4:18pm | Jul 24, 2026 4:19pm | Jul 24, 2026 4:59pm | Jul 24, 2026 5:44pm | Jul 24, 2026 6:53pm | Jul 24, 2026 7:11pm | Jul 24, 2026 7:11pm | Jul 24, 2026 7:11pm |  |  | Fair | No | Found 1 30 amp junction out cause by lightning replace no pole #
Outage | J.E.26.07.30279 | C001864699 | Derrick Dawkins | St.James | Completed | Load_266674 | Bogue - 410 | Jul 24, 2026 4:14pm | Jul 24, 2026 4:16pm | Jul 24, 2026 5:50pm | Jul 24, 2026 5:50pm | Jul 24, 2026 6:39pm | Jul 24, 2026 6:28pm | Jul 24, 2026 8:17pm | Jul 24, 2026 8:17pm |  |  | Fair | No | Found one 167 transformer blown due to contamination replaced 20k fuse no pole number available
Outage | J.E.26.07.30490 | C001864698 | Andrew Powell | St.Elizabeth | Completed | Load_292171 | Maggotty - 210 | Jul 24, 2026 4:14pm | Jul 24, 2026 4:18pm | Jul 24, 2026 5:51pm | Jul 24, 2026 5:51pm | Jul 24, 2026 5:53pm | Jul 24, 2026 5:53pm | Jul 24, 2026 5:54pm | Jul 24, 2026 5:54pm |  |  | Fair | No | Premises found okay customer stated that supply restored.
Outage | J.E.26.07.30497 | C001864697 | Milton Charlton | KSAN | Completed | Load_262358 | West Kings House - 410 | Jul 24, 2026 4:13pm | Jul 24, 2026 4:13pm | Jul 25, 2026 9:04am | Jul 25, 2026 4:03pm | Jul 25, 2026 4:03pm | Jul 25, 2026 1:05pm | Jul 25, 2026 4:04pm | Jul 25, 2026 4:04pm |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Non-Outage | J.E.26.07.29799 | C001864696 | Romaine Roberts | St.Mary | Completed | Load_268770 | Annotto Bay - 210 | Jul 24, 2026 4:04pm | Jul 24, 2026 4:05pm | Jul 24, 2026 4:25pm | Jul 24, 2026 4:25pm | Jul 24, 2026 5:39pm | Jul 24, 2026 5:53pm | Jul 24, 2026 5:54pm | Jul 24, 2026 5:54pm |  |  | Fair | No | Visit to the area was found ok
Outage | J.E.26.07.27270 | C001864695 | Andrew Powell | St.Elizabeth | Completed | Load_292458 | Maggotty - 210 | Jul 24, 2026 4:03pm | Jul 24, 2026 4:03pm | Jul 24, 2026 4:10pm | Jul 24, 2026 4:10pm | Jul 24, 2026 5:20pm | Jul 24, 2026 5:48pm | Jul 24, 2026 5:50pm | Jul 24, 2026 5:50pm |  |  | Fair | No | Patrol and found clear, replace blown 10 amp junction fuse, no pole number by switch location, restore supply okay.
Outage | J.E.26.07.29773 | C001864694 | Wayne Dillion | St.Elizabeth | Completed | Load_255977 | Maggotty - 110 | Jul 24, 2026 4:02pm | Jul 24, 2026 4:03pm | Jul 24, 2026 6:06pm | Jul 24, 2026 6:06pm | Jul 24, 2026 6:06pm | Jul 24, 2026 6:30pm | Jul 24, 2026 6:49pm | Jul 24, 2026 6:49pm | BrokenWire |  | Fair | No | Reconnect customer using 70 feet of number 6 triplex 3 linket 3 one bolt clamp voltage reading 112v 113v 225v supply working ok
Outage | J.E.26.07.30182 | C001864693 | Wayne Dillion | St.Elizabeth | Completed | Load_569186 | Maggotty - 110 | Jul 24, 2026 4:02pm | Jul 24, 2026 4:03pm | Jul 24, 2026 6:52pm | Jul 24, 2026 6:52pm | Jul 24, 2026 7:17pm | Jul 24, 2026 9:16pm | Jul 24, 2026 9:26pm | Jul 24, 2026 9:26pm |  |  | Fair | No | Patrol and found 2 open 2 amp fuse open close the same one blown other check found one defective 25 KVA transformer please refer to maintenance to have the transformer replaced
Outage | J.E.26.07.30476 | C001864691 | Elvis Trowers | KSAN | Completed | Load_257676 | Constant Spring - 210 | Jul 24, 2026 3:58pm | Jul 24, 2026 3:59pm | Jul 24, 2026 4:45pm | Jul 24, 2026 4:45pm | Jul 24, 2026 4:45pm | Jul 24, 2026 4:58pm | Jul 24, 2026 4:58pm | Jul 24, 2026 4:58pm |  |  | Fair | Yes | Premises not located and customer could not be contacted by telephone either after several calls, and was unable to leave a message, area was checked and found with regular electricity supply.
Outage | J.E.26.07.29314 | C001864690 | Oshane Warren | Westmoreland | Completed | Load_248174 | Paradise - 310 | Jul 24, 2026 3:54pm | Jul 24, 2026 3:55pm | Jul 24, 2026 5:27pm | Jul 24, 2026 7:55pm | Jul 24, 2026 8:14pm | Jul 24, 2026 1:00am | Jul 24, 2026 8:15pm | Jul 24, 2026 8:15pm |  |  | Fair | No | Unable to locate or contact customer
Outage | J.E.26.07.30403 | C001864689 | Oshane Warren | Westmoreland | Completed | Load_246222 | Paradise - 310 | Jul 24, 2026 3:54pm | Jul 24, 2026 3:55pm | Jul 24, 2026 6:20pm | Jul 24, 2026 6:20pm | Jul 24, 2026 6:20pm | Jul 24, 2026 6:25pm | Jul 24, 2026 6:26pm | Jul 24, 2026 6:26pm |  |  | Fair | No | Meter defective unable to connect customer meter needs to change refer to feel service
Outage | J.E.26.07.30477 | C001864688 | Eric Williams | KSAN | Completed | Load_567704 | Washington Blvd - 310 | Jul 24, 2026 3:53pm | Jul 24, 2026 3:56pm | Jul 24, 2026 5:12pm | Jul 24, 2026 5:12pm | Jul 24, 2026 5:29pm | Jul 24, 2026 5:29pm | Jul 24, 2026 5:30pm | Jul 24, 2026 5:30pm |  |  | Fair | No | Call to customer went unanswered,
Outage | J.E.26.07.30233 | C001864685 | Nickolas Rodriques | Portmore | Completed | Load_242899 | Naggo Head - 510 | Jul 24, 2026 3:48pm | Jul 24, 2026 3:48pm | Jul 24, 2026 4:17pm | Jul 24, 2026 7:56pm | Jul 24, 2026 8:29pm | Jul 24, 2026 9:02pm | Jul 24, 2026 9:04pm | Jul 24, 2026 9:04pm |  |  | Fair | No | Upon arrival checks were done which revealed that no power was flowing from one leg. Reading found at pothead (243-246). No noticeable fuse was seen blown from my point of view and also no broken wire was observed. However, unable to gain access to the transformer pole to do further checks due to vegetation that is required to clear path. Please note that efforts to reach the customer on the contact number provided were unsuccessful.
Outage | J.E.26.07.30440 | C001864681 | Nickolas Rodriques | Portmore | Completed | Load_253463 | Naggo Head - 610 | Jul 24, 2026 3:44pm | Jul 24, 2026 3:46pm | Jul 24, 2026 5:30pm | Jul 24, 2026 5:30pm | Jul 24, 2026 6:04pm | Jul 24, 2026 6:14pm | Jul 24, 2026 6:27pm | Jul 24, 2026 6:27pm | Fire |  | Fair | No | Checked and found customer with unstable voltage caused by corroded transformer drop leads. Isolate 50 KVA transformer for safety to repair. Repaired by cleaning and tightening transformer drop leads using three clamps, current reading is (118-118-236).
Non-Outage | J.E.26.07.19952 | C001864677 | Richard Nicholas | St.Catherine | Completed | Load_240550 | Tredegar - 210 | Jul 24, 2026 3:34pm | Jul 24, 2026 3:34pm | Jul 24, 2026 6:47pm | Jul 24, 2026 6:47pm | Jul 24, 2026 7:49pm | Jul 24, 2026 8:03pm | Jul 24, 2026 8:10pm | Jul 24, 2026 8:10pm | LeaningPole |  | Fair | No | Leaning 40ft class 6 pole with 3phase primary T-off to Mahon drive leaned towards the main road,two more 40ft pole also leaned as a result primary conductors become low hanging across a few premises gate that customer unable to drive in truck on to the premises.urgent follow up to rectify the fault.
Outage | J.E.26.07.30327 | C001864675 | Richard Nicholas | St.Catherine | Completed | Load_256300 | Tredegar - 210 | Jul 24, 2026 3:32pm | Jul 24, 2026 6:56pm | Jul 24, 2026 9:53pm | Jul 24, 2026 10:17pm | Jul 24, 2026 10:17pm | Jul 24, 2026 10:17pm | Jul 24, 2026 10:18pm | Jul 24, 2026 10:18pm |  |  | Fair | No | Area found ok
Outage | J.E.26.07.30422 | C001864674 | Richard Nicholas | St.Catherine | Completed | Load_251786 | Tredegar - 510 | Jul 24, 2026 3:32pm | Jul 24, 2026 7:05pm | Jul 24, 2026 10:18pm | Jul 24, 2026 10:18pm | Jul 24, 2026 11:13pm | Jul 24, 2026 11:13pm | Jul 24, 2026 11:13pm | Jul 24, 2026 11:13pm |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.07.27904 | C001864666 | Ricky Hall | St.Catherine | Completed | Load_245855 | New Michelton - 210 | Jul 24, 2026 3:26pm | Jul 24, 2026 3:32pm | Jul 24, 2026 8:07pm | Jul 24, 2026 9:31pm | Jul 24, 2026 9:43pm | Jul 24, 2026 9:43pm | Jul 24, 2026 9:43pm | Jul 24, 2026 9:43pm | Fire |  | Fair | No | No fire seen
Non-Outage | J.E.26.07.29406 | C001864665 | Ricky Hall | St.Catherine | Completed | Load_245855 | New Michelton - 210 | Jul 24, 2026 3:26pm | Jul 24, 2026 3:26pm | Jul 24, 2026 8:07pm | Jul 24, 2026 8:23pm | Jul 24, 2026 9:23pm | Jul 24, 2026 9:31pm | Jul 24, 2026 9:31pm | Jul 24, 2026 9:31pm | Fire |  | Fair | No | No fire seen
Non-Outage | J.E.26.07.29407 | C001864664 | Ricky Hall | St.Catherine | Completed | Load_245855 | New Michelton - 210 | Jul 24, 2026 3:26pm | Jul 24, 2026 3:26pm | Jul 24, 2026 8:07pm | Jul 24, 2026 9:44pm | Jul 24, 2026 9:44pm | Jul 24, 2026 9:44pm | Jul 24, 2026 9:44pm | Jul 24, 2026 9:44pm | Fire |  | Fair | No | Call was duplicated
Outage | J.E.26.07.30277 | C001864667 | Milton Charlton | KSAN | Completed | Load_255998 | Washington Blvd - 610 | Jul 24, 2026 3:26pm | Jul 24, 2026 3:42pm | Jul 24, 2026 6:41pm | Jul 24, 2026 7:49pm | Jul 24, 2026 7:50pm | Jul 24, 2026 7:35pm | Jul 24, 2026 7:52pm | Jul 24, 2026 7:52pm | BrokenWire |  | Fair | No | Found okay upon arrival. Customer did not made a report to JPS.
Outage | J.E.26.07.30405 | C001864661 | Elvis Trowers | KSAN | Completed | Load_269551 | Constant Spring - 210 | Jul 24, 2026 3:25pm | Jul 24, 2026 3:26pm | Jul 24, 2026 6:06pm | Jul 24, 2026 6:07pm | Jul 24, 2026 6:27pm | Jul 24, 2026 7:41pm | Jul 24, 2026 7:41pm | Jul 24, 2026 7:41pm |  |  | Fair | Yes | Areas was found without electricity supply when checked, and during patrol 3 blown junction fuses were found at separate locations, and was replaced after, 1/40 amp at pole #0011648 and 1/20 amp at pole #0011666 and another at pole #0011663.
Outage | J.E.26.07.30335 | C001864660 | Ricky Hall | St.Catherine | Completed | Load_246200 | New Michelton - 410 | Jul 24, 2026 3:24pm | Jul 24, 2026 3:26pm | Jul 24, 2026 3:36pm | Jul 24, 2026 3:37pm | Jul 24, 2026 5:04pm | Jul 24, 2026 5:39pm | Jul 24, 2026 5:40pm | Jul 24, 2026 5:40pm |  |  | Rains | No | Replace blown 25 amps junction fuse
Outage | J.E.26.07.30339 | C001864659 | Ricky Hall | St.Catherine | Completed | Load_251641 | New Michelton - 410 | Jul 24, 2026 3:24pm | Jul 24, 2026 3:26pm | Jul 24, 2026 3:37pm | Jul 24, 2026 5:40pm | Jul 24, 2026 5:40pm | Jul 24, 2026 5:41pm | Jul 24, 2026 5:41pm | Jul 24, 2026 5:41pm |  |  | Rains | No | Call associated with outage #30335
Outage | J.E.26.07.30391 | C001864658 | Milton Charlton | KSAN | Completed | Load_578940 | Hope - 510 | Jul 24, 2026 3:24pm | Jul 24, 2026 3:24pm | Jul 24, 2026 5:42pm | Jul 24, 2026 5:42pm | Jul 24, 2026 6:35pm | Jul 24, 2026 6:35pm | Jul 24, 2026 6:39pm | Jul 24, 2026 6:39pm |  |  | Fair | No | Refused and reclosed 30amps junction blown at pole #0119228 using one 30 amps fuse.
Outage | J.E.26.07.30421 | C001864657 | Milton Charlton | KSAN | Completed | Load_239076 | Hope - 510 | Jul 24, 2026 3:24pm | Jul 24, 2026 3:24pm | Jul 24, 2026 3:45pm | Jul 24, 2026 3:45pm | Jul 24, 2026 5:37pm | Jul 24, 2026 5:20pm | Jul 24, 2026 5:42pm | Jul 24, 2026 5:42pm |  |  | Fair | No | Customer service wire #6 triplex corroded at pothead. Repair using three 1- bolt clamps. Readings at meter socket117-118-236 volts.
Outage | J.E.26.07.30425 | C001864656 | Christopher Edwards | KSAN | Completed | Load_258240 | Constant Spring - 410 | Jul 24, 2026 3:24pm | Jul 24, 2026 3:25pm | Jul 24, 2026 4:50pm | Jul 24, 2026 4:50pm | Jul 24, 2026 6:43pm | Jul 24, 2026 6:30pm | Jul 24, 2026 7:25pm | Jul 24, 2026 7:25pm |  |  | Fair | No | Clear vegetation off transformer pole Refuse blown 25 kva transformer using (1) 2 amps
Outage | J.E.26.07.29766 | C001864655 | Jermaine Williams | St.Catherine | Completed | Load_269475 | Rhodens Pen - 310 | Jul 24, 2026 3:23pm | Jul 24, 2026 6:43pm | Jul 24, 2026 8:42pm | Jul 24, 2026 8:42pm | Jul 24, 2026 9:55pm | Jul 24, 2026 9:55pm | Jul 24, 2026 9:56pm | Jul 24, 2026 9:56pm |  |  | Fair | No | Replace Defective switch, left ok.
Outage | J.E.26.07.30206 | C001864653 | Cliton Henry | St.Mary | Completed | Load_269770 | Blackstonedge - 110 | Jul 24, 2026 3:22pm | Jul 24, 2026 3:22pm | Jul 24, 2026 7:35pm | Jul 24, 2026 7:35pm | Jul 24, 2026 8:16pm | Jul 24, 2026 8:52pm | Jul 24, 2026 8:56pm | Jul 24, 2026 8:56pm |  |  | Fair | No | The customer service wire was reconnected at pothead using 3 one bolt clamps. Voltage left were 110-111/221 volts. The meter is defective kindly refer to Field Service Department for a meter replacement.
Outage | J.E.26.07.30320 | C001864651 | Neckell Ormsby | St.Mary | Completed | Load_258768 | Highgate - 210 | Jul 24, 2026 3:19pm | Jul 24, 2026 3:19pm | Jul 24, 2026 3:23pm | Jul 24, 2026 3:24pm | Jul 24, 2026 4:44pm | Jul 24, 2026 5:54pm | Jul 24, 2026 5:54pm | Jul 24, 2026 5:54pm | BrokenWire |  | Fair | No | Found junction fuse blown no pole number seen patrol and found tree on primary with dislodge insulator, cut and remove tree and reinstall conductor also replace 1- 20 amp fuse
Outage | J.E.26.07.29741 | C001864647 | Clyde Brown | Clarendon | Completed | Load_242961 | Parnassus - 210 | Jul 24, 2026 3:14pm | Jul 25, 2026 11:31am | Jul 25, 2026 11:42am | Jul 25, 2026 11:42am | Jul 25, 2026 1:16pm | Jul 25, 2026 1:20pm | Jul 25, 2026 1:29pm | Jul 25, 2026 1:29pm |  |  | Fair | No
Outage | J.E.26.07.30283 | C001864646 | Jermaine Williams | Clarendon | Completed | Load_245178 | Parnassus - 310 | Jul 24, 2026 3:14pm | Jul 24, 2026 3:14pm | Jul 24, 2026 3:37pm | Jul 24, 2026 3:37pm | Jul 24, 2026 3:53pm | Jul 24, 2026 3:53pm | Jul 24, 2026 3:54pm | Jul 24, 2026 3:54pm |  |  | Fair | No | Premises found ok.
Outage | J.E.26.07.30385 | C001864644 | Jermaine Williams | Clarendon | Completed | Load_247213 | Parnassus - 310 | Jul 24, 2026 3:14pm | Jul 24, 2026 3:14pm | Jul 24, 2026 8:39pm | Jul 24, 2026 8:39pm | Jul 24, 2026 8:39pm | Jul 24, 2026 8:39pm | Jul 24, 2026 8:40pm | Jul 24, 2026 8:40pm |  |  | Fair | No | Replace 1-7A Junction fuse
Outage | J.E.26.07.30402 | C001864643 | Jermaine Williams | Clarendon | Completed | Load_253435 | Parnassus - 310 | Jul 24, 2026 3:14pm | Jul 24, 2026 3:14pm | Jul 24, 2026 7:19pm | Jul 24, 2026 7:19pm | Jul 24, 2026 8:08pm | Jul 24, 2026 8:27pm | Jul 24, 2026 8:27pm | Jul 24, 2026 8:27pm |  |  | Fair | No | Replace 1-30A Junction fuse
Outage | J.E.26.07.30431 | C001864645 | Jermaine Williams | Clarendon | Completed | Load_254877 | Parnassus - 310 | Jul 24, 2026 3:14pm | Jul 24, 2026 3:14pm | Jul 24, 2026 9:56pm | Jul 24, 2026 9:56pm | Jul 24, 2026 9:56pm | Jul 24, 2026 9:57pm | Jul 24, 2026 9:57pm | Jul 24, 2026 9:57pm |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.07.29664 | C001864640 | Eric Williams | null | Completed | null | null | Jul 24, 2026 3:11pm | Jul 24, 2026 3:55pm | Jul 24, 2026 8:54pm | Jul 24, 2026 8:54pm | Jul 24, 2026 9:51pm | Jul 24, 2026 9:51pm | Jul 24, 2026 9:52pm | Jul 24, 2026 9:52pm | LeaningPole |  | Fair | No | Rotten 30 class6 pole refer to maintenance department
Outage | J.E.26.07.30273 | C001864639 | Eric Williams | KSAN | Completed | Load_293895 | Washington Blvd - 710 | Jul 24, 2026 3:11pm | Jul 24, 2026 3:54pm | Jul 24, 2026 5:10pm | Jul 24, 2026 5:10pm | Jul 24, 2026 5:10pm | Jul 24, 2026 5:11pm | Jul 24, 2026 5:11pm | Jul 24, 2026 5:11pm |  |  | Fair | No | Premises lock, several calls to customer went unanswered.
Outage | J.E.26.07.30384 | C001864638 | Stephen Taylor | St.Thomas | Completed | Load_556320 | Good Year - 210 | Jul 24, 2026 3:11pm | Jul 24, 2026 3:13pm | Jul 24, 2026 3:33pm | Jul 24, 2026 3:33pm | Jul 24, 2026 3:33pm | Jul 24, 2026 3:33pm | Jul 24, 2026 3:36pm | Jul 24, 2026 3:36pm |  |  | Fair | No | Rami box rami box is hanging a single phase coming from the box and need field service technician to correct problem as soon as possible
Non-Outage | J.E.26.07.24840 | C001864635 | Shamour Haughton | null | Completed | null | null | Jul 24, 2026 3:10pm | Jul 24, 2026 3:10pm | Jul 24, 2026 3:19pm | Jul 24, 2026 3:19pm | Jul 24, 2026 4:51pm | Jul 24, 2026 4:51pm | Jul 24, 2026 5:01pm | Jul 24, 2026 5:01pm | LowHangingWires |  | Fair | No | Found secondary phase low, isolate 50kva to retention secondary phase, using 1#2 preform and 1 clamp and reclose 50kva
Outage | J.E.26.07.29441 | C001864634 | Richard Samuda | Manchester | Completed | Load_267659 | Spur Tree - 310 | Jul 24, 2026 3:09pm | Jul 24, 2026 3:10pm | Jul 24, 2026 3:36pm | Jul 24, 2026 3:36pm | Jul 24, 2026 3:46pm | Jul 24, 2026 4:20pm | Jul 24, 2026 4:23pm | Jul 24, 2026 4:23pm |  |  | Fair | No | Customer back to normal
Outage | J.E.26.07.29680 | C001864632 | Richard Samuda | Manchester | Completed | Load_294633 | Spur Tree - 310 | Jul 24, 2026 3:09pm | Jul 24, 2026 3:10pm | Jul 24, 2026 4:24pm | Jul 24, 2026 4:42pm | Jul 24, 2026 4:42pm | Jul 24, 2026 4:44pm | Jul 24, 2026 4:45pm | Jul 24, 2026 4:45pm |  |  | Fair | No | Refer call to field service customer breaker is tripped and needs to reset customer is on a rami system
Outage | J.E.26.07.30183 | C001864627 | Kenroy Dale | Manchester | Completed | Load_269460 | Porus - 310 | Jul 24, 2026 3:09pm | Jul 24, 2026 3:09pm | Jul 24, 2026 7:45pm | Jul 24, 2026 7:45pm | Jul 24, 2026 9:00pm | Jul 24, 2026 9:37pm | Jul 24, 2026 9:39pm | Jul 24, 2026 9:39pm |  |  | Fair | No | Low voltage coming from RAMI box, field service is required
Outage | J.E.26.07.30189 | C001864628 | Kenroy Dale | Manchester | Completed | Load_246578 | Porus - 310 | Jul 24, 2026 3:09pm | Jul 24, 2026 3:09pm | Jul 24, 2026 5:54pm | Jul 24, 2026 6:01pm | Jul 24, 2026 7:13pm | Jul 24, 2026 7:44pm | Jul 24, 2026 7:45pm | Jul 24, 2026 7:45pm |  |  | Fair | No | Burned off neutral found at pole, remade connection using 1 one bolt clamp. Voltage reading 114/116/230
Outage | J.E.26.07.30257 | C001864633 | Richard Samuda | Manchester | Completed | Load_302011 | Spur Tree - 310 | Jul 24, 2026 3:09pm | Jul 24, 2026 3:10pm | Jul 24, 2026 7:07pm | Jul 24, 2026 7:07pm | Jul 24, 2026 7:11pm | Jul 24, 2026 7:11pm | Jul 24, 2026 7:12pm | Jul 24, 2026 7:12pm |  |  | Fair | No | Customer say he’s back to normal
Outage | J.E.26.07.30298 | C001864607 | Nickolas Rodriques | Portmore | Completed | Load_243615 | Naggo Head - 510 | Jul 24, 2026 2:30pm | Jul 24, 2026 3:46pm | Jul 24, 2026 4:41pm | Jul 24, 2026 4:42pm | Jul 24, 2026 5:08pm | Jul 24, 2026 5:22pm | Jul 24, 2026 5:28pm | Jul 24, 2026 5:28pm |  |  | Fair | No | Found customers with electricity. Customer confirmed that the area outage was restored.
Outage | J.E.26.07.30313 | C001864604 | Daniel Francis | St.Ann | Completed | Load_257880 | Roaring River - 410 | Jul 24, 2026 2:24pm | Jul 24, 2026 3:23pm | Jul 24, 2026 3:31pm | Jul 24, 2026 3:31pm | Jul 24, 2026 3:45pm | Jul 24, 2026 4:42pm | Jul 24, 2026 4:45pm | Jul 24, 2026 4:45pm |  |  | Fair | No | Remade joint at JPS pole using two 1bolt clamps voltage 120/120/207/ 240/239/236
Outage | J.E.26.07.29733 | C001864596 | Moses Elliston | St.Catherine | Completed | Load_240276 | Tredegar - 210 | Jul 24, 2026 2:15pm | Jul 24, 2026 2:15pm | Jul 24, 2026 2:30pm | Jul 24, 2026 2:30pm | Jul 24, 2026 2:30pm | Jul 24, 2026 12:20pm | Jul 24, 2026 2:34pm | Jul 24, 2026 2:34pm |  |  | Fair | No | Burnt 3 wire service repaired with 40 ‘ #6 triplex 4 linkets,1clamp.Short circuit in building.Service disconnected at meter .Customer advised
Outage | J.E.26.07.29758 | C001864597 | Moses Elliston | St.Catherine | Completed | Load_270021 | Tredegar - 210 | Jul 24, 2026 2:15pm | Jul 24, 2026 2:16pm | Jul 24, 2026 2:37pm | Jul 24, 2026 2:37pm | Jul 24, 2026 2:37pm | Jul 24, 2026 2:45pm | Jul 24, 2026 2:45pm | Jul 24, 2026 2:45pm |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.07.30285 | C001864595 | Tyrese Williams | St.Ann | Completed | Load_262944 | Cardiff Hall - 210 | Jul 24, 2026 2:12pm | Jul 24, 2026 2:12pm | Jul 24, 2026 2:59pm | Jul 24, 2026 3:24pm | Jul 24, 2026 3:25pm | Jul 24, 2026 3:25pm | Jul 24, 2026 3:25pm | Jul 24, 2026 3:25pm | Fire |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.07.30295 | C001864594 | Cliton Henry | St.Mary | Completed | Load_237637 | Blackstonedge - 110 | Jul 24, 2026 2:10pm | Jul 24, 2026 3:21pm | Jul 24, 2026 6:02pm | Jul 24, 2026 6:02pm | Jul 24, 2026 6:37pm | Jul 24, 2026 7:10pm | Jul 24, 2026 7:11pm | Jul 24, 2026 7:11pm | BrokenWire |  | Fair | No | The customer meter found disconnected for debt. The customer was advised.
Outage | J.E.26.07.29368 | C001864579 | Jermaine Williams | Clarendon | Completed | Load_265061 | Monymusk - 410 | Jul 24, 2026 1:58pm | Jul 24, 2026 3:15pm | Jul 24, 2026 9:57pm | Jul 24, 2026 9:57pm | Jul 24, 2026 9:57pm | Jul 24, 2026 9:57pm | Jul 24, 2026 9:59pm | Jul 24, 2026 9:59pm |  |  | Fair | No | Splice and retention broken phase Conductor using 5ft #4 bare copper and left ok.
Non-Outage | J.E.26.07.30240 | C001864577 | Marlon Brown | Trelawny | Completed | Load_572265 | Duncans - 110 | Jul 24, 2026 1:53pm | Jul 24, 2026 1:54pm | Jul 24, 2026 2:02pm | Jul 24, 2026 2:02pm | Jul 24, 2026 2:02pm | Jul 24, 2026 2:54pm | Jul 24, 2026 2:56pm | Jul 24, 2026 2:56pm |  |  | Fair | Yes | Isolated 3 100kva transformers to change phase @ transformer drop lead for customer 3 phase supply to operate properly. Customer motors were reversing due to a phase issue. Voltage found at pothead 120/120/208=240/239/241Voltage leaving 120/120/208=240/241/239
Outage | J.E.26.07.30279 | C001864576 | Romeo Brissett | St.James | Completed | Load_266674 | Bogue - 410 | Jul 24, 2026 1:51pm | Jul 25, 2026 7:14am | Jul 25, 2026 9:02am | Jul 25, 2026 9:02am | Jul 25, 2026 9:11am | Jul 25, 2026 9:25am | Jul 25, 2026 9:27am | Jul 25, 2026 9:27am |  |  | Fair | No | Security at the gate stated issue was resolved from yesterday.
Outage | J.E.26.07.29772 | C001864571 | Ricky Hall | St.Catherine | Completed | Load_242271 | New Michelton - 410 | Jul 24, 2026 1:49pm | Jul 24, 2026 3:25pm | Jul 24, 2026 5:43pm | Jul 24, 2026 5:43pm | Jul 24, 2026 7:07pm | Jul 24, 2026 7:58pm | Jul 24, 2026 7:59pm | Jul 24, 2026 7:59pm | BrokenWire |  | Fair | No | Conduct spot bushing replaced blow 2 amps fuse 25 kva xfmr
Non-Outage | J.E.26.07.26865 | C001864563 | Christopher Edwards | KSAN | Completed | Load_249915 | Constant Spring - 410 | Jul 24, 2026 1:27pm | Jul 24, 2026 1:28pm | Jul 24, 2026 1:35pm | Jul 24, 2026 1:38pm | Jul 24, 2026 3:27pm | Jul 24, 2026 4:49pm | Jul 24, 2026 4:50pm | Jul 24, 2026 4:50pm |  |  | Fair | No | Remake burnt open secondary neutral jumper Using (1) one bolt clamps
Outage | J.E.26.07.29791 | C001864554 | Gregory Grossett | Portland | Completed | Load_247300 | Port Antonio - 410 | Jul 24, 2026 1:12pm | Jul 24, 2026 3:32pm | Jul 24, 2026 4:01pm | Jul 24, 2026 4:01pm | Jul 24, 2026 5:01pm | Jul 24, 2026 5:12pm | Jul 24, 2026 5:13pm | Jul 24, 2026 5:13pm | LeakingTransformer |  | Fair | No | 25kva transformer leaking badly and needs to change please refer to maintenance pole#0097909.
Outage | J.E.26.07.30199 | C001864546 | Edward Royal | KSAS | Completed | Load_254801 | Greenwich - 510 | Jul 24, 2026 1:09pm | Jul 24, 2026 1:35pm | Jul 24, 2026 1:59pm | Jul 24, 2026 1:59pm | Jul 24, 2026 2:02pm | Jul 24, 2026 2:09pm | Jul 24, 2026 2:10pm | Jul 24, 2026 2:10pm |  |  | Fair | No | Premises found close
Outage | J.E.26.07.29717 | C001864544 | Rusean Allen | KSAS | Completed | Load_290055 | Hunts Bay - 810 | Jul 24, 2026 1:02pm | Jul 24, 2026 1:02pm | Jul 24, 2026 2:52pm | Jul 24, 2026 2:52pm | Jul 24, 2026 3:01pm | Jul 24, 2026 3:07pm | Jul 24, 2026 3:08pm | Jul 24, 2026 3:08pm |  |  | Fair | No | Hexing failure, hexing enclosure installation incomplete. Refer to field service department.
Outage | J.E.26.07.30202 | C001864543 | Rusean Allen | KSAS | Completed | Load_301332 | Hunts Bay - 410 | Jul 24, 2026 1:02pm | Jul 24, 2026 1:02pm | Jul 24, 2026 4:54pm | Jul 24, 2026 4:54pm | Jul 24, 2026 7:17pm | Jul 24, 2026 7:48pm | Jul 24, 2026 7:48pm | Jul 24, 2026 7:48pm |  |  | Fair | No | 1x 3amp fuse found 1x 3amp fuse replaced
Non-Outage | J.E.26.07.30181 | C001864525 | Andre Williams | Trelawny | Completed | Load_294464 | Greenwood - 110 | Jul 24, 2026 12:42pm | Jul 25, 2026 7:56am | Jul 25, 2026 8:04am | Jul 25, 2026 9:02am | Jul 25, 2026 9:02am | Jul 25, 2026 9:04am | Jul 25, 2026 9:06am | Jul 25, 2026 9:06am |  |  | Fair | No | Premises with supply confirm by customer
Non-Outage | J.E.26.07.16558 | C001864520 | Tajay Bernard | Hanover | Completed | Load_253325 | Orange Bay - 210 | Jul 24, 2026 12:40pm | Jul 25, 2026 1:34pm | Jul 25, 2026 2:35pm | Jul 25, 2026 2:35pm | Jul 25, 2026 2:35pm | Jul 25, 2026 2:36pm | Jul 25, 2026 2:36pm | Jul 25, 2026 2:36pm |  |  | Fair | No | Customer stated that the issue has been resolved
Non-Outage | J.E.26.07.17011 | C001864519 | Rayon Foster | Hanover | Completed | Load_243094 | Orange Bay - 210 | Jul 24, 2026 12:40pm | Jul 24, 2026 12:40pm | Jul 24, 2026 12:48pm | Jul 24, 2026 12:48pm | Jul 24, 2026 12:57pm | Jul 24, 2026 1:19pm | Jul 24, 2026 1:19pm | Jul 24, 2026 1:19pm |  |  | Fair | No | Found working ok voltage check in meter socket 116/117AB233vilts
Non-Outage | J.E.26.07.26571 | C001864518 | Tajay Bernard | Hanover | Completed | Load_267889 | Orange Bay - 210 | Jul 24, 2026 12:40pm | Jul 25, 2026 1:34pm | Jul 25, 2026 2:40pm | Jul 25, 2026 2:40pm | Jul 25, 2026 3:12pm | Jul 25, 2026 3:13pm | Jul 25, 2026 3:13pm | Jul 25, 2026 3:13pm |  |  | Fair | No | Area check and found unable to locate customer on premises multiple phone calls to customer number went unanswered
Non-Outage | J.E.26.07.26590 | C001864517 | Rayon Foster | Hanover | Completed | Load_568368 | Orange Bay - 210 | Jul 24, 2026 12:39pm | Jul 24, 2026 12:40pm | Jul 24, 2026 1:02pm | Jul 24, 2026 1:50pm | Jul 24, 2026 3:40pm | Jul 24, 2026 3:42pm | Jul 24, 2026 3:43pm | Jul 24, 2026 3:43pm |  |  | Rains | No | Found working ok customer said he received back power after a power outage
Non-Outage | J.E.26.07.21687 | C001864512 | Rayon Foster | Hanover | Completed | Load_573736 | Orange Bay - 210 | Jul 24, 2026 12:38pm | Jul 24, 2026 12:39pm | Jul 24, 2026 6:49pm | Jul 24, 2026 7:05pm | Jul 24, 2026 7:48pm | Jul 24, 2026 8:07pm | Jul 24, 2026 8:07pm | Jul 24, 2026 8:07pm |  |  | Rains | No | Low voltage issue was resolved weeks ago by a jps team when speak to customer
Non-Outage | J.E.26.07.25031 | C001864516 | Tajay Bernard | Hanover | Completed | Load_303124 | Orange Bay - 210 | Jul 24, 2026 12:38pm | Jul 25, 2026 1:34pm | Jul 25, 2026 1:43pm | Jul 25, 2026 1:43pm | Jul 25, 2026 2:08pm | Jul 25, 2026 2:31pm | Jul 25, 2026 2:31pm | Jul 25, 2026 2:31pm |  |  | Fair | No | Check and found customer meter burned which causes customer to be single phasing refer to field service Cause ( meter socket need to be replace which lead to the meter burning)Customer was advised
Non-Outage | J.E.26.07.26545 | C001864514 | Rayon Foster | Hanover | Completed | Load_573746 | Orange Bay - 210 | Jul 24, 2026 12:38pm | Jul 24, 2026 12:39pm | Jul 24, 2026 1:29pm | Jul 24, 2026 1:29pm | Jul 24, 2026 1:37pm | Jul 24, 2026 1:50pm | Jul 24, 2026 1:50pm | Jul 24, 2026 1:50pm |  |  | Rains | No | Unable to reach customer on cell number provided or locate premises power in area voltage check in area 115/114AB229
Non-Outage | J.E.26.07.26612 | C001864515 | Tajay Bernard | Hanover | Completed | Load_292767 | Orange Bay - 210 | Jul 24, 2026 12:38pm | Jul 25, 2026 1:34pm | Jul 25, 2026 2:34pm | Jul 25, 2026 2:34pm | Jul 25, 2026 2:34pm | Jul 25, 2026 2:35pm | Jul 25, 2026 2:35pm | Jul 25, 2026 2:35pm |  |  | Fair | No | Customer stated that the issue has been resolved
Non-Outage | J.E.26.07.26694 | C001864513 | Rayon Foster | Hanover | Completed | Load_252846 | Orange Bay - 210 | Jul 24, 2026 12:38pm | Jul 24, 2026 12:39pm | Jul 24, 2026 5:22pm | Jul 24, 2026 5:24pm | Jul 24, 2026 5:56pm | Jul 24, 2026 6:38pm | Jul 24, 2026 6:38pm | Jul 24, 2026 6:38pm |  |  | Fair | No | Not enough driving detail can’t reach customer on cell phone
Non-Outage | J.E.26.07.16167 | C001864510 | Rayon Foster | Hanover | Completed | Load_555701 | Orange Bay - 210 | Jul 24, 2026 12:37pm | Jul 24, 2026 12:39pm | Jul 24, 2026 1:13pm | Jul 24, 2026 3:43pm | Jul 24, 2026 4:12pm | Jul 24, 2026 4:41pm | Jul 24, 2026 4:41pm | Jul 24, 2026 4:41pm | BrokenPole |  | Fair | No | Customer said issue was resolved by JPS maintenance team
Non-Outage | J.E.26.07.26669 | C001864511 | Tajay Bernard | Hanover | Completed | Load_303172 | Orange Bay - 210 | Jul 24, 2026 12:37pm | Jul 25, 2026 1:34pm | Jul 25, 2026 2:36pm | Jul 25, 2026 2:37pm | Jul 25, 2026 2:39pm | Jul 25, 2026 2:40pm | Jul 25, 2026 2:40pm | Jul 25, 2026 2:40pm |  |  | Fair | No | Area check and found customer unable to locate customer on premises multiple phone calls to customer number went unanswered
Outage | J.E.26.07.30143 | C001864486 | Raymond Lewis | St.Ann | Completed | Load_239976 | Cardiff Hall - 210 | Jul 24, 2026 12:16pm | Jul 24, 2026 12:17pm | Jul 24, 2026 2:11pm | Jul 24, 2026 2:11pm | Jul 24, 2026 2:29pm | Jul 24, 2026 2:31pm | Jul 24, 2026 2:31pm | Jul 24, 2026 2:31pm |  |  | Fair | No | Supply restored
Non-Outage | J.E.26.07.29785 | C001864482 | Raymond Lewis | St.Ann | Completed | Load_257880 | Roaring River - 410 | Jul 24, 2026 12:14pm | Jul 24, 2026 12:15pm | Jul 24, 2026 12:22pm | Jul 24, 2026 12:22pm | Jul 24, 2026 12:30pm | Jul 24, 2026 12:38pm | Jul 24, 2026 12:37pm | Jul 24, 2026 12:37pm |  |  | SevereWind | No | Open 3 x 50 kva x former
Outage | J.E.26.07.29956 | C001864481 | Swon Miller | St.James | Completed | Load_557020 | Bogue - 310 | Jul 24, 2026 12:12pm | Jul 24, 2026 12:12pm | Jul 24, 2026 1:50pm | Jul 24, 2026 1:50pm | Jul 24, 2026 2:36pm | Jul 28, 2026 2:50am | Jul 24, 2026 2:50pm | Jul 24, 2026 2:50pm | LowHangingWires |  | Fair | No | Found multiple services wires hanging low across customer gate a 30 ft class six pole is needed to raise wires.wires are not able to be tension due to pole being about 300 feet apart from each others and multiple mid span connections intermediate pole is urgently required to rise up the wires plz refer to maintenance/k.Frazier
Non-Outage | J.E.26.07.15283 | C001864477 | Derrick Grubb | St.Thomas | Completed | Load_269237 | Good Year - 210 | Jul 24, 2026 12:10pm | Jul 24, 2026 12:10pm | Jul 24, 2026 12:15pm | Jul 24, 2026 12:15pm | Jul 24, 2026 1:02pm | Jul 24, 2026 1:03pm | Jul 24, 2026 1:03pm | Jul 24, 2026 1:03pm |  |  | Fair | No | Premises not located. Several calls to customer phone went unanswered.
Non-Outage | J.E.26.07.29856 | C001864476 | Milton Charlton | null | Completed | null | null | Jul 24, 2026 12:08pm | Jul 24, 2026 12:08pm | Jul 24, 2026 12:20pm | Jul 24, 2026 12:20pm | Jul 24, 2026 1:00pm | Jul 24, 2026 12:55pm | Jul 24, 2026 1:06pm | Jul 24, 2026 1:06pm | BrokenPole |  | Fair | No | 30ft wooden pole #0001994 broken in motor vehicle accident. Need immediate attention. Pole has on open wire 4-wire secondary D/E on 8ft crossarm and 3- wire secondary D/E on the other side and street light. No customer is without supply.
Non-Outage | J.E.26.07.27608 | C001864470 | Marlon Brown | Trelawny | Completed | Load_250973 | Greenwood - 110 | Jul 24, 2026 11:57am | Jul 24, 2026 11:59am | Jul 24, 2026 12:06pm | Jul 24, 2026 12:06pm | Jul 24, 2026 1:38pm | Jul 24, 2026 1:40pm | Jul 24, 2026 1:40pm | Jul 24, 2026 1:40pm |  |  | Fair | No | Rectified by NWC personnel.
Outage | J.E.26.07.29782 | C001864468 | Neckell Ormsby | St.Mary | Completed | Load_237969 | Highgate - 210 | Jul 24, 2026 11:55am | Jul 24, 2026 3:20pm | Jul 24, 2026 5:58pm | Jul 24, 2026 5:58pm | Jul 24, 2026 6:49pm | Jul 24, 2026 7:11pm | Jul 24, 2026 7:11pm | Jul 24, 2026 7:11pm | BrokenWire |  | Fair | No | Found corrosion at pole used 2- one bolt clamps on phase and neutral voltage left 115v 113v 228v
Outage | J.E.26.07.29678 | C001864467 | Raymond Lewis | St.Ann | Completed | Load_260937 | Roaring River - 210 | Jul 24, 2026 11:53am | Jul 24, 2026 12:19pm | Jul 24, 2026 12:44pm | Jul 24, 2026 12:44pm | Jul 24, 2026 1:49pm | Jul 24, 2026 2:10pm | Jul 24, 2026 2:10pm | Jul 24, 2026 2:10pm |  |  | Fair | No | Refuse and close 15 amp junction
Outage | J.E.26.07.29775 | C001864466 | Tajay Bernard | Hanover | Completed | Load_252494 | Orange Bay - 310 | Jul 24, 2026 11:51am | Jul 24, 2026 12:01pm | Jul 24, 2026 12:07pm | Jul 24, 2026 12:08pm | Jul 24, 2026 1:05pm | Jul 24, 2026 1:47pm | Jul 24, 2026 1:48pm | Jul 24, 2026 1:48pm |  |  | Fair | No | Isolate 1 25kva Transformer to clean and remake transformer drop Leeds, 2 clamps was used Voltage found 112Voltage left 112/112/224
Outage | J.E.26.07.29760 | C001864453 | Romeo Brissett | St.James | Completed | Load_244720 | Bogue - 510 | Jul 24, 2026 11:41am | Jul 24, 2026 11:46am | Jul 24, 2026 12:38pm | Jul 24, 2026 12:38pm | Jul 24, 2026 1:07pm | Jul 24, 2026 2:22pm | Jul 24, 2026 2:22pm | Jul 24, 2026 2:22pm |  |  | EarthMovement | No | Clear primary jumper from pole and replaced (1)20amps junction fuse
Outage | J.E.26.07.29756 | C001864448 | Derrick Dawkins | St.James | Completed | Load_248436 | Queens Drive - 310 | Jul 24, 2026 11:39am | Jul 24, 2026 4:17pm | Jul 24, 2026 4:43pm | Jul 24, 2026 4:43pm | Jul 24, 2026 5:42pm | Jul 24, 2026 5:48pm | Jul 24, 2026 5:50pm | Jul 24, 2026 5:50pm |  |  | Fair | No | Premises found ok voltage left 120/120/240
Non-Outage | J.E.26.07.29748 | C001864447 | Andre Smith | null | Completed | null | null | Jul 24, 2026 11:35am | Jul 24, 2026 11:36am | Jul 24, 2026 12:52pm | Jul 24, 2026 12:52pm | Jul 24, 2026 1:09pm | Jul 24, 2026 1:09pm | Jul 24, 2026 1:10pm | Jul 24, 2026 1:10pm | BrokenWire |  | Fair | No | Repair burnt phase at pothead supply restored 114V
Outage | J.E.26.07.29719 | C001864434 | Elvis Trowers | KSAN | Completed | Load_245203 | Constant Spring - 210 | Jul 24, 2026 11:27am | Jul 24, 2026 11:27am | Jul 24, 2026 12:00pm | Jul 24, 2026 12:00pm | Jul 24, 2026 1:08pm | Jul 24, 2026 2:18pm | Jul 24, 2026 2:18pm | Jul 24, 2026 2:18pm |  |  | Fair | Yes | Premises was found without electricity supply when checked, and defective lighting arrester was found during patrol and was removed then replaced 3/7 amp junction fuses at pole #0011273.
Non-Outage | J.E.26.07.26057 | C001864416 | Derrick Grubb | St.Thomas | Completed | Load_262336 | Good Year - 110 | Jul 24, 2026 11:14am | Jul 24, 2026 11:15am | Jul 24, 2026 1:03pm | Jul 24, 2026 1:03pm | Jul 24, 2026 1:07pm | Jul 24, 2026 1:10pm | Jul 24, 2026 1:10pm | Jul 24, 2026 1:10pm |  |  | Fair | No | Contact customer by phone and customer said premises is okay.
Outage | J.E.26.07.29558 | C001864415 | Marlon Brown | Trelawny | Completed | Load_292657 | Duncans - 110 | Jul 24, 2026 11:12am | Jul 24, 2026 11:35am | Jul 24, 2026 11:58am | Jul 24, 2026 11:58am | Jul 24, 2026 12:02pm | Jul 24, 2026 12:06pm | Jul 24, 2026 12:06pm | Jul 24, 2026 12:06pm |  |  | Fair | No | Customer says it was internal issues and they had fixed the issue.
Outage | J.E.26.07.29576 | C001864409 | Richard Nicholas | St.Catherine | Completed | Load_252298 | Twickenham - 410 | Jul 24, 2026 11:09am | Jul 24, 2026 11:09am | Jul 24, 2026 2:36pm | Jul 24, 2026 2:36pm | Jul 24, 2026 3:18pm | Jul 24, 2026 6:40pm | Jul 24, 2026 6:47pm | Jul 24, 2026 6:47pm |  |  | Fair | No | Replaced blown 40x2 junctions fuse on pole #008007,replaced blown 30amp junctions at the intersection,replaced blown 10amp junctions on pole #620620.replaced blown 10amp junctions fuse near to pole #595835.replaced blown 50kva x2 transformer 3amp fuse on pole #014029.replaced blown 15amp junctions fuse at the 3phase T-off to the cold storage and blown 100kva transformer 10amp fuse and blown 50kva transformer 5amp fuse at the cold storage.
Outage | J.E.26.07.29660 | C001864410 | Wan Carlos Scarlett | Portmore | Completed | Load_579367 | Naggo Head - 610 | Jul 24, 2026 11:09am | Jul 24, 2026 11:10am | Jul 24, 2026 2:53pm | Jul 24, 2026 2:53pm | Jul 24, 2026 3:05pm | Jul 24, 2026 3:14pm | Jul 24, 2026 4:07pm | Jul 24, 2026 4:07pm | BrokenWire |  | Fair | No | Found cable and wireless wire broken and on the ground customer not available at this time premises closed
Outage | J.E.26.07.29673 | C001864411 | Hartley Chin | Clarendon | Completed | Load_263640 | Parnassus - 310 | Jul 24, 2026 11:09am | Jul 24, 2026 11:10am | Jul 24, 2026 12:27pm | Jul 24, 2026 12:32pm | Jul 24, 2026 12:58pm | Jul 24, 2026 1:12pm | Jul 24, 2026 1:14pm | Jul 24, 2026 1:14pm |  |  | Fair | No | Found blown 10 amp junction fuse @ pole # 614281 due to tree contact, cut tree limb . Junction refused…
Non-Outage | J.E.26.07.29653 | C001864408 | Jowayne Newmans | Portland | Completed | Load_267156 | Port Antonio - 410 | Jul 24, 2026 11:07am | Jul 25, 2026 7:21am | Jul 25, 2026 8:18am | Jul 25, 2026 8:18am | Jul 25, 2026 9:15am | Jul 25, 2026 9:39am | Jul 25, 2026 9:39am | Jul 25, 2026 9:39am |  |  | Fair | No | Customer was experiencing low voltage 115v, 99v, 200v cause by corrosion at secondary connection. Repair by reconnecting service wire using three one bolt clamp. Voltage reading after repair 115v, 115v, 230v.
Outage | J.E.26.07.29575 | C001864407 | Romeo Brissett | St.James | Completed | Load_242321 | Bogue - 510 | Jul 24, 2026 11:06am | Jul 24, 2026 11:32am | Jul 24, 2026 11:36am | Jul 24, 2026 11:36am | Jul 24, 2026 11:51am | Jul 24, 2026 12:27pm | Jul 24, 2026 12:38pm | Jul 24, 2026 12:38pm |  |  | Fair | No | Found tree fell on one pole span of touch conductor primary line, need bucket truck team to cut and removed tree, line is still energized and system neutral is broken. Please send to maintenance. Was advised by Mr Richard’s.
Outage | J.E.26.07.29570 | C001864399 | Romeo Brissett | St.James | Completed | Load_263487 | Bogue - 510 | Jul 24, 2026 11:05am | Jul 24, 2026 11:32am | Jul 24, 2026 2:24pm | Jul 24, 2026 2:24pm | Jul 24, 2026 2:47pm | Jul 24, 2026 3:00pm | Jul 24, 2026 3:01pm | Jul 24, 2026 3:01pm |  |  | Fair | No | Cut and Removed vegetation and replaced (1)25 kva transformer fuse, no phone service in the area. Used (1)2amps fuse.
Outage | J.E.26.07.29579 | C001864398 | Romeo Brissett | St.James | Completed | Load_237873 | Bogue - 510 | Jul 24, 2026 11:05am | Jul 24, 2026 11:32am | Jul 24, 2026 2:22pm | Jul 24, 2026 2:22pm | Jul 24, 2026 2:22pm | Jul 24, 2026 2:20pm | Jul 24, 2026 2:23pm | Jul 24, 2026 2:23pm |  |  | Fair | No | Check and found ok related to job #29760
Non-Outage | J.E.26.07.29487 | C001864393 | Wan Carlos Scarlett | null | Completed | null | null | Jul 24, 2026 10:58am | Jul 24, 2026 10:58am | Jul 24, 2026 1:27pm | Jul 24, 2026 1:27pm | Jul 24, 2026 2:10pm | Jul 24, 2026 2:38pm | Jul 24, 2026 2:53pm | Jul 24, 2026 2:53pm | BrokenWire |  | Fair | No | Found 30ft dead end pole with hexing service box and numbers of service wires hanging low towards the ground 30ft pole with guy wire rooting up from the ground cause pole to lean towards the ground need urgent attention pole # 0061654 call referred to maintenance department
Outage | J.E.26.07.29552 | C001864392 | Richard Nicholas | St.Catherine | Completed | Load_254602 | Tredegar - 310 | Jul 24, 2026 10:57am | Jul 24, 2026 10:58am | Jul 24, 2026 12:37pm | Jul 24, 2026 12:37pm | Jul 24, 2026 12:54pm | Jul 24, 2026 1:07pm | Jul 24, 2026 1:08pm | Jul 24, 2026 1:08pm | BrokenWire |  | Fair | No | Cannot locate,directions needed.
Outage | J.E.26.07.29554 | C001864391 | Raheem Ricketts | Manchester | Completed | Load_292660 | Spur Tree - 210 | Jul 24, 2026 10:56am | Jul 24, 2026 10:56am | Jul 24, 2026 12:14pm | Jul 24, 2026 12:15pm | Jul 24, 2026 12:15pm | Jul 24, 2026 12:16pm | Jul 24, 2026 12:16pm | Jul 24, 2026 12:16pm |  |  | Fair | No | Customer power has been restored
Outage | J.E.26.07.27899 | C001864385 | Jermaine Williams | Clarendon | Completed | Load_352081 | Parnassus - 310 | Jul 24, 2026 10:53am | Jul 24, 2026 3:16pm | Jul 24, 2026 4:19pm | Jul 24, 2026 4:19pm | Jul 24, 2026 4:29pm | Jul 24, 2026 4:35pm | Jul 24, 2026 4:36pm | Jul 24, 2026 4:36pm |  |  | Fair | No | Premises not located.
Outage | J.E.26.07.27953 | C001864384 | Jermaine Williams | Clarendon | Completed | Load_1003527 | Parnassus - 310 | Jul 24, 2026 10:53am | Jul 24, 2026 3:16pm | Jul 24, 2026 3:54pm | Jul 24, 2026 3:54pm | Jul 24, 2026 4:13pm | Jul 24, 2026 4:18pm | Jul 24, 2026 4:19pm | Jul 24, 2026 4:19pm |  |  | Fair | No | Premises found ok.
Outage | J.E.26.07.29494 | C001864383 | Jermaine Williams | Clarendon | Completed | Load_244771 | Parnassus - 210 | Jul 24, 2026 10:53am | Jul 24, 2026 3:15pm | Jul 24, 2026 4:52pm | Jul 24, 2026 4:52pm | Jul 24, 2026 6:00pm | Jul 24, 2026 6:00pm | Jul 24, 2026 6:01pm | Jul 24, 2026 6:01pm |  |  | Fair | No | 40’ class 4 xfmr pole at location, urgent attention needed.
Non-Outage | J.E.26.07.26662 | C001864370 | Edward Royal | KSAS | Completed | Load_248816 | Three Miles - 510 | Jul 24, 2026 10:45am | Jul 24, 2026 10:45am | Jul 24, 2026 12:53pm | Jul 24, 2026 12:54pm | Jul 24, 2026 1:02pm | Jul 24, 2026 1:20pm | Jul 24, 2026 1:20pm | Jul 24, 2026 1:20pm | Fire |  | Fair | No | Replaced 15A junction fuse
Non-Outage | J.E.26.07.29409 | C001864369 | Edward Royal | KSAS | Completed | Load_300617 | Hunts Bay - 710 | Jul 24, 2026 10:43am | Jul 24, 2026 10:45am | Jul 24, 2026 11:14am | Jul 24, 2026 11:14am | Jul 24, 2026 11:33am | Jul 24, 2026 12:48pm | Jul 24, 2026 12:48pm | Jul 24, 2026 12:48pm |  |  | Fair | No | Premises found ok voltage reading 220 227 221 112 109 197
Non-Outage | J.E.26.07.29491 | C001864362 | Andrae Clarke | Portland | Completed | Load_267978 | Port Antonio - 310 | Jul 24, 2026 10:37am | Jul 24, 2026 10:37am | Jul 24, 2026 1:47pm | Jul 24, 2026 2:36pm | Jul 24, 2026 2:36pm | Jul 24, 2026 2:30pm | Jul 24, 2026 2:38pm | Jul 24, 2026 2:38pm |  |  | Fair | No | Made phone calls to the customer several times and no response
Outage | J.E.26.07.29524 | C001864361 | Evan Spaulding | St.Mary | Completed | Load_254695 | Annotto Bay - 310 | Jul 24, 2026 10:36am | Jul 24, 2026 10:37am | Jul 24, 2026 2:19pm | Jul 24, 2026 2:19pm | Jul 24, 2026 2:19pm | Jul 24, 2026 2:21pm | Jul 24, 2026 2:21pm | Jul 24, 2026 2:21pm |  |  | Fair | No | Associated call
Outage | J.E.26.07.29508 | C001864352 | Evan Spaulding | St.Mary | Completed | Load_241075 | Annotto Bay - 210 | Jul 24, 2026 10:33am | Jul 24, 2026 10:36am | Jul 24, 2026 12:25pm | Jul 24, 2026 12:25pm | Jul 24, 2026 12:25pm | Jul 24, 2026 12:26pm | Jul 24, 2026 12:26pm | Jul 24, 2026 12:26pm | BrokenWire |  | Fair | No | Associated call
Non-Outage | J.E.26.03.25846 | C001864349 | Raheem Ricketts | Manchester | Completed | Load_1002283 | Spur Tree - 210 | Jul 24, 2026 10:28am | Jul 24, 2026 10:28am | Jul 24, 2026 12:10pm | Jul 24, 2026 12:10pm | Jul 24, 2026 12:11pm | Jul 24, 2026 12:14pm | Jul 24, 2026 12:14pm | Jul 24, 2026 12:14pm |  |  | Fair | No | Customer says report was made from last year an the problem has been solved
Non-Outage | J.E.26.04.05539 | C001864347 | Raheem Ricketts | Manchester | Completed | Load_1002283 | Spur Tree - 210 | Jul 24, 2026 10:28am | Jul 24, 2026 10:28am | Jul 24, 2026 11:51am | Jul 24, 2026 11:51am | Jul 24, 2026 11:51am | Jul 24, 2026 11:53am | Jul 24, 2026 11:54am | Jul 24, 2026 11:54am |  |  | Fair | No | Unable to locate customer cell phone went voicemail after several calls
Non-Outage | J.E.26.04.05591 | C001864346 | Raheem Ricketts | Manchester | Completed | Load_1002283 | Maggotty - 210 | Jul 24, 2026 10:28am | Jul 24, 2026 10:28am | Jul 24, 2026 11:00am | Jul 24, 2026 11:01am | Jul 24, 2026 11:01am | Jul 24, 2026 11:01am | Jul 24, 2026 11:02am | Jul 24, 2026 11:02am |  |  | Fair | No | Customer says she didn’t make any report an power is at her house
Non-Outage | J.E.26.04.05636 | C001864348 | Raheem Ricketts | Manchester | Completed | Load_265389 | Maggotty - 210 | Jul 24, 2026 10:28am | Jul 24, 2026 10:28am | Jul 24, 2026 11:54am | Jul 24, 2026 11:54am | Jul 24, 2026 11:54am | Jul 24, 2026 11:57am | Jul 24, 2026 11:57am | Jul 24, 2026 11:57am |  |  | Fair | No | Cell phone went straight voicemail
Non-Outage | J.E.26.04.06229 | C001864344 | Raheem Ricketts | Manchester | Completed | Load_238422 | Maggotty - 210 | Jul 24, 2026 10:28am | Jul 24, 2026 10:28am | Jul 24, 2026 10:54am | Jul 24, 2026 10:54am | Jul 24, 2026 10:54am | Jul 24, 2026 10:54am | Jul 24, 2026 10:54am | Jul 24, 2026 10:54am |  |  | Fair | No | Customer says problem has been solved
Non-Outage | J.E.26.05.22140 | C001864345 | Raheem Ricketts | Manchester | Completed | Load_292321 | Spur Tree - 210 | Jul 24, 2026 10:28am | Jul 24, 2026 10:28am | Jul 24, 2026 11:48am | Jul 24, 2026 11:48am | Jul 24, 2026 11:48am | Jul 24, 2026 11:50am | Jul 24, 2026 11:50am | Jul 24, 2026 11:50am |  |  | Fair | No | Check and found okay customer says problem has been solved
Outage | J.E.26.07.29519 | C001864334 | Swon Miller | St.James | Completed | Load_301686 | Bogue - 310 | Jul 24, 2026 10:20am | Jul 24, 2026 10:22am | Jul 24, 2026 11:57am | Jul 24, 2026 11:57am | Jul 24, 2026 1:07pm | Jul 21, 2026 1:36pm | Jul 24, 2026 1:45pm | Jul 24, 2026 1:45pm | BrokenPole |  | Fair | No | This call belongs to trelawny found 1,35 ft class six retired concrete pole broken at the base customer requested pole to be removed
Outage | J.E.26.07.29525 | C001864333 | Romeo Brissett | St.James | Completed | Load_240769 | Bogue - 510 | Jul 24, 2026 10:20am | Jul 24, 2026 10:23am | Jul 24, 2026 11:07am | Jul 24, 2026 11:07am | Jul 24, 2026 11:20am | Jul 24, 2026 11:30am | Jul 24, 2026 11:36am | Jul 24, 2026 11:36am | BrokenWire |  | Fair | No | Spliced and retention customer service wire, used 10ft of #6 and 2 clamps. V/R 114-114-229
Outage | J.E.26.07.29517 | C001864332 | Elvis Trowers | KSAN | Completed | Load_269344 | Constant Spring - 210 | Jul 24, 2026 10:18am | Jul 24, 2026 10:19am | Jul 24, 2026 2:21pm | Jul 24, 2026 2:21pm | Jul 24, 2026 2:41pm | Jul 24, 2026 3:22pm | Jul 24, 2026 3:22pm | Jul 24, 2026 3:22pm |  | Y | Fair | Yes | Areas found without electricity supply during patrol and 2 blown junction fuses were found at separate locations, 1/10 amp at pole #0012001 and 1/15 amp at pole #043282.
Outage | J.E.26.07.29468 | C001864324 | Andre Smith | KSAS | Completed | Load_406024 | Three Miles - 410 | Jul 24, 2026 10:15am | Jul 24, 2026 10:16am | Jul 24, 2026 11:31am | Jul 24, 2026 11:31am | Jul 24, 2026 12:23pm | Jul 24, 2026 12:23pm | Jul 24, 2026 12:23pm | Jul 24, 2026 12:23pm |  |  | Fair | No | Replace defective meter supply restored
Outage | J.E.26.07.29488 | C001864306 | Hartley Chin | Clarendon | Completed | Load_253474 | Parnassus - 310 | Jul 24, 2026 10:00am | Jul 24, 2026 10:00am | Jul 24, 2026 10:49am | Jul 24, 2026 1:14pm | Jul 24, 2026 1:48pm | Jul 24, 2026 2:42pm | Jul 24, 2026 2:52pm | Jul 24, 2026 2:52pm |  |  | Fair | No | Found 2 of 3 blown 5 AMP fuse for 50 KVA (bank of 3) transformer no pole # . Line patrolled and found okay , transformer refused..
Non-Outage | J.E.26.07.29484 | C001864297 | Evan Spaulding | null | Completed | null | null | Jul 24, 2026 9:50am | Jul 24, 2026 9:50am | Jul 24, 2026 12:27pm | Jul 24, 2026 12:27pm | Jul 24, 2026 12:27pm | Jul 24, 2026 12:27pm | Jul 24, 2026 12:27pm | Jul 24, 2026 12:27pm | BrokenWire |  | Fair | No | Associated call
Outage | J.E.26.07.29481 | C001864298 | Romeo Brissett | St.James | Completed | Load_254670 | Bogue - 510 | Jul 24, 2026 9:50am | Jul 24, 2026 9:53am | Jul 24, 2026 2:23pm | Jul 24, 2026 2:23pm | Jul 24, 2026 2:23pm | Jul 24, 2026 2:23pm | Jul 24, 2026 2:24pm | Jul 24, 2026 2:24pm |  |  | Fair | No | Check and found ok, related to job#29760
Non-Outage | J.E.26.06.34959 | C001864294 | Hopeton Henry | St.Thomas | Completed | Load_266155 | Good Year - 210 | Jul 24, 2026 9:43am | Jul 24, 2026 9:44am | Jul 24, 2026 10:10am | Jul 24, 2026 10:47am | Jul 24, 2026 1:27pm | Jul 24, 2026 1:27pm | Jul 24, 2026 1:28pm | Jul 24, 2026 1:28pm |  |  | Fair | No | Reconnect phase at pole reading 117 volts
Non-Outage | J.E.26.07.05325 | C001864292 | Hopeton Henry | null | Completed | null | null | Jul 24, 2026 9:43am | Jul 24, 2026 9:44am | Jul 24, 2026 10:10am | Jul 24, 2026 5:10pm | Jul 24, 2026 5:10pm | Jul 24, 2026 5:11pm | Jul 24, 2026 5:11pm | Jul 24, 2026 5:11pm |  |  | Fair | No | Customer not located
Non-Outage | J.E.26.07.06490 | C001864293 | Hopeton Henry | St.Thomas | Completed | Load_256397 | Good Year - 210 | Jul 24, 2026 9:43am | Jul 24, 2026 9:44am | Jul 24, 2026 10:10am | Jul 24, 2026 1:28pm | Jul 24, 2026 1:28pm | Jul 24, 2026 1:29pm | Jul 24, 2026 1:29pm | Jul 24, 2026 1:29pm |  |  | Fair | No | Customer not located
Outage | J.E.26.07.29444 | C001864291 | Moses Elliston | St.Catherine | Completed | Load_293139 | Rhodens Pen - 210 | Jul 24, 2026 9:43am | Jul 24, 2026 11:14am | Jul 24, 2026 11:22am | Jul 24, 2026 11:22am | Jul 24, 2026 11:22am | Jul 24, 2026 11:44am | Jul 24, 2026 11:44am | Jul 24, 2026 11:44am |  |  | Fair | No | Credit added to prepaid account.
Non-Outage | J.E.26.07.27848 | C001864290 | Hopeton Henry | St.Thomas | Completed | Load_243367 | Good Year - 210 | Jul 24, 2026 9:41am | Jul 25, 2026 8:34am | Jul 25, 2026 11:54am | Jul 25, 2026 11:59am | Jul 25, 2026 12:27pm | Jul 25, 2026 12:27pm | Jul 25, 2026 12:28pm | Jul 25, 2026 12:28pm | Fire |  | Fair | No | Check and found ok
Outage | J.E.26.07.29462 | C001864286 | Elvis Trowers | KSAN | Completed | Load_247199 | Constant Spring - 210 | Jul 24, 2026 9:40am | Jul 24, 2026 10:18am | Jul 24, 2026 3:25pm | Jul 24, 2026 3:25pm | Jul 24, 2026 3:57pm | Jul 24, 2026 4:02pm | Jul 24, 2026 4:02pm | Jul 24, 2026 4:02pm |  |  | Fair | Yes | Premises checked and found ok upon arrival, customer was also spoken with however he suggested that situation was resolved from yesterday.
Outage | J.E.26.07.29412 | C001864285 | Richard Nicholas | St.Catherine | Completed | Load_242765 | Twickenham - 310 | Jul 24, 2026 9:35am | Jul 24, 2026 9:36am | Jul 24, 2026 1:09pm | Jul 24, 2026 1:09pm | Jul 24, 2026 1:54pm | Jul 24, 2026 2:34pm | Jul 24, 2026 2:35pm | Jul 24, 2026 2:35pm |  |  | Fair | No | Remade burnt off 3w service phase joint at pothead,2 clamp was used to correct the fault.voltage reading 112,113 and 225v.
Outage | J.E.26.07.29427 | C001864280 | Ricky Hall | St.Catherine | Completed | Load_248443 | New Michelton - 210 | Jul 24, 2026 9:34am | Jul 24, 2026 6:55pm | Jul 24, 2026 9:44pm | Jul 24, 2026 9:44pm | Jul 24, 2026 10:35pm | Jul 24, 2026 10:35pm | Jul 24, 2026 10:35pm | Jul 24, 2026 10:35pm |  |  | Fair | No | Premises closed
Outage | J.E.26.07.29387 | C001864278 | Nickolas Rodriques | St.Catherine | Completed | Load_568118 | Rhodens Pen - 210 | Jul 24, 2026 9:33am | Jul 24, 2026 9:33am | Jul 24, 2026 1:44pm | Jul 24, 2026 1:47pm | Jul 24, 2026 2:03pm | Jul 24, 2026 2:18pm | Jul 24, 2026 2:22pm | Jul 24, 2026 2:22pm |  |  | Fair | No | Customer was contacted and stated that no one is currently home to accommodate the team before 6pm.
Outage | J.E.26.07.29440 | C001864279 | Nickolas Rodriques | St.Catherine | Completed | Load_269173 | Tredegar - 510 | Jul 24, 2026 9:33am | Jul 24, 2026 9:33am | Jul 24, 2026 11:13am | Jul 24, 2026 11:14am | Jul 24, 2026 11:17am | Jul 24, 2026 11:23am | Jul 24, 2026 11:32am | Jul 24, 2026 11:32am |  |  | Fair | No | Power restored. Call relates to the 10 amp junction fuse that was replaced.
Outage | J.E.26.07.29448 | C001864277 | Nickolas Rodriques | St.Catherine | Completed | Load_288492 | Rhodens Pen - 210 | Jul 24, 2026 9:33am | Jul 24, 2026 9:33am | Jul 24, 2026 11:32am | Jul 24, 2026 11:32am | Jul 24, 2026 12:41pm | Jul 24, 2026 1:43pm | Jul 24, 2026 1:44pm | Jul 24, 2026 1:44pm |  |  | Fair | No | Checked and found customer without electricity. All necessary checks were done and it was found that the issue is stemming from the hexing box. (Hex01973).
Outage | J.E.26.07.29450 | C001864276 | Nickolas Rodriques | St.Catherine | Completed | Load_290087 | Rhodens Pen - 210 | Jul 24, 2026 9:33am | Jul 24, 2026 9:33am | Jul 24, 2026 2:22pm | Jul 24, 2026 2:23pm | Jul 24, 2026 2:35pm | Jul 24, 2026 2:56pm | Jul 24, 2026 2:59pm | Jul 24, 2026 2:59pm |  |  | Fair | No | Checked and found customer single phasing (118). All necessary checks were done and it was found that the issue is stemming from the hexing box (hex00996). Refer to field service.
Outage | J.E.26.07.29410 | C001864274 | Richard Nicholas | KSAS | Completed | Load_288343 | Duhaney - 210 | Jul 24, 2026 9:31am | Jul 24, 2026 9:31am | Jul 24, 2026 12:00pm | Jul 24, 2026 12:00pm | Jul 24, 2026 12:20pm | Jul 24, 2026 12:34pm | Jul 24, 2026 12:36pm | Jul 24, 2026 12:36pm | Fire |  | Fair | No | 3w meter found burnt,same was replaced.new meter #3020728 and green seal #04925551.
Outage | J.E.26.07.29434 | C001864272 | Neville Spencer | Clarendon | Completed | Load_239286 | May Pen - 110 | Jul 24, 2026 9:28am | Jul 24, 2026 9:31am | Jul 24, 2026 10:40am | Jul 24, 2026 10:40am | Jul 24, 2026 10:49am | Jul 24, 2026 10:49am | Jul 24, 2026 11:22am | Jul 24, 2026 11:22am | BrokenWire |  | Fair | No | Open 25 kva xmfr at pole # 0101852 splice and retention broken secondary neutral conductor used 30 ft wire, 2 clamps, 1 preform supply restored.
Non-Outage | J.E.26.06.02058 | C001864263 | Royston Montague | St.Catherine | Completed | Load_1000347 | Twickenham - 210 | Jul 24, 2026 9:15am | Jul 24, 2026 9:16am | Jul 24, 2026 9:28am | Jul 24, 2026 2:05pm | Jul 24, 2026 3:10pm | Jul 24, 2026 3:11pm | Jul 24, 2026 3:11pm | Jul 24, 2026 3:11pm |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.06.02791 | C001864264 | Royston Montague | St.Catherine | Completed | Load_252474 | Rhodens Pen - 210 | Jul 24, 2026 9:15am | Jul 24, 2026 9:16am | Jul 24, 2026 9:28am | Jul 24, 2026 9:42am | Jul 24, 2026 10:02am | Jul 24, 2026 10:03am | Jul 24, 2026 10:03am | Jul 24, 2026 10:03am |  |  | Fair | No | Customer confirmed issue resolved, please update thanks.
Non-Outage | J.E.26.06.03770 | C001864262 | Royston Montague | St.Catherine | Completed | Load_239255 | Rhodens Pen - 310 | Jul 24, 2026 9:15am | Jul 24, 2026 9:16am | Jul 24, 2026 9:28am | Jul 24, 2026 11:44am | Jul 24, 2026 12:41pm | Jul 24, 2026 12:48pm | Jul 24, 2026 12:49pm | Jul 24, 2026 12:49pm |  |  | Fair | No | Customer confirmed issue resolved issue resolved.
Non-Outage | J.E.26.06.03898 | C001864261 | Royston Montague | St.Catherine | Completed | Load_305219 | Rhodens Pen - 210 | Jul 24, 2026 9:15am | Jul 24, 2026 9:16am | Jul 24, 2026 9:28am | Jul 24, 2026 12:49pm | Jul 24, 2026 2:04pm | Jul 24, 2026 2:05pm | Jul 24, 2026 2:05pm | Jul 24, 2026 2:05pm |  |  | Fair | No | Found ok.
Non-Outage | J.E.26.06.04222 | C001864260 | Royston Montague | St.Catherine | Completed | Load_252474 | Rhodens Pen - 210 | Jul 24, 2026 9:15am | Jul 24, 2026 9:16am | Jul 24, 2026 9:28am | Jul 24, 2026 10:03am | Jul 24, 2026 10:58am | Jul 24, 2026 11:40am | Jul 24, 2026 11:40am | Jul 24, 2026 11:40am |  |  | Fair | No | Faulty joints at customer take off point. Voltage found 184v 114v 78v voltage after job completion are 230v 114v 114v
Outage | J.E.26.07.29139 | C001864258 | Swon Miller | St.James | Completed | Load_1000496 | Bogue - 310 | Jul 24, 2026 9:15am | Jul 24, 2026 9:29am | Jul 24, 2026 10:02am | Jul 24, 2026 10:02am | Jul 24, 2026 10:57am | Jul 14, 2026 11:16am | Jul 24, 2026 11:19am | Jul 24, 2026 11:19am |  |  | Fair | No | Check and found okay customer states that power supply was restored
Outage | J.E.26.07.29214 | C001864257 | Swon Miller | St.James | Completed | Load_264733 | Bogue - 310 | Jul 24, 2026 9:15am | Jul 24, 2026 9:29am | Jul 24, 2026 11:20am | Jul 24, 2026 11:20am | Jul 24, 2026 11:37am | Jul 21, 2026 11:48am | Jul 24, 2026 11:49am | Jul 24, 2026 11:49am |  |  | Fair | No | Check and found area okay unable to locate customer voltage found 113/112/225 voltage left 113/112/225
Non-Outage | J.E.26.05.06504 | C001864252 | Royston Montague | St.Catherine | Completed | Load_249185 | Rhodens Pen - 410 | Jul 24, 2026 9:14am | Jul 24, 2026 9:14am | Jul 24, 2026 9:28am | Jul 24, 2026 11:41am | Jul 24, 2026 11:43am | Jul 24, 2026 11:43am | Jul 24, 2026 11:43am | Jul 24, 2026 11:43am |  |  | Fair | No | Multiple calls to customer phone go without answer.
Non-Outage | J.E.26.05.15315 | C001864251 | Royston Montague | St.Catherine | Completed | Load_266683 | Twickenham - 210 | Jul 24, 2026 9:14am | Jul 24, 2026 9:14am | Jul 24, 2026 9:28am | Jul 24, 2026 3:14pm | Jul 24, 2026 3:53pm | Jul 24, 2026 3:55pm | Jul 24, 2026 3:56pm | Jul 24, 2026 3:56pm |  |  | Fair | No | Hazardous condition, a lot of illegal connections on pole unable to use ladder to check joints. Voltage at pothead 207v 110 96v , meter socket in good condition, bucket truck required.
Non-Outage | J.E.26.01.27019 | C001864249 | Javid Vernon | Westmoreland | Completed | Load_262213 | Paradise - 210 | Jul 24, 2026 9:13am | Jul 24, 2026 9:13am | Jul 24, 2026 11:24am | Jul 24, 2026 11:26am | Jul 24, 2026 11:26am | Jul 24, 2026 11:26am | Jul 24, 2026 11:28am | Jul 24, 2026 11:28am |  |  | Fair | No | Customer stated that the issue has been resolved
Non-Outage | J.E.26.01.27124 | C001864247 | Javid Vernon | Westmoreland | Completed | Load_251278 | Paradise - 210 | Jul 24, 2026 9:13am | Jul 24, 2026 9:13am | Jul 24, 2026 11:34am | Jul 24, 2026 11:34am | Jul 24, 2026 11:34am | Jul 24, 2026 11:34am | Jul 24, 2026 11:36am | Jul 24, 2026 11:36am |  |  | Fair | No | Customer stated that the issue has been resolved
Non-Outage | J.E.26.01.27497 | C001864248 | Javid Vernon | Westmoreland | Completed | Load_241682 | Paradise - 210 | Jul 24, 2026 9:13am | Jul 24, 2026 9:13am | Jul 24, 2026 12:09pm | Jul 24, 2026 12:09pm | Jul 24, 2026 12:09pm | Jul 24, 2026 12:09pm | Jul 24, 2026 12:09pm | Jul 24, 2026 12:09pm |  |  | Fair | No | Customer stated that the issue has been resolved
Non-Outage | J.E.26.01.27956 | C001864244 | Javid Vernon | Westmoreland | Completed | Load_292015 | Paradise - 210 | Jul 24, 2026 9:13am | Jul 24, 2026 9:13am | Jul 24, 2026 11:29am | Jul 24, 2026 11:29am | Jul 24, 2026 11:29am | Jul 24, 2026 11:29am | Jul 24, 2026 11:30am | Jul 24, 2026 11:30am |  |  | Fair | No | Customer stated that the issue has been resolved
Non-Outage | J.E.26.01.27956 | C001864245 | Javid Vernon | Westmoreland | Completed | Load_292015 | Paradise - 210 | Jul 24, 2026 9:13am | Jul 24, 2026 9:13am | Jul 24, 2026 11:24am | Jul 24, 2026 11:28am | Jul 24, 2026 11:28am | Jul 24, 2026 11:28am | Jul 24, 2026 11:28am | Jul 24, 2026 11:28am |  |  | Fair | No | Customer stated that the issue has been resolved
Non-Outage | J.E.26.01.31516 | C001864246 | Javid Vernon | Westmoreland | Completed | Load_266123 | Paradise - 210 | Jul 24, 2026 9:13am | Jul 24, 2026 9:13am | Jul 24, 2026 12:11pm | Jul 24, 2026 12:11pm | Jul 24, 2026 12:11pm | Jul 24, 2026 12:11pm | Jul 24, 2026 12:12pm | Jul 24, 2026 12:12pm |  |  | Fair | No | Customer stated that issue has been resolved
Non-Outage | J.E.26.01.35047 | C001864243 | Javid Vernon | Westmoreland | Completed | Load_261695 | Paradise - 210 | Jul 24, 2026 9:13am | Jul 24, 2026 9:13am | Jul 24, 2026 11:36am | Jul 24, 2026 11:36am | Jul 24, 2026 11:36am | Jul 24, 2026 11:36am | Jul 24, 2026 11:37am | Jul 24, 2026 11:37am |  |  | Fair | No | Customer stated that the issue has been resolved
Non-Outage | J.E.26.01.38300 | C001864242 | Javid Vernon | Westmoreland | Completed | Load_246523 | Paradise - 210 | Jul 24, 2026 9:13am | Jul 24, 2026 9:13am | Jul 24, 2026 11:40am | Jul 24, 2026 11:40am | Jul 24, 2026 11:59am | Jul 24, 2026 12:08pm | Jul 24, 2026 12:08pm | Jul 24, 2026 12:08pm |  |  | Fair | No | Premises check and found okay customer stated that the issue has been resolved
Non-Outage | J.E.26.01.38308 | C001864241 | Javid Vernon | Westmoreland | Completed | Load_246523 | Paradise - 210 | Jul 24, 2026 9:13am | Jul 24, 2026 9:13am | Jul 24, 2026 12:09pm | Jul 24, 2026 12:09pm | Jul 24, 2026 12:10pm | Jul 24, 2026 12:10pm | Jul 24, 2026 12:11pm | Jul 24, 2026 12:11pm |  |  | Fair | No | Customer stated that the issue has been resolved
Non-Outage | J.E.26.02.06710 | C001864240 | Javid Vernon | Westmoreland | Completed | Load_241658 | Orange Bay - 210 | Jul 24, 2026 9:13am | Jul 24, 2026 9:13am | Jul 24, 2026 9:55am | Jul 24, 2026 9:55am | Jul 24, 2026 10:41am | Jul 24, 2026 11:18am | Jul 24, 2026 11:22am | Jul 24, 2026 11:22am |  |  | Fair | No | Customer service wire check and found okay voltage reading 105/105/110 customer meter is approximately 800ft away from the JPS pole
Outage | J.E.26.07.29425 | C001864250 | Tajay Bernard | Hanover | Completed | Load_252494 | Orange Bay - 310 | Jul 24, 2026 9:13am | Jul 24, 2026 9:14am | Jul 24, 2026 9:27am | Jul 24, 2026 9:27am | Jul 24, 2026 10:31am | Jul 24, 2026 10:57am | Jul 24, 2026 10:57am | Jul 24, 2026 10:57am |  |  | Fair | No | Area check and found okay unable to locate customer on premises, phone number that was given was an international number
Non-Outage | J.E.26.02.12892 | C001864238 | Javid Vernon | Westmoreland | Completed | Load_292673 | Orange Bay - 210 | Jul 24, 2026 9:12am | Jul 24, 2026 9:13am | Jul 24, 2026 9:50am | Jul 24, 2026 9:50am | Jul 24, 2026 9:50am | Jul 24, 2026 9:50am | Jul 24, 2026 9:51am | Jul 24, 2026 9:51am |  |  | Fair | No | Customer stated that the issue has been resolved
Non-Outage | J.E.26.02.21737 | C001864239 | Javid Vernon | Westmoreland | Completed | Load_267276 | Paradise - 210 | Jul 24, 2026 9:12am | Jul 24, 2026 9:13am | Jul 24, 2026 9:50am | Jul 24, 2026 9:51am | Jul 24, 2026 9:51am | Jul 24, 2026 9:52am | Jul 24, 2026 9:53am | Jul 24, 2026 9:53am |  |  | Fair | No | Customer stated that the issue has been resolved
Outage | J.E.26.07.27897 | C001864237 | Javid Vernon | Westmoreland | Completed | Load_256472 | Paradise - 110 | Jul 24, 2026 9:11am | Jul 24, 2026 9:13am | Jul 24, 2026 9:44am | Jul 24, 2026 9:44am | Jul 24, 2026 9:45am | Jul 24, 2026 9:45am | Jul 24, 2026 9:46am | Jul 24, 2026 9:46am |  |  | Fair | No | Customer stated that the power was restored
Non-Outage | J.E.26.07.29443 | C001864227 | Damion Reid | null | Completed | null | null | Jul 24, 2026 9:05am | Jul 24, 2026 9:07am | Jul 24, 2026 1:36pm | Jul 24, 2026 1:36pm | Jul 24, 2026 2:48pm | Jul 24, 2026 2:56pm | Jul 24, 2026 2:57pm | Jul 24, 2026 2:57pm |  |  | Fair | No | Area found ok
Non-Outage | J.E.26.07.08479 | C001864224 | Elvis Trowers | KSAN | Completed | Load_249367 | Washington Blvd - 810 | Jul 24, 2026 9:04am | Jul 24, 2026 9:04am | Jul 24, 2026 11:26am | Jul 24, 2026 11:26am | Jul 24, 2026 11:54am | Jul 24, 2026 11:59am | Jul 24, 2026 12:00pm | Jul 24, 2026 12:00pm |  |  | Fair | Yes | Premises found closed upon arrival and customer could not be contacted by telephone either after several calls.
Non-Outage | J.E.26.07.24324 | C001864222 | Elvis Trowers | KSAN | Completed | Load_579324 | Washington Blvd - 610 | Jul 24, 2026 9:04am | Jul 24, 2026 9:04am | Jul 24, 2026 9:03pm | Jul 24, 2026 9:03pm | Jul 24, 2026 9:25pm | Jul 24, 2026 9:28pm | Jul 24, 2026 9:28pm | Jul 24, 2026 9:28pm |  |  | Fair | Yes | Premises checked and found ok upon arrival, customer was also spoken with however she suggested that the situation was resolved from earlier this afternoon.
Non-Outage | J.E.26.07.26065 | C001864226 | Elvis Trowers | KSAN | Completed | Load_256268 | Washington Blvd - 810 | Jul 24, 2026 9:04am | Jul 24, 2026 9:04am | Jul 24, 2026 10:12am | Jul 24, 2026 10:12am | Jul 24, 2026 10:24am | Jul 24, 2026 10:28am | Jul 24, 2026 10:28am | Jul 24, 2026 10:28am |  |  | Fair | Yes | Customer was contacted and she said it was from days ago and she’s not having an issue with her power supply.
Non-Outage | J.E.26.07.26618 | C001864223 | Roemello Brown | Trelawny | Completed | Load_294240 | Greenwood - 110 | Jul 24, 2026 9:04am | Jul 24, 2026 9:05am | Jul 24, 2026 12:52pm | Jul 24, 2026 1:52pm | Jul 24, 2026 2:32pm | Jul 24, 2026 2:32pm | Jul 24, 2026 2:38pm | Jul 24, 2026 2:38pm |  |  | Fair | No | Premises check premises found working Voltage found 117/117/234 Voltage leave 117/117/234
Non-Outage | J.E.26.07.26686 | C001864221 | Roemello Brown | Trelawny | Completed | Load_249132 | Greenwood - 110 | Jul 24, 2026 9:04am | Jul 24, 2026 9:05am | Jul 24, 2026 2:44pm | Jul 24, 2026 2:44pm | Jul 24, 2026 3:39pm | Jul 24, 2026 3:39pm | Jul 24, 2026 3:56pm | Jul 24, 2026 3:56pm |  |  | Fair | No | Premises found working okay Voltage found 114/113/227Voltage leave 114/113/227
Non-Outage | J.E.26.07.26712 | C001864220 | Andre Williams | Trelawny | Completed | Load_249132 | Greenwood - 110 | Jul 24, 2026 9:04am | Jul 25, 2026 7:55am | Jul 25, 2026 8:04am | Jul 25, 2026 9:07am | Jul 25, 2026 9:10am | Jul 25, 2026 9:13am | Jul 25, 2026 9:13am | Jul 25, 2026 9:13am |  |  | Fair | No | Customer says high voltage issue was resolved
Non-Outage | J.E.26.07.26720 | C001864219 | Andre Williams | Trelawny | Completed | Load_302540 | Duncans - 110 | Jul 24, 2026 9:04am | Jul 25, 2026 7:58am | Jul 25, 2026 8:04am | Jul 25, 2026 8:08am | Jul 25, 2026 8:23am | Jul 25, 2026 8:33am | Jul 25, 2026 8:34am | Jul 25, 2026 8:34am |  |  | Fair | No | Measure voltage at pothead on two #2 two naut triplex conductors voltage 110+110=220/ 192 volts, ustomer in hexing box reffer to field service for further checks
Non-Outage | J.E.26.07.29339 | C001864225 | Elvis Trowers | KSAN | Completed | Load_264071 | Washington Blvd - 810 | Jul 24, 2026 9:04am | Jul 24, 2026 9:04am | Jul 24, 2026 11:25am | Jul 24, 2026 5:03pm | Jul 24, 2026 5:59pm | Jul 24, 2026 6:06pm | Jul 24, 2026 6:06pm | Jul 24, 2026 6:06pm |  |  | Fair | Yes | Happened to be internal when checked, electrician was also correcting the problem.
Non-Outage | J.E.26.07.25726 | C001864212 | Milton Charlton | KSAS | Completed | Load_266410 | Up Park Camp - 410 | Jul 24, 2026 9:03am | Jul 24, 2026 9:03am | Jul 24, 2026 9:18am | Jul 24, 2026 9:18am | Jul 24, 2026 10:21am | Jul 24, 2026 10:20am | Jul 24, 2026 10:24am | Jul 24, 2026 10:24am |  |  | Fair | No | Refused and reclosed 2 amps transformer switch at pole# 0211406 using one 2 amps fuse.
Non-Outage | J.E.26.07.26839 | C001864218 | Andre Williams | Trelawny | Completed | Load_255841 | Duncans - 110 | Jul 24, 2026 9:03am | Jul 25, 2026 7:55am | Jul 25, 2026 8:03am | Jul 25, 2026 9:14am | Jul 25, 2026 9:20am | Jul 25, 2026 9:22am | Jul 25, 2026 9:33am | Jul 25, 2026 9:33am |  |  | Fair | No | Premises ok electrician switch phases in panel motors now spinning in correct direction
Non-Outage | J.E.26.07.27638 | C001864217 | Roemello Brown | Trelawny | Completed | Load_247929 | Greenwood - 110 | Jul 24, 2026 9:03am | Jul 24, 2026 9:05am | Jul 24, 2026 9:42am | Jul 24, 2026 11:17am | Jul 24, 2026 12:35pm | Jul 24, 2026 12:38pm | Jul 24, 2026 12:48pm | Jul 24, 2026 12:48pm |  |  | Fair | No | Premises found working okay Voltage found 110/105/215Voltage leave 110/105/215
Non-Outage | J.E.26.07.27724 | C001864214 | Roemello Brown | Trelawny | Completed | Load_250518 | Duncans - 110 | Jul 24, 2026 9:03am | Jul 24, 2026 9:05am | Jul 24, 2026 9:38am | Jul 24, 2026 10:01am | Jul 24, 2026 11:06am | Jul 24, 2026 11:06am | Jul 24, 2026 11:15am | Jul 24, 2026 11:15am |  |  | Fair | No | Premises found working okay Voltage found 116/117/233Voltage leave 116/117/233
Outage | J.E.26.07.25908 | C001864197 | Rusean Allen | KSAS | Completed | Load_264363 | Hunts Bay - 410 | Jul 24, 2026 8:56am | Jul 24, 2026 8:56am | Jul 24, 2026 10:25am | Jul 24, 2026 10:25am | Jul 24, 2026 11:19am | Jul 24, 2026 11:19am | Jul 24, 2026 11:19am | Jul 24, 2026 11:19am |  |  | Fair | No | Premises okay
Outage | J.E.26.07.27772 | C001864198 | Richard Nicholas | KSAS | Completed | Load_294344 | Duhaney - 210 | Jul 24, 2026 8:56am | Jul 24, 2026 9:27am | Jul 24, 2026 10:20am | Jul 24, 2026 10:20am | Jul 24, 2026 11:31am | Jul 24, 2026 11:59am | Jul 24, 2026 12:00pm | Jul 24, 2026 12:00pm |  |  | Fair | No | Replaced blown 25kva transformer 3amp fuse on pole #0105818.
Non-Outage | J.E.26.07.29386 | C001864194 | Hartley Chin | Clarendon | Completed | Load_301251 | Monymusk - 410 | Jul 24, 2026 8:55am | Jul 24, 2026 8:55am | Jul 24, 2026 10:49am | Jul 24, 2026 10:50am | Jul 24, 2026 11:53am | Jul 24, 2026 12:24pm | Jul 24, 2026 12:27pm | Jul 24, 2026 12:27pm |  |  | Fair | No | Found 1 of 3 blown 65 amp junction (no pole #) line patrolled and found okay , junction refused…
Non-Outage | J.E.26.07.20399 | C001864189 | Rusean Allen | KSAS | Completed | Load_242523 | Greenwich - 310 | Jul 24, 2026 8:52am | Jul 24, 2026 8:52am | Jul 24, 2026 10:18am | Jul 24, 2026 10:20am | Jul 24, 2026 10:23am | Jul 24, 2026 10:24am | Jul 24, 2026 10:24am | Jul 24, 2026 10:24am |  |  | Fair | No | Found okay
Non-Outage | J.E.26.07.26643 | C001864192 | Swon Miller | St.James | Completed | Load_250164 | Rose Hall - 210 | Jul 24, 2026 8:52am | Jul 25, 2026 7:26am | Jul 25, 2026 8:22am | Jul 25, 2026 8:22am | Jul 25, 2026 8:56am | Jul 29, 2026 9:04am | Jul 25, 2026 9:06am | Jul 25, 2026 9:06am |  |  | Fair | No | Check and found okay voltage found 115/115/114 voltage left 115/115/114
Non-Outage | J.E.26.07.27167 | C001864190 | Tajay Bernard | St.James | Completed | Load_238186 | Bogue - 510 | Jul 24, 2026 8:52am | Jul 25, 2026 7:44am | Jul 25, 2026 9:32am | Jul 25, 2026 10:11am | Jul 25, 2026 10:17am | Jul 25, 2026 10:45am | Jul 25, 2026 10:46am | Jul 25, 2026 10:46am |  |  | Fair | No | Customer has internal problems
Non-Outage | J.E.26.06.35360 | C001864187 | Rusean Allen | KSAS | Completed | Load_258696 | Hunts Bay - 310 | Jul 24, 2026 8:51am | Jul 24, 2026 8:52am | Jul 24, 2026 1:09pm | Jul 24, 2026 1:09pm | Jul 24, 2026 1:16pm | Jul 24, 2026 1:16pm | Jul 24, 2026 1:17pm | Jul 24, 2026 1:17pm |  |  | Fair | No | Unable to reach premises road under construction.
Non-Outage | J.E.26.07.27905 | C001864182 | Romeo Brissett | St.James | Completed | Load_242778 | Bogue - 510 | Jul 24, 2026 8:50am | Jul 24, 2026 9:34am | Jul 24, 2026 10:26am | Jul 24, 2026 10:26am | Jul 24, 2026 10:27am | Jul 24, 2026 10:30am | Jul 24, 2026 10:46am | Jul 24, 2026 10:46am | BrokenPole |  | Fair | No | Found (1)40ft TA pole with 3 phase Primary and open secondary, urgently need to change. Pole is located around the corner just before you reach hopewell square, below shakes garage. Please send to maintenance.
Non-Outage | J.E.26.07.27925 | C001864181 | Romeo Brissett | St.James | Completed | Load_243584 | Bogue - 510 | Jul 24, 2026 8:50am | Jul 24, 2026 9:34am | Jul 24, 2026 10:47am | Jul 24, 2026 10:47am | Jul 24, 2026 10:52am | Jul 24, 2026 11:00am | Jul 24, 2026 11:07am | Jul 24, 2026 11:07am | BrokenPole |  | Fair | No | Customer reported about a streetlight and was advised to report to is councilor about it.
Non-Outage | J.E.26.07.28133 | C001864180 | Junior Scarlett | St.James | Completed | Load_569159 | Queens Drive - 710 | Jul 24, 2026 8:50am | Jul 24, 2026 8:54am | Jul 24, 2026 10:59am | Jul 24, 2026 2:20pm | Jul 24, 2026 2:44pm | Jul 24, 2026 2:59pm | Jul 24, 2026 2:59pm | Jul 24, 2026 2:59pm |  |  | Fair | No | Check and found okVoltage found 115v 115v 230v
Non-Outage | J.E.26.07.28144 | C001864179 | Junior Scarlett | St.James | Completed | Load_263410 | Queens Drive - 710 | Jul 24, 2026 8:49am | Jul 24, 2026 8:54am | Jul 24, 2026 10:59am | Jul 24, 2026 1:12pm | Jul 24, 2026 1:47pm | Jul 24, 2026 2:14pm | Jul 24, 2026 2:14pm | Jul 24, 2026 2:14pm |  |  | Fair | No | Check ad found okVoltage found 115v 115v 230v
Non-Outage | J.E.26.07.25108 | C001864176 | Tyrese Williams | St.Ann | Completed | Load_304980 | Cardiff Hall - 310 | Jul 24, 2026 8:48am | Jul 24, 2026 8:49am | Jul 24, 2026 8:58am | Jul 24, 2026 9:41am | Jul 24, 2026 10:52am | Jul 24, 2026 11:00am | Jul 24, 2026 11:00am | Jul 24, 2026 11:00am |  |  | Fair | No | Premises not found not getting customer on phone
Non-Outage | J.E.26.07.25501 | C001864174 | Tyrese Williams | St.Ann | Completed | Load_253779 | Cardiff Hall - 310 | Jul 24, 2026 8:48am | Jul 24, 2026 8:49am | Jul 24, 2026 8:58am | Jul 24, 2026 11:01am | Jul 24, 2026 11:01am | Jul 24, 2026 12:29pm | Jul 24, 2026 12:30pm | Jul 24, 2026 12:30pm |  |  | Fair | No | Open a 100kva transformer to change Transformer tapping voltage left 116/113/229
Non-Outage | J.E.26.07.24843 | C001864170 | Milton Charlton | null | Completed | null | null | Jul 24, 2026 8:45am | Jul 24, 2026 8:45am | Jul 24, 2026 10:36am | Jul 24, 2026 10:36am | Jul 24, 2026 11:07am | Jul 24, 2026 11:05am | Jul 24, 2026 11:21am | Jul 24, 2026 11:21am |  |  | Fair | No | Switch top at the gate of Musgrave Mews and pole #000902 64-66 Lady Musgrave Road sparking at the top of the junction switch at nights. If you stand outside the gate it is the switch on the right. Need bucket truck to repair switch top.
Non-Outage | J.E.26.07.24755 | C001864164 | Fredrick Hamilton | KSAN | Completed | Load_264383 | Constant Spring - 210 | Jul 24, 2026 8:44am | Jul 24, 2026 8:45am | Jul 24, 2026 8:49am | Jul 24, 2026 8:53am | Jul 24, 2026 8:53am | Jul 24, 2026 8:56am | Jul 24, 2026 8:56am | Jul 24, 2026 8:56am |  |  | Fair | No | Please have emergency inspect transformer multiple customers been complaining of high voltage during a certain time of day
Non-Outage | J.E.26.07.27372 | C001864165 | Fredrick Hamilton | KSAN | Completed | Load_302960 | Constant Spring - 210 | Jul 24, 2026 8:44am | Jul 24, 2026 8:45am | Jul 24, 2026 8:49am | Jul 24, 2026 10:13am | Jul 24, 2026 10:41am | Jul 24, 2026 10:48am | Jul 24, 2026 10:48am | Jul 24, 2026 10:48am |  |  | Fair | No | 246v/123v/123v obtained High voltage detected affecting multiple customers experiencing lowPlease have emergency check transformer Getting reports of customers appliances being damaged
Non-Outage | J.E.26.07.27459 | C001864167 | Fredrick Hamilton | KSAN | Completed | Load_267672 | Constant Spring - 210 | Jul 24, 2026 8:44am | Jul 24, 2026 8:45am | Jul 24, 2026 8:49am | Jul 24, 2026 9:13am | Jul 24, 2026 9:54am | Jul 24, 2026 10:09am | Jul 24, 2026 10:09am | Jul 24, 2026 10:09am |  |  | Fair | No | 226v/119v/105v obtained Please have emergency inspect transformer multiple customers experiencing low voltage in area Pothead and pole was previously cleaned up and reclamped
Non-Outage | J.E.26.07.28279 | C001864168 | Fredrick Hamilton | KSAN | Completed | Load_238924 | Constant Spring - 210 | Jul 24, 2026 8:44am | Jul 24, 2026 8:45am | Jul 24, 2026 8:49am | Jul 24, 2026 10:09am | Jul 24, 2026 10:09am | Jul 24, 2026 10:12am | Jul 24, 2026 10:12am | Jul 24, 2026 10:12am |  |  | Fair | No | Customer contacted and stated that power was restored fully previously Premises is ok
Non-Outage | J.E.26.07.28623 | C001864166 | Fredrick Hamilton | KSAN | Completed | Load_240269 | Constant Spring - 210 | Jul 24, 2026 8:44am | Jul 24, 2026 8:45am | Jul 24, 2026 8:49am | Jul 24, 2026 9:00am | Jul 24, 2026 9:01am | Jul 24, 2026 9:02am | Jul 24, 2026 9:02am | Jul 24, 2026 9:02am |  |  | Fair | No | Customer contacted and stated that power was restored fully Premises is ok
Outage | J.E.26.07.29403 | C001864163 | Raymond Carr | St.Mary | Completed | Load_253313 | Oracabessa - 210 | Jul 24, 2026 8:42am | Jul 24, 2026 8:42am | Jul 24, 2026 10:59am | Jul 24, 2026 10:59am | Jul 24, 2026 11:30am | Jul 24, 2026 11:26am | Jul 24, 2026 11:31am | Jul 24, 2026 11:31am | BrokenWire |  | Fair | No | Customer was advised to have damaged, pothead/ stanchion fixed.
Non-Outage | J.E.26.07.26505 | C001864161 | Andre Smith | KSAN | Completed | Load_249051 | Washington Blvd - 710 | Jul 24, 2026 8:39am | Jul 24, 2026 8:42am | Jul 24, 2026 2:27pm | Jul 24, 2026 2:27pm | Jul 24, 2026 2:34pm | Jul 24, 2026 2:35pm | Jul 24, 2026 2:57pm | Jul 24, 2026 2:57pm | BrokenWire |  | Fair | No | Premises found okay customer complaint about telephone cable wires
Non-Outage | J.E.26.07.16473 | C001864159 | Hopeton Henry | St.Thomas | Completed | Load_247908 | Good Year - 210 | Jul 24, 2026 8:38am | Jul 24, 2026 8:38am | Jul 24, 2026 10:10am | Jul 24, 2026 10:25am | Jul 24, 2026 10:25am | Jul 24, 2026 10:28am | Jul 24, 2026 10:28am | Jul 24, 2026 10:28am |  |  | Fair | No | Issue resolved
Non-Outage | J.E.26.07.17378 | C001864160 | Hopeton Henry | St.Thomas | Completed | Load_247908 | Good Year - 210 | Jul 24, 2026 8:38am | Jul 24, 2026 8:38am | Jul 24, 2026 10:10am | Jul 24, 2026 10:15am | Jul 24, 2026 10:22am | Jul 24, 2026 10:22am | Jul 24, 2026 10:25am | Jul 24, 2026 10:25am |  |  | Fair | No | Reconnect service at pole , 112-110-222 volts at meter
Non-Outage | J.E.26.07.17396 | C001864158 | Hopeton Henry | St.Thomas | Completed | Load_248673 | Good Year - 210 | Jul 24, 2026 8:38am | Jul 24, 2026 8:38am | Jul 24, 2026 10:10am | Jul 24, 2026 10:33am | Jul 24, 2026 10:37am | Jul 24, 2026 10:46am | Jul 24, 2026 10:47am | Jul 24, 2026 10:47am |  |  | Fair | No | Found ok , customer said the issue was resolved
Outage | J.E.26.07.29400 | C001864156 | Andre Smith | KSAN | Completed | Load_270237 | Washington Blvd - 710 | Jul 24, 2026 8:34am | Jul 24, 2026 8:34am | Jul 24, 2026 1:10pm | Jul 24, 2026 1:10pm | Jul 24, 2026 1:47pm | Jul 24, 2026 1:48pm | Jul 24, 2026 1:48pm | Jul 24, 2026 1:48pm |  |  | Fair | No | Replace blown transformer fuse 10A supply restored
Non-Outage | J.E.26.03.38924 | C001864153 | Marlon Authors | Manchester | Completed | Load_258771 | Spur Tree - 210 | Jul 24, 2026 8:32am | Jul 24, 2026 8:32am | Jul 24, 2026 11:19am | Jul 24, 2026 11:19am | Jul 24, 2026 11:19am | Jul 24, 2026 11:46am | Jul 24, 2026 11:46am | Jul 24, 2026 11:46am | LowHangingWires |  | Fair | No | Supply checked and found service wire hanging low across roadway. Retention same, unable to check supply premises is located
Non-Outage | J.E.26.06.34120 | C001864154 | Marlon Authors | Manchester | Completed | Load_258771 | Spur Tree - 210 | Jul 24, 2026 8:32am | Jul 24, 2026 8:32am | Jul 24, 2026 12:01pm | Jul 24, 2026 12:01pm | Jul 24, 2026 12:01pm | Jul 24, 2026 12:05pm | Jul 24, 2026 12:05pm | Jul 24, 2026 12:05pm |  |  | Fair | No | This customer is being supplied by the 167 transformer circuit that is tapped out and the voltage is low, circuit needs to be split
Outage | J.E.26.07.29398 | C001864155 | Christopher Edwards | KSAN | Completed | Load_239719 | Constant Spring - 410 | Jul 24, 2026 8:32am | Jul 24, 2026 8:32am | Jul 24, 2026 9:46am | Jul 24, 2026 9:46am | Jul 24, 2026 10:21am | Jul 24, 2026 10:40am | Jul 24, 2026 10:41am | Jul 24, 2026 10:41am |  |  | Fair | No | Customer meter is burnt Customer is experiencing single phasing as a result Meter needs to be replaced
Non-Outage | J.E.26.03.29412 | C001864150 | Marlon Authors | Manchester | Completed | Load_242182 | Spur Tree - 210 | Jul 24, 2026 8:31am | Jul 24, 2026 8:32am | Jul 24, 2026 1:39pm | Jul 24, 2026 1:39pm | Jul 24, 2026 1:39pm | Jul 24, 2026 1:40pm | Jul 24, 2026 1:40pm | Jul 24, 2026 1:40pm |  |  | Fair | No | Customer said supply is okay
Non-Outage | J.E.26.03.33856 | C001864151 | Raheem Ricketts | Manchester | Completed | Load_295725 | Spur Tree - 210 | Jul 24, 2026 8:31am | Jul 24, 2026 10:26am | Jul 24, 2026 11:07am | Jul 24, 2026 11:07am | Jul 24, 2026 11:18am | Jul 24, 2026 11:46am | Jul 24, 2026 11:46am | Jul 24, 2026 11:46am |  |  | Fair | No | Check and found one joint of customer wire burn at pole remake joint at pole using one clamp
Non-Outage | J.E.26.04.05623 | C001864152 | Raheem Ricketts | Manchester | Completed | Load_252793 | Maggotty - 210 | Jul 24, 2026 8:31am | Jul 24, 2026 10:26am | Jul 24, 2026 10:57am | Jul 24, 2026 10:57am | Jul 24, 2026 10:57am | Jul 24, 2026 10:57am | Jul 24, 2026 10:57am | Jul 24, 2026 10:57am |  |  | Fair | No | Unable to locate customer cell phone went unanswered after several calls
Non-Outage | J.E.26.05.19048 | C001864149 | Marlon Authors | Manchester | Completed | Load_556490 | Spur Tree - 210 | Jul 24, 2026 8:31am | Jul 24, 2026 8:32am | Jul 24, 2026 2:37pm | Jul 24, 2026 2:37pm | Jul 24, 2026 2:37pm | Jul 24, 2026 3:06pm | Jul 24, 2026 3:06pm | Jul 24, 2026 3:06pm |  |  | Fair | No | Customer said that the issue was resolved
Non-Outage | J.E.26.05.19650 | C001864148 | Marlon Authors | Manchester | Completed | Load_258771 | Spur Tree - 210 | Jul 24, 2026 8:31am | Jul 24, 2026 8:32am | Jul 24, 2026 12:12pm | Jul 24, 2026 12:12pm | Jul 24, 2026 12:13pm | Jul 24, 2026 12:16pm | Jul 24, 2026 12:16pm | Jul 24, 2026 12:16pm |  |  | Fair | No | Customer is connected to the 167 transformer circuit that is tapped out and still experiencing low voltage, circuit needs to split
Non-Outage | J.E.26.05.19652 | C001864147 | Marlon Authors | Manchester | Completed | Load_258771 | Spur Tree - 210 | Jul 24, 2026 8:31am | Jul 24, 2026 8:32am | Jul 24, 2026 9:28am | Jul 24, 2026 9:28am | Jul 24, 2026 9:41am | Jul 24, 2026 11:15am | Jul 24, 2026 11:16am | Jul 24, 2026 11:16am |  |  | Fair | No | Supply checked and found low voltage rdg 104v,106v and cross phased 210 volts. Further checks revealed that 167 transformer is at tap 5. This circuit needs to be split it supplies six plazas, tax office, police station and the primary school. Please refer same to the maintenance department for further assistance
Non-Outage | J.E.26.07.26507 | C001864146 | Locksley Allen | St.Mary | Completed | Load_239259 | Annotto Bay - 310 | Jul 24, 2026 8:29am | Jul 24, 2026 8:30am | Jul 24, 2026 10:39am | Jul 24, 2026 11:17am | Jul 24, 2026 11:17am | Jul 24, 2026 11:40am | Jul 24, 2026 11:41am | Jul 24, 2026 11:41am |  |  | Fair | No | The switch at the dead end is openVoltage at meter socket phase to neutral 128v &150v respectively and the 190v is 150v. Check transformer
Non-Outage | J.E.26.07.26639 | C001864145 | Locksley Allen | St.Mary | Completed | Load_239259 | Annotto Bay - 310 | Jul 24, 2026 8:29am | Jul 24, 2026 8:30am | Jul 24, 2026 11:41am | Jul 24, 2026 11:41am | Jul 24, 2026 11:41am | Jul 24, 2026 11:46am | Jul 24, 2026 11:48am | Jul 24, 2026 11:48am |  |  | Fair | No | Switch at dead end is open. Voltage at meter socket phase to neutral 128v and 150v respectively and the 190 is 150v. Check transformer Two report for the same location
Non-Outage | J.E.26.04.04723 | C001864136 | Nicholas Dillon | St.Elizabeth | Completed | Load_292120 | Maggotty - 210 | Jul 24, 2026 8:27am | Jul 24, 2026 8:27am | Jul 24, 2026 9:37am | Jul 24, 2026 9:37am | Jul 24, 2026 9:37am | Jul 24, 2026 10:03am | Jul 24, 2026 10:05am | Jul 24, 2026 10:05am |  |  | Fair | Yes | Corrosion found at pole clean and use 2 one bolt clamp before I left voltage is 115 115 phase to phase 230
Non-Outage | J.E.26.05.29229 | C001864133 | Nicholas Dillon | Manchester | Completed | Load_256912 | Spur Tree - 210 | Jul 24, 2026 8:26am | Jul 24, 2026 8:27am | Jul 24, 2026 10:11am | Jul 24, 2026 10:11am | Jul 24, 2026 10:11am | Jul 24, 2026 10:11am | Jul 24, 2026 10:13am | Jul 24, 2026 10:13am |  |  | Fair | Yes | Check and found neutral wire burn off at pole clean joint and use 1 one bolt clamp before I left voltage is 117 116 phase to phase 234
Non-Outage | J.E.26.05.33331 | C001864134 | Nicholas Dillon | Manchester | Completed | Load_255892 | Spur Tree - 210 | Jul 24, 2026 8:26am | Jul 24, 2026 8:27am | Jul 24, 2026 10:17am | Jul 24, 2026 10:17am | Jul 24, 2026 10:18am | Jul 24, 2026 10:18am | Jul 24, 2026 10:20am | Jul 24, 2026 10:20am | Fire |  | Fair | No | Check voltage before at meter 117 117 phase to phase 236 . Premises found working ok
Non-Outage | J.E.26.07.08782 | C001864126 | Odeanie Davis | KSAS | Completed | Load_269273 | Rockfort - 410 | Jul 24, 2026 8:24am | Jul 24, 2026 8:24am | Jul 24, 2026 10:36am | Jul 24, 2026 10:45am | Jul 24, 2026 10:46am | Jul 24, 2026 11:34am | Jul 24, 2026 11:34am | Jul 24, 2026 11:34am |  |  | Fair | No | 123/103 at arrival, Corrosion at pothead and secondary corrected, 3 one bolt clamps, 113v/113v & 226v after correction
Non-Outage | J.E.26.07.09617 | C001864125 | Odeanie Davis | KSAS | Completed | Load_266339 | Rockfort - 410 | Jul 24, 2026 8:24am | Jul 24, 2026 8:24am | Jul 24, 2026 10:36am | Jul 24, 2026 12:45pm | Jul 24, 2026 12:51pm | Jul 24, 2026 1:29pm | Jul 24, 2026 1:18pm | Jul 24, 2026 1:18pm |  |  | Fair | No | 112v/105v & 218v at location from secondary line, customer stated that voltage drop in the night when everyone is home and they lose power at that time, pole rotten at root and need to be replaced, pole # 0030921.
Non-Outage | J.E.26.07.10449 | C001864124 | Odeanie Davis | KSAS | Completed | Load_241156 | Rockfort - 410 | Jul 24, 2026 8:24am | Jul 24, 2026 8:24am | Jul 24, 2026 10:36am | Jul 24, 2026 10:36am | Jul 24, 2026 10:36am | Jul 24, 2026 10:45am | Jul 24, 2026 10:45am | Jul 24, 2026 10:45am |  |  | Fair | No | Customer stated that issue was resolved by their electrician
Non-Outage | J.E.26.07.10971 | C001864123 | Odeanie Davis | KSAS | Completed | Load_265849 | Rockfort - 210 | Jul 24, 2026 8:24am | Jul 24, 2026 8:24am | Jul 24, 2026 10:36am | Jul 24, 2026 12:34pm | Jul 24, 2026 12:34pm | Jul 24, 2026 12:41pm | Jul 24, 2026 12:41pm | Jul 24, 2026 12:41pm |  |  | Fair | No | 98v/108v and 207v at location from secondary line, emergency team needed
Non-Outage | J.E.26.07.25880 | C001864129 | Rusean Allen | null | Completed | null | null | Jul 24, 2026 8:24am | Jul 24, 2026 8:25am | Jul 24, 2026 12:27pm | Jul 24, 2026 12:59pm | Jul 24, 2026 12:59pm | Jul 24, 2026 12:59pm | Jul 24, 2026 12:59pm | Jul 24, 2026 12:59pm |  |  | Fair | No | Not found
Non-Outage | J.E.26.07.26773 | C001864128 | Andre Smith | null | Completed | null | null | Jul 24, 2026 8:24am | Jul 24, 2026 8:25am | Jul 24, 2026 12:24pm | Jul 24, 2026 12:24pm | Jul 24, 2026 12:51pm | Jul 24, 2026 12:52pm | Jul 24, 2026 12:52pm | Jul 24, 2026 12:52pm |  |  | Fair | No | Premises found close
Non-Outage | J.E.26.07.27292 | C001864127 | Andre Smith | null | Completed | null | null | Jul 24, 2026 8:24am | Jul 24, 2026 8:25am | Jul 24, 2026 9:28am | Jul 24, 2026 9:28am | Jul 24, 2026 10:20am | Jul 24, 2026 10:28am | Jul 24, 2026 10:28am | Jul 24, 2026 10:28am |  |  | Fair | No | Premises found okay supply restored already
Outage | J.E.26.07.28957 | C001864121 | Andre Smith | KSAN | Completed | Load_242589 | Washington Blvd - 710 | Jul 24, 2026 8:23am | Jul 24, 2026 8:23am | Jul 24, 2026 12:24pm | Jul 24, 2026 2:12pm | Jul 24, 2026 2:12pm | Jul 24, 2026 2:27pm | Jul 24, 2026 2:27pm | Jul 24, 2026 2:27pm |  |  | Fair | No | Premises found okay supply restored already
Outage | J.E.26.07.29032 | C001864122 | Andre Smith | KSAN | Completed | Load_293695 | Washington Blvd - 710 | Jul 24, 2026 8:23am | Jul 24, 2026 8:23am | Jul 24, 2026 12:24pm | Jul 24, 2026 1:48pm | Jul 24, 2026 2:12pm | Jul 24, 2026 2:12pm | Jul 24, 2026 2:12pm | Jul 24, 2026 2:12pm |  |  | Fair | No | Premises found okay supply restored already
Outage | J.E.26.07.28774 | C001864119 | Andre Smith | KSAS | Completed | Load_256957 | Three Miles - 510 | Jul 24, 2026 8:22am | Jul 24, 2026 8:22am | Jul 24, 2026 10:31am | Jul 24, 2026 10:31am | Jul 24, 2026 11:25am | Jul 24, 2026 11:30am | Jul 24, 2026 11:30am | Jul 24, 2026 11:30am |  |  | Fair | No | Premises found okay supply restored already
Outage | J.E.26.07.29329 | C001864120 | Edward Royal | KSAS | Completed | Load_261135 | Up Park Camp - 510 | Jul 24, 2026 8:22am | Jul 24, 2026 8:22am | Jul 24, 2026 12:53pm | Jul 24, 2026 1:47pm | Jul 24, 2026 1:47pm | Jul 24, 2026 1:54pm | Jul 24, 2026 1:59pm | Jul 24, 2026 1:59pm |  |  | Fair | No | Premises found ok customer breaker trip. Voltage reading 119 120 238
Outage | J.E.26.07.28761 | C001864118 | Edward Royal | KSAS | Completed | Load_241830 | Rockfort - 210 | Jul 24, 2026 8:21am | Jul 24, 2026 8:21am | Jul 24, 2026 8:49am | Jul 24, 2026 8:49am | Jul 24, 2026 8:49am | Jul 24, 2026 8:52am | Jul 24, 2026 8:53am | Jul 24, 2026 8:53am |  |  | Fair | No | Contact customer by phone customer said the power was restored
Outage | J.E.26.07.27994 | C001864116 | Raheem Ricketts | Manchester | Completed | Load_249828 | Spur Tree - 210 | Jul 24, 2026 8:19am | Jul 24, 2026 8:19am | Jul 24, 2026 10:51am | Jul 24, 2026 10:51am | Jul 24, 2026 10:51am | Jul 24, 2026 10:51am | Jul 24, 2026 10:51am | Jul 24, 2026 10:51am |  |  | Fair | No | Related call
Outage | J.E.26.07.28529 | C001864115 | Raheem Ricketts | Manchester | Completed | Load_242701 | Spur Tree - 210 | Jul 24, 2026 8:19am | Jul 24, 2026 8:19am | Jul 24, 2026 10:29am | Jul 24, 2026 10:30am | Jul 24, 2026 10:30am | Jul 24, 2026 10:31am | Jul 24, 2026 10:31am | Jul 24, 2026 10:31am |  |  | Fair | No | Call related
Outage | J.E.26.07.29366 | C001864117 | Nickolas Rodriques | St.Catherine | Completed | Load_263396 | Tredegar - 510 | Jul 24, 2026 8:19am | Jul 24, 2026 8:20am | Jul 24, 2026 8:28am | Jul 24, 2026 8:46am | Jul 24, 2026 10:20am | Jul 24, 2026 11:05am | Jul 24, 2026 11:12am | Jul 24, 2026 11:12am |  |  | Fair | No | Checked and found a 10 amp junction fuse blown caused by tree contacting with primary line. Repaired by removing the tree limb and replaced the fuse after completing patrol.
Outage | J.E.26.07.29373 | C001864113 | Raheem Ricketts | Manchester | Completed | Load_241798 | Spur Tree - 210 | Jul 24, 2026 8:19am | Jul 24, 2026 8:19am | Jul 24, 2026 8:36am | Jul 24, 2026 12:06pm | Jul 24, 2026 12:06pm | Jul 24, 2026 12:07pm | Jul 24, 2026 12:07pm | Jul 24, 2026 12:07pm |  |  | Fair | No | Unable to locate customer cell number went voicemail after several calls
Outage | J.E.26.07.29384 | C001864114 | Raheem Ricketts | Manchester | Completed | Load_258909 | Spur Tree - 210 | Jul 24, 2026 8:19am | Jul 24, 2026 8:19am | Jul 24, 2026 8:50am | Jul 24, 2026 8:50am | Jul 24, 2026 9:23am | Jul 24, 2026 10:29am | Jul 24, 2026 10:29am | Jul 24, 2026 10:29am |  |  | Fair | No | Check an found one 30,amp junction fuse blown replace junction fuse using one 30,amp fuse
Non-Outage | J.E.26.07.26621 | C001864108 | Odeanie Davis | KSAS | Completed | Load_269212 | Rockfort - 410 | Jul 24, 2026 8:16am | Jul 24, 2026 8:17am | Jul 24, 2026 8:36am | Jul 24, 2026 9:03am | Jul 24, 2026 9:06am | Jul 24, 2026 9:12am | Jul 24, 2026 9:07am | Jul 24, 2026 9:07am |  |  | Fair | No | Customer stated that issue was resolved by their electrician
Non-Outage | J.E.26.07.27105 | C001864111 | Odeanie Davis | KSAS | Completed | Load_244754 | Rockfort - 410 | Jul 24, 2026 8:16am | Jul 24, 2026 8:17am | Jul 24, 2026 10:36am | Jul 24, 2026 4:34pm | Jul 24, 2026 4:34pm | Jul 24, 2026 4:19pm | Jul 24, 2026 4:34pm | Jul 24, 2026 4:34pm |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.07.27157 | C001864109 | Odeanie Davis | KSAS | Completed | Load_255918 | Rockfort - 410 | Jul 24, 2026 8:16am | Jul 24, 2026 8:17am | Jul 24, 2026 10:36am | Jul 24, 2026 11:41am | Jul 24, 2026 11:41am | Jul 24, 2026 12:06pm | Jul 24, 2026 12:09pm | Jul 24, 2026 12:09pm |  |  | Fair | No | 109v/0V at location, open circuit at secondary corrected, 2 penn union & 2 one bolt clamps, 109v/111v & 220v after correction
Non-Outage | J.E.26.07.27173 | C001864110 | Odeanie Davis | KSAS | Completed | Load_257693 | Rockfort - 410 | Jul 24, 2026 8:16am | Jul 24, 2026 8:17am | Jul 24, 2026 8:36am | Jul 24, 2026 9:07am | Jul 24, 2026 9:08am | Jul 24, 2026 9:57am | Jul 24, 2026 9:57am | Jul 24, 2026 9:57am |  |  | Fair | No | 129v/99v at arrival, open neutral at secondary corrected, 3 one bolt clamps, 113v/116v & 230v, 193v on 190 phase,
Non-Outage | J.E.26.07.27700 | C001864112 | Odeanie Davis | KSAS | Completed | Load_247308 | Rockfort - 410 | Jul 24, 2026 8:16am | Jul 24, 2026 8:17am | Jul 24, 2026 8:37am | Jul 24, 2026 9:59am | Jul 24, 2026 10:01am | Jul 24, 2026 10:19am | Jul 24, 2026 10:19am | Jul 24, 2026 10:19am |  |  | Fair | No | 77v/0V at location, secondary line seen broken coming from transformer, location in on law st in between gold st & foster Ln
Outage | J.E.26.07.28989 | C001864106 | Richard Nicholas | St.Catherine | Completed | Load_1000822 | Rhodens Pen - 210 | Jul 24, 2026 8:14am | Jul 24, 2026 8:18am | Jul 24, 2026 8:10pm | Jul 24, 2026 8:10pm | Jul 24, 2026 8:47pm | Jul 24, 2026 9:09pm | Jul 24, 2026 9:09pm | Jul 24, 2026 9:09pm |  |  | Fair | No | Area found ok
Outage | J.E.26.07.29010 | C001864104 | Richard Nicholas | St.Catherine | Completed | Load_266508 | Twickenham - 210 | Jul 24, 2026 8:14am | Jul 24, 2026 8:18am | Jul 24, 2026 8:34am | Jul 24, 2026 8:34am | Jul 24, 2026 9:50am | Jul 24, 2026 10:15am | Jul 24, 2026 10:15am | Jul 24, 2026 10:15am |  |  | Fair | No | Found ok
Outage | J.E.26.07.29380 | C001864105 | Elvis Trowers | KSAN | Completed | Load_240040 | Constant Spring - 410 | Jul 24, 2026 8:14am | Jul 24, 2026 8:14am | Jul 24, 2026 10:24am | Jul 24, 2026 10:29am | Jul 24, 2026 10:49am | Jul 24, 2026 11:22am | Jul 24, 2026 11:22am | Jul 24, 2026 11:22am |  |  | Fair | Yes | Customer was found without electricity supply when checked, and and was reconnected with the assistant of escalation service department.
Non-Outage | J.E.26.07.20206 | C001864102 | Raymond Carr | St.Mary | Completed | Load_266413 | Oracabessa - 210 | Jul 24, 2026 8:13am | Jul 24, 2026 8:13am | Jul 24, 2026 8:25am | Jul 24, 2026 8:25am | Jul 24, 2026 10:07am | Jul 24, 2026 10:15am | Jul 24, 2026 10:35am | Jul 24, 2026 10:35am |  |  | Fair | No | Voltage readings 123/124/247. Customer was advised to an electrician check wiring.
Non-Outage | J.E.26.07.21300 | C001864099 | Raymond Carr | St.Mary | Completed | Load_254936 | Oracabessa - 210 | Jul 24, 2026 8:13am | Jul 24, 2026 8:13am | Jul 24, 2026 10:37am | Jul 24, 2026 10:37am | Jul 24, 2026 10:49am | Jul 24, 2026 10:46am | Jul 24, 2026 10:58am | Jul 24, 2026 10:58am |  |  | Fair | No | Voltage readings at meter socket 120/120/240. Customer was advised to have an electrician check wiring.
Non-Outage | J.E.26.07.26245 | C001864100 | Raymond Carr | St.Mary | Completed | Load_254009 | Oracabessa - 210 | Jul 24, 2026 8:13am | Jul 24, 2026 8:13am | Jul 24, 2026 12:50pm | Jul 24, 2026 12:50pm | Jul 24, 2026 1:35pm | Jul 24, 2026 1:31pm | Jul 24, 2026 1:36pm | Jul 24, 2026 1:36pm |  |  | Fair | No | Several calls to contact number went straight to voicemail.
Non-Outage | J.E.26.07.27487 | C001864101 | Raymond Carr | St.Mary | Completed | Load_254009 | Oracabessa - 210 | Jul 24, 2026 8:13am | Jul 24, 2026 8:13am | Jul 24, 2026 11:31am | Jul 24, 2026 11:31am | Jul 24, 2026 11:42am | Jul 24, 2026 12:45pm | Jul 24, 2026 12:49pm | Jul 24, 2026 12:49pm |  |  | Fair | No | Several calls to contact number went unanswered.
Outage | J.E.26.07.29382 | C001864103 | Hartley Chin | Clarendon | Completed | Load_245076 | Parnassus - 310 | Jul 24, 2026 8:13am | Jul 24, 2026 8:13am | Jul 24, 2026 8:34am | Jul 24, 2026 8:34am | Jul 24, 2026 9:38am | Jul 24, 2026 10:47am | Jul 24, 2026 10:49am | Jul 24, 2026 10:49am |  |  | Fair | No | Found 1 of 3 open 50 amp Tripsaver @ pole # 0128885 line patrolled and found okay , close trip-saver …
Outage | J.E.26.07.29291 | C001864098 | Neville Spencer | Clarendon | Completed | Load_253796 | May Pen - 110 | Jul 24, 2026 8:10am | Jul 24, 2026 8:12am | Jul 24, 2026 8:28am | Jul 24, 2026 8:28am | Jul 24, 2026 10:39am | Jul 24, 2026 10:39am | Jul 24, 2026 10:40am | Jul 24, 2026 10:40am |  |  | Fair | No | Found supply at location.
Outage | J.E.26.07.29160 | C001864097 | Wan Carlos Scarlett | Portmore | Completed | Load_252395 | Naggo Head - 610 | Jul 24, 2026 8:07am | Jul 24, 2026 8:11am | Jul 24, 2026 10:00am | Jul 24, 2026 11:53am | Jul 24, 2026 12:02pm | Jul 24, 2026 12:20pm | Jul 24, 2026 12:20pm | Jul 24, 2026 12:20pm |  |  | Fair | No | Call related customer confirm that power supply has been restored
Outage | J.E.26.07.29165 | C001864096 | Wan Carlos Scarlett | Portmore | Completed | Load_260602 | Naggo Head - 510 | Jul 24, 2026 8:07am | Jul 24, 2026 8:11am | Jul 24, 2026 10:38am | Jul 24, 2026 12:20pm | Jul 24, 2026 12:56pm | Jul 24, 2026 1:23pm | Jul 24, 2026 1:25pm | Jul 24, 2026 1:25pm |  |  | Fair | No | Found 25KVA transformer drop lead wire to open secondary line phase and neutral corroded use 3 one bolt clamps at pole readings 117-116-234
Non-Outage | J.E.26.07.27298 | C001864092 | Marlon Brown | null | Completed | null | null | Jul 24, 2026 8:06am | Jul 24, 2026 8:11am | Jul 24, 2026 8:17am | Jul 24, 2026 8:17am | Jul 24, 2026 8:17am | Jul 24, 2026 8:18am | Jul 24, 2026 8:18am | Jul 24, 2026 8:18am |  |  | Fair | No | Manchester call, however customer says her electricity has been restored.
Outage | J.E.26.07.27858 | C001864093 | Floyd Taylor | Trelawny | Completed | Load_240966 | Greenwood - 110 | Jul 24, 2026 8:06am | Jul 24, 2026 9:11am | Jul 24, 2026 9:51am | Jul 24, 2026 9:51am | Jul 24, 2026 10:42am | Jul 24, 2026 12:04pm | Jul 24, 2026 12:05pm | Jul 24, 2026 12:05pm |  |  | Fair | No | Remove illegal connection from isolated 25kva transformer and remake transformer neutral drop lead voltage readings left 115,115,229
Outage | J.E.26.07.29162 | C001864095 | Wan Carlos Scarlett | Portmore | Completed | Load_265721 | Naggo Head - 610 | Jul 24, 2026 8:06am | Jul 24, 2026 8:11am | Jul 24, 2026 10:27am | Jul 24, 2026 10:27am | Jul 24, 2026 11:06am | Jul 24, 2026 11:49am | Jul 24, 2026 11:53am | Jul 24, 2026 11:53am |  |  | Fair | No | Refuse 20 Amp junction pole#598020 nothing was found on primary line cause by lightning
Outage | J.E.26.07.29274 | C001864094 | Wan Carlos Scarlett | Portmore | Completed | Load_268319 | Naggo Head - 610 | Jul 24, 2026 8:06am | Jul 24, 2026 8:10am | Jul 24, 2026 8:13am | Jul 24, 2026 8:13am | Jul 24, 2026 9:13am | Jul 24, 2026 10:25am | Jul 24, 2026 10:26am | Jul 24, 2026 10:26am |  |  | Fair | No | Refuse 15amp junction no pole # was found suspect lightning take out power supply
Non-Outage | J.E.26.07.09731 | C001864088 | Error Coore | Manchester | Completed | Load_238510 | Kendal - 310 | Jul 24, 2026 8:04am | Jul 24, 2026 8:05am | Jul 24, 2026 1:44pm | Jul 24, 2026 1:44pm | Jul 24, 2026 2:16pm | Jul 24, 2026 2:24pm | Jul 24, 2026 2:24pm | Jul 24, 2026 2:24pm |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.12936 | C001864084 | Error Coore | Manchester | Completed | Load_255369 | Kendal - 310 | Jul 24, 2026 8:03am | Jul 24, 2026 8:05am | Jul 24, 2026 1:00pm | Jul 24, 2026 1:00pm | Jul 24, 2026 1:29pm | Jul 24, 2026 1:42pm | Jul 24, 2026 1:44pm | Jul 24, 2026 1:44pm |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.13089 | C001864083 | Error Coore | Manchester | Completed | Load_255372 | Kendal - 310 | Jul 24, 2026 8:03am | Jul 24, 2026 8:05am | Jul 24, 2026 8:17am | Jul 24, 2026 9:27am | Jul 24, 2026 9:27am | Jul 24, 2026 9:28am | Jul 24, 2026 9:29am | Jul 24, 2026 9:29am |  |  | Fair | No | Premises found ok call customer and customer said that she didn’t make any report
Non-Outage | J.E.26.07.14852 | C001864082 | Error Coore | Manchester | Completed | Load_260369 | Kendal - 310 | Jul 24, 2026 8:03am | Jul 24, 2026 8:05am | Jul 24, 2026 2:25pm | Jul 24, 2026 2:25pm | Jul 24, 2026 2:52pm | Jul 24, 2026 3:02pm | Jul 24, 2026 3:03pm | Jul 24, 2026 3:03pm |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.16025 | C001864080 | Error Coore | Manchester | Completed | Load_1002521 | Kendal - 310 | Jul 24, 2026 8:03am | Jul 24, 2026 8:05am | Jul 24, 2026 8:20am | Jul 24, 2026 8:20am | Jul 24, 2026 8:36am | Jul 24, 2026 9:25am | Jul 24, 2026 9:26am | Jul 24, 2026 9:26am |  |  | Fair | No | Premise found ok customer have internal problem voltage reading 114/110/224 volts
Non-Outage | J.E.26.07.19968 | C001864079 | Error Coore | Manchester | Completed | Load_255590 | Kendal - 310 | Jul 24, 2026 8:03am | Jul 24, 2026 8:05am | Jul 24, 2026 10:24am | Jul 24, 2026 10:24am | Jul 24, 2026 10:24am | Jul 24, 2026 11:57am | Jul 24, 2026 12:00pm | Jul 24, 2026 12:00pm |  |  | Fair | No | Found customer with corroded phase and neutral at pothead remade corroded phase and neutral using 2 service sleeve and 1 one bolt clamp voltage reading 110/111/221 volts
Non-Outage | J.E.26.07.22280 | C001864078 | Error Coore | Manchester | Completed | Load_243875 | Kendal - 310 | Jul 24, 2026 8:03am | Jul 24, 2026 8:05am | Jul 24, 2026 12:02pm | Jul 24, 2026 12:02pm | Jul 24, 2026 12:50pm | Jul 24, 2026 12:59pm | Jul 24, 2026 1:00pm | Jul 24, 2026 1:00pm |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.27202 | C001864076 | Kenroy Dale | Manchester | Completed | Load_244764 | Kendal - 310 | Jul 24, 2026 8:03am | Jul 24, 2026 3:19pm | Jul 24, 2026 3:28pm | Jul 24, 2026 3:28pm | Jul 24, 2026 4:13pm | Jul 24, 2026 5:52pm | Jul 24, 2026 5:52pm | Jul 24, 2026 5:52pm |  |  | Fair | No | Feedback from customer premises (meter number 2449823) cause service wire to burn, neutral jumper was also burnt. Opened 25 kva transformer to remove defective service wire and remake burned off neutral. Connection was remade and transformer re-closed, area now with supply. Voltage reading 118/118/236
Non-Outage | J.E.26.07.27322 | C001864077 | Error Coore | Manchester | Completed | Load_293050 | Kendal - 310 | Jul 24, 2026 8:03am | Jul 24, 2026 8:05am | Jul 24, 2026 3:03pm | Jul 24, 2026 3:03pm | Jul 24, 2026 3:24pm | Jul 24, 2026 3:41pm | Jul 24, 2026 3:42pm | Jul 24, 2026 3:42pm |  |  | Fair | No | Premises not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.06.37999 | C001864074 | Oshane Warren | Westmoreland | Completed | Load_242476 | Paradise - 210 | Jul 24, 2026 7:59am | Jul 24, 2026 8:00am | Jul 24, 2026 8:30am | Jul 24, 2026 8:33am | Jul 24, 2026 9:21am | Jul 24, 2026 9:28am | Jul 24, 2026 9:28am | Jul 24, 2026 9:28am |  |  | Fair | No | Check and find ok
Non-Outage | J.E.26.07.24181 | C001864072 | Raymond Lewis | St.Ann | Completed | Load_239944 | Roaring River - 410 | Jul 24, 2026 7:58am | Jul 24, 2026 7:58am | Jul 24, 2026 9:39am | Jul 24, 2026 9:39am | Jul 24, 2026 10:12am | Jul 24, 2026 10:13pm | Jul 24, 2026 10:14am | Jul 24, 2026 10:14am |  |  | Fair | No | Customer have internal fault
Non-Outage | J.E.26.07.27825 | C001864073 | Raymond Lewis | St.Ann | Completed | Load_246075 | Roaring River - 410 | Jul 24, 2026 7:58am | Jul 24, 2026 7:58am | Jul 24, 2026 10:14am | Jul 24, 2026 10:14am | Jul 24, 2026 11:07am | Jul 24, 2026 11:07pm | Jul 24, 2026 11:08am | Jul 24, 2026 11:08am |  |  | Fair | No | Phone not answering
Outage | J.E.26.07.26746 | C001864071 | Oshane Warren | Westmoreland | Completed | Load_292071 | Paradise - 310 | Jul 24, 2026 7:58am | Jul 24, 2026 7:58am | Jul 24, 2026 2:12pm | Jul 24, 2026 2:12pm | Jul 24, 2026 2:12pm | Jul 24, 2026 2:24pm | Jul 24, 2026 2:25pm | Jul 24, 2026 2:25pm |  |  | Fair | No | Reconnect back service wire at pathead and secondary line used 40ft of number 6 twisted wire voltage 116 116 232
Outage | J.E.26.07.29349 | C001864070 | Oshane Warren | Westmoreland | Completed | Load_292666 | Paradise - 110 | Jul 24, 2026 7:57am | Jul 24, 2026 7:58am | Jul 24, 2026 11:05am | Jul 24, 2026 11:05am | Jul 24, 2026 11:05am | Jul 24, 2026 11:08am | Jul 24, 2026 11:08am | Jul 24, 2026 11:08am |  |  | Fair | No | Check and find ok
Non-Outage | J.E.26.07.24594 | C001864066 | Omar King | St.Ann | Completed | Load_245278 | Upper White River - 210 | Jul 24, 2026 7:53am | Jul 24, 2026 7:53am | Jul 24, 2026 11:43am | Jul 24, 2026 11:43am | Jul 24, 2026 12:50pm | Jul 24, 2026 12:50pm | Jul 24, 2026 12:51pm | Jul 24, 2026 12:51pm |  |  | Fair | No | Found customer meter socket defective I advise customer to a electrician to resolve matter
Non-Outage | J.E.26.07.27024 | C001864067 | Omar King | St.Ann | Completed | Load_268103 | Upper White River - 210 | Jul 24, 2026 7:53am | Jul 24, 2026 7:53am | Jul 24, 2026 9:46am | Jul 24, 2026 9:46am | Jul 24, 2026 11:42am | Jul 24, 2026 11:43am | Jul 24, 2026 11:43am | Jul 24, 2026 11:43am |  |  | Fair | No | Unable to find customer call several times no answer directions not sufficient
Non-Outage | J.E.26.07.27210 | C001864065 | Raymond Carr | St.Ann | Completed | Load_269054 | Upper White River - 110 | Jul 24, 2026 7:51am | Jul 24, 2026 8:47am | Jul 24, 2026 1:37pm | Jul 24, 2026 1:37pm | Jul 24, 2026 2:52pm | Jul 24, 2026 2:50pm | Jul 24, 2026 2:53pm | Jul 24, 2026 2:53pm |  |  | Fair | No | Customer reported that supply is okay now.
Outage | J.E.26.07.28407 | C001864064 | Omar King | St.Ann | Completed | Load_253537 | Upper White River - 210 | Jul 24, 2026 7:49am | Jul 24, 2026 7:50am | Jul 24, 2026 8:51am | Jul 24, 2026 8:51am | Jul 24, 2026 8:52am | Jul 24, 2026 8:54am | Jul 24, 2026 8:54am | Jul 24, 2026 8:54am |  |  | Fair | No | Customer argued that she did not make a report i must not call back her phone
Outage | J.E.26.07.27749 | C001864063 | Rayon Foster | Hanover | Completed | Load_258609 | Orange Bay - 210 | Jul 24, 2026 7:46am | Jul 24, 2026 7:46am | Jul 24, 2026 8:25am | Jul 24, 2026 8:25am | Jul 24, 2026 10:54am | Jul 24, 2026 11:27am | Jul 24, 2026 11:28am | Jul 24, 2026 11:28am |  |  | Fair | No | Damage #6 service wire coming rom jps pole remove and replace 100 feet of #6 service wire using three linnets and three clamps voltage check in meter socket after repair
Outage | J.E.26.07.29216 | C001864061 | Raymond Lewis | St.Ann | Completed | Load_237943 | Roaring River - 210 | Jul 24, 2026 7:45am | Jul 24, 2026 7:49am | Jul 24, 2026 7:55am | Jul 24, 2026 7:55am | Jul 24, 2026 9:32am | Jul 24, 2026 9:38am | Jul 24, 2026 9:38am | Jul 24, 2026 9:38am |  |  | Fair | No | Hexing box turn on by field service team
Non-Outage | J.E.26.07.00457 | C001864060 | Dwain Samuels | Westmoreland | Completed | Load_248383 | Orange Bay - 310 | Jul 24, 2026 7:44am | Jul 24, 2026 7:44am | Jul 24, 2026 8:20am | Jul 24, 2026 11:43am | Jul 24, 2026 11:55am | Jul 24, 2026 12:02pm | Jul 24, 2026 12:03pm | Jul 24, 2026 12:03pm |  |  | Fair | No | Area having low voltage. Transformer serving too far
Non-Outage | J.E.26.07.07532 | C001864059 | Dwain Samuels | Westmoreland | Completed | Load_261442 | Orange Bay - 310 | Jul 24, 2026 7:44am | Jul 24, 2026 7:44am | Jul 24, 2026 8:20am | Jul 24, 2026 12:03pm | Jul 24, 2026 12:03pm | Jul 24, 2026 12:03pm | Jul 24, 2026 12:04pm | Jul 24, 2026 12:04pm |  |  | Fair | No | Found working okay. Voltage check 112-113-225
Non-Outage | J.E.26.07.10609 | C001864058 | Dwain Samuels | Westmoreland | Completed | Load_247383 | Orange Bay - 310 | Jul 24, 2026 7:44am | Jul 24, 2026 7:44am | Jul 24, 2026 8:20am | Jul 24, 2026 11:18am | Jul 24, 2026 11:18am | Jul 24, 2026 11:29am | Jul 24, 2026 11:30am | Jul 24, 2026 11:30am |  |  | Fair | No | Found working okay. Voltage check 111-110-221
Non-Outage | J.E.26.07.12735 | C001864057 | Dwain Samuels | Westmoreland | Completed | Load_238910 | Orange Bay - 310 | Jul 24, 2026 7:44am | Jul 24, 2026 7:44am | Jul 24, 2026 8:20am | Jul 24, 2026 1:04pm | Jul 24, 2026 1:10pm | Jul 24, 2026 1:22pm | Jul 24, 2026 1:24pm | Jul 24, 2026 1:24pm |  |  | Fair | No | Corrosion found at 3 wire pole. Voltage check 115-100-215. Corrosion clear use 3 one bolt clamp. Voltage check 115-116-231
Non-Outage | J.E.26.07.22618 | C001864056 | Dwain Samuels | Westmoreland | Completed | Load_247446 | Orange Bay - 310 | Jul 24, 2026 7:44am | Jul 24, 2026 7:44am | Jul 24, 2026 8:20am | Jul 24, 2026 12:09pm | Jul 24, 2026 12:17pm | Jul 24, 2026 12:57pm | Jul 24, 2026 1:00pm | Jul 24, 2026 1:00pm |  |  | Fair | No | Throw ups and irregularities on the causing low voltage for paying customers. Voltage check 99-113-212
Non-Outage | J.E.26.07.23350 | C001864054 | Dwain Samuels | Westmoreland | Completed | Load_292064 | Paradise - 110 | Jul 24, 2026 7:44am | Jul 24, 2026 7:44am | Jul 24, 2026 8:20am | Jul 24, 2026 10:36am | Jul 24, 2026 10:36am | Jul 24, 2026 10:36am | Jul 24, 2026 10:37am | Jul 24, 2026 10:37am |  |  | Fair | No | Called customer said service was restored
Non-Outage | J.E.26.07.26647 | C001864055 | Dwain Samuels | Westmoreland | Completed | Load_263345 | Orange Bay - 310 | Jul 24, 2026 7:44am | Jul 24, 2026 7:44am | Jul 24, 2026 8:20am | Jul 24, 2026 11:38am | Jul 24, 2026 11:38am | Jul 24, 2026 11:38am | Jul 24, 2026 11:39am | Jul 24, 2026 11:39am |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.07.27587 | C001864052 | Dwain Samuels | Westmoreland | Completed | Load_301743 | Paradise - 110 | Jul 24, 2026 7:43am | Jul 24, 2026 7:44am | Jul 24, 2026 8:20am | Jul 24, 2026 10:41am | Jul 24, 2026 11:02am | Jul 24, 2026 11:14am | Jul 24, 2026 11:15am | Jul 24, 2026 11:15am |  |  | Fair | No | Unable to locate need proper directions and contact information
Non-Outage | J.E.26.07.29336 | C001864050 | Oshane Warren | Westmoreland | Completed | Load_244663 | Paradise - 110 | Jul 24, 2026 7:43am | Jul 24, 2026 7:43am | Jul 24, 2026 9:43am | Jul 24, 2026 9:43am | Jul 24, 2026 10:11am | Jul 24, 2026 10:25am | Jul 24, 2026 10:27am | Jul 24, 2026 10:27am |  |  | Fair | No | Check and find ok voltage 230 231 240 408 416 392
Outage | J.E.26.07.29347 | C001864051 | Christopher Edwards | KSAN | Completed | Load_264247 | Constant Spring - 410 | Jul 24, 2026 7:43am | Jul 24, 2026 7:43am | Jul 24, 2026 10:42am | Jul 24, 2026 10:42am | Jul 24, 2026 12:10pm | Jul 24, 2026 1:27pm | Jul 24, 2026 1:27pm | Jul 24, 2026 1:27pm |  |  | Fair | No | Defective 25 transformer Transformer is burnt on the secondary bushing Causing customers to experiencing single phasing Transformer pole is located off the main road And no vehicle can access pole have to walk over a foot bridge smoke and oil is seen coming from x3 secondary bushing Overload is the suspected cause as there’s many illegal connections
Outage | J.E.26.07.29332 | C001864049 | Christopher Edwards | KSAN | Completed | Load_269344 | Constant Spring - 210 | Jul 24, 2026 7:42am | Jul 24, 2026 7:43am | Jul 24, 2026 8:26am | Jul 24, 2026 8:56am | Jul 24, 2026 8:56am | Jul 24, 2026 9:45am | Jul 24, 2026 9:46am | Jul 24, 2026 9:46am |  |  | Fair | No | Unable to reach customer by phone Observed supply is in the area
Outage | J.E.26.07.27048 | C001864045 | Evan Spaulding | St.Mary | Completed | Load_238891 | Annotto Bay - 310 | Jul 24, 2026 7:41am | Jul 24, 2026 7:41am | Jul 24, 2026 12:30pm | Jul 24, 2026 12:30pm | Jul 24, 2026 12:50pm | Jul 24, 2026 2:18pm | Jul 24, 2026 2:19pm | Jul 24, 2026 2:19pm |  |  | Fair | No | Replace defective drop out switch and bracket, replace 1-50 amps junction fuse at pole number 0099070
Outage | J.E.26.07.27947 | C001864043 | Evan Spaulding | St.Mary | Completed | Load_249363 | Annotto Bay - 210 | Jul 24, 2026 7:39am | Jul 24, 2026 7:39am | Jul 24, 2026 10:28am | Jul 24, 2026 10:28am | Jul 24, 2026 10:28am | Jul 24, 2026 10:28am | Jul 24, 2026 10:28am | Jul 24, 2026 10:28am |  |  | Fair | No | Associated call
Outage | J.E.26.07.29279 | C001864042 | Evan Spaulding | St.Mary | Completed | Load_241075 | Annotto Bay - 210 | Jul 24, 2026 7:38am | Jul 24, 2026 7:38am | Jul 24, 2026 10:28am | Jul 24, 2026 10:28am | Jul 24, 2026 12:11pm | Jul 24, 2026 12:12pm | Jul 24, 2026 12:16pm | Jul 24, 2026 12:16pm |  |  | Fair | No | Splice and retention two spans MV conductor and two spans neutral conductor using 120ft #2 AAAC conductor,2-#2 splicing sleeves,4- 1 bolts clamps and replace 1-15 amps junction fuse at pole number 0005287.
Outage | J.E.26.07.29293 | C001864041 | Evan Spaulding | St.Mary | Completed | Load_249363 | Annotto Bay - 210 | Jul 24, 2026 7:37am | Jul 24, 2026 7:37am | Jul 24, 2026 8:08am | Jul 24, 2026 8:08am | Jul 24, 2026 9:33am | Jul 24, 2026 10:23am | Jul 24, 2026 10:27am | Jul 24, 2026 10:27am |  |  | Fair | No | Remove creepers from Transformer pole,replace two junction fuses at pole numbe 0181809 (15 amps), pole number 0005292 (10amps ), 1-5amps Transformer fuse at pole number 0005291.
Outage | J.E.26.07.28381 | C001864038 | Swon Miller | St.James | Completed | Load_260177 | Queens Drive - 710 | Jul 24, 2026 7:33am | Jul 24, 2026 7:34am | Jul 24, 2026 7:42am | Jul 24, 2026 7:42am | Jul 24, 2026 7:50am | Jul 21, 2026 8:07am | Jul 24, 2026 8:12am | Jul 24, 2026 8:12am |  |  | Fair | No | Check and found okay customer states that power supply is in the area
Outage | J.E.26.07.29292 | C001864037 | Swon Miller | St.James | Completed | Load_245113 | Queens Drive - 710 | Jul 24, 2026 7:33am | Jul 24, 2026 7:34am | Jul 24, 2026 8:56am | Jul 24, 2026 8:56am | Jul 24, 2026 9:24am | Jul 15, 2026 9:55am | Jul 24, 2026 10:02am | Jul 24, 2026 10:02am |  |  | Fair | No | Check and found okay customer states that power supply was restored voltage found 116/115/231 voltage left 116/115/231
Outage | J.E.26.07.29135 | C001864036 | Derrick Grubb | St.Thomas | Completed | Load_249841 | Good Year - 210 | Jul 24, 2026 7:31am | Jul 24, 2026 7:34am | Jul 24, 2026 12:10pm | Jul 24, 2026 12:10pm | Jul 24, 2026 12:11pm | Jul 24, 2026 12:12pm | Jul 24, 2026 12:12pm | Jul 24, 2026 12:12pm |  |  | Fair | No | Check and found okay.
Outage | J.E.26.07.29316 | C001864034 | Derrick Grubb | St.Thomas | Completed | Load_261867 | Good Year - 110 | Jul 24, 2026 7:31am | Jul 24, 2026 7:34am | Jul 24, 2026 8:03am | Jul 24, 2026 8:03am | Jul 24, 2026 9:40am | Jul 24, 2026 9:48am | Jul 24, 2026 9:48am | Jul 24, 2026 9:48am |  |  | Fair | No | Premises not found. However, light is in the area.
Outage | J.E.26.07.29343 | C001864035 | Derrick Grubb | St.Thomas | Completed | Load_249841 | Good Year - 210 | Jul 24, 2026 7:31am | Jul 24, 2026 7:34am | Jul 24, 2026 9:48am | Jul 24, 2026 9:49am | Jul 24, 2026 10:54am | Jul 24, 2026 12:09pm | Jul 24, 2026 12:10pm | Jul 24, 2026 12:10pm |  |  | Fair | No | Troubleshoot and clear corrosion at jumper on pole using four one bolt clamps. Voltage readings when leaving 118v, 119v, 238v.
Non-Outage | J.E.26.06.01916 | C001864031 | Richard Samuda | Manchester | Completed | Load_269851 | Spur Tree - 310 | Jul 24, 2026 7:24am | Jul 24, 2026 3:23pm | Jul 24, 2026 4:53pm | Jul 24, 2026 4:53pm | Jul 24, 2026 6:43pm | Jul 24, 2026 6:58pm | Jul 24, 2026 6:58pm | Jul 24, 2026 6:58pm |  |  | Fair | No | Found ok voltage 116/116/232
Non-Outage | J.E.26.06.08610 | C001864029 | Ryan Richards | Manchester | Completed | Load_260169 | Spur Tree - 310 | Jul 24, 2026 7:24am | Jul 24, 2026 7:34am | Jul 24, 2026 7:50am | Jul 24, 2026 7:50am | Jul 24, 2026 9:02am | Jul 24, 2026 9:10am | Jul 24, 2026 9:10am | Jul 24, 2026 9:10am | Fire |  | Fair | No | Blown 5 amp fuse found for 50kva transformer in closed bank line check nothing found blown fuse was replaced
Non-Outage | J.E.26.07.17495 | C001864030 | Ryan Richards | Manchester | Completed | Load_250223 | Spur Tree - 310 | Jul 24, 2026 7:24am | Jul 24, 2026 7:34am | Jul 24, 2026 9:11am | Jul 24, 2026 9:11am | Jul 24, 2026 10:26am | Jul 24, 2026 11:28am | Jul 24, 2026 11:30am | Jul 24, 2026 11:30am |  |  | Fair | No | Corroded phase found at pole for 3 wire remade using 2 one bolt clamps voltage 114/116/230 volts
Non-Outage | J.E.26.07.27579 | C001864028 | Andrae Clarke | Portland | Completed | Load_243555 | Port Antonio - 410 | Jul 24, 2026 7:24am | Jul 24, 2026 7:28am | Jul 24, 2026 10:52am | Jul 24, 2026 1:41pm | Jul 24, 2026 1:41pm | Jul 24, 2026 11:29am | Jul 24, 2026 1:43pm | Jul 24, 2026 1:43pm |  |  | Fair | No | Check voltage 117/110/227Premises found okay
Non-Outage | J.E.26.07.27611 | C001864027 | Andrae Clarke | Portland | Completed | Load_268045 | Port Antonio - 410 | Jul 24, 2026 7:24am | Jul 24, 2026 7:28am | Jul 24, 2026 8:07am | Jul 24, 2026 8:07am | Jul 24, 2026 10:25am | Jul 24, 2026 9:33am | Jul 24, 2026 11:09am | Jul 24, 2026 11:09am |  |  | Fair | No | Check voltage 118/119/237Meter defective one side of meter burnt outReferring to field service
Outage | J.E.26.07.27051 | C001864026 | Ryan Richards | Manchester | Completed | Load_255650 | Spur Tree - 310 | Jul 24, 2026 7:24am | Jul 24, 2026 7:34am | Jul 24, 2026 11:30am | Jul 24, 2026 11:31am | Jul 24, 2026 12:41pm | Jul 24, 2026 2:13pm | Jul 24, 2026 2:13pm | Jul 24, 2026 2:13pm |  |  | Fair | No | Burn off phase found at pole remade burn off phase using 1 one bolt clamp voltage 113/115/229 volts
Non-Outage | J.E.26.07.23120 | C001864021 | Damion Reid | Manchester | Completed | Load_267213 | Kendal - 210 | Jul 24, 2026 7:22am | Jul 24, 2026 7:22am | Jul 24, 2026 9:31am | Jul 24, 2026 9:31am | Jul 24, 2026 9:37am | Jul 24, 2026 9:57am | Jul 24, 2026 9:58am | Jul 24, 2026 9:58am |  |  | Fair | No | Premises found ok call was already completed
Non-Outage | J.E.26.07.24030 | C001864022 | Damion Reid | Manchester | Completed | Load_267213 | Kendal - 210 | Jul 24, 2026 7:22am | Jul 24, 2026 7:22am | Jul 24, 2026 8:21am | Jul 24, 2026 8:21am | Jul 24, 2026 9:20am | Jul 24, 2026 9:30am | Jul 24, 2026 9:31am | Jul 24, 2026 9:31am | BrokenWire |  | Fair | No | Premises found ok
Outage | J.E.26.07.27418 | C001864024 | Barnett Brown | Manchester | Completed | Load_258374 | Kendal - 210 | Jul 24, 2026 7:22am | Jul 24, 2026 3:12pm | Jul 24, 2026 4:24pm | Jul 24, 2026 4:25pm | Jul 24, 2026 6:45pm | Jul 24, 2026 7:05pm | Jul 24, 2026 7:06pm | Jul 24, 2026 7:06pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.29213 | C001864020 | Damion Reid | Manchester | Completed | Load_254977 | Kendal - 210 | Jul 24, 2026 7:21am | Jul 24, 2026 7:22am | Jul 24, 2026 10:01am | Jul 24, 2026 10:01am | Jul 24, 2026 11:06am | Jul 24, 2026 11:41am | Jul 24, 2026 11:44am | Jul 24, 2026 11:44am |  |  | Fair | No | Team unable to reconnect customer not enough service wire reconnection need approximately 150ft of #6 triplex
Outage | J.E.26.07.29300 | C001864019 | Damion Reid | Manchester | Completed | Load_254895 | Kendal - 210 | Jul 24, 2026 7:21am | Jul 24, 2026 7:22am | Jul 24, 2026 11:47am | Jul 24, 2026 11:47am | Jul 24, 2026 12:35pm | Jul 24, 2026 1:32pm | Jul 24, 2026 1:36pm | Jul 24, 2026 1:36pm |  |  | Fair | No | Blown 3amp fuse found for 25kva transformer cause by banging of secondary conductor retention conductor replace 2/0 preform and replace blown fuse
Outage | J.E.26.07.29245 | C001863937 | Horace Malcolm | St.James | Completed | Load_245810 | Queens Drive - 710 | Jul 24, 2026 6:03am | Jul 24, 2026 6:03am | Jul 24, 2026 6:24am | Jul 24, 2026 6:24am | Jul 24, 2026 6:24am | Jul 24, 2026 6:26am | Jul 24, 2026 6:26am | Jul 24, 2026 6:26am |  |  | Fair | No | Customer says supply went away last night but supply is back
Outage | J.E.26.07.28232 | C001863932 | Roxroy Needham | St.Ann | Completed | Load_252510 | Cardiff Hall - 210 | Jul 24, 2026 4:53am | Jul 24, 2026 4:53am | Jul 24, 2026 5:05am | Jul 24, 2026 5:05am | Jul 24, 2026 5:05am | Jul 24, 2026 5:06am | Jul 24, 2026 5:06am | Jul 24, 2026 5:06am |  |  | Fair | No | Call customer and customer say light is back
Outage | J.E.26.07.28972 | C001863933 | Roxroy Needham | St.Ann | Completed | Load_573811 | Cardiff Hall - 210 | Jul 24, 2026 4:53am | Jul 24, 2026 4:53am | Jul 24, 2026 5:04am | Jul 24, 2026 5:04am | Jul 24, 2026 5:04am | Jul 24, 2026 5:05am | Jul 24, 2026 5:05am | Jul 24, 2026 5:05am |  |  | Fair | No | Call customer and customer say light is back
Outage | J.E.26.07.29250 | C001863931 | Edward Royal | KSAS | Completed | Load_572515 | Up Park Camp - 510 | Jul 24, 2026 4:50am | Jul 24, 2026 4:50am | Jul 24, 2026 8:19am | Jul 24, 2026 8:39am | Jul 24, 2026 8:39am | Jul 24, 2026 8:41am | Jul 24, 2026 8:42am | Jul 24, 2026 8:42am |  |  | Fair | No | Contact customer by phone customer the power was restored
Outage | J.E.26.07.29252 | C001863930 | Edward Royal | KSAS | Completed | Load_245693 | Up Park Camp - 510 | Jul 24, 2026 4:50am | Jul 24, 2026 4:50am | Jul 24, 2026 8:16am | Jul 24, 2026 8:44am | Jul 24, 2026 8:44am | Jul 24, 2026 8:45am | Jul 24, 2026 8:46am | Jul 24, 2026 8:46am |  |  | Fair | No | Contact customer by phone customer the power was restored
Non-Outage | J.E.26.07.25765 | C001863927 | Edward Royal | null | Completed | null | null | Jul 24, 2026 12:39am | Jul 24, 2026 12:41am | Jul 24, 2026 1:26am | Jul 24, 2026 1:26am | Jul 24, 2026 1:26am | Jul 24, 2026 1:28am | Jul 24, 2026 1:28am | Jul 24, 2026 1:28am | Fire |  | Fair | No | When contacted customer, customer said the problem was resolved
Non-Outage | J.E.26.07.27781 | C001863922 | Horace Malcolm | null | Completed | null | null | Jul 23, 2026 11:59pm | Jul 24, 2026 12:00am | Jul 24, 2026 12:17am | Jul 24, 2026 12:17am | Jul 24, 2026 12:41am | Jul 24, 2026 1:04am | Jul 24, 2026 1:05am | Jul 24, 2026 1:05am |  |  | Fair | No | Check and found customer having no supply from meter to premises call to call center shows customer not disconnected referred to field service
Outage | J.E.26.07.27152 | C001863920 | Delano Gayle | St.Catherine | Completed | Load_270150 | Twickenham - 410 | Jul 23, 2026 11:54pm | Jul 23, 2026 11:55pm | Jul 24, 2026 5:06am | Jul 24, 2026 5:06am | Jul 24, 2026 5:29am | Jul 24, 2026 5:38am | Jul 24, 2026 5:38am | Jul 24, 2026 5:38am |  |  | Fair | No | Premises not found no answer from customer phone, area patrolled and found okay
Outage | J.E.26.07.27827 | C001863918 | Delano Gayle | St.Catherine | Completed | Load_254399 | Tredegar - 310 | Jul 23, 2026 11:54pm | Jul 23, 2026 11:55pm | Jul 24, 2026 5:42am | Jul 24, 2026 5:42am | Jul 24, 2026 5:57am | Jul 24, 2026 5:59am | Jul 24, 2026 5:59am | Jul 24, 2026 5:59am |  |  | Fair | No | Premises found okay power restored
Outage | J.E.26.07.27889 | C001863910 | Delano Gayle | St.Catherine | Completed | Load_253898 | Twickenham - 310 | Jul 23, 2026 9:39pm | Jul 23, 2026 11:55pm | Jul 24, 2026 2:26am | Jul 24, 2026 2:26am | Jul 24, 2026 2:59am | Jul 24, 2026 4:15am | Jul 24, 2026 4:15am | Jul 24, 2026 4:15am | BrokenWire |  | Fair | No | Premises not located no proper contact information or directions in repoty
Outage | J.E.26.07.27876 | C001863906 | Romaine Roberts | St.Mary | Completed | Load_254695 | Annotto Bay - 310 | Jul 23, 2026 9:29pm | Jul 23, 2026 9:30pm | Jul 23, 2026 9:42pm | Jul 23, 2026 9:45pm | Jul 23, 2026 10:05pm | Jul 23, 2026 10:06pm | Jul 23, 2026 10:06pm | Jul 23, 2026 10:06pm |  |  | Fair | No | Power restore
Outage | J.E.26.07.27843 | C001863903 | Barnett Brown | Manchester | Completed | Load_270122 | Kendal - 210 | Jul 23, 2026 9:07pm | Jul 23, 2026 9:08pm | Jul 23, 2026 9:27pm | Jul 23, 2026 9:27pm | Jul 23, 2026 9:48pm | Jul 23, 2026 10:08pm | Jul 23, 2026 10:10pm | Jul 23, 2026 10:10pm |  |  | Fair | No | Related to Warsop call where two 40 amp trip savers were down
Outage | J.E.26.07.27800 | C001863900 | Richman Whyte | Westmoreland | Completed | Load_256472 | Paradise - 110 | Jul 23, 2026 8:52pm | Jul 23, 2026 8:53pm | Jul 23, 2026 9:20pm | Jul 23, 2026 9:20pm | Jul 23, 2026 11:10pm | Jul 23, 2026 11:17pm | Jul 23, 2026 11:18pm | Jul 23, 2026 11:18pm |  |  | Rains | No | Replace five amp junction fuse
Non-Outage | J.E.26.07.26894 | C001863898 | Neckell Ormsby | St.Mary | Completed | Load_249746 | Highgate -110 | Jul 23, 2026 8:26pm | Jul 23, 2026 8:26pm | Jul 23, 2026 8:33pm | Jul 23, 2026 8:33pm | Jul 23, 2026 9:32pm | Jul 23, 2026 9:49pm | Jul 23, 2026 9:49pm | Jul 23, 2026 9:49pm | LeakingTransformer |  | Fair | No | Remove illegal connection that customer was reporting no leaking transformer at location
Outage | J.E.26.07.27461 | C001863896 | Gregory Grossett | Portland | Completed | Load_261260 | Port Antonio - 410 | Jul 23, 2026 8:23pm | Jul 23, 2026 8:23pm | Jul 23, 2026 8:36pm | Jul 23, 2026 8:36pm | Jul 23, 2026 8:36pm | Jul 23, 2026 8:37pm | Jul 23, 2026 8:37pm | Jul 23, 2026 8:37pm |  |  | Fair | No | Jps 220 meter is defective replace and customer is now ok.
Non-Outage | J.E.26.07.25862 | C001863893 | Christopher Edwards | KSAS | Completed | Load_247943 | Duhaney - 310 | Jul 23, 2026 8:11pm | Jul 23, 2026 8:12pm | Jul 23, 2026 8:19pm | Jul 23, 2026 9:33pm | Jul 23, 2026 9:34pm | Jul 23, 2026 9:35pm | Jul 23, 2026 9:41pm | Jul 23, 2026 9:41pm | Fire |  | Fair | No | Customer was contacted and said that the issue was resolved
Non-Outage | J.E.26.07.27502 | C001863891 | Christopher Edwards | KSAS | Completed | Load_578720 | Duhaney - 310 | Jul 23, 2026 8:11pm | Jul 23, 2026 8:12pm | Jul 23, 2026 8:24pm | Jul 23, 2026 8:24pm | Jul 23, 2026 9:00pm | Jul 23, 2026 9:31pm | Jul 23, 2026 9:32pm | Jul 23, 2026 9:32pm |  |  | Fair | No | Remake burnt offPhase joint using (1) one bolt clamps
Non-Outage | J.E.26.07.27559 | C001863892 | Milton Charlton | KSAN | Completed | Load_249728 | West Kings House - 410 | Jul 23, 2026 8:11pm | Jul 23, 2026 8:12pm | Jul 23, 2026 8:21pm | Jul 23, 2026 8:21pm | Jul 23, 2026 8:52pm | Jul 23, 2026 9:10pm | Jul 23, 2026 9:13pm | Jul 23, 2026 9:13pm |  |  | Fair | No | Found okay upon arrival. Readings at meter socket 118-118-236 volts. Customer has an internal problem.
Non-Outage | J.E.26.07.27803 | C001863884 | Cliton Henry | null | Completed | null | null | Jul 23, 2026 7:40pm | Jul 23, 2026 7:41pm | Jul 23, 2026 9:51pm | Jul 23, 2026 9:51pm | Jul 23, 2026 11:19pm | Jul 23, 2026 11:41pm | Jul 23, 2026 11:44pm | Jul 23, 2026 11:44pm | BrokenWire |  | Fair | No | Customers service wires torn down by a truck were disconnected. The report was made by passerby. The customers were not advised due to no contact info available.
Outage | J.E.26.07.27784 | C001863883 | Cliton Henry | St.Mary | Completed | Load_269770 | Blackstonedge - 110 | Jul 23, 2026 7:38pm | Jul 23, 2026 7:39pm | Jul 23, 2026 8:17pm | Jul 23, 2026 8:30pm | Jul 23, 2026 8:30pm | Jul 23, 2026 8:47pm | Jul 23, 2026 8:49pm | Jul 23, 2026 8:49pm |  |  | Fair | No | A #6 triplex service wire was disconnected due to a burnt meter socket. The customer was advised to get a licensed electrician to carryout repairs and call upon completion.
Outage | J.E.26.07.26755 | C001863878 | Eric Williams | KSAS | Completed | Load_301332 | Hunts Bay - 410 | Jul 23, 2026 7:24pm | Jul 23, 2026 7:25pm | Jul 23, 2026 7:59pm | Jul 23, 2026 8:02pm | Jul 23, 2026 8:02pm | Jul 23, 2026 8:39pm | Jul 23, 2026 8:39pm | Jul 23, 2026 8:39pm |  |  | Fair | No | Burnt hotline clamp found and replaced
Outage | J.E.26.07.27100 | C001863879 | Rusean Allen | KSAS | Completed | Load_264323 | Greenwich - 310 | Jul 23, 2026 7:24pm | Jul 24, 2026 8:20am | Jul 24, 2026 9:07am | Jul 24, 2026 9:31am | Jul 24, 2026 10:13am | Jul 24, 2026 10:14am | Jul 24, 2026 10:14am | Jul 24, 2026 10:14am |  |  | Fair | No | Premises okay
Outage | J.E.26.07.27146 | C001863880 | Edward Royal | KSAS | Completed | Load_238206 | Cane River - 410 | Jul 23, 2026 7:24pm | Jul 24, 2026 12:06am | Jul 24, 2026 8:14am | Jul 24, 2026 8:42am | Jul 24, 2026 8:42am | Jul 24, 2026 8:43am | Jul 24, 2026 8:44am | Jul 24, 2026 8:44am |  |  | Fair | No | Contact customer by phone customer the power was restored
Outage | J.E.26.07.27751 | C001863875 | Andrew Powell | Manchester | Completed | Load_292660 | Spur Tree - 210 | Jul 23, 2026 7:20pm | Jul 23, 2026 7:20pm | Jul 23, 2026 8:12pm | Jul 23, 2026 8:15pm | Jul 23, 2026 9:11pm | Jul 23, 2026 9:28pm | Jul 23, 2026 9:31pm | Jul 23, 2026 9:31pm |  |  | Fair | No | Found customers experiencing single phasing issues inside HEX boxes approximately 5 boxes affected, please refer to field service department for repair work.
Outage | J.E.26.07.27575 | C001863873 | Kaydon Taylor | KSAN | Completed | Load_258952 | Constant Spring - 210 | Jul 23, 2026 7:17pm | Jul 23, 2026 7:17pm | Jul 23, 2026 9:36pm | Jul 23, 2026 9:36pm | Jul 23, 2026 10:05pm | Jul 23, 2026 10:05pm | Jul 23, 2026 10:06pm | Jul 23, 2026 10:06pm |  |  | Fair | No | Found okay
Outage | J.E.26.07.27758 | C001863874 | Kaydon Taylor | KSAN | Completed | Load_260633 | Constant Spring - 210 | Jul 23, 2026 7:17pm | Jul 23, 2026 7:17pm | Jul 23, 2026 8:46pm | Jul 23, 2026 8:46pm | Jul 23, 2026 9:09pm | Jul 23, 2026 9:32pm | Jul 23, 2026 9:32pm | Jul 23, 2026 9:32pm |  |  | Fair | No | Escalation reset disconnected meter
Non-Outage | J.E.26.07.27641 | C001863868 | Cliton Henry | null | Completed | null | null | Jul 23, 2026 7:12pm | Jul 23, 2026 7:15pm | Jul 23, 2026 7:39pm | Jul 23, 2026 7:39pm | Jul 23, 2026 7:56pm | Jul 23, 2026 8:13pm | Jul 23, 2026 8:13pm | Jul 23, 2026 8:13pm | Fire |  | Fair | No | A burnt service wire was disconnected due to fire. The customer was advised to get a licensed electrician to check internally.
Outage | J.E.26.07.27691 | C001863869 | Delano Gayle | St.Catherine | Completed | Load_255398 | Tredegar - 510 | Jul 23, 2026 7:12pm | Jul 23, 2026 11:53pm | Jul 24, 2026 2:10am | Jul 24, 2026 2:10am | Jul 24, 2026 2:22am | Jul 24, 2026 2:23am | Jul 24, 2026 2:23am | Jul 24, 2026 2:23am |  |  | Fair | No | Single customer states bill was paid today yet still got disconnected, premises not found, area found okay
Outage | J.E.26.07.27653 | C001863863 | Derrick Dawkins | St.James | Completed | Load_254099 | Bogue - 310 | Jul 23, 2026 7:05pm | Jul 23, 2026 7:06pm | Jul 23, 2026 9:01pm | Jul 23, 2026 9:01pm | Jul 23, 2026 10:43pm | Jul 23, 2026 10:45pm | Jul 23, 2026 10:45pm | Jul 23, 2026 10:45pm |  |  | Fair | No | Cannot locate customer
Outage | J.E.26.07.27749 | C001863862 | Dean Smith | Hanover | Completed | Load_258609 | Orange Bay - 210 | Jul 23, 2026 7:04pm | Jul 23, 2026 7:04pm | Jul 23, 2026 8:45pm | Jul 23, 2026 8:45pm | Jul 23, 2026 8:45pm | Jul 23, 2026 8:45pm | Jul 23, 2026 8:46pm | Jul 23, 2026 8:46pm |  |  | Rains | No | Unable to complete because of rain, please forward to morning chew.
Non-Outage | J.E.26.07.26966 | C001863861 | Jermaine Williams | Clarendon | Completed | Load_258821 | Parnassus - 310 | Jul 23, 2026 7:03pm | Jul 23, 2026 7:16pm | Jul 23, 2026 8:02pm | Jul 23, 2026 8:02pm | Jul 23, 2026 8:33pm | Jul 23, 2026 8:33pm | Jul 23, 2026 8:33pm | Jul 23, 2026 8:33pm | Fire |  | Fair | No | Issue was resolved earlier.
Non-Outage | J.E.26.07.21656 | C001863852 | Michael Christian | St.James | Completed | Load_238044 | Queens Drive - 710 | Jul 23, 2026 7:00pm | Jul 23, 2026 7:00pm | Jul 23, 2026 7:07pm | Jul 23, 2026 7:07pm | Jul 23, 2026 7:30pm | Jul 23, 2026 7:40pm | Jul 23, 2026 7:40pm | Jul 23, 2026 7:40pm |  |  | Fair | No | Check and found voltage 110 109 221 at meter
Non-Outage | J.E.26.07.25838 | C001863851 | Michael Christian | St.James | Completed | Load_259218 | Queens Drive - 710 | Jul 23, 2026 6:59pm | Jul 23, 2026 7:00pm | Jul 23, 2026 7:30pm | Jul 23, 2026 7:40pm | Jul 23, 2026 8:51pm | Jul 23, 2026 8:54pm | Jul 23, 2026 8:54pm | Jul 23, 2026 8:54pm |  |  | Fair | No | Check and found okay voltage 111 113 225 at pothead
Outage | J.E.26.07.27729 | C001863832 | Andre Williams | Trelawny | Completed | Load_249194 | Duncans - 110 | Jul 23, 2026 6:47pm | Jul 23, 2026 6:49pm | Jul 23, 2026 6:57pm | Jul 23, 2026 6:57pm | Jul 23, 2026 7:32pm | Jul 23, 2026 7:37pm | Jul 23, 2026 7:38pm | Jul 23, 2026 7:38pm | BrokenWire |  | Fair | No | Open 50 kva transformer splice and region broken lower secondary phase , 50 kva on pole need to be straighten, reffer to maintenance, area now with full supply
Non-Outage | J.E.26.07.27127 | C001863825 | Milton Charlton | KSAN | Completed | Load_238339 | Hope - 410 | Jul 23, 2026 6:34pm | Jul 23, 2026 6:34pm | Jul 23, 2026 7:07pm | Jul 23, 2026 7:07pm | Jul 23, 2026 7:43pm | Jul 23, 2026 7:40pm | Jul 23, 2026 7:48pm | Jul 23, 2026 7:48pm |  |  | Fair | No | Customer is fed from EN # 05283 and is getting no supply from the box. JPS escalation is unable to reconnect meter. Refer to field service.
Non-Outage | J.E.26.07.27563 | C001863823 | Shamour Haughton | null | Completed | null | null | Jul 23, 2026 6:31pm | Jul 23, 2026 6:32pm | Jul 23, 2026 6:43pm | Jul 23, 2026 6:43pm | Jul 23, 2026 6:50pm | Jul 23, 2026 6:50pm | Jul 23, 2026 6:52pm | Jul 23, 2026 6:52pm | Fire |  | Fair | No | Check and found okay, customer states that there electrician had rectified the issue
Outage | J.E.26.07.27650 | C001863824 | Rayon Foster | Hanover | Completed | Load_230038 | Orange Bay - 310 | Jul 23, 2026 6:31pm | Jul 23, 2026 6:32pm | Jul 23, 2026 7:30pm | Jul 23, 2026 7:59pm | Jul 23, 2026 8:26pm | Jul 23, 2026 8:31pm | Jul 23, 2026 8:32pm | Jul 23, 2026 8:32pm |  |  | Fair | No | When spoke with customer he said that he did not make a report
Outage | J.E.26.07.26440 | C001863815 | Jermaine Williams | Clarendon | Completed | Load_246015 | Monymusk - 410 | Jul 23, 2026 6:13pm | Jul 23, 2026 7:21pm | Jul 24, 2026 8:47am | Jul 24, 2026 8:48am | Jul 24, 2026 8:48am | Jul 24, 2026 8:48am | Jul 24, 2026 8:49am | Jul 24, 2026 8:49am |  |  | Fair | No | Premises found ok.
Non-Outage | J.E.26.07.27573 | C001863809 | Gregory Grossett | null | Completed | null | null | Jul 23, 2026 6:01pm | Jul 23, 2026 6:02pm | Jul 23, 2026 8:06pm | Jul 23, 2026 8:06pm | Jul 23, 2026 8:33pm | Jul 23, 2026 8:36pm | Jul 23, 2026 8:36pm | Jul 23, 2026 8:36pm |  |  | Fair | No | After finding the customer she said she did not make a report and supply in the area is ok.
Outage | J.E.26.07.27622 | C001863810 | Gregory Grossett | Portland | Completed | Load_241944 | Port Antonio - 410 | Jul 23, 2026 6:01pm | Jul 23, 2026 6:02pm | Jul 23, 2026 6:08pm | Jul 23, 2026 6:08pm | Jul 23, 2026 6:55pm | Jul 23, 2026 8:00pm | Jul 23, 2026 8:06pm | Jul 23, 2026 8:06pm | BrokenWire |  | Fair | No | Two pole span of open secondary neutral conductor bursts down cause by truck entangled with conductors. Open 25kva transformer fuse then splice and retention conductors close transformer fuse to restore supply to the area.Material use 70ft aa conductor 2 number 2 splicing sleeve 4 one bolt clamps.
Outage | J.E.26.07.27503 | C001863800 | Christopher Edwards | KSAS | Completed | Load_248546 | Duhaney - 310 | Jul 23, 2026 5:30pm | Jul 23, 2026 5:31pm | Jul 23, 2026 6:22pm | Jul 23, 2026 6:26pm | Jul 23, 2026 6:26pm | Jul 23, 2026 6:56pm | Jul 23, 2026 6:57pm | Jul 23, 2026 6:57pm |  |  | Fair | No | Customer was disconnected for late payment Metering department was contacted and service is restored
Outage | J.E.26.07.27531 | C001863801 | Christopher Edwards | KSAN | Completed | Load_253397 | Washington Blvd - 810 | Jul 23, 2026 5:30pm | Jul 23, 2026 5:31pm | Jul 23, 2026 5:42pm | Jul 23, 2026 5:44pm | Jul 23, 2026 5:44pm | Jul 23, 2026 6:22pm | Jul 23, 2026 6:22pm | Jul 23, 2026 6:22pm | Fire | Y | Fair | No | Required bushing on secondary line As secondary lines runs through trees Supply is in the area
Non-Outage | J.E.26.07.20942 | C001863795 | Rodclif Dawkins | Portmore | Completed | Load_573422 | Naggo Head - 610 | Jul 23, 2026 5:23pm | Jul 23, 2026 5:24pm | Jul 23, 2026 10:04pm | Jul 23, 2026 10:04pm | Jul 23, 2026 10:25pm | Jul 23, 2026 10:47pm | Jul 23, 2026 10:51pm | Jul 23, 2026 10:51pm |  |  | Fair | No | At premises crew found triplex #6 supplying 3w meter with corroded joints at pole and pothead. Using 3 pen unions along with 3-1bolt clamps joints replaced, customer okay
Outage | J.E.26.07.27571 | C001863794 | Donald Cunningham | St.Catherine | Completed | Load_241212 | Tredegar - 510 | Jul 23, 2026 5:21pm | Jul 23, 2026 5:22pm | Jul 23, 2026 8:37pm | Jul 23, 2026 8:37pm | Jul 23, 2026 9:31pm | Jul 23, 2026 9:46pm | Jul 23, 2026 9:48pm | Jul 23, 2026 9:48pm |  |  | Fair | No | Blown transformer fuse for 10kva replace with 3 amp fuse by pole # 010989
Non-Outage | J.E.26.07.26737 | C001863791 | Andre Williams | Trelawny | Completed | Load_302800 | Duncans - 110 | Jul 23, 2026 5:17pm | Jul 23, 2026 5:31pm | Jul 23, 2026 5:59pm | Jul 23, 2026 6:01pm | Jul 23, 2026 6:21pm | Jul 23, 2026 6:47pm | Jul 23, 2026 6:54pm | Jul 23, 2026 6:54pm |  |  | Fair | No | Clean coroded joints at pothead Voltage at pothead 114+114=228, reffer to field service to check meter ,meter is barrel lock customer also advice to get there electrician to check low voltage on there side
Non-Outage | J.E.26.07.27193 | C001863789 | Andre Williams | Trelawny | Completed | Load_292529 | Duncans - 210 | Jul 23, 2026 5:17pm | Jul 23, 2026 5:17pm | Jul 23, 2026 5:31pm | Jul 23, 2026 7:38pm | Jul 23, 2026 8:32pm | Jul 23, 2026 8:44pm | Jul 23, 2026 8:45pm | Jul 23, 2026 8:45pm |  |  | Fair | No | Remake burnt off joint at Jps pole on customer 3 wire service #6 wire voltage 116+116=232
Non-Outage | J.E.26.07.27498 | C001863787 | Roemello Brown | Trelawny | Completed | Load_248304 | Greenwood - 110 | Jul 23, 2026 5:16pm | Jul 24, 2026 9:09am | Jul 24, 2026 9:33am | Jul 24, 2026 12:49pm | Jul 24, 2026 1:42pm | Jul 24, 2026 1:42pm | Jul 24, 2026 1:52pm | Jul 24, 2026 1:52pm |  |  | Fair | No | Corrosion at pole side have clamps change Voltage found 116/78/178Voltage leave 114/109/223
Outage | J.E.26.07.27495 | C001863786 | Derrick Dawkins | St.James | Completed | Load_246965 | Bogue - 310 | Jul 23, 2026 5:16pm | Jul 23, 2026 5:17pm | Jul 23, 2026 6:21pm | Jul 23, 2026 6:21pm | Jul 23, 2026 6:29pm | Jul 23, 2026 8:15pm | Jul 23, 2026 8:18pm | Jul 23, 2026 8:18pm |  |  | Fair | No | Found a 10 kva transformer chip due to secondary phase and neutral banging up retention one span secondary phase and reset 10 kva transformer no pole # available
Outage | J.E.26.07.27580 | C001863785 | Shamour Haughton | St.James | Completed | Load_252042 | Bogue - 510 | Jul 23, 2026 5:16pm | Jul 23, 2026 5:17pm | Jul 23, 2026 5:33pm | Jul 23, 2026 5:33pm | Jul 23, 2026 5:58pm | Jul 23, 2026 6:33pm | Jul 23, 2026 6:41pm | Jul 23, 2026 6:41pm |  |  | Fair | No | Found customer experiencing internal issues, customer was advised to get an electrician and then recall Jps
Non-Outage | J.E.26.07.27563 | C001863779 | Rayon Foster | null | Completed | null | null | Jul 23, 2026 5:07pm | Jul 23, 2026 5:11pm | Jul 23, 2026 6:13pm | Jul 23, 2026 6:13pm | Jul 23, 2026 6:13pm | Jul 23, 2026 6:14pm | Jul 23, 2026 6:14pm | Jul 23, 2026 6:14pm | Fire |  | Fair | No | St James call
Outage | J.E.26.07.26581 | C001863773 | Kaydon Taylor | KSAN | Completed | Load_246214 | Constant Spring - 210 | Jul 23, 2026 5:05pm | Jul 23, 2026 5:05pm | Jul 23, 2026 5:58pm | Jul 23, 2026 5:58pm | Jul 23, 2026 6:32pm | Jul 23, 2026 7:05pm | Jul 23, 2026 7:05pm | Jul 23, 2026 7:05pm |  |  | Fair | No | 15 amp fuse found blown and replace at pole #0011661
Non-Outage | J.E.26.07.27585 | C001863772 | Eric Williams | KSAS | Completed | Load_413076 | Up Park Camp - 310 | Jul 23, 2026 5:04pm | Jul 23, 2026 5:05pm | Jul 23, 2026 5:47pm | Jul 23, 2026 5:47pm | Jul 23, 2026 6:43pm | Jul 23, 2026 7:01pm | Jul 23, 2026 7:25pm | Jul 23, 2026 7:25pm |  |  | Fair | No | 2 pad mount transformer, voltage on 1 transformer 121,121,211,242,241,243, volt on the next transformer 244,243,242,421,422, 422 volt, customer complain that voltage too high so refer to SMD department
Outage | J.E.26.07.27534 | C001863771 | Cliton Henry | St.Mary | Completed | Load_240179 | Blackstonedge - 110 | Jul 23, 2026 5:01pm | Jul 23, 2026 5:01pm | Jul 23, 2026 9:00pm | Jul 23, 2026 9:00pm | Jul 23, 2026 9:32pm | Jul 23, 2026 9:50pm | Jul 23, 2026 9:51pm | Jul 23, 2026 9:51pm | Fire |  | Fair | No | A burnt off secondary phase jumper found at the 25 kva transformer pole. The transformer was de energized to carryout repairs. Corrective work done to reconnected the secondary phase jumper using 2- one bolt clamps. Supply restored to energized the 25 kva transformer. Voltages left 118-118/236 volts
Non-Outage | J.E.26.07.27207 | C001863756 | Richard Samuda | null | Completed | null | null | Jul 23, 2026 4:46pm | Jul 23, 2026 4:53pm | Jul 23, 2026 9:29pm | Jul 23, 2026 9:29pm | Jul 23, 2026 9:39pm | Jul 23, 2026 9:41pm | Jul 23, 2026 9:40pm | Jul 23, 2026 9:40pm |  |  | Fair | No | Found ok
Outage | J.E.26.07.26889 | C001863751 | Kenroy Dale | Manchester | Completed | Load_246578 | Porus - 310 | Jul 23, 2026 4:45pm | Jul 23, 2026 4:46pm | Jul 23, 2026 5:04pm | Jul 23, 2026 5:04pm | Jul 23, 2026 5:46pm | Jul 23, 2026 5:49pm | Jul 23, 2026 5:51pm | Jul 23, 2026 5:51pm |  |  | Fair | No | Effort to contact customer was unsuccessful, no proper driving directions was advised to write off call by dispatch
Outage | J.E.26.07.26780 | C001863742 | Eric Williams | KSAN | Completed | Load_293333 | Washington Blvd - 710 | Jul 23, 2026 4:40pm | Jul 23, 2026 4:41pm | Jul 23, 2026 4:54pm | Jul 23, 2026 4:54pm | Jul 23, 2026 5:46pm | Jul 23, 2026 5:46pm | Jul 23, 2026 5:47pm | Jul 23, 2026 5:47pm |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.26863 | C001863741 | Eric Williams | KSAN | Completed | Load_293864 | Washington Blvd - 710 | Jul 23, 2026 4:39pm | Jul 23, 2026 4:41pm | Jul 23, 2026 9:55pm | Jul 23, 2026 9:55pm | Jul 23, 2026 9:55pm | Jul 23, 2026 9:55pm | Jul 23, 2026 9:55pm | Jul 23, 2026 9:55pm |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.27483 | C001863725 | Rodclif Dawkins | Portmore | Completed | Load_573422 | Naggo Head - 610 | Jul 23, 2026 4:30pm | Jul 23, 2026 4:31pm | Jul 23, 2026 7:09pm | Jul 23, 2026 10:51pm | Jul 23, 2026 10:51pm | Jul 23, 2026 10:52pm | Jul 23, 2026 10:52pm | Jul 23, 2026 10:52pm | Fire |  | Fair | No | At premises crew found triplex #6 supplying 3w meter with corroded joints at pole and pothead. Using 3 pen unions along with 3-1bolt clamps joints replaced, customer okay
Non-Outage | J.E.26.07.25557 | C001863720 | Wayne Dillion | null | Completed | null | null | Jul 23, 2026 4:21pm | Jul 23, 2026 4:22pm | Jul 23, 2026 8:12pm | Jul 23, 2026 8:12pm | Jul 23, 2026 9:22pm | Jul 23, 2026 9:22pm | Jul 23, 2026 9:29pm | Jul 23, 2026 9:29pm | BrokenPole |  | Fair | No | Reconnect customer using 70 feet of number six triplex 3 linket 3 one bolt clamp voltage reading 116v 116v 234v supply working ok
Outage | J.E.26.07.27224 | C001863703 | Ricky Hall | St.Catherine | Completed | Load_258753 | New Michelton - 210 | Jul 23, 2026 4:09pm | Jul 23, 2026 4:13pm | Jul 23, 2026 8:06pm | Jul 23, 2026 8:06pm | Jul 23, 2026 8:57pm | Jul 23, 2026 9:04pm | Jul 23, 2026 9:05pm | Jul 23, 2026 9:05pm |  |  | Fair | No | Premises closed
Outage | J.E.26.07.27415 | C001863706 | Donald Cunningham | St.Catherine | Completed | Load_242765 | Twickenham - 310 | Jul 23, 2026 4:09pm | Jul 23, 2026 7:43pm | Jul 23, 2026 9:49pm | Jul 23, 2026 9:49pm | Jul 23, 2026 10:45pm | Jul 23, 2026 10:50pm | Jul 23, 2026 10:51pm | Jul 23, 2026 10:51pm |  |  | Fair | No | Premises closed
Outage | J.E.26.07.27494 | C001863704 | Ricky Hall | St.Catherine | Completed | Load_244637 | New Michelton - 210 | Jul 23, 2026 4:09pm | Jul 23, 2026 4:13pm | Jul 23, 2026 4:53pm | Jul 23, 2026 4:54pm | Jul 23, 2026 6:16pm | Jul 23, 2026 6:34pm | Jul 23, 2026 6:34pm | Jul 23, 2026 6:34pm |  |  | Fair | No | Customer found disconnected for non payment of bill
Outage | J.E.26.07.27499 | C001863705 | Ricky Hall | St.Catherine | Completed | Load_242473 | New Michelton - 410 | Jul 23, 2026 4:09pm | Jul 23, 2026 4:13pm | Jul 23, 2026 6:57pm | Jul 23, 2026 6:57pm | Jul 23, 2026 8:02pm | Jul 23, 2026 8:03pm | Jul 23, 2026 8:04pm | Jul 23, 2026 8:04pm |  |  | Fair | No | Issue was resolved by st Mary team
Outage | J.E.26.07.27520 | C001863699 | Michael Christian | St.James | Completed | Load_251221 | Queens Drive - 810 | Jul 23, 2026 4:04pm | Jul 23, 2026 4:05pm | Jul 23, 2026 4:16pm | Jul 23, 2026 4:57pm | Jul 23, 2026 6:00pm | Jul 23, 2026 6:22pm | Jul 23, 2026 6:22pm | Jul 23, 2026 6:22pm |  |  | Rains | No | Internal fault
Outage | J.E.26.07.27423 | C001863697 | Milton Charlton | KSAS | Completed | Load_255178 | Up Park Camp - 410 | Jul 23, 2026 4:01pm | Jul 23, 2026 4:01pm | Jul 23, 2026 5:02pm | Jul 23, 2026 5:02pm | Jul 23, 2026 5:02pm | Jul 23, 2026 5:10pm | Jul 23, 2026 5:06pm | Jul 23, 2026 5:06pm | TreeContact |  | Fair | No | Found okay upon arrival. Secondary bushing is required urgently. Tree limbs going up through open wire secondary on 5ft crossarm.
Outage | J.E.26.07.27289 | C001863690 | Richard Samuda | Manchester | Completed | Load_294633 | Spur Tree - 310 | Jul 23, 2026 4:00pm | Jul 23, 2026 6:39pm | Jul 23, 2026 9:42pm | Jul 23, 2026 9:56pm | Jul 23, 2026 9:56pm | Jul 23, 2026 9:56pm | Jul 23, 2026 9:57pm | Jul 23, 2026 9:57pm |  |  | Fair | No | Premises not located and call to check no answer
Outage | J.E.26.07.27425 | C001863689 | Richard Samuda | Manchester | Completed | Load_260365 | Spur Tree - 310 | Jul 23, 2026 4:00pm | Jul 23, 2026 4:52pm | Jul 23, 2026 5:34pm | Jul 23, 2026 5:36pm | Jul 23, 2026 5:56pm | Jul 23, 2026 5:57pm | Jul 23, 2026 5:57pm | Jul 23, 2026 5:57pm |  |  | Fair | No | Customer back to normal
Outage | J.E.26.07.27451 | C001863688 | Richard Samuda | Manchester | Completed | Load_266469 | Spur Tree - 310 | Jul 23, 2026 4:00pm | Jul 23, 2026 4:01pm | Jul 23, 2026 5:58pm | Jul 23, 2026 5:58pm | Jul 23, 2026 6:04pm | Jul 23, 2026 8:20pm | Jul 23, 2026 8:21pm | Jul 23, 2026 8:21pm |  |  | Fair | No | Change corroded 1bolt clamps on customer pothead that are causing customer to experience low voltage 119/119/238 customer back to normal
Outage | J.E.26.07.27506 | C001863687 | Cliton Henry | St.Mary | Completed | Load_245290 | Blackstonedge - 110 | Jul 23, 2026 3:59pm | Jul 23, 2026 3:59pm | Jul 23, 2026 5:28pm | Jul 23, 2026 5:28pm | Jul 23, 2026 6:47pm | Jul 23, 2026 7:17pm | Jul 23, 2026 7:17pm | Jul 23, 2026 7:17pm |  |  | Fair | No | A blown 3 amp fuse found for a 25 kva transformer at pole #0100670 due to entangled secondary conductors cause by a truck. The secondary conductors were cleared and supply restored using 1- 3 amp fuse.
Non-Outage | J.E.26.07.26592 | C001863686 | Daniel Francis | St.Ann | Completed | Load_246075 | Roaring River - 410 | Jul 23, 2026 3:58pm | Jul 23, 2026 3:59pm | Jul 23, 2026 10:28pm | Jul 23, 2026 10:28pm | Jul 23, 2026 10:28pm | Jul 23, 2026 10:29pm | Jul 23, 2026 10:29pm | Jul 23, 2026 10:29pm |  |  | Fair | No | Not found
Non-Outage | J.E.26.07.27154 | C001863685 | Daniel Francis | St.Ann | Completed | Load_260101 | Ocho Rios - 310 | Jul 23, 2026 3:58pm | Jul 23, 2026 3:59pm | Jul 23, 2026 5:16pm | Jul 23, 2026 5:16pm | Jul 23, 2026 5:50pm | Jul 23, 2026 5:56pm | Jul 23, 2026 6:23pm | Jul 23, 2026 6:23pm |  |  | Fair | No | Change 5 one bolt clamp 3 at pothead and 2 at pole
Non-Outage | J.E.26.07.27268 | C001863683 | Andrew Powell | null | Completed | null | null | Jul 23, 2026 3:56pm | Jul 23, 2026 4:07pm | Jul 23, 2026 4:57pm | Jul 23, 2026 4:57pm | Jul 23, 2026 5:15pm | Jul 23, 2026 5:45pm | Jul 23, 2026 5:51pm | Jul 23, 2026 5:51pm |  |  | Fair | No | Replace three blown 25 amp fuse protect 750 kva pod mounted transformer circuit which one of the fuse rejected due to internal issues, customer leaves without supply, advise customer.
Outage | J.E.26.07.27456 | C001863682 | Andrew Powell | Manchester | Completed | Load_265389 | Spur Tree - 210 | Jul 23, 2026 3:56pm | Jul 23, 2026 4:08pm | Jul 23, 2026 5:52pm | Jul 23, 2026 5:52pm | Jul 23, 2026 6:12pm | Jul 23, 2026 6:53pm | Jul 23, 2026 6:55pm | Jul 23, 2026 6:55pm |  |  | Fair | No | Remade corroded service wire joints at secondary line 3 wire using three clamps, voltage reading 112v-112v phase to neutral 224v cross phase.
Outage | J.E.26.07.27461 | C001863684 | Gregory Grossett | Portland | Completed | Load_261260 | Port Antonio - 410 | Jul 23, 2026 3:56pm | Jul 23, 2026 3:57pm | Jul 23, 2026 4:28pm | Jul 23, 2026 4:28pm | Jul 23, 2026 5:20pm | Jul 23, 2026 5:22pm | Jul 23, 2026 5:22pm | Jul 23, 2026 5:22pm |  |  | Fair | No | Jps meter is defective please refer to field service department to have it change.
Non-Outage | J.E.26.07.27490 | C001863677 | Kaydon Taylor | null | Completed | null | null | Jul 23, 2026 3:54pm | Jul 23, 2026 3:54pm | Jul 23, 2026 4:34pm | Jul 23, 2026 4:36pm | Jul 23, 2026 5:03pm | Jul 23, 2026 5:57pm | Jul 23, 2026 5:58pm | Jul 23, 2026 5:58pm | BrokenWire |  | Rains | No | 3 clamps at pot head
Outage | J.E.26.07.26990 | C001863676 | Jermaine Williams | Clarendon | Completed | Load_262510 | May Pen - 210 | Jul 23, 2026 3:52pm | Jul 23, 2026 3:52pm | Jul 23, 2026 4:31pm | Jul 23, 2026 4:31pm | Jul 23, 2026 4:31pm | Jul 23, 2026 4:31pm | Jul 23, 2026 4:31pm | Jul 23, 2026 4:31pm |  |  | Fair | No | Replace 1-15A Junction fuse
Non-Outage | J.E.26.07.26415 | C001863675 | Jermaine Williams | null | Completed | null | null | Jul 23, 2026 3:51pm | Jul 23, 2026 3:52pm | Jul 23, 2026 4:33pm | Jul 23, 2026 4:33pm | Jul 23, 2026 4:34pm | Jul 23, 2026 4:34pm | Jul 23, 2026 4:34pm | Jul 23, 2026 4:34pm | Fire |  | Fair | Yes | Premises found ok
Outage | J.E.26.07.26468 | C001863670 | Jermaine Williams | Clarendon | Completed | Load_251038 | Parnassus - 310 | Jul 23, 2026 3:51pm | Jul 23, 2026 3:52pm | Jul 23, 2026 7:10pm | Jul 23, 2026 7:10pm | Jul 23, 2026 8:00pm | Jul 23, 2026 8:00pm | Jul 23, 2026 8:00pm | Jul 23, 2026 8:00pm |  |  | Fair | No | Premises found ok.
Outage | J.E.26.07.26726 | C001863667 | Jermaine Williams | Clarendon | Completed | Load_256859 | Parnassus - 310 | Jul 23, 2026 3:51pm | Jul 23, 2026 3:53pm | Jul 23, 2026 9:04pm | Jul 23, 2026 9:04pm | Jul 23, 2026 10:01pm | Jul 23, 2026 10:01pm | Jul 23, 2026 10:01pm | Jul 23, 2026 10:01pm |  |  | Fair | No | Premises found ok.
Outage | J.E.26.07.26728 | C001863669 | Jermaine Williams | Clarendon | Completed | Load_253979 | Parnassus - 210 | Jul 23, 2026 3:51pm | Jul 23, 2026 3:52pm | Jul 23, 2026 4:36pm | Jul 23, 2026 4:36pm | Jul 23, 2026 4:37pm | Jul 23, 2026 4:38pm | Jul 23, 2026 4:38pm | Jul 23, 2026 4:38pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.26924 | C001863668 | Jermaine Williams | Clarendon | Completed | Load_262121 | Parnassus - 310 | Jul 23, 2026 3:51pm | Jul 23, 2026 3:52pm | Jul 23, 2026 10:01pm | Jul 23, 2026 10:01pm | Jul 24, 2026 8:46am | Jul 24, 2026 8:46am | Jul 24, 2026 8:47am | Jul 24, 2026 8:47am |  |  | Fair | No | Premises found ok.
Outage | J.E.26.07.27469 | C001863671 | Jermaine Williams | Clarendon | Completed | Load_265303 | May Pen - 210 | Jul 23, 2026 3:51pm | Jul 23, 2026 3:52pm | Jul 23, 2026 4:17pm | Jul 23, 2026 4:17pm | Jul 23, 2026 4:29pm | Jul 23, 2026 4:29pm | Jul 23, 2026 4:30pm | Jul 23, 2026 4:30pm |  |  | SevereWind | No | Removed kite from line and replaced blown 10amp junction fuse.
Non-Outage | J.E.26.07.27273 | C001863655 | Andrew Powell | null | Completed | null | null | Jul 23, 2026 3:49pm | Jul 23, 2026 3:51pm | Jul 23, 2026 4:34pm | Jul 23, 2026 4:34pm | Jul 23, 2026 4:51pm | Jul 23, 2026 4:55pm | Jul 23, 2026 4:57pm | Jul 23, 2026 4:57pm |  |  | Fair | No | Isolate three drop out switches protect 750 kva pod mount transformer which facilitate NIC pumping station, no pole number by switch location.
Non-Outage | J.E.26.07.27439 | C001863654 | Christopher Edwards | null | Completed | null | null | Jul 23, 2026 3:49pm | Jul 23, 2026 7:08pm | Jul 23, 2026 7:42pm | Jul 23, 2026 7:55pm | Jul 23, 2026 7:55pm | Jul 23, 2026 7:59pm | Jul 23, 2026 7:59pm | Jul 23, 2026 7:59pm | BrokenWire |  | Fair | No | Customer was contacted and stated that the issue was resolved
Outage | J.E.26.07.25984 | C001863642 | Donald Cunningham | St.Catherine | Completed | Load_245725 | Rhodens Pen - 410 | Jul 23, 2026 3:42pm | Jul 23, 2026 3:43pm | Jul 23, 2026 3:50pm | Jul 23, 2026 4:34pm | Jul 23, 2026 7:09pm | Jul 23, 2026 7:11pm | Jul 23, 2026 7:12pm | Jul 23, 2026 7:12pm |  |  | Fair | No | Premises not located customer not reachable
Outage | J.E.26.07.27500 | C001863630 | Tajay Bernard | Hanover | Completed | Load_294683 | Orange Bay - 310 | Jul 23, 2026 3:37pm | Jul 23, 2026 3:38pm | Jul 23, 2026 3:56pm | Jul 23, 2026 3:58pm | Jul 23, 2026 4:26pm | Jul 23, 2026 4:31pm | Jul 23, 2026 4:32pm | Jul 23, 2026 4:32pm |  |  | Fair | No | Premises check and found okay customer has internal problems voltage reading 117/116/233
Outage | J.E.26.07.27162 | C001863628 | Wayne Dillion | Manchester | Completed | Load_302821 | Spur Tree - 210 | Jul 23, 2026 3:36pm | Jul 23, 2026 3:52pm | Jul 23, 2026 5:23pm | Jul 23, 2026 5:23pm | Jul 23, 2026 5:23pm | Jul 23, 2026 6:00pm | Jul 23, 2026 6:10pm | Jul 23, 2026 6:10pm |  |  | Fair | No | Patrol and found clear replace one 30 amp junction no pole number supply restore to customer successfully however a 35 feet wooden pole rotten at the foot and lean over on a customer wall and threes conductor holding up the pole please refer to maintenance to have the pole replaced as soon as possible
Outage | J.E.26.07.27244 | C001863626 | Selvin White | St.Elizabeth | Completed | Load_262625 | Maggotty - 210 | Jul 23, 2026 3:36pm | Jul 23, 2026 3:53pm | Jul 23, 2026 4:52pm | Jul 23, 2026 4:52pm | Jul 23, 2026 5:48pm | Jul 23, 2026 6:22pm | Jul 23, 2026 6:47pm | Jul 23, 2026 6:47pm | LowHangingWires |  | Fair | No | Retention customer service wires that was hanging low across roadway since the last hurricane. Supply left okay with voltage readings of 223,112,111 volts. 3 customers service wires were affected.
Outage | J.E.26.07.27270 | C001863625 | Selvin White | St.Elizabeth | Completed | Load_292458 | Maggotty - 210 | Jul 23, 2026 3:36pm | Jul 23, 2026 6:07pm | Jul 23, 2026 7:04pm | Jul 23, 2026 7:04pm | Jul 23, 2026 7:19pm | Jul 23, 2026 7:31pm | Jul 23, 2026 7:31pm | Jul 23, 2026 7:31pm |  |  | Fair | No | Daylight attention is required due to terrain that cannot be patrolled at.2 customers are affected.
Outage | J.E.26.07.27375 | C001863629 | Wayne Dillion | Manchester | Completed | Load_292105 | Spur Tree - 210 | Jul 23, 2026 3:36pm | Jul 23, 2026 10:24pm | Jul 23, 2026 10:27pm | Jul 23, 2026 10:27pm | Jul 23, 2026 10:27pm | Jul 23, 2026 10:27pm | Jul 23, 2026 10:32pm | Jul 23, 2026 10:32pm | BrokenPole |  | Fair | No | Supply check and found every customer has supply no outage however one 30 feet wooden class 6 pole badly leaning guy needed open secondary need to retired pole need straightening please refer to maintenance
Outage | J.E.26.07.27144 | C001863620 | Selvin White | St.Elizabeth | Completed | Load_258901 | Maggotty - 110 | Jul 23, 2026 3:34pm | Jul 23, 2026 9:12pm | Jul 23, 2026 9:19pm | Jul 23, 2026 9:23pm | Jul 23, 2026 9:38pm | Jul 23, 2026 9:43pm | Jul 23, 2026 9:43pm | Jul 23, 2026 9:43pm |  |  | Fair | No | Same was referred to Simone Bicarie at the field service department and an order was generated for the field service technician to visit and inspect the premises before reconnecting can be done as premises was damaged during the last hurricane.
Non-Outage | J.E.26.07.27344 | C001863618 | Daniel Francis | null | Completed | null | null | Jul 23, 2026 3:33pm | Jul 23, 2026 3:34pm | Jul 23, 2026 6:26pm | Jul 23, 2026 6:26pm | Jul 23, 2026 7:03pm | Jul 23, 2026 7:27pm | Jul 23, 2026 7:33pm | Jul 23, 2026 7:33pm | BrokenWire |  | Fair | No | Change 4 one bolt clamp 3 at pothead one at pole 117 117 234 in all
Outage | J.E.26.07.26768 | C001863619 | Wayne Dillion | St.Elizabeth | Completed | Load_240462 | Maggotty - 110 | Jul 23, 2026 3:33pm | Jul 23, 2026 3:35pm | Jul 23, 2026 6:17pm | Jul 23, 2026 6:17pm | Jul 23, 2026 7:05pm | Jul 23, 2026 7:55pm | Jul 23, 2026 8:09pm | Jul 23, 2026 8:09pm |  |  | Fair | No | Supply check and found customer experiencing low voltage reading 85v remade joint at pole and pothead using 2 linket 2 one bolt clamp voltage leave at premises 120v supply working ok
Non-Outage | J.E.26.07.26603 | C001863617 | Dean Smith | Hanover | Completed | Load_573743 | Orange Bay - 210 | Jul 23, 2026 3:31pm | Jul 23, 2026 3:54pm | Jul 23, 2026 8:44pm | Jul 23, 2026 8:44pm | Jul 23, 2026 8:44pm | Jul 23, 2026 8:45pm | Jul 23, 2026 8:45pm | Jul 23, 2026 8:45pm |  |  | Rains | No | Check and found ok
Outage | J.E.26.07.27190 | C001863611 | Dean Smith | Hanover | Completed | Load_264875 | Orange Bay - 210 | Jul 23, 2026 3:30pm | Jul 23, 2026 3:51pm | Jul 23, 2026 4:45pm | Jul 23, 2026 4:45pm | Jul 23, 2026 6:33pm | Jul 23, 2026 6:33pm | Jul 23, 2026 6:38pm | Jul 23, 2026 6:38pm | LeaningPole |  | Rains | No | Customer has electricity; Secondary 30/6 DE pole decay and broken at ground level, need change ASAP. Please forward to maintenance dept. orange bay board scheme, first left turn.....
Non-Outage | J.E.26.07.26641 | C001863608 | Richman Whyte | null | Completed | null | null | Jul 23, 2026 3:28pm | Jul 23, 2026 3:47pm | Jul 23, 2026 5:45pm | Jul 23, 2026 5:45pm | Jul 23, 2026 5:45pm | Jul 23, 2026 5:46pm | Jul 23, 2026 5:46pm | Jul 23, 2026 5:46pm |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.26746 | C001863609 | Oshane Warren | Westmoreland | Completed | Load_292071 | Paradise - 310 | Jul 23, 2026 3:28pm | Jul 23, 2026 3:35pm | Jul 23, 2026 5:11pm | Jul 23, 2026 5:11pm | Jul 23, 2026 5:20pm | Jul 23, 2026 5:21pm | Jul 23, 2026 5:25pm | Jul 23, 2026 5:25pm |  |  | Fair | No | Mr Richard stated that Crew should visit the location in morning with the correct amount of wire to carry out the reconnection
Outage | J.E.26.07.27112 | C001863610 | Romeo Brissett | St.James | Completed | Load_302110 | Bogue - 610 | Jul 23, 2026 3:28pm | Jul 23, 2026 3:29pm | Jul 23, 2026 4:19pm | Jul 23, 2026 4:19pm | Jul 23, 2026 4:34pm | Jul 23, 2026 4:28pm | Jul 23, 2026 4:45pm | Jul 23, 2026 4:45pm |  |  | Fair | No | Line patrolled and found power in the area, line was energize earlier, Customer meter was checked and found powered.
Outage | J.E.26.07.27263 | C001863607 | Derrick Dawkins | St.James | Completed | Load_246427 | Bogue - 310 | Jul 23, 2026 3:26pm | Jul 23, 2026 3:27pm | Jul 23, 2026 4:20pm | Jul 23, 2026 8:37pm | Jul 23, 2026 8:57pm | Jul 23, 2026 9:00pm | Jul 23, 2026 9:01pm | Jul 23, 2026 9:01pm |  |  | Fair | No | Premises closed
Outage | J.E.26.07.27409 | C001863606 | Derrick Dawkins | St.James | Completed | Load_253389 | Bogue - 310 | Jul 23, 2026 3:26pm | Jul 23, 2026 3:27pm | Jul 23, 2026 8:22pm | Jul 23, 2026 8:25pm | Jul 23, 2026 8:33pm | Jul 23, 2026 8:35pm | Jul 23, 2026 8:35pm | Jul 23, 2026 8:35pm | BrokenPole |  | Fair | No | Found street light broken in 2 by tree falling on it
Outage | J.E.26.07.27130 | C001863600 | Richman Whyte | Westmoreland | Completed | Load_262008 | Paradise - 110 | Jul 23, 2026 3:22pm | Jul 23, 2026 3:30pm | Jul 23, 2026 5:44pm | Jul 23, 2026 5:44pm | Jul 23, 2026 5:44pm | Jul 23, 2026 5:45pm | Jul 23, 2026 5:45pm | Jul 23, 2026 5:45pm |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.27184 | C001863598 | Roxroy Needham | St.Ann | Completed | Load_239508 | Cardiff Hall - 310 | Jul 23, 2026 3:22pm | Jul 23, 2026 3:22pm | Jul 23, 2026 6:03pm | Jul 23, 2026 6:03pm | Jul 23, 2026 6:04pm | Jul 23, 2026 6:05pm | Jul 23, 2026 6:05pm | Jul 23, 2026 6:05pm |  |  | Fair | No | Customer say light was restored
Outage | J.E.26.07.27230 | C001863599 | Richman Whyte | Westmoreland | Completed | Load_292176 | Paradise - 110 | Jul 23, 2026 3:22pm | Jul 23, 2026 3:30pm | Jul 23, 2026 6:36pm | Jul 23, 2026 6:36pm | Jul 23, 2026 6:36pm | Jul 23, 2026 6:44pm | Jul 23, 2026 6:45pm | Jul 23, 2026 6:45pm |  |  | Fair | No | Replace 8 amp junction fuse
Outage | J.E.26.07.27454 | C001863587 | Barnett Brown | Manchester | Completed | Load_255541 | Kendal - 210 | Jul 23, 2026 3:19pm | Jul 23, 2026 3:20pm | Jul 23, 2026 4:45pm | Jul 23, 2026 4:45pm | Jul 23, 2026 6:22pm | Jul 23, 2026 6:25pm | Jul 23, 2026 6:27pm | Jul 23, 2026 6:27pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.27048 | C001863581 | Romaine Roberts | St.Mary | Completed | Load_238891 | Annotto Bay - 310 | Jul 23, 2026 3:17pm | Jul 23, 2026 3:19pm | Jul 23, 2026 7:51pm | Jul 23, 2026 7:51pm | Jul 23, 2026 8:47pm | Jul 23, 2026 9:35pm | Jul 23, 2026 9:42pm | Jul 23, 2026 9:42pm |  |  | Fair | No | Found defective switch that need to be change attempts made to restore supply however was unable to complete day light attention needed
Outage | J.E.26.07.27148 | C001863582 | Romaine Roberts | St.Mary | Completed | Load_240255 | Annotto Bay - 310 | Jul 23, 2026 3:17pm | Jul 23, 2026 3:19pm | Jul 23, 2026 4:27pm | Jul 23, 2026 4:27pm | Jul 23, 2026 5:15pm | Jul 23, 2026 5:38pm | Jul 23, 2026 5:41pm | Jul 23, 2026 5:41pm |  |  | Fair | No | Disconnection was done at premises customer paid their light bill but there was still no light ,but it was a result of customer breaker turn off
Outage | J.E.26.07.27317 | C001863583 | Neckell Ormsby | St.Mary | Completed | Load_576595 | Highgate -110 | Jul 23, 2026 3:17pm | Jul 23, 2026 3:19pm | Jul 23, 2026 4:56pm | Jul 23, 2026 4:56pm | Jul 23, 2026 6:29pm | Jul 23, 2026 7:32pm | Jul 23, 2026 7:33pm | Jul 23, 2026 7:33pm |  |  | Fair | No | Patrol and found blown 10 amp junction fuse pole #479565 cut and remove bamboo tree limb from primary conductor replace 10 amp junction fuse
Outage | J.E.26.07.27325 | C001863584 | Barnett Brown | Manchester | Completed | Load_254176 | Kendal - 210 | Jul 23, 2026 3:17pm | Jul 23, 2026 3:20pm | Jul 23, 2026 6:28pm | Jul 23, 2026 6:28pm | Jul 23, 2026 8:25pm | Jul 23, 2026 9:19pm | Jul 23, 2026 9:21pm | Jul 23, 2026 9:21pm |  |  | Fair | No | Patrol line, found nothing, close two 40 amp trip saver, pole number 0131150
Non-Outage | J.E.26.07.26771 | C001863575 | Stephen Taylor | null | Completed | null | null | Jul 23, 2026 3:12pm | Jul 23, 2026 3:13pm | Jul 23, 2026 3:25pm | Jul 23, 2026 5:38pm | Jul 23, 2026 5:38pm | Jul 23, 2026 5:38pm | Jul 23, 2026 5:38pm | Jul 23, 2026 5:38pm | Fire |  | Fair | No | See junction link down no number on pole patrol a clear of tree of line and close up back junction with 10 amp fuse all customer is now okay
Non-Outage | J.E.26.07.27365 | C001863574 | Stephen Taylor | null | Completed | null | null | Jul 23, 2026 3:12pm | Jul 23, 2026 3:13pm | Jul 23, 2026 4:53pm | Jul 23, 2026 4:53pm | Jul 23, 2026 4:53pm | Jul 23, 2026 4:54pm | Jul 23, 2026 5:36pm | Jul 23, 2026 5:36pm |  |  | Fair | No | See junction link down no number on pole patrol a clear of tree of line and close up back junction with 10 amp fuse all customer is now okay
Outage | J.E.26.07.26671 | C001863572 | Stephen Taylor | St.Thomas | Completed | Load_268000 | Lysson - 410 | Jul 23, 2026 3:12pm | Jul 23, 2026 3:12pm | Jul 23, 2026 6:26pm | Jul 23, 2026 6:26pm | Jul 23, 2026 6:26pm | Jul 23, 2026 6:26pm | Jul 23, 2026 6:27pm | Jul 23, 2026 6:27pm |  |  | Fair | No | Contact customer and customer said that power was restored
Outage | J.E.26.07.27071 | C001863573 | Stephen Taylor | St.Thomas | Completed | Load_270158 | Lysson - 410 | Jul 23, 2026 3:12pm | Jul 23, 2026 3:12pm | Jul 23, 2026 6:28pm | Jul 23, 2026 6:28pm | Jul 23, 2026 6:28pm | Jul 23, 2026 6:28pm | Jul 23, 2026 6:28pm | Jul 23, 2026 6:28pm |  |  | Fair | No | Contact customer and customer said that power was restored
Outage | J.E.26.07.26777 | C001863569 | Stephen Taylor | St.Thomas | Completed | Load_245985 | Good Year - 110 | Jul 23, 2026 3:11pm | Jul 23, 2026 3:12pm | Jul 23, 2026 5:36pm | Jul 23, 2026 5:36pm | Jul 23, 2026 5:37pm | Jul 23, 2026 5:37pm | Jul 23, 2026 5:37pm | Jul 23, 2026 5:37pm | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | See junction link down no number on pole patrol a clear of tree of line and close up back junction with 10 amp fuse all customer is now okay
Outage | J.E.26.07.26890 | C001863570 | Stephen Taylor | St.Thomas | Completed | Load_248857 | Lysson - 410 | Jul 23, 2026 3:11pm | Jul 23, 2026 3:12pm | Jul 23, 2026 6:27pm | Jul 23, 2026 6:27pm | Jul 23, 2026 6:27pm | Jul 23, 2026 6:27pm | Jul 23, 2026 6:28pm | Jul 23, 2026 6:28pm |  |  | Fair | No | Contact customer and customer said that power was restored
Outage | J.E.26.07.27370 | C001863571 | Stephen Taylor | St.Thomas | Completed | Load_253050 | Lysson - 410 | Jul 23, 2026 3:11pm | Jul 23, 2026 3:12pm | Jul 23, 2026 5:47pm | Jul 23, 2026 6:16pm | Jul 23, 2026 6:16pm | Jul 23, 2026 6:16pm | Jul 23, 2026 6:23pm | Jul 23, 2026 6:23pm |  |  | Fair | No | Premise found okay
Outage | J.E.26.07.27185 | C001863557 | Roxroy Needham | St.Ann | Completed | Load_238156 | Cardiff Hall - 310 | Jul 23, 2026 3:05pm | Jul 23, 2026 3:21pm | Jul 23, 2026 3:51pm | Jul 23, 2026 3:51pm | Jul 23, 2026 5:45pm | Jul 23, 2026 6:03pm | Jul 23, 2026 6:03pm | Jul 23, 2026 6:03pm | BrokenWire |  | Fair | No | Splice and retention customer service wire
Outage | J.E.26.07.27221 | C001863556 | Roxroy Needham | St.Ann | Completed | Load_249861 | Cardiff Hall - 310 | Jul 23, 2026 3:05pm | Jul 23, 2026 3:21pm | Jul 23, 2026 3:27pm | Jul 23, 2026 3:27pm | Jul 23, 2026 3:48pm | Jul 23, 2026 3:50pm | Jul 23, 2026 3:50pm | Jul 23, 2026 3:50pm |  |  | Fair | No | Customer say issue was resolved
Outage | J.E.26.07.27215 | C001863542 | Christopher Edwards | KSAN | Completed | Load_258962 | Constant Spring - 410 | Jul 23, 2026 2:49pm | Jul 23, 2026 2:51pm | Jul 23, 2026 3:03pm | Jul 23, 2026 3:50pm | Jul 23, 2026 3:50pm | Jul 23, 2026 4:22pm | Jul 23, 2026 4:23pm | Jul 23, 2026 4:23pm |  |  | Fair | No | Customer was disconnected Supply has been restored to premises
Outage | J.E.26.07.27378 | C001863541 | Christopher Edwards | KSAN | Completed | Load_252601 | Constant Spring - 310 | Jul 23, 2026 2:49pm | Jul 23, 2026 2:51pm | Jul 23, 2026 3:07pm | Jul 23, 2026 3:07pm | Jul 23, 2026 3:07pm | Jul 23, 2026 3:49pm | Jul 23, 2026 3:49pm | Jul 23, 2026 3:49pm |  |  | Fair | No | Customer was disconnected for late payment Metering department was contacted and supply was restored
Non-Outage | J.E.26.07.27303 | C001863516 | Andrew Powell | null | Completed | null | null | Jul 23, 2026 2:22pm | Jul 23, 2026 2:26pm | Jul 23, 2026 2:39pm | Jul 23, 2026 2:39pm | Jul 23, 2026 3:28pm | Jul 23, 2026 4:26pm | Jul 23, 2026 4:30pm | Jul 23, 2026 4:30pm | Fire |  | Fair | No | Found burnt up PMC box with two 3 wire meter. Isolate and close 25 kva transformer circuit to repair burnt off secondary phase jumper joints using two clamps, voltage reading 115v-115v phase to neutral 230v cross phase. Two customers affected, please refer to field service department.
Non-Outage | J.E.26.07.23693 | C001863505 | Tyrese Williams | St.Ann | Completed | Load_243438 | Cardiff Hall - 310 | Jul 23, 2026 2:14pm | Jul 23, 2026 2:15pm | Jul 23, 2026 2:19pm | Jul 23, 2026 2:23pm | Jul 23, 2026 3:05pm | Jul 23, 2026 3:07pm | Jul 23, 2026 3:07pm | Jul 23, 2026 3:07pm |  |  | Fair | No | Meter found burnt recommend to be change customer only getting 110 at the premises
Outage | J.E.26.07.26784 | C001863498 | Moses Elliston | St.Catherine | Completed | Load_568931 | Twickenham - 310 | Jul 23, 2026 2:08pm | Jul 23, 2026 2:08pm | Jul 23, 2026 4:19pm | Jul 23, 2026 4:19pm | Jul 23, 2026 4:19pm | Jul 23, 2026 4:19pm | Jul 23, 2026 4:20pm | Jul 23, 2026 4:20pm |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.07.27118 | C001863496 | Derrick Dawkins | St.James | Completed | Load_246965 | Bogue - 310 | Jul 23, 2026 2:07pm | Jul 23, 2026 7:05pm | Jul 23, 2026 8:21pm | Jul 23, 2026 8:21pm | Jul 23, 2026 8:21pm | Jul 23, 2026 8:21pm | Jul 23, 2026 8:22pm | Jul 23, 2026 8:22pm |  |  | Fair | No | Checked and found ok
Outage | J.E.26.07.27188 | C001863497 | Derrick Dawkins | St.James | Completed | Load_256381 | Bogue - 310 | Jul 23, 2026 2:07pm | Jul 23, 2026 3:27pm | Jul 23, 2026 6:10pm | Jul 23, 2026 6:10pm | Jul 23, 2026 6:19pm | Jul 23, 2026 6:20pm | Jul 23, 2026 6:21pm | Jul 23, 2026 6:21pm |  |  | Fair | No | Calls to customer went unanswered cannot locate customer
Non-Outage | J.E.26.07.27255 | C001863484 | Romeo Brissett | null | Completed | null | null | Jul 23, 2026 1:52pm | Jul 23, 2026 2:06pm | Jul 23, 2026 2:16pm | Jul 23, 2026 2:16pm | Jul 23, 2026 2:36pm | Jul 23, 2026 2:40pm | Jul 23, 2026 3:17pm | Jul 23, 2026 3:17pm |  |  | Rains | No | Customer stated they didn’t make any report.
Outage | J.E.26.07.27248 | C001863483 | Romeo Brissett | St.James | Completed | Load_238926 | Bogue - 610 | Jul 23, 2026 1:52pm | Jul 23, 2026 2:06pm | Jul 23, 2026 3:17pm | Jul 23, 2026 3:17pm | Jul 23, 2026 3:17pm | Jul 23, 2026 4:17pm | Jul 23, 2026 4:19pm | Jul 23, 2026 4:19pm | LowHangingWires |  | Rains | No | Found primary and secondary lines hanging low, Isolated (1)15 kva transformer, removed illegal connections, attached secondary to existing telephone pole, retention secondary and reset (1)15KVA transformer fuse.
Outage | J.E.26.07.26464 | C001863463 | Richard Nicholas | St.Catherine | Completed | Load_243462 | Twickenham - 410 | Jul 23, 2026 1:24pm | Jul 23, 2026 1:24pm | Jul 23, 2026 3:25pm | Jul 23, 2026 3:25pm | Jul 23, 2026 3:25pm | Jul 23, 2026 3:25pm | Jul 23, 2026 3:26pm | Jul 23, 2026 3:26pm |  |  | Fair | No | Found ok
Outage | J.E.26.07.27142 | C001863460 | Jermaine Williams | Clarendon | Completed | Load_240881 | Parnassus - 210 | Jul 23, 2026 1:17pm | Jul 23, 2026 4:04pm | Jul 23, 2026 4:38pm | Jul 23, 2026 4:38pm | Jul 23, 2026 7:09pm | Jul 23, 2026 6:00pm | Jul 23, 2026 7:10pm | Jul 23, 2026 7:10pm | BrokenWire |  | Fair | No | Premises found ok.
Non-Outage | J.E.26.07.26963 | C001863455 | Tajay Bernard | null | Completed | null | null | Jul 23, 2026 1:12pm | Jul 23, 2026 1:12pm | Jul 23, 2026 2:49pm | Jul 23, 2026 2:49pm | Jul 23, 2026 2:50pm | Jul 23, 2026 2:50pm | Jul 23, 2026 2:50pm | Jul 23, 2026 2:50pm |  |  | Fair | No | Related to previous call job number 26991
Non-Outage | J.E.26.07.24840 | C001863448 | Romeo Brissett | null | Completed | null | null | Jul 23, 2026 1:04pm | Jul 23, 2026 1:37pm | Jul 23, 2026 2:11pm | Jul 23, 2026 2:11pm | Jul 23, 2026 2:11pm | Jul 23, 2026 11:00am | Jul 23, 2026 2:16pm | Jul 23, 2026 2:16pm | LowHangingWires |  | Fair | No | Found one(1) pole span of secondary bottom phase hanging low due hurricane Melissa. We are unable to retention line, line is tied up with cable strand, we have already detached some of the wire off the cable however it Need bucket truck to safely complete it, please send to bucket truck team.
Outage | J.E.26.07.26991 | C001863447 | Tajay Bernard | Hanover | Completed | Load_230038 | Orange Bay - 310 | Jul 23, 2026 1:02pm | Jul 23, 2026 1:09pm | Jul 23, 2026 1:54pm | Jul 23, 2026 1:54pm | Jul 23, 2026 2:42pm | Jul 23, 2026 2:48pm | Jul 23, 2026 2:49pm | Jul 23, 2026 2:49pm |  |  | Fair | No | Area check and found okay
Outage | J.E.26.07.26944 | C001863436 | Marlon Brown | Trelawny | Completed | Load_252424 | Duncans - 210 | Jul 23, 2026 1:00pm | Jul 23, 2026 1:02pm | Jul 23, 2026 2:59pm | Jul 23, 2026 2:59pm | Jul 23, 2026 2:59pm | Jul 23, 2026 3:00pm | Jul 23, 2026 3:00pm | Jul 23, 2026 3:00pm |  |  | Fair | No | Same as call number 26310
Outage | J.E.26.07.27147 | C001863437 | Marlon Brown | Trelawny | Completed | Load_250805 | Greenwood - 110 | Jul 23, 2026 1:00pm | Jul 24, 2026 8:12am | Jul 24, 2026 8:31am | Jul 24, 2026 8:31am | Jul 24, 2026 9:46am | Jul 24, 2026 9:47am | Jul 24, 2026 9:47am | Jul 24, 2026 9:47am |  |  | Fair | No | Unable to locate customer via telephone nor direction
Outage | J.E.26.07.26922 | C001863435 | Marlon Brown | Trelawny | Completed | Load_573822 | Duncans - 110 | Jul 23, 2026 12:59pm | Jul 23, 2026 1:00pm | Jul 23, 2026 1:13pm | Jul 23, 2026 1:14pm | Jul 23, 2026 1:43pm | Jul 23, 2026 1:54pm | Jul 23, 2026 1:54pm | Jul 23, 2026 1:54pm |  |  | Fair | No | Replaced 5amps 50kva Transformer fuse Voltage found at pothead 120/120/208=240/239/241vVoltage leaving at pothead 120/120/208=240/239/241v.
Non-Outage | J.E.26.07.26502 | C001863434 | Derrick Grubb | St.Thomas | Completed | Load_253050 | Lysson - 410 | Jul 23, 2026 12:58pm | Jul 23, 2026 12:58pm | Jul 23, 2026 1:46pm | Jul 23, 2026 1:46pm | Jul 23, 2026 2:09pm | Jul 23, 2026 2:56pm | Jul 23, 2026 2:56pm | Jul 23, 2026 2:56pm |  |  | Fair | No | Troubleshoot and clear corrosion at transformer drop lead using two one bolt clamps. Voltage readings when leaving 116v, 117v, 233v.
Outage | J.E.26.07.26689 | C001863433 | Richard Nicholas | St.Catherine | Completed | Load_250042 | Twickenham - 410 | Jul 23, 2026 12:57pm | Jul 23, 2026 1:48pm | Jul 23, 2026 3:26pm | Jul 23, 2026 3:26pm | Jul 23, 2026 3:26pm | Jul 23, 2026 3:26pm | Jul 23, 2026 3:27pm | Jul 23, 2026 3:27pm |  |  | Fair | No | Found ok
Outage | J.E.26.07.26948 | C001863429 | Kaydon Taylor | KSAN | Completed | Load_258921 | Constant Spring - 210 | Jul 23, 2026 12:51pm | Jul 23, 2026 12:53pm | Jul 23, 2026 2:20pm | Jul 23, 2026 2:20pm | Jul 23, 2026 3:34pm | Jul 23, 2026 3:43pm | Jul 23, 2026 3:44pm | Jul 23, 2026 3:44pm | LeaningPole |  | Rains | No | Defective 40’ pole #0077232
Outage | J.E.26.07.27011 | C001863398 | Kaydon Taylor | KSAN | Completed | Load_239202 | Constant Spring - 210 | Jul 23, 2026 12:40pm | Jul 23, 2026 12:42pm | Jul 23, 2026 7:05pm | Jul 23, 2026 9:33pm | Jul 23, 2026 9:33pm | Jul 23, 2026 9:34pm | Jul 23, 2026 9:34pm | Jul 23, 2026 9:34pm |  |  | Fair | No | Unable to get customer via telecommunication
Outage | J.E.26.07.27138 | C001863397 | Christopher Edwards | KSAN | Completed | Load_240180 | Constant Spring - 410 | Jul 23, 2026 12:40pm | Jul 23, 2026 12:41pm | Jul 23, 2026 12:52pm | Jul 23, 2026 12:54pm | Jul 23, 2026 12:54pm | Jul 23, 2026 1:40pm | Jul 23, 2026 1:41pm | Jul 23, 2026 1:41pm |  |  | Fair | No | Customer was disconnected for late payment Metering department was contacted and service was restored
Outage | J.E.26.07.27124 | C001863396 | Milton Charlton | KSAN | Completed | Load_265074 | West Kings House - 310 | Jul 23, 2026 12:39pm | Jul 23, 2026 12:42pm | Jul 23, 2026 3:53pm | Jul 23, 2026 3:53pm | Jul 23, 2026 4:13pm | Jul 23, 2026 4:20pm | Jul 23, 2026 4:24pm | Jul 23, 2026 4:24pm |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.07.26849 | C001863365 | Donald Cunningham | St.Catherine | Completed | Load_255125 | Rhodens Pen - 210 | Jul 23, 2026 12:21pm | Jul 23, 2026 5:21pm | Jul 23, 2026 7:12pm | Jul 23, 2026 7:12pm | Jul 23, 2026 8:23pm | Jul 23, 2026 8:34pm | Jul 23, 2026 8:37pm | Jul 23, 2026 8:37pm |  |  | Fair | No | Area found ok with supply customer premises not located customer not reachable
Outage | J.E.26.07.26784 | C001863350 | Richard Grant | St.Catherine | Completed | Load_568931 | Twickenham - 310 | Jul 23, 2026 12:06pm | Jul 23, 2026 12:59pm | Jul 23, 2026 1:03pm | Jul 23, 2026 1:03pm | Jul 23, 2026 1:49pm | Jul 23, 2026 1:54pm | Jul 23, 2026 1:54pm | Jul 23, 2026 1:54pm |  |  | Fair | No | Customer is unable to tap up prepaid meter. Please refer call to Moses
Non-Outage | J.E.26.07.07850 | C001863342 | Locksley Allen | St.Mary | Completed | Load_256416 | Highgate -110 | Jul 23, 2026 12:03pm | Jul 23, 2026 12:03pm | Jul 23, 2026 1:48pm | Jul 23, 2026 2:40pm | Jul 23, 2026 2:40pm | Jul 23, 2026 2:46pm | Jul 23, 2026 2:49pm | Jul 23, 2026 2:49pm |  |  | Fair | No | No low voltage problem found at the premises.Voltage at meter socket phase to phase 223v. Phase to neutral 110&115v Customer needs to change the meter socket,socket is corroded.The current in this area is fluctuating,especially when the breeze is blowing The secondary line needs to be bush. Check
Non-Outage | J.E.26.07.09499 | C001863341 | Locksley Allen | St.Mary | Completed | Load_244524 | Highgate -110 | Jul 23, 2026 12:03pm | Jul 23, 2026 12:03pm | Jul 23, 2026 2:50pm | Jul 23, 2026 2:51pm | Jul 23, 2026 2:52pm | Jul 23, 2026 2:54pm | Jul 23, 2026 2:54pm | Jul 23, 2026 2:54pm |  |  | Rains | No | Customer said JPS came and corrected the problem from sometime ago
Non-Outage | J.E.26.07.25105 | C001863343 | Locksley Allen | St.Mary | Completed | Load_265580 | Highgate - 210 | Jul 23, 2026 12:03pm | Jul 23, 2026 12:03pm | Jul 23, 2026 2:55pm | Jul 23, 2026 4:32pm | Jul 23, 2026 4:32pm | Jul 23, 2026 4:37pm | Jul 23, 2026 4:38pm | Jul 23, 2026 4:38pm |  |  | Fair | No | Pothead found corroded,and was clean up Voltage at meter socket phase to phase. Phase to neutral 114&112vThe pimento tree and several other trees are entangle in the secondary line
Outage | J.E.26.07.26702 | C001863331 | Rodclif Dawkins | Portmore | Completed | Load_579367 | Naggo Head - 610 | Jul 23, 2026 11:59am | Jul 23, 2026 4:32pm | Jul 23, 2026 7:09pm | Jul 23, 2026 7:31pm | Jul 23, 2026 8:26pm | Jul 23, 2026 8:59pm | Jul 23, 2026 8:59pm | Jul 23, 2026 8:59pm |  |  | Fair | No | Customer found okay
Outage | J.E.26.07.26992 | C001863330 | Kaydon Taylor | KSAN | Completed | Load_245203 | Constant Spring - 210 | Jul 23, 2026 11:59am | Jul 23, 2026 12:00pm | Jul 23, 2026 9:33pm | Jul 23, 2026 9:33pm | Jul 23, 2026 9:33pm | Jul 23, 2026 9:33pm | Jul 23, 2026 9:33pm | Jul 23, 2026 9:33pm |  |  | Fair | No | Found okay
Outage | J.E.26.07.27078 | C001863320 | Neville Spencer | Clarendon | Completed | Load_239165 | Parnassus - 310 | Jul 23, 2026 11:52am | Jul 23, 2026 11:52am | Jul 23, 2026 1:29pm | Jul 23, 2026 1:29pm | Jul 23, 2026 1:36pm | Jul 23, 2026 1:36pm | Jul 23, 2026 3:42pm | Jul 23, 2026 3:42pm | Fire |  | Fair | No | Open 3, 60 amp trip saver switch at pole # 585474 to install pole top lap and insulators on intermediate pole.
Outage | J.E.26.07.27044 | C001863300 | Neville Spencer | Clarendon | Completed | Load_237834 | Parnassus - 210 | Jul 23, 2026 11:43am | Jul 23, 2026 11:44am | Jul 23, 2026 12:46pm | Jul 23, 2026 12:46pm | Jul 23, 2026 12:46pm | Jul 23, 2026 12:46pm | Jul 23, 2026 12:50pm | Jul 23, 2026 12:50pm |  |  | Fair | No | Open 25 kva xmfr at pole #011814 splice and retention broken secondary phase Conductor used 50 ft wire, 2 clamps, 2 , preform , 1 , D iron supply restored.
Outage | J.E.26.07.27052 | C001863301 | Neville Spencer | Clarendon | Completed | Load_267964 | Parnassus - 310 | Jul 23, 2026 11:43am | Jul 23, 2026 11:44am | Jul 23, 2026 3:43pm | Jul 23, 2026 3:43pm | Jul 23, 2026 3:43pm | Jul 23, 2026 3:43pm | Jul 23, 2026 3:46pm | Jul 23, 2026 3:46pm |  |  | Fair | No | Open 3, 60 amp trip saver switch at pole #. 585474 to install pole top lap and insulators on intermediate pole supply restored.
Outage | J.E.26.07.26909 | C001863298 | Fitzroy Turner | KSAS | Completed | Load_242005 | Rockfort - 410 | Jul 23, 2026 11:42am | Jul 23, 2026 11:47am | Jul 23, 2026 12:10pm | Jul 23, 2026 12:10pm | Jul 23, 2026 12:58pm | Jul 23, 2026 1:12pm | Jul 23, 2026 1:17pm | Jul 23, 2026 1:17pm |  |  | Fair | No | Pole #565919 found two 25amps junction fuse blown at the intersection windward rd and outlook avenue cause by dislodge conductor at outlook avenue use one 2/0 preform to carry out repair supply restored to areas
Outage | J.E.26.07.27030 | C001863299 | Rusean Allen | KSAS | Completed | Load_1002676 | Cane River - 410 | Jul 23, 2026 11:42am | Jul 23, 2026 11:47am | Jul 23, 2026 12:45pm | Jul 23, 2026 12:45pm | Jul 23, 2026 1:01pm | Jul 23, 2026 1:02pm | Jul 23, 2026 1:41pm | Jul 23, 2026 1:41pm | TreeContact |  | Fair | No | Customer was advised to cut tree hanging over house
Outage | J.E.26.07.26051 | C001863294 | Moses Elliston | St.Catherine | Completed | Load_246045 | Tredegar - 510 | Jul 23, 2026 11:39am | Jul 23, 2026 11:39am | Jul 23, 2026 3:09pm | Jul 23, 2026 3:09pm | Jul 23, 2026 3:09pm | Jul 23, 2026 3:10pm | Jul 23, 2026 3:12pm | Jul 23, 2026 3:12pm |  |  | Fair | No | Customer reported wrong account.Should be meter #2806804.
Outage | J.E.26.07.27036 | C001863293 | Raymond Lewis | St.Ann | Completed | Load_239944 | Roaring River - 410 | Jul 23, 2026 11:38am | Jul 23, 2026 11:38am | Jul 23, 2026 1:10pm | Jul 23, 2026 1:10pm | Jul 23, 2026 2:26pm | Jul 23, 2026 2:28pm | Jul 23, 2026 2:28pm | Jul 23, 2026 2:28pm | BrokenWire |  | Fair | No | Premises found ok
Outage | J.E.26.07.26974 | C001863292 | Marlon Brown | Trelawny | Completed | Load_295092 | Duncans - 110 | Jul 23, 2026 11:37am | Jul 23, 2026 11:39am | Jul 23, 2026 2:58pm | Jul 23, 2026 2:58pm | Jul 23, 2026 2:58pm | Jul 23, 2026 2:59pm | Jul 23, 2026 2:59pm | Jul 23, 2026 2:59pm |  |  | Fair | No | Schedule outage
Outage | J.E.26.07.26981 | C001863291 | Marlon Brown | Trelawny | Completed | Load_295089 | Duncans - 110 | Jul 23, 2026 11:37am | Jul 23, 2026 11:39am | Jul 23, 2026 2:57pm | Jul 23, 2026 2:57pm | Jul 23, 2026 2:57pm | Jul 23, 2026 2:57pm | Jul 23, 2026 2:57pm | Jul 23, 2026 2:57pm |  |  | Fair | No | Schedule outage
Outage | J.E.26.07.26546 | C001863286 | Raymond Lewis | St.Ann | Completed | Load_252213 | Cardiff Hall - 210 | Jul 23, 2026 11:32am | Jul 23, 2026 11:37am | Jul 23, 2026 2:28pm | Jul 23, 2026 2:28pm | Jul 23, 2026 2:42pm | Jul 23, 2026 2:43pm | Jul 23, 2026 2:43pm | Jul 23, 2026 2:43pm |  |  | Fair | No | Supply restored to the site
Non-Outage | J.E.26.07.25068 | C001863278 | Horace Malcolm | St.James | Completed | Load_412876 | Bogue - 310 | Jul 23, 2026 11:26am | Jul 23, 2026 11:27am | Jul 23, 2026 11:43am | Jul 23, 2026 11:43am | Jul 23, 2026 11:43am | Jul 23, 2026 11:44am | Jul 23, 2026 11:44am | Jul 23, 2026 11:44am |  |  | Fair | No | Check and premises ok
Outage | J.E.26.07.26946 | C001863275 | Richard Samuda | Manchester | Completed | Load_251290 | Spur Tree - 310 | Jul 23, 2026 11:23am | Jul 23, 2026 6:43pm | Jul 23, 2026 8:33pm | Jul 23, 2026 8:38pm | Jul 23, 2026 8:48pm | Jul 23, 2026 9:30pm | Jul 23, 2026 9:29pm | Jul 23, 2026 9:29pm |  |  | Fair | No | Customer was disconnected for bad death
Non-Outage | J.E.26.07.26722 | C001863272 | Damion Reid | Manchester | Completed | Load_1002547 | Kendal - 310 | Jul 23, 2026 11:17am | Jul 23, 2026 11:18am | Jul 23, 2026 12:30pm | Jul 23, 2026 12:31pm | Jul 23, 2026 1:47pm | Jul 23, 2026 2:32pm | Jul 23, 2026 2:34pm | Jul 23, 2026 2:34pm |  |  | Fair | No | Blown 7amp fuse found for 100kva transformer line patrol nothing was found blown fuse replace
Outage | J.E.26.07.26782 | C001863269 | Richard Samuda | Manchester | Completed | Load_270226 | Spur Tree - 210 | Jul 23, 2026 11:13am | Jul 23, 2026 3:33pm | Jul 23, 2026 3:55pm | Jul 23, 2026 3:55pm | Jul 23, 2026 3:58pm | Jul 23, 2026 4:43pm | Jul 23, 2026 4:44pm | Jul 23, 2026 4:44pm | BrokenWire |  | Fair | No | Reconnect customer service wire to lower phase of secondary line that was broken off causing customer to experience single phase using one 1bolt clamp customer back to normal voltage 116/118/234
Non-Outage | J.E.26.07.26583 | C001863254 | Neville Spencer | null | Completed | null | null | Jul 23, 2026 10:57am | Jul 23, 2026 10:58am | Jul 23, 2026 11:12am | Jul 23, 2026 11:12am | Jul 23, 2026 11:29am | Jul 23, 2026 11:30am | Jul 23, 2026 12:45pm | Jul 23, 2026 12:45pm | Fire |  | Fair | No | Open 25 kva xmfr at pole # 011814 splice and retention broken secondary phase Conductor used 50 ft wire,2 ,clamps 1, D iron , 2, preform supply restored.
Outage | J.E.26.07.26059 | C001863242 | Neville Spencer | Clarendon | Completed | Load_254405 | Parnassus - 210 | Jul 23, 2026 10:51am | Jul 23, 2026 10:51am | Jul 23, 2026 11:05am | Jul 23, 2026 11:05am | Jul 23, 2026 11:08am | Jul 23, 2026 11:08am | Jul 23, 2026 11:10am | Jul 23, 2026 11:10am |  |  | Fair | No | Renew blown 30 amp j/ fuse at pole #568668 supply restored.
Outage | J.E.26.07.26788 | C001863241 | Floyd Taylor | Trelawny | Completed | Load_258323 | Greenwood - 210 | Jul 23, 2026 10:50am | Jul 23, 2026 10:51am | Jul 23, 2026 3:11pm | Jul 23, 2026 3:12pm | Jul 23, 2026 3:59pm | Jul 23, 2026 4:02pm | Jul 23, 2026 4:02pm | Jul 23, 2026 4:02pm | Fire |  | Fair | No | Remake joint at pole using 1pg clamp , voltage readings left 112,115,223
Non-Outage | J.E.26.07.18121 | C001863240 | Tajay Bernard | Hanover | Completed | Load_250960 | Orange Bay - 310 | Jul 23, 2026 10:47am | Jul 23, 2026 10:48am | Jul 23, 2026 11:02am | Jul 23, 2026 11:11am | Jul 23, 2026 11:58am | Jul 23, 2026 12:25pm | Jul 23, 2026 12:29pm | Jul 23, 2026 12:29pm |  |  | Fair | No | Clean and remake joints at jps pole use 3 clamps Voltage found 109/103/212Voltage left 112/112/224
Non-Outage | J.E.26.07.26543 | C001863229 | Milton Charlton | KSAN | Completed | Load_258324 | Hope - 510 | Jul 23, 2026 10:45am | Jul 23, 2026 12:48pm | Jul 23, 2026 3:19pm | Jul 23, 2026 3:19pm | Jul 23, 2026 3:50pm | Jul 23, 2026 3:50pm | Jul 23, 2026 3:53pm | Jul 23, 2026 3:53pm |  |  | Fair | No | Refused and reclosed 20 amps junction blown at pole#( no pole#) using one 30 amps fuse.
Non-Outage | J.E.26.07.26696 | C001863228 | Fredrick Hamilton | KSAN | Completed | Load_265507 | Washington Blvd - 810 | Jul 23, 2026 10:45am | Jul 23, 2026 10:47am | Jul 23, 2026 10:55am | Jul 23, 2026 11:34am | Jul 23, 2026 11:58am | Jul 23, 2026 12:20pm | Jul 23, 2026 12:20pm | Jul 23, 2026 12:20pm |  |  | Fair | No | 117.2v obtained Corrosion detected on customer installation Customer advised
Non-Outage | J.E.26.07.26744 | C001863227 | Rochaine Hussey | KSAN | Completed | Load_266471 | Constant Spring - 410 | Jul 23, 2026 10:45am | Jul 23, 2026 10:46am | Jul 23, 2026 11:21am | Jul 23, 2026 11:23am | Jul 23, 2026 11:23am | Jul 23, 2026 11:26am | Jul 23, 2026 11:28am | Jul 23, 2026 11:28am |  |  | Fair | No | Customer meter is defective and needs to be changed ,customer is getting a single phase and is say it make the light bill goes up Referring to the field service team and customer is unable to use equipment
Non-Outage | J.E.26.07.26754 | C001863230 | Rochaine Hussey | KSAN | Completed | Load_250229 | Constant Spring - 410 | Jul 23, 2026 10:45am | Jul 23, 2026 10:46am | Jul 23, 2026 11:30am | Jul 23, 2026 1:30pm | Jul 23, 2026 1:52pm | Jul 23, 2026 1:53pm | Jul 23, 2026 1:53pm | Jul 23, 2026 1:53pm |  |  | Fair | No | Unable to locate customer was called multiple times no answer
Non-Outage | J.E.26.07.26865 | C001863231 | Rochaine Hussey | KSAN | Completed | Load_249915 | Constant Spring - 410 | Jul 23, 2026 10:45am | Jul 23, 2026 10:46am | Jul 23, 2026 2:54pm | Jul 23, 2026 2:54pm | Jul 23, 2026 2:54pm | Jul 23, 2026 3:27pm | Jul 23, 2026 3:28pm | Jul 23, 2026 3:28pm |  |  | Fair | No | Mid span on neutral wire needs to be checkBucket truck needed
Outage | J.E.26.07.26708 | C001863226 | Omar King | St.Ann | Completed | Load_303102 | Ocho Rios - 410 | Jul 23, 2026 10:45am | Jul 23, 2026 10:46am | Jul 23, 2026 10:58am | Jul 23, 2026 10:58am | Jul 23, 2026 12:03pm | Jul 23, 2026 12:43pm | Jul 23, 2026 12:44pm | Jul 23, 2026 12:44pm |  |  | Fair | No | Please refer to field service to resolve matter only customer with out supply on the plaza
Outage | J.E.26.07.26749 | C001863199 | Christopher Edwards | KSAN | Completed | Load_244539 | Constant Spring - 410 | Jul 23, 2026 10:32am | Jul 23, 2026 10:54am | Jul 23, 2026 11:06am | Jul 23, 2026 12:22pm | Jul 23, 2026 12:33pm | Jul 23, 2026 12:52pm | Jul 23, 2026 12:52pm | Jul 23, 2026 12:52pm |  |  | Fair | No | Premises closed unable to reach customer by phone
Outage | J.E.26.07.26750 | C001863200 | Christopher Edwards | KSAN | Completed | Load_264739 | Constant Spring - 410 | Jul 23, 2026 10:32am | Jul 23, 2026 10:54am | Jul 23, 2026 11:06am | Jul 23, 2026 11:09am | Jul 23, 2026 12:04pm | Jul 23, 2026 12:21pm | Jul 23, 2026 12:22pm | Jul 23, 2026 12:22pm |  |  | Fair | No | Customer was disconnected for late payment Metering department was contacted and supply has returned to premises
Outage | J.E.26.07.26759 | C001863198 | Christopher Edwards | KSAN | Completed | Load_248715 | Washington Blvd - 610 | Jul 23, 2026 10:31am | Jul 23, 2026 5:31pm | Jul 23, 2026 6:57pm | Jul 23, 2026 7:12pm | Jul 23, 2026 7:36pm | Jul 23, 2026 7:41pm | Jul 23, 2026 7:42pm | Jul 23, 2026 7:42pm |  |  | Fair | No | Unable to reach customer by phone Supply is in the area
Outage | J.E.26.07.26657 | C001863155 | Neville Spencer | Clarendon | Completed | Load_569742 | Parnassus - 210 | Jul 23, 2026 10:06am | Jul 23, 2026 10:06am | Jul 23, 2026 1:09pm | Jul 23, 2026 1:09pm | Jul 23, 2026 1:26pm | Jul 23, 2026 1:26pm | Jul 23, 2026 1:28pm | Jul 23, 2026 1:28pm |  |  | Fair | No | Unable to locate customer.
Outage | J.E.26.07.26558 | C001863151 | Wan Carlos Scarlett | St.Catherine | Completed | Load_243320 | Twickenham - 210 | Jul 23, 2026 10:04am | Jul 23, 2026 10:04am | Jul 23, 2026 11:05am | Jul 23, 2026 11:05am | Jul 23, 2026 11:33am | Jul 23, 2026 12:16pm | Jul 23, 2026 12:19pm | Jul 23, 2026 12:19pm |  |  | Fair | No | Found customer 2 wire service at pothead with phase corroded use one Penn union at service wire phase reading 115
Outage | J.E.26.07.26515 | C001863150 | Floyd Taylor | St.James | Completed | Load_245469 | Bogue - 310 | Jul 23, 2026 10:03am | Jul 23, 2026 10:05am | Jul 23, 2026 12:46pm | Jul 23, 2026 12:46pm | Jul 23, 2026 2:17pm | Jul 23, 2026 3:10pm | Jul 23, 2026 3:10pm | Jul 23, 2026 3:10pm |  |  | Fair | No | Cut tree from line and replace two fuse 1-8amp and 1-3 amp
Outage | J.E.26.07.26703 | C001863149 | Wan Carlos Scarlett | Portmore | Completed | Load_1003660 | Naggo Head - 610 | Jul 23, 2026 10:02am | Jul 23, 2026 10:02am | Jul 23, 2026 12:19pm | Jul 23, 2026 12:19pm | Jul 23, 2026 12:54pm | Jul 23, 2026 1:50pm | Jul 23, 2026 2:01pm | Jul 23, 2026 2:01pm |  |  | SevereWind | No | Refuse 2 65 Amps Junction pole #617072 also refuse 2 50 Amps junction no pole # was found refused 2 40 Amps junction no pole # was found refuse 2 30 Amps junction no pole # was found refuse 2 15 Amp junction no pole # was found
Non-Outage | J.E.26.07.24840 | C001863129 | Romeo Brissett | null | Completed | null | null | Jul 23, 2026 9:54am | Jul 23, 2026 9:55am | Jul 23, 2026 10:35am | Jul 23, 2026 10:35am | Jul 23, 2026 10:56am | Jul 23, 2026 11:00am | Jul 23, 2026 11:10am | Jul 23, 2026 11:10am | LowHangingWires |  | Fair | No | Found secondary bottom phase hanging low and tied up with cable wires due hurricane Melissa. Please send to bucket team. No customer supplies is affected by the issue and no short circuit is on the circuit due to the issue, conductor just needs to be clear from telephone lines and retention.
Non-Outage | J.E.26.07.09515 | C001863123 | Orville Lee | Portmore | Completed | Load_253869 | Naggo Head - 510 | Jul 23, 2026 9:46am | Jul 23, 2026 9:46am | Jul 23, 2026 10:00am | Jul 23, 2026 10:06am | Jul 23, 2026 10:52am | Jul 23, 2026 11:02am | Jul 23, 2026 11:07am | Jul 23, 2026 11:07am |  |  | Fair | No | Voltage at drop lead 119V118V238VMultiple joints seen on open secondary Voltage after joints 104V115V229VRefer to maintenance
Non-Outage | J.E.26.07.26492 | C001863117 | Richard Nicholas | null | Completed | null | null | Jul 23, 2026 9:44am | Jul 23, 2026 9:44am | Jul 23, 2026 11:56am | Jul 23, 2026 11:56am | Jul 23, 2026 12:59pm | Jul 23, 2026 12:59pm | Jul 23, 2026 1:02pm | Jul 23, 2026 1:02pm |  |  | Fair | No | Replaced blown 30amp junctions fuse at the intersection.replaced missing junctions fuse holder with 10amp junctions fuse at the 3phase T-off to the premises and replaced missing 50kva transformer fuse holder with 5amp fuse.voltage reading 115,116,231,191,231 and 230v..
Outage | J.E.26.07.26663 | C001863103 | Tajay Bernard | Hanover | Completed | Load_302758 | Orange Bay - 310 | Jul 23, 2026 9:40am | Jul 23, 2026 10:48am | Jul 23, 2026 11:03am | Jul 23, 2026 11:10am | Jul 23, 2026 11:10am | Jul 23, 2026 11:11am | Jul 23, 2026 11:11am | Jul 23, 2026 11:11am |  |  | Fair | No | Customer stated that power was restored
Outage | J.E.26.07.26508 | C001863102 | Raymond Lewis | St.Ann | Completed | Load_574533 | Roaring River - 210 | Jul 23, 2026 9:38am | Jul 23, 2026 9:39am | Jul 23, 2026 11:46am | Jul 23, 2026 11:46am | Jul 23, 2026 11:46am | Jul 23, 2026 11:48am | Jul 23, 2026 11:48am | Jul 23, 2026 11:48am | BrokenWire |  | Fair | No | Phone not answering
Non-Outage | J.E.26.07.21916 | C001863099 | Richard Grant | St.Catherine | Completed | Load_574680 | Tredegar - 210 | Jul 23, 2026 9:37am | Jul 23, 2026 9:37am | Jul 23, 2026 10:48am | Jul 23, 2026 11:19am | Jul 23, 2026 11:19am | Jul 23, 2026 11:56am | Jul 23, 2026 11:56am | Jul 23, 2026 11:56am |  |  | Fair | No | Broken service neutral found at midspan connection causing high voltage to be at premises. 2 onebolt clamps and 3 for service neutral used to correct fault. Customer complained about damage appliances. Kindly send email to claims department. 115 115 230 voltages left at premises. Premises left okay
Non-Outage | J.E.26.07.08883 | C001863097 | Orville Lee | Portmore | Completed | Load_268319 | Naggo Head - 610 | Jul 23, 2026 9:36am | Jul 23, 2026 9:36am | Jul 23, 2026 10:00am | Jul 23, 2026 11:08am | Jul 23, 2026 11:43am | Jul 23, 2026 12:50pm | Jul 23, 2026 12:53pm | Jul 23, 2026 12:53pm |  |  | Fair | No | Checks made and found pothead and secondary lines corroded Four one 1bolt clamps and three pen union used Voltage 120v240v
Non-Outage | J.E.26.07.26679 | C001863091 | Fitzroy Turner | null | Completed | null | null | Jul 23, 2026 9:35am | Jul 23, 2026 10:00am | Jul 23, 2026 10:27am | Jul 23, 2026 10:27am | Jul 23, 2026 10:28am | Jul 23, 2026 10:28am | Jul 23, 2026 10:51am | Jul 23, 2026 10:51am |  |  | Fair | No | Found 15 amps junction fuse blown at the intersection of darling st and beckford st .15 amps junction replaced supply restored to the areas
Outage | J.E.26.07.26563 | C001863090 | Evan Spaulding | St.Mary | Completed | Load_266559 | Highgate - 210 | Jul 23, 2026 9:35am | Jul 23, 2026 9:35am | Jul 23, 2026 12:35pm | Jul 23, 2026 12:35pm | Jul 23, 2026 12:47pm | Jul 23, 2026 1:31pm | Jul 23, 2026 1:33pm | Jul 23, 2026 1:33pm |  |  | Fair | No | Replace 1-25amps junction fuse at pole number 0010728 and 1-5 amps Transformer fuse at pole number 0010734.
Outage | J.E.26.07.26597 | C001863088 | Evan Spaulding | St.Mary | Completed | Load_260492 | Highgate - 210 | Jul 23, 2026 9:35am | Jul 23, 2026 9:35am | Jul 23, 2026 1:33pm | Jul 23, 2026 1:33pm | Jul 23, 2026 1:33pm | Jul 23, 2026 1:33pm | Jul 23, 2026 1:35pm | Jul 23, 2026 1:35pm |  |  | Fair | No | Replace 1-25amps junction fuse at pole number 0010728 and 1-5 amps Transformer fuse at pole number 0010734.
Outage | J.E.26.07.26628 | C001863085 | Derrick Grubb | St.Thomas | Completed | Load_264975 | Lysson - 410 | Jul 23, 2026 9:35am | Jul 23, 2026 9:36am | Jul 23, 2026 12:20pm | Jul 23, 2026 12:20pm | Jul 23, 2026 12:58pm | Jul 23, 2026 1:04pm | Jul 23, 2026 1:04pm | Jul 23, 2026 1:04pm |  |  | Fair | No | Premises found okay.
Outage | J.E.26.07.26666 | C001863086 | Derrick Grubb | St.Thomas | Completed | Load_243667 | Lysson - 410 | Jul 23, 2026 9:35am | Jul 23, 2026 9:36am | Jul 23, 2026 1:08pm | Jul 23, 2026 1:08pm | Jul 23, 2026 1:26pm | Jul 23, 2026 1:46pm | Jul 23, 2026 1:46pm | Jul 23, 2026 1:46pm |  |  | Fair | No | Patrol, found no visible faults on the line and refuse 15amp junction at pole number 0004874. Power restored.
Outage | J.E.26.07.26683 | C001863087 | Derrick Grubb | St.Thomas | Completed | Load_405559 | Lysson - 410 | Jul 23, 2026 9:35am | Jul 23, 2026 9:36am | Jul 23, 2026 12:48pm | Jul 23, 2026 1:04pm | Jul 23, 2026 1:04pm | Jul 23, 2026 1:05pm | Jul 23, 2026 1:05pm | Jul 23, 2026 1:05pm |  |  | Fair | No | Contact customer by phone and customer said premises is okay.
Outage | J.E.26.07.26687 | C001863084 | Marlon Brown | Trelawny | Completed | Load_249132 | Greenwood - 110 | Jul 23, 2026 9:34am | Jul 23, 2026 10:01am | Jul 23, 2026 10:39am | Jul 23, 2026 10:39am | Jul 23, 2026 11:01am | Jul 23, 2026 12:03pm | Jul 23, 2026 12:05pm | Jul 23, 2026 12:05pm | Fire |  | Fair | No | Isolated 25kva & 10kva transformers to repair 1 span secondary neutral Use 60ft #2 AAC, 1 #2 preform and 2 pg clampsVoltage found at meter socket 199/24=223vVoltage leaving at meter socket 114/115=229v. Illegal connections caused wire to burn down.
Outage | J.E.26.07.26562 | C001863082 | Kaydon Taylor | KSAN | Completed | Load_243612 | Constant Spring - 210 | Jul 23, 2026 9:33am | Jul 23, 2026 9:34am | Jul 23, 2026 3:48pm | Jul 23, 2026 3:49pm | Jul 23, 2026 4:29pm | Jul 23, 2026 4:31pm | Jul 23, 2026 4:31pm | Jul 23, 2026 4:31pm |  |  | Rains | No | Found okay
Outage | J.E.26.07.26581 | C001863080 | Kaydon Taylor | KSAN | Completed | Load_246214 | Constant Spring - 210 | Jul 23, 2026 9:33am | Jul 23, 2026 9:34am | Jul 23, 2026 4:31pm | Jul 23, 2026 4:32pm | Jul 23, 2026 4:32pm | Jul 23, 2026 4:32pm | Jul 23, 2026 4:33pm | Jul 23, 2026 4:33pm |  |  | Rains | No | Premises closed
Outage | J.E.26.07.26610 | C001863081 | Milton Charlton | KSAS | Completed | Load_264050 | Up Park Camp - 410 | Jul 23, 2026 9:33am | Jul 23, 2026 9:34am | Jul 23, 2026 9:42am | Jul 23, 2026 9:42am | Jul 23, 2026 11:41am | Jul 23, 2026 10:15am | Jul 23, 2026 11:45am | Jul 23, 2026 11:45am |  |  | Fair | No | Refused and reclosed one 20 amps and one 10amps junction at pole #0015894 using one20 amps and one10 amps fuses and reclosed both junction switches.
Outage | J.E.26.07.26682 | C001863083 | Milton Charlton | KSAN | Completed | Load_256996 | Washington Blvd - 510 | Jul 23, 2026 9:33am | Jul 23, 2026 12:42pm | Jul 23, 2026 2:34pm | Jul 23, 2026 2:34pm | Jul 23, 2026 3:16pm | Jul 23, 2026 2:40pm | Jul 23, 2026 3:19pm | Jul 23, 2026 3:19pm |  |  | Fair | No | Refused and reclosed 30 amps junction at pole #0077956 using one 30 amps fuse.
Outage | J.E.26.07.26527 | C001863079 | Rusean Allen | KSAS | Completed | Load_300858 | Cane River - 410 | Jul 23, 2026 9:31am | Jul 23, 2026 9:32am | Jul 23, 2026 11:34am | Jul 23, 2026 11:35am | Jul 23, 2026 11:50am | Jul 23, 2026 11:54am | Jul 23, 2026 11:55am | Jul 23, 2026 11:55am | BrokenWire |  | Fair | No | Hexing failure, service wire coming hexing enclosure defective and needs to be changed Hex02246. Refer to field service department urgently..Customer has been out of service since march.
Outage | J.E.26.07.26537 | C001863077 | Fitzroy Turner | KSAS | Completed | Load_261769 | Hunts Bay - 310 | Jul 23, 2026 9:31am | Jul 23, 2026 9:32am | Jul 23, 2026 9:38am | Jul 23, 2026 9:38am | Jul 23, 2026 10:07am | Jul 23, 2026 10:25am | Jul 23, 2026 10:27am | Jul 23, 2026 10:27am |  |  | Fair | No | Found 5amps transformer fuse blown and the school compound. 5 amp fuse replaced supply restored customer
Outage | J.E.26.07.26572 | C001863076 | Fitzroy Turner | KSAS | Completed | Load_261838 | Hunts Bay - 210 | Jul 23, 2026 9:31am | Jul 23, 2026 9:32am | Jul 23, 2026 10:51am | Jul 23, 2026 10:51am | Jul 23, 2026 11:01am | Jul 23, 2026 11:01am | Jul 23, 2026 11:04am | Jul 23, 2026 11:04am |  |  | Fair | No | Customer supply restored after replace blown 15 amp fuse at the intersection darling st and beckford st
Outage | J.E.26.07.26667 | C001863078 | Andre Smith | KSAS | Completed | Load_268624 | Greenwich - 710 | Jul 23, 2026 9:31am | Jul 23, 2026 9:32am | Jul 23, 2026 10:58am | Jul 23, 2026 10:58am | Jul 23, 2026 11:12am | Jul 23, 2026 11:50am | Jul 23, 2026 11:50am | Jul 23, 2026 11:50am |  |  | Fair | No | Replace defective one bolt clamps at pole on phase supply restored
Non-Outage | J.E.26.07.26659 | C001863071 | Javid Vernon | null | Completed | null | null | Jul 23, 2026 9:28am | Jul 23, 2026 9:29am | Jul 23, 2026 10:06am | Jul 23, 2026 10:06am | Jul 23, 2026 11:40am | Jul 23, 2026 12:40pm | Jul 23, 2026 12:41pm | Jul 23, 2026 12:41pm |  |  | Fair | No | Clean and remake joints at JPS pole and customer pothead voltage found 110/99/201 voltage left 112/106/218
Non-Outage | J.E.26.07.26485 | C001863070 | Derrick Grubb | St.Thomas | Completed | Load_252941 | Good Year - 110 | Jul 23, 2026 9:26am | Jul 23, 2026 9:28am | Jul 23, 2026 10:41am | Jul 23, 2026 10:41am | Jul 23, 2026 12:15pm | Jul 23, 2026 12:19pm | Jul 23, 2026 12:19pm | Jul 23, 2026 12:19pm |  |  | Fair | No | Splice and retention one pole span of open secondary neutral wire using approximately 50’ of #2aaa wire one #2 splicing sleeve and a one bolt clamp. Voltage readings when leaving 120v, 119v, 238v.
Non-Outage | J.E.26.07.26395 | C001863061 | Floyd Taylor | null | Completed | null | null | Jul 23, 2026 9:25am | Jul 23, 2026 9:27am | Jul 23, 2026 11:38am | Jul 23, 2026 11:38am | Jul 23, 2026 12:12pm | Jul 23, 2026 12:37pm | Jul 23, 2026 12:46pm | Jul 23, 2026 12:46pm |  |  | Fair | No | Customer having internal issues voltage readings left 117,118,204,238,239,239
Outage | J.E.26.07.24289 | C001863057 | Rodclif Dawkins | Portmore | Completed | Load_266570 | Naggo Head - 610 | Jul 23, 2026 9:23am | Jul 23, 2026 4:32pm | Jul 23, 2026 7:08pm | Jul 23, 2026 7:17pm | Jul 23, 2026 7:24pm | Jul 23, 2026 7:25pm | Jul 23, 2026 7:25pm | Jul 23, 2026 7:25pm | Fire |  | Fair | No | Customer found okay
Outage | J.E.26.07.26412 | C001863059 | Floyd Taylor | Trelawny | Completed | Load_292845 | Greenwood - 110 | Jul 23, 2026 9:23am | Jul 23, 2026 9:26am | Jul 23, 2026 5:07pm | Jul 23, 2026 5:07pm | Jul 23, 2026 5:07pm | Jul 23, 2026 5:07pm | Jul 23, 2026 5:08pm | Jul 23, 2026 5:08pm |  |  | Fair | No | Found ok,customer power was restored.
Outage | J.E.26.07.26513 | C001863058 | Floyd Taylor | Trelawny | Completed | Load_238624 | Greenwood - 210 | Jul 23, 2026 9:23am | Jul 23, 2026 9:26am | Jul 23, 2026 5:09pm | Jul 23, 2026 5:09pm | Jul 23, 2026 5:09pm | Jul 23, 2026 5:09pm | Jul 23, 2026 5:10pm | Jul 23, 2026 5:10pm |  |  | Fair | No | Customer power was restored
Outage | J.E.26.07.26305 | C001863056 | Marlon Brown | Trelawny | Completed | Load_241826 | null | Jul 23, 2026 9:22am | Jul 23, 2026 9:23am | Jul 23, 2026 12:11pm | Jul 23, 2026 3:03pm | Jul 23, 2026 3:03pm | Jul 23, 2026 3:03pm | Jul 23, 2026 3:03pm | Jul 23, 2026 3:03pm |  |  | Fair | No | Feeder issue
Outage | J.E.26.07.26306 | C001863055 | Marlon Brown | Trelawny | Completed | Load_570270 | null | Jul 23, 2026 9:22am | Jul 23, 2026 9:23am | Jul 23, 2026 1:57pm | Jul 23, 2026 1:57pm | Jul 23, 2026 2:29pm | Jul 23, 2026 2:37pm | Jul 23, 2026 2:37pm | Jul 23, 2026 2:37pm |  |  | Fair | No | Check and found ok Voltage found at pothead 115/115=230vVoltage leaving at pothead 115/115=230v
Outage | J.E.26.07.26310 | C001863054 | Marlon Brown | Trelawny | Completed | Load_239166 | Duncans - 110 | Jul 23, 2026 9:22am | Jul 23, 2026 9:23am | Jul 23, 2026 12:23pm | Jul 23, 2026 12:23pm | Jul 23, 2026 12:48pm | Jul 23, 2026 1:08pm | Jul 23, 2026 1:09pm | Jul 23, 2026 1:09pm |  |  | Fair | No | Replaced 10amps junction fuse @ pole number 575751
Outage | J.E.26.07.26338 | C001863052 | Andre Williams | Trelawny | Completed | Load_302569 | null | Jul 23, 2026 9:21am | Jul 23, 2026 3:23pm | Jul 23, 2026 3:38pm | Jul 23, 2026 3:53pm | Jul 23, 2026 3:53pm | Jul 23, 2026 3:54pm | Jul 23, 2026 3:55pm | Jul 23, 2026 3:55pm |  |  | Fair | No | Premises ok and with supply call related to earlier outage
Outage | J.E.26.07.26378 | C001863050 | Marlon Brown | Trelawny | Completed | Load_294393 | Duncans - 110 | Jul 23, 2026 9:21am | Jul 23, 2026 9:23am | Jul 23, 2026 12:23pm | Jul 23, 2026 3:01pm | Jul 23, 2026 3:01pm | Jul 23, 2026 3:02pm | Jul 23, 2026 3:02pm | Jul 23, 2026 3:02pm |  |  | Fair | No | Customer has electricity, feeder was out.
Outage | J.E.26.07.26425 | C001863049 | Marlon Brown | Trelawny | Completed | Load_238727 | Duncans - 110 | Jul 23, 2026 9:21am | Jul 23, 2026 9:23am | Jul 23, 2026 12:13pm | Jul 23, 2026 3:02pm | Jul 23, 2026 3:02pm | Jul 23, 2026 3:02pm | Jul 23, 2026 3:02pm | Jul 23, 2026 3:02pm |  |  | Fair | No | Feeder was out
Outage | J.E.26.07.26598 | C001863048 | Marlon Brown | Trelawny | Completed | Load_256637 | Duncans - 110 | Jul 23, 2026 9:21am | Jul 23, 2026 9:23am | Jul 23, 2026 10:32am | Jul 23, 2026 10:32am | Jul 23, 2026 10:32am | Jul 23, 2026 10:33am | Jul 23, 2026 10:33am | Jul 23, 2026 10:33am | Fire |  | Fair | Yes | Same as call number 26598
Outage | J.E.26.07.26499 | C001863041 | Marlon Brown | Trelawny | Completed | Load_239166 | Duncans - 110 | Jul 23, 2026 9:20am | Jul 23, 2026 9:23am | Jul 23, 2026 1:10pm | Jul 23, 2026 1:10pm | Jul 23, 2026 1:10pm | Jul 23, 2026 1:11pm | Jul 23, 2026 1:11pm | Jul 23, 2026 1:11pm |  |  | Fair | No | Same as call number 26310.
Outage | J.E.26.07.26598 | C001863039 | Marlon Brown | Trelawny | Completed | Load_256637 | Duncans - 110 | Jul 23, 2026 9:19am | Jul 23, 2026 9:23am | Jul 23, 2026 9:32am | Jul 23, 2026 9:40am | Jul 23, 2026 9:52am | Jul 23, 2026 10:32am | Jul 23, 2026 10:32am | Jul 23, 2026 10:32am | Fire |  | Fair | Yes | Phase change done for rotation of customers motorsVoltage found 113/110/19o=232/233/235Voltage leaving at pothead 113/110/199=232/233/235
Outage | J.E.26.07.26216 | C001863037 | Romeo Brissett | St.James | Completed | Load_302110 | Bogue - 610 | Jul 23, 2026 9:16am | Jul 23, 2026 9:17am | Jul 23, 2026 2:08pm | Jul 23, 2026 2:10pm | Jul 23, 2026 2:10pm | Jul 23, 2026 2:00pm | Jul 23, 2026 2:11pm | Jul 23, 2026 2:11pm |  |  | Rains | No | Removed Illegal connections clear secondary jumper and replaced (1)15KVA transformer fuse.k
Outage | J.E.26.07.26547 | C001863023 | Swon Miller | St.James | Completed | Load_292863 | Queens Drive - 710 | Jul 23, 2026 9:14am | Jul 23, 2026 9:17am | Jul 23, 2026 1:01pm | Jul 23, 2026 1:01pm | Jul 23, 2026 1:52pm | Jul 21, 2026 2:05am | Jul 23, 2026 2:12pm | Jul 23, 2026 2:12pm |  |  | Fair | No | Check and found okay voltage found 110/111/221 voltage left 110/111/211
Outage | J.E.26.07.26568 | C001863024 | Horace Malcolm | St.James | Completed | Load_412876 | Bogue - 310 | Jul 23, 2026 9:14am | Jul 23, 2026 9:17am | Jul 23, 2026 9:53am | Jul 23, 2026 9:53am | Jul 23, 2026 10:15am | Jul 23, 2026 10:19am | Jul 23, 2026 10:19am | Jul 23, 2026 10:19am |  |  | Fair | No | Check and found customer got disconnected got customer reconnected
Outage | J.E.26.07.26578 | C001863025 | Horace Malcolm | St.James | Completed | Load_246965 | Bogue - 310 | Jul 23, 2026 9:14am | Jul 23, 2026 9:17am | Jul 23, 2026 11:37am | Jul 23, 2026 11:44am | Jul 23, 2026 12:30pm | Jul 23, 2026 1:43pm | Jul 23, 2026 1:43pm | Jul 23, 2026 1:43pm |  |  | Fair | No | Splice and retention two pole span secondary phase and nuetral used 60ft #2 conductor (2)#2 preforms 3clamps
Outage | J.E.26.07.26596 | C001863026 | Horace Malcolm | St.James | Completed | Load_262397 | Bogue - 310 | Jul 23, 2026 9:14am | Jul 23, 2026 11:59pm | Jul 24, 2026 1:05am | Jul 24, 2026 1:05am | Jul 24, 2026 3:01am | Jul 24, 2026 3:31am | Jul 24, 2026 3:32am | Jul 24, 2026 3:32am |  |  | Fair | No | Check and found area single phasing clean corrosion on transformer drop voltage 111-113-224 (customer meter pole is more than 100ft away from JPS pole customer needs 132 ft #6 triplex in order to get back supply unable to reach out to customer to advise customer)
Outage | J.E.26.07.26619 | C001863027 | Horace Malcolm | St.James | Completed | Load_268055 | Bogue - 310 | Jul 23, 2026 9:14am | Jul 23, 2026 9:17am | Jul 23, 2026 10:56am | Jul 23, 2026 10:56am | Jul 23, 2026 10:56am | Jul 23, 2026 10:57am | Jul 23, 2026 10:57am | Jul 23, 2026 10:57am |  |  | Fair | No | Related to previous call job number 26636
Outage | J.E.26.07.26636 | C001863028 | Horace Malcolm | St.James | Completed | Load_251106 | Bogue - 310 | Jul 23, 2026 9:14am | Jul 23, 2026 9:17am | Jul 23, 2026 10:22am | Jul 23, 2026 10:22am | Jul 23, 2026 10:33am | Jul 23, 2026 10:56am | Jul 23, 2026 10:56am | Jul 23, 2026 10:56am |  |  | Fair | No | Refused one 20amp junction fuse
Non-Outage | J.E.26.03.34070 | C001863021 | Junior Scarlett | St.James | Completed | Load_250374 | Bogue - 510 | Jul 23, 2026 9:11am | Jul 23, 2026 9:13am | Jul 23, 2026 9:28am | Jul 24, 2026 12:43pm | Jul 24, 2026 1:08pm | Jul 24, 2026 1:08pm | Jul 24, 2026 1:08pm | Jul 24, 2026 1:08pm | LeaningPole |  | Fair | No
Non-Outage | J.E.26.04.23163 | C001863016 | Junior Scarlett | St.James | Completed | Load_240294 | Bogue - 610 | Jul 23, 2026 9:10am | Jul 23, 2026 9:13am | Jul 23, 2026 9:28am | Jul 23, 2026 3:09pm | Jul 23, 2026 3:39pm | Jul 23, 2026 3:54pm | Jul 23, 2026 3:54pm | Jul 23, 2026 3:54pm | BrokenPole |  | Fair | No | Check and found okVoltage found 112v 112v 224v
Non-Outage | J.E.26.07.05344 | C001863015 | Rayon Foster | St.James | Completed | Load_238185 | Bogue - 510 | Jul 23, 2026 9:09am | Jul 23, 2026 9:43am | Jul 23, 2026 1:40pm | Jul 23, 2026 1:40pm | Jul 23, 2026 2:10pm | Jul 23, 2026 2:21pm | Jul 23, 2026 2:26pm | Jul 23, 2026 2:26pm |  |  | Fair | No | Check and found voltage working ok voltage found on arrival 113v/111v/224v
Non-Outage | J.E.26.07.16096 | C001863014 | Junior Scarlett | St.James | Completed | Load_255008 | Bogue - 510 | Jul 23, 2026 9:09am | Jul 23, 2026 9:13am | Jul 23, 2026 9:28am | Jul 23, 2026 10:03am | Jul 23, 2026 10:13am | Jul 23, 2026 10:34am | Jul 23, 2026 10:35am | Jul 23, 2026 10:35am | LeaningPole |  | Fair | No | Check and found okVoltage found 115v 115v 230v
Non-Outage | J.E.26.07.21641 | C001863011 | Junior Scarlett | St.James | Completed | Load_257529 | Bogue - 610 | Jul 23, 2026 9:08am | Jul 23, 2026 9:13am | Jul 23, 2026 9:28am | Jul 23, 2026 1:45pm | Jul 23, 2026 2:49pm | Jul 23, 2026 3:09pm | Jul 23, 2026 3:09pm | Jul 23, 2026 3:09pm |  |  | Fair | No | Check and found okVoltage found 114v 114v 227v
Non-Outage | J.E.26.07.23570 | C001863008 | Junior Scarlett | St.James | Completed | Load_268070 | Bogue - 510 | Jul 23, 2026 9:08am | Jul 23, 2026 9:13am | Jul 23, 2026 9:28am | Jul 24, 2026 8:19am | Jul 24, 2026 8:44am | Jul 24, 2026 9:15pm | Jul 24, 2026 9:15am | Jul 24, 2026 9:15am | LowHangingWires |  | Fair | No | Check and found okVoltage found 115v 115v 230v
Non-Outage | J.E.26.07.23706 | C001863007 | Junior Scarlett | St.James | Completed | Load_251779 | Bogue - 510 | Jul 23, 2026 9:08am | Jul 23, 2026 9:12am | Jul 23, 2026 9:28am | Jul 24, 2026 9:20am | Jul 24, 2026 9:37am | Jul 24, 2026 10:15am | Jul 24, 2026 10:16am | Jul 24, 2026 10:16am |  |  | Fair | No | Corrosion at potheadFixed issue voltage found 114v 86v 199vVoltage leave 114v 114v 228vJob completed
Non-Outage | J.E.26.07.24258 | C001863006 | Junior Scarlett | St.James | Completed | Load_238867 | Bogue - 610 | Jul 23, 2026 9:08am | Jul 23, 2026 9:12am | Jul 23, 2026 9:28am | Jul 23, 2026 10:38am | Jul 23, 2026 11:00am | Jul 23, 2026 11:35am | Jul 23, 2026 11:37am | Jul 23, 2026 11:37am |  |  | Fair | No | Check and found okVoltage found 115v 115v 230v
Non-Outage | J.E.26.07.24752 | C001863005 | Junior Scarlett | St.James | Completed | Load_269051 | Bogue - 610 | Jul 23, 2026 9:08am | Jul 23, 2026 9:12am | Jul 23, 2026 9:28am | Jul 23, 2026 11:44am | Jul 23, 2026 12:35pm | Jul 23, 2026 1:20am | Jul 23, 2026 1:28pm | Jul 23, 2026 1:28pm |  |  | Fair | No | Install two clampReattach wire clean corrosionVoltage found 101v 113v 227vVoltage leave 113v 113v 227vJon completed
Non-Outage | J.E.26.07.25182 | C001863003 | Junior Scarlett | St.James | Completed | Load_240027 | Bogue - 610 | Jul 23, 2026 9:07am | Jul 23, 2026 9:12am | Jul 23, 2026 9:28am | Jul 24, 2026 11:51am | Jul 24, 2026 11:51am | Jul 24, 2026 12:40pm | Jul 24, 2026 12:41pm | Jul 24, 2026 12:41pm |  |  | Fair | No | Require emergency team The whole area experience low voltage at nightVoltage found 109v 101v 226v
Non-Outage | J.E.26.07.25289 | C001863002 | Junior Scarlett | St.James | Completed | Load_238682 | Bogue - 510 | Jul 23, 2026 9:07am | Jul 23, 2026 9:12am | Jul 23, 2026 9:19am | Jul 23, 2026 9:19am | Jul 23, 2026 9:58am | Jul 23, 2026 9:59am | Jul 23, 2026 10:00am | Jul 23, 2026 10:00am |  |  | Fair | No | Premeis lockVoltage from pole 115v 115v 230v
Non-Outage | J.E.26.07.14995 | C001862999 | Romeo Brissett | St.James | Completed | Load_262522 | Bogue - 510 | Jul 23, 2026 9:06am | Jul 23, 2026 9:11am | Jul 23, 2026 11:10am | Jul 23, 2026 11:10am | Jul 23, 2026 11:14am | Jul 23, 2026 11:48am | Jul 23, 2026 11:52am | Jul 23, 2026 11:52am | BrokenPole |  | Fair | No | Found three (3) defective pole in camp road hopewell. One(1) overhead guy pole broken and leaning in road way, one(1)T pole broken with open secondary, one (1)35ft pole severely rotten at the foot and need to change with single phase Primary and open secondary, one (1)35ft pole leaning with single phase Primary and open secondary need to be straighten.
Non-Outage | J.E.26.03.34070 | C001862996 | Junior Scarlett | St.James | Completed | Load_250374 | Bogue - 510 | Jul 23, 2026 9:05am | Jul 23, 2026 9:12am | Jul 23, 2026 9:28am | Jul 24, 2026 10:29am | Jul 24, 2026 10:58am | Jul 24, 2026 11:10am | Jul 24, 2026 11:11am | Jul 24, 2026 11:11am | LeaningPole |  | Fair | No | Check and found okVoltage found 115v 115v 230v
Non-Outage | J.E.26.02.39553 | C001862990 | Andrae Dawkins | St.James | Completed | Load_292555 | Bogue - 310 | Jul 23, 2026 9:03am | Jul 23, 2026 9:04am | Jul 23, 2026 12:02pm | Jul 23, 2026 1:25pm | Jul 23, 2026 2:21pm | Jul 23, 2026 2:45pm | Jul 23, 2026 2:49pm | Jul 23, 2026 2:49pm |  |  | Fair | No | Found multiple customers in the area experiencing low voltage voltage found 137/84/206
Non-Outage | J.E.26.02.39605 | C001862991 | Andrae Dawkins | St.James | Completed | Load_301732 | Bogue - 310 | Jul 23, 2026 9:03am | Jul 23, 2026 9:04am | Jul 23, 2026 11:58am | Jul 23, 2026 1:19pm | Jul 23, 2026 1:19pm | Jul 23, 2026 12:20pm | Jul 23, 2026 1:23pm | Jul 23, 2026 1:23pm |  |  | Fair | No | Check and found ok customer said that that they didn’t make any report and that they don’t have any issue at the premises
Outage | J.E.26.07.26510 | C001862987 | Richard Nicholas | St.Catherine | Completed | Load_239948 | Twickenham - 410 | Jul 23, 2026 9:03am | Jul 23, 2026 1:25pm | Jul 23, 2026 1:32pm | Jul 23, 2026 1:32pm | Jul 23, 2026 2:05pm | Jul 23, 2026 3:23pm | Jul 23, 2026 3:25pm | Jul 23, 2026 3:25pm |  |  | Fair | No | Replaced blown 30amp junctions fuse near to the square of hill run,and blown 10amp junctions fuse on pole #620620.
Non-Outage | J.E.26.05.06350 | C001862973 | Swon Miller | St.James | Completed | Load_260338 | Queens Drive - 710 | Jul 23, 2026 9:00am | Jul 23, 2026 9:01am | Jul 24, 2026 8:12am | Jul 24, 2026 8:12am | Jul 24, 2026 8:37am | Jul 28, 2026 8:55am | Jul 24, 2026 8:56am | Jul 24, 2026 8:56am |  |  | Fair | No | Check and found customer single phasing cause by contamination at pole clean and remake joints use 1 pg voltage found 116 voltage left 116/114/230 also there is a 30ft class 6 pole at the end of the line with secondary and street lights on it the pole is broken at the base and needs to be urgently replaced plz refer to maintenance
Non-Outage | J.E.26.02.31100 | C001862969 | Andrae Dawkins | St.James | Completed | Load_239386 | Queens Drive - 710 | Jul 23, 2026 8:58am | Jul 23, 2026 9:00am | Jul 23, 2026 9:26am | Jul 23, 2026 10:30am | Jul 23, 2026 10:30am | Jul 23, 2026 10:05am | Jul 23, 2026 10:31am | Jul 23, 2026 10:31am | LeaningPole |  | Fair | No | Found 3 30ft class 6 pole with secondary only leaning about to fall needs to be straightened refer back to maintenance
Non-Outage | J.E.26.02.32431 | C001862970 | Andrae Dawkins | St.James | Completed | Load_1002030 | Queens Drive - 710 | Jul 23, 2026 8:58am | Jul 23, 2026 9:00am | Jul 23, 2026 9:27am | Jul 23, 2026 10:47am | Jul 23, 2026 10:47am | Jul 23, 2026 10:37am | Jul 23, 2026 10:50am | Jul 23, 2026 10:50am | BrokenPole |  | Fair | No | Check and found ok customer said that they didn’t make any report and that she doesn’t have any issue
Non-Outage | J.E.26.03.12304 | C001862972 | Andrae Dawkins | St.James | Completed | Load_239386 | Queens Drive - 710 | Jul 23, 2026 8:58am | Jul 23, 2026 9:00am | Jul 23, 2026 9:27am | Jul 23, 2026 10:15am | Jul 23, 2026 10:15am | Jul 23, 2026 10:05am | Jul 23, 2026 10:30am | Jul 23, 2026 10:30am | LeaningPole |  | Fair | No | Found 3 30ft class 6 pole with secondary only leaning about to fall needs to be straightened refer back to maintenance
Non-Outage | J.E.26.04.18664 | C001862971 | Andrae Dawkins | St.James | Completed | Load_258945 | Queens Drive - 710 | Jul 23, 2026 8:58am | Jul 23, 2026 9:00am | Jul 23, 2026 11:44am | Jul 23, 2026 1:05pm | Jul 23, 2026 1:05pm | Jul 23, 2026 11:49am | Jul 23, 2026 1:08pm | Jul 23, 2026 1:08pm |  |  | Fair | No | Cannot locate customer due to no directions also unable to reach customer mobile
Non-Outage | J.E.26.07.25386 | C001862966 | Hartley Chin | Clarendon | Completed | Load_245801 | May Pen - 110 | Jul 23, 2026 8:54am | Jul 23, 2026 8:55am | Jul 23, 2026 2:19pm | Jul 23, 2026 2:19pm | Jul 23, 2026 3:04pm | Jul 23, 2026 3:05pm | Jul 23, 2026 3:05pm | Jul 23, 2026 3:05pm |  |  | Rains | No | Found ok
Outage | J.E.26.07.26559 | C001862956 | Javid Vernon | Westmoreland | Completed | Load_247636 | Paradise - 210 | Jul 23, 2026 8:44am | Jul 23, 2026 9:29am | Jul 23, 2026 12:41pm | Jul 23, 2026 12:41pm | Jul 23, 2026 1:36pm | Jul 23, 2026 1:53pm | Jul 23, 2026 1:55pm | Jul 23, 2026 1:55pm |  |  | Fair | No | Reconnect customer service wire use two clamps voltage reading 117/117/234
Non-Outage | J.E.26.07.14350 | C001862955 | Romeo Brissett | St.James | Completed | Load_255565 | Bogue - 510 | Jul 23, 2026 8:42am | Jul 23, 2026 8:43am | Jul 23, 2026 8:50am | Jul 23, 2026 8:50am | Jul 23, 2026 9:42am | Jul 23, 2026 10:16am | Jul 23, 2026 10:35am | Jul 23, 2026 10:35am |  |  | Fair | No | Check and found internal fault, V/R 108-109-218
Outage | J.E.26.07.26534 | C001862951 | Damion Reid | Manchester | Completed | Load_256064 | Kendal - 310 | Jul 23, 2026 8:36am | Jul 23, 2026 8:38am | Jul 23, 2026 10:47am | Jul 23, 2026 10:47am | Jul 23, 2026 10:59am | Jul 23, 2026 11:09am | Jul 23, 2026 11:14am | Jul 23, 2026 11:14am |  |  | Fair | No | Customer meter is defective refer to field service customer meter #3044312 voltage reading at meter socket phase to neutral 115v-115v across phase 232v
Non-Outage | J.E.26.07.24171 | C001862947 | Orville Lee | Portmore | Completed | Load_245935 | Naggo Head - 610 | Jul 23, 2026 8:35am | Jul 23, 2026 8:36am | Jul 23, 2026 10:00am | Jul 23, 2026 4:04pm | Jul 23, 2026 4:04pm | Jul 23, 2026 4:37pm | Jul 23, 2026 4:39pm | Jul 23, 2026 4:39pm |  |  | Fair | No | Defective service wire changedTwo1bolt clamp, four pen union and 30ft wire usedVoltage120v120v240v
Non-Outage | J.E.26.07.25448 | C001862946 | Rayon Foster | null | Completed | null | null | Jul 23, 2026 8:32am | Jul 23, 2026 8:33am | Jul 23, 2026 7:31pm | Jul 23, 2026 8:34pm | Jul 23, 2026 8:57pm | Jul 23, 2026 9:04pm | Jul 23, 2026 9:05pm | Jul 23, 2026 9:05pm | TreeContact |  | Fair | No | When checked power is in area no meter number is available to locate customer premises and unable to reach customer on cellphone
Outage | J.E.26.07.26117 | C001862945 | Rayon Foster | Hanover | Completed | Load_258609 | Orange Bay - 210 | Jul 23, 2026 8:31am | Jul 23, 2026 8:33am | Jul 23, 2026 10:56am | Jul 23, 2026 1:01pm | Jul 23, 2026 1:02pm | Jul 23, 2026 1:13pm | Jul 23, 2026 1:14pm | Jul 23, 2026 1:14pm |  |  | Fair | No | Customer meter pole broken down and her meter burn refer to Clint Johnson from Westmoreland to change meter customer was advised to repair meter pole before her supply can be restored
Outage | J.E.26.07.26538 | C001862944 | Rayon Foster | Hanover | Completed | Load_573746 | Orange Bay - 210 | Jul 23, 2026 8:31am | Jul 23, 2026 8:33am | Jul 23, 2026 10:11am | Jul 23, 2026 10:46am | Jul 23, 2026 12:56pm | Jul 23, 2026 1:00pm | Jul 23, 2026 1:00pm | Jul 23, 2026 1:00pm |  |  | Fair | No | Unable to reach customer on cell number provided or locate premises power in area walkers view Negril
Outage | J.E.26.07.26539 | C001862943 | Rayon Foster | Hanover | Completed | Load_258609 | Orange Bay - 210 | Jul 23, 2026 8:31am | Jul 23, 2026 8:33am | Jul 23, 2026 10:05am | Jul 23, 2026 10:12am | Jul 23, 2026 10:43am | Jul 23, 2026 10:44am | Jul 23, 2026 10:46am | Jul 23, 2026 10:46am |  |  | Fair | No | When spoke with customer they said that their power supply was already restored by a jps team.
Non-Outage | J.E.26.07.26323 | C001862934 | Roemello Brown | Trelawny | Completed | Load_249132 | null | Jul 23, 2026 8:24am | Jul 23, 2026 8:26am | Jul 23, 2026 1:21pm | Jul 23, 2026 2:48pm | Jul 23, 2026 3:15pm | Jul 23, 2026 3:15pm | Jul 23, 2026 3:17pm | Jul 23, 2026 3:17pm |  |  | Fair | No | Customer states that I have the wrong number also I need proper directions an landmark please
Non-Outage | J.E.26.07.26327 | C001862935 | Roemello Brown | Trelawny | Completed | Load_260728 | null | Jul 23, 2026 8:24am | Jul 23, 2026 8:26am | Jul 23, 2026 12:39pm | Jul 23, 2026 12:49pm | Jul 23, 2026 1:11pm | Jul 23, 2026 1:11pm | Jul 23, 2026 1:21pm | Jul 23, 2026 1:21pm |  |  | Rains | No | Premises found working okay Voltage found 110/113/223
Non-Outage | J.E.26.07.26329 | C001862933 | Roemello Brown | Trelawny | Completed | Load_261797 | Martha Brae - 210 | Jul 23, 2026 8:24am | Jul 23, 2026 8:26am | Jul 23, 2026 1:21pm | Jul 23, 2026 1:24pm | Jul 23, 2026 2:08pm | Jul 23, 2026 2:08pm | Jul 23, 2026 2:11pm | Jul 23, 2026 2:11pm |  |  | Rains | No | Premises found working okay Voltage found 115/116/231Voltage leave 115/116/231
Non-Outage | J.E.26.07.26392 | C001862932 | Roemello Brown | Trelawny | Completed | Load_302565 | null | Jul 23, 2026 8:24am | Jul 23, 2026 8:26am | Jul 23, 2026 9:13am | Jul 23, 2026 11:30am | Jul 23, 2026 11:52am | Jul 23, 2026 11:52am | Jul 23, 2026 12:13pm | Jul 23, 2026 12:13pm |  |  | Fair | No | Customer meter socket neutral lug rotten out I informed the customer to get an private electrician to have it rectified Voltage found 116/116/232
Non-Outage | J.E.26.07.25279 | C001862927 | Orville Lee | Portmore | Completed | Load_245174 | Naggo Head - 610 | Jul 23, 2026 8:23am | Jul 23, 2026 8:24am | Jul 23, 2026 10:00am | Jul 23, 2026 1:11pm | Jul 23, 2026 1:18pm | Jul 23, 2026 1:53pm | Jul 23, 2026 1:55pm | Jul 23, 2026 1:55pm |  |  | Fair | No | Checks were made and found pothead corroded Six 1bolt clamps usedVoltage118v119v237v
Non-Outage | J.E.26.07.26397 | C001862931 | Roemello Brown | Trelawny | Completed | Load_570271 | null | Jul 23, 2026 8:23am | Jul 23, 2026 8:26am | Jul 23, 2026 9:16am | Jul 23, 2026 11:02am | Jul 23, 2026 11:18am | Jul 23, 2026 11:18am | Jul 23, 2026 11:29am | Jul 23, 2026 11:29am |  |  | Fair | No | Premises found working okay Voltage found 114/115/229Voltage leave 114/115/229
Non-Outage | J.E.26.07.26439 | C001862930 | Roemello Brown | Trelawny | Completed | Load_267113 | Greenwood - 110 | Jul 23, 2026 8:23am | Jul 23, 2026 8:26am | Jul 23, 2026 9:28am | Jul 23, 2026 12:13pm | Jul 23, 2026 12:26pm | Jul 23, 2026 12:26pm | Jul 23, 2026 12:31pm | Jul 23, 2026 12:31pm |  |  | Fair | No | Premises found working okay Voltage found 118/118/236Voltage leave 118/118/236
Non-Outage | J.E.26.07.26454 | C001862928 | Roemello Brown | Trelawny | Completed | Load_294320 | Greenwood - 110 | Jul 23, 2026 8:23am | Jul 23, 2026 8:26am | Jul 23, 2026 9:23am | Jul 23, 2026 9:37am | Jul 23, 2026 10:56am | Jul 23, 2026 10:57am | Jul 23, 2026 11:02am | Jul 23, 2026 11:02am |  |  | Fair | No | Premises found working okay Voltage found 116/117/233Voltage leave 116/117/233
Non-Outage | J.E.26.07.26480 | C001862929 | Roemello Brown | Trelawny | Completed | Load_256637 | Duncans - 110 | Jul 23, 2026 8:23am | Jul 23, 2026 8:26am | Jul 23, 2026 12:55pm | Jul 23, 2026 2:11pm | Jul 23, 2026 2:46pm | Jul 23, 2026 2:46pm | Jul 23, 2026 2:48pm | Jul 23, 2026 2:48pm |  |  | Fair | No | Premises found okay emergency team visit the location already Voltage found 110/113/199/223Voltage leave 110/113/199/223
Non-Outage | J.E.26.07.26289 | C001862918 | Swon Miller | null | Completed | null | null | Jul 23, 2026 8:14am | Jul 23, 2026 8:15am | Jul 23, 2026 8:22am | Jul 23, 2026 8:22am | Jul 23, 2026 9:27am | Jul 28, 2026 11:25am | Jul 23, 2026 11:41am | Jul 23, 2026 11:41am | Fire |  | Fair | No | Found 1;50 amp junction fuse blown cause by breaking down of fuse barrel cap replaced 1 fuse barrel and 1,50 amp junction fuse voltage found 115/113 voltage left 115/115/114
Outage | J.E.26.07.26515 | C001862919 | Horace Malcolm | St.James | Completed | Load_245469 | Bogue - 310 | Jul 23, 2026 8:14am | Jul 23, 2026 8:15am | Jul 23, 2026 8:55am | Jul 23, 2026 8:55am | Jul 23, 2026 8:55am | Jul 23, 2026 8:56am | Jul 23, 2026 8:56am | Jul 23, 2026 8:56am |  |  | Fair | No | Call belongs to trelawny
Non-Outage | J.E.26.07.25340 | C001862914 | Dwain Samuels | Hanover | Completed | Load_301743 | Orange Bay - 310 | Jul 23, 2026 8:11am | Jul 23, 2026 8:11am | Jul 23, 2026 8:41am | Jul 23, 2026 10:55am | Jul 23, 2026 12:04pm | Jul 23, 2026 12:21pm | Jul 23, 2026 12:22pm | Jul 23, 2026 12:22pm |  |  | Fair | No | Customer removed meter from original location . Unable to locate
Non-Outage | J.E.26.07.25509 | C001862915 | Dwain Samuels | Westmoreland | Completed | Load_292703 | Paradise - 210 | Jul 23, 2026 8:11am | Jul 23, 2026 8:11am | Jul 23, 2026 8:41am | Jul 23, 2026 1:58pm | Jul 23, 2026 1:58pm | Jul 23, 2026 1:58pm | Jul 23, 2026 1:58pm | Jul 23, 2026 1:58pm |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.07.25549 | C001862916 | Dwain Samuels | Hanover | Completed | Load_261442 | Orange Bay - 310 | Jul 23, 2026 8:11am | Jul 23, 2026 8:11am | Jul 23, 2026 8:41am | Jul 23, 2026 12:22pm | Jul 23, 2026 12:22pm | Jul 23, 2026 12:37pm | Jul 23, 2026 12:40pm | Jul 23, 2026 12:40pm |  |  | Fair | No | Found working okay. Voltage check 113-112-225
Non-Outage | J.E.26.07.26482 | C001862917 | Dwain Samuels | Westmoreland | Completed | Load_264652 | Paradise - 210 | Jul 23, 2026 8:11am | Jul 23, 2026 8:11am | Jul 23, 2026 8:41am | Jul 23, 2026 12:52pm | Jul 23, 2026 1:06pm | Jul 23, 2026 1:48pm | Jul 23, 2026 1:51pm | Jul 23, 2026 1:51pm |  |  | Fair | No | Corrosion found at 3 wire pot head. Voltage check 120-90-210. Corrosion clear use 3 pen union clamp. Voltage check 120-120-240
Non-Outage | J.E.26.07.26188 | C001862912 | Fredrick Hamilton | KSAN | Completed | Load_250041 | Washington Blvd - 510 | Jul 23, 2026 8:10am | Jul 23, 2026 8:11am | Jul 23, 2026 8:17am | Jul 23, 2026 8:46am | Jul 23, 2026 8:46am | Jul 23, 2026 8:48am | Jul 23, 2026 8:49am | Jul 23, 2026 8:49am |  |  | Fair | No | Premises was visited previously by technicians however no JPS defect was detected,there is a customer defect at location Property manager in process of having there electrician carry out maintenance
Non-Outage | J.E.26.07.20256 | C001862911 | Royston Montague | St.Catherine | Completed | Load_254124 | Tredegar - 510 | Jul 23, 2026 8:09am | Jul 23, 2026 8:13am | Jul 23, 2026 8:43am | Jul 23, 2026 8:50am | Jul 23, 2026 9:20am | Jul 23, 2026 9:20am | Jul 23, 2026 9:21am | Jul 23, 2026 9:21am |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.07.25922 | C001862910 | Javid Vernon | null | Completed | null | null | Jul 23, 2026 8:08am | Jul 23, 2026 9:27am | Jul 23, 2026 1:56pm | Jul 23, 2026 1:56pm | Jul 23, 2026 1:56pm | Jul 23, 2026 1:57pm | Jul 23, 2026 1:57pm | Jul 23, 2026 1:57pm |  |  | Fair | No | Customer stated that the power was restored
Non-Outage | J.E.26.07.25643 | C001862908 | Kaydon Taylor | KSAN | Completed | Load_245833 | Constant Spring - 210 | Jul 23, 2026 8:07am | Jul 23, 2026 8:08am | Jul 23, 2026 11:40am | Jul 23, 2026 1:20pm | Jul 23, 2026 1:20pm | Jul 23, 2026 2:15pm | Jul 23, 2026 2:15pm | Jul 23, 2026 2:15pm |  |  | Rains | No | Bank of (3) 1 x 100 2 x 50 kva transformer . Two 5 amp fuse found blown n replaced v 115, 114, 210, 232,239 ,238
Non-Outage | J.E.26.07.25666 | C001862909 | Fredrick Hamilton | KSAN | Completed | Load_263157 | Washington Blvd - 610 | Jul 23, 2026 8:07am | Jul 23, 2026 8:09am | Jul 23, 2026 8:17am | Jul 23, 2026 8:37am | Jul 23, 2026 8:38am | Jul 23, 2026 8:46am | Jul 23, 2026 8:46am | Jul 23, 2026 8:46am |  |  | Fair | No | Customer contacted and stated that power was restored fully yesterday Premises is now ok
Non-Outage | J.E.26.07.25697 | C001862907 | Fredrick Hamilton | KSAN | Completed | Load_579328 | Washington Blvd - 610 | Jul 23, 2026 8:07am | Jul 23, 2026 8:09am | Jul 23, 2026 8:17am | Jul 23, 2026 8:35am | Jul 23, 2026 8:35am | Jul 23, 2026 8:37am | Jul 23, 2026 8:37am | Jul 23, 2026 8:37am |  |  | Fair | No | Customer contacted and stated that power was fully restored yesterday Premises is ok
Non-Outage | J.E.26.07.21460 | C001862906 | Royston Montague | St.Catherine | Completed | Load_258881 | Tredegar - 310 | Jul 23, 2026 8:06am | Jul 23, 2026 8:08am | Jul 23, 2026 8:43am | Jul 23, 2026 12:24pm | Jul 23, 2026 12:58pm | Jul 23, 2026 12:59pm | Jul 23, 2026 1:00pm | Jul 23, 2026 1:00pm |  |  | Fair | No | Faulty neutral was the culprit on load side, customer confirmed his electrician corrected same, voltage found 229v 114v 113v
Non-Outage | J.E.26.07.23724 | C001862905 | Royston Montague | St.Catherine | Completed | Load_257732 | Tredegar - 510 | Jul 23, 2026 8:05am | Jul 23, 2026 8:08am | Jul 23, 2026 8:43am | Jul 23, 2026 11:24am | Jul 23, 2026 11:26am | Jul 23, 2026 11:28am | Jul 23, 2026 11:28am | Jul 23, 2026 11:28am |  |  | Fair | No | Faulty joints at transformer drop lead, 10 kva transformer fuse open to do repair. 230v 113v 115v
Non-Outage | J.E.26.07.24457 | C001862903 | Royston Montague | St.Catherine | Completed | Load_257732 | Tredegar - 510 | Jul 23, 2026 8:05am | Jul 23, 2026 8:07am | Jul 23, 2026 8:43am | Jul 23, 2026 9:26am | Jul 23, 2026 10:20am | Jul 23, 2026 11:24am | Jul 23, 2026 11:24am | Jul 23, 2026 11:24am |  |  | Fair | No | Faulty joints at transformer drop lead. 10kva transformer fuse open to do repair. Voltage 230v 115v 113v
Non-Outage | J.E.26.07.24993 | C001862899 | Marlon Authors | Manchester | Completed | Load_244726 | Spur Tree - 210 | Jul 23, 2026 8:05am | Jul 23, 2026 8:05am | Jul 23, 2026 10:26am | Jul 23, 2026 10:26am | Jul 23, 2026 10:43am | Jul 23, 2026 11:22am | Jul 23, 2026 11:22am | Jul 23, 2026 11:22am |  |  | Fair | No | Supply checked and found working ok rdg 112v,112v and cross phased 224 volts. Further checks revealed that the meter is burnt. Please refer same to the field services department for replacement
Non-Outage | J.E.26.07.25285 | C001862901 | Royston Montague | St.Catherine | Completed | Load_269784 | Tredegar - 510 | Jul 23, 2026 8:05am | Jul 23, 2026 8:07am | Jul 23, 2026 8:43am | Jul 23, 2026 11:32am | Jul 23, 2026 11:47am | Jul 23, 2026 12:03pm | Jul 23, 2026 12:03pm | Jul 23, 2026 12:03pm |  |  | Fair | No | Customer confirmed issue resolved. Please update thanks.
Non-Outage | J.E.26.02.09570 | C001862893 | Hopeton Henry | St.Thomas | Completed | Load_240437 | Good Year - 210 | Jul 23, 2026 8:04am | Jul 23, 2026 8:05am | Jul 23, 2026 9:39am | Jul 23, 2026 10:27am | Jul 23, 2026 10:30am | Jul 23, 2026 10:37am | Jul 23, 2026 10:40am | Jul 23, 2026 10:40am | TreeContact |  | Fair | No | Cut tree from service wire and reconnect phase , 113-117-230 v
Non-Outage | J.E.26.07.10331 | C001862894 | Hopeton Henry | St.Thomas | Completed | Load_577255 | Good Year - 210 | Jul 23, 2026 8:04am | Jul 23, 2026 8:05am | Jul 23, 2026 9:39am | Jul 23, 2026 10:40am | Jul 23, 2026 11:48am | Jul 23, 2026 11:48am | Jul 23, 2026 11:49am | Jul 23, 2026 11:49am |  |  | Fair | No | Use 3 connector at pole 115- 115-230 volt , issue resolved
Non-Outage | J.E.26.07.10591 | C001862895 | Hopeton Henry | St.Thomas | Completed | Load_262162 | Good Year - 110 | Jul 23, 2026 8:04am | Jul 23, 2026 8:05am | Jul 23, 2026 9:39am | Jul 23, 2026 11:49am | Jul 23, 2026 12:05pm | Jul 23, 2026 12:18pm | Jul 23, 2026 12:19pm | Jul 23, 2026 12:19pm |  |  | Fair | No | Check and found ok
Non-Outage | J.E.26.07.25345 | C001862896 | Marlon Authors | Manchester | Completed | Load_292993 | Spur Tree - 210 | Jul 23, 2026 8:04am | Jul 23, 2026 8:05am | Jul 23, 2026 11:31am | Jul 23, 2026 11:31am | Jul 23, 2026 12:15pm | Jul 23, 2026 2:15pm | Jul 23, 2026 2:16pm | Jul 23, 2026 2:16pm | Fire |  | Fair | No | Supply checked and found low voltage rdg 104v,107v and cross phased 211 volts. Isolate and close 10 kva transformer circuit no pole #, to tap up transformer to tap 5. Reading now 117v,117v and cross phased 235 volts from the drop leads, further checks revealed defective #2 splicing sleeve. Repair same using two feet of #2 conductor and two clamps, supply leave working ok rdg 116v,113v and cross phased 230 volts
Non-Outage | J.E.26.07.25993 | C001862898 | Marlon Authors | Manchester | Completed | Load_258671 | Spur Tree - 210 | Jul 23, 2026 8:04am | Jul 23, 2026 8:05am | Jul 23, 2026 8:57am | Jul 23, 2026 8:57am | Jul 23, 2026 9:40am | Jul 23, 2026 10:25am | Jul 23, 2026 10:25am | Jul 23, 2026 10:25am |  |  | Fair | No | Supply checked and found damaged service wire. Repair same using six linkets and three clamps. Supply leave working okay rdg 113v,110v and cross phased 223 volts
Non-Outage | J.E.26.07.25430 | C001862857 | Odaine Johnson | Clarendon | Completed | Load_269219 | Parnassus - 310 | Jul 23, 2026 8:01am | Jul 23, 2026 8:01am | Jul 23, 2026 1:02pm | Jul 23, 2026 1:03pm | Jul 23, 2026 1:11pm | Jul 23, 2026 1:12pm | Jul 23, 2026 1:12pm | Jul 23, 2026 1:12pm |  |  | Fair | No | Premises found okay voltage reading 115/115/230 volts
Non-Outage | J.E.26.07.25952 | C001862854 | Odaine Johnson | Clarendon | Completed | Load_238965 | Parnassus - 210 | Jul 23, 2026 8:01am | Jul 23, 2026 8:02am | Jul 23, 2026 1:03pm | Jul 23, 2026 2:29pm | Jul 23, 2026 2:49pm | Jul 23, 2026 2:53am | Jul 23, 2026 2:56pm | Jul 23, 2026 2:56pm |  |  | Fair | No | No supply was found at premises because of damaged service wire, wire was peacen and problem was fixed Voltage reading before A0 B0 AB00Voltage reading after A110 B110 AB220
Non-Outage | J.E.26.07.26107 | C001862855 | Odaine Johnson | Clarendon | Completed | Load_263977 | Monymusk - 410 | Jul 23, 2026 8:01am | Jul 23, 2026 8:02am | Jul 23, 2026 10:35am | Jul 23, 2026 10:35am | Jul 23, 2026 11:00am | Jul 23, 2026 11:00am | Jul 23, 2026 11:43am | Jul 23, 2026 11:43am |  |  | Fair | No | Burn off phase found at pole remade connection using 1 one bolt clamp voltage reading 112/108/220 volts
Non-Outage | J.E.26.07.26139 | C001862853 | Neville Spencer | null | Completed | null | null | Jul 23, 2026 8:01am | Jul 23, 2026 8:03am | Jul 23, 2026 12:50pm | Jul 23, 2026 12:51pm | Jul 23, 2026 12:51pm | Jul 23, 2026 12:51pm | Jul 23, 2026 1:03pm | Jul 23, 2026 1:03pm | Fire |  | Fair | No | Open 25 kva xmfr # 011814 splice and retention broken secondary phase Conductor used 50 ft wire, 2 , clamps, 2 , preform , 1 , D iron supply restored.
Non-Outage | J.E.26.07.26359 | C001862851 | Odaine Johnson | Clarendon | Completed | Load_258346 | Parnassus - 210 | Jul 23, 2026 8:01am | Jul 23, 2026 8:04am | Jul 23, 2026 1:03pm | Jul 23, 2026 1:13pm | Jul 23, 2026 2:28pm | Jul 23, 2026 2:28pm | Jul 23, 2026 2:28pm | Jul 23, 2026 2:28pm |  |  | Fair | No | Premises found okay customer said problem was resolved
Non-Outage | J.E.26.07.26447 | C001862849 | Odaine Johnson | Clarendon | Completed | Load_257822 | Parnassus - 310 | Jul 23, 2026 8:00am | Jul 23, 2026 8:04am | Jul 23, 2026 11:45am | Jul 23, 2026 11:45am | Jul 23, 2026 12:44pm | Jul 23, 2026 12:59am | Jul 23, 2026 12:59pm | Jul 23, 2026 12:59pm |  |  | Fair | No | Corrosion was found at service pole 3 one bolt clamps was replaced and problem was fixed Voltage reading before A114 B100 AB214Voltage reading after A114 B115 AB229
Outage | J.E.26.07.26456 | C001862847 | Selvin White | St.Elizabeth | Completed | Load_258901 | Maggotty - 110 | Jul 23, 2026 7:55am | Jul 23, 2026 3:57pm | Jul 23, 2026 6:48pm | Jul 23, 2026 7:31pm | Jul 23, 2026 8:34pm | Jul 23, 2026 8:37pm | Jul 23, 2026 8:37pm | Jul 23, 2026 8:37pm |  |  | Fair | No | Customer says problem was resolved from today by the morning crew.
Non-Outage | J.E.26.07.07997 | C001862842 | Locksley Allen | St.Ann | Completed | Load_270005 | Blackstonedge - 110 | Jul 23, 2026 7:54am | Jul 23, 2026 7:55am | Jul 23, 2026 9:06am | Jul 23, 2026 9:07am | Jul 23, 2026 11:07am | Jul 23, 2026 11:07am | Jul 23, 2026 11:08am | Jul 23, 2026 11:08am |  |  | Fair | No | No light is in the area
Outage | J.E.26.07.26366 | C001862837 | Oshane Warren | St.Elizabeth | Completed | Load_259919 | Maggotty - 110 | Jul 23, 2026 7:54am | Jul 23, 2026 6:18pm | Jul 23, 2026 8:56pm | Jul 23, 2026 8:56pm | Jul 23, 2026 8:56pm | Jul 23, 2026 8:57pm | Jul 23, 2026 8:57pm | Jul 23, 2026 8:57pm |  |  | Fair | No | St Elizabeth call
Non-Outage | J.E.26.07.25947 | C001862836 | Eric Williams | null | Completed | null | null | Jul 23, 2026 7:53am | Jul 23, 2026 4:24pm | Jul 23, 2026 7:25pm | Jul 23, 2026 8:43pm | Jul 23, 2026 9:40pm | Jul 23, 2026 9:54pm | Jul 23, 2026 9:54pm | Jul 23, 2026 9:54pm | BrokenWire |  | Fair | No | Premises found okay
Non-Outage | J.E.26.07.17997 | C001862827 | Oraine Minto | null | Completed | null | null | Jul 23, 2026 7:50am | Jul 23, 2026 7:50am | Jul 24, 2026 1:02pm | Jul 24, 2026 1:31pm | Jul 24, 2026 1:31pm | Jul 24, 2026 1:31pm | Jul 24, 2026 1:32pm | Jul 24, 2026 1:32pm |  |  | Fair | No | 231v 112v 118v
Non-Outage | J.E.26.07.22147 | C001862824 | Oraine Minto | St.Ann | Completed | Load_262944 | Cardiff Hall - 210 | Jul 23, 2026 7:50am | Jul 23, 2026 7:50am | Jul 24, 2026 10:37am | Jul 24, 2026 10:37am | Jul 24, 2026 12:24pm | Jul 24, 2026 12:27pm | Jul 24, 2026 12:35pm | Jul 24, 2026 12:35pm |  |  | Fair | No | Refer to maintenance Transformer overcrowded 50kva #pole 0091783 There is a transformer in the street that look to be damaged need to replace at pole# 019405 and primary need to tension Customer states that the issue happens anytime after 5pm to 9pm in the nights.
Non-Outage | J.E.26.07.23044 | C001862825 | Oraine Minto | St.Ann | Completed | Load_254597 | Cardiff Hall - 210 | Jul 23, 2026 7:50am | Jul 23, 2026 7:50am | Jul 23, 2026 12:57pm | Jul 23, 2026 12:57pm | Jul 23, 2026 12:57pm | Jul 23, 2026 2:05pm | Jul 23, 2026 2:06pm | Jul 23, 2026 2:06pm |  |  | Fair | No | 100ft of #6 3 one bolt clamp was used 3 red to red was used 236v 118v 113v
Non-Outage | J.E.26.07.23662 | C001862826 | Oraine Minto | St.Ann | Completed | Load_258820 | Cardiff Hall - 210 | Jul 23, 2026 7:50am | Jul 23, 2026 7:50am | Jul 23, 2026 9:21am | Jul 23, 2026 9:53am | Jul 23, 2026 9:53am | Jul 23, 2026 9:56am | Jul 23, 2026 9:58am | Jul 23, 2026 9:58am |  |  | Fair | No | 230v 116v 113v
Non-Outage | J.E.26.07.25039 | C001862823 | Oraine Minto | St.Ann | Completed | Load_263508 | Cardiff Hall - 210 | Jul 23, 2026 7:49am | Jul 23, 2026 7:50am | Jul 23, 2026 10:40am | Jul 23, 2026 10:40am | Jul 23, 2026 12:16pm | Jul 23, 2026 12:17pm | Jul 23, 2026 12:21pm | Jul 23, 2026 12:21pm |  |  | Fair | No | 118v Service wire replacement was done2 red to red 2 one bolt clamp was used
Non-Outage | J.E.26.07.25559 | C001862821 | Oraine Minto | St.Ann | Completed | Load_254196 | Cardiff Hall - 210 | Jul 23, 2026 7:49am | Jul 23, 2026 7:50am | Jul 24, 2026 12:44pm | Jul 24, 2026 12:44pm | Jul 24, 2026 12:45pm | Jul 24, 2026 12:45pm | Jul 24, 2026 12:49pm | Jul 24, 2026 12:49pm |  |  | Fair | No | Refer to emergency Secondary lines touching right in front customer house Pole#0121287
Non-Outage | J.E.26.07.25831 | C001862822 | Oraine Minto | St.Ann | Completed | Load_268647 | Cardiff Hall - 210 | Jul 23, 2026 7:49am | Jul 23, 2026 7:50am | Jul 24, 2026 1:01pm | Jul 24, 2026 1:01pm | Jul 24, 2026 1:01pm | Jul 24, 2026 1:01pm | Jul 24, 2026 1:02pm | Jul 24, 2026 1:02pm |  |  | Fair | No | Not getting through to customer
Non-Outage | J.E.26.07.26490 | C001862820 | Fitzroy Turner | null | Completed | null | null | Jul 23, 2026 7:48am | Jul 23, 2026 7:48am | Jul 23, 2026 11:04am | Jul 23, 2026 11:04am | Jul 23, 2026 11:44am | Jul 23, 2026 11:45am | Jul 23, 2026 11:46am | Jul 23, 2026 11:46am |  |  | Fair | No | Found 10kva transformer fuse blown at beckford st replaced one 10 amps fuse supply restored to the areas
Non-Outage | J.E.26.07.26038 | C001862819 | Fitzroy Turner | null | Completed | null | null | Jul 23, 2026 7:47am | Jul 23, 2026 7:47am | Jul 23, 2026 11:46am | Jul 23, 2026 11:46am | Jul 23, 2026 12:07pm | Jul 23, 2026 12:07pm | Jul 23, 2026 12:10pm | Jul 23, 2026 12:10pm | LeaningPole |  | Fair | No | Found 30/6 wooden pole needs to transfer to concrete pole 4 wires open secondary with twisted service wire attached please send email to district to have pole change off
Outage | J.E.26.07.26269 | C001862817 | Neville Spencer | Clarendon | Completed | Load_243173 | May Pen - 210 | Jul 23, 2026 7:43am | Jul 23, 2026 7:43am | Jul 23, 2026 7:48am | Jul 23, 2026 7:48am | Jul 23, 2026 8:30am | Jul 23, 2026 8:30am | Jul 23, 2026 9:32am | Jul 23, 2026 9:32am |  |  | Fair | No | Found broken Primary netural Conductor make safe renew blown 20 amp j/ fuse at pole # 517735 supply restored.
Non-Outage | J.E.26.07.24650 | C001862813 | Damion Reid | Manchester | Completed | Load_1002548 | Kendal - 310 | Jul 23, 2026 7:42am | Jul 23, 2026 7:42am | Jul 23, 2026 8:30am | Jul 23, 2026 8:30am | Jul 23, 2026 9:28am | Jul 23, 2026 10:42am | Jul 23, 2026 10:45am | Jul 23, 2026 10:45am |  |  | Fair | No | Replace 60ft of defective #6 triplex service wire for 3 wire service using 3 one bolt clamp voltage reading at meter socket phase to neutral 113v-114v across phase 229v
Non-Outage | J.E.26.07.24658 | C001862814 | Ryan Richards | Manchester | Completed | Load_257876 | Spur Tree - 310 | Jul 23, 2026 7:42am | Jul 23, 2026 7:43am | Jul 23, 2026 10:14am | Jul 23, 2026 10:14am | Jul 23, 2026 11:34am | Jul 23, 2026 12:42pm | Jul 23, 2026 12:42pm | Jul 23, 2026 12:42pm |  |  | Fair | No | Corroded neutral jumper and corroded splicing sleeve found remade corroded neutral using 2 one bolt clamps jump splicing sleeve using 1 ft#2 aluminum and 2 one bolt clamps customers supply now working ok 115/118/234 volt
Outage | J.E.26.07.25887 | C001862810 | Rusean Allen | KSAS | Completed | Load_245759 | Hunts Bay - 410 | Jul 23, 2026 7:41am | Jul 24, 2026 8:21am | Jul 24, 2026 12:26pm | Jul 24, 2026 12:27pm | Jul 24, 2026 12:27pm | Jul 24, 2026 12:58pm | Jul 24, 2026 12:59pm | Jul 24, 2026 12:59pm |  |  | Fair | No | Premises not found, customer phone went unanswered.
Outage | J.E.26.07.26052 | C001862811 | Damion Reid | Manchester | Completed | Load_267976 | Kendal - 310 | Jul 23, 2026 7:41am | Jul 23, 2026 7:41am | Jul 23, 2026 11:15am | Jul 23, 2026 11:15am | Jul 23, 2026 12:03pm | Jul 23, 2026 12:29pm | Jul 23, 2026 12:30pm | Jul 23, 2026 12:30pm |  |  | Rains | No | Premises found ok
Outage | J.E.26.07.26123 | C001862812 | Rusean Allen | KSAS | Completed | Load_268100 | Cane River - 610 | Jul 23, 2026 7:41am | Jul 23, 2026 7:47am | Jul 23, 2026 12:35pm | Jul 23, 2026 12:35pm | Jul 23, 2026 12:44pm | Jul 23, 2026 12:44pm | Jul 23, 2026 12:45pm | Jul 23, 2026 12:45pm |  |  | Fair | No | Premises okay
Non-Outage | J.E.26.07.18779 | C001862807 | Evan Spaulding | St.Mary | Completed | Load_262869 | Highgate -110 | Jul 23, 2026 7:39am | Jul 23, 2026 7:40am | Jul 23, 2026 8:20am | Jul 23, 2026 8:20am | Jul 23, 2026 9:11am | Jul 23, 2026 11:04am | Jul 23, 2026 11:05am | Jul 23, 2026 11:05am |  |  | Fair | No | Replace 90ft #6 Triplex service wire and 6-1 bolt clamps, voltage left 115v,117v,232v.
Non-Outage | J.E.26.07.19774 | C001862808 | Evan Spaulding | St.Mary | Completed | Load_265883 | Highgate -110 | Jul 23, 2026 7:39am | Jul 23, 2026 7:40am | Jul 23, 2026 12:32pm | Jul 23, 2026 12:32pm | Jul 23, 2026 12:32pm | Jul 23, 2026 12:33pm | Jul 23, 2026 12:33pm | Jul 23, 2026 12:33pm |  |  | Fair | No | Issue was resolved last week
Non-Outage | J.E.26.07.19914 | C001862806 | Evan Spaulding | St.Mary | Completed | Load_265883 | Highgate -110 | Jul 23, 2026 7:39am | Jul 23, 2026 7:40am | Jul 23, 2026 11:06am | Jul 23, 2026 11:06am | Jul 23, 2026 12:31pm | Jul 23, 2026 12:31pm | Jul 23, 2026 12:31pm | Jul 23, 2026 12:31pm |  |  | Fair | No | Customer says issue was resolved from last week
Non-Outage | J.E.26.07.21381 | C001862804 | Evan Spaulding | St.Mary | Completed | Load_254528 | Highgate -110 | Jul 23, 2026 7:39am | Jul 23, 2026 7:40am | Jul 23, 2026 1:46pm | Jul 23, 2026 1:46pm | Jul 24, 2026 8:04am | Jul 24, 2026 8:04am | Jul 24, 2026 8:05am | Jul 24, 2026 8:05am |  |  | Fair | No | Premises not found
Non-Outage | J.E.26.07.25679 | C001862809 | Ryan Richards | null | Completed | null | null | Jul 23, 2026 7:39am | Jul 23, 2026 7:40am | Jul 23, 2026 9:00am | Jul 23, 2026 9:00am | Jul 23, 2026 9:37am | Jul 23, 2026 10:13am | Jul 23, 2026 10:13am | Jul 23, 2026 10:13am | BrokenWire |  | Fair | No | Service wire found hanging low cause by rubbish truck customer Stanton broken down and needed to be replaced customer was advised to carry out repairs
Non-Outage | J.E.26.07.26122 | C001862803 | Ryan Richards | null | Completed | null | null | Jul 23, 2026 7:39am | Jul 23, 2026 7:40am | Jul 23, 2026 7:48am | Jul 23, 2026 7:48am | Jul 23, 2026 8:44am | Jul 23, 2026 8:56am | Jul 23, 2026 8:56am | Jul 23, 2026 8:56am |  |  | Fair | No | Blown 3 amp fuse found for 25 kva transformer line patrol nothing found lighting suspected to be the cause all customers are now with supply
Outage | J.E.26.07.26464 | C001862800 | Nickolas Rodriques | St.Catherine | Completed | Load_243462 | Twickenham - 410 | Jul 23, 2026 7:37am | Jul 23, 2026 1:01pm | Jul 23, 2026 1:37pm | Jul 23, 2026 2:04pm | Jul 23, 2026 2:49pm | Jul 23, 2026 3:08pm | Jul 23, 2026 3:09pm | Jul 23, 2026 3:09pm |  |  | Fair | No | Customer was contacted and stated that no one is currently home. However the area was patrolled and no noticeable outage was found.
Outage | J.E.26.07.26496 | C001862799 | Delano Gayle | St.Catherine | Completed | Load_239794 | Tredegar - 210 | Jul 23, 2026 7:37am | Jul 23, 2026 11:53pm | Jul 24, 2026 12:28am | Jul 24, 2026 12:28am | Jul 24, 2026 1:14am | Jul 24, 2026 2:05am | Jul 24, 2026 2:05am | Jul 24, 2026 2:05am |  |  | Fair | No | Single customer premises not found area found okay
Outage | J.E.26.07.26469 | C001862794 | Jermaine Williams | Clarendon | Completed | Load_568659 | Parnassus - 310 | Jul 23, 2026 7:35am | Jul 23, 2026 4:04pm | Jul 23, 2026 8:34pm | Jul 23, 2026 8:34pm | Jul 23, 2026 9:01pm | Jul 23, 2026 9:04pm | Jul 23, 2026 9:04pm | Jul 23, 2026 9:04pm |  |  | Fair | No | Premises found ok.
Non-Outage | J.E.26.07.26431 | C001862793 | Hartley Chin | null | Completed | null | null | Jul 23, 2026 7:34am | Jul 23, 2026 7:34am | Jul 23, 2026 8:43am | Jul 23, 2026 1:43pm | Jul 23, 2026 1:43pm | Jul 23, 2026 2:14pm | Jul 23, 2026 2:19pm | Jul 23, 2026 2:19pm |  |  | Rains | No | Found 10 KVA transformer Trip , line patrolled and reset
Outage | J.E.26.07.25893 | C001862792 | Neville Spencer | Clarendon | Completed | Load_247436 | Parnassus - 210 | Jul 23, 2026 7:33am | Jul 23, 2026 7:33am | Jul 23, 2026 10:08am | Jul 23, 2026 10:08am | Jul 23, 2026 10:48am | Jul 23, 2026 10:48am | Jul 23, 2026 11:03am | Jul 23, 2026 11:03am |  |  | Fair | No | Renew blown 30 j/ fuse at pole #568660 area restored
Non-Outage | J.E.26.07.10128 | C001862790 | Raymond Carr | St.Mary | Completed | Load_241937 | Oracabessa - 110 | Jul 23, 2026 7:32am | Jul 23, 2026 7:33am | Jul 23, 2026 8:45am | Jul 23, 2026 8:45am | Jul 23, 2026 8:58am | Jul 23, 2026 8:43am | Jul 23, 2026 9:00am | Jul 23, 2026 9:00am |  |  | Fair | No | Customer reported that she had fault corrected.
Non-Outage | J.E.26.07.10425 | C001862789 | Raymond Carr | St.Mary | Completed | Load_243605 | Oracabessa - 110 | Jul 23, 2026 7:32am | Jul 23, 2026 7:33am | Jul 23, 2026 11:24am | Jul 23, 2026 11:24am | Jul 23, 2026 12:26pm | Jul 23, 2026 12:16am | Jul 23, 2026 12:28pm | Jul 23, 2026 12:28pm |  |  | Fair | No | Customer reported that fault was corrected, and supply is normal.
Non-Outage | J.E.26.07.12042 | C001862788 | Raymond Carr | St.Mary | Completed | Load_243605 | Oracabessa - 110 | Jul 23, 2026 7:32am | Jul 23, 2026 7:33am | Jul 23, 2026 12:28pm | Jul 23, 2026 12:28pm | Jul 23, 2026 2:12pm | Jul 23, 2026 2:05pm | Jul 23, 2026 2:18pm | Jul 23, 2026 2:18pm |  |  | Fair | No | Customer reported that supply is okay.
Non-Outage | J.E.26.07.18065 | C001862785 | Raymond Carr | St.Mary | Completed | Load_350817 | Oracabessa - 110 | Jul 23, 2026 7:32am | Jul 23, 2026 7:33am | Jul 23, 2026 9:01am | Jul 23, 2026 9:01am | Jul 23, 2026 10:45am | Jul 23, 2026 11:07am | Jul 23, 2026 11:23am | Jul 23, 2026 11:23am |  |  | Fair | No | Three defective clamps replaced at transformer drop leads. Voltage readings 120/120/240.
Outage | J.E.26.07.26448 | C001862791 | Hartley Chin | Clarendon | Completed | Load_237880 | May Pen - 110 | Jul 23, 2026 7:32am | Jul 23, 2026 7:33am | Jul 23, 2026 8:41am | Jul 23, 2026 8:41am | Jul 23, 2026 8:41am | Jul 23, 2026 8:42am | Jul 23, 2026 8:42am | Jul 23, 2026 8:42am |  |  | Fair | No | Found ok
Non-Outage | J.E.26.07.26083 | C001862782 | Neville Spencer | null | Completed | null | null | Jul 23, 2026 7:31am | Jul 23, 2026 7:32am | Jul 23, 2026 9:33am | Jul 23, 2026 9:33am | Jul 23, 2026 9:51am | Jul 23, 2026 9:55am | Jul 23, 2026 9:58am | Jul 23, 2026 9:58am | BrokenPole |  | Fair | No | Found 40 ft wooden pole defective construction D E with 3 phase primary line and open secondary lines back to back ,street lights not working pole # 157336
Non-Outage | J.E.26.07.26158 | C001862783 | Neville Spencer | null | Completed | null | null | Jul 23, 2026 7:31am | Jul 23, 2026 7:32am | Jul 23, 2026 1:04pm | Jul 23, 2026 1:04pm | Jul 23, 2026 1:04pm | Jul 23, 2026 1:04pm | Jul 23, 2026 1:08pm | Jul 23, 2026 1:08pm | Fire |  | Fair | No | Open 25 kva xmf at pole # 012814 splice and retention broken secondary phase Conductor used 50 ft wire, 2 , preform , 2 , clamps ,1 , D iron supply restored.
Outage | J.E.26.07.26318 | C001862776 | Wan Carlos Scarlett | Portmore | Completed | Load_239358 | Naggo Head - 510 | Jul 23, 2026 7:28am | Jul 23, 2026 7:28am | Jul 23, 2026 8:46am | Jul 23, 2026 8:49am | Jul 23, 2026 9:22am | Jul 23, 2026 9:55am | Jul 23, 2026 9:57am | Jul 23, 2026 9:57am |  |  | Fair | No | Refuse 25KVA transformer with a 3amp fuse pole # 014382 clear from off transformer bushing
Outage | J.E.26.07.26470 | C001862774 | Raymond Lewis | St.Ann | Completed | Load_267559 | Roaring River - 410 | Jul 23, 2026 7:27am | Jul 23, 2026 7:29am | Jul 23, 2026 10:18am | Jul 23, 2026 10:18am | Jul 23, 2026 10:54am | Jul 23, 2026 11:08am | Jul 23, 2026 11:09am | Jul 23, 2026 11:09am |  |  | Fair | No | Refuse and close 25 amp junction
Outage | J.E.26.07.26477 | C001862775 | Raymond Lewis | St.Ann | Completed | Load_259787 | Roaring River - 410 | Jul 23, 2026 7:27am | Jul 23, 2026 7:29am | Jul 23, 2026 11:51am | Jul 23, 2026 11:51am | Jul 23, 2026 12:08pm | Jul 23, 2026 12:09pm | Jul 23, 2026 12:09pm | Jul 23, 2026 12:09pm |  |  | Fair | No | Phone not answering
Non-Outage | J.E.26.07.22954 | C001862771 | Omar King | St.Ann | Completed | Load_412814 | Roaring River - 210 | Jul 23, 2026 7:25am | Jul 23, 2026 7:26am | Jul 23, 2026 9:18am | Jul 23, 2026 9:18am | Jul 23, 2026 10:26am | Jul 23, 2026 10:55am | Jul 23, 2026 10:55am | Jul 23, 2026 10:55am | LowHangingWires |  | Fair | No | Found wire hanging low I observed
Outage | J.E.26.07.26209 | C001862768 | Christopher Edwards | KSAN | Completed | Load_244326 | Washington Blvd - 510 | Jul 23, 2026 7:25am | Jul 23, 2026 7:27am | Jul 23, 2026 10:28am | Jul 23, 2026 10:28am | Jul 23, 2026 10:42am | Jul 23, 2026 11:05am | Jul 23, 2026 11:06am | Jul 23, 2026 11:06am |  |  | Fair | No | Customer was disconnected for non payment Customer was advised to pay bill before service can be reconnected
Outage | J.E.26.07.26246 | C001862770 | Christopher Edwards | KSAN | Completed | Load_248279 | Washington Blvd - 810 | Jul 23, 2026 7:25am | Jul 23, 2026 7:27am | Jul 23, 2026 8:07am | Jul 23, 2026 8:34am | Jul 23, 2026 8:34am | Jul 23, 2026 9:21am | Jul 23, 2026 9:22am | Jul 23, 2026 9:22am |  |  | Fair | No | Customer pre paid device is not accepting the credit Required field service to rectify issue
Outage | J.E.26.07.26459 | C001862772 | Milton Charlton | KSAS | Completed | Load_240463 | Up Park Camp - 410 | Jul 23, 2026 7:25am | Jul 23, 2026 7:27am | Jul 23, 2026 11:45am | Jul 23, 2026 11:45am | Jul 23, 2026 11:46am | Jul 23, 2026 10:20am | Jul 23, 2026 11:48am | Jul 23, 2026 11:48am |  |  | Fair | No | Call related to other call at 17 Latham Avenue.
Non-Outage | J.E.26.07.26096 | C001862767 | Andre Smith | null | Completed | null | null | Jul 23, 2026 7:24am | Jul 23, 2026 12:09pm | Jul 23, 2026 12:18pm | Jul 23, 2026 12:18pm | Jul 23, 2026 12:55pm | Jul 23, 2026 1:58pm | Jul 23, 2026 2:00pm | Jul 23, 2026 2:00pm |  |  | Fair | No | Repair burnt primary jumper supply restored
Non-Outage | J.E.26.07.26205 | C001862766 | Wan Carlos Scarlett | Portmore | Completed | Load_261160 | Naggo Head - 510 | Jul 23, 2026 7:23am | Jul 23, 2026 7:24am | Jul 23, 2026 9:31am | Jul 23, 2026 10:01am | Jul 23, 2026 10:32am | Jul 23, 2026 11:03am | Jul 23, 2026 11:05am | Jul 23, 2026 11:05am | Fire |  | Fair | No | Found one span of open secondary line phase jumper burn out from the one bolt clamp use 2 one bolt clamps at pole readings 117-116-234
Outage | J.E.26.07.25778 | C001862758 | Nickolas Rodriques | St.Catherine | Completed | Load_568270 | New Michelton - 410 | Jul 23, 2026 7:18am | Jul 23, 2026 7:19am | Jul 23, 2026 11:05am | Jul 23, 2026 11:18am | Jul 23, 2026 12:53pm | Jul 23, 2026 1:14pm | Jul 23, 2026 1:32pm | Jul 23, 2026 1:32pm |  |  | Fair | No | Checked and found a 10 amp junction fuse blown. Patrol and found nothing on line. Repaired placed by replacing the fuse after completing patrol.
Outage | J.E.26.07.26051 | C001862756 | Richard Grant | St.Catherine | Completed | Load_246045 | Tredegar - 510 | Jul 23, 2026 7:18am | Jul 23, 2026 7:55am | Jul 23, 2026 11:18am | Jul 23, 2026 11:18am | Jul 23, 2026 11:18am | Jul 23, 2026 11:19am | Jul 23, 2026 11:19am | Jul 23, 2026 11:19am |  |  | Fair | No | Customer get supply from HEXIM box. Kindly refer call to Moses
Outage | J.E.26.07.26393 | C001862753 | Richard Grant | St.Catherine | Completed | Load_248862 | Tredegar - 510 | Jul 23, 2026 7:18am | Jul 23, 2026 7:42am | Jul 23, 2026 7:58am | Jul 23, 2026 7:58am | Jul 23, 2026 10:25am | Jul 23, 2026 10:39am | Jul 23, 2026 10:39am | Jul 23, 2026 10:39am | Fire |  | Fair | No | Premises visited, no sparking nor fire seen at time of visit. Premises found and left okay and with supply
Outage | J.E.26.07.26441 | C001862750 | Nickolas Rodriques | St.Catherine | Completed | Load_263099 | Tredegar - 310 | Jul 23, 2026 7:18am | Jul 23, 2026 7:21am | Jul 23, 2026 9:06am | Jul 23, 2026 9:06am | Jul 23, 2026 9:56am | Jul 23, 2026 10:25am | Jul 23, 2026 10:32am | Jul 23, 2026 10:32am |  |  | Fair | No | Checked and found a 20 amp junction fuse blown. Patrol and found nothing on line. Repaired by replacing the fuse after completing patrol.
Outage | J.E.26.07.26442 | C001862748 | Nickolas Rodriques | St.Catherine | Completed | Load_254900 | Tredegar - 310 | Jul 23, 2026 7:18am | Jul 23, 2026 7:22am | Jul 23, 2026 10:45am | Jul 23, 2026 10:49am | Jul 23, 2026 10:58am | Jul 23, 2026 11:03am | Jul 23, 2026 11:05am | Jul 23, 2026 11:05am |  |  | Fair | No | Power restored. Call relates to the 20 amp junction fuse that was replaced.
Outage | J.E.26.07.26443 | C001862747 | Nickolas Rodriques | St.Catherine | Completed | Load_260327 | Tredegar - 310 | Jul 23, 2026 7:18am | Jul 23, 2026 7:22am | Jul 23, 2026 10:32am | Jul 23, 2026 10:35am | Jul 23, 2026 10:38am | Jul 23, 2026 10:43am | Jul 23, 2026 10:45am | Jul 23, 2026 10:45am |  |  | Fair | No | Power restored. Call relates to the 20 amp junction fuse that was replaced.
Non-Outage | J.E.26.07.26251 | C001862741 | Collin Robinson | null | Completed | null | null | Jul 23, 2026 7:12am | Jul 23, 2026 7:12am | Jul 23, 2026 9:26am | Jul 23, 2026 9:26am | Jul 23, 2026 9:31am | Jul 23, 2026 9:36am | Jul 23, 2026 9:36am | Jul 23, 2026 9:36am | Fire |  | Rains | No | Information received firefighter that realized they were no current and premises after making the report
Non-Outage | J.E.26.07.26476 | C001862740 | Collin Robinson | Portland | Completed | Load_259838 | Port Antonio - 410 | Jul 23, 2026 7:12am | Jul 23, 2026 7:12am | Jul 23, 2026 9:37am | Jul 23, 2026 9:37am | Jul 23, 2026 11:10am | Jul 23, 2026 11:34am | Jul 23, 2026 11:35am | Jul 23, 2026 11:35am | BrokenWire |  | Fair | No | Isolate 25KVA transformer to splice and retention one span of broken open secondary conductor Voltage reading 118v 118v 236v
Outage | J.E.26.07.26465 | C001862739 | Collin Robinson | Portland | Completed | Load_261986 | Port Antonio - 310 | Jul 23, 2026 7:12am | Jul 23, 2026 7:12am | Jul 23, 2026 8:31am | Jul 23, 2026 8:31am | Jul 23, 2026 9:05am | Jul 23, 2026 9:26am | Jul 23, 2026 9:26am | Jul 23, 2026 9:26am |  |  | Rains | No | Splice and retention two pole span of broken open secondary conductor And replace 3 amps fuse at pole 0014593
Outage | J.E.26.07.26307 | C001862686 | Horace Malcolm | St.James | Completed | Load_251205 | Queens Drive - 710 | Jul 23, 2026 5:01am | Jul 23, 2026 5:01am | Jul 23, 2026 6:39am | Jul 23, 2026 6:39am | Jul 23, 2026 7:50am | Jul 23, 2026 8:12am | Jul 23, 2026 8:12am | Jul 23, 2026 8:12am | Fire |  | Fair | No | Remove illegal connections from secondary line causing spark on wires
Non-Outage | J.E.26.07.26285 | C001862682 | Edward Royal | null | Completed | null | null | Jul 23, 2026 1:03am | Jul 23, 2026 7:36am | Jul 23, 2026 2:47pm | Jul 23, 2026 2:47pm | Jul 23, 2026 2:47pm | Jul 23, 2026 2:48pm | Jul 23, 2026 2:49pm | Jul 23, 2026 2:49pm | Fire |  | Fair | No | Replaced 2A transformer fuse
Outage | J.E.26.07.26296 | C001862683 | Rusean Allen | KSAS | Completed | Load_238206 | Cane River - 410 | Jul 23, 2026 1:03am | Jul 23, 2026 1:03am | Jul 23, 2026 8:51am | Jul 23, 2026 8:51am | Jul 23, 2026 11:30am | Jul 23, 2026 11:34am | Jul 23, 2026 11:35am | Jul 23, 2026 11:35am |  |  | Fair | No | 1x 10amp fuse found 1x 10amp fuse replaced 1x 30amp fuse found 1x 30amp fuse replaced.
Non-Outage | J.E.26.07.25583 | C001862669 | Horace Malcolm | null | Completed | null | null | Jul 22, 2026 11:36pm | Jul 22, 2026 11:37pm | Jul 23, 2026 1:52am | Jul 23, 2026 1:53am | Jul 23, 2026 2:49am | Jul 23, 2026 3:29am | Jul 23, 2026 3:29am | Jul 23, 2026 3:29am |  |  | Fair | No | Check and found customer having no supply coming from EG referred to field service
Outage | J.E.26.07.24745 | C001862671 | Horace Malcolm | St.James | Completed | Load_242717 | Bogue - 310 | Jul 22, 2026 11:36pm | Jul 22, 2026 11:37pm | Jul 23, 2026 12:22am | Jul 23, 2026 12:22am | Jul 23, 2026 12:41am | Jul 23, 2026 12:56am | Jul 23, 2026 12:56am | Jul 23, 2026 12:56am |  |  | Fair | No | Unable to locate premises from directions given calls to customer,customer says wrong number
Outage | J.E.26.07.25560 | C001862668 | Horace Malcolm | St.James | Completed | Load_237816 | Rose Hall - 210 | Jul 22, 2026 11:36pm | Jul 22, 2026 11:37pm | Jul 23, 2026 12:57am | Jul 23, 2026 12:57am | Jul 23, 2026 1:22am | Jul 23, 2026 1:52am | Jul 23, 2026 1:52am | Jul 23, 2026 1:52am | LeaningPole |  | Fair | No | Found one secondary 35ft wooden pole leaning down pole foot rotten the premises located from directions given have no occupant the meter number in report and meter at premises are different call to customer unavailable voltage reading from pothead 113-115-228
Outage | J.E.26.07.25698 | C001862670 | Horace Malcolm | St.James | Completed | Load_248472 | Bogue - 310 | Jul 22, 2026 11:36pm | Jul 22, 2026 11:37pm | Jul 23, 2026 3:30am | Jul 23, 2026 3:30am | Jul 23, 2026 4:49am | Jul 23, 2026 4:50am | Jul 23, 2026 4:50am | Jul 23, 2026 4:50am |  |  | Fair | No | Premises not found from directions phone call unavailable
Non-Outage | J.E.26.07.05201 | C001862667 | Richard Nicholas | null | Completed | null | null | Jul 22, 2026 11:33pm | Jul 23, 2026 8:40am | Jul 23, 2026 10:25am | Jul 23, 2026 10:26am | Jul 23, 2026 10:26am | Jul 23, 2026 10:31am | Jul 23, 2026 10:32am | Jul 23, 2026 10:32am | LowHangingWires |  | Fair | No | Retention low hanging #6 triplex service wire.
Outage | J.E.26.07.25810 | C001862664 | Delano Gayle | St.Catherine | Completed | Load_264046 | Rhodens Pen - 410 | Jul 22, 2026 11:04pm | Jul 22, 2026 11:06pm | Jul 23, 2026 2:43am | Jul 23, 2026 4:50am | Jul 23, 2026 5:47am | Jul 23, 2026 6:07am | Jul 23, 2026 6:08am | Jul 23, 2026 6:08am | BrokenPole |  | Fair | No | Broken down 35c6 pole, CV construction with single phase primary, open secondary back to back,2 torn down customer service wires, 4 back guy, torn down telecommunications wires, line section isolated as junction fuse was found blown out by main, send call to maintenance urgent attention needed
Outage | J.E.26.07.26174 | C001862656 | Stephen Taylor | St.Thomas | Completed | Load_260689 | Good Year - 110 | Jul 22, 2026 10:16pm | Jul 22, 2026 10:16pm | Jul 22, 2026 10:20pm | Jul 22, 2026 10:20pm | Jul 22, 2026 10:20pm | Jul 22, 2026 10:20pm | Jul 22, 2026 10:22pm | Jul 22, 2026 10:22pm |  |  | Fair | No | Patrol clear line and close up 25 kva transformer safely all customer is now okay
Non-Outage | J.E.26.07.26191 | C001862653 | Collin Robinson | null | Completed | null | null | Jul 22, 2026 10:07pm | Jul 22, 2026 10:07pm | Jul 23, 2026 7:33am | Jul 23, 2026 7:33am | Jul 23, 2026 8:23am | Jul 23, 2026 8:29am | Jul 23, 2026 8:29am | Jul 23, 2026 8:29am | Fire |  | Fair | No | Change corroded one bolt clamp at pole Voltage reading 118v 118v 236v
Outage | J.E.26.07.26130 | C001862646 | Shamour Haughton | St.James | Completed | Load_256990 | Queens Drive - 710 | Jul 22, 2026 9:18pm | Jul 22, 2026 9:18pm | Jul 22, 2026 10:19pm | Jul 22, 2026 10:19pm | Jul 22, 2026 10:19pm | Jul 22, 2026 10:19pm | Jul 22, 2026 10:20pm | Jul 22, 2026 10:20pm | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Related to previous call
Outage | J.E.26.07.26145 | C001862639 | Fitzroy Turner | KSAS | Completed | Load_251504 | Hunts Bay - 510 | Jul 22, 2026 9:11pm | Jul 22, 2026 9:11pm | Jul 22, 2026 9:37pm | Jul 22, 2026 9:37pm | Jul 22, 2026 9:37pm | Jul 22, 2026 9:58pm | Jul 22, 2026 10:22pm | Jul 22, 2026 10:22pm |  |  | Fair | No | Found 50kva transformer fuse blown at the intersection of north avenue and locket avenue.replace one 5amps fuse and fuse holder.supply restored to areas
Outage | J.E.26.07.26040 | C001862637 | Delano Gayle | Portmore | Completed | Load_242156 | Naggo Head - 510 | Jul 22, 2026 8:56pm | Jul 22, 2026 11:09pm | Jul 23, 2026 1:16am | Jul 23, 2026 1:16am | Jul 23, 2026 1:54am | Jul 23, 2026 2:13am | Jul 23, 2026 2:13am | Jul 23, 2026 2:13am | Fire |  | Fair | No | Premises found okay,Burnt off telecommunications wires advised customer
Outage | J.E.26.07.25261 | C001862608 | Moses Elliston | St.Catherine | Completed | Load_1001436 | Tredegar - 210 | Jul 22, 2026 8:25pm | Jul 22, 2026 8:43pm | Jul 23, 2026 10:07am | Jul 23, 2026 10:07am | Jul 23, 2026 10:07am | Jul 22, 2026 11:26am | Jul 23, 2026 10:09am | Jul 23, 2026 10:09am |  |  | Fair | No | Credit added to prepaid account
Outage | J.E.26.07.25438 | C001862605 | Richman Whyte | Westmoreland | Completed | Load_250796 | Paradise - 210 | Jul 22, 2026 8:19pm | Jul 22, 2026 8:19pm | Jul 22, 2026 8:53pm | Jul 22, 2026 8:53pm | Jul 22, 2026 9:42pm | Jul 22, 2026 9:55pm | Jul 22, 2026 10:48pm | Jul 22, 2026 10:48pm |  |  | Fair | No | Replace 25 kva transformer fuse
Outage | J.E.26.07.26043 | C001862603 | Richard Samuda | Manchester | Completed | Load_266353 | Kendal - 210 | Jul 22, 2026 8:15pm | Jul 22, 2026 8:16pm | Jul 22, 2026 8:22pm | Jul 22, 2026 8:46pm | Jul 22, 2026 9:27pm | Jul 22, 2026 10:01pm | Jul 22, 2026 10:02pm | Jul 22, 2026 10:02pm |  |  | Fair | No | Found 30amp junction fuse blown patrol line found nothing replaced fuse close line customer back to normal
Outage | J.E.26.07.25803 | C001862601 | Michael Christian | St.James | Completed | Load_246965 | Bogue - 310 | Jul 22, 2026 8:12pm | Jul 22, 2026 8:12pm | Jul 22, 2026 9:49pm | Jul 22, 2026 9:49pm | Jul 22, 2026 10:38pm | Jul 22, 2026 11:12pm | Jul 22, 2026 11:13pm | Jul 22, 2026 11:13pm |  |  | Fair | No | Found 1 10 kava out reset cause by cable wire
Outage | J.E.26.07.25998 | C001862599 | Barnett Brown | Manchester | Completed | Load_294493 | Spur Tree - 210 | Jul 22, 2026 8:06pm | Jul 22, 2026 8:07pm | Jul 22, 2026 8:20pm | Jul 22, 2026 8:20pm | Jul 22, 2026 9:33pm | Jul 22, 2026 10:15pm | Jul 22, 2026 10:19pm | Jul 22, 2026 10:19pm |  |  | Fair | No | Patrol line, found nothing, replace blown 30 amp junction fuse.
Outage | J.E.26.07.25717 | C001862597 | Rusean Allen | KSAS | Completed | Load_260015 | Greenwich - 710 | Jul 22, 2026 8:05pm | Jul 22, 2026 10:34pm | Jul 22, 2026 11:57pm | Jul 22, 2026 11:57pm | Jul 23, 2026 12:08am | Jul 23, 2026 12:21am | Jul 23, 2026 12:21am | Jul 23, 2026 12:21am |  |  | Fair | No | Found 2 40 amps fuseReplaced 2 40 amps fuse
Outage | J.E.26.07.25910 | C001862596 | Fitzroy Turner | KSAS | Completed | Load_251504 | Hunts Bay - 510 | Jul 22, 2026 8:02pm | Jul 22, 2026 8:03pm | Jul 22, 2026 8:08pm | Jul 22, 2026 8:08pm | Jul 22, 2026 8:09pm | Jul 22, 2026 8:10pm | Jul 22, 2026 8:16pm | Jul 22, 2026 8:16pm |  |  | Fair | No | Found tree 50 amps at pole number #617996 no fault found tree 50 amps fuse replaced at the intersection of north street and locket avenue
Outage | J.E.26.07.25795 | C001862595 | Andre Smith | KSAS | Completed | Load_242370 | Greenwich - 710 | Jul 22, 2026 7:58pm | Jul 23, 2026 7:50am | Jul 23, 2026 9:00am | Jul 23, 2026 9:00am | Jul 23, 2026 9:56am | Jul 23, 2026 10:52am | Jul 23, 2026 10:52am | Jul 23, 2026 10:52am | TreeContact |  | Fair | No | Reconnect 80ft #6 triplex service wire supply restored 112V
Outage | J.E.26.07.25745 | C001862591 | Edward Royal | KSAS | Completed | Load_242712 | Duhaney - 410 | Jul 22, 2026 7:49pm | Jul 23, 2026 7:33am | Jul 23, 2026 10:00am | Jul 23, 2026 10:00am | Jul 23, 2026 10:00am | Jul 23, 2026 11:08am | Jul 23, 2026 11:08am | Jul 23, 2026 11:08am |  |  | Fair | No | Replaced 2 30A junction fuse.it was not easy I did of to clear rubbish from pole foot and cutting down a maca tree.
Outage | J.E.26.07.25986 | C001862590 | Edward Royal | KSAS | Completed | Load_569191 | Duhaney - 410 | Jul 22, 2026 7:49pm | Jul 23, 2026 7:35am | Jul 23, 2026 2:09pm | Jul 23, 2026 2:09pm | Jul 23, 2026 2:09pm | Jul 23, 2026 2:47pm | Jul 23, 2026 2:47pm | Jul 23, 2026 2:47pm |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.07.26070 | C001862588 | Shamour Haughton | St.James | Completed | Load_293410 | Queens Drive - 310 | Jul 22, 2026 7:46pm | Jul 22, 2026 7:46pm | Jul 22, 2026 10:21pm | Jul 22, 2026 10:21pm | Jul 22, 2026 10:21pm | Jul 22, 2026 10:21pm | Jul 22, 2026 10:22pm | Jul 22, 2026 10:22pm |  |  | Fair | No | Related to previous call
Outage | J.E.26.07.26079 | C001862589 | Shamour Haughton | St.James | Completed | Load_293234 | Queens Drive - 310 | Jul 22, 2026 7:46pm | Jul 22, 2026 7:46pm | Jul 22, 2026 9:38pm | Jul 22, 2026 9:38pm | Jul 22, 2026 10:08pm | Jul 22, 2026 10:18pm | Jul 22, 2026 10:18pm | Jul 22, 2026 10:18pm |  |  | Fair | No | Found insulator defective, change insulator and refuse one 15amp junction fuse
Outage | J.E.26.07.25721 | C001862584 | Fitzroy Turner | KSAS | Completed | Load_266084 | Rockfort - 410 | Jul 22, 2026 7:29pm | Jul 22, 2026 7:48pm | Jul 22, 2026 9:13pm | Jul 22, 2026 9:13pm | Jul 22, 2026 9:32pm | Jul 22, 2026 9:33pm | Jul 22, 2026 9:36pm | Jul 22, 2026 9:36pm |  |  | Rains | No | Pole #600315 at the intersection of st James and lighbourne st found 10 amp junction fuse blown replace with the same 10 amp fuse supply restored to the areas
Outage | J.E.26.07.25940 | C001862581 | Delano Gayle | St.Catherine | Completed | Load_244281 | Tredegar - 510 | Jul 22, 2026 7:29pm | Jul 22, 2026 11:06pm | Jul 23, 2026 12:19am | Jul 23, 2026 12:19am | Jul 23, 2026 12:50am | Jul 23, 2026 1:16am | Jul 23, 2026 1:16am | Jul 23, 2026 1:16am | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Found customer pothead wire disconnected, reconnect using 2 linkets, customer neighbor had burnt wires at pothead, disconnect pothead and make safe as wire was sparking, advised customer
Outage | J.E.26.07.25742 | C001862579 | Rusean Allen | KSAS | Completed | Load_239100 | Hunts Bay - 410 | Jul 22, 2026 7:28pm | Jul 22, 2026 10:34pm | Jul 23, 2026 12:58am | Jul 23, 2026 2:27am | Jul 23, 2026 2:27am | Jul 23, 2026 2:28am | Jul 23, 2026 2:28am | Jul 23, 2026 2:28am |  |  | Fair | No | Related to race course lane
Outage | J.E.26.07.25966 | C001862578 | Rusean Allen | KSAS | Completed | Load_266467 | Hunts Bay - 310 | Jul 22, 2026 7:28pm | Jul 22, 2026 10:34pm | Jul 23, 2026 12:58am | Jul 23, 2026 2:29am | Jul 23, 2026 2:29am | Jul 23, 2026 2:30am | Jul 23, 2026 2:30am | Jul 23, 2026 2:30am |  |  | Fair | No | Related
Outage | J.E.26.07.25996 | C001862580 | Delano Gayle | St.Catherine | Completed | Load_568831 | Twickenham - 310 | Jul 22, 2026 7:28pm | Jul 22, 2026 11:07pm | Jul 22, 2026 11:22pm | Jul 22, 2026 11:22pm | Jul 23, 2026 12:12am | Jul 23, 2026 12:18am | Jul 23, 2026 12:18am | Jul 23, 2026 12:18am | BrokenPole |  | Fair | No | No broken JPS pole seen. Broken telecommunications pole with telecommunications leaning down in road way
Outage | J.E.26.07.25706 | C001862577 | Rusean Allen | KSAS | Completed | Load_264363 | Hunts Bay - 410 | Jul 22, 2026 7:27pm | Jul 22, 2026 10:34pm | Jul 23, 2026 12:57am | Jul 23, 2026 2:28am | Jul 23, 2026 2:28am | Jul 23, 2026 2:29am | Jul 23, 2026 2:29am | Jul 23, 2026 2:29am |  |  | Fair | No | Related to race course lane
Outage | J.E.26.07.25962 | C001862572 | Eric Williams | KSAS | Completed | Load_254675 | Duhaney - 310 | Jul 22, 2026 7:08pm | Jul 22, 2026 7:08pm | Jul 22, 2026 7:14pm | Jul 22, 2026 7:14pm | Jul 22, 2026 8:10pm | Jul 22, 2026 8:22pm | Jul 22, 2026 8:22pm | Jul 22, 2026 8:22pm |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.25967 | C001862571 | Eric Williams | KSAS | Completed | Load_254791 | Duhaney - 310 | Jul 22, 2026 7:08pm | Jul 22, 2026 7:08pm | Jul 22, 2026 8:22pm | Jul 22, 2026 8:22pm | Jul 22, 2026 8:48pm | Jul 22, 2026 8:48pm | Jul 22, 2026 8:48pm | Jul 22, 2026 8:48pm |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.25676 | C001862568 | Fitzroy Turner | KSAS | Completed | Load_244159 | Hunts Bay - 310 | Jul 22, 2026 6:58pm | Jul 22, 2026 6:59pm | Jul 22, 2026 8:18pm | Jul 22, 2026 8:18pm | Jul 22, 2026 8:36pm | Jul 22, 2026 9:08pm | Jul 22, 2026 9:12pm | Jul 22, 2026 9:12pm |  |  | Fair | No | Found 20 amps junction fuse blown at the intersection pole #507109 heroes circle and wild st found primary jumper burnt off .use one #2 ampact and one 20 amps fuse to carry out repair supply restored to areas
Outage | J.E.26.07.25916 | C001862564 | Edward Royal | KSAS | Completed | Load_244743 | Hunts Bay - 810 | Jul 22, 2026 6:56pm | Jul 23, 2026 7:36am | Jul 23, 2026 11:09am | Jul 23, 2026 11:09am | Jul 23, 2026 11:42am | Jul 23, 2026 11:52am | Jul 23, 2026 11:53am | Jul 23, 2026 11:53am |  |  | Fair | No | Premises found close
Outage | J.E.26.07.25442 | C001862561 | Nickolas Rodriques | Portmore | Completed | Load_412899 | Naggo Head - 510 | Jul 22, 2026 6:49pm | Jul 22, 2026 6:50pm | Jul 22, 2026 8:26pm | Jul 22, 2026 8:27pm | Jul 22, 2026 8:57pm | Jul 22, 2026 9:12pm | Jul 22, 2026 9:14pm | Jul 22, 2026 9:14pm |  |  | Fair | No | Customer stated that she is experiencing low voltage. Reading found at transformer (115-115-230). Checks were done which revealed that the issue is stemming from the hexing box (HEX 02547). Refer to field service.
Outage | J.E.26.07.25273 | C001862560 | Nickolas Rodriques | St.Catherine | Completed | Load_256976 | Twickenham - 210 | Jul 22, 2026 6:48pm | Jul 22, 2026 6:50pm | Jul 22, 2026 9:14pm | Jul 22, 2026 9:16pm | Jul 22, 2026 9:44pm | Jul 22, 2026 10:10pm | Jul 22, 2026 10:11pm | Jul 22, 2026 10:11pm |  |  | Fair | No | Found customer with electricity. Reading found (115-114-229).
Outage | J.E.26.07.25860 | C001862558 | Dean Smith | Hanover | Completed | Load_302811 | Orange Bay - 310 | Jul 22, 2026 6:47pm | Jul 22, 2026 6:47pm | Jul 22, 2026 9:37pm | Jul 22, 2026 9:37pm | Jul 22, 2026 10:03pm | Jul 22, 2026 10:03pm | Jul 22, 2026 10:04pm | Jul 22, 2026 10:04pm |  |  | Fair | No | Area was restored
Outage | J.E.26.07.25944 | C001862559 | Rayon Foster | Hanover | Completed | Load_253314 | Orange Bay - 310 | Jul 22, 2026 6:47pm | Jul 22, 2026 6:47pm | Jul 22, 2026 6:54pm | Jul 22, 2026 6:57pm | Jul 22, 2026 8:52pm | Jul 22, 2026 9:09pm | Jul 22, 2026 9:09pm | Jul 22, 2026 9:09pm |  |  | Fair | No | Unable to reach on cell phone call JPS customer care to pin meter customer care said meter was active meter is working power in area
Outage | J.E.26.07.25877 | C001862557 | Nickolas Rodriques | Portmore | Completed | Load_266759 | Naggo Head - 510 | Jul 22, 2026 6:46pm | Jul 22, 2026 6:47pm | Jul 22, 2026 7:51pm | Jul 22, 2026 7:53pm | Jul 22, 2026 8:09pm | Jul 22, 2026 8:23pm | Jul 22, 2026 8:26pm | Jul 22, 2026 8:26pm |  |  | Fair | No | Power restored. Call relates to the 10 amp junction fuse that was replaced.
Outage | J.E.26.07.25939 | C001862556 | Rusean Allen | KSAS | Completed | Load_1002724 | Cane River - 610 | Jul 22, 2026 6:43pm | Jul 23, 2026 7:53am | Jul 23, 2026 11:57am | Jul 23, 2026 11:57am | Jul 23, 2026 12:18pm | Jul 23, 2026 12:34pm | Jul 23, 2026 12:34pm | Jul 23, 2026 12:34pm | BrokenWire |  | Fair | No | 1x 20amp fuse found 1x 20amp fuse replaced
Outage | J.E.26.07.25778 | C001862553 | Ricky Hall | St.Catherine | Completed | Load_568270 | New Michelton - 410 | Jul 22, 2026 6:33pm | Jul 22, 2026 6:44pm | Jul 22, 2026 7:46pm | Jul 22, 2026 7:46pm | Jul 22, 2026 9:10pm | Jul 22, 2026 9:17pm | Jul 22, 2026 9:17pm | Jul 22, 2026 9:17pm |  |  | Rains | No | Area unsafe daylight attention required
Non-Outage | J.E.26.07.25827 | C001862550 | Rusean Allen | null | Completed | null | null | Jul 22, 2026 6:27pm | Jul 22, 2026 10:34pm | Jul 23, 2026 12:57am | Jul 23, 2026 12:57am | Jul 23, 2026 12:58am | Jul 23, 2026 2:27am | Jul 23, 2026 2:27am | Jul 23, 2026 2:27am | BrokenPole |  | Fair | No | 2x 50amp fuse found 2x 50amp fuse replaced 2x 30amp fuse found 2x 30amp fuse replaced.1x 20amp fuse found 1x 20amp fuse replaced.
Outage | J.E.26.07.25832 | C001862549 | Horace Malcolm | St.James | Completed | Load_266659 | Bogue - 310 | Jul 22, 2026 6:18pm | Jul 23, 2026 8:19am | Jul 23, 2026 8:57am | Jul 23, 2026 8:57am | Jul 23, 2026 9:49am | Jul 23, 2026 9:51am | Jul 23, 2026 9:51am | Jul 23, 2026 9:51am | BrokenPole |  | Fair | No | Found no broken pole unable to locate customer multiple calls unavailable
Outage | J.E.26.07.25805 | C001862546 | Selvin White | St.Elizabeth | Completed | Load_249245 | Maggotty - 110 | Jul 22, 2026 6:12pm | Jul 22, 2026 6:12pm | Jul 22, 2026 6:29pm | Jul 22, 2026 6:29pm | Jul 22, 2026 6:48pm | Jul 22, 2026 7:33pm | Jul 22, 2026 7:37pm | Jul 22, 2026 7:37pm |  |  | Rains | No | Replace a blown 15 amp junction fuse at the entrance to Galleon Beach community, also replace a blown 2 amp fuse for a 25 KVA transformer circuit after patrolling.Lightning strike was said to be the cause. Supply restored to the affected customers.
Outage | J.E.26.07.25834 | C001862547 | Richman Whyte | Hanover | Completed | Load_238992 | Orange Bay - 310 | Jul 22, 2026 6:12pm | Jul 22, 2026 6:13pm | Jul 22, 2026 10:48pm | Jul 22, 2026 10:48pm | Jul 22, 2026 10:48pm | Jul 22, 2026 10:48pm | Jul 22, 2026 10:49pm | Jul 22, 2026 10:49pm |  |  | Fair | No | Clean corrosion on service wire at secondary line
Non-Outage | J.E.26.07.25557 | C001862544 | Wayne Dillion | null | Completed | null | null | Jul 22, 2026 6:11pm | Jul 22, 2026 6:11pm | Jul 22, 2026 7:52pm | Jul 22, 2026 7:52pm | Jul 22, 2026 7:52pm | Jul 22, 2026 7:52pm | Jul 22, 2026 7:58pm | Jul 22, 2026 7:58pm | BrokenPole |  | Fair | No | Unable to connect customer repair not yet completed wire still on the ground
Non-Outage | J.E.26.07.25679 | C001862545 | Wayne Dillion | null | Completed | null | null | Jul 22, 2026 6:11pm | Jul 22, 2026 6:11pm | Jul 22, 2026 7:59pm | Jul 22, 2026 7:59pm | Jul 22, 2026 7:59pm | Jul 22, 2026 8:00pm | Jul 22, 2026 8:00pm | Jul 22, 2026 8:00pm | BrokenWire |  | Fair | No | Please refer this call to a Mandeville team
Non-Outage | J.E.26.07.25729 | C001862539 | Milton Charlton | KSAN | Completed | Load_258324 | Hope - 510 | Jul 22, 2026 6:03pm | Jul 22, 2026 6:03pm | Jul 22, 2026 7:54pm | Jul 22, 2026 7:54pm | Jul 22, 2026 7:54pm | Jul 22, 2026 7:50pm | Jul 22, 2026 7:56pm | Jul 22, 2026 7:56pm |  |  | Fair | No | Call related to call at 237 Old Hope Road.
Outage | J.E.26.07.25811 | C001862536 | Donald Cunningham | St.Catherine | Completed | Load_264169 | Tredegar - 510 | Jul 22, 2026 5:59pm | Jul 22, 2026 6:45pm | Jul 22, 2026 8:10pm | Jul 22, 2026 8:10pm | Jul 22, 2026 9:14pm | Jul 22, 2026 9:38pm | Jul 22, 2026 9:42pm | Jul 22, 2026 9:42pm |  |  | Fair | No | T/off to Henrique blvd blown junction fuse found and replace with 30 amp fuse
Outage | J.E.26.07.25839 | C001862537 | Donald Cunningham | St.Catherine | Completed | Load_568679 | Tredegar - 510 | Jul 22, 2026 5:59pm | Jul 22, 2026 6:45pm | Jul 22, 2026 9:44pm | Jul 22, 2026 9:44pm | Jul 22, 2026 9:53pm | Jul 22, 2026 9:58pm | Jul 22, 2026 9:59pm | Jul 22, 2026 9:59pm |  |  | Fair | No | Supply restored
Outage | J.E.26.07.25775 | C001862535 | Nickolas Rodriques | Portmore | Completed | Load_250964 | Naggo Head - 510 | Jul 22, 2026 5:55pm | Jul 22, 2026 6:46pm | Jul 22, 2026 7:06pm | Jul 22, 2026 7:06pm | Jul 22, 2026 7:27pm | Jul 22, 2026 7:42pm | Jul 22, 2026 7:51pm | Jul 22, 2026 7:51pm | Fire |  | Fair | No | Checked and found a 10 amp junction fuse blown. Patrol and found nothing on line. Repaired by replacing the fuse after completing patrol.
Outage | J.E.26.07.25874 | C001862534 | Milton Charlton | KSAN | Completed | Load_260845 | Hope - 510 | Jul 22, 2026 5:47pm | Jul 22, 2026 5:47pm | Jul 22, 2026 6:02pm | Jul 22, 2026 7:58pm | Jul 22, 2026 8:17pm | Jul 22, 2026 8:25pm | Jul 22, 2026 8:23pm | Jul 22, 2026 8:23pm | LeaningPole |  | Fair | No | 40ft wooden pole #0075687 cut and telephone cables removed rotten at the foot and leaning badly. Need to be retired urgently.
Outage | J.E.26.07.25851 | C001862533 | Marlon Brown | Trelawny | Completed | Load_574390 | Duncans - 110 | Jul 22, 2026 5:42pm | Jul 22, 2026 5:42pm | Jul 22, 2026 5:47pm | Jul 22, 2026 5:47pm | Jul 22, 2026 6:13pm | Jul 22, 2026 6:39pm | Jul 22, 2026 6:39pm | Jul 22, 2026 6:39pm |  |  | Fair | No | Check and found ok voltage leaving at meter socket 116/117=233v. Voltage found at meter socket 116/117=233v
Non-Outage | J.E.26.07.25767 | C001862527 | Milton Charlton | KSAN | Completed | Load_253447 | Hope - 510 | Jul 22, 2026 5:35pm | Jul 22, 2026 5:35pm | Jul 22, 2026 6:58pm | Jul 22, 2026 6:58pm | Jul 22, 2026 7:50pm | Jul 22, 2026 7:50pm | Jul 22, 2026 7:54pm | Jul 22, 2026 7:54pm |  |  | Fair | No | Refused and reclosed 80amps junction blown at pole#( no pole #) using one 80amps fuse.
Outage | J.E.26.07.25813 | C001862524 | Dean Smith | Hanover | Completed | Load_258609 | Orange Bay - 210 | Jul 22, 2026 5:28pm | Jul 22, 2026 5:29pm | Jul 22, 2026 5:50pm | Jul 22, 2026 5:51pm | Jul 22, 2026 6:22pm | Jul 22, 2026 7:58pm | Jul 22, 2026 8:01pm | Jul 22, 2026 8:01pm | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Rains | No | Cut and remove illegal burnt service wires, splice and retention (2) span of secondary phase conductor. Opened and closed 50kva transformer to do repair. Pole number N/A
Outage | J.E.26.07.24975 | C001862523 | Stephen Taylor | St.Thomas | Completed | Load_268474 | Good Year - 210 | Jul 22, 2026 5:26pm | Jul 22, 2026 5:27pm | Jul 22, 2026 5:39pm | Jul 22, 2026 5:39pm | Jul 22, 2026 5:40pm | Jul 22, 2026 5:40pm | Jul 22, 2026 5:40pm | Jul 22, 2026 5:40pm |  |  | Fair | No | Need more information a lot of call to customer no one answered the phone
Outage | J.E.26.07.25804 | C001862520 | Stephen Taylor | St.Thomas | Completed | Load_260689 | Good Year - 110 | Jul 22, 2026 5:25pm | Jul 22, 2026 5:26pm | Jul 22, 2026 6:32pm | Jul 22, 2026 6:55pm | Jul 22, 2026 6:55pm | Jul 22, 2026 6:56pm | Jul 22, 2026 6:57pm | Jul 22, 2026 6:57pm |  |  | Fair | No | Customer say power is back
Outage | J.E.26.07.25836 | C001862516 | Kaydon Taylor | KSAN | Completed | Load_251827 | Constant Spring - 210 | Jul 22, 2026 5:19pm | Jul 22, 2026 5:20pm | Jul 22, 2026 7:23pm | Jul 22, 2026 7:23pm | Jul 22, 2026 8:55pm | Jul 22, 2026 8:58pm | Jul 22, 2026 8:58pm | Jul 22, 2026 8:58pm | BrokenWire |  | Fair | No | String 120’# 6 service wire (6) one bolt clamps v 116 117 238
Non-Outage | J.E.26.07.11298 | C001862513 | Shamour Haughton | St.James | Completed | Load_256990 | Queens Drive - 710 | Jul 22, 2026 5:07pm | Jul 22, 2026 5:07pm | Jul 22, 2026 6:41pm | Jul 22, 2026 6:41pm | Jul 22, 2026 9:30pm | Jul 22, 2026 9:30pm | Jul 22, 2026 9:38pm | Jul 22, 2026 9:38pm |  |  | Fair | No | Secondary fell from D iron, reinstall secondary and reclose 25kva, voltage left 113,114,227
Non-Outage | J.E.26.07.25799 | C001862512 | Derrick Dawkins | St.James | Completed | Load_248617 | Bogue - 610 | Jul 22, 2026 5:04pm | Jul 22, 2026 5:05pm | Jul 22, 2026 5:15pm | Jul 22, 2026 5:15pm | Jul 22, 2026 5:44pm | Jul 22, 2026 6:36pm | Jul 22, 2026 6:37pm | Jul 22, 2026 6:37pm |  |  | Fair | No | Found customer pot head corroded clean and remade joint voltage 110/115=226
Non-Outage | J.E.26.07.23409 | C001862510 | Daniel Francis | St.Ann | Completed | Load_263615 | Roaring River - 210 | Jul 22, 2026 4:57pm | Jul 22, 2026 4:57pm | Jul 22, 2026 6:24pm | Jul 22, 2026 6:24pm | Jul 22, 2026 7:27pm | Jul 22, 2026 8:05pm | Jul 22, 2026 8:07pm | Jul 22, 2026 8:07pm |  |  | Fair | No | Change 3 pen union at pat head 116 116 232 in all
Non-Outage | J.E.26.07.25755 | C001862506 | Kaydon Taylor | null | Completed | null | null | Jul 22, 2026 4:52pm | Jul 23, 2026 7:36am | Jul 23, 2026 8:51am | Jul 23, 2026 9:32am | Jul 23, 2026 10:39am | Jul 23, 2026 11:39am | Jul 23, 2026 11:40am | Jul 23, 2026 11:40am | Fire |  | Fair | No | 3 clamps at pot head
Non-Outage | J.E.26.07.25760 | C001862505 | Eric Williams | null | Completed | null | null | Jul 22, 2026 4:51pm | Jul 22, 2026 4:53pm | Jul 22, 2026 6:30pm | Jul 22, 2026 9:55pm | Jul 22, 2026 9:55pm | Jul 22, 2026 10:23pm | Jul 22, 2026 10:24pm | Jul 22, 2026 10:24pm | BrokenWire |  | Fair | No | Premises found okay customer reported for somewhere else
Outage | J.E.26.07.25731 | C001862500 | Edward Royal | KSAS | Completed | Load_253227 | Cane River - 610 | Jul 22, 2026 4:46pm | Jul 22, 2026 5:34pm | Jul 22, 2026 6:28pm | Jul 22, 2026 6:28pm | Jul 22, 2026 7:19pm | Jul 22, 2026 10:55pm | Jul 22, 2026 10:55pm | Jul 22, 2026 10:55pm |  |  | Fair | No | Spliced and reconnected primary line using 30ft open number 2 conductor replaced 2 30A junction fuse
Outage | J.E.26.07.25471 | C001862496 | Fitzroy Turner | KSAS | Completed | Load_239957 | Hunts Bay - 210 | Jul 22, 2026 4:44pm | Jul 22, 2026 4:44pm | Jul 22, 2026 6:57pm | Jul 22, 2026 6:57pm | Jul 22, 2026 6:59pm | Jul 22, 2026 6:59pm | Jul 22, 2026 7:01pm | Jul 22, 2026 7:01pm |  |  | Fair | No | Supply restored to after replace blown 65amps fuse at the intersection of Marcus Garvey drive and Newport Blvd
Outage | J.E.26.07.25750 | C001862484 | Marlon Brown | Trelawny | Completed | Load_555893 | Martha Brae - 210 | Jul 22, 2026 4:35pm | Jul 22, 2026 4:35pm | Jul 22, 2026 4:48pm | Jul 22, 2026 4:49pm | Jul 22, 2026 4:57pm | Jul 22, 2026 5:45pm | Jul 22, 2026 5:45pm | Jul 22, 2026 5:45pm | Fire |  | Fair | No | Isolated 25kva transformer to repair broken 2/0 twisted, use 2 pg clamps
Outage | J.E.26.07.25589 | C001862479 | Stephen Taylor | St.Thomas | Completed | Load_262336 | Good Year - 110 | Jul 22, 2026 4:28pm | Jul 22, 2026 4:28pm | Jul 22, 2026 5:41pm | Jul 22, 2026 5:41pm | Jul 22, 2026 6:52pm | Jul 22, 2026 6:52pm | Jul 22, 2026 6:55pm | Jul 22, 2026 6:55pm |  |  | Fair | No | Patrol and clear line close up back junction with 10ams fuse
Outage | J.E.26.07.25552 | C001862473 | Jermaine Williams | Clarendon | Completed | Load_240175 | May Pen - 210 | Jul 22, 2026 4:25pm | Jul 22, 2026 4:26pm | Jul 22, 2026 4:46pm | Jul 22, 2026 4:46pm | Jul 22, 2026 4:46pm | Jul 22, 2026 4:46pm | Jul 22, 2026 4:47pm | Jul 22, 2026 4:47pm |  |  | Fair | No | Customer states no reports was made
Outage | J.E.26.07.25594 | C001862472 | Jermaine Williams | Clarendon | Completed | Load_243173 | May Pen - 210 | Jul 22, 2026 4:25pm | Jul 22, 2026 4:26pm | Jul 22, 2026 8:00pm | Jul 22, 2026 8:00pm | Jul 22, 2026 8:59pm | Jul 22, 2026 9:00pm | Jul 22, 2026 9:00pm | Jul 22, 2026 9:00pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.25634 | C001862471 | Jermaine Williams | Clarendon | Completed | Load_251754 | May Pen - 210 | Jul 22, 2026 4:25pm | Jul 22, 2026 4:26pm | Jul 22, 2026 9:00pm | Jul 22, 2026 9:00pm | Jul 22, 2026 10:20pm | Jul 22, 2026 10:21pm | Jul 22, 2026 10:21pm | Jul 22, 2026 10:21pm |  |  | Fair | No | Premises found ok.
Outage | J.E.26.07.25649 | C001862470 | Jermaine Williams | Clarendon | Completed | Load_250813 | Monymusk - 210 | Jul 22, 2026 4:25pm | Jul 22, 2026 4:26pm | Jul 22, 2026 6:18pm | Jul 22, 2026 6:18pm | Jul 22, 2026 7:59pm | Jul 22, 2026 7:59pm | Jul 22, 2026 7:59pm | Jul 22, 2026 7:59pm |  |  | Fair | No | Replace 1-25A Junction Fuse, left ok.
Outage | J.E.26.07.25687 | C001862475 | Eric Williams | KSAN | Completed | Load_579328 | Washington Blvd - 610 | Jul 22, 2026 4:25pm | Jul 22, 2026 4:27pm | Jul 22, 2026 4:41pm | Jul 22, 2026 4:41pm | Jul 22, 2026 5:24pm | Jul 22, 2026 6:06pm | Jul 22, 2026 6:09pm | Jul 22, 2026 6:09pm |  |  | Rains | No | Blown 50amps junction fuse found and replaced
Outage | J.E.26.07.25734 | C001862469 | Jermaine Williams | Clarendon | Completed | Load_238965 | Parnassus - 210 | Jul 22, 2026 4:25pm | Jul 22, 2026 4:26pm | Jul 22, 2026 4:49pm | Jul 22, 2026 4:49pm | Jul 22, 2026 5:07pm | Jul 22, 2026 5:39pm | Jul 22, 2026 5:41pm | Jul 22, 2026 5:41pm | Fire |  | SevereWind | No | Splice and retention one span of broken secondary phase conductor using 100ft #2 aac and two clamps. Left ok.
Outage | J.E.26.07.25739 | C001862474 | Eric Williams | KSAN | Completed | Load_264486 | Washington Blvd - 510 | Jul 22, 2026 4:25pm | Jul 22, 2026 4:27pm | Jul 22, 2026 6:10pm | Jul 22, 2026 6:10pm | Jul 22, 2026 6:31pm | Jul 22, 2026 7:13pm | Jul 22, 2026 7:14pm | Jul 22, 2026 7:14pm |  |  | Rains | No | 2 blown 10amps transformer fuse found and replaced
Outage | J.E.26.07.25714 | C001862468 | Wan Carlos Scarlett | St.Catherine | Completed | Load_263124 | Twickenham - 210 | Jul 22, 2026 4:22pm | Jul 23, 2026 7:26am | Jul 23, 2026 7:32am | Jul 23, 2026 7:32am | Jul 23, 2026 8:25am | Jul 23, 2026 8:47am | Jul 23, 2026 8:49am | Jul 23, 2026 8:49am | BrokenWire |  | Fair | No | Found customer 3 wire service at pole with one of the phase broken off use one bolt clamp at open secondary line phase readings 116-115-231
Outage | J.E.26.07.25675 | C001862455 | Dean Smith | Hanover | Completed | Load_252494 | Orange Bay - 310 | Jul 22, 2026 4:15pm | Jul 22, 2026 4:22pm | Jul 22, 2026 4:29pm | Jul 22, 2026 10:42pm | Jul 22, 2026 10:42pm | Jul 22, 2026 10:42pm | Jul 22, 2026 10:43pm | Jul 22, 2026 10:43pm |  |  | Fair | No | Shift ended
Outage | J.E.26.07.25677 | C001862454 | Fitzroy Turner | KSAS | Completed | Load_1003920 | Hunts Bay - 110 | Jul 22, 2026 4:13pm | Jul 22, 2026 5:05pm | Jul 22, 2026 6:32pm | Jul 22, 2026 6:32pm | Jul 22, 2026 6:32pm | Jul 22, 2026 6:51pm | Jul 22, 2026 6:56pm | Jul 22, 2026 6:56pm |  |  | Fair | No | Found tree 65amps junction fuse blown at the intersection of Marcus Garvey drive and Newport Blvd .change one drop out switch at the underground cables and replaced tree 20amp fuse at the cable pole tree 65amps replaced supply restored to the areas
Non-Outage | J.E.26.07.22704 | C001862452 | Neckell Ormsby | St.Mary | Completed | Load_242932 | Annotto Bay - 210 | Jul 22, 2026 4:12pm | Jul 22, 2026 4:13pm | Jul 22, 2026 4:18pm | Jul 22, 2026 4:19pm | Jul 22, 2026 5:28pm | Jul 22, 2026 5:39pm | Jul 22, 2026 5:50pm | Jul 22, 2026 5:50pm |  |  | Rains | No | Customer not at home however she said power came back
Non-Outage | J.E.26.07.25208 | C001862446 | Neckell Ormsby | St.Mary | Completed | Load_574190 | Annotto Bay - 310 | Jul 22, 2026 4:12pm | Jul 22, 2026 4:13pm | Jul 22, 2026 5:50pm | Jul 22, 2026 5:50pm | Jul 22, 2026 5:50pm | Jul 22, 2026 6:24pm | Jul 22, 2026 6:24pm | Jul 22, 2026 6:24pm |  |  | Rains | No | Found defective 25 kva transformer in bank of 3 no pole # seenDoctors office urgently requires power
Outage | J.E.26.07.25645 | C001862449 | Rusean Allen | KSAS | Completed | Load_237939 | Hunts Bay - 310 | Jul 22, 2026 4:12pm | Jul 22, 2026 10:34pm | Jul 23, 2026 2:30am | Jul 23, 2026 2:30am | Jul 23, 2026 2:31am | Jul 23, 2026 2:31am | Jul 23, 2026 2:32am | Jul 23, 2026 2:32am |  |  | Fair | No | Light seen at premises
Outage | J.E.26.07.25648 | C001862453 | Rusean Allen | KSAS | Completed | Load_243158 | Greenwich - 710 | Jul 22, 2026 4:12pm | Jul 22, 2026 10:34pm | Jul 23, 2026 12:22am | Jul 23, 2026 12:33am | Jul 23, 2026 12:56am | Jul 23, 2026 12:57am | Jul 23, 2026 12:57am | Jul 23, 2026 12:57am |  |  | Fair | No | Daylight attention area not self
Outage | J.E.26.07.25672 | C001862450 | Rusean Allen | KSAS | Completed | Load_556074 | Hunts Bay - 410 | Jul 22, 2026 4:12pm | Jul 22, 2026 10:34pm | Jul 23, 2026 2:30am | Jul 23, 2026 2:32am | Jul 23, 2026 2:33am | Jul 23, 2026 2:33am | Jul 23, 2026 2:33am | Jul 23, 2026 2:33am |  |  | Fair | No | No access
Non-Outage | J.E.26.07.25436 | C001862439 | Daniel Francis | null | Completed | null | null | Jul 22, 2026 4:09pm | Jul 22, 2026 4:35pm | Jul 22, 2026 4:59pm | Jul 22, 2026 8:07pm | Jul 22, 2026 8:27pm | Jul 22, 2026 8:54pm | Jul 22, 2026 8:54pm | Jul 22, 2026 8:54pm |  |  | Fair | No | Daylight attention needs for further check voltage found 106/107/175/213/211/198
Non-Outage | J.E.26.07.25716 | C001862440 | Romaine Roberts | null | Completed | null | null | Jul 22, 2026 4:09pm | Jul 22, 2026 4:11pm | Jul 22, 2026 7:10pm | Jul 22, 2026 7:10pm | Jul 22, 2026 7:18pm | Jul 22, 2026 7:19pm | Jul 22, 2026 7:20pm | Jul 22, 2026 7:20pm | Fire |  | Fair | No | Premises not found
Outage | J.E.26.07.25684 | C001862438 | Oshane Warren | St.Elizabeth | Completed | Load_238977 | Maggotty - 110 | Jul 22, 2026 4:09pm | Jul 22, 2026 4:09pm | Jul 22, 2026 9:33pm | Jul 22, 2026 9:33pm | Jul 22, 2026 10:11pm | Jul 22, 2026 10:13pm | Jul 22, 2026 10:14pm | Jul 22, 2026 10:14pm |  |  | Rains | No | Replace 8 amp junction fuse
Outage | J.E.26.07.25699 | C001862436 | Edward Royal | KSAS | Completed | Load_253639 | Up Park Camp - 510 | Jul 22, 2026 4:08pm | Jul 22, 2026 4:09pm | Jul 22, 2026 6:18pm | Jul 22, 2026 6:18pm | Jul 22, 2026 6:19pm | Jul 22, 2026 6:26pm | Jul 22, 2026 6:27pm | Jul 22, 2026 6:27pm |  |  | Fair | No | Replaced 5A transformer fuse
Outage | J.E.26.07.25704 | C001862437 | Wayne Dillion | St.Elizabeth | Completed | Load_252908 | Maggotty - 110 | Jul 22, 2026 4:08pm | Jul 22, 2026 4:09pm | Jul 22, 2026 4:57pm | Jul 22, 2026 4:57pm | Jul 22, 2026 5:34pm | Jul 22, 2026 5:55pm | Jul 22, 2026 5:55pm | Jul 22, 2026 5:55pm |  |  | Fair | No | Patrol and an found one 10 KVA transformer tripped cause by illegal connection remove illegal connection and reset transformer supply restore to customer successfully
Outage | J.E.26.07.25611 | C001862431 | Cliton Henry | St.Mary | Completed | Load_240442 | Oracabessa - 210 | Jul 22, 2026 4:04pm | Jul 22, 2026 4:06pm | Jul 22, 2026 4:23pm | Jul 22, 2026 4:23pm | Jul 22, 2026 5:08pm | Jul 22, 2026 6:20pm | Jul 22, 2026 6:25pm | Jul 22, 2026 6:25pm |  |  | Fair | No | RAMI infrastructure zero volts found at the customer’s pothead. The supply was restored restored by the assistance from F. Coach.
Outage | J.E.26.07.25622 | C001862432 | Romaine Roberts | St.Mary | Completed | Load_248289 | Highgate -110 | Jul 22, 2026 4:04pm | Jul 22, 2026 4:06pm | Jul 22, 2026 4:25pm | Jul 22, 2026 4:25pm | Jul 22, 2026 6:08pm | Jul 22, 2026 6:45pm | Jul 22, 2026 6:46pm | Jul 22, 2026 6:46pm |  |  | Fair | No | Found junction fuse blown patrol line nothing found replace 15 amp no pole number
Outage | J.E.26.07.25700 | C001862430 | Daniel Francis | St.Ann | Completed | Load_237943 | Roaring River - 210 | Jul 22, 2026 4:04pm | Jul 22, 2026 4:06pm | Jul 22, 2026 4:48pm | Jul 22, 2026 4:48pm | Jul 22, 2026 4:59pm | Jul 22, 2026 5:00pm | Jul 22, 2026 5:01pm | Jul 22, 2026 5:01pm |  |  | Fair | No | Power restored
Outage | J.E.26.07.25456 | C001862425 | Jermaine Williams | Clarendon | Completed | Load_405421 | Parnassus - 210 | Jul 22, 2026 4:00pm | Jul 22, 2026 4:24pm | Jul 22, 2026 4:45pm | Jul 22, 2026 4:45pm | Jul 22, 2026 4:45pm | Jul 22, 2026 4:46pm | Jul 22, 2026 4:46pm | Jul 22, 2026 4:46pm |  |  | Fair | No | Supply came back
Outage | J.E.26.07.25586 | C001862424 | Jermaine Williams | Clarendon | Completed | Load_241561 | Parnassus - 310 | Jul 22, 2026 4:00pm | Jul 22, 2026 4:24pm | Jul 22, 2026 5:43pm | Jul 22, 2026 5:43pm | Jul 22, 2026 6:17pm | Jul 22, 2026 6:17pm | Jul 22, 2026 6:18pm | Jul 22, 2026 6:18pm | BrokenWire |  | Fair | No | Wire not property of JPS.
Outage | J.E.26.07.25667 | C001862420 | Roxroy Needham | St.Ann | Completed | Load_250710 | Cardiff Hall - 310 | Jul 22, 2026 3:55pm | Jul 22, 2026 3:56pm | Jul 22, 2026 5:55pm | Jul 22, 2026 5:55pm | Jul 22, 2026 6:57pm | Jul 22, 2026 7:00pm | Jul 22, 2026 7:00pm | Jul 22, 2026 7:00pm |  |  | Fair | No | Not getting customer on phone
Non-Outage | J.E.26.07.25007 | C001862404 | Romeo Brissett | null | Completed | null | null | Jul 22, 2026 3:46pm | Jul 22, 2026 3:46pm | Jul 22, 2026 4:01pm | Jul 22, 2026 4:01pm | Jul 22, 2026 4:52pm | Jul 22, 2026 5:20pm | Jul 22, 2026 5:26pm | Jul 22, 2026 5:26pm |  |  | Fair | No | Customer was connected by escalation technician.
Outage | J.E.26.07.25581 | C001862413 | Oshane Warren | Westmoreland | Completed | Load_244752 | Paradise - 310 | Jul 22, 2026 3:46pm | Jul 22, 2026 3:48pm | Jul 22, 2026 5:33pm | Jul 22, 2026 5:34pm | Jul 22, 2026 5:34pm | Jul 22, 2026 5:34pm | Jul 22, 2026 5:34pm | Jul 22, 2026 5:34pm |  |  | Rains | No | St James call
Outage | J.E.26.07.25626 | C001862403 | Jermaine Williams | Clarendon | Completed | null | null | Jul 22, 2026 3:44pm | Jul 22, 2026 4:24pm | Jul 22, 2026 4:47pm | Jul 22, 2026 4:47pm | Jul 22, 2026 4:47pm | Jul 22, 2026 4:47pm | Jul 22, 2026 4:48pm | Jul 22, 2026 4:48pm |  |  | Fair | No | Unable to locate
Outage | J.E.26.07.25431 | C001862400 | Roxroy Needham | St.Ann | Completed | Load_258300 | Cardiff Hall - 310 | Jul 22, 2026 3:40pm | Jul 22, 2026 3:44pm | Jul 22, 2026 5:42pm | Jul 22, 2026 5:42pm | Jul 22, 2026 5:54pm | Jul 22, 2026 5:55pm | Jul 22, 2026 5:55pm | Jul 22, 2026 5:55pm |  |  | Fair | No | Premises found with different meter need field service to check for meter
Outage | J.E.26.07.25473 | C001862399 | Roxroy Needham | St.Ann | Completed | Load_269493 | Cardiff Hall - 310 | Jul 22, 2026 3:40pm | Jul 22, 2026 3:44pm | Jul 22, 2026 5:34pm | Jul 22, 2026 5:34pm | Jul 22, 2026 5:40pm | Jul 22, 2026 5:41pm | Jul 22, 2026 5:41pm | Jul 22, 2026 5:41pm |  |  | Fair | No | Customer say he doesn’t know about any report that was made
Outage | J.E.26.07.25432 | C001862396 | Donald Cunningham | St.Catherine | Completed | Load_267523 | Tredegar - 410 | Jul 22, 2026 3:39pm | Jul 22, 2026 3:40pm | Jul 22, 2026 4:05pm | Jul 22, 2026 4:05pm | Jul 22, 2026 5:13pm | Jul 22, 2026 5:16pm | Jul 22, 2026 7:13pm | Jul 22, 2026 7:13pm | BrokenWire |  | Fair | No | Broken secondary neural splice and retention using 120 of #2 aa 1 automatic splice and 6 clamps for repair also bushing done voltage readings 115/2/230 customer in area complaint of damage appliances
Outage | J.E.26.07.25446 | C001862398 | Donald Cunningham | St.Catherine | Completed | Load_1001271 | Twickenham - 410 | Jul 22, 2026 3:39pm | Jul 22, 2026 3:40pm | Jul 22, 2026 7:14pm | Jul 22, 2026 7:14pm | Jul 22, 2026 8:02pm | Jul 22, 2026 8:09pm | Jul 22, 2026 8:09pm | Jul 22, 2026 8:09pm |  |  | Fair | No | Rami system box need to check refer to mr Ellison
Outage | J.E.26.07.25618 | C001862397 | Donald Cunningham | St.Catherine | Completed | Load_260981 | Tredegar - 210 | Jul 22, 2026 3:39pm | Jul 22, 2026 3:40pm | Jul 22, 2026 9:59pm | Jul 22, 2026 9:59pm | Jul 22, 2026 10:56pm | Jul 22, 2026 10:59pm | Jul 22, 2026 10:59pm | Jul 22, 2026 10:59pm | Fire |  | Fair | No | No broken wire seen
Outage | J.E.26.07.25598 | C001862395 | Derrick Dawkins | St.James | Completed | Load_266674 | Bogue - 410 | Jul 22, 2026 3:36pm | Jul 22, 2026 4:56pm | Jul 22, 2026 5:04pm | Jul 22, 2026 5:06pm | Jul 22, 2026 5:06pm | Jul 22, 2026 5:15pm | Jul 22, 2026 5:15pm | Jul 22, 2026 5:15pm | Fire |  | Fair | No | Checked and found ok
Outage | J.E.26.07.25561 | C001862391 | Romeo Brissett | St.James | Completed | Load_260210 | Bogue - 610 | Jul 22, 2026 3:34pm | Jul 22, 2026 3:35pm | Jul 22, 2026 3:45pm | Jul 22, 2026 3:45pm | Jul 22, 2026 3:45pm | Jul 22, 2026 3:40pm | Jul 22, 2026 3:46pm | Jul 22, 2026 3:46pm |  |  | Rains | No | Check and found ok
Outage | J.E.26.07.25388 | C001862389 | Eric Williams | KSAS | Completed | Load_249275 | Duhaney - 310 | Jul 22, 2026 3:32pm | Jul 22, 2026 3:34pm | Jul 22, 2026 8:49pm | Jul 22, 2026 8:49pm | Jul 22, 2026 9:21pm | Jul 22, 2026 9:54pm | Jul 22, 2026 9:55pm | Jul 22, 2026 9:55pm |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.25573 | C001862387 | Milton Charlton | KSAN | Completed | Load_269372 | West Kings House - 310 | Jul 22, 2026 3:32pm | Jul 22, 2026 5:22pm | Jul 22, 2026 6:02pm | Jul 22, 2026 6:02pm | Jul 22, 2026 6:54pm | Jul 22, 2026 6:35pm | Jul 22, 2026 6:56pm | Jul 22, 2026 6:56pm |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.07.25600 | C001862388 | Shamour Haughton | St.James | Completed | Load_293476 | Queens Drive - 310 | Jul 22, 2026 3:32pm | Jul 22, 2026 4:41pm | Jul 22, 2026 4:57pm | Jul 22, 2026 4:57pm | Jul 22, 2026 6:00pm | Jul 22, 2026 6:26pm | Jul 22, 2026 6:26pm | Jul 22, 2026 6:26pm |  |  | Fair | No | Refuse one 15amp junction fuse
Outage | J.E.26.07.25606 | C001862390 | Shamour Haughton | St.James | Completed | Load_293234 | Queens Drive - 310 | Jul 22, 2026 3:32pm | Jul 22, 2026 4:41pm | Jul 22, 2026 6:26pm | Jul 22, 2026 6:26pm | Jul 22, 2026 6:26pm | Jul 22, 2026 6:30pm | Jul 22, 2026 6:30pm | Jul 22, 2026 6:30pm |  |  | Fair | No | Refuse one 15amp junction fuse
Outage | J.E.26.07.25487 | C001862385 | Ricky Hall | St.Catherine | Completed | Load_260627 | New Michelton - 210 | Jul 22, 2026 3:31pm | Jul 22, 2026 3:32pm | Jul 22, 2026 6:47pm | Jul 22, 2026 6:47pm | Jul 22, 2026 7:42pm | Jul 22, 2026 7:44pm | Jul 22, 2026 7:45pm | Jul 22, 2026 7:45pm |  |  | Rains | No | Issue was resolved on previous shift
Outage | J.E.26.07.25224 | C001862380 | Ricky Hall | St.Catherine | Completed | Load_556137 | New Michelton - 410 | Jul 22, 2026 3:30pm | Jul 22, 2026 3:31pm | Jul 22, 2026 4:38pm | Jul 22, 2026 4:39pm | Jul 22, 2026 5:57pm | Jul 22, 2026 6:43pm | Jul 22, 2026 6:44pm | Jul 22, 2026 6:44pm |  |  | Rains | No | Replaced blown 20 amps junction fuse
Non-Outage | J.E.26.07.17009 | C001862379 | Edward Royal | KSAS | Completed | Load_267551 | Cane River - 410 | Jul 22, 2026 3:27pm | Jul 22, 2026 3:28pm | Jul 22, 2026 3:47pm | Jul 22, 2026 3:47pm | Jul 22, 2026 3:47pm | Jul 22, 2026 3:47pm | Jul 22, 2026 3:47pm | Jul 22, 2026 3:47pm |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.07.25464 | C001862373 | Rusean Allen | KSAS | Completed | Load_268624 | Greenwich - 710 | Jul 22, 2026 3:25pm | Jul 22, 2026 10:34pm | Jul 23, 2026 12:21am | Jul 23, 2026 12:23am | Jul 23, 2026 12:25am | Jul 23, 2026 12:26am | Jul 23, 2026 12:27am | Jul 23, 2026 12:27am |  |  | Fair | No | Premises locked.
Outage | J.E.26.07.25474 | C001862372 | Edward Royal | KSAN | Completed | Load_293895 | Washington Blvd - 710 | Jul 22, 2026 3:24pm | Jul 22, 2026 3:58pm | Jul 22, 2026 5:37pm | Jul 22, 2026 5:37pm | Jul 22, 2026 5:37pm | Jul 22, 2026 5:38pm | Jul 22, 2026 5:38pm | Jul 22, 2026 5:38pm |  |  | Fair | No | When contacted customer said that the premises is close and nobody is at home
Non-Outage | J.E.26.07.25452 | C001862368 | Edward Royal | null | Completed | null | null | Jul 22, 2026 3:23pm | Jul 22, 2026 3:24pm | Jul 22, 2026 5:20pm | Jul 22, 2026 5:20pm | Jul 22, 2026 5:20pm | Jul 22, 2026 5:35pm | Jul 22, 2026 5:36pm | Jul 22, 2026 5:36pm |  |  | Fair | No | Meter not responding meter need to be check reffered to field service
Outage | J.E.26.07.25528 | C001862371 | Edward Royal | KSAS | Completed | Load_269025 | Hunts Bay - 210 | Jul 22, 2026 3:23pm | Jul 22, 2026 3:24pm | Jul 22, 2026 4:08pm | Jul 22, 2026 4:08pm | Jul 22, 2026 4:08pm | Jul 22, 2026 4:15pm | Jul 22, 2026 4:15pm | Jul 22, 2026 4:15pm |  |  | Fair | No | Incorrect procedure advice customer to visit ruthven road for more information
Outage | J.E.26.07.25567 | C001862367 | Selvin White | St.Elizabeth | Completed | Load_270217 | Maggotty - 110 | Jul 22, 2026 3:22pm | Jul 22, 2026 3:24pm | Jul 22, 2026 4:41pm | Jul 22, 2026 5:02pm | Jul 22, 2026 5:22pm | Jul 22, 2026 5:59pm | Jul 22, 2026 6:02pm | Jul 22, 2026 6:02pm |  |  | Rains | No | Replace approximately 12 ft of number six triplex service wire that was damaged and removed after hurricane Melissa . Voltage readings left inside customer’s meter socket are 221,110,111 volts.
Non-Outage | J.E.26.07.25583 | C001862360 | Michael Christian | null | Completed | null | null | Jul 22, 2026 3:20pm | Jul 22, 2026 3:23pm | Jul 22, 2026 4:19pm | Jul 23, 2026 4:00pm | Jul 23, 2026 4:52pm | Jul 23, 2026 4:57pm | Jul 23, 2026 4:57pm | Jul 23, 2026 4:57pm |  |  | Rains | No | E N connection send to field service
Outage | J.E.26.07.25544 | C001862359 | Michael Christian | St.James | Completed | Load_249876 | Bogue - 310 | Jul 22, 2026 3:20pm | Jul 22, 2026 3:23pm | Jul 22, 2026 7:48pm | Jul 22, 2026 7:48pm | Jul 22, 2026 7:59pm | Jul 22, 2026 8:00pm | Jul 22, 2026 8:00pm | Jul 22, 2026 8:00pm |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.25550 | C001862358 | Michael Christian | St.James | Completed | Load_245091 | Bogue - 310 | Jul 22, 2026 3:20pm | Jul 22, 2026 3:23pm | Jul 22, 2026 4:31pm | Jul 22, 2026 4:31pm | Jul 22, 2026 6:17pm | Jul 22, 2026 7:46pm | Jul 22, 2026 7:46pm | Jul 22, 2026 7:46pm |  |  | Fair | No | Found 1 50 amp out replace 1 50 amp no pole
Outage | J.E.26.07.25562 | C001862361 | Michael Christian | St.James | Completed | Load_238640 | Bogue - 310 | Jul 22, 2026 3:20pm | Jul 22, 2026 3:23pm | Jul 22, 2026 7:47pm | Jul 22, 2026 7:47pm | Jul 22, 2026 7:47pm | Jul 22, 2026 7:48pm | Jul 22, 2026 7:48pm | Jul 22, 2026 7:48pm |  |  | Fair | No | Replace 1 50 amp no pole #
Outage | J.E.26.07.25481 | C001862357 | Michael Christian | St.James | Completed | Load_557020 | Bogue - 310 | Jul 22, 2026 3:19pm | Jul 22, 2026 3:23pm | Jul 22, 2026 8:54pm | Jul 22, 2026 8:54pm | Jul 22, 2026 9:41pm | Jul 22, 2026 9:49pm | Jul 22, 2026 9:49pm | Jul 22, 2026 9:49pm | LowHangingWires |  | Fair | No | Check and found okay
Outage | J.E.26.07.25579 | C001862356 | Michael Christian | St.James | Completed | Load_246542 | Bogue - 310 | Jul 22, 2026 3:19pm | Jul 22, 2026 3:23pm | Jul 22, 2026 8:00pm | Jul 22, 2026 8:00pm | Jul 22, 2026 8:35pm | Jul 22, 2026 8:53pm | Jul 22, 2026 8:53pm | Jul 22, 2026 8:53pm | Fire |  | Fair | No | Found 1 25 kava transformer out cause by tree replace 1 2 amp in 1 25 no pole #
Outage | J.E.26.07.25593 | C001862355 | Michael Christian | St.James | Completed | Load_301652 | Bogue - 310 | Jul 22, 2026 3:19pm | Jul 22, 2026 3:23pm | Jul 22, 2026 3:37pm | Jul 22, 2026 3:37pm | Jul 22, 2026 4:20pm | Jul 22, 2026 4:31pm | Jul 22, 2026 4:31pm | Jul 22, 2026 4:31pm |  |  | Fair | No | Check and found okay voltage 111 112 223 at pothead
Outage | J.E.26.07.24406 | C001862345 | Kenroy Dale | Manchester | Completed | Load_244557 | Kendal - 310 | Jul 22, 2026 3:13pm | Jul 22, 2026 3:19pm | Jul 22, 2026 6:07pm | Jul 22, 2026 6:07pm | Jul 22, 2026 6:07pm | Jul 22, 2026 6:08pm | Jul 22, 2026 6:11pm | Jul 22, 2026 6:11pm |  |  | Rains | No | Customer meter was disconnected payment was made and call center was contacted, customer now with supply
Outage | J.E.26.07.25247 | C001862346 | Kenroy Dale | Manchester | Completed | Load_405391 | Kendal - 310 | Jul 22, 2026 3:13pm | Jul 22, 2026 3:19pm | Jul 22, 2026 7:48pm | Jul 22, 2026 7:48pm | Jul 22, 2026 8:07pm | Jul 22, 2026 8:07pm | Jul 22, 2026 8:10pm | Jul 22, 2026 8:10pm |  |  | Fair | No | Customer have internal problems voltage reading 112/114/226
Outage | J.E.26.07.25496 | C001862347 | Kenroy Dale | Manchester | Completed | Load_238663 | Kendal - 310 | Jul 22, 2026 3:13pm | Jul 22, 2026 3:19pm | Jul 22, 2026 4:41pm | Jul 22, 2026 6:12pm | Jul 22, 2026 6:47pm | Jul 22, 2026 7:46pm | Jul 22, 2026 7:48pm | Jul 22, 2026 7:48pm | BrokenWire |  | Rains | No | Defective service wire found, service wires was replaced with approximately 90 feet of #6 triple x and 2 one bolt clamp voltage reading 110
Outage | J.E.26.07.25485 | C001862344 | Richard Samuda | Manchester | Completed | Load_265474 | Kendal - 210 | Jul 22, 2026 3:12pm | Jul 22, 2026 3:13pm | Jul 22, 2026 3:26pm | Jul 22, 2026 3:31pm | Jul 22, 2026 3:32pm | Jul 22, 2026 3:33pm | Jul 22, 2026 3:34pm | Jul 22, 2026 3:34pm |  |  | Fair | No | Customer say she’s back to normal
Outage | J.E.26.07.25407 | C001862331 | Barnett Brown | Manchester | Completed | Load_267897 | Spur Tree - 310 | Jul 22, 2026 3:09pm | Jul 22, 2026 3:11pm | Jul 22, 2026 6:18pm | Jul 22, 2026 6:18pm | Jul 22, 2026 7:18pm | Jul 22, 2026 7:27pm | Jul 22, 2026 7:28pm | Jul 22, 2026 7:28pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.25462 | C001862333 | Barnett Brown | Manchester | Completed | Load_258623 | Spur Tree - 310 | Jul 22, 2026 3:09pm | Jul 22, 2026 3:11pm | Jul 22, 2026 5:47pm | Jul 22, 2026 5:47pm | Jul 22, 2026 5:59pm | Jul 22, 2026 6:00pm | Jul 22, 2026 6:01pm | Jul 22, 2026 6:01pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.25483 | C001862334 | Barnett Brown | Manchester | Completed | Load_247129 | Spur Tree - 310 | Jul 22, 2026 3:09pm | Jul 22, 2026 3:11pm | Jul 22, 2026 7:32pm | Jul 22, 2026 7:32pm | Jul 22, 2026 7:49pm | Jul 22, 2026 8:16pm | Jul 22, 2026 8:20pm | Jul 22, 2026 8:20pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.25497 | C001862335 | Barnett Brown | Manchester | Completed | Load_245920 | Spur Tree - 310 | Jul 22, 2026 3:09pm | Jul 22, 2026 3:11pm | Jul 22, 2026 6:01pm | Jul 22, 2026 6:03pm | Jul 22, 2026 6:03pm | Jul 22, 2026 6:03pm | Jul 22, 2026 6:04pm | Jul 22, 2026 6:04pm | Fire |  | Fair | No | Premises found ok
Outage | J.E.26.07.25547 | C001862336 | Barnett Brown | Manchester | Completed | Load_240457 | Spur Tree - 310 | Jul 22, 2026 3:09pm | Jul 22, 2026 3:12pm | Jul 22, 2026 3:34pm | Jul 22, 2026 3:34pm | Jul 22, 2026 5:15pm | Jul 22, 2026 5:38pm | Jul 22, 2026 5:40pm | Jul 22, 2026 5:40pm |  |  | Fair | No | Replace blown 3 amp transformer fuse
Outage | J.E.26.07.25070 | C001862329 | Richard Samuda | Manchester | Completed | Load_250940 | Spur Tree - 310 | Jul 22, 2026 3:08pm | Jul 23, 2026 4:00pm | Jul 23, 2026 5:14pm | Jul 23, 2026 5:14pm | Jul 23, 2026 5:31pm | Jul 23, 2026 5:33pm | Jul 23, 2026 5:34pm | Jul 23, 2026 5:34pm |  |  | Fair | No | Refer call to field service customer say he needs his meter to be clamps and lock because they take out his meter
Non-Outage | J.E.26.07.23586 | C001862307 | Moses Elliston | Portmore | Completed | Load_239843 | Naggo Head - 610 | Jul 22, 2026 2:53pm | Jul 22, 2026 2:55pm | Jul 22, 2026 4:27pm | Jul 22, 2026 4:27pm | Jul 22, 2026 4:27pm | Jul 22, 2026 4:27pm | Jul 22, 2026 4:32pm | Jul 22, 2026 4:32pm |  |  | Fair | No | Meter not seen.Seen at location is # 2790106.Replaced with meter # 3069767 due to burnt meter socket phase lead that was repaired.118-118-236 volts
Outage | J.E.26.07.25400 | C001862292 | Edward Royal | KSAS | Completed | Load_1002691 | Cane River - 410 | Jul 22, 2026 2:40pm | Jul 22, 2026 2:41pm | Jul 22, 2026 2:48pm | Jul 22, 2026 2:48pm | Jul 22, 2026 3:38pm | Jul 22, 2026 3:43pm | Jul 22, 2026 3:43pm | Jul 22, 2026 3:43pm |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.07.25424 | C001862291 | Floyd Taylor | Trelawny | Completed | Load_251536 | Greenwood - 210 | Jul 22, 2026 2:39pm | Jul 22, 2026 2:39pm | Jul 23, 2026 4:02pm | Jul 23, 2026 4:02pm | Jul 23, 2026 5:04pm | Jul 23, 2026 5:06pm | Jul 23, 2026 5:07pm | Jul 23, 2026 5:07pm |  |  | Fair | No | Remake joint at pole using 3pg clamps voltage readings left 115,112,232
Outage | J.E.26.07.25517 | C001862282 | Collin Robinson | Portland | Completed | Load_261260 | Port Antonio - 410 | Jul 22, 2026 2:19pm | Jul 22, 2026 5:30pm | Jul 22, 2026 6:51pm | Jul 22, 2026 7:05pm | Jul 22, 2026 7:54pm | Jul 22, 2026 7:59pm | Jul 22, 2026 7:59pm | Jul 22, 2026 7:59pm |  |  | Fair | No | Premises found with supply Voltage reading 115v 114v 229v
Non-Outage | J.E.26.07.25514 | C001862280 | Gregory Grossett | null | Completed | null | null | Jul 22, 2026 2:13pm | Jul 22, 2026 2:14pm | Jul 22, 2026 3:15pm | Jul 22, 2026 3:15pm | Jul 22, 2026 4:21pm | Jul 22, 2026 5:06pm | Jul 22, 2026 5:07pm | Jul 22, 2026 5:07pm | Fire |  | Fair | No | 10kva transformer trip at pole#556713 cause by truck entangled with conductors causing them to bang and burn.Repair conductor then restore supply to the area material use 1 one bolt clamp.
Outage | J.E.26.07.25482 | C001862275 | Daniel Francis | St.Ann | Completed | Load_303102 | Ocho Rios - 410 | Jul 22, 2026 2:08pm | Jul 22, 2026 3:57pm | Jul 22, 2026 9:01pm | Jul 22, 2026 9:01pm | Jul 22, 2026 9:47pm | Jul 22, 2026 9:48pm | Jul 22, 2026 9:48pm | Jul 22, 2026 9:48pm |  |  | Fair | No | Not found customer not answering phone
Outage | J.E.26.07.25496 | C001862267 | Kenroy Dale | Manchester | Completed | Load_238663 | Kendal - 310 | Jul 22, 2026 2:03pm | Jul 22, 2026 3:47pm | Jul 22, 2026 8:11pm | Jul 22, 2026 8:12pm | Jul 22, 2026 8:28pm | Jul 22, 2026 8:34pm | Jul 22, 2026 8:37pm | Jul 22, 2026 8:37pm | BrokenWire |  | Fair | No | Duplicated services order
Outage | J.E.26.07.25472 | C001862263 | Neville Spencer | Clarendon | Completed | Load_265095 | Parnassus - 310 | Jul 22, 2026 1:59pm | Jul 22, 2026 2:00pm | Jul 22, 2026 2:06pm | Jul 22, 2026 2:06pm | Jul 22, 2026 2:42pm | Jul 22, 2026 2:42pm | Jul 22, 2026 2:44pm | Jul 22, 2026 2:44pm |  |  | Rains | No | Found supply at location.
Outage | J.E.26.07.25489 | C001862262 | Raheem Ricketts | Manchester | Completed | Load_255096 | Spur Tree - 210 | Jul 22, 2026 1:58pm | Jul 22, 2026 1:58pm | Jul 22, 2026 2:07pm | Jul 22, 2026 2:51pm | Jul 22, 2026 2:51pm | Jul 22, 2026 2:52pm | Jul 22, 2026 2:52pm | Jul 22, 2026 2:52pm |  |  | Rains | No | Check and found customer experiencing an internal problem
Outage | J.E.26.07.25486 | C001862260 | Clyde Brown | Clarendon | Completed | Load_253095 | May Pen - 110 | Jul 22, 2026 1:57pm | Jul 22, 2026 4:26pm | Jul 22, 2026 4:38pm | Jul 22, 2026 4:38pm | Jul 22, 2026 5:48pm | Jul 22, 2026 6:17pm | Jul 22, 2026 6:24pm | Jul 22, 2026 6:24pm | BrokenWire |  | Fair | No | Broken 2wire service caused by car replaced with 80ft-#6 triplex service wire and 4 one bolt clamp.
Outage | J.E.26.07.25478 | C001862250 | Tajay Bernard | Hanover | Completed | Load_261071 | Orange Bay - 310 | Jul 22, 2026 1:50pm | Jul 22, 2026 1:50pm | Jul 22, 2026 1:56pm | Jul 22, 2026 1:56pm | Jul 22, 2026 2:14pm | Jul 22, 2026 3:26pm | Jul 22, 2026 3:26pm | Jul 22, 2026 3:26pm | Fire |  | Fair | No | Isolate 1 25kva Transformer to retention 1 pole span of secondary phase use 1 pre form and 1 clamp
Non-Outage | J.E.26.07.25383 | C001862245 | Edward Royal | KSAS | Completed | Load_300873 | Cane River - 410 | Jul 22, 2026 1:40pm | Jul 22, 2026 2:38pm | Jul 22, 2026 3:43pm | Jul 22, 2026 3:43pm | Jul 22, 2026 3:43pm | Jul 22, 2026 3:44pm | Jul 22, 2026 3:44pm | Jul 22, 2026 3:44pm |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.07.25467 | C001862244 | Neckell Ormsby | null | Completed | null | null | Jul 22, 2026 1:38pm | Jul 22, 2026 4:34pm | Jul 22, 2026 6:24pm | Jul 22, 2026 6:24pm | Jul 22, 2026 7:00pm | Jul 22, 2026 7:06pm | Jul 22, 2026 7:06pm | Jul 22, 2026 7:06pm | BrokenWire |  | Fair | No | Found leaning concrete pole needs straighten so customer can be connected please refer to maintenance department
Outage | J.E.26.07.25399 | C001862234 | Edward Royal | KSAS | Completed | Load_268953 | Up Park Camp - 410 | Jul 22, 2026 1:32pm | Jul 22, 2026 1:36pm | Jul 22, 2026 2:24pm | Jul 22, 2026 2:24pm | Jul 22, 2026 2:36pm | Jul 22, 2026 2:37pm | Jul 22, 2026 2:37pm | Jul 22, 2026 2:37pm |  |  | Fair | No | Replaced 3A transformer fuse
Outage | J.E.26.07.25434 | C001862233 | Nickolas Rodriques | St.Catherine | Completed | Load_252346 | Rhodens Pen - 410 | Jul 22, 2026 1:32pm | Jul 23, 2026 7:19am | Jul 23, 2026 7:59am | Jul 23, 2026 8:00am | Jul 23, 2026 8:44am | Jul 23, 2026 8:58am | Jul 23, 2026 9:00am | Jul 23, 2026 9:00am |  |  | Fair | No | Kingston call
Outage | J.E.26.07.25359 | C001862227 | Richard Grant | St.Catherine | Completed | Load_254015 | New Michelton - 410 | Jul 22, 2026 1:29pm | Jul 22, 2026 1:30pm | Jul 22, 2026 2:02pm | Jul 22, 2026 2:02pm | Jul 22, 2026 2:02pm | Jul 22, 2026 2:02pm | Jul 22, 2026 2:02pm | Jul 22, 2026 2:02pm |  | Y | Rains | No | Blown junction fuse seen for single phase primary caused by jps bushing contractor, however, heavy rain preventing crew from re-energizing line section. Kindly assign call to evening crew.
Outage | J.E.26.07.25445 | C001862223 | Edward Royal | KSAS | Completed | Load_248770 | Up Park Camp - 510 | Jul 22, 2026 1:24pm | Jul 22, 2026 2:38pm | Jul 22, 2026 5:36pm | Jul 22, 2026 5:36pm | Jul 22, 2026 5:36pm | Jul 22, 2026 5:36pm | Jul 22, 2026 5:37pm | Jul 22, 2026 5:37pm |  |  | Fair | No | When contacted customer said that they were testing out the mobile app
Outage | J.E.26.07.24626 | C001862219 | Edward Royal | KSAS | Completed | Load_266567 | Up Park Camp - 310 | Jul 22, 2026 1:11pm | Jul 22, 2026 1:16pm | Jul 22, 2026 1:33pm | Jul 22, 2026 1:33pm | Jul 22, 2026 1:47pm | Jul 22, 2026 2:24pm | Jul 22, 2026 2:24pm | Jul 22, 2026 2:24pm |  |  | Fair | No | Spliced and reconnected service cable using 20ft service cable 3 single bolt clamp
Outage | J.E.26.07.25408 | C001862215 | Roxroy Needham | St.Ann | Completed | Load_260564 | Cardiff Hall - 210 | Jul 22, 2026 1:10pm | Jul 22, 2026 4:01pm | Jul 22, 2026 4:12pm | Jul 22, 2026 4:12pm | Jul 22, 2026 5:07pm | Jul 22, 2026 5:24pm | Jul 22, 2026 5:27pm | Jul 22, 2026 5:27pm |  |  | Fair | No | Clean and remake joints at pole and pothead used 2- 1bolt clamps voltage readings left 112
Outage | J.E.26.07.25333 | C001862207 | Raymond Carr | St.Ann | Completed | Load_576564 | Upper White River - 210 | Jul 22, 2026 1:01pm | Jul 22, 2026 1:02pm | Jul 22, 2026 2:32pm | Jul 22, 2026 2:32pm | Jul 22, 2026 3:06pm | Jul 22, 2026 3:27pm | Jul 22, 2026 3:29pm | Jul 22, 2026 3:29pm |  |  | Fair | No | Blown junction fuse found at pole number 0059883, line patrol and found okay, however bird contact was suspected. A 10 amp fuse fuse was used to renew, supply was restored.
Outage | J.E.26.07.25425 | C001862204 | Floyd Taylor | Trelawny | Completed | Load_259034 | Greenwood - 110 | Jul 22, 2026 1:00pm | Jul 22, 2026 1:00pm | Jul 22, 2026 1:35pm | Jul 22, 2026 1:35pm | Jul 22, 2026 2:45pm | Jul 22, 2026 3:49pm | Jul 22, 2026 3:50pm | Jul 22, 2026 3:50pm | BrokenWire |  | Fair | No | Isolate 25kva transformer, splice and retention 2 spans of secondary phase and 1 tree wire service using 4pg clamps, voltage reading 117,118,234
Outage | J.E.26.07.25391 | C001862200 | Romeo Brissett | St.James | Completed | Load_244051 | Bogue - 610 | Jul 22, 2026 12:54pm | Jul 22, 2026 12:55pm | Jul 22, 2026 3:36pm | Jul 22, 2026 3:36pm | Jul 22, 2026 3:37pm | Jul 22, 2026 3:37pm | Jul 22, 2026 3:42pm | Jul 22, 2026 3:42pm |  |  | Rains | No | Check and found ok.
Non-Outage | J.E.26.07.25403 | C001862179 | Andrae Clarke | Portland | Completed | Load_240419 | Port Antonio - 410 | Jul 22, 2026 12:39pm | Jul 22, 2026 12:39pm | Jul 22, 2026 1:52pm | Jul 22, 2026 1:52pm | Jul 22, 2026 1:59pm | Jul 22, 2026 3:36pm | Jul 22, 2026 3:25pm | Jul 22, 2026 3:25pm |  |  | Fair | No | Premises okay Check voltage 117/118/236Customer need an electrician to check internal
Non-Outage | J.E.26.07.25397 | C001862178 | Andrae Clarke | Portland | Completed | Load_242336 | Port Antonio - 410 | Jul 22, 2026 12:37pm | Jul 22, 2026 12:38pm | Jul 22, 2026 12:49pm | Jul 22, 2026 12:49pm | Jul 22, 2026 12:57pm | Jul 22, 2026 12:57pm | Jul 22, 2026 1:01pm | Jul 22, 2026 1:01pm |  |  | Fair | No | Lead from transformer to secondary line corroded connections needs cleaning Emergency crew needed
Outage | J.E.26.07.25395 | C001862174 | Javid Vernon | Hanover | Completed | Load_301743 | Orange Bay - 310 | Jul 22, 2026 12:34pm | Jul 22, 2026 12:36pm | Jul 22, 2026 2:05pm | Jul 22, 2026 2:05pm | Jul 22, 2026 2:14pm | Jul 22, 2026 2:21pm | Jul 22, 2026 2:22pm | Jul 22, 2026 2:22pm |  |  | Fair | No | Premises check and found okay voltage found and left 113/116/231
Non-Outage | J.E.26.07.16574 | C001862173 | Rusean Allen | KSAS | Completed | Load_260269 | Up Park Camp - 510 | Jul 22, 2026 12:33pm | Jul 22, 2026 12:34pm | Jul 22, 2026 1:22pm | Jul 22, 2026 1:22pm | Jul 22, 2026 1:36pm | Jul 22, 2026 1:36pm | Jul 22, 2026 1:37pm | Jul 22, 2026 1:37pm |  |  | Fair | No | Premises found locked
Non-Outage | J.E.26.07.25374 | C001862166 | Marlon Brown | Trelawny | Completed | Load_302472 | Duncans - 210 | Jul 22, 2026 12:27pm | Jul 22, 2026 3:27pm | Jul 22, 2026 4:01pm | Jul 22, 2026 4:01pm | Jul 22, 2026 4:46pm | Jul 22, 2026 4:48pm | Jul 22, 2026 4:48pm | Jul 22, 2026 4:48pm |  |  | Fair | No | Customer needs to visit the commercial office to have the account registered to him.
Outage | J.E.26.07.25230 | C001862165 | Daniel Francis | St.Ann | Completed | Load_260731 | Roaring River - 210 | Jul 22, 2026 12:27pm | Jul 22, 2026 3:59pm | Jul 22, 2026 5:22pm | Jul 22, 2026 5:22pm | Jul 22, 2026 6:17pm | Jul 22, 2026 6:16pm | Jul 22, 2026 6:20pm | Jul 22, 2026 6:20pm |  |  | Fair | No | Disconnected for none payment
Non-Outage | J.E.26.07.25252 | C001862160 | Milton Charlton | KSAN | Completed | Load_246103 | Constant Spring - 210 | Jul 22, 2026 12:24pm | Jul 22, 2026 3:33pm | Jul 22, 2026 5:18pm | Jul 22, 2026 5:18pm | Jul 22, 2026 5:18pm | Jul 22, 2026 2:55pm | Jul 22, 2026 5:23pm | Jul 22, 2026 5:23pm | Fire |  | Fair | No | Isolate 25 kva transformer at pole #0077489 and repair broken open wire secondary neutral using 30ft #2AA conductor, one #2 preform and three 1- bolt clamps and reclosed transformer switch.
Outage | J.E.26.07.25286 | C001862158 | Andre Williams | Trelawny | Completed | Load_255636 | Duncans - 210 | Jul 22, 2026 12:22pm | Jul 22, 2026 12:23pm | Jul 22, 2026 12:40pm | Jul 22, 2026 12:42pm | Jul 22, 2026 1:55pm | Jul 22, 2026 2:14pm | Jul 22, 2026 2:15pm | Jul 22, 2026 2:15pm |  |  | Fair | No | Patrol line section re fuse and close main 30 amp on 20 amp junction on 3 phase line
Outage | J.E.26.07.25369 | C001862155 | Javid Vernon | Westmoreland | Completed | Load_261485 | Paradise - 210 | Jul 22, 2026 12:18pm | Jul 22, 2026 1:18pm | Jul 22, 2026 2:23pm | Jul 22, 2026 2:23pm | Jul 22, 2026 3:07pm | Jul 22, 2026 3:31pm | Jul 22, 2026 3:35pm | Jul 22, 2026 3:35pm |  |  | Fair | No | Clean and remake joints at JPS pole use two clamp voltage found 101/117/218 voltage left 111/117/228
Outage | J.E.26.07.25375 | C001862151 | Romeo Brissett | St.James | Completed | Load_292985 | Bogue - 610 | Jul 22, 2026 12:15pm | Jul 22, 2026 12:16pm | Jul 22, 2026 1:42pm | Jul 22, 2026 1:42pm | Jul 22, 2026 2:23pm | Jul 22, 2026 3:34pm | Jul 22, 2026 3:36pm | Jul 22, 2026 3:36pm |  |  | Rains | No | Removed bamboos and replaced (1)50amps junction fuse.
Non-Outage | J.E.26.07.25338 | C001862139 | Romeo Brissett | null | Completed | null | null | Jul 22, 2026 12:07pm | Jul 22, 2026 12:07pm | Jul 22, 2026 12:21pm | Jul 22, 2026 12:22pm | Jul 22, 2026 1:37pm | Jul 22, 2026 1:38pm | Jul 22, 2026 1:42pm | Jul 22, 2026 1:42pm | BrokenWire |  | Fair | No | Line patrolled and found ok, resident stated issue is resolved and no broken wire found in the area .
Non-Outage | J.E.26.07.24434 | C001862132 | Oshane Warren | null | Completed | null | null | Jul 22, 2026 12:05pm | Jul 22, 2026 12:06pm | Jul 22, 2026 12:59pm | Jul 22, 2026 12:59pm | Jul 22, 2026 12:59pm | Jul 22, 2026 12:59pm | Jul 22, 2026 1:00pm | Jul 22, 2026 1:00pm | BrokenWire |  | Rains | No | Splice and retention one spand of secondary conductor and replace 5amp 50kva xformer fuse
Outage | J.E.26.07.25217 | C001862130 | Kaydon Taylor | KSAN | Completed | Load_263471 | Washington Blvd - 410 | Jul 22, 2026 12:05pm | Jul 22, 2026 1:57pm | Jul 22, 2026 3:19pm | Jul 22, 2026 8:58pm | Jul 22, 2026 10:17pm | Jul 22, 2026 10:18pm | Jul 22, 2026 10:18pm | Jul 22, 2026 10:18pm |  |  | Fair | No | Premises closed
Outage | J.E.26.07.25314 | C001862131 | Nickolas Rodriques | St.Catherine | Completed | Load_1000355 | Rhodens Pen - 210 | Jul 22, 2026 12:05pm | Jul 22, 2026 12:10pm | Jul 22, 2026 2:06pm | Jul 22, 2026 2:06pm | Jul 22, 2026 2:50pm | Jul 22, 2026 3:06pm | Jul 22, 2026 3:17pm | Jul 22, 2026 3:17pm |  |  | Fair | No | Found customer with electricity. The customer stated that there was an area outage which was restored little after making the report.
Outage | J.E.26.07.25336 | C001862129 | Richard Nicholas | St.Catherine | Completed | Load_242765 | Twickenham - 310 | Jul 22, 2026 12:04pm | Jul 23, 2026 7:39am | Jul 23, 2026 8:00am | Jul 23, 2026 10:32am | Jul 23, 2026 11:52am | Jul 23, 2026 11:54am | Jul 23, 2026 11:55am | Jul 23, 2026 11:55am |  |  | Fair | No | Remade burnt off twisted secondary phase at pole.2 clamp was used.voltage reading 112,113 and 225v.
Non-Outage | J.E.26.07.25133 | C001862125 | Moses Elliston | null | Completed | null | null | Jul 22, 2026 11:56am | Jul 22, 2026 11:56am | Jul 22, 2026 4:36pm | Jul 22, 2026 5:11pm | Jul 22, 2026 5:11pm | Jul 22, 2026 5:11pm | Jul 22, 2026 5:12pm | Jul 22, 2026 5:12pm |  |  | Fair | No | Supply connected.New Installation
Outage | J.E.26.07.25245 | C001862117 | Milton Charlton | KSAN | Completed | Load_246103 | Constant Spring - 210 | Jul 22, 2026 11:54am | Jul 22, 2026 12:03pm | Jul 22, 2026 3:21pm | Jul 22, 2026 3:21pm | Jul 22, 2026 3:26pm | Jul 22, 2026 2:55pm | Jul 22, 2026 3:30pm | Jul 22, 2026 3:30pm |  |  | Fair | No | Isolate 25 kva transformer at pole #0077489 and repair broken open wire secondary neutral using 30ft #2AA conductor, one #2 preform and three 1- bolt clamps. Reclosed transformer switch.
Outage | J.E.26.07.25268 | C001862118 | Milton Charlton | KSAN | Completed | Load_412822 | Constant Spring - 210 | Jul 22, 2026 11:54am | Jul 22, 2026 12:03pm | Jul 22, 2026 12:47pm | Jul 22, 2026 12:47pm | Jul 22, 2026 3:18pm | Jul 22, 2026 11:40am | Jul 22, 2026 3:21pm | Jul 22, 2026 3:21pm |  |  | Fair | No | Unable to locate customer by telephone. Telephone number on report is temporarily out of service.
Outage | J.E.26.07.25272 | C001862110 | Damion Reid | Manchester | Completed | Load_255147 | Kendal - 210 | Jul 22, 2026 11:50am | Jul 22, 2026 11:51am | Jul 22, 2026 12:16pm | Jul 22, 2026 12:16pm | Jul 22, 2026 1:17pm | Jul 22, 2026 1:55pm | Jul 22, 2026 1:56pm | Jul 22, 2026 1:56pm |  |  | Fair | No | Remade corroded phase at secondary jumper using one 1 bolt clamp
Non-Outage | J.E.26.07.24292 | C001862106 | Omar King | St.Ann | Completed | Load_239479 | Ocho Rios - 310 | Jul 22, 2026 11:48am | Jul 22, 2026 11:48am | Jul 22, 2026 12:27pm | Jul 22, 2026 12:27pm | Jul 22, 2026 1:49pm | Jul 22, 2026 1:52pm | Jul 22, 2026 1:52pm | Jul 22, 2026 1:52pm |  |  | Fair | No | Found customer pothead with corrosion as been repaired customer is now with supply Voltage reading 113-111-229 Volts
Outage | J.E.26.07.25128 | C001862107 | Fitzroy Turner | KSAS | Completed | Load_261030 | Rockfort - 410 | Jul 22, 2026 11:48am | Jul 22, 2026 11:50am | Jul 22, 2026 1:24pm | Jul 22, 2026 1:24pm | Jul 22, 2026 1:52pm | Jul 22, 2026 2:09pm | Jul 22, 2026 2:10pm | Jul 22, 2026 2:10pm |  |  | Fair | No | Customer have defective meter socket customer advised to carry out repairs
Outage | J.E.26.07.25200 | C001862105 | Rusean Allen | KSAS | Completed | Load_247229 | Hunts Bay - 310 | Jul 22, 2026 11:47am | Jul 22, 2026 11:49am | Jul 22, 2026 12:29pm | Jul 22, 2026 12:50pm | Jul 22, 2026 12:51pm | Jul 22, 2026 12:53pm | Jul 22, 2026 12:53pm | Jul 22, 2026 12:53pm |  |  | Fair | No | Meter socket barrel locked, unable to check meter, refer to field service department.
Outage | J.E.26.07.25263 | C001862095 | Evan Spaulding | St.Mary | Completed | Load_257596 | Annotto Bay - 310 | Jul 22, 2026 11:36am | Jul 22, 2026 11:37am | Jul 22, 2026 1:12pm | Jul 22, 2026 1:12pm | Jul 22, 2026 1:12pm | Jul 22, 2026 1:12pm | Jul 22, 2026 1:13pm | Jul 22, 2026 1:13pm |  |  | Fair | No | Associated call
Outage | J.E.26.07.25066 | C001862088 | Hartley Chin | Clarendon | Completed | Load_262567 | May Pen - 110 | Jul 22, 2026 11:34am | Jul 22, 2026 11:35am | Jul 22, 2026 12:58pm | Jul 22, 2026 12:58pm | Jul 22, 2026 2:29pm | Jul 22, 2026 2:40pm | Jul 22, 2026 2:42pm | Jul 22, 2026 2:42pm | BrokenWire |  | Fair | No | Found damage service wire. Changed 60ft #6 triplex.114v115v230v
Outage | J.E.26.07.22384 | C001862087 | Edward Royal | KSAS | Completed | Load_258668 | Greenwich - 710 | Jul 22, 2026 11:32am | Jul 22, 2026 11:32am | Jul 22, 2026 11:51am | Jul 22, 2026 11:51am | Jul 22, 2026 12:02pm | Jul 22, 2026 12:51pm | Jul 22, 2026 12:51pm | Jul 22, 2026 12:51pm |  |  | Fair | No | EN box need to be check box is burnt up reffered to field service
Outage | J.E.26.07.25261 | C001862086 | Richard Nicholas | St.Catherine | Completed | Load_1001436 | Tredegar - 210 | Jul 22, 2026 11:32am | Jul 22, 2026 11:34am | Jul 22, 2026 2:51pm | Jul 22, 2026 2:51pm | Jul 22, 2026 3:37pm | Jul 22, 2026 4:18pm | Jul 22, 2026 4:19pm | Jul 22, 2026 4:19pm |  |  | Fair | No | Prepaid rammy failure.
Outage | J.E.26.07.25258 | C001862085 | Richard Grant | St.Catherine | Completed | Load_257901 | New Michelton - 410 | Jul 22, 2026 11:31am | Jul 22, 2026 11:32am | Jul 22, 2026 12:38pm | Jul 22, 2026 1:46pm | Jul 22, 2026 1:46pm | Jul 22, 2026 1:47pm | Jul 22, 2026 1:47pm | Jul 22, 2026 1:47pm |  | Y | Rains | No | Blown junction fuse seen for single phase primary caused by jps bushing contractor, however, heavy rain preventing crew from re-energizing line section. Kindly assign call to evening crew.
Outage | J.E.26.07.25149 | C001862072 | Barrington Brown | St.James | Completed | Load_261501 | Bogue - 310 | Jul 22, 2026 11:21am | Jul 22, 2026 11:22am | Jul 22, 2026 2:57pm | Jul 22, 2026 2:57pm | Jul 22, 2026 4:14pm | Jul 22, 2026 4:18pm | Jul 22, 2026 4:19pm | Jul 22, 2026 4:19pm |  |  | SevereWind | No | 2 junction fuse found blown on location due to bird contact on switch top jumper, crew reshaped jumper and replaced 2 15amps fuses. Customers now restored
Outage | J.E.26.07.25248 | C001862068 | Ryan Richards | Manchester | Completed | Load_254948 | Spur Tree - 310 | Jul 22, 2026 11:20am | Jul 23, 2026 7:37am | Jul 23, 2026 12:43pm | Jul 23, 2026 12:43pm | Jul 23, 2026 2:17pm | Jul 23, 2026 3:17pm | Jul 23, 2026 3:17pm | Jul 23, 2026 3:17pm |  |  | Fair | No | Areas found ok area was checked customer said that the power was restored yesterday evening
Outage | J.E.26.07.25219 | C001862064 | Wan Carlos Scarlett | Portmore | Completed | Load_249933 | Naggo Head - 510 | Jul 22, 2026 11:18am | Jul 22, 2026 11:19am | Jul 22, 2026 2:12pm | Jul 22, 2026 2:12pm | Jul 22, 2026 2:53pm | Jul 22, 2026 3:39pm | Jul 22, 2026 3:42pm | Jul 22, 2026 3:42pm |  |  | Fair | No | Found customer 240 meter single phasing meter # 2218958 call refer to field service
Outage | J.E.26.07.25224 | C001862066 | Richard Grant | St.Catherine | Completed | Load_556137 | New Michelton - 410 | Jul 22, 2026 11:18am | Jul 22, 2026 11:20am | Jul 22, 2026 12:38pm | Jul 22, 2026 12:38pm | Jul 22, 2026 1:23pm | Jul 22, 2026 1:46pm | Jul 22, 2026 1:46pm | Jul 22, 2026 1:46pm |  | Y | Rains | No | Blown junction fuse seen for single phase primary caused by jps bushing contractor, however, heavy rain preventing crew from re-energizing line section. Kindly assign call to evening crew.
Outage | J.E.26.07.25227 | C001862065 | Wan Carlos Scarlett | Portmore | Completed | Load_567928 | Naggo Head - 610 | Jul 22, 2026 11:18am | Jul 23, 2026 7:26am | Jul 23, 2026 9:31am | Jul 23, 2026 2:01pm | Jul 23, 2026 2:32pm | Jul 23, 2026 3:02pm | Jul 23, 2026 3:03pm | Jul 23, 2026 3:03pm | BrokenWire |  | Fair | No | Found customer 3 wire service at pole with the neutral broken off use one bolt clamp at secondary line neutral readings 114-115-230
Outage | J.E.26.07.24963 | C001862039 | Ryan Richards | Manchester | Completed | Load_263270 | Spur Tree - 310 | Jul 22, 2026 11:04am | Jul 22, 2026 11:04am | Jul 22, 2026 11:43am | Jul 22, 2026 11:43am | Jul 22, 2026 12:39pm | Jul 22, 2026 2:46pm | Jul 22, 2026 2:46pm | Jul 22, 2026 2:46pm |  |  | Fair | No | Blown 30 amp junction fuse found line patrol coconut tree limb found an the primary conductor junction switch bottom also burnt off one span of primary conductor also straun out replace that span using 100ft#2 aluminum 1 dead end insulator and dead end clamp …..chop coconut tree limbs off the line and remade burn off switch bottom also replaced blown 30 amp junction area was recheck and all customers are with supply
Outage | J.E.26.07.25097 | C001862038 | Oshane Warren | Westmoreland | Completed | Load_267097 | Paradise - 310 | Jul 22, 2026 11:03am | Jul 22, 2026 11:04am | Jul 22, 2026 12:31pm | Jul 22, 2026 12:31pm | Jul 22, 2026 12:31pm | Jul 22, 2026 12:31pm | Jul 22, 2026 12:32pm | Jul 22, 2026 12:32pm |  |  | Rains | No | Splice and retention one spand of secondary conductor and replace 5amp 50kva xformer fuse
Non-Outage | J.E.26.07.24890 | C001862036 | Rochaine Hussey | KSAN | Completed | Load_249728 | West Kings House - 410 | Jul 22, 2026 11:01am | Jul 22, 2026 11:03am | Jul 22, 2026 2:30pm | Jul 22, 2026 2:30pm | Jul 22, 2026 2:32pm | Jul 22, 2026 2:36pm | Jul 22, 2026 2:36pm | Jul 22, 2026 2:36pm | Fire |  | Fair | No | Customer was called multiple times no answer Unable to locate
Non-Outage | J.E.26.07.24987 | C001862035 | Rochaine Hussey | KSAN | Completed | Load_269372 | West Kings House - 310 | Jul 22, 2026 11:01am | Jul 22, 2026 11:03am | Jul 22, 2026 1:02pm | Jul 22, 2026 1:26pm | Jul 22, 2026 1:26pm | Jul 22, 2026 2:22pm | Jul 22, 2026 2:22pm | Jul 22, 2026 2:22pm |  |  | Fair | No | Mid span connection was burnt out in clamp wire was rejoined and issue was resolved 115/116/231v6 1 bolt clamp was used
Outage | J.E.26.07.25194 | C001862026 | Collin Robinson | Portland | Completed | Load_249793 | Port Antonio - 310 | Jul 22, 2026 10:59am | Jul 22, 2026 2:49pm | Jul 22, 2026 4:41pm | Jul 22, 2026 4:41pm | Jul 22, 2026 6:39pm | Jul 22, 2026 6:51pm | Jul 22, 2026 6:51pm | Jul 22, 2026 6:51pm |  |  | Fair | No | Change one corroded one bolt clamp at pothead Voltage reading 117v to wire service
Outage | J.E.26.07.25193 | C001862010 | Raymond Carr | St.Mary | Completed | Load_261367 | Oracabessa - 210 | Jul 22, 2026 10:55am | Jul 22, 2026 10:55am | Jul 22, 2026 12:35pm | Jul 22, 2026 12:35pm | Jul 22, 2026 1:38pm | Jul 22, 2026 2:31pm | Jul 22, 2026 2:31pm | Jul 22, 2026 2:31pm |  |  | Fair | No | Blown junction fuse found at pole number 0013524, line patrol and found okay, however tree contact was suspected. A 20 amp fuse fuse was used to renew supply was restored.
Outage | J.E.26.07.25213 | C001862012 | Evan Spaulding | St.Mary | Completed | Load_252552 | Annotto Bay - 310 | Jul 22, 2026 10:55am | Jul 22, 2026 10:57am | Jul 22, 2026 11:58am | Jul 22, 2026 11:58am | Jul 22, 2026 12:54pm | Jul 22, 2026 1:07pm | Jul 22, 2026 1:10pm | Jul 22, 2026 1:10pm |  |  | Fair | No | No power coming from Hexin box 03350,refer to field service .
Outage | J.E.26.07.25218 | C001862011 | Tajay Bernard | Hanover | Completed | Load_259482 | Orange Bay - 310 | Jul 22, 2026 10:55am | Jul 22, 2026 10:55am | Jul 22, 2026 11:21am | Jul 22, 2026 11:21am | Jul 22, 2026 1:30pm | Jul 22, 2026 1:53pm | Jul 22, 2026 1:55pm | Jul 22, 2026 1:55pm | BrokenWire |  | Fair | No | Disconnect service wire that wasn’t in use and was hanging
Non-Outage | J.E.26.07.25116 | C001862006 | Devon Grant | KSAN | Completed | Load_244170 | Constant Spring - 310 | Jul 22, 2026 10:54am | Jul 22, 2026 10:56am | Jul 22, 2026 11:15am | Jul 22, 2026 11:16am | Jul 22, 2026 12:51pm | Jul 22, 2026 12:56pm | Jul 22, 2026 12:57pm | Jul 22, 2026 12:57pm |  |  | Fair | No | Internal problem.it was corrected by their electrician.no fire was seen at time of visit
Non-Outage | J.E.26.07.25140 | C001862007 | Neville Spencer | Clarendon | Completed | Load_247646 | Parnassus - 210 | Jul 22, 2026 10:54am | Jul 22, 2026 10:55am | Jul 22, 2026 12:39pm | Jul 22, 2026 12:39pm | Jul 22, 2026 1:25pm | Jul 22, 2026 1:44pm | Jul 22, 2026 1:46pm | Jul 22, 2026 1:46pm |  |  | Fair | No | Renew blown 10 amp fuse protecting 100 kva xmfr in bank of 3 supply restored.
Outage | J.E.26.07.22461 | C001862005 | Moses Elliston | St.Catherine | Completed | Load_265933 | New Michelton - 210 | Jul 22, 2026 10:53am | Jul 22, 2026 10:53am | Jul 23, 2026 10:36am | Jul 23, 2026 10:36am | Jul 23, 2026 10:36am | Jul 23, 2026 10:36am | Jul 23, 2026 10:38am | Jul 23, 2026 10:38am |  |  | Fair | No | Customer made a complain about bills
Non-Outage | J.E.26.06.38555 | C001861994 | Fredrick Hamilton | KSAN | Completed | Load_253373 | Constant Spring - 410 | Jul 22, 2026 10:49am | Jul 22, 2026 10:52am | Jul 22, 2026 11:01am | Jul 23, 2026 8:19am | Jul 23, 2026 8:20am | Jul 23, 2026 8:21am | Jul 23, 2026 8:22am | Jul 23, 2026 8:22am |  |  | Fair | No | Customer contacted and stated power was restored fully to location from last week Premises is ok
Non-Outage | J.E.26.07.23450 | C001861993 | Fredrick Hamilton | KSAN | Completed | Load_270019 | Constant Spring - 410 | Jul 22, 2026 10:49am | Jul 22, 2026 10:52am | Jul 22, 2026 11:01am | Jul 22, 2026 2:24pm | Jul 22, 2026 2:25pm | Jul 22, 2026 2:29pm | Jul 22, 2026 2:29pm | Jul 22, 2026 2:29pm |  |  | Fair | No | Customer contacted and stated that power was restored fully previously Premises is ok
Non-Outage | J.E.26.07.25159 | C001861991 | Fredrick Hamilton | KSAN | Completed | Load_256754 | Constant Spring - 410 | Jul 22, 2026 10:49am | Jul 22, 2026 10:52am | Jul 22, 2026 11:01am | Jul 22, 2026 12:00pm | Jul 22, 2026 12:00pm | Jul 22, 2026 12:01pm | Jul 22, 2026 12:01pm | Jul 22, 2026 12:01pm |  |  | Fair | No | Customer contacted and stated that power was restored fully previously Premises is ok
Non-Outage | J.E.26.07.24515 | C001861990 | Fredrick Hamilton | KSAN | Completed | Load_265865 | Washington Blvd - 810 | Jul 22, 2026 10:48am | Jul 22, 2026 10:52am | Jul 22, 2026 11:01am | Jul 22, 2026 11:49am | Jul 22, 2026 11:49am | Jul 22, 2026 11:53am | Jul 22, 2026 11:53am | Jul 22, 2026 11:53am |  |  | Fair | No | Customer contacted and stated that power was restored fully to location Premises is ok
Non-Outage | J.E.26.07.25133 | C001861989 | Wan Carlos Scarlett | null | Completed | null | null | Jul 22, 2026 10:48am | Jul 22, 2026 10:50am | Jul 22, 2026 10:55am | Jul 22, 2026 10:55am | Jul 22, 2026 11:16am | Jul 22, 2026 11:52am | Jul 22, 2026 11:54am | Jul 22, 2026 11:54am |  |  | Fair | No | Found hexing service box customer not getting any supply from the hexing contact escalation department for assistance escalation not getting any communication from the hexing.Call refer to Moses
Non-Outage | J.E.26.07.24047 | C001861988 | Fredrick Hamilton | KSAN | Completed | Load_301912 | Constant Spring - 210 | Jul 22, 2026 10:46am | Jul 22, 2026 10:52am | Jul 22, 2026 11:01am | Jul 22, 2026 11:55am | Jul 22, 2026 11:56am | Jul 22, 2026 11:58am | Jul 22, 2026 11:58am | Jul 22, 2026 11:58am |  |  | Fair | No | Customer contacted and stated that no disconnection was required Premises is ok customer has full power at location
Non-Outage | J.E.26.07.24399 | C001861987 | Fredrick Hamilton | KSAN | Completed | Load_412822 | Constant Spring - 210 | Jul 22, 2026 10:46am | Jul 22, 2026 10:52am | Jul 22, 2026 11:01am | Jul 22, 2026 11:23am | Jul 22, 2026 11:34am | Jul 22, 2026 11:44am | Jul 22, 2026 11:44am | Jul 22, 2026 11:44am |  |  | Fair | No | Premises found ok no issues detected on JPS supply 246v/122v/122v obtained
Non-Outage | J.E.26.07.25024 | C001861986 | Fredrick Hamilton | KSAN | Completed | Load_261228 | Constant Spring - 210 | Jul 22, 2026 10:46am | Jul 22, 2026 10:52am | Jul 22, 2026 11:01am | Jul 22, 2026 12:02pm | Jul 22, 2026 12:15pm | Jul 22, 2026 1:25pm | Jul 22, 2026 1:25pm | Jul 22, 2026 1:25pm |  |  | Fair | No | 232v/115.5v/115.7v obtained Customer defect defect detected customer advised
Outage | J.E.26.07.25211 | C001861978 | Raheem Ricketts | Manchester | Completed | Load_240892 | Spur Tree - 210 | Jul 22, 2026 10:45am | Jul 22, 2026 10:45am | Jul 22, 2026 10:56am | Jul 22, 2026 11:35am | Jul 22, 2026 11:41am | Jul 22, 2026 2:03pm | Jul 22, 2026 2:03pm | Jul 22, 2026 2:03pm |  |  | Fair | No | Check and found customer experiencing an internal problem
Outage | J.E.26.07.25153 | C001861976 | Rayon Foster | Westmoreland | Completed | Load_250796 | Paradise - 210 | Jul 22, 2026 10:39am | Jul 22, 2026 10:57am | Jul 22, 2026 2:27pm | Jul 22, 2026 2:28pm | Jul 22, 2026 2:28pm | Jul 22, 2026 2:29pm | Jul 22, 2026 2:30pm | Jul 22, 2026 2:30pm |  |  | Fair | No | Westmoreland call
Non-Outage | J.E.26.07.20448 | C001861944 | Nickolas Rodriques | null | Completed | null | null | Jul 22, 2026 10:29am | Jul 22, 2026 10:30am | Jul 22, 2026 12:34pm | Jul 22, 2026 12:38pm | Jul 22, 2026 1:31pm | Jul 22, 2026 1:55pm | Jul 22, 2026 2:06pm | Jul 22, 2026 2:06pm | LowHangingWires |  | Fair | No | Unable to communicate with the customer. However, no low hanging wire was seen upon arrival.
Outage | J.E.26.07.25145 | C001861941 | Raheem Ricketts | Manchester | Completed | Load_252793 | Spur Tree - 210 | Jul 22, 2026 10:28am | Jul 22, 2026 10:34am | Jul 22, 2026 10:38am | Jul 22, 2026 10:43am | Jul 22, 2026 11:23am | Jul 22, 2026 11:24am | Jul 22, 2026 11:26am | Jul 22, 2026 11:26am |  |  | Fair | No | Connect one leg of customer service wire at pole using 1,clamp
Non-Outage | J.E.26.07.05176 | C001861939 | Nickolas Rodriques | St.Catherine | Completed | Load_556350 | Rhodens Pen - 210 | Jul 22, 2026 10:27am | Jul 22, 2026 10:27am | Jul 22, 2026 10:44am | Jul 22, 2026 10:50am | Jul 22, 2026 11:43am | Jul 22, 2026 12:16pm | Jul 22, 2026 12:34pm | Jul 22, 2026 12:34pm | LowHangingWires |  | Fair | No | Customer confirmed that the issue was already resolved. Reading found (116-117-233)
Non-Outage | J.E.26.07.05301 | C001861940 | Richard Grant | St.Catherine | Completed | Load_268102 | New Michelton - 310 | Jul 22, 2026 10:27am | Jul 22, 2026 10:28am | Jul 22, 2026 11:47am | Jul 22, 2026 11:47am | Jul 22, 2026 12:26pm | Jul 22, 2026 12:38pm | Jul 22, 2026 12:38pm | Jul 22, 2026 12:38pm | LowHangingWires |  | Fair | No | Premises not found. Calls to customer goes straight to voicemail
Non-Outage | J.E.26.07.01303 | C001861938 | Richard Grant | St.Catherine | Completed | Load_245338 | New Michelton - 310 | Jul 22, 2026 10:26am | Jul 22, 2026 10:26am | Jul 22, 2026 11:20am | Jul 22, 2026 11:20am | Jul 22, 2026 11:43am | Jul 22, 2026 11:47am | Jul 22, 2026 11:47am | Jul 22, 2026 11:47am | LeaningPole |  | Fair | No | 30ft open secondary deadend pole found 100% rotten and leaning. Please send email to A Murray to have defective pole change.
Non-Outage | J.E.26.07.24797 | C001861937 | Andre Williams | null | Completed | null | null | Jul 22, 2026 10:26am | Jul 22, 2026 10:26am | Jul 22, 2026 11:16am | Jul 22, 2026 11:38am | Jul 22, 2026 12:35pm | Jul 22, 2026 12:42pm | Jul 22, 2026 12:42pm | Jul 22, 2026 12:42pm | Fire |  | Fair | No | Clean coroded clamp at pothead voltage 118+116=234
Outage | J.E.26.07.25143 | C001861929 | Kaydon Taylor | KSAN | Completed | Load_574807 | Washington Blvd - 610 | Jul 22, 2026 10:26am | Jul 22, 2026 10:31am | Jul 22, 2026 11:16am | Jul 22, 2026 11:16am | Jul 22, 2026 12:12pm | Jul 22, 2026 1:52pm | Jul 22, 2026 1:52pm | Jul 22, 2026 1:52pm |  |  | Fair | No | 15 amp junction found blown and replace at the intersection of wickham dr n grants dr. 25 amp junction fuse also found blown and replace on grants pen road.
Outage | J.E.26.07.25161 | C001861927 | Barrington Brown | St.James | Completed | Load_238595 | Bogue - 510 | Jul 22, 2026 10:25am | Jul 22, 2026 10:25am | Jul 22, 2026 1:55pm | Jul 22, 2026 1:56pm | Jul 22, 2026 2:36pm | Jul 22, 2026 2:56pm | Jul 22, 2026 2:56pm | Jul 22, 2026 2:56pm |  |  | Fair | No | Checked and found ok
Non-Outage | J.E.26.07.22956 | C001861922 | Richard Grant | St.Catherine | Completed | Load_267869 | New Michelton - 410 | Jul 22, 2026 10:23am | Jul 22, 2026 10:24am | Jul 22, 2026 11:49am | Jul 22, 2026 1:47pm | Jul 22, 2026 1:47pm | Jul 22, 2026 2:01pm | Jul 22, 2026 2:01pm | Jul 22, 2026 2:01pm | LeaningPole |  | Rains | No | Customer complaining about the placement of steel rail down guy at premises wall outlining perimeter by contractor for newly built line section. Kindly send email to A Murray or the necessary department to have steel rail relocated.
Outage | J.E.26.07.25157 | C001861920 | Neville Spencer | St.Catherine | Completed | Load_261578 | Rhodens Pen - 310 | Jul 22, 2026 10:21am | Jul 22, 2026 10:24am | Jul 22, 2026 10:48am | Jul 22, 2026 10:48am | Jul 22, 2026 11:09am | Jul 22, 2026 11:09am | Jul 22, 2026 11:10am | Jul 22, 2026 11:10am |  |  | Fair | No | Customer not located.
Non-Outage | J.E.26.07.25125 | C001861905 | Raymond Lewis | St.Ann | Completed | Load_269625 | Roaring River - 410 | Jul 22, 2026 10:16am | Jul 22, 2026 10:37am | Jul 22, 2026 11:00am | Jul 22, 2026 11:00am | Jul 22, 2026 11:56am | Jul 22, 2026 12:17pm | Jul 22, 2026 12:18pm | Jul 22, 2026 12:18pm | BrokenWire |  | SevereWind | No | Splice and retention 3 wire service
Outage | J.E.26.07.25126 | C001861903 | Evan Spaulding | St.Mary | Completed | Load_259689 | Annotto Bay - 310 | Jul 22, 2026 10:14am | Jul 22, 2026 11:35am | Jul 22, 2026 1:11pm | Jul 22, 2026 1:11pm | Jul 22, 2026 1:11pm | Jul 22, 2026 1:11pm | Jul 22, 2026 1:12pm | Jul 22, 2026 1:12pm |  |  | Fair | No | Associated call
Outage | J.E.26.07.25121 | C001861900 | Tyrese Williams | St.Ann | Completed | Load_270080 | Cardiff Hall - 310 | Jul 22, 2026 10:13am | Jul 22, 2026 10:13am | Jul 22, 2026 10:22am | Jul 22, 2026 12:32pm | Jul 22, 2026 12:45pm | Jul 22, 2026 1:17pm | Jul 22, 2026 1:18pm | Jul 22, 2026 1:18pm | Fire |  | Fair | No | Open a 25 kva transformer fuse to splice and retention 2 span of secondary neutral use 30 ft of #2AA and 1 pg clamp
Outage | J.E.26.07.25123 | C001861901 | Gregory Grossett | Portland | Completed | Load_242336 | Port Antonio - 410 | Jul 22, 2026 10:13am | Jul 22, 2026 2:13pm | Jul 22, 2026 4:02pm | Jul 22, 2026 5:08pm | Jul 22, 2026 5:50pm | Jul 22, 2026 6:48pm | Jul 22, 2026 6:53pm | Jul 22, 2026 6:53pm |  |  | Fair | No | 25kva transformer casing ground and neutral corroded open transformer fuse to make repairs then close transformer fuse to restore normal supply to the area.Material use 4 one bolt clamps area is now ok.
Non-Outage | J.E.26.07.24722 | C001861884 | Error Coore | Manchester | Completed | Load_295311 | Spur Tree - 310 | Jul 22, 2026 10:01am | Jul 22, 2026 10:01am | Jul 22, 2026 10:08am | Jul 22, 2026 10:08am | Jul 22, 2026 11:09am | Jul 22, 2026 12:10pm | Jul 22, 2026 12:14pm | Jul 22, 2026 12:14pm |  |  | Fair | No | Open a 25 KVA xformer to remade corroded drop lead remade corroded phase and neutral drop lead using 3 one bolt clamp voltage reading 118/118/236 volts
Outage | J.E.26.07.25120 | C001861868 | Javid Vernon | Westmoreland | Completed | Load_242110 | Paradise - 110 | Jul 22, 2026 9:55am | Jul 22, 2026 9:56am | Jul 22, 2026 11:01am | Jul 22, 2026 11:01am | Jul 22, 2026 11:32am | Jul 22, 2026 11:51am | Jul 22, 2026 11:51am | Jul 22, 2026 11:51am |  |  | Fair | No | Refuse one 8amp junction fuse
Outage | J.E.26.07.24056 | C001861867 | Dwain Samuels | Westmoreland | Completed | Load_265674 | Paradise - 310 | Jul 22, 2026 9:54am | Jul 22, 2026 9:55am | Jul 22, 2026 10:01am | Jul 22, 2026 10:21am | Jul 22, 2026 10:47am | Jul 22, 2026 11:14am | Jul 22, 2026 11:22am | Jul 22, 2026 11:22am |  |  | Fair | No | Connect 3 wire meter. Use 3 one bolt clamp 3 pen union clamp and 80ft #6 service wire
Non-Outage | J.E.26.07.18060 | C001861858 | Hopeton Henry | St.Thomas | Completed | Load_247908 | Good Year - 210 | Jul 22, 2026 9:50am | Jul 22, 2026 9:51am | Jul 22, 2026 10:23am | Jul 23, 2026 8:59am | Jul 23, 2026 9:05am | Jul 23, 2026 9:10am | Jul 23, 2026 9:12am | Jul 23, 2026 9:12am |  |  | Fair | No | Customer not located, several attempts made to contact customer
Non-Outage | J.E.26.07.18094 | C001861859 | Hopeton Henry | St.Thomas | Completed | Load_253956 | Good Year - 210 | Jul 22, 2026 9:50am | Jul 22, 2026 9:51am | Jul 22, 2026 10:23am | Jul 23, 2026 9:12am | Jul 23, 2026 9:39am | Jul 23, 2026 10:26am | Jul 23, 2026 10:27am | Jul 23, 2026 10:27am |  |  | Fair | No | Customer reporting defective street light , call customer for directions
Non-Outage | J.E.26.07.18398 | C001861857 | Hopeton Henry | St.Thomas | Completed | Load_245707 | Good Year - 210 | Jul 22, 2026 9:50am | Jul 22, 2026 9:51am | Jul 22, 2026 10:23am | Jul 23, 2026 12:19pm | Jul 23, 2026 12:20pm | Jul 23, 2026 12:20pm | Jul 23, 2026 12:21pm | Jul 23, 2026 12:21pm |  |  | Fair | No | Check and found ok 107-108-215 volts
Non-Outage | J.E.26.07.18684 | C001861856 | Hopeton Henry | St.Thomas | Completed | Load_247145 | Good Year - 110 | Jul 22, 2026 9:50am | Jul 22, 2026 9:51am | Jul 22, 2026 10:23am | Jul 22, 2026 3:13pm | Jul 22, 2026 3:13pm | Jul 22, 2026 3:17pm | Jul 22, 2026 3:18pm | Jul 22, 2026 3:18pm |  |  | Fair | No | Customer not located
Non-Outage | J.E.26.07.18697 | C001861854 | Hopeton Henry | St.Thomas | Completed | Load_261596 | Good Year - 210 | Jul 22, 2026 9:50am | Jul 22, 2026 9:51am | Jul 22, 2026 10:23am | Jul 23, 2026 1:46pm | Jul 23, 2026 1:47pm | Jul 23, 2026 2:32pm | Jul 23, 2026 2:34pm | Jul 23, 2026 2:34pm |  |  | Fair | No | Found corrosion at pole , use 1 clamp 110-111-222v
Non-Outage | J.E.26.07.19907 | C001861852 | Hopeton Henry | St.Thomas | Completed | Load_405682 | Lysson - 410 | Jul 22, 2026 9:50am | Jul 22, 2026 9:51am | Jul 22, 2026 10:23am | Jul 23, 2026 12:41pm | Jul 23, 2026 12:48pm | Jul 23, 2026 1:10pm | Jul 23, 2026 1:12pm | Jul 23, 2026 1:12pm |  |  | Fair | No | Use 3 connector 118-119-237 volts
Non-Outage | J.E.26.07.25136 | C001861848 | Hopeton Henry | St.Thomas | Completed | Load_240594 | Good Year - 210 | Jul 22, 2026 9:49am | Jul 22, 2026 9:51am | Jul 22, 2026 10:23am | Jul 23, 2026 2:35pm | Jul 23, 2026 2:54pm | Jul 23, 2026 3:38pm | Jul 23, 2026 3:39pm | Jul 23, 2026 3:39pm |  |  | Fair | Yes | Found corrosion at pole , use 6 connector 118-119-237 volts
Non-Outage | J.E.26.07.24983 | C001861845 | Hopeton Henry | St.Thomas | Completed | Load_577132 | Lysson - 410 | Jul 22, 2026 9:48am | Jul 22, 2026 9:51am | Jul 22, 2026 10:23am | Jul 23, 2026 12:24pm | Jul 23, 2026 12:24pm | Jul 23, 2026 12:40pm | Jul 23, 2026 12:41pm | Jul 23, 2026 12:41pm |  |  | Fair | No | Check and found ok
Outage | J.E.26.07.25101 | C001861844 | Rayon Foster | Hanover | Completed | Load_258239 | Orange Bay - 210 | Jul 22, 2026 9:46am | Jul 22, 2026 9:47am | Jul 22, 2026 2:34pm | Jul 22, 2026 2:34pm | Jul 22, 2026 2:34pm | Jul 22, 2026 2:36pm | Jul 22, 2026 2:36pm | Jul 22, 2026 2:36pm |  |  | Fair | No | Customer received back power after on internal issue was rectified
Non-Outage | J.E.26.07.15019 | C001861810 | Odeanie Davis | KSAS | Completed | Load_267551 | Cane River - 410 | Jul 22, 2026 9:30am | Jul 22, 2026 9:36am | Jul 22, 2026 1:27pm | Jul 22, 2026 2:45pm | Jul 22, 2026 2:45pm | Jul 22, 2026 3:36pm | Jul 23, 2026 8:15am | Jul 23, 2026 8:15am |  |  | Fair | No | 112v/0V at arrival, open circuit at secondary corrected, 3 one bolt clamps, 112v/110v after correction
Non-Outage | J.E.26.07.15151 | C001861808 | Odeanie Davis | KSAS | Completed | Load_249201 | Cane River - 310 | Jul 22, 2026 9:29am | Jul 22, 2026 9:36am | Jul 22, 2026 1:28pm | Jul 22, 2026 2:21pm | Jul 22, 2026 2:22pm | Jul 22, 2026 2:44pm | Jul 22, 2026 2:45pm | Jul 22, 2026 2:45pm |  |  | Fair | No | 119v/117v at location, customer stated that issue was resolved
Non-Outage | J.E.26.07.15295 | C001861807 | Odeanie Davis | KSAN | Completed | Load_244711 | Washington Blvd - 710 | Jul 22, 2026 9:29am | Jul 22, 2026 9:36am | Jul 23, 2026 8:19am | Jul 23, 2026 10:44am | Jul 23, 2026 10:44am | Jul 23, 2026 10:50am | Jul 23, 2026 10:44am | Jul 23, 2026 10:44am |  |  | Fair | No | Customer stated that issue was resolved by their electrician
Non-Outage | J.E.26.07.16390 | C001861803 | Fitzroy Turner | KSAS | Completed | Load_254610 | Cane River - 610 | Jul 22, 2026 9:27am | Jul 22, 2026 9:34am | Jul 22, 2026 12:57pm | Jul 22, 2026 12:58pm | Jul 22, 2026 1:21pm | Jul 22, 2026 1:21pm | Jul 22, 2026 1:23pm | Jul 22, 2026 1:23pm | LowHangingWires |  | Fair | No | Found #2 twisted secondary cut down splice and retention using 6 one bolt clamps and 5ft of #2 aluminum to carry out repair supply restored to areas
Non-Outage | J.E.26.07.16574 | C001861797 | Odeanie Davis | KSAS | Completed | Load_260269 | Up Park Camp - 510 | Jul 22, 2026 9:25am | Jul 22, 2026 9:36am | Jul 22, 2026 10:03am | Jul 22, 2026 10:53am | Jul 22, 2026 10:53am | Jul 22, 2026 11:01am | Jul 22, 2026 11:01am | Jul 22, 2026 11:01am |  |  | Fair | No | 117v/16v & 235v at location, customer stated that they are still having issues, transformer team needed, bucket truck needed.
Non-Outage | J.E.26.07.17057 | C001861795 | Rusean Allen | KSAS | Completed | Load_266530 | Hunts Bay - 310 | Jul 22, 2026 9:25am | Jul 22, 2026 9:33am | Jul 22, 2026 11:00am | Jul 22, 2026 11:00am | Jul 22, 2026 12:45pm | Jul 22, 2026 12:46pm | Jul 22, 2026 12:46pm | Jul 22, 2026 12:46pm |  |  | Fair | No | Corroded clamp found at pothead, clamp was changed.Voltage:116 116 232
Non-Outage | J.E.26.07.17401 | C001861794 | Odeanie Davis | KSAN | Completed | Load_573771 | Washington Blvd - 310 | Jul 22, 2026 9:25am | Jul 22, 2026 9:36am | Jul 23, 2026 8:18am | Jul 23, 2026 11:01am | Jul 23, 2026 11:06am | Jul 23, 2026 11:45am | Jul 23, 2026 11:41am | Jul 23, 2026 11:41am |  |  | Fair | No | 106v/107v at arrival, open circuit at secondary corrected, 3 one bolt clamps, 111v/110v & 222v after correction.
Non-Outage | J.E.26.07.18435 | C001861793 | Rusean Allen | KSAS | Completed | Load_262439 | Hunts Bay - 310 | Jul 22, 2026 9:25am | Jul 22, 2026 9:33am | Jul 22, 2026 1:18pm | Jul 22, 2026 1:18pm | Jul 22, 2026 1:21pm | Jul 22, 2026 1:21pm | Jul 22, 2026 1:22pm | Jul 22, 2026 1:22pm |  |  | Fair | No | Phone went unanswered
Non-Outage | J.E.26.07.24732 | C001861778 | Rayon Foster | Hanover | Completed | Load_264233 | Orange Bay - 310 | Jul 22, 2026 9:13am | Jul 22, 2026 9:13am | Jul 22, 2026 5:35pm | Jul 23, 2026 2:38pm | Jul 23, 2026 2:38pm | Jul 23, 2026 2:50pm | Jul 23, 2026 2:50pm | Jul 23, 2026 2:50pm |  |  | Fair | No | Voltage check at transformer pole on arrival 118/119/237 requesting for the circuit to be split into 2 separate circuits customer meter is in locking band voltage found at customer pothead 109v/110v/219v
Non-Outage | J.E.26.07.24840 | C001861776 | Tajay Bernard | null | Completed | null | null | Jul 22, 2026 9:12am | Jul 22, 2026 9:12am | Jul 22, 2026 9:31am | Jul 22, 2026 9:31am | Jul 22, 2026 9:33am | Jul 22, 2026 9:34am | Jul 22, 2026 9:34am | Jul 22, 2026 9:34am | LowHangingWires |  | Fair | No | This call belongs to st james
Non-Outage | J.E.26.07.19218 | C001861772 | Odeanie Davis | KSAS | Completed | Load_573491 | Duhaney - 410 | Jul 22, 2026 9:11am | Jul 22, 2026 9:23am | Jul 22, 2026 10:45am | Jul 22, 2026 11:10am | Jul 22, 2026 11:10am | Jul 22, 2026 11:15am | Jul 22, 2026 11:13am | Jul 22, 2026 11:13am |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.07.20335 | C001861771 | Odeanie Davis | KSAS | Completed | Load_260097 | Up Park Camp - 510 | Jul 22, 2026 9:11am | Jul 22, 2026 9:23am | Jul 23, 2026 8:19am | Jul 23, 2026 1:46pm | Jul 23, 2026 1:56pm | Jul 23, 2026 2:25pm | Jul 23, 2026 2:25pm | Jul 23, 2026 2:25pm |  |  | Fair | No | 120v/121v & 241v at location. Customer power found ok, no issues found at location.
Non-Outage | J.E.26.07.22457 | C001861774 | Rusean Allen | KSAS | Completed | Load_256911 | Hunts Bay - 510 | Jul 22, 2026 9:11am | Jul 22, 2026 9:13am | Jul 22, 2026 10:42am | Jul 22, 2026 10:42am | Jul 22, 2026 10:44am | Jul 22, 2026 10:47am | Jul 22, 2026 10:47am | Jul 22, 2026 10:47am |  |  | Fair | No | Defective 3wire meter found, meter needs to be changed refer to field service department.
Non-Outage | J.E.26.07.22490 | C001861773 | Rusean Allen | KSAS | Completed | Load_293995 | Hunts Bay - 510 | Jul 22, 2026 9:11am | Jul 22, 2026 9:15am | Jul 22, 2026 10:48am | Jul 22, 2026 10:48am | Jul 22, 2026 10:49am | Jul 22, 2026 10:49am | Jul 22, 2026 10:49am | Jul 22, 2026 10:49am |  |  | Fair | No | Premises okay
Non-Outage | J.E.26.07.24893 | C001861775 | Edward Royal | KSAS | Completed | Load_413074 | Hunts Bay - 710 | Jul 22, 2026 9:11am | Jul 22, 2026 9:16am | Jul 22, 2026 10:05am | Jul 22, 2026 10:05am | Jul 22, 2026 10:05am | Jul 22, 2026 10:11am | Jul 22, 2026 10:11am | Jul 22, 2026 10:11am |  |  | Fair | No | Contact customer by phone customer said the power was restored
Non-Outage | J.E.26.07.20399 | C001861763 | Odeanie Davis | KSAS | Completed | Load_242523 | Greenwich - 310 | Jul 22, 2026 9:10am | Jul 22, 2026 9:23am | Jul 23, 2026 8:18am | Jul 23, 2026 1:35pm | Jul 23, 2026 1:36pm | Jul 23, 2026 1:42pm | Jul 23, 2026 1:42pm | Jul 23, 2026 1:42pm |  |  | Fair | No | Open circuit at secondary corrected, 2 one bolt clamps, 112v/118v & 230v after correction, however customer stated that they are still having the same issue, technician request for the transformer to be checked, issue didn’t occur at the time of the visit
Non-Outage | J.E.26.07.20502 | C001861761 | Odeanie Davis | KSAS | Completed | Load_293369 | Hunts Bay - 810 | Jul 22, 2026 9:10am | Jul 22, 2026 9:23am | Jul 23, 2026 8:17am | Jul 23, 2026 8:59am | Jul 23, 2026 9:11am | Jul 23, 2026 9:41am | Jul 23, 2026 9:41am | Jul 23, 2026 9:41am |  |  | Fair | No | 117v/121v at location, phase test was done and found that no 240v across phases, meter not communicating, rammi team needed
Non-Outage | J.E.26.07.20741 | C001861760 | Odeanie Davis | KSAS | Completed | Load_269065 | Three Miles - 410 | Jul 22, 2026 9:10am | Jul 22, 2026 9:23am | Jul 23, 2026 8:17am | Jul 23, 2026 9:47am | Jul 23, 2026 9:47am | Jul 23, 2026 10:11am | Jul 23, 2026 10:11am | Jul 23, 2026 10:11am |  |  | Fair | No | 117v/118v at arrival, open neutral at pothead corrected, 117v/118v & 235v after correction, 1 bolt clamps.
Non-Outage | J.E.26.07.21183 | C001861759 | Odeanie Davis | KSAS | Completed | Load_256571 | Greenwich - 510 | Jul 22, 2026 9:10am | Jul 22, 2026 9:23am | Jul 23, 2026 8:16am | Jul 23, 2026 12:21pm | Jul 23, 2026 12:22pm | Jul 23, 2026 12:40pm | Jul 23, 2026 12:40pm | Jul 23, 2026 12:40pm |  |  | Fair | No | 122v/122v & 244v at location, meter seen burnt on load side, meter needs to changed, field service team needed.
Non-Outage | J.E.26.07.21284 | C001861758 | Odeanie Davis | KSAS | Completed | Load_267729 | Rockfort - 410 | Jul 22, 2026 9:10am | Jul 22, 2026 9:23am | Jul 22, 2026 11:03am | Jul 22, 2026 12:50pm | Jul 22, 2026 12:50pm | Jul 22, 2026 1:15pm | Jul 22, 2026 1:15pm | Jul 22, 2026 1:15pm |  |  | Fair | No | 102v/124v on secondary line from transformer. Emergency team needed
Non-Outage | J.E.26.07.21374 | C001861756 | Odeanie Davis | KSAS | Completed | Load_258681 | Three Miles - 410 | Jul 22, 2026 9:10am | Jul 22, 2026 9:17am | Jul 23, 2026 8:16am | Jul 23, 2026 10:26am | Jul 23, 2026 10:30am | Jul 23, 2026 10:41am | Jul 23, 2026 10:42am | Jul 23, 2026 10:42am |  |  | Fair | No | Power outage in the area
Non-Outage | J.E.26.07.21525 | C001861755 | Odeanie Davis | KSAS | Completed | Load_239845 | Rockfort - 410 | Jul 22, 2026 9:10am | Jul 22, 2026 9:17am | Jul 22, 2026 11:04am | Jul 22, 2026 11:58am | Jul 22, 2026 12:01pm | Jul 22, 2026 12:50pm | Jul 22, 2026 12:50pm | Jul 22, 2026 12:50pm |  |  | Fair | No | 109v at arrival, open circuit at pothead and secondary corrected, 3 one bolt clamps & 2 penn , 110v after correction .
Outage | J.E.26.07.25049 | C001861757 | Tajay Bernard | Hanover | Completed | Load_260136 | Orange Bay - 310 | Jul 22, 2026 9:10am | Jul 22, 2026 9:11am | Jul 22, 2026 10:38am | Jul 22, 2026 10:38am | Jul 22, 2026 10:38am | Jul 22, 2026 10:38am | Jul 22, 2026 10:38am | Jul 22, 2026 10:38am |  |  | Fair | No | Customer stated that power was restored
Non-Outage | J.E.26.07.21854 | C001861754 | Odeanie Davis | KSAS | Completed | Load_262444 | Hunts Bay - 310 | Jul 22, 2026 9:09am | Jul 22, 2026 9:17am | Jul 22, 2026 11:04am | Jul 22, 2026 11:37am | Jul 22, 2026 11:37am | Jul 22, 2026 11:49am | Jul 22, 2026 11:49am | Jul 22, 2026 11:49am |  |  | Fair | No | Fuse seen open, emergency team needed
Non-Outage | J.E.26.07.22625 | C001861751 | Odeanie Davis | KSAN | Completed | Load_249051 | Washington Blvd - 710 | Jul 22, 2026 9:09am | Jul 22, 2026 9:17am | Jul 23, 2026 8:15am | Jul 23, 2026 10:12am | Jul 23, 2026 10:14am | Jul 23, 2026 10:19am | Jul 23, 2026 10:15am | Jul 23, 2026 10:15am |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.07.23360 | C001861752 | Odeanie Davis | null | Completed | null | null | Jul 22, 2026 9:09am | Jul 22, 2026 9:17am | Jul 23, 2026 10:47am | Jul 23, 2026 10:47am | Jul 23, 2026 10:47am | Jul 23, 2026 10:59am | Jul 23, 2026 10:50am | Jul 23, 2026 10:50am |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.07.24298 | C001861749 | Odeanie Davis | KSAS | Completed | Load_251141 | Cane River - 410 | Jul 22, 2026 9:08am | Jul 22, 2026 9:17am | Jul 22, 2026 1:26pm | Jul 22, 2026 1:38pm | Jul 22, 2026 1:38pm | Jul 22, 2026 2:07pm | Jul 22, 2026 2:07pm | Jul 22, 2026 2:07pm |  |  | Fair | No | Meter found burnt on line side & needs to be replaced. 119v/118v & 237v at location, meter was reported to be changed
Non-Outage | J.E.26.07.24730 | C001861741 | Fitzroy Turner | KSAS | Completed | Load_244455 | Cane River - 610 | Jul 22, 2026 9:05am | Jul 22, 2026 9:06am | Jul 22, 2026 10:16am | Jul 22, 2026 11:20am | Jul 22, 2026 12:38pm | Jul 22, 2026 12:39pm | Jul 22, 2026 12:57pm | Jul 22, 2026 12:57pm |  |  | Fair | No | Found tree wire service phase and neutral corroded at meter pole use too one bolt clamps and 5tf aluminum to carry out repair supply restored to customer
Non-Outage | J.E.26.07.25046 | C001861740 | Milton Charlton | KSAS | Completed | Load_265242 | Three Miles - 410 | Jul 22, 2026 9:03am | Jul 22, 2026 9:05am | Jul 22, 2026 10:33am | Jul 22, 2026 10:34am | Jul 22, 2026 11:06am | Jul 22, 2026 11:15am | Jul 22, 2026 11:10am | Jul 22, 2026 11:10am | Fire |  | Fair | No | Customer feeding fromHexing box #01074 at pole 501299 are without supply. Hexing box#01074 caught fire. Approximately 15 customers are without supply. Need immediate attention.
Non-Outage | J.E.26.07.24438 | C001861739 | Rayon Foster | null | Completed | null | null | Jul 22, 2026 9:02am | Jul 22, 2026 9:12am | Jul 22, 2026 2:26pm | Jul 22, 2026 2:44pm | Jul 22, 2026 2:44pm | Jul 22, 2026 2:49pm | Jul 22, 2026 2:49pm | Jul 22, 2026 2:49pm |  |  | Fair | No | Unable to reach on cell phone no meter number no driving details but when reach out to JPS customers care he said the meter was active and connected
Outage | J.E.26.07.25081 | C001861736 | Wan Carlos Scarlett | St.Catherine | Completed | Load_255400 | Twickenham - 210 | Jul 22, 2026 8:59am | Jul 22, 2026 11:58am | Jul 22, 2026 12:46pm | Jul 22, 2026 12:47pm | Jul 22, 2026 1:23pm | Jul 22, 2026 1:55pm | Jul 22, 2026 2:01pm | Jul 22, 2026 2:01pm |  |  | Rains | No | Found customer with internal problem pothead wire to meter socket found defective readings from pothead service wire 112-112-225.isolate 3 wire service at pothead
Non-Outage | J.E.26.07.24926 | C001861726 | Neville Spencer | null | Completed | null | null | Jul 22, 2026 8:53am | Jul 22, 2026 8:54am | Jul 22, 2026 10:18am | Jul 22, 2026 10:18am | Jul 22, 2026 10:36am | Jul 22, 2026 10:36am | Jul 22, 2026 10:37am | Jul 22, 2026 10:37am | Fire |  | Fair | No | Found supply in area .
Outage | J.E.26.07.25076 | C001861728 | Devon Grant | KSAN | Completed | Load_244170 | Constant Spring - 310 | Jul 22, 2026 8:53am | Jul 22, 2026 10:25am | Jul 22, 2026 12:50pm | Jul 22, 2026 12:59pm | Jul 22, 2026 12:59pm | Jul 22, 2026 12:59pm | Jul 22, 2026 1:00pm | Jul 22, 2026 1:00pm | Fire |  | Fair | No | Premises found ok
Non-Outage | J.E.26.07.19844 | C001861724 | Raymond Lewis | St.Ann | Completed | Load_264030 | Roaring River - 410 | Jul 22, 2026 8:52am | Jul 22, 2026 8:52am | Jul 22, 2026 12:19pm | Jul 22, 2026 12:19pm | Jul 22, 2026 12:31pm | Jul 22, 2026 1:33pm | Jul 22, 2026 1:33pm | Jul 22, 2026 1:33pm |  |  | Fair | No | Change 50 ft #6 service wire
Outage | J.E.26.07.25033 | C001861720 | Neville Spencer | Clarendon | Completed | Load_252801 | Parnassus - 210 | Jul 22, 2026 8:46am | Jul 22, 2026 8:47am | Jul 22, 2026 10:37am | Jul 22, 2026 10:37am | Jul 22, 2026 10:37am | Jul 22, 2026 10:38am | Jul 22, 2026 10:39am | Jul 22, 2026 10:39am |  |  | Fair | No | Renew blown 20 amp j/ fuse at pole # 055817 area restored.
Non-Outage | J.E.26.07.24515 | C001861713 | Christopher Edwards | KSAN | Completed | Load_265865 | Washington Blvd - 810 | Jul 22, 2026 8:44am | Jul 22, 2026 8:44am | Jul 22, 2026 8:58am | Jul 22, 2026 8:58am | Jul 22, 2026 8:58am | Jul 22, 2026 9:23am | Jul 22, 2026 9:23am | Jul 22, 2026 9:23am |  |  | Fair | No | Refuse blown junction fuse Using (1) 20 amps
Outage | J.E.26.07.25048 | C001861712 | Tyrese Williams | St.Ann | Completed | Load_573918 | Cardiff Hall - 310 | Jul 22, 2026 8:43am | Jul 22, 2026 8:43am | Jul 22, 2026 8:58am | Jul 22, 2026 10:18am | Jul 22, 2026 10:20am | Jul 22, 2026 10:20am | Jul 22, 2026 10:20am | Jul 22, 2026 10:20am |  |  | Fair | No | Replace a 20 amp junction fuse at pole
Outage | J.E.26.07.25057 | C001861711 | Tyrese Williams | St.Ann | Completed | Load_573919 | Cardiff Hall - 310 | Jul 22, 2026 8:43am | Jul 22, 2026 8:43am | Jul 22, 2026 8:58am | Jul 22, 2026 9:47am | Jul 22, 2026 9:47am | Jul 22, 2026 10:18am | Jul 22, 2026 10:18am | Jul 22, 2026 10:18am |  |  | Fair | No | Replace a 20 amp junction fuse at pole
Outage | J.E.26.07.25047 | C001861710 | Tyrese Williams | St.Ann | Completed | Load_251763 | Cardiff Hall - 310 | Jul 22, 2026 8:42am | Jul 22, 2026 8:43am | Jul 22, 2026 11:10am | Jul 22, 2026 2:51pm | Jul 22, 2026 2:51pm | Jul 22, 2026 2:52pm | Jul 22, 2026 2:52pm | Jul 22, 2026 2:52pm | Fire |  | Fair | No | Premises Found ok call related to banning secondary line
Outage | J.E.26.07.25042 | C001861704 | Wan Carlos Scarlett | Portmore | Completed | Load_576151 | Naggo Head - 610 | Jul 22, 2026 8:38am | Jul 22, 2026 8:39am | Jul 22, 2026 10:32am | Jul 22, 2026 10:46am | Jul 22, 2026 10:46am | Jul 22, 2026 10:46am | Jul 22, 2026 10:47am | Jul 22, 2026 10:47am |  |  | Fair | No | Call related customer confirm that power supply has been restored
Non-Outage | J.E.26.07.24432 | C001861703 | Rusean Allen | KSAS | Completed | Load_293995 | Hunts Bay - 510 | Jul 22, 2026 8:37am | Jul 22, 2026 8:39am | Jul 22, 2026 10:50am | Jul 22, 2026 10:50am | Jul 22, 2026 10:50am | Jul 22, 2026 10:56am | Jul 22, 2026 10:57am | Jul 22, 2026 10:57am |  |  | Fair | No | Defective 3w meter found, one side of meter socket burnt causing to be having single phasing. Meter needs to be changed refer to field service department.
Non-Outage | J.E.26.07.15699 | C001861701 | Orville Lee | St.Catherine | Completed | Load_267039 | Twickenham - 210 | Jul 22, 2026 8:36am | Jul 22, 2026 8:43am | Jul 22, 2026 10:20am | Jul 22, 2026 1:00pm | Jul 22, 2026 1:50pm | Jul 22, 2026 2:18pm | Jul 22, 2026 2:18pm | Jul 22, 2026 2:18pm |  |  | Fair | No | Multiple joints seen on open secondary line Voltage104v119vVoltage at droplead 114v115v229vBucket truck required
Non-Outage | J.E.26.07.15788 | C001861699 | Orville Lee | St.Catherine | Completed | Load_260875 | Twickenham - 210 | Jul 22, 2026 8:36am | Jul 22, 2026 8:38am | Jul 22, 2026 10:20am | Jul 22, 2026 10:20am | Jul 22, 2026 10:54am | Jul 22, 2026 10:55am | Jul 22, 2026 11:01am | Jul 22, 2026 11:01am |  |  | Fair | No | Premises found k upon arival116v117v234v
Non-Outage | J.E.26.07.16396 | C001861698 | Orville Lee | St.Catherine | Completed | Load_248359 | Twickenham - 210 | Jul 22, 2026 8:36am | Jul 22, 2026 8:38am | Jul 22, 2026 10:20am | Jul 22, 2026 11:54am | Jul 22, 2026 12:19pm | Jul 22, 2026 12:41pm | Jul 22, 2026 12:43pm | Jul 22, 2026 12:43pm |  |  | Fair | No | Premise found ok upon arrival Voltage 117V118V237VDefective meter was changed by a technician
Non-Outage | J.E.26.07.16520 | C001861697 | Orville Lee | St.Catherine | Completed | Load_247555 | Twickenham - 210 | Jul 22, 2026 8:36am | Jul 22, 2026 8:38am | Jul 22, 2026 10:20am | Jul 22, 2026 11:12am | Jul 22, 2026 11:12am | Jul 22, 2026 11:14am | Jul 22, 2026 11:16am | Jul 22, 2026 11:16am |  |  | Fair | No | Premises closed Customer was told to make a report when available
Non-Outage | J.E.26.07.25015 | C001861700 | Orville Lee | St.Catherine | Completed | Load_266052 | Twickenham - 210 | Jul 22, 2026 8:36am | Jul 22, 2026 8:38am | Jul 22, 2026 10:20am | Jul 22, 2026 4:12pm | Jul 22, 2026 4:12pm | Jul 22, 2026 4:12pm | Jul 22, 2026 4:14pm | Jul 22, 2026 4:14pm |  |  | Fair | No | Checks made and found pothead and secondary line corroded Four 1bolt clamps usedVoltage116v117v233v
Non-Outage | J.E.26.07.25015 | C001861702 | Orville Lee | St.Catherine | Completed | Load_266052 | Twickenham - 210 | Jul 22, 2026 8:36am | Jul 22, 2026 8:43am | Jul 22, 2026 10:20am | Jul 22, 2026 3:02pm | Jul 22, 2026 3:34pm | Jul 22, 2026 4:03pm | Jul 22, 2026 4:11pm | Jul 22, 2026 4:11pm |  |  | Fair | No | Checks made and found pothead and secondary line corroded Four 1bolt clamps usedVoltage116v117v233v
Outage | J.E.26.07.25029 | C001861696 | Richard Nicholas | St.Catherine | Completed | Load_269784 | Tredegar - 510 | Jul 22, 2026 8:36am | Jul 22, 2026 8:37am | Jul 22, 2026 1:01pm | Jul 22, 2026 1:01pm | Jul 22, 2026 1:43pm | Jul 22, 2026 2:46pm | Jul 22, 2026 2:49pm | Jul 22, 2026 2:49pm |  |  | Fair | No | Replaced blown P.T 2amp fuse on pole #0076989 and remade slack 25kva transformer phase and neutral drop lead joint on pole #0101762.voltage reading 116x 2 and 232v.5 clamp was used to completed the repair.
Non-Outage | J.E.26.07.16903 | C001861695 | Orville Lee | St.Catherine | Completed | Load_266814 | Twickenham - 210 | Jul 22, 2026 8:35am | Jul 22, 2026 8:38am | Jul 22, 2026 9:14am | Jul 22, 2026 9:14am | Jul 22, 2026 9:53am | Jul 22, 2026 10:18am | Jul 22, 2026 10:19am | Jul 22, 2026 10:19am |  |  | Fair | No | Two one bolt clamps where changed at secondary 119v
Non-Outage | J.E.26.07.17127 | C001861694 | Orville Lee | St.Catherine | Completed | Load_263069 | Twickenham - 210 | Jul 22, 2026 8:35am | Jul 22, 2026 8:38am | Jul 22, 2026 10:20am | Jul 22, 2026 2:19pm | Jul 22, 2026 2:28pm | Jul 22, 2026 2:57pm | Jul 22, 2026 2:58pm | Jul 22, 2026 2:58pm |  |  | Fair | No | Checks made and found defective service wire80ft service wire and four one bolt clamps usedVoltage 117v
Non-Outage | J.E.26.07.19859 | C001861690 | Orville Lee | St.Catherine | Completed | Load_238982 | Twickenham - 210 | Jul 22, 2026 8:35am | Jul 23, 2026 8:21am | Jul 23, 2026 10:00am | Jul 23, 2026 1:55pm | Jul 23, 2026 2:47pm | Jul 23, 2026 3:21pm | Jul 23, 2026 3:23pm | Jul 23, 2026 3:23pm |  |  | Fair | No | Checks made and found secondary connection Corroded Voltage119v
Non-Outage | J.E.26.07.25015 | C001861689 | Orville Lee | St.Catherine | Completed | Load_266052 | Twickenham - 210 | Jul 22, 2026 8:34am | Jul 22, 2026 8:38am | Jul 22, 2026 10:20am | Jul 22, 2026 4:11pm | Jul 22, 2026 4:11pm | Jul 22, 2026 4:11pm | Jul 22, 2026 4:12pm | Jul 22, 2026 4:12pm |  |  | Fair | No | Checks made and found pothead and secondary line corroded Four 1bolt clamps usedVoltage116v117v233v
Non-Outage | J.E.26.07.25061 | C001861688 | Fitzroy Turner | null | Completed | null | null | Jul 22, 2026 8:33am | Jul 22, 2026 8:45am | Jul 22, 2026 9:24am | Jul 22, 2026 9:24am | Jul 22, 2026 9:44am | Jul 22, 2026 10:14am | Jul 22, 2026 10:15am | Jul 22, 2026 10:15am | Fire |  | Fair | No | Found 4 wires meter socket burnt up.transformer isolate and customer advised
Non-Outage | J.E.26.07.25054 | C001861686 | Odaine Johnson | Clarendon | Completed | Load_248180 | Monymusk - 210 | Jul 22, 2026 8:31am | Jul 22, 2026 8:32am | Jul 22, 2026 10:13am | Jul 22, 2026 10:15am | Jul 22, 2026 10:21am | Jul 22, 2026 10:21am | Jul 22, 2026 10:22am | Jul 22, 2026 10:22am |  |  | Fair | No | Premises was found working ok voltage reading is A115 B116 AB231
Outage | J.E.26.07.25058 | C001861687 | Ryan Richards | Manchester | Completed | Load_292650 | Spur Tree - 210 | Jul 22, 2026 8:31am | Jul 22, 2026 8:38am | Jul 22, 2026 9:19am | Jul 22, 2026 9:19am | Jul 22, 2026 10:07am | Jul 22, 2026 10:49am | Jul 22, 2026 10:49am | Jul 22, 2026 10:49am |  |  | Fair | No | Blown 20&30 amp junction fuse found line patrol nothing found blown fuse replaced and all customers are now with supply
Non-Outage | J.E.26.06.36887 | C001861682 | Nicholas Dillon | St.Elizabeth | Completed | Load_302999 | Maggotty - 110 | Jul 22, 2026 8:29am | Jul 22, 2026 8:29am | Jul 22, 2026 4:17pm | Jul 22, 2026 4:17pm | Jul 22, 2026 4:37pm | Jul 22, 2026 4:37pm | Jul 22, 2026 4:38pm | Jul 22, 2026 4:38pm |  |  | Fair | Yes | Check and found corrosion at pothead clean joint and use 2 pen union before I left voltage is 119 120 phase to phase 240
Non-Outage | J.E.26.07.25021 | C001861680 | Tyrese Williams | St.Ann | Completed | Load_251763 | Cardiff Hall - 310 | Jul 22, 2026 8:26am | Jul 22, 2026 8:26am | Jul 22, 2026 11:10am | Jul 22, 2026 1:19pm | Jul 22, 2026 2:40pm | Jul 22, 2026 2:41pm | Jul 22, 2026 2:43pm | Jul 22, 2026 2:43pm | BangingWires |  | Fair | No | Open a 25 kva transformer fuse to retention 2 span of secondary phase
Non-Outage | J.E.26.07.22943 | C001861674 | Collin Robinson | Portland | Completed | Load_351431 | Port Antonio - 410 | Jul 22, 2026 8:24am | Jul 22, 2026 3:15pm | Jul 22, 2026 3:39pm | Jul 22, 2026 3:39pm | Jul 22, 2026 4:22pm | Jul 22, 2026 4:37pm | Jul 22, 2026 4:37pm | Jul 22, 2026 4:37pm |  |  | Fair | No | Change burn fuse barrel and replace 3 amps Voltage reading 120v 120v 240v
Non-Outage | J.E.26.07.25041 | C001861673 | Andrae Clarke | Portland | Completed | Load_242336 | Port Antonio - 410 | Jul 22, 2026 8:23am | Jul 22, 2026 8:23am | Jul 22, 2026 8:41am | Jul 22, 2026 8:41am | Jul 22, 2026 10:07am | Jul 22, 2026 10:00am | Jul 22, 2026 10:20am | Jul 22, 2026 10:20am |  |  | Fair | No | Check voltage 115Lead from transformer to secondary line needs to be cleaned corroded Emergency crew requires Transformer pole number 0014831
Non-Outage | J.E.26.07.24537 | C001861672 | Andrae Clarke | Portland | Completed | Load_238655 | Port Antonio - 310 | Jul 22, 2026 8:22am | Jul 22, 2026 8:22am | Jul 22, 2026 10:20am | Jul 22, 2026 10:20am | Jul 22, 2026 11:23am | Jul 22, 2026 10:22am | Jul 22, 2026 11:25am | Jul 22, 2026 11:25am |  |  | Fair | No | Premises found okay Check voltage 117/119/236
Outage | J.E.26.07.24661 | C001861670 | Collin Robinson | Portland | Completed | Load_243555 | Port Antonio - 410 | Jul 22, 2026 8:21am | Jul 22, 2026 8:21am | Jul 22, 2026 9:07am | Jul 22, 2026 9:07am | Jul 22, 2026 11:50am | Jul 22, 2026 12:14pm | Jul 22, 2026 12:14pm | Jul 22, 2026 12:14pm |  |  | Fair | No | Change corroded #2 splicing sleeve voltage 113 114 227v
Outage | J.E.26.07.24958 | C001861667 | Hartley Chin | Clarendon | Completed | Load_237880 | May Pen - 110 | Jul 22, 2026 8:19am | Jul 22, 2026 8:20am | Jul 22, 2026 12:57pm | Jul 22, 2026 12:57pm | Jul 22, 2026 12:57pm | Jul 22, 2026 12:57pm | Jul 22, 2026 12:58pm | Jul 22, 2026 12:58pm |  |  | Fair | No | CAll related to job 24776
Non-Outage | J.E.26.07.11597 | C001861665 | Junior Scarlett | St.James | Completed | Load_237885 | Queens Drive - 710 | Jul 22, 2026 8:17am | Jul 22, 2026 8:17am | Jul 22, 2026 9:26am | Jul 22, 2026 9:41am | Jul 22, 2026 9:54am | Jul 22, 2026 10:31am | Jul 22, 2026 10:32am | Jul 22, 2026 10:32am |  |  | Fair | No | Check and found okVoltage found 115v 115v 230v Customer suggested that her remote gate is damaged doing the island blockout so she need compensation for the damage
Non-Outage | J.E.26.07.12837 | C001861664 | Junior Scarlett | St.James | Completed | Load_251499 | Queens Drive - 710 | Jul 22, 2026 8:17am | Jul 22, 2026 8:17am | Jul 22, 2026 9:26am | Jul 22, 2026 10:47am | Jul 22, 2026 11:26am | Jul 22, 2026 12:36pm | Jul 22, 2026 12:37pm | Jul 22, 2026 12:37pm |  |  | Fair | No | Install two clampVoltage found 115v 114v 229vVoltage found 115v 114v 229v
Non-Outage | J.E.26.07.22117 | C001861659 | Odaine Johnson | null | Completed | null | null | Jul 22, 2026 8:15am | Jul 22, 2026 8:32am | Jul 22, 2026 10:13am | Jul 22, 2026 12:16pm | Jul 22, 2026 12:16pm | Jul 22, 2026 12:22pm | Jul 22, 2026 12:23pm | Jul 22, 2026 12:23pm |  |  | Fair | No | Premises found okay customer said power was restored
Non-Outage | J.E.26.07.24206 | C001861660 | Odaine Johnson | Clarendon | Completed | Load_266996 | Monymusk - 210 | Jul 22, 2026 8:15am | Jul 22, 2026 8:32am | Jul 22, 2026 10:13am | Jul 22, 2026 11:23am | Jul 22, 2026 12:12pm | Jul 22, 2026 12:14pm | Jul 22, 2026 12:15pm | Jul 22, 2026 12:15pm |  |  | Fair | No | Corroded phase found at pole remade connection using 1 one bolt clamp voltage reading 117/115/232 volts
Non-Outage | J.E.26.07.24572 | C001861661 | Odaine Johnson | Clarendon | Completed | Load_350768 | May Pen - 110 | Jul 22, 2026 8:15am | Jul 22, 2026 8:32am | Jul 22, 2026 10:13am | Jul 22, 2026 1:07pm | Jul 23, 2026 9:45am | Jul 23, 2026 9:45am | Jul 23, 2026 9:45am | Jul 23, 2026 9:45am |  |  | Fair | No | Premises found okay
Non-Outage | J.E.26.07.24939 | C001861662 | Odaine Johnson | Clarendon | Completed | Load_251131 | Parnassus - 210 | Jul 22, 2026 8:15am | Jul 22, 2026 8:32am | Jul 22, 2026 10:13am | Jul 22, 2026 1:00pm | Jul 22, 2026 1:05pm | Jul 22, 2026 1:06pm | Jul 22, 2026 1:07pm | Jul 22, 2026 1:07pm |  |  | Fair | No | Premises found okay customer said problem was resolved
Outage | J.E.26.07.24905 | C001861663 | Neville Spencer | Clarendon | Completed | Load_568340 | May Pen - 110 | Jul 22, 2026 8:15am | Jul 22, 2026 8:23am | Jul 22, 2026 11:11am | Jul 22, 2026 11:11am | Jul 22, 2026 11:14am | Jul 22, 2026 11:15am | Jul 22, 2026 11:16am | Jul 22, 2026 11:16am |  |  | Fair | No | Found supply in area .
Outage | J.E.26.07.24919 | C001861657 | Hartley Chin | Clarendon | Completed | Load_262567 | May Pen - 110 | Jul 22, 2026 8:14am | Jul 22, 2026 8:15am | Jul 22, 2026 12:56pm | Jul 22, 2026 12:56pm | Jul 22, 2026 12:56pm | Jul 22, 2026 12:56pm | Jul 22, 2026 12:57pm | Jul 22, 2026 12:57pm |  |  | Fair | No | Un able to contact customer
Outage | J.E.26.07.24924 | C001861658 | Hartley Chin | Clarendon | Completed | Load_240504 | May Pen - 110 | Jul 22, 2026 8:14am | Jul 22, 2026 8:15am | Jul 22, 2026 8:26am | Jul 22, 2026 8:26am | Jul 22, 2026 8:26am | Jul 22, 2026 8:26am | Jul 22, 2026 8:26am | Jul 22, 2026 8:26am |  |  | Fair | No | Found ok customer states power was restored
Non-Outage | J.E.26.07.23680 | C001861654 | Roemello Brown | Trelawny | Completed | Load_269251 | Martha Brae - 210 | Jul 22, 2026 8:13am | Jul 22, 2026 8:13am | Jul 22, 2026 10:22am | Jul 22, 2026 10:22am | Jul 22, 2026 10:55am | Jul 22, 2026 10:55am | Jul 22, 2026 11:06am | Jul 22, 2026 11:06am |  |  | Fair | No | Premises check premises found working okay Voltage found 117/116/233Voltage leave 117/116/233
Non-Outage | J.E.26.07.24588 | C001861655 | Floyd Taylor | Trelawny | Completed | Load_291988 | Greenwood - 210 | Jul 22, 2026 8:13am | Jul 22, 2026 9:03am | Jul 22, 2026 12:04pm | Jul 22, 2026 12:04pm | Jul 22, 2026 12:27pm | Jul 22, 2026 1:23pm | Jul 22, 2026 1:31pm | Jul 22, 2026 1:31pm |  |  | Fair | No | Splice and retention customer service wire using 2 penunion, voltage reading left 111,112, 223
Non-Outage | J.E.26.07.25035 | C001861656 | Christopher Edwards | KSAN | Completed | Load_248491 | Constant Spring - 410 | Jul 22, 2026 8:13am | Jul 22, 2026 8:14am | Jul 22, 2026 9:24am | Jul 22, 2026 9:24am | Jul 22, 2026 10:16am | Jul 22, 2026 11:16am | Jul 22, 2026 11:17am | Jul 22, 2026 11:17am | BrokenWire |  | Fair | No | Splice and retention broken #6 service wire Using:40ft #6 service wire (3 one bolt clamps
Non-Outage | J.E.26.07.23976 | C001861653 | Roemello Brown | Trelawny | Completed | Load_555893 | Martha Brae - 210 | Jul 22, 2026 8:12am | Jul 22, 2026 8:13am | Jul 22, 2026 11:52am | Jul 22, 2026 11:52am | Jul 22, 2026 12:01pm | Jul 22, 2026 12:01pm | Jul 22, 2026 12:08pm | Jul 22, 2026 12:08pm |  |  | Fair | No | Have premises check premises found working okay Voltage found 114/115/229Voltage leave 114/115/229
Non-Outage | J.E.26.07.24148 | C001861652 | Roemello Brown | Trelawny | Completed | Load_251614 | Martha Brae - 210 | Jul 22, 2026 8:12am | Jul 22, 2026 8:13am | Jul 22, 2026 9:28am | Jul 22, 2026 9:59am | Jul 22, 2026 10:14am | Jul 22, 2026 10:14am | Jul 22, 2026 10:16am | Jul 22, 2026 10:16am |  |  | Fair | No | Premises check premises found working okay Voltage found 116/116/232Voltage leave 116/116/ 232
Non-Outage | J.E.26.07.24156 | C001861650 | Roemello Brown | Trelawny | Completed | Load_257206 | Martha Brae - 210 | Jul 22, 2026 8:12am | Jul 22, 2026 8:13am | Jul 22, 2026 10:17am | Jul 22, 2026 1:37pm | Jul 22, 2026 2:06pm | Jul 22, 2026 2:07pm | Jul 22, 2026 2:08pm | Jul 22, 2026 2:08pm |  |  | Fair | No | Premises check premises found working okay Voltage found 116/117/233Voltage leave 117/116/233
Non-Outage | J.E.26.07.24285 | C001861651 | Roemello Brown | Trelawny | Completed | Load_249135 | Martha Brae - 210 | Jul 22, 2026 8:12am | Jul 22, 2026 8:13am | Jul 22, 2026 11:16am | Jul 22, 2026 11:16am | Jul 22, 2026 11:40am | Jul 22, 2026 11:40am | Jul 22, 2026 11:51am | Jul 22, 2026 11:51am |  |  | Fair | No | Meter burn needs field service team to have meter change please Voltage found 113/114/228Voltage leave 113/114/228
Non-Outage | J.E.26.07.24475 | C001861649 | Roemello Brown | Trelawny | Completed | Load_1001477 | Martha Brae - 210 | Jul 22, 2026 8:12am | Jul 22, 2026 8:13am | Jul 22, 2026 9:24am | Jul 22, 2026 1:06pm | Jul 22, 2026 1:17pm | Jul 22, 2026 1:17pm | Jul 22, 2026 1:37pm | Jul 22, 2026 1:37pm |  |  | Fair | No | Corrosion at the pothead have linkets installed at pothead Voltage found 115/119/234Voltage leave 117/117/234
Non-Outage | J.E.26.02.39217 | C001861636 | Dwain Samuels | Westmoreland | Completed | Load_261697 | Paradise - 310 | Jul 22, 2026 8:11am | Jul 22, 2026 8:11am | Jul 22, 2026 9:13am | Jul 22, 2026 12:41pm | Jul 22, 2026 12:41pm | Jul 22, 2026 12:41pm | Jul 22, 2026 12:41pm | Jul 22, 2026 12:41pm |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.03.31191 | C001861635 | Dwain Samuels | Westmoreland | Completed | Load_268740 | Paradise - 310 | Jul 22, 2026 8:11am | Jul 22, 2026 8:11am | Jul 22, 2026 9:13am | Jul 22, 2026 11:24am | Jul 22, 2026 11:24am | Jul 22, 2026 11:24am | Jul 22, 2026 11:25am | Jul 22, 2026 11:25am |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.07.15993 | C001861641 | Andrae Dawkins | St.James | Completed | Load_254221 | Queens Drive - 710 | Jul 22, 2026 8:11am | Jul 22, 2026 8:12am | Jul 22, 2026 2:56pm | Jul 23, 2026 10:56am | Jul 23, 2026 11:08am | Jul 23, 2026 11:37am | Jul 23, 2026 11:42am | Jul 23, 2026 11:42am |  |  | Fair | No | Found one leg of customer service wire burnt at pole due to slack connection cleaned and remade joints used one pg clamp voltage left 115/116/231
Non-Outage | J.E.26.07.16105 | C001861639 | Andrae Dawkins | St.James | Completed | Load_247836 | Queens Drive - 710 | Jul 22, 2026 8:11am | Jul 22, 2026 8:12am | Jul 22, 2026 8:40am | Jul 22, 2026 12:40pm | Jul 22, 2026 1:58pm | Jul 22, 2026 2:23pm | Jul 22, 2026 2:24pm | Jul 22, 2026 2:24pm |  |  | Fair | No | Found multiple customers experiencing low voltage due to slack neural wire cleaned and remade joints used one pg clamp voltage left 110/112/222 customer also requested her meter to be relocated
Non-Outage | J.E.26.07.17357 | C001861642 | Andrae Dawkins | St.James | Completed | Load_250208 | Queens Drive - 710 | Jul 22, 2026 8:11am | Jul 22, 2026 8:12am | Jul 22, 2026 8:40am | Jul 22, 2026 11:36am | Jul 22, 2026 11:39am | Jul 22, 2026 12:30pm | Jul 22, 2026 12:34pm | Jul 22, 2026 12:34pm |  |  | Fair | No | Found customer single phasing due to service wire connected parallel reconnected customer service wire properly voltage left 108/111/221
Non-Outage | J.E.26.07.17365 | C001861644 | Andrae Dawkins | St.James | Completed | Load_245808 | Queens Drive - 710 | Jul 22, 2026 8:11am | Jul 22, 2026 8:12am | Jul 22, 2026 2:56pm | Jul 22, 2026 5:10pm | Jul 22, 2026 5:11pm | Jul 22, 2026 3:19pm | Jul 22, 2026 5:12pm | Jul 22, 2026 5:12pm |  |  | Fair | No | Unable to locate customer unable to reach customer mobile
Non-Outage | J.E.26.07.17443 | C001861648 | Andrae Dawkins | St.James | Completed | Load_247367 | Queens Drive - 710 | Jul 22, 2026 8:11am | Jul 22, 2026 8:13am | Jul 22, 2026 8:41am | Jul 22, 2026 10:23am | Jul 22, 2026 11:18am | Jul 22, 2026 10:53am | Jul 22, 2026 11:30am | Jul 22, 2026 11:30am |  |  | Fair | No | Check and found ok voltage found 115/116/232
Non-Outage | J.E.26.07.17777 | C001861646 | Andrae Dawkins | St.James | Completed | Load_269689 | Queens Drive - 710 | Jul 22, 2026 8:11am | Jul 22, 2026 8:13am | Jul 22, 2026 2:27pm | Jul 22, 2026 2:48pm | Jul 22, 2026 2:49pm | Jul 22, 2026 2:45pm | Jul 22, 2026 2:53pm | Jul 22, 2026 2:53pm |  |  | Fair | No | Cannot locate customer unable to reach customer mobile phone
Non-Outage | J.E.26.07.24764 | C001861634 | Dwain Samuels | Westmoreland | Completed | Load_263447 | Paradise - 310 | Jul 22, 2026 8:10am | Jul 22, 2026 8:11am | Jul 22, 2026 9:13am | Jul 23, 2026 2:14pm | Jul 23, 2026 2:49pm | Jul 23, 2026 3:08pm | Jul 23, 2026 3:11pm | Jul 23, 2026 3:11pm |  |  | Fair | No | Found working okay. Voltage check 114-115-229. Customer has internal problems
Outage | J.E.26.07.24362 | C001861633 | Hartley Chin | Clarendon | Completed | Load_267628 | May Pen - 110 | Jul 22, 2026 8:10am | Jul 22, 2026 8:11am | Jul 22, 2026 12:55pm | Jul 22, 2026 12:55pm | Jul 22, 2026 12:55pm | Jul 22, 2026 12:55pm | Jul 22, 2026 12:56pm | Jul 22, 2026 12:56pm |  |  | Fair | No | Call related to job 24776
Non-Outage | J.E.26.07.24434 | C001861631 | Romeo Brissett | null | Completed | null | null | Jul 22, 2026 8:06am | Jul 22, 2026 8:08am | Jul 22, 2026 11:21am | Jul 22, 2026 11:21am | Jul 22, 2026 12:04pm | Jul 22, 2026 12:04pm | Jul 22, 2026 12:05pm | Jul 22, 2026 12:05pm | BrokenWire |  | Fair | No | Westmoreland call, please send to Westmoreland team.
Non-Outage | J.E.26.07.24517 | C001861632 | Romeo Brissett | null | Completed | null | null | Jul 22, 2026 8:06am | Jul 22, 2026 8:08am | Jul 22, 2026 11:19am | Jul 22, 2026 11:19am | Jul 22, 2026 11:19am | Jul 22, 2026 11:20am | Jul 22, 2026 11:21am | Jul 22, 2026 11:21am | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Check and found ok
Non-Outage | J.E.26.07.24600 | C001861630 | Rayon Foster | null | Completed | null | null | Jul 22, 2026 8:06am | Jul 22, 2026 8:06am | Jul 22, 2026 2:19pm | Jul 22, 2026 2:19pm | Jul 22, 2026 2:19pm | Jul 22, 2026 2:23pm | Jul 22, 2026 2:24pm | Jul 22, 2026 2:24pm |  |  | Fair | No | Customer said she received back light after a power outage earlier today
Non-Outage | J.E.26.07.24554 | C001861626 | Tajay Bernard | null | Completed | null | null | Jul 22, 2026 8:04am | Jul 22, 2026 9:10am | Jul 22, 2026 9:23am | Jul 22, 2026 9:34am | Jul 22, 2026 10:36am | Jul 22, 2026 10:37am | Jul 22, 2026 10:37am | Jul 22, 2026 10:37am |  |  | Fair | No | Customer stated that power was restored
Outage | J.E.26.07.24927 | C001861621 | Neville Spencer | Clarendon | Completed | Load_268691 | May Pen - 210 | Jul 22, 2026 7:57am | Jul 22, 2026 7:58am | Jul 22, 2026 8:27am | Jul 22, 2026 8:27am | Jul 22, 2026 8:28am | Jul 22, 2026 8:28am | Jul 22, 2026 8:28am | Jul 22, 2026 8:28am |  |  | Fair | No | Found ok.
Outage | J.E.26.07.24932 | C001861622 | Neville Spencer | Clarendon | Completed | Load_1000625 | May Pen - 210 | Jul 22, 2026 7:57am | Jul 22, 2026 7:58am | Jul 22, 2026 12:36pm | Jul 22, 2026 12:36pm | Jul 22, 2026 12:36pm | Jul 22, 2026 12:36pm | Jul 22, 2026 12:37pm | Jul 22, 2026 12:37pm |  |  | Fair | No | Unable to locate customer.
Outage | J.E.26.07.24935 | C001861623 | Neville Spencer | Clarendon | Completed | Load_243347 | May Pen - 210 | Jul 22, 2026 7:57am | Jul 22, 2026 7:58am | Jul 22, 2026 1:49pm | Jul 22, 2026 1:55pm | Jul 22, 2026 2:03pm | Jul 22, 2026 2:03pm | Jul 22, 2026 2:05pm | Jul 22, 2026 2:05pm |  |  | Fair | No | Customer not located.
Non-Outage | J.E.26.07.24558 | C001861618 | Oshane Warren | null | Completed | null | null | Jul 22, 2026 7:55am | Jul 22, 2026 7:56am | Jul 22, 2026 10:11am | Jul 22, 2026 10:11am | Jul 22, 2026 10:11am | Jul 22, 2026 10:12am | Jul 22, 2026 10:12am | Jul 22, 2026 10:12am |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.07.25026 | C001861617 | Tyrese Williams | null | Completed | null | null | Jul 22, 2026 7:55am | Jul 22, 2026 7:55am | Jul 22, 2026 11:10am | Jul 22, 2026 2:43pm | Jul 22, 2026 2:43pm | Jul 22, 2026 2:44pm | Jul 22, 2026 2:51pm | Jul 22, 2026 2:51pm | Fire |  | Fair | No | Premises found ok call related to banning wire
Outage | J.E.26.07.24825 | C001861613 | Oshane Warren | Westmoreland | Completed | Load_267097 | Paradise - 310 | Jul 22, 2026 7:54am | Jul 22, 2026 7:56am | Jul 22, 2026 10:15am | Jul 22, 2026 10:16am | Jul 22, 2026 11:35am | Jul 22, 2026 12:29pm | Jul 22, 2026 12:30pm | Jul 22, 2026 12:30pm |  |  | Rains | No | Splice and retention one spand of secondary conductor and replace 5amp 50kva xformer fuse
Outage | J.E.26.07.24845 | C001861615 | Javid Vernon | Hanover | Completed | Load_244663 | Orange Bay - 310 | Jul 22, 2026 7:54am | Jul 22, 2026 12:48pm | Jul 22, 2026 12:53pm | Jul 22, 2026 12:53pm | Jul 22, 2026 1:46pm | Jul 22, 2026 2:04pm | Jul 22, 2026 2:05pm | Jul 22, 2026 2:05pm |  |  | Fair | No | Refuse two 10amp junction fuse
Outage | J.E.26.07.24943 | C001861614 | Javid Vernon | Westmoreland | Completed | Load_268175 | Paradise - 110 | Jul 22, 2026 7:54am | Jul 22, 2026 7:57am | Jul 22, 2026 11:53am | Jul 22, 2026 11:53am | Jul 22, 2026 11:53am | Jul 22, 2026 11:53am | Jul 22, 2026 11:54am | Jul 22, 2026 11:54am |  |  | Fair | No | Customer stated that the issue has been resolved
Outage | J.E.26.07.24956 | C001861611 | Tajay Bernard | Hanover | Completed | Load_253387 | Orange Bay - 310 | Jul 22, 2026 7:54am | Jul 22, 2026 9:10am | Jul 22, 2026 10:39am | Jul 22, 2026 10:39am | Jul 22, 2026 10:39am | Jul 22, 2026 10:39am | Jul 22, 2026 10:39am | Jul 22, 2026 10:39am |  |  | Fair | No | Customer stated that the issue has been resolved
Outage | J.E.26.07.25016 | C001861612 | Dwain Samuels | Westmoreland | Completed | Load_267481 | Paradise - 310 | Jul 22, 2026 7:54am | Jul 22, 2026 8:08am | Jul 22, 2026 9:13am | Jul 22, 2026 9:25am | Jul 22, 2026 9:26am | Jul 22, 2026 9:59am | Jul 22, 2026 10:00am | Jul 22, 2026 10:00am |  |  | Fair | No | Connect 3 wire meter. Use 100ft service wire. Use 3 one bolt clamp and 2 pen union clamp
Non-Outage | J.E.26.07.16717 | C001861609 | Rayon Foster | Hanover | Completed | Load_259314 | Orange Bay - 310 | Jul 22, 2026 7:51am | Jul 22, 2026 7:53am | Jul 22, 2026 2:57pm | Jul 22, 2026 4:27pm | Jul 22, 2026 5:30pm | Jul 22, 2026 5:34pm | Jul 22, 2026 5:34pm | Jul 22, 2026 5:34pm |  |  | Fair | No | Premises not found needed more driving detail unable to reach on cell phone
Non-Outage | J.E.26.07.23409 | C001861605 | Raymond Lewis | St.Ann | Completed | Load_263615 | Roaring River - 210 | Jul 22, 2026 7:50am | Jul 22, 2026 7:51am | Jul 22, 2026 2:04pm | Jul 22, 2026 2:04pm | Jul 22, 2026 3:49pm | Jul 22, 2026 3:58pm | Jul 22, 2026 4:01pm | Jul 22, 2026 4:01pm |  |  | Fair | No | Premises not found and phone not answering
Non-Outage | J.E.26.07.23617 | C001861604 | Raymond Lewis | St.Ann | Completed | Load_240533 | Roaring River - 410 | Jul 22, 2026 7:50am | Jul 22, 2026 7:51am | Jul 22, 2026 9:42am | Jul 22, 2026 9:42am | Jul 22, 2026 9:43am | Jul 22, 2026 9:44am | Jul 22, 2026 9:44am | Jul 22, 2026 9:44am |  |  | Fair | No | Refer to field service
Non-Outage | J.E.26.07.24143 | C001861603 | Raymond Lewis | St.Ann | Completed | Load_240533 | Roaring River - 410 | Jul 22, 2026 7:50am | Jul 22, 2026 7:51am | Jul 22, 2026 8:18am | Jul 22, 2026 8:18am | Jul 22, 2026 9:22am | Jul 22, 2026 9:41am | Jul 22, 2026 9:41am | Jul 22, 2026 9:41am |  |  | Fair | No | Refer to field service, PMC box , customer out of supply (2) two days
Non-Outage | J.E.26.07.24687 | C001861602 | Raymond Lewis | St.Ann | Completed | Load_265774 | Roaring River - 410 | Jul 22, 2026 7:50am | Jul 22, 2026 7:51am | Jul 22, 2026 9:55am | Jul 22, 2026 9:55am | Jul 22, 2026 9:55am | Jul 22, 2026 10:27am | Jul 22, 2026 10:27am | Jul 22, 2026 10:27am |  |  | Fair | No | Remade joints at pothead 3 wire service,voltage 118/117/236
Outage | J.E.26.07.24990 | C001861600 | Neville Spencer | Clarendon | Completed | Load_249758 | Parnassus - 210 | Jul 22, 2026 7:48am | Jul 22, 2026 7:49am | Jul 22, 2026 10:40am | Jul 22, 2026 10:40am | Jul 22, 2026 10:40am | Jul 22, 2026 10:40am | Jul 22, 2026 10:41am | Jul 22, 2026 10:41am | Fire |  | Fair | No | Renew blown 20 amp j/ fuse at pole #=055817 area restored.
Outage | J.E.26.07.24970 | C001861598 | Neville Spencer | Clarendon | Completed | Load_249990 | Parnassus - 210 | Jul 22, 2026 7:46am | Jul 22, 2026 7:47am | Jul 22, 2026 8:37am | Jul 22, 2026 8:37am | Jul 22, 2026 9:09am | Jul 22, 2026 10:16am | Jul 22, 2026 10:17am | Jul 22, 2026 10:17am |  |  | Fair | No | Renew blown 20 amp j/ fuse at pole # 055817 area restored.
Non-Outage | J.E.26.07.22540 | C001861594 | Evan Spaulding | St.Mary | Completed | Load_241233 | Highgate -110 | Jul 22, 2026 7:43am | Jul 22, 2026 7:44am | Jul 22, 2026 10:10am | Jul 22, 2026 10:10am | Jul 22, 2026 11:00am | Jul 22, 2026 11:51am | Jul 22, 2026 11:52am | Jul 22, 2026 11:52am |  |  | Fair | No | Use 6- 1 bolt clamps at location,voltage left 114v,114v,228v.
Non-Outage | J.E.26.07.23046 | C001861595 | Evan Spaulding | St.Mary | Completed | Load_266257 | Highgate -110 | Jul 22, 2026 7:43am | Jul 22, 2026 7:44am | Jul 22, 2026 9:40am | Jul 22, 2026 9:40am | Jul 22, 2026 9:58am | Jul 22, 2026 10:09am | Jul 22, 2026 10:10am | Jul 22, 2026 10:10am |  |  | Fair | No | Burnt meter jaw,refer to field service.
Outage | J.E.26.07.24957 | C001861593 | Horace Malcolm | St.James | Completed | Load_557023 | Bogue - 310 | Jul 22, 2026 7:41am | Jul 23, 2026 8:17am | Jul 23, 2026 11:03am | Jul 23, 2026 11:03am | Jul 23, 2026 11:37am | Jul 23, 2026 11:43am | Jul 23, 2026 11:43am | Jul 23, 2026 11:43am |  |  | Fair | No | Check and found premises ok supply restored
Non-Outage | J.E.26.07.24803 | C001861591 | Andre Williams | Trelawny | Completed | Load_263290 | Martha Brae - 210 | Jul 22, 2026 7:38am | Jul 22, 2026 7:38am | Jul 22, 2026 7:48am | Jul 22, 2026 7:51am | Jul 22, 2026 8:13am | Jul 22, 2026 8:24am | Jul 22, 2026 8:31am | Jul 22, 2026 8:31am | Fire |  | Fair | No | Clean and tighten clamp at transformer pole that was burning
Outage | J.E.26.07.24960 | C001861592 | Neville Spencer | Clarendon | Completed | Load_238332 | Parnassus - 210 | Jul 22, 2026 7:38am | Jul 22, 2026 7:43am | Jul 22, 2026 10:42am | Jul 22, 2026 10:42am | Jul 22, 2026 10:42am | Jul 22, 2026 10:42am | Jul 22, 2026 10:44am | Jul 22, 2026 10:44am |  |  | EarthMovement | No | Renew blown 20 amp j/ fuse at pole # 055817 area restored.
Non-Outage | J.E.26.07.23986 | C001861589 | Andre Williams | Trelawny | Completed | Load_294412 | Duncans - 110 | Jul 22, 2026 7:37am | Jul 22, 2026 7:38am | Jul 22, 2026 8:33am | Jul 22, 2026 8:33am | Jul 22, 2026 8:35am | Jul 22, 2026 8:36am | Jul 22, 2026 8:37am | Jul 22, 2026 8:37am |  |  | Fair | No | Issue was resolved confirmed by call
Non-Outage | J.E.26.07.24054 | C001861590 | Andre Williams | Trelawny | Completed | Load_245182 | Duncans - 210 | Jul 22, 2026 7:37am | Jul 22, 2026 7:38am | Jul 22, 2026 8:38am | Jul 22, 2026 8:45am | Jul 22, 2026 10:11am | Jul 22, 2026 10:31am | Jul 22, 2026 10:31am | Jul 22, 2026 10:31am |  |  | Fair | No | Measure voltage at Jps pole customer meter pole defective unable to climb as well as meter barrel lock. Voltage going to meter pole 118+116=234 customer was advice to change meter pole
Outage | J.E.26.07.24920 | C001861586 | Nickolas Rodriques | St.Catherine | Completed | Load_305230 | Rhodens Pen - 210 | Jul 22, 2026 7:34am | Jul 22, 2026 7:35am | Jul 22, 2026 7:49am | Jul 22, 2026 8:10am | Jul 22, 2026 9:44am | Jul 22, 2026 10:20am | Jul 22, 2026 10:29am | Jul 22, 2026 10:29am |  |  | Fair | No | Unable to communicate with the customer after several attempts. Report was apparently made for Monymusk HScheme Clarendon based on notes.
Outage | J.E.26.07.24984 | C001861587 | Neville Spencer | St.Catherine | Completed | Load_261578 | Rhodens Pen - 310 | Jul 22, 2026 7:34am | Jul 22, 2026 10:13am | Jul 22, 2026 11:16am | Jul 22, 2026 11:16am | Jul 22, 2026 11:42am | Jul 22, 2026 12:33pm | Jul 22, 2026 12:33pm | Jul 22, 2026 12:33pm | LowHangingWires |  | Fair | No | Foun secondary phase and neutral conductor entangled. Open 25 kva xmfr at pole #569599 retention 2, spans of secondary phase and neutral conductor used 2, preform, 2 clamps supply restored.
Non-Outage | J.E.26.07.24235 | C001861585 | Omar King | St.Ann | Completed | Load_240309 | Ocho Rios - 310 | Jul 22, 2026 7:32am | Jul 22, 2026 7:32am | Jul 22, 2026 1:52pm | Jul 22, 2026 1:52pm | Jul 22, 2026 2:55pm | Jul 22, 2026 3:00pm | Jul 22, 2026 3:01pm | Jul 22, 2026 3:01pm |  |  | Fair | No | Unable to find customer customer call several times no answer directions not sufficient
Non-Outage | J.E.26.07.24292 | C001861583 | Omar King | St.Ann | Completed | Load_239479 | Ocho Rios - 310 | Jul 22, 2026 7:32am | Jul 22, 2026 7:32am | Jul 22, 2026 8:51am | Jul 22, 2026 8:51am | Jul 22, 2026 9:17am | Jul 22, 2026 9:18am | Jul 22, 2026 9:18am | Jul 22, 2026 9:18am |  |  | Fair | No | Unable to find customer call several times no answer.
Outage | J.E.26.07.24540 | C001861582 | Richard Nicholas | St.Catherine | Completed | Load_255497 | Twickenham - 410 | Jul 22, 2026 7:32am | Jul 22, 2026 7:32am | Jul 22, 2026 10:12am | Jul 22, 2026 10:12am | Jul 22, 2026 11:05am | Jul 22, 2026 12:56pm | Jul 22, 2026 1:00pm | Jul 22, 2026 1:00pm |  |  | Fair | No | Several leaning 40ft pole with 3phase primary need to dig and straighten.replaced blown 10amp junctions fuse on pole #158992,blown 30amp x2 junctions fuse on pole#008129 and blown 25amp junctions in the square.please note that the middle switch on pole #008129 is very slack and need to tighten.
Outage | J.E.26.07.24977 | C001861581 | Ryan Richards | Manchester | Completed | Load_1002370 | Spur Tree - 310 | Jul 22, 2026 7:31am | Jul 22, 2026 7:36am | Jul 22, 2026 7:41am | Jul 22, 2026 8:09am | Jul 22, 2026 9:00am | Jul 22, 2026 1:00am | Jul 22, 2026 9:15am | Jul 22, 2026 9:15am |  |  | Fair | No | Defective transformer found primary bushing brake off and cover lift off transformer and to replace urgently 20 to 25 customer are affected
Outage | J.E.26.07.24965 | C001861576 | Wan Carlos Scarlett | Portmore | Completed | Load_576151 | Naggo Head - 610 | Jul 22, 2026 7:23am | Jul 22, 2026 7:24am | Jul 22, 2026 10:33am | Jul 22, 2026 10:45am | Jul 22, 2026 10:45am | Jul 22, 2026 10:45am | Jul 22, 2026 10:46am | Jul 22, 2026 10:46am |  |  | Fair | No | Call related customer confirm that power supply has been restored
Outage | J.E.26.07.24976 | C001861577 | Wan Carlos Scarlett | Portmore | Completed | Load_574643 | Naggo Head - 610 | Jul 22, 2026 7:23am | Jul 22, 2026 7:24am | Jul 22, 2026 8:54am | Jul 22, 2026 8:54am | Jul 22, 2026 9:37am | Jul 22, 2026 10:40am | Jul 22, 2026 10:42am | Jul 22, 2026 10:42am |  |  | Fair | No | Refuse 30amp junction pole # 035255 and refuse 15KVA transformer with a 2amp fuse no pole # was found.Clear bird from off transformer bushing
Outage | J.E.26.07.23686 | C001861575 | Christopher Edwards | KSAN | Completed | Load_246237 | Constant Spring - 410 | Jul 22, 2026 7:22am | Jul 22, 2026 8:01am | Jul 22, 2026 8:27am | Jul 22, 2026 11:17am | Jul 22, 2026 11:46am | Jul 22, 2026 12:23pm | Jul 22, 2026 12:24pm | Jul 22, 2026 12:24pm |  |  | Fair | No | Unable to locate premises no broken wire found
Non-Outage | J.E.26.07.24173 | C001861571 | Tyrese Williams | St.Ann | Completed | Load_256057 | Cardiff Hall - 310 | Jul 22, 2026 7:21am | Jul 22, 2026 7:21am | Jul 23, 2026 8:45am | Jul 23, 2026 8:45am | Jul 23, 2026 9:36am | Jul 23, 2026 9:38am | Jul 23, 2026 9:39am | Jul 23, 2026 9:39am | LeaningPole |  | Fair | No | Found a 30ft class 4 wooden pole open secondary leaning
Non-Outage | J.E.26.07.24265 | C001861573 | Tyrese Williams | St.Ann | Completed | Load_244653 | Cardiff Hall - 310 | Jul 22, 2026 7:21am | Jul 22, 2026 7:21am | Jul 22, 2026 2:55pm | Jul 22, 2026 2:55pm | Jul 22, 2026 2:56pm | Jul 22, 2026 2:58pm | Jul 22, 2026 2:58pm | Jul 22, 2026 2:58pm | LeaningPole |  | Fair | No | Found a 30 ft class 4 wooden pole , twisted secondary leaning leaning need to be changed
Non-Outage | J.E.26.07.24367 | C001861574 | Tyrese Williams | St.Ann | Completed | Load_252510 | Cardiff Hall - 210 | Jul 22, 2026 7:21am | Jul 22, 2026 7:21am | Jul 22, 2026 8:58am | Jul 22, 2026 10:20am | Jul 22, 2026 11:04am | Jul 22, 2026 11:09am | Jul 22, 2026 11:10am | Jul 22, 2026 11:10am |  |  | Fair | No | Premises found ok customer has internal problem
Outage | J.E.26.07.24974 | C001861570 | Wan Carlos Scarlett | Portmore | Completed | Load_244214 | Naggo Head - 510 | Jul 22, 2026 7:20am | Jul 22, 2026 7:21am | Jul 22, 2026 10:33am | Jul 22, 2026 10:44am | Jul 22, 2026 10:44am | Jul 22, 2026 10:45am | Jul 22, 2026 10:45am | Jul 22, 2026 10:45am |  |  | Fair | No | Call related customer confirm that power supply has been restored
Non-Outage | J.E.26.07.22393 | C001861569 | Raymond Carr | St.Mary | Completed | Load_349785 | Oracabessa - 210 | Jul 22, 2026 7:19am | Jul 22, 2026 7:19am | Jul 22, 2026 8:35am | Jul 22, 2026 8:35am | Jul 22, 2026 9:42am | Jul 22, 2026 9:43am | Jul 22, 2026 9:53am | Jul 22, 2026 9:53am |  |  | Fair | No | Customer was advised to have an electrician repaired stanchion and pothead, before service wire can be tensioned.
Non-Outage | J.E.26.07.24883 | C001861567 | Raymond Carr | St.Ann | Completed | Load_265293 | Upper White River - 110 | Jul 22, 2026 7:19am | Jul 22, 2026 7:19am | Jul 22, 2026 9:55am | Jul 22, 2026 9:55am | Jul 22, 2026 10:34am | Jul 22, 2026 11:22am | Jul 22, 2026 11:32am | Jul 22, 2026 11:32am |  |  | Fair | No | Slack secondary neutral bushing was tightened, also a clamp was replaced on neutral at JPS pole. Voltage readings 124/110/234.
Outage | J.E.26.07.23495 | C001861564 | Ryan Richards | Manchester | Completed | Load_262542 | Spur Tree - 310 | Jul 22, 2026 7:17am | Jul 22, 2026 7:53am | Jul 22, 2026 10:50am | Jul 22, 2026 10:50am | Jul 22, 2026 11:37am | Jul 22, 2026 11:42am | Jul 22, 2026 11:42am | Jul 22, 2026 11:42am |  |  | Fair | No | Premises found with supply 119/120/240/205 principal said that the report was made from Monday and the supply seems to be working well
Outage | J.E.26.07.24967 | C001861562 | Tyrese Williams | St.Ann | Completed | Load_239328 | Cardiff Hall - 210 | Jul 22, 2026 7:15am | Jul 22, 2026 7:15am | Jul 22, 2026 8:59am | Jul 22, 2026 11:10am | Jul 22, 2026 11:59am | Jul 22, 2026 12:28pm | Jul 22, 2026 12:31pm | Jul 22, 2026 12:31pm |  |  | Fair | No | Remove illegal connections from secondary line that was causing the wires to bang and Reset a 25kva transformer
Non-Outage | J.E.26.07.15033 | C001861559 | Swon Miller | St.James | Completed | Load_251737 | Queens Drive - 810 | Jul 22, 2026 7:14am | Jul 22, 2026 7:14am | Jul 22, 2026 9:23am | Jul 22, 2026 9:23am | Jul 22, 2026 9:40am | Jul 20, 2026 12:02am | Jul 22, 2026 12:02pm | Jul 22, 2026 12:02pm |  |  | Fair | No | Found customer with low voltage voltage found line side 105/105/210 loab side 102/102/202 100 kva transformer at max. Customers with low voltage are at the end of the circuit voltage left 105/104/210/load side 102/101/202 Recommend secondary circuit be split plz refer to maintenance
Outage | J.E.26.07.24966 | C001861560 | Fitzroy Turner | KSAS | Completed | Load_239591 | Cane River - 610 | Jul 22, 2026 7:14am | Jul 22, 2026 7:51am | Jul 22, 2026 8:50am | Jul 22, 2026 8:50am | Jul 22, 2026 9:18am | Jul 22, 2026 9:18am | Jul 22, 2026 9:23am | Jul 22, 2026 9:23am |  |  | EarthMovement | No | Found 20amp fuse blown at bank of three 50kva transformer replaced with one 5amps fuse supply restored to customer
Outage | J.E.26.07.24988 | C001861561 | Edward Royal | KSAS | Completed | Load_244171 | Hunts Bay - 810 | Jul 22, 2026 7:14am | Jul 22, 2026 8:18am | Jul 22, 2026 8:48am | Jul 22, 2026 8:48am | Jul 22, 2026 9:03am | Jul 22, 2026 9:22am | Jul 22, 2026 9:23am | Jul 22, 2026 9:23am |  |  | Fair | No | I was unable to communicate with the petrojam maintenance personnel to get more information
Non-Outage | J.E.26.02.42066 | C001861558 | Swon Miller | St.James | Completed | Load_263530 | Rose Hall - 210 | Jul 22, 2026 7:13am | Jul 22, 2026 7:14am | Jul 22, 2026 7:47am | Jul 22, 2026 7:47am | Jul 22, 2026 8:24am | Jul 22, 2026 9:00am | Jul 22, 2026 9:02am | Jul 22, 2026 9:02am | LeaningPole |  | Fair | No | Found 40ft class 6 switch pole rotten at the base. TDE with return 3 phase primary and secondary lines cable wires and secondary lines hanging very very low urgent attention required (customer states that a truck pulled on the cable wires last week causing pole the pole to be leaning pulling on stanchion pole is leaning at a 70 degree angle pole needs to be replaced urgently plz refer to k.frazer operation pole #567750
Non-Outage | J.E.26.07.15164 | C001861557 | Swon Miller | St.James | Completed | Load_260850 | Rose Hall - 210 | Jul 22, 2026 7:13am | Jul 22, 2026 7:14am | Jul 22, 2026 9:03am | Jul 22, 2026 9:04am | Jul 22, 2026 9:14am | Jul 21, 2026 9:22am | Jul 22, 2026 9:23am | Jul 22, 2026 9:23am |  |  | Fair | No | Check and found okay voltage found 117/116/234 voltage left 117/116/234
Outage | J.E.26.07.24997 | C001861552 | Marlon Authors | Manchester | Completed | Load_239279 | Spur Tree - 210 | Jul 22, 2026 7:10am | Jul 22, 2026 7:45am | Jul 22, 2026 9:40am | Jul 22, 2026 9:40am | Jul 22, 2026 11:15am | Jul 22, 2026 11:27am | Jul 22, 2026 11:27am | Jul 22, 2026 11:27am |  |  | Fair | No | Supply checked and found breaker in pic box tripped. Reset same and supply restored,rdg 115v,117v and cross phased 232 volts
Non-Outage | J.E.26.07.24887 | C001861549 | Damion Reid | null | Completed | null | null | Jul 22, 2026 7:07am | Jul 22, 2026 7:26am | Jul 22, 2026 8:50am | Jul 22, 2026 8:50am | Jul 22, 2026 10:13am | Jul 22, 2026 11:20am | Jul 22, 2026 11:24am | Jul 22, 2026 11:24am |  |  | Fair | No | Remade burnt off service phase at secondary pole for 3 wire service using one bolt clamp voltage reading at meter socket phase to neutral 115v-115v access phase 232v
Outage | J.E.26.07.24971 | C001861465 | Fitzroy Turner | KSAS | Completed | Load_1002691 | Cane River - 410 | Jul 22, 2026 6:18am | Jul 22, 2026 8:16am | Jul 22, 2026 11:14am | Jul 22, 2026 11:17am | Jul 22, 2026 11:17am | Jul 22, 2026 11:17am | Jul 22, 2026 11:20am | Jul 22, 2026 11:20am |  |  | Fair | No | Found 5amp fuse blown for 50kva transformer cause by salt from the sea replaced 5amp fuse at 31 mars drive supply restored to the areas
Outage | J.E.26.07.24961 | C001861448 | Swon Miller | St.James | Completed | Load_267656 | Queens Drive - 710 | Jul 22, 2026 5:32am | Jul 22, 2026 7:06am | Jul 22, 2026 2:14pm | Jul 22, 2026 2:14pm | Jul 22, 2026 2:38pm | Jul 14, 2026 3:07pm | Jul 22, 2026 3:07pm | Jul 22, 2026 3:07pm |  |  | Fair | No | Check and found okay voltage found 114/110/224 voltage left 114/110 /224
Non-Outage | J.E.26.07.24881 | C001861445 | Milton Charlton | null | Completed | null | null | Jul 22, 2026 4:33am | Jul 22, 2026 8:20am | Jul 22, 2026 10:27am | Jul 22, 2026 10:31am | Jul 22, 2026 10:31am | Jul 22, 2026 10:45am | Jul 22, 2026 10:33am | Jul 22, 2026 10:33am |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.07.24758 | C001861444 | Delano Gayle | St.Catherine | Completed | Load_266407 | Twickenham - 310 | Jul 22, 2026 3:58am | Jul 22, 2026 3:58am | Jul 22, 2026 4:21am | Jul 22, 2026 4:27am | Jul 22, 2026 5:11am | Jul 22, 2026 5:14am | Jul 22, 2026 5:15am | Jul 22, 2026 5:15am |  |  | Fair | No | Premises not found, no answer from customer phone,area found okay
Outage | J.E.26.07.24946 | C001861443 | Daniel Francis | St.Ann | Completed | Load_239328 | Cardiff Hall - 210 | Jul 22, 2026 3:56am | Jul 22, 2026 3:56am | Jul 22, 2026 5:17am | Jul 22, 2026 5:17am | Jul 22, 2026 5:18am | Jul 22, 2026 5:19am | Jul 22, 2026 5:21am | Jul 22, 2026 5:21am |  |  | Fair | No | Premises not found no directions customer not answering phone
Outage | J.E.26.07.24894 | C001861439 | Horace Malcolm | St.James | Completed | Load_249184 | Bogue - 610 | Jul 22, 2026 1:20am | Jul 22, 2026 1:20am | Jul 22, 2026 3:00am | Jul 22, 2026 3:00am | Jul 22, 2026 3:00am | Jul 22, 2026 3:01am | Jul 22, 2026 3:01am | Jul 22, 2026 3:01am | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards | Y | Fair | No | Related to previous call job number 24888
Outage | J.E.26.07.24853 | C001861434 | Daniel Francis | St.Ann | Completed | Load_239328 | Cardiff Hall - 210 | Jul 22, 2026 12:46am | Jul 22, 2026 12:46am | Jul 22, 2026 3:24am | Jul 22, 2026 3:25am | Jul 22, 2026 3:25am | Jul 22, 2026 3:26am | Jul 22, 2026 3:27am | Jul 22, 2026 3:27am |  |  | Fair | No | Unable to locate customer not;answering
Outage | J.E.26.07.24888 | C001861433 | Horace Malcolm | St.James | Completed | Load_249166 | Bogue - 610 | Jul 22, 2026 12:42am | Jul 22, 2026 12:43am | Jul 22, 2026 12:48am | Jul 22, 2026 12:48am | Jul 22, 2026 2:08am | Jul 22, 2026 3:00am | Jul 22, 2026 3:00am | Jul 22, 2026 3:00am | BrokenWire |  | Fair | No | Found one 40ft wooden pole broken with single phase primary and secondary line due to vichele accident islolate one pole span secondary line to give back customers supply only three customers is without supply pole need replacement ASAP due to pole leaning towards the road ,primary line dislodge from broken pole caused primary line touching tree wen breeze blows
Outage | J.E.26.07.24471 | C001861421 | Wan Carlos Scarlett | St.Catherine | Completed | Load_254797 | Twickenham - 210 | Jul 21, 2026 11:14pm | Jul 22, 2026 7:24am | Jul 22, 2026 7:36am | Jul 22, 2026 7:36am | Jul 22, 2026 8:17am | Jul 22, 2026 8:52am | Jul 22, 2026 8:54am | Jul 22, 2026 8:54am |  |  | Fair | No | Found customer 3 wire service at pole with phase and neutral corroded use 3-one bolt clamps at open secondary line readings 116-117-234
Outage | J.E.26.07.24574 | C001861422 | Wan Carlos Scarlett | Portmore | Completed | Load_245535 | Naggo Head - 610 | Jul 21, 2026 11:14pm | Jul 22, 2026 7:22am | Jul 22, 2026 12:02pm | Jul 22, 2026 12:02pm | Jul 22, 2026 12:30pm | Jul 22, 2026 12:45pm | Jul 22, 2026 12:46pm | Jul 22, 2026 12:46pm |  |  | Fair | No | Found customer 3 wire service at pole with one of the phase corroded use one bolt clamp at open secondary line phase readings 114-115-230
Outage | J.E.26.07.24850 | C001861420 | Christopher Edwards | KSAS | Completed | Load_259334 | Cane River - 610 | Jul 21, 2026 11:11pm | Jul 21, 2026 11:11pm | Jul 21, 2026 11:41pm | Jul 21, 2026 11:46pm | Jul 21, 2026 11:46pm | Jul 22, 2026 12:03am | Jul 22, 2026 12:04am | Jul 22, 2026 12:04am | Fire |  | Fair | No | Customer was contacted and stated that the issue was resolved
Outage | J.E.26.07.24835 | C001861419 | Barrington Brown | St.James | Completed | Load_267460 | Bogue - 510 | Jul 21, 2026 11:09pm | Jul 22, 2026 7:42am | Jul 22, 2026 11:26am | Jul 22, 2026 11:26am | Jul 22, 2026 11:43am | Jul 22, 2026 1:54pm | Jul 22, 2026 1:54pm | Jul 22, 2026 1:54pm |  |  | Fair | No | Checked and found ok
Non-Outage | J.E.26.07.23671 | C001861415 | Delano Gayle | null | Completed | null | null | Jul 21, 2026 10:43pm | Jul 21, 2026 10:45pm | Jul 21, 2026 11:03pm | Jul 22, 2026 1:00am | Jul 22, 2026 3:25am | Jul 22, 2026 3:28am | Jul 22, 2026 3:28am | Jul 22, 2026 3:28am |  |  | Fair | No | Single customer with issue, non outage call
Outage | J.E.26.07.24480 | C001861414 | Delano Gayle | St.Catherine | Completed | Load_246786 | Tredegar - 410 | Jul 21, 2026 10:43pm | Jul 21, 2026 10:44pm | Jul 21, 2026 11:03pm | Jul 22, 2026 3:28am | Jul 22, 2026 3:29am | Jul 22, 2026 3:30am | Jul 22, 2026 3:30am | Jul 22, 2026 3:30am | TreeContact |  | Fair | No | Single customer experiencing low voltage as stated in report,
Outage | J.E.26.07.24540 | C001861413 | Delano Gayle | St.Catherine | Completed | Load_255497 | Twickenham - 410 | Jul 21, 2026 10:43pm | Jul 21, 2026 10:43pm | Jul 21, 2026 11:03pm | Jul 22, 2026 3:43am | Jul 22, 2026 3:44am | Jul 22, 2026 3:44am | Jul 22, 2026 3:44am | Jul 22, 2026 3:44am |  |  | Fair | No | Daylight attention required to visit location
Outage | J.E.26.07.24833 | C001861412 | Horace Malcolm | St.James | Completed | Load_249326 | Queens Drive - 810 | Jul 21, 2026 10:31pm | Jul 22, 2026 4:08am | Jul 22, 2026 6:21am | Jul 22, 2026 6:21am | Jul 22, 2026 6:55am | Jul 22, 2026 6:58am | Jul 22, 2026 6:58am | Jul 22, 2026 6:58am |  |  | Fair | No | Reconnect customer service at pole splice customer service nuetral used 5ft #6 triplex wire voltage 115-113-228 after carry out repair found customer have internal issues
Outage | J.E.26.07.23727 | C001861403 | Devon Grant | KSAN | Completed | Load_242541 | Constant Spring - 410 | Jul 21, 2026 9:24pm | Jul 22, 2026 8:37am | Jul 22, 2026 9:28am | Jul 22, 2026 9:28am | Jul 22, 2026 11:12am | Jul 22, 2026 11:13am | Jul 22, 2026 11:15am | Jul 22, 2026 11:15am | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Repair switch top jumper, supply now restore.
Non-Outage | J.E.26.07.24813 | C001861402 | Eric Williams | KSAN | Completed | Load_247868 | Washington Blvd - 810 | Jul 21, 2026 9:18pm | Jul 21, 2026 9:18pm | Jul 21, 2026 9:34pm | Jul 21, 2026 9:34pm | Jul 21, 2026 10:11pm | Jul 21, 2026 10:11pm | Jul 21, 2026 10:12pm | Jul 21, 2026 10:12pm | Fire |  | Fair | No | No fire seeing,
Non-Outage | J.E.26.07.24809 | C001861400 | Hopeton Henry | null | Completed | null | null | Jul 21, 2026 9:03pm | Jul 21, 2026 9:05pm | Jul 21, 2026 11:03pm | Jul 21, 2026 11:03pm | Jul 21, 2026 11:30pm | Jul 21, 2026 11:30pm | Jul 21, 2026 11:32pm | Jul 21, 2026 11:32pm | BrokenWire |  | Fair | No | Use preform to anchor dislodge secondary , no pole number
Outage | J.E.26.07.24798 | C001861399 | Neville Spencer | Clarendon | Completed | Load_243081 | Parnassus - 310 | Jul 21, 2026 9:02pm | Jul 22, 2026 7:50am | Jul 22, 2026 8:30am | Jul 22, 2026 8:30am | Jul 22, 2026 8:30am | Jul 22, 2026 8:31am | Jul 22, 2026 8:31am | Jul 22, 2026 8:31am |  |  | Fair | No | Found supply in area .
Outage | J.E.26.07.24746 | C001861396 | Romeo Brissett | St.James | Completed | Load_257764 | Bogue - 310 | Jul 21, 2026 8:42pm | Jul 21, 2026 8:44pm | Jul 21, 2026 8:48pm | Jul 21, 2026 8:48pm | Jul 21, 2026 9:48pm | Jul 21, 2026 10:00pm | Jul 21, 2026 10:05pm | Jul 21, 2026 10:05pm |  |  | Fair | No | Location was visited and power found in the area.
Outage | J.E.26.07.24759 | C001861395 | Romeo Brissett | St.James | Completed | Load_262175 | Bogue - 310 | Jul 21, 2026 8:42pm | Jul 21, 2026 8:44pm | Jul 21, 2026 10:05pm | Jul 21, 2026 10:05pm | Jul 21, 2026 10:22pm | Jul 21, 2026 11:06pm | Jul 21, 2026 11:10pm | Jul 21, 2026 11:10pm |  |  | Fair | No | Isolated (1)10KVA transformer, repaired transformer drop lead, however 2 customers still without supply. Please send to,field service.
Outage | J.E.26.07.24770 | C001861397 | Horace Malcolm | St.James | Completed | Load_254829 | Bogue - 310 | Jul 21, 2026 8:42pm | Jul 21, 2026 11:09pm | Jul 21, 2026 11:24pm | Jul 21, 2026 11:24pm | Jul 21, 2026 11:40pm | Jul 22, 2026 12:11am | Jul 22, 2026 12:11am | Jul 22, 2026 12:11am | BrokenWire |  | Fair | No | Clean and remake joints at pole used 1clamp voltage 115-117-232
Non-Outage | J.E.26.03.06461 | C001861390 | Andrew Powell | St.Elizabeth | Completed | Load_263724 | Maggotty - 210 | Jul 21, 2026 8:11pm | Jul 21, 2026 8:11pm | Jul 22, 2026 3:59pm | Jul 22, 2026 3:59pm | Jul 22, 2026 3:59pm | Jul 22, 2026 3:59pm | Jul 22, 2026 4:00pm | Jul 22, 2026 4:00pm |  |  | Fair | No | Premises not located inadequately direction contact customer by telephone unsuccessful.
Non-Outage | J.E.26.03.11789 | C001861391 | Andrew Powell | St.Elizabeth | Completed | Load_267239 | Maggotty - 210 | Jul 21, 2026 8:11pm | Jul 21, 2026 8:11pm | Jul 21, 2026 9:10pm | Jul 21, 2026 9:10pm | Jul 21, 2026 10:17pm | Jul 21, 2026 10:31pm | Jul 21, 2026 10:33pm | Jul 21, 2026 10:33pm |  |  | Fair | No | Premises closed daylight attention required please follow up report.
Non-Outage | J.E.26.02.31903 | C001861389 | Andrew Powell | Manchester | Completed | Load_259960 | Spur Tree - 210 | Jul 21, 2026 8:09pm | Jul 21, 2026 8:09pm | Jul 21, 2026 9:09pm | Jul 21, 2026 9:09pm | Jul 21, 2026 9:09pm | Jul 21, 2026 9:09pm | Jul 21, 2026 9:10pm | Jul 21, 2026 9:10pm | LeaningPole |  | Fair | No | Premises found okay customer stated that fault resolved yesterday.
Outage | J.E.26.07.24772 | C001861386 | Hartley Chin | Clarendon | Completed | Load_579438 | May Pen - 110 | Jul 21, 2026 7:55pm | Jul 22, 2026 8:12am | Jul 22, 2026 12:54pm | Jul 22, 2026 12:54pm | Jul 22, 2026 12:54pm | Jul 22, 2026 12:54pm | Jul 22, 2026 12:55pm | Jul 22, 2026 12:55pm |  |  | Fair | No | Call related to job 24776
Outage | J.E.26.07.24776 | C001861385 | Hartley Chin | Clarendon | Completed | Load_240964 | May Pen - 110 | Jul 21, 2026 7:55pm | Jul 22, 2026 8:14am | Jul 22, 2026 9:02am | Jul 22, 2026 9:02am | Jul 22, 2026 11:10am | Jul 22, 2026 11:44am | Jul 22, 2026 11:45am | Jul 22, 2026 11:45am | BrokenWire |  | Fair | No | Found 15 amp junction blown line patrolled and refused
Outage | J.E.26.07.24718 | C001861384 | Richard Samuda | Manchester | Completed | Load_1002370 | Spur Tree - 310 | Jul 21, 2026 7:54pm | Jul 21, 2026 7:55pm | Jul 21, 2026 8:58pm | Jul 21, 2026 8:58pm | Jul 21, 2026 8:58pm | Jul 21, 2026 9:43pm | Jul 21, 2026 9:43pm | Jul 21, 2026 9:43pm |  |  | Fair | No | 0131338found 25 amp junction blown patrol line found 8 amps take off fuse blown patrol line found 25 kv transformer fuse blown patrol line found nothing replaced 25 amps junction fuse than close 8 amps take off fuse than close 25 kv transformer fuse customer back to normal
Outage | J.E.26.07.24719 | C001861381 | Richard Samuda | Manchester | Completed | Load_257666 | Kendal - 310 | Jul 21, 2026 7:49pm | Jul 21, 2026 9:06pm | Jul 21, 2026 9:53pm | Jul 21, 2026 9:53pm | Jul 21, 2026 10:07pm | Jul 21, 2026 10:25pm | Jul 21, 2026 10:25pm | Jul 21, 2026 10:25pm |  |  | Fair | No | Customer was disconnected due to bad death but he has paid his bill and was not reconnected but with the help of the escalation he now back to normal
Non-Outage | J.E.26.07.24750 | C001861376 | Milton Charlton | null | Completed | null | null | Jul 21, 2026 7:27pm | Jul 21, 2026 7:35pm | Jul 21, 2026 8:18pm | Jul 21, 2026 8:18pm | Jul 21, 2026 8:54pm | Jul 21, 2026 9:50pm | Jul 21, 2026 9:50pm | Jul 21, 2026 9:50pm | BrokenWire |  | Fair | No | Refused and reclosed 5amps transformer switch at pole #0057482 using one 5 amps fuse.
Outage | J.E.26.07.23949 | C001861378 | Daniel Francis | St.Ann | Completed | Load_249107 | Cardiff Hall - 310 | Jul 21, 2026 7:27pm | Jul 21, 2026 10:46pm | Jul 21, 2026 10:58pm | Jul 21, 2026 10:58pm | Jul 21, 2026 11:56pm | Jul 21, 2026 11:57pm | Jul 21, 2026 11:57pm | Jul 21, 2026 11:57pm | BrokenWire |  | Fair | No | Not found customer not answering phone
Outage | J.E.26.07.24176 | C001861377 | Tyrese Williams | St.Ann | Completed | Load_255835 | Cardiff Hall - 310 | Jul 21, 2026 7:27pm | Jul 22, 2026 7:14am | Jul 22, 2026 3:01pm | Jul 22, 2026 3:01pm | Jul 22, 2026 3:01pm | Jul 22, 2026 3:02pm | Jul 22, 2026 3:02pm | Jul 22, 2026 3:02pm | BrokenWire |  | Fair | No | Premises not found not getting customer on phone
Non-Outage | J.E.26.07.22645 | C001861375 | Richman Whyte | Westmoreland | Completed | Load_248554 | Paradise - 210 | Jul 21, 2026 7:22pm | Jul 21, 2026 7:23pm | Jul 21, 2026 8:13pm | Jul 21, 2026 8:13pm | Jul 21, 2026 8:13pm | Jul 21, 2026 8:13pm | Jul 21, 2026 8:14pm | Jul 21, 2026 8:14pm |  |  | Fair | No | Check and found okay problem was fixed from yesterday
Outage | J.E.26.07.24717 | C001861373 | Derrick Grubb | St.Thomas | Completed | Load_251564 | Good Year - 110 | Jul 21, 2026 7:09pm | Jul 22, 2026 7:58am | Jul 22, 2026 9:10am | Jul 22, 2026 9:10am | Jul 22, 2026 9:10am | Jul 22, 2026 9:23am | Jul 22, 2026 9:24am | Jul 22, 2026 9:24am |  |  | Fair | No | Premises found okay. Issue was a result of a outage in the area yesterday.
Outage | J.E.26.07.24726 | C001861372 | Hopeton Henry | St.Thomas | Completed | Load_242575 | Lysson - 410 | Jul 21, 2026 7:09pm | Jul 21, 2026 7:10pm | Jul 21, 2026 7:37pm | Jul 21, 2026 8:52pm | Jul 21, 2026 9:03pm | Jul 21, 2026 9:03pm | Jul 21, 2026 9:04pm | Jul 21, 2026 9:04pm |  |  | Fair | No | Customer confirmed the issue was resolved
Outage | J.E.26.07.24713 | C001861371 | Selvin White | St.Elizabeth | Completed | Load_239037 | Maggotty - 110 | Jul 21, 2026 7:03pm | Jul 21, 2026 7:03pm | Jul 21, 2026 7:28pm | Jul 21, 2026 7:57pm | Jul 21, 2026 8:10pm | Jul 21, 2026 8:39pm | Jul 21, 2026 8:39pm | Jul 21, 2026 8:39pm |  |  | Rains | No | Replace a blown 2 amp fuse for a 25 KVA transformer circuit at pole number 0116438 after clearing runner that was coming into contact with transformer primary drop lead. Supply restored to the affected customers.
Outage | J.E.26.07.24698 | C001861370 | Evan Spaulding | St.Mary | Completed | Load_268726 | Highgate -110 | Jul 21, 2026 7:02pm | Jul 22, 2026 7:42am | Jul 22, 2026 8:05am | Jul 22, 2026 8:05am | Jul 22, 2026 9:25am | Jul 22, 2026 9:37am | Jul 22, 2026 9:38am | Jul 22, 2026 9:38am |  |  | Fair | No | Defective meter socket,customer advised.
Outage | J.E.26.07.24723 | C001861365 | Edward Royal | KSAS | Completed | Load_1002678 | Cane River - 410 | Jul 21, 2026 6:55pm | Jul 21, 2026 7:03pm | Jul 21, 2026 7:13pm | Jul 21, 2026 10:09pm | Jul 21, 2026 10:09pm | Jul 21, 2026 10:11pm | Jul 21, 2026 10:11pm | Jul 21, 2026 10:11pm | Fire |  | Fair | No | Premises not found unable to communicate with customer
Non-Outage | J.E.26.07.24253 | C001861361 | Andre Williams | null | Completed | Load_241676 | null | Jul 21, 2026 6:50pm | Jul 21, 2026 6:51pm | Jul 21, 2026 7:12pm | Jul 21, 2026 7:12pm | Jul 21, 2026 7:38pm | Jul 21, 2026 8:56pm | Jul 21, 2026 8:37pm | Jul 21, 2026 8:37pm |  |  | Fair | No | Patrol 3phase line re fuse and close main 40 amp junction Fuse.
Non-Outage | J.E.26.07.23175 | C001861360 | Hopeton Henry | St.Thomas | Completed | Load_241688 | Lysson - 410 | Jul 21, 2026 6:47pm | Jul 21, 2026 7:10pm | Jul 21, 2026 7:37pm | Jul 21, 2026 8:40pm | Jul 21, 2026 8:41pm | Jul 21, 2026 8:50pm | Jul 21, 2026 8:52pm | Jul 21, 2026 8:52pm |  |  | Fair | No | Reconnect service at pole 116-114-230v
Outage | J.E.26.07.24704 | C001861358 | Romeo Brissett | St.James | Completed | Load_258788 | Bogue - 610 | Jul 21, 2026 6:36pm | Jul 22, 2026 8:41am | Jul 22, 2026 9:32am | Jul 22, 2026 10:57am | Jul 22, 2026 11:17am | Jul 22, 2026 11:17am | Jul 22, 2026 11:19am | Jul 22, 2026 11:19am |  |  | Fair | No | Replaced (1)25 kva transformer fuse.
Outage | J.E.26.07.24700 | C001861357 | Andre Williams | Trelawny | Completed | Load_292657 | Martha Brae - 210 | Jul 21, 2026 6:35pm | Jul 21, 2026 6:35pm | Jul 21, 2026 8:37pm | Jul 21, 2026 8:59pm | Jul 21, 2026 9:19pm | Jul 21, 2026 9:20pm | Jul 21, 2026 9:20pm | Jul 21, 2026 9:20pm |  |  | Fair | No | Premises found ok and with supply single phase was cause by outage earlier during the day
Outage | J.E.26.07.24451 | C001861353 | Roxroy Needham | St.Ann | Completed | Load_260645 | Cardiff Hall - 310 | Jul 21, 2026 6:32pm | Jul 21, 2026 6:33pm | Jul 21, 2026 8:54pm | Jul 21, 2026 8:54pm | Jul 21, 2026 9:26pm | Jul 21, 2026 10:36pm | Jul 21, 2026 10:51pm | Jul 21, 2026 10:51pm |  | Y | Fair | No | Change service wire used 80 ft of # 6 service wire 6 pg clamp voltage left at meter 113-112-218
Outage | J.E.26.07.24683 | C001861355 | Roxroy Needham | St.Ann | Completed | Load_258300 | Cardiff Hall - 310 | Jul 21, 2026 6:32pm | Jul 21, 2026 6:33pm | Jul 21, 2026 6:43pm | Jul 21, 2026 6:43pm | Jul 21, 2026 8:23pm | Jul 21, 2026 8:52pm | Jul 21, 2026 8:54pm | Jul 21, 2026 8:54pm |  | Y | Fair | No | Open a 25 KVA transformer at pole to repair a span of secondary neutral used 2 pg clamp
Outage | J.E.26.07.24040 | C001861351 | Eric Williams | KSAN | Completed | Load_301912 | Constant Spring - 210 | Jul 21, 2026 6:21pm | Jul 21, 2026 7:41pm | Jul 21, 2026 9:12pm | Jul 21, 2026 9:12pm | Jul 21, 2026 9:26pm | Jul 21, 2026 9:26pm | Jul 21, 2026 9:27pm | Jul 21, 2026 9:27pm |  |  | Fair | No | Defective meter, refer to field service department
Outage | J.E.26.07.24682 | C001861349 | Edward Royal | KSAS | Completed | Load_1003920 | Hunts Bay - 110 | Jul 21, 2026 6:11pm | Jul 21, 2026 6:17pm | Jul 21, 2026 7:13pm | Jul 21, 2026 7:17pm | Jul 21, 2026 7:17pm | Jul 21, 2026 7:18pm | Jul 21, 2026 7:18pm | Jul 21, 2026 7:18pm |  |  | Fair | No | Premises found ok related outage
Outage | J.E.26.07.24659 | C001861346 | Richard Samuda | Manchester | Completed | Load_257876 | Spur Tree - 310 | Jul 21, 2026 5:50pm | Jul 21, 2026 6:23pm | Jul 21, 2026 6:56pm | Jul 21, 2026 7:46pm | Jul 21, 2026 7:46pm | Jul 21, 2026 8:19pm | Jul 21, 2026 8:19pm | Jul 21, 2026 8:19pm | BrokenWire |  | Fair | No | Change corroded 1bolt clamp on secondary jumper that was brunt out causing customer to experience single phase voltage 118/120/238
Non-Outage | J.E.26.01.03462 | C001861344 | Andrew Powell | Manchester | Completed | Load_256206 | Spur Tree - 210 | Jul 21, 2026 5:48pm | Jul 21, 2026 5:48pm | Jul 21, 2026 6:02pm | Jul 21, 2026 6:02pm | Jul 21, 2026 6:02pm | Jul 21, 2026 6:02pm | Jul 21, 2026 6:02pm | Jul 21, 2026 6:02pm | BrokenWire |  | Fair | No | Manchester called.
Non-Outage | J.E.26.01.16199 | C001861342 | Andrew Powell | Manchester | Completed | Load_247501 | Spur Tree - 210 | Jul 21, 2026 5:46pm | Jul 21, 2026 5:47pm | Jul 21, 2026 7:09pm | Jul 21, 2026 7:09pm | Jul 21, 2026 7:35pm | Jul 21, 2026 7:40pm | Jul 21, 2026 7:42pm | Jul 21, 2026 7:42pm | BrokenPole |  | Fair | No | Found defective 35 class 6 T construction wooden pole with single phase primary and open wire secondary conductor attached, please refer to maintenance department for replacement.
Non-Outage | J.E.26.01.24557 | C001861343 | Andrew Powell | Manchester | Completed | Load_246559 | Spur Tree - 210 | Jul 21, 2026 5:46pm | Jul 21, 2026 5:47pm | Jul 21, 2026 7:42pm | Jul 21, 2026 7:42pm | Jul 21, 2026 7:48pm | Jul 21, 2026 7:49pm | Jul 21, 2026 7:49pm | Jul 21, 2026 7:49pm |  |  | Fair | No | Premises found okay customer stated that fault resolved supply restored.
Non-Outage | J.E.25.12.19505 | C001861340 | Andrew Powell | Manchester | Completed | Load_263480 | Spur Tree - 210 | Jul 21, 2026 5:44pm | Jul 21, 2026 5:44pm | Jul 21, 2026 6:25pm | Jul 21, 2026 6:27pm | Jul 21, 2026 7:07pm | Jul 21, 2026 7:08pm | Jul 21, 2026 7:08pm | Jul 21, 2026 7:08pm | BrokenPole |  | Fair | No | Premises found okay fault resolved.
Non-Outage | J.E.26.07.24421 | C001861334 | Andre Williams | Trelawny | Completed | Load_292776 | Greenwood - 210 | Jul 21, 2026 5:39pm | Jul 21, 2026 5:39pm | Jul 21, 2026 10:30pm | Jul 21, 2026 11:36pm | Jul 21, 2026 11:36pm | Jul 21, 2026 11:37pm | Jul 21, 2026 11:37pm | Jul 21, 2026 11:37pm |  |  | Fair | No | Day light attention needed, multiple illegal connection on line causing low voltage, 120+120=240 at transformer, 3 pole span from transformer line voltage 103+102=205 remove five illegal connection, voltage rose to 111+105 at the end where customer is 105+103=208 reffer to loses to rectify low voltage issue
Non-Outage | J.E.26.07.24642 | C001861336 | Richard Samuda | null | Completed | null | null | Jul 21, 2026 5:39pm | Jul 21, 2026 5:50pm | Jul 21, 2026 6:00pm | Jul 21, 2026 6:17pm | Jul 21, 2026 6:38pm | Jul 21, 2026 6:50pm | Jul 21, 2026 6:50pm | Jul 21, 2026 6:50pm |  |  | Fair | No | Customer was disconnected for bad death
Outage | J.E.26.07.24647 | C001861335 | Kenroy Dale | Manchester | Completed | Load_254691 | Porus - 310 | Jul 21, 2026 5:39pm | Jul 21, 2026 7:41pm | Jul 21, 2026 9:51pm | Jul 21, 2026 9:51pm | Jul 21, 2026 10:31pm | Jul 21, 2026 10:32pm | Jul 21, 2026 10:34pm | Jul 21, 2026 10:34pm |  |  | Fair | No | Blown 3 amp transformer fuse found. Line patrol nothing found, blown fuse was replaced and area now with supply
Non-Outage | J.E.26.07.24534 | C001861333 | Andre Williams | Trelawny | Completed | Load_292776 | Greenwood - 210 | Jul 21, 2026 5:38pm | Jul 21, 2026 5:38pm | Jul 21, 2026 9:20pm | Jul 21, 2026 9:21pm | Jul 21, 2026 11:31pm | Jul 21, 2026 11:35pm | Jul 21, 2026 11:36pm | Jul 21, 2026 11:36pm |  |  | Fair | No | Day light attention needed, multiple illegal connection on line causing low voltage, 120+120=240 at transformer, 3 pole span from transformer line voltage 103+102=205 remove five illegal connection, voltage rose to 111+105 at the end where customer is 105+103=208 reffer to loses to rectify low voltage issue
Non-Outage | J.E.26.03.00274 | C001861332 | Wayne Dillion | Manchester | Completed | Load_258714 | Spur Tree - 210 | Jul 21, 2026 5:35pm | Jul 22, 2026 3:55pm | Jul 22, 2026 4:51pm | Jul 22, 2026 4:51pm | Jul 22, 2026 4:51pm | Jul 22, 2026 4:55pm | Jul 22, 2026 4:55pm | Jul 22, 2026 4:55pm |  |  | Fair | No | Customer said it is the wrong contact and they didn’t make any report
Non-Outage | J.E.26.07.23573 | C001861331 | Cliton Henry | St.Mary | Completed | Load_262298 | Oracabessa - 210 | Jul 21, 2026 5:33pm | Jul 21, 2026 5:33pm | Jul 21, 2026 6:31pm | Jul 21, 2026 6:31pm | Jul 21, 2026 6:39pm | Jul 21, 2026 7:20pm | Jul 21, 2026 7:26pm | Jul 21, 2026 7:26pm |  |  | Fair | No | A broken service wire neutral and wrapped joint found at the customer pothead. Corrective work done to spliced and retention service wire neutral and reconnected joints using 3 one bolt clamps amd 2-#6-#2 pen unions. Voltages left 114-120/235 volts.
Outage | J.E.26.07.24646 | C001861330 | Eric Williams | KSAN | Completed | Load_245669 | Constant Spring - 210 | Jul 21, 2026 5:31pm | Jul 21, 2026 5:33pm | Jul 21, 2026 6:35pm | Jul 21, 2026 6:56pm | Jul 21, 2026 7:14pm | Jul 21, 2026 7:17pm | Jul 21, 2026 7:18pm | Jul 21, 2026 7:18pm |  |  | Fair | No | Premises found okay
Non-Outage | J.E.26.07.24203 | C001861327 | Richard Samuda | null | Completed | null | null | Jul 21, 2026 5:29pm | Jul 21, 2026 5:30pm | Jul 21, 2026 5:38pm | Jul 21, 2026 5:38pm | Jul 21, 2026 5:39pm | Jul 21, 2026 5:39pm | Jul 21, 2026 5:41pm | Jul 21, 2026 5:41pm | BrokenWire |  | EarthMovement | No | Situation was resolved
Outage | J.E.26.07.24472 | C001861325 | Michael Christian | St.James | Completed | Load_245248 | Queens Drive - 810 | Jul 21, 2026 5:29pm | Jul 21, 2026 5:31pm | Jul 21, 2026 7:11pm | Jul 21, 2026 7:11pm | Jul 21, 2026 8:15pm | Jul 21, 2026 8:22pm | Jul 21, 2026 8:22pm | Jul 21, 2026 8:22pm |  |  | Fair | No | Premises found located
Outage | J.E.26.07.24493 | C001861324 | Michael Christian | St.James | Completed | Load_260155 | Queens Drive - 710 | Jul 21, 2026 5:29pm | Jul 21, 2026 5:31pm | Jul 21, 2026 8:23pm | Jul 21, 2026 8:23pm | Jul 21, 2026 8:59pm | Jul 21, 2026 10:53pm | Jul 21, 2026 10:53pm | Jul 21, 2026 10:53pm |  |  | Fair | No | Internal fault
Outage | J.E.26.07.24559 | C001861326 | Shamour Haughton | St.James | Completed | Load_243551 | Bogue - 610 | Jul 21, 2026 5:29pm | Jul 21, 2026 5:31pm | Jul 21, 2026 7:15pm | Jul 21, 2026 7:15pm | Jul 21, 2026 8:47pm | Jul 21, 2026 9:38pm | Jul 21, 2026 9:56pm | Jul 21, 2026 9:56pm | BrokenWire |  | Fair | No | Found 3 pole span of secondary broken, isolate 25kva to splice and retention 3 pole span using 50ft of #2 conductor, 3clamps and 2#2 preform and reclose 25kva
Outage | J.E.26.07.24636 | C001861328 | Michael Christian | St.James | Completed | Load_256990 | Queens Drive - 710 | Jul 21, 2026 5:29pm | Jul 21, 2026 5:36pm | Jul 21, 2026 6:37pm | Jul 21, 2026 6:37pm | Jul 21, 2026 7:02pm | Jul 21, 2026 7:10pm | Jul 21, 2026 7:11pm | Jul 21, 2026 7:11pm | TreeContact |  | Fair | No | Check and found okay voltage 111 110 at pothead
Non-Outage | J.E.26.07.24429 | C001861321 | Dean Smith | null | Completed | null | null | Jul 21, 2026 5:24pm | Jul 21, 2026 5:25pm | Jul 21, 2026 7:08pm | Jul 21, 2026 7:08pm | Jul 21, 2026 8:57pm | Jul 21, 2026 8:57pm | Jul 21, 2026 8:58pm | Jul 21, 2026 8:58pm | Fire |  | Rains | No | Area was restored
Outage | J.E.26.07.24266 | C001861320 | Jermaine Williams | St.Catherine | Completed | Load_567903 | Rhodens Pen - 310 | Jul 21, 2026 5:22pm | Jul 21, 2026 5:22pm | Jul 21, 2026 7:40pm | Jul 21, 2026 7:41pm | Jul 21, 2026 9:55pm | Jul 21, 2026 8:44pm | Jul 21, 2026 9:56pm | Jul 21, 2026 9:56pm |  |  | Fair | No | Premises not located.
Non-Outage | J.E.26.07.24349 | C001861319 | Christopher Edwards | null | Completed | null | null | Jul 21, 2026 5:21pm | Jul 21, 2026 11:22pm | Jul 21, 2026 11:26pm | Jul 21, 2026 11:40pm | Jul 21, 2026 11:40pm | Jul 21, 2026 11:40pm | Jul 21, 2026 11:40pm | Jul 21, 2026 11:40pm |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Non-Outage | J.E.26.07.24517 | C001861315 | Oshane Warren | null | Completed | null | null | Jul 21, 2026 5:20pm | Jul 21, 2026 5:20pm | Jul 21, 2026 7:52pm | Jul 21, 2026 7:52pm | Jul 21, 2026 7:52pm | Jul 21, 2026 7:52pm | Jul 21, 2026 7:53pm | Jul 21, 2026 7:53pm | BrokenWire |  | Rains | No | St James call
Outage | J.E.26.07.24639 | C001861316 | Edward Royal | KSAS | Completed | Load_261859 | Hunts Bay - 210 | Jul 21, 2026 5:20pm | Jul 21, 2026 5:23pm | Jul 21, 2026 7:13pm | Jul 21, 2026 7:18pm | Jul 21, 2026 7:18pm | Jul 21, 2026 7:18pm | Jul 21, 2026 7:19pm | Jul 21, 2026 7:19pm |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.07.24637 | C001861314 | Kaydon Taylor | KSAN | Completed | Load_248491 | Constant Spring - 410 | Jul 21, 2026 5:18pm | Jul 21, 2026 5:20pm | Jul 21, 2026 8:14pm | Jul 21, 2026 8:14pm | Jul 21, 2026 9:35pm | Jul 21, 2026 10:37pm | Jul 21, 2026 10:37pm | Jul 21, 2026 10:37pm |  |  | Fair | No | Internal problem
Outage | J.E.26.07.24499 | C001861311 | Dean Smith | Hanover | Completed | Load_268094 | Orange Bay - 310 | Jul 21, 2026 5:16pm | Jul 21, 2026 5:16pm | Jul 21, 2026 8:58pm | Jul 21, 2026 8:58pm | Jul 21, 2026 9:51pm | Jul 21, 2026 9:51pm | Jul 21, 2026 10:15pm | Jul 21, 2026 10:15pm |  |  | Rains | No | Replace 8amp junction fuse. Pole number n/a
Outage | J.E.26.07.24279 | C001861309 | Christopher Edwards | KSAN | Completed | Load_241329 | Constant Spring - 410 | Jul 21, 2026 5:14pm | Jul 22, 2026 8:01am | Jul 22, 2026 12:24pm | Jul 22, 2026 12:24pm | Jul 22, 2026 1:17pm | Jul 22, 2026 2:09pm | Jul 22, 2026 2:10pm | Jul 22, 2026 2:10pm |  |  | Fair | No | Customer is having an internal issue Customer was advised to get electrician to rectify issue
Outage | J.E.26.07.24626 | C001861308 | Edward Royal | KSAS | Completed | Load_266567 | Up Park Camp - 310 | Jul 21, 2026 5:11pm | Jul 21, 2026 9:11pm | Jul 21, 2026 9:18pm | Jul 21, 2026 9:18pm | Jul 21, 2026 9:45pm | Jul 21, 2026 10:03pm | Jul 21, 2026 10:03pm | Jul 21, 2026 10:03pm |  |  | Fair | No | Requesting secondary bushing crew tree grow up in secondary line and in customer service with affect there supply tree need to be cut urgently so customer can get back supply
Outage | J.E.26.07.24628 | C001861303 | Oshane Warren | Westmoreland | Completed | Load_245673 | Paradise - 310 | Jul 21, 2026 5:09pm | Jul 21, 2026 5:18pm | Jul 21, 2026 7:54pm | Jul 21, 2026 7:54pm | Jul 21, 2026 7:55pm | Jul 21, 2026 7:55pm | Jul 21, 2026 7:56pm | Jul 21, 2026 7:56pm |  |  | Rains | No | Check and found okay
Outage | J.E.26.07.24445 | C001861301 | Andre Williams | Trelawny | Completed | Load_267562 | Duncans - 210 | Jul 21, 2026 5:08pm | Jul 21, 2026 5:08pm | Jul 21, 2026 5:23pm | Jul 21, 2026 5:28pm | Jul 21, 2026 5:28pm | Jul 21, 2026 5:28pm | Jul 21, 2026 5:29pm | Jul 21, 2026 5:29pm |  |  | Fair | No | Premises ok and with supply confirm by call
Outage | J.E.26.07.24552 | C001861302 | Richman Whyte | Westmoreland | Completed | Load_259530 | Paradise - 110 | Jul 21, 2026 5:08pm | Jul 21, 2026 5:19pm | Jul 21, 2026 7:39pm | Jul 21, 2026 7:39pm | Jul 21, 2026 7:39pm | Jul 21, 2026 7:39pm | Jul 21, 2026 7:41pm | Jul 21, 2026 7:41pm |  |  | Fair | No | Customer have internal problem advise to fix customer hasn’t made any repairs to pothead
Outage | J.E.26.07.24605 | C001861300 | Andre Williams | Trelawny | Completed | Load_302817 | Duncans - 110 | Jul 21, 2026 5:08pm | Jul 21, 2026 5:08pm | Jul 21, 2026 5:29pm | Jul 21, 2026 5:42pm | Jul 21, 2026 6:14pm | Jul 21, 2026 7:02pm | Jul 21, 2026 7:07pm | Jul 21, 2026 7:07pm | BrokenPole |  | Fair | No | Replace burnt #6 and #2 wire that was splice to gather with #6 conductor reffer to field service to upgrade back to # 2 , total wire lengthy roughly 50:ft total wire length, ( total length of wire is between the #2 and #6 that was there before ) voltage 113+115=228
Non-Outage | J.E.26.07.24424 | C001861298 | Kenroy Dale | null | Completed | null | null | Jul 21, 2026 5:07pm | Jul 21, 2026 5:07pm | Jul 21, 2026 5:22pm | Jul 21, 2026 5:22pm | Jul 21, 2026 5:22pm | Jul 21, 2026 9:48pm | Jul 21, 2026 9:51pm | Jul 21, 2026 9:51pm | BrokenPole |  | Fair | No | Opened 25 amp junction fuse to float primary conductor off broken post caused by vehicle accident, area was de-bushed in order for conductor to be floated. Conductor was floated and junction re-closed, area now with supply
Outage | J.E.26.07.24528 | C001861293 | Rayon Foster | Hanover | Completed | Load_258239 | Orange Bay - 210 | Jul 21, 2026 5:05pm | Jul 21, 2026 5:22pm | Jul 21, 2026 6:18pm | Jul 21, 2026 6:18pm | Jul 21, 2026 7:18pm | Jul 21, 2026 8:56pm | Jul 21, 2026 8:56pm | Jul 21, 2026 8:56pm |  |  | Fair | No | Found working ok Voltage check at transformer pole 116/116AB232volts meter room close issue suspected in meter room witch is close day time checks neededto complete tomorrow
Outage | J.E.26.07.24350 | C001861289 | Richard Samuda | Manchester | Completed | Load_237916 | Spur Tree - 310 | Jul 21, 2026 5:01pm | Jul 21, 2026 5:01pm | Jul 21, 2026 5:26pm | Jul 21, 2026 5:26pm | Jul 21, 2026 5:26pm | Jul 21, 2026 5:26pm | Jul 21, 2026 5:27pm | Jul 21, 2026 5:27pm | Fire |  | Fair | No | Situation was resolved
Outage | J.E.26.07.24592 | C001861288 | Richard Samuda | Manchester | Completed | Load_265753 | Spur Tree - 310 | Jul 21, 2026 5:01pm | Jul 21, 2026 5:01pm | Jul 21, 2026 5:51pm | Jul 21, 2026 5:51pm | Jul 21, 2026 5:55pm | Jul 21, 2026 5:57pm | Jul 21, 2026 5:57pm | Jul 21, 2026 5:57pm |  |  | Fair | No | Customer say supply was restored
Non-Outage | J.E.26.07.24583 | C001861275 | Milton Charlton | KSAN | Completed | Load_258324 | Hope - 510 | Jul 21, 2026 4:35pm | Jul 21, 2026 4:38pm | Jul 21, 2026 5:24pm | Jul 21, 2026 5:24pm | Jul 21, 2026 5:24pm | Jul 21, 2026 5:20pm | Jul 21, 2026 5:26pm | Jul 21, 2026 5:26pm |  |  | Fair | No | Call related to call at 237 Old Hope Road.
Outage | J.E.26.07.24561 | C001861272 | Milton Charlton | KSAN | Completed | Load_243040 | Washington Blvd - 310 | Jul 21, 2026 4:32pm | Jul 22, 2026 8:32am | Jul 22, 2026 8:57am | Jul 22, 2026 8:59am | Jul 22, 2026 10:16am | Jul 22, 2026 9:55am | Jul 22, 2026 10:18am | Jul 22, 2026 10:18am |  |  | Fair | No | Found okay upon arrival. Customer has an internal problem.
Outage | J.E.26.07.24580 | C001861274 | Selvin White | St.Elizabeth | Completed | Load_254094 | Maggotty - 110 | Jul 21, 2026 4:32pm | Jul 21, 2026 4:37pm | Jul 21, 2026 7:28pm | Jul 21, 2026 8:40pm | Jul 21, 2026 9:31pm | Jul 21, 2026 10:22pm | Jul 21, 2026 10:22pm | Jul 21, 2026 10:22pm |  |  | Rains | No | Replace a blown 10 amp junction fuse at pole number 0111609 after patrolling single phase primary line. Also replace a 1 amp fuse for a 10 KVA transformer circuit with no pole number at location. Supply restored to the affected customers including the digicel cell site.
Outage | J.E.26.07.24544 | C001861271 | Hopeton Henry | St.Thomas | Completed | Load_268474 | Good Year - 210 | Jul 21, 2026 4:31pm | Jul 21, 2026 4:33pm | Jul 21, 2026 7:37pm | Jul 21, 2026 9:04pm | Jul 21, 2026 11:02pm | Jul 21, 2026 11:03pm | Jul 21, 2026 11:03pm | Jul 21, 2026 11:03pm |  |  | Fair | No | Check and found ok
Outage | J.E.26.07.24422 | C001861262 | Richman Whyte | Westmoreland | Completed | Load_266673 | Paradise - 110 | Jul 21, 2026 4:22pm | Jul 21, 2026 5:22pm | Jul 21, 2026 5:51pm | Jul 21, 2026 5:51pm | Jul 21, 2026 7:00pm | Jul 21, 2026 7:30pm | Jul 21, 2026 7:31pm | Jul 21, 2026 7:31pm | BrokenWire |  | Rains | No | Open twenty five kva transformer fuse and repair and retention three span open secondary conductor use two one bolt clamps voltage 115 115 230
Outage | J.E.26.07.24426 | C001861263 | Richman Whyte | Westmoreland | Completed | Load_258782 | Paradise - 110 | Jul 21, 2026 4:22pm | Jul 21, 2026 5:22pm | Jul 21, 2026 8:15pm | Jul 21, 2026 8:15pm | Jul 21, 2026 8:15pm | Jul 21, 2026 8:15pm | Jul 21, 2026 8:17pm | Jul 21, 2026 8:17pm | BrokenWire |  | Fair | No | Restore earlier related to the compbellton call
Outage | J.E.26.07.24498 | C001861261 | Selvin White | St.Elizabeth | Completed | Load_574151 | Maggotty - 110 | Jul 21, 2026 4:21pm | Jul 21, 2026 4:27pm | Jul 21, 2026 7:28pm | Jul 21, 2026 10:24pm | Jul 21, 2026 10:34pm | Jul 21, 2026 10:39pm | Jul 21, 2026 10:40pm | Jul 21, 2026 10:40pm |  |  | Rains | No | Please refer to C Johnson and Simone Bicarie at the field service department so premises can be checked thoroughly during the day as call is hurricane related.
Outage | J.E.26.07.24547 | C001861257 | Andre Williams | Trelawny | Completed | Load_1001476 | Martha Brae - 210 | Jul 21, 2026 4:18pm | Jul 21, 2026 4:19pm | Jul 21, 2026 5:19pm | Jul 21, 2026 5:21pm | Jul 21, 2026 5:21pm | Jul 21, 2026 5:22pm | Jul 21, 2026 5:22pm | Jul 21, 2026 5:22pm |  |  | Fair | No | Premises found ok upon visit call related to earlier outage
Non-Outage | J.E.26.07.24372 | C001861253 | Milton Charlton | KSAN | Completed | Load_253447 | Hope - 510 | Jul 21, 2026 4:13pm | Jul 21, 2026 4:14pm | Jul 21, 2026 6:08pm | Jul 21, 2026 6:08pm | Jul 21, 2026 6:08pm | Jul 21, 2026 5:20pm | Jul 21, 2026 6:10pm | Jul 21, 2026 6:10pm |  |  | Fair | No | Call duplicated..
Non-Outage | J.E.26.07.21692 | C001861250 | Edward Royal | KSAS | Completed | Load_1002929 | Hunts Bay - 810 | Jul 21, 2026 4:11pm | Jul 21, 2026 4:13pm | Jul 21, 2026 7:13pm | Jul 21, 2026 8:18pm | Jul 21, 2026 8:18pm | Jul 21, 2026 8:18pm | Jul 21, 2026 8:18pm | Jul 21, 2026 8:18pm | BrokenWire |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.07.24278 | C001861252 | Daniel Francis | null | Completed | null | null | Jul 21, 2026 4:11pm | Jul 21, 2026 4:12pm | Jul 21, 2026 4:45pm | Jul 21, 2026 4:45pm | Jul 21, 2026 5:02pm | Jul 21, 2026 5:23pm | Jul 21, 2026 5:26pm | Jul 21, 2026 5:26pm |  |  | Fair | No | Found palm branch resting close to JPS primary line remove
Non-Outage | J.E.26.07.24501 | C001861251 | Eric Williams | KSAN | Completed | Load_251827 | Washington Blvd - 810 | Jul 21, 2026 4:11pm | Jul 21, 2026 4:12pm | Jul 21, 2026 7:18pm | Jul 21, 2026 7:18pm | Jul 21, 2026 8:49pm | Jul 21, 2026 9:11pm | Jul 21, 2026 9:12pm | Jul 21, 2026 9:12pm | BrokenWire |  | Fair | No | Premises found okay, cable wires not JPS wires
Non-Outage | J.E.26.07.24432 | C001861244 | Edward Royal | KSAS | Completed | Load_293995 | Hunts Bay - 510 | Jul 21, 2026 4:10pm | Jul 21, 2026 5:40pm | Jul 21, 2026 7:13pm | Jul 21, 2026 8:18pm | Jul 21, 2026 8:18pm | Jul 21, 2026 8:19pm | Jul 21, 2026 8:19pm | Jul 21, 2026 8:19pm |  |  | Fair | No | When contacted customer said that no one is at the premises at these hours
Outage | J.E.26.07.24116 | C001861242 | Daniel Francis | St.Ann | Completed | Load_246497 | Roaring River - 210 | Jul 21, 2026 4:10pm | Jul 21, 2026 4:12pm | Jul 21, 2026 5:26pm | Jul 21, 2026 5:26pm | Jul 21, 2026 6:30pm | Jul 21, 2026 6:40pm | Jul 21, 2026 6:42pm | Jul 21, 2026 6:42pm |  |  | Fair | No | Open all 3 25kva transformer pole # 038661 as requested by nwc
Outage | J.E.26.07.24523 | C001861243 | Daniel Francis | St.Ann | Completed | Load_241596 | Roaring River - 210 | Jul 21, 2026 4:10pm | Jul 21, 2026 4:12pm | Jul 21, 2026 6:48pm | Jul 21, 2026 6:48pm | Jul 21, 2026 6:48pm | Jul 21, 2026 6:50pm | Jul 21, 2026 6:51pm | Jul 21, 2026 6:51pm |  |  | Fair | No | We this # and the customer say she did not make a report
Non-Outage | J.E.26.07.24509 | C001861240 | Cliton Henry | null | Completed | null | null | Jul 21, 2026 4:06pm | Jul 21, 2026 4:06pm | Jul 21, 2026 5:01pm | Jul 21, 2026 5:18pm | Jul 21, 2026 5:18pm | Jul 21, 2026 5:23pm | Jul 21, 2026 5:23pm | Jul 21, 2026 5:23pm |  |  | Fair | No | The customer contact number provided went unanswered, There insufficient information to locate the customer.
Outage | J.E.26.07.24522 | C001861238 | Cliton Henry | St.Mary | Completed | Load_249140 | Oracabessa - 210 | Jul 21, 2026 4:06pm | Jul 21, 2026 4:06pm | Jul 21, 2026 5:01pm | Jul 21, 2026 5:01pm | Jul 21, 2026 5:06pm | Jul 21, 2026 5:08pm | Jul 21, 2026 5:09pm | Jul 21, 2026 5:09pm |  |  | Fair | No | The customer stated the the supply was restored a few minutes after he made the report
Non-Outage | J.E.26.07.24483 | C001861234 | Rodclif Dawkins | Portmore | Completed | Load_557212 | Naggo Head - 610 | Jul 21, 2026 4:05pm | Jul 21, 2026 4:06pm | null | Jul 21, 2026 5:24pm | Jul 21, 2026 6:12pm | Jul 21, 2026 6:33pm | Jul 21, 2026 6:36pm | Jul 21, 2026 6:36pm |  |  | Fair | No | Found blown fuse from lightning transformer,from bank of 3. No defects observed at time of visit. Found and replaced 3amp fuse.
Outage | J.E.26.07.24458 | C001861233 | Eric Williams | KSAN | Completed | Load_579165 | Constant Spring - 210 | Jul 21, 2026 4:05pm | Jul 21, 2026 5:12pm | Jul 21, 2026 6:30pm | Jul 21, 2026 6:36pm | Jul 21, 2026 6:54pm | Jul 21, 2026 6:56pm | Jul 21, 2026 6:56pm | Jul 21, 2026 6:56pm | Fire |  | Fair | No | Premises found okay
Non-Outage | J.E.26.07.24327 | C001861225 | Cliton Henry | null | Completed | null | null | Jul 21, 2026 3:57pm | Jul 21, 2026 4:07pm | Jul 21, 2026 5:01pm | Jul 21, 2026 5:30pm | Jul 21, 2026 5:30pm | Jul 21, 2026 5:37pm | Jul 21, 2026 5:37pm | Jul 21, 2026 5:37pm |  |  | Fair | No | The customer contact number provided went unanswered. This report need a proper direction.
Outage | J.E.26.07.24412 | C001861222 | Selvin White | St.Elizabeth | Completed | Load_264265 | Maggotty - 210 | Jul 21, 2026 3:54pm | Jul 21, 2026 3:55pm | Jul 21, 2026 4:01pm | Jul 21, 2026 4:01pm | Jul 21, 2026 4:18pm | Jul 21, 2026 6:54pm | Jul 21, 2026 6:57pm | Jul 21, 2026 6:57pm |  |  | Rains | No | Isolate drop out switches in order to remade burnt off connection at switch bottom. Supply restored to the affected customers.
Outage | J.E.26.07.24454 | C001861221 | Edward Royal | null | Completed | Load_1003930 | Hunts Bay - 710 | Jul 21, 2026 3:53pm | Jul 21, 2026 3:54pm | Jul 21, 2026 7:13pm | Jul 21, 2026 7:19pm | Jul 21, 2026 7:31pm | Jul 21, 2026 8:17pm | Jul 21, 2026 8:17pm | Jul 21, 2026 8:17pm |  |  | Fair | No | Jps was doing some work and switch the feeder to hunts bay that where the low voltage coming from jps team is notified about the issue
Outage | J.E.26.07.22445 | C001861212 | Rodclif Dawkins | Portmore | Completed | Load_266899 | Naggo Head - 510 | Jul 21, 2026 3:44pm | Jul 21, 2026 3:44pm | null | Jul 21, 2026 6:37pm | Jul 21, 2026 7:21pm | Jul 21, 2026 7:21pm | Jul 21, 2026 7:22pm | Jul 21, 2026 7:22pm |  |  | Fair | No | Customer not found, calls to number provided went unanswered. GPS was incorrect
Outage | J.E.26.07.21212 | C001861211 | Rodclif Dawkins | Portmore | Completed | Load_557214 | Naggo Head - 610 | Jul 21, 2026 3:43pm | Jul 21, 2026 3:44pm | null | Jul 21, 2026 8:40pm | Jul 21, 2026 9:10pm | Jul 21, 2026 9:10pm | Jul 21, 2026 9:23pm | Jul 21, 2026 9:23pm |  |  | Fair | No | Customer found okay
Outage | J.E.26.07.24237 | C001861208 | Edward Royal | KSAS | Completed | Load_242370 | Greenwich - 710 | Jul 21, 2026 3:43pm | Jul 21, 2026 3:54pm | Jul 21, 2026 7:13pm | Jul 21, 2026 8:48pm | Jul 21, 2026 8:48pm | Jul 21, 2026 9:08pm | Jul 21, 2026 9:08pm | Jul 21, 2026 9:08pm |  |  | Fair | No | Customer have internal problems customer have defective stanchion pole advise customer to get a electrician to fix the problem customer was disconnected truck pass a tore down customer service line and stanchion pole
Outage | J.E.26.07.24325 | C001861209 | Edward Royal | KSAS | Completed | Load_574063 | Cane River - 410 | Jul 21, 2026 3:43pm | Jul 21, 2026 3:54pm | Jul 21, 2026 7:13pm | Jul 21, 2026 8:36pm | Jul 21, 2026 8:36pm | Jul 21, 2026 8:46pm | Jul 21, 2026 8:48pm | Jul 21, 2026 8:48pm |  |  | Fair | No | Contact customer by phone customer said the power was restored
Outage | J.E.26.07.24196 | C001861207 | Edward Royal | KSAS | Completed | Load_251755 | Rockfort - 410 | Jul 21, 2026 3:42pm | Jul 21, 2026 3:54pm | Jul 21, 2026 7:13pm | Jul 21, 2026 8:30pm | Jul 21, 2026 8:30pm | Jul 21, 2026 8:32pm | Jul 21, 2026 8:32pm | Jul 21, 2026 8:32pm |  |  | Fair | No | Contact customer by phone customer said the power was restored
Outage | J.E.26.07.24416 | C001861206 | Eric Williams | KSAS | Completed | Load_265991 | Greenwich - 710 | Jul 21, 2026 3:42pm | Jul 21, 2026 4:10pm | Jul 21, 2026 5:37pm | Jul 21, 2026 5:37pm | Jul 21, 2026 6:09pm | Jul 21, 2026 6:09pm | Jul 21, 2026 6:10pm | Jul 21, 2026 6:10pm |  |  | Fair | No | Premises found okay
Non-Outage | J.E.26.07.20874 | C001861202 | Donald Cunningham | St.Catherine | Completed | Load_253874 | New Michelton - 210 | Jul 21, 2026 3:41pm | Jul 21, 2026 3:41pm | Jul 21, 2026 3:46pm | Jul 21, 2026 3:46pm | Jul 21, 2026 5:40pm | Jul 21, 2026 5:40pm | Jul 21, 2026 5:43pm | Jul 21, 2026 5:43pm |  |  | Fair | No | Sub station issues transformer need to replace that I was told by the person that made the report by the plant
Non-Outage | J.E.26.07.22053 | C001861200 | Donald Cunningham | St.Catherine | Completed | Load_568233 | New Michelton - 210 | Jul 21, 2026 3:40pm | Jul 21, 2026 3:40pm | Jul 21, 2026 6:50pm | Jul 21, 2026 6:50pm | Jul 21, 2026 7:21pm | Jul 21, 2026 7:21pm | Jul 21, 2026 7:23pm | Jul 21, 2026 7:23pm |  |  | Fair | No | Premises closed
Non-Outage | J.E.26.07.22157 | C001861201 | Donald Cunningham | St.Catherine | Completed | Load_242607 | New Michelton - 210 | Jul 21, 2026 3:40pm | Jul 21, 2026 3:40pm | Jul 21, 2026 9:05pm | Jul 21, 2026 9:05pm | Jul 21, 2026 9:39pm | Jul 21, 2026 9:40pm | Jul 21, 2026 9:50pm | Jul 21, 2026 9:50pm |  |  | Fair | No | Premises not located customer not reachable
Non-Outage | J.E.26.07.22466 | C001861198 | Donald Cunningham | St.Catherine | Completed | Load_258753 | New Michelton - 210 | Jul 21, 2026 3:40pm | Jul 21, 2026 3:40pm | Jul 21, 2026 7:24pm | Jul 21, 2026 7:24pm | Jul 21, 2026 8:40pm | Jul 21, 2026 9:04pm | Jul 21, 2026 9:05pm | Jul 21, 2026 9:05pm |  |  | Fair | No | Premises closed
Non-Outage | J.E.26.07.22563 | C001861199 | Donald Cunningham | St.Catherine | Completed | Load_568233 | New Michelton - 210 | Jul 21, 2026 3:40pm | Jul 21, 2026 3:40pm | Jul 21, 2026 5:44pm | Jul 21, 2026 5:44pm | Jul 21, 2026 6:41pm | Jul 21, 2026 6:42pm | Jul 21, 2026 6:50pm | Jul 21, 2026 6:50pm |  |  | Fair | No | Issues already resolved
Outage | J.E.26.07.24340 | C001861197 | Hopeton Henry | St.Thomas | Completed | Load_251845 | Lysson - 410 | Jul 21, 2026 3:36pm | Jul 21, 2026 3:42pm | Jul 21, 2026 7:37pm | Jul 21, 2026 7:39pm | Jul 21, 2026 7:51pm | Jul 21, 2026 8:40pm | Jul 21, 2026 8:40pm | Jul 21, 2026 8:40pm |  |  | Fair | No | Found disconnected for nonpayment
Outage | J.E.26.07.24413 | C001861196 | Rayon Foster | Hanover | Completed | Load_568371 | Orange Bay - 210 | Jul 21, 2026 3:36pm | Jul 21, 2026 5:23pm | Jul 21, 2026 8:56pm | Jul 21, 2026 8:57pm | Jul 21, 2026 9:32pm | Jul 21, 2026 9:53pm | Jul 21, 2026 9:54pm | Jul 21, 2026 9:54pm |  |  | Fair | No | Patrol primary line to find one blow 10 amps junction fuse blown line was safe to close replace with same and close
Non-Outage | J.E.26.07.24395 | C001861185 | Milton Charlton | null | Completed | null | null | Jul 21, 2026 3:33pm | Jul 21, 2026 3:42pm | Jul 21, 2026 5:20pm | Jul 21, 2026 5:20pm | Jul 21, 2026 5:20pm | Jul 21, 2026 5:20pm | Jul 21, 2026 5:23pm | Jul 21, 2026 5:23pm |  |  | Fair | No | Refused and reclosed two80amps junction at pole #( no pole#) using two 80 amps fuses and reclosed junction switches.
Outage | J.E.26.07.24250 | C001861183 | Andre Williams | Trelawny | Completed | Load_1001462 | null | Jul 21, 2026 3:31pm | Jul 21, 2026 3:31pm | Jul 21, 2026 4:48pm | Jul 21, 2026 4:53pm | Jul 21, 2026 4:54pm | Jul 21, 2026 4:54pm | Jul 21, 2026 4:55pm | Jul 21, 2026 4:55pm |  |  | Fair | No | Customer says they are not in Granville they are in Sherwood and with supply
Outage | J.E.26.07.22039 | C001861175 | Ricky Hall | St.Catherine | Completed | Load_268625 | Rhodens Pen - 210 | Jul 21, 2026 3:27pm | Jul 21, 2026 3:28pm | Jul 21, 2026 4:18pm | Jul 21, 2026 4:18pm | Jul 21, 2026 5:17pm | Jul 21, 2026 5:40pm | Jul 21, 2026 5:41pm | Jul 21, 2026 5:41pm |  |  | Fair | No | Install 3 w service use 100’#6/ triplex 3 clamps 3 pen union 118/116/233
Outage | J.E.26.07.22327 | C001861176 | Ricky Hall | St.Catherine | Completed | Load_259647 | Rhodens Pen - 410 | Jul 21, 2026 3:27pm | Jul 21, 2026 3:28pm | Jul 21, 2026 7:04pm | Jul 21, 2026 7:05pm | Jul 21, 2026 8:22pm | Jul 21, 2026 9:01pm | Jul 21, 2026 9:01pm | Jul 21, 2026 9:01pm |  |  | Fair | No
Outage | J.E.26.07.22328 | C001861177 | Ricky Hall | St.Catherine | Completed | Load_263631 | Rhodens Pen - 410 | Jul 21, 2026 3:27pm | Jul 21, 2026 3:28pm | Jul 21, 2026 6:30pm | Jul 21, 2026 6:31pm | Jul 21, 2026 6:57pm | Jul 21, 2026 7:04pm | Jul 21, 2026 7:04pm | Jul 21, 2026 7:04pm |  |  | Fair | No | Issue was resolved on previous shift
Outage | J.E.26.07.22755 | C001861174 | Ricky Hall | St.Catherine | Completed | Load_243118 | Rhodens Pen - 410 | Jul 21, 2026 3:27pm | Jul 21, 2026 3:28pm | Jul 21, 2026 5:26pm | Jul 21, 2026 5:41pm | Jul 21, 2026 5:53pm | Jul 21, 2026 6:29pm | Jul 21, 2026 6:30pm | Jul 21, 2026 6:30pm |  |  | Fair | No | Clean and reconnect (4)3W service at pothead use 2 clamps 119/119/238
Outage | J.E.26.07.24299 | C001861173 | Dean Smith | Hanover | Completed | Load_261071 | Orange Bay - 310 | Jul 21, 2026 3:27pm | Jul 21, 2026 3:27pm | Jul 21, 2026 6:58pm | Jul 21, 2026 10:15pm | Jul 21, 2026 10:43pm | Jul 21, 2026 10:43pm | Jul 21, 2026 10:44pm | Jul 21, 2026 10:44pm | Fire |  | Rains | No | Check and found ok.
Outage | J.E.26.07.23941 | C001861163 | Neville Spencer | Clarendon | Completed | Load_237777 | Parnassus - 310 | Jul 21, 2026 3:21pm | Jul 22, 2026 7:50am | Jul 22, 2026 8:04am | Jul 22, 2026 8:04am | Jul 22, 2026 8:13am | Jul 22, 2026 8:16am | Jul 22, 2026 8:16am | Jul 22, 2026 8:16am |  |  | Fair | No | Found supply at location.
Outage | J.E.26.07.23966 | C001861156 | Moses Elliston | St.Catherine | Completed | Load_256848 | Tredegar - 510 | Jul 21, 2026 3:20pm | Jul 21, 2026 3:20pm | Jul 21, 2026 3:52pm | Jul 21, 2026 3:52pm | Jul 21, 2026 3:52pm | Jul 21, 2026 3:53pm | Jul 21, 2026 3:53pm | Jul 21, 2026 3:53pm |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.07.24034 | C001861158 | Jermaine Williams | Clarendon | Completed | Load_256205 | May Pen - 210 | Jul 21, 2026 3:20pm | Jul 21, 2026 3:24pm | Jul 21, 2026 9:57pm | Jul 21, 2026 9:57pm | Jul 21, 2026 9:57pm | Jul 21, 2026 9:57pm | Jul 22, 2026 4:42pm | Jul 22, 2026 4:42pm |  |  | Fair | No | Premises found ok.
Outage | J.E.26.07.23721 | C001861155 | Marlon Authors | St.Elizabeth | Completed | Load_245938 | Maggotty - 110 | Jul 21, 2026 3:19pm | Jul 21, 2026 3:20pm | Jul 21, 2026 10:20pm | Jul 21, 2026 10:20pm | Jul 21, 2026 10:20pm | Jul 21, 2026 10:30pm | Jul 21, 2026 10:30pm | Jul 21, 2026 10:30pm | BrokenPole |  | Fair | No | Unable to locate and the customer not answering the phone
Outage | J.E.26.07.24217 | C001861154 | Jermaine Williams | Clarendon | Completed | Load_266996 | Monymusk - 210 | Jul 21, 2026 3:19pm | Jul 21, 2026 3:24pm | Jul 21, 2026 7:08pm | Jul 21, 2026 7:08pm | Jul 21, 2026 7:38pm | Jul 21, 2026 7:45pm | Jul 21, 2026 7:39pm | Jul 21, 2026 7:39pm |  |  | LandSlide | No | Repair defective service wire using 10’ #6 triplex.
Non-Outage | J.E.26.02.45210 | C001861152 | Andrew Powell | St.Elizabeth | Completed | Load_242601 | Maggotty - 210 | Jul 21, 2026 3:16pm | Jul 21, 2026 3:17pm | Jul 21, 2026 3:24pm | Jul 21, 2026 3:26pm | Jul 21, 2026 3:32pm | Jul 21, 2026 3:33pm | Jul 21, 2026 3:33pm | Jul 21, 2026 3:33pm |  |  | Fair | No | Premises found okay customer stated that fault resolved supply restored.
Non-Outage | J.E.26.02.03170 | C001861144 | Andrew Powell | St.Elizabeth | Completed | Load_246111 | Maggotty - 210 | Jul 21, 2026 3:15pm | Jul 21, 2026 3:15pm | Jul 21, 2026 3:19pm | Jul 21, 2026 3:22pm | Jul 21, 2026 3:22pm | Jul 21, 2026 3:23pm | Jul 21, 2026 3:23pm | Jul 21, 2026 3:23pm |  |  | Fair | No | Premises found okay customer stated that fault resolved supply restored.
Outage | J.E.26.07.23690 | C001861142 | Shamour Haughton | St.James | Completed | Load_249633 | Bogue - 610 | Jul 21, 2026 3:15pm | Jul 21, 2026 3:16pm | Jul 21, 2026 4:44pm | Jul 21, 2026 4:44pm | Jul 21, 2026 6:16pm | Jul 21, 2026 6:26pm | Jul 21, 2026 6:27pm | Jul 21, 2026 6:27pm |  |  | Fair | No | Need 110 ft of #6 triplex please refer to field service
Outage | J.E.26.07.24024 | C001861140 | Michael Christian | St.James | Completed | Load_268435 | Queens Drive - 710 | Jul 21, 2026 3:15pm | Jul 21, 2026 3:15pm | Jul 21, 2026 3:42pm | Jul 21, 2026 3:42pm | Jul 21, 2026 4:34pm | Jul 21, 2026 4:41pm | Jul 21, 2026 4:41pm | Jul 21, 2026 4:41pm |  |  | Fair | No | Check and found okay voltage 111 113 225 at meter
Outage | J.E.26.07.24045 | C001861141 | Romeo Brissett | St.James | Completed | Load_556273 | Bogue - 610 | Jul 21, 2026 3:15pm | Jul 22, 2026 8:41am | Jul 22, 2026 8:44am | Jul 22, 2026 8:44am | Jul 22, 2026 9:15am | Jul 22, 2026 9:28am | Jul 22, 2026 9:32am | Jul 22, 2026 9:32am |  |  | Fair | No | Check and found 26-32 volts coming from Rammy box, please send to field service.
Outage | J.E.26.07.24254 | C001861139 | Michael Christian | St.James | Completed | Load_259998 | Queens Drive - 710 | Jul 21, 2026 3:15pm | Jul 21, 2026 3:15pm | Jul 21, 2026 5:58pm | Jul 21, 2026 6:18pm | Jul 21, 2026 6:18pm | Jul 21, 2026 6:36pm | Jul 21, 2026 6:36pm | Jul 21, 2026 6:36pm |  |  | Fair | No | Check and found okay voltage 111 112 223 at meter
Outage | J.E.26.07.24315 | C001861143 | Barrington Brown | St.James | Completed | Load_253413 | Bogue - 510 | Jul 21, 2026 3:15pm | Jul 22, 2026 7:40am | Jul 22, 2026 9:18am | Jul 22, 2026 9:20am | Jul 22, 2026 10:33am | Jul 22, 2026 11:26am | Jul 22, 2026 11:26am | Jul 22, 2026 11:26am |  |  | SaltSprays | No | Corrosion found at pole remake joints using 2 clamps 117v/119v/236v
Outage | J.E.26.07.24316 | C001861138 | Michael Christian | St.James | Completed | Load_240194 | Queens Drive - 710 | Jul 21, 2026 3:15pm | Jul 21, 2026 3:15pm | Jul 21, 2026 4:42pm | Jul 21, 2026 4:42pm | Jul 21, 2026 5:58pm | Jul 21, 2026 6:17pm | Jul 21, 2026 6:17pm | Jul 21, 2026 6:17pm | LeaningPole |  | Fair | No | Check and found okay t o j pole
Outage | J.E.26.07.24322 | C001861137 | Romaine Roberts | St.Mary | Completed | Load_242187 | Highgate -110 | Jul 21, 2026 3:14pm | Jul 21, 2026 3:14pm | Jul 21, 2026 3:31pm | Jul 21, 2026 3:31pm | Jul 21, 2026 4:10pm | Jul 21, 2026 4:18pm | Jul 21, 2026 4:18pm | Jul 21, 2026 4:18pm |  |  | Fair | No | Cannot reach customer after several attempts insufficient direction
Outage | J.E.26.07.24314 | C001861135 | Moses Elliston | St.Catherine | Completed | Load_575219 | Rhodens Pen - 410 | Jul 21, 2026 3:13pm | Jul 21, 2026 3:15pm | Jul 22, 2026 12:36pm | Jul 22, 2026 12:36pm | Jul 22, 2026 12:36pm | Jul 22, 2026 12:36pm | Jul 22, 2026 12:39pm | Jul 22, 2026 12:39pm |  |  | Fair | No | Meter changed to # 3026260 due to credit adding issues
Non-Outage | J.E.26.07.24008 | C001861133 | Andre Williams | null | Completed | null | null | Jul 21, 2026 3:12pm | Jul 21, 2026 3:13pm | Jul 21, 2026 4:55pm | Jul 21, 2026 5:03pm | Jul 21, 2026 5:20pm | Jul 21, 2026 5:20pm | Jul 21, 2026 5:21pm | Jul 21, 2026 5:21pm |  |  | Fair | No | Power was restored
Outage | J.E.26.07.23987 | C001861134 | Moses Elliston | St.Catherine | Completed | Load_1001076 | Tredegar - 210 | Jul 21, 2026 3:12pm | Jul 21, 2026 3:15pm | Jul 21, 2026 3:49pm | Jul 21, 2026 3:49pm | Jul 21, 2026 3:49pm | Jul 21, 2026 3:40pm | Jul 21, 2026 3:51pm | Jul 21, 2026 3:51pm |  |  | Fair | No | Credit added to prepaid account
Non-Outage | J.E.26.07.20313 | C001861131 | Daniel Francis | St.Ann | Completed | Load_257307 | Roaring River - 410 | Jul 21, 2026 3:11pm | Jul 21, 2026 3:12pm | Jul 21, 2026 3:38pm | Jul 21, 2026 3:38pm | Jul 21, 2026 4:13pm | Jul 21, 2026 4:31pm | Jul 21, 2026 4:39pm | Jul 21, 2026 4:39pm |  |  | Fair | No | Change two one bolt clamp 117 116 233 in all
Outage | J.E.26.07.24021 | C001861132 | Moses Elliston | St.Catherine | Completed | Load_242134 | New Michelton - 210 | Jul 21, 2026 3:11pm | Jul 21, 2026 3:15pm | Jul 22, 2026 10:59am | Jul 22, 2026 10:59am | Jul 22, 2026 10:59am | Jul 22, 2026 10:59am | Jul 22, 2026 11:01am | Jul 22, 2026 11:01am |  |  | Fair | No | Supply at premises.Defective collector to be change .Refer to P.Francis
Outage | J.E.26.07.24010 | C001861115 | Richard Samuda | Manchester | Completed | Load_244583 | Spur Tree - 310 | Jul 21, 2026 3:04pm | Jul 21, 2026 3:04pm | Jul 21, 2026 5:41pm | Jul 21, 2026 5:41pm | Jul 21, 2026 5:47pm | Jul 21, 2026 5:51pm | Jul 21, 2026 5:51pm | Jul 21, 2026 5:51pm |  |  | Fair | No | Customer back to normal
Outage | J.E.26.07.24023 | C001861116 | Richard Samuda | Manchester | Completed | Load_244583 | Spur Tree - 310 | Jul 21, 2026 3:04pm | Jul 21, 2026 3:04pm | Jul 21, 2026 3:54pm | Jul 21, 2026 5:27pm | Jul 21, 2026 5:27pm | Jul 21, 2026 5:29pm | Jul 21, 2026 5:30pm | Jul 21, 2026 5:30pm |  |  | Fair | No | Customer say she back to normal
Non-Outage | J.E.26.07.24309 | C001861114 | Richard Samuda | null | Completed | null | null | Jul 21, 2026 3:03pm | Jul 21, 2026 3:06pm | Jul 21, 2026 3:41pm | Jul 21, 2026 3:41pm | Jul 21, 2026 3:54pm | Jul 21, 2026 3:54pm | Jul 21, 2026 3:55pm | Jul 21, 2026 3:55pm |  |  | Fair | No | Customer back to normal
Outage | J.E.26.07.24213 | C001861112 | Richard Samuda | Manchester | Completed | Load_257171 | Spur Tree - 310 | Jul 21, 2026 3:03pm | Jul 21, 2026 3:03pm | Jul 21, 2026 3:56pm | Jul 21, 2026 3:56pm | Jul 21, 2026 4:26pm | Jul 21, 2026 5:28pm | Jul 21, 2026 5:23pm | Jul 21, 2026 5:23pm | BrokenWire |  | Fair | No | Splice and Reconnect customer service wire that was broken using 5ft of #4 service wire customer back to normal voltage 114/116/230 customer back to normal 2840510 customer meter number
Outage | J.E.26.07.24276 | C001861113 | Kenroy Dale | Manchester | Completed | Load_243321 | Porus - 310 | Jul 21, 2026 3:03pm | Jul 21, 2026 3:11pm | Jul 21, 2026 3:48pm | Jul 21, 2026 3:48pm | Jul 21, 2026 4:59pm | Jul 21, 2026 5:09pm | Jul 21, 2026 5:21pm | Jul 21, 2026 5:21pm | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Area found with supply, customers also confirmed that supply was restored was advised to write off call by dispatch
Outage | J.E.26.07.24221 | C001861111 | Barnett Brown | Manchester | Completed | Load_244332 | Kendal - 310 | Jul 21, 2026 3:02pm | Jul 21, 2026 3:09pm | Jul 21, 2026 9:29pm | Jul 21, 2026 9:29pm | Jul 21, 2026 10:40pm | Jul 21, 2026 11:30pm | Jul 21, 2026 11:31pm | Jul 21, 2026 11:31pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.24174 | C001861110 | Roxroy Needham | St.Ann | Completed | Load_1003810 | Cardiff Hall - 210 | Jul 21, 2026 3:01pm | Jul 21, 2026 3:02pm | Jul 21, 2026 4:35pm | Jul 21, 2026 4:35pm | Jul 21, 2026 4:35pm | Jul 21, 2026 4:37pm | Jul 21, 2026 4:38pm | Jul 21, 2026 4:38pm |  |  | Fair | No | Premises found ok call customer and customer say that the light is back and ok
Outage | J.E.26.07.24290 | C001861109 | Roxroy Needham | St.Ann | Completed | Load_295239 | Cardiff Hall - 210 | Jul 21, 2026 3:01pm | Jul 21, 2026 3:02pm | Jul 21, 2026 4:16pm | Jul 21, 2026 4:16pm | Jul 21, 2026 4:34pm | Jul 21, 2026 4:28pm | Jul 21, 2026 4:35pm | Jul 21, 2026 4:35pm |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.07.24043 | C001861105 | Richman Whyte | Hanover | Completed | Load_238992 | Orange Bay - 310 | Jul 21, 2026 3:00pm | Jul 21, 2026 3:01pm | Jul 21, 2026 9:42pm | Jul 21, 2026 9:42pm | Jul 21, 2026 9:42pm | Jul 21, 2026 9:42pm | Jul 21, 2026 9:44pm | Jul 21, 2026 9:44pm |  |  | Fair | No | Unable to locate and call to customer went unanswered after I reach in the community
Outage | J.E.26.07.24185 | C001861104 | Richman Whyte | Westmoreland | Completed | Load_258460 | Paradise - 110 | Jul 21, 2026 2:59pm | Jul 21, 2026 3:00pm | Jul 21, 2026 4:02pm | Jul 21, 2026 4:02pm | Jul 21, 2026 5:46pm | Jul 21, 2026 5:47pm | Jul 21, 2026 5:48pm | Jul 21, 2026 5:48pm |  |  | Rains | No | Connect back customer after hurricane use 4 one bolt clamps voltage 113 113 226
Outage | J.E.26.07.24212 | C001861103 | Javid Vernon | Westmoreland | Completed | Load_261485 | Paradise - 210 | Jul 21, 2026 2:59pm | Jul 22, 2026 7:56am | Jul 22, 2026 9:35am | Jul 22, 2026 9:35am | Jul 22, 2026 10:40am | Jul 22, 2026 11:00am | Jul 22, 2026 11:00am | Jul 22, 2026 11:00am |  |  | Fair | No | Area check and found okay Unable to locate customer and premises even after asking persons in the area for customer phone calls to customer number went unanswered
Outage | J.E.26.07.24280 | C001861101 | Oshane Warren | Westmoreland | Completed | Load_265176 | Paradise - 310 | Jul 21, 2026 2:57pm | Jul 21, 2026 2:58pm | Jul 21, 2026 4:37pm | Jul 21, 2026 4:37pm | Jul 21, 2026 5:28pm | Jul 21, 2026 5:33pm | Jul 21, 2026 5:34pm | Jul 21, 2026 5:34pm |  |  | Rains | Yes | Check and found okay
Outage | J.E.26.07.24311 | C001861102 | Oshane Warren | Westmoreland | Completed | Load_245673 | Paradise - 310 | Jul 21, 2026 2:57pm | Jul 21, 2026 2:58pm | Jul 21, 2026 3:45pm | Jul 21, 2026 3:45pm | Jul 21, 2026 3:45pm | Jul 21, 2026 3:46pm | Jul 21, 2026 3:46pm | Jul 21, 2026 3:46pm |  |  | Rains | No | Plan outage is in the area
Outage | J.E.26.07.23744 | C001861091 | Romeo Brissett | St.James | Completed | Load_258487 | Bogue - 310 | Jul 21, 2026 2:49pm | Jul 21, 2026 2:55pm | Jul 21, 2026 5:01pm | Jul 21, 2026 5:01pm | Jul 21, 2026 7:11pm | Jul 21, 2026 8:00pm | Jul 21, 2026 8:07pm | Jul 21, 2026 8:07pm |  |  | Fair | No | Installed 40ft of #6. V/R 110-111-221.
Outage | J.E.26.07.24219 | C001861090 | Romeo Brissett | St.James | Completed | Load_269842 | Bogue - 310 | Jul 21, 2026 2:49pm | Jul 21, 2026 2:55pm | Jul 21, 2026 3:17pm | Jul 21, 2026 3:17pm | Jul 21, 2026 3:57pm | Jul 21, 2026 5:00pm | Jul 21, 2026 5:01pm | Jul 21, 2026 5:01pm |  |  | Fair | No | Removed vegetation and replaced (1)25KVA transformer fuse.
Non-Outage | J.E.26.07.24260 | C001861047 | Andrew Powell | null | Completed | null | null | Jul 21, 2026 2:14pm | Jul 22, 2026 4:26pm | Jul 22, 2026 4:37pm | Jul 22, 2026 4:37pm | Jul 22, 2026 5:22pm | Jul 22, 2026 5:52pm | Jul 22, 2026 6:01pm | Jul 22, 2026 6:01pm |  |  | Fair | No | Found customer experiencing serious low voltage from bank of three 100 kva transformer circuit, voltage reading 223v-226v-227v phase to neutral, 389v-391v-402v cross phase off load . Customer unable to apparate machinery due to low voltage, please refer to maintenance department.
Non-Outage | J.E.26.07.24208 | C001861023 | Rayon Foster | Hanover | Completed | Load_258316 | Orange Bay - 310 | Jul 21, 2026 1:58pm | Jul 21, 2026 1:59pm | Jul 21, 2026 5:33pm | Jul 21, 2026 5:33pm | Jul 21, 2026 5:33pm | Jul 21, 2026 5:58pm | Jul 21, 2026 6:17pm | Jul 21, 2026 6:17pm |  |  | Fair | No | Patrol primary line to fine one blow 15 amp junction fuse no visible fault found isolate 50 kva transformer and test close junction fuse 15 amps junction fuse blown suspected defected d/0 switch please refer to maintenance department
Outage | J.E.26.07.24228 | C001861022 | Oshane Warren | Westmoreland | Completed | Load_253660 | Paradise - 310 | Jul 21, 2026 1:57pm | Jul 21, 2026 1:57pm | Jul 21, 2026 8:03pm | Jul 21, 2026 8:05pm | Jul 21, 2026 8:05pm | Jul 21, 2026 8:05pm | Jul 21, 2026 8:06pm | Jul 21, 2026 8:06pm |  |  | Rains | No | Internal problem avoids to fix
Outage | J.E.26.07.23730 | C001861014 | Rusean Allen | KSAS | Completed | Load_264436 | Hunts Bay - 510 | Jul 21, 2026 1:52pm | Jul 22, 2026 8:15am | Jul 22, 2026 9:07am | Jul 22, 2026 9:07am | Jul 22, 2026 9:57am | Jul 22, 2026 10:42am | Jul 22, 2026 10:42am | Jul 22, 2026 10:42am |  |  | Fair | No | Defective 4wire meter found, defective meter socket also found, customer was advised to contact electrician. Meter needs to be changed, refer to field service department.
Non-Outage | J.E.26.07.23717 | C001860999 | Andrae Clarke | Portland | Completed | Load_251580 | Port Antonio - 310 | Jul 21, 2026 1:40pm | Jul 21, 2026 1:41pm | Jul 22, 2026 11:25am | Jul 22, 2026 11:25am | Jul 22, 2026 11:25am | Jul 22, 2026 11:31am | Jul 22, 2026 12:09pm | Jul 22, 2026 12:09pm |  |  | Fair | No | Check connections found corroded clean up connections use three one bolt clamp Check voltage 121/119/240
Non-Outage | J.E.26.07.23640 | C001860997 | Andrae Clarke | Portland | Completed | Load_243555 | Port Antonio - 410 | Jul 21, 2026 1:39pm | Jul 21, 2026 1:41pm | Jul 21, 2026 1:58pm | Jul 21, 2026 4:47pm | Jul 21, 2026 4:47pm | Jul 21, 2026 1:15pm | Jul 21, 2026 4:48pm | Jul 21, 2026 4:48pm |  |  | Fair | No | Premises found okay
Non-Outage | J.E.26.07.23642 | C001860998 | Andrae Clarke | Portland | Completed | Load_243555 | Port Antonio - 410 | Jul 21, 2026 1:39pm | Jul 21, 2026 1:41pm | Jul 21, 2026 4:48pm | Jul 21, 2026 4:48pm | Jul 21, 2026 4:53pm | Jul 21, 2026 2:10pm | Jul 21, 2026 4:55pm | Jul 21, 2026 4:55pm |  |  | Fair | No | Premises found okay 119/117/236
Outage | J.E.26.07.24222 | C001860992 | Tyrese Williams | St.Ann | Completed | Load_258300 | Cardiff Hall - 310 | Jul 21, 2026 1:35pm | Jul 21, 2026 1:36pm | Jul 21, 2026 2:38pm | Jul 21, 2026 2:38pm | Jul 21, 2026 2:40pm | Jul 21, 2026 2:40pm | Jul 21, 2026 2:42pm | Jul 21, 2026 2:42pm |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.07.24056 | C001860979 | Oshane Warren | Westmoreland | Completed | Load_265674 | Paradise - 310 | Jul 21, 2026 1:13pm | Jul 21, 2026 1:14pm | Jul 21, 2026 6:01pm | Jul 21, 2026 6:01pm | Jul 21, 2026 7:40pm | Jul 21, 2026 7:52pm | Jul 21, 2026 7:52pm | Jul 21, 2026 7:52pm | BrokenWire |  | Rains | No | Unable to reach location due to terrain however Richard stated that power quality crew should visit the location tomorrow morning
Non-Outage | J.E.26.07.24192 | C001860975 | Eric Williams | KSAN | Completed | Load_245509 | Washington Blvd - 710 | Jul 21, 2026 1:07pm | Jul 21, 2026 4:07pm | Jul 21, 2026 4:55pm | Jul 21, 2026 4:55pm | Jul 21, 2026 5:29pm | Jul 21, 2026 5:33pm | Jul 21, 2026 5:35pm | Jul 21, 2026 5:35pm | Fire |  | Fair | No | Premises found okay, no fire
Outage | J.E.26.07.24050 | C001860968 | Romeo Brissett | St.James | Completed | Load_572392 | Bogue - 310 | Jul 21, 2026 1:00pm | Jul 21, 2026 1:00pm | Jul 21, 2026 1:18pm | Jul 21, 2026 1:18pm | Jul 21, 2026 2:43pm | Jul 21, 2026 3:15pm | Jul 21, 2026 3:17pm | Jul 21, 2026 3:17pm | LeaningPole |  | Fair | No | Found (1)40ft wood pole leaning with 3 phase Primary, twisted secondary and customer service wires resulting tearing off customer stanchion. Spliced and release tension off customer service wire, used 3ft of #6 and 1 clamp. Please send to maintenance to straighten pole.
Outage | J.E.26.07.24176 | C001860964 | Tyrese Williams | St.Ann | Completed | Load_255835 | Cardiff Hall - 310 | Jul 21, 2026 12:54pm | Jul 21, 2026 1:03pm | Jul 22, 2026 2:58pm | Jul 22, 2026 3:00pm | Jul 22, 2026 3:00pm | Jul 22, 2026 3:01pm | Jul 22, 2026 3:01pm | Jul 22, 2026 3:01pm | BrokenWire |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.07.24140 | C001860952 | Marlon Brown | Trelawny | Completed | Load_294436 | Duncans - 110 | Jul 21, 2026 12:44pm | Jul 21, 2026 12:44pm | Jul 21, 2026 1:09pm | Jul 21, 2026 1:09pm | Jul 21, 2026 2:04pm | Jul 21, 2026 2:06pm | Jul 21, 2026 2:06pm | Jul 21, 2026 2:06pm |  |  | Fair | No | Feeder issue
Non-Outage | J.E.26.07.24018 | C001860946 | Eric Williams | KSAN | Completed | Load_263967 | Constant Spring - 210 | Jul 21, 2026 12:36pm | Jul 21, 2026 4:11pm | Jul 21, 2026 6:10pm | Jul 21, 2026 6:10pm | Jul 21, 2026 6:22pm | Jul 21, 2026 6:22pm | Jul 21, 2026 6:27pm | Jul 21, 2026 6:27pm | BrokenPole |  | Fair | No | Rotten 30 class 6 secondary pole with 3 wire open secondary and streetlight refer to maintenance department
Non-Outage | J.E.26.07.24049 | C001860932 | Edward Royal | KSAS | Completed | Load_261859 | Hunts Bay - 210 | Jul 21, 2026 12:23pm | Jul 21, 2026 4:09pm | Jul 21, 2026 4:14pm | Jul 21, 2026 4:14pm | Jul 21, 2026 5:25pm | Jul 21, 2026 7:16pm | Jul 21, 2026 7:17pm | Jul 21, 2026 7:17pm |  |  | Fair | No | Replaced 6 junction fuse 2 80 4 50A Defective 50kva transformer need to be change it a banker of 3 transformer the lightening transformer defective reffered to maintenance
Outage | J.E.26.07.24032 | C001860922 | Nickolas Rodriques | St.Catherine | Completed | Load_557064 | Twickenham - 210 | Jul 21, 2026 12:14pm | Jul 21, 2026 12:16pm | Jul 21, 2026 1:20pm | Jul 21, 2026 1:33pm | Jul 21, 2026 1:44pm | Jul 21, 2026 1:48pm | Jul 21, 2026 2:21pm | Jul 21, 2026 2:21pm |  |  | Fair | No | Call relates to the 5 amp transformer fuse that was replaced. Power restored.
Outage | J.E.26.07.24028 | C001860908 | Oshane Warren | Westmoreland | Completed | Load_292679 | Paradise - 310 | Jul 21, 2026 11:59am | Jul 21, 2026 11:59am | Jul 21, 2026 8:10pm | Jul 21, 2026 8:10pm | Jul 21, 2026 10:23pm | Jul 21, 2026 10:29pm | Jul 21, 2026 10:30pm | Jul 21, 2026 10:30pm |  |  | Rains | No | Internal problem advice to fix voltage 111 115 226
Outage | J.E.26.07.24033 | C001860906 | Tyrese Williams | St.Ann | Completed | Load_251522 | Cardiff Hall - 310 | Jul 21, 2026 11:56am | Jul 21, 2026 11:57am | Jul 21, 2026 12:35pm | Jul 21, 2026 12:36pm | Jul 21, 2026 2:02pm | Jul 21, 2026 2:14pm | Jul 21, 2026 2:14pm | Jul 21, 2026 2:14pm | Fire |  | Fair | No | Premises found ok some was in the community cut tree and was banging the secondary wires together
Outage | J.E.26.07.24022 | C001860903 | Richard Grant | St.Catherine | Completed | Load_256890 | New Michelton - 210 | Jul 21, 2026 11:52am | Jul 21, 2026 11:53am | Jul 21, 2026 1:27pm | Jul 21, 2026 1:27pm | Jul 21, 2026 1:27pm | Jul 21, 2026 2:32pm | Jul 21, 2026 2:57pm | Jul 21, 2026 2:57pm | BrokenWire |  | Fair | No | Broken open secondary phase found cause by illegal connections, use 20 feet 2/0 AAA , 2 2/0 splicing sleeves to splice and retention, area left ok
Outage | J.E.26.07.24014 | C001860899 | Evan Spaulding | St.Mary | Completed | Load_258693 | Highgate -110 | Jul 21, 2026 11:50am | Jul 21, 2026 11:50am | Jul 21, 2026 12:07pm | Jul 21, 2026 12:07pm | Jul 21, 2026 12:38pm | Jul 21, 2026 12:39pm | Jul 21, 2026 12:40pm | Jul 21, 2026 12:40pm | BrokenPole |  | Fair | No | Third party pole,Flow pole broken.
Outage | J.E.26.07.23940 | C001860897 | Clyde Brown | Clarendon | Completed | Load_261166 | May Pen - 110 | Jul 21, 2026 11:46am | Jul 21, 2026 3:25pm | Jul 21, 2026 4:16pm | Jul 21, 2026 4:16pm | Jul 21, 2026 5:39pm | Jul 21, 2026 10:10pm | Jul 21, 2026 10:17pm | Jul 21, 2026 10:17pm |  | Y | Fair | No | Secondary phase and neutral entangled caused by slack secondary phase ,open 25kva transformer and retention secondary line with 2-2/0 preform and 2-#2 preform on hillside and 2- clamp.VOltage left 113/113 and 227V
Outage | J.E.26.07.24015 | C001860893 | Richman Whyte | Westmoreland | Completed | Load_242418 | Paradise - 110 | Jul 21, 2026 11:46am | Jul 21, 2026 3:27pm | Jul 21, 2026 7:41pm | Jul 21, 2026 7:41pm | Jul 21, 2026 7:41pm | Jul 21, 2026 7:42pm | Jul 21, 2026 7:42pm | Jul 21, 2026 7:42pm |  |  | Rains | No | Check and found okay customer stated that she didn’t make any call
Outage | J.E.26.07.23776 | C001860892 | Oshane Warren | Westmoreland | Completed | Load_259993 | Paradise - 310 | Jul 21, 2026 11:45am | Jul 21, 2026 11:59am | Jul 21, 2026 1:38pm | Jul 21, 2026 1:38pm | Jul 21, 2026 3:40pm | Jul 21, 2026 3:44pm | Jul 21, 2026 3:44pm | Jul 21, 2026 3:44pm |  |  | Rains | No | Plan outage was in the area
Outage | J.E.26.07.24013 | C001860891 | Neville Spencer | Clarendon | Completed | Load_568659 | Parnassus - 310 | Jul 21, 2026 11:45am | Jul 21, 2026 11:46am | Jul 21, 2026 1:50pm | Jul 21, 2026 1:50pm | Jul 21, 2026 2:27pm | Jul 21, 2026 2:27pm | Jul 21, 2026 3:21pm | Jul 21, 2026 3:21pm |  |  | Fair | No | Replace 2 blown 30 amp j/ fuse and fuse holder supply restored.
Outage | J.E.26.07.23977 | C001860889 | Marlon Brown | Trelawny | Completed | Load_1001506 | Duncans - 110 | Jul 21, 2026 11:42am | Jul 21, 2026 11:46am | Jul 21, 2026 12:08pm | Jul 21, 2026 12:08pm | Jul 21, 2026 1:08pm | Jul 21, 2026 1:08pm | Jul 21, 2026 1:09pm | Jul 21, 2026 1:09pm |  |  | Fair | No | Unable to locate customer via telephone nor direction
Outage | J.E.26.07.23727 | C001860888 | Kaydon Taylor | KSAN | Completed | Load_261490 | Constant Spring - 410 | Jul 21, 2026 11:41am | Jul 21, 2026 4:06pm | Jul 21, 2026 4:33pm | Jul 21, 2026 4:36pm | Jul 21, 2026 6:38pm | Jul 21, 2026 7:53pm | Jul 21, 2026 7:53pm | Jul 21, 2026 7:53pm | LeaningPole,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards | Y | Fair | No | #4 Copper wire at Switch top burn off at junction pole. Carried out medium bushing cut bamboos off the line. Also required a 30’ intermediate pole for low hanging open secondary wire. 30 amp trip saver needs to isolate to carry out the repair of the switch top at paisley district. Refer to the in house team with load breaker tool.
Outage | J.E.26.07.23970 | C001860882 | Richard Nicholas | St.Catherine | Completed | Load_291969 | Rhodens Pen - 210 | Jul 21, 2026 11:37am | Jul 21, 2026 11:37am | Jul 21, 2026 1:57pm | Jul 21, 2026 2:53pm | Jul 21, 2026 2:53pm | Jul 21, 2026 2:53pm | Jul 21, 2026 2:54pm | Jul 21, 2026 2:54pm | Fire |  | Fair | No | Found ok
Outage | J.E.26.07.23988 | C001860883 | Moses Elliston | St.Catherine | Completed | Load_1001441 | Tredegar - 210 | Jul 21, 2026 11:37am | Jul 21, 2026 11:37am | Jul 21, 2026 4:46pm | Jul 21, 2026 4:46pm | Jul 21, 2026 4:47pm | Jul 21, 2026 4:47pm | Jul 21, 2026 4:48pm | Jul 21, 2026 4:48pm |  |  | Fair | No | Credit added to prepaid account
Outage | J.E.26.07.23990 | C001860875 | Swon Miller | St.James | Completed | Load_252950 | Bogue - 410 | Jul 21, 2026 11:36am | Jul 21, 2026 11:36am | Jul 21, 2026 12:50pm | Jul 21, 2026 12:50pm | Jul 21, 2026 1:15pm | Jul 14, 2026 2:02am | Jul 21, 2026 2:02pm | Jul 21, 2026 2:02pm | Fire |  | Fair | No | Found 1,15 amp junction fuse blown cause by contamination replace 15 amp junction fuse no pole number available voltage found 0.000 voltage left 115/115/231
Outage | J.E.26.07.22616 | C001860873 | Kaydon Taylor | KSAN | Completed | Load_266412 | West Kings House - 410 | Jul 21, 2026 11:31am | Jul 22, 2026 8:05am | Jul 22, 2026 8:26am | Jul 22, 2026 10:05am | Jul 22, 2026 10:36am | Jul 22, 2026 11:14am | Jul 22, 2026 11:14am | Jul 22, 2026 11:14am |  |  | Fair | No | Broken neutral wire repair in mid span. 2’ of #2 aaa conductor wire (2) one bolt clamps. V 116 117 237.
Outage | J.E.26.07.23574 | C001860872 | Wan Carlos Scarlett | Portmore | Completed | Load_253463 | Naggo Head - 610 | Jul 21, 2026 11:31am | Jul 21, 2026 11:33am | Jul 21, 2026 12:31pm | Jul 21, 2026 12:31pm | Jul 21, 2026 1:14pm | Jul 21, 2026 2:07pm | Jul 21, 2026 2:09pm | Jul 21, 2026 2:09pm |  |  | Fair | No | Found 25KVA transformer drop lead wire to secondary line phase corroded use 2 one bolt clamps at open secondary line phase readings 117-116-234
Outage | J.E.26.07.23620 | C001860874 | Nickolas Rodriques | St.Catherine | Completed | Load_557064 | Twickenham - 210 | Jul 21, 2026 11:31am | Jul 21, 2026 11:33am | Jul 21, 2026 12:03pm | Jul 21, 2026 12:04pm | Jul 21, 2026 1:05pm | Jul 21, 2026 1:17pm | Jul 21, 2026 1:20pm | Jul 21, 2026 1:20pm |  |  | Fair | No | Checked and found a 5 amp transformer fuse blown caused by bird. Repaired by replacing the fuse after completing patrol.
Outage | J.E.26.07.23943 | C001860865 | Collin Robinson | Portland | Completed | Load_244598 | Port Antonio - 410 | Jul 21, 2026 11:30am | Jul 21, 2026 11:40am | Jul 21, 2026 12:06pm | Jul 21, 2026 12:06pm | Jul 21, 2026 12:23pm | Jul 21, 2026 12:23pm | Jul 21, 2026 12:27pm | Jul 21, 2026 12:27pm |  |  | Fair | No | Unable to locate customer
Non-Outage | J.E.26.07.22278 | C001860860 | Fitzroy Turner | KSAS | Completed | Load_245415 | Hunts Bay - 210 | Jul 21, 2026 11:25am | Jul 21, 2026 11:25am | Jul 21, 2026 12:06pm | Jul 21, 2026 12:13pm | Jul 21, 2026 12:13pm | Jul 21, 2026 12:13pm | Jul 21, 2026 12:14pm | Jul 21, 2026 12:14pm |  |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.07.23775 | C001860859 | Barnett Brown | Manchester | Completed | Load_241322 | Kendal - 210 | Jul 21, 2026 11:24am | Jul 21, 2026 11:26am | Jul 21, 2026 11:58am | Jul 21, 2026 11:58am | Jul 21, 2026 12:41pm | Jul 21, 2026 1:08pm | Jul 21, 2026 1:09pm | Jul 21, 2026 1:09pm |  |  | Fair | No | Please refer to field service, as there’s a meter mix up.
Outage | J.E.26.07.23944 | C001860836 | Raymond Lewis | St.Ann | Completed | Load_265774 | Roaring River - 410 | Jul 21, 2026 11:07am | Jul 21, 2026 11:10am | Jul 21, 2026 11:35am | Jul 21, 2026 11:35am | Jul 21, 2026 12:56pm | Jul 21, 2026 1:19pm | Jul 21, 2026 1:20pm | Jul 21, 2026 1:20pm |  |  | Fair | No | Refuse and close two 100 kva x former in bank a 2
Outage | J.E.26.07.23942 | C001860833 | Andre Williams | Trelawny | Completed | Load_241826 | Martha Brae - 110 | Jul 21, 2026 11:05am | Jul 21, 2026 3:12pm | Jul 21, 2026 3:17pm | Jul 21, 2026 3:17pm | Jul 21, 2026 3:39pm | Jul 21, 2026 3:59pm | Jul 21, 2026 4:03pm | Jul 21, 2026 4:03pm | Fire |  | Fair | No | Tighten loose clamp on customer 3 wire service at Jps pole, voltage 112+111=223
Non-Outage | J.E.26.07.16342 | C001860831 | Tajay Bernard | Hanover | Completed | Load_242763 | Orange Bay - 310 | Jul 21, 2026 11:03am | Jul 21, 2026 11:04am | Jul 21, 2026 11:37am | Jul 21, 2026 11:40am | Jul 21, 2026 11:57am | Jul 21, 2026 12:16pm | Jul 21, 2026 12:16pm | Jul 21, 2026 12:16pm |  |  | Fair | No | Area check and found okay unable to locate customer on premises multiple phone calls to customer number went unanswered
Non-Outage | J.E.26.07.16342 | C001860832 | Tajay Bernard | Hanover | Completed | Load_242763 | Orange Bay - 310 | Jul 21, 2026 11:03am | Jul 21, 2026 11:04am | Jul 21, 2026 12:16pm | Jul 21, 2026 12:16pm | Jul 21, 2026 12:16pm | Jul 21, 2026 12:17pm | Jul 21, 2026 12:17pm | Jul 21, 2026 12:17pm |  |  | Fair | No | Area check and found okay unable to locate customer on premises multiple phone calls to customer number went unanswered
Outage | J.E.26.07.23905 | C001860825 | Floyd Taylor | Trelawny | Completed | Load_251614 | Martha Brae - 210 | Jul 21, 2026 10:59am | Jul 21, 2026 10:59am | Jul 21, 2026 2:45pm | Jul 21, 2026 2:45pm | Jul 21, 2026 2:46pm | Jul 21, 2026 3:05pm | Jul 21, 2026 3:06pm | Jul 21, 2026 3:06pm |  |  | Fair | No | Switch defective and needs to be replaced, refer to maintenance maintenance.
Outage | J.E.26.07.23745 | C001860808 | Romeo Brissett | St.James | Completed | Load_302249 | Bogue - 510 | Jul 21, 2026 10:47am | Jul 21, 2026 10:48am | Jul 21, 2026 10:52am | Jul 21, 2026 12:34pm | Jul 21, 2026 12:49pm | Jul 21, 2026 1:15pm | Jul 21, 2026 1:17pm | Jul 21, 2026 1:17pm |  |  | Fair | No | Replaced (1)25KVA transformer fuse.
Outage | J.E.26.07.23756 | C001860807 | Romeo Brissett | St.James | Completed | Load_247912 | Bogue - 510 | Jul 21, 2026 10:47am | Jul 21, 2026 10:48am | Jul 21, 2026 11:47am | Jul 21, 2026 11:47am | Jul 21, 2026 11:53am | Jul 21, 2026 12:34pm | Jul 21, 2026 12:34pm | Jul 21, 2026 12:34pm |  |  | Fair | No | Removed vegetation and replaced (1)20amps junction.
Non-Outage | J.E.26.07.23720 | C001860799 | Devon Grant | KSAN | Completed | Load_268847 | Constant Spring - 310 | Jul 21, 2026 10:45am | Jul 21, 2026 10:45am | Jul 21, 2026 1:25pm | Jul 21, 2026 1:25pm | Jul 21, 2026 1:50pm | Jul 21, 2026 2:27pm | Jul 21, 2026 2:36pm | Jul 21, 2026 2:36pm |  |  | Fair | No | Splice customer burnt service wire using 3ft #6 triplex.
Outage | J.E.26.07.23715 | C001860797 | Devon Grant | KSAN | Completed | Load_268847 | Constant Spring - 310 | Jul 21, 2026 10:44am | Jul 21, 2026 10:44am | Jul 22, 2026 1:00pm | Jul 22, 2026 1:01pm | Jul 22, 2026 2:19pm | Jul 22, 2026 2:34pm | Jul 22, 2026 2:35pm | Jul 22, 2026 2:35pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.23748 | C001860786 | Stephen Taylor | St.Thomas | Completed | Load_247908 | Good Year - 210 | Jul 21, 2026 10:40am | Jul 21, 2026 12:23pm | Jul 21, 2026 1:03pm | Jul 21, 2026 1:24pm | Jul 21, 2026 1:48pm | Jul 21, 2026 2:03pm | Jul 21, 2026 2:05pm | Jul 21, 2026 2:05pm | BrokenWire |  | Fair | No | Connect back single phase wire and customer is now ok reading 111,112,225
Non-Outage | J.E.26.07.23739 | C001860782 | Neville Spencer | null | Completed | null | null | Jul 21, 2026 10:33am | Jul 21, 2026 10:33am | Jul 21, 2026 1:24pm | Jul 21, 2026 1:24pm | Jul 21, 2026 1:46pm | Jul 21, 2026 1:46pm | Jul 21, 2026 1:50pm | Jul 21, 2026 1:50pm |  |  | Fair | No | Renew blown 3 amp fuse protecting 25 kva xmfr in bank of 3 supply restored.
Non-Outage | J.E.26.07.23751 | C001860776 | Royston Montague | St.Catherine | Completed | Load_253729 | Rhodens Pen - 210 | Jul 21, 2026 10:28am | Jul 21, 2026 10:29am | Jul 21, 2026 12:43pm | Jul 21, 2026 1:14pm | Jul 21, 2026 1:16pm | Jul 21, 2026 1:29pm | Jul 21, 2026 1:32pm | Jul 21, 2026 1:32pm | Fire |  | Fair | No | Faulty phase at pothead, same corrected. Voltage 230v 114v 114v
Non-Outage | J.E.26.07.23763 | C001860775 | Odaine Johnson | St.Catherine | Completed | Load_263085 | Rhodens Pen - 310 | Jul 21, 2026 10:28am | Jul 21, 2026 10:29am | Jul 21, 2026 11:20am | Jul 21, 2026 11:20am | Jul 21, 2026 11:20am | Jul 21, 2026 11:20am | Jul 21, 2026 11:21am | Jul 21, 2026 11:21am | Fire |  | Fair | No | Premises found okay
Non-Outage | J.E.26.07.23735 | C001860773 | Collin Robinson | null | Completed | null | null | Jul 21, 2026 10:22am | Jul 21, 2026 10:25am | Jul 21, 2026 10:34am | Jul 21, 2026 10:34am | Jul 21, 2026 11:12am | Jul 21, 2026 12:03pm | Jul 21, 2026 12:03pm | Jul 21, 2026 12:03pm |  |  | Fair | No | Isolate 25KVA transformer at pole 036712 to change corroded clamps that connect to transformer drop lead Voltage reading 118v 118v 236v
Non-Outage | J.E.26.07.22922 | C001860758 | Kaydon Taylor | KSAN | Completed | Load_263471 | Washington Blvd - 410 | Jul 21, 2026 10:04am | Jul 21, 2026 10:04am | Jul 21, 2026 12:52pm | Jul 21, 2026 12:56pm | Jul 21, 2026 12:56pm | Jul 21, 2026 12:58pm | Jul 21, 2026 12:58pm | Jul 21, 2026 12:58pm |  |  | Fair | No | Defective 100kva transformer found
Outage | J.E.26.07.23722 | C001860750 | Romeo Brissett | St.James | Completed | Load_267214 | Bogue - 510 | Jul 21, 2026 9:56am | Jul 21, 2026 9:57am | Jul 21, 2026 11:05am | Jul 21, 2026 11:05am | Jul 21, 2026 11:05am | Jul 21, 2026 11:40am | Jul 21, 2026 11:47am | Jul 21, 2026 11:47am |  |  | Fair | No | Isolated (1)100kva transformer, repaired transformer switch bottom.
Outage | J.E.26.07.23707 | C001860740 | Andre Williams | Trelawny | Completed | Load_264087 | Martha Brae - 110 | Jul 21, 2026 9:54am | Jul 21, 2026 3:12pm | Jul 21, 2026 3:40pm | Jul 21, 2026 4:11pm | Jul 21, 2026 4:26pm | Jul 21, 2026 4:47pm | Jul 21, 2026 4:47pm | Jul 21, 2026 4:47pm | BrokenWire |  | Fair | No | Reconnect customer #6 three wire service at Jps pole voltage 118+118=236
Outage | J.E.26.07.23663 | C001860727 | Error Coore | Manchester | Completed | Load_244583 | Spur Tree - 310 | Jul 21, 2026 9:50am | Jul 21, 2026 9:50am | Jul 21, 2026 1:21pm | Jul 21, 2026 1:21pm | Jul 21, 2026 1:21pm | Jul 21, 2026 1:24pm | Jul 21, 2026 1:27pm | Jul 21, 2026 1:27pm |  |  | Fair | No | Found customer meter badly burn disconnect customer at pothead customer is now doing repairs customer need a new meter
Non-Outage | J.E.26.07.23542 | C001860715 | Rochaine Hussey | KSAN | Completed | Load_261490 | Constant Spring - 410 | Jul 21, 2026 9:46am | Jul 21, 2026 9:46am | Jul 21, 2026 12:08pm | Jul 21, 2026 12:08pm | Jul 21, 2026 12:39pm | Jul 21, 2026 12:44pm | Jul 21, 2026 12:45pm | Jul 21, 2026 12:45pm |  |  | Fair | No | Pole#0001063Primary line jumper fuse holder burnt off Bucket truck needed
Non-Outage | J.E.26.07.23555 | C001860716 | Rochaine Hussey | KSAN | Completed | Load_261490 | Constant Spring - 410 | Jul 21, 2026 9:46am | Jul 21, 2026 9:46am | Jul 21, 2026 1:34pm | Jul 21, 2026 1:58pm | Jul 21, 2026 1:58pm | Jul 21, 2026 2:00pm | Jul 21, 2026 2:01pm | Jul 21, 2026 2:01pm |  |  | Fair | No | Fuse was left open Primary line jumper burnt
Non-Outage | J.E.26.07.23600 | C001860718 | Rochaine Hussey | KSAN | Completed | Load_261228 | Constant Spring - 210 | Jul 21, 2026 9:46am | Jul 21, 2026 9:46am | Jul 21, 2026 1:22pm | Jul 21, 2026 1:30pm | Jul 21, 2026 1:30pm | Jul 21, 2026 1:34pm | Jul 21, 2026 1:34pm | Jul 21, 2026 1:34pm |  |  | Fair | No | Premises closed Customer was called multiple times no answer
Non-Outage | J.E.26.07.23704 | C001860726 | Neville Spencer | null | Completed | null | null | Jul 21, 2026 9:46am | Jul 21, 2026 9:47am | Jul 21, 2026 11:40am | Jul 21, 2026 11:40am | Jul 21, 2026 1:19pm | Jul 21, 2026 1:24pm | Jul 21, 2026 1:24pm | Jul 21, 2026 1:24pm | Fire |  | Fair | No | Not getting trough to customer..
Outage | J.E.26.07.23709 | C001860714 | Fitzroy Turner | KSAS | Completed | Load_261859 | Hunts Bay - 210 | Jul 21, 2026 9:45am | Jul 21, 2026 9:45am | Jul 21, 2026 12:03pm | Jul 21, 2026 12:03pm | Jul 21, 2026 12:12pm | Jul 21, 2026 12:13pm | Jul 21, 2026 12:13pm | Jul 21, 2026 12:13pm |  |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.07.23701 | C001860713 | Fitzroy Turner | KSAS | Completed | Load_258668 | Greenwich - 710 | Jul 21, 2026 9:44am | Jul 21, 2026 9:45am | Jul 21, 2026 10:49am | Jul 21, 2026 10:49am | Jul 21, 2026 11:21am | Jul 21, 2026 11:22am | Jul 21, 2026 11:23am | Jul 21, 2026 11:23am | Fire |  | Fair | No | Found pole mountain meter socket defective customer with out supply please send email to field service department to have meter socket changed
Non-Outage | J.E.26.07.22261 | C001860706 | Evan Spaulding | St.Mary | Completed | Load_253844 | Highgate - 210 | Jul 21, 2026 9:39am | Jul 21, 2026 9:40am | Jul 22, 2026 1:59pm | Jul 22, 2026 1:59pm | Jul 22, 2026 1:59pm | Jul 22, 2026 2:00pm | Jul 22, 2026 2:00pm | Jul 22, 2026 2:00pm |  |  | Fair | No | Associated call.
Non-Outage | J.E.26.07.22264 | C001860707 | Evan Spaulding | St.Mary | Completed | Load_237969 | Highgate - 210 | Jul 21, 2026 9:39am | Jul 21, 2026 9:40am | Jul 22, 2026 1:58pm | Jul 22, 2026 1:58pm | Jul 22, 2026 1:58pm | Jul 22, 2026 1:59pm | Jul 22, 2026 1:59pm | Jul 22, 2026 1:59pm |  |  | Fair | No | Not getting through to this customer from yesterday.
Non-Outage | J.E.26.07.22460 | C001860709 | Evan Spaulding | St.Mary | Completed | Load_266176 | Highgate - 210 | Jul 21, 2026 9:39am | Jul 21, 2026 9:40am | Jul 21, 2026 9:52am | Jul 21, 2026 9:52am | Jul 21, 2026 10:17am | Jul 21, 2026 10:37am | Jul 21, 2026 10:39am | Jul 21, 2026 10:39am |  |  | Fair | No | Use 3-1 bolt clamps at pot head, voltage left 110v,111v,221v.
Non-Outage | J.E.26.07.23653 | C001860708 | Milton Charlton | null | Completed | null | null | Jul 21, 2026 9:39am | Jul 21, 2026 9:40am | Jul 21, 2026 11:17am | Jul 21, 2026 11:17am | Jul 21, 2026 11:36am | Jul 21, 2026 11:40am | Jul 21, 2026 11:42am | Jul 21, 2026 11:42am | BrokenPole |  | Fair | No | 40ft wooden pole #0119087 rotten at the foot and held up by primary conductors and telephone cables. Pole is T construction with three phase primary and neutral, street light and twisted secondary conductors from Hexing boxes. Need urgent attention.
Non-Outage | J.E.26.07.21716 | C001860704 | Evan Spaulding | St.Mary | Completed | Load_247768 | Highgate - 210 | Jul 21, 2026 9:38am | Jul 21, 2026 9:40am | Jul 21, 2026 10:43am | Jul 21, 2026 10:43am | Jul 21, 2026 11:18am | Jul 21, 2026 12:02pm | Jul 21, 2026 12:04pm | Jul 21, 2026 12:04pm |  |  | Fair | No | Tap 25 kva Transformer from position 3 to position 4,voltage left 116v,117v,223v.
Non-Outage | J.E.26.07.23700 | C001860703 | Derrick Grubb | null | Completed | null | null | Jul 21, 2026 9:37am | Jul 21, 2026 9:38am | Jul 21, 2026 10:39am | Jul 21, 2026 10:39am | Jul 21, 2026 10:39am | Jul 21, 2026 10:41am | Jul 21, 2026 10:41am | Jul 21, 2026 10:41am |  |  | Fair | No | Premises is affected by a planned outage in the area.
Non-Outage | J.E.26.07.23028 | C001860696 | Kaydon Taylor | KSAN | Completed | Load_247215 | Washington Blvd - 410 | Jul 21, 2026 9:32am | Jul 21, 2026 9:35am | Jul 21, 2026 9:43am | Jul 21, 2026 12:58pm | Jul 21, 2026 1:14pm | Jul 21, 2026 4:23pm | Jul 21, 2026 4:23pm | Jul 21, 2026 4:23pm |  |  | Fair | No | 10 amp fuse found blown and replace at pole #0064723. V 119 119 212 239/239/240.
Outage | J.E.26.07.23658 | C001860694 | Raymond Lewis | St.Ann | Completed | Load_269408 | Ocho Rios - 310 | Jul 21, 2026 9:30am | Jul 21, 2026 9:31am | Jul 21, 2026 1:20pm | Jul 21, 2026 1:20pm | Jul 21, 2026 2:06pm | Jul 21, 2026 2:30pm | Jul 21, 2026 2:30pm | Jul 21, 2026 2:30pm |  |  | Fair | No | Remove vegetation from line and refuse and close 25 kva x former in bank a two
Outage | J.E.26.07.23672 | C001860693 | Raymond Lewis | St.Ann | Completed | Load_246122 | Roaring River - 210 | Jul 21, 2026 9:30am | Jul 21, 2026 9:31am | Jul 21, 2026 10:03am | Jul 21, 2026 10:03am | Jul 21, 2026 10:03am | Jul 21, 2026 10:11pm | Jul 21, 2026 10:11am | Jul 21, 2026 10:11am |  |  | Fair | No | Sharlene Boothe making comeplion about nwc
Outage | J.E.26.07.23694 | C001860691 | Marlon Brown | Trelawny | Completed | Load_252012 | Duncans - 210 | Jul 21, 2026 9:27am | Jul 21, 2026 9:28am | Jul 21, 2026 10:46am | Jul 21, 2026 10:46am | Jul 21, 2026 11:41am | Jul 21, 2026 11:41am | Jul 21, 2026 11:42am | Jul 21, 2026 11:42am | BrokenWire |  | Fair | No | Premises closed
Outage | J.E.26.07.23615 | C001860686 | Neville Spencer | Clarendon | Completed | Load_573393 | Parnassus - 310 | Jul 21, 2026 9:24am | Jul 21, 2026 9:24am | Jul 21, 2026 10:10am | Jul 21, 2026 10:10am | Jul 21, 2026 10:23am | Jul 21, 2026 10:23am | Jul 21, 2026 10:49am | Jul 21, 2026 10:49am |  |  | Fair | No | Renew 2 blown 2 amp fuse protecting 5 kva xmfr in bank of 3 at pole # 0125732.Also renew blown 15 amp j/ fuse supply restored.
Outage | J.E.26.07.23604 | C001860685 | Wayne Dillion | St.Elizabeth | Completed | Load_252693 | Maggotty - 210 | Jul 21, 2026 9:22am | Jul 21, 2026 9:23am | Jul 21, 2026 10:38am | Jul 21, 2026 10:38am | Jul 21, 2026 11:07am | Jul 21, 2026 11:49am | Jul 21, 2026 11:49am | Jul 21, 2026 11:49am | Fire |  | Fair | No | Patrol and found secondary upper phase stranded out isolate 25 KVA transformer no pole number.splice and retention the same using 2 one bolt 20 feet of 2/0 conductor recluse transformer supply restored to customer successfully
Non-Outage | J.E.26.07.23091 | C001860683 | Wayne Dillion | null | Completed | null | null | Jul 21, 2026 9:18am | Jul 21, 2026 9:18am | Jul 21, 2026 10:17am | Jul 21, 2026 10:17am | Jul 21, 2026 10:17am | Jul 21, 2026 10:30am | Jul 21, 2026 10:30am | Jul 21, 2026 10:30am |  |  | Fair | No | Customer requested for a isolation to carry out maintenance work Open three 30 at junction no pole however this premises is located at new Forrest not in pepper
Non-Outage | J.E.26.07.23630 | C001860682 | Swon Miller | St.James | Completed | Load_555956 | Bogue - 410 | Jul 21, 2026 9:18am | Jul 22, 2026 10:09am | Jul 22, 2026 12:06pm | Jul 22, 2026 12:06pm | Jul 22, 2026 12:54pm | Jul 20, 2026 1:50am | Jul 22, 2026 1:50pm | Jul 22, 2026 1:50pm |  |  | Fair | No | Check and found customer single phasing cause by contamination at pothead clean and remake use 1pg voltage found 117 voltage left 117/116/234
Non-Outage | J.E.26.07.23651 | C001860676 | Barnett Brown | null | Completed | null | null | Jul 21, 2026 9:14am | Jul 21, 2026 9:15am | Jul 21, 2026 9:54am | Jul 21, 2026 9:54am | Jul 21, 2026 11:11am | Jul 21, 2026 11:43am | Jul 21, 2026 11:49am | Jul 21, 2026 11:49am |  |  | Fair | No | Replace blown 3 amp fuse with 8 amp, protecting 100 kva transformer
Outage | J.E.26.07.23390 | C001860671 | Richard Samuda | Manchester | Completed | Load_253356 | Spur Tree - 310 | Jul 21, 2026 9:06am | Jul 21, 2026 3:07pm | Jul 21, 2026 3:16pm | Jul 21, 2026 3:16pm | Jul 21, 2026 3:34pm | Jul 21, 2026 3:34pm | Jul 21, 2026 3:40pm | Jul 21, 2026 3:40pm |  |  | Fair | No | Customer say power was restored
Outage | J.E.26.07.23646 | C001860666 | Edward Royal | null | Completed | Load_270073 | null | Jul 21, 2026 9:02am | Jul 21, 2026 5:20pm | Jul 21, 2026 7:13pm | Jul 21, 2026 8:27pm | Jul 21, 2026 8:27pm | Jul 21, 2026 8:28pm | Jul 21, 2026 8:29pm | Jul 21, 2026 8:29pm |  |  | Fair | No | Contact customer by phone customer said the power was restored
Non-Outage | J.E.26.07.23139 | C001860658 | Edward Royal | null | Completed | null | null | Jul 21, 2026 9:00am | Jul 22, 2026 8:23am | Jul 22, 2026 9:47am | Jul 22, 2026 9:47am | Jul 22, 2026 9:47am | Jul 22, 2026 9:55am | Jul 22, 2026 9:55am | Jul 22, 2026 9:55am |  |  | Fair | No | Defective 15 Kva transformer needs change pole # 0052395 referred to maintenance
Non-Outage | J.E.26.07.23182 | C001860656 | Rusean Allen | null | Completed | null | null | Jul 21, 2026 9:00am | Jul 22, 2026 8:19am | Jul 22, 2026 1:49pm | Jul 22, 2026 1:49pm | Jul 22, 2026 2:05pm | Jul 22, 2026 2:05pm | Jul 22, 2026 2:06pm | Jul 22, 2026 2:06pm |  |  | Fair | No | Not found
Non-Outage | J.E.26.07.23378 | C001860654 | Barnett Brown | null | Completed | null | null | Jul 21, 2026 9:00am | Jul 21, 2026 9:02am | Jul 21, 2026 5:18pm | Jul 21, 2026 5:18pm | Jul 21, 2026 6:38pm | Jul 21, 2026 9:27pm | Jul 21, 2026 9:29pm | Jul 21, 2026 9:29pm |  |  | Fair | No | Splice and retention service wire
Outage | J.E.26.07.23418 | C001860655 | Barnett Brown | Manchester | Completed | Load_262762 | Kendal - 210 | Jul 21, 2026 9:00am | Jul 21, 2026 9:01am | Jul 21, 2026 3:10pm | Jul 21, 2026 3:10pm | Jul 21, 2026 4:27pm | Jul 21, 2026 5:16pm | Jul 21, 2026 5:18pm | Jul 21, 2026 5:18pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.23654 | C001860657 | Rusean Allen | KSAS | Completed | Load_290055 | Hunts Bay - 810 | Jul 21, 2026 9:00am | Jul 21, 2026 9:00am | Jul 21, 2026 9:51am | Jul 21, 2026 9:51am | Jul 21, 2026 10:43am | Jul 21, 2026 10:44am | Jul 21, 2026 10:44am | Jul 21, 2026 10:44am |  |  | Fair | No | Related to the burn box from yesterday
Outage | J.E.26.07.23568 | C001860653 | Richard Nicholas | St.Catherine | Completed | Load_266407 | Twickenham - 310 | Jul 21, 2026 8:57am | Jul 22, 2026 7:31am | Jul 22, 2026 8:15am | Jul 22, 2026 8:15am | Jul 22, 2026 9:47am | Jul 22, 2026 10:11am | Jul 22, 2026 10:12am | Jul 22, 2026 10:12am | BrokenWire |  | Fair | No | Area found ok,fault was rectified last night customer said.
Non-Outage | J.E.26.02.36056 | C001860646 | Dwain Samuels | Westmoreland | Completed | Load_265450 | Paradise - 210 | Jul 21, 2026 8:56am | Jul 21, 2026 8:58am | Jul 21, 2026 9:17am | Jul 21, 2026 11:40am | Jul 21, 2026 11:40am | Jul 21, 2026 11:44am | Jul 21, 2026 11:44am | Jul 21, 2026 11:44am |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.02.38771 | C001860651 | Dwain Samuels | Westmoreland | Completed | Load_240178 | Paradise - 210 | Jul 21, 2026 8:56am | Jul 21, 2026 8:58am | Jul 21, 2026 9:17am | Jul 21, 2026 11:35am | Jul 21, 2026 11:35am | Jul 21, 2026 11:36am | Jul 21, 2026 11:36am | Jul 21, 2026 11:36am |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.04.04408 | C001860652 | Dwain Samuels | null | Completed | null | null | Jul 21, 2026 8:56am | Jul 21, 2026 8:58am | Jul 21, 2026 9:17am | Jul 21, 2026 11:48am | Jul 21, 2026 11:48am | Jul 21, 2026 11:48am | Jul 21, 2026 11:49am | Jul 21, 2026 11:49am |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.02.26405 | C001860645 | Dwain Samuels | Hanover | Completed | Load_238992 | Orange Bay - 310 | Jul 21, 2026 8:55am | Jul 21, 2026 8:58am | Jul 21, 2026 9:17am | Jul 21, 2026 12:20pm | Jul 21, 2026 12:20pm | Jul 21, 2026 12:21pm | Jul 21, 2026 12:21pm | Jul 21, 2026 12:21pm |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.02.26824 | C001860644 | Dwain Samuels | Westmoreland | Completed | Load_247604 | Paradise - 110 | Jul 21, 2026 8:55am | Jul 21, 2026 8:58am | Jul 21, 2026 9:17am | Jul 21, 2026 9:28am | Jul 21, 2026 9:46am | Jul 21, 2026 9:54am | Jul 21, 2026 9:56am | Jul 21, 2026 9:56am |  |  | Fair | No | Meter found burnt needs to be changed ergently
Non-Outage | J.E.26.02.40337 | C001860643 | Dwain Samuels | null | Completed | null | null | Jul 21, 2026 8:55am | Jul 21, 2026 8:58am | Jul 21, 2026 9:17am | Jul 21, 2026 3:16pm | Jul 21, 2026 3:16pm | Jul 21, 2026 3:17pm | Jul 21, 2026 3:19pm | Jul 21, 2026 3:19pm |  |  | Rains | No | Customer said supply was restored
Non-Outage | J.E.26.07.22959 | C001860642 | Dwain Samuels | Westmoreland | Completed | Load_237679 | Paradise - 210 | Jul 21, 2026 8:54am | Jul 21, 2026 8:58am | Jul 21, 2026 9:17am | Jul 21, 2026 10:09am | Jul 21, 2026 10:09am | Jul 21, 2026 10:14am | Jul 21, 2026 10:15am | Jul 21, 2026 10:15am |  |  | Fair | No | Found working okay. Voltage check 115-116-231
Non-Outage | J.E.26.07.23161 | C001860631 | Error Coore | Manchester | Completed | Load_242813 | Spur Tree - 310 | Jul 21, 2026 8:50am | Jul 21, 2026 8:51am | Jul 21, 2026 1:29pm | Jul 21, 2026 1:29pm | Jul 21, 2026 1:46pm | Jul 21, 2026 2:00pm | Jul 21, 2026 2:02pm | Jul 21, 2026 2:02pm |  |  | Fair | No | Premise found ok voltage reading 116/115/231 volts
Non-Outage | J.E.26.07.23190 | C001860632 | Error Coore | Manchester | Completed | Load_244583 | Spur Tree - 310 | Jul 21, 2026 8:50am | Jul 21, 2026 8:51am | Jul 21, 2026 8:57am | Jul 21, 2026 8:57am | Jul 21, 2026 9:10am | Jul 21, 2026 1:16pm | Jul 21, 2026 1:21pm | Jul 21, 2026 1:21pm |  |  | Fair | No | Open a 25 KVA xformer to jump out a defective splicing sleeve and retention the span of secondary phase using 4 one bolt clamp voltage reading 118/117/235 volts
Non-Outage | J.E.26.07.23612 | C001860633 | Error Coore | Manchester | Completed | Load_260683 | Kendal - 310 | Jul 21, 2026 8:50am | Jul 21, 2026 8:51am | Jul 22, 2026 3:10pm | Jul 22, 2026 3:12pm | Jul 22, 2026 3:33pm | Jul 22, 2026 3:39pm | Jul 22, 2026 3:41pm | Jul 22, 2026 3:41pm |  |  | Fair | No | Premise not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.20044 | C001860628 | Rayon Foster | Hanover | Completed | Load_244707 | Orange Bay - 310 | Jul 21, 2026 8:49am | Jul 21, 2026 8:50am | Jul 21, 2026 11:57am | Jul 21, 2026 11:57am | Jul 21, 2026 12:06pm | Jul 21, 2026 12:45pm | Jul 21, 2026 12:45pm | Jul 21, 2026 12:45pm |  |  | Fair | No | Corrosion on jps pole and customer pathead was the cause of low repair using four clamps voltage after repair 116/114AB230
Non-Outage | J.E.26.07.23447 | C001860626 | Rayon Foster | Hanover | Completed | Load_244715 | Orange Bay - 310 | Jul 21, 2026 8:48am | Jul 21, 2026 8:50am | Jul 21, 2026 12:50pm | Jul 21, 2026 12:50pm | Jul 21, 2026 1:00pm | Jul 21, 2026 1:15pm | Jul 21, 2026 1:15pm | Jul 21, 2026 1:15pm |  |  | Fair | No | Unable to reach customer on cellphone and unable to locate meter unclear directions
Non-Outage | J.E.26.05.32908 | C001860624 | Error Coore | Manchester | Completed | Load_292949 | Spur Tree - 310 | Jul 21, 2026 8:47am | Jul 21, 2026 8:48am | Jul 22, 2026 12:18pm | Jul 22, 2026 12:18pm | Jul 22, 2026 12:48pm | Jul 22, 2026 12:59pm | Jul 22, 2026 1:00pm | Jul 22, 2026 1:00pm |  |  | Fair | No | Premise not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.18155 | C001860613 | Nicholas Dillon | Manchester | Completed | Load_238470 | Spur Tree - 210 | Jul 21, 2026 8:43am | Jul 21, 2026 8:44am | Jul 21, 2026 10:48am | Jul 21, 2026 3:02pm | Jul 21, 2026 3:05pm | Jul 21, 2026 3:05pm | Jul 21, 2026 3:06pm | Jul 21, 2026 3:06pm |  |  | Fair | Yes | Check and found corrosion at pothead clean corrosion use 2 pen union before I left voltage is 115 115 phase to phase 231
Non-Outage | J.E.26.07.18960 | C001860612 | Nicholas Dillon | Manchester | Completed | Load_264579 | Spur Tree - 210 | Jul 21, 2026 8:43am | Jul 21, 2026 8:44am | Jul 21, 2026 10:48am | Jul 22, 2026 10:20am | Jul 22, 2026 10:20am | Jul 22, 2026 10:22am | Jul 22, 2026 10:23am | Jul 22, 2026 10:23am |  |  | Fair | No | Unable to locate premises. Not getting customer by phone
Non-Outage | J.E.26.07.19264 | C001860610 | Nicholas Dillon | Manchester | Completed | Load_261914 | Spur Tree - 210 | Jul 21, 2026 8:43am | Jul 21, 2026 8:44am | Jul 21, 2026 10:48am | Jul 21, 2026 3:08pm | Jul 21, 2026 3:08pm | Jul 21, 2026 3:10pm | Jul 21, 2026 3:12pm | Jul 21, 2026 3:12pm |  |  | Fair | No | Check and found customer meter burn up refer to maintenance to change meter. Voltage is ok 112 114 phase to phase 227
Non-Outage | J.E.26.07.21523 | C001860608 | Nicholas Dillon | Manchester | Completed | Load_292982 | Spur Tree - 210 | Jul 21, 2026 8:43am | Jul 21, 2026 8:44am | Jul 21, 2026 10:48am | Jul 21, 2026 2:57pm | Jul 21, 2026 2:57pm | Jul 21, 2026 2:57pm | Jul 21, 2026 2:58pm | Jul 21, 2026 2:58pm |  |  | Fair | Yes | Check and found corrosion at pole clean corrosion use 2 one bolt clamp before I left voltage is 109 109 phase to phase 219
Non-Outage | J.E.26.07.21643 | C001860609 | Nicholas Dillon | Manchester | Completed | Load_262636 | Spur Tree - 210 | Jul 21, 2026 8:43am | Jul 21, 2026 8:44am | Jul 21, 2026 10:48am | Jul 21, 2026 12:30pm | Jul 21, 2026 12:57pm | Jul 21, 2026 12:57pm | Jul 21, 2026 1:52pm | Jul 21, 2026 1:52pm |  |  | Fair | Yes | Check and found service wire burn up charge service wire and use 3 one bolt clamp and 3 pen union before I left voltage is 106 106 phase to phase 212
Non-Outage | J.E.26.07.22308 | C001860606 | Nicholas Dillon | Manchester | Completed | Load_251650 | Spur Tree - 210 | Jul 21, 2026 8:42am | Jul 21, 2026 8:44am | Jul 21, 2026 10:48am | Jul 21, 2026 4:12pm | Jul 21, 2026 4:12pm | Jul 21, 2026 4:12pm | Jul 21, 2026 4:13pm | Jul 21, 2026 4:13pm |  |  | Fair | Yes | Check and found corrosion at pole clean corrosion use 1 one bolt clamp before I left voltage is 107 110 phase to phase 217
Non-Outage | J.E.26.07.22367 | C001860605 | Nicholas Dillon | Manchester | Completed | Load_253297 | Spur Tree - 210 | Jul 21, 2026 8:42am | Jul 21, 2026 8:44am | Jul 21, 2026 10:48am | Jul 22, 2026 5:10pm | Jul 22, 2026 5:35pm | Jul 22, 2026 6:05pm | Jul 22, 2026 6:06pm | Jul 22, 2026 6:06pm |  |  | Fair | Yes | Check and found corrosion at pole clean corrosion and use 2 one bolt clamp before I left voltage is 111 111 phase to phase 222
Non-Outage | J.E.26.07.22420 | C001860604 | Nicholas Dillon | Manchester | Completed | Load_260212 | Spur Tree - 210 | Jul 21, 2026 8:42am | Jul 21, 2026 8:44am | Jul 21, 2026 10:48am | Jul 21, 2026 1:55pm | Jul 21, 2026 1:55pm | Jul 21, 2026 2:12pm | Jul 21, 2026 2:16pm | Jul 21, 2026 2:16pm |  |  | Fair | No | Check voltage before at meter 104 96 phase to phase 199. Whole area experiencing low voltage refer to maintenance to top up the transformer
Non-Outage | J.E.26.07.23167 | C001860602 | Nicholas Dillon | Manchester | Completed | Load_251650 | Spur Tree - 210 | Jul 21, 2026 8:42am | Jul 21, 2026 8:44am | Jul 21, 2026 10:48am | Jul 21, 2026 3:22pm | Jul 21, 2026 3:22pm | Jul 21, 2026 3:50pm | Jul 21, 2026 3:51pm | Jul 21, 2026 3:51pm |  |  | Fair | No | Check voltage before at meter 110 104 phase to phase 214. Premises found working ok
Outage | J.E.26.07.23628 | C001860607 | Swon Miller | Trelawny | Completed | Load_245327 | Duncans - 210 | Jul 21, 2026 8:42am | Jul 21, 2026 8:43am | Jul 21, 2026 9:27am | Jul 21, 2026 9:29am | Jul 21, 2026 9:34am | Jul 21, 2026 9:25am | Jul 21, 2026 9:41am | Jul 21, 2026 9:41am |  |  | Fair | No | Check and found okay voltage found 115/114/229 voltage left 115/114/229
Non-Outage | J.E.26.06.11912 | C001860600 | Nicholas Dillon | St.Elizabeth | Completed | Load_250863 | Maggotty - 110 | Jul 21, 2026 8:41am | Jul 21, 2026 8:44am | Jul 21, 2026 10:48am | Jul 22, 2026 11:07am | Jul 22, 2026 11:56am | Jul 22, 2026 11:56am | Jul 22, 2026 11:57am | Jul 22, 2026 11:57am |  |  | Fair | Yes | Check and found corrosion at pole clean corrosion use 1 one bolt clamp before I left voltage is 110 110 phase to phase 221
Non-Outage | J.E.26.07.22642 | C001860592 | Damion Reid | null | Completed | null | null | Jul 21, 2026 8:39am | Jul 21, 2026 9:03am | Jul 21, 2026 11:44am | Jul 21, 2026 11:44am | Jul 21, 2026 12:29pm | Jul 21, 2026 1:09pm | Jul 21, 2026 1:10pm | Jul 21, 2026 1:10pm |  |  | Fair | No | Area found ok
Non-Outage | J.E.26.07.23265 | C001860591 | Damion Reid | null | Completed | null | null | Jul 21, 2026 8:39am | Jul 21, 2026 9:04am | Jul 21, 2026 10:31am | Jul 21, 2026 10:31am | Jul 21, 2026 10:48am | Jul 21, 2026 11:37am | Jul 21, 2026 11:39am | Jul 21, 2026 11:39am |  |  | Fair | No | Blown 10amp junction fuse found line patrol nothing was found blown fuse replace
Non-Outage | J.E.26.07.21580 | C001860581 | Andrae Dawkins | St.James | Completed | Load_260922 | Queens Drive - 710 | Jul 21, 2026 8:31am | Jul 21, 2026 8:31am | Jul 21, 2026 8:52am | Jul 21, 2026 9:37am | Jul 21, 2026 10:20am | Jul 21, 2026 9:59am | Jul 21, 2026 10:34am | Jul 21, 2026 10:34am |  |  | Fair | No | Unable to locate customer due to no directions also unable to reach customer phone
Non-Outage | J.E.26.07.21582 | C001860582 | Andrae Dawkins | St.James | Completed | Load_260922 | Queens Drive - 710 | Jul 21, 2026 8:31am | Jul 21, 2026 8:31am | Jul 21, 2026 8:52am | Jul 21, 2026 10:34am | Jul 21, 2026 10:35am | Jul 21, 2026 9:59am | Jul 21, 2026 10:35am | Jul 21, 2026 10:35am |  |  | Fair | No | Unable to locate customer due to no directions also unable to reach customer phone
Non-Outage | J.E.26.07.21754 | C001860580 | Andrae Dawkins | St.James | Completed | Load_239266 | Queens Drive - 710 | Jul 21, 2026 8:31am | Jul 21, 2026 8:31am | Jul 21, 2026 1:18pm | Jul 21, 2026 1:20pm | Jul 21, 2026 1:21pm | Jul 21, 2026 1:22pm | Jul 21, 2026 1:22pm | Jul 21, 2026 1:22pm |  |  | Fair | No | Check and found ok customer said that the problem was already resolved
Non-Outage | J.E.26.07.15033 | C001860574 | Andrae Dawkins | St.James | Completed | Load_251737 | Queens Drive - 810 | Jul 21, 2026 8:28am | Jul 21, 2026 8:31am | Jul 21, 2026 1:22pm | Jul 21, 2026 1:22pm | Jul 21, 2026 2:06pm | Jul 21, 2026 2:51pm | Jul 21, 2026 3:26pm | Jul 21, 2026 3:26pm |  |  | Fair | No | Found customer experiencing low voltage five pole span from transformer voltage found 108/100/208 voltage found at transformer pole 122/122/245 voltage found two pole span from transformer 108/113/222 urgent attention required
Non-Outage | J.E.26.07.15102 | C001860573 | Andrae Dawkins | St.James | Completed | Load_260850 | Rose Hall - 210 | Jul 21, 2026 8:27am | Jul 21, 2026 8:28am | Jul 21, 2026 1:15pm | Jul 21, 2026 1:15pm | Jul 21, 2026 1:15pm | Jul 21, 2026 1:05pm | Jul 21, 2026 1:16pm | Jul 21, 2026 1:16pm |  |  | Fair | No | Unable to locate customer customer mobile not registered
Non-Outage | J.E.26.07.15406 | C001860572 | Andrae Dawkins | St.James | Completed | Load_260850 | Rose Hall - 210 | Jul 21, 2026 8:27am | Jul 21, 2026 8:28am | Jul 21, 2026 1:12pm | Jul 21, 2026 1:12pm | Jul 21, 2026 1:12pm | Jul 21, 2026 1:05pm | Jul 21, 2026 1:14pm | Jul 21, 2026 1:14pm |  |  | Fair | No | Unable to reach customer customer mobile not registered
Non-Outage | J.E.26.07.15434 | C001860571 | Andrae Dawkins | St.James | Completed | Load_269402 | Rose Hall - 210 | Jul 21, 2026 8:27am | Jul 21, 2026 8:27am | Jul 21, 2026 11:06am | Jul 21, 2026 12:19pm | Jul 21, 2026 12:21pm | Jul 21, 2026 12:19pm | Jul 21, 2026 12:22pm | Jul 21, 2026 12:22pm |  |  | Fair | No | Check and found ok customer said that the problem was already resolved
Non-Outage | J.E.26.07.16206 | C001860570 | Andrae Dawkins | St.James | Completed | Load_269402 | Rose Hall - 210 | Jul 21, 2026 8:27am | Jul 21, 2026 8:27am | Jul 21, 2026 10:14am | Jul 21, 2026 10:41am | Jul 21, 2026 10:55am | Jul 21, 2026 10:54am | Jul 21, 2026 11:05am | Jul 21, 2026 11:05am |  |  | Fair | No | Check and found ok customer said that it was the breaker in her house was the issue
Non-Outage | J.E.26.07.16214 | C001860569 | Andrae Dawkins | St.James | Completed | Load_267001 | Rose Hall - 210 | Jul 21, 2026 8:26am | Jul 21, 2026 8:27am | Jul 21, 2026 10:14am | Jul 21, 2026 12:24pm | Jul 21, 2026 12:48pm | Jul 21, 2026 12:45pm | Jul 21, 2026 12:51pm | Jul 21, 2026 12:51pm |  |  | Fair | No | Unable to locate customer due to no directions also unable to reach customer mobile
Non-Outage | J.E.26.07.16244 | C001860568 | Andrae Dawkins | St.James | Completed | Load_269402 | Rose Hall - 210 | Jul 21, 2026 8:26am | Jul 21, 2026 8:27am | Jul 21, 2026 10:14am | Jul 21, 2026 11:46am | Jul 21, 2026 12:03pm | Jul 21, 2026 12:06pm | Jul 21, 2026 12:12pm | Jul 21, 2026 12:12pm |  |  | Fair | No | Check and found ok customer said that the problem was already resolved
Outage | J.E.26.07.23592 | C001860567 | Neville Spencer | Clarendon | Completed | Load_268434 | May Pen - 210 | Jul 21, 2026 8:26am | Jul 21, 2026 10:27am | Jul 21, 2026 10:50am | Jul 21, 2026 10:50am | Jul 21, 2026 10:59am | Jul 21, 2026 10:59am | Jul 21, 2026 11:39am | Jul 21, 2026 11:39am |  |  | Fair | No | Renew blown 15 amp j/ fuse at pole # 024026.Also renew blown 20 & 30 amp j/ fuse area restored.
Outage | J.E.26.07.23116 | C001860563 | Rusean Allen | KSAS | Completed | Load_254544 | Hunts Bay - 310 | Jul 21, 2026 8:25am | Jul 21, 2026 8:59am | Jul 21, 2026 12:05pm | Jul 21, 2026 12:05pm | Jul 21, 2026 12:10pm | Jul 21, 2026 12:23pm | Jul 21, 2026 12:23pm | Jul 21, 2026 12:23pm |  |  | Fair | No | Meter not communicating Refer to field service department
Outage | J.E.26.07.23540 | C001860559 | Ryan Richards | Manchester | Completed | Load_250755 | Spur Tree - 310 | Jul 21, 2026 8:24am | Jul 21, 2026 8:25am | Jul 21, 2026 8:30am | Jul 21, 2026 8:30am | Jul 21, 2026 10:01am | Jul 21, 2026 2:46pm | Jul 21, 2026 2:46pm | Jul 21, 2026 2:46pm | LeaningPole |  | Fair | No | Dislocated DV primary insulators and burn pole top Found line patrol where 1 span of broken secondary phase and neutral found further check made where two trip savers found down at Lancaster….open the other trip saver …replace dislocated DV insulator pole top lop and insulator and retention primary …..splice and retention secondary conductors using 60ft#2/0 aluminum 1#2/0 preform 4 one bolt clamps and reclose tripped savers at Lancaster all customers are now with supply
Outage | J.E.26.07.23610 | C001860562 | Rusean Allen | KSAS | Completed | Load_249126 | Up Park Camp - 510 | Jul 21, 2026 8:24am | Jul 21, 2026 8:59am | Jul 21, 2026 10:46am | Jul 21, 2026 10:46am | Jul 21, 2026 11:59am | Jul 21, 2026 12:02pm | Jul 21, 2026 12:04pm | Jul 21, 2026 12:04pm | BrokenPole |  | Fair | No | 30ft class 6 pole need to change Contains streetlight and triple x
Non-Outage | J.E.26.07.09084 | C001860557 | Junior Scarlett | St.James | Completed | Load_575863 | Bogue - 410 | Jul 21, 2026 8:23am | Jul 21, 2026 8:24am | Jul 21, 2026 8:49am | Jul 21, 2026 12:15pm | Jul 21, 2026 1:10pm | Jul 21, 2026 1:38pm | Jul 21, 2026 1:37pm | Jul 21, 2026 1:37pm |  |  | Fair | No | Change one clampVoltage found 115v 114v 229vVoltage leave 115v 114v 229v
Non-Outage | J.E.26.07.22741 | C001860551 | Fredrick Hamilton | KSAS | Completed | Load_247730 | Duhaney - 310 | Jul 21, 2026 8:21am | Jul 22, 2026 10:53am | Jul 22, 2026 11:01am | Jul 22, 2026 11:05am | Jul 22, 2026 11:13am | Jul 22, 2026 11:20am | Jul 22, 2026 11:21am | Jul 22, 2026 11:21am |  |  | Fair | No | Premises found ok at time of visit 235v/118v/119v obtained
Non-Outage | J.E.26.07.23089 | C001860550 | Tyrese Williams | St.Ann | Completed | Load_262861 | Cardiff Hall - 310 | Jul 21, 2026 8:21am | Jul 21, 2026 8:22am | Jul 21, 2026 8:31am | Jul 21, 2026 9:07am | Jul 21, 2026 9:52am | Jul 21, 2026 10:06am | Jul 21, 2026 10:06am | Jul 21, 2026 10:06am |  |  | Fair | No | Premises Found ok
Non-Outage | J.E.26.07.23519 | C001860552 | Eric Williams | KSAS | Completed | Load_254254 | Duhaney - 310 | Jul 21, 2026 8:21am | Jul 21, 2026 4:07pm | Jul 21, 2026 4:25pm | Jul 21, 2026 4:26pm | Jul 21, 2026 4:53pm | Jul 21, 2026 4:54pm | Jul 21, 2026 4:54pm | Jul 21, 2026 4:54pm | LowHangingWires |  | Fair | No | Not JPS wire, cable wire
Outage | J.E.26.07.23589 | C001860554 | Javid Vernon | Hanover | Completed | Load_240037 | Orange Bay - 310 | Jul 21, 2026 8:21am | Jul 21, 2026 8:22am | Jul 21, 2026 10:31am | Jul 21, 2026 10:31am | Jul 21, 2026 10:49am | Jul 21, 2026 11:04am | Jul 21, 2026 11:04am | Jul 21, 2026 11:04am |  |  | Fair | No | Premises check and found okay voltage reading 116/113/230
Outage | J.E.26.07.23591 | C001860555 | Javid Vernon | Hanover | Completed | Load_301764 | Orange Bay - 310 | Jul 21, 2026 8:21am | Jul 21, 2026 8:22am | Jul 21, 2026 9:44am | Jul 21, 2026 9:44am | Jul 21, 2026 10:14am | Jul 21, 2026 10:25am | Jul 21, 2026 10:27am | Jul 21, 2026 10:27am |  |  | Fair | No | Premises check and found okay voltage reading 108/108/216
Non-Outage | J.E.26.06.38611 | C001860546 | Dwain Samuels | Westmoreland | Completed | Load_237775 | Paradise - 210 | Jul 21, 2026 8:20am | Jul 21, 2026 8:20am | Jul 21, 2026 9:17am | Jul 21, 2026 11:22am | Jul 21, 2026 11:22am | Jul 21, 2026 11:22am | Jul 21, 2026 11:23am | Jul 21, 2026 11:23am |  |  | Fair | No | Area affected by low voltage. Area needs an additional transformer
Non-Outage | J.E.26.07.22570 | C001860545 | Oraine Minto | St.Ann | Completed | Load_252451 | Cardiff Hall - 310 | Jul 21, 2026 8:20am | Jul 21, 2026 8:21am | Jul 21, 2026 12:42pm | Jul 21, 2026 12:42pm | Jul 21, 2026 1:13pm | Jul 21, 2026 1:13pm | Jul 21, 2026 1:14pm | Jul 21, 2026 1:14pm |  |  | Fair | No | Premises not found Called customer and the person said she did not make a report
Non-Outage | J.E.26.07.23165 | C001860547 | Oraine Minto | St.Ann | Completed | Load_260245 | Cardiff Hall - 310 | Jul 21, 2026 8:20am | Jul 21, 2026 8:21am | Jul 21, 2026 10:24am | Jul 21, 2026 10:24am | Jul 21, 2026 11:02am | Jul 21, 2026 11:02am | Jul 21, 2026 11:03am | Jul 21, 2026 11:03am |  |  | Fair | No | Power was restored
Non-Outage | J.E.26.07.15755 | C001860544 | Oraine Minto | St.Ann | Completed | Load_237710 | Cardiff Hall - 310 | Jul 21, 2026 8:19am | Jul 21, 2026 8:20am | Jul 21, 2026 11:39am | Jul 21, 2026 11:40am | Jul 21, 2026 11:40am | Jul 21, 2026 11:41am | Jul 21, 2026 11:43am | Jul 21, 2026 11:43am | LeaningPole |  | Fair | No | Refer to maintenance Pole falling over in customer yard primary conductor almost touching a tree Photos taken
Non-Outage | J.E.26.07.18691 | C001860543 | Oraine Minto | St.Ann | Completed | Load_304934 | Cardiff Hall - 310 | Jul 21, 2026 8:19am | Jul 21, 2026 8:19am | Jul 21, 2026 3:46pm | Jul 21, 2026 3:46pm | Jul 21, 2026 4:07pm | Jul 21, 2026 4:08pm | Jul 21, 2026 4:08pm | Jul 21, 2026 4:08pm |  |  | Fair | No | 225v 113v 113v
Non-Outage | J.E.26.07.20648 | C001860541 | Oraine Minto | St.Ann | Completed | Load_262708 | Cardiff Hall - 310 | Jul 21, 2026 8:19am | Jul 21, 2026 8:19am | Jul 21, 2026 3:01pm | Jul 21, 2026 3:02pm | Jul 21, 2026 3:02pm | Jul 21, 2026 3:04pm | Jul 21, 2026 3:05pm | Jul 21, 2026 3:05pm |  |  | Fair | No | Issue resolved
Non-Outage | J.E.26.07.21196 | C001860542 | Oraine Minto | St.Ann | Completed | Load_242498 | Cardiff Hall - 310 | Jul 21, 2026 8:19am | Jul 21, 2026 8:19am | Jul 21, 2026 1:16pm | Jul 21, 2026 2:07pm | Jul 21, 2026 2:16pm | Jul 21, 2026 2:17pm | Jul 21, 2026 2:21pm | Jul 21, 2026 2:21pm |  |  | Fair | No | Refer to maintenance Secondary conductors need to change to the new pole customer meter not working and the old pole is falling unable to put ladder on it Old pole is 0185802
Outage | J.E.26.07.23587 | C001860540 | Swon Miller | St.James | Completed | Load_292863 | Queens Drive - 710 | Jul 21, 2026 8:18am | Jul 21, 2026 8:18am | Jul 21, 2026 9:41am | Jul 21, 2026 9:41am | Jul 21, 2026 9:41am | Jul 28, 2026 9:40am | Jul 21, 2026 9:51am | Jul 21, 2026 9:51am |  |  | Fair | No | Check and found okay internal work ongoing at the site voltage found 110/111/221 voltage left 110/111/221
Non-Outage | J.E.26.07.17013 | C001860537 | Nicholas Dillon | St.Elizabeth | Completed | Load_305116 | Maggotty - 110 | Jul 21, 2026 8:17am | Jul 21, 2026 8:18am | Jul 21, 2026 10:48am | Jul 21, 2026 10:57am | Jul 21, 2026 11:54am | Jul 21, 2026 11:54am | Jul 21, 2026 11:55am | Jul 21, 2026 11:55am |  |  | Fair | Yes | Check and found corrosion at pole clean corrosion and use 2 one bolt clamp before I left voltage is 113 114 phase to phase 228
Non-Outage | J.E.26.07.20353 | C001860538 | Oraine Minto | St.Ann | Completed | Load_262708 | Cardiff Hall - 310 | Jul 21, 2026 8:17am | Jul 21, 2026 8:18am | Jul 21, 2026 3:05pm | Jul 21, 2026 3:05pm | Jul 21, 2026 3:05pm | Jul 21, 2026 3:05pm | Jul 21, 2026 3:05pm | Jul 21, 2026 3:05pm |  |  | Fair | No | Issue was fixed
Non-Outage | J.E.26.07.20484 | C001860539 | Oraine Minto | St.Ann | Completed | Load_262708 | Cardiff Hall - 310 | Jul 21, 2026 8:17am | Jul 21, 2026 8:18am | Jul 21, 2026 2:33pm | Jul 21, 2026 2:33pm | Jul 21, 2026 2:33pm | Jul 21, 2026 2:33pm | Jul 21, 2026 2:33pm | Jul 21, 2026 2:33pm |  |  | Fair | No | Issue was resolved
Non-Outage | J.E.26.07.22634 | C001860536 | Milton Charlton | KSAN | Completed | Load_575759 | Hope - 310 | Jul 21, 2026 8:17am | Jul 21, 2026 8:17am | Jul 21, 2026 10:27am | Jul 21, 2026 10:27am | Jul 21, 2026 11:11am | Jul 21, 2026 11:05am | Jul 21, 2026 11:14am | Jul 21, 2026 11:14am |  |  | Fair | No | Change clamp on customer #6 triplex service wire using one 1- bolt clamp. Readings at meter socket 120-120-240 volts.
Non-Outage | J.E.26.07.23375 | C001860535 | Milton Charlton | KSAN | Completed | Load_252805 | Hope - 310 | Jul 21, 2026 8:17am | Jul 21, 2026 8:17am | Jul 21, 2026 11:44am | Jul 21, 2026 11:44am | Jul 21, 2026 12:17pm | Jul 21, 2026 12:16pm | Jul 21, 2026 12:20pm | Jul 21, 2026 12:20pm |  |  | Fair | No | Found okay upon arrival. Readings at meter socket117-117-234 volts.
Outage | J.E.26.07.23588 | C001860534 | Romeo Brissett | St.James | Completed | Load_301723 | Bogue - 310 | Jul 21, 2026 8:16am | Jul 21, 2026 8:16am | Jul 21, 2026 9:29am | Jul 21, 2026 9:29am | Jul 21, 2026 10:06am | Jul 21, 2026 10:15am | Jul 21, 2026 10:24am | Jul 21, 2026 10:24am |  |  | Fair | No | Found customer stanchion defective, customer was advised to get an electrician, however customer would need over 60ft estimated of #6 service wire, 3 links and 3 clamps
Outage | J.E.26.07.23128 | C001860523 | Milton Charlton | KSAN | Completed | Load_243040 | Washington Blvd - 310 | Jul 21, 2026 8:15am | Jul 22, 2026 8:30am | Jul 22, 2026 9:58am | Jul 22, 2026 10:21am | Jul 22, 2026 10:21am | Jul 22, 2026 10:20am | Jul 22, 2026 10:26am | Jul 22, 2026 10:26am | LeaningPole |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.07.23286 | C001860522 | Fitzroy Turner | KSAN | Completed | Load_249802 | Washington Blvd - 310 | Jul 21, 2026 8:15am | Jul 21, 2026 8:15am | Jul 21, 2026 11:35am | Jul 21, 2026 11:35am | Jul 21, 2026 11:40am | Jul 21, 2026 11:41am | Jul 21, 2026 11:44am | Jul 21, 2026 11:44am |  |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.07.23417 | C001860521 | Fitzroy Turner | KSAN | Completed | Load_575407 | Washington Blvd - 710 | Jul 21, 2026 8:15am | Jul 21, 2026 8:15am | Jul 21, 2026 12:12pm | Jul 21, 2026 12:14pm | Jul 21, 2026 12:14pm | Jul 21, 2026 12:14pm | Jul 21, 2026 12:15pm | Jul 21, 2026 12:15pm |  |  | Fair | No | Customer supply restored with the help of the call center
Outage | J.E.26.07.23459 | C001860525 | Milton Charlton | KSAS | Completed | Load_406024 | Three Miles - 410 | Jul 21, 2026 8:15am | Jul 22, 2026 8:21am | Jul 22, 2026 11:10am | Jul 22, 2026 11:10am | Jul 22, 2026 11:39am | Jul 22, 2026 11:40am | Jul 22, 2026 11:41am | Jul 22, 2026 11:41am |  |  | Fair | No | Unable to locate customer by telephone. Telephone number temporarily out of service..
Outage | J.E.26.07.23598 | C001860526 | Hartley Chin | St.Ann | Completed | Load_260792 | Cardiff Hall - 310 | Jul 21, 2026 8:15am | Jul 21, 2026 8:16am | Jul 21, 2026 12:24pm | Jul 21, 2026 12:24pm | Jul 21, 2026 1:55pm | Jul 21, 2026 2:22pm | Jul 21, 2026 2:23pm | Jul 21, 2026 2:23pm |  |  | Fair | No | Found two out of three blown 20 AMP junction at pole # 025130, Line patrolled and refused .
Outage | J.E.26.07.23584 | C001860520 | Tajay Bernard | Hanover | Completed | Load_575279 | Orange Bay - 310 | Jul 21, 2026 8:14am | Jul 21, 2026 8:15am | Jul 21, 2026 8:48am | Jul 21, 2026 8:55am | Jul 21, 2026 8:55am | Jul 21, 2026 10:11am | Jul 21, 2026 10:14am | Jul 21, 2026 10:14am |  |  | Fair | No | Isolate 1 25kva Transformer to clean and remake transformer drop Leeds and 2 customer pothead use 9 clamps Voltage found 109Voltage left 109/108/217
Non-Outage | J.E.26.07.17438 | C001860518 | Collin Robinson | Portland | Completed | Load_263601 | Port Antonio - 310 | Jul 21, 2026 8:11am | Jul 21, 2026 8:12am | Jul 21, 2026 8:28am | Jul 21, 2026 8:28am | Jul 21, 2026 9:46am | Jul 21, 2026 9:51am | Jul 21, 2026 9:51am | Jul 21, 2026 9:51am |  |  | Rains | No | Repair corroded joint at pole and replace one bolt clamps Voltage reading 117v 118v 235v
Non-Outage | J.E.26.07.22580 | C001860516 | Andrae Clarke | Portland | Completed | Load_243555 | Port Antonio - 410 | Jul 21, 2026 8:10am | Jul 21, 2026 8:11am | Jul 21, 2026 12:25pm | Jul 21, 2026 12:25pm | Jul 21, 2026 12:25pm | Jul 21, 2026 12:32pm | Jul 21, 2026 1:55pm | Jul 21, 2026 1:55pm |  |  | Fair | No | Premises found okay
Non-Outage | J.E.26.07.22922 | C001860511 | Fredrick Hamilton | KSAN | Completed | Load_263471 | Washington Blvd - 410 | Jul 21, 2026 8:10am | Jul 21, 2026 8:11am | Jul 21, 2026 8:20am | Jul 21, 2026 9:40am | Jul 21, 2026 9:58am | Jul 21, 2026 10:03am | Jul 21, 2026 10:03am | Jul 21, 2026 10:03am |  |  | Fair | No | Fuse link open at location please send emergency crew
Non-Outage | J.E.26.07.22943 | C001860514 | Andrae Clarke | Portland | Completed | Load_351431 | Port Antonio - 410 | Jul 21, 2026 8:10am | Jul 21, 2026 8:11am | Jul 21, 2026 8:29am | Jul 21, 2026 8:30am | Jul 21, 2026 10:35am | Jul 21, 2026 10:29am | Jul 21, 2026 10:38am | Jul 21, 2026 10:38am |  |  | Rains | No | Fuse holder burn need one fuse holder Refer to Emergency Crew
Non-Outage | J.E.26.07.23028 | C001860512 | Fredrick Hamilton | KSAN | Completed | Load_247215 | Washington Blvd - 410 | Jul 21, 2026 8:10am | Jul 21, 2026 8:11am | Jul 21, 2026 8:20am | Jul 21, 2026 8:48am | Jul 21, 2026 9:26am | Jul 21, 2026 9:36am | Jul 21, 2026 9:36am | Jul 21, 2026 9:36am |  |  | Fair | No | Please assign to emergency crew location having low voltage fluctuations CT 3 phase supply Location is Lasco financial
Non-Outage | J.E.26.07.23169 | C001860509 | Fredrick Hamilton | KSAN | Completed | Load_557747 | Washington Blvd - 610 | Jul 21, 2026 8:10am | Jul 21, 2026 8:11am | Jul 21, 2026 8:20am | Jul 21, 2026 8:23am | Jul 21, 2026 8:23am | Jul 21, 2026 8:26am | Jul 21, 2026 8:26am | Jul 21, 2026 8:26am |  |  | Fair | No | Customer contacted and stated that power was restored yesterday Premises is ok
Non-Outage | J.E.26.07.23171 | C001860510 | Fredrick Hamilton | KSAN | Completed | Load_250041 | Constant Spring - 410 | Jul 21, 2026 8:10am | Jul 21, 2026 8:11am | Jul 21, 2026 8:20am | Jul 21, 2026 10:42am | Jul 21, 2026 10:42am | Jul 21, 2026 10:44am | Jul 21, 2026 10:44am | Jul 21, 2026 10:44am |  |  | Fair | No | 234v/119v/115v obtained no JPS defect detected at location Customer advised
Non-Outage | J.E.26.07.23261 | C001860513 | Andrae Clarke | Portland | Completed | Load_243555 | Port Antonio - 410 | Jul 21, 2026 8:10am | Jul 21, 2026 8:11am | Jul 21, 2026 10:38am | Jul 21, 2026 10:38am | Jul 21, 2026 12:22pm | Jul 21, 2026 12:21pm | Jul 21, 2026 12:25pm | Jul 21, 2026 12:25pm |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.23517 | C001860515 | Oshane Warren | St.Elizabeth | Completed | Load_292266 | Maggotty - 110 | Jul 21, 2026 8:10am | Jul 21, 2026 9:46pm | Jul 21, 2026 10:22pm | Jul 21, 2026 10:30pm | Jul 21, 2026 11:34pm | Jul 21, 2026 11:37pm | Jul 21, 2026 11:39pm | Jul 21, 2026 11:39pm |  |  | Rains | No | Check and found okay voltage 118 118 236
Outage | J.E.26.07.23581 | C001860508 | Tyrese Williams | St.Ann | Completed | Load_242864 | Cardiff Hall - 310 | Jul 21, 2026 8:06am | Jul 21, 2026 8:07am | Jul 21, 2026 8:31am | Jul 21, 2026 10:07am | Jul 21, 2026 10:47am | Jul 21, 2026 10:57am | Jul 21, 2026 10:57am | Jul 21, 2026 10:57am |  |  | Fair | No | Replace a 8 amp junction fuse at pole
Outage | J.E.26.07.23561 | C001860504 | Raymond Carr | St.Ann | Completed | Load_261238 | Upper White River - 110 | Jul 21, 2026 8:04am | Jul 21, 2026 8:06am | Jul 21, 2026 10:21am | Jul 21, 2026 10:21am | Jul 21, 2026 11:14am | Jul 21, 2026 11:39am | Jul 21, 2026 11:44am | Jul 21, 2026 11:44am |  |  | Fair | No | Blown junction fuse found at pole number 565261, line patrol and found okay however tree contact was suspected. A 30 amp fuse was used to renew supply was restored.
Non-Outage | J.E.26.07.22594 | C001860500 | Stephen Taylor | St.Thomas | Completed | Load_261279 | Good Year - 210 | Jul 21, 2026 7:59am | Jul 21, 2026 8:08am | Jul 21, 2026 12:14pm | Jul 21, 2026 12:14pm | Jul 21, 2026 12:38pm | Jul 21, 2026 12:38pm | Jul 21, 2026 1:02pm | Jul 21, 2026 1:02pm |  |  | Fair | No | Premise found found found okay reading 111,110
Non-Outage | J.E.26.07.22973 | C001860499 | Hopeton Henry | St.Thomas | Completed | Load_266044 | Good Year - 210 | Jul 21, 2026 7:59am | Jul 22, 2026 10:00am | Jul 22, 2026 10:23am | Jul 22, 2026 3:09pm | Jul 22, 2026 3:09pm | Jul 22, 2026 3:10pm | Jul 22, 2026 3:12pm | Jul 22, 2026 3:12pm |  |  | Fair | No | Refresh connection at pot head112-115-227 volts
Non-Outage | J.E.26.07.23312 | C001860496 | Stephen Taylor | null | Completed | null | null | Jul 21, 2026 7:59am | Jul 21, 2026 8:08am | Jul 21, 2026 8:58am | Jul 21, 2026 8:58am | Jul 21, 2026 11:19am | Jul 21, 2026 11:19am | Jul 21, 2026 11:20am | Jul 21, 2026 11:20am | LowHangingWires |  | Fair | No | Patrol the area no low hanging wire see a lot of call to single customer no one answered the phone
Non-Outage | J.E.26.07.23336 | C001860494 | Odaine Johnson | Clarendon | Completed | Load_238199 | Parnassus - 310 | Jul 21, 2026 7:59am | Jul 21, 2026 8:00am | Jul 21, 2026 8:56am | Jul 21, 2026 11:21am | Jul 21, 2026 12:05pm | Jul 21, 2026 12:05pm | Jul 21, 2026 12:06pm | Jul 21, 2026 12:06pm |  |  | Fair | No | Premises found okay voltage reading 116/116/232 volts
Non-Outage | J.E.26.07.23358 | C001860495 | Stephen Taylor | St.Thomas | Completed | Load_257499 | Good Year - 210 | Jul 21, 2026 7:59am | Jul 21, 2026 8:08am | Jul 21, 2026 2:55pm | Jul 21, 2026 2:55pm | Jul 21, 2026 3:26pm | Jul 21, 2026 3:26pm | Jul 21, 2026 3:28pm | Jul 21, 2026 3:28pm |  |  | Fair | No | Clean up single phase wire and customer is now okay
Non-Outage | J.E.26.07.23234 | C001860493 | Tajay Bernard | null | Completed | null | null | Jul 21, 2026 7:54am | Jul 21, 2026 7:54am | Jul 21, 2026 11:01am | Jul 21, 2026 11:01am | Jul 21, 2026 11:01am | Jul 21, 2026 11:01am | Jul 21, 2026 11:02am | Jul 21, 2026 11:02am |  |  | Fair | No | Customer stated that power was restored
Non-Outage | J.E.26.07.23193 | C001860492 | Fredrick Hamilton | KSAN | Completed | Load_250041 | Constant Spring - 410 | Jul 21, 2026 7:53am | Jul 21, 2026 7:53am | Jul 21, 2026 8:00am | Jul 21, 2026 10:03am | Jul 21, 2026 10:14am | Jul 21, 2026 10:41am | Jul 21, 2026 10:41am | Jul 21, 2026 10:41am |  |  | Fair | No | 234v/115v/119v obtained no JPS defect detected
Outage | J.E.26.07.23369 | C001860491 | Christopher Edwards | KSAN | Completed | Load_249929 | Constant Spring - 410 | Jul 21, 2026 7:51am | Jul 21, 2026 7:51am | Jul 21, 2026 12:10pm | Jul 21, 2026 12:11pm | Jul 21, 2026 12:39pm | Jul 21, 2026 3:34pm | Jul 21, 2026 3:34pm | Jul 21, 2026 3:34pm |  | Y | Fair | No | Refuse blown junction fuseUsing (1) 30 amps
Outage | J.E.26.07.23456 | C001860489 | Christopher Edwards | KSAN | Completed | Load_270019 | Constant Spring - 410 | Jul 21, 2026 7:51am | Jul 21, 2026 7:51am | Jul 21, 2026 7:57am | Jul 21, 2026 11:40am | Jul 21, 2026 12:09pm | Jul 21, 2026 12:10pm | Jul 21, 2026 12:10pm | Jul 21, 2026 12:10pm |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Non-Outage | J.E.26.04.00063 | C001860484 | Swon Miller | St.James | Completed | Load_251418 | Queens Drive - 710 | Jul 21, 2026 7:50am | Jul 21, 2026 7:50am | Jul 21, 2026 11:03am | Jul 21, 2026 11:03am | Jul 21, 2026 11:30am | Jul 20, 2026 12:17am | Jul 21, 2026 12:42pm | Jul 21, 2026 12:42pm |  |  | Fair | No | Check and found okay voltage voltage found 108/108/217 voltage left 108/108/217
Outage | J.E.26.07.23478 | C001860483 | Milton Charlton | KSAN | Completed | Load_252899 | Hope - 410 | Jul 21, 2026 7:50am | Jul 21, 2026 7:50am | Jul 21, 2026 9:39am | Jul 21, 2026 9:39am | Jul 21, 2026 10:23am | Jul 21, 2026 10:05am | Jul 21, 2026 10:26am | Jul 21, 2026 10:26am |  |  | Fair | No | Reset customer circuit breaker that was tripped. Readings at meter socket118-118-236 volts.
Non-Outage | J.E.26.04.29936 | C001860480 | Swon Miller | St.James | Completed | Load_267271 | Queens Drive - 810 | Jul 21, 2026 7:49am | Jul 21, 2026 7:50am | Jul 21, 2026 9:51am | Jul 21, 2026 9:51am | Jul 21, 2026 10:07am | Jul 14, 2026 11:00am | Jul 21, 2026 11:02am | Jul 21, 2026 11:02am |  |  | Fair | No | Check and found customer single phasing cause by contamination at pole clean remake joints use 1 pg voltage found 115 voltage left 115/116/231
Non-Outage | J.E.26.07.07928 | C001860482 | Swon Miller | St.James | Completed | Load_270234 | Queens Drive - 710 | Jul 21, 2026 7:49am | Jul 21, 2026 7:50am | Jul 21, 2026 7:57am | Jul 21, 2026 7:57am | Jul 21, 2026 8:23am | Jul 21, 2026 9:15am | Jul 21, 2026 9:26am | Jul 21, 2026 9:26am | Fire |  | Fair | No | Found secondary lines bang up due to mid span connections open 50 kva transformer to carry out repairs retention secondary phase and remove illegal connections and close up 50 kva transformer
Non-Outage | J.E.26.07.08459 | C001860481 | Swon Miller | St.James | Completed | Load_254425 | Queens Drive - 710 | Jul 21, 2026 7:49am | Jul 21, 2026 7:50am | Jul 21, 2026 2:33pm | Jul 21, 2026 2:33pm | Jul 21, 2026 2:50pm | Jul 22, 2026 3:11am | Jul 21, 2026 3:11pm | Jul 21, 2026 3:11pm |  |  | Fair | No | Check and found okay voltage found 109/108/217 voltage left 109/108/217
Non-Outage | J.E.26.07.16409 | C001860476 | Romeo Brissett | St.James | Completed | Load_269249 | Bogue - 310 | Jul 21, 2026 7:47am | Jul 21, 2026 7:47am | Jul 21, 2026 9:32am | Jul 21, 2026 10:51am | Jul 21, 2026 10:51am | Jul 21, 2026 10:51am | Jul 21, 2026 10:52am | Jul 21, 2026 10:52am |  |  | Fair | No | Customer stated issue resolved.
Non-Outage | J.E.26.07.23316 | C001860478 | Raymond Lewis | null | Completed | null | null | Jul 21, 2026 7:47am | Jul 21, 2026 7:48am | Jul 21, 2026 11:04am | Jul 21, 2026 11:04am | Jul 21, 2026 11:04am | Jul 21, 2026 11:14pm | Jul 21, 2026 11:15am | Jul 21, 2026 11:15am |  |  | Fair | No | Voltage found 232:229:238:399:404:412
Outage | J.E.26.07.23415 | C001860479 | Raymond Lewis | St.Ann | Completed | Load_240824 | Roaring River - 210 | Jul 21, 2026 7:47am | Jul 21, 2026 7:48am | Jul 21, 2026 8:29am | Jul 21, 2026 8:30am | Jul 21, 2026 9:09am | Jul 21, 2026 9:57pm | Jul 21, 2026 9:57am | Jul 21, 2026 9:57am |  |  | Fair | No | Customer problem
Non-Outage | J.E.26.07.05588 | C001860475 | Romeo Brissett | St.James | Completed | Load_1001899 | Bogue - 310 | Jul 21, 2026 7:46am | Jul 21, 2026 7:46am | Jul 21, 2026 7:53am | Jul 21, 2026 8:52am | Jul 21, 2026 8:52am | Jul 21, 2026 8:55am | Jul 21, 2026 9:04am | Jul 21, 2026 9:04am | BrokenPole |  | Fair | No | Found (1)30ft pole retired Leaning on customer property with 5 customer service wire from rammy system and streetlight, new pole exit beside old pole. Please to field service to transfer services wire and streetlight, and to maintenance to removed defective retired pole.
Non-Outage | J.E.26.07.23224 | C001860471 | Romeo Brissett | St.James | Completed | Load_301730 | Bogue - 310 | Jul 21, 2026 7:45am | Jul 21, 2026 7:46am | Jul 21, 2026 9:32am | Jul 21, 2026 10:24am | Jul 21, 2026 10:24am | Jul 21, 2026 10:48am | Jul 21, 2026 10:51am | Jul 21, 2026 10:51am |  |  | Fair | No | Found customer service wire, broken in midair, spliced and retention customer service wire.
Non-Outage | J.E.26.07.23508 | C001860470 | Edward Royal | null | Completed | null | null | Jul 21, 2026 7:44am | Jul 21, 2026 7:47am | Jul 21, 2026 11:05am | Jul 21, 2026 11:05am | Jul 21, 2026 11:33am | Jul 21, 2026 1:31pm | Jul 21, 2026 1:31pm | Jul 21, 2026 1:31pm | Fire |  | Fair | No | Replaced 3A transformer fuse
Non-Outage | J.E.26.07.23465 | C001860469 | Floyd Taylor | Trelawny | Completed | Load_243007 | Greenwood - 110 | Jul 21, 2026 7:42am | Jul 21, 2026 7:43am | Jul 21, 2026 8:42am | Jul 21, 2026 8:42am | Jul 21, 2026 9:13am | Jul 21, 2026 11:06am | Jul 21, 2026 11:10am | Jul 21, 2026 11:10am | Fire |  | Fair | No | Isolate 25kva transformer, splice and retention 2 spands of secondary conductor using 20 ft of number 2AAC and 3pg clamp, voltage reading left 114,117,231
Outage | J.E.26.07.23426 | C001860468 | Javid Vernon | Hanover | Completed | Load_262008 | Orange Bay - 310 | Jul 21, 2026 7:42am | Jul 21, 2026 7:44am | Jul 21, 2026 2:09pm | Jul 21, 2026 2:09pm | Jul 21, 2026 2:47pm | Jul 21, 2026 2:53pm | Jul 21, 2026 2:53pm | Jul 21, 2026 2:53pm | BrokenWire |  | Fair | No | Area check and found okay unable to locate customer and premises phone calls to customer number unanswered
Outage | J.E.26.07.23430 | C001860467 | Javid Vernon | Westmoreland | Completed | Load_292064 | Paradise - 110 | Jul 21, 2026 7:42am | Jul 21, 2026 8:31am | Jul 21, 2026 9:31am | Jul 21, 2026 11:04am | Jul 21, 2026 11:38am | Jul 21, 2026 12:30pm | Jul 21, 2026 12:31pm | Jul 21, 2026 12:31pm |  |  | Fair | No | Isolate 50kva transformer to remove illegal connections to splice and retention one pole span of secondary phase use 10ft #2 conductor one clamp and reclose 50kva transformer
Outage | J.E.26.07.23515 | C001860466 | Richman Whyte | Hanover | Completed | Load_247383 | Orange Bay - 310 | Jul 21, 2026 7:41am | Jul 21, 2026 3:26pm | Jul 21, 2026 9:45pm | Jul 21, 2026 9:45pm | Jul 21, 2026 9:45pm | Jul 21, 2026 9:45pm | Jul 21, 2026 9:46pm | Jul 21, 2026 9:46pm |  |  | Fair | No | Hexing area referr to field service
Outage | J.E.26.07.23444 | C001860460 | Romeo Brissett | St.James | Completed | Load_269651 | Bogue - 310 | Jul 21, 2026 7:40am | Jul 21, 2026 7:44am | Jul 21, 2026 8:00am | Jul 21, 2026 9:04am | Jul 21, 2026 9:15am | Jul 21, 2026 9:27am | Jul 21, 2026 9:28am | Jul 21, 2026 9:28am |  |  | Fair | No | Check and found rammy connection issue please send to field service. Single phasing coming from box
Non-Outage | J.E.26.07.21511 | C001860458 | Roemello Brown | Trelawny | Completed | Load_1001458 | Martha Brae - 110 | Jul 21, 2026 7:38am | Jul 21, 2026 7:38am | Jul 21, 2026 10:47am | Jul 21, 2026 10:55am | Jul 21, 2026 11:10am | Jul 21, 2026 11:10am | Jul 21, 2026 11:22am | Jul 21, 2026 11:22am |  |  | Fair | No | Have premises check premises found working okay Voltage found 118/119/237Voltage leave 118/119/237
Outage | J.E.26.07.23283 | C001860456 | Ricky Hall | St.Catherine | Completed | Load_257349 | Tredegar - 310 | Jul 21, 2026 7:38am | Jul 21, 2026 3:20pm | Jul 21, 2026 3:36pm | Jul 21, 2026 3:46pm | Jul 21, 2026 4:15pm | Jul 21, 2026 4:16pm | Jul 21, 2026 4:16pm | Jul 21, 2026 4:16pm | LowHangingWires,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | No low hanging wire seen
Outage | J.E.26.07.23510 | C001860454 | Richard Nicholas | St.Catherine | Completed | Load_255156 | Tredegar - 210 | Jul 21, 2026 7:38am | Jul 21, 2026 7:39am | Jul 21, 2026 11:09am | Jul 21, 2026 11:09am | Jul 21, 2026 11:55am | Jul 21, 2026 12:45pm | Jul 21, 2026 12:46pm | Jul 21, 2026 12:46pm |  |  | Fair | No | Replaced blown 50amp junctions fuse on pole #555196.
Outage | J.E.26.07.23523 | C001860455 | Richard Nicholas | St.Catherine | Completed | Load_239833 | Tredegar - 510 | Jul 21, 2026 7:38am | Jul 21, 2026 7:39am | Jul 21, 2026 10:22am | Jul 21, 2026 10:22am | Jul 21, 2026 10:56am | Jul 21, 2026 11:06am | Jul 21, 2026 11:08am | Jul 21, 2026 11:08am |  |  | Fair | No | Replaced blown 15amp junctions fuse on pole #0084854 and blown 15kva transformer 2amp fuse on pole #0101673.bird come in contact with line.
Outage | J.E.26.07.23533 | C001860459 | Richard Nicholas | St.Catherine | Completed | Load_245093 | Rhodens Pen - 210 | Jul 21, 2026 7:38am | Jul 21, 2026 7:39am | Jul 21, 2026 12:46pm | Jul 21, 2026 12:47pm | Jul 21, 2026 2:20pm | Jul 21, 2026 2:50pm | Jul 21, 2026 2:53pm | Jul 21, 2026 2:53pm |  |  | Fair | No | Replaced burnt out fuse holder with a 20amp junctions fuse on pole #0123716 and blown Rammy 15kva x2 transformer 5amp fuse on pole #0095315.one drop out switch operating two transformer on the same pole.
Non-Outage | J.E.26.07.22373 | C001860450 | Royston Montague | St.Catherine | Completed | Load_251951 | Tredegar - 510 | Jul 21, 2026 7:37am | Jul 21, 2026 7:40am | Jul 21, 2026 8:04am | Jul 21, 2026 10:31am | Jul 21, 2026 11:00am | Jul 21, 2026 11:03am | Jul 21, 2026 11:05am | Jul 21, 2026 11:05am |  |  | Fair | No | Full voltage found. 229v 114v 114v , not seeing anyone at home. Multiple calls to customer phone go without answer
Non-Outage | J.E.26.07.22473 | C001860449 | Royston Montague | St.Catherine | Completed | Load_262937 | Tredegar - 410 | Jul 21, 2026 7:37am | Jul 21, 2026 7:37am | Jul 21, 2026 8:04am | Jul 21, 2026 9:47am | Jul 21, 2026 10:03am | Jul 21, 2026 10:28am | Jul 21, 2026 10:28am | Jul 21, 2026 10:28am |  |  | Fair | No | Open phase at customer take off point. Same corrected. Voltage found 115v voltage after job completion are 227v 110v 114v
Non-Outage | J.E.26.07.22553 | C001860447 | Royston Montague | St.Catherine | Completed | Load_412872 | Tredegar - 510 | Jul 21, 2026 7:37am | Jul 21, 2026 7:37am | Jul 21, 2026 8:04am | Jul 21, 2026 11:06am | Jul 21, 2026 11:17am | Jul 21, 2026 12:13pm | Jul 21, 2026 12:14pm | Jul 21, 2026 12:14pm |  |  | Fair | No | Faulty neutral at customer take off point. Voltage found 165v 65v voltage after job completion are 229v 113v 113v
Non-Outage | J.E.26.07.22761 | C001860448 | Royston Montague | St.Catherine | Completed | Load_243635 | Twickenham - 310 | Jul 21, 2026 7:37am | Jul 21, 2026 7:37am | Jul 21, 2026 8:04am | Jul 21, 2026 8:48am | Jul 21, 2026 9:26am | Jul 21, 2026 9:46am | Jul 21, 2026 9:47am | Jul 21, 2026 9:47am |  |  | Fair | No | Defective transformer lug. Please inform maintenance department thanks. Many customer affecting.
Outage | J.E.26.07.23539 | C001860452 | Richard Nicholas | St.Catherine | Completed | Load_265602 | Tredegar - 510 | Jul 21, 2026 7:37am | Jul 21, 2026 7:39am | Jul 21, 2026 8:09am | Jul 21, 2026 8:09am | Jul 21, 2026 9:57am | Jul 21, 2026 10:20am | Jul 21, 2026 10:21am | Jul 21, 2026 10:21am | BrokenWire |  | Fair | No | Remade burnt off 3w service phase joint at pole,1 clamp was used.voltage reading 118x 2 and 236v.
Non-Outage | J.E.26.07.23055 | C001860446 | Royston Montague | St.Catherine | Completed | Load_557211 | Tredegar - 410 | Jul 21, 2026 7:36am | Jul 21, 2026 7:37am | Jul 21, 2026 8:04am | Jul 21, 2026 1:34pm | Jul 21, 2026 2:17pm | Jul 21, 2026 2:18pm | Jul 21, 2026 2:18pm | Jul 21, 2026 2:18pm | Fire |  | Fair | No | Team seen on location carrying out repair.
Non-Outage | J.E.26.07.23060 | C001860445 | Royston Montague | St.Catherine | Completed | Load_269355 | Tredegar - 210 | Jul 21, 2026 7:36am | Jul 21, 2026 7:37am | Jul 21, 2026 8:04am | Jul 21, 2026 12:35pm | Jul 21, 2026 12:36pm | Jul 21, 2026 12:38pm | Jul 21, 2026 12:38pm | Jul 21, 2026 12:38pm |  |  | Fair | No
Non-Outage | J.E.26.07.23310 | C001860444 | Royston Montague | St.Catherine | Completed | Load_251595 | Tredegar - 210 | Jul 21, 2026 7:36am | Jul 21, 2026 7:37am | Jul 21, 2026 8:04am | Jul 21, 2026 2:26pm | Jul 21, 2026 2:47pm | Jul 21, 2026 4:09pm | Jul 21, 2026 4:29pm | Jul 21, 2026 4:29pm |  |  | Fair | No | Faulty joint at transformer drop lead, 25kva transformer fuse open to do repair. 220v 108v 108
Outage | J.E.26.07.23553 | C001860442 | Tajay Bernard | Hanover | Completed | Load_252494 | Orange Bay - 310 | Jul 21, 2026 7:36am | Jul 21, 2026 7:36am | Jul 21, 2026 10:14am | Jul 21, 2026 10:14am | Jul 21, 2026 10:43am | Jul 21, 2026 10:59am | Jul 21, 2026 11:00am | Jul 21, 2026 11:00am |  |  | Fair | No | Refuse 1 25kva Transformer use 3amp fuse
Non-Outage | J.E.26.07.23326 | C001860439 | Roemello Brown | Trelawny | Completed | Load_267113 | Martha Brae - 110 | Jul 21, 2026 7:35am | Jul 21, 2026 7:35am | Jul 21, 2026 11:22am | Jul 21, 2026 11:24am | Jul 21, 2026 12:34pm | Jul 21, 2026 12:43pm | Jul 21, 2026 12:46pm | Jul 21, 2026 12:46pm |  |  | Fair | No | There is an outage in the area everyone affected
Outage | J.E.26.07.22434 | C001860440 | Hartley Chin | Clarendon | Completed | Load_251963 | May Pen - 110 | Jul 21, 2026 7:35am | Jul 21, 2026 7:42am | Jul 21, 2026 2:23pm | Jul 21, 2026 2:23pm | Jul 21, 2026 3:15pm | Jul 21, 2026 3:16pm | Jul 21, 2026 3:21pm | Jul 21, 2026 3:21pm |  |  | Fair | No | Premisis found ok. Voltage readings v114 - v113 - v228
Non-Outage | J.E.26.07.23340 | C001860438 | Roemello Brown | Trelawny | Completed | Load_412865 | Martha Brae - 110 | Jul 21, 2026 7:33am | Jul 21, 2026 7:35am | Jul 21, 2026 8:21am | Jul 21, 2026 9:17am | Jul 21, 2026 9:36am | Jul 21, 2026 9:36am | Jul 21, 2026 9:52am | Jul 21, 2026 9:52am |  |  | Fair | No | Premises check premises found working okay Voltage found 113/114/227Voltage leave 113/114/227
Non-Outage | J.E.26.07.23344 | C001860436 | Roemello Brown | Trelawny | Completed | Load_249132 | Martha Brae - 110 | Jul 21, 2026 7:33am | Jul 21, 2026 7:33am | Jul 21, 2026 9:30am | Jul 21, 2026 9:53am | Jul 21, 2026 10:22am | Jul 21, 2026 10:22am | Jul 21, 2026 10:46am | Jul 21, 2026 10:46am |  |  | Fair | No | One leg dropping below 100 need emergency team to assist also alot of illegal connections in the area need strike force team to assist as well Voltage found 120/102/222Voltage leave 120/102/222
Non-Outage | J.E.26.07.23384 | C001860435 | Roemello Brown | Trelawny | Completed | Load_292384 | Martha Brae - 110 | Jul 21, 2026 7:33am | Jul 21, 2026 7:33am | Jul 21, 2026 8:21am | Jul 21, 2026 8:21am | Jul 21, 2026 8:44am | Jul 21, 2026 8:44am | Jul 21, 2026 9:00am | Jul 21, 2026 9:00am |  |  | Fair | No | Premises check premises found working okay Voltage found 117/117/234Voltage leave 117/117/234
Non-Outage | J.E.26.07.23396 | C001860433 | Roemello Brown | Trelawny | Completed | Load_263107 | Martha Brae - 210 | Jul 21, 2026 7:33am | Jul 21, 2026 7:33am | Jul 21, 2026 9:38am | Jul 21, 2026 2:47pm | Jul 21, 2026 3:04pm | Jul 21, 2026 3:04pm | Jul 21, 2026 3:15pm | Jul 21, 2026 3:15pm |  |  | Fair | No | Have premises check premises found working okay Voltage found 118/118/236Voltage leave 118/118/236
Non-Outage | J.E.26.07.23401 | C001860434 | Roemello Brown | Trelawny | Completed | Load_262089 | Martha Brae - 210 | Jul 21, 2026 7:33am | Jul 21, 2026 7:33am | Jul 21, 2026 1:58pm | Jul 21, 2026 3:15pm | Jul 21, 2026 3:29pm | Jul 21, 2026 3:29pm | Jul 21, 2026 3:33pm | Jul 21, 2026 3:33pm |  |  | Fair | No | Have premises check premises found working okay Voltage found 118/118/236Voltage leave 118/118/236
Outage | J.E.26.07.23543 | C001860437 | Derrick Grubb | St.Thomas | Completed | Load_239440 | Good Year - 110 | Jul 21, 2026 7:33am | Jul 21, 2026 7:33am | Jul 21, 2026 8:54am | Jul 21, 2026 8:54am | Jul 21, 2026 8:54am | Jul 21, 2026 8:56am | Jul 21, 2026 8:56am | Jul 21, 2026 8:56am |  |  | Fair | No | Planed outage in the area.
Non-Outage | J.E.26.07.23222 | C001860431 | Marlon Brown | Trelawny | Completed | Load_245182 | Duncans - 210 | Jul 21, 2026 7:32am | Jul 21, 2026 7:32am | Jul 21, 2026 9:53am | Jul 21, 2026 9:53am | Jul 21, 2026 10:39am | Jul 21, 2026 10:45am | Jul 21, 2026 10:45am | Jul 21, 2026 10:45am |  |  | Fair | No | Unable to locate customer, however the school doesn’t know anyone by that name and they didn’t make any report to jps.
Non-Outage | J.E.26.07.23386 | C001860432 | Roemello Brown | Trelawny | Completed | Load_261797 | Martha Brae - 210 | Jul 21, 2026 7:32am | Jul 21, 2026 7:33am | Jul 21, 2026 2:01pm | Jul 21, 2026 2:01pm | Jul 21, 2026 2:04pm | Jul 21, 2026 2:27pm | Jul 21, 2026 2:47pm | Jul 21, 2026 2:47pm |  |  | Fair | No | Premises check premises found working okay Voltage found 115/116/231Voltage leave 115/116/231
Outage | J.E.26.07.22394 | C001860430 | Wan Carlos Scarlett | Portmore | Completed | Load_269140 | Naggo Head - 510 | Jul 21, 2026 7:31am | Jul 21, 2026 7:31am | Jul 21, 2026 7:45am | Jul 21, 2026 7:45am | Jul 21, 2026 8:46am | Jul 21, 2026 9:04am | Jul 21, 2026 9:04am | Jul 21, 2026 9:04am |  |  | Fair | No | Reset customer breaker power supply has been restored
Outage | J.E.26.07.22445 | C001860429 | Wan Carlos Scarlett | Portmore | Completed | Load_266899 | Naggo Head - 510 | Jul 21, 2026 7:31am | Jul 21, 2026 7:31am | Jul 21, 2026 2:09pm | Jul 21, 2026 2:09pm | Jul 21, 2026 2:54pm | Jul 21, 2026 3:10pm | Jul 21, 2026 3:11pm | Jul 21, 2026 3:11pm |  |  | Fair | No | Reach at location been calling customer but no answer premises closed
Outage | J.E.26.07.22985 | C001860428 | Wan Carlos Scarlett | Portmore | Completed | Load_240031 | Naggo Head - 610 | Jul 21, 2026 7:31am | Jul 21, 2026 7:31am | Jul 21, 2026 11:30am | Jul 21, 2026 11:30am | Jul 21, 2026 12:06pm | Jul 21, 2026 12:30pm | Jul 21, 2026 12:31pm | Jul 21, 2026 12:31pm |  |  | Fair | No | Reach at location been calling customer but no answer premises closed
Outage | J.E.26.07.23210 | C001860427 | Wan Carlos Scarlett | Portmore | Completed | Load_255006 | Naggo Head - 610 | Jul 21, 2026 7:31am | Jul 21, 2026 7:31am | Jul 21, 2026 8:03am | Jul 21, 2026 9:04am | Jul 21, 2026 9:25am | Jul 21, 2026 10:11am | Jul 21, 2026 10:12am | Jul 21, 2026 10:12am |  |  | Fair | No | Customer get disconnected because of nonpayment of bill
Outage | J.E.26.07.23549 | C001860422 | Wan Carlos Scarlett | Portmore | Completed | Load_240031 | Naggo Head - 610 | Jul 21, 2026 7:30am | Jul 21, 2026 7:31am | Jul 21, 2026 10:12am | Jul 21, 2026 10:12am | Jul 21, 2026 10:45am | Jul 21, 2026 11:21am | Jul 21, 2026 11:30am | Jul 21, 2026 11:30am |  |  | Fair | No | Found 25KVA transformer switch jumper to transformer bushing burn off use one bolt at transformer bushing jumper no pole # was found isolate and close 25KVA transformer
Non-Outage | J.E.26.07.12544 | C001860421 | Raymond Carr | St.Ann | Completed | Load_265293 | Blackstonedge - 110 | Jul 21, 2026 7:25am | Jul 21, 2026 7:25am | Jul 21, 2026 12:32pm | Jul 21, 2026 12:32pm | Jul 21, 2026 12:32pm | Jul 21, 2026 12:17am | Jul 21, 2026 1:02pm | Jul 21, 2026 1:02pm |  |  | Fair | No | Customer couldn’t be contacted.
Non-Outage | J.E.26.07.12598 | C001860420 | Raymond Carr | St.Ann | Completed | Load_269054 | Blackstonedge - 110 | Jul 21, 2026 7:23am | Jul 21, 2026 7:24am | Jul 21, 2026 1:58pm | Jul 21, 2026 1:58pm | Jul 21, 2026 2:37pm | Jul 21, 2026 1:30pm | Jul 21, 2026 2:39pm | Jul 21, 2026 2:39pm |  |  | Fair | No | Supply okay.
Outage | J.E.26.07.23552 | C001860419 | Edward Royal | KSAS | Completed | Load_268953 | Up Park Camp - 410 | Jul 21, 2026 7:23am | Jul 21, 2026 7:47am | Jul 21, 2026 11:32am | Jul 21, 2026 3:17pm | Jul 21, 2026 3:18pm | Jul 21, 2026 3:18pm | Jul 21, 2026 3:18pm | Jul 21, 2026 3:18pm | Fire |  | Fair | No | Premises found ok related to outage
Non-Outage | J.E.26.07.12609 | C001860417 | Raymond Carr | St.Ann | Completed | Load_265293 | Blackstonedge - 110 | Jul 21, 2026 7:22am | Jul 21, 2026 7:24am | Jul 22, 2026 11:33am | Jul 22, 2026 11:33am | Jul 22, 2026 11:33am | Jul 22, 2026 11:26am | Jul 22, 2026 11:35am | Jul 22, 2026 11:35am |  |  | Fair | No | Fault corrected.Related to labyrinth.
Non-Outage | J.E.26.07.13175 | C001860416 | Raymond Carr | St.Ann | Completed | Load_265293 | Blackstonedge - 110 | Jul 21, 2026 7:22am | Jul 21, 2026 7:24am | Jul 21, 2026 11:46am | Jul 21, 2026 11:46am | Jul 21, 2026 12:02pm | Jul 21, 2026 12:00am | Jul 21, 2026 12:04pm | Jul 21, 2026 12:04pm |  |  | Fair | No | Several calls to contact number went unanswered.
Non-Outage | J.E.26.07.17832 | C001860415 | Raymond Carr | St.Ann | Completed | Load_248758 | Blackstonedge - 110 | Jul 21, 2026 7:22am | Jul 21, 2026 7:24am | Jul 22, 2026 11:40am | Jul 22, 2026 11:40am | Jul 22, 2026 12:29pm | Jul 22, 2026 12:20am | Jul 22, 2026 12:32pm | Jul 22, 2026 12:32pm |  |  | Fair | No | Customer reported that fault was corrected last week.
Non-Outage | J.E.26.07.20274 | C001860414 | Raymond Carr | St.Ann | Completed | Load_247343 | Blackstonedge - 110 | Jul 21, 2026 7:22am | Jul 21, 2026 7:24am | Jul 21, 2026 2:39pm | Jul 21, 2026 2:39pm | Jul 21, 2026 2:56pm | Jul 21, 2026 3:00pm | Jul 21, 2026 3:02pm | Jul 21, 2026 3:02pm |  |  | Fair | No | Supply found okay.
Non-Outage | J.E.26.07.21629 | C001860418 | Richard Grant | St.Catherine | Completed | Load_247419 | New Michelton - 410 | Jul 21, 2026 7:22am | Jul 21, 2026 7:22am | Jul 21, 2026 8:20am | Jul 21, 2026 8:20am | Jul 21, 2026 10:17am | Jul 21, 2026 10:42am | Jul 21, 2026 10:42am | Jul 21, 2026 10:42am |  |  | Fair | No | Defective 50kva transformer in Wye Wye bank connection found. Kindly send email to A Murray to have defective transformer replaced. Remaining transformers in bank left isolated
Non-Outage | J.E.26.07.23013 | C001860412 | Raymond Carr | St.Ann | Completed | Load_244965 | Upper White River - 110 | Jul 21, 2026 7:21am | Jul 21, 2026 7:24am | Jul 21, 2026 1:03pm | Jul 21, 2026 1:03pm | Jul 21, 2026 1:56pm | Jul 21, 2026 1:55pm | Jul 21, 2026 1:58pm | Jul 21, 2026 1:58pm |  |  | Fair | No | Customer reported that supply is okay.
Outage | J.E.26.07.22274 | C001860409 | Nickolas Rodriques | St.Catherine | Completed | Load_255400 | Twickenham - 210 | Jul 21, 2026 7:20am | Jul 21, 2026 7:20am | Jul 21, 2026 2:21pm | Jul 21, 2026 2:25pm | Jul 21, 2026 2:53pm | Jul 21, 2026 3:29pm | Jul 21, 2026 3:30pm | Jul 21, 2026 3:30pm |  |  | Fair | No | Checked and found customer single phasing at meter (114) caused by defective meter wires. Current reading found at pothead (114-116-230). Their maintenance team was on site and was advised to consult a license Electrician to do repairs.
Outage | J.E.26.07.22471 | C001860408 | Nickolas Rodriques | St.Catherine | Completed | Load_252984 | Twickenham - 210 | Jul 21, 2026 7:19am | Jul 21, 2026 7:20am | Jul 21, 2026 10:20am | Jul 21, 2026 10:21am | Jul 21, 2026 10:58am | Jul 21, 2026 11:17am | Jul 21, 2026 11:18am | Jul 21, 2026 11:18am | TreeContact |  | Fair | No | Checked and found a huge mango tree growing on to secondary wires that needs to be cut. Refer to maintenance.
Outage | J.E.26.07.23243 | C001860406 | Nickolas Rodriques | St.Catherine | Completed | Load_294602 | Twickenham - 210 | Jul 21, 2026 7:19am | Jul 21, 2026 7:20am | Jul 21, 2026 8:00am | Jul 21, 2026 8:14am | Jul 21, 2026 9:18am | Jul 21, 2026 10:01am | Jul 21, 2026 10:20am | Jul 21, 2026 10:20am |  |  | Fair | No | Checked and found customer 3w meter disconnected. Repaired by connecting meter after inspection completing. Current reading is (114-114-228).
Outage | J.E.26.07.23427 | C001860405 | Nickolas Rodriques | St.Catherine | Completed | Load_268709 | Twickenham - 210 | Jul 21, 2026 7:19am | Jul 21, 2026 7:20am | Jul 21, 2026 11:18am | Jul 21, 2026 11:21am | Jul 21, 2026 11:47am | Jul 21, 2026 11:58am | Jul 21, 2026 12:03pm | Jul 21, 2026 12:03pm |  |  | Fair | No | Checked and found customer single phasing (116) caused by broken service wire at pole. Repaired by connecting wire using one clamp, current reading is (116-116-232). Customer confirmed that all is well now.
Outage | J.E.26.07.22592 | C001860404 | Tajay Bernard | Hanover | Completed | Load_241288 | Orange Bay - 310 | Jul 21, 2026 7:17am | Jul 21, 2026 7:17am | Jul 21, 2026 8:02am | Jul 21, 2026 8:02am | Jul 21, 2026 8:38am | Jul 21, 2026 8:42am | Jul 21, 2026 8:48am | Jul 21, 2026 8:48am |  |  | Fair | No | Premises check and found okay voltage found 112/116/228
Outage | J.E.26.07.23338 | C001860399 | Neville Spencer | Clarendon | Completed | Load_245051 | Parnassus - 310 | Jul 21, 2026 7:13am | Jul 21, 2026 7:13am | Jul 21, 2026 7:51am | Jul 21, 2026 7:51am | Jul 21, 2026 8:52am | Jul 21, 2026 9:20am | Jul 21, 2026 9:22am | Jul 21, 2026 9:22am |  |  | Fair | No | Found supply at location . Found CT burning make safe
Non-Outage | J.E.26.07.22331 | C001860377 | Denton Williams | null | Completed | null | null | Jul 21, 2026 7:12am | Jul 21, 2026 7:17am | Jul 21, 2026 7:47am | Jul 21, 2026 7:47am | Jul 21, 2026 7:47am | Jul 21, 2026 7:48am | Jul 21, 2026 7:49am | Jul 21, 2026 7:49am |  | Y | Fair | No | Matter was dealt with from yesterday.
Outage | J.E.26.07.23289 | C001860393 | Jermaine Williams | Clarendon | Completed | Load_1000166 | Parnassus - 210 | Jul 21, 2026 7:12am | Jul 21, 2026 3:27pm | Jul 21, 2026 4:06pm | Jul 21, 2026 4:06pm | Jul 21, 2026 5:30pm | Jul 21, 2026 5:33pm | Jul 21, 2026 5:34pm | Jul 21, 2026 5:34pm | BrokenPole |  | Fair | No | Replace 1-5A Junction Fuse, Left ok.
Outage | J.E.26.07.22212 | C001860368 | Tajay Bernard | Hanover | Completed | Load_575278 | Orange Bay - 310 | Jul 21, 2026 7:11am | Jul 21, 2026 7:12am | Jul 21, 2026 7:14am | Jul 21, 2026 7:15am | Jul 21, 2026 7:45am | Jul 21, 2026 8:02am | Jul 21, 2026 8:02am | Jul 21, 2026 8:02am |  |  | Fair | No | Premises check and found okay voltage readings 113/113/26
Non-Outage | J.E.26.07.23006 | C001860367 | Stephen Taylor | St.Thomas | Completed | Load_577225 | Good Year - 210 | Jul 21, 2026 7:08am | Jul 21, 2026 1:56pm | Jul 21, 2026 2:10pm | Jul 21, 2026 2:10pm | Jul 21, 2026 2:45pm | Jul 21, 2026 2:46pm | Jul 21, 2026 2:47pm | Jul 21, 2026 2:47pm |  |  | Fair | No | Clearly up single phase customer is now okay reading 111,112,225
Outage | J.E.26.07.23448 | C001860297 | Rusean Allen | KSAN | Completed | Load_239779 | Constant Spring - 410 | Jul 20, 2026 11:58pm | Jul 20, 2026 11:59pm | Jul 21, 2026 2:24am | Jul 21, 2026 2:24am | Jul 21, 2026 2:55am | Jul 21, 2026 2:56am | Jul 21, 2026 2:56am | Jul 21, 2026 2:56am |  |  | Fair | No | Found a 3 amps fuseReplace a 3 amps fuse
Outage | J.E.26.07.23425 | C001860295 | Rusean Allen | KSAS | Completed | Load_239090 | Up Park Camp - 310 | Jul 20, 2026 11:29pm | Jul 20, 2026 11:48pm | Jul 21, 2026 2:56am | Jul 21, 2026 2:56am | Jul 21, 2026 4:09am | Jul 21, 2026 4:09am | Jul 21, 2026 4:09am | Jul 21, 2026 4:09am |  |  | Fair | No | Reconnected jumper at pole
Outage | J.E.26.07.23368 | C001860294 | Rusean Allen | KSAS | Completed | Load_260234 | Cane River - 610 | Jul 20, 2026 11:11pm | Jul 20, 2026 11:11pm | Jul 21, 2026 1:20am | Jul 21, 2026 1:20am | Jul 21, 2026 1:20am | Jul 21, 2026 1:41am | Jul 21, 2026 1:41am | Jul 21, 2026 1:41am |  |  | Fair | No | Reconnected secondary jumper at pole
Outage | J.E.26.07.23361 | C001860293 | Delano Gayle | St.Catherine | Completed | Load_266407 | Twickenham - 310 | Jul 20, 2026 11:02pm | Jul 20, 2026 11:03pm | Jul 20, 2026 11:09pm | Jul 20, 2026 11:09pm | Jul 21, 2026 2:03am | Jul 21, 2026 2:07am | Jul 21, 2026 2:08am | Jul 21, 2026 2:08am |  |  | Fair | No | Premises found okay power was restored to area
Outage | J.E.26.07.23096 | C001860292 | Delano Gayle | Portmore | Completed | Load_255129 | Naggo Head - 610 | Jul 20, 2026 11:01pm | Jul 20, 2026 11:03pm | Jul 21, 2026 2:52am | Jul 21, 2026 2:52am | Jul 21, 2026 3:13am | Jul 21, 2026 3:30am | Jul 21, 2026 3:30am | Jul 21, 2026 3:30am | BrokenPole |  | Fair | No | Premises not found, no answer from customer phone,area found okay,
Outage | J.E.26.07.23153 | C001860291 | Delano Gayle | Portmore | Completed | Load_240031 | Naggo Head - 610 | Jul 20, 2026 11:01pm | Jul 20, 2026 11:03pm | Jul 21, 2026 2:08am | Jul 21, 2026 2:08am | Jul 21, 2026 2:41am | Jul 21, 2026 2:51am | Jul 21, 2026 2:51am | Jul 21, 2026 2:51am |  |  | Fair | No | Premises not found no answer from customer phone, area patrolled and area found okay
Outage | J.E.26.07.23290 | C001860286 | Raymond Carr | St.Ann | Completed | Load_243058 | Upper White River - 210 | Jul 20, 2026 10:24pm | Jul 21, 2026 7:18am | Jul 21, 2026 8:36am | Jul 21, 2026 8:36am | Jul 21, 2026 10:00am | Jul 21, 2026 10:00am | Jul 21, 2026 10:19am | Jul 21, 2026 10:19am |  |  | Fair | No | Voltage readings at meter socket 120/120/240. Customer was advised to have an electrician check wiring.
Non-Outage | J.E.26.07.08227 | C001860284 | Shamour Haughton | St.James | Completed | Load_292555 | Bogue - 310 | Jul 20, 2026 10:14pm | Jul 20, 2026 10:14pm | Jul 20, 2026 10:26pm | Jul 20, 2026 10:26pm | Jul 20, 2026 11:16pm | Jul 20, 2026 11:16pm | Jul 20, 2026 11:27pm | Jul 20, 2026 11:27pm |  |  | Fair | No | Customer number went voicemail after several calls, unable to locate customer
Non-Outage | J.E.26.07.18110 | C001860281 | Horace Malcolm | St.James | Completed | Load_259498 | Queens Drive - 710 | Jul 20, 2026 10:09pm | Jul 20, 2026 10:09pm | Jul 20, 2026 10:16pm | Jul 20, 2026 10:16pm | Jul 20, 2026 10:41pm | Jul 20, 2026 10:51pm | Jul 20, 2026 10:51pm | Jul 20, 2026 10:51pm |  |  | Fair | No | Check and found ok supply restored
Outage | J.E.26.07.23341 | C001860268 | Richman Whyte | Westmoreland | Completed | Load_256052 | Paradise - 210 | Jul 20, 2026 9:24pm | Jul 20, 2026 9:27pm | Jul 21, 2026 6:57am | Jul 21, 2026 6:57am | Jul 21, 2026 6:57am | Jul 21, 2026 6:57am | Jul 21, 2026 6:58am | Jul 21, 2026 6:58am |  |  | Fair | No | Check and found ok
Outage | J.E.26.07.23345 | C001860266 | Barnett Brown | Manchester | Completed | Load_257034 | Kendal - 210 | Jul 20, 2026 8:51pm | Jul 21, 2026 9:01am | Jul 21, 2026 1:10pm | Jul 21, 2026 1:10pm | Jul 21, 2026 2:37pm | Jul 21, 2026 3:02pm | Jul 21, 2026 3:06pm | Jul 21, 2026 3:06pm |  |  | Fair | No | Customer has internal fault. Voltage 116.
Outage | J.E.26.07.23323 | C001860264 | Andre Williams | Trelawny | Completed | Load_260728 | Martha Brae - 110 | Jul 20, 2026 8:37pm | Jul 21, 2026 3:12pm | Jul 21, 2026 3:40pm | Jul 21, 2026 4:04pm | Jul 21, 2026 4:04pm | Jul 21, 2026 4:08pm | Jul 21, 2026 4:09pm | Jul 21, 2026 4:09pm |  |  | Fair | No | Premises ok power was restored
Outage | J.E.26.07.23324 | C001860262 | Marlon Brown | Trelawny | Completed | Load_268459 | Duncans - 210 | Jul 20, 2026 8:37pm | Jul 20, 2026 8:38pm | Jul 21, 2026 7:39am | Jul 21, 2026 7:39am | Jul 21, 2026 7:39am | Jul 21, 2026 7:39am | Jul 21, 2026 7:39am | Jul 21, 2026 7:39am |  |  | Fair | No | Supply has been restored.
Outage | J.E.26.07.23216 | C001860259 | Moses Elliston | Portmore | Completed | Load_258293 | Naggo Head - 510 | Jul 20, 2026 8:22pm | Jul 20, 2026 8:22pm | Jul 21, 2026 12:33pm | Jul 21, 2026 12:33pm | Jul 21, 2026 12:33pm | Jul 21, 2026 12:33pm | Jul 21, 2026 12:35pm | Jul 21, 2026 12:35pm |  |  | Fair | No | Supply ok .Outage was in area
Outage | J.E.26.07.22412 | C001860258 | Moses Elliston | Portmore | Completed | Load_576173 | Naggo Head - 510 | Jul 20, 2026 8:21pm | Jul 20, 2026 8:22pm | Jul 21, 2026 12:12pm | Jul 21, 2026 12:12pm | Jul 21, 2026 12:12pm | Jul 21, 2026 12:12pm | Jul 21, 2026 12:21pm | Jul 21, 2026 12:21pm |  |  | Fair | No | Wrapped 3 wire service phases ,4 linkets used .117-118 235 volts
Outage | J.E.26.07.23318 | C001860257 | Javid Vernon | Hanover | Completed | Load_242329 | Orange Bay - 310 | Jul 20, 2026 8:19pm | Jul 21, 2026 7:46am | Jul 21, 2026 12:34pm | Jul 21, 2026 12:34pm | Jul 21, 2026 1:52pm | Jul 21, 2026 2:08pm | Jul 21, 2026 2:09pm | Jul 21, 2026 2:09pm |  |  | Fair | No | Area and premises check and found okay customer stated that the power was restored
Outage | J.E.26.07.22444 | C001860256 | Cliton Henry | St.Mary | Completed | Load_350137 | Oracabessa - 210 | Jul 20, 2026 8:13pm | Jul 20, 2026 8:14pm | Jul 20, 2026 9:54pm | Jul 20, 2026 9:54pm | Jul 20, 2026 9:54pm | Jul 20, 2026 9:54pm | Jul 20, 2026 9:56pm | Jul 20, 2026 9:56pm |  |  | Fair | No | The customer stated that the supply was restored since 5 pm
Outage | J.E.26.07.23307 | C001860255 | Cliton Henry | St.Mary | Completed | Load_351415 | Oracabessa - 210 | Jul 20, 2026 8:13pm | Jul 20, 2026 8:14pm | Jul 20, 2026 10:13pm | Jul 20, 2026 10:13pm | Jul 20, 2026 10:29pm | Jul 20, 2026 10:53pm | Jul 20, 2026 10:54pm | Jul 20, 2026 10:54pm |  |  | Fair | No | Zero voltage at the customer pothead, kindly refer to Field Service Department for execution, NB. Escalation team confirmed that the meters. are not disconnected. The other premises number 581748 on the same property is also out of supply..
Outage | J.E.26.07.23276 | C001860253 | Javid Vernon | Westmoreland | Completed | Load_261485 | Paradise - 210 | Jul 20, 2026 8:08pm | Jul 21, 2026 7:45am | Jul 21, 2026 8:17am | Jul 21, 2026 8:17am | Jul 21, 2026 9:21am | Jul 21, 2026 9:31am | Jul 21, 2026 9:31am | Jul 21, 2026 9:31am |  |  | Fair | No | Area check and found okay Unable to locate customer and premises phone calls to customer number went unanswered
Outage | J.E.26.07.23288 | C001860252 | Shamour Haughton | St.James | Completed | Load_263681 | Queens Drive - 710 | Jul 20, 2026 8:07pm | Jul 20, 2026 8:08pm | Jul 20, 2026 9:12pm | Jul 20, 2026 9:12pm | Jul 20, 2026 9:12pm | Jul 20, 2026 9:13pm | Jul 20, 2026 9:15pm | Jul 20, 2026 9:15pm |  |  | Fair | No | Customer number went voicemail after several calls, need better direction
Outage | J.E.26.07.23247 | C001860250 | Jermaine Williams | Clarendon | Completed | Load_292407 | Parnassus - 310 | Jul 20, 2026 8:01pm | Jul 20, 2026 8:01pm | Jul 20, 2026 8:54pm | Jul 20, 2026 8:54pm | Jul 20, 2026 10:18pm | Jul 20, 2026 10:18pm | Jul 20, 2026 10:19pm | Jul 20, 2026 10:19pm |  |  | Fair | No | Bird flew in line, patrol and replaced blown 25kva 3amp xfmr fuse.
Non-Outage | J.E.26.07.23270 | C001860248 | Edward Royal | null | Completed | null | null | Jul 20, 2026 7:58pm | Jul 20, 2026 7:58pm | Jul 20, 2026 8:14pm | Jul 20, 2026 8:14pm | Jul 20, 2026 8:14pm | Jul 20, 2026 8:15pm | Jul 20, 2026 8:15pm | Jul 20, 2026 8:15pm | Fire |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.07.23238 | C001860247 | Andrew Powell | Manchester | Completed | Load_264792 | Spur Tree - 210 | Jul 20, 2026 7:56pm | Jul 20, 2026 7:57pm | Jul 20, 2026 9:04pm | Jul 20, 2026 9:04pm | Jul 20, 2026 9:24pm | Jul 20, 2026 9:44pm | Jul 20, 2026 9:46pm | Jul 20, 2026 9:46pm |  |  | Fair | No | Remade corroded service wire joints at secondary line 3 wire using three clamps, voltage reading 114v-115v phase to neutral 229v cross phase.
Outage | J.E.26.07.23251 | C001860243 | Richman Whyte | Hanover | Completed | Load_260765 | Orange Bay - 310 | Jul 20, 2026 7:46pm | Jul 20, 2026 7:46pm | Jul 20, 2026 8:27pm | Jul 20, 2026 8:27pm | Jul 20, 2026 9:13pm | Jul 20, 2026 9:45pm | Jul 20, 2026 9:45pm | Jul 20, 2026 9:45pm |  |  | Rains | No | Twenty five kva transformer burned
Outage | J.E.26.07.23275 | C001860242 | Kaydon Taylor | KSAN | Completed | Load_269774 | Constant Spring - 410 | Jul 20, 2026 7:40pm | Jul 20, 2026 7:40pm | Jul 20, 2026 7:56pm | Jul 20, 2026 7:56pm | Jul 20, 2026 9:53pm | Jul 20, 2026 9:53pm | Jul 20, 2026 9:53pm | Jul 20, 2026 9:53pm |  |  | Fair | No | Reset customer breaker
Outage | J.E.26.07.23202 | C001860241 | Roxroy Needham | St.Ann | Completed | Load_575948 | Cardiff Hall - 210 | Jul 20, 2026 7:39pm | Jul 20, 2026 8:09pm | Jul 20, 2026 9:20pm | Jul 20, 2026 9:20pm | Jul 20, 2026 9:53pm | Jul 20, 2026 9:53pm | Jul 20, 2026 9:54pm | Jul 20, 2026 9:54pm |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.07.23231 | C001860240 | Andrew Powell | St.Elizabeth | Completed | Load_293011 | Maggotty - 210 | Jul 20, 2026 7:38pm | Jul 20, 2026 7:40pm | Jul 20, 2026 7:57pm | Jul 20, 2026 7:58pm | Jul 20, 2026 8:30pm | Jul 20, 2026 8:55pm | Jul 20, 2026 8:57pm | Jul 20, 2026 8:57pm |  |  | Fair | No | Remade corroded service wire neutral joint at meter pothead 3 wire using one service sleeves, voltage reading 107v-108v phase to neutral 215v cross phase.
Outage | J.E.26.07.23183 | C001860235 | Collin Robinson | Portland | Completed | Load_261581 | Port Antonio - 410 | Jul 20, 2026 7:21pm | Jul 20, 2026 7:23pm | Jul 20, 2026 7:31pm | Jul 20, 2026 7:31pm | Jul 20, 2026 8:15pm | Jul 20, 2026 8:25pm | Jul 20, 2026 8:26pm | Jul 20, 2026 8:26pm |  |  | Fair | No | Clear vine from pole and replace 3 amps fuse at pole 602755
Outage | J.E.26.07.23240 | C001860236 | Collin Robinson | Portland | Completed | Load_253288 | Port Antonio - 410 | Jul 20, 2026 7:21pm | Jul 20, 2026 7:23pm | Jul 20, 2026 9:25pm | Jul 20, 2026 9:25pm | Jul 20, 2026 9:26pm | Jul 20, 2026 9:31pm | Jul 20, 2026 9:31pm | Jul 20, 2026 9:31pm |  |  | Fair | No | Information received from customer that supply was restored
Outage | J.E.26.07.23245 | C001860237 | Collin Robinson | Portland | Completed | Load_259093 | Port Antonio - 410 | Jul 20, 2026 7:21pm | Jul 20, 2026 7:23pm | Jul 20, 2026 8:26pm | Jul 20, 2026 8:26pm | Jul 20, 2026 9:06pm | Jul 20, 2026 9:17pm | Jul 20, 2026 9:17pm | Jul 20, 2026 9:17pm | Fire |  | Fair | No | Change 1burn one bolt clamp at pole Voltage reading 119v 120v 239v
Non-Outage | J.E.26.07.22162 | C001860233 | Michael Christian | St.James | Completed | Load_257529 | Bogue - 610 | Jul 20, 2026 7:08pm | Jul 20, 2026 7:08pm | Jul 20, 2026 7:51pm | Jul 20, 2026 7:51pm | Jul 20, 2026 9:33pm | Jul 20, 2026 9:35pm | Jul 20, 2026 9:35pm | Jul 20, 2026 9:35pm |  |  | Fair | No | Check and found voltage 111 110 221 at pothead
Non-Outage | J.E.26.07.22389 | C001860232 | Shamour Haughton | St.James | Completed | Load_260391 | Bogue - 310 | Jul 20, 2026 7:03pm | Jul 20, 2026 7:04pm | Jul 20, 2026 8:36pm | Jul 20, 2026 8:36pm | Jul 20, 2026 8:36pm | Jul 20, 2026 8:36pm | Jul 20, 2026 8:39pm | Jul 20, 2026 8:39pm |  |  | Fair | No | Customer experiencing internal problem, voltage left 118,117,235
Non-Outage | J.E.26.07.23224 | C001860231 | Shamour Haughton | St.James | Completed | Load_301730 | Bogue - 310 | Jul 20, 2026 7:03pm | Jul 20, 2026 7:03pm | Jul 20, 2026 7:12pm | Jul 20, 2026 7:12pm | Jul 20, 2026 7:49pm | Jul 20, 2026 7:49pm | Jul 20, 2026 7:52pm | Jul 20, 2026 7:52pm |  |  | Fair | No | Customer experiencing single phasing, area needs daylight attention, the customer service wire has been joined several times, pole is full of vegetation and a lot of other service wires
Non-Outage | J.E.26.07.23042 | C001860230 | Horace Malcolm | St.James | Completed | Load_238044 | Queens Drive - 710 | Jul 20, 2026 7:02pm | Jul 20, 2026 7:02pm | Jul 20, 2026 7:39pm | Jul 20, 2026 7:39pm | Jul 20, 2026 7:57pm | Jul 20, 2026 8:04pm | Jul 20, 2026 8:04pm | Jul 20, 2026 8:04pm |  |  | Fair | No | Check and found ok issue resolved
Outage | J.E.26.07.23211 | C001860222 | Wayne Dillion | St.Elizabeth | Completed | Load_247131 | Maggotty - 110 | Jul 20, 2026 6:43pm | Jul 20, 2026 6:44pm | Jul 20, 2026 7:16pm | Jul 20, 2026 7:16pm | Jul 20, 2026 7:34pm | Jul 20, 2026 8:12pm | Jul 20, 2026 8:13pm | Jul 20, 2026 8:13pm | BrokenWire |  | Fair | No | Reconnect customer using 80 feet of number 6 triplex 3 linket 3 one bolt clamp voltage reading 112v 111v 224v supply working ok
Outage | J.E.26.07.23216 | C001860221 | Donald Cunningham | Portmore | Completed | Load_258293 | Naggo Head - 510 | Jul 20, 2026 6:38pm | Jul 20, 2026 6:38pm | Jul 20, 2026 7:01pm | Jul 20, 2026 7:01pm | Jul 20, 2026 7:22pm | Jul 20, 2026 7:22pm | Jul 20, 2026 7:22pm | Jul 20, 2026 7:22pm |  |  | Fair | No | Premises not located customer not reachable
Outage | J.E.26.07.23194 | C001860218 | Dean Smith | Hanover | Completed | Load_302783 | Orange Bay - 310 | Jul 20, 2026 6:36pm | Jul 20, 2026 6:36pm | Jul 20, 2026 7:14pm | Jul 20, 2026 7:14pm | Jul 20, 2026 9:54pm | Jul 20, 2026 9:54pm | Jul 20, 2026 10:26pm | Jul 20, 2026 10:26pm | LeakingTransformer |  | Fair | No | Replace 25amp fuse . Pole number n/a
Outage | J.E.26.07.23212 | C001860219 | Marlon Brown | Trelawny | Completed | Load_246391 | Martha Brae - 210 | Jul 20, 2026 6:36pm | Jul 20, 2026 7:54pm | Jul 20, 2026 10:05pm | Jul 20, 2026 10:05pm | Jul 20, 2026 10:29pm | Jul 20, 2026 10:45pm | Jul 20, 2026 10:45pm | Jul 20, 2026 10:45pm |  |  | Fair | No | Replaced 10amps junction fuses, however 15kva transformer suspect defective as oil is running from it.
Non-Outage | J.E.26.07.23180 | C001860207 | Shamour Haughton | St.James | Completed | Load_247124 | Bogue - 310 | Jul 20, 2026 6:07pm | Jul 20, 2026 6:07pm | Jul 20, 2026 6:29pm | Jul 20, 2026 6:29pm | Jul 20, 2026 6:58pm | Jul 20, 2026 6:58pm | Jul 20, 2026 7:02pm | Jul 20, 2026 7:02pm |  |  | Fair | No | Check and found customer experiencing internal problem, voltage left 115,114,229
Outage | J.E.26.07.22666 | C001860201 | Moses Elliston | St.Catherine | Completed | Load_263594 | Rhodens Pen - 210 | Jul 20, 2026 5:46pm | Jul 20, 2026 5:47pm | Jul 21, 2026 1:04pm | Jul 21, 2026 1:04pm | Jul 21, 2026 1:04pm | Jul 21, 2026 1:04pm | Jul 21, 2026 1:05pm | Jul 21, 2026 1:05pm |  |  | Fair | No | Customer added credit to prepaid account.
Non-Outage | J.E.26.07.23021 | C001860200 | Moses Elliston | null | Completed | null | null | Jul 20, 2026 5:43pm | Jul 20, 2026 5:44pm | Jul 21, 2026 1:57pm | Jul 21, 2026 1:57pm | Jul 21, 2026 2:16pm | Jul 21, 2026 2:17pm | Jul 21, 2026 2:20pm | Jul 21, 2026 2:20pm |  |  | Fair | No | Supply ok at premises.
Non-Outage | J.E.26.07.23132 | C001860199 | Hopeton Henry | null | Completed | null | null | Jul 20, 2026 5:43pm | Jul 20, 2026 5:44pm | Jul 20, 2026 5:54pm | Jul 20, 2026 10:23pm | Jul 20, 2026 10:23pm | Jul 20, 2026 10:23pm | Jul 20, 2026 10:24pm | Jul 20, 2026 10:24pm |  |  | Fair | No | Customer not located
Non-Outage | J.E.26.07.23142 | C001860198 | Hopeton Henry | null | Completed | null | null | Jul 20, 2026 5:43pm | Jul 20, 2026 5:44pm | Jul 20, 2026 6:39pm | Jul 20, 2026 8:14pm | Jul 20, 2026 8:14pm | Jul 20, 2026 10:21pm | Jul 20, 2026 10:23pm | Jul 20, 2026 10:23pm |  |  | Fair | No | Found broken neutral connection at transformer,120-122-242 volts
Non-Outage | J.E.26.07.23068 | C001860197 | Moses Elliston | null | Completed | null | null | Jul 20, 2026 5:39pm | Jul 20, 2026 5:39pm | Jul 21, 2026 4:44pm | Jul 21, 2026 4:44pm | Jul 21, 2026 4:44pm | Jul 21, 2026 4:20pm | Jul 21, 2026 4:46pm | Jul 21, 2026 4:46pm |  |  | Fair | No | Credit added to prepaid account.Meter sn 14295741442
Outage | J.E.26.07.23130 | C001860194 | Barnett Brown | Manchester | Completed | Load_266399 | Porus - 310 | Jul 20, 2026 5:28pm | Jul 20, 2026 5:31pm | Jul 20, 2026 6:07pm | Jul 20, 2026 6:07pm | Jul 20, 2026 6:46pm | Jul 20, 2026 7:01pm | Jul 20, 2026 7:05pm | Jul 20, 2026 7:05pm | BrokenWire |  | Fair | No | Premises found ok
Outage | J.E.26.07.23155 | C001860192 | Richman Whyte | Hanover | Completed | Load_292031 | Orange Bay - 310 | Jul 20, 2026 5:24pm | Jul 20, 2026 5:25pm | Jul 20, 2026 9:46pm | Jul 20, 2026 9:46pm | Jul 20, 2026 10:52pm | Jul 20, 2026 11:09pm | Jul 20, 2026 11:10pm | Jul 20, 2026 11:10pm |  |  | Fair | No | Replace 2amp 25 kva transformer fuse
Outage | J.E.26.07.23143 | C001860188 | Andre Smith | KSAS | Completed | Load_251380 | Up Park Camp - 510 | Jul 20, 2026 5:06pm | Jul 20, 2026 5:07pm | Jul 20, 2026 5:21pm | Jul 20, 2026 5:21pm | Jul 20, 2026 5:58pm | Jul 20, 2026 6:54pm | Jul 20, 2026 6:56pm | Jul 20, 2026 6:56pm | BrokenPole |  | Fair | No | Remove broken abondand pole from truck...maintenance department required to remove pole from roadway
Non-Outage | J.E.26.07.22991 | C001860183 | Gregory Grossett | null | Completed | null | null | Jul 20, 2026 5:04pm | Jul 20, 2026 5:04pm | Jul 20, 2026 5:10pm | Jul 20, 2026 5:10pm | Jul 20, 2026 5:25pm | Jul 20, 2026 5:38pm | Jul 20, 2026 5:40pm | Jul 20, 2026 5:40pm | LowHangingWires |  | Fair | No | Upon arrival at premises customer said issue was resolved by there internal team.
Non-Outage | J.E.26.07.23091 | C001860182 | Andrew Powell | null | Completed | null | null | Jul 20, 2026 5:03pm | Jul 20, 2026 5:04pm | Jul 20, 2026 6:12pm | Jul 20, 2026 6:12pm | Jul 20, 2026 6:25pm | Jul 20, 2026 6:26pm | Jul 20, 2026 6:28pm | Jul 20, 2026 6:28pm |  |  | Fair | No | Customer stated that temporary disconnection was done yesterday at NIC pumping station.
Non-Outage | J.E.26.07.15400 | C001860157 | Roxroy Needham | St.Ann | Completed | Load_244118 | Cardiff Hall - 310 | Jul 20, 2026 4:50pm | Jul 20, 2026 4:50pm | Jul 20, 2026 6:44pm | Jul 20, 2026 6:44pm | Jul 20, 2026 9:16pm | Jul 20, 2026 9:17pm | Jul 20, 2026 9:18pm | Jul 20, 2026 9:18pm |  |  | Fair | No | Premises found ok customer say that JPS team come today before
Outage | J.E.26.07.23101 | C001860155 | Daniel Francis | St.Ann | Completed | Load_246929 | Ocho Rios - 410 | Jul 20, 2026 4:47pm | Jul 20, 2026 4:47pm | Jul 20, 2026 5:13pm | Jul 20, 2026 5:13pm | Jul 20, 2026 5:46pm | Jul 20, 2026 6:20pm | Jul 20, 2026 6:25pm | Jul 20, 2026 6:25pm |  |  | Fair | No | Not JPS internal fault voltage 206/118/119 / 240 /238/240
Outage | J.E.26.07.23117 | C001860152 | Ricky Hall | St.Catherine | Completed | Load_267448 | Tredegar - 310 | Jul 20, 2026 4:45pm | Jul 20, 2026 4:45pm | Jul 20, 2026 4:56pm | Jul 20, 2026 5:24pm | Jul 20, 2026 5:24pm | Jul 20, 2026 5:25pm | Jul 20, 2026 5:25pm | Jul 20, 2026 5:25pm |  |  | Fair | No | Call associated with outage #23118
Outage | J.E.26.07.23075 | C001860151 | Barnett Brown | Manchester | Completed | Load_266581 | Porus - 310 | Jul 20, 2026 4:44pm | Jul 20, 2026 7:55pm | Jul 20, 2026 8:59pm | Jul 20, 2026 8:59pm | Jul 20, 2026 10:03pm | Jul 20, 2026 10:48pm | Jul 20, 2026 10:50pm | Jul 20, 2026 10:50pm |  |  | Fair | No | Clear runner from switch drop lead, replace blown 3 amp transformer fuse
Outage | J.E.26.07.23118 | C001860150 | Ricky Hall | St.Catherine | Completed | Load_253137 | Tredegar - 310 | Jul 20, 2026 4:44pm | Jul 20, 2026 4:45pm | Jul 20, 2026 4:56pm | Jul 20, 2026 4:57pm | Jul 20, 2026 5:06pm | Jul 20, 2026 5:23pm | Jul 20, 2026 5:23pm | Jul 20, 2026 5:23pm |  |  | Fair | No | Replace blown 30 amps junction fuse
Outage | J.E.26.07.22610 | C001860141 | Moses Elliston | St.Catherine | Completed | Load_249045 | Tredegar - 210 | Jul 20, 2026 4:36pm | Jul 20, 2026 4:36pm | Jul 21, 2026 10:17am | Jul 21, 2026 10:17am | Jul 21, 2026 10:17am | Jul 21, 2026 10:17am | Jul 21, 2026 10:18am | Jul 21, 2026 10:18am |  |  | EarthMovement | No | Customer said supply ok at premises
Non-Outage | J.E.26.07.23063 | C001860139 | Horace Malcolm | St.James | Completed | Load_268910 | Queens Drive - 710 | Jul 20, 2026 4:34pm | Jul 20, 2026 4:34pm | Jul 20, 2026 5:28pm | Jul 20, 2026 5:28pm | Jul 20, 2026 6:01pm | Jul 20, 2026 6:32pm | Jul 20, 2026 6:32pm | Jul 20, 2026 6:32pm |  |  | Fair | No | Isolate one 25kva transformer to clean and remake transformer drop leads and replace one 25 kva transformer used one 2amp fuse
Outage | J.E.26.07.23107 | C001860138 | Collin Robinson | Portland | Completed | Load_263453 | Port Antonio - 410 | Jul 20, 2026 4:31pm | Jul 20, 2026 4:32pm | Jul 20, 2026 4:38pm | Jul 20, 2026 4:38pm | Jul 20, 2026 5:17pm | Jul 20, 2026 5:22pm | Jul 20, 2026 5:23pm | Jul 20, 2026 5:23pm |  |  | Fair | No | Clear coconut tree limb from open secondary conductor
Non-Outage | J.E.26.07.21221 | C001860135 | Andrew Powell | St.Elizabeth | Completed | Load_269119 | Spur Tree - 210 | Jul 20, 2026 4:27pm | Jul 20, 2026 4:28pm | Jul 20, 2026 4:36pm | Jul 20, 2026 4:37pm | Jul 20, 2026 5:48pm | Jul 20, 2026 6:06pm | Jul 20, 2026 6:08pm | Jul 20, 2026 6:08pm |  |  | SevereWind | No | Remade broken service wire phase joint at secondary line 3 wire using one clamp, voltage reading 112v-112v phase to neutral 224v cross phase.
Outage | J.E.26.07.23073 | C001860129 | Oshane Warren | Westmoreland | Completed | Load_257936 | Paradise - 310 | Jul 20, 2026 4:23pm | Jul 20, 2026 4:25pm | Jul 20, 2026 5:19pm | Jul 20, 2026 5:19pm | Jul 20, 2026 6:34pm | Jul 20, 2026 6:56pm | Jul 20, 2026 6:57pm | Jul 20, 2026 6:57pm |  |  | Rains | No | Isolate 2 50kva xformer 35ft class 6wood pole broken into 2 primary and secondary on it over head guy pole held up half of the pole in the air pole need to change urgently refer to maintenance
Outage | J.E.26.07.23087 | C001860130 | Oshane Warren | Westmoreland | Completed | Load_249968 | Paradise - 310 | Jul 20, 2026 4:23pm | Jul 20, 2026 4:25pm | Jul 20, 2026 8:01pm | Jul 20, 2026 8:01pm | Jul 20, 2026 8:01pm | Jul 20, 2026 8:01pm | Jul 20, 2026 8:01pm | Jul 20, 2026 8:01pm |  |  | Rains | No | Customer states that power is restored
Outage | J.E.26.07.23093 | C001860131 | Oshane Warren | Westmoreland | Completed | Load_241015 | Paradise - 310 | Jul 20, 2026 4:23pm | Jul 20, 2026 4:25pm | Jul 20, 2026 6:57pm | Jul 20, 2026 6:57pm | Jul 20, 2026 7:45pm | Jul 20, 2026 7:49pm | Jul 20, 2026 7:50pm | Jul 20, 2026 7:50pm |  |  | Rains | No | Replace 5amp junction fuse
Non-Outage | J.E.26.07.23071 | C001860122 | Shamour Haughton | null | Completed | null | null | Jul 20, 2026 4:19pm | Jul 20, 2026 4:19pm | Jul 20, 2026 4:27pm | Jul 20, 2026 4:27pm | Jul 20, 2026 5:09pm | Jul 20, 2026 5:25pm | Jul 20, 2026 5:29pm | Jul 20, 2026 5:29pm |  |  | Fair | No | Found customer single phasing, EN 06759, voltage left 117
Outage | J.E.26.07.22592 | C001860120 | Dean Smith | Hanover | Completed | Load_241288 | Orange Bay - 310 | Jul 20, 2026 4:18pm | Jul 20, 2026 4:22pm | Jul 20, 2026 10:53pm | Jul 20, 2026 10:53pm | Jul 20, 2026 10:53pm | Jul 20, 2026 10:53pm | Jul 20, 2026 10:54pm | Jul 20, 2026 10:54pm |  |  | Rains | No | Shift ended
Outage | J.E.26.07.22940 | C001860121 | Dean Smith | Hanover | Completed | Load_252795 | Orange Bay - 310 | Jul 20, 2026 4:18pm | Jul 20, 2026 4:19pm | Jul 20, 2026 10:27pm | Jul 20, 2026 10:27pm | Jul 20, 2026 10:27pm | Jul 20, 2026 10:27pm | Jul 20, 2026 10:28pm | Jul 20, 2026 10:28pm |  |  | Rains | No | Area was restored
Outage | J.E.26.07.21600 | C001860118 | Kaydon Taylor | KSAN | Completed | Load_252893 | Constant Spring - 410 | Jul 20, 2026 4:17pm | Jul 20, 2026 4:17pm | Jul 21, 2026 4:31pm | Jul 21, 2026 4:33pm | Jul 21, 2026 4:33pm | Jul 21, 2026 4:33pm | Jul 21, 2026 4:33pm | Jul 21, 2026 4:33pm |  |  | Fair | No | Found okay
Outage | J.E.26.07.22109 | C001860119 | Marlon Brown | Trelawny | Completed | Load_240708 | Duncans - 210 | Jul 20, 2026 4:17pm | Jul 20, 2026 4:17pm | Jul 20, 2026 7:38pm | Jul 20, 2026 7:38pm | Jul 20, 2026 7:38pm | Jul 20, 2026 7:46pm | Jul 20, 2026 7:46pm | Jul 20, 2026 7:46pm | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Please see permit number 33356 for details.
Non-Outage | J.E.26.07.09676 | C001860112 | Jermaine Williams | Clarendon | Completed | Load_248117 | Parnassus - 210 | Jul 20, 2026 4:14pm | Jul 20, 2026 4:14pm | Jul 20, 2026 6:38pm | Jul 20, 2026 6:38pm | Jul 20, 2026 7:16pm | Jul 20, 2026 7:16pm | Jul 20, 2026 7:16pm | Jul 20, 2026 7:16pm |  |  | Fair | No | Premises Lock
Outage | J.E.26.07.23064 | C001860111 | Rayon Foster | Hanover | Completed | Load_260650 | Orange Bay - 210 | Jul 20, 2026 4:11pm | Jul 20, 2026 4:12pm | Jul 20, 2026 6:00pm | Jul 20, 2026 6:00pm | Jul 20, 2026 6:00pm | Jul 20, 2026 5:53pm | Jul 20, 2026 6:25pm | Jul 20, 2026 6:25pm |  |  | Fair | No | Patrol primary line to find one blown 8amp junction fuse and 1 blown 15kva transformer fuse complete line patrol before replacing one 8amp junction and one 1 amp transformer fuse at same and close.
Outage | J.E.26.07.23072 | C001860109 | Rayon Foster | Hanover | Completed | Load_303135 | Orange Bay - 210 | Jul 20, 2026 4:11pm | Jul 20, 2026 4:12pm | Jul 20, 2026 4:54pm | Jul 20, 2026 4:54pm | Jul 20, 2026 4:54pm | Jul 20, 2026 5:52pm | Jul 20, 2026 6:00pm | Jul 20, 2026 6:00pm |  |  | Fair | No | Patrol primary line to find one blown 8amp junction fuse and 1 blown 15kva transformer fuse complete line patrol before replacing one 8amp junction and one 1 amp transformer fuse at same and close.
Non-Outage | J.E.26.07.20893 | C001860100 | Edward Royal | KSAN | Completed | Load_259850 | Washington Blvd - 310 | Jul 20, 2026 4:07pm | Jul 20, 2026 4:07pm | Jul 20, 2026 6:15pm | Jul 20, 2026 6:15pm | Jul 20, 2026 6:15pm | Jul 20, 2026 6:19pm | Jul 20, 2026 6:19pm | Jul 20, 2026 6:19pm | Fire |  | Fair | No | When arrived at location we didn’t notice and fire or anything burning
Non-Outage | J.E.26.07.21689 | C001860099 | Edward Royal | KSAN | Completed | Load_412891 | Washington Blvd - 310 | Jul 20, 2026 4:07pm | Jul 20, 2026 4:07pm | Jul 20, 2026 5:47pm | Jul 20, 2026 5:47pm | Jul 20, 2026 5:47pm | Jul 20, 2026 5:50pm | Jul 20, 2026 5:50pm | Jul 20, 2026 5:50pm |  |  | Fair | No | When contacted customer said that a team came there today she is not sure if it has be fix customer said when she at the premises she will check it
Non-Outage | J.E.26.07.20083 | C001860098 | Edward Royal | KSAN | Completed | Load_262237 | Washington Blvd - 310 | Jul 20, 2026 4:06pm | Jul 20, 2026 4:07pm | Jul 20, 2026 8:15pm | Jul 20, 2026 8:15pm | Jul 20, 2026 8:15pm | Jul 20, 2026 8:15pm | Jul 20, 2026 8:15pm | Jul 20, 2026 8:15pm |  |  | Fair | No | Premises found ok related to outage
Non-Outage | J.E.26.07.18638 | C001860094 | Edward Royal | KSAN | Completed | Load_262237 | Washington Blvd - 310 | Jul 20, 2026 4:05pm | Jul 20, 2026 4:07pm | Jul 20, 2026 6:25pm | Jul 20, 2026 6:25pm | Jul 20, 2026 6:25pm | Jul 20, 2026 8:14pm | Jul 20, 2026 8:14pm | Jul 20, 2026 8:14pm |  |  | Fair | No | Replaced ampack from drop lead to secondary line replaced 2 junction fuse 2 15A voltage reading 235 118 117 v
Outage | J.E.26.07.22992 | C001860093 | Moses Elliston | St.Catherine | Completed | Load_263708 | Twickenham - 310 | Jul 20, 2026 4:02pm | Jul 20, 2026 4:02pm | Jul 20, 2026 4:42pm | Jul 20, 2026 4:42pm | Jul 20, 2026 4:42pm | Jul 20, 2026 4:00pm | Jul 20, 2026 4:45pm | Jul 20, 2026 4:45pm |  |  | Fair | No | Burnt meter socket line side phase lead repaired.Customer advised to check internal wiring.
Outage | J.E.26.07.22464 | C001860092 | Andre Smith | KSAN | Completed | Load_293845 | Washington Blvd - 710 | Jul 20, 2026 4:01pm | Jul 20, 2026 4:02pm | Jul 20, 2026 6:56pm | Jul 20, 2026 6:56pm | Jul 20, 2026 7:24pm | Jul 20, 2026 7:25pm | Jul 20, 2026 7:25pm | Jul 20, 2026 7:25pm |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.22749 | C001860083 | Andre Smith | KSAS | Completed | Load_267289 | Hunts Bay - 710 | Jul 20, 2026 4:01pm | Jul 20, 2026 4:01pm | Jul 20, 2026 4:19pm | Jul 20, 2026 4:19pm | Jul 20, 2026 4:48pm | Jul 20, 2026 5:21pm | Jul 20, 2026 5:21pm | Jul 20, 2026 5:21pm | BrokenWire |  | Fair | No | Premises found okay
Outage | J.E.26.07.22319 | C001860082 | Ricky Hall | St.Catherine | Completed | Load_262738 | Tredegar - 310 | Jul 20, 2026 3:58pm | Jul 20, 2026 5:32pm | Jul 20, 2026 7:41pm | Jul 20, 2026 7:41pm | Jul 20, 2026 8:03pm | Jul 20, 2026 8:03pm | Jul 20, 2026 8:04pm | Jul 20, 2026 8:04pm |  |  | Fair | No | Internal issues resolved by electrician
Outage | J.E.26.07.23011 | C001860075 | Eric Williams | KSAS | Completed | Load_269327 | Duhaney - 310 | Jul 20, 2026 3:52pm | Jul 20, 2026 3:52pm | Jul 20, 2026 5:30pm | Jul 20, 2026 7:44pm | Jul 20, 2026 8:50pm | Jul 20, 2026 9:07pm | Jul 20, 2026 9:08pm | Jul 20, 2026 9:08pm |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.23036 | C001860074 | Eric Williams | KSAN | Completed | Load_244010 | Washington Blvd - 610 | Jul 20, 2026 3:52pm | Jul 20, 2026 3:52pm | Jul 20, 2026 6:07pm | Jul 20, 2026 6:07pm | Jul 20, 2026 6:34pm | Jul 20, 2026 6:49pm | Jul 20, 2026 6:50pm | Jul 20, 2026 6:50pm |  |  | Fair | No | Internal problem problems, meter on
Outage | J.E.26.07.22936 | C001860061 | Eric Williams | KSAN | Completed | Load_248130 | West Kings House - 310 | Jul 20, 2026 3:44pm | Jul 20, 2026 3:48pm | Jul 20, 2026 7:14pm | Jul 20, 2026 7:14pm | Jul 20, 2026 7:22pm | Jul 20, 2026 7:43pm | Jul 20, 2026 7:44pm | Jul 20, 2026 7:44pm |  |  | Fair | No | Reading check at pothead and pole, 120,119,239 volts, customer complained that there breaker keep tripping, internal problem
Outage | J.E.26.07.22742 | C001860060 | Eric Williams | KSAN | Completed | Load_253424 | West Kings House - 210 | Jul 20, 2026 3:43pm | Jul 20, 2026 3:48pm | Jul 20, 2026 6:50pm | Jul 20, 2026 6:51pm | Jul 20, 2026 7:02pm | Jul 20, 2026 7:02pm | Jul 20, 2026 7:02pm | Jul 20, 2026 7:02pm |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.22983 | C001860058 | Milton Charlton | KSAN | Completed | Load_245588 | Constant Spring - 210 | Jul 20, 2026 3:43pm | Jul 21, 2026 7:49am | Jul 21, 2026 12:20pm | Jul 21, 2026 12:20pm | Jul 21, 2026 12:22pm | Jul 21, 2026 2:05pm | Jul 21, 2026 2:05pm | Jul 21, 2026 2:05pm |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.07.22512 | C001860043 | Cliton Henry | St.Mary | Completed | Load_264056 | Oracabessa - 210 | Jul 20, 2026 3:39pm | Jul 20, 2026 3:41pm | Jul 20, 2026 3:47pm | Jul 20, 2026 3:47pm | Jul 20, 2026 3:56pm | Jul 20, 2026 4:23pm | Jul 20, 2026 4:27pm | Jul 20, 2026 4:27pm |  |  | Fair | No | RAMI infrastructure area. The meter found off and was reconnected by F. Coach.
Outage | J.E.26.07.22610 | C001860042 | Ricky Hall | St.Catherine | Completed | Load_249045 | Tredegar - 210 | Jul 20, 2026 3:38pm | Jul 20, 2026 3:56pm | Jul 20, 2026 4:08pm | Jul 20, 2026 4:10pm | Jul 20, 2026 4:29pm | Jul 20, 2026 4:30pm | Jul 20, 2026 4:31pm | Jul 20, 2026 4:31pm |  |  | Fair | No | Rami failure customer had transferred from prepaid to postpaid still without supply plz refer to the relevant team
Outage | J.E.26.07.23039 | C001860041 | Daniel Francis | St.Ann | Completed | Load_269468 | Ocho Rios - 510 | Jul 20, 2026 3:37pm | Jul 20, 2026 3:37pm | Jul 20, 2026 6:27pm | Jul 20, 2026 6:27pm | Jul 20, 2026 6:42pm | Jul 20, 2026 7:23pm | Jul 20, 2026 7:24pm | Jul 20, 2026 7:24pm |  |  | Fair | No | Found switch jumper dislodge remade and renew fuse 2amp for 25kva tra
Outage | J.E.26.07.22903 | C001860031 | Ricky Hall | St.Catherine | Completed | Load_261841 | Tredegar - 310 | Jul 20, 2026 3:35pm | Jul 20, 2026 3:56pm | Jul 20, 2026 4:32pm | Jul 20, 2026 4:32pm | Jul 20, 2026 4:51pm | Jul 20, 2026 4:55pm | Jul 20, 2026 4:55pm | Jul 20, 2026 4:55pm | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | 30c6 T secondary pole needs dig and straighten
Non-Outage | J.E.26.07.22812 | C001860030 | Marlon Brown | Trelawny | Completed | Load_242318 | Duncans - 210 | Jul 20, 2026 3:33pm | Jul 21, 2026 7:32am | Jul 21, 2026 7:48am | Jul 21, 2026 7:48am | Jul 21, 2026 9:13am | Jul 21, 2026 9:51am | Jul 21, 2026 9:51am | Jul 21, 2026 9:51am |  |  | Fair | No | Isolated 25kva transformer to retention 1 span secondary phase and neutral Voltage found 116/117=233Voltage leaving 116/117=233.
Outage | J.E.26.07.23007 | C001860029 | Moses Elliston | St.Catherine | Completed | Load_243890 | New Michelton - 210 | Jul 20, 2026 3:33pm | Jul 20, 2026 3:33pm | Jul 21, 2026 10:31am | Jul 21, 2026 10:31am | Jul 21, 2026 10:31am | Jul 21, 2026 10:32am | Jul 21, 2026 10:33am | Jul 21, 2026 10:33am |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.07.22881 | C001860028 | Kenroy Dale | Manchester | Completed | Load_268261 | Kendal - 210 | Jul 20, 2026 3:32pm | Jul 20, 2026 3:33pm | Jul 20, 2026 5:10pm | Jul 20, 2026 5:10pm | Jul 20, 2026 5:56pm | Jul 20, 2026 6:46pm | Jul 20, 2026 6:49pm | Jul 20, 2026 6:49pm |  |  | Fair | No | Corrosion found at pole and pothead remade connections using 2 one bolt clamp and 1 service sleeve voltage reading 115/115/230
Outage | J.E.26.07.22467 | C001860027 | Dean Smith | Trelawny | Completed | Load_252729 | Martha Brae - 210 | Jul 20, 2026 3:31pm | Jul 20, 2026 3:32pm | Jul 20, 2026 5:03pm | Jul 20, 2026 5:03pm | Jul 20, 2026 5:26pm | Jul 20, 2026 5:26pm | Jul 20, 2026 6:29pm | Jul 20, 2026 6:29pm |  |  | Rains | No | Replace 8amp 100kva transformer fuse ( bank of 3 at location). Bank of (3) transformer joints need cleaning , please forward to maintenance dept. voltage left,R-N 109vB-N 110vY-N 203vR-Y 234vB-Y 226vR-B 220v
Outage | J.E.26.07.23035 | C001860025 | Jermaine Williams | Clarendon | Completed | Load_262277 | May Pen - 210 | Jul 20, 2026 3:31pm | Jul 20, 2026 3:31pm | Jul 20, 2026 10:20pm | Jul 20, 2026 10:20pm | Jul 20, 2026 10:45pm | Jul 20, 2026 10:45pm | Jul 20, 2026 10:46pm | Jul 20, 2026 10:46pm |  |  | Fair | No | Replaced blown 100kva 10amp xfmr fuse at bank of three.
Outage | J.E.26.07.23038 | C001860026 | Jermaine Williams | Clarendon | Completed | Load_1000166 | Parnassus - 210 | Jul 20, 2026 3:31pm | Jul 21, 2026 3:27pm | Jul 21, 2026 5:34pm | Jul 21, 2026 5:34pm | Jul 21, 2026 5:35pm | Jul 21, 2026 5:35pm | Jul 21, 2026 5:35pm | Jul 21, 2026 5:35pm |  |  | Fair | No | Replace 1-5A Junction Fuse, Left ok.
Non-Outage | J.E.26.07.22092 | C001860022 | Marlon Brown | Trelawny | Completed | Load_264646 | Duncans - 210 | Jul 20, 2026 3:30pm | Jul 20, 2026 3:31pm | Jul 20, 2026 4:02pm | Jul 20, 2026 8:49pm | Jul 20, 2026 9:24pm | Jul 20, 2026 10:05pm | Jul 20, 2026 10:05pm | Jul 20, 2026 10:05pm |  |  | Fair | No | Check and found ok, internal issues customer advised. Voltage found at pothead 113/107=220Voltage leaving at pothead 113/107=220.
Non-Outage | J.E.26.07.22469 | C001860019 | Donald Cunningham | St.Catherine | Completed | Load_576125 | Twickenham - 210 | Jul 20, 2026 3:26pm | Jul 20, 2026 3:26pm | Jul 20, 2026 4:05pm | Jul 20, 2026 5:00pm | Jul 20, 2026 5:00pm | Jul 20, 2026 5:46pm | Jul 20, 2026 5:47pm | Jul 20, 2026 5:47pm |  |  | Fair | No | Blown junction fuse by pole #486013 replace 30 amp fuse
Outage | J.E.26.07.22529 | C001860012 | Donald Cunningham | Portmore | Completed | Load_248603 | Naggo Head - 510 | Jul 20, 2026 3:25pm | Jul 20, 2026 3:26pm | Jul 20, 2026 8:01pm | Jul 20, 2026 8:02pm | Jul 20, 2026 8:46pm | Jul 20, 2026 8:46pm | Jul 20, 2026 8:56pm | Jul 20, 2026 8:56pm | BrokenWire |  | Fair | No | Premises found close
Outage | J.E.26.07.22722 | C001860011 | Kemark Slue | Portmore | Completed | Load_556669 | Naggo Head - 510 | Jul 20, 2026 3:25pm | Jul 20, 2026 6:37pm | Jul 20, 2026 7:26pm | Jul 20, 2026 7:26pm | Jul 20, 2026 7:26pm | Jul 20, 2026 8:44pm | Jul 20, 2026 9:14pm | Jul 20, 2026 9:14pm |  |  | SevereWind | No | Found 1 blown junction. From 3 phase line section. Patrol and found 1blown fuse from 2 phase junction. Crew found 1phase broken conductor. Remaining fuse was open and using #2 splicing sleeve conductor retention. Found and replace 15amp. And at 3phase junction found and replaced 40amp. Area okay
Non-Outage | J.E.26.07.22768 | C001859997 | Derrick Grubb | null | Completed | null | null | Jul 20, 2026 3:20pm | Jul 21, 2026 7:11am | Jul 21, 2026 10:36am | Jul 21, 2026 10:36am | Jul 21, 2026 10:36am | Jul 21, 2026 10:38am | Jul 21, 2026 10:38am | Jul 21, 2026 10:38am |  |  | Fair | No | Premises not located, several calls to customer phone went unanswered.
Non-Outage | J.E.26.07.22657 | C001859994 | Jermaine Williams | Clarendon | Completed | Load_255474 | Parnassus - 210 | Jul 20, 2026 3:18pm | Jul 20, 2026 3:19pm | Jul 20, 2026 8:19pm | Jul 20, 2026 8:19pm | Jul 20, 2026 8:53pm | Jul 20, 2026 8:53pm | Jul 20, 2026 8:54pm | Jul 20, 2026 8:54pm |  |  | Fair | No | Premises not found.
Non-Outage | J.E.26.07.22963 | C001859993 | Jermaine Williams | Clarendon | Completed | Load_255181 | Monymusk - 410 | Jul 20, 2026 3:18pm | Jul 20, 2026 3:19pm | Jul 20, 2026 7:17pm | Jul 20, 2026 7:17pm | Jul 20, 2026 8:13pm | Jul 20, 2026 8:14pm | Jul 20, 2026 8:16pm | Jul 20, 2026 8:16pm |  |  | Fair | No | Defective 25kva xfmr, xfmr X1 bushing burnt out and causing intermittent low voltage. Xfmr also leaking oil. Refer to mtce to have xfmr replace urgently.
Outage | J.E.26.07.22615 | C001859991 | Jermaine Williams | Clarendon | Completed | Load_1000625 | May Pen - 210 | Jul 20, 2026 3:18pm | Jul 20, 2026 3:19pm | Jul 20, 2026 6:17pm | Jul 20, 2026 6:17pm | Jul 20, 2026 6:34pm | Jul 20, 2026 6:37pm | Jul 20, 2026 6:38pm | Jul 20, 2026 6:38pm |  |  | Fair | No | Area found with supply
Outage | J.E.26.07.22745 | C001859992 | Jermaine Williams | Clarendon | Completed | Load_249409 | May Pen - 110 | Jul 20, 2026 3:18pm | Jul 20, 2026 3:19pm | Jul 20, 2026 4:50pm | Jul 20, 2026 5:15pm | Jul 20, 2026 6:07pm | Jul 20, 2026 6:13pm | Jul 20, 2026 6:14pm | Jul 20, 2026 6:14pm | BrokenWire |  | Fair | No | Change 70’ defective #6 triplex.
Outage | J.E.26.07.22994 | C001859995 | Roxroy Needham | St.Ann | Completed | Load_244666 | Cardiff Hall - 310 | Jul 20, 2026 3:18pm | Jul 20, 2026 3:20pm | Jul 20, 2026 4:48pm | Jul 20, 2026 4:48pm | Jul 20, 2026 6:34pm | Jul 20, 2026 6:43pm | Jul 20, 2026 6:44pm | Jul 20, 2026 6:44pm |  | Y | Fair | No | Reset a 25 KVA transformer at pole # 603452
Outage | J.E.26.07.23004 | C001859989 | Roxroy Needham | St.Ann | Completed | Load_268647 | Cardiff Hall - 210 | Jul 20, 2026 3:18pm | Jul 20, 2026 3:34pm | Jul 20, 2026 9:18pm | Jul 20, 2026 9:18pm | Jul 20, 2026 9:18pm | Jul 20, 2026 9:16pm | Jul 20, 2026 9:19pm | Jul 20, 2026 9:19pm |  |  | Fair | No | Premises found ok call customer and customer say she didn’t make a report
Outage | J.E.26.07.22311 | C001859988 | Tyrese Williams | St.Ann | Completed | Load_264409 | Cardiff Hall - 310 | Jul 20, 2026 3:17pm | Jul 21, 2026 8:08am | Jul 21, 2026 8:31am | Jul 21, 2026 10:58am | Jul 21, 2026 11:37am | Jul 21, 2026 12:34pm | Jul 21, 2026 12:35pm | Jul 21, 2026 12:35pm | BrokenWire |  | Fair | No | Splice and retention 2 span of phase and neutral and replace a 25 kva transformer fuse with a 3 amp
Outage | J.E.26.07.22964 | C001859987 | Daniel Francis | St.Ann | Completed | Load_267320 | Roaring River - 210 | Jul 20, 2026 3:17pm | Jul 20, 2026 3:17pm | Jul 20, 2026 11:07pm | Jul 20, 2026 11:07pm | Jul 20, 2026 11:08pm | Jul 20, 2026 11:14pm | Jul 20, 2026 11:14pm | Jul 20, 2026 11:14pm |  |  | Fair | No | Found okay customer say them don’t have water not light so we tell them to call nwc not JPS we don’t do water we do light for the people from JPS line to the house so you can have light
Outage | J.E.26.07.23019 | C001859986 | Daniel Francis | St.Ann | Completed | Load_262751 | Roaring River - 210 | Jul 20, 2026 3:17pm | Jul 20, 2026 3:17pm | Jul 20, 2026 11:15pm | Jul 20, 2026 11:15pm | Jul 21, 2026 12:27am | Jul 21, 2026 12:29am | Jul 21, 2026 12:29am | Jul 21, 2026 12:29am |  |  | Fair | No | Found okay
Outage | J.E.26.07.22940 | C001859985 | Dean Smith | Hanover | Completed | Load_252795 | Orange Bay - 310 | Jul 20, 2026 3:16pm | Jul 20, 2026 3:16pm | Jul 20, 2026 6:31pm | Jul 20, 2026 6:31pm | Jul 20, 2026 7:13pm | Jul 20, 2026 7:13pm | Jul 20, 2026 7:14pm | Jul 20, 2026 7:14pm |  |  | Rains | No | Reset 10kva transformer.
Non-Outage | J.E.26.07.22486 | C001859974 | Hartley Chin | Clarendon | Completed | Load_579438 | May Pen - 110 | Jul 20, 2026 3:14pm | Jul 21, 2026 7:35am | Jul 21, 2026 10:59am | Jul 21, 2026 10:59am | Jul 21, 2026 11:53am | Jul 21, 2026 12:22pm | Jul 21, 2026 12:23pm | Jul 21, 2026 12:23pm |  |  | Fair | No | Found ok customer wanted service wire to be changed due fire yesterday, service wire is ok and voltage reading is as follows 111v 113v 225v
Outage | J.E.26.07.22434 | C001859976 | Clyde Brown | Clarendon | Completed | Load_251963 | May Pen - 110 | Jul 20, 2026 3:14pm | Jul 20, 2026 3:15pm | Jul 20, 2026 4:22pm | Jul 20, 2026 4:22pm | Jul 20, 2026 5:12pm | Jul 20, 2026 6:10pm | Jul 20, 2026 6:24pm | Jul 20, 2026 6:24pm |  |  | Fair | No | Voltage found 132/81 on each phase,line patrolled and isolate 3wire service leaving one customer without supply to again patrolled line with one meter at top of hill to get day attention.
Outage | J.E.26.07.22537 | C001859973 | Hartley Chin | Clarendon | Completed | Load_254174 | May Pen - 110 | Jul 20, 2026 3:14pm | Jul 21, 2026 7:34am | Jul 21, 2026 8:10am | Jul 21, 2026 8:10am | Jul 21, 2026 10:42am | Jul 21, 2026 10:57am | Jul 21, 2026 10:58am | Jul 21, 2026 10:58am |  |  | Fair | No | Refer to field service. Customer has defective meter .
Outage | J.E.26.07.23017 | C001859972 | Horace Malcolm | null | Completed | Load_1002435 | Queens Drive - 810 | Jul 20, 2026 3:12pm | Jul 20, 2026 3:19pm | Jul 20, 2026 3:28pm | Jul 20, 2026 3:28pm | Jul 20, 2026 3:58pm | Jul 20, 2026 4:05pm | Jul 20, 2026 4:05pm | Jul 20, 2026 4:05pm |  |  | Fair | No | Check and found ok customer says no report was made only there elactrician is there working
Outage | J.E.26.07.23015 | C001859967 | Horace Malcolm | St.James | Completed | Load_250410 | Queens Drive - 710 | Jul 20, 2026 3:10pm | Jul 20, 2026 3:11pm | Jul 20, 2026 4:13pm | Jul 20, 2026 4:13pm | Jul 20, 2026 4:58pm | Jul 20, 2026 5:28pm | Jul 20, 2026 5:28pm | Jul 20, 2026 5:28pm |  |  | Fair | No | Clean and remake joints at pole used 1clamp voltage 113-115-228
Non-Outage | J.E.26.07.21816 | C001859966 | Clyde Brown | Clarendon | Completed | Load_238175 | May Pen - 110 | Jul 20, 2026 3:09pm | Jul 20, 2026 3:11pm | Jul 20, 2026 6:24pm | Jul 20, 2026 6:24pm | Jul 20, 2026 8:53pm | Jul 20, 2026 8:46pm | Jul 20, 2026 8:59pm | Jul 20, 2026 8:59pm |  |  | Fair | No | Found 25kva transformer phase and neutral lead corroded one bolt clamp replaced,Voltage left 118/113V and 232V
Outage | J.E.26.07.22961 | C001859962 | Barnett Brown | Manchester | Completed | Load_269342 | Porus - 310 | Jul 20, 2026 3:08pm | Jul 20, 2026 3:10pm | Jul 20, 2026 3:23pm | Jul 20, 2026 3:23pm | Jul 20, 2026 5:11pm | Jul 20, 2026 5:45pm | Jul 20, 2026 5:46pm | Jul 20, 2026 5:46pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.22969 | C001859963 | Damion Reid | Manchester | Completed | Load_574231 | Porus - 310 | Jul 20, 2026 3:08pm | Jul 21, 2026 8:37am | Jul 21, 2026 9:08am | Jul 21, 2026 9:08am | Jul 21, 2026 9:53am | Jul 21, 2026 10:03am | Jul 21, 2026 10:05am | Jul 21, 2026 10:05am |  |  | Fair | No | Unable to contact or locate customer
Outage | J.E.26.07.22974 | C001859964 | Barnett Brown | Manchester | Completed | Load_247696 | Porus - 310 | Jul 20, 2026 3:08pm | Jul 20, 2026 3:10pm | Jul 20, 2026 8:10pm | Jul 20, 2026 8:10pm | Jul 20, 2026 8:51pm | Jul 20, 2026 8:51pm | Jul 20, 2026 8:59pm | Jul 20, 2026 8:59pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.22995 | C001859965 | Damion Reid | Manchester | Completed | Load_242146 | Porus - 310 | Jul 20, 2026 3:08pm | Jul 21, 2026 8:37am | Jul 21, 2026 10:07am | Jul 21, 2026 10:07am | Jul 21, 2026 10:22am | Jul 21, 2026 10:30am | Jul 21, 2026 10:30am | Jul 21, 2026 10:30am |  |  | Fair | No | Area found ok
Outage | J.E.26.07.22930 | C001859961 | Michael Christian | St.James | Completed | Load_239990 | Bogue - 610 | Jul 20, 2026 3:07pm | Jul 20, 2026 3:08pm | Jul 20, 2026 4:10pm | Jul 20, 2026 4:10pm | Jul 20, 2026 4:48pm | Jul 20, 2026 5:07pm | Jul 20, 2026 5:07pm | Jul 20, 2026 5:07pm |  |  | Rains | No | Found 1 15 amp junction out cause by lightning replace at pole # 606648
Outage | J.E.26.07.22999 | C001859960 | Michael Christian | St.James | Completed | Load_556247 | Bogue - 610 | Jul 20, 2026 3:07pm | Jul 20, 2026 3:08pm | Jul 20, 2026 3:26pm | Jul 20, 2026 3:26pm | Jul 20, 2026 4:00pm | Jul 20, 2026 4:03pm | Jul 20, 2026 4:04pm | Jul 20, 2026 4:04pm |  |  | Rains | No | Found disconnection send to field service
Non-Outage | J.E.26.07.23010 | C001859952 | Edward Royal | null | Completed | null | null | Jul 20, 2026 3:05pm | Jul 20, 2026 3:05pm | Jul 20, 2026 3:26pm | Jul 20, 2026 3:26pm | Jul 20, 2026 3:47pm | Jul 20, 2026 5:43pm | Jul 20, 2026 5:43pm | Jul 20, 2026 5:43pm | BrokenWire |  | Fair | No | Spliced and reconnected secondary phase and neutral using 50 ft 2 north cable and 5 single bolt clamp
Outage | J.E.26.07.22988 | C001859950 | Milton Charlton | KSAN | Completed | Load_265781 | Hope - 510 | Jul 20, 2026 3:04pm | Jul 20, 2026 3:05pm | Jul 20, 2026 3:16pm | Jul 20, 2026 3:16pm | Jul 20, 2026 4:41pm | Jul 20, 2026 4:40pm | Jul 20, 2026 4:46pm | Jul 20, 2026 4:46pm | TreeContact |  | Fair | No | Primary and secondary bushing is required.Tree limb touching primary conductors.
Outage | J.E.26.07.22530 | C001859948 | Richman Whyte | Westmoreland | Completed | Load_250735 | Paradise - 210 | Jul 20, 2026 3:02pm | Jul 20, 2026 3:04pm | Jul 20, 2026 3:47pm | Jul 20, 2026 3:47pm | Jul 20, 2026 4:50pm | Jul 20, 2026 7:04pm | Jul 20, 2026 7:06pm | Jul 20, 2026 7:06pm | Fire |  | Rains | No | Open bank a two transformer and repair one span open secondary conductor use one #2/0 splicing sleeve 8 one bolt clamps voltage 116 117 205 236 235 235
Outage | J.E.26.07.22982 | C001859947 | Richman Whyte | Westmoreland | Completed | Load_255000 | Paradise - 110 | Jul 20, 2026 3:02pm | Jul 20, 2026 3:04pm | Jul 20, 2026 7:43pm | Jul 20, 2026 7:43pm | Jul 20, 2026 7:58pm | Jul 20, 2026 8:25pm | Jul 20, 2026 8:26pm | Jul 20, 2026 8:26pm |  |  | Rains | No | Replace two amp twenty five kva transformer fuse
Non-Outage | J.E.26.07.22660 | C001859914 | Kemark Slue | St.Catherine | Completed | Load_266407 | Twickenham - 310 | Jul 20, 2026 2:36pm | Jul 20, 2026 3:34pm | Jul 20, 2026 3:44pm | Jul 20, 2026 3:44pm | Jul 20, 2026 4:10pm | Jul 20, 2026 4:19pm | Jul 20, 2026 4:21pm | Jul 20, 2026 4:21pm |  |  | Fair | No | At location crew found defective 50kva transformer with x1 bushing burnt out . Transformer was left energized to supply 2w customers. Please notify maintenance
Outage | J.E.26.07.22946 | C001859902 | Eric Williams | KSAS | Completed | Load_256528 | Duhaney - 310 | Jul 20, 2026 2:35pm | Jul 20, 2026 3:53pm | Jul 20, 2026 5:29pm | Jul 20, 2026 5:30pm | Jul 20, 2026 6:00pm | Jul 20, 2026 6:03pm | Jul 20, 2026 6:05pm | Jul 20, 2026 6:05pm | LowHangingWires |  | Fair | No | Both number on account say they didn’t make a report, premises lock.
Non-Outage | J.E.26.07.21021 | C001859895 | Error Coore | Manchester | Completed | Load_239869 | Porus - 310 | Jul 20, 2026 2:26pm | Jul 20, 2026 2:27pm | Jul 20, 2026 3:32pm | Jul 20, 2026 3:32pm | Jul 20, 2026 3:44pm | Jul 20, 2026 3:50pm | Jul 20, 2026 3:52pm | Jul 20, 2026 3:52pm |  |  | Fair | No | Called customer and customer said no one will be home until 5:00
Non-Outage | J.E.26.07.22747 | C001859893 | Error Coore | Manchester | Completed | Load_245911 | Kendal - 310 | Jul 20, 2026 2:26pm | Jul 20, 2026 2:27pm | Jul 20, 2026 2:39pm | Jul 20, 2026 2:39pm | Jul 20, 2026 2:59pm | Jul 20, 2026 3:28pm | Jul 20, 2026 3:31pm | Jul 20, 2026 3:31pm |  |  | Fair | No | Found customer three phase service wire defective customer service wire need to be replaced
Non-Outage | J.E.26.07.22846 | C001859872 | Edward Royal | KSAS | Completed | Load_259251 | Greenwich - 410 | Jul 20, 2026 2:20pm | Jul 21, 2026 7:46am | Jul 21, 2026 8:54am | Jul 21, 2026 8:54am | Jul 21, 2026 8:54am | Jul 21, 2026 11:04am | Jul 21, 2026 11:04am | Jul 21, 2026 11:04am | Fire |  | Fair | No | Spliced and reconnected 4 north quad cable and spliced and reconnected 2 triplex cable using 30ft 4 north quad cables and 20 ft #2 triplex cable 10 one bolt clamps no pole #
Non-Outage | J.E.26.07.22751 | C001859861 | Damion Reid | null | Completed | null | null | Jul 20, 2026 2:11pm | Jul 21, 2026 8:37am | Jul 21, 2026 1:10pm | Jul 21, 2026 1:10pm | Jul 21, 2026 1:56pm | Jul 21, 2026 2:44pm | Jul 21, 2026 2:45pm | Jul 21, 2026 2:45pm | Fire |  | Fair | No | Premises found ok
Outage | J.E.26.07.22727 | C001859860 | Barnett Brown | Manchester | Completed | Load_266399 | Porus - 310 | Jul 20, 2026 2:11pm | Jul 20, 2026 3:12pm | Jul 20, 2026 7:05pm | Jul 20, 2026 7:05pm | Jul 20, 2026 7:51pm | Jul 20, 2026 7:51pm | Jul 20, 2026 8:09pm | Jul 20, 2026 8:09pm | Fire |  | Fair | No | Premises found ok
Outage | J.E.26.07.22924 | C001859854 | Kenroy Dale | Manchester | Completed | Load_270122 | Kendal - 210 | Jul 20, 2026 2:07pm | Jul 20, 2026 3:34pm | Jul 20, 2026 8:07pm | Jul 20, 2026 8:07pm | Jul 20, 2026 9:12pm | Jul 20, 2026 9:19pm | Jul 20, 2026 9:26pm | Jul 20, 2026 9:26pm |  |  | Fair | No | Area visited and found with supply, customer also confirmed that supply was restored and was advised to write off call by dispatch
Outage | J.E.26.07.22764 | C001859827 | Oshane Warren | St.Elizabeth | Completed | Load_292665 | Maggotty - 110 | Jul 20, 2026 1:56pm | Jul 20, 2026 7:45pm | Jul 20, 2026 7:55pm | Jul 20, 2026 7:55pm | Jul 20, 2026 7:55pm | Jul 20, 2026 7:56pm | Jul 20, 2026 7:56pm | Jul 20, 2026 7:56pm |  |  | Rains | No | Hexing metering system refer to feel service
Non-Outage | J.E.26.07.22645 | C001859808 | Dwain Samuels | Westmoreland | Completed | Load_248554 | Paradise - 210 | Jul 20, 2026 1:45pm | Jul 20, 2026 1:45pm | Jul 20, 2026 1:51pm | Jul 20, 2026 2:01pm | Jul 20, 2026 2:11pm | Jul 20, 2026 2:53pm | Jul 20, 2026 2:57pm | Jul 20, 2026 2:57pm |  |  | Fair | No | 1 pole spend of secondary line burnt down at the Texaco at Lewis street ina savannalamar needs urgent attention
Non-Outage | J.E.26.07.22739 | C001859809 | Dwain Samuels | Westmoreland | Completed | Load_248554 | Paradise - 210 | Jul 20, 2026 1:45pm | Jul 20, 2026 1:45pm | Jul 20, 2026 1:51pm | Jul 21, 2026 9:59am | Jul 21, 2026 10:00am | Jul 21, 2026 10:06am | Jul 21, 2026 10:07am | Jul 21, 2026 10:07am |  |  | Fair | No | Found working okay. Voltage check 114-116-230
Outage | J.E.26.07.22692 | C001859790 | Andrew Powell | St.Elizabeth | Completed | Load_262286 | Maggotty - 210 | Jul 20, 2026 1:30pm | Jul 20, 2026 3:17pm | Jul 20, 2026 3:29pm | Jul 20, 2026 3:29pm | Jul 20, 2026 3:30pm | Jul 20, 2026 3:30pm | Jul 20, 2026 3:31pm | Jul 20, 2026 3:31pm |  |  | Fair | No | Premises found okay customer stated that supply restored.
Outage | J.E.26.07.21445 | C001859785 | Moses Elliston | Portmore | Completed | Load_300752 | Naggo Head - 610 | Jul 20, 2026 1:21pm | Jul 20, 2026 1:22pm | Jul 20, 2026 2:00pm | Jul 20, 2026 2:00pm | Jul 20, 2026 2:00pm | Jul 20, 2026 2:21pm | Jul 20, 2026 2:23pm | Jul 20, 2026 2:23pm |  |  | Fair | No | Customer said Private Electrician attended.
Outage | J.E.26.07.22646 | C001859784 | Ryan Richards | Manchester | Completed | Load_242635 | Spur Tree - 310 | Jul 20, 2026 1:21pm | Jul 20, 2026 1:22pm | Jul 20, 2026 2:35pm | Jul 20, 2026 2:35pm | Jul 20, 2026 4:24pm | Jul 20, 2026 6:26pm | Jul 20, 2026 6:28pm | Jul 20, 2026 6:28pm |  |  | Fair | No | Blown 3 amp fuse found for 25 kva transformer line patrol nothing found blown fuse was replaced
Outage | J.E.26.07.22650 | C001859783 | Andre Williams | Trelawny | Completed | Load_302817 | Duncans - 110 | Jul 20, 2026 1:21pm | Jul 20, 2026 1:24pm | Jul 20, 2026 1:34pm | Jul 20, 2026 1:37pm | Jul 20, 2026 1:37pm | Jul 20, 2026 1:38pm | Jul 20, 2026 1:39pm | Jul 20, 2026 1:39pm |  |  | Fair | No | Unable to locate pole no clear direction given to find location
Outage | J.E.26.07.22616 | C001859760 | Milton Charlton | KSAN | Completed | Load_266412 | West Kings House - 410 | Jul 20, 2026 1:05pm | Jul 20, 2026 1:06pm | Jul 20, 2026 1:36pm | Jul 20, 2026 1:36pm | Jul 20, 2026 2:10pm | Jul 20, 2026 2:00pm | Jul 20, 2026 2:16pm | Jul 20, 2026 2:16pm |  |  | Fair | No | Customer service wire #2/0 triplex neutral broken in mid- span. Need bucket truck to repair broken neutral..
Outage | J.E.26.07.22627 | C001859759 | Milton Charlton | KSAN | Completed | Load_579112 | West Kings House - 410 | Jul 20, 2026 1:05pm | Jul 20, 2026 1:06pm | Jul 20, 2026 2:20pm | Jul 20, 2026 2:20pm | Jul 20, 2026 3:01pm | Jul 20, 2026 2:55pm | Jul 20, 2026 3:03pm | Jul 20, 2026 3:03pm |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.07.22611 | C001859743 | Edward Royal | KSAN | Completed | Load_241915 | Washington Blvd - 710 | Jul 20, 2026 12:53pm | Jul 20, 2026 12:54pm | Jul 20, 2026 8:16pm | Jul 20, 2026 8:16pm | Jul 20, 2026 8:23pm | Jul 20, 2026 8:35pm | Jul 20, 2026 8:35pm | Jul 20, 2026 8:35pm |  |  | Fair | No | Customer have internal problems customer have defective breaker advise customer to get a electrician to fix the problem voltage reading 236 117 118 v
Non-Outage | J.E.26.07.22613 | C001859737 | Edward Royal | null | Completed | null | null | Jul 20, 2026 12:51pm | Jul 20, 2026 12:51pm | Jul 20, 2026 3:04pm | Jul 20, 2026 3:04pm | Jul 20, 2026 3:04pm | Jul 20, 2026 3:05pm | Jul 20, 2026 3:05pm | Jul 20, 2026 3:05pm | BrokenWire |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.07.22576 | C001859742 | Neville Spencer | Clarendon | Completed | Load_572086 | Parnassus - 310 | Jul 20, 2026 12:51pm | Jul 20, 2026 1:04pm | Jul 20, 2026 1:54pm | Jul 20, 2026 1:54pm | Jul 20, 2026 2:03pm | Jul 20, 2026 2:03pm | Jul 20, 2026 3:12pm | Jul 20, 2026 3:12pm |  |  | Fair | No | Found blown 25 amp fuse in 15 kva xmfr at pole # 0107876 replace with 2 amp fuse.Also renew blown 20 amp j/ fuse at pole # 0183780 area restored.
Outage | J.E.26.07.22592 | C001859728 | Dean Smith | Hanover | Completed | Load_241288 | Orange Bay - 310 | Jul 20, 2026 12:40pm | Jul 20, 2026 3:17pm | Jul 20, 2026 10:53pm | Jul 20, 2026 10:53pm | Jul 20, 2026 10:53pm | Jul 20, 2026 10:53pm | Jul 20, 2026 10:53pm | Jul 20, 2026 10:53pm |  |  | Rains | No | Shift ended
Non-Outage | J.E.26.07.22535 | C001859727 | Dwain Samuels | Westmoreland | Completed | Load_240753 | Paradise - 210 | Jul 20, 2026 12:39pm | Jul 20, 2026 12:40pm | Jul 20, 2026 1:34pm | Jul 21, 2026 10:19am | Jul 21, 2026 10:47am | Jul 21, 2026 11:02am | Jul 21, 2026 11:04am | Jul 21, 2026 11:04am |  |  | Fair | No | Meter found burnt needs changing ergently
Outage | J.E.26.07.22597 | C001859726 | Javid Vernon | Westmoreland | Completed | Load_244638 | Paradise - 210 | Jul 20, 2026 12:39pm | Jul 20, 2026 12:40pm | Jul 20, 2026 1:34pm | Jul 20, 2026 1:34pm | Jul 20, 2026 1:56pm | Jul 20, 2026 2:30pm | Jul 20, 2026 2:31pm | Jul 20, 2026 2:31pm |  |  | Fair | No | Remove illegal connection and Refuse one 25kva transformer 3amp fuse
Outage | J.E.26.07.22599 | C001859725 | Stephen Taylor | Trelawny | Completed | Load_259034 | Greenwood - 110 | Jul 20, 2026 12:38pm | Jul 20, 2026 12:38pm | Jul 20, 2026 1:56pm | Jul 20, 2026 1:56pm | Jul 20, 2026 1:56pm | Jul 20, 2026 1:56pm | Jul 20, 2026 1:56pm | Jul 20, 2026 1:56pm | BrokenWire |  | Fair | No | Wrong address
Non-Outage | J.E.26.07.22578 | C001859724 | Kaydon Taylor | null | Completed | null | null | Jul 20, 2026 12:37pm | Jul 20, 2026 3:50pm | Jul 20, 2026 4:44pm | Jul 20, 2026 4:44pm | Jul 20, 2026 7:41pm | Jul 20, 2026 7:49pm | Jul 20, 2026 7:49pm | Jul 20, 2026 7:49pm |  |  | Fair | No | Work started today is expected to resume tomorrow morning so that the isolated line section can be re- energized .
Non-Outage | J.E.26.07.22590 | C001859719 | Edward Royal | null | Completed | null | null | Jul 20, 2026 12:35pm | Jul 20, 2026 12:50pm | Jul 20, 2026 2:11pm | Jul 20, 2026 2:11pm | Jul 20, 2026 2:11pm | Jul 20, 2026 3:03pm | Jul 20, 2026 3:04pm | Jul 20, 2026 3:04pm | BrokenWire |  | Fair | No | Spliced and reconnected secondary phase using 30ft open number 2 conductor 3 single bolt clamp pole #0018895
Outage | J.E.26.07.22556 | C001859718 | Kaydon Taylor | KSAN | Completed | Load_239302 | Constant Spring - 210 | Jul 20, 2026 12:34pm | Jul 20, 2026 12:35pm | Jul 20, 2026 2:24pm | Jul 20, 2026 2:24pm | Jul 20, 2026 2:41pm | Jul 20, 2026 2:51pm | Jul 20, 2026 2:51pm | Jul 20, 2026 2:51pm |  |  | Fair | No | Reset customer breaker
Outage | J.E.26.07.22591 | C001859717 | Milton Charlton | KSAN | Completed | Load_243463 | Hope - 510 | Jul 20, 2026 12:33pm | Jul 20, 2026 12:34pm | Jul 20, 2026 3:04pm | Jul 20, 2026 4:54pm | Jul 20, 2026 5:14pm | Jul 20, 2026 5:20pm | Jul 20, 2026 5:17pm | Jul 20, 2026 5:17pm |  |  | Fair | No | Reconnect customer meter that was disconnected. Reconnection was done by JPS escalation.
Outage | J.E.26.07.22538 | C001859713 | Daniel Francis | St.Ann | Completed | Load_258103 | Roaring River - 410 | Jul 20, 2026 12:30pm | Jul 20, 2026 3:07pm | Jul 20, 2026 4:34pm | Jul 20, 2026 4:34pm | Jul 20, 2026 4:49pm | Jul 20, 2026 4:58pm | Jul 20, 2026 5:01pm | Jul 20, 2026 5:01pm | BrokenWire |  | Fair | No | Remade service wire joints at JPS pole two 1bolt voltage 1@17/117/234
Non-Outage | J.E.26.07.22550 | C001859712 | Moses Elliston | null | Completed | null | null | Jul 20, 2026 12:29pm | Jul 20, 2026 12:30pm | Jul 20, 2026 2:24pm | Jul 20, 2026 2:24pm | Jul 20, 2026 3:04pm | Jul 20, 2026 2:50pm | Jul 20, 2026 3:06pm | Jul 20, 2026 3:06pm |  |  | Fair | No | Supply ok at premises.
Outage | J.E.26.07.22296 | C001859710 | Moses Elliston | St.Catherine | Completed | Load_266292 | Tredegar - 310 | Jul 20, 2026 12:29pm | Jul 20, 2026 12:30pm | Jul 20, 2026 1:14pm | Jul 20, 2026 1:14pm | Jul 20, 2026 1:14pm | Jul 20, 2026 1:43pm | Jul 20, 2026 1:44pm | Jul 20, 2026 1:44pm |  |  | Fair | No | Meter changed to # 3069917. No indicating lights .Also not communicating
Outage | J.E.26.07.22545 | C001859711 | Moses Elliston | St.Catherine | Completed | Load_268576 | Rhodens Pen - 410 | Jul 20, 2026 12:29pm | Jul 20, 2026 12:30pm | Jul 20, 2026 4:49pm | Jul 20, 2026 4:49pm | Jul 20, 2026 4:49pm | Jul 20, 2026 4:49pm | Jul 20, 2026 4:52pm | Jul 20, 2026 4:52pm |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.07.22561 | C001859704 | Raymond Lewis | St.Ann | Completed | Load_264669 | Cardiff Hall - 310 | Jul 20, 2026 12:23pm | Jul 20, 2026 12:24pm | Jul 20, 2026 3:01pm | Jul 20, 2026 3:01pm | Jul 20, 2026 3:43pm | Jul 20, 2026 4:02pm | Jul 20, 2026 4:03pm | Jul 20, 2026 4:03pm |  |  | Rains | No | Refuse and close 40 amp junction
Non-Outage | J.E.26.07.22584 | C001859703 | Milton Charlton | null | Completed | null | null | Jul 20, 2026 12:22pm | Jul 20, 2026 12:27pm | Jul 20, 2026 3:03pm | Jul 20, 2026 3:03pm | Jul 20, 2026 3:09pm | Jul 20, 2026 3:40pm | Jul 20, 2026 3:16pm | Jul 20, 2026 3:16pm | Fire |  | Fair | No | Primary and secondary bushing is required urgently at pole #0057228.Bushing required urgently along line section.
Outage | J.E.26.07.22582 | C001859702 | Michael Christian | St.James | Completed | Load_261318 | Bogue - 610 | Jul 20, 2026 12:22pm | Jul 20, 2026 3:08pm | Jul 20, 2026 4:00pm | Jul 20, 2026 5:07pm | Jul 20, 2026 6:07pm | Jul 20, 2026 6:15pm | Jul 20, 2026 6:15pm | Jul 20, 2026 6:15pm |  |  | Rains | No | Connection customer service wire at pole and pothead voltage 111 110 221 at meter
Outage | J.E.26.07.22443 | C001859696 | Hopeton Henry | St.Thomas | Completed | Load_262336 | Good Year - 110 | Jul 20, 2026 12:19pm | Jul 20, 2026 3:21pm | Jul 20, 2026 6:39pm | Jul 20, 2026 6:45pm | Jul 20, 2026 6:45pm | Jul 20, 2026 6:45pm | Jul 20, 2026 6:46pm | Jul 20, 2026 6:46pm |  |  | Fair | No | Found ok , customer was disconnected for nonpayment
Outage | J.E.26.07.22467 | C001859697 | Tajay Bernard | Trelawny | Completed | Load_252729 | Martha Brae - 210 | Jul 20, 2026 12:19pm | Jul 20, 2026 12:36pm | Jul 20, 2026 1:08pm | Jul 20, 2026 1:08pm | Jul 20, 2026 1:08pm | Jul 20, 2026 1:09pm | Jul 20, 2026 1:10pm | Jul 20, 2026 1:10pm |  |  | Fair | No | This call belongs to st trelawny
Outage | J.E.26.07.22508 | C001859695 | Derrick Grubb | St.Thomas | Completed | Load_256512 | Good Year - 110 | Jul 20, 2026 12:19pm | Jul 21, 2026 7:11am | Jul 21, 2026 8:48am | Jul 21, 2026 8:48am | Jul 21, 2026 8:48am | Jul 21, 2026 8:54am | Jul 21, 2026 8:54am | Jul 21, 2026 8:54am |  |  | Fair | No | Contact customer by phone and customer said premises is okay. The report she’s making is about a defective streetlight at her gate.
Non-Outage | J.E.26.07.22524 | C001859690 | Wan Carlos Scarlett | St.Elizabeth | Completed | Load_249708 | Maggotty - 110 | Jul 20, 2026 12:15pm | Jul 20, 2026 12:24pm | Jul 20, 2026 12:30pm | Jul 20, 2026 12:30pm | Jul 20, 2026 1:08pm | Jul 20, 2026 2:45pm | Jul 20, 2026 2:47pm | Jul 20, 2026 2:47pm | Fire |  | Fair | No | Found 2 span of open secondary line phase jumper burn out from the one bolt clamp use 4 one bolt clamps at pole readings 117-115-234
Outage | J.E.26.07.22572 | C001859684 | Richman Whyte | Westmoreland | Completed | Load_269914 | Paradise - 110 | Jul 20, 2026 12:10pm | Jul 20, 2026 4:25pm | Jul 20, 2026 7:37pm | Jul 20, 2026 7:37pm | Jul 20, 2026 7:37pm | Jul 20, 2026 7:40pm | Jul 20, 2026 7:42pm | Jul 20, 2026 7:42pm |  |  | Fair | No | Change defective clamp at pothead use 1 one bolt clamp voltage 114 115 230
Outage | J.E.26.07.22564 | C001859683 | Rusean Allen | KSAS | Completed | Load_572216 | Cane River - 610 | Jul 20, 2026 12:07pm | Jul 20, 2026 12:08pm | Jul 20, 2026 2:25pm | Jul 20, 2026 2:25pm | Jul 20, 2026 2:25pm | Jul 20, 2026 2:27pm | Jul 20, 2026 2:29pm | Jul 20, 2026 2:29pm |  |  | Fair | No | Primary voltage 25.53 25.61Pad mount transformer needs to check Refer to SMDSecondary voltage 405v 399v 391v
Outage | J.E.26.07.22514 | C001859673 | Horace Malcolm | St.James | Completed | Load_262551 | Queens Drive - 710 | Jul 20, 2026 12:01pm | Jul 20, 2026 4:34pm | Jul 20, 2026 6:33pm | Jul 20, 2026 6:33pm | Jul 20, 2026 7:16pm | Jul 20, 2026 7:38pm | Jul 20, 2026 7:39pm | Jul 20, 2026 7:39pm | BrokenWire |  | Fair | No | Splice and retention customer service nuetral used 10ft #6 triplex wire and 1clamp voltage 112-114-226
Outage | J.E.26.07.22516 | C001859674 | Shamour Haughton | St.James | Completed | Load_301686 | Bogue - 310 | Jul 20, 2026 12:01pm | Jul 20, 2026 4:36pm | Jul 20, 2026 5:45pm | Jul 20, 2026 5:45pm | Jul 20, 2026 5:45pm | Jul 20, 2026 5:45pm | Jul 20, 2026 5:47pm | Jul 20, 2026 5:47pm |  |  | Fair | No | Customer number went voicemail after several calls, directions needed, unable to locate customer
Non-Outage | J.E.26.07.22555 | C001859672 | Andre Williams | null | Completed | null | null | Jul 20, 2026 12:00pm | Jul 20, 2026 12:00pm | Jul 20, 2026 12:27pm | Jul 20, 2026 12:30pm | Jul 20, 2026 12:36pm | Jul 20, 2026 12:38pm | Jul 20, 2026 12:40pm | Jul 20, 2026 12:40pm |  |  | Fair | No | LOC on meter field service working on issue
Outage | J.E.26.07.22518 | C001859670 | Andre Williams | Trelawny | Completed | Load_249135 | Martha Brae - 210 | Jul 20, 2026 11:57am | Jul 20, 2026 11:58am | Jul 20, 2026 12:19pm | Jul 20, 2026 12:46pm | Jul 20, 2026 12:59pm | Jul 20, 2026 1:13pm | Jul 20, 2026 1:14pm | Jul 20, 2026 1:14pm |  |  | Fair | No | Unable to locate customer need more directions to get to papagus restaurant, phone not answering
Outage | J.E.26.07.22515 | C001859643 | Milton Charlton | KSAN | Completed | Load_237926 | Washington Blvd - 310 | Jul 20, 2026 11:36am | Jul 20, 2026 12:07pm | Jul 20, 2026 12:26pm | Jul 20, 2026 12:27pm | Jul 20, 2026 12:27pm | Jul 20, 2026 1:10pm | Jul 20, 2026 1:33pm | Jul 20, 2026 1:33pm | BrokenWire |  | Fair | No | Customer stanchion damaged in motor vehicle accident. Customer need to repair stanchion in order to retention low hanging wire.
Non-Outage | J.E.26.07.22504 | C001859633 | Andre Williams | Trelawny | Completed | Load_249132 | Martha Brae - 110 | Jul 20, 2026 11:33am | Jul 20, 2026 11:33am | Jul 20, 2026 1:15pm | Jul 20, 2026 1:43pm | Jul 20, 2026 1:43pm | Jul 20, 2026 1:44pm | Jul 20, 2026 1:45pm | Jul 20, 2026 1:45pm | Fire |  | Fair | No | Unable to locate phone not answering
Outage | J.E.26.07.22488 | C001859632 | Denton Williams | Portland | Completed | Load_268231 | Port Antonio - 410 | Jul 20, 2026 11:32am | Jul 20, 2026 11:33am | Jul 20, 2026 12:25pm | Jul 20, 2026 12:25pm | Jul 20, 2026 12:25pm | Jul 20, 2026 12:25pm | Jul 20, 2026 12:27pm | Jul 20, 2026 12:27pm |  | Y | Fair | No | Remove tree and replace two junction fuses.
Non-Outage | J.E.26.07.22386 | C001859621 | Andrae Dawkins | St.James | Completed | Load_257601 | Bogue - 610 | Jul 20, 2026 11:27am | Jul 20, 2026 11:32am | Jul 20, 2026 12:30pm | Jul 20, 2026 12:30pm | Jul 20, 2026 1:06pm | Jul 20, 2026 2:18pm | Jul 20, 2026 2:26pm | Jul 20, 2026 2:26pm |  |  | Rains | No | Found customer single phasing due to slack connection at pothead clean and remade joints used one pg clamp voltage found 115/96/227voltage left 114/113/228
Non-Outage | J.E.26.07.22497 | C001859613 | Ryan Richards | Manchester | Completed | Load_238957 | Porus - 310 | Jul 20, 2026 11:24am | Jul 20, 2026 11:24am | Jul 20, 2026 11:29am | Jul 20, 2026 11:29am | Jul 20, 2026 11:30am | Jul 20, 2026 1:19pm | Jul 20, 2026 1:19pm | Jul 20, 2026 1:19pm |  |  | Fair | No | Burn drop lead found in closed bank of 100 transformers replaced 5ft#2/0 copper 6 one bolt clamps the the phases where also clean
Outage | J.E.26.07.22467 | C001859612 | Andre Williams | Trelawny | Completed | Load_252729 | Martha Brae - 210 | Jul 20, 2026 11:24am | Jul 20, 2026 11:24am | Jul 20, 2026 12:03pm | Jul 20, 2026 12:15pm | Jul 20, 2026 12:15pm | Jul 20, 2026 12:15pm | Jul 20, 2026 12:17pm | Jul 20, 2026 12:17pm |  |  | Fair | No | Outage report is for Noel Holmes hospital in lucea reffer to Hanover emergency
Outage | J.E.26.07.22474 | C001859611 | Floyd Taylor | Trelawny | Completed | Load_239628 | Greenwood - 110 | Jul 20, 2026 11:23am | Jul 20, 2026 11:25am | Jul 20, 2026 12:17pm | Jul 20, 2026 12:17pm | Jul 20, 2026 2:53pm | Jul 20, 2026 7:14pm | Jul 20, 2026 7:16pm | Jul 20, 2026 7:16pm |  |  | Fair | No | Replace 100ft of #6 wire using 3pg clamps and 3 penunion, voltage readings left 114,117,231.
Outage | J.E.26.07.22495 | C001859610 | Fitzroy Turner | KSAS | Completed | Load_290055 | Hunts Bay - 810 | Jul 20, 2026 11:23am | Jul 20, 2026 11:23am | Jul 20, 2026 11:53am | Jul 20, 2026 11:53am | Jul 20, 2026 12:19pm | Jul 20, 2026 12:20pm | Jul 20, 2026 12:20pm | Jul 20, 2026 12:20pm |  |  | Fair | No | Defective hexing box burnt up cause by illegal connections
Outage | J.E.26.07.22491 | C001859602 | Shamour Haughton | St.James | Completed | Load_241675 | Bogue - 310 | Jul 20, 2026 11:19am | Jul 20, 2026 4:36pm | Jul 20, 2026 5:35pm | Jul 20, 2026 5:35pm | Jul 20, 2026 5:35pm | Jul 20, 2026 5:35pm | Jul 20, 2026 5:39pm | Jul 20, 2026 5:39pm |  |  | Fair | No | Unable to locate customer, call number keeps going voicemail, needs better direction
Outage | J.E.26.07.22492 | C001859601 | Romeo Brissett | St.James | Completed | Load_302188 | Bogue - 610 | Jul 20, 2026 11:19am | Jul 20, 2026 11:22am | Jul 20, 2026 1:59pm | Jul 20, 2026 1:59pm | Jul 20, 2026 3:05pm | Jul 20, 2026 3:24pm | Jul 20, 2026 3:33pm | Jul 20, 2026 3:33pm |  |  | Rains | No | Unable to locate customer phone ring to voicemail, directions unclear.
Outage | J.E.26.07.22482 | C001859588 | Daniel Francis | St.Ann | Completed | Load_269325 | Upper White River - 110 | Jul 20, 2026 11:07am | Jul 20, 2026 3:07pm | Jul 20, 2026 7:24pm | Jul 20, 2026 7:25pm | Jul 20, 2026 9:19pm | Jul 20, 2026 10:37pm | Jul 20, 2026 10:41pm | Jul 20, 2026 10:41pm | Fire |  | Fair | No | Remade all 3 joints for transformer drop leads also 3 service wire
Outage | J.E.26.07.22423 | C001859582 | Nickolas Rodriques | Portmore | Completed | Load_251574 | Naggo Head - 610 | Jul 20, 2026 11:03am | Jul 20, 2026 11:03am | Jul 20, 2026 1:03pm | Jul 20, 2026 1:03pm | Jul 20, 2026 1:49pm | Jul 20, 2026 2:33pm | Jul 20, 2026 2:33pm | Jul 20, 2026 2:33pm |  |  | Fair | No | Checked and found a 10 amp junction fuse blown. Patrol and found nothing on line. Repaired by replacing the fuse after completing patrol.
Outage | J.E.26.07.22401 | C001859574 | Edward Royal | KSAS | Completed | Load_267104 | Greenwich - 710 | Jul 20, 2026 11:00am | Jul 20, 2026 11:00am | Jul 20, 2026 1:07pm | Jul 20, 2026 1:07pm | Jul 20, 2026 1:07pm | Jul 20, 2026 1:07pm | Jul 20, 2026 1:07pm | Jul 20, 2026 1:07pm |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.07.22477 | C001859575 | Kenroy Dale | Manchester | Completed | Load_270008 | Kendal - 210 | Jul 20, 2026 11:00am | Jul 20, 2026 3:35pm | Jul 20, 2026 6:53pm | Jul 20, 2026 6:53pm | Jul 20, 2026 7:41pm | Jul 20, 2026 8:05pm | Jul 20, 2026 8:07pm | Jul 20, 2026 8:07pm |  |  | Fair | No | Blown 5 amp fuse found for 50 kva transformer in banker 2, blown fuse was replaced and area no with supply
Outage | J.E.26.07.22476 | C001859573 | Richard Samuda | Manchester | Completed | Load_251837 | Spur Tree - 310 | Jul 20, 2026 10:59am | Jul 20, 2026 3:06pm | Jul 20, 2026 3:45pm | Jul 20, 2026 3:45pm | Jul 20, 2026 4:23pm | Jul 20, 2026 5:25pm | Jul 20, 2026 5:25pm | Jul 20, 2026 5:25pm |  |  | Fair | No | Customer is disconnected for bad death
Outage | J.E.26.07.22463 | C001859572 | Milton Charlton | KSAN | Completed | Load_246577 | Hope - 410 | Jul 20, 2026 10:56am | Jul 20, 2026 10:57am | Jul 20, 2026 11:14am | Jul 20, 2026 12:04pm | Jul 20, 2026 12:23pm | Jul 20, 2026 12:20pm | Jul 20, 2026 12:26pm | Jul 20, 2026 12:26pm |  |  | Fair | No | Found okay upon arrival. Readings at meter socket 117-117236 volts.
Outage | J.E.26.07.22371 | C001859561 | Richard Nicholas | St.Catherine | Completed | Load_251951 | Tredegar - 510 | Jul 20, 2026 10:50am | Jul 20, 2026 10:51am | Jul 20, 2026 1:05pm | Jul 20, 2026 1:05pm | Jul 20, 2026 1:48pm | Jul 20, 2026 2:10pm | Jul 20, 2026 2:11pm | Jul 20, 2026 2:11pm |  |  | Fair | No | Premises found locked
Outage | J.E.26.07.22444 | C001859562 | Raymond Carr | St.Mary | Completed | Load_350137 | Oracabessa - 210 | Jul 20, 2026 10:50am | Jul 20, 2026 10:50am | Jul 20, 2026 1:13pm | Jul 20, 2026 1:13pm | Jul 20, 2026 2:29pm | Jul 20, 2026 2:45pm | Jul 20, 2026 2:31pm | Jul 20, 2026 2:31pm |  |  | Fair | No | No access to rammy system.
Outage | J.E.26.07.22422 | C001859559 | Neville Spencer | Clarendon | Completed | Load_405778 | Parnassus - 310 | Jul 20, 2026 10:48am | Jul 20, 2026 10:49am | Jul 20, 2026 12:42pm | Jul 20, 2026 12:43pm | Jul 20, 2026 12:58pm | Jul 20, 2026 1:47pm | Jul 20, 2026 1:54pm | Jul 20, 2026 1:54pm |  |  | Fair | No | Found main breaker trip voltage reading 231 233 234 412 416 418 advise.
Outage | J.E.26.07.22455 | C001859549 | Marlon Authors | Manchester | Completed | Load_266073 | Spur Tree - 210 | Jul 20, 2026 10:42am | Jul 20, 2026 10:43am | Jul 20, 2026 10:53am | Jul 20, 2026 11:16am | Jul 20, 2026 11:48am | Jul 20, 2026 12:15pm | Jul 20, 2026 12:15pm | Jul 20, 2026 12:15pm |  |  | Fair | No | Patrol and found clear. Replace one blown 10 amp junction fuse no pole #. Restored supply okay
Outage | J.E.26.07.22448 | C001859538 | Collin Robinson | Portland | Completed | Load_351292 | Port Antonio - 410 | Jul 20, 2026 10:38am | Jul 20, 2026 3:04pm | Jul 20, 2026 3:18pm | Jul 20, 2026 3:18pm | Jul 20, 2026 4:11pm | Jul 20, 2026 4:37pm | Jul 20, 2026 4:37pm | Jul 20, 2026 4:37pm |  |  | Fair | No | Clear vine from pole and replace 2 amps fuse.maintenance need follow up to strengthen leaning concrete pole with transformer
Outage | J.E.26.07.22451 | C001859537 | Selvin White | St.Elizabeth | Completed | Load_263142 | Maggotty - 110 | Jul 20, 2026 10:38am | Jul 20, 2026 6:10pm | Jul 20, 2026 6:15pm | Jul 20, 2026 6:29pm | Jul 20, 2026 7:36pm | Jul 20, 2026 7:55pm | Jul 20, 2026 7:55pm | Jul 20, 2026 7:55pm | BrokenWire |  | Fair | No | Splice and retention approximately 10 ft of number six triplex service wire that was damaged during the recent hurricane. Supply restored to the customer with voltage readings left inside meter socket of 223,111,112 volts.
Non-Outage | J.E.26.07.22399 | C001859536 | Edward Royal | KSAS | Completed | Load_267104 | Greenwich - 710 | Jul 20, 2026 10:37am | Jul 20, 2026 10:37am | Jul 20, 2026 11:52am | Jul 20, 2026 11:52am | Jul 20, 2026 12:20pm | Jul 20, 2026 1:07pm | Jul 20, 2026 1:07pm | Jul 20, 2026 1:07pm |  |  | Fair | No | Spliced and reconnected 190 leg using 2 single bolt clamp voltage reading 238 118 119 208
Non-Outage | J.E.26.07.04664 | C001859534 | Edward Royal | KSAS | Completed | Load_268624 | Greenwich - 710 | Jul 20, 2026 10:36am | Jul 20, 2026 10:37am | Jul 20, 2026 11:50am | Jul 20, 2026 11:50am | Jul 20, 2026 11:50am | Jul 20, 2026 11:51am | Jul 20, 2026 11:51am | Jul 20, 2026 11:51am |  |  | Fair | No | Premises found close unable to communicate with customer by phone
Non-Outage | J.E.26.07.17884 | C001859535 | Edward Royal | KSAS | Completed | Load_268624 | Greenwich - 710 | Jul 20, 2026 10:36am | Jul 20, 2026 10:37am | Jul 20, 2026 11:36am | Jul 20, 2026 11:36am | Jul 20, 2026 11:40am | Jul 20, 2026 11:49am | Jul 20, 2026 11:50am | Jul 20, 2026 11:50am |  |  | Fair | No | Premises found close unable to communicate with customer by phone
Non-Outage | J.E.26.07.22396 | C001859530 | Edward Royal | null | Completed | null | null | Jul 20, 2026 10:33am | Jul 20, 2026 10:33am | Jul 20, 2026 2:05pm | Jul 20, 2026 2:05pm | Jul 20, 2026 2:05pm | Jul 20, 2026 2:06pm | Jul 20, 2026 2:06pm | Jul 20, 2026 2:06pm | Fire |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.07.22440 | C001859522 | Ryan Richards | Manchester | Completed | Load_254141 | Spur Tree - 310 | Jul 20, 2026 10:31am | Jul 20, 2026 10:33am | Jul 20, 2026 1:23pm | Jul 20, 2026 1:24pm | Jul 20, 2026 1:55pm | Jul 20, 2026 2:31pm | Jul 20, 2026 2:32pm | Jul 20, 2026 2:32pm |  |  | Fair | No | Blown 3 amp fuse found for 25 kva transformer line patrol nothing found blown fuse replaced and all customers are now with supply
Non-Outage | J.E.26.07.22411 | C001859521 | Neville Spencer | null | Completed | null | null | Jul 20, 2026 10:30am | Jul 20, 2026 10:31am | Jul 20, 2026 12:19pm | Jul 20, 2026 12:19pm | Jul 20, 2026 12:40pm | Jul 20, 2026 12:40pm | Jul 20, 2026 12:42pm | Jul 20, 2026 12:42pm | Fire |  | Fair | No | No fire seen at location .
Outage | J.E.26.07.22438 | C001859520 | Denton Williams | Portland | Completed | Load_252875 | Port Antonio - 410 | Jul 20, 2026 10:29am | Jul 20, 2026 10:29am | Jul 20, 2026 12:28pm | Jul 20, 2026 12:28pm | Jul 20, 2026 2:50pm | Jul 20, 2026 2:51pm | Jul 20, 2026 2:55pm | Jul 20, 2026 2:55pm | TreeContact |  | Fair | No | We are familiar with area and some de-bushing is required.
Outage | J.E.26.07.22417 | C001859514 | Richard Grant | St.Catherine | Completed | Load_245523 | New Michelton - 410 | Jul 20, 2026 10:24am | Jul 20, 2026 10:27am | Jul 20, 2026 10:44am | Jul 20, 2026 10:44am | Jul 20, 2026 11:15am | Jul 20, 2026 12:06pm | Jul 20, 2026 12:06pm | Jul 20, 2026 12:06pm |  |  | Fair | No | Premises found disconnected and account inactive. Customer was advised.
Outage | J.E.26.07.22437 | C001859513 | Richard Samuda | Manchester | Completed | Load_260536 | Spur Tree - 210 | Jul 20, 2026 10:24am | Jul 20, 2026 3:05pm | Jul 20, 2026 6:00pm | Jul 20, 2026 7:26pm | Jul 20, 2026 7:26pm | Jul 20, 2026 8:02pm | Jul 20, 2026 8:02pm | Jul 20, 2026 8:02pm | BrokenWire |  | Fair | No | Splice and reconnect customer service neutral that was broken using 5 ft of #6 service neutral customer back to normal 116/118/234
Outage | J.E.26.07.22414 | C001859489 | Omar King | St.Ann | Completed | Load_256006 | Roaring River - 210 | Jul 20, 2026 10:14am | Jul 20, 2026 10:16am | Jul 20, 2026 10:51am | Jul 20, 2026 1:14pm | Jul 20, 2026 1:56pm | Jul 20, 2026 2:27pm | Jul 20, 2026 2:28pm | Jul 20, 2026 2:28pm |  |  | Fair | No | Found 30 amp trip saver open as been closed and hold customer is now with supply
Non-Outage | J.E.26.07.22391 | C001859486 | Error Coore | Manchester | Completed | Load_255680 | Spur Tree - 310 | Jul 20, 2026 10:11am | Jul 20, 2026 10:17am | Jul 20, 2026 11:48am | Jul 20, 2026 11:48am | Jul 20, 2026 12:05pm | Jul 20, 2026 1:30pm | Jul 20, 2026 1:33pm | Jul 20, 2026 1:33pm |  |  | Fair | No | Open a 25 KVA xformer to remade corroded drop lead also changed corroded jumper using 8 one bolt clamp voltage reading 110/111/221 volts
Outage | J.E.26.07.22301 | C001859470 | Nickolas Rodriques | Portmore | Completed | Load_243287 | Naggo Head - 510 | Jul 20, 2026 10:06am | Jul 20, 2026 10:07am | Jul 20, 2026 2:36pm | Jul 20, 2026 2:36pm | Jul 20, 2026 3:10pm | Jul 20, 2026 3:21pm | Jul 20, 2026 3:30pm | Jul 20, 2026 3:30pm |  |  | Fair | No | Found premises with electricity. Customer stated that he was having an internal issue that was already resolved by his Electrician.
Outage | J.E.26.07.22309 | C001859472 | Nickolas Rodriques | Portmore | Completed | Load_238728 | Naggo Head - 610 | Jul 20, 2026 10:06am | Jul 20, 2026 10:07am | Jul 20, 2026 10:44am | Jul 20, 2026 10:46am | Jul 20, 2026 11:12am | Jul 20, 2026 11:42am | Jul 20, 2026 11:42am | Jul 20, 2026 11:42am |  |  | Fair | No | Checked and found a 25 amp junction fuse blown caused by defective fuse holder. Repaired by replacing the fuse and a fuse holder after completing patrol.
Outage | J.E.26.07.22412 | C001859471 | Donald Cunningham | Portmore | Completed | Load_576173 | Naggo Head - 510 | Jul 20, 2026 10:06am | Jul 20, 2026 3:25pm | Jul 20, 2026 7:23pm | Jul 20, 2026 7:23pm | Jul 20, 2026 7:58pm | Jul 20, 2026 7:58pm | Jul 20, 2026 8:01pm | Jul 20, 2026 8:01pm |  |  | Fair | No | Rami system refer to mr box need to check
Outage | J.E.26.07.22403 | C001859460 | Romeo Brissett | St.James | Completed | Load_265202 | Bogue - 610 | Jul 20, 2026 10:05am | Jul 20, 2026 10:06am | Jul 20, 2026 11:15am | Jul 20, 2026 11:15am | Jul 20, 2026 12:59pm | Jul 20, 2026 1:58pm | Jul 20, 2026 1:59pm | Jul 20, 2026 1:59pm |  |  | Fair | No | Cut and removed bamboo, replaced (1)20amps junction fuse.
Outage | J.E.26.07.22400 | C001859436 | Omar King | St.Ann | Completed | Load_255731 | Roaring River - 410 | Jul 20, 2026 9:49am | Jul 20, 2026 9:49am | Jul 20, 2026 10:00am | Jul 20, 2026 10:00am | Jul 20, 2026 10:49am | Jul 20, 2026 10:50am | Jul 20, 2026 10:50am | Jul 20, 2026 10:50am |  |  | Fair | No | Problem as been resolved
Outage | J.E.26.07.22387 | C001859421 | Omar King | St.Ann | Completed | Load_319640 | Roaring River - 210 | Jul 20, 2026 9:41am | Jul 20, 2026 9:41am | Jul 20, 2026 10:51am | Jul 20, 2026 10:51am | Jul 20, 2026 11:52am | Jul 20, 2026 1:14pm | Jul 20, 2026 1:14pm | Jul 20, 2026 1:14pm |  |  | Fair | No | Problem as been resolved with the help of customer service
Outage | J.E.26.07.22384 | C001859420 | Edward Royal | KSAS | Completed | Load_258668 | Greenwich - 710 | Jul 20, 2026 9:37am | Jul 20, 2026 9:41am | Jul 20, 2026 3:13pm | Jul 20, 2026 3:13pm | Jul 20, 2026 3:14pm | Jul 20, 2026 3:23pm | Jul 20, 2026 3:23pm | Jul 20, 2026 3:23pm |  |  | Fair | No | Meter not responding meter need to check reffered to field service
Non-Outage | J.E.26.07.22303 | C001859415 | Kaydon Taylor | KSAN | Completed | Load_265507 | Washington Blvd - 810 | Jul 20, 2026 9:35am | Jul 20, 2026 9:37am | Jul 20, 2026 10:45am | Jul 20, 2026 10:53am | Jul 20, 2026 11:18am | Jul 20, 2026 2:22pm | Jul 20, 2026 2:22pm | Jul 20, 2026 2:22pm |  |  | Fair | No | Isolate 50 kva transformer. 7 clamps at transformer pole. V114 115 233
Non-Outage | J.E.26.07.22381 | C001859416 | Kaydon Taylor | KSAN | Completed | Load_256268 | Washington Blvd - 810 | Jul 20, 2026 9:35am | Jul 20, 2026 9:37am | Jul 20, 2026 2:51pm | Jul 20, 2026 2:51pm | Jul 20, 2026 2:51pm | Jul 20, 2026 2:51pm | Jul 20, 2026 2:52pm | Jul 20, 2026 2:52pm |  |  | Fair | No | Found okay
Outage | J.E.26.07.22377 | C001859413 | Christopher Edwards | KSAN | Completed | Load_578934 | Constant Spring - 410 | Jul 20, 2026 9:33am | Jul 20, 2026 9:34am | Jul 20, 2026 11:16am | Jul 20, 2026 1:52pm | Jul 20, 2026 1:52pm | Jul 20, 2026 2:12pm | Jul 20, 2026 2:12pm | Jul 20, 2026 2:12pm |  |  | Fair | No | Isolate bank of 3 transformersTo remake burnt off 2/0 twisted phase joint Using (1) one bolt clamps Voltage:119,120,240v
Non-Outage | J.E.26.07.22375 | C001859411 | Shamour Haughton | St.James | Completed | Load_269651 | Bogue - 310 | Jul 20, 2026 9:31am | Jul 20, 2026 7:04pm | Jul 20, 2026 8:43pm | Jul 20, 2026 8:43pm | Jul 20, 2026 8:57pm | Jul 20, 2026 8:58pm | Jul 20, 2026 9:05pm | Jul 20, 2026 9:05pm |  |  | Fair | No | Customer number went voicemail after several calls, directions needed
Non-Outage | J.E.26.07.22383 | C001859412 | Kaydon Taylor | KSAS | Completed | Load_247730 | Duhaney - 310 | Jul 20, 2026 9:31am | Jul 20, 2026 9:31am | Jul 20, 2026 10:45am | Jul 20, 2026 10:50am | Jul 20, 2026 10:50am | Jul 20, 2026 10:50am | Jul 20, 2026 10:50am | Jul 20, 2026 10:50am |  |  | Fair | No | Incorrect procedure
Outage | J.E.26.07.22326 | C001859406 | Denton Williams | Portland | Completed | Load_353118 | Port Antonio - 410 | Jul 20, 2026 9:31am | Jul 20, 2026 9:31am | Jul 20, 2026 9:49am | Jul 20, 2026 9:49am | Jul 20, 2026 11:44am | Jul 20, 2026 12:22pm | Jul 20, 2026 12:25pm | Jul 20, 2026 12:25pm |  | Y | Fair | No | Remove bamboos from power line and replace two junction fuses 10amp and a 15 amp.
Outage | J.E.26.07.22360 | C001859403 | Gregory Grossett | Portland | Completed | Load_349991 | Port Antonio - 310 | Jul 20, 2026 9:30am | Jul 20, 2026 3:04pm | Jul 20, 2026 3:19pm | Jul 20, 2026 3:19pm | Jul 20, 2026 4:21pm | Jul 20, 2026 4:55pm | Jul 20, 2026 5:09pm | Jul 20, 2026 5:09pm |  |  | Fair | No | 220 service phase broken in midair repair and ok material use 2 one bolt clamps 5ft of service phase.voltage readings before repair 119v voltage reading after repair 119/120/240 on both phase.
Outage | J.E.26.07.22376 | C001859402 | Tajay Bernard | Hanover | Completed | Load_259360 | Orange Bay - 310 | Jul 20, 2026 9:29am | Jul 20, 2026 9:29am | Jul 20, 2026 9:39am | Jul 20, 2026 9:42am | Jul 20, 2026 10:46am | Jul 20, 2026 11:00am | Jul 20, 2026 11:01am | Jul 20, 2026 11:01am |  |  | Fair | No | Premises check and found okay found customer meter single phasing, refer to field service Voltage reading 116/117/232
Non-Outage | J.E.26.06.38269 | C001859394 | Damion Reid | Manchester | Completed | Load_248941 | Kendal - 210 | Jul 20, 2026 9:22am | Jul 20, 2026 9:23am | Jul 20, 2026 10:21am | Jul 20, 2026 10:21am | Jul 20, 2026 11:23am | Jul 20, 2026 1:59pm | Jul 20, 2026 2:03pm | Jul 20, 2026 2:03pm |  |  | Fair | No | Remade corroded neutral at secondary jumper using one 1 bolt clamp voltage reading at meter socket after correction phase to neutral 108v-111v across phase 222v
Non-Outage | J.E.26.07.22364 | C001859383 | Fitzroy Turner | KSAS | Completed | Load_1002855 | Rockfort - 210 | Jul 20, 2026 9:15am | Jul 20, 2026 9:16am | Jul 20, 2026 9:49am | Jul 20, 2026 10:07am | Jul 20, 2026 10:07am | Jul 20, 2026 10:10am | Jul 20, 2026 10:11am | Jul 20, 2026 10:11am | Fire |  | Fair | No | Defective hexing box caught fire cause by illegal connections
Non-Outage | J.E.26.07.22362 | C001859379 | Fitzroy Turner | KSAS | Completed | Load_241056 | Hunts Bay - 710 | Jul 20, 2026 9:12am | Jul 20, 2026 9:13am | Jul 20, 2026 9:19am | Jul 20, 2026 9:19am | Jul 20, 2026 9:49am | Jul 20, 2026 10:02am | Jul 20, 2026 10:06am | Jul 20, 2026 10:06am | Fire |  | Fair | No | Found hexing box and 25 kva transformer box burnt up cause by illegal connections
Non-Outage | J.E.26.07.16117 | C001859368 | Andrae Dawkins | St.James | Completed | Load_573595 | Bogue - 610 | Jul 20, 2026 9:09am | Jul 20, 2026 9:09am | Jul 20, 2026 9:37am | Jul 20, 2026 9:37am | Jul 20, 2026 10:07am | Jul 20, 2026 9:57am | Jul 20, 2026 10:08am | Jul 20, 2026 10:08am |  |  | Fair | No | Check and found ok customer said that the problem was already resolved
Non-Outage | J.E.26.07.22282 | C001859367 | Andrae Dawkins | St.James | Completed | Load_267492 | Bogue - 610 | Jul 20, 2026 9:09am | Jul 20, 2026 9:09am | Jul 20, 2026 9:37am | Jul 20, 2026 10:09am | Jul 20, 2026 11:33am | Jul 20, 2026 12:01pm | Jul 20, 2026 12:24pm | Jul 20, 2026 12:24pm |  |  | Fair | No | Found multiple customers experiencing low voltage 10 pole span from transformer voltage found at customers meter 105/92/198 voltage found found at transformer 112/115/227 refer back to emergency crew
Non-Outage | J.E.26.07.22341 | C001859366 | Javid Vernon | null | Completed | null | null | Jul 20, 2026 9:08am | Jul 20, 2026 9:08am | Jul 20, 2026 12:33pm | Jul 20, 2026 12:34pm | Jul 20, 2026 12:47pm | Jul 20, 2026 1:33pm | Jul 20, 2026 1:34pm | Jul 20, 2026 1:34pm | BrokenWire |  | Fair | No | Splice and retention customer service wire use 30ft #6 triplex wire and three clamps voltage reading 113/117/236
Non-Outage | J.E.26.07.14466 | C001859363 | Junior Scarlett | St.James | Completed | Load_251906 | Bogue - 310 | Jul 20, 2026 9:07am | Jul 20, 2026 9:07am | Jul 20, 2026 9:30am | Jul 20, 2026 11:27am | Jul 20, 2026 12:03pm | Jul 20, 2026 12:43pm | Jul 20, 2026 12:43pm | Jul 20, 2026 12:43pm |  |  | Fair | No | Corrosion at poleInstall two clampVoltage found 115v 0.11v 115vVoltage leave 115v 115v 230vJob completed
Non-Outage | J.E.26.07.14532 | C001859362 | Junior Scarlett | St.James | Completed | Load_556943 | Bogue - 310 | Jul 20, 2026 9:07am | Jul 20, 2026 9:07am | Jul 20, 2026 9:30am | Jul 20, 2026 1:54pm | Jul 20, 2026 1:54pm | Jul 20, 2026 1:54pm | Jul 20, 2026 1:55pm | Jul 20, 2026 1:55pm |  |  | Flood | No | Check and found okVoltage 115v 115v 230v
Non-Outage | J.E.26.07.14962 | C001859361 | Junior Scarlett | St.James | Completed | Load_251906 | Bogue - 310 | Jul 20, 2026 9:07am | Jul 20, 2026 9:07am | Jul 20, 2026 9:30am | Jul 20, 2026 10:25am | Jul 20, 2026 10:43am | Jul 20, 2026 11:16am | Jul 20, 2026 11:20am | Jul 20, 2026 11:20am |  |  | Fair | No | Reattach wireTrim tree limbInstall 3 clampVoltage found 115v 0.11v 115vVoltage leave 115v 115v 230vJob completed
Non-Outage | J.E.26.07.15680 | C001859360 | Junior Scarlett | St.James | Completed | Load_249504 | Bogue - 310 | Jul 20, 2026 9:07am | Jul 20, 2026 9:07am | Jul 20, 2026 9:30am | Jul 20, 2026 1:59pm | Jul 20, 2026 2:38pm | Jul 20, 2026 3:22pm | Jul 20, 2026 3:23pm | Jul 20, 2026 3:23pm |  |  | Fair | No | Refer to field service EG system EN# 04518Voltage found 87v 84v 200v
Non-Outage | J.E.26.01.36809 | C001859355 | Junior Scarlett | St.James | Completed | Load_242456 | Bogue - 310 | Jul 20, 2026 9:06am | Jul 20, 2026 9:07am | Jul 20, 2026 9:30am | Jul 21, 2026 8:17am | Jul 21, 2026 8:49am | Jul 21, 2026 9:15am | Jul 21, 2026 9:15am | Jul 21, 2026 9:15am |  |  | Fair | No | Check and found okVoltage found 115v 115v 230v
Non-Outage | J.E.26.07.16200 | C001859358 | Junior Scarlett | St.James | Completed | Load_576009 | Bogue - 310 | Jul 20, 2026 9:06am | Jul 20, 2026 9:07am | Jul 20, 2026 9:30am | Jul 20, 2026 3:42pm | Jul 20, 2026 3:42pm | Jul 20, 2026 3:47pm | Jul 20, 2026 3:48pm | Jul 20, 2026 3:48pm |  |  | Fair | No | Check and found okVoltage found 115v 115v 230v
Non-Outage | J.E.26.07.17307 | C001859359 | Shamour Haughton | St.James | Completed | Load_301747 | Bogue - 310 | Jul 20, 2026 9:06am | Jul 20, 2026 7:05pm | Jul 20, 2026 9:35pm | Jul 20, 2026 9:36pm | Jul 20, 2026 9:36pm | Jul 20, 2026 9:36pm | Jul 20, 2026 9:38pm | Jul 20, 2026 9:38pm |  |  | Fair | No | Customer calling about bill
Non-Outage | J.E.26.01.25282 | C001859343 | Junior Scarlett | St.James | Completed | Load_556785 | Bogue - 310 | Jul 20, 2026 9:05am | Jul 21, 2026 8:22am | Jul 21, 2026 8:49am | Jul 21, 2026 10:37am | Jul 21, 2026 10:37am | Jul 21, 2026 11:23am | Jul 21, 2026 11:22am | Jul 21, 2026 11:22am |  |  | Fair | No | Check and found okVoltage found 115v 115v 230v
Non-Outage | J.E.26.01.26527 | C001859345 | Junior Scarlett | St.James | Completed | Load_268015 | Bogue - 310 | Jul 20, 2026 9:05am | Jul 21, 2026 8:23am | Jul 21, 2026 8:49am | Jul 21, 2026 9:16am | Jul 21, 2026 9:32am | Jul 21, 2026 10:00am | Jul 21, 2026 10:01am | Jul 21, 2026 10:01am |  |  | Fair | No | Install two clampClean corrosion Voltage 115v
Outage | J.E.26.07.22315 | C001859341 | Damion Reid | Manchester | Completed | Load_258481 | Kendal - 210 | Jul 20, 2026 9:02am | Jul 20, 2026 9:02am | Jul 20, 2026 2:47pm | Jul 20, 2026 2:47pm | Jul 20, 2026 3:15pm | Jul 20, 2026 3:27pm | Jul 20, 2026 3:30pm | Jul 20, 2026 3:30pm | BrokenWire |  | Fair | No | Reconnect service wire for 3 wire service that was disconnected for repairs using 80ft of #6 triplex service wire 3 one bolt clamp and 3 pen union
Outage | J.E.26.07.22320 | C001859342 | Richard Samuda | Manchester | Completed | Load_245114 | Spur Tree - 310 | Jul 20, 2026 9:02am | Jul 20, 2026 3:07pm | Jul 20, 2026 3:25pm | Jul 20, 2026 5:25pm | Jul 20, 2026 5:41pm | Jul 20, 2026 6:00pm | Jul 20, 2026 5:59pm | Jul 20, 2026 5:59pm | LeaningPole |  | EarthMovement | No | Remove overhead guy from railing that was broken however guy needs t be replaced pole leaning forward and pole foot is also 35 feet DVpole refer call to
Non-Outage | J.E.26.07.22166 | C001859335 | Kaydon Taylor | null | Completed | null | null | Jul 20, 2026 8:59am | Jul 20, 2026 8:59am | Jul 20, 2026 9:05am | Jul 20, 2026 9:10am | Jul 20, 2026 9:10am | Jul 20, 2026 9:12am | Jul 20, 2026 9:12am | Jul 20, 2026 9:12am |  |  | Fair | No | Customer is reporting about her streetlight that’s not working since last week.
Outage | J.E.26.07.22312 | C001859326 | Milton Charlton | KSAS | Completed | Load_264050 | Up Park Camp - 410 | Jul 20, 2026 8:54am | Jul 20, 2026 8:55am | Jul 20, 2026 9:39am | Jul 20, 2026 9:39am | Jul 20, 2026 11:04am | Jul 20, 2026 10:35am | Jul 20, 2026 11:09am | Jul 20, 2026 11:09am |  |  | Fair | No | Refused and reclosed three 50 kva transformer switches at pole#0211250 using three 5 amps fuses and reclosed transformer switches.
Outage | J.E.26.07.22318 | C001859325 | Swon Miller | St.James | Completed | Load_557700 | Bogue - 410 | Jul 20, 2026 8:52am | Jul 20, 2026 9:01am | Jul 20, 2026 10:53am | Jul 20, 2026 10:53am | Jul 20, 2026 11:20am | Jul 14, 2026 12:40am | Jul 20, 2026 12:47pm | Jul 20, 2026 12:47pm |  |  | Fair | No | Check and found customer pothead burn due to slack connection open bank of 3 ,100 kva transformer clean and remake joints use 4pg to carry out repairs close up bank of 3 1000 kva transformer’s voltage found 117/1117 voltage left 117/117/206
Non-Outage | J.E.26.07.22317 | C001859324 | Dwayne Samuels | Trelawny | Completed | Load_267437 | Greenwood - 110 | Jul 20, 2026 8:51am | Jul 20, 2026 3:28pm | Jul 20, 2026 4:26pm | Jul 20, 2026 4:26pm | Jul 20, 2026 6:03pm | Jul 20, 2026 6:56pm | Jul 20, 2026 7:00pm | Jul 20, 2026 7:00pm |  |  | Fair | No | Defective meter refer to field service voltage found at pothead is 113v 116v 228v
Non-Outage | J.E.26.07.21734 | C001859308 | Floyd Taylor | null | Completed | null | null | Jul 20, 2026 8:50am | Jul 20, 2026 8:50am | Jul 20, 2026 10:10am | Jul 20, 2026 10:10am | Jul 20, 2026 10:58am | Jul 20, 2026 10:59am | Jul 20, 2026 10:59am | Jul 20, 2026 10:59am | Fire |  | Fair | No | No fire was found
Non-Outage | J.E.26.07.22284 | C001859306 | Richard Grant | null | Completed | null | null | Jul 20, 2026 8:47am | Jul 20, 2026 8:48am | Jul 20, 2026 10:20am | Jul 20, 2026 10:20am | Jul 20, 2026 10:42am | Jul 20, 2026 10:44am | Jul 20, 2026 10:44am | Jul 20, 2026 10:44am | BrokenWire |  | Fair | No | Area visited, no broken wire seen. Wrong contact number given. Area left okay
Non-Outage | J.E.26.07.21255 | C001859290 | Rochaine Hussey | KSAN | Completed | Load_264383 | Constant Spring - 210 | Jul 20, 2026 8:37am | Jul 20, 2026 8:37am | Jul 20, 2026 2:04pm | Jul 20, 2026 2:05pm | Jul 20, 2026 2:05pm | Jul 20, 2026 2:47pm | Jul 20, 2026 2:47pm | Jul 20, 2026 2:47pm |  |  | Fair | No | Transformer was isolated ant top downIssue resolved 119/119/238v
Non-Outage | J.E.26.07.21475 | C001859289 | Rochaine Hussey | KSAN | Completed | Load_264841 | Constant Spring - 410 | Jul 20, 2026 8:36am | Jul 20, 2026 8:36am | Jul 20, 2026 9:18am | Jul 20, 2026 10:57am | Jul 20, 2026 11:04am | Jul 20, 2026 11:11am | Jul 20, 2026 11:11am | Jul 20, 2026 11:11am |  |  | Fair | No | Customer meter burnt which causes customer to experience single phasing 117/117/235vReferring to field service
Non-Outage | J.E.26.07.22123 | C001859286 | Rochaine Hussey | KSAN | Completed | Load_245773 | Constant Spring - 410 | Jul 20, 2026 8:36am | Jul 20, 2026 8:36am | Jul 20, 2026 11:57am | Jul 20, 2026 11:57am | Jul 20, 2026 12:01pm | Jul 20, 2026 12:42pm | Jul 20, 2026 12:43pm | Jul 20, 2026 12:43pm |  |  | Fair | No | Corrosion on pothead 2 clamp usedIssue resolved 120/121/241v
Non-Outage | J.E.26.07.18186 | C001859283 | Fredrick Hamilton | KSAN | Completed | Load_248819 | Washington Blvd - 310 | Jul 20, 2026 8:34am | Jul 20, 2026 8:34am | Jul 20, 2026 8:46am | Jul 20, 2026 12:26pm | Jul 20, 2026 12:39pm | Jul 20, 2026 1:03pm | Jul 20, 2026 1:03pm | Jul 20, 2026 1:03pm |  |  | Fair | No | Corrosion detected at pothead same was corrected 3 penunion used 228v/120v/108v obtained
Non-Outage | J.E.26.07.18638 | C001859282 | Fredrick Hamilton | KSAN | Completed | Load_262237 | Washington Blvd - 310 | Jul 20, 2026 8:34am | Jul 20, 2026 8:34am | Jul 20, 2026 8:46am | Jul 20, 2026 1:56pm | Jul 20, 2026 1:56pm | Jul 20, 2026 1:57pm | Jul 20, 2026 1:58pm | Jul 20, 2026 1:58pm |  |  | Fair | No | 214v/108v/104v obtained low voltage affecting multiple customers Please have emergency check transformer
Non-Outage | J.E.26.07.20000 | C001859281 | Fredrick Hamilton | KSAN | Completed | Load_242335 | Washington Blvd - 310 | Jul 20, 2026 8:34am | Jul 20, 2026 8:34am | Jul 20, 2026 8:46am | Jul 20, 2026 11:52am | Jul 20, 2026 12:02pm | Jul 20, 2026 12:25pm | Jul 20, 2026 12:25pm | Jul 20, 2026 12:25pm |  |  | Fair | No | Burnt wires detected in customer meter socket customer advised no JPS defect detected
Non-Outage | J.E.26.07.20083 | C001859279 | Fredrick Hamilton | KSAN | Completed | Load_262237 | Washington Blvd - 310 | Jul 20, 2026 8:34am | Jul 20, 2026 8:34am | Jul 20, 2026 8:46am | Jul 20, 2026 1:35pm | Jul 20, 2026 1:43pm | Jul 20, 2026 1:55pm | Jul 20, 2026 1:55pm | Jul 20, 2026 1:55pm |  |  | Fair | No | 213v/106v/104v obtained low voltage detected affecting multiple customers Please have emergency check transformer
Non-Outage | J.E.26.07.21689 | C001859280 | Fredrick Hamilton | KSAN | Completed | Load_412891 | Washington Blvd - 310 | Jul 20, 2026 8:34am | Jul 20, 2026 8:34am | Jul 20, 2026 8:46am | Jul 20, 2026 11:13am | Jul 20, 2026 11:21am | Jul 20, 2026 11:35am | Jul 20, 2026 11:35am | Jul 20, 2026 11:35am |  |  | Fair | No | Please assign to field service emergency CT 3 phase supply
Non-Outage | J.E.26.07.21738 | C001859278 | Fredrick Hamilton | KSAN | Completed | Load_244711 | Washington Blvd - 710 | Jul 20, 2026 8:34am | Jul 20, 2026 8:34am | Jul 20, 2026 8:46am | Jul 20, 2026 10:53am | Jul 20, 2026 11:08am | Jul 20, 2026 11:12am | Jul 20, 2026 11:12am | Jul 20, 2026 11:12am |  |  | Fair | No | Premises found ok no tree contact seen on the JPS supply
Non-Outage | J.E.26.07.22243 | C001859277 | Fredrick Hamilton | KSAN | Completed | Load_250296 | Washington Blvd - 310 | Jul 20, 2026 8:33am | Jul 20, 2026 8:34am | Jul 20, 2026 8:46am | Jul 20, 2026 1:05pm | Jul 20, 2026 1:09pm | Jul 20, 2026 1:34pm | Jul 20, 2026 1:34pm | Jul 20, 2026 1:34pm |  |  | Fair | No | Open neutral corrected at pole 232v/119v/118v obtained Customer supply restored fully
Non-Outage | J.E.26.07.17845 | C001859274 | Rusean Allen | KSAS | Completed | Load_239878 | Cane River - 410 | Jul 20, 2026 8:31am | Jul 20, 2026 8:31am | Jul 20, 2026 11:31am | Jul 20, 2026 11:31am | Jul 20, 2026 12:26pm | Jul 20, 2026 12:27pm | Jul 20, 2026 12:27pm | Jul 20, 2026 12:27pm |  |  | Fair | No | Found okay voltage readings 113v
Non-Outage | J.E.26.07.19839 | C001859269 | Rusean Allen | KSAS | Completed | Load_249081 | Cane River - 310 | Jul 20, 2026 8:30am | Jul 20, 2026 8:31am | Jul 20, 2026 10:48am | Jul 20, 2026 10:48am | Jul 20, 2026 11:26am | Jul 20, 2026 11:27am | Jul 20, 2026 11:27am | Jul 20, 2026 11:27am |  |  | Fair | No | Customer cell phone ring with out answering
Non-Outage | J.E.26.07.20403 | C001859271 | Rusean Allen | KSAS | Completed | Load_253227 | Cane River - 610 | Jul 20, 2026 8:30am | Jul 20, 2026 8:31am | Jul 20, 2026 12:29pm | Jul 20, 2026 12:29pm | Jul 20, 2026 12:44pm | Jul 20, 2026 2:24pm | Jul 20, 2026 2:24pm | Jul 20, 2026 2:24pm |  |  | Fair | No | Reconnected wire at pole
Non-Outage | J.E.26.07.21552 | C001859270 | Rusean Allen | KSAS | Completed | Load_244455 | Cane River - 610 | Jul 20, 2026 8:30am | Jul 20, 2026 8:31am | Jul 20, 2026 12:28pm | Jul 20, 2026 12:28pm | Jul 20, 2026 12:28pm | Jul 20, 2026 12:29pm | Jul 20, 2026 12:29pm | Jul 20, 2026 12:29pm |  |  | Fair | No | Voltage reading 114v 115v 234v
Outage | J.E.26.07.22292 | C001859267 | Marlon Authors | Manchester | Completed | Load_252348 | Spur Tree - 210 | Jul 20, 2026 8:29am | Jul 20, 2026 8:30am | Jul 20, 2026 10:32am | Jul 20, 2026 10:32am | Jul 20, 2026 10:32am | Jul 20, 2026 10:49am | Jul 20, 2026 10:49am | Jul 20, 2026 10:49am |  |  | Fair | No | Supply checked and found one, 100 kva transformer burnt and approximately 200 feet or one pole span of 2/0 twisted conductor also damaged. Please refer same to the maintenance department for replacement . A section of the town is without power
Outage | J.E.26.07.22287 | C001859257 | Nickolas Rodriques | Portmore | Completed | Load_570097 | Naggo Head - 610 | Jul 20, 2026 8:17am | Jul 20, 2026 8:19am | Jul 20, 2026 8:39am | Jul 20, 2026 8:40am | Jul 20, 2026 9:19am | Jul 20, 2026 10:15am | Jul 20, 2026 10:22am | Jul 20, 2026 10:22am |  |  | Fair | No | Checked and found two 30 amp and a 15 amp junction fuse blown. Patrol and found nothing on line. Repaired by replacing the fuses after completing patrol.
Non-Outage | J.E.26.07.21664 | C001859250 | Roemello Brown | Trelawny | Completed | Load_257206 | Martha Brae - 210 | Jul 20, 2026 8:13am | Jul 20, 2026 8:51am | Jul 20, 2026 9:41am | Jul 20, 2026 9:41am | Jul 20, 2026 10:33am | Jul 20, 2026 10:33am | Jul 20, 2026 10:39am | Jul 20, 2026 10:39am |  |  | Fair | No | Premises found working okay Voltage found 125/125/251Voltage leave 125/125/251
Non-Outage | J.E.26.07.21762 | C001859251 | Roemello Brown | null | Completed | null | null | Jul 20, 2026 8:13am | Jul 20, 2026 8:51am | Jul 20, 2026 1:42pm | Jul 20, 2026 1:42pm | Jul 20, 2026 2:09pm | Jul 20, 2026 2:09pm | Jul 20, 2026 2:14pm | Jul 20, 2026 2:14pm |  |  | Fair | No | Premises check premises found working okay Voltage found 115/116/231Voltage leave 115/116/231
Non-Outage | J.E.26.07.22092 | C001859248 | Roemello Brown | Trelawny | Completed | Load_264646 | Duncans - 210 | Jul 20, 2026 8:13am | Jul 20, 2026 8:51am | Jul 20, 2026 12:03pm | Jul 20, 2026 12:04pm | Jul 20, 2026 1:05pm | Jul 20, 2026 1:05pm | Jul 20, 2026 1:26pm | Jul 20, 2026 1:26pm |  |  | Fair | No | Needs emergency team to assist secondary line fluctuating one leg given 104volts an then 100Voltage found 104/117/221Voltage leave 104/117/221
Non-Outage | J.E.26.07.22126 | C001859249 | Floyd Taylor | Trelawny | Completed | Load_292361 | Greenwood - 210 | Jul 20, 2026 8:13am | Jul 20, 2026 8:13am | Jul 20, 2026 8:31am | Jul 20, 2026 9:03am | Jul 20, 2026 9:33am | Jul 20, 2026 10:09am | Jul 20, 2026 10:10am | Jul 20, 2026 10:10am | BangingWires |  | Fair | No | No fire was found issues only happened in the ni when residents puts on the illegal connection
Non-Outage | J.E.26.07.22141 | C001859247 | Roemello Brown | Trelawny | Completed | Load_243206 | Duncans - 210 | Jul 20, 2026 8:13am | Jul 20, 2026 8:51am | Jul 20, 2026 10:58am | Jul 20, 2026 10:58am | Jul 20, 2026 11:39am | Jul 20, 2026 11:40am | Jul 20, 2026 12:00pm | Jul 20, 2026 12:00pm |  |  | Fair | No | Premises check premises found working okay Voltage found 117/117/235Voltage leave 117/117/235
Non-Outage | J.E.26.07.22143 | C001859246 | Roemello Brown | Trelawny | Completed | Load_257511 | Martha Brae - 210 | Jul 20, 2026 8:13am | Jul 20, 2026 8:51am | Jul 20, 2026 9:37am | Jul 20, 2026 10:41am | Jul 20, 2026 10:41am | Jul 20, 2026 10:41am | Jul 20, 2026 10:43am | Jul 20, 2026 10:43am |  |  | Fair | No | Premises found working okay Voltage found 125/125/250Voltage leave 125/125/250
Non-Outage | J.E.26.07.15748 | C001859239 | Tyrese Williams | St.Ann | Completed | Load_239552 | Cardiff Hall - 210 | Jul 20, 2026 8:10am | Jul 20, 2026 8:10am | Jul 20, 2026 1:00pm | Jul 20, 2026 3:58pm | Jul 20, 2026 3:58pm | Jul 20, 2026 4:00pm | Jul 20, 2026 4:01pm | Jul 20, 2026 4:01pm |  |  | Fair | No | Premises found ok customer said everything is ok
Non-Outage | J.E.26.07.18459 | C001859240 | Tyrese Williams | St.Ann | Completed | Load_244118 | Cardiff Hall - 310 | Jul 20, 2026 8:10am | Jul 20, 2026 8:10am | Jul 20, 2026 8:30am | Jul 20, 2026 10:15am | Jul 20, 2026 10:15am | Jul 20, 2026 10:30am | Jul 20, 2026 10:31am | Jul 20, 2026 10:31am |  |  | Fair | No | Repair secondary neutral jumper voltage left 117/116/233
Non-Outage | J.E.26.07.18668 | C001859241 | Tyrese Williams | St.Ann | Completed | Load_239011 | Cardiff Hall - 210 | Jul 20, 2026 8:10am | Jul 20, 2026 8:10am | Jul 20, 2026 8:37am | Jul 20, 2026 8:37am | Jul 20, 2026 8:37am | Jul 20, 2026 8:38am | Jul 20, 2026 8:38am | Jul 20, 2026 8:38am |  |  | Fair | No | Premises found ok customer made a complaint about high billing
Non-Outage | J.E.26.07.13145 | C001859235 | Tyrese Williams | St.Ann | Completed | Load_246384 | Cardiff Hall - 210 | Jul 20, 2026 8:07am | Jul 20, 2026 8:07am | Jul 20, 2026 8:22am | Jul 20, 2026 10:37am | Jul 20, 2026 10:37am | Jul 20, 2026 10:38am | Jul 20, 2026 10:38am | Jul 20, 2026 10:38am |  |  | Fair | No | Customer meter is in hexing box
Non-Outage | J.E.26.07.14424 | C001859236 | Tyrese Williams | St.Ann | Completed | Load_246792 | Cardiff Hall - 310 | Jul 20, 2026 8:07am | Jul 20, 2026 8:08am | Jul 20, 2026 10:33am | Jul 20, 2026 2:11pm | Jul 20, 2026 2:11pm | Jul 20, 2026 2:12pm | Jul 20, 2026 2:12pm | Jul 20, 2026 2:12pm |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.07.14558 | C001859237 | Tyrese Williams | St.Ann | Completed | Load_251828 | Cardiff Hall - 210 | Jul 20, 2026 8:07am | Jul 20, 2026 8:08am | Jul 20, 2026 12:59pm | Jul 20, 2026 2:12pm | Jul 20, 2026 3:17pm | Jul 20, 2026 3:54pm | Jul 20, 2026 3:54pm | Jul 20, 2026 3:54pm |  |  | Fair | No | Remove illegal connections off secondary line voltage check 111/112/223
Non-Outage | J.E.26.07.12977 | C001859233 | Tyrese Williams | St.Ann | Completed | Load_239713 | Cardiff Hall - 210 | Jul 20, 2026 8:06am | Jul 20, 2026 8:07am | Jul 20, 2026 10:33am | Jul 20, 2026 12:44pm | Jul 20, 2026 1:19pm | Jul 20, 2026 1:21pm | Jul 20, 2026 1:21pm | Jul 20, 2026 1:21pm |  |  | Fair | No | Premises not found not getting customer on phone
Non-Outage | J.E.26.07.13059 | C001859234 | Tyrese Williams | St.Ann | Completed | Load_265779 | Cardiff Hall - 210 | Jul 20, 2026 8:06am | Jul 20, 2026 8:07am | Jul 20, 2026 10:33am | Jul 20, 2026 1:22pm | Jul 20, 2026 1:55pm | Jul 20, 2026 2:05pm | Jul 20, 2026 2:09pm | Jul 20, 2026 2:09pm |  |  | Fair | No | Premises not found not getting customer on phone
Non-Outage | J.E.26.07.10790 | C001859228 | Tyrese Williams | St.Ann | Completed | Load_243889 | Cardiff Hall - 310 | Jul 20, 2026 8:03am | Jul 20, 2026 8:03am | Jul 20, 2026 8:10am | Jul 20, 2026 11:03am | Jul 20, 2026 11:03am | Jul 20, 2026 12:03pm | Jul 20, 2026 12:03pm | Jul 20, 2026 12:03pm |  |  | Fair | No | Me repair neutral joint at pothead use 1 pg clamp voltage left 112/111/223
Non-Outage | J.E.26.07.12762 | C001859229 | Tyrese Williams | St.Ann | Completed | Load_265779 | Cardiff Hall - 210 | Jul 20, 2026 8:03am | Jul 20, 2026 8:04am | Jul 20, 2026 8:10am | Jul 20, 2026 12:03pm | Jul 20, 2026 12:32pm | Jul 20, 2026 12:43pm | Jul 20, 2026 12:44pm | Jul 20, 2026 12:44pm |  |  | Fair | No | Remade service wire neutral at pole use 1 pg clamp voltage check 114/115/229
Non-Outage | J.E.26.07.21059 | C001859221 | Ryan Richards | Manchester | Completed | Load_1002521 | Kendal - 310 | Jul 20, 2026 8:01am | Jul 20, 2026 8:01am | Jul 20, 2026 9:48am | Jul 20, 2026 9:48am | Jul 20, 2026 10:24am | Jul 20, 2026 10:47am | Jul 20, 2026 10:47am | Jul 20, 2026 10:47am |  |  | Fair | No | Premises found ok voltage 110/112/223 volts
Non-Outage | J.E.26.07.22171 | C001859226 | Neville Spencer | null | Completed | null | null | Jul 20, 2026 8:01am | Jul 20, 2026 8:04am | Jul 20, 2026 8:28am | Jul 20, 2026 8:28am | Jul 20, 2026 9:02am | Jul 20, 2026 9:03am | Jul 20, 2026 9:07am | Jul 20, 2026 9:07am | BrokenWire |  | Fair | No | No broken wire seen at location private line in the LANE.
Non-Outage | J.E.26.07.22193 | C001859227 | Odaine Johnson | null | Completed | null | null | Jul 20, 2026 8:01am | Jul 21, 2026 7:59am | Jul 21, 2026 8:56am | Jul 21, 2026 9:59am | Jul 21, 2026 11:19am | Jul 21, 2026 11:19am | Jul 21, 2026 11:19am | Jul 21, 2026 11:19am | Fire |  | Fair | No | Premises found okay
Outage | J.E.26.07.22200 | C001859218 | Rusean Allen | KSAS | Completed | Load_244455 | Cane River - 610 | Jul 20, 2026 8:01am | Jul 20, 2026 8:01am | Jul 20, 2026 2:24pm | Jul 20, 2026 2:24pm | Jul 20, 2026 2:24pm | Jul 20, 2026 2:25pm | Jul 20, 2026 2:25pm | Jul 20, 2026 2:25pm |  |  | Fair | No | Illegal connections need to remove
Outage | J.E.26.07.22248 | C001859225 | Neville Spencer | Clarendon | Completed | Load_247436 | Parnassus - 210 | Jul 20, 2026 8:01am | Jul 20, 2026 8:01am | Jul 20, 2026 12:02pm | Jul 20, 2026 12:02pm | Jul 20, 2026 12:17pm | Jul 20, 2026 12:17pm | Jul 20, 2026 12:19pm | Jul 20, 2026 12:19pm |  |  | Fair | No | Replace 2 blown 40 amp J/ fuse at pole #0177669 supply restored.
Outage | J.E.26.07.22253 | C001859219 | Fitzroy Turner | KSAS | Completed | Load_1003920 | Hunts Bay - 110 | Jul 20, 2026 8:01am | Jul 20, 2026 8:21am | Jul 20, 2026 10:11am | Jul 20, 2026 10:12am | Jul 20, 2026 10:12am | Jul 20, 2026 11:15am | Jul 20, 2026 11:38am | Jul 20, 2026 11:38am |  |  | Fair | No | Found too 65amps junction fuse blown at the intersection of Marcus Garvey drive and new port Blvd blown cause by 50kva transformer drop leads burnt and transformer panel have drop leads remove and replaced too 65amps supply restored to areas
Outage | J.E.26.07.22270 | C001859223 | Hartley Chin | Clarendon | Completed | Load_568431 | May Pen - 110 | Jul 20, 2026 8:01am | Jul 20, 2026 8:01am | Jul 20, 2026 1:39pm | Jul 20, 2026 1:39pm | Jul 20, 2026 2:30pm | Jul 20, 2026 2:31pm | Jul 20, 2026 2:34pm | Jul 20, 2026 2:34pm |  |  | Fair | No | Premisis found ok. Broken wire was behind meter, internal issue.
Outage | J.E.26.07.22273 | C001859224 | Rusean Allen | KSAS | Completed | Load_269790 | Cane River - 310 | Jul 20, 2026 8:01am | Jul 20, 2026 8:01am | Jul 20, 2026 8:26am | Jul 20, 2026 8:54am | Jul 20, 2026 10:34am | Jul 20, 2026 10:46am | Jul 20, 2026 10:46am | Jul 20, 2026 10:46am |  |  | Fair | No | Found a 20 amps fuse Replace a 20 amps fuse
Outage | J.E.26.07.22274 | C001859220 | Kemark Slue | St.Catherine | Completed | Load_255400 | Twickenham - 210 | Jul 20, 2026 8:01am | Jul 20, 2026 3:50pm | Jul 20, 2026 4:22pm | Jul 20, 2026 4:30pm | Jul 20, 2026 4:35pm | Jul 20, 2026 4:35pm | Jul 20, 2026 4:36pm | Jul 20, 2026 4:36pm |  |  | Fair | No | Site located beside the hatchery in Cumberland
Outage | J.E.26.07.22250 | C001859217 | Fitzroy Turner | KSAS | Completed | Load_261859 | Hunts Bay - 210 | Jul 20, 2026 8:00am | Jul 20, 2026 8:21am | Jul 20, 2026 11:38am | Jul 20, 2026 11:38am | Jul 20, 2026 11:50am | Jul 20, 2026 11:51am | Jul 20, 2026 11:53am | Jul 20, 2026 11:53am |  |  | Fair | No | Customer supply restored after replace too 25amp cables fuses
Non-Outage | J.E.26.07.18608 | C001859215 | Error Coore | Manchester | Completed | Load_252266 | Spur Tree - 310 | Jul 20, 2026 7:59am | Jul 20, 2026 8:00am | Jul 20, 2026 8:28am | Jul 20, 2026 8:28am | Jul 20, 2026 9:11am | Jul 20, 2026 11:40am | Jul 20, 2026 11:42am | Jul 20, 2026 11:42am |  |  | Fair | No | Open a 25 KVA xformer to remade corroded jumper at pole using 2 one bolt clamp voltage reading 118/118/236 volts
Non-Outage | J.E.26.07.18611 | C001859214 | Error Coore | Manchester | Completed | Load_252759 | Spur Tree - 310 | Jul 20, 2026 7:59am | Jul 20, 2026 8:00am | Jul 21, 2026 3:02pm | Jul 21, 2026 3:02pm | Jul 21, 2026 3:20pm | Jul 21, 2026 3:31pm | Jul 21, 2026 3:33pm | Jul 21, 2026 3:33pm |  |  | Fair | No | Premise not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.18923 | C001859213 | Error Coore | Manchester | Completed | Load_256785 | Spur Tree - 310 | Jul 20, 2026 7:59am | Jul 20, 2026 8:00am | Jul 21, 2026 3:33pm | Jul 21, 2026 3:33pm | Jul 21, 2026 3:58pm | Jul 21, 2026 4:00pm | Jul 21, 2026 4:00pm | Jul 21, 2026 4:00pm |  |  | Rains | No | Premise not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.18988 | C001859212 | Error Coore | Manchester | Completed | Load_250166 | Spur Tree - 310 | Jul 20, 2026 7:58am | Jul 20, 2026 8:00am | Jul 20, 2026 2:13pm | Jul 20, 2026 2:13pm | Jul 20, 2026 2:29pm | Jul 20, 2026 2:32pm | Jul 20, 2026 2:33pm | Jul 20, 2026 2:33pm |  |  | Fair | No | Premise not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.20537 | C001859211 | Error Coore | Manchester | Completed | Load_262800 | Spur Tree - 310 | Jul 20, 2026 7:58am | Jul 20, 2026 8:00am | Jul 20, 2026 2:07pm | Jul 20, 2026 2:07pm | Jul 20, 2026 2:11pm | Jul 20, 2026 2:12pm | Jul 20, 2026 2:13pm | Jul 20, 2026 2:13pm |  |  | Fair | No | Premise not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.21002 | C001859210 | Error Coore | Manchester | Completed | Load_270110 | Spur Tree - 310 | Jul 20, 2026 7:58am | Jul 20, 2026 8:00am | Jul 21, 2026 2:02pm | Jul 21, 2026 2:02pm | Jul 21, 2026 2:50pm | Jul 21, 2026 2:58pm | Jul 21, 2026 3:00pm | Jul 21, 2026 3:00pm |  |  | Fair | No | Premise not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.21366 | C001859209 | Error Coore | Manchester | Completed | Load_238945 | Spur Tree - 310 | Jul 20, 2026 7:58am | Jul 20, 2026 8:00am | Jul 20, 2026 1:35pm | Jul 20, 2026 1:35pm | Jul 20, 2026 1:58pm | Jul 20, 2026 2:05pm | Jul 20, 2026 2:07pm | Jul 20, 2026 2:07pm |  |  | Fair | No | Premise found ok customer said that the problem was resolved
Non-Outage | J.E.26.07.22037 | C001859205 | Oraine Minto | St.Ann | Completed | Load_264221 | Ocho Rios - 310 | Jul 20, 2026 7:58am | Jul 20, 2026 8:01am | Jul 20, 2026 11:04am | Jul 20, 2026 11:04am | Jul 20, 2026 11:04am | Jul 20, 2026 11:04am | Jul 20, 2026 11:05am | Jul 20, 2026 11:05am |  |  | Fair | No | Issue was resolved
Non-Outage | J.E.26.07.22266 | C001859207 | Error Coore | Manchester | Completed | Load_239919 | Spur Tree - 310 | Jul 20, 2026 7:58am | Jul 20, 2026 8:00am | Jul 21, 2026 8:28am | Jul 21, 2026 8:28am | Jul 21, 2026 8:52am | Jul 21, 2026 8:54am | Jul 21, 2026 8:54am | Jul 21, 2026 8:54am |  |  | Fair | No | Premise not found unable to locate customer not getting customer on phone
Outage | J.E.26.07.22230 | C001859206 | Nickolas Rodriques | Portmore | Completed | Load_260555 | Naggo Head - 610 | Jul 20, 2026 7:58am | Jul 20, 2026 7:59am | Jul 20, 2026 11:43am | Jul 20, 2026 11:44am | Jul 20, 2026 11:53am | Jul 20, 2026 11:55am | Jul 20, 2026 12:03pm | Jul 20, 2026 12:03pm |  |  | Fair | No | Call relates to the 25 amp junction fuse that was replaced with a fuse holder. Power restored.
Non-Outage | J.E.26.07.20599 | C001859204 | Oraine Minto | St.Ann | Completed | Load_267166 | Roaring River - 210 | Jul 20, 2026 7:55am | Jul 20, 2026 7:55am | Jul 20, 2026 11:07am | Jul 20, 2026 11:08am | Jul 20, 2026 11:08am | Jul 20, 2026 11:08am | Jul 20, 2026 11:09am | Jul 20, 2026 11:09am |  |  | Fair | No | Power was restored
Non-Outage | J.E.26.07.20709 | C001859203 | Oraine Minto | St.Ann | Completed | Load_256766 | Roaring River - 210 | Jul 20, 2026 7:54am | Jul 20, 2026 7:55am | Jul 20, 2026 1:55pm | Jul 20, 2026 1:55pm | Jul 20, 2026 1:55pm | Jul 20, 2026 1:55pm | Jul 20, 2026 1:57pm | Jul 20, 2026 1:57pm |  |  | Fair | No | Customer issues fix 2 red to red was used Refer to maintenance Pole# 0078208 need to change
Non-Outage | J.E.26.07.21225 | C001859202 | Oraine Minto | St.Ann | Completed | Load_243819 | Roaring River - 210 | Jul 20, 2026 7:54am | Jul 20, 2026 7:55am | Jul 20, 2026 12:54pm | Jul 20, 2026 12:54pm | Jul 20, 2026 12:54pm | Jul 20, 2026 12:54pm | Jul 20, 2026 12:55pm | Jul 20, 2026 12:55pm |  |  | Fair | No | Issue was resolved233v 233v 237v
Non-Outage | J.E.26.07.21902 | C001859201 | Oraine Minto | St.Ann | Completed | Load_261149 | Roaring River - 410 | Jul 20, 2026 7:54am | Jul 20, 2026 7:55am | Jul 20, 2026 2:04pm | Jul 20, 2026 2:04pm | Jul 20, 2026 2:04pm | Jul 20, 2026 2:04pm | Jul 20, 2026 2:04pm | Jul 20, 2026 2:04pm |  |  | Fair | No | Issue was already resolved
Non-Outage | J.E.26.07.22031 | C001859200 | Oraine Minto | St.Ann | Completed | Load_264221 | Ocho Rios - 310 | Jul 20, 2026 7:54am | Jul 20, 2026 7:55am | Jul 20, 2026 10:56am | Jul 20, 2026 10:56am | Jul 20, 2026 10:56am | Jul 20, 2026 10:56am | Jul 20, 2026 10:56am | Jul 20, 2026 10:56am |  |  | Fair | No | Issue was resolved
Non-Outage | J.E.26.07.22035 | C001859199 | Oraine Minto | St.Ann | Completed | Load_264221 | Ocho Rios - 310 | Jul 20, 2026 7:53am | Jul 20, 2026 7:55am | Jul 20, 2026 9:49am | Jul 20, 2026 9:50am | Jul 20, 2026 9:50am | Jul 20, 2026 10:55am | Jul 20, 2026 10:55am | Jul 20, 2026 10:55am |  |  | Fair | No | Issue resolved
Non-Outage | J.E.26.07.21413 | C001859194 | Stephen Taylor | St.Thomas | Completed | Load_577225 | Good Year - 210 | Jul 20, 2026 7:52am | Jul 20, 2026 7:52am | Jul 20, 2026 11:48am | Jul 20, 2026 12:48pm | Jul 20, 2026 12:51pm | Jul 20, 2026 12:51pm | Jul 20, 2026 12:52pm | Jul 20, 2026 12:52pm |  |  | Fair | No | Contact customer and customer say that we have the wrong number need more details
Non-Outage | J.E.26.07.21467 | C001859195 | Stephen Taylor | St.Thomas | Completed | Load_265771 | Lysson - 410 | Jul 20, 2026 7:52am | Jul 20, 2026 7:52am | Jul 20, 2026 8:26am | Jul 20, 2026 8:26am | Jul 20, 2026 10:24am | Jul 20, 2026 10:24am | Jul 20, 2026 10:26am | Jul 20, 2026 10:26am |  |  | Fair | No | Clamp up single phase use 2 clamps customer is now okay
Non-Outage | J.E.26.07.21857 | C001859196 | Stephen Taylor | St.Thomas | Completed | Load_257499 | Good Year - 210 | Jul 20, 2026 7:52am | Jul 20, 2026 7:52am | Jul 20, 2026 11:44am | Jul 20, 2026 11:44am | Jul 20, 2026 11:44am | Jul 20, 2026 11:44am | Jul 20, 2026 11:46am | Jul 20, 2026 11:46am |  |  | Fair | No | Patrol the area power is in the area a lot of call to customer no one answered the phone
Non-Outage | J.E.26.07.22055 | C001859198 | Omar King | St.Ann | Completed | Load_255942 | Ocho Rios - 310 | Jul 20, 2026 7:52am | Jul 20, 2026 7:52am | Jul 20, 2026 8:16am | Jul 20, 2026 8:16am | Jul 20, 2026 8:56am | Jul 20, 2026 8:56am | Jul 20, 2026 8:56am | Jul 20, 2026 8:56am | BrokenWire |  | Fair | No | Problem as been resolved
Outage | J.E.26.07.21927 | C001859193 | Moses Elliston | St.Catherine | Completed | Load_1001269 | Twickenham - 410 | Jul 20, 2026 7:51am | Jul 20, 2026 7:51am | Jul 20, 2026 11:13am | Jul 20, 2026 3:06pm | Jul 20, 2026 3:07pm | Jul 20, 2026 3:20pm | Jul 20, 2026 3:21pm | Jul 20, 2026 3:21pm |  |  | Fair | No | Premises closed .No answer from cell.
Non-Outage | J.E.26.07.22223 | C001859191 | Wan Carlos Scarlett | null | Completed | null | null | Jul 20, 2026 7:47am | Jul 20, 2026 7:48am | Jul 20, 2026 11:14am | Jul 20, 2026 11:14am | Jul 20, 2026 11:47am | Jul 20, 2026 12:26pm | Jul 20, 2026 12:29pm | Jul 20, 2026 12:29pm |  |  | Fair | No | Found cable and wireless pole leaning towards the road advise customer to contact cable provider for assistance
Outage | J.E.26.07.21833 | C001859189 | Wan Carlos Scarlett | St.Catherine | Completed | Load_251909 | Twickenham - 210 | Jul 20, 2026 7:47am | Jul 20, 2026 7:47am | Jul 20, 2026 7:52am | Jul 20, 2026 7:52am | Jul 20, 2026 8:51am | Jul 20, 2026 9:12am | Jul 20, 2026 9:13am | Jul 20, 2026 9:13am |  |  | Fair | No | Found customer 3 wire service at pole and one of the phase broken off use 2 one bolt clamps at open secondary line readings 116-117-234
Outage | J.E.26.07.22256 | C001859190 | Wan Carlos Scarlett | St.Catherine | Completed | Load_294338 | Twickenham - 210 | Jul 20, 2026 7:47am | Jul 20, 2026 7:47am | Jul 20, 2026 9:14am | Jul 20, 2026 9:14am | Jul 20, 2026 9:51am | Jul 20, 2026 10:00am | Jul 20, 2026 10:02am | Jul 20, 2026 10:02am |  |  | Fair | No | Reach at location been calling customer but no answer premises closed
Outage | J.E.26.07.22115 | C001859188 | Wan Carlos Scarlett | St.Catherine | Completed | Load_244819 | Twickenham - 210 | Jul 20, 2026 7:46am | Jul 20, 2026 7:47am | Jul 20, 2026 10:02am | Jul 20, 2026 10:02am | Jul 20, 2026 10:56am | Jul 20, 2026 11:11am | Jul 20, 2026 11:14am | Jul 20, 2026 11:14am |  |  | Fair | No | Found customer 3 wire service at pole with one of the phase ordered use one bolt clamp at secondary line phase readings 115-114-230
Non-Outage | J.E.26.07.18107 | C001859184 | Marlon Authors | Manchester | Completed | Load_240660 | Spur Tree - 210 | Jul 20, 2026 7:45am | Jul 20, 2026 7:46am | Jul 20, 2026 2:15pm | Jul 20, 2026 2:23pm | Jul 20, 2026 2:23pm | Jul 20, 2026 2:24pm | Jul 20, 2026 2:24pm | Jul 20, 2026 2:24pm | BrokenWire |  | Fair | No | Unable to locate and the customer not answering the phone
Non-Outage | J.E.26.07.18262 | C001859183 | Marlon Authors | null | Completed | null | null | Jul 20, 2026 7:45am | Jul 20, 2026 7:46am | Jul 20, 2026 12:50pm | Jul 20, 2026 12:50pm | Jul 20, 2026 1:20pm | Jul 20, 2026 1:21pm | Jul 20, 2026 1:21pm | Jul 20, 2026 1:21pm | Fire |  | Fair | No | Customer said the issue was resolved
Outage | J.E.26.07.22236 | C001859182 | Oshane Warren | St.Elizabeth | Completed | Load_292266 | Maggotty - 110 | Jul 20, 2026 7:45am | Jul 20, 2026 7:46am | Jul 20, 2026 9:30am | Jul 20, 2026 9:30am | Jul 20, 2026 9:40am | Jul 20, 2026 9:40am | Jul 20, 2026 9:43am | Jul 20, 2026 9:43am |  |  | Fair | No | Customer states that the power was restored
Non-Outage | J.E.26.07.22061 | C001859172 | Swon Miller | null | Completed | null | null | Jul 20, 2026 7:43am | Jul 20, 2026 8:50am | Jul 20, 2026 8:53am | Jul 20, 2026 8:53am | Jul 20, 2026 10:34am | Jul 22, 2026 10:40am | Jul 20, 2026 10:53am | Jul 20, 2026 10:53am | BrokenWire |  | Fair | No | Found one span of secondary neutral broken cause by tree limbs open 100 kva transformer to carry out repairs cut and remove tree limbs from secondary lines and splice and retention two span of secondary neutral and one span of secondary phase use about 25ft#2AA conductor 1#2 preform 1,2/o preform 3pg and close up 100 kva transformer 005665
Outage | J.E.26.07.21912 | C001859180 | Ricky Hall | St.Catherine | Completed | Load_242360 | Tredegar - 510 | Jul 20, 2026 7:43am | Jul 20, 2026 3:57pm | Jul 20, 2026 7:10pm | Jul 20, 2026 7:10pm | Jul 20, 2026 7:39pm | Jul 20, 2026 7:41pm | Jul 20, 2026 7:41pm | Jul 20, 2026 7:41pm |  |  | Fair | No | Issue was resolved on previous shift
Outage | J.E.26.07.21922 | C001859181 | Richard Nicholas | St.Catherine | Completed | Load_405835 | Tredegar - 510 | Jul 20, 2026 7:43am | Jul 20, 2026 7:44am | Jul 20, 2026 2:11pm | Jul 20, 2026 2:11pm | Jul 20, 2026 2:35pm | Jul 20, 2026 2:41pm | Jul 20, 2026 2:43pm | Jul 20, 2026 2:43pm |  |  | Fair | No | Area found ok,customer said that he could not wait on the JPS.co team so he paid someone to replaced the blown transformer fuse.
Outage | J.E.26.07.22112 | C001859178 | Marlon Authors | Manchester | Completed | Load_244043 | Spur Tree - 210 | Jul 20, 2026 7:43am | Jul 20, 2026 7:45am | Jul 20, 2026 9:29am | Jul 20, 2026 9:29am | Jul 20, 2026 9:41am | Jul 20, 2026 10:08am | Jul 20, 2026 10:08am | Jul 20, 2026 10:08am |  |  | Fair | No | Supply checked and found corrosion at pothead. Repair same using two linkets and one clamp, supply leave working ok rdg 107 volts
Outage | J.E.26.07.22245 | C001859176 | Evan Spaulding | St.Mary | Completed | Load_245223 | Highgate - 210 | Jul 20, 2026 7:43am | Jul 20, 2026 7:44am | Jul 20, 2026 8:17am | Jul 20, 2026 8:17am | Jul 20, 2026 10:28am | Jul 20, 2026 10:28am | Jul 20, 2026 10:31am | Jul 20, 2026 10:31am | Fire |  | Fair | No | Retention two spans secondary conductors using 25ft 2/0 AAAC conductor,3-2/0 splicing sleeves and 4-1bolt clamps,voltage left 116v117v,233v.
Outage | J.E.26.07.22257 | C001859175 | Raymond Carr | St.Mary | Completed | Load_257590 | Oracabessa - 210 | Jul 20, 2026 7:43am | Jul 20, 2026 7:44am | Jul 20, 2026 8:38am | Jul 20, 2026 8:38am | Jul 20, 2026 9:14am | Jul 20, 2026 9:32am | Jul 20, 2026 9:46am | Jul 20, 2026 9:46am |  |  | Fair | No | Blown junction fuse found at pole number 005486, line patrol and found okay, however after several tests close 100kva found to be defective. Kindly refer to maintenance department for replacement. Two blocks are affected.
Outage | J.E.26.07.22258 | C001859173 | Raymond Carr | St.Mary | Completed | Load_256495 | Oracabessa - 110 | Jul 20, 2026 7:43am | Jul 20, 2026 7:44am | Jul 20, 2026 10:18am | Jul 20, 2026 10:18am | Jul 20, 2026 11:43am | Jul 20, 2026 12:00am | Jul 20, 2026 12:00pm | Jul 20, 2026 12:00pm |  |  | Fair | No | Voltage readings at meter socket 120V. Customer was advised to have an electrician check wiring.
Outage | J.E.26.07.22259 | C001859171 | Evan Spaulding | St.Mary | Completed | Load_257699 | Highgate -110 | Jul 20, 2026 7:43am | Jul 20, 2026 7:44am | Jul 20, 2026 10:32am | Jul 20, 2026 10:33am | Jul 20, 2026 12:41pm | Jul 20, 2026 1:09pm | Jul 20, 2026 1:10pm | Jul 20, 2026 1:10pm |  | Y | Fair | No | Remove Bamboo from top of Transformer and replace 1-2 amps Transformer fuse,no pole.
Outage | J.E.26.07.22145 | C001859169 | Romeo Brissett | St.James | Completed | Load_262522 | Bogue - 510 | Jul 20, 2026 7:42am | Jul 20, 2026 7:44am | Jul 20, 2026 7:58am | Jul 20, 2026 7:58am | Jul 20, 2026 10:47am | Jul 20, 2026 10:50am | Jul 20, 2026 11:15am | Jul 20, 2026 11:15am | LeaningPole |  | Fair | No | Removed several illegal connections, retention secondary and repaired secondary jumper.
Outage | J.E.26.07.22212 | C001859170 | Dean Smith | Hanover | Completed | Load_575278 | Orange Bay - 310 | Jul 20, 2026 7:42am | Jul 20, 2026 4:35pm | Jul 20, 2026 10:29pm | Jul 20, 2026 10:29pm | Jul 20, 2026 10:52pm | Jul 20, 2026 10:52pm | Jul 20, 2026 10:52pm | Jul 20, 2026 10:52pm |  |  | Rains | No | Premises not found
Non-Outage | J.E.26.07.21229 | C001859167 | Javid Vernon | Westmoreland | Completed | Load_264370 | Paradise - 210 | Jul 20, 2026 7:41am | Jul 20, 2026 7:42am | Jul 20, 2026 9:52am | Jul 20, 2026 9:52am | Jul 20, 2026 10:38am | Jul 20, 2026 12:07pm | Jul 20, 2026 12:13pm | Jul 20, 2026 12:13pm |  |  | Fair | No | Check and found customer having low voltage after checking pothead and the JPS line isolate one 50kva transformer to change the tap change on the transformer from three to four voltage found at the end of the secondary line 99/105/203 voltage left 112/108/220And customer meter is single phasing needs to be replaced refer to field service customer needs urgent assistance
Non-Outage | J.E.26.07.21399 | C001859162 | Dwain Samuels | Westmoreland | Completed | Load_266966 | Paradise - 210 | Jul 20, 2026 7:41am | Jul 20, 2026 12:41pm | Jul 20, 2026 1:34pm | Jul 20, 2026 1:41pm | Jul 20, 2026 1:51pm | Jul 20, 2026 1:51pm | Jul 20, 2026 1:51pm | Jul 20, 2026 1:51pm |  |  | Fair | No | Called and customer said supply was restored
Outage | J.E.26.07.22018 | C001859168 | Richard Grant | St.Catherine | Completed | Load_568233 | New Michelton - 210 | Jul 20, 2026 7:41am | Jul 20, 2026 7:42am | Jul 20, 2026 7:57am | Jul 20, 2026 7:57am | Jul 20, 2026 9:53am | Jul 20, 2026 10:20am | Jul 20, 2026 10:20am | Jul 20, 2026 10:20am |  |  | Fair | No | Checks revealed customer has internal issues. Customer was advised. 117 117 234 voltages left at premises.
Outage | J.E.26.07.22032 | C001859163 | Clyde Brown | Clarendon | Completed | Load_242695 | May Pen - 110 | Jul 20, 2026 7:41am | Jul 20, 2026 3:16pm | Jul 20, 2026 9:42pm | Jul 20, 2026 9:42pm | Jul 20, 2026 9:42pm | Jul 20, 2026 9:28pm | Jul 20, 2026 9:46pm | Jul 20, 2026 9:46pm | BrokenWire |  | Fair | No | Customer said people stealing electricity through her property and was advised to report this to the police
Outage | J.E.26.07.22221 | C001859160 | Neville Spencer | Clarendon | Completed | Load_263164 | Monymusk - 410 | Jul 20, 2026 7:40am | Jul 20, 2026 7:41am | Jul 20, 2026 9:08am | Jul 20, 2026 9:08am | Jul 20, 2026 9:55am | Jul 20, 2026 9:55am | Jul 20, 2026 10:35am | Jul 20, 2026 10:35am |  |  | Fair | No | Check joints at xmfr pole found ok voltage reading 110 114 225 .Gate pad lock unable to check pothead meter blank.
Outage | J.E.26.07.22235 | C001859161 | Neville Spencer | Clarendon | Completed | Load_257573 | Parnassus - 210 | Jul 20, 2026 7:40am | Jul 20, 2026 7:41am | Jul 20, 2026 10:36am | Jul 20, 2026 10:36am | Jul 20, 2026 11:14am | Jul 20, 2026 11:56am | Jul 20, 2026 12:02pm | Jul 20, 2026 12:02pm |  |  | Fair | No | Renew 2, blown 40 amp j/ fuse at pole # 0177669 area restored.
Outage | J.E.26.07.21264 | C001859159 | Stephen Taylor | St.Thomas | Completed | Load_352530 | Good Year - 210 | Jul 20, 2026 7:38am | Jul 20, 2026 7:39am | Jul 20, 2026 10:34am | Jul 20, 2026 10:34am | Jul 20, 2026 10:58am | Jul 20, 2026 11:01am | Jul 20, 2026 11:01am | Jul 20, 2026 11:01am |  |  | Fair | No | Rami dox connection
Outage | J.E.26.07.21026 | C001859158 | Derrick Grubb | St.Thomas | Completed | Load_268013 | Good Year - 210 | Jul 20, 2026 7:36am | Jul 21, 2026 7:10am | Jul 21, 2026 8:58am | Jul 21, 2026 11:29am | Jul 21, 2026 11:29am | Jul 21, 2026 12:19pm | Jul 21, 2026 12:19pm | Jul 21, 2026 12:19pm | Fire |  | Fair | No | Change defective services wire feeling multiple customers, using approximately 150ft of #2aaa triplex and six one bolt clamps.
Outage | J.E.26.07.21930 | C001859154 | Raymond Lewis | St.Ann | Completed | Load_269661 | Cardiff Hall - 310 | Jul 20, 2026 7:32am | Jul 20, 2026 7:32am | Jul 20, 2026 7:54am | Jul 20, 2026 7:54am | Jul 20, 2026 10:20am | Jul 20, 2026 11:47pm | Jul 20, 2026 11:48am | Jul 20, 2026 11:48am | BrokenWire |  | Fair | No | Remade joint at pole and pothead 2 wire service phese and neutral voltage :111
Outage | J.E.26.07.22182 | C001859153 | Roxroy Needham | St.Ann | Completed | Load_242864 | Cardiff Hall - 310 | Jul 20, 2026 7:30am | Jul 20, 2026 3:06pm | Jul 20, 2026 3:31pm | Jul 20, 2026 3:31pm | Jul 20, 2026 4:26pm | Jul 20, 2026 4:44pm | Jul 20, 2026 4:46pm | Jul 20, 2026 4:46pm |  | Y | Fair | No | Replace a 8 amps junction fuse at pole
Outage | J.E.26.07.21928 | C001859152 | Raymond Lewis | St.Ann | Completed | Load_258246 | Cardiff Hall - 310 | Jul 20, 2026 7:28am | Jul 20, 2026 7:28am | Jul 20, 2026 2:37pm | Jul 20, 2026 2:37pm | Jul 20, 2026 2:37pm | Jul 20, 2026 2:39pm | Jul 20, 2026 2:39pm | Jul 20, 2026 2:39pm |  |  | Fair | No | Supply restored
Outage | J.E.26.07.22096 | C001859150 | Raymond Lewis | St.Ann | Completed | Load_258246 | Cardiff Hall - 310 | Jul 20, 2026 7:27am | Jul 20, 2026 7:29am | Jul 20, 2026 12:01pm | Jul 20, 2026 12:01pm | Jul 20, 2026 1:22pm | Jul 20, 2026 2:36pm | Jul 20, 2026 2:37pm | Jul 20, 2026 2:37pm |  |  | Fair | No | Cut and remove tree from secondary reset 10 kva x former
Outage | J.E.26.07.22106 | C001859151 | Hartley Chin | St.Ann | Completed | Load_262673 | Cardiff Hall - 310 | Jul 20, 2026 7:27am | Jul 20, 2026 7:29am | Jul 20, 2026 7:34am | Jul 20, 2026 12:49pm | Jul 20, 2026 12:49pm | Jul 20, 2026 12:50pm | Jul 20, 2026 12:50pm | Jul 20, 2026 12:50pm |  |  | Fair | No | Call related to job 22232
Outage | J.E.26.07.22232 | C001859149 | Hartley Chin | St.Ann | Completed | Load_262673 | Cardiff Hall - 310 | Jul 20, 2026 7:27am | Jul 20, 2026 7:29am | Jul 20, 2026 7:34am | Jul 20, 2026 12:18pm | Jul 20, 2026 12:18pm | Jul 20, 2026 12:44pm | Jul 20, 2026 12:49pm | Jul 20, 2026 12:49pm |  |  | Fair | No | Found corrosion on transformer neutral clamp. Voltage reading 156v 75v 230v after clamp change 116v 115v 231v
Outage | J.E.26.07.21619 | C001859143 | Kaydon Taylor | KSAN | Completed | Load_261661 | Constant Spring - 410 | Jul 20, 2026 7:23am | Jul 21, 2026 4:04pm | Jul 21, 2026 4:24pm | Jul 21, 2026 4:30pm | Jul 21, 2026 4:30pm | Jul 21, 2026 4:30pm | Jul 21, 2026 4:30pm | Jul 21, 2026 4:30pm |  |  | Fair | No | Found okay
Outage | J.E.26.07.21873 | C001859147 | Rayon Foster | Hanover | Completed | Load_303135 | Orange Bay - 210 | Jul 20, 2026 7:23am | Jul 20, 2026 7:58am | Jul 20, 2026 8:05am | Jul 20, 2026 8:06am | Jul 20, 2026 12:19pm | Jul 20, 2026 12:45pm | Jul 20, 2026 12:50pm | Jul 20, 2026 12:50pm |  |  | Fair | No | Patrol primary line to find 1 blown 8amp junction fuse and 1 blown 15kva transformer fuse complete line patrol before replacing 1 8amp junction and 1 2 amp transformer fuse at same and close
Outage | J.E.26.07.21880 | C001859145 | Rayon Foster | Hanover | Completed | Load_260650 | Orange Bay - 210 | Jul 20, 2026 7:23am | Jul 20, 2026 8:00am | Jul 20, 2026 8:04am | Jul 20, 2026 12:51pm | Jul 20, 2026 12:51pm | Jul 20, 2026 12:51pm | Jul 20, 2026 12:52pm | Jul 20, 2026 12:52pm |  |  | Fair | No | Patrol primary line to find 1 blown 8amp junction fuse and 1 blown 15kva transformer fuse complete line patrol before replacing 1 8amp junction and 1 2 amp transformer fuse at same and close
Outage | J.E.26.07.22059 | C001859144 | Tajay Bernard | Hanover | Completed | Load_266878 | Orange Bay - 310 | Jul 20, 2026 7:23am | Jul 20, 2026 7:33am | Jul 20, 2026 7:36am | Jul 20, 2026 7:37am | Jul 20, 2026 7:59am | Jul 20, 2026 8:01am | Jul 20, 2026 8:02am | Jul 20, 2026 8:02am | BrokenWire |  | Fair | No | Customer stated that the issue has been resolved
Outage | J.E.26.07.22241 | C001859142 | Damion Reid | Manchester | Completed | Load_238663 | Kendal - 310 | Jul 20, 2026 7:21am | Jul 20, 2026 7:21am | Jul 20, 2026 7:43am | Jul 20, 2026 7:43am | Jul 20, 2026 9:00am | Jul 20, 2026 9:56am | Jul 20, 2026 9:57am | Jul 20, 2026 9:57am | BrokenWire |  | Fair | No | Customer have internal problem customer have been advised
Outage | J.E.26.07.21760 | C001859133 | Christopher Edwards | KSAN | Completed | Load_257180 | Constant Spring - 410 | Jul 20, 2026 5:52am | Jul 20, 2026 5:53am | Jul 20, 2026 6:07am | Jul 20, 2026 7:07am | Jul 20, 2026 8:34am | Jul 20, 2026 11:22am | Jul 20, 2026 11:22am | Jul 20, 2026 11:22am | TreeContact,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Isolate 25 kva transformer To splice and retention broken open secondary neutral Using 50ft #2 AA conductor (2)#2 preform 2one bolt clamps Clear tree branch off open secondary lines
Outage | J.E.26.07.22151 | C001859130 | Derrick Dawkins | St.James | Completed | Load_1001861 | Bogue - 310 | Jul 20, 2026 12:09am | Jul 20, 2026 12:10am | Jul 20, 2026 4:01am | Jul 20, 2026 4:02am | Jul 20, 2026 4:02am | Jul 20, 2026 4:03am | Jul 20, 2026 4:03am | Jul 20, 2026 4:03am |  |  | Fair | No | Check and found premises ok
Outage | J.E.26.07.22174 | C001859131 | Derrick Dawkins | St.James | Completed | Load_261491 | Bogue - 310 | Jul 20, 2026 12:09am | Jul 20, 2026 12:10am | Jul 20, 2026 12:15am | Jul 20, 2026 12:15am | Jul 20, 2026 1:46am | Jul 20, 2026 2:59am | Jul 20, 2026 4:01am | Jul 20, 2026 4:01am |  |  | Fair | No | Found 20amp trip saver down due to tree fell on primary line cut and removed tree limb. Reclosed 20amp trip saver on pole number available
Outage | J.E.26.07.22176 | C001859129 | Derrick Dawkins | St.James | Completed | Load_249916 | Bogue - 310 | Jul 20, 2026 12:09am | Jul 20, 2026 12:10am | Jul 20, 2026 4:03am | Jul 20, 2026 4:03am | Jul 20, 2026 4:03am | Jul 20, 2026 4:05am | Jul 20, 2026 4:05am | Jul 20, 2026 4:05am |  |  | Fair | No
Outage | J.E.26.07.22068 | C001859127 | Delano Gayle | St.Catherine | Completed | Load_244050 | Tredegar - 410 | Jul 19, 2026 11:04pm | Jul 19, 2026 11:04pm | Jul 20, 2026 2:58am | Jul 20, 2026 2:58am | Jul 20, 2026 3:16am | Jul 20, 2026 3:29am | Jul 20, 2026 3:29am | Jul 20, 2026 3:29am |  |  | Fair | No | Trip 25kva transformer no pole number patrolled line section and found okay, reset transformer
Outage | J.E.26.07.22153 | C001859126 | Delano Gayle | St.Catherine | Completed | Load_1001612 | Tredegar - 310 | Jul 19, 2026 11:04pm | Jul 19, 2026 11:04pm | Jul 20, 2026 1:26am | Jul 20, 2026 1:35am | Jul 20, 2026 2:28am | Jul 20, 2026 2:58am | Jul 20, 2026 2:58am | Jul 20, 2026 2:58am |  |  | Fair | No | Trip 25kva transformer no pole number patrolled line section and found okay, reset transformer
Outage | J.E.26.07.22109 | C001859119 | Marlon Brown | Trelawny | Completed | Load_257971 | Duncans - 210 | Jul 19, 2026 9:37pm | Jul 19, 2026 9:38pm | Jul 19, 2026 9:52pm | Jul 19, 2026 9:52pm | Jul 19, 2026 10:45pm | Jul 19, 2026 11:46pm | Jul 19, 2026 11:46pm | Jul 19, 2026 11:46pm |  |  | Fair | No | Tree fell on line, causing 6 spans of primary and secondary conductors to be broken, tree is still on the line and poles needs to be straightened. Fuse isolated at comfort hall and 25amps trip saver closed at Alps. Refer to maintenance personnel O. Ellis.
Non-Outage | J.E.26.07.22014 | C001859118 | Evan Spaulding | null | Completed | null | null | Jul 19, 2026 9:35pm | Jul 20, 2026 7:46am | Jul 20, 2026 2:23pm | Jul 20, 2026 2:23pm | Jul 20, 2026 2:46pm | Jul 20, 2026 2:46pm | Jul 20, 2026 2:46pm | Jul 20, 2026 2:46pm |  |  | Fair | No | Issue was resolved yesterday
Outage | J.E.26.07.22058 | C001859117 | Romaine Roberts | St.Mary | Completed | Load_266257 | Highgate -110 | Jul 19, 2026 9:35pm | Jul 19, 2026 9:41pm | null | Jul 19, 2026 10:32pm | Jul 19, 2026 10:32pm | Jul 19, 2026 10:33pm | Jul 19, 2026 10:33pm | Jul 19, 2026 10:33pm |  |  | Fair | No | Cannot reach customer by phone insufficient direction
Outage | J.E.26.07.21934 | C001859110 | Oshane Warren | Hanover | Completed | Load_260765 | Orange Bay - 310 | Jul 19, 2026 8:44pm | Jul 19, 2026 8:44pm | Jul 19, 2026 9:46pm | Jul 19, 2026 9:46pm | Jul 20, 2026 12:10am | Jul 20, 2026 12:13am | Jul 20, 2026 12:14am | Jul 20, 2026 12:14am |  |  | Rains | No | Replace 3 amp 25 kva transformer fuse
Outage | J.E.26.07.22085 | C001859105 | Raymond Lewis | St.Ann | Completed | Load_264221 | Ocho Rios - 310 | Jul 19, 2026 8:10pm | Jul 19, 2026 8:10pm | Jul 19, 2026 10:07pm | Jul 19, 2026 10:07pm | Jul 19, 2026 10:07pm | Jul 19, 2026 10:08pm | Jul 19, 2026 10:08pm | Jul 19, 2026 10:08pm | BrokenWire |  | Fair | No | Supply restored
Outage | J.E.26.07.22084 | C001859104 | Raymond Carr | St.Mary | Completed | Load_576530 | Oracabessa - 110 | Jul 19, 2026 8:05pm | Jul 19, 2026 8:08pm | Jul 19, 2026 8:11pm | Jul 19, 2026 8:11pm | Jul 19, 2026 8:15pm | Jul 19, 2026 8:10pm | Jul 19, 2026 8:17pm | Jul 19, 2026 8:17pm |  |  | Fair | No | Customer was advised to contact customer care regarding prepaid account.
Outage | J.E.26.07.22046 | C001859102 | Richard Samuda | Manchester | Completed | Load_258623 | Spur Tree - 310 | Jul 19, 2026 7:55pm | Jul 19, 2026 7:55pm | Jul 19, 2026 8:08pm | Jul 19, 2026 8:08pm | Jul 19, 2026 8:15pm | Jul 19, 2026 8:52pm | Jul 19, 2026 8:52pm | Jul 19, 2026 8:52pm |  |  | Fair | No | Customer had tripped breaker advised customer to. Reset breaker customer back to normal 115/115/230
Outage | J.E.26.07.21986 | C001859097 | Andrew Powell | Manchester | Completed | Load_264623 | Spur Tree - 210 | Jul 19, 2026 7:22pm | Jul 19, 2026 7:23pm | Jul 19, 2026 8:39pm | Jul 19, 2026 8:39pm | Jul 19, 2026 8:39pm | Jul 19, 2026 8:39pm | Jul 19, 2026 8:40pm | Jul 19, 2026 8:40pm |  |  | Rains | No | Called related to blown fuse by Cheapside supply restored.
Outage | J.E.26.07.22029 | C001859098 | Andrew Powell | Manchester | Completed | Load_240578 | Spur Tree - 210 | Jul 19, 2026 7:22pm | Jul 19, 2026 7:23pm | Jul 19, 2026 8:40pm | Jul 19, 2026 8:40pm | Jul 19, 2026 8:40pm | Jul 19, 2026 8:41pm | Jul 19, 2026 8:42pm | Jul 19, 2026 8:42pm |  |  | Rains | No | Called related to blown fuse by Cheapside customer stated that supply restored.
Outage | J.E.26.07.21879 | C001859095 | Marlon Authors | Manchester | Completed | Load_240172 | Spur Tree - 210 | Jul 19, 2026 7:21pm | Jul 19, 2026 7:21pm | Jul 19, 2026 7:40pm | Jul 19, 2026 8:54pm | Jul 19, 2026 8:54pm | Jul 19, 2026 8:15pm | Jul 19, 2026 9:11pm | Jul 19, 2026 9:11pm | BrokenWire |  | Fair | No | Patrol and found one 35 feet T wooden pole up rooted, leaning across the road and resting in a ackee tree one span of primary conductor broken. Please refer same to the maintenance department for further assistance
Outage | J.E.26.07.21891 | C001859093 | Marlon Authors | St.Elizabeth | Completed | Load_302915 | Maggotty - 110 | Jul 19, 2026 7:20pm | Jul 19, 2026 7:20pm | Jul 19, 2026 10:01pm | Jul 19, 2026 10:01pm | Jul 19, 2026 10:09pm | Jul 19, 2026 10:25pm | Jul 19, 2026 10:25pm | Jul 19, 2026 10:25pm | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Patrol and found clear. Replace one blown 8 amp junction fuse no pole #. Restored supply okay
Outage | J.E.26.07.21897 | C001859092 | Marlon Authors | St.Elizabeth | Completed | Load_255287 | Maggotty - 110 | Jul 19, 2026 7:20pm | Jul 19, 2026 7:20pm | Jul 19, 2026 9:22pm | Jul 19, 2026 9:22pm | Jul 19, 2026 9:22pm | Jul 19, 2026 9:09pm | Jul 19, 2026 9:23pm | Jul 19, 2026 9:23pm |  |  | Fair | No | Supply restored to the area
Outage | J.E.26.07.21994 | C001859090 | Andrew Powell | Manchester | Completed | Load_247046 | Spur Tree - 210 | Jul 19, 2026 7:12pm | Jul 19, 2026 7:13pm | Jul 19, 2026 7:18pm | Jul 19, 2026 7:27pm | Jul 19, 2026 7:28pm | Jul 19, 2026 8:35pm | Jul 19, 2026 8:38pm | Jul 19, 2026 8:38pm |  |  | Rains | No | Patrol and found clear, replace one blown 40 amp junction fuse by Cheapside to Port sea, no pole number by switch location, restore supply okay.
Outage | J.E.26.07.22027 | C001859089 | Raymond Lewis | St.Ann | Completed | Load_255942 | Ocho Rios - 310 | Jul 19, 2026 7:10pm | Jul 19, 2026 7:10pm | Jul 19, 2026 8:10pm | Jul 19, 2026 8:10pm | Jul 19, 2026 8:10pm | Jul 19, 2026 10:04pm | Jul 19, 2026 10:04pm | Jul 19, 2026 10:04pm |  |  | Fair | No | Open 50 KVA x former to splice and retention four span secondary phase and neutral
Outage | J.E.26.07.21967 | C001859088 | Marlon Brown | Trelawny | Completed | Load_257002 | Duncans - 210 | Jul 19, 2026 6:55pm | Jul 19, 2026 6:55pm | Jul 19, 2026 7:01pm | Jul 19, 2026 7:05pm | Jul 19, 2026 7:45pm | Jul 19, 2026 8:45pm | Jul 19, 2026 8:45pm | Jul 19, 2026 8:45pm |  |  | Fair | No | Replaced 20amps junction fuse
Outage | J.E.26.07.21949 | C001859085 | Romaine Roberts | St.Mary | Completed | Load_252159 | Highgate - 210 | Jul 19, 2026 6:22pm | Jul 19, 2026 6:22pm | null | Jul 19, 2026 8:07pm | Jul 19, 2026 9:29pm | Jul 19, 2026 9:48pm | Jul 19, 2026 9:51pm | Jul 19, 2026 9:51pm |  |  | Fair | No | Suspect bird to blow junction fuse patrol plane burn found on ground replace 40 amp no pole number power restore
Non-Outage | J.E.26.07.21963 | C001859080 | Andrew Powell | null | Completed | null | null | Jul 19, 2026 6:16pm | Jul 19, 2026 6:16pm | Jul 19, 2026 6:21pm | Jul 19, 2026 6:21pm | Jul 19, 2026 6:41pm | Jul 19, 2026 6:52pm | Jul 19, 2026 6:56pm | Jul 19, 2026 6:56pm |  |  | Fair | No | Found three blown 25 amp fuse protect 750 kva pad mount transformer cause from burnt up main breaker panel which facilitated NIC pumping station customer leaves without supply due to repair work required.
Outage | J.E.26.07.21920 | C001859078 | Omar King | St.Ann | Completed | Load_1000620 | Roaring River - 410 | Jul 19, 2026 6:10pm | Jul 20, 2026 7:31am | Jul 20, 2026 8:57am | Jul 20, 2026 8:57am | Jul 20, 2026 9:57am | Jul 20, 2026 9:58am | Jul 20, 2026 9:58am | Jul 20, 2026 9:58am |  |  | Fair | No | Unable to find customer call several times no answer directions not sufficient
Outage | J.E.26.07.21928 | C001859077 | Daniel Francis | St.Ann | Completed | Load_258246 | Cardiff Hall - 310 | Jul 19, 2026 6:10pm | Jul 19, 2026 6:11pm | Jul 19, 2026 7:10pm | Jul 19, 2026 7:10pm | Jul 19, 2026 11:35pm | Jul 19, 2026 11:37pm | Jul 19, 2026 11:47pm | Jul 19, 2026 11:47pm |  |  | Fair | No | Daylight attention found 10kva transformer out can’t get to all of the lines at this time the line come true some of the hillside we can’t get there in the night try to give them light but it can’t work transformer not going in
Outage | J.E.26.07.21930 | C001859079 | Daniel Francis | St.Ann | Completed | Load_269661 | Cardiff Hall - 310 | Jul 19, 2026 6:10pm | Jul 19, 2026 6:11pm | Jul 19, 2026 7:10pm | Jul 20, 2026 12:20am | Jul 20, 2026 12:40am | Jul 20, 2026 12:45am | Jul 20, 2026 12:49am | Jul 20, 2026 12:49am | BrokenWire |  | Fair | No | Premises lock
Non-Outage | J.E.26.07.21389 | C001859076 | Richard Nicholas | St.Catherine | Completed | Load_269718 | Tredegar - 510 | Jul 19, 2026 6:01pm | Jul 19, 2026 6:02pm | Jul 19, 2026 7:45pm | Jul 19, 2026 7:45pm | Jul 19, 2026 8:52pm | Jul 19, 2026 10:40pm | Jul 19, 2026 10:42pm | Jul 19, 2026 10:42pm |  |  | Fair | No | Spot bushing done.splice and retention 2 span of broken secondary neutral.1 splicing sleeve,4 clamp and 1 preformed was used to complete the repair.
Outage | J.E.26.07.21931 | C001859072 | Marlon Brown | Trelawny | Completed | Load_556439 | Duncans - 210 | Jul 19, 2026 5:50pm | Jul 19, 2026 5:51pm | Jul 19, 2026 6:17pm | Jul 19, 2026 6:17pm | Jul 19, 2026 6:17pm | Jul 19, 2026 6:23pm | Jul 19, 2026 6:23pm | Jul 19, 2026 6:23pm |  |  | Fair | No | Customer meter is burnt, please refer to Field Service Department. Hence customer is without electricity.
Outage | J.E.26.07.21859 | C001859069 | Rusean Allen | KSAN | Completed | Load_240099 | Constant Spring - 410 | Jul 19, 2026 4:55pm | Jul 19, 2026 4:57pm | Jul 19, 2026 5:23pm | Jul 19, 2026 5:23pm | Jul 19, 2026 6:56pm | Jul 19, 2026 8:00pm | Jul 19, 2026 8:00pm | Jul 19, 2026 8:00pm |  |  | Fair | No | Broken secondary wire found, wire was spliced and retention.Spot bushing was done.
Outage | J.E.26.07.21905 | C001859068 | Christopher Edwards | KSAS | Completed | Load_264050 | Up Park Camp - 410 | Jul 19, 2026 4:54pm | Jul 19, 2026 11:01pm | Jul 19, 2026 11:04pm | Jul 19, 2026 11:28pm | Jul 19, 2026 11:45pm | Jul 20, 2026 12:26am | Jul 20, 2026 12:27am | Jul 20, 2026 12:27am |  |  | Fair | No | Refuse blown junction fuseUsing (1) 20 amps
Outage | J.E.26.07.21809 | C001859067 | Andre Smith | KSAN | Completed | Load_238567 | Washington Blvd - 310 | Jul 19, 2026 4:40pm | Jul 19, 2026 4:40pm | Jul 19, 2026 7:11pm | Jul 19, 2026 7:11pm | Jul 19, 2026 7:50pm | Jul 19, 2026 8:24pm | Jul 19, 2026 8:25pm | Jul 19, 2026 8:25pm |  |  | Fair | No | Reconnection done in ypp box supply restored
Outage | J.E.26.07.21894 | C001859066 | Raymond Carr | St.Mary | Completed | Load_260552 | Oracabessa - 210 | Jul 19, 2026 4:34pm | Jul 19, 2026 4:34pm | Jul 19, 2026 4:40pm | Jul 19, 2026 4:40pm | Jul 19, 2026 4:58pm | Jul 19, 2026 5:07pm | Jul 19, 2026 5:15pm | Jul 19, 2026 5:15pm |  |  | Fair | No | Voltage readings at meter socket 120/120/240. Customer breaker was turned off.
Outage | J.E.26.07.21890 | C001859065 | Collin Robinson | Portland | Completed | Load_243977 | Port Antonio - 410 | Jul 19, 2026 4:33pm | Jul 19, 2026 4:33pm | Jul 19, 2026 4:40pm | Jul 19, 2026 4:40pm | Jul 19, 2026 4:53pm | Jul 19, 2026 5:07pm | Jul 19, 2026 5:07pm | Jul 19, 2026 5:07pm | Fire |  | Fair | No | Reconnect broken #6 twisted wire at pole Voltage reading 115v 115 v 230v
Non-Outage | J.E.26.07.21257 | C001859063 | Hartley Chin | Clarendon | Completed | Load_257058 | Monymusk - 410 | Jul 19, 2026 4:09pm | Jul 19, 2026 4:11pm | Jul 19, 2026 8:41pm | Jul 19, 2026 8:41pm | Jul 19, 2026 9:29pm | Jul 19, 2026 9:37pm | Jul 19, 2026 9:45pm | Jul 19, 2026 9:45pm |  |  | Fair | No | Prem not found … unable to contact customer with contact # provided.. direction inconclusive…
Non-Outage | J.E.26.07.21832 | C001859064 | Hartley Chin | Clarendon | Completed | Load_247306 | Monymusk - 410 | Jul 19, 2026 4:09pm | Jul 19, 2026 4:11pm | Jul 19, 2026 8:40pm | Jul 19, 2026 9:45pm | Jul 19, 2026 10:33pm | Jul 19, 2026 10:34pm | Jul 19, 2026 10:35pm | Jul 19, 2026 10:35pm |  |  | Fair | No | Contacted customer… was told supply is okay …
Non-Outage | J.E.26.05.36822 | C001859062 | Hartley Chin | Clarendon | Completed | Load_262026 | Monymusk - 210 | Jul 19, 2026 4:06pm | Jul 19, 2026 4:11pm | Jul 19, 2026 6:43pm | Jul 19, 2026 6:43pm | Jul 19, 2026 7:57pm | Jul 19, 2026 8:35pm | Jul 19, 2026 8:40pm | Jul 19, 2026 8:40pm |  |  | Fair | No | Ref to maintenance!!! Found leaning 35ft pole with single phase Primary, and open secondary circuit.. pole foot is okay , pole only need to be straighten… Note : customer supply is okay …
Outage | J.E.26.07.21457 | C001859061 | Andre Smith | St.Catherine | Completed | Load_244637 | New Michelton - 210 | Jul 19, 2026 4:05pm | Jul 19, 2026 4:06pm | Jul 19, 2026 4:21pm | Jul 19, 2026 4:21pm | Jul 19, 2026 5:52pm | Jul 19, 2026 7:10pm | Jul 19, 2026 7:10pm | Jul 19, 2026 7:10pm |  |  | Fair | No | Replace defective 25kva transformer supply restored
Outage | J.E.26.07.21893 | C001859060 | Neville Spencer | Clarendon | Completed | Load_555853 | May Pen - 110 | Jul 19, 2026 4:03pm | Jul 19, 2026 4:03pm | Jul 19, 2026 5:50pm | Jul 19, 2026 5:50pm | Jul 19, 2026 6:13pm | Jul 19, 2026 6:13pm | Jul 19, 2026 6:54pm | Jul 19, 2026 6:54pm |  |  | Fair | No | Renew blown 8 amp j/ fuse.Also renew blown 20 amp j/ fuse at pole # 18 19 83 area restored.
Outage | J.E.26.07.21778 | C001859059 | Neville Spencer | Clarendon | Completed | Load_1003526 | May Pen - 110 | Jul 19, 2026 3:58pm | Jul 19, 2026 3:58pm | Jul 19, 2026 6:55pm | Jul 19, 2026 6:55pm | Jul 19, 2026 7:19pm | Jul 19, 2026 7:19pm | Jul 19, 2026 7:23pm | Jul 19, 2026 7:23pm |  |  | Fair | No | Renew 2 blown 10 amp J/ fuse at pole #599378 area restored.
Non-Outage | J.E.26.07.21829 | C001859053 | Collin Robinson | null | Completed | null | null | Jul 19, 2026 3:51pm | Jul 19, 2026 3:52pm | Jul 19, 2026 3:58pm | Jul 19, 2026 3:58pm | Jul 19, 2026 3:58pm | Jul 19, 2026 4:02pm | Jul 19, 2026 4:02pm | Jul 19, 2026 4:02pm | BrokenPole |  | Fair | No | Information received from customer that the report they made was not a brokering pole issue it was on outage and power was restored back the Area
Outage | J.E.26.07.21852 | C001859055 | Marlon Authors | St.Elizabeth | Completed | Load_252908 | Maggotty - 110 | Jul 19, 2026 3:51pm | Jul 19, 2026 3:52pm | Jul 19, 2026 9:23pm | Jul 19, 2026 9:23pm | Jul 19, 2026 9:30pm | Jul 19, 2026 9:59pm | Jul 19, 2026 9:59pm | Jul 19, 2026 9:59pm |  |  | Fair | No | Patrol and found clear. Replace one blown 20 amp junction fuse no pole #. Restored supply ok
Outage | J.E.26.07.21862 | C001859054 | Marlon Authors | St.Elizabeth | Completed | Load_260242 | Maggotty - 110 | Jul 19, 2026 3:51pm | Jul 19, 2026 3:52pm | Jul 19, 2026 10:28pm | Jul 19, 2026 10:28pm | Jul 19, 2026 10:28pm | Jul 19, 2026 10:28pm | Jul 19, 2026 10:29pm | Jul 19, 2026 10:29pm |  |  | Fair | No | Supply restored to the area
Outage | J.E.26.07.21888 | C001859056 | Marlon Authors | St.Elizabeth | Completed | Load_292945 | Maggotty - 110 | Jul 19, 2026 3:51pm | Jul 19, 2026 3:52pm | Jul 19, 2026 8:04pm | Jul 19, 2026 9:14pm | Jul 19, 2026 9:14pm | Jul 19, 2026 8:59pm | Jul 19, 2026 9:20pm | Jul 19, 2026 9:20pm |  |  | Fair | No | Patrol and found clear. Replace two blown 30 amp junction fuses no pole # and one blown 15 amp. Restored supply ok
Outage | J.E.26.07.21885 | C001859052 | Oshane Warren | Hanover | Completed | Load_262008 | Orange Bay - 310 | Jul 19, 2026 3:50pm | Jul 19, 2026 5:11pm | Jul 19, 2026 5:43pm | Jul 19, 2026 6:01pm | Jul 19, 2026 6:55pm | Jul 19, 2026 6:56pm | Jul 19, 2026 6:56pm | Jul 19, 2026 6:56pm |  |  | Fair | No | Unable to locate or contact customer
Outage | J.E.26.07.21784 | C001859051 | Neville Spencer | Clarendon | Completed | Load_252982 | May Pen - 110 | Jul 19, 2026 3:47pm | Jul 19, 2026 3:53pm | Jul 19, 2026 7:23pm | Jul 19, 2026 7:23pm | Jul 19, 2026 8:00pm | Jul 19, 2026 8:40pm | Jul 19, 2026 8:43pm | Jul 19, 2026 8:43pm |  |  | Fair | No | Renew blown 3 amp fuse protecting 25 kva xmfr supply restored.
Outage | J.E.26.07.21882 | C001859049 | Raymond Lewis | St.Ann | Completed | Load_264624 | Ocho Rios - 310 | Jul 19, 2026 3:41pm | Jul 19, 2026 3:41pm | Jul 19, 2026 3:59pm | Jul 19, 2026 3:59pm | Jul 19, 2026 4:55pm | Jul 19, 2026 4:57pm | Jul 19, 2026 4:57pm | Jul 19, 2026 4:57pm |  |  | Fair | No | Customer M, Hayley’s said supply restored
Non-Outage | J.E.26.07.10766 | C001859048 | Clyde Brown | Clarendon | Completed | Load_267585 | Parnassus - 310 | Jul 19, 2026 3:37pm | Jul 19, 2026 3:38pm | Jul 19, 2026 6:54pm | Jul 19, 2026 6:54pm | Jul 19, 2026 7:44pm | Jul 19, 2026 7:43pm | Jul 19, 2026 7:48pm | Jul 19, 2026 7:48pm |  |  | Fair | No | Found ok
Non-Outage | J.E.26.07.19946 | C001859041 | Clyde Brown | Clarendon | Completed | Load_245743 | Parnassus - 310 | Jul 19, 2026 3:37pm | Jul 19, 2026 3:38pm | Jul 19, 2026 5:06pm | Jul 19, 2026 5:06pm | Jul 19, 2026 5:06pm | Jul 19, 2026 4:05pm | Jul 19, 2026 5:09pm | Jul 19, 2026 5:09pm |  |  | Fair | No | Found ok
Outage | J.E.26.07.21855 | C001859046 | Stephen Taylor | St.Thomas | Completed | Load_256439 | Good Year - 110 | Jul 19, 2026 3:37pm | Jul 19, 2026 3:38pm | Jul 19, 2026 7:07pm | Jul 19, 2026 7:07pm | Jul 19, 2026 7:07pm | Jul 19, 2026 7:08pm | Jul 19, 2026 7:09pm | Jul 19, 2026 7:09pm | Fire |  | Fair | No | Check with customer and say power is back on they now ok
Outage | J.E.26.07.21766 | C001859040 | Clyde Brown | Clarendon | Completed | Load_245656 | May Pen - 210 | Jul 19, 2026 3:35pm | Jul 19, 2026 3:38pm | Jul 19, 2026 7:56pm | Jul 19, 2026 7:56pm | Jul 19, 2026 7:56pm | Jul 19, 2026 7:49pm | Jul 19, 2026 8:00pm | Jul 19, 2026 8:00pm |  |  | Fair | No | Cannot be located customer not answering phone
Outage | J.E.26.07.21861 | C001859039 | Marlon Authors | Manchester | Completed | Load_248505 | Spur Tree - 210 | Jul 19, 2026 3:29pm | Jul 19, 2026 3:51pm | Jul 19, 2026 6:20pm | Jul 19, 2026 6:20pm | Jul 19, 2026 7:01pm | Jul 19, 2026 7:08pm | Jul 19, 2026 7:08pm | Jul 19, 2026 7:08pm |  |  | Fair | No | Patrol and found clear. Replace one blown 10 amp junction fuse no pole #. Restored supply ok
Non-Outage | J.E.26.07.21734 | C001859038 | Swon Miller | null | Completed | null | null | Jul 19, 2026 3:15pm | Jul 19, 2026 3:15pm | Jul 19, 2026 3:42pm | Jul 19, 2026 3:42pm | Jul 19, 2026 3:42pm | Jul 19, 2026 3:42pm | Jul 19, 2026 3:43pm | Jul 19, 2026 3:43pm | Fire |  | Fair | No | This call belongs to trelawny
Outage | J.E.26.07.21845 | C001859037 | Donald Cunningham | St.Catherine | Completed | Load_240664 | New Michelton - 210 | Jul 19, 2026 3:08pm | Jul 19, 2026 3:08pm | Jul 19, 2026 6:34pm | Jul 19, 2026 6:34pm | Jul 19, 2026 8:18pm | Jul 19, 2026 8:37pm | Jul 19, 2026 8:41pm | Jul 19, 2026 8:41pm | Fire |  | Fair | No | Blown transformer fuse by one pole span away from Morris lane 25 kva replace 3 amp fuse
Outage | J.E.26.07.21835 | C001859035 | Daniel Francis | St.Ann | Completed | Load_312801 | Roaring River - 410 | Jul 19, 2026 3:05pm | Jul 19, 2026 3:15pm | Jul 19, 2026 4:57pm | Jul 19, 2026 4:57pm | Jul 19, 2026 4:57pm | Jul 19, 2026 6:31pm | Jul 19, 2026 6:38pm | Jul 19, 2026 6:38pm |  |  | Fair | No | Patrol and found junction blown at pole #0036588 two 40 amp replace
Non-Outage | J.E.26.07.21423 | C001859034 | Milton Charlton | KSAN | Completed | Load_239696 | Washington Blvd - 510 | Jul 19, 2026 2:45pm | Jul 19, 2026 2:50pm | Jul 19, 2026 4:51pm | Jul 19, 2026 4:51pm | Jul 19, 2026 6:22pm | Jul 19, 2026 6:20pm | Jul 19, 2026 6:26pm | Jul 19, 2026 6:26pm |  |  | Fair | No | Isolate 25 kva transformer at pole#0104301 and repair corroded #6 triplex joints at pothead using four 1- bolt clamps and reclosed transformer switch. Readings at pothead 116-117-234 volts.
Outage | J.E.26.07.21838 | C001859033 | Nickolas Rodriques | Portmore | Completed | Load_567928 | Naggo Head - 610 | Jul 19, 2026 2:42pm | Jul 20, 2026 7:59am | Jul 20, 2026 8:14am | Jul 20, 2026 10:22am | Jul 20, 2026 10:34am | Jul 20, 2026 10:36am | Jul 20, 2026 10:44am | Jul 20, 2026 10:44am |  |  | Fair | No | Power restored. Call relates to the junction fuses that was replaced.
Outage | J.E.26.07.21718 | C001859031 | Wan Carlos Scarlett | Portmore | Completed | Load_251292 | Naggo Head - 510 | Jul 19, 2026 2:41pm | Jul 19, 2026 2:44pm | Jul 19, 2026 6:33pm | Jul 19, 2026 9:37pm | Jul 19, 2026 10:42pm | Jul 19, 2026 10:58pm | Jul 19, 2026 11:00pm | Jul 19, 2026 11:00pm |  |  | Fair | No | Found customer 3 wire service at pole with phase and neutral corroded use 3 one bolt clamps at open secondary line readings 115-114-230
Non-Outage | J.E.26.07.21537 | C001859030 | Marlon Authors | Manchester | Completed | Load_252348 | Spur Tree - 210 | Jul 19, 2026 2:38pm | Jul 19, 2026 2:38pm | Jul 19, 2026 5:19pm | Jul 19, 2026 5:19pm | Jul 19, 2026 5:45pm | Jul 19, 2026 6:13pm | Jul 19, 2026 6:13pm | Jul 19, 2026 6:13pm |  |  | Fair | No | Patrol and found clear. Further checks revealed that 100 kva transformer is burnt and approximately 200 feet or one pole span of 2/0 twisted secondary conductor is damaged and needs to be replaced also. Please refer same to the maintenance department for further assistance
Outage | J.E.26.07.21789 | C001859027 | Donald Cunningham | St.Catherine | Completed | Load_258745 | New Michelton - 210 | Jul 19, 2026 2:22pm | Jul 19, 2026 2:24pm | Jul 19, 2026 3:28pm | Jul 19, 2026 3:28pm | Jul 19, 2026 4:47pm | Jul 19, 2026 4:48pm | Jul 19, 2026 4:50pm | Jul 19, 2026 4:50pm |  |  | Rains | No | Entrance to vanfair garden blown junction fuse found and replace with 8 amp also blown transformer fuse replace with 2 amp after removing whiss from transformer 25 kva
Outage | J.E.26.07.21823 | C001859026 | Richard Nicholas | St.Catherine | Completed | Load_257183 | Tredegar - 210 | Jul 19, 2026 2:21pm | Jul 19, 2026 2:22pm | Jul 19, 2026 4:53pm | Jul 19, 2026 4:53pm | Jul 19, 2026 5:52pm | Jul 19, 2026 6:28pm | Jul 19, 2026 6:30pm | Jul 19, 2026 6:30pm |  |  | Fair | No | Area found ok,customer said that the report was for st.thomas and not st.catherine.
Outage | J.E.26.07.21798 | C001859024 | Ricky Hall | St.Catherine | Completed | Load_269949 | Rhodens Pen - 410 | Jul 19, 2026 2:19pm | Jul 19, 2026 2:22pm | Jul 19, 2026 4:27pm | Jul 19, 2026 4:27pm | Jul 19, 2026 6:33pm | Jul 19, 2026 7:04pm | Jul 19, 2026 7:04pm | Jul 19, 2026 7:04pm |  |  | EarthMovement | No | Replace 2 blown 20 junction fuse
Outage | J.E.26.07.21707 | C001859022 | Collin Robinson | Portland | Completed | Load_252093 | Port Antonio - 310 | Jul 19, 2026 2:14pm | Jul 19, 2026 2:14pm | Jul 19, 2026 3:07pm | Jul 19, 2026 3:07pm | Jul 19, 2026 3:46pm | Jul 19, 2026 3:53pm | Jul 19, 2026 3:53pm | Jul 19, 2026 3:53pm | Fire |  | Fair | No | Clear tree branches from near primary conductor and replace 15 amps junction fuse
Outage | J.E.26.07.21773 | C001859023 | Marlon Authors | Manchester | Completed | Load_245331 | Spur Tree - 210 | Jul 19, 2026 2:14pm | Jul 19, 2026 2:15pm | Jul 19, 2026 2:28pm | Jul 19, 2026 2:28pm | Jul 19, 2026 2:28pm | Jul 19, 2026 2:30pm | Jul 19, 2026 2:30pm | Jul 19, 2026 2:30pm |  |  | Rains | No | Customer said supply was restored
Non-Outage | J.E.26.07.21821 | C001859021 | Collin Robinson | null | Completed | null | null | Jul 19, 2026 2:10pm | Jul 19, 2026 3:52pm | Jul 19, 2026 4:24pm | Jul 19, 2026 4:24pm | Jul 19, 2026 4:30pm | Jul 19, 2026 4:34pm | Jul 19, 2026 4:34pm | Jul 19, 2026 4:34pm |  |  | Fair | No | Information received from customer that issue was resolved
Outage | J.E.26.07.21810 | C001859020 | Collin Robinson | Portland | Completed | Load_248557 | Port Antonio - 410 | Jul 19, 2026 2:09pm | Jul 19, 2026 2:10pm | Jul 19, 2026 2:16pm | Jul 19, 2026 2:16pm | Jul 19, 2026 2:16pm | Jul 19, 2026 2:44pm | Jul 19, 2026 2:44pm | Jul 19, 2026 2:44pm |  |  | Fair | No | Customer main breaker trip
Outage | J.E.26.07.21803 | C001859019 | Andrew Powell | St.Elizabeth | Completed | Load_248202 | Maggotty - 210 | Jul 19, 2026 2:07pm | Jul 19, 2026 7:26pm | Jul 19, 2026 8:42pm | Jul 19, 2026 8:42pm | Jul 19, 2026 9:26pm | Jul 19, 2026 10:17pm | Jul 19, 2026 10:20pm | Jul 19, 2026 10:20pm | BrokenWire |  | Fair | No | Replace burnt up service wire using 100 feet #6 triplex, three clamps and three service sleeves, voltage reading 110v-112v phase to neutral 222v cross phase, meter #2859394.
Outage | J.E.26.07.21794 | C001859016 | Rusean Allen | KSAN | Completed | Load_257226 | Constant Spring - 410 | Jul 19, 2026 1:47pm | Jul 19, 2026 4:57pm | Jul 19, 2026 8:01pm | Jul 19, 2026 8:01pm | Jul 19, 2026 8:35pm | Jul 19, 2026 8:38pm | Jul 19, 2026 8:38pm | Jul 19, 2026 8:38pm |  |  | Fair | No | Smaller vehicle required
Outage | J.E.26.07.21777 | C001859012 | Richman Whyte | Westmoreland | Completed | Load_260892 | Paradise - 310 | Jul 19, 2026 1:30pm | Jul 19, 2026 1:30pm | Jul 19, 2026 3:52pm | Jul 19, 2026 3:53pm | Jul 19, 2026 3:53pm | Jul 19, 2026 3:53pm | Jul 19, 2026 3:54pm | Jul 19, 2026 3:54pm |  |  | Rains | No | Replace 2 amp 25 kva transformer fuse
Outage | J.E.26.07.21742 | C001859011 | Marlon Authors | Manchester | Completed | Load_264579 | Spur Tree - 210 | Jul 19, 2026 1:21pm | Jul 19, 2026 1:24pm | Jul 19, 2026 1:44pm | Jul 19, 2026 1:44pm | Jul 19, 2026 1:44pm | Jul 19, 2026 2:05pm | Jul 19, 2026 2:05pm | Jul 19, 2026 2:05pm |  |  | Rains | No | Patrol and found clear . Replace one blown 30 amp junction fuse no pole #. Restored supply ok
Outage | J.E.26.07.21764 | C001859009 | Rusean Allen | KSAN | Completed | Load_248587 | Constant Spring - 410 | Jul 19, 2026 1:16pm | Jul 19, 2026 4:59pm | Jul 19, 2026 7:38pm | Jul 19, 2026 8:00pm | Jul 19, 2026 8:00pm | Jul 19, 2026 8:01pm | Jul 19, 2026 8:01pm | Jul 19, 2026 8:01pm | BrokenWire |  | Fair | No | Related
Outage | J.E.26.07.21749 | C001859004 | Wan Carlos Scarlett | Portmore | Completed | Load_240647 | Naggo Head - 610 | Jul 19, 2026 12:50pm | Jul 19, 2026 12:51pm | Jul 19, 2026 1:31pm | Jul 19, 2026 2:28pm | Jul 19, 2026 2:38pm | Jul 19, 2026 2:38pm | Jul 19, 2026 2:40pm | Jul 19, 2026 2:40pm |  |  | Fair | No | Found customer 3 wire service at pothead with one of the phase corroded use one Penn union at service wire phase readings 114-115-230
Outage | J.E.26.07.21747 | C001859003 | Rusean Allen | KSAN | Completed | Load_245923 | Constant Spring - 410 | Jul 19, 2026 12:48pm | Jul 19, 2026 8:24pm | Jul 19, 2026 8:39pm | Jul 19, 2026 8:40pm | Jul 19, 2026 10:06pm | Jul 19, 2026 10:06pm | Jul 19, 2026 10:07pm | Jul 19, 2026 10:07pm |  |  | Fair | No | Premises okay
Outage | J.E.26.07.21731 | C001859001 | Oshane Warren | Westmoreland | Completed | Load_258236 | Paradise - 110 | Jul 19, 2026 12:46pm | Jul 19, 2026 12:46pm | Jul 19, 2026 1:01pm | Jul 19, 2026 1:02pm | Jul 19, 2026 1:02pm | Jul 19, 2026 1:02pm | Jul 19, 2026 1:03pm | Jul 19, 2026 1:03pm |  |  | Fair | No | Customer stated that the power was restored
Outage | J.E.26.07.21659 | C001858999 | Richard Nicholas | St.Catherine | Completed | Load_243121 | Tredegar - 310 | Jul 19, 2026 12:33pm | Jul 20, 2026 7:43am | Jul 20, 2026 8:29am | Jul 20, 2026 8:29am | Jul 20, 2026 11:02am | Jul 20, 2026 12:53pm | Jul 20, 2026 1:03pm | Jul 20, 2026 1:03pm | BrokenWire | Y | Fair | No | Resident in the area stripped twisted secondary phase and connect illegal throw up connections as a result secondary phase and neutral burnt off.same was repaired using 1 2/0 splicing sleeve and 2 clamp also 2 span of low hanging secondary was retention.voltage reading 113,115 and 228v.
Outage | J.E.26.07.21721 | C001858994 | Andre Williams | Trelawny | Completed | Load_255782 | Martha Brae - 210 | Jul 19, 2026 12:17pm | Jul 19, 2026 12:17pm | Jul 19, 2026 1:35pm | Jul 19, 2026 1:35pm | Jul 19, 2026 1:35pm | Jul 19, 2026 1:36pm | Jul 19, 2026 1:37pm | Jul 19, 2026 1:37pm | Fire |  | Fair | No | Call same as job #21589 customer requesting disconection to carry carry out repairs on panel
Outage | J.E.26.07.21704 | C001858993 | Andre Williams | Trelawny | Completed | Load_246391 | Martha Brae - 210 | Jul 19, 2026 12:16pm | Jul 19, 2026 12:17pm | Jul 19, 2026 1:12pm | Jul 19, 2026 1:28pm | Jul 19, 2026 1:30pm | Jul 19, 2026 1:34pm | Jul 19, 2026 1:34pm | Jul 19, 2026 1:34pm |  |  | Fair | No | Customer reconnected with the help of meter center premises now with supply
Outage | J.E.26.07.21648 | C001858987 | Clyde Brown | Clarendon | Completed | Load_268691 | May Pen - 210 | Jul 19, 2026 12:15pm | Jul 19, 2026 12:18pm | Jul 19, 2026 2:01pm | Jul 19, 2026 2:01pm | Jul 19, 2026 2:01pm | Jul 19, 2026 1:45pm | Jul 19, 2026 2:06pm | Jul 19, 2026 2:06pm |  |  | Fair | No | Blown 30 amps junction fuse at Lower Rhymesbury,line patrolled and no fault seen,blown fuse replaced.
Outage | J.E.26.07.21658 | C001858986 | Neville Spencer | Clarendon | Completed | Load_237880 | May Pen - 110 | Jul 19, 2026 12:15pm | Jul 19, 2026 12:18pm | Jul 19, 2026 4:09pm | Jul 19, 2026 4:09pm | Jul 19, 2026 4:53pm | Jul 19, 2026 5:45pm | Jul 19, 2026 5:49pm | Jul 19, 2026 5:49pm | BrokenWire | Y | Fair | No | Cleared bamboo from 13.8 kv line Also splice and retention broken neutral on 3, wire service renew blown 15 amp j/ fuse at pole #03233 area restored.
Non-Outage | J.E.26.07.21720 | C001858984 | Kenroy Dale | null | Completed | null | null | Jul 19, 2026 12:08pm | Jul 19, 2026 12:13pm | Jul 19, 2026 1:40pm | Jul 19, 2026 1:40pm | Jul 19, 2026 2:20pm | Jul 19, 2026 3:09pm | Jul 19, 2026 3:13pm | Jul 19, 2026 3:13pm | TreeContact |  | Rains | No | Burn off phase found at pole remade connection using 1 one bolt clamp voltage reading 111/113/224
Outage | J.E.26.07.21714 | C001858983 | Edward Royal | KSAN | Completed | Load_574490 | Constant Spring - 210 | Jul 19, 2026 12:07pm | Jul 19, 2026 12:22pm | Jul 19, 2026 12:37pm | Jul 19, 2026 12:37pm | Jul 19, 2026 12:59pm | Jul 19, 2026 1:02pm | Jul 19, 2026 1:02pm | Jul 19, 2026 1:02pm |  |  | Fair | No | Defective 15 kva transformer needs changes no pole# referred to maintenance
Outage | J.E.26.07.21574 | C001858976 | Wan Carlos Scarlett | Portmore | Completed | Load_253463 | Naggo Head - 610 | Jul 19, 2026 11:48am | Jul 19, 2026 11:56am | Jul 19, 2026 3:36pm | Jul 19, 2026 3:36pm | Jul 19, 2026 4:33pm | Jul 19, 2026 5:49pm | Jul 19, 2026 5:52pm | Jul 19, 2026 5:52pm | Fire |  | Fair | No | Found customer service wire defective use 60ft of # 6 service wire use 2 Penn union at pothead use 2 one bolt clamps at open secondary line readings 115.2 wire service
Outage | J.E.26.07.21677 | C001858973 | Richard Samuda | Manchester | Completed | Load_251691 | Spur Tree - 310 | Jul 19, 2026 11:45am | Jul 19, 2026 11:45am | Jul 19, 2026 11:57am | Jul 19, 2026 11:57am | Jul 19, 2026 12:34pm | Jul 19, 2026 1:16pm | Jul 19, 2026 1:17pm | Jul 19, 2026 1:17pm | BrokenWire |  | SevereWind | No | Splice and reconnect 1span of secondary lower phase that was broken by vehicle using one 2/0 splicing sleeve and 1bolt clamp customer back to normal
Outage | J.E.26.07.21639 | C001858972 | Edward Royal | KSAS | Completed | Load_254287 | Duhaney - 310 | Jul 19, 2026 11:42am | Jul 19, 2026 11:43am | Jul 19, 2026 1:03pm | Jul 19, 2026 1:03pm | Jul 19, 2026 1:43pm | Jul 19, 2026 2:04pm | Jul 19, 2026 2:04pm | Jul 19, 2026 2:04pm | BrokenPole |  | Fair | No | Broken guy pole need to be replaced also a customer service cable Brest down customer pothead wire was damage I advice customer to get a electrician to fix the pothead when repaired is complete customer is to contact jps customer care
Outage | J.E.26.07.21673 | C001858969 | Edward Royal | KSAN | Completed | Load_237914 | Constant Spring - 310 | Jul 19, 2026 11:41am | Jul 19, 2026 11:43am | Jul 19, 2026 12:15pm | Jul 19, 2026 12:15pm | Jul 19, 2026 12:15pm | Jul 19, 2026 12:36pm | Jul 19, 2026 12:37pm | Jul 19, 2026 12:37pm | Fire |  | Fair | No | Premises found ok no fire was seen on pole and the area have supply
Non-Outage | J.E.26.07.21589 | C001858968 | Andre Williams | Trelawny | Completed | Load_255782 | Martha Brae - 210 | Jul 19, 2026 11:39am | Jul 19, 2026 11:39am | Jul 19, 2026 11:43am | Jul 19, 2026 11:45am | Jul 19, 2026 11:45am | Jul 19, 2026 11:54am | Jul 19, 2026 11:54am | Jul 19, 2026 11:54am |  |  | Fair | No | Customer requesting disconection to carry out repairs on panel , customer in hexing box , also premises close , phone going to voice mail unable to assist
Outage | J.E.26.07.21393 | C001858967 | Neville Spencer | St.Ann | Completed | Load_257906 | Cardiff Hall - 310 | Jul 19, 2026 11:37am | Jul 19, 2026 1:44pm | Jul 19, 2026 3:13pm | Jul 19, 2026 3:13pm | Jul 19, 2026 3:16pm | Jul 19, 2026 3:16pm | Jul 19, 2026 3:18pm | Jul 19, 2026 3:18pm |  | Y | Rains | No | Cleared bamboo from secondary lines reset trip 10 kva xmfr supply restored.
Non-Outage | J.E.26.07.21697 | C001858965 | Moses Elliston | St.Catherine | Completed | Load_300754 | Twickenham - 410 | Jul 19, 2026 11:33am | Jul 19, 2026 12:02pm | Jul 19, 2026 12:44pm | Jul 19, 2026 12:44pm | Jul 19, 2026 2:45pm | Jul 19, 2026 2:45pm | Jul 19, 2026 2:47pm | Jul 19, 2026 2:47pm |  |  | Fair | No | Burnt meter changed to # 3069924
Non-Outage | J.E.26.07.21694 | C001858964 | Collin Robinson | Portland | Completed | Load_352869 | Port Antonio - 410 | Jul 19, 2026 11:31am | Jul 19, 2026 11:32am | Jul 19, 2026 12:40pm | Jul 19, 2026 12:40pm | Jul 19, 2026 12:41pm | Jul 19, 2026 12:47pm | Jul 19, 2026 12:47pm | Jul 19, 2026 12:47pm |  |  | Fair | No | Change one corroded one bolt clamp at pothead Voltage reading 120v 120v 240v
Non-Outage | J.E.26.07.20965 | C001858960 | Nickolas Rodriques | Portmore | Completed | Load_1003656 | Naggo Head - 610 | Jul 19, 2026 11:26am | Jul 19, 2026 11:30am | Jul 19, 2026 8:45pm | Jul 19, 2026 8:55pm | Jul 19, 2026 9:31pm | Jul 19, 2026 10:41pm | Jul 19, 2026 10:43pm | Jul 19, 2026 10:43pm | BrokenPole |  | Fair | No | Customer stated that the report was made for his premises located at Seymour Avenue, Kingston.
Non-Outage | J.E.26.07.21556 | C001858962 | Nickolas Rodriques | Portmore | Completed | Load_567929 | Naggo Head - 610 | Jul 19, 2026 11:26am | Jul 19, 2026 11:30am | Jul 19, 2026 7:01pm | Jul 19, 2026 7:09pm | Jul 19, 2026 7:47pm | Jul 19, 2026 8:34pm | Jul 19, 2026 8:44pm | Jul 19, 2026 8:44pm | BrokenWire |  | Fair | No | Checked and found 2-north twisted wire hanging low due to a leaning 35 ft wooden pole which was caused by a vehicle accident. It is a (T) pole which consists of single phase primary, two guy wires, 2-north twisted and one streetlight. Refer to maintenance. (The pole can be re-used. Pole # 0057680)
Non-Outage | J.E.26.07.21629 | C001858959 | Donald Cunningham | St.Catherine | Completed | Load_247419 | New Michelton - 410 | Jul 19, 2026 11:21am | Jul 19, 2026 11:22am | Jul 19, 2026 12:07pm | Jul 19, 2026 12:07pm | Jul 19, 2026 1:51pm | Jul 19, 2026 1:52pm | Jul 19, 2026 2:06pm | Jul 19, 2026 2:06pm |  |  | Fair | No | Repair not completed raining heavy in area
Non-Outage | J.E.26.07.21684 | C001858956 | Ricky Hall | St.Catherine | Completed | Load_269718 | Tredegar - 510 | Jul 19, 2026 11:16am | Jul 19, 2026 11:17am | Jul 19, 2026 3:00pm | Jul 19, 2026 3:00pm | Jul 19, 2026 3:49pm | Jul 19, 2026 3:57pm | Jul 19, 2026 3:58pm | Jul 19, 2026 3:58pm |  |  | Fair | No | Premises not located insufficient information
Non-Outage | J.E.26.07.21007 | C001858952 | Ricky Hall | St.Catherine | Completed | Load_237657 | Rhodens Pen - 410 | Jul 19, 2026 11:15am | Jul 19, 2026 11:17am | Jul 19, 2026 1:10pm | Jul 19, 2026 1:10pm | Jul 19, 2026 1:43pm | Jul 19, 2026 2:57pm | Jul 19, 2026 2:59pm | Jul 19, 2026 2:59pm |  |  | Fair | No | Change 25 kva xfmr secondary tap from Pos 3-pos -5 116/115/230
Non-Outage | J.E.26.06.03988 | C001858950 | Richard Samuda | Manchester | Completed | Load_575039 | Spur Tree - 310 | Jul 19, 2026 11:01am | Jul 19, 2026 11:09am | Jul 19, 2026 1:58pm | Jul 19, 2026 1:58pm | Jul 19, 2026 2:17pm | Jul 19, 2026 2:36pm | Jul 19, 2026 2:37pm | Jul 19, 2026 2:37pm | LeaningPole |  | Rains | No | Found 30 ft twisted secondary T pole leaning on customer permitter wall and she concern that it my fall
Non-Outage | J.E.26.07.15882 | C001858951 | Richard Samuda | Manchester | Completed | Load_250297 | Spur Tree - 310 | Jul 19, 2026 11:01am | Jul 19, 2026 11:12am | Jul 19, 2026 3:10pm | Jul 19, 2026 3:10pm | Jul 19, 2026 3:26pm | Jul 19, 2026 3:33pm | Jul 19, 2026 3:34pm | Jul 19, 2026 3:34pm | LeaningPole |  | Fair | No | Two 35 ft secondary two TA pole foot rotten and customer concern they my fall and cause damage ref call to maintenance
Outage | J.E.26.07.21472 | C001858949 | Stephen Taylor | St.Thomas | Completed | Load_269057 | Lysson - 410 | Jul 19, 2026 11:00am | Jul 19, 2026 11:02am | Jul 19, 2026 12:06pm | Jul 19, 2026 12:06pm | Jul 19, 2026 12:17pm | Jul 19, 2026 12:19pm | Jul 19, 2026 12:19pm | Jul 19, 2026 12:19pm |  |  | Fair | No | Patrol and clear line reset 25kva transformer all customer is now in service
Outage | J.E.26.07.21665 | C001858948 | Stephen Taylor | St.Thomas | Completed | Load_246042 | Good Year - 110 | Jul 19, 2026 11:00am | Jul 19, 2026 11:02am | Jul 19, 2026 4:12pm | Jul 19, 2026 4:18pm | Jul 19, 2026 6:23pm | Jul 19, 2026 6:23pm | Jul 19, 2026 7:07pm | Jul 19, 2026 7:07pm | Fire |  | Fair | No | Patrol and clear line with switch stick then close up junction With 10ams fuse
Non-Outage | J.E.26.07.21431 | C001858947 | Collin Robinson | Portland | Completed | Load_241801 | Port Antonio - 310 | Jul 19, 2026 10:51am | Jul 19, 2026 10:56am | Jul 19, 2026 4:02pm | Jul 19, 2026 4:02pm | Jul 19, 2026 4:10pm | Jul 19, 2026 4:12pm | Jul 19, 2026 4:12pm | Jul 19, 2026 4:12pm |  |  | Fair | No | Information received from customer that issue was resolved from yesterday
Non-Outage | J.E.26.07.17141 | C001858941 | Nickolas Rodriques | St.Catherine | Completed | Load_567663 | Tredegar - 310 | Jul 19, 2026 10:48am | Jul 19, 2026 10:59am | Jul 19, 2026 11:23am | Jul 19, 2026 11:31am | Jul 19, 2026 12:33pm | Jul 19, 2026 12:52pm | Jul 19, 2026 1:17pm | Jul 19, 2026 1:17pm | BrokenPole |  | Fair | No | Customer is following up on the transferring of services wires from an old rotten leaning pole to the newly installed pole.
Non-Outage | J.E.26.07.19114 | C001858942 | Richard Nicholas | St.Catherine | Completed | Load_305191 | Tredegar - 210 | Jul 19, 2026 10:48am | Jul 19, 2026 10:59am | Jul 19, 2026 6:31pm | Jul 19, 2026 6:31pm | Jul 19, 2026 7:22pm | Jul 19, 2026 7:44pm | Jul 19, 2026 7:45pm | Jul 19, 2026 7:45pm | BrokenPole |  | Fair | No | Area found ok,no broken pole seen.
Non-Outage | J.E.26.07.19822 | C001858940 | Wan Carlos Scarlett | null | Completed | null | null | Jul 19, 2026 10:48am | Jul 19, 2026 10:57am | Jul 19, 2026 12:49pm | Jul 19, 2026 12:49pm | Jul 19, 2026 1:24pm | Jul 19, 2026 2:23pm | Jul 19, 2026 2:28pm | Jul 19, 2026 2:28pm | BrokenWire |  | Fair | No | Found cable and wireless wire hanging low advised customer to contact cable provider
Non-Outage | J.E.26.07.02886 | C001858939 | Donald Cunningham | St.Catherine | Completed | Load_252447 | New Michelton - 210 | Jul 19, 2026 10:47am | Jul 19, 2026 10:50am | Jul 19, 2026 4:50pm | Jul 19, 2026 4:50pm | Jul 19, 2026 6:11pm | Jul 19, 2026 6:21pm | Jul 19, 2026 6:22pm | Jul 19, 2026 6:22pm | BrokenPole |  | Fair | No | No broken pole seenn customer not reachable
Non-Outage | J.E.26.07.20359 | C001858936 | Richard Nicholas | St.Catherine | Completed | Load_246786 | Tredegar - 410 | Jul 19, 2026 10:46am | Jul 19, 2026 10:56am | Jul 19, 2026 1:09pm | Jul 19, 2026 1:09pm | Jul 19, 2026 1:38pm | Jul 19, 2026 2:11pm | Jul 19, 2026 2:13pm | Jul 19, 2026 2:13pm | BrokenWire |  | Fair | No | One span of secondary neutral missing however it was unable to replace due to overgrown trees.two over grown trees need to cut before secondary neutral can be replace.
Non-Outage | J.E.26.07.20497 | C001858937 | Wan Carlos Scarlett | null | Completed | null | null | Jul 19, 2026 10:46am | Jul 19, 2026 10:56am | Jul 19, 2026 11:44am | Jul 19, 2026 5:53pm | Jul 19, 2026 7:10pm | Jul 19, 2026 8:06pm | Jul 19, 2026 8:07pm | Jul 19, 2026 8:07pm | BrokenWire |  | Fair | No | Found cable and wireless wires hanging low to the ground advised customer to contact cable provider for assistance
Non-Outage | J.E.26.07.09223 | C001858933 | Ricky Hall | St.Catherine | Completed | Load_239074 | Rhodens Pen - 310 | Jul 19, 2026 10:45am | Jul 19, 2026 10:49am | Jul 19, 2026 12:02pm | Jul 19, 2026 12:02pm | Jul 19, 2026 12:53pm | Jul 19, 2026 1:10pm | Jul 19, 2026 1:10pm | Jul 19, 2026 1:10pm | BrokenWire |  | Fair | No | No broken wire seen
Non-Outage | J.E.26.07.10041 | C001858934 | Nickolas Rodriques | null | Completed | null | null | Jul 19, 2026 10:45am | Jul 19, 2026 10:55am | Jul 19, 2026 1:18pm | Jul 19, 2026 1:20pm | Jul 19, 2026 2:18pm | Jul 19, 2026 3:48pm | Jul 19, 2026 4:22pm | Jul 19, 2026 4:22pm | BrokenWire |  | Fair | No | Checked and found a switch without fuse link and a 25 KVA transformer drop lead isolated which makes up a bank of three transformer which now forms an open delta. Refer to maintenance for further investigation.
Non-Outage | J.E.26.05.35700 | C001858932 | Richard Nicholas | St.Catherine | Completed | Load_246786 | Tredegar - 410 | Jul 19, 2026 10:44am | Jul 19, 2026 10:53am | Jul 19, 2026 2:14pm | Jul 19, 2026 2:14pm | Jul 19, 2026 2:41pm | Jul 19, 2026 3:32pm | Jul 19, 2026 3:36pm | Jul 19, 2026 3:36pm | BrokenWire |  | Fair | No | Premises found ok.
Non-Outage | J.E.26.06.12330 | C001858929 | Richard Nicholas | null | Completed | null | null | Jul 19, 2026 10:41am | Jul 19, 2026 10:51am | Jul 19, 2026 3:37pm | Jul 19, 2026 3:37pm | Jul 19, 2026 4:21pm | Jul 19, 2026 4:52pm | Jul 19, 2026 4:52pm | Jul 19, 2026 4:52pm | BrokenPole |  | Fair | No | Found ok
Non-Outage | J.E.26.05.33220 | C001858922 | Wan Carlos Scarlett | null | Completed | null | null | Jul 19, 2026 10:40am | Jul 19, 2026 10:52am | Jul 19, 2026 11:31am | Jul 19, 2026 8:08pm | Jul 19, 2026 9:22pm | Jul 19, 2026 9:35pm | Jul 19, 2026 9:37pm | Jul 19, 2026 9:37pm | BangingWires |  | Fair | No | Found cable and wireless wires banging on each other advise customer to contact cable provider for assistance
Non-Outage | J.E.26.07.04750 | C001858923 | Richard Nicholas | null | Completed | null | null | Jul 19, 2026 10:40am | Jul 19, 2026 10:52am | Jul 19, 2026 11:51am | Jul 19, 2026 11:51am | Jul 19, 2026 12:47pm | Jul 19, 2026 1:07pm | Jul 19, 2026 1:08pm | Jul 19, 2026 1:08pm | BrokenPole |  | Fair | No | Area found ok,no broken pole seen
Outage | J.E.26.07.21649 | C001858919 | Romeo Brissett | St.James | Completed | Load_267225 | Bogue - 510 | Jul 19, 2026 10:35am | Jul 19, 2026 10:36am | Jul 19, 2026 10:45am | Jul 19, 2026 10:45am | Jul 19, 2026 11:37am | Jul 19, 2026 1:00pm | Jul 19, 2026 1:05pm | Jul 19, 2026 1:05pm |  |  | Fair | No | Cut and removed vegetation, replaced (1)15amps junction fuse.
Non-Outage | J.E.26.07.20738 | C001858918 | Donald Cunningham | null | Completed | null | null | Jul 19, 2026 10:33am | Jul 19, 2026 11:13am | Jul 19, 2026 8:42pm | Jul 19, 2026 8:42pm | Jul 19, 2026 9:44pm | Jul 19, 2026 9:47pm | Jul 19, 2026 9:54pm | Jul 19, 2026 9:54pm | Fire |  | Fair | No | No fire seen
Outage | J.E.26.07.21638 | C001858916 | Oshane Warren | Westmoreland | Completed | Load_266123 | Paradise - 210 | Jul 19, 2026 10:30am | Jul 19, 2026 10:45am | Jul 19, 2026 12:36pm | Jul 19, 2026 12:36pm | Jul 19, 2026 12:36pm | Jul 19, 2026 12:38pm | Jul 19, 2026 12:39pm | Jul 19, 2026 12:39pm |  |  | Fair | No | Customer is complaining about high bill
Outage | J.E.26.07.21499 | C001858915 | Neville Spencer | St.Ann | Completed | Load_1003292 | Cardiff Hall - 310 | Jul 19, 2026 10:28am | Jul 19, 2026 10:28am | Jul 19, 2026 1:57pm | Jul 19, 2026 1:58pm | Jul 19, 2026 3:10pm | Jul 19, 2026 3:10pm | Jul 19, 2026 3:12pm | Jul 19, 2026 3:12pm |  | Y | Rains | No | Cleared tree limb from xmfr pole renew blown 3 amp fuse protecting 25 kva xmfr supply restored.
Outage | J.E.26.07.21569 | C001858914 | Neville Spencer | St.Ann | Completed | Load_264725 | Cardiff Hall - 310 | Jul 19, 2026 10:28am | Jul 19, 2026 10:28am | Jul 19, 2026 1:37pm | Jul 19, 2026 1:37pm | Jul 19, 2026 1:47pm | Jul 19, 2026 1:47pm | Jul 19, 2026 1:56pm | Jul 19, 2026 1:56pm |  |  | Rains | No | Found 35 c6 wooden pole broken off at root construction T pole. Also leaning towards road way3, customer out of supply 8 amp j/ fuse blown POLE NEED TO REPLACED.
Outage | J.E.26.07.21636 | C001858913 | Edward Royal | KSAN | Completed | Load_253122 | Constant Spring - 210 | Jul 19, 2026 10:26am | Jul 19, 2026 10:27am | Jul 19, 2026 10:55am | Jul 19, 2026 10:55am | Jul 19, 2026 10:55am | Jul 19, 2026 10:58am | Jul 19, 2026 10:58am | Jul 19, 2026 10:58am |  |  | Fair | No | Customer having challenges adding credit referred to field service
Outage | J.E.26.07.21567 | C001858910 | Swon Miller | St.James | Completed | Load_238044 | Queens Drive - 710 | Jul 19, 2026 10:25am | Jul 19, 2026 10:25am | Jul 19, 2026 10:36am | Jul 19, 2026 10:36am | Jul 19, 2026 11:15am | Jul 14, 2026 12:11am | Jul 19, 2026 12:11pm | Jul 19, 2026 12:11pm | BrokenWire |  | Fair | No | Found two span of secondary phase down cause by tree limbs voltage found 115open 50 kva transformer to carry out repairs cut and remove tree limbs from secondary lines and splice and retention two span of secondary phase use about 15ft#2AA conductor 1#2 preform 3pg close up 50 kva transformer voltage left 115/116/232
Non-Outage | J.E.26.07.21635 | C001858908 | Kenroy Dale | null | Completed | null | null | Jul 19, 2026 10:20am | Jul 19, 2026 10:22am | Jul 19, 2026 10:54am | Jul 19, 2026 10:55am | Jul 19, 2026 11:43am | Jul 19, 2026 12:29pm | Jul 19, 2026 12:32pm | Jul 19, 2026 12:32pm | BrokenWire |  | Fair | No | Blown 8 amp junction found causing from vehicle accident, blown fuse was replaced and area now with supply
Non-Outage | J.E.26.07.20666 | C001858905 | Neville Spencer | Clarendon | Completed | Load_246254 | May Pen - 110 | Jul 19, 2026 10:16am | Jul 19, 2026 10:28am | Jul 19, 2026 12:09pm | Jul 19, 2026 12:09pm | Jul 19, 2026 12:09pm | Jul 19, 2026 12:20pm | Jul 19, 2026 12:21pm | Jul 19, 2026 12:21pm |  |  | Fair | No | Found ok.
Non-Outage | J.E.26.07.21257 | C001858906 | Clyde Brown | Clarendon | Completed | Load_257058 | Monymusk - 410 | Jul 19, 2026 10:16am | Jul 19, 2026 10:28am | Jul 19, 2026 10:44am | Jul 19, 2026 2:37pm | Jul 19, 2026 2:43pm | Jul 19, 2026 2:42pm | Jul 19, 2026 2:47pm | Jul 19, 2026 2:47pm |  |  | Fair | No | Cannot be located customer not answering phone
Non-Outage | J.E.26.07.21532 | C001858907 | Clyde Brown | Clarendon | Completed | Load_570300 | Parnassus - 310 | Jul 19, 2026 10:16am | Jul 19, 2026 10:28am | Jul 19, 2026 10:44am | Jul 19, 2026 7:51pm | Jul 19, 2026 7:51pm | Jul 19, 2026 7:49pm | Jul 19, 2026 7:54pm | Jul 19, 2026 7:54pm |  |  | Fair | No | Cannot be located customer not answering phone
Non-Outage | J.E.26.07.20619 | C001858904 | Clyde Brown | Clarendon | Completed | Load_247306 | Monymusk - 410 | Jul 19, 2026 10:15am | Jul 19, 2026 10:17am | Jul 19, 2026 10:44am | Jul 19, 2026 2:07pm | Jul 19, 2026 2:07pm | Jul 19, 2026 2:28pm | Jul 19, 2026 2:37pm | Jul 19, 2026 2:37pm |  |  | Fair | No | Secondary phase lead burnt in clamp,open 25 kva transformer and change defective clamp,voltage left 108/104 and 112V
Non-Outage | J.E.26.06.17732 | C001858901 | Barnett Brown | null | Completed | null | null | Jul 19, 2026 10:14am | Jul 19, 2026 1:38pm | Jul 19, 2026 5:11pm | Jul 19, 2026 5:11pm | Jul 19, 2026 7:13pm | Jul 19, 2026 7:29pm | Jul 19, 2026 7:30pm | Jul 19, 2026 7:30pm | LeaningPole |  | Fair | No | Premises found ok
Non-Outage | J.E.26.07.20225 | C001858902 | Hartley Chin | Clarendon | Completed | Load_251963 | May Pen - 110 | Jul 19, 2026 10:14am | Jul 20, 2026 8:28am | Jul 20, 2026 10:16am | Jul 20, 2026 10:16am | Jul 20, 2026 10:19am | Jul 20, 2026 11:01am | Jul 20, 2026 11:04am | Jul 20, 2026 11:04am |  |  | Fair | No | Found 172v on a 110 customer after making checks found a broken neutral jumper. Jumper repair with bolt camps and reading nw 111v
Non-Outage | J.E.26.07.20326 | C001858903 | Clyde Brown | Clarendon | Completed | Load_247306 | Monymusk - 410 | Jul 19, 2026 10:14am | Jul 19, 2026 1:48pm | Jul 19, 2026 2:47pm | Jul 19, 2026 2:47pm | Jul 19, 2026 2:47pm | Jul 19, 2026 2:28pm | Jul 19, 2026 2:51pm | Jul 19, 2026 2:51pm |  |  | Fair | No | Burnt out one bolt clamp for 25 kva transformer open transformer and replaced clamp,voltage left 108/104 and 212V
Non-Outage | J.E.26.07.20443 | C001858896 | Neville Spencer | Clarendon | Completed | Load_246095 | May Pen - 110 | Jul 19, 2026 10:11am | Jul 19, 2026 10:18am | Jul 19, 2026 10:59am | Jul 19, 2026 10:59am | Jul 19, 2026 11:50am | Jul 19, 2026 11:51am | Jul 19, 2026 12:06pm | Jul 19, 2026 12:06pm | Fire |  | Fair | No | Found 35 c6 wooden pole broken off at root construction TA with single phase primary and open secondary POLE Need To Replace Urgently.
Non-Outage | J.E.26.07.20461 | C001858897 | Neville Spencer | Clarendon | Completed | Load_270252 | May Pen - 110 | Jul 19, 2026 10:11am | Jul 19, 2026 10:18am | Jul 19, 2026 12:07pm | Jul 19, 2026 12:07pm | Jul 19, 2026 12:07pm | Jul 19, 2026 12:07pm | Jul 19, 2026 12:08pm | Jul 19, 2026 12:08pm | Fire |  | Fair | No | Found 35 c6 wooden pole broken off at root construction T A with single phase primary and open secondary pole need to replace urgently.
Non-Outage | J.E.26.07.21597 | C001858898 | Clyde Brown | Clarendon | Completed | Load_265898 | Parnassus - 310 | Jul 19, 2026 10:11am | Jul 19, 2026 10:17am | Jul 19, 2026 10:44am | Jul 19, 2026 2:51pm | Jul 19, 2026 4:33pm | Jul 19, 2026 4:30pm | Jul 19, 2026 4:40pm | Jul 19, 2026 4:40pm | BrokenWire |  | Fair | No | Defective service 3 wire service same replaced with 70ft-#6 triplex service with 3 one bolt clamp.
Non-Outage | J.E.26.07.18838 | C001858893 | Rusean Allen | null | Completed | null | null | Jul 19, 2026 10:04am | Jul 19, 2026 10:06am | Jul 19, 2026 11:52am | Jul 19, 2026 11:52am | Jul 19, 2026 12:08pm | Jul 19, 2026 12:08pm | Jul 19, 2026 12:08pm | Jul 19, 2026 12:08pm | BrokenPole |  | Fair | No | Found okay
Non-Outage | J.E.26.07.20166 | C001858892 | Fitzroy Turner | KSAS | Completed | Load_265032 | Hunts Bay - 710 | Jul 19, 2026 10:04am | Jul 19, 2026 10:05am | Jul 19, 2026 10:39am | Jul 19, 2026 10:39am | Jul 19, 2026 11:06am | Jul 19, 2026 11:15am | Jul 19, 2026 11:17am | Jul 19, 2026 11:17am | BrokenPole |  | Fair | No | Found 40/4 wooden pole crock up but not in any danger at this time.checked at a later date
Non-Outage | J.E.26.07.19835 | C001858889 | Fitzroy Turner | null | Completed | null | null | Jul 19, 2026 10:03am | Jul 19, 2026 10:06am | Jul 19, 2026 11:40am | Jul 19, 2026 11:57am | Jul 19, 2026 11:57am | Jul 19, 2026 1:03pm | Jul 19, 2026 1:05pm | Jul 19, 2026 1:05pm | BrokenWire |  | Fair | No | Found some twisted secondary hanging low needs to transfer to other pole from old pole
Non-Outage | J.E.26.07.20321 | C001858884 | Fredrick Hamilton | KSAN | Completed | Load_246522 | Washington Blvd - 710 | Jul 19, 2026 10:02am | Jul 20, 2026 8:33am | Jul 20, 2026 8:46am | Jul 20, 2026 10:28am | Jul 20, 2026 10:49am | Jul 20, 2026 10:51am | Jul 20, 2026 10:51am | Jul 20, 2026 10:51am | Fire |  | Fair | No | Location found ok at time of visit no banging wires or low hanging wires seen
Non-Outage | J.E.26.07.20774 | C001858885 | Rusean Allen | KSAS | Completed | Load_246603 | Cane River - 610 | Jul 19, 2026 10:02am | Jul 19, 2026 10:06am | Jul 19, 2026 1:19pm | Jul 19, 2026 1:19pm | Jul 19, 2026 1:29pm | Jul 19, 2026 1:30pm | Jul 19, 2026 1:30pm | Jul 19, 2026 1:30pm | Fire |  | Fair | No | Found okay
Non-Outage | J.E.26.07.20847 | C001858886 | Fitzroy Turner | null | Completed | null | null | Jul 19, 2026 10:02am | Jul 19, 2026 10:07am | Jul 19, 2026 11:52am | Jul 19, 2026 11:53am | Jul 19, 2026 11:53am | Jul 19, 2026 11:54am | Jul 19, 2026 11:57am | Jul 19, 2026 11:57am | Fire |  | Fair | No | Checked location and there no wires found at the location
Non-Outage | J.E.26.07.20893 | C001858887 | Fredrick Hamilton | KSAN | Completed | Load_259850 | Washington Blvd - 310 | Jul 19, 2026 10:02am | Jul 20, 2026 8:32am | Jul 20, 2026 8:46am | Jul 20, 2026 11:37am | Jul 20, 2026 11:38am | Jul 20, 2026 11:51am | Jul 20, 2026 11:51am | Jul 20, 2026 11:51am | Illegal connections at pole and loose banging wires |  | Fair | No | 222v/120v/100v obtained Low voltage detected,Burt wire at pole recommend switcher to isolate and correct same
Non-Outage | J.E.26.07.00220 | C001858882 | Rusean Allen | KSAS | Completed | Load_239260 | Hunts Bay - 210 | Jul 19, 2026 10:01am | Jul 19, 2026 10:07am | Jul 19, 2026 11:42am | Jul 19, 2026 11:42am | Jul 19, 2026 11:51am | Jul 19, 2026 11:51am | Jul 19, 2026 11:52am | Jul 19, 2026 11:52am | Fire |  | Fair | No | Found okay
Non-Outage | J.E.26.07.00276 | C001858883 | Fitzroy Turner | KSAS | Completed | Load_261859 | Hunts Bay - 210 | Jul 19, 2026 10:01am | Jul 19, 2026 10:07am | Jul 19, 2026 11:18am | Jul 19, 2026 11:24am | Jul 19, 2026 11:52am | Jul 19, 2026 11:53am | Jul 19, 2026 11:53am | Jul 19, 2026 11:53am | Fire |  | Fair | No | Customer premises found with electricity supply electrician carry out repairs
Outage | J.E.26.07.21626 | C001858880 | Richard Samuda | Manchester | Completed | Load_241372 | Spur Tree - 310 | Jul 19, 2026 9:58am | Jul 19, 2026 9:58am | Jul 19, 2026 10:11am | Jul 19, 2026 10:29am | Jul 19, 2026 10:46am | Jul 19, 2026 11:19am | Jul 19, 2026 11:19am | Jul 19, 2026 11:19am | Fire |  | Fair | No | Use switch stick to remove cut tree off secondary line that cause to bang and fire in area customer back to normal
Outage | J.E.26.07.21622 | C001858879 | Wayne Dillion | Manchester | Completed | Load_303002 | Spur Tree - 210 | Jul 19, 2026 9:50am | Jul 19, 2026 9:51am | Jul 19, 2026 11:10am | Jul 19, 2026 11:10am | Jul 19, 2026 11:10am | Jul 19, 2026 12:00pm | Jul 19, 2026 12:06pm | Jul 19, 2026 12:06pm |  |  | Fair | No | Reconnect customer service wire that was broken down by a truck using 80 feet of number 6 triplex 3 linket 3 one bolt clamp
Non-Outage | J.E.26.06.38586 | C001858878 | Wayne Dillion | St.Elizabeth | Completed | Load_249630 | Maggotty - 210 | Jul 19, 2026 9:48am | Jul 19, 2026 9:49am | Jul 19, 2026 10:22am | Jul 19, 2026 10:22am | Jul 19, 2026 10:22am | Jul 19, 2026 10:23am | Jul 19, 2026 10:23am | Jul 19, 2026 10:23am | Fire |  | Fair | No | Premises not found customer phone not working
Non-Outage | J.E.26.06.35177 | C001858877 | Wayne Dillion | St.Elizabeth | Completed | Load_269827 | Maggotty - 210 | Jul 19, 2026 9:47am | Jul 19, 2026 9:49am | Jul 19, 2026 10:25am | Jul 19, 2026 10:25am | Jul 19, 2026 10:25am | Jul 19, 2026 10:26am | Jul 19, 2026 10:26am | Jul 19, 2026 10:26am | BrokenWire |  | Fair | No | Customer said supply ok
Non-Outage | J.E.26.03.11821 | C001858873 | Wayne Dillion | Manchester | Completed | Load_292761 | Spur Tree - 210 | Jul 19, 2026 9:46am | Jul 19, 2026 9:49am | Jul 19, 2026 10:19am | Jul 19, 2026 10:19am | Jul 19, 2026 10:19am | Jul 19, 2026 10:20am | Jul 19, 2026 10:20am | Jul 19, 2026 10:20am | Fire |  | Fair | No | Customer phone no working and premises not found
Non-Outage | J.E.26.05.27095 | C001858876 | Wayne Dillion | St.Elizabeth | Completed | Load_270094 | Maggotty - 210 | Jul 19, 2026 9:46am | Jul 19, 2026 9:49am | Jul 19, 2026 10:17am | Jul 19, 2026 10:17am | Jul 19, 2026 10:17am | Jul 19, 2026 10:18am | Jul 19, 2026 10:18am | Jul 19, 2026 10:18am | Fire |  | Fair | No | Customer said supply ok
Outage | J.E.26.07.21565 | C001858874 | Neville Spencer | St.Ann | Completed | Load_256560 | Cardiff Hall - 310 | Jul 19, 2026 9:46am | Jul 19, 2026 9:47am | Jul 19, 2026 3:18pm | Jul 19, 2026 3:18pm | Jul 19, 2026 4:06pm | Jul 19, 2026 4:08pm | Jul 19, 2026 4:08pm | Jul 19, 2026 4:08pm |  |  | Fair | No | Customer not located.
Non-Outage | J.E.26.06.22301 | C001858872 | Barnett Brown | null | Completed | null | null | Jul 19, 2026 9:41am | Jul 19, 2026 9:41am | Jul 19, 2026 9:56am | Jul 19, 2026 9:56am | Jul 19, 2026 11:00am | Jul 19, 2026 11:09am | Jul 19, 2026 11:12am | Jul 19, 2026 11:12am | BrokenPole |  | Fair | No | Premises found ok, call was already dealt with.
Outage | J.E.26.07.21578 | C001858870 | Collin Robinson | Portland | Completed | Load_268045 | Port Antonio - 410 | Jul 19, 2026 9:39am | Jul 19, 2026 9:48am | Jul 19, 2026 10:27am | Jul 19, 2026 10:27am | Jul 19, 2026 10:27am | Jul 19, 2026 10:30am | Jul 19, 2026 10:30am | Jul 19, 2026 10:30am |  |  | Fair | No | Unable to locate customer
Non-Outage | J.E.26.07.14494 | C001858869 | Barnett Brown | Manchester | Completed | Load_255863 | Kendal - 210 | Jul 19, 2026 9:37am | Jul 19, 2026 9:38am | Jul 19, 2026 9:31pm | Jul 19, 2026 9:31pm | Jul 19, 2026 10:29pm | Jul 19, 2026 10:29pm | Jul 19, 2026 11:04pm | Jul 19, 2026 11:04pm | BrokenWire |  | Fair | No | Overhead guy pole supporting 35 class 6 with single phase primary and secondary rotten and broken at root and need to be change
Outage | J.E.26.07.21611 | C001858868 | Edward Royal | KSAN | Completed | Load_252084 | Constant Spring - 310 | Jul 19, 2026 9:35am | Jul 19, 2026 9:35am | Jul 19, 2026 9:46am | Jul 19, 2026 9:46am | Jul 19, 2026 9:56am | Jul 19, 2026 10:44am | Jul 19, 2026 10:44am | Jul 19, 2026 10:44am | Fire |  | Fair | No | Defective fuse holder replaced fuse holder with 10A fuse . The switch is not hundred need to replace soon pole # 0034536
Non-Outage | J.E.26.07.16103 | C001858867 | Barnett Brown | Manchester | Completed | Load_239350 | Kendal - 210 | Jul 19, 2026 9:34am | Jul 19, 2026 9:36am | Jul 19, 2026 11:14am | Jul 19, 2026 11:14am | Jul 19, 2026 12:10pm | Jul 19, 2026 12:21pm | Jul 19, 2026 12:27pm | Jul 19, 2026 12:27pm | LeaningPole |  | Fair | No | Customer is concern about secondary pole that was already changed off to new pole but pole has cable wires on it.
Non-Outage | J.E.26.06.27045 | C001858865 | Barnett Brown | Manchester | Completed | Load_248128 | Kendal - 210 | Jul 19, 2026 9:32am | Jul 19, 2026 9:32am | Jul 19, 2026 7:30pm | Jul 19, 2026 7:30pm | Jul 19, 2026 9:24pm | Jul 19, 2026 9:24pm | Jul 19, 2026 9:30pm | Jul 19, 2026 9:30pm | LeaningPole |  | Fair | No | Premises found ok
Non-Outage | J.E.26.06.32693 | C001858866 | Barnett Brown | Manchester | Completed | Load_251321 | Kendal - 210 | Jul 19, 2026 9:32am | Jul 19, 2026 9:32am | Jul 19, 2026 12:29pm | Jul 19, 2026 12:29pm | Jul 19, 2026 1:57pm | Jul 19, 2026 2:13pm | Jul 19, 2026 2:19pm | Jul 19, 2026 2:19pm | LeaningPole |  | Fair | No | Overhead guy pole supporting 35 class 6 TA is rotten at root and needs to be cleaned
Non-Outage | J.E.26.06.17781 | C001858864 | Barnett Brown | Manchester | Completed | Load_264065 | Kendal - 210 | Jul 19, 2026 9:31am | Jul 19, 2026 9:32am | Jul 19, 2026 2:26pm | Jul 19, 2026 2:27pm | Jul 19, 2026 4:33pm | Jul 19, 2026 4:33pm | Jul 19, 2026 5:11pm | Jul 19, 2026 5:11pm | LowHangingWires,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Premises found ok
Outage | J.E.26.07.21603 | C001858862 | Christopher Edwards | KSAN | Completed | Load_269590 | Constant Spring - 410 | Jul 19, 2026 9:29am | Jul 19, 2026 9:30am | Jul 19, 2026 10:53am | Jul 19, 2026 10:53am | Jul 19, 2026 11:45am | Jul 19, 2026 3:13pm | Jul 19, 2026 3:14pm | Jul 19, 2026 3:14pm |  |  | Fair | No | Blown junction fuseArea requires primary bushing Vegetation is too thick to gain access to where to primary line runs through the hill side
Non-Outage | J.E.25.12.09742 | C001858861 | Richard Samuda | Manchester | Completed | Load_244314 | Spur Tree - 210 | Jul 19, 2026 9:25am | Jul 19, 2026 9:26am | Jul 19, 2026 1:52pm | Jul 19, 2026 1:52pm | Jul 19, 2026 1:52pm | Jul 19, 2026 1:57pm | Jul 19, 2026 1:57pm | Jul 19, 2026 1:57pm | BrokenPoleg S |  | Fair | No | Premises not located and call to check no answer
Non-Outage | J.E.26.01.38347 | C001858859 | Rayon Foster | null | Completed | null | null | Jul 19, 2026 9:03am | Jul 19, 2026 9:04am | Jul 19, 2026 10:06am | Jul 19, 2026 1:15pm | Jul 19, 2026 1:15pm | Jul 19, 2026 1:21pm | Jul 19, 2026 1:22pm | Jul 19, 2026 1:22pm | LowHangingWires |  | Fair | No | Over sea phone attach unable to reach not enough driving detail
Non-Outage | J.E.26.01.26364 | C001858858 | Oshane Warren | Westmoreland | Completed | Load_246442 | Orange Bay - 310 | Jul 19, 2026 9:01am | Jul 19, 2026 9:02am | Jul 19, 2026 9:48am | Jul 19, 2026 9:48am | Jul 19, 2026 9:48am | Jul 19, 2026 9:49am | Jul 19, 2026 9:49am | Jul 19, 2026 9:49am | LeaningPole |  | Fair | No | Check and found ok
Non-Outage | J.E.26.01.36773 | C001858857 | Oshane Warren | null | Completed | null | null | Jul 19, 2026 9:01am | Jul 19, 2026 9:02am | Jul 19, 2026 9:46am | Jul 19, 2026 9:46am | Jul 19, 2026 9:46am | Jul 19, 2026 9:46am | Jul 19, 2026 9:47am | Jul 19, 2026 9:47am | LeaningPole |  | Fair | No | Unable to locate or contact customer need direction
Non-Outage | J.E.26.02.24481 | C001858856 | Richman Whyte | Westmoreland | Completed | Load_257730 | Paradise - 310 | Jul 19, 2026 9:00am | Jul 19, 2026 9:01am | Jul 19, 2026 10:26am | Jul 19, 2026 10:26am | Jul 19, 2026 10:26am | Jul 19, 2026 10:26am | Jul 19, 2026 10:27am | Jul 19, 2026 10:27am | LeaningPole |  | Fair | No | Check and found ok
Non-Outage | J.E.26.02.11430 | C001858853 | Rayon Foster | null | Completed | null | null | Jul 19, 2026 8:56am | Jul 19, 2026 8:57am | Jul 19, 2026 10:16am | Jul 19, 2026 11:44am | Jul 19, 2026 11:59am | Jul 19, 2026 12:11pm | Jul 19, 2026 12:11pm | Jul 19, 2026 12:11pm | BrokenWire |  | Fair | No | Customer said issue was resolved Weseks ago by a jps team
Non-Outage | J.E.26.02.34561 | C001858854 | Rayon Foster | Westmoreland | Completed | Load_247022 | Orange Bay - 210 | Jul 19, 2026 8:56am | Jul 19, 2026 8:57am | Jul 19, 2026 10:05am | Jul 19, 2026 10:05am | Jul 19, 2026 11:30am | Jul 19, 2026 11:41am | Jul 19, 2026 11:41am | Jul 19, 2026 11:41am | BrokenWire |  | Fair | No | Customer said the issue was resolved from February
Non-Outage | J.E.26.04.31913 | C001858855 | Rayon Foster | Westmoreland | Completed | Load_239066 | Paradise - 210 | Jul 19, 2026 8:56am | Jul 19, 2026 8:57am | Jul 19, 2026 10:07am | Jul 19, 2026 1:06pm | Jul 19, 2026 1:06pm | Jul 19, 2026 1:14pm | Jul 19, 2026 1:14pm | Jul 19, 2026 1:14pm | BrokenPole |  | Fair | No | Leaning 30ft DV pole with two guy attach open secondary and one street light pole ratten at foot refer to maintenance
Non-Outage | J.E.26.04.24866 | C001858852 | Richman Whyte | Westmoreland | Completed | Load_246884 | Paradise - 310 | Jul 19, 2026 8:55am | Jul 19, 2026 8:55am | Jul 19, 2026 10:28am | Jul 19, 2026 10:28am | Jul 19, 2026 10:28am | Jul 19, 2026 10:28am | Jul 19, 2026 10:29am | Jul 19, 2026 10:29am | BrokenWire |  | Fair | No | Check and found okay
Outage | J.E.26.07.21566 | C001858850 | Christopher Edwards | KSAN | Completed | Load_257226 | Constant Spring - 410 | Jul 19, 2026 8:24am | Jul 20, 2026 7:24am | Jul 20, 2026 11:16am | Jul 20, 2026 11:23am | Jul 20, 2026 12:18pm | Jul 20, 2026 12:40pm | Jul 20, 2026 12:41pm | Jul 20, 2026 12:41pm |  |  | Fair | No | Check and found okSupply is at the premises
Outage | J.E.26.07.21565 | C001858849 | Roxroy Needham | St.Ann | Completed | Load_256560 | Cardiff Hall - 310 | Jul 19, 2026 8:22am | Jul 19, 2026 8:25am | Jul 19, 2026 9:45am | Jul 19, 2026 9:45am | Jul 19, 2026 9:45am | Jul 19, 2026 9:42am | Jul 19, 2026 9:47am | Jul 19, 2026 9:47am |  |  | Fair | No | Call is not for st ann
Outage | J.E.26.07.21569 | C001858848 | Roxroy Needham | St.Ann | Completed | Load_264725 | Cardiff Hall - 310 | Jul 19, 2026 8:22am | Jul 19, 2026 8:25am | Jul 19, 2026 9:47am | Jul 19, 2026 9:48am | Jul 19, 2026 9:48am | Jul 19, 2026 9:49am | Jul 19, 2026 9:52am | Jul 19, 2026 9:52am |  |  | Fair | No | Call is not for st ann
Outage | J.E.26.07.21561 | C001858846 | Marlon Authors | Manchester | Completed | Load_240804 | Spur Tree - 210 | Jul 19, 2026 8:19am | Jul 19, 2026 8:20am | Jul 19, 2026 9:05am | Jul 19, 2026 9:05am | Jul 19, 2026 10:07am | Jul 19, 2026 10:47am | Jul 19, 2026 10:47am | Jul 19, 2026 10:47am |  |  | Fair | No | Patrol and found clear. Replace one blown 15 amp junction fuse no pole #. Restored supply ok
Outage | J.E.26.07.21404 | C001858845 | Wan Carlos Scarlett | Portmore | Completed | Load_257303 | Naggo Head - 510 | Jul 19, 2026 8:18am | Jul 19, 2026 8:21am | Jul 19, 2026 11:06am | Jul 19, 2026 11:37am | Jul 19, 2026 11:37am | Jul 19, 2026 11:37am | Jul 19, 2026 11:41am | Jul 19, 2026 11:41am |  |  | Fair | No | Found HEXING service box customer having issues with power supply going in and out coming from the hexing.Call refer to Moses
Outage | J.E.26.07.21434 | C001858844 | Nickolas Rodriques | Portmore | Completed | Load_239843 | Naggo Head - 610 | Jul 19, 2026 8:18am | Jul 19, 2026 11:50am | Jul 19, 2026 4:30pm | Jul 19, 2026 5:01pm | Jul 19, 2026 5:31pm | Jul 19, 2026 6:40pm | Jul 19, 2026 6:43pm | Jul 19, 2026 6:43pm |  |  | Fair | No | Unable to proceed, as access to the meter is restricted by a locked electric gate.
Outage | J.E.26.07.21437 | C001858843 | Ricky Hall | St.Catherine | Completed | Load_251932 | Twickenham - 210 | Jul 19, 2026 8:18am | Jul 19, 2026 8:24am | Jul 19, 2026 9:03am | Jul 19, 2026 10:29am | Jul 19, 2026 10:29am | Jul 19, 2026 10:29am | Jul 19, 2026 10:33am | Jul 19, 2026 10:33am |  |  | Fair | No | Call associated with outage #21322
Outage | J.E.26.07.21445 | C001858842 | Nickolas Rodriques | Portmore | Completed | Load_300752 | Naggo Head - 610 | Jul 19, 2026 8:18am | Jul 20, 2026 8:00am | Jul 20, 2026 12:03pm | Jul 20, 2026 12:22pm | Jul 20, 2026 12:49pm | Jul 20, 2026 12:52pm | Jul 20, 2026 1:03pm | Jul 20, 2026 1:03pm |  |  | Fair | No | Found premises locked. Unable to communicate with the customer after several attempts. Hexing customer (hex00412).
Outage | J.E.26.07.21526 | C001858840 | Wan Carlos Scarlett | Portmore | Completed | Load_243287 | Naggo Head - 510 | Jul 19, 2026 8:18am | Jul 19, 2026 8:21am | Jul 19, 2026 11:06am | Jul 19, 2026 2:41pm | Jul 19, 2026 3:31pm | Jul 19, 2026 3:35pm | Jul 19, 2026 3:36pm | Jul 19, 2026 3:36pm |  |  | Fair | No | Customer confirm that power supply has been restored
Outage | J.E.26.07.21535 | C001858838 | Wan Carlos Scarlett | Portmore | Completed | Load_237810 | Naggo Head - 510 | Jul 19, 2026 8:17am | Jul 19, 2026 8:21am | Jul 19, 2026 8:45am | Jul 19, 2026 8:45am | Jul 19, 2026 10:29am | Jul 19, 2026 11:20am | Jul 19, 2026 11:22am | Jul 19, 2026 11:22am |  |  | Fair | No | Refuse 2,40amp junction pole # 016275 clear bird from off primary line
Outage | J.E.26.07.21558 | C001858837 | Wan Carlos Scarlett | St.Catherine | Completed | Load_248359 | Twickenham - 210 | Jul 19, 2026 8:17am | Jul 19, 2026 8:21am | Jul 19, 2026 11:42am | Jul 19, 2026 11:42am | Jul 19, 2026 11:55am | Jul 19, 2026 12:48pm | Jul 19, 2026 12:49pm | Jul 19, 2026 12:49pm |  |  | Fair | No | Found customer 3 wire service at pole with one of the phase broken off use 3 one bolt clamps at open secondary line phase and neutral readings 116-115-231
Outage | J.E.26.07.21485 | C001858836 | Nickolas Rodriques | St.Catherine | Completed | Load_242971 | Twickenham - 310 | Jul 19, 2026 8:11am | Jul 19, 2026 8:13am | Jul 19, 2026 8:25am | Jul 19, 2026 8:33am | Jul 19, 2026 9:48am | Jul 19, 2026 10:28am | Jul 19, 2026 10:37am | Jul 19, 2026 10:37am |  |  | Fair | No | Unable to locate or communicate with the customer after several attempts. (Need proper direction)
Outage | J.E.26.07.21322 | C001858835 | Ricky Hall | St.Catherine | Completed | Load_245276 | Tredegar - 210 | Jul 19, 2026 8:05am | Jul 19, 2026 8:14am | Jul 19, 2026 9:06am | Jul 19, 2026 9:06am | Jul 19, 2026 10:04am | Jul 19, 2026 10:28am | Jul 19, 2026 10:28am | Jul 19, 2026 10:28am |  |  | Fair | No | Issue was resolved on previous shift
Outage | J.E.26.07.21457 | C001858834 | Donald Cunningham | St.Catherine | Completed | Load_244637 | New Michelton - 210 | Jul 19, 2026 8:05am | Jul 19, 2026 8:11am | Jul 19, 2026 2:06pm | Jul 19, 2026 3:22pm | Jul 19, 2026 3:22pm | Jul 19, 2026 3:23pm | Jul 19, 2026 3:26pm | Jul 19, 2026 3:26pm |  |  | Rains | No | Not located customer stated the call is for Kingston she was advised
Outage | J.E.26.07.21528 | C001858833 | Donald Cunningham | St.Catherine | Completed | Load_568213 | New Michelton - 210 | Jul 19, 2026 8:04am | Jul 19, 2026 8:11am | Jul 19, 2026 11:14am | Jul 19, 2026 11:14am | Jul 19, 2026 12:00pm | Jul 19, 2026 12:00pm | Jul 19, 2026 12:06pm | Jul 19, 2026 12:06pm |  |  | Fair | No | Supply restored
Outage | J.E.26.07.21529 | C001858832 | Donald Cunningham | St.Catherine | Completed | Load_248615 | New Michelton - 210 | Jul 19, 2026 8:04am | Jul 19, 2026 8:11am | Jul 19, 2026 8:48am | Jul 19, 2026 8:48am | Jul 19, 2026 11:05am | Jul 19, 2026 11:05am | Jul 19, 2026 11:11am | Jul 19, 2026 11:11am |  |  | Fair | No | Premises closed
Non-Outage | J.E.26.07.19971 | C001858830 | Rusean Allen | null | Completed | null | null | Jul 19, 2026 7:58am | Jul 19, 2026 8:02am | Jul 19, 2026 1:05pm | Jul 19, 2026 1:05pm | Jul 19, 2026 1:17pm | Jul 19, 2026 1:18pm | Jul 19, 2026 1:18pm | Jul 19, 2026 1:18pm |  |  | Fair | No | Corroded wires were found at pothead, wires were disconnected and reconnected with one bolt clamps. Voltage: 117 117 235
Non-Outage | J.E.26.07.21205 | C001858829 | Rusean Allen | null | Completed | null | null | Jul 19, 2026 7:57am | Jul 19, 2026 8:00am | Jul 19, 2026 10:33am | Jul 19, 2026 10:33am | Jul 19, 2026 11:37am | Jul 19, 2026 11:41am | Jul 19, 2026 11:41am | Jul 19, 2026 11:41am | Fire |  | Fair | No | Related to defective transformer in torriton park. outage #21334
Outage | J.E.26.07.21091 | C001858828 | Rusean Allen | KSAS | Completed | Load_250430 | Up Park Camp - 510 | Jul 19, 2026 7:53am | Jul 19, 2026 8:00am | Jul 19, 2026 12:18pm | Jul 19, 2026 12:18pm | Jul 19, 2026 12:23pm | Jul 19, 2026 12:25pm | Jul 19, 2026 12:26pm | Jul 19, 2026 12:26pm | LeaningPole |  | Fair | No | Pole is of telecommunications company.
Outage | J.E.26.07.21390 | C001858827 | Rusean Allen | KSAS | Completed | Load_257086 | Up Park Camp - 510 | Jul 19, 2026 7:51am | Jul 19, 2026 8:00am | Jul 19, 2026 12:26pm | Jul 19, 2026 12:26pm | Jul 19, 2026 12:36pm | Jul 19, 2026 12:44pm | Jul 19, 2026 12:44pm | Jul 19, 2026 12:44pm |  |  | Fair | No | Meter found disconnected at meter socket, meter was reconnected.
Outage | J.E.26.07.18964 | C001858826 | Fitzroy Turner | KSAS | Completed | Load_255982 | Three Miles - 510 | Jul 19, 2026 7:47am | Jul 19, 2026 7:49am | Jul 19, 2026 9:16am | Jul 19, 2026 9:19am | Jul 19, 2026 9:57am | Jul 19, 2026 10:20am | Jul 19, 2026 10:20am | Jul 19, 2026 10:20am |  |  | Fair | No | Customer premises found with electricity supply
Non-Outage | J.E.26.07.21102 | C001858824 | Milton Charlton | null | Completed | null | null | Jul 19, 2026 7:43am | Jul 19, 2026 7:43am | Jul 19, 2026 9:38am | Jul 19, 2026 9:39am | Jul 19, 2026 9:47am | Jul 19, 2026 9:40am | Jul 19, 2026 9:51am | Jul 19, 2026 9:51am | BrokenPole |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.07.21140 | C001858823 | Milton Charlton | KSAS | Completed | Load_248546 | Duhaney - 310 | Jul 19, 2026 7:43am | Jul 19, 2026 5:06pm | Jul 19, 2026 6:29pm | Jul 19, 2026 6:29pm | Jul 19, 2026 7:33pm | Jul 19, 2026 7:40pm | Jul 19, 2026 7:36pm | Jul 19, 2026 7:36pm |  |  | Fair | No | Customer service wire #6 triplex phase burn off at pole. Repair using one 1- bolt clamp. Readings at meter socket 116-115-234 volts.
Outage | J.E.26.07.21285 | C001858822 | Christopher Edwards | KSAN | Completed | Load_240374 | Constant Spring - 210 | Jul 19, 2026 7:43am | Jul 19, 2026 9:34am | Jul 19, 2026 10:01am | Jul 19, 2026 10:04am | Jul 19, 2026 10:24am | Jul 19, 2026 10:53am | Jul 19, 2026 10:53am | Jul 19, 2026 10:53am |  |  | Fair | No | Remake burnt neutral joint at poleUsing (1) one bolt clamps Voltage,115,114,230v
Outage | J.E.26.07.21313 | C001858821 | Christopher Edwards | KSAN | Completed | Load_579095 | Constant Spring - 210 | Jul 19, 2026 7:43am | Jul 19, 2026 7:45am | Jul 19, 2026 8:06am | Jul 19, 2026 9:16am | Jul 19, 2026 9:42am | Jul 19, 2026 10:00am | Jul 19, 2026 10:00am | Jul 19, 2026 10:00am |  |  | Fair | No | Check and found okSupply is at the premises Voltage:115,116,230v
Outage | J.E.26.07.21393 | C001858814 | Roxroy Needham | St.Ann | Completed | Load_257906 | Cardiff Hall - 310 | Jul 19, 2026 7:42am | Jul 19, 2026 7:44am | Jul 19, 2026 9:54am | Jul 19, 2026 9:54am | Jul 19, 2026 9:55am | Jul 19, 2026 9:56am | Jul 19, 2026 9:57am | Jul 19, 2026 9:57am |  |  | Fair | No | Call is not for st ann
Outage | J.E.26.07.21410 | C001858820 | Edward Royal | KSAN | Completed | Load_253160 | Constant Spring - 210 | Jul 19, 2026 7:42am | Jul 19, 2026 7:45am | Jul 19, 2026 11:44am | Jul 19, 2026 11:44am | Jul 19, 2026 11:44am | Aug 6, 2026 11:11am | Jul 19, 2026 11:48am | Jul 19, 2026 11:48am |  |  | Fair | No | Spliced reconnected service cable #6 triplex using 3 one bolt clamps pole # 052821
Outage | J.E.26.07.21435 | C001858817 | Milton Charlton | KSAN | Completed | Load_262660 | West Kings House - 410 | Jul 19, 2026 7:42am | Jul 19, 2026 7:45am | Jul 19, 2026 9:53am | Jul 19, 2026 9:53am | Jul 19, 2026 10:52am | Jul 19, 2026 10:55am | Jul 19, 2026 12:05pm | Jul 19, 2026 12:05pm | BrokenWire |  | Fair | No | Customer service wire #6 triplex phases disconnected at ole. Reconnect using two 1- bolt clamps. Readings at meter socket 115-116-232 volts.
Outage | J.E.26.07.21490 | C001858818 | Edward Royal | KSAN | Completed | Load_265722 | Washington Blvd - 810 | Jul 19, 2026 7:42am | Jul 19, 2026 7:45am | Jul 19, 2026 2:05pm | Jul 19, 2026 2:05pm | Jul 19, 2026 2:05pm | Jul 19, 2026 2:06pm | Jul 19, 2026 2:07pm | Jul 19, 2026 2:07pm |  |  | Fair | No | Premises not found unable to communicate with customer
Outage | J.E.26.07.21133 | C001858810 | Romaine Roberts | St.Mary | Completed | Load_243461 | Highgate - 210 | Jul 19, 2026 7:40am | Jul 19, 2026 8:09am | Jul 19, 2026 10:35am | Jul 19, 2026 10:35am | Jul 19, 2026 10:48am | Jul 19, 2026 1:06pm | Jul 19, 2026 1:10pm | Jul 19, 2026 1:10pm |  | Y | Fair | No | High wind and vegetation bang secondary conductor and blow 25 kva transformer fuse carry out bushing to clear line replace 3 amp power restore
Outage | J.E.26.07.21383 | C001858808 | Fitzroy Turner | KSAN | Completed | Load_575448 | Washington Blvd - 710 | Jul 19, 2026 7:34am | Jul 19, 2026 7:35am | Jul 19, 2026 8:31am | Jul 19, 2026 8:31am | Jul 19, 2026 8:37am | Jul 19, 2026 8:38am | Jul 19, 2026 8:39am | Jul 19, 2026 8:39am |  |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.07.21540 | C001858807 | Fitzroy Turner | KSAS | Completed | Load_239323 | Duhaney - 410 | Jul 19, 2026 7:34am | Jul 19, 2026 7:35am | Jul 19, 2026 7:49am | Jul 19, 2026 7:49am | Jul 19, 2026 8:20am | Jul 19, 2026 8:25am | Jul 19, 2026 8:26am | Jul 19, 2026 8:26am |  |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.07.21541 | C001858806 | Fitzroy Turner | KSAS | Completed | Load_258681 | Three Miles - 410 | Jul 19, 2026 7:33am | Jul 19, 2026 7:35am | Jul 19, 2026 8:39am | Jul 19, 2026 8:39am | Jul 19, 2026 8:59am | Jul 19, 2026 9:14am | Jul 19, 2026 9:15am | Jul 19, 2026 9:15am |  |  | Fair | No | Found tree wire twisted secondary phases burnt off at pole cause by illegal connections use one clamp to carry out repair supply restored to areas
Outage | J.E.26.07.21355 | C001858804 | Roxroy Needham | St.Ann | Completed | Load_260641 | Cardiff Hall - 310 | Jul 19, 2026 7:26am | Jul 19, 2026 7:47am | Jul 19, 2026 9:58am | Jul 19, 2026 9:58am | Jul 19, 2026 11:32am | Jul 19, 2026 11:35am | Jul 19, 2026 11:36am | Jul 19, 2026 11:36am |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.07.21506 | C001858803 | Marlon Authors | Manchester | Completed | Load_556606 | Spur Tree - 210 | Jul 19, 2026 7:24am | Jul 19, 2026 7:26am | Jul 19, 2026 10:56am | Jul 19, 2026 10:56am | Jul 19, 2026 1:06pm | Jul 19, 2026 1:10pm | Jul 19, 2026 1:11pm | Jul 19, 2026 1:11pm |  |  | Fair | No | Customer has hexing meter at premises that is pre-paid and the CIU/ key pad is missing so the credit is unable to add to the account. Please refer same to the field services department for further assistance
Outage | J.E.26.07.21542 | C001858802 | Marlon Authors | Manchester | Completed | Load_268017 | Spur Tree - 210 | Jul 19, 2026 7:24am | Jul 19, 2026 7:26am | Jul 19, 2026 10:50am | Jul 19, 2026 10:50am | Jul 19, 2026 10:50am | Jul 19, 2026 10:54am | Jul 19, 2026 10:54am | Jul 19, 2026 10:54am |  |  | Fair | No | Supply restored to the area
Outage | J.E.26.07.21499 | C001858801 | Roxroy Needham | St.Ann | Completed | Load_1003292 | Cardiff Hall - 310 | Jul 19, 2026 2:45am | Jul 19, 2026 7:47am | Jul 19, 2026 9:52am | Jul 19, 2026 9:52am | Jul 19, 2026 9:52am | Jul 19, 2026 9:51am | Jul 19, 2026 9:53am | Jul 19, 2026 9:53am |  |  | Fair | No | Call is not for st ann
Outage | J.E.26.07.21493 | C001858800 | Edward Royal | KSAN | Completed | Load_245923 | Constant Spring - 410 | Jul 19, 2026 2:16am | Jul 19, 2026 2:16am | Jul 19, 2026 4:32am | Jul 19, 2026 4:32am | Jul 19, 2026 4:32am | Jul 19, 2026 4:32am | Jul 19, 2026 4:32am | Jul 19, 2026 4:32am |  |  | Fair | No | Premises not found unable to communicate with customer
Outage | J.E.26.07.21490 | C001858799 | Edward Royal | KSAN | Completed | Load_265722 | Washington Blvd - 810 | Jul 19, 2026 2:15am | Jul 19, 2026 2:16am | Jul 19, 2026 4:31am | Jul 19, 2026 4:31am | Jul 19, 2026 4:31am | Jul 19, 2026 4:31am | Jul 19, 2026 4:31am | Jul 19, 2026 4:31am |  |  | Fair | No | Premises found close unable to communicate with customer
Outage | J.E.26.07.21323 | C001858795 | Raymond Lewis | St.Ann | Completed | Load_248644 | Roaring River - 210 | Jul 18, 2026 11:01pm | Jul 18, 2026 11:02pm | Jul 18, 2026 11:31pm | Jul 18, 2026 11:31pm | Jul 18, 2026 11:31pm | Jul 18, 2026 11:32pm | Jul 18, 2026 11:33pm | Jul 18, 2026 11:33pm |  |  | Fair | No | Phone unavailable
Outage | J.E.26.07.21227 | C001858794 | Raymond Lewis | St.Ann | Completed | Load_255731 | Roaring River - 410 | Jul 18, 2026 11:00pm | Jul 18, 2026 11:02pm | Jul 18, 2026 11:35pm | Jul 18, 2026 11:35pm | Jul 18, 2026 11:35pm | Jul 18, 2026 11:37pm | Jul 18, 2026 11:38pm | Jul 18, 2026 11:38pm |  |  | Fair | No | Customer disconnected due to none payment
Outage | J.E.26.07.21286 | C001858792 | Raymond Lewis | St.Ann | Completed | Load_260731 | Roaring River - 210 | Jul 18, 2026 11:00pm | Jul 18, 2026 11:02pm | Jul 19, 2026 1:24am | Jul 19, 2026 1:24am | Jul 19, 2026 1:41am | Jul 19, 2026 1:42am | Jul 19, 2026 1:42am | Jul 19, 2026 1:42am |  |  | Fair | No | Customer phone is unavailable
Outage | J.E.26.07.21471 | C001858790 | Delano Gayle | St.Catherine | Completed | Load_557143 | Tredegar - 410 | Jul 18, 2026 10:56pm | Jul 18, 2026 10:58pm | Jul 19, 2026 12:25am | Jul 19, 2026 12:25am | Jul 19, 2026 12:38am | Jul 19, 2026 12:40am | Jul 19, 2026 12:40am | Jul 19, 2026 12:40am |  |  | Fair | No | Premises found okay related to call where 15amps junction fuse was replaced
Outage | J.E.26.07.21444 | C001858789 | Edward Royal | KSAN | Completed | Load_238279 | Constant Spring - 410 | Jul 18, 2026 10:51pm | Jul 18, 2026 10:54pm | Jul 19, 2026 4:53am | Jul 19, 2026 4:53am | Jul 19, 2026 4:53am | Jul 19, 2026 4:54am | Jul 19, 2026 4:54am | Jul 19, 2026 4:54am |  |  | Fair | No | Premises found close
Outage | J.E.26.07.21435 | C001858786 | Edward Royal | KSAN | Completed | Load_262660 | West Kings House - 410 | Jul 18, 2026 10:48pm | Jul 18, 2026 10:54pm | Jul 19, 2026 1:13am | Jul 19, 2026 1:13am | Jul 19, 2026 1:13am | Jul 19, 2026 1:14am | Jul 19, 2026 1:15am | Jul 19, 2026 1:15am | BrokenWire |  | Fair | No | When contacted customer said that no one at premises requesting daylight attention
Outage | J.E.26.07.21461 | C001858787 | Delano Gayle | St.Catherine | Completed | Load_239334 | Tredegar - 410 | Jul 18, 2026 10:48pm | Jul 18, 2026 10:52pm | Jul 18, 2026 11:02pm | Jul 18, 2026 11:02pm | Jul 18, 2026 11:34pm | Jul 19, 2026 12:22am | Jul 19, 2026 12:22am | Jul 19, 2026 12:22am |  |  | Fair | No | Blown junction on main no pole number, patrolled line section and found hexing transformer with H1 bushing defective, transformer spraying oil from bushing, replace 15amps at blown junction, transformer circuit remains without supply send call to maintenance/ field services
Outage | J.E.26.07.21378 | C001858782 | Andre Smith | KSAN | Completed | Load_574257 | Washington Blvd - 710 | Jul 18, 2026 9:12pm | Jul 18, 2026 9:13pm | Jul 18, 2026 10:40pm | Jul 18, 2026 10:40pm | Jul 18, 2026 10:49pm | Jul 18, 2026 10:50pm | Jul 18, 2026 10:50pm | Jul 18, 2026 10:50pm |  |  | Fair | No | Replace blown junction fuses 40A/2 cause by bird making contact with conductor supply restored
Outage | J.E.26.07.21342 | C001858780 | Omar King | St.Ann | Completed | Load_256334 | Ocho Rios - 310 | Jul 18, 2026 8:22pm | Jul 18, 2026 8:23pm | Jul 18, 2026 8:45pm | Jul 18, 2026 8:45pm | Jul 18, 2026 9:13pm | Jul 18, 2026 9:19pm | Jul 18, 2026 9:24pm | Jul 18, 2026 9:24pm |  |  | Fair | No | Found 20amp junction fuse blow cause by vegetation and the fuse has been replaced, the area is now with supply
Outage | J.E.26.07.21409 | C001858779 | Omar King | St.Ann | Completed | Load_312577 | Roaring River - 410 | Jul 18, 2026 8:22pm | Jul 18, 2026 8:23pm | Jul 18, 2026 9:25pm | Jul 18, 2026 9:25pm | Jul 18, 2026 10:03pm | Jul 18, 2026 10:09pm | Jul 18, 2026 10:11pm | Jul 18, 2026 10:11pm |  |  | Fair | No | Found a 25 KVA transformer defective I strongly believe load is a factor that cause transformer I recommend that transformer should upgrade to a 50 KVA
Outage | J.E.26.07.21419 | C001858778 | Raymond Lewis | St.Ann | Completed | Load_237920 | Roaring River - 410 | Jul 18, 2026 8:22pm | Jul 18, 2026 10:53pm | Jul 19, 2026 12:37am | Jul 19, 2026 12:37am | Jul 19, 2026 1:22am | Jul 19, 2026 1:23am | Jul 19, 2026 1:24am | Jul 19, 2026 1:24am |  |  | Fair | No | Customer phone unavailable
Outage | J.E.26.07.21420 | C001858777 | Collin Robinson | Portland | Completed | Load_241801 | Port Antonio - 310 | Jul 18, 2026 8:19pm | Jul 18, 2026 8:19pm | Jul 18, 2026 8:41pm | Jul 18, 2026 8:41pm | Jul 18, 2026 9:40pm | Jul 18, 2026 9:53pm | Jul 18, 2026 9:53pm | Jul 18, 2026 9:53pm |  |  | Fair | No | Remove illegal connection and reset 10KVA transformer pole at 0014642
Non-Outage | J.E.26.07.21416 | C001858775 | Collin Robinson | Portland | Completed | Load_242386 | Port Antonio - 410 | Jul 18, 2026 8:05pm | Jul 19, 2026 12:39pm | Jul 19, 2026 12:48pm | Jul 19, 2026 12:48pm | Jul 19, 2026 1:12pm | Jul 19, 2026 1:30pm | Jul 19, 2026 1:30pm | Jul 19, 2026 1:30pm |  |  | Fair | No | Change 3 corroded one bolt clamp at pole Voltage reading 116v 117v 233v
Outage | J.E.26.07.21405 | C001858774 | Oshane Warren | Hanover | Completed | Load_245791 | Orange Bay - 310 | Jul 18, 2026 7:47pm | Jul 18, 2026 7:48pm | Jul 18, 2026 8:24pm | Jul 18, 2026 8:24pm | Jul 18, 2026 10:56pm | Jul 18, 2026 10:59pm | Jul 18, 2026 11:00pm | Jul 18, 2026 11:00pm |  |  | Fair | No | 25 kva transformer Defective leaking oil needs to change refer to maintenance
Outage | J.E.26.07.21382 | C001858772 | Wayne Dillion | St.Elizabeth | Completed | Load_255118 | Maggotty - 210 | Jul 18, 2026 7:30pm | Jul 18, 2026 7:52pm | Jul 18, 2026 8:55pm | Jul 18, 2026 8:55pm | Jul 18, 2026 8:55pm | Jul 18, 2026 9:16pm | Jul 18, 2026 9:16pm | Jul 18, 2026 9:16pm |  |  | Fair | No | Patrol and found clear replace one 2 amp fuse that protects 15 KVA no pole number supply restore to customer successfully
Outage | J.E.26.07.21370 | C001858768 | Stephen Taylor | St.Thomas | Completed | Load_241803 | Good Year - 110 | Jul 18, 2026 6:57pm | Jul 18, 2026 6:59pm | Jul 19, 2026 1:41pm | Jul 19, 2026 1:41pm | Jul 19, 2026 4:12pm | Jul 19, 2026 4:15pm | Jul 19, 2026 4:18pm | Jul 19, 2026 4:18pm |  |  | Fair | No | Clean up transformer droplead and close up 25kva transformer all customer are now back in service
Outage | J.E.26.07.21335 | C001858767 | Horace Malcolm | St.James | Completed | Load_249364 | Rose Hall - 210 | Jul 18, 2026 6:55pm | Jul 18, 2026 6:56pm | Jul 18, 2026 7:32pm | Jul 18, 2026 7:51pm | Jul 18, 2026 8:08pm | Jul 18, 2026 8:16pm | Jul 18, 2026 8:16pm | Jul 18, 2026 8:16pm | Fire |  | Fair | No | Unable to locate premises from directions given multiple phone calls to customer unavailable
Outage | J.E.26.07.21337 | C001858766 | Michael Christian | St.James | Completed | Load_575161 | Bogue - 310 | Jul 18, 2026 6:55pm | Jul 18, 2026 6:56pm | Jul 18, 2026 7:01pm | Jul 18, 2026 7:01pm | Jul 18, 2026 7:50pm | Jul 18, 2026 8:13pm | Jul 18, 2026 8:13pm | Jul 18, 2026 8:13pm |  |  | Fair | No | Check and found okay voltage 111 113 225 at pothead
Outage | J.E.26.07.21353 | C001858765 | Horace Malcolm | St.James | Completed | Load_256619 | Rose Hall - 210 | Jul 18, 2026 6:55pm | Jul 18, 2026 6:56pm | Jul 18, 2026 7:32pm | Jul 18, 2026 7:33pm | Jul 18, 2026 7:50pm | Jul 18, 2026 7:51pm | Jul 18, 2026 7:51pm | Jul 18, 2026 7:51pm |  |  | Fair | No | Check and found ok
Outage | J.E.26.07.21356 | C001858760 | Christopher Edwards | KSAN | Completed | Load_260614 | Constant Spring - 410 | Jul 18, 2026 6:37pm | Jul 18, 2026 6:37pm | Jul 18, 2026 7:27pm | Jul 18, 2026 7:35pm | Jul 18, 2026 7:35pm | Jul 18, 2026 7:58pm | Jul 18, 2026 7:59pm | Jul 18, 2026 7:59pm |  |  | Fair | No | Refuse blown junction fuseUsing (1) 30 amps
Outage | J.E.26.07.21340 | C001858757 | Milton Charlton | KSAN | Completed | Load_269372 | West Kings House - 310 | Jul 18, 2026 6:24pm | Jul 18, 2026 6:25pm | Jul 18, 2026 6:44pm | Jul 18, 2026 6:44pm | Jul 18, 2026 7:24pm | Jul 18, 2026 7:05pm | Jul 18, 2026 7:27pm | Jul 18, 2026 7:27pm |  |  | Fair | No | Found okay upon arrival. Customer has an internal problem. Readings at meter socket 117-117-236 volts.
Non-Outage | J.E.26.07.20232 | C001858755 | Andre Smith | KSAS | Completed | Load_258668 | Greenwich - 710 | Jul 18, 2026 6:20pm | Jul 18, 2026 6:20pm | Jul 18, 2026 9:33pm | Jul 18, 2026 9:33pm | Jul 18, 2026 10:13pm | Jul 18, 2026 10:14pm | Jul 18, 2026 10:14pm | Jul 18, 2026 10:14pm |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.21320 | C001858754 | Richard Samuda | Manchester | Completed | Load_257074 | Spur Tree - 210 | Jul 18, 2026 6:20pm | Jul 19, 2026 7:18am | Jul 19, 2026 7:39am | Jul 19, 2026 7:39am | Jul 19, 2026 7:57am | Jul 19, 2026 8:18am | Jul 19, 2026 8:20am | Jul 19, 2026 8:20am | BrokenWire |  | SevereWind | No | Found one phase of 10 kv transformer lead burn off customer service wire reconnected customer service wire using one 1 bolt customer back to normal voltage 118/120/238
Outage | J.E.26.07.21308 | C001858751 | Delano Gayle | St.Catherine | Completed | Load_262747 | Rhodens Pen - 410 | Jul 18, 2026 6:11pm | Jul 18, 2026 6:11pm | Jul 18, 2026 6:17pm | Jul 18, 2026 6:17pm | Jul 18, 2026 7:18pm | Jul 18, 2026 7:31pm | Jul 18, 2026 7:32pm | Jul 18, 2026 7:32pm |  |  | Fair | No | Premises not found no proper contact information in report
Outage | J.E.26.07.21318 | C001858750 | Delano Gayle | St.Catherine | Completed | Load_290087 | Rhodens Pen - 210 | Jul 18, 2026 6:11pm | Jul 18, 2026 6:11pm | Jul 18, 2026 8:17pm | Jul 18, 2026 8:17pm | Jul 18, 2026 8:22pm | Jul 18, 2026 8:23pm | Jul 18, 2026 8:23pm | Jul 18, 2026 8:23pm |  |  | Fair | No | Premises found okay power restored
Outage | J.E.26.07.21339 | C001858752 | Delano Gayle | St.Catherine | Completed | Load_250687 | Rhodens Pen - 210 | Jul 18, 2026 6:11pm | Jul 18, 2026 6:11pm | Jul 18, 2026 7:32pm | Jul 18, 2026 7:32pm | Jul 18, 2026 8:09pm | Jul 18, 2026 8:16pm | Jul 18, 2026 8:17pm | Jul 18, 2026 8:17pm |  |  | Fair | No | Hexing meter disconnected in box, reconnected with assistance from call center representative
Non-Outage | J.E.26.07.21061 | C001858748 | Rusean Allen | null | Completed | null | null | Jul 18, 2026 6:07pm | Jul 18, 2026 6:08pm | Jul 18, 2026 9:40pm | Jul 18, 2026 9:40pm | Jul 18, 2026 9:40pm | Jul 18, 2026 9:41pm | Jul 18, 2026 9:41pm | Jul 18, 2026 9:41pm | BrokenWire |  | Fair | No
Outage | J.E.26.07.21302 | C001858747 | Tajay Bernard | Hanover | Completed | Load_264833 | Orange Bay - 310 | Jul 18, 2026 6:05pm | Jul 18, 2026 6:06pm | Jul 18, 2026 6:25pm | Jul 18, 2026 6:30pm | Jul 18, 2026 7:19pm | Jul 18, 2026 8:28pm | Jul 18, 2026 8:29pm | Jul 18, 2026 8:29pm |  |  | Fair | No | Remove vegetation and refuse a 20amp and a 10amp junction fuse
Outage | J.E.26.07.21317 | C001858746 | Tajay Bernard | Hanover | Completed | Load_258910 | Orange Bay - 310 | Jul 18, 2026 6:05pm | Jul 18, 2026 6:06pm | Jul 18, 2026 8:30pm | Jul 18, 2026 8:30pm | Jul 18, 2026 8:30pm | Jul 18, 2026 8:31pm | Jul 18, 2026 8:31pm | Jul 18, 2026 8:31pm | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Related to previous call job number 21302
Outage | J.E.26.07.21083 | C001858744 | Andre Smith | KSAS | Completed | Load_1002838 | Greenwich - 710 | Jul 18, 2026 6:04pm | Jul 18, 2026 6:04pm | Jul 18, 2026 7:44pm | Jul 18, 2026 7:44pm | Jul 18, 2026 8:25pm | Jul 18, 2026 9:33pm | Jul 18, 2026 9:33pm | Jul 18, 2026 9:33pm | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Replace defective service wire 50ft #6triplex cause by truck making contact with conductor supply restored
Outage | J.E.26.07.21334 | C001858745 | Andre Smith | KSAS | Completed | Load_253076 | Greenwich - 310 | Jul 18, 2026 6:04pm | Jul 18, 2026 6:04pm | Jul 18, 2026 10:14pm | Jul 18, 2026 10:14pm | Jul 18, 2026 10:39pm | Jul 18, 2026 10:39pm | Jul 18, 2026 10:39pm | Jul 18, 2026 10:39pm |  |  | Fair | No | Defective 25kva transformer found maintenance department required
Non-Outage | J.E.26.07.21293 | C001858742 | Andre Smith | null | Completed | null | null | Jul 18, 2026 6:02pm | Jul 18, 2026 6:02pm | Jul 18, 2026 6:41pm | Jul 18, 2026 6:41pm | Jul 18, 2026 7:31pm | Jul 18, 2026 7:43pm | Jul 18, 2026 7:43pm | Jul 18, 2026 7:43pm |  |  | Fair | No | Cable wire found on location
Non-Outage | J.E.26.07.21296 | C001858743 | Andre Smith | null | Completed | null | null | Jul 18, 2026 6:02pm | Jul 18, 2026 6:02pm | Jul 18, 2026 7:43pm | Jul 18, 2026 7:43pm | Jul 18, 2026 7:43pm | Jul 18, 2026 7:44pm | Jul 18, 2026 7:44pm | Jul 18, 2026 7:44pm | BrokenWire |  | Fair | No | Cable wire found at location
Outage | J.E.26.07.15065 | C001858741 | Raymond Lewis | St.Ann | Completed | Load_255835 | Cardiff Hall - 310 | Jul 18, 2026 6:01pm | Jul 18, 2026 6:11pm | Jul 18, 2026 11:22pm | Jul 18, 2026 11:22pm | Jul 18, 2026 11:22pm | Jul 18, 2026 11:23pm | Jul 18, 2026 11:23pm | Jul 18, 2026 11:23pm | BrokenWire |  | Fair | No | Supply restored
Outage | J.E.26.07.21273 | C001858740 | Raymond Lewis | St.Ann | Completed | Load_268142 | Cardiff Hall - 310 | Jul 18, 2026 6:01pm | Jul 18, 2026 6:11pm | Jul 18, 2026 8:02pm | Jul 18, 2026 8:02pm | Jul 18, 2026 10:03pm | Jul 18, 2026 11:19pm | Jul 18, 2026 11:19pm | Jul 18, 2026 11:19pm |  |  | Fair | No | Remove street light neutral from secondary phase reset 25 KVA X former
Outage | J.E.26.07.21262 | C001858738 | Floyd Taylor | Trelawny | Completed | Load_259077 | Greenwood - 110 | Jul 18, 2026 5:53pm | Jul 18, 2026 5:55pm | Jul 18, 2026 6:41pm | Jul 18, 2026 6:41pm | Jul 18, 2026 7:04pm | Jul 18, 2026 7:47pm | Jul 18, 2026 7:48pm | Jul 18, 2026 7:48pm |  |  | Fair | No | Replace one 30Amp junction fuse after bird was removed from line
Outage | J.E.26.07.21246 | C001858734 | Marlon Brown | Trelawny | Completed | Load_252516 | Martha Brae - 110 | Jul 18, 2026 5:52pm | Jul 18, 2026 5:54pm | Jul 18, 2026 6:15pm | Jul 18, 2026 6:15pm | Jul 18, 2026 6:52pm | Jul 18, 2026 7:14pm | Jul 18, 2026 7:14pm | Jul 18, 2026 7:14pm |  |  | Fair | No | Check and found at pothead 118/118=236Voltage leaving at pothead 118/118=236v. Problem is at the meter socket, customer meter socket repair and has been advised.
Outage | J.E.26.07.21330 | C001858728 | Tajay Bernard | St.James | Completed | Load_268070 | Bogue - 510 | Jul 18, 2026 5:49pm | Jul 18, 2026 6:55pm | Jul 18, 2026 8:31pm | Jul 18, 2026 8:31pm | Jul 18, 2026 8:31pm | Jul 18, 2026 8:33pm | Jul 18, 2026 8:33pm | Jul 18, 2026 8:33pm |  |  | Fair | No | Related to previous call job number 21302
Non-Outage | J.E.26.07.21311 | C001858722 | Collin Robinson | Portland | Completed | Load_240419 | Port Antonio - 410 | Jul 18, 2026 5:45pm | Jul 18, 2026 5:45pm | Jul 18, 2026 6:50pm | Jul 18, 2026 6:51pm | Jul 18, 2026 8:02pm | Jul 18, 2026 8:10pm | Jul 18, 2026 8:10pm | Jul 18, 2026 8:10pm |  |  | Fair | No | Customer meter socket defective Voltage reading 115v 115v 230v
Outage | J.E.26.07.21291 | C001858721 | Collin Robinson | Portland | Completed | Load_349991 | Port Antonio - 310 | Jul 18, 2026 5:45pm | Jul 18, 2026 5:45pm | Jul 18, 2026 6:08pm | Jul 18, 2026 6:08pm | Jul 18, 2026 6:47pm | Jul 18, 2026 6:50pm | Jul 18, 2026 6:50pm | Jul 18, 2026 6:50pm |  |  | Fair | No | Premises not found call customer several times phone ring with out answer
Outage | J.E.26.07.21320 | C001858718 | Andrew Powell | Manchester | Completed | Load_257074 | Spur Tree - 210 | Jul 18, 2026 5:34pm | Jul 18, 2026 5:34pm | Jul 18, 2026 6:19pm | Jul 18, 2026 6:19pm | Jul 18, 2026 6:19pm | Jul 18, 2026 6:20pm | Jul 18, 2026 6:20pm | Jul 18, 2026 6:20pm | BrokenWire |  | Fair | No | Manchester called.
Non-Outage | J.E.26.06.33923 | C001858716 | Oshane Warren | Westmoreland | Completed | Load_240178 | Paradise - 210 | Jul 18, 2026 5:32pm | Jul 18, 2026 5:32pm | Jul 18, 2026 7:46pm | Jul 18, 2026 7:46pm | Jul 18, 2026 8:22pm | Jul 18, 2026 8:22pm | Jul 18, 2026 8:23pm | Jul 18, 2026 8:23pm | LeaningPole |  | Fair | No | Customer stated that the pole was removed
Non-Outage | J.E.26.06.38075 | C001858715 | Oshane Warren | Hanover | Completed | Load_238910 | Orange Bay - 310 | Jul 18, 2026 5:32pm | Jul 18, 2026 5:32pm | Jul 18, 2026 11:02pm | Jul 18, 2026 11:02pm | Jul 18, 2026 11:02pm | Jul 18, 2026 11:02pm | Jul 18, 2026 11:03pm | Jul 18, 2026 11:03pm | LowHangingWires |  | Fair | No | Unable to locate or contact customer
Non-Outage | J.E.26.07.18835 | C001858717 | Oshane Warren | Westmoreland | Completed | Load_243369 | Paradise - 210 | Jul 18, 2026 5:32pm | Jul 18, 2026 5:33pm | Jul 19, 2026 9:39am | Jul 19, 2026 9:39am | Jul 19, 2026 9:39am | Jul 19, 2026 9:39am | Jul 19, 2026 9:39am | Jul 19, 2026 9:39am | LeaningPole |  | Fair | No | Unable to locate or contact customer
Non-Outage | J.E.26.02.29474 | C001858714 | Oshane Warren | Hanover | Completed | Load_245791 | Orange Bay - 310 | Jul 18, 2026 5:31pm | Jul 18, 2026 5:32pm | Jul 18, 2026 6:45pm | Jul 18, 2026 6:45pm | Jul 18, 2026 6:46pm | Jul 18, 2026 6:46pm | Jul 18, 2026 6:47pm | Jul 18, 2026 6:47pm | LowHangingWires |  | Fair | No | Customer stated that the issue was resolved
Non-Outage | J.E.26.06.37580 | C001858713 | Richman Whyte | null | Completed | null | null | Jul 18, 2026 5:30pm | Jul 18, 2026 5:31pm | Jul 19, 2026 10:23am | Jul 19, 2026 10:24am | Jul 19, 2026 10:24am | Jul 19, 2026 10:24am | Jul 19, 2026 10:25am | Jul 19, 2026 10:25am | BrokenPole |  | Fair | No | Broken pole that was in the change already
Non-Outage | J.E.26.02.02407 | C001858709 | Oshane Warren | null | Completed | null | null | Jul 18, 2026 5:29pm | Jul 18, 2026 5:30pm | Jul 18, 2026 7:42pm | Jul 18, 2026 7:42pm | Jul 18, 2026 7:42pm | Jul 18, 2026 7:43pm | Jul 18, 2026 7:45pm | Jul 18, 2026 7:45pm | BrokenPole |  | Fair | No | Unable to locate or contact need direction
Non-Outage | J.E.26.02.09250 | C001858708 | Oshane Warren | null | Completed | null | null | Jul 18, 2026 5:29pm | Jul 18, 2026 5:30pm | Jul 18, 2026 7:41pm | Jul 18, 2026 7:41pm | Jul 18, 2026 7:41pm | Jul 18, 2026 7:41pm | Jul 18, 2026 7:42pm | Jul 18, 2026 7:42pm | BrokenPole |  | Fair | No | Unable to locate or contact customer need direction
Non-Outage | J.E.26.03.02719 | C001858707 | Oshane Warren | Hanover | Completed | Load_238442 | Orange Bay - 310 | Jul 18, 2026 5:29pm | Jul 18, 2026 5:30pm | Jul 18, 2026 6:05pm | Jul 18, 2026 6:05pm | Jul 18, 2026 6:05pm | Jul 18, 2026 1:00am | Jul 18, 2026 6:07pm | Jul 18, 2026 6:07pm | BrokenWire |  | Fair | No | Customer states that the issue was resolved
Outage | J.E.26.07.21241 | C001858697 | Nickolas Rodriques | Portmore | Completed | Load_258293 | Naggo Head - 510 | Jul 18, 2026 5:13pm | Jul 18, 2026 5:16pm | Jul 18, 2026 6:24pm | Jul 18, 2026 6:24pm | Jul 18, 2026 7:17pm | Jul 18, 2026 7:33pm | Jul 18, 2026 7:38pm | Jul 18, 2026 7:38pm |  |  | Fair | No | Checked and found customer 3w meter disconnected at meter due to burnt meter socket. The customer was advised to get an Electrician to do repairs.
Outage | J.E.26.07.21249 | C001858696 | Hartley Chin | Clarendon | Completed | Load_257058 | Monymusk - 410 | Jul 18, 2026 5:13pm | Jul 18, 2026 5:14pm | Jul 18, 2026 5:18pm | Jul 18, 2026 7:10pm | Jul 18, 2026 8:16pm | Jul 18, 2026 8:17pm | Jul 18, 2026 8:40pm | Jul 18, 2026 8:40pm |  |  | Fair | No | Prem not found … person who answered contact # provided stated that contact # is incorrect… contacted escalation was told that there is no other local contact # available …
Outage | J.E.26.07.21312 | C001858695 | Damion Reid | Manchester | Completed | Load_251691 | Spur Tree - 310 | Jul 18, 2026 5:13pm | Jul 18, 2026 5:14pm | Jul 18, 2026 5:21pm | Jul 18, 2026 5:21pm | Jul 18, 2026 7:00pm | Jul 18, 2026 7:31pm | Jul 18, 2026 7:32pm | Jul 18, 2026 7:32pm | BrokenWire |  | Fair | No | Remade burnt off phase at secondary pole for 3 wire service using one 1 bolt clamp
Outage | J.E.26.07.21287 | C001858685 | Andrew Powell | Manchester | Completed | Load_244454 | Spur Tree - 210 | Jul 18, 2026 4:58pm | Jul 18, 2026 5:00pm | Jul 18, 2026 6:20pm | Jul 18, 2026 6:20pm | Jul 18, 2026 6:47pm | Jul 18, 2026 7:48pm | Jul 18, 2026 7:51pm | Jul 18, 2026 7:51pm |  |  | Fair | No | Patrol and disconnect defective 18 kv overhead lightning arrestor. Replace blown 10 amp junction fuse by Duff house, no pole number by switch location, restore supply okay.
Non-Outage | J.E.26.07.21237 | C001858683 | Richard Samuda | null | Completed | null | null | Jul 18, 2026 4:56pm | Jul 19, 2026 7:18am | Jul 19, 2026 8:23am | Jul 19, 2026 8:23am | Jul 19, 2026 9:17am | Jul 19, 2026 10:00am | Jul 19, 2026 10:00am | Jul 19, 2026 10:00am | BrokenWire |  | SevereWind | No | Reroute customer service wire to existing line because customer was contacted in mid span and harder to maintenance using two 1 bolt clamps customer back to normal voltage 114/116/230
Outage | J.E.26.07.21180 | C001858673 | Damion Reid | Manchester | Completed | Load_238945 | Spur Tree - 310 | Jul 18, 2026 4:37pm | Jul 18, 2026 4:51pm | Jul 18, 2026 7:34pm | Jul 18, 2026 7:35pm | Jul 18, 2026 8:56pm | Jul 18, 2026 10:36pm | Jul 18, 2026 10:42pm | Jul 18, 2026 10:42pm | BrokenWire |  | Fair | No | Remade corroded phase at secondary jumper using one 1 bolt clamp
Outage | J.E.26.07.21265 | C001858665 | Horace Malcolm | St.James | Completed | Load_249364 | Rose Hall - 210 | Jul 18, 2026 4:26pm | Jul 18, 2026 4:27pm | Jul 18, 2026 5:01pm | Jul 18, 2026 5:08pm | Jul 18, 2026 5:08pm | Jul 18, 2026 5:25pm | Jul 18, 2026 5:26pm | Jul 18, 2026 5:26pm | Fire |  | Fair | No | Check and found area ok no fire found on wire
Outage | J.E.26.07.21203 | C001858663 | Cliton Henry | St.Ann | Completed | Load_261992 | Upper White River - 110 | Jul 18, 2026 4:25pm | Jul 18, 2026 4:26pm | Jul 18, 2026 7:03pm | Jul 18, 2026 7:03pm | Jul 18, 2026 7:03pm | Jul 18, 2026 7:04pm | Jul 18, 2026 7:04pm | Jul 18, 2026 7:04pm |  |  | Fair | No | Supply restored, related to outage #21250
Outage | J.E.26.07.21250 | C001858664 | Cliton Henry | St.Ann | Completed | Load_257713 | Upper White River - 110 | Jul 18, 2026 4:25pm | Jul 18, 2026 4:26pm | Jul 18, 2026 4:47pm | Jul 18, 2026 4:47pm | Jul 18, 2026 5:02pm | Jul 18, 2026 6:56pm | Jul 18, 2026 7:01pm | Jul 18, 2026 7:01pm |  |  | Fair | No | A blown 20 amp junction fuse found at Derry crossing pole # 0014181. Corrective work done to retensioned 2 spans of single primary conductor. Supply restored using 1-20 amp fuse.
Outage | J.E.26.07.21149 | C001858659 | Richard Nicholas | St.Catherine | Completed | Load_258211 | Tredegar - 510 | Jul 18, 2026 4:21pm | Jul 18, 2026 4:22pm | Jul 18, 2026 5:36pm | Jul 18, 2026 5:36pm | Jul 18, 2026 7:25pm | Jul 18, 2026 7:52pm | Jul 18, 2026 7:53pm | Jul 18, 2026 7:53pm | LowHangingWires |  | EarthMovement | No | Area found ok,no low hanging JPS.co wire seen.only low hanging cable wire.supply also found ok in the area.
Outage | J.E.26.07.20036 | C001858654 | Nickolas Rodriques | St.Catherine | Completed | Load_288548 | Twickenham - 210 | Jul 18, 2026 4:18pm | Jul 18, 2026 4:19pm | Jul 18, 2026 6:24pm | Jul 18, 2026 7:50pm | Jul 18, 2026 8:24pm | Jul 18, 2026 9:16pm | Jul 18, 2026 9:23pm | Jul 18, 2026 9:23pm |  |  | Fair | No | Unable to locate or communicate with the customer after several attempts.
Outage | J.E.26.07.21226 | C001858653 | Donald Cunningham | St.Catherine | Completed | Load_557066 | Twickenham - 210 | Jul 18, 2026 4:18pm | Jul 18, 2026 6:58pm | Jul 18, 2026 7:32pm | Jul 18, 2026 7:32pm | Jul 18, 2026 8:18pm | Jul 18, 2026 9:11pm | Jul 18, 2026 9:26pm | Jul 18, 2026 9:26pm |  | Y | Fair | No | Burnt off transformer drop lead corrected using 1 clamp also light bushing done by transformer
Outage | J.E.26.07.20214 | C001858643 | Delano Gayle | St.Catherine | Completed | Load_556138 | New Michelton - 410 | Jul 18, 2026 4:01pm | Jul 18, 2026 4:01pm | Jul 18, 2026 4:12pm | Jul 18, 2026 4:12pm | Jul 18, 2026 5:19pm | Jul 18, 2026 5:21pm | Jul 18, 2026 5:21pm | Jul 18, 2026 5:21pm |  |  | Fair | No | Premises found okay power restored
Outage | J.E.26.07.21230 | C001858642 | Shamour Haughton | St.James | Completed | Load_249166 | Bogue - 610 | Jul 18, 2026 4:00pm | Jul 18, 2026 4:06pm | Jul 18, 2026 7:17pm | Jul 18, 2026 7:17pm | Jul 18, 2026 7:17pm | Jul 18, 2026 7:17pm | Jul 18, 2026 7:18pm | Jul 18, 2026 7:18pm | BrokenWire |  | Fair | No | Customer meter socket defective and customer was advised to get an electrician
Outage | J.E.26.07.21113 | C001858641 | Christopher Edwards | KSAN | Completed | Load_239302 | Constant Spring - 210 | Jul 18, 2026 3:56pm | Jul 18, 2026 3:56pm | Jul 18, 2026 6:26pm | Jul 18, 2026 7:59pm | Jul 18, 2026 8:52pm | Jul 18, 2026 9:44pm | Jul 18, 2026 9:44pm | Jul 18, 2026 9:44pm |  |  | Fair | No | Refuse blown 25 kva transformer Using (1) 2 ampsRefuse blown junction fuse Using (1) 15 ampsAlso clear vegetation off transformer pole
Outage | J.E.26.07.21206 | C001858639 | Christopher Edwards | KSAN | Completed | Load_260614 | Constant Spring - 410 | Jul 18, 2026 3:46pm | Jul 18, 2026 3:47pm | Jul 18, 2026 4:52pm | Jul 18, 2026 4:52pm | Jul 18, 2026 5:35pm | Jul 18, 2026 6:24pm | Jul 18, 2026 6:25pm | Jul 18, 2026 6:25pm |  |  | Fair | No | Refuse blown junction fuseUsing (1) 40 amps
Non-Outage | J.E.26.07.00688 | C001858636 | Omar King | St.Ann | Completed | Load_239077 | Ocho Rios - 310 | Jul 18, 2026 3:41pm | Jul 18, 2026 3:43pm | Jul 18, 2026 6:39pm | Jul 18, 2026 6:39pm | Jul 18, 2026 7:05pm | Jul 18, 2026 7:07pm | Jul 18, 2026 7:10pm | Jul 18, 2026 7:10pm |  |  | Fair | No | Customer reporting numbers of illegal connection in the area causing on off supply
Non-Outage | J.E.26.07.17244 | C001858634 | Omar King | St.Ann | Completed | Load_239479 | Ocho Rios - 310 | Jul 18, 2026 3:41pm | Jul 18, 2026 3:43pm | Jul 18, 2026 7:15pm | Jul 18, 2026 7:15pm | Jul 18, 2026 7:25pm | Jul 18, 2026 7:25pm | Jul 18, 2026 7:26pm | Jul 18, 2026 7:26pm |  |  | Fair | No | Unable to find customer call several times no answer directions not sufficient
Non-Outage | J.E.26.07.19062 | C001858633 | Omar King | St.Ann | Completed | Load_261479 | Ocho Rios - 310 | Jul 18, 2026 3:41pm | Jul 18, 2026 3:43pm | Jul 18, 2026 7:26pm | Jul 18, 2026 7:26pm | Jul 18, 2026 8:32pm | Jul 18, 2026 8:33pm | Jul 18, 2026 8:33pm | Jul 18, 2026 8:33pm |  |  | Fair | No | Problem as been resolved
Non-Outage | J.E.26.07.21198 | C001858628 | Collin Robinson | Portland | Completed | Load_240419 | Port Antonio - 410 | Jul 18, 2026 3:31pm | Jul 18, 2026 3:39pm | Jul 18, 2026 4:54pm | Jul 18, 2026 4:54pm | Jul 18, 2026 6:03pm | Jul 18, 2026 6:07pm | Jul 18, 2026 6:07pm | Jul 18, 2026 6:07pm |  |  | Fair | No | Premises found ok .Pothead voltage reading 118v 118v 236v
Outage | J.E.26.07.21199 | C001858627 | Richman Whyte | Westmoreland | Completed | Load_240662 | Paradise - 310 | Jul 18, 2026 3:28pm | Jul 18, 2026 3:35pm | Jul 18, 2026 5:38pm | Jul 18, 2026 5:39pm | Jul 18, 2026 5:39pm | Jul 18, 2026 5:45pm | Jul 18, 2026 5:46pm | Jul 18, 2026 5:46pm |  |  | Fair | No | Connect back customer after hurricane use 105ft #6 triplex voltage 115 115 230
Non-Outage | J.E.26.07.21037 | C001858626 | Cliton Henry | St.Ann | Completed | Load_244509 | Upper White River - 110 | Jul 18, 2026 3:26pm | Jul 18, 2026 3:27pm | Jul 18, 2026 4:11pm | Jul 18, 2026 4:11pm | Jul 18, 2026 4:22pm | Jul 18, 2026 4:27pm | Jul 18, 2026 4:29pm | Jul 18, 2026 4:29pm |  |  | Fair | No | The supply at the pump found ok, Voltages found were 119-119/238 Hp 205 volts
Outage | J.E.26.07.21003 | C001858622 | Cliton Henry | St.Ann | Completed | Load_249600 | Blackstonedge - 110 | Jul 18, 2026 3:25pm | Jul 18, 2026 3:26pm | Jul 18, 2026 4:42pm | Jul 18, 2026 4:42pm | Jul 18, 2026 4:43pm | Jul 18, 2026 4:46pm | Jul 18, 2026 4:47pm | Jul 18, 2026 4:47pm | BrokenWire |  | Fair | No | Supply found ok
Outage | J.E.26.07.21168 | C001858621 | Cliton Henry | St.Ann | Completed | Load_354897 | Upper White River - 110 | Jul 18, 2026 3:19pm | Jul 18, 2026 3:19pm | Jul 18, 2026 3:28pm | Jul 18, 2026 3:28pm | Jul 18, 2026 4:07pm | Jul 18, 2026 4:09pm | Jul 18, 2026 4:11pm | Jul 18, 2026 4:11pm |  |  | Fair | No | The supply was restored, related to planned outage switching
Non-Outage | J.E.26.07.11011 | C001858612 | Omar King | St.Ann | Completed | Load_412814 | Roaring River - 210 | Jul 18, 2026 3:15pm | Jul 18, 2026 3:16pm | Jul 18, 2026 3:42pm | Jul 18, 2026 3:42pm | Jul 18, 2026 6:30pm | Jul 18, 2026 6:36pm | Jul 18, 2026 6:37pm | Jul 18, 2026 6:37pm | LowHangingWires |  | Fair | No | Unable to find customer call several times no answer directions not sufficient
Non-Outage | J.E.26.07.16442 | C001858613 | Raymond Lewis | St.Ann | Completed | Load_257880 | Roaring River - 410 | Jul 18, 2026 3:15pm | Jul 18, 2026 3:42pm | Jul 18, 2026 4:43pm | Jul 18, 2026 4:44pm | Jul 18, 2026 5:15pm | Jul 18, 2026 6:20pm | Jul 18, 2026 6:21pm | Jul 18, 2026 6:21pm |  |  | Fair | No | Remade joint at pole four wire service voltages 241-243-240 voltages 121- 121- 208
Non-Outage | J.E.26.07.14387 | C001858609 | Raymond Lewis | St.Ann | Completed | Load_254597 | Cardiff Hall - 210 | Jul 18, 2026 3:13pm | Jul 18, 2026 3:13pm | Jul 18, 2026 6:35pm | Jul 18, 2026 7:21pm | Jul 18, 2026 7:21pm | Jul 18, 2026 7:23pm | Jul 18, 2026 7:23pm | Jul 18, 2026 7:23pm |  |  | Fair | No | Premises close
Non-Outage | J.E.26.07.14792 | C001858608 | Raymond Lewis | St.Ann | Completed | Load_258820 | Cardiff Hall - 210 | Jul 18, 2026 3:13pm | Jul 18, 2026 3:13pm | Jul 18, 2026 7:31pm | Jul 18, 2026 7:31pm | Jul 18, 2026 7:31pm | Jul 18, 2026 7:32pm | Jul 18, 2026 7:33pm | Jul 18, 2026 7:33pm |  |  | Fair | No | Phone not answering
Non-Outage | J.E.26.07.14835 | C001858607 | Raymond Lewis | St.Ann | Completed | Load_258820 | Cardiff Hall - 210 | Jul 18, 2026 3:13pm | Jul 18, 2026 3:13pm | Jul 18, 2026 7:34pm | Jul 18, 2026 7:34pm | Jul 18, 2026 7:34pm | Jul 18, 2026 7:36pm | Jul 18, 2026 7:44pm | Jul 18, 2026 7:44pm |  |  | Fair | No | Phone not answering
Outage | J.E.26.07.19740 | C001858602 | Hartley Chin | Clarendon | Completed | Load_267388 | Parnassus - 310 | Jul 18, 2026 3:06pm | Jul 18, 2026 3:06pm | Jul 18, 2026 5:19pm | Jul 18, 2026 5:28pm | Jul 18, 2026 6:58pm | Jul 18, 2026 7:09pm | Jul 18, 2026 7:10pm | Jul 18, 2026 7:10pm | BrokenWire |  | Fair | No | Found okay , voltage read 112v , 113v …
Outage | J.E.26.07.21179 | C001858599 | Stephen Taylor | St.Thomas | Completed | Load_261596 | Good Year - 210 | Jul 18, 2026 3:00pm | Jul 18, 2026 3:00pm | Jul 18, 2026 8:26pm | Jul 18, 2026 8:26pm | Jul 18, 2026 8:26pm | Jul 18, 2026 8:26pm | Jul 18, 2026 8:27pm | Jul 18, 2026 8:27pm | BrokenWire |  | Fair | No | Patrol the area power is in the area a lot of call to single customer no one answered the phone need more information
Outage | J.E.26.07.21158 | C001858587 | Richman Whyte | Westmoreland | Completed | Load_241109 | Paradise - 310 | Jul 18, 2026 2:52pm | Jul 18, 2026 2:53pm | Jul 18, 2026 7:12pm | Jul 18, 2026 7:12pm | Jul 18, 2026 7:12pm | Jul 18, 2026 7:13pm | Jul 18, 2026 7:13pm | Jul 18, 2026 7:13pm |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.21172 | C001858586 | Oshane Warren | Westmoreland | Completed | Load_269914 | Paradise - 110 | Jul 18, 2026 2:52pm | Jul 18, 2026 2:53pm | Jul 18, 2026 4:35pm | Jul 18, 2026 4:35pm | Jul 18, 2026 5:04pm | Jul 18, 2026 5:16pm | Jul 18, 2026 5:20pm | Jul 18, 2026 5:20pm |  |  | Fair | No | Reconnection back service wire at secondary line used 3 1 bolt clamps
Outage | J.E.26.07.21148 | C001858585 | Ryan Richards | Manchester | Completed | Load_267253 | Kendal - 210 | Jul 18, 2026 2:48pm | Jul 18, 2026 2:52pm | Jul 18, 2026 5:37pm | Jul 18, 2026 5:37pm | Jul 18, 2026 6:26pm | Jul 18, 2026 7:47pm | Jul 18, 2026 7:47pm | Jul 18, 2026 7:47pm |  |  | Rains | No | 2 blown 10 amp junction fuse found line patrol bird found entangled an the primary remove bird and replace the 2 blow 10 amp junction fuse
Outage | J.E.26.07.21160 | C001858570 | Shamour Haughton | St.James | Completed | Load_242618 | Bogue - 610 | Jul 18, 2026 2:44pm | Jul 18, 2026 2:55pm | Jul 18, 2026 3:46pm | Jul 18, 2026 4:30pm | Jul 18, 2026 4:30pm | Jul 18, 2026 4:30pm | Jul 18, 2026 4:33pm | Jul 18, 2026 4:33pm |  |  | Rains | No | Unable to locate premises, cell number went voicemail after several attempts, needs better directions
Non-Outage | J.E.26.07.21142 | C001858566 | Neville Spencer | Clarendon | Completed | Load_238064 | May Pen - 110 | Jul 18, 2026 2:11pm | Jul 18, 2026 2:13pm | Jul 18, 2026 2:19pm | Jul 18, 2026 2:19pm | Jul 18, 2026 2:36pm | Jul 18, 2026 2:37pm | Jul 18, 2026 3:13pm | Jul 18, 2026 3:13pm |  |  | Fair | No | Remade defective netural joint at pothead & secondary on 3, wire service used 2, clamps voltage reading 112 114 227 .
Outage | J.E.26.07.21144 | C001858565 | Andrew Powell | Manchester | Completed | Load_292691 | Spur Tree - 210 | Jul 18, 2026 2:10pm | Jul 18, 2026 2:10pm | Jul 18, 2026 4:37pm | Jul 18, 2026 4:37pm | Jul 18, 2026 5:44pm | Jul 18, 2026 6:15pm | Jul 18, 2026 6:18pm | Jul 18, 2026 6:18pm |  |  | SevereWind | No | Isolate and close 10 kva transformer circuit to repair burnt off phase and neutral drop lead at secondary line using 12 feet pvc copper and three clamps, no pole number by switch location restore supply okay.
Non-Outage | J.E.26.07.21123 | C001858561 | Andrew Powell | null | Completed | null | null | Jul 18, 2026 1:52pm | Jul 18, 2026 1:52pm | Jul 18, 2026 2:40pm | Jul 18, 2026 2:40pm | Jul 18, 2026 3:35pm | Jul 18, 2026 4:17pm | Jul 18, 2026 4:20pm | Jul 18, 2026 4:20pm | Fire |  | Fair | No | Isolate and close 25 kva transformer circuit by pole number 026872 to retention two pole span of sagging secondary top phase conductor using two preform, restore supply okay.
Non-Outage | J.E.26.07.21115 | C001858560 | Hartley Chin | null | Completed | null | null | Jul 18, 2026 1:51pm | Jul 18, 2026 1:52pm | Jul 18, 2026 8:40pm | Jul 18, 2026 8:40pm | Jul 18, 2026 10:10pm | Jul 18, 2026 10:10pm | Jul 18, 2026 10:12pm | Jul 18, 2026 10:12pm |  |  | Fair | No | Foun okay .. contacted customer , was told that customer supply is okay …
Outage | J.E.26.07.21129 | C001858558 | Horace Malcolm | St.James | Completed | Load_256619 | Rose Hall - 210 | Jul 18, 2026 1:48pm | Jul 18, 2026 1:51pm | Jul 18, 2026 4:25pm | Jul 18, 2026 4:53pm | Jul 18, 2026 4:53pm | Jul 18, 2026 4:55pm | Jul 18, 2026 4:55pm | Jul 18, 2026 4:55pm |  |  | Fair | No | Refused one 50kva transformer used one 5amp fuse
Outage | J.E.26.07.21124 | C001858553 | Michael Christian | St.James | Completed | Load_575161 | Bogue - 310 | Jul 18, 2026 1:35pm | Jul 18, 2026 1:37pm | Jul 18, 2026 2:05pm | Jul 18, 2026 2:05pm | Jul 18, 2026 2:19pm | Jul 18, 2026 2:21pm | Jul 18, 2026 2:21pm | Jul 18, 2026 2:21pm |  |  | Fair | No | Check and found voltage 112 113 225 at pothead
Non-Outage | J.E.26.07.18405 | C001858552 | Richard Nicholas | St.Catherine | Completed | Load_241538 | Twickenham - 310 | Jul 18, 2026 1:31pm | Jul 18, 2026 1:32pm | Jul 18, 2026 1:39pm | Jul 18, 2026 1:39pm | Jul 18, 2026 3:11pm | Jul 18, 2026 5:31pm | Jul 18, 2026 5:33pm | Jul 18, 2026 5:33pm |  |  | Fair | No | Remade slack 3w service phase and neutral joint at pole.3 clamp was used.voltage reading 117,115 and 232v.
Outage | J.E.26.07.21118 | C001858549 | Edward Royal | KSAS | Completed | Load_254287 | Duhaney - 310 | Jul 18, 2026 1:26pm | Jul 18, 2026 10:59pm | Jul 19, 2026 1:15am | Jul 19, 2026 1:16am | Jul 19, 2026 1:16am | Jul 19, 2026 1:17am | Jul 19, 2026 1:17am | Jul 19, 2026 1:17am | BrokenPole |  | Fair | No | Premises not found unable to communicate with customer
Outage | J.E.26.07.21108 | C001858543 | Cliton Henry | St.Mary | Completed | Load_245666 | Oracabessa - 210 | Jul 18, 2026 1:10pm | Jul 18, 2026 1:12pm | Jul 18, 2026 7:04pm | Jul 18, 2026 7:05pm | Jul 18, 2026 9:20pm | Jul 18, 2026 9:45pm | Jul 18, 2026 9:49pm | Jul 18, 2026 9:49pm |  |  | Fair | No | The corroded joints found at the customer pothead were reconnected using 3 #2-#2 pen unions. Voltages left were 119-119/238 volts.
Non-Outage | J.E.26.07.20869 | C001858542 | Romaine Roberts | St.Mary | Completed | Load_267975 | Highgate - 210 | Jul 18, 2026 1:04pm | Jul 18, 2026 1:06pm | Jul 18, 2026 5:42pm | Jul 18, 2026 5:42pm | Jul 18, 2026 7:04pm | Jul 18, 2026 7:05pm | Jul 18, 2026 7:07pm | Jul 18, 2026 7:07pm | BrokenWire |  | Fair | No | Premises not found insufficient direction a visit to area made but no broken wire seen visible
Non-Outage | J.E.26.07.21023 | C001858541 | Edward Royal | null | Completed | null | null | Jul 18, 2026 1:02pm | Jul 18, 2026 1:03pm | Jul 18, 2026 1:09pm | Jul 18, 2026 1:09pm | Jul 18, 2026 1:09pm | Jul 18, 2026 1:09pm | Jul 18, 2026 1:09pm | Jul 18, 2026 1:09pm | Fire |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.07.21104 | C001858539 | Andrew Powell | Manchester | Completed | Load_246355 | Spur Tree - 210 | Jul 18, 2026 12:52pm | Jul 18, 2026 12:52pm | Jul 18, 2026 1:03pm | Jul 18, 2026 1:05pm | Jul 18, 2026 1:46pm | Jul 18, 2026 2:31pm | Jul 18, 2026 2:33pm | Jul 18, 2026 2:33pm |  |  | Fair | No | Splice and tension broken service wire at secondary line 3 wire using 5 feet #6 triplex and two clamps, voltage leave 116v-116v phase to neutral 232v cross phase.
Outage | J.E.26.07.21100 | C001858538 | Horace Malcolm | St.James | Completed | Load_269402 | Rose Hall - 210 | Jul 18, 2026 12:49pm | Jul 18, 2026 12:52pm | Jul 18, 2026 3:09pm | Jul 18, 2026 3:09pm | Jul 18, 2026 4:07pm | Jul 18, 2026 4:22pm | Jul 18, 2026 4:23pm | Jul 18, 2026 4:23pm |  |  | Fair | No | Clean and remake joints at customer pothead used 3clamps voltage 114-118-232
Outage | J.E.26.07.21103 | C001858537 | Stephen Taylor | St.Thomas | Completed | Load_245707 | Good Year - 210 | Jul 18, 2026 12:49pm | Jul 18, 2026 12:52pm | Jul 18, 2026 5:05pm | Jul 18, 2026 5:05pm | Jul 18, 2026 5:07pm | Jul 18, 2026 5:08pm | Jul 18, 2026 5:19pm | Jul 18, 2026 5:19pm | Fire |  | Fair | No | Clean up single phase use 2 Linkeet customer is now ok reading 111,112,224
Outage | J.E.26.07.21092 | C001858533 | Rusean Allen | KSAS | Completed | Load_257412 | Rockfort - 410 | Jul 18, 2026 12:36pm | Jul 18, 2026 12:36pm | Jul 18, 2026 7:03pm | Jul 18, 2026 7:03pm | Jul 18, 2026 7:57pm | Jul 18, 2026 8:01pm | Jul 18, 2026 8:01pm | Jul 18, 2026 8:01pm | BrokenWire |  | Fair | No | Reconnected wire at pole
Outage | J.E.26.07.20958 | C001858532 | Richman Whyte | St.Elizabeth | Completed | Load_264525 | Maggotty - 110 | Jul 18, 2026 12:27pm | Jul 18, 2026 12:27pm | Jul 18, 2026 2:49pm | Jul 18, 2026 2:49pm | Jul 18, 2026 4:06pm | Jul 18, 2026 4:06pm | Jul 18, 2026 4:07pm | Jul 18, 2026 4:07pm | BrokenWire |  | Fair | No | Customer have internal problem however calls to customer went unanswered
Non-Outage | J.E.26.07.21050 | C001858531 | Marlon Brown | Trelawny | Completed | Load_239537 | Duncans - 210 | Jul 18, 2026 12:22pm | Jul 18, 2026 12:24pm | Jul 18, 2026 2:18pm | Jul 18, 2026 2:18pm | Jul 18, 2026 2:30pm | Jul 18, 2026 2:33pm | Jul 18, 2026 2:33pm | Jul 18, 2026 2:33pm |  |  | Fair | No | Customer says her premises is unoccupied and she’s getting a estimated bill she wants it to be adjusted.
Outage | J.E.26.07.21088 | C001858530 | Stephen Taylor | St.Thomas | Completed | Load_241803 | Good Year - 110 | Jul 18, 2026 12:22pm | Jul 18, 2026 12:25pm | Jul 18, 2026 2:25pm | Jul 18, 2026 2:25pm | Jul 18, 2026 2:25pm | Jul 18, 2026 2:26pm | Jul 18, 2026 2:26pm | Jul 18, 2026 2:26pm |  |  | Fair | No | Clean up transformer drop leads use 2 clamps and close up back 50 amp transformer all customer is now okay
Non-Outage | J.E.26.07.20098 | C001858529 | Horace Malcolm | St.James | Completed | Load_260155 | Queens Drive - 710 | Jul 18, 2026 12:21pm | Jul 18, 2026 12:24pm | Jul 18, 2026 1:05pm | Jul 18, 2026 1:05pm | Jul 18, 2026 1:05pm | Jul 18, 2026 1:09pm | Jul 18, 2026 1:09pm | Jul 18, 2026 1:09pm |  |  | Fair | No | Clean and remake joints at pole used 1clamp voltage 106-106-212
Outage | J.E.26.07.21084 | C001858526 | Tajay Bernard | Hanover | Completed | Load_257085 | Orange Bay - 310 | Jul 18, 2026 12:12pm | Jul 18, 2026 12:13pm | Jul 18, 2026 6:28pm | Jul 18, 2026 6:28pm | Jul 18, 2026 6:28pm | Jul 18, 2026 6:29pm | Jul 18, 2026 6:30pm | Jul 18, 2026 6:30pm |  |  | Fair | No | Area check and found okay unable to locate customer on premises multiple phone to customer number went unanswered
Outage | J.E.26.07.21066 | C001858524 | Romaine Roberts | St.Mary | Completed | Load_350780 | Blackstonedge - 110 | Jul 18, 2026 12:00pm | Jul 18, 2026 1:22pm | Jul 18, 2026 1:38pm | Jul 18, 2026 1:38pm | Jul 18, 2026 5:21pm | Jul 18, 2026 5:27pm | Jul 18, 2026 5:32pm | Jul 18, 2026 5:32pm | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards | Y | Fair | No | Bamboo fall on line and blow junction and transformer fuse patrol and clear line replace 5 amp and 10 amp junction power restore
Outage | J.E.26.07.21067 | C001858523 | Christopher Edwards | KSAN | Completed | Load_261490 | Constant Spring - 410 | Jul 18, 2026 11:58am | Jul 18, 2026 11:59am | Jul 18, 2026 2:06pm | Jul 18, 2026 2:06pm | Jul 18, 2026 2:21pm | Jul 18, 2026 2:52pm | Jul 18, 2026 2:53pm | Jul 18, 2026 2:53pm | LowHangingWires |  | Fair | No | Leaning 35 ft concrete poleConsist of open secondary and single phase primary Pole is leaning and needs to be straightened Supply is in the area
Non-Outage | J.E.26.07.21069 | C001858521 | Stephen Taylor | null | Completed | null | null | Jul 18, 2026 11:57am | Jul 18, 2026 11:57am | Jul 18, 2026 3:23pm | Jul 18, 2026 6:25pm | Jul 18, 2026 6:25pm | Jul 18, 2026 6:27pm | Jul 18, 2026 6:56pm | Jul 18, 2026 6:56pm | LeakingTransformer |  | Fair | No | See junction link down no number on pole patrol see nothing and close up back junction with a 15 amp fuse all customer is now okay
Outage | J.E.26.07.21073 | C001858522 | Rayon Foster | Hanover | Completed | Load_265877 | Orange Bay - 310 | Jul 18, 2026 11:57am | Jul 18, 2026 11:58am | Jul 18, 2026 3:25pm | Jul 18, 2026 4:39pm | Jul 18, 2026 5:13pm | Jul 18, 2026 5:16pm | Jul 18, 2026 5:41pm | Jul 18, 2026 5:41pm | Fire |  | Fair | No | Customer meter is burnt and meter box has already been restored refer to field service to have customer meter changed
Outage | J.E.26.07.21065 | C001858519 | Stephen Taylor | St.Thomas | Completed | Load_243194 | Good Year - 210 | Jul 18, 2026 11:49am | Jul 18, 2026 11:51am | Jul 18, 2026 6:57pm | Jul 18, 2026 6:57pm | Jul 18, 2026 6:57pm | Jul 18, 2026 6:57pm | Jul 18, 2026 6:58pm | Jul 18, 2026 6:58pm |  |  | Fair | No | See junction link down no number on pole patrol see nothing and close up back junction with a 15 amp fuse all customer is now okay
Outage | J.E.26.07.21057 | C001858518 | Donald Cunningham | St.Catherine | Completed | Load_244884 | Twickenham - 210 | Jul 18, 2026 11:48am | Jul 18, 2026 11:49am | Jul 18, 2026 2:05pm | Jul 18, 2026 2:05pm | Jul 18, 2026 2:47pm | Jul 18, 2026 2:48pm | Jul 18, 2026 2:49pm | Jul 18, 2026 2:49pm |  |  | Fair | No | Need more directions customer customer not reachable
Outage | J.E.26.07.21048 | C001858517 | Nickolas Rodriques | Portmore | Completed | Load_262697 | Naggo Head - 610 | Jul 18, 2026 11:46am | Jul 18, 2026 11:48am | Jul 18, 2026 1:07pm | Jul 18, 2026 1:23pm | Jul 18, 2026 1:26pm | Jul 18, 2026 1:44pm | Jul 18, 2026 1:45pm | Jul 18, 2026 1:45pm | Fire |  | Fair | No | No fire seen upon arrival. (Area has electricity).
Outage | J.E.26.07.21054 | C001858516 | Michael Christian | St.James | Completed | Load_263504 | Bogue - 310 | Jul 18, 2026 11:41am | Jul 18, 2026 11:42am | Jul 18, 2026 1:14pm | Jul 18, 2026 1:14pm | Jul 18, 2026 1:14pm | Jul 18, 2026 1:23pm | Jul 18, 2026 1:23pm | Jul 18, 2026 1:23pm |  |  | Fair | No | Premises found located
Non-Outage | J.E.26.07.17021 | C001858511 | Shamour Haughton | null | Completed | null | null | Jul 18, 2026 11:34am | Jul 18, 2026 11:39am | Jul 18, 2026 9:39pm | Jul 18, 2026 9:39pm | Jul 18, 2026 9:39pm | Jul 18, 2026 9:39pm | Jul 18, 2026 9:39pm | Jul 18, 2026 9:39pm |  |  | Fair | No | Customer states they didn’t make report
Non-Outage | J.E.26.07.21009 | C001858513 | Stephen Taylor | null | Completed | null | null | Jul 18, 2026 11:34am | Jul 18, 2026 11:38am | Jul 18, 2026 10:02pm | Jul 18, 2026 10:02pm | Jul 19, 2026 9:23am | Jul 19, 2026 9:23am | Jul 19, 2026 9:25am | Jul 19, 2026 9:25am | BangingWires |  | Fair | No | Clear out banging wires with switch stick area is now okay
Outage | J.E.26.07.21044 | C001858512 | Collin Robinson | Portland | Completed | Load_250217 | Port Antonio - 310 | Jul 18, 2026 11:34am | Jul 18, 2026 11:36am | Jul 18, 2026 1:01pm | Jul 18, 2026 1:01pm | Jul 18, 2026 1:16pm | Jul 18, 2026 1:29pm | Jul 18, 2026 1:30pm | Jul 18, 2026 1:30pm |  |  | Fair | No | Remove wild bird from 25KVA transformer switch bottom and replace 3 amps fuse
Non-Outage | J.E.26.07.21040 | C001858509 | Eric Williams | null | Completed | null | null | Jul 18, 2026 11:31am | Jul 18, 2026 11:31am | Jul 18, 2026 11:35am | Jul 18, 2026 11:35am | Jul 18, 2026 11:56am | Jul 18, 2026 1:25pm | Jul 18, 2026 1:58pm | Jul 18, 2026 1:58pm | BrokenPole |  | SevereWind | No | Broken 3 phase primary pole with return, cause by truck ( truck license plate number CF2388)maintenance team on location carrying assessment for repairs
Outage | J.E.26.07.21033 | C001858508 | Collin Robinson | Portland | Completed | Load_349128 | Port Antonio - 410 | Jul 18, 2026 11:28am | Jul 18, 2026 11:35am | Jul 18, 2026 1:30pm | Jul 18, 2026 1:30pm | Jul 18, 2026 1:57pm | Jul 18, 2026 2:32pm | Jul 18, 2026 2:39pm | Jul 18, 2026 2:39pm |  |  | Fair | No | Reconnect broken #6 twisted at pole and reconnect pothead use 6 one bolt clamp Voltage reading 117v 118v 235v
Outage | J.E.26.07.20912 | C001858505 | Nickolas Rodriques | Portmore | Completed | Load_245535 | Naggo Head - 610 | Jul 18, 2026 11:18am | Jul 18, 2026 11:22am | Jul 18, 2026 1:46pm | Jul 18, 2026 1:54pm | Jul 18, 2026 2:33pm | Jul 18, 2026 2:50pm | Jul 18, 2026 2:54pm | Jul 18, 2026 2:54pm |  |  | Fair | No | Customer confirmed that the power was restored.
Outage | J.E.26.07.21026 | C001858504 | Stephen Taylor | St.Thomas | Completed | Load_268013 | Good Year - 210 | Jul 18, 2026 11:16am | Jul 18, 2026 11:17am | Jul 18, 2026 7:29pm | Jul 18, 2026 7:29pm | Jul 18, 2026 7:58pm | Jul 18, 2026 7:58pm | Jul 18, 2026 8:10pm | Jul 18, 2026 8:10pm | Fire |  | Fair | No | Daylight attention because of the traffic
Outage | J.E.26.07.20455 | C001858503 | Nickolas Rodriques | Portmore | Completed | Load_244041 | Naggo Head - 610 | Jul 18, 2026 11:14am | Jul 18, 2026 11:15am | Jul 18, 2026 11:57am | Jul 18, 2026 12:11pm | Jul 18, 2026 12:42pm | Jul 18, 2026 1:02pm | Jul 18, 2026 1:05pm | Jul 18, 2026 1:05pm |  |  | Fair | No | Checked and found customer single phasing (120) caused by broken service wire at pole. Repaired by connecting wire using one clamp, current reading is (120-119-239). Customers confirmed that all is well now.
Non-Outage | J.E.26.07.20948 | C001858499 | Edward Royal | null | Completed | null | null | Jul 18, 2026 10:56am | Jul 18, 2026 10:59am | Jul 18, 2026 11:35am | Jul 18, 2026 11:35am | Jul 18, 2026 12:10pm | Jul 18, 2026 12:35pm | Jul 18, 2026 12:56pm | Jul 18, 2026 12:56pm | BrokenWire |  | Fair | No | Spliced and reconnected transformer drop lead using 4 one bolt clamps 2 ft 4 north cable
Non-Outage | J.E.26.07.20982 | C001858496 | Nickolas Rodriques | null | Completed | null | null | Jul 18, 2026 10:55am | Jul 18, 2026 10:57am | Jul 18, 2026 3:13pm | Jul 18, 2026 3:13pm | Jul 18, 2026 3:43pm | Jul 18, 2026 3:44pm | Jul 18, 2026 3:59pm | Jul 18, 2026 3:59pm | Fire |  | Fair | No | Customer stated that the report was made for his address in Torrington avenue Kingston.
Outage | J.E.26.07.20966 | C001858498 | Edward Royal | KSAS | Completed | Load_246294 | Greenwich - 310 | Jul 18, 2026 10:55am | Jul 18, 2026 10:57am | Jul 18, 2026 12:57pm | Jul 18, 2026 12:57pm | Jul 18, 2026 12:57pm | Jul 18, 2026 1:07pm | Jul 18, 2026 1:07pm | Jul 18, 2026 1:07pm |  |  | Fair | No | Replaced 2 junction fuse 1 transformer fuse 40A 30A 5A
Outage | J.E.26.07.20987 | C001858497 | Rusean Allen | KSAS | Completed | Load_249389 | Rockfort - 410 | Jul 18, 2026 10:55am | Jul 18, 2026 10:58am | Jul 18, 2026 11:24am | Jul 18, 2026 11:24am | Jul 18, 2026 3:16pm | Jul 18, 2026 3:17pm | Jul 18, 2026 3:17pm | Jul 18, 2026 3:17pm | BrokenWire |  | Fair | No | Splice and retention secondary wire
Outage | J.E.26.07.20979 | C001858495 | Wan Carlos Scarlett | St.Catherine | Completed | Load_269949 | Rhodens Pen - 410 | Jul 18, 2026 10:51am | Jul 18, 2026 10:52am | Jul 18, 2026 11:31am | Jul 18, 2026 11:31am | Jul 18, 2026 12:30pm | Jul 18, 2026 2:47pm | Jul 18, 2026 2:49pm | Jul 18, 2026 2:49pm |  |  | Fair | No | Refuse 15 Amps Junction no pole # was found nothing was found on primary line suspect lightning
Non-Outage | J.E.26.07.20835 | C001858492 | Milton Charlton | KSAN | Completed | Load_259174 | Hope - 510 | Jul 18, 2026 10:38am | Jul 18, 2026 10:42am | Jul 18, 2026 11:13am | Jul 18, 2026 11:13am | Jul 18, 2026 6:25pm | Jul 18, 2026 1:50pm | Jul 18, 2026 6:31pm | Jul 18, 2026 6:31pm |  |  | Fair | No | Isolate 25kva transformer at pole #( no pole#) and charge clamps on transformer drop leads using six 1- bolt clamps and reclosed transformer switch. Readings at transformer drop leads 115-114-230 volts.
Non-Outage | J.E.26.07.20985 | C001858490 | Christopher Edwards | KSAN | Completed | Load_262953 | Constant Spring - 410 | Jul 18, 2026 10:38am | Jul 18, 2026 10:42am | Jul 18, 2026 10:55am | Jul 18, 2026 11:02am | Jul 18, 2026 11:43am | Jul 18, 2026 12:22pm | Jul 18, 2026 12:22pm | Jul 18, 2026 12:22pm |  |  | Fair | No | Removed illegal connections off open secondary wiresIllegal connections was on customer neutral clamp and cause clamp to burnt Remake joint using (1) one bolt clampVoltage:112,113,227vThe area has a lot of illegal connections
Non-Outage | J.E.26.07.20223 | C001858488 | Stephen Taylor | St.Thomas | Completed | Load_254904 | Good Year - 110 | Jul 18, 2026 10:25am | Jul 18, 2026 10:26am | Jul 18, 2026 12:49pm | Jul 18, 2026 12:49pm | Jul 18, 2026 2:05pm | Jul 18, 2026 2:05pm | Jul 18, 2026 2:07pm | Jul 18, 2026 2:07pm |  |  | Fair | No | Clean up transformer drop leads use 2 clamps and close up back 50 amp transformer all customer is now okay
Non-Outage | J.E.26.07.20431 | C001858487 | Stephen Taylor | St.Thomas | Completed | Load_254720 | Good Year - 110 | Jul 18, 2026 10:25am | Jul 18, 2026 10:26am | Jul 18, 2026 2:26pm | Jul 18, 2026 2:26pm | Jul 18, 2026 2:26pm | Jul 18, 2026 2:26pm | Jul 18, 2026 2:27pm | Jul 18, 2026 2:27pm |  |  | Fair | No | Clean up transformer drop leads use 2 clamps and close up back 50 amp transformer all customer is now okay
Non-Outage | J.E.26.07.20907 | C001858486 | Stephen Taylor | St.Thomas | Completed | Load_577172 | Good Year - 110 | Jul 18, 2026 10:25am | Jul 18, 2026 10:26am | Jul 19, 2026 9:25am | Jul 19, 2026 9:26am | Jul 19, 2026 10:53am | Jul 19, 2026 10:55am | Jul 19, 2026 10:56am | Jul 19, 2026 10:56am |  |  | Fair | No | Patrol the area and power is in the area several call to single customer no one answer
Outage | J.E.26.07.20989 | C001858485 | Marlon Brown | Trelawny | Completed | Load_268209 | Martha Brae - 210 | Jul 18, 2026 10:24am | Jul 18, 2026 10:25am | Jul 18, 2026 11:49am | Jul 18, 2026 2:33pm | Jul 18, 2026 2:38pm | Jul 18, 2026 2:40pm | Jul 18, 2026 2:40pm | Jul 18, 2026 2:40pm |  |  | Fair | No | Refer to Field Service Department
Outage | J.E.26.07.20962 | C001858484 | Ryan Richards | Manchester | Completed | Load_265440 | Kendal - 210 | Jul 18, 2026 10:23am | Jul 18, 2026 10:24am | Jul 18, 2026 2:47pm | Jul 18, 2026 2:47pm | Jul 18, 2026 4:05pm | Jul 18, 2026 4:30pm | Jul 18, 2026 4:30pm | Jul 18, 2026 4:30pm | BrokenWire |  | Rains | No | Blown 3 amp fuse found for 25 kva transformer line patrol banging secondary phase found retention neutral using 1#2 preform and replace blown 3 amp fuse all customers are now with supply
Outage | J.E.26.07.20968 | C001858483 | Roxroy Needham | St.Ann | Completed | Load_238506 | Cardiff Hall - 310 | Jul 18, 2026 10:18am | Jul 18, 2026 10:19am | Jul 18, 2026 11:11am | Jul 18, 2026 11:11am | Jul 18, 2026 12:05pm | Jul 18, 2026 12:07pm | Jul 18, 2026 12:07pm | Jul 18, 2026 12:07pm |  |  | Fair | No | Premises found ok customer have internal problem voltage left at meter 113-114-228
Non-Outage | J.E.26.07.19157 | C001858481 | Milton Charlton | KSAN | Completed | Load_302445 | Hope - 510 | Jul 18, 2026 10:13am | Jul 18, 2026 10:20am | Jul 18, 2026 6:32pm | Jul 18, 2026 6:32pm | Jul 18, 2026 6:32pm | Jul 18, 2026 2:55pm | Jul 18, 2026 6:37pm | Jul 18, 2026 6:37pm | TreeContact |  | Fair | No | Primary and secondary spot bushing is required. Palm tree leaves touching Primary conductor. Bushing required urgently.
Non-Outage | J.E.26.07.20978 | C001858480 | Cliton Henry | null | Completed | null | null | Jul 18, 2026 10:11am | Jul 18, 2026 10:32am | Jul 18, 2026 1:44pm | Jul 18, 2026 1:44pm | Jul 18, 2026 1:44pm | Jul 18, 2026 1:45pm | Jul 18, 2026 1:45pm | Jul 18, 2026 1:45pm |  |  | Fair | No | Supply restored, related to outage #16120
Non-Outage | J.E.26.07.20955 | C001858473 | Collin Robinson | null | Completed | null | null | Jul 18, 2026 9:47am | Jul 18, 2026 9:48am | Jul 18, 2026 9:50am | Jul 18, 2026 9:50am | Jul 18, 2026 10:16am | Jul 18, 2026 10:24am | Jul 18, 2026 10:24am | Jul 18, 2026 10:24am |  |  | Fair | No | Premises found with supply Meter socket voltage reading 120v 120v 240v
Outage | J.E.26.07.20953 | C001858471 | Michael Christian | St.James | Completed | Load_301833 | Bogue - 310 | Jul 18, 2026 9:43am | Jul 18, 2026 9:44am | Jul 18, 2026 11:47am | Jul 18, 2026 11:47am | Jul 18, 2026 12:12pm | Jul 18, 2026 12:15pm | Jul 18, 2026 12:15pm | Jul 18, 2026 12:15pm |  |  | Fair | No | Customer needs meter to disconnection
Outage | J.E.26.07.20939 | C001858470 | Damion Reid | Manchester | Completed | Load_269975 | Spur Tree - 310 | Jul 18, 2026 9:40am | Jul 18, 2026 9:40am | Jul 18, 2026 2:43pm | Jul 18, 2026 2:43pm | Jul 18, 2026 3:17pm | Jul 18, 2026 4:49pm | Jul 18, 2026 4:53pm | Jul 18, 2026 4:53pm | BrokenWire |  | Fair | No | Blown 3amp fuse found for 25kva transformer cause by one span of broken secondary phase an neutral conductor splice an retention conductor using 80ft of #2 aluminum conductor two #2 preform 3 one bolt clamp and replace blown fuse
Outage | J.E.26.07.20407 | C001858468 | Ricky Hall | St.Catherine | Completed | Load_254015 | New Michelton - 410 | Jul 18, 2026 9:26am | Jul 18, 2026 9:27am | Jul 18, 2026 12:52pm | Jul 18, 2026 12:52pm | Jul 18, 2026 2:24pm | Jul 18, 2026 2:56pm | Jul 18, 2026 2:57pm | Jul 18, 2026 2:57pm |  |  | Fair | No | Issue was resolved previously
Outage | J.E.26.07.20940 | C001858467 | Stephen Taylor | St.Thomas | Completed | Load_241803 | Good Year - 110 | Jul 18, 2026 9:23am | Jul 18, 2026 9:23am | Jul 18, 2026 2:21pm | Jul 18, 2026 2:21pm | Jul 18, 2026 2:21pm | Jul 18, 2026 2:25pm | Jul 18, 2026 2:25pm | Jul 18, 2026 2:25pm |  |  | Fair | No | Clean up transformer drop leads use 2 clamps and close up back 50 amp transformer all customer is now okay
Outage | J.E.26.07.20918 | C001858465 | Stephen Taylor | St.Thomas | Completed | Load_247908 | Good Year - 210 | Jul 18, 2026 8:44am | Jul 18, 2026 8:51am | Jul 18, 2026 7:04pm | Jul 18, 2026 7:04pm | Jul 18, 2026 7:17pm | Jul 18, 2026 7:27pm | Jul 18, 2026 7:28pm | Jul 18, 2026 7:28pm |  |  | Fair | No | Clean up single phase use 1 clamp reading 112,113,225 customer is now okay
Outage | J.E.26.07.20915 | C001858464 | Rayon Foster | Hanover | Completed | Load_253221 | Orange Bay - 310 | Jul 18, 2026 8:36am | Jul 18, 2026 8:37am | Jul 18, 2026 11:03am | Jul 18, 2026 11:10am | Jul 18, 2026 11:19am | Jul 18, 2026 11:25am | Jul 18, 2026 11:26am | Jul 18, 2026 11:26am |  |  | Fair | No | Customer bill payment reconnection was delayed customer power supply was restored after speaking with customer service.
Non-Outage | J.E.26.07.15615 | C001858463 | Dwain Samuels | null | Completed | null | null | Jul 18, 2026 8:35am | Jul 18, 2026 8:36am | Jul 18, 2026 9:22am | Jul 18, 2026 10:57am | Jul 18, 2026 10:57am | Jul 18, 2026 10:57am | Jul 18, 2026 10:58am | Jul 18, 2026 10:58am | LowHangingWires |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.07.18770 | C001858460 | Dwain Samuels | Westmoreland | Completed | Load_238268 | Paradise - 210 | Jul 18, 2026 8:35am | Jul 18, 2026 8:36am | Jul 18, 2026 9:22am | Jul 18, 2026 9:34am | Jul 18, 2026 9:55am | Jul 18, 2026 10:06am | Jul 18, 2026 10:08am | Jul 18, 2026 10:08am |  |  | Fair | No | Connect 3 wire service. Used 3 one bolt clamp and. Voltage check
Non-Outage | J.E.26.07.19005 | C001858461 | Dwain Samuels | Westmoreland | Completed | Load_238268 | Paradise - 210 | Jul 18, 2026 8:35am | Jul 18, 2026 8:36am | Jul 18, 2026 9:22am | Jul 18, 2026 10:08am | Jul 18, 2026 10:08am | Jul 18, 2026 10:08am | Jul 18, 2026 10:09am | Jul 18, 2026 10:09am |  |  | Fair | No | Found working okay . Voltage check 115-115-230
Non-Outage | J.E.26.07.19808 | C001858459 | Dwain Samuels | Westmoreland | Completed | Load_292434 | Paradise - 310 | Jul 18, 2026 8:35am | Jul 18, 2026 8:36am | Jul 18, 2026 9:22am | Jul 18, 2026 10:21am | Jul 18, 2026 10:31am | Jul 18, 2026 10:50am | Jul 18, 2026 10:53am | Jul 18, 2026 10:53am |  |  | Fair | No | Corrosion found at 3 wire pole. Corrosion clear use 2 one bolt clamp. Voltage check 115-117-232
Non-Outage | J.E.26.07.20898 | C001858458 | Marlon Brown | Trelawny | Completed | Load_556439 | Duncans - 210 | Jul 18, 2026 8:15am | Jul 18, 2026 8:17am | Jul 18, 2026 9:22am | Jul 18, 2026 11:49am | Jul 18, 2026 12:42pm | Jul 18, 2026 2:16pm | Jul 18, 2026 2:16pm | Jul 18, 2026 2:16pm |  |  | Fair | No | Repair secondary neutral jumper and phase use 3 pg clamps, Voltage found at meter socket 117/84=190Voltage leaving at meter socket 102/103=205v. 100kva transformer supply ove4 70 meters and a lot of illegal connections Customer meter is burnt please refer to Field Service Department. Voltage @ transformer drop lead 113/115=229vCurrent @drop lead x1 156, x2 24 X3 171Transformer @ tap 3.
Non-Outage | J.E.26.07.20871 | C001858457 | Andrew Powell | Manchester | Completed | Load_253758 | Spur Tree - 210 | Jul 18, 2026 8:11am | Jul 18, 2026 8:11am | Jul 18, 2026 9:27am | Jul 18, 2026 9:54am | Jul 18, 2026 10:18am | Jul 18, 2026 10:55am | Jul 18, 2026 10:57am | Jul 18, 2026 10:57am |  |  | Fair | No | Isolate and close 25 kva transformer circuit to repair corroded drop lead joints at secondary line using three clamps, voltage reading 118v-118v phase to neutral 236v cross phase, no pole number by switch location.
Non-Outage | J.E.26.07.20411 | C001858456 | Oshane Warren | Hanover | Completed | Load_239573 | Orange Bay - 310 | Jul 18, 2026 8:10am | Jul 18, 2026 8:10am | Jul 18, 2026 9:19am | Jul 18, 2026 9:26am | Jul 18, 2026 10:39am | Jul 18, 2026 11:10am | Jul 18, 2026 11:12am | Jul 18, 2026 11:12am |  |  | Fair | No | Voltage 220 109 111
Non-Outage | J.E.26.07.20729 | C001858455 | Oshane Warren | Hanover | Completed | Load_261442 | Orange Bay - 310 | Jul 18, 2026 8:10am | Jul 18, 2026 8:10am | Jul 18, 2026 11:37am | Jul 18, 2026 11:37am | Jul 18, 2026 12:38pm | Jul 18, 2026 12:41pm | Jul 18, 2026 12:44pm | Jul 18, 2026 12:44pm |  |  | Fair | No | Open bank a 2 transformer and splice and retention one spand secondary neutral conductor used 1 splicing sleeve 2 1 bolt clamps
Non-Outage | J.E.26.07.15478 | C001858454 | Shamour Haughton | null | Completed | null | null | Jul 18, 2026 8:08am | Jul 18, 2026 5:40pm | Jul 18, 2026 7:32pm | Jul 18, 2026 7:32pm | Jul 18, 2026 7:32pm | Jul 18, 2026 7:32pm | Jul 18, 2026 7:33pm | Jul 18, 2026 7:33pm |  |  | Fair | No | Customer states that power was restored
Non-Outage | J.E.26.07.19353 | C001858453 | Damion Reid | Manchester | Completed | Load_269942 | Spur Tree - 310 | Jul 18, 2026 8:08am | Jul 18, 2026 8:08am | Jul 18, 2026 10:10am | Jul 18, 2026 10:10am | Jul 18, 2026 11:49am | Jul 18, 2026 12:15pm | Jul 18, 2026 12:16pm | Jul 18, 2026 12:16pm |  |  | Fair | No | Remade corroded phase jumper at secondary pole using two one bolt clamp
Non-Outage | J.E.26.07.19994 | C001858452 | Damion Reid | Manchester | Completed | Load_264130 | Spur Tree - 310 | Jul 18, 2026 8:08am | Jul 18, 2026 8:08am | Jul 18, 2026 12:17pm | Jul 18, 2026 12:17pm | Jul 18, 2026 12:36pm | Jul 18, 2026 1:00pm | Jul 18, 2026 1:01pm | Jul 18, 2026 1:01pm |  |  | Fair | No | Customer meter and meter socket is defective customer have been advised refer to field service
Non-Outage | J.E.26.07.18861 | C001858449 | Ryan Richards | Manchester | Completed | Load_259982 | Kendal - 210 | Jul 18, 2026 8:07am | Jul 18, 2026 8:07am | Jul 18, 2026 12:50pm | Jul 18, 2026 12:50pm | Jul 18, 2026 2:09pm | Jul 18, 2026 2:46pm | Jul 18, 2026 2:46pm | Jul 18, 2026 2:46pm |  |  | Fair | No | Corroded neutral found at pole remade neutral using 1 one bolt clamp voltage 115/117/233 volt
Non-Outage | J.E.26.07.19099 | C001858448 | Ryan Richards | Manchester | Completed | Load_262141 | Kendal - 210 | Jul 18, 2026 8:07am | Jul 18, 2026 8:07am | Jul 18, 2026 11:56am | Jul 18, 2026 11:56am | Jul 18, 2026 12:34pm | Jul 18, 2026 12:50pm | Jul 18, 2026 12:50pm | Jul 18, 2026 12:50pm |  |  | Fair | No | Burn off neutral found at pole splice neutral using 4ft#6 service 1 one bolt clamp voltage 116/118/235 volts
Non-Outage | J.E.26.07.20061 | C001858451 | Damion Reid | Manchester | Completed | Load_250211 | Porus - 210 | Jul 18, 2026 8:07am | Jul 18, 2026 8:08am | Jul 18, 2026 8:17am | Jul 18, 2026 8:17am | Jul 18, 2026 9:11am | Jul 18, 2026 10:06am | Jul 18, 2026 10:07am | Jul 18, 2026 10:07am | BangingWires |  | SevereWind | No | Remade broken service neutral at secondary pole for 3 wire service using one pen union
Non-Outage | J.E.26.07.20553 | C001858450 | Damion Reid | Manchester | Completed | Load_262800 | Spur Tree - 310 | Jul 18, 2026 8:07am | Jul 18, 2026 8:08am | Jul 18, 2026 1:10pm | Jul 18, 2026 1:10pm | Jul 18, 2026 2:25pm | Jul 18, 2026 2:40pm | Jul 18, 2026 2:43pm | Jul 18, 2026 2:43pm |  |  | SevereWind | No | Remade burnt off neutral at secondary pole for 3 wire service using one 1 bolt clamp voltage reading at meter socket phase to neutral 111v-112v across phase 224v
Non-Outage | J.E.26.02.13811 | C001858446 | Tajay Bernard | Hanover | Completed | Load_575278 | Orange Bay - 310 | Jul 18, 2026 8:06am | Jul 18, 2026 8:07am | Jul 18, 2026 10:22am | Jul 18, 2026 10:23am | Jul 18, 2026 10:35am | Jul 18, 2026 10:36am | Jul 18, 2026 10:36am | Jul 18, 2026 10:36am | LowHangingWires |  | Fair | No | Area check and found okay no low hanging found
Non-Outage | J.E.26.05.13738 | C001858442 | Tajay Bernard | Hanover | Completed | Load_265327 | Bogue - 510 | Jul 18, 2026 8:06am | Jul 18, 2026 8:07am | Jul 18, 2026 10:37am | Jul 18, 2026 10:37am | Jul 18, 2026 10:37am | Jul 18, 2026 10:37am | Jul 18, 2026 10:37am | Jul 18, 2026 10:37am |  |  | Fair | No | Customer stated that the issue has been resolved
Non-Outage | J.E.26.07.07578 | C001858444 | Tajay Bernard | Hanover | Completed | Load_573823 | Orange Bay - 310 | Jul 18, 2026 8:06am | Jul 18, 2026 8:07am | Jul 18, 2026 10:03am | Jul 18, 2026 10:03am | Jul 18, 2026 10:22am | Jul 18, 2026 10:22am | Jul 18, 2026 10:22am | Jul 18, 2026 10:22am |  |  | Fair | No | Customer stated that the issue has been resolved
Non-Outage | J.E.26.07.14186 | C001858447 | Tajay Bernard | Hanover | Completed | Load_256684 | Orange Bay - 310 | Jul 18, 2026 8:06am | Jul 18, 2026 8:07am | Jul 18, 2026 10:57am | Jul 18, 2026 10:58am | Jul 18, 2026 11:42am | Jul 18, 2026 11:50am | Jul 18, 2026 11:51am | Jul 18, 2026 11:51am |  |  | Fair | No | Clean and remake joints at jps pole use 2 clampsVoltage found 103/106/209Voltage left 106/106/212
Non-Outage | J.E.26.07.14534 | C001858443 | Tajay Bernard | Hanover | Completed | Load_258303 | Orange Bay - 310 | Jul 18, 2026 8:06am | Jul 18, 2026 8:07am | Jul 18, 2026 10:43am | Jul 18, 2026 10:44am | Jul 18, 2026 10:44am | Jul 18, 2026 10:45am | Jul 18, 2026 10:45am | Jul 18, 2026 10:45am |  |  | Fair | No | Area check and found okay unable okay unable to locate customer on premises multiple phone to customer number went unanswered
Non-Outage | J.E.26.07.20885 | C001858445 | Ryan Richards | Manchester | Completed | Load_263608 | Kendal - 210 | Jul 18, 2026 8:06am | Jul 18, 2026 8:07am | Jul 18, 2026 8:36am | Jul 18, 2026 8:36am | Jul 18, 2026 9:59am | Jul 18, 2026 11:54am | Jul 18, 2026 11:55am | Jul 18, 2026 11:55am |  |  | Fair | No | Customer found getting low voltage checkes made where one we discovered one span of secondary neutral under heavy vegetation broken open 25 kva transformer carried out spot bushing then splice and retention neutral using 25ft#2 aluminum 2 one bolt and 1#2 preform and reclose transformer
Outage | J.E.26.07.20854 | C001858440 | Rusean Allen | KSAS | Completed | Load_244646 | Cane River - 310 | Jul 18, 2026 8:02am | Jul 18, 2026 8:03am | Jul 18, 2026 9:16am | Jul 18, 2026 9:39am | Jul 18, 2026 11:21am | Jul 18, 2026 11:22am | Jul 18, 2026 11:22am | Jul 18, 2026 11:22am |  |  | Fair | No | Found a 40 amps fuseReplace a 40 amp fuse
Outage | J.E.26.07.19831 | C001858439 | Rusean Allen | KSAS | Completed | Load_249081 | Cane River - 310 | Jul 18, 2026 8:01am | Jul 18, 2026 8:03am | Jul 18, 2026 5:07pm | Jul 18, 2026 5:07pm | Jul 18, 2026 5:07pm | Jul 18, 2026 5:07pm | Jul 18, 2026 5:07pm | Jul 18, 2026 5:07pm |  |  | Fair | No
Outage | J.E.26.07.20881 | C001858438 | Donald Cunningham | Portmore | Completed | Load_252448 | Naggo Head - 510 | Jul 18, 2026 7:59am | Jul 18, 2026 7:59am | Jul 18, 2026 8:10am | Jul 18, 2026 9:24am | Jul 18, 2026 9:43am | Jul 18, 2026 10:28am | Jul 18, 2026 10:31am | Jul 18, 2026 10:31am | Fire |  | Fair | No | Burnt and corroded phase by pothead and pole corrected 4 clamps and 2 feet of service phase use voltage readings 119/2/239
Non-Outage | J.E.26.07.14605 | C001858437 | Shamour Haughton | St.James | Completed | Load_301818 | Bogue - 310 | Jul 18, 2026 7:58am | Jul 18, 2026 8:18am | Jul 18, 2026 9:10am | Jul 18, 2026 9:10am | Jul 18, 2026 9:41am | Jul 18, 2026 10:02am | Jul 18, 2026 10:06am | Jul 18, 2026 10:06am |  |  | Fair | No | Found customer experiencing single phasing, box number en06750
Non-Outage | J.E.26.07.14727 | C001858436 | Michael Christian | St.James | Completed | Load_570299 | Bogue - 310 | Jul 18, 2026 7:58am | Jul 18, 2026 8:07am | Jul 18, 2026 8:16am | Jul 18, 2026 8:17am | Jul 18, 2026 9:10am | Jul 18, 2026 9:28am | Jul 18, 2026 9:29am | Jul 18, 2026 9:29am |  |  | Fair | No | Bucket needs e n box
Non-Outage | J.E.26.07.20673 | C001858435 | Michael Christian | St.James | Completed | Load_576009 | Bogue - 310 | Jul 18, 2026 7:58am | Jul 18, 2026 8:07am | Jul 18, 2026 9:29am | Jul 18, 2026 9:29am | Jul 18, 2026 10:55am | Jul 18, 2026 11:02am | Jul 18, 2026 11:02am | Jul 18, 2026 11:02am |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.20889 | C001858434 | Shamour Haughton | St.James | Completed | Load_240742 | Bogue - 610 | Jul 18, 2026 7:58am | Jul 18, 2026 8:01am | Jul 18, 2026 1:44pm | Jul 18, 2026 1:44pm | Jul 18, 2026 2:39pm | Jul 18, 2026 2:45pm | Jul 18, 2026 2:53pm | Jul 18, 2026 2:53pm | BrokenWire |  | Fair | No | Found customer meter socket defective, customer was advised to get and electrician then report back to jps
Non-Outage | J.E.26.07.20072 | C001858433 | Donald Cunningham | Portmore | Completed | Load_252448 | Naggo Head - 510 | Jul 18, 2026 7:57am | Jul 18, 2026 7:59am | Jul 18, 2026 10:31am | Jul 18, 2026 10:31am | Jul 18, 2026 10:32am | Jul 18, 2026 10:32am | Jul 18, 2026 10:33am | Jul 18, 2026 10:33am |  |  | Fair | No | Supply restored
Non-Outage | J.E.26.07.18814 | C001858432 | Shamour Haughton | St.James | Completed | Load_264514 | Rose Hall - 210 | Jul 18, 2026 7:56am | Jul 18, 2026 5:34pm | Jul 18, 2026 7:39pm | Jul 18, 2026 7:39pm | Jul 18, 2026 7:39pm | Jul 18, 2026 7:40pm | Jul 18, 2026 9:39pm | Jul 18, 2026 9:39pm |  |  | Fair | No | Customer states that they didn’t make a report
Non-Outage | J.E.26.07.19132 | C001858431 | Horace Malcolm | St.James | Completed | Load_238044 | Queens Drive - 710 | Jul 18, 2026 7:56am | Jul 18, 2026 7:57am | Jul 18, 2026 8:17am | Jul 18, 2026 8:17am | Jul 18, 2026 8:29am | Jul 18, 2026 9:02am | Jul 18, 2026 9:02am | Jul 18, 2026 9:02am |  |  | Fair | No | Clean and remake ues 1 clamp at customer service wire at pole voltage 110 111 223 at meter
Non-Outage | J.E.26.07.19513 | C001858430 | Horace Malcolm | St.James | Completed | Load_248368 | Queens Drive - 310 | Jul 18, 2026 7:56am | Jul 18, 2026 7:57am | Jul 18, 2026 1:23pm | Jul 18, 2026 1:43pm | Jul 18, 2026 1:59pm | Jul 18, 2026 2:00pm | Jul 18, 2026 2:01pm | Jul 18, 2026 2:01pm |  |  | Fair | No | Check and found ok supply restored
Non-Outage | J.E.26.07.19726 | C001858428 | Horace Malcolm | St.James | Completed | Load_265675 | Queens Drive - 710 | Jul 18, 2026 7:56am | Jul 18, 2026 7:57am | Jul 18, 2026 8:12am | Jul 18, 2026 9:02am | Jul 18, 2026 10:00am | Jul 18, 2026 11:46am | Jul 18, 2026 11:46am | Jul 18, 2026 11:46am |  |  | Fair | No | Clean and remake joints at pole used 2clamps voltage 115-117-232
Non-Outage | J.E.26.07.19799 | C001858429 | Horace Malcolm | St.James | Completed | Load_261958 | Queens Drive - 710 | Jul 18, 2026 7:56am | Jul 18, 2026 7:57am | Jul 18, 2026 11:47am | Jul 18, 2026 12:35pm | Jul 18, 2026 12:35pm | Jul 18, 2026 12:43pm | Jul 18, 2026 12:43pm | Jul 18, 2026 12:43pm |  |  | Fair | No | Check and found ok issue resolved
Non-Outage | J.E.26.07.19829 | C001858426 | Horace Malcolm | St.James | Completed | Load_261958 | Queens Drive - 710 | Jul 18, 2026 7:56am | Jul 18, 2026 7:57am | Jul 18, 2026 2:01pm | Jul 18, 2026 2:01pm | Jul 18, 2026 2:25pm | Jul 18, 2026 3:09pm | Jul 18, 2026 3:09pm | Jul 18, 2026 3:09pm |  |  | Fair | No | Check and found customer meter burnt meter is single phasing referred to field service
Non-Outage | J.E.26.07.19837 | C001858425 | Horace Malcolm | St.James | Completed | Load_258945 | Queens Drive - 710 | Jul 18, 2026 7:56am | Jul 18, 2026 7:57am | Jul 18, 2026 5:07pm | Jul 18, 2026 5:31pm | Jul 18, 2026 6:02pm | Jul 18, 2026 6:33pm | Jul 18, 2026 6:33pm | Jul 18, 2026 6:33pm |  |  | Fair | No | Clean and remake joints at pole used 3clamps voltage 110-112-222
Non-Outage | J.E.26.07.20632 | C001858427 | Tajay Bernard | St.James | Completed | Load_260344 | Bogue - 510 | Jul 18, 2026 7:56am | Jul 18, 2026 8:08am | Jul 18, 2026 9:02am | Jul 18, 2026 9:14am | Jul 18, 2026 9:55am | Jul 18, 2026 9:59am | Jul 18, 2026 10:01am | Jul 18, 2026 10:01am |  |  | Fair | No | Clean and remake customer service neutral at customer pothead, 1 clamp was usedVoltage found 109/125/234Voltage left 112/114/226
Non-Outage | J.E.26.07.19286 | C001858424 | Rayon Foster | Hanover | Completed | Load_244632 | Orange Bay - 210 | Jul 18, 2026 7:55am | Jul 18, 2026 7:56am | Jul 18, 2026 11:11am | Jul 18, 2026 11:27am | Jul 18, 2026 12:46pm | Jul 18, 2026 12:48pm | Jul 18, 2026 12:48pm | Jul 18, 2026 12:48pm |  |  | Fair | No | Check and found working ok customer power supply was already restored by emergency team yesterday.
Non-Outage | J.E.26.07.19704 | C001858422 | Rayon Foster | Hanover | Completed | Load_244632 | Orange Bay - 210 | Jul 18, 2026 7:55am | Jul 18, 2026 7:56am | Jul 18, 2026 11:11am | Jul 18, 2026 12:48pm | Jul 18, 2026 1:03pm | Jul 18, 2026 1:04pm | Jul 18, 2026 1:06pm | Jul 18, 2026 1:06pm |  |  | Fair | No | Check and found working ok customer power supply was restored yesterday by emergency team
Non-Outage | J.E.26.07.19966 | C001858423 | Rayon Foster | Hanover | Completed | Load_247572 | Orange Bay - 210 | Jul 18, 2026 7:55am | Jul 18, 2026 7:56am | Jul 18, 2026 1:07pm | Jul 18, 2026 1:07pm | Jul 18, 2026 1:22pm | Jul 18, 2026 2:13pm | Jul 18, 2026 2:29pm | Jul 18, 2026 2:29pm |  |  | Fair | No | Check and found voltage at pothead on arrival 112v/106v/218v and voltage found at transformer pole 118v/117v/235v
Non-Outage | J.E.26.07.20047 | C001858421 | Rayon Foster | Hanover | Completed | Load_243937 | Orange Bay - 210 | Jul 18, 2026 7:55am | Jul 18, 2026 7:56am | Jul 18, 2026 11:13am | Jul 18, 2026 2:29pm | Jul 18, 2026 3:25pm | Jul 18, 2026 3:31pm | Jul 18, 2026 4:39pm | Jul 18, 2026 4:39pm |  |  | Fair | No | Check and found working ok customer supply was already restored by emergency team yesterday
Non-Outage | J.E.26.07.13061 | C001858414 | Tajay Bernard | Hanover | Completed | Load_265275 | Orange Bay - 310 | Jul 18, 2026 7:54am | Jul 18, 2026 7:54am | Jul 18, 2026 11:52am | Jul 18, 2026 11:53am | Jul 18, 2026 12:46pm | Jul 18, 2026 12:51pm | Jul 18, 2026 12:51pm | Jul 18, 2026 12:51pm |  |  | Fair | No | Area check and found okay unable to locate customer on premises multiple phone call to customer number went unanswered
Non-Outage | J.E.26.07.13532 | C001858415 | Tajay Bernard | null | Completed | null | null | Jul 18, 2026 7:54am | Jul 18, 2026 7:54am | Jul 18, 2026 10:40am | Jul 18, 2026 10:40am | Jul 18, 2026 10:42am | Jul 18, 2026 10:43am | Jul 18, 2026 10:43am | Jul 18, 2026 10:43am | BrokenWire |  | Fair | No | Customer stated that the problem was resolved
Non-Outage | J.E.26.07.17021 | C001858420 | Tajay Bernard | null | Completed | null | null | Jul 18, 2026 7:54am | Jul 18, 2026 7:54am | Jul 18, 2026 10:46am | Jul 18, 2026 10:54am | Jul 18, 2026 10:54am | Jul 18, 2026 10:55am | Jul 18, 2026 10:55am | Jul 18, 2026 10:55am |  |  | Fair | No | This call belongs to st james
Non-Outage | J.E.26.07.20298 | C001858409 | Christopher Edwards | KSAN | Completed | Load_268886 | Constant Spring - 310 | Jul 18, 2026 7:52am | Jul 18, 2026 7:54am | Jul 18, 2026 2:53pm | Jul 18, 2026 2:53pm | Jul 18, 2026 3:47pm | Jul 18, 2026 4:51pm | Jul 18, 2026 4:51pm | Jul 18, 2026 4:51pm |  |  | Fair | No | Corroded neutral joint At pole and potheadRemake joint using (2) one bolt clamps Voltage:120,119,240v
Non-Outage | J.E.26.07.20803 | C001858413 | Rayon Foster | Hanover | Completed | Load_294682 | Orange Bay - 310 | Jul 18, 2026 7:52am | Jul 18, 2026 7:53am | Jul 18, 2026 11:14am | Jul 18, 2026 9:15pm | Jul 18, 2026 9:49pm | Jul 18, 2026 9:51pm | Jul 18, 2026 10:01pm | Jul 18, 2026 10:01pm | LowHangingWires |  | Fair | No | Splice and retention customer service wire using about 5 ft of number 6 wire to reconnect customer service wire to pothead voltage left after repairs 113/110v/223v
Non-Outage | J.E.26.07.20812 | C001858410 | Christopher Edwards | KSAN | Completed | Load_261490 | Constant Spring - 410 | Jul 18, 2026 7:52am | Jul 18, 2026 7:55am | Jul 18, 2026 12:22pm | Jul 18, 2026 12:22pm | Jul 18, 2026 1:13pm | Jul 18, 2026 2:05pm | Jul 18, 2026 2:06pm | Jul 18, 2026 2:06pm |  |  | Fair | No | Clear bamboo from open secondary lineThat was causing phase to be tangled with open secondary neutral Voltage:118,119,240v
Outage | J.E.26.07.20140 | C001858412 | Tajay Bernard | Hanover | Completed | Load_257085 | Orange Bay - 310 | Jul 18, 2026 7:52am | Jul 18, 2026 7:53am | Jul 18, 2026 8:04am | Jul 18, 2026 8:04am | Jul 18, 2026 8:57am | Jul 18, 2026 8:59am | Jul 18, 2026 8:59am | Jul 18, 2026 8:59am |  |  | Fair | No | Area check and found okay unable to locate customer on premises international number was given so was unable to get the customer
Outage | J.E.26.07.20818 | C001858407 | Rusean Allen | KSAS | Completed | Load_245037 | Cane River - 410 | Jul 18, 2026 7:51am | Jul 18, 2026 7:54am | Jul 18, 2026 5:08pm | Jul 18, 2026 5:08pm | Jul 18, 2026 7:03pm | Jul 18, 2026 7:03pm | Jul 18, 2026 7:03pm | Jul 18, 2026 7:03pm |  |  | Fair | No
Outage | J.E.26.07.20844 | C001858408 | Rayon Foster | Hanover | Completed | Load_258804 | Orange Bay - 310 | Jul 18, 2026 7:51am | Jul 18, 2026 7:51am | Jul 18, 2026 8:07am | Jul 18, 2026 8:08am | Jul 18, 2026 8:23am | Jul 18, 2026 9:19am | Jul 18, 2026 9:19am | Jul 18, 2026 9:19am | Fire |  | Fair | No | Patrol primary line to find 1 blown 10amp junction fuse complete line patrol before replacing 1 10amp junction at same and close
Non-Outage | J.E.26.07.17816 | C001858405 | Horace Malcolm | null | Completed | null | null | Jul 18, 2026 7:46am | Jul 18, 2026 10:11am | Jul 18, 2026 1:11pm | Jul 18, 2026 1:11pm | Jul 18, 2026 1:18pm | Jul 18, 2026 1:43pm | Jul 18, 2026 1:43pm | Jul 18, 2026 1:43pm |  |  | Fair | No | Check and premises ok issue resolved
Non-Outage | J.E.26.07.20185 | C001858403 | Shamour Haughton | St.James | Completed | Load_292067 | Bogue - 610 | Jul 18, 2026 7:46am | Jul 18, 2026 7:50am | Jul 18, 2026 11:40am | Jul 18, 2026 11:40am | Jul 18, 2026 1:36pm | Jul 18, 2026 1:36pm | Jul 18, 2026 1:40pm | Jul 18, 2026 1:40pm |  |  | Fair | No | Found customer experiencing internal problem, voltage left 115,116,231
Non-Outage | J.E.26.07.20395 | C001858404 | Shamour Haughton | St.James | Completed | Load_567708 | Bogue - 610 | Jul 18, 2026 7:46am | Jul 18, 2026 7:50am | Jul 18, 2026 8:06am | Jul 18, 2026 8:06am | Jul 18, 2026 8:21am | Jul 18, 2026 8:44am | Jul 18, 2026 9:07am | Jul 18, 2026 9:07am |  |  | Fair | No | Check and found okay, voltage left 120,121,242
Non-Outage | J.E.26.07.20406 | C001858402 | Shamour Haughton | St.James | Completed | Load_292622 | Bogue - 610 | Jul 18, 2026 7:46am | Jul 18, 2026 7:50am | Jul 18, 2026 10:12am | Jul 18, 2026 10:12am | Jul 18, 2026 10:48am | Jul 18, 2026 11:31am | Jul 18, 2026 11:35am | Jul 18, 2026 11:35am |  |  | Fair | No | Found secondary jumper burnt of at pole, remake jumper use 1 clamp, voltage left 115,116,231
Outage | J.E.26.07.20857 | C001858401 | Stephen Taylor | St.Thomas | Completed | Load_267304 | Lysson - 410 | Jul 18, 2026 7:41am | Jul 18, 2026 7:41am | Jul 18, 2026 8:18am | Jul 18, 2026 8:18am | Jul 18, 2026 9:14am | Jul 18, 2026 9:14am | Jul 18, 2026 9:54am | Jul 18, 2026 9:54am |  |  | Fair | No | Chip saver out no # and pole patrol clear line with switch stick and close up back chip saver safely all customer is now okay 20 amp
Outage | J.E.26.07.20878 | C001858400 | Stephen Taylor | St.Thomas | Completed | Load_250959 | Lysson - 410 | Jul 18, 2026 7:41am | Jul 18, 2026 7:41am | Jul 18, 2026 9:54am | Jul 18, 2026 9:54am | Jul 18, 2026 9:54am | Jul 18, 2026 9:55am | Jul 18, 2026 9:55am | Jul 18, 2026 9:55am |  |  | Fair | No | Check with customer and customer said power is back now and okay
Outage | J.E.26.07.20778 | C001858398 | Hartley Chin | St.Catherine | Completed | Load_240023 | Rhodens Pen - 310 | Jul 18, 2026 7:40am | Jul 18, 2026 7:40am | Jul 18, 2026 7:54am | Jul 18, 2026 10:52am | Jul 18, 2026 11:10am | Jul 18, 2026 11:57am | Jul 18, 2026 12:01pm | Jul 18, 2026 12:01pm |  |  | SevereWind | No | Repair burnt service phase found @ meter pole .. use 1 clamp … voltage read 114v, 115v …
Non-Outage | J.E.26.07.20794 | C001858397 | Marlon Brown | Trelawny | Completed | Load_555930 | Martha Brae - 210 | Jul 18, 2026 7:39am | Jul 18, 2026 7:41am | Jul 18, 2026 9:21am | Jul 18, 2026 9:21am | Jul 18, 2026 9:21am | Jul 18, 2026 9:22am | Jul 18, 2026 9:22am | Jul 18, 2026 9:22am |  |  | Fair | No | Same as call number 20796
Non-Outage | J.E.26.07.20796 | C001858396 | Marlon Brown | Trelawny | Completed | Load_555930 | Martha Brae - 210 | Jul 18, 2026 7:39am | Jul 18, 2026 7:41am | Jul 18, 2026 8:00am | Jul 18, 2026 8:00am | Jul 18, 2026 8:54am | Jul 18, 2026 9:20am | Jul 18, 2026 9:20am | Jul 18, 2026 9:20am |  |  | Fair | No | Voltage at meter socket 109/110=219vVoltage leaving at meter socket 109/110=219v Check and found ok, customer reports about outage on the 17th. Which was a feeder issue.
Non-Outage | J.E.26.07.20864 | C001858394 | Marlon Brown | Trelawny | Completed | Load_243305 | Duncans - 210 | Jul 18, 2026 7:39am | Jul 18, 2026 7:41am | Jul 18, 2026 10:41am | Jul 18, 2026 10:41am | Jul 18, 2026 11:07am | Jul 18, 2026 11:49am | Jul 18, 2026 11:49am | Jul 18, 2026 11:49am |  |  | Fair | No | Clean and remake joint at pothead use 3 linkers Voltage found @ pothead 113/116=229Voltage leaving at pothead 113/116=229
Outage | J.E.26.07.20705 | C001858395 | Wan Carlos Scarlett | St.Catherine | Completed | Load_250547 | Rhodens Pen - 210 | Jul 18, 2026 7:39am | Jul 18, 2026 7:49am | Jul 18, 2026 9:55am | Jul 18, 2026 9:55am | Jul 18, 2026 10:47am | Jul 18, 2026 11:31am | Jul 18, 2026 11:31am | Jul 18, 2026 11:31am |  |  | Fair | No | Customer report streetlight not working
Non-Outage | J.E.26.07.20344 | C001858393 | Richman Whyte | null | Completed | null | null | Jul 18, 2026 7:38am | Jul 18, 2026 7:40am | Jul 18, 2026 4:08pm | Jul 18, 2026 4:08pm | Jul 18, 2026 4:08pm | Jul 18, 2026 4:09pm | Jul 18, 2026 4:09pm | Jul 18, 2026 4:09pm |  |  | Fair | No | Already completed from this morning
Outage | J.E.26.07.20848 | C001858392 | Ryan Richards | Manchester | Completed | Load_265440 | Kendal - 210 | Jul 18, 2026 7:33am | Jul 18, 2026 7:34am | Jul 18, 2026 4:30pm | Jul 18, 2026 4:30pm | Jul 18, 2026 4:50pm | Jul 18, 2026 5:36pm | Jul 18, 2026 5:36pm | Jul 18, 2026 5:36pm |  |  | Rains | No | Area found ok call related to the other Troy call
Outage | J.E.26.07.20643 | C001858390 | Neville Spencer | Clarendon | Completed | Load_251082 | May Pen - 110 | Jul 18, 2026 7:31am | Jul 18, 2026 7:32am | Jul 18, 2026 7:37am | Jul 18, 2026 7:37am | Jul 18, 2026 9:00am | Jul 18, 2026 9:01am | Jul 18, 2026 9:04am | Jul 18, 2026 9:04am |  |  | Fair | No | Found ok call resolved last night.
Non-Outage | J.E.26.07.20156 | C001858388 | Moses Elliston | null | Completed | null | null | Jul 18, 2026 7:30am | Jul 18, 2026 7:32am | Jul 18, 2026 11:12am | Jul 18, 2026 11:12am | Jul 18, 2026 11:12am | Jul 17, 2026 1:05pm | Jul 18, 2026 11:13am | Jul 18, 2026 11:13am |  |  | Fair | No | Credit added to prepaid account
Outage | J.E.26.07.20175 | C001858386 | Moses Elliston | St.Catherine | Completed | Load_557176 | Tredegar - 410 | Jul 18, 2026 7:30am | Jul 18, 2026 7:32am | Jul 19, 2026 12:27pm | Jul 19, 2026 12:27pm | Jul 19, 2026 12:27pm | Jul 19, 2026 12:40pm | Jul 19, 2026 12:41pm | Jul 19, 2026 12:41pm |  |  | Fair | No | Customer said credit added to prepaid account
Outage | J.E.26.07.20726 | C001858387 | Wayne Dillion | St.Elizabeth | Completed | Load_249684 | Maggotty - 110 | Jul 18, 2026 7:30am | Jul 18, 2026 7:32am | Jul 18, 2026 6:34pm | Jul 18, 2026 6:34pm | Jul 18, 2026 6:34pm | Jul 18, 2026 6:35pm | Jul 18, 2026 6:35pm | Jul 18, 2026 6:35pm | Fire |  | Fair | No | Customer said the problem has been resolved by and electrician is was internal problem
Outage | J.E.26.07.20756 | C001858389 | Andrew Powell | Manchester | Completed | Load_265103 | Spur Tree - 210 | Jul 18, 2026 7:30am | Jul 18, 2026 7:31am | Jul 18, 2026 7:46am | Jul 18, 2026 7:46am | Jul 18, 2026 8:03am | Jul 18, 2026 8:03am | Jul 18, 2026 8:05am | Jul 18, 2026 8:05am | BrokenWire |  | Fair | No | Premises not located inadequately direction incorrect contact number.
Non-Outage | J.E.26.07.19854 | C001858384 | Moses Elliston | null | Completed | null | null | Jul 18, 2026 7:29am | Jul 18, 2026 7:32am | Jul 18, 2026 11:07am | Jul 18, 2026 11:07am | Jul 18, 2026 11:07am | Jul 17, 2026 12:50pm | Jul 18, 2026 11:10am | Jul 18, 2026 11:10am |  |  | Fair | No | Meter changed to # 3069918..Not collecting
Outage | J.E.26.07.19861 | C001858385 | Moses Elliston | St.Catherine | Completed | Load_1001429 | Tredegar - 210 | Jul 18, 2026 7:29am | Jul 18, 2026 7:32am | Jul 18, 2026 11:05am | Jul 18, 2026 11:05am | Jul 18, 2026 11:05am | Jul 17, 2026 1:35am | Jul 18, 2026 11:06am | Jul 18, 2026 11:06am |  |  | Fair | No | Credit added to prepaid account
Outage | J.E.26.07.20856 | C001858383 | Wayne Dillion | St.Elizabeth | Completed | Load_239391 | Maggotty - 110 | Jul 18, 2026 7:29am | Jul 18, 2026 7:29am | Jul 18, 2026 8:50am | Jul 18, 2026 8:50am | Jul 18, 2026 10:00am | Jul 18, 2026 12:15pm | Jul 18, 2026 12:30pm | Jul 18, 2026 12:30pm |  |  | Fair | No | Patrol and found one blown 20 amp junction and one blown 5 amp fuse that protects 50KVA bank of three transformer no pole number replace the same supply restore to customer successfully
Outage | J.E.26.07.20734 | C001858382 | Ricky Hall | St.Catherine | Completed | Load_264678 | New Michelton - 410 | Jul 18, 2026 7:28am | Jul 18, 2026 7:28am | Jul 18, 2026 9:03am | Jul 18, 2026 9:04am | Jul 18, 2026 10:00am | Jul 18, 2026 12:44pm | Jul 18, 2026 12:48pm | Jul 18, 2026 12:48pm |  |  | SevereWind | No | Conduct spot bushing retention sagging primary neural replace trip saver
Non-Outage | J.E.26.07.20507 | C001858381 | Collin Robinson | Portland | Completed | Load_238988 | Port Antonio - 310 | Jul 18, 2026 7:27am | Jul 18, 2026 7:27am | Jul 18, 2026 10:58am | Jul 18, 2026 10:59am | Jul 18, 2026 11:30am | Jul 18, 2026 11:33am | Jul 18, 2026 11:33am | Jul 18, 2026 11:33am |  |  | Fair | No | Premises found ok Voltage reading 118v 117v 235v
Non-Outage | J.E.26.07.20534 | C001858379 | Collin Robinson | Portland | Completed | Load_239206 | Port Antonio - 410 | Jul 18, 2026 7:27am | Jul 18, 2026 7:27am | Jul 18, 2026 8:02am | Jul 18, 2026 8:26am | Jul 18, 2026 9:32am | Jul 18, 2026 9:40am | Jul 18, 2026 9:40am | Jul 18, 2026 9:40am | Fire |  | Fair | No | Remove fallen tree limb from primary conductor
Outage | J.E.26.07.20332 | C001858376 | Nickolas Rodriques | Portmore | Completed | Load_238351 | Naggo Head - 610 | Jul 18, 2026 7:26am | Jul 18, 2026 7:27am | Jul 18, 2026 4:58pm | Jul 18, 2026 5:01pm | Jul 18, 2026 5:56pm | Jul 18, 2026 6:21pm | Jul 18, 2026 6:24pm | Jul 18, 2026 6:24pm |  |  | Fair | No | Customer was located and stated that he was having an internal issue which was resolved by his electrician.
Outage | J.E.26.07.20636 | C001858375 | Nickolas Rodriques | Portmore | Completed | Load_240647 | Naggo Head - 610 | Jul 18, 2026 7:26am | Jul 18, 2026 7:27am | Jul 18, 2026 4:00pm | Jul 18, 2026 4:01pm | Jul 18, 2026 4:39pm | Jul 18, 2026 4:51pm | Jul 18, 2026 4:53pm | Jul 18, 2026 4:53pm |  |  | Fair | No | Customer stated that she did not make any report and she is not having any issues with her power supply at her premises.
Outage | J.E.26.07.20671 | C001858374 | Donald Cunningham | St.Catherine | Completed | Load_268607 | Twickenham - 210 | Jul 18, 2026 7:26am | Jul 18, 2026 8:00am | Jul 18, 2026 11:27am | Jul 18, 2026 12:55pm | Jul 18, 2026 1:46pm | Jul 18, 2026 2:03pm | Jul 18, 2026 2:05pm | Jul 18, 2026 2:05pm |  |  | Fair | No | Banging secondary conductor cause by illegal connection have same removed and restored supply
Outage | J.E.26.07.20730 | C001858373 | Nickolas Rodriques | Portmore | Completed | Load_570185 | Naggo Head - 610 | Jul 18, 2026 7:25am | Jul 18, 2026 7:27am | Jul 18, 2026 11:45am | Jul 18, 2026 11:46am | Jul 18, 2026 11:53am | Jul 18, 2026 11:55am | Jul 18, 2026 11:56am | Jul 18, 2026 11:56am |  |  | Fair | No | Area has electricity. Customer is reporting a defective streetlight. Refer to maintenance.
Outage | J.E.26.07.20790 | C001858372 | Moses Elliston | Portmore | Completed | Load_253527 | Naggo Head - 610 | Jul 18, 2026 7:25am | Jul 18, 2026 7:27am | Jul 18, 2026 11:25am | Jul 18, 2026 11:25am | Jul 18, 2026 12:33pm | Jul 18, 2026 12:34pm | Jul 18, 2026 12:35pm | Jul 18, 2026 12:35pm |  |  | Fair | No | Credit added to prepaid account,also defective collector changed.
Outage | J.E.26.07.19855 | C001858371 | Donald Cunningham | Portmore | Completed | Load_257303 | Naggo Head - 510 | Jul 18, 2026 7:24am | Jul 18, 2026 8:00am | Jul 18, 2026 10:34am | Jul 18, 2026 10:34am | Jul 18, 2026 11:15am | Jul 18, 2026 11:15am | Jul 18, 2026 11:21am | Jul 18, 2026 11:21am |  |  | Fair | No | Premises not located customer not reachable
Outage | J.E.26.07.20721 | C001858370 | Donald Cunningham | St.Catherine | Completed | Load_245565 | Twickenham - 210 | Jul 18, 2026 7:24am | Jul 18, 2026 8:00am | Jul 18, 2026 11:29am | Jul 18, 2026 11:29am | Jul 18, 2026 12:30pm | Jul 18, 2026 12:55pm | Jul 18, 2026 12:55pm | Jul 18, 2026 12:55pm |  |  | Fair | No | Premises closed
Outage | J.E.26.07.20860 | C001858368 | Christopher Edwards | KSAN | Completed | Load_259340 | Constant Spring - 410 | Jul 18, 2026 7:22am | Jul 18, 2026 7:25am | Jul 18, 2026 7:33am | Jul 18, 2026 9:11am | Jul 18, 2026 10:22am | Jul 18, 2026 10:53am | Jul 18, 2026 10:54am | Jul 18, 2026 10:54am |  |  | Fair | No | Reset 25 kva transformer Clear tree limb off open secondary that was causing open secondary wire to bang
Outage | J.E.26.07.16120 | C001858367 | Cliton Henry | St.Ann | Completed | Load_265764 | Upper White River - 110 | Jul 18, 2026 7:20am | Jul 18, 2026 7:50am | Jul 18, 2026 11:16am | Jul 18, 2026 11:16am | Jul 18, 2026 1:19pm | Jul 18, 2026 1:31pm | Jul 18, 2026 1:40pm | Jul 18, 2026 1:40pm |  |  | Fair | No | A blown 20 amp junction fuse found at Bellevue property at pole #0145043. Supply restored using 1-20 amp fuse
Outage | J.E.26.07.20400 | C001858366 | Collin Robinson | Portland | Completed | Load_251558 | Port Antonio - 310 | Jul 18, 2026 7:14am | Jul 18, 2026 7:25am | Jul 18, 2026 9:42am | Jul 18, 2026 9:42am | Jul 18, 2026 9:44am | Jul 18, 2026 9:47am | Jul 18, 2026 9:47am | Jul 18, 2026 9:47am |  |  | Fair | No | Unable to locate customer
Non-Outage | J.E.26.07.20103 | C001858363 | Milton Charlton | KSAN | Completed | Load_266412 | West Kings House - 410 | Jul 18, 2026 2:26am | Jul 18, 2026 7:54am | Jul 18, 2026 9:10am | Jul 18, 2026 10:14am | Jul 18, 2026 10:57am | Jul 18, 2026 10:10am | Jul 18, 2026 11:01am | Jul 18, 2026 11:01am |  |  | Fair | No | Customer service wire #2/0 triplex neutral broken in mid-span ( disconnected from splicing sleeve). Need bucket truck to repair broken neutral.
Outage | J.E.26.07.20776 | C001858351 | Edward Royal | KSAS | Completed | Load_238088 | Hunts Bay - 510 | Jul 17, 2026 11:47pm | Jul 17, 2026 11:48pm | Jul 18, 2026 12:31am | Jul 18, 2026 12:31am | Jul 18, 2026 1:21am | Jul 18, 2026 1:31am | Jul 18, 2026 1:32am | Jul 18, 2026 1:32am |  |  | Fair | No | Replaced 30A junction fuse no pole #. Also defective 15kva transformer needs to be replaced box # EG 01317 pole #0052395 referred to in house crew
Outage | J.E.26.07.20519 | C001858350 | Delano Gayle | St.Catherine | Completed | Load_1001610 | Tredegar - 310 | Jul 17, 2026 11:46pm | Jul 17, 2026 11:46pm | Jul 18, 2026 5:25am | Jul 18, 2026 5:25am | Jul 18, 2026 5:26am | Jul 18, 2026 5:27am | Jul 18, 2026 5:27am | Jul 18, 2026 5:27am |  |  | Fair | No | Premises not located no answer from customer phone
Outage | J.E.26.07.19989 | C001858348 | Edward Royal | KSAS | Completed | Load_257086 | Up Park Camp - 510 | Jul 17, 2026 11:04pm | Jul 18, 2026 8:04am | Jul 18, 2026 1:07pm | Jul 18, 2026 1:07pm | Jul 18, 2026 1:07pm | Jul 18, 2026 1:08pm | Jul 18, 2026 1:08pm | Jul 18, 2026 1:08pm |  |  | Fair | No | When contacted customer said that nobody is at home
Outage | J.E.26.07.20318 | C001858347 | Edward Royal | KSAS | Completed | Load_245738 | Rockfort - 210 | Jul 17, 2026 11:02pm | Jul 17, 2026 11:03pm | Jul 18, 2026 12:02am | Jul 18, 2026 2:09am | Jul 18, 2026 2:09am | Jul 18, 2026 2:11am | Jul 18, 2026 2:11am | Jul 18, 2026 2:11am |  |  | Fair | No | Unable to communicate with customer
Outage | J.E.26.07.20678 | C001858345 | Edward Royal | KSAN | Completed | Load_244713 | Washington Blvd - 310 | Jul 17, 2026 11:00pm | Jul 17, 2026 11:03pm | Jul 18, 2026 12:20am | Jul 18, 2026 12:20am | Jul 18, 2026 12:23am | Jul 18, 2026 12:30am | Jul 18, 2026 12:31am | Jul 18, 2026 12:31am |  |  | Fair | No | When arrived area was with supply premises found ok
Outage | J.E.26.07.20362 | C001858344 | Edward Royal | KSAN | Completed | Load_249976 | Washington Blvd - 610 | Jul 17, 2026 10:55pm | Jul 17, 2026 10:55pm | Jul 17, 2026 11:33pm | Jul 17, 2026 11:33pm | Jul 17, 2026 11:33pm | Jul 17, 2026 11:47pm | Jul 17, 2026 11:48pm | Jul 17, 2026 11:48pm |  |  | Fair | No | Customer said a jps technician removed the meter from the premises customer was asked to replace a meter socket. Customer reported that they installed a new meter socket and need reconnecting .I asked the customer for the technician number that visit the premises the technician number is 8768783385. He have the meter for the customer
Outage | J.E.26.07.20757 | C001858329 | Hartley Chin | Clarendon | Completed | Load_265787 | Monymusk - 210 | Jul 17, 2026 10:09pm | Jul 18, 2026 7:47am | Jul 18, 2026 12:01pm | Jul 18, 2026 12:01pm | Jul 18, 2026 12:28pm | Jul 18, 2026 1:08pm | Jul 18, 2026 1:15pm | Jul 18, 2026 1:15pm |  |  | SevereWind | No | Found blown 3 AMP fuse on 25 KVA transformer @ pole #0129643 due to tree contact. Cut tree from line, transformer refused.
Outage | J.E.26.07.20733 | C001858328 | Ricky Hall | St.Catherine | Completed | Load_244880 | New Michelton - 410 | Jul 17, 2026 10:08pm | Jul 18, 2026 7:28am | Jul 18, 2026 9:03am | Jul 18, 2026 12:48pm | Jul 18, 2026 12:48pm | Jul 18, 2026 12:48pm | Jul 18, 2026 12:49pm | Jul 18, 2026 12:49pm |  |  | Fair | No | Call associated with outage #20734
Outage | J.E.26.07.20734 | C001858327 | Delano Gayle | St.Catherine | Completed | Load_264678 | New Michelton - 410 | Jul 17, 2026 10:08pm | Jul 17, 2026 10:48pm | Jul 18, 2026 2:24am | Jul 18, 2026 2:24am | Jul 18, 2026 3:29am | Jul 18, 2026 4:43am | Jul 18, 2026 4:43am | Jul 18, 2026 4:43am |  |  | Fair | No | Down 50amps trip saver in 3 phase line heading to riversdale, patrolled line section found line okay for closure test close trip saver however that wasn’t successful, open 1 junction fuse link in 3 phase line just before lucky valley turn off, close trip saver, daylight attention required to detail patrol from junction fuse which was opened to riversdale as line runs through bushes in some spans
Outage | J.E.26.07.20763 | C001858325 | Ricky Hall | St.Catherine | Completed | Load_250039 | New Michelton - 410 | Jul 17, 2026 10:07pm | Jul 18, 2026 7:33am | Jul 18, 2026 12:44pm | Jul 18, 2026 12:51pm | Jul 18, 2026 12:51pm | Jul 18, 2026 12:51pm | Jul 18, 2026 12:51pm | Jul 18, 2026 12:51pm |  |  | Fair | No | Call associated with outage #20374
Outage | J.E.26.07.20727 | C001858311 | Floyd Taylor | Trelawny | Completed | Load_292876 | Greenwood - 210 | Jul 17, 2026 9:21pm | Jul 18, 2026 9:09am | Jul 18, 2026 9:54am | null | Jul 18, 2026 9:54am | Jul 18, 2026 9:57am | Jul 18, 2026 9:57am | Jul 18, 2026 9:57am |  |  | Fair | No | Isolate 25kva transformer,retention lower secondary phase also remake jumper using 2pg clamps. Voltage 116,115,232
Outage | J.E.26.07.20627 | C001858310 | Clyde Brown | Clarendon | Completed | Load_568383 | May Pen - 110 | Jul 17, 2026 9:20pm | Jul 17, 2026 9:21pm | Jul 17, 2026 9:53pm | Jul 17, 2026 9:53pm | Jul 17, 2026 9:53pm | Jul 17, 2026 9:39pm | Jul 17, 2026 9:56pm | Jul 17, 2026 9:56pm |  | Y | Fair | No | Blown 25 amps junction fuse near Big stone caused by tree contact,line cleared and blown fuse replaced.
Outage | J.E.26.07.20704 | C001858309 | Derrick Dawkins | St.James | Completed | Load_575161 | Bogue - 310 | Jul 17, 2026 9:20pm | Jul 17, 2026 11:43pm | Jul 18, 2026 12:06am | Jul 18, 2026 12:06am | Jul 18, 2026 3:50am | Jul 18, 2026 12:20am | Jul 18, 2026 5:08am | Jul 18, 2026 5:08am |  |  | Fair | No | Only customer with out supply refer to field service kaydian
Outage | J.E.26.07.20725 | C001858307 | Nickolas Rodriques | Portmore | Completed | Load_570098 | Naggo Head - 610 | Jul 17, 2026 9:19pm | Jul 17, 2026 9:20pm | Jul 18, 2026 10:39am | Jul 18, 2026 10:45am | Jul 18, 2026 11:35am | Jul 18, 2026 11:43am | Jul 18, 2026 11:45am | Jul 18, 2026 11:45am | BrokenPole |  | Fair | No | No broken pole was found upon arrival. Customer is reporting a defective streetlight (Pole #0086909). Refer to streetlight department.
Outage | J.E.26.07.20712 | C001858302 | Hartley Chin | St.Catherine | Completed | Load_270222 | Rhodens Pen - 310 | Jul 17, 2026 9:09pm | Jul 17, 2026 9:19pm | Jul 18, 2026 7:54am | Jul 18, 2026 9:29am | Jul 18, 2026 9:34am | Jul 18, 2026 10:36am | Jul 18, 2026 10:52am | Jul 18, 2026 10:52am | BrokenWire |  | SevereWind | No | Isolate 100 KVA bank of 2 @ pole # 058490 due to broken open secondary phase found , repair broken phase, re-energized transformer…
Outage | J.E.26.07.20700 | C001858294 | Marlon Brown | Trelawny | Completed | Load_294512 | Duncans - 110 | Jul 17, 2026 8:42pm | Jul 17, 2026 8:44pm | Jul 17, 2026 9:06pm | Jul 17, 2026 9:06pm | Jul 17, 2026 9:42pm | Jul 17, 2026 11:59pm | Jul 17, 2026 11:59pm | Jul 17, 2026 11:59pm |  |  | Fair | No | See permit number 11031 for details. Repair 1 span primary phase.
Outage | J.E.26.07.20660 | C001858289 | Gregory Grossett | Portland | Completed | Load_263641 | Port Antonio - 410 | Jul 17, 2026 8:08pm | Jul 17, 2026 8:09pm | Jul 17, 2026 8:11pm | Jul 17, 2026 8:11pm | Jul 17, 2026 9:28pm | Jul 17, 2026 9:41pm | Jul 17, 2026 9:46pm | Jul 17, 2026 9:46pm |  |  | Fair | No | 3wire meter newly installed found with only one phase connected.Connect phase wire from service line to open secondary line. Voltage readings leave 116, 116 & 233 volts.
Outage | J.E.26.07.20432 | C001858286 | Nickolas Rodriques | Portmore | Completed | Load_262697 | Naggo Head - 610 | Jul 17, 2026 7:50pm | Jul 17, 2026 7:59pm | Jul 17, 2026 8:33pm | Jul 17, 2026 9:13pm | Jul 17, 2026 9:44pm | Jul 17, 2026 9:51pm | Jul 17, 2026 9:54pm | Jul 17, 2026 9:54pm | Fire |  | Fair | No | Unable to locate or communicate with this specific customer. However, the area was patrolled and no noticeable fire/outage was seen.
Outage | J.E.26.07.20642 | C001858285 | Christopher Edwards | null | Completed | Load_253609 | Constant Spring - 310 | Jul 17, 2026 7:50pm | Jul 17, 2026 7:56pm | Jul 17, 2026 8:03pm | Jul 17, 2026 8:03pm | Jul 17, 2026 8:39pm | Jul 17, 2026 9:13pm | Jul 17, 2026 9:14pm | Jul 17, 2026 9:14pm |  |  | Fair | No | Refuse blown junction fuse Using (1) 20 amps
Outage | J.E.26.07.20451 | C001858281 | Delano Gayle | St.Catherine | Completed | Load_241734 | Twickenham - 310 | Jul 17, 2026 7:48pm | Jul 17, 2026 10:50pm | Jul 17, 2026 11:56pm | Jul 17, 2026 11:56pm | Jul 18, 2026 1:19am | Jul 18, 2026 1:39am | Jul 18, 2026 1:39am | Jul 18, 2026 1:39am |  |  | Fair | No | Blown 25kva transformer fuse no pole number patrolled line section and found okay for closure replace 3amps
Outage | J.E.26.07.20623 | C001858282 | Clyde Brown | Clarendon | Completed | Load_255025 | May Pen - 110 | Jul 17, 2026 7:48pm | Jul 17, 2026 7:48pm | Jul 17, 2026 8:14pm | Jul 17, 2026 8:14pm | Jul 17, 2026 9:15pm | Jul 17, 2026 9:39pm | Jul 17, 2026 9:52pm | Jul 17, 2026 9:52pm | Fire | Y | Fair | No | Blown 25 amps junction fuse caused by tree contact,line cleared and blown fuse replaced at Near Big stone.
Outage | J.E.26.07.20503 | C001858279 | Richard Nicholas | St.Catherine | Completed | Load_249979 | Tredegar - 210 | Jul 17, 2026 7:47pm | Jul 18, 2026 7:49am | Jul 18, 2026 8:13am | Jul 18, 2026 8:13am | Jul 18, 2026 10:53am | Jul 18, 2026 11:15am | Jul 18, 2026 11:16am | Jul 18, 2026 11:16am | BrokenWire |  | Fair | No | Area found ok,premises found locked.
Outage | J.E.26.07.20505 | C001858280 | Delano Gayle | St.Catherine | Completed | Load_1001612 | Tredegar - 310 | Jul 17, 2026 7:47pm | Jul 17, 2026 10:49pm | Jul 18, 2026 4:51am | Jul 18, 2026 4:51am | Jul 18, 2026 5:24am | Jul 18, 2026 5:25am | Jul 18, 2026 5:25am | Jul 18, 2026 5:25am |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.20628 | C001858277 | Tyrese Williams | St.Ann | Completed | Load_262708 | Cardiff Hall - 310 | Jul 17, 2026 7:42pm | Jul 17, 2026 7:45pm | Jul 17, 2026 8:18pm | Jul 17, 2026 8:18pm | Jul 17, 2026 10:07pm | Jul 17, 2026 10:09pm | Jul 17, 2026 10:12pm | Jul 17, 2026 10:12pm | Fire |  | Fair | No | Open a 25 kva to splice and retention 3 span of secondary neutral and repair transformer neutral jumper use 1 pg clamp voltage check 114/114/228
Outage | J.E.26.07.20562 | C001858276 | Hartley Chin | Clarendon | Completed | Load_268010 | Parnassus - 310 | Jul 17, 2026 7:36pm | Jul 17, 2026 7:38pm | Jul 17, 2026 8:03pm | Jul 17, 2026 8:03pm | Jul 17, 2026 8:03pm | Jul 17, 2026 8:05pm | Jul 17, 2026 8:05pm | Jul 17, 2026 8:05pm |  |  | Fair | No | Call related to job # 20272 ..
Outage | J.E.26.07.20583 | C001858274 | Floyd Taylor | Trelawny | Completed | Load_237701 | Greenwood - 110 | Jul 17, 2026 7:32pm | Jul 17, 2026 7:39pm | Jul 18, 2026 8:04am | Jul 18, 2026 8:04am | Jul 18, 2026 8:04am | Jul 18, 2026 8:05am | Jul 18, 2026 8:05am | Jul 18, 2026 8:05am |  |  | Fair | No | Isolated 25kva transformer retention one span of secondary,remake secondary jumper using 3pg clamps.
Non-Outage | J.E.26.07.20571 | C001858273 | Floyd Taylor | Trelawny | Completed | Load_237701 | Greenwood - 110 | Jul 17, 2026 7:29pm | Jul 17, 2026 7:39pm | Jul 18, 2026 8:02am | Jul 18, 2026 8:02am | Jul 18, 2026 8:02am | Jul 18, 2026 8:03am | Jul 18, 2026 8:04am | Jul 18, 2026 8:04am |  |  | Fair | No | Isolated 25kva transformer retention one span of secondary,remake secondary jumper using 3pg clamps.c
Outage | J.E.26.07.20589 | C001858272 | Ryan Richards | Manchester | Completed | Load_268222 | Spur Tree - 310 | Jul 17, 2026 7:26pm | Jul 17, 2026 7:26pm | Jul 17, 2026 8:46pm | Jul 17, 2026 8:46pm | Jul 17, 2026 9:05pm | Jul 17, 2026 10:35pm | Jul 17, 2026 10:35pm | Jul 17, 2026 10:35pm |  |  | Fair | No | Area found with out supply line patrol where we located burn off conductor an switch bottom open main junction and reconnected switch bottom and reclose main junction all customers are now with supply
Non-Outage | J.E.26.07.20516 | C001858259 | Floyd Taylor | Trelawny | Completed | Load_237701 | Greenwood - 110 | Jul 17, 2026 7:03pm | Jul 17, 2026 7:08pm | Jul 17, 2026 8:57pm | Jul 17, 2026 8:57pm | Jul 17, 2026 9:31pm | Jul 17, 2026 10:47pm | Jul 17, 2026 10:51pm | Jul 17, 2026 10:51pm |  |  | Fair | No | Retention 1 span of secondary, and remake secondary jumper using 3 clamp and 10ft of number 2 AAC, voltage reading left 117,119,236
Non-Outage | J.E.26.07.20518 | C001858260 | Floyd Taylor | Trelawny | Completed | Load_261734 | Duncans - 210 | Jul 17, 2026 7:03pm | Jul 17, 2026 7:38pm | Jul 18, 2026 9:58am | Jul 18, 2026 9:59am | Jul 18, 2026 10:54am | Jul 18, 2026 10:55am | Jul 18, 2026 10:57am | Jul 18, 2026 10:57am |  |  | Fair | No | Clean and remake joints at pot head using 3 clamps voltage readings left 114,117,221
Outage | J.E.26.07.20525 | C001858258 | Horace Malcolm | St.James | Completed | Load_266637 | Rose Hall - 210 | Jul 17, 2026 7:01pm | Jul 17, 2026 7:08pm | Jul 17, 2026 8:17pm | Jul 17, 2026 8:17pm | Jul 17, 2026 8:50pm | Jul 17, 2026 9:04pm | Jul 17, 2026 9:04pm | Jul 17, 2026 9:04pm |  |  | Fair | No | Clean and remake joints at customer pothead and pole used 3clamps voltage 115-113-228
Outage | J.E.26.07.18254 | C001858255 | Andre Smith | KSAS | Completed | Load_264663 | Three Miles - 410 | Jul 17, 2026 6:49pm | Jul 17, 2026 7:39pm | Jul 17, 2026 10:38pm | Jul 17, 2026 10:38pm | Jul 17, 2026 10:38pm | Jul 17, 2026 10:40pm | Jul 17, 2026 10:40pm | Jul 17, 2026 10:40pm |  |  | Fair | No | Premises found okay supply restored already
Outage | J.E.26.07.19269 | C001858252 | Andre Smith | KSAS | Completed | Load_264663 | Three Miles - 410 | Jul 17, 2026 6:49pm | Jul 17, 2026 7:39pm | Jul 17, 2026 10:40pm | Jul 17, 2026 10:40pm | Jul 17, 2026 10:40pm | Jul 17, 2026 10:40pm | Jul 17, 2026 10:40pm | Jul 17, 2026 10:40pm |  |  | Fair | No | Premises found okay supply restored already
Outage | J.E.26.07.20048 | C001858253 | Andre Smith | KSAS | Completed | Load_264663 | Three Miles - 410 | Jul 17, 2026 6:49pm | Jul 17, 2026 7:39pm | Jul 17, 2026 8:18pm | Jul 17, 2026 8:18pm | Jul 17, 2026 10:00pm | Jul 17, 2026 10:34pm | Jul 17, 2026 10:34pm | Jul 17, 2026 10:34pm |  |  | Fair | No | Premises found okay supply restored already
Non-Outage | J.E.26.07.20477 | C001858247 | Horace Malcolm | St.James | Completed | Load_259132 | Queens Drive - 710 | Jul 17, 2026 6:33pm | Jul 17, 2026 6:44pm | Jul 17, 2026 7:57pm | Jul 17, 2026 7:57pm | Jul 17, 2026 8:04pm | Jul 17, 2026 8:16pm | Jul 17, 2026 8:16pm | Jul 17, 2026 8:16pm |  |  | Fair | No | Unable to locate premises from directions given multiple phone calls to customer unavailable
Outage | J.E.26.07.20346 | C001858246 | Richman Whyte | Westmoreland | Completed | Load_246221 | Paradise - 310 | Jul 17, 2026 6:26pm | Jul 17, 2026 6:26pm | Jul 18, 2026 11:49am | Jul 18, 2026 11:49am | Jul 18, 2026 11:49am | Jul 18, 2026 12:19pm | Jul 18, 2026 12:20pm | Jul 18, 2026 12:20pm |  |  | Fair | No | Connect back customer after hurricane voltage 114 115 230 use 103 feet #6 triplex
Outage | J.E.26.07.20404 | C001858245 | Richman Whyte | Westmoreland | Completed | Load_241436 | Paradise - 310 | Jul 17, 2026 6:26pm | Jul 17, 2026 6:26pm | Jul 18, 2026 4:07pm | Jul 18, 2026 4:07pm | Jul 18, 2026 4:07pm | Jul 18, 2026 4:07pm | Jul 18, 2026 4:08pm | Jul 18, 2026 4:08pm |  |  | Fair | No | Restore from yesterday burnt transformer was in the area
Outage | J.E.26.07.20425 | C001858244 | Hartley Chin | Clarendon | Completed | Load_268157 | Parnassus - 210 | Jul 17, 2026 6:21pm | Jul 17, 2026 7:49pm | Jul 17, 2026 8:54pm | Jul 17, 2026 8:54pm | Jul 17, 2026 10:28pm | Jul 17, 2026 11:06pm | Jul 17, 2026 11:12pm | Jul 17, 2026 11:12pm |  |  | Fair | No | Re-energize bank of 3 (100 KVA transformer) @ pole # 575381 … voltage read : 235v-236v-235v …
Outage | J.E.26.07.20384 | C001858241 | Nickolas Rodriques | St.Catherine | Completed | Load_269729 | Twickenham - 210 | Jul 17, 2026 6:10pm | Jul 17, 2026 6:11pm | Jul 17, 2026 6:25pm | Jul 17, 2026 6:33pm | Jul 17, 2026 7:04pm | Jul 17, 2026 7:40pm | Jul 17, 2026 7:43pm | Jul 17, 2026 7:43pm |  |  | Fair | No | Checked and found junction fuse link open due to switch lead burnt off from switch bottom. Repaired by connecting lead and replaced the fuse after completing patrol.
Outage | J.E.26.07.20390 | C001858240 | Nickolas Rodriques | St.Catherine | Completed | Load_256307 | Twickenham - 210 | Jul 17, 2026 6:10pm | Jul 17, 2026 6:11pm | Jul 17, 2026 7:44pm | Jul 17, 2026 7:44pm | Jul 17, 2026 8:26pm | Jul 17, 2026 8:27pm | Jul 17, 2026 8:29pm | Jul 17, 2026 8:29pm |  |  | Fair | No | Call relates to the switch lead that was repaired. Power restored.
Non-Outage | J.E.26.07.20416 | C001858236 | Stephen Taylor | St.Thomas | Completed | Load_577158 | Lysson - 410 | Jul 17, 2026 5:57pm | Jul 17, 2026 5:59pm | Jul 18, 2026 10:33am | Jul 18, 2026 10:33am | Jul 18, 2026 10:53am | Jul 18, 2026 10:54am | Jul 18, 2026 10:55am | Jul 18, 2026 10:55am | BrokenWire |  | Fair | No | Failed to locate customer several calls to phone and no one answering need more information
Outage | J.E.26.07.20459 | C001858234 | Marlon Brown | Trelawny | Completed | Load_257490 | Duncans - 210 | Jul 17, 2026 5:57pm | Jul 17, 2026 5:59pm | Jul 17, 2026 7:04pm | Jul 17, 2026 7:06pm | Jul 17, 2026 7:06pm | Jul 17, 2026 7:38pm | Jul 17, 2026 7:38pm | Jul 17, 2026 7:38pm |  |  | Fair | No | Isolated 50kva transformer to repair 1 span secondary neutral. Illegal connections caused line to burn down. Voltage found at pole 116/114=230vVoltage leaving at pole 116/114=230v.
Outage | J.E.26.07.20467 | C001858235 | Marlon Brown | Trelawny | Completed | Load_267170 | Duncans - 210 | Jul 17, 2026 5:57pm | Jul 17, 2026 5:59pm | Jul 17, 2026 7:38pm | Jul 17, 2026 7:38pm | Jul 17, 2026 7:38pm | Jul 17, 2026 7:39pm | Jul 17, 2026 7:40pm | Jul 17, 2026 7:40pm |  |  | Fair | No | Same as call number 20459.
Non-Outage | J.E.26.07.06494 | C001858231 | Raymond Carr | St.Mary | Completed | Load_266777 | Blackstonedge - 110 | Jul 17, 2026 5:41pm | Jul 17, 2026 5:41pm | Jul 17, 2026 6:42pm | Jul 17, 2026 6:42pm | Jul 17, 2026 7:20pm | Jul 17, 2026 7:00pm | Jul 17, 2026 7:22pm | Jul 17, 2026 7:22pm | Fire |  | Fair | No | Customer was contacted, however she did not make any report.
Non-Outage | J.E.26.07.06937 | C001858230 | Raymond Carr | St.Mary | Completed | Load_265217 | Blackstonedge - 110 | Jul 17, 2026 5:41pm | Jul 17, 2026 5:41pm | Jul 17, 2026 5:48pm | Jul 17, 2026 5:48pm | Jul 17, 2026 6:40pm | Jul 17, 2026 6:30pm | Jul 17, 2026 6:41pm | Jul 17, 2026 6:41pm | LeaningPole |  | EarthMovement | No | Several calls to contact number went unanswered.
Non-Outage | J.E.26.07.06383 | C001858227 | Omar King | St.Ann | Completed | Load_269325 | Upper White River - 110 | Jul 17, 2026 5:36pm | Jul 17, 2026 5:36pm | Jul 17, 2026 6:33pm | Jul 17, 2026 6:33pm | Jul 17, 2026 6:34pm | Jul 17, 2026 7:57pm | Jul 17, 2026 7:58pm | Jul 17, 2026 7:58pm | LeaningPole |  | Fair | No | Found secondary pole leaning need maintenance attention
Outage | J.E.26.07.20441 | C001858225 | Wan Carlos Scarlett | St.Catherine | Completed | Load_268625 | Rhodens Pen - 210 | Jul 17, 2026 5:29pm | Jul 17, 2026 6:09pm | Jul 18, 2026 7:28am | Jul 18, 2026 7:28am | Jul 18, 2026 8:57am | Jul 18, 2026 9:52am | Jul 18, 2026 9:55am | Jul 18, 2026 9:55am | BrokenWire |  | Fair | No | Found customer 3 wire service at pothead with one of the phase broken off use one Penn union at service wire phase readings 115-114-230
Non-Outage | J.E.26.07.20435 | C001858222 | Tyrese Williams | null | Completed | null | null | Jul 17, 2026 5:22pm | Jul 17, 2026 5:24pm | Jul 17, 2026 7:05pm | Jul 17, 2026 7:05pm | Jul 17, 2026 7:07pm | Jul 17, 2026 7:08pm | Jul 17, 2026 7:08pm | Jul 17, 2026 7:08pm | BrokenWire |  | Fair | No | Premises found ok call related to broken secondary phase and neutral
Non-Outage | J.E.26.07.18517 | C001858216 | Marlon Brown | Trelawny | Completed | Load_257942 | Duncans - 210 | Jul 17, 2026 5:09pm | Jul 17, 2026 5:10pm | Jul 17, 2026 6:10pm | Jul 18, 2026 9:27am | Jul 18, 2026 10:09am | Jul 18, 2026 10:39am | Jul 18, 2026 10:39am | Jul 18, 2026 10:39am | LeaningPole |  | Fair | No | 2 class 4 40ft poles are leaning needs to be straightened, refer to maintenance personnel O. Ellis.
Non-Outage | J.E.26.07.20378 | C001858215 | Marlon Brown | Trelawny | Completed | Load_556439 | Duncans - 210 | Jul 17, 2026 5:08pm | Jul 17, 2026 5:10pm | Jul 17, 2026 6:11pm | Jul 17, 2026 7:40pm | Jul 17, 2026 7:58pm | Jul 17, 2026 7:59pm | Jul 17, 2026 7:59pm | Jul 17, 2026 7:59pm |  |  | Fair | No | Unable to locate customer via telephone nor direction
Outage | J.E.26.07.20418 | C001858213 | Evan Spaulding | St.Mary | Completed | Load_249746 | Highgate -110 | Jul 17, 2026 5:03pm | Jul 17, 2026 5:12pm | Jul 17, 2026 7:29pm | Jul 17, 2026 7:29pm | Jul 17, 2026 7:43pm | Jul 17, 2026 8:14pm | Jul 17, 2026 8:15pm | Jul 17, 2026 8:15pm | BrokenWire |  | Fair | No | Use 2-1 bolt clamps at pole, voltage left 113v.
Outage | J.E.26.07.20294 | C001858208 | Ryan Richards | Manchester | Completed | Load_241372 | Spur Tree - 310 | Jul 17, 2026 4:55pm | Jul 17, 2026 4:56pm | Jul 17, 2026 7:05pm | Jul 17, 2026 7:05pm | Jul 17, 2026 7:40pm | Jul 17, 2026 8:46pm | Jul 17, 2026 8:46pm | Jul 17, 2026 8:46pm | Fire |  | Fair | No | Secondary and primary line banging after vegetation work where carried out in area line is extensive long and needs an intermediate pole to resolve the issue permanently however efforts made to carry out repairs but pol is rocking badly And rotten at base there four no tension can be done an the line safety please refer to maintenance to plant an intermediate and also replace the rotten pole all customers are with supply but if any heavy breeze or any adverse weather conditions the line can bang again
Outage | J.E.26.07.19992 | C001858205 | Wan Carlos Scarlett | St.Catherine | Completed | Load_252781 | Tredegar - 210 | Jul 17, 2026 4:53pm | Jul 17, 2026 4:54pm | Jul 17, 2026 10:01pm | Jul 17, 2026 10:01pm | Jul 17, 2026 10:39pm | Jul 18, 2026 7:26am | Jul 18, 2026 7:27am | Jul 18, 2026 7:27am | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Found customer 3 wire service at pole with phase and neutral corroded use 3 one bolt clamps at open secondary line readings 115-116-231
Outage | J.E.26.07.20330 | C001858203 | Wan Carlos Scarlett | St.Catherine | Completed | Load_257606 | Rhodens Pen - 210 | Jul 17, 2026 4:53pm | Jul 17, 2026 4:54pm | Jul 17, 2026 5:38pm | Jul 17, 2026 9:35pm | Jul 17, 2026 9:35pm | Jul 17, 2026 9:51pm | Jul 17, 2026 9:59pm | Jul 17, 2026 9:59pm |  |  | Fair | No | Found customer with internal problem advised customer to get a licensed electrician to fix the problem.Meter socket defective isolate 3 wire service at pothead
Outage | J.E.26.07.20355 | C001858204 | Wan Carlos Scarlett | St.Catherine | Completed | Load_256389 | Rhodens Pen - 210 | Jul 17, 2026 4:53pm | Jul 17, 2026 4:54pm | Jul 17, 2026 5:06pm | Jul 17, 2026 5:06pm | Jul 17, 2026 6:58pm | Jul 17, 2026 9:30pm | Jul 17, 2026 9:33pm | Jul 17, 2026 9:33pm |  |  | Fair | No | Found 25KVA transformer drop lead wire to open secondary line phase burn out from the one bolt clamps use 6 one bolt clamps at pole readings 116-117-234
Outage | J.E.26.07.19969 | C001858202 | Richard Grant | St.Catherine | Completed | Load_556137 | New Michelton - 410 | Jul 17, 2026 4:52pm | Jul 17, 2026 4:52pm | Jul 17, 2026 5:10pm | Jul 17, 2026 5:10pm | Jul 17, 2026 6:11pm | Jul 17, 2026 7:12pm | Jul 17, 2026 7:12pm | Jul 17, 2026 7:12pm |  |  | Fair | No | 8amps fuse found blown and 25kva transformer found tripped caused by jps bushing contractor cutting tree and banging lines. 8amps fuse replaced with same, 25kva transformer reset and supply restored in area. A single customer complained about damaged stanchion caused by bushing team. Kindly send email to A. Murray informing about customer complaint. Area left okay.
Outage | J.E.26.07.20272 | C001858196 | Hartley Chin | Clarendon | Completed | Load_247186 | Parnassus - 310 | Jul 17, 2026 4:48pm | Jul 17, 2026 4:49pm | Jul 17, 2026 5:30pm | Jul 17, 2026 5:34pm | Jul 17, 2026 6:57pm | Jul 17, 2026 7:26pm | Jul 17, 2026 7:28pm | Jul 17, 2026 7:28pm |  |  | Fair | No | Isolate 50 KVA transformer @ pole # 0122555 due to open secondary span found with missing neutral , replace approximately 120ft #2 conductor (neutral) in 1 span , re-energize transformer… use 120 ft #2 conductor, 3 clamp …
Outage | J.E.26.07.20176 | C001858195 | Hartley Chin | Clarendon | Completed | Load_265787 | Monymusk - 210 | Jul 17, 2026 4:46pm | Jul 17, 2026 4:46pm | Jul 17, 2026 5:11pm | Jul 17, 2026 8:15pm | Jul 17, 2026 8:44pm | Jul 17, 2026 8:53pm | Jul 17, 2026 8:54pm | Jul 17, 2026 8:54pm |  |  | SevereWind | No | Found blown 3 amp fuse on 25 KVA transformer @ pole # 0129643 line patrolled and found okay , transformer refused..
Outage | J.E.26.07.20331 | C001858194 | Hartley Chin | Clarendon | Completed | Load_265466 | Parnassus - 210 | Jul 17, 2026 4:46pm | Jul 17, 2026 4:46pm | Jul 18, 2026 1:15pm | Jul 18, 2026 1:16pm | Jul 18, 2026 4:23pm | Jul 18, 2026 5:16pm | Jul 18, 2026 5:28pm | Jul 18, 2026 5:28pm |  |  | SevereWind | No | Prem not found .. area patrolled, unable to find customer meter… unable to contact customer with contact # provided…
Outage | J.E.26.07.20372 | C001858193 | Hartley Chin | Clarendon | Completed | Load_259064 | Parnassus - 310 | Jul 17, 2026 4:46pm | Jul 17, 2026 4:46pm | Jul 17, 2026 5:30pm | Jul 17, 2026 8:09pm | Jul 17, 2026 8:10pm | Jul 17, 2026 8:11pm | Jul 17, 2026 8:15pm | Jul 17, 2026 8:15pm |  |  | Fair | No | Premisis not found. Unable to contact customer.
Outage | J.E.26.07.20408 | C001858188 | Tyrese Williams | St.Ann | Completed | Load_262708 | Cardiff Hall - 310 | Jul 17, 2026 4:40pm | Jul 17, 2026 4:41pm | Jul 17, 2026 7:09pm | Jul 17, 2026 7:09pm | Jul 17, 2026 7:13pm | Jul 17, 2026 7:15pm | Jul 17, 2026 7:19pm | Jul 17, 2026 7:19pm | Fire |  | Fair | No | Premises not not found not getting customer
Non-Outage | J.E.26.07.19697 | C001858179 | Richard Grant | null | Completed | null | null | Jul 17, 2026 4:28pm | Jul 17, 2026 4:30pm | Jul 17, 2026 9:41pm | Jul 17, 2026 9:41pm | Jul 17, 2026 9:41pm | Jul 17, 2026 9:42pm | Jul 17, 2026 9:42pm | Jul 17, 2026 9:42pm |  |  | Fair | No | Premises found okay
Non-Outage | J.E.26.07.19711 | C001858176 | Richard Grant | null | Completed | null | null | Jul 17, 2026 4:28pm | Jul 17, 2026 4:30pm | Jul 17, 2026 8:08pm | Jul 17, 2026 8:08pm | Jul 17, 2026 8:38pm | Jul 17, 2026 8:42pm | Jul 17, 2026 8:42pm | Jul 17, 2026 8:42pm |  |  | Fair | No | Premises found okay
Non-Outage | J.E.26.07.19750 | C001858178 | Richard Grant | null | Completed | null | null | Jul 17, 2026 4:28pm | Jul 17, 2026 4:30pm | Jul 17, 2026 9:15pm | Jul 17, 2026 9:15pm | Jul 17, 2026 9:37pm | Jul 17, 2026 9:38pm | Jul 17, 2026 9:39pm | Jul 17, 2026 9:39pm |  |  | Fair | No | Premises found okay
Non-Outage | J.E.26.07.19769 | C001858177 | Richard Grant | null | Completed | null | null | Jul 17, 2026 4:28pm | Jul 17, 2026 4:30pm | Jul 17, 2026 8:42pm | Jul 17, 2026 8:42pm | Jul 17, 2026 9:15pm | Jul 17, 2026 9:15pm | Jul 17, 2026 9:15pm | Jul 17, 2026 9:15pm |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.19633 | C001858182 | Richard Grant | St.Catherine | Completed | Load_240025 | New Michelton - 410 | Jul 17, 2026 4:28pm | Jul 17, 2026 4:30pm | Jul 17, 2026 9:43pm | Jul 17, 2026 9:44pm | Jul 17, 2026 10:28pm | Jul 17, 2026 10:29pm | Jul 17, 2026 10:33pm | Jul 17, 2026 10:33pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.19660 | C001858181 | Richard Grant | St.Catherine | Completed | Load_255806 | New Michelton - 410 | Jul 17, 2026 4:28pm | Jul 17, 2026 4:30pm | Jul 17, 2026 9:43pm | Jul 17, 2026 9:43pm | Jul 17, 2026 9:43pm | Jul 17, 2026 9:43pm | Jul 17, 2026 9:43pm | Jul 17, 2026 9:43pm |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.19694 | C001858180 | Richard Grant | St.Catherine | Completed | Load_257901 | New Michelton - 410 | Jul 17, 2026 4:28pm | Jul 17, 2026 4:30pm | Jul 17, 2026 9:42pm | Jul 17, 2026 9:42pm | Jul 17, 2026 9:42pm | Jul 17, 2026 9:42pm | Jul 17, 2026 9:42pm | Jul 17, 2026 9:42pm |  |  | Fair | No | Premises found okay
Non-Outage | J.E.26.07.19811 | C001858174 | Richard Grant | null | Completed | null | null | Jul 17, 2026 4:27pm | Jul 17, 2026 4:30pm | Jul 17, 2026 7:15pm | Jul 17, 2026 7:15pm | Jul 17, 2026 7:55pm | Jul 17, 2026 8:08pm | Jul 17, 2026 8:08pm | Jul 17, 2026 8:08pm |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.20226 | C001858175 | Richard Grant | St.Catherine | Completed | Load_257901 | New Michelton - 410 | Jul 17, 2026 4:27pm | Jul 17, 2026 4:30pm | Jul 17, 2026 5:15pm | Jul 17, 2026 7:13pm | Jul 17, 2026 7:13pm | Jul 17, 2026 7:15pm | Jul 17, 2026 7:15pm | Jul 17, 2026 7:15pm |  |  | Fair | No | 8amps fuse found blown and 25kva transformer found tripped caused by jps bushing contractor cutting tree and banging lines. 8amps fuse replaced with same, 25kva transformer reset and supply restored in area. A single customer complained about damaged stanchion caused by bushing team. Kindly send email to A. Murray informing about customer complaint. Customers name is Sylvia Ashman and her contact is 876 427-0227. Area left okay.
Outage | J.E.26.07.20374 | C001858173 | Gregory Grossett | Portland | Completed | Load_349128 | Port Antonio - 410 | Jul 17, 2026 4:27pm | Jul 17, 2026 4:40pm | Jul 17, 2026 5:08pm | Jul 17, 2026 5:08pm | Jul 17, 2026 5:32pm | Jul 17, 2026 5:55pm | Jul 17, 2026 6:01pm | Jul 17, 2026 6:01pm | BrokenWire |  | Fair | No | Tree fell on service lines resulting broken wire, fallen meter pole and damaged pothead wires. Advised customer to contact a licensed electrician to carry out repairs. Disconnect to service line at pole to make area safe.
Outage | J.E.26.07.20119 | C001858172 | Nickolas Rodriques | St.Catherine | Completed | Load_239984 | Twickenham - 210 | Jul 17, 2026 4:26pm | Jul 17, 2026 4:59pm | Jul 17, 2026 8:40pm | Jul 17, 2026 8:40pm | Jul 17, 2026 9:05pm | Jul 17, 2026 9:11pm | Jul 17, 2026 9:12pm | Jul 17, 2026 9:12pm | BrokenWire |  | Fair | No | Found customer with electricity. Issue was resolved earlier today.
Outage | J.E.26.07.20141 | C001858170 | Donald Cunningham | St.Catherine | Completed | Load_270044 | Twickenham - 210 | Jul 17, 2026 4:23pm | Jul 18, 2026 8:00am | Jul 18, 2026 5:26pm | Jul 18, 2026 5:26pm | Jul 18, 2026 6:23pm | Jul 18, 2026 6:24pm | Jul 18, 2026 6:28pm | Jul 18, 2026 6:28pm |  |  | Fair | No | Premises closed
Outage | J.E.26.07.20383 | C001858163 | Evan Spaulding | St.Mary | Completed | Load_265883 | Highgate -110 | Jul 17, 2026 4:15pm | Jul 17, 2026 4:16pm | Jul 17, 2026 5:35pm | Jul 17, 2026 5:35pm | Jul 17, 2026 6:58pm | Jul 17, 2026 6:58pm | Jul 17, 2026 7:00pm | Jul 17, 2026 7:00pm |  |  | SevereWind | No | Retention secondary conductors and use 6-1 bolt clamps, 117v,117v,234v.
Outage | J.E.26.07.20189 | C001858153 | Christopher Edwards | KSAN | Completed | Load_250736 | Constant Spring - 210 | Jul 17, 2026 4:03pm | Jul 17, 2026 4:04pm | Jul 17, 2026 4:06pm | Jul 17, 2026 4:21pm | Jul 17, 2026 4:44pm | Jul 17, 2026 5:22pm | Jul 17, 2026 5:23pm | Jul 17, 2026 5:23pm |  |  | Fair | No | Customer seems to be having an issue with faulty breaker Voltage at meter pole 115,114,230vCustomer was advised to get electrician to fix issue
Outage | J.E.26.07.20216 | C001858154 | Christopher Edwards | KSAN | Completed | Load_579095 | Constant Spring - 210 | Jul 17, 2026 4:03pm | Jul 17, 2026 4:04pm | Jul 17, 2026 5:24pm | Jul 17, 2026 5:24pm | Jul 17, 2026 5:39pm | Jul 17, 2026 6:55pm | Jul 17, 2026 8:03pm | Jul 17, 2026 8:03pm |  |  | Fair | No | Remake corroded phase joint Using (2) one bolt clamps Voltage:115,114,230v
Non-Outage | J.E.26.07.19151 | C001858152 | Andre Smith | KSAS | Completed | Load_263277 | Hunts Bay - 310 | Jul 17, 2026 4:02pm | Jul 17, 2026 4:03pm | Jul 17, 2026 4:30pm | Jul 17, 2026 4:30pm | Jul 17, 2026 5:39pm | Jul 17, 2026 6:03pm | Jul 17, 2026 6:03pm | Jul 17, 2026 6:03pm |  |  | Fair | No | Replace defective hotline clamp supply restored
Outage | J.E.26.07.20367 | C001858149 | Evan Spaulding | St.Mary | Completed | Load_258006 | Highgate -110 | Jul 17, 2026 3:58pm | Jul 17, 2026 3:58pm | Jul 17, 2026 7:00pm | Jul 17, 2026 7:00pm | Jul 17, 2026 7:25pm | Jul 17, 2026 7:25pm | Jul 17, 2026 7:27pm | Jul 17, 2026 7:27pm | Fire |  | Fair | No | Not getting through to customer,went to location no fire seeing.
Outage | J.E.26.07.20363 | C001858144 | Raymond Lewis | St.Ann | Completed | Load_575099 | Roaring River - 410 | Jul 17, 2026 3:54pm | Jul 17, 2026 3:55pm | Jul 17, 2026 6:26pm | Jul 17, 2026 6:26pm | Jul 17, 2026 6:35pm | Jul 17, 2026 6:36pm | Jul 17, 2026 6:37pm | Jul 17, 2026 6:37pm |  |  | Fair | No | Need local number to call customer
Outage | J.E.26.07.20342 | C001858143 | Rayon Foster | Hanover | Completed | Load_269750 | Orange Bay - 210 | Jul 17, 2026 3:51pm | Jul 17, 2026 3:52pm | Jul 17, 2026 4:17pm | Jul 17, 2026 5:26pm | Jul 17, 2026 5:27pm | Jul 17, 2026 6:48pm | Jul 17, 2026 6:48pm | Jul 17, 2026 6:48pm |  |  | Fair | No | Patrol primary line to fine one blow 15 amps junction fuse blow line was safe to close replace with same and close
Outage | J.E.26.07.20295 | C001858138 | Raymond Carr | St.Mary | Completed | Load_261325 | Blackstonedge - 110 | Jul 17, 2026 3:47pm | Jul 17, 2026 3:49pm | Jul 17, 2026 4:30pm | Jul 17, 2026 4:30pm | Jul 17, 2026 4:30pm | Jul 17, 2026 4:15pm | Jul 17, 2026 4:31pm | Jul 17, 2026 4:31pm |  |  | Fair | No | Supply was restored.
Non-Outage | J.E.26.07.13003 | C001858126 | Tajay Bernard | null | Completed | null | null | Jul 17, 2026 3:39pm | Jul 17, 2026 3:52pm | Jul 17, 2026 6:29pm | Jul 17, 2026 6:29pm | Jul 17, 2026 6:29pm | Jul 17, 2026 6:30pm | Jul 17, 2026 6:30pm | Jul 17, 2026 6:30pm |  |  | Fair | No | Customer stated that the issue has been resolved
Outage | J.E.26.07.20341 | C001858127 | Tyrese Williams | St.Ann | Completed | Load_263962 | Cardiff Hall - 310 | Jul 17, 2026 3:39pm | Jul 17, 2026 3:40pm | Jul 17, 2026 3:57pm | Jul 17, 2026 4:09pm | Jul 17, 2026 4:30pm | Jul 17, 2026 4:30pm | Jul 17, 2026 4:30pm | Jul 17, 2026 4:30pm |  |  | Fair | No | Premises found ok customer said everything is ok at the premises
Non-Outage | J.E.26.07.18078 | C001858125 | Stephen Taylor | St.Thomas | Completed | Load_258784 | Lysson - 410 | Jul 17, 2026 3:38pm | Jul 17, 2026 3:39pm | Jul 17, 2026 4:14pm | Jul 17, 2026 4:14pm | Jul 17, 2026 5:54pm | Jul 17, 2026 5:54pm | Jul 17, 2026 5:56pm | Jul 17, 2026 5:56pm | Fire |  | Fair | No | Clear tree from line. Area is okay now
Non-Outage | J.E.26.07.18226 | C001858124 | Stephen Taylor | null | Completed | null | null | Jul 17, 2026 3:38pm | Jul 17, 2026 3:39pm | Jul 17, 2026 5:57pm | Jul 17, 2026 5:57pm | Jul 17, 2026 5:57pm | Jul 17, 2026 5:57pm | Jul 17, 2026 5:58pm | Jul 17, 2026 5:58pm | Fire |  | Fair | No | Clear tree from line area is now safe customer is now okay
Outage | J.E.26.07.20208 | C001858123 | Stephen Taylor | St.Thomas | Completed | Load_268030 | Lysson - 410 | Jul 17, 2026 3:38pm | Jul 17, 2026 3:39pm | Jul 17, 2026 6:00pm | Jul 17, 2026 6:01pm | Jul 17, 2026 7:28pm | Jul 17, 2026 7:28pm | Jul 17, 2026 7:42pm | Jul 17, 2026 7:42pm |  |  | Fair | No | Clean secondary line with switch stick and close up back 10 amp transformer safely all customer is now okay
Outage | J.E.26.07.20333 | C001858122 | Stephen Taylor | St.Thomas | Completed | Load_243004 | Good Year - 110 | Jul 17, 2026 3:38pm | Jul 17, 2026 3:39pm | Jul 17, 2026 7:42pm | Jul 17, 2026 7:42pm | Jul 17, 2026 8:24pm | Jul 17, 2026 8:24pm | Jul 17, 2026 8:25pm | Jul 17, 2026 8:25pm |  |  | Fair | No | Close up back 25 kva transformer customer is now okay
Outage | J.E.26.07.20217 | C001858119 | Tyrese Williams | St.Ann | Completed | Load_269661 | Cardiff Hall - 310 | Jul 17, 2026 3:35pm | Jul 17, 2026 3:39pm | Jul 17, 2026 3:57pm | Jul 17, 2026 4:32pm | Jul 17, 2026 6:00pm | Jul 17, 2026 7:04pm | Jul 17, 2026 7:04pm | Jul 17, 2026 7:04pm | TreeContact | Y | Fair | No | Open a 50 kva transformer fuse to cut tree from secondary line and splice and retention 4 span of secondary phase and neutral
Outage | J.E.26.07.20110 | C001858109 | Wayne Dillion | St.Elizabeth | Completed | Load_264727 | Maggotty - 110 | Jul 17, 2026 3:30pm | Jul 17, 2026 3:30pm | Jul 17, 2026 5:18pm | Jul 17, 2026 5:18pm | Jul 17, 2026 5:18pm | Jul 17, 2026 6:08pm | Jul 17, 2026 6:07pm | Jul 17, 2026 6:07pm |  |  | Fair | No | Patrol and found one blown 20 amp junction and one blown 15 amp junction no pole number replace the same supply restore to customer successfully
Outage | J.E.26.07.20118 | C001858103 | Ryan Richards | Manchester | Completed | Load_264034 | Porus - 210 | Jul 17, 2026 3:26pm | Jul 17, 2026 3:27pm | Jul 17, 2026 5:54pm | Jul 17, 2026 5:54pm | Jul 17, 2026 6:26pm | Jul 17, 2026 7:05pm | Jul 17, 2026 7:05pm | Jul 17, 2026 7:05pm |  |  | Fair | No | Burn off phase and neutral found affecting three 3 wire meter remade burn off phase and neutral using 4ft#6 service wire 3 one bolt clamps voltage 113/115/219 volts
Outage | J.E.26.07.20200 | C001858101 | Ryan Richards | Manchester | Completed | Load_251668 | Spur Tree - 310 | Jul 17, 2026 3:26pm | Jul 17, 2026 3:27pm | Jul 17, 2026 4:31pm | Jul 17, 2026 4:31pm | Jul 17, 2026 5:33pm | Jul 17, 2026 5:53pm | Jul 17, 2026 5:53pm | Jul 17, 2026 5:53pm |  |  | Fair | No | Burn off phase found at pole caused by illegal connections remade burn off phase using 1 one bolt clamps voltage 114/115/230 volts
Outage | J.E.26.07.20292 | C001858079 | Marlon Authors | Manchester | Completed | Load_302816 | Spur Tree - 210 | Jul 17, 2026 3:21pm | Jul 17, 2026 3:21pm | Jul 17, 2026 5:42pm | Jul 17, 2026 5:42pm | Jul 17, 2026 6:48pm | Jul 17, 2026 6:56pm | Jul 17, 2026 6:56pm | Jul 17, 2026 6:56pm |  |  | Fair | No | Supply checked and found service wires disconnected at pole. Connect same using two clamps
Outage | J.E.26.07.20259 | C001858078 | Romeo Brissett | St.James | Completed | Load_249037 | Bogue - 610 | Jul 17, 2026 3:20pm | Jul 17, 2026 3:23pm | Jul 17, 2026 8:12pm | Jul 17, 2026 8:12pm | Jul 17, 2026 9:53pm | Jul 17, 2026 10:20pm | Jul 17, 2026 10:23pm | Jul 17, 2026 10:23pm |  |  | Fair | No | Customer stated, service wire should not be connect because there’s no one living at the premises
Outage | J.E.26.07.20304 | C001858073 | Raymond Carr | St.Mary | Completed | Load_352949 | Blackstonedge - 110 | Jul 17, 2026 3:19pm | Jul 17, 2026 3:20pm | Jul 17, 2026 4:27pm | Jul 17, 2026 4:27pm | Jul 17, 2026 4:27pm | Jul 17, 2026 4:23pm | Jul 17, 2026 4:28pm | Jul 17, 2026 4:28pm |  |  | Fair | No | Supply was restored.
Non-Outage | J.E.26.07.20192 | C001858072 | Swon Miller | St.James | Completed | Load_269651 | Bogue - 310 | Jul 17, 2026 3:18pm | Jul 17, 2026 3:20pm | Jul 17, 2026 3:33pm | Jul 17, 2026 3:33pm | Jul 17, 2026 3:48pm | Jul 17, 2026 4:16pm | Jul 17, 2026 4:20pm | Jul 17, 2026 4:20pm |  |  | Fair | No | Check and found okay voltage found 116/117/234 customer have internal problems voltage left 117/116/234
Non-Outage | J.E.26.07.20268 | C001858067 | Romeo Brissett | null | Completed | null | null | Jul 17, 2026 3:18pm | Jul 17, 2026 3:19pm | Jul 17, 2026 4:50pm | Jul 17, 2026 4:51pm | Jul 17, 2026 5:16pm | Jul 17, 2026 8:00pm | Jul 17, 2026 8:12pm | Jul 17, 2026 8:12pm |  |  | Fair | No | Over 200ft of Customer service wire was found broken and dislodged from poles by Melissa, however a little over a hundred ft was found in bushes, spliced and retention customer service wire, used 100ft of #6 and 1 clamp. V/R 114-115-230
Non-Outage | J.E.26.07.20288 | C001858071 | Swon Miller | St.James | Completed | Load_242384 | Bogue - 310 | Jul 17, 2026 3:18pm | Jul 17, 2026 3:20pm | Jul 17, 2026 6:22pm | Jul 17, 2026 6:22pm | Jul 17, 2026 8:28pm | Jul 17, 2026 9:18pm | Jul 17, 2026 9:23pm | Jul 17, 2026 9:23pm |  |  | Fair | No | Found customer single phasing at pole voltage found 113 clean and remake joint use 1pg voltage left 115/113/228
Outage | J.E.26.07.20271 | C001858066 | Raymond Carr | St.Mary | Completed | Load_261553 | Blackstonedge - 110 | Jul 17, 2026 3:18pm | Jul 17, 2026 3:20pm | Jul 17, 2026 3:48pm | Jul 17, 2026 3:48pm | Jul 17, 2026 4:22pm | Jul 17, 2026 4:00pm | Jul 17, 2026 4:23pm | Jul 17, 2026 4:23pm |  |  | Fair | No | Customer reported that supply was restored.
Outage | J.E.26.07.20290 | C001858068 | Raymond Carr | St.Mary | Completed | Load_354886 | Blackstonedge - 110 | Jul 17, 2026 3:18pm | Jul 17, 2026 3:20pm | Jul 17, 2026 4:23pm | Jul 17, 2026 4:23pm | Jul 17, 2026 4:23pm | Jul 17, 2026 4:09pm | Jul 17, 2026 4:25pm | Jul 17, 2026 4:25pm |  |  | Fair | No | Supply was restored.
Outage | J.E.26.07.20300 | C001858069 | Raymond Carr | St.Mary | Completed | Load_257713 | Blackstonedge - 110 | Jul 17, 2026 3:18pm | Jul 17, 2026 3:20pm | Jul 17, 2026 4:32pm | Jul 17, 2026 4:32pm | Jul 17, 2026 4:32pm | Jul 17, 2026 4:18pm | Jul 17, 2026 4:33pm | Jul 17, 2026 4:33pm |  |  | Fair | No | Supply was restored.
Outage | J.E.26.07.20322 | C001858057 | Swon Miller | St.James | Completed | Load_268089 | Bogue - 310 | Jul 17, 2026 3:14pm | Jul 17, 2026 3:17pm | Jul 17, 2026 4:20pm | Jul 17, 2026 4:20pm | Jul 17, 2026 5:47pm | Jul 17, 2026 6:16pm | Jul 17, 2026 6:21pm | Jul 17, 2026 6:21pm |  |  | Fair | No | Found customer without supply voltage found 0.000 customer meter pole is more than a 120ft from jps main plz refer to field service voltage left 0.000
Outage | J.E.26.07.20308 | C001858054 | Tajay Bernard | Hanover | Completed | Load_575278 | Orange Bay - 310 | Jul 17, 2026 3:12pm | Jul 17, 2026 3:13pm | Jul 17, 2026 6:30pm | Jul 17, 2026 6:49pm | Jul 17, 2026 7:14pm | Jul 17, 2026 7:22pm | Jul 17, 2026 7:22pm | Jul 17, 2026 7:22pm |  |  | Fair | No | Area check and found okay unable to locate customer on premises multiple phone calls to customer number went unanswered
Outage | J.E.26.07.20241 | C001858049 | Wayne Dillion | St.Elizabeth | Completed | Load_254094 | Maggotty - 110 | Jul 17, 2026 3:11pm | Jul 17, 2026 3:12pm | Jul 17, 2026 6:10pm | Jul 17, 2026 6:10pm | Jul 17, 2026 10:53pm | Jul 18, 2026 9:15am | Jul 18, 2026 12:18am | Jul 18, 2026 12:18am |  |  | Fair | No | Reconnect customer using 300 feet of number 6 triplex 3 linket 3 one bolt clamp voltage reading 112v 111v 224v supply working ok
Outage | J.E.26.07.20140 | C001858047 | Tajay Bernard | Hanover | Completed | Load_257085 | Orange Bay - 310 | Jul 17, 2026 3:08pm | Jul 17, 2026 3:09pm | Jul 17, 2026 6:24pm | Jul 17, 2026 6:24pm | Jul 17, 2026 6:24pm | Jul 17, 2026 6:25pm | Jul 17, 2026 6:25pm | Jul 17, 2026 6:25pm |  |  | Fair | No | This call belongs to st james
Outage | J.E.26.07.20253 | C001858048 | Rayon Foster | Hanover | Completed | Load_251872 | Orange Bay - 210 | Jul 17, 2026 3:08pm | Jul 17, 2026 3:09pm | Jul 17, 2026 4:16pm | Jul 17, 2026 6:49pm | Jul 17, 2026 8:19pm | Jul 17, 2026 8:28pm | Jul 17, 2026 8:28pm | Jul 17, 2026 8:28pm |  |  | Fair | No | Customer reporting resident connected a street light on her service wire going to her house before her meter refer to strike force to investigate
Non-Outage | J.E.26.07.19826 | C001858016 | Omar King | St.Ann | Completed | Load_260347 | Ocho Rios - 410 | Jul 17, 2026 2:36pm | Jul 17, 2026 2:36pm | Jul 17, 2026 3:11pm | Jul 17, 2026 3:11pm | Jul 17, 2026 3:42pm | Jul 17, 2026 3:52pm | Jul 17, 2026 3:53pm | Jul 17, 2026 3:53pm |  |  | Fair | No | Found customer meter socket defective I advise customer to use electrician
Non-Outage | J.E.26.07.19329 | C001858008 | Daniel Francis | St.Ann | Completed | Load_265449 | Ocho Rios - 310 | Jul 17, 2026 2:35pm | Jul 18, 2026 10:37am | Jul 18, 2026 10:46am | Jul 18, 2026 10:46am | Jul 18, 2026 10:47am | Jul 18, 2026 10:48am | Jul 18, 2026 10:48am | Jul 18, 2026 10:48am |  |  | Fair | No | Customer not answering phone not found
Non-Outage | J.E.26.07.20172 | C001858007 | Omar King | St.Ann | Completed | Load_251708 | Ocho Rios - 310 | Jul 17, 2026 2:34pm | Jul 17, 2026 2:34pm | Jul 17, 2026 3:54pm | Jul 17, 2026 3:57pm | Jul 17, 2026 5:21pm | Jul 17, 2026 6:31pm | Jul 17, 2026 6:32pm | Jul 17, 2026 6:32pm |  |  | Fair | No | Premises not found call several times no answer directions not sufficient
Outage | J.E.26.07.20173 | C001858005 | Omar King | St.Ann | Completed | Load_246497 | Roaring River - 210 | Jul 17, 2026 2:31pm | Jul 17, 2026 2:32pm | Jul 17, 2026 7:58pm | Jul 17, 2026 7:58pm | Jul 17, 2026 7:58pm | Jul 17, 2026 10:46pm | Jul 17, 2026 10:47pm | Jul 17, 2026 10:47pm | LeaningPole |  | Fair | No | Check as been carry out at location voltage reading show 220-228-236 to neutral from each phase we check transformer topping and discovered that all transformer position at top five (5) so we come to the conclusion that primary voltage can be the problem
Outage | J.E.26.07.20243 | C001857995 | Horace Malcolm | St.James | Completed | Load_265835 | Queens Drive - 310 | Jul 17, 2026 2:27pm | Jul 17, 2026 2:27pm | Jul 17, 2026 4:40pm | Jul 17, 2026 4:40pm | Jul 17, 2026 4:40pm | Jul 17, 2026 4:41pm | Jul 17, 2026 4:41pm | Jul 17, 2026 4:41pm |  |  | Fair | No | Related to previous call job number 20258
Outage | J.E.26.07.20258 | C001857996 | Horace Malcolm | St.James | Completed | Load_291010 | Queens Drive - 310 | Jul 17, 2026 2:27pm | Jul 17, 2026 2:27pm | Jul 17, 2026 3:08pm | Jul 17, 2026 3:08pm | Jul 17, 2026 3:57pm | Jul 17, 2026 4:40pm | Jul 17, 2026 4:40pm | Jul 17, 2026 4:40pm |  |  | SevereWind | No | Refused one 20amp junction fuse
Outage | J.E.26.07.20199 | C001857960 | Andrew Powell | Manchester | Completed | Load_258654 | Spur Tree - 210 | Jul 17, 2026 1:42pm | Jul 17, 2026 1:42pm | Jul 17, 2026 2:56pm | Jul 17, 2026 2:56pm | Jul 17, 2026 2:56pm | Jul 17, 2026 4:06pm | Jul 17, 2026 4:08pm | Jul 17, 2026 4:08pm | BrokenWire |  | Fair | No | Isolate and close 25 kva transformer circuit to repair two pole span of broken secondary neutral conductor using one automatic splicing sleeves, two preform, and one clamp, no pole number by switch location, restore supply okay.
Non-Outage | J.E.26.07.19121 | C001857956 | Ricky Hall | St.Catherine | Completed | Load_247419 | New Michelton - 410 | Jul 17, 2026 1:36pm | Jul 18, 2026 11:47am | Jul 18, 2026 3:28pm | Jul 18, 2026 3:40pm | Jul 18, 2026 4:13pm | Jul 18, 2026 5:12pm | Jul 18, 2026 5:14pm | Jul 18, 2026 5:14pm |  |  | Fair | No | Internal issues identified customer advised xfmr bank remain isolated
Non-Outage | J.E.26.07.20161 | C001857948 | Daniel Francis | null | Completed | null | null | Jul 17, 2026 1:32pm | Jul 18, 2026 8:35am | Jul 18, 2026 8:56am | Jul 18, 2026 8:56am | Jul 18, 2026 9:47am | Jul 18, 2026 9:47am | Jul 18, 2026 9:49am | Jul 18, 2026 9:49am | BrokenWire |  | Fair | No | Found okay customer say someone come there yesterday
Outage | J.E.26.07.20181 | C001857927 | Horace Malcolm | St.James | Completed | Load_570264 | Queens Drive - 810 | Jul 17, 2026 1:20pm | Jul 17, 2026 1:21pm | Jul 17, 2026 3:06pm | Jul 17, 2026 3:06pm | Jul 17, 2026 3:06pm | Jul 17, 2026 3:07pm | Jul 17, 2026 3:07pm | Jul 17, 2026 3:07pm |  |  | Fair | No | Related to previous call job number 20136
Outage | J.E.26.07.20196 | C001857928 | Horace Malcolm | St.James | Completed | Load_253128 | Queens Drive - 710 | Jul 17, 2026 1:20pm | Jul 17, 2026 3:17pm | Jul 17, 2026 6:03pm | Jul 17, 2026 6:03pm | Jul 17, 2026 7:38pm | Jul 17, 2026 7:48pm | Jul 17, 2026 7:48pm | Jul 17, 2026 7:48pm | BrokenPole |  | Fair | No | Flow pole not related to JPS
Outage | J.E.26.07.20169 | C001857917 | Rayon Foster | Hanover | Completed | Load_244632 | Orange Bay - 210 | Jul 17, 2026 1:14pm | Jul 17, 2026 1:14pm | Jul 17, 2026 3:00pm | Jul 17, 2026 3:00pm | Jul 17, 2026 4:40pm | Jul 17, 2026 5:24pm | Jul 17, 2026 5:26pm | Jul 17, 2026 5:26pm | Fire |  | Fair | No | Unable to reach and locate customer no fire on meter voltage check online 116 114
Non-Outage | J.E.26.07.17042 | C001857895 | Daniel Francis | St.Ann | Completed | Load_246719 | Ocho Rios - 310 | Jul 17, 2026 12:54pm | Jul 17, 2026 12:54pm | Jul 17, 2026 3:06pm | Jul 17, 2026 3:06pm | Jul 17, 2026 3:06pm | Jul 17, 2026 2:00am | Jul 17, 2026 3:09pm | Jul 17, 2026 3:09pm |  |  | Fair | No | Premises not found
Non-Outage | J.E.26.07.19985 | C001857887 | Moses Elliston | null | Completed | null | null | Jul 17, 2026 12:45pm | Jul 17, 2026 12:46pm | Jul 18, 2026 12:35pm | Jul 18, 2026 12:36pm | Jul 18, 2026 1:39pm | Jul 18, 2026 1:40pm | Jul 18, 2026 1:41pm | Jul 18, 2026 1:41pm |  |  | Fair | No | Broken 3 wire service phase and neutral repaired.117-117-234 volts
Outage | J.E.26.07.20144 | C001857882 | Andrew Powell | Manchester | Completed | Load_245516 | Spur Tree - 210 | Jul 17, 2026 12:43pm | Jul 17, 2026 12:47pm | Jul 17, 2026 12:57pm | Jul 17, 2026 12:57pm | Jul 17, 2026 1:46pm | Jul 17, 2026 2:08pm | Jul 17, 2026 2:13pm | Jul 17, 2026 2:13pm |  |  | Fair | No | Remade corroded service wire phase joint at secondary line 3 wire using one clamp, voltage reading 112v-112v phase to neutral 224v cross phase.
Non-Outage | J.E.26.07.20032 | C001857877 | Delano Gayle | null | Completed | null | null | Jul 17, 2026 12:35pm | Jul 17, 2026 11:44pm | Jul 18, 2026 1:44am | Jul 18, 2026 1:44am | Jul 18, 2026 2:23am | Jul 18, 2026 2:24am | Jul 18, 2026 2:24am | Jul 18, 2026 2:24am | BrokenWire |  | Fair | No | Premises found okay via phone call
Outage | J.E.26.07.20005 | C001857872 | Raymond Lewis | St.Ann | Completed | Load_336272 | Roaring River - 410 | Jul 17, 2026 12:34pm | Jul 17, 2026 3:35pm | Jul 17, 2026 6:37pm | Jul 17, 2026 6:37pm | Jul 17, 2026 6:38pm | Jul 17, 2026 6:44pm | Jul 17, 2026 6:44pm | Jul 17, 2026 6:44pm |  |  | Fair | No | Premises locked
Outage | J.E.26.07.20152 | C001857871 | Eric Williams | KSAN | Completed | Load_253886 | Washington Blvd - 510 | Jul 17, 2026 12:34pm | Jul 17, 2026 12:34pm | Jul 17, 2026 12:50pm | Jul 17, 2026 12:50pm | Jul 17, 2026 1:07pm | Jul 17, 2026 1:44pm | Jul 17, 2026 1:44pm | Jul 17, 2026 1:44pm | BrokenPole |  | Fair | No | 30 ft cl 6 pole broken, refer to maintenance
Outage | J.E.26.07.20137 | C001857869 | Raymond Lewis | St.Ann | Completed | Load_243376 | Roaring River - 210 | Jul 17, 2026 12:31pm | Jul 17, 2026 3:35pm | Jul 17, 2026 5:55pm | Jul 17, 2026 5:55pm | Jul 17, 2026 6:10pm | Jul 17, 2026 6:25pm | Jul 17, 2026 6:26pm | Jul 17, 2026 6:26pm | BrokenWire |  | Fair | No | 30 feet pole need to replant secondary wire holding up pole
Outage | J.E.26.07.20150 | C001857866 | Romaine Roberts | St.Mary | Completed | Load_241710 | Oracabessa - 110 | Jul 17, 2026 12:29pm | Jul 17, 2026 12:30pm | Jul 17, 2026 1:13pm | Jul 17, 2026 1:13pm | Jul 17, 2026 2:00pm | Jul 17, 2026 12:46am | Jul 17, 2026 2:11pm | Jul 17, 2026 2:11pm | BrokenWire |  | Fair | No | A visit to the area and checks carry out where supply found ok voltage 119-119-228 however the lines that got burst down by the truck is telephone wires and pole no disruption in pjs supply
Non-Outage | J.E.26.07.19910 | C001857865 | Clyde Brown | Clarendon | Completed | Load_263360 | May Pen - 110 | Jul 17, 2026 12:25pm | Jul 17, 2026 12:28pm | Jul 17, 2026 2:27pm | Jul 17, 2026 2:27pm | Jul 17, 2026 2:28pm | Jul 17, 2026 2:13pm | Jul 17, 2026 2:31pm | Jul 17, 2026 2:31pm | BrokenWire |  | Fair | No | Broken secondary phase caused by truck,open 25kva transformer and repaired with 6 ft-#6 conductor 4-preform and and 3 one bolt clamp.
Non-Outage | J.E.26.07.19964 | C001857853 | Donald Cunningham | St.Catherine | Completed | Load_263708 | Twickenham - 310 | Jul 17, 2026 12:20pm | Jul 17, 2026 12:34pm | Jul 18, 2026 3:56pm | Jul 18, 2026 3:56pm | Jul 18, 2026 4:56pm | Jul 18, 2026 4:59pm | Jul 18, 2026 5:26pm | Jul 18, 2026 5:26pm |  |  | Fair | No | Premises not located
Non-Outage | J.E.26.07.18851 | C001857840 | Floyd Taylor | Trelawny | Completed | Load_244909 | Greenwood - 110 | Jul 17, 2026 12:15pm | Jul 17, 2026 5:09pm | Jul 17, 2026 8:49pm | Jul 17, 2026 8:49pm | Jul 17, 2026 8:51pm | Jul 17, 2026 8:53pm | Jul 17, 2026 8:55pm | Jul 17, 2026 8:55pm |  |  | Fair | No | Isolate 25kva transformer, retention 3 span of secondary neutral, voltage reading left 116,118,234
Non-Outage | J.E.26.07.18864 | C001857841 | Roemello Brown | Trelawny | Completed | Load_249132 | Martha Brae - 110 | Jul 17, 2026 12:15pm | Jul 17, 2026 12:15pm | Jul 17, 2026 2:16pm | Jul 17, 2026 2:16pm | Jul 17, 2026 3:57pm | Jul 17, 2026 3:57pm | Jul 17, 2026 4:17pm | Jul 17, 2026 4:17pm |  |  | Fair | No | Customer meter socket defective inform customer to get an private electrician to have it change Voltage found 118/119/237Voltage leave 118/119/237
Non-Outage | J.E.26.07.18906 | C001857842 | Marlon Brown | Trelawny | Completed | Load_302800 | Duncans - 110 | Jul 17, 2026 12:15pm | Jul 17, 2026 3:49pm | Jul 17, 2026 3:52pm | Jul 17, 2026 3:52pm | Jul 17, 2026 4:40pm | Jul 17, 2026 6:07pm | Jul 17, 2026 6:07pm | Jul 17, 2026 6:07pm |  |  | SevereWind | No | Voltage found at pole 149/53=199Voltage leaving at pole 112/110=222vIsolated 25kva transformer to replace 100ft #2 AAC @ secondary. Use 2 pg clamps and 100ft #2 AAC. 077616
Non-Outage | J.E.26.07.20065 | C001857843 | Floyd Taylor | Trelawny | Completed | Load_244593 | Greenwood - 110 | Jul 17, 2026 12:15pm | Jul 18, 2026 9:09am | Jul 18, 2026 10:57am | Jul 18, 2026 10:57am | Jul 18, 2026 12:53pm | Jul 18, 2026 1:16pm | Jul 18, 2026 1:16pm | Jul 18, 2026 1:16pm |  |  | Fair | No | Clean and remake joints at pot head using 3 penunion. Voltage readings left 113,111,226
Non-Outage | J.E.26.07.18543 | C001857839 | Horace Malcolm | St.James | Completed | Load_240693 | Queens Drive - 710 | Jul 17, 2026 12:13pm | Jul 17, 2026 12:29pm | Jul 17, 2026 9:04pm | Jul 17, 2026 9:04pm | Jul 17, 2026 9:31pm | Jul 17, 2026 9:35pm | Jul 17, 2026 9:35pm | Jul 17, 2026 9:35pm | LeaningPole |  | Fair | No | Customer reporting about guy wire on premises need it to be removed
Outage | J.E.26.07.20119 | C001857838 | Nickolas Rodriques | St.Catherine | Completed | Load_239984 | Twickenham - 210 | Jul 17, 2026 12:13pm | Jul 17, 2026 12:22pm | Jul 17, 2026 1:17pm | Jul 17, 2026 1:30pm | Jul 17, 2026 1:48pm | Jul 17, 2026 2:00pm | Jul 17, 2026 2:07pm | Jul 17, 2026 2:07pm | BrokenWire |  | Fair | No | Checked and found customer service wire neutral broken caused by wind. Repaired by splice and retention wire using two splicing sleeves, current reading is (118-120-238).
Outage | J.E.26.07.19901 | C001857830 | Stephen Taylor | St.Thomas | Completed | Load_405682 | Lysson - 410 | Jul 17, 2026 12:10pm | Jul 17, 2026 12:21pm | Jul 18, 2026 9:56am | Jul 18, 2026 9:56am | Jul 18, 2026 10:30am | Jul 18, 2026 10:30am | Jul 18, 2026 10:32am | Jul 18, 2026 10:32am |  |  | Fair | No | Rami box customer is having a single phase coming from the box and need the field service technician to come and resolve problem urgent
Outage | J.E.26.07.19919 | C001857831 | Stephen Taylor | St.Thomas | Completed | Load_252941 | Good Year - 110 | Jul 17, 2026 12:10pm | Jul 17, 2026 12:21pm | Jul 17, 2026 8:55pm | Jul 17, 2026 8:55pm | Jul 17, 2026 8:55pm | Jul 17, 2026 8:55pm | Jul 17, 2026 8:57pm | Jul 17, 2026 8:57pm |  |  | Fair | No | Patrol area and power is in the area but several calls to single customer and no one answering the phone failed to locate customer
Non-Outage | J.E.26.07.18405 | C001857829 | Donald Cunningham | St.Catherine | Completed | Load_241538 | Twickenham - 310 | Jul 17, 2026 12:09pm | Jul 17, 2026 12:10pm | Jul 17, 2026 1:55pm | Jul 17, 2026 1:55pm | Jul 17, 2026 2:50pm | Jul 17, 2026 2:51pm | Jul 17, 2026 2:53pm | Jul 17, 2026 2:53pm |  |  | Fair | No | Premises closed
Outage | J.E.26.07.20111 | C001857828 | Daniel Francis | St.Ann | Completed | Load_351915 | Upper White River - 110 | Jul 17, 2026 12:08pm | Jul 17, 2026 1:05pm | Jul 17, 2026 1:18pm | Jul 17, 2026 1:18pm | Jul 17, 2026 2:27pm | Jul 17, 2026 3:04pm | Jul 17, 2026 3:06pm | Jul 17, 2026 3:06pm |  |  | Fair | No | Patrol and found 10amp junction at pole #0143658
Outage | J.E.26.07.20134 | C001857826 | Horace Malcolm | St.James | Completed | Load_269483 | Queens Drive - 310 | Jul 17, 2026 12:06pm | Jul 17, 2026 12:29pm | Jul 17, 2026 1:35pm | Jul 17, 2026 1:35pm | Jul 17, 2026 2:18pm | Jul 17, 2026 2:20pm | Jul 17, 2026 2:21pm | Jul 17, 2026 2:21pm |  |  | Fair | No | Check and found customer have no supply coming from meter EG box referred to field service
Outage | J.E.26.07.20136 | C001857827 | Horace Malcolm | St.James | Completed | Load_243821 | Bogue - 310 | Jul 17, 2026 12:06pm | Jul 17, 2026 12:29pm | Jul 17, 2026 2:22pm | Jul 17, 2026 2:22pm | Jul 17, 2026 2:47pm | Jul 17, 2026 3:05pm | Jul 17, 2026 3:06pm | Jul 17, 2026 3:06pm |  |  | Fair | No | Reclosed one 20amp junction fuse premises needs five junction switches the switches area defective three on the main line and two on the riser pole
Outage | J.E.26.07.20133 | C001857817 | Rusean Allen | KSAS | Completed | Load_239142 | Cane River - 610 | Jul 17, 2026 12:03pm | Jul 17, 2026 12:32pm | Jul 17, 2026 6:43pm | Jul 17, 2026 6:43pm | Jul 17, 2026 6:43pm | Jul 17, 2026 7:58pm | Jul 17, 2026 7:59pm | Jul 17, 2026 7:59pm |  |  | Fair | No | Reconnected wire at drop led
Non-Outage | J.E.26.07.20057 | C001857804 | Christopher Edwards | KSAN | Completed | Load_240017 | Constant Spring - 410 | Jul 17, 2026 11:57am | Jul 17, 2026 12:22pm | Jul 17, 2026 1:58pm | Jul 17, 2026 2:09pm | Jul 17, 2026 2:09pm | Jul 17, 2026 3:04pm | Jul 17, 2026 3:05pm | Jul 17, 2026 3:05pm |  |  | Fair | No | Corroded neutral joint At poleRemake joint using (1) one bolt clamps Voltage:114,115,230v
Non-Outage | J.E.26.07.20081 | C001857803 | Rochaine Hussey | KSAN | Completed | Load_268886 | Constant Spring - 310 | Jul 17, 2026 11:57am | Jul 17, 2026 12:22pm | Jul 17, 2026 1:31pm | Jul 17, 2026 1:31pm | Jul 17, 2026 1:31pm | Jul 17, 2026 1:33pm | Jul 17, 2026 1:33pm | Jul 17, 2026 1:33pm |  |  | Fair | No | In the area and unable to locate premises, customer was called multiple times and no answer
Outage | J.E.26.07.20104 | C001857802 | Rayon Foster | Hanover | Completed | Load_292767 | Orange Bay - 210 | Jul 17, 2026 11:57am | Jul 17, 2026 11:57am | Jul 17, 2026 1:30pm | Jul 17, 2026 2:16pm | Jul 17, 2026 2:17pm | Jul 17, 2026 2:54pm | Jul 17, 2026 2:54pm | Jul 17, 2026 2:54pm |  |  | Fair | No | Customer receive back power after current went out last night
Non-Outage | J.E.26.07.20123 | C001857801 | Error Coore | Manchester | Completed | Load_257847 | Kendal - 310 | Jul 17, 2026 11:56am | Jul 17, 2026 11:57am | Jul 17, 2026 12:06pm | Jul 17, 2026 12:06pm | Jul 17, 2026 12:40pm | Jul 17, 2026 12:52pm | Jul 17, 2026 12:54pm | Jul 17, 2026 12:54pm |  |  | Fair | No | Premise not found effort to contact back customer upon reaching to the area no answer
Outage | J.E.26.07.20010 | C001857795 | Kemark Slue | St.Catherine | Completed | Load_252825 | New Michelton - 210 | Jul 17, 2026 11:52am | Jul 17, 2026 11:54am | Jul 17, 2026 12:00pm | Jul 17, 2026 12:00pm | Jul 17, 2026 12:03pm | Jul 17, 2026 12:34pm | Jul 17, 2026 1:36pm | Jul 17, 2026 1:36pm | LowHangingWires |  | Fair | No | Upon arrival at the location the crew discovered that road phase 100 amps trip saver from three phases had operated further patrol revealed that the said phase was broken resulting from a joint that was wrapped with copper from one side of the said line and aluminum from the other, terminate conductor, splice and retention conductor using approximately 20 ft of #2 aaac, two one bolt clamps, a splicing sleeve, and re-energized line section.
Outage | J.E.26.07.20114 | C001857794 | Kemark Slue | St.Catherine | Completed | Load_250997 | New Michelton - 210 | Jul 17, 2026 11:52am | Jul 17, 2026 11:54am | Jul 17, 2026 1:00pm | Jul 17, 2026 2:28pm | Jul 17, 2026 2:28pm | Jul 17, 2026 2:28pm | Jul 17, 2026 2:29pm | Jul 17, 2026 2:29pm |  |  | Fair | No | Upon arrival at the location the crew discovered that x1 drop lead was burnt off at the joint from open secondary, isolate 25 kva 13.8 kv transformer at pole # 0103394, terminate conductor and remake joint using one 2/0-2/0 ampact and re-energized circuit.
Outage | J.E.26.07.20094 | C001857771 | Cliton Henry | St.Ann | Completed | Load_244965 | Upper White River - 110 | Jul 17, 2026 11:32am | Jul 17, 2026 11:36am | Jul 17, 2026 11:40am | Jul 17, 2026 11:40am | Jul 17, 2026 11:52am | Jul 17, 2026 12:42pm | Jul 17, 2026 1:00pm | Jul 17, 2026 1:00pm |  |  | Fair | No | A blown 8 amp junction fuse found at Labrynth Square at pole # 0145073 due to tree contact. Corrective work done to cut and remove branches from the single phase primary line. Supply restored using 1-10 amp fuse.
Non-Outage | J.E.26.07.20090 | C001857743 | Eric Williams | null | Completed | null | null | Jul 17, 2026 11:17am | Jul 17, 2026 11:55am | Jul 17, 2026 11:58am | Jul 17, 2026 11:58am | Jul 17, 2026 12:23pm | Jul 17, 2026 12:47pm | Jul 17, 2026 12:47pm | Jul 17, 2026 12:47pm | BrokenPole |  | Fair | No | 40 ft class 4 pole broken cause by vehicle accident, T construction pole carrying 3 phase primary conductors with across arm dead end open secondary conductors, streetlight and third party wires, also one pole span primary across arm defective, middle phase pole top leap dislodged, road phase insulator protruding through crossarm.
Non-Outage | J.E.26.07.18121 | C001857721 | Dean Smith | Hanover | Completed | Load_250960 | Orange Bay - 310 | Jul 17, 2026 11:09am | Jul 17, 2026 11:16am | Jul 17, 2026 5:40pm | Jul 17, 2026 5:40pm | Jul 17, 2026 5:40pm | Jul 17, 2026 5:40pm | Jul 17, 2026 5:41pm | Jul 17, 2026 5:41pm |  |  | Fair | No | Shift ended
Non-Outage | J.E.26.07.19983 | C001857720 | Eric Williams | null | Completed | null | null | Jul 17, 2026 11:07am | Jul 17, 2026 12:35pm | Jul 17, 2026 1:44pm | Jul 17, 2026 1:44pm | Jul 17, 2026 1:50pm | Jul 17, 2026 2:23pm | Jul 17, 2026 2:23pm | Jul 17, 2026 2:23pm | BrokenPole |  | Fair | No | Over head guy pole broken, refer to ksan maintenance, crew made area safe.
Outage | J.E.26.07.20087 | C001857719 | Milton Charlton | KSAN | Completed | Load_265279 | Hope - 510 | Jul 17, 2026 11:07am | Jul 17, 2026 11:08am | Jul 17, 2026 12:44pm | Jul 17, 2026 12:44pm | Jul 17, 2026 3:27pm | Jul 17, 2026 12:10pm | Jul 17, 2026 3:33pm | Jul 17, 2026 3:33pm |  |  | Fair | No | Found okay upon arrival. Matter was resolved but customer is complaining that an illegal connection, connected to his service wire causing him to have frequent on and off supply.
Non-Outage | J.E.26.07.19878 | C001857718 | Odaine Johnson | Clarendon | Completed | Load_237834 | Parnassus - 210 | Jul 17, 2026 11:06am | Jul 17, 2026 12:28pm | Jul 17, 2026 1:20pm | Jul 17, 2026 1:20pm | Jul 17, 2026 2:03pm | Jul 17, 2026 2:03pm | Jul 17, 2026 2:05pm | Jul 17, 2026 2:05pm |  |  | Fair | No | Area experiencing low voltage due to secondary low phase conduct broken, emergency team needed
Non-Outage | J.E.26.07.19925 | C001857716 | Odaine Johnson | Clarendon | Completed | Load_266196 | Parnassus - 310 | Jul 17, 2026 11:06am | Jul 17, 2026 12:29pm | Jul 17, 2026 1:18pm | Jul 17, 2026 1:18pm | Jul 17, 2026 1:18pm | Jul 17, 2026 1:18pm | Jul 17, 2026 1:19pm | Jul 17, 2026 1:19pm |  |  | Fair | No | Outage in the area emergency team needed
Non-Outage | J.E.26.07.19946 | C001857717 | Odaine Johnson | Clarendon | Completed | Load_245743 | Parnassus - 310 | Jul 17, 2026 11:06am | Jul 17, 2026 12:31pm | Jul 17, 2026 1:19pm | Jul 17, 2026 1:19pm | Jul 17, 2026 1:19pm | Jul 17, 2026 1:19pm | Jul 17, 2026 1:20pm | Jul 17, 2026 1:20pm |  |  | Fair | No | Outage in the area emergency team needed
Non-Outage | J.E.26.07.20001 | C001857699 | Horace Malcolm | St.James | Completed | Load_250164 | Rose Hall - 210 | Jul 17, 2026 10:51am | Jul 17, 2026 12:29pm | Jul 17, 2026 12:36pm | Jul 17, 2026 12:36pm | Jul 17, 2026 12:53pm | Jul 17, 2026 1:25pm | Jul 17, 2026 1:25pm | Jul 17, 2026 1:25pm |  |  | Fair | No | Isolate three 50 amp junction fuses and disconnect three phase padmounted lines for customer to carry repairs on their property
Outage | J.E.26.07.17138 | C001857689 | Dean Smith | Hanover | Completed | Load_575279 | Orange Bay - 310 | Jul 17, 2026 10:47am | Jul 17, 2026 10:47am | Jul 17, 2026 1:24pm | Jul 17, 2026 1:24pm | Jul 17, 2026 4:11pm | Jul 17, 2026 4:11pm | Jul 17, 2026 4:12pm | Jul 17, 2026 4:12pm |  |  | Fair | No | Unable to locate
Outage | J.E.26.07.20014 | C001857691 | Andrew Powell | Manchester | Completed | Load_265672 | Spur Tree - 210 | Jul 17, 2026 10:47am | Jul 17, 2026 10:47am | Jul 17, 2026 12:08pm | Jul 17, 2026 12:08pm | Jul 17, 2026 12:10pm | Jul 17, 2026 12:11pm | Jul 17, 2026 12:11pm | Jul 17, 2026 12:11pm |  |  | Fair | No | Premises found okay customers stated that supply restored.
Outage | J.E.26.07.20045 | C001857690 | Andrew Powell | Manchester | Completed | Load_251464 | Spur Tree - 210 | Jul 17, 2026 10:47am | Jul 17, 2026 10:47am | Jul 17, 2026 12:01pm | Jul 17, 2026 12:06pm | Jul 17, 2026 12:06pm | Jul 17, 2026 12:07pm | Jul 17, 2026 12:07pm | Jul 17, 2026 12:07pm |  |  | Fair | No | Premises not located inadequately direction contact customer by telephone unsuccessful.
Non-Outage | J.E.26.07.20034 | C001857677 | Edward Royal | null | Completed | null | null | Jul 17, 2026 10:36am | Jul 17, 2026 11:17am | Jul 17, 2026 11:20am | Jul 17, 2026 11:20am | Jul 17, 2026 11:32am | Jul 17, 2026 11:33am | Jul 17, 2026 11:58am | Jul 17, 2026 11:58am | BrokenPole |  | Fair | No | A Nissan frontier 4 by 4 van get out of control and run in of jps light pole, so pole need to be change. pole construction 40 foot T pole on pole we have 3 face primary open secondary we have two street light on it and third part cable pole # 0001994 refer to maintenance
Non-Outage | J.E.26.07.19960 | C001857664 | Rochaine Hussey | KSAN | Completed | Load_567618 | Constant Spring - 310 | Jul 17, 2026 10:28am | Jul 17, 2026 10:29am | Jul 17, 2026 10:46am | Jul 17, 2026 12:41pm | Jul 17, 2026 12:42pm | Jul 17, 2026 1:26pm | Jul 17, 2026 1:27pm | Jul 17, 2026 1:27pm |  |  | Fair | No | Customer meter socket defective Customer was advised to get an electrician to change socket 120/120/240v
Outage | J.E.26.07.19866 | C001857654 | Clyde Brown | Clarendon | Completed | Load_263360 | May Pen - 110 | Jul 17, 2026 10:25am | Jul 17, 2026 10:32am | Jul 17, 2026 10:56am | Jul 17, 2026 10:56am | Jul 17, 2026 12:22pm | Jul 17, 2026 2:12pm | Jul 17, 2026 2:20pm | Jul 17, 2026 2:20pm | BrokenWire |  | Fair | No | Broken secondary phase conductor caused by truck,3span broken conductor open 25 kva transformer and repaired with 6ft-#2/0 ,4- preform and 3 one bolt clamp.
Outage | J.E.26.07.20003 | C001857653 | Oshane Warren | Hanover | Completed | Load_263899 | Orange Bay - 310 | Jul 17, 2026 10:25am | Jul 17, 2026 10:25am | Jul 17, 2026 10:56am | Jul 17, 2026 10:56am | Jul 17, 2026 1:22pm | Jul 17, 2026 1:39pm | Jul 17, 2026 1:39pm | Jul 17, 2026 1:39pm |  |  | Fair | No | Reconnected meter to secondary line used 100 ft of wire with 3 pg clamps
Outage | J.E.26.07.19991 | C001857645 | Daniel Francis | St.Ann | Completed | Load_265449 | Ocho Rios - 310 | Jul 17, 2026 10:17am | Jul 17, 2026 10:17am | Jul 17, 2026 10:41am | Jul 17, 2026 10:42am | Jul 17, 2026 11:30am | Jul 17, 2026 12:18pm | Jul 17, 2026 12:23pm | Jul 17, 2026 12:23pm |  |  | Fair | No | Found secondary neutral joint corroded open 25kva at pole #0010357 and remade using two 1bolt clamps
Outage | J.E.26.07.19905 | C001857635 | Roxroy Needham | St.Ann | Completed | Load_238506 | Cardiff Hall - 310 | Jul 17, 2026 10:06am | Jul 17, 2026 10:07am | Jul 17, 2026 11:57am | Jul 17, 2026 11:57am | Jul 17, 2026 12:52pm | Jul 17, 2026 1:46pm | Jul 17, 2026 1:51pm | Jul 17, 2026 1:51pm |  | Y | Fair | No | Open a 25 KVA transformer at pole to repair jumper used 2 pg clamp voltage left at meter 113-114-229
Outage | J.E.26.07.19908 | C001857627 | Michael Christian | St.James | Completed | Load_260155 | Queens Drive - 710 | Jul 17, 2026 10:03am | Jul 17, 2026 10:04am | Jul 17, 2026 10:34am | Jul 17, 2026 10:34am | Jul 17, 2026 11:13am | Jul 17, 2026 11:20am | Jul 17, 2026 11:20am | Jul 17, 2026 11:20am |  |  | Fair | No | Found 1 50 kava out and defective oil come out needed 1 50 kava transformer
Non-Outage | J.E.26.07.18596 | C001857626 | Andrae Dawkins | St.James | Completed | Load_576009 | Bogue - 310 | Jul 17, 2026 10:00am | Jul 17, 2026 10:01am | Jul 17, 2026 10:20am | Jul 17, 2026 12:42pm | Jul 17, 2026 2:12pm | Jul 17, 2026 12:53pm | Jul 17, 2026 2:23pm | Jul 17, 2026 2:23pm |  |  | Fair | No | Found customer single phasing from EN box 07114 refer back to field service kaydian
Non-Outage | J.E.26.07.18656 | C001857625 | Andrae Dawkins | St.James | Completed | Load_252935 | Bogue - 610 | Jul 17, 2026 10:00am | Jul 17, 2026 10:01am | Jul 17, 2026 10:20am | Jul 17, 2026 10:59am | Jul 17, 2026 12:04pm | Jul 17, 2026 11:25am | Jul 17, 2026 12:16pm | Jul 17, 2026 12:16pm |  |  | Fair | No | Found customer single Phasing from hexing box refer back to field service kaydian
Non-Outage | J.E.26.07.19163 | C001857621 | Andrae Dawkins | St.James | Completed | Load_303199 | Bogue - 310 | Jul 17, 2026 10:00am | Jul 17, 2026 10:01am | Jul 17, 2026 2:56pm | Jul 17, 2026 2:57pm | Jul 17, 2026 2:57pm | Jul 17, 2026 2:57pm | Jul 17, 2026 2:59pm | Jul 17, 2026 2:59pm |  |  | Fair | No | Check and found okay customer said that the problem was already resolved
Non-Outage | J.E.26.07.19886 | C001857619 | Andrae Dawkins | St.James | Completed | Load_301741 | Bogue - 310 | Jul 17, 2026 9:59am | Jul 17, 2026 10:01am | Jul 17, 2026 10:20am | Jul 17, 2026 2:23pm | Jul 17, 2026 2:23pm | Jul 17, 2026 2:19pm | Jul 17, 2026 2:53pm | Jul 17, 2026 2:53pm |  |  | Fair | No | Found customer one leg of customer service wire burnt due to vegetation cleaned and remade joints voltage left 114/116/230
Non-Outage | J.E.26.07.19940 | C001857620 | Andrae Dawkins | St.James | Completed | Load_239760 | Bogue - 610 | Jul 17, 2026 9:59am | Jul 17, 2026 10:01am | Jul 17, 2026 10:21am | Jul 17, 2026 12:16pm | Jul 17, 2026 12:17pm | Jul 17, 2026 11:52am | Jul 17, 2026 12:41pm | Jul 17, 2026 12:41pm |  |  | Fair | No | Found customer meter defective meter needs to be replaced voltage found 119/119/238
Non-Outage | J.E.26.07.19486 | C001857618 | Rayon Foster | null | Completed | null | null | Jul 17, 2026 9:58am | Jul 18, 2026 7:51am | Jul 18, 2026 9:20am | Jul 18, 2026 9:20am | Jul 18, 2026 10:37am | Jul 18, 2026 11:01am | Jul 18, 2026 11:03am | Jul 18, 2026 11:03am |  |  | Fair | No | Check and found voltage working ok in customer area customer has no meter number attached to report voltage left on line 114v/115v/229v
Non-Outage | J.E.26.07.19534 | C001857617 | Tajay Bernard | null | Completed | null | null | Jul 17, 2026 9:57am | Jul 17, 2026 3:09pm | Jul 17, 2026 3:21pm | Jul 17, 2026 3:21pm | Jul 17, 2026 3:40pm | Jul 17, 2026 3:41pm | Jul 17, 2026 3:41pm | Jul 17, 2026 3:41pm |  |  | Flood | No | Customer stated that issue has been resolved
Outage | J.E.26.07.19471 | C001857616 | Tajay Bernard | Hanover | Completed | Load_575054 | Orange Bay - 310 | Jul 17, 2026 9:56am | Jul 17, 2026 3:08pm | Jul 17, 2026 7:23pm | Jul 17, 2026 7:23pm | Jul 17, 2026 8:06pm | Jul 17, 2026 8:07pm | Jul 17, 2026 8:07pm | Jul 17, 2026 8:07pm | BangingWires |  | Fair | No | Customer stated that power was restored
Outage | J.E.26.07.19522 | C001857615 | Tajay Bernard | Hanover | Completed | Load_253913 | Orange Bay - 310 | Jul 17, 2026 9:56am | Jul 17, 2026 3:08pm | Jul 17, 2026 3:18pm | Jul 17, 2026 3:42pm | Jul 17, 2026 3:42pm | Jul 17, 2026 6:20pm | Jul 17, 2026 6:21pm | Jul 17, 2026 6:21pm | Fire |  | Fair | No | Isolate 1 25kva transformer to clean and remake transformer drop Leeds and transformer casing ground Voltage found 109/104/212Voltage left 112/112/224
Outage | J.E.26.07.19892 | C001857614 | Dean Smith | Hanover | Completed | Load_1001405 | Orange Bay - 310 | Jul 17, 2026 9:56am | Jul 17, 2026 9:57am | Jul 17, 2026 10:27am | Jul 17, 2026 10:28am | Jul 17, 2026 1:16pm | Jul 17, 2026 1:16pm | Jul 17, 2026 1:17pm | Jul 17, 2026 1:17pm |  |  | Fair | No | Cut and remove tree, splice and retention (4) span of secondary phase and neutral conductor. Opened and closed 25kva transformer to do repair.
Non-Outage | J.E.26.07.18750 | C001857582 | Selvin White | St.Elizabeth | Completed | Load_264511 | Maggotty - 210 | Jul 17, 2026 9:34am | Jul 17, 2026 9:34am | Jul 17, 2026 9:40am | Jul 17, 2026 9:40am | Jul 17, 2026 10:36am | Jul 17, 2026 10:39am | Jul 17, 2026 10:40am | Jul 17, 2026 10:40am |  |  | Fair | No | Replace approximately 60 ft of number six triplex service wire. Voltage readings after installation are 230,115,115 volts.
Outage | J.E.26.07.19845 | C001857581 | Milton Charlton | KSAN | Completed | Load_256672 | Hope - 410 | Jul 17, 2026 9:31am | Jul 17, 2026 9:32am | Jul 17, 2026 11:00am | Jul 17, 2026 11:09am | Jul 17, 2026 12:38pm | Jul 17, 2026 12:05pm | Jul 17, 2026 12:44pm | Jul 17, 2026 12:44pm |  |  | Fair | No | Refused and reclosed 20 amps junction at pole #0174847 and one 3amps transformer fuse at pole #0110253 using one 20 amps amp one 3 amps fuses.
Non-Outage | J.E.26.07.19890 | C001857574 | Eric Williams | KSAN | Completed | Load_258770 | Washington Blvd - 510 | Jul 17, 2026 9:30am | Jul 17, 2026 9:35am | Jul 17, 2026 9:54am | Jul 17, 2026 9:54am | Jul 17, 2026 10:14am | Jul 17, 2026 10:29am | Jul 17, 2026 10:29am | Jul 17, 2026 10:29am |  |  | Fair | No | Customer not at location, premises closed
Outage | J.E.26.07.19873 | C001857573 | Richard Samuda | Manchester | Completed | Load_258481 | Kendal - 210 | Jul 17, 2026 9:27am | Jul 17, 2026 9:28am | Jul 17, 2026 12:05pm | Jul 17, 2026 12:42pm | Jul 17, 2026 12:42pm | Jul 17, 2026 12:58pm | Jul 17, 2026 1:01pm | Jul 17, 2026 1:01pm | BrokenWire |  | Fair | No | Customer seems she had a temporary connection because the braker panel is out side and they are damaged advised customer to get them replaced and make a call back
Outage | J.E.26.07.19882 | C001857572 | Damion Reid | Manchester | Completed | Load_251607 | Kendal - 210 | Jul 17, 2026 9:27am | Jul 17, 2026 3:23pm | Jul 17, 2026 4:28pm | Jul 17, 2026 4:28pm | Jul 17, 2026 5:37pm | Jul 17, 2026 6:07pm | Jul 17, 2026 6:10pm | Jul 17, 2026 6:10pm | LeaningPole |  | Fair | No | Defective 35ft T construction pole found cause by decay about 70% of pole foot decay pole need to rectify soon
Outage | J.E.26.07.19816 | C001857570 | Andrew Powell | St.Elizabeth | Completed | Load_257287 | Maggotty - 210 | Jul 17, 2026 9:25am | Jul 17, 2026 9:26am | Jul 17, 2026 11:56am | Jul 17, 2026 11:56am | Jul 17, 2026 11:56am | Jul 17, 2026 11:56am | Jul 17, 2026 12:00pm | Jul 17, 2026 12:00pm |  |  | Fair | No | Customer states that their is no supply to the premises, property damage and still getting light bill, please refer to field service department for investigation.
Outage | J.E.26.07.19869 | C001857564 | Andrew Powell | St.Elizabeth | Completed | Load_238861 | Maggotty - 210 | Jul 17, 2026 9:25am | Jul 17, 2026 9:26am | Jul 17, 2026 10:22am | Jul 17, 2026 10:22am | Jul 17, 2026 11:16am | Jul 17, 2026 11:44am | Jul 17, 2026 11:46am | Jul 17, 2026 11:46am |  |  | Fair | No | Remade corroded service wire phase joint at meter pothead 3 wire using one clamp, voltage reading 115v-115v phase to neutral 230v cross phase.
Outage | J.E.26.07.19846 | C001857563 | Denton Williams | Portland | Completed | Load_557379 | Port Antonio - 410 | Jul 17, 2026 9:21am | Jul 17, 2026 9:23am | Jul 17, 2026 9:28am | Jul 17, 2026 9:35am | Jul 17, 2026 10:11am | Jul 17, 2026 11:05am | Jul 17, 2026 11:20am | Jul 17, 2026 11:20am |  |  | Fair | No | Use one clamp to correct open jumper on pole
Outage | J.E.26.07.19870 | C001857562 | Shamour Haughton | St.James | Completed | Load_257529 | Bogue - 610 | Jul 17, 2026 9:20am | Jul 17, 2026 9:40am | Jul 17, 2026 10:00am | Jul 17, 2026 10:00am | Jul 17, 2026 1:45pm | Jul 17, 2026 1:45pm | Jul 17, 2026 1:48pm | Jul 17, 2026 1:48pm |  |  | Fair | No | Found transformer neutral corroded at pole, change clamp, voltage left 118,116,234
Outage | J.E.26.07.19876 | C001857561 | Daniel Francis | St.Ann | Completed | Load_242133 | Roaring River - 410 | Jul 17, 2026 9:20am | Jul 17, 2026 9:24am | Jul 17, 2026 10:36am | Jul 17, 2026 10:36am | Jul 17, 2026 10:36am | Jul 17, 2026 10:37am | Jul 17, 2026 10:38am | Jul 17, 2026 10:38am |  |  | Fair | No | Found okay 117 117 234 in all
Outage | J.E.26.07.19879 | C001857556 | Romaine Roberts | St.Mary | Completed | Load_245666 | Oracabessa - 210 | Jul 17, 2026 9:20am | Jul 17, 2026 9:25am | Jul 17, 2026 11:51am | Jul 17, 2026 11:51am | Jul 17, 2026 11:52am | Jul 17, 2026 11:53am | Jul 17, 2026 11:53am | Jul 17, 2026 11:53am |  |  | Fair | No | In sufficient direction cannot reach customer by phone
Outage | J.E.26.07.19898 | C001857555 | Daniel Francis | St.Ann | Completed | Load_258982 | Ocho Rios - 310 | Jul 17, 2026 9:20am | Jul 17, 2026 9:24am | Jul 17, 2026 12:23pm | Jul 17, 2026 12:23pm | Jul 17, 2026 12:52pm | Jul 17, 2026 12:56pm | Jul 17, 2026 12:57pm | Jul 17, 2026 12:57pm |  |  | Fair | No | Meter need to change
Outage | J.E.26.07.19896 | C001857554 | Horace Malcolm | St.James | Completed | Load_301671 | Bogue - 310 | Jul 17, 2026 9:17am | Jul 17, 2026 9:18am | Jul 17, 2026 9:25am | Jul 17, 2026 9:25am | Jul 17, 2026 10:03am | Jul 17, 2026 10:39am | Jul 17, 2026 10:39am | Jul 17, 2026 10:39am | Fire |  | Fair | No | Clear cable wire touching secondary phase line cause wire to sparks wen breeze blows
Outage | J.E.26.07.19862 | C001857533 | Donald Cunningham | St.Catherine | Completed | Load_260975 | Twickenham - 210 | Jul 17, 2026 9:04am | Jul 17, 2026 12:23pm | Jul 17, 2026 12:27pm | Jul 17, 2026 12:27pm | Jul 17, 2026 1:42pm | Jul 17, 2026 1:51pm | Jul 17, 2026 1:55pm | Jul 17, 2026 1:55pm | BrokenWire |  | Fair | No | Broken service neural splice and retention using 2 feet of service neural
Non-Outage | J.E.26.07.18635 | C001857521 | Royston Montague | St.Catherine | Completed | Load_247345 | Tredegar - 310 | Jul 17, 2026 9:00am | Jul 17, 2026 9:01am | Jul 17, 2026 9:19am | Jul 17, 2026 9:43am | Jul 17, 2026 10:24am | Jul 17, 2026 10:49am | Jul 17, 2026 10:49am | Jul 17, 2026 10:49am |  |  | Fair | No | Open phase at customer take off point. Same corrected. Voltage found 114v voltage after job completion are 229v 114v 113v
Non-Outage | J.E.26.07.19125 | C001857515 | Royston Montague | St.Catherine | Completed | Load_246772 | Rhodens Pen - 410 | Jul 17, 2026 8:59am | Jul 17, 2026 9:01am | Jul 17, 2026 9:19am | Jul 17, 2026 2:07pm | Jul 17, 2026 2:50pm | Jul 17, 2026 2:53pm | Jul 17, 2026 2:53pm | Jul 17, 2026 2:53pm |  |  | Fair | No | Damage joint on #6 wire, same repair. Voltage found 222v 110v 109v
Non-Outage | J.E.26.07.19130 | C001857514 | Royston Montague | St.Catherine | Completed | Load_259256 | Tredegar - 410 | Jul 17, 2026 8:58am | Jul 17, 2026 9:01am | Jul 17, 2026 9:19am | Jul 17, 2026 3:17pm | Jul 17, 2026 4:34pm | Jul 17, 2026 5:02pm | Jul 17, 2026 5:02pm | Jul 17, 2026 5:02pm |  |  | Fair | No | Broken phase on transformer circuit. 25 kva transformer fuse open to do repair.
Non-Outage | J.E.26.07.19207 | C001857512 | Royston Montague | St.Catherine | Completed | Load_257606 | Rhodens Pen - 210 | Jul 17, 2026 8:58am | Jul 17, 2026 9:02am | Jul 17, 2026 9:19am | Jul 17, 2026 12:01pm | Jul 17, 2026 12:46pm | Jul 17, 2026 1:18pm | Jul 17, 2026 1:19pm | Jul 17, 2026 1:19pm |  |  | Fair | No | Faulty joints at customer pothead, same corrected. Voltage found, 113v voltage after job completion are 227v 113v 112v
Non-Outage | J.E.26.07.19323 | C001857509 | Royston Montague | St.Catherine | Completed | Load_248420 | Rhodens Pen - 410 | Jul 17, 2026 8:58am | Jul 17, 2026 9:02am | Jul 17, 2026 9:19am | Jul 17, 2026 1:21pm | Jul 17, 2026 1:36pm | Jul 17, 2026 2:06pm | Jul 17, 2026 2:06pm | Jul 17, 2026 2:06pm |  |  | Fair | No | Slack connection at pothead. Same corrected. Voltage 229v 114v 114v
Non-Outage | J.E.26.07.17835 | C001857501 | Orville Lee | Portmore | Completed | Load_248603 | Naggo Head - 510 | Jul 17, 2026 8:52am | Jul 17, 2026 8:54am | Jul 17, 2026 9:21am | Jul 17, 2026 3:22pm | Jul 17, 2026 3:26pm | Jul 17, 2026 3:30pm | Jul 17, 2026 3:32pm | Jul 17, 2026 3:32pm |  |  | Fair | No | Premises found ok upon arrival Voltage 116v117v233v
Non-Outage | J.E.26.07.18212 | C001857498 | Orville Lee | Portmore | Completed | Load_241503 | Naggo Head - 510 | Jul 17, 2026 8:52am | Jul 17, 2026 8:54am | Jul 17, 2026 9:21am | Jul 17, 2026 12:49pm | Jul 17, 2026 1:33pm | Jul 17, 2026 1:59pm | Jul 17, 2026 2:01pm | Jul 17, 2026 2:01pm |  |  | Fair | No | Changed corroded clamps at secondary line Two one 1 bolt clamp andVoltage120v121v
Non-Outage | J.E.26.07.18842 | C001857499 | Orville Lee | Portmore | Completed | Load_257519 | Naggo Head - 610 | Jul 17, 2026 8:52am | Jul 17, 2026 8:54am | Jul 17, 2026 9:21am | Jul 17, 2026 9:44am | Jul 17, 2026 9:56am | Jul 17, 2026 9:59am | Jul 17, 2026 9:59am | Jul 17, 2026 9:59am |  |  | Fair | No | Premises closed
Non-Outage | J.E.26.07.18984 | C001857497 | Orville Lee | Portmore | Completed | Load_239593 | Naggo Head - 510 | Jul 17, 2026 8:52am | Jul 17, 2026 8:54am | Jul 17, 2026 9:21am | Jul 17, 2026 2:02pm | Jul 17, 2026 2:13pm | Jul 17, 2026 2:16pm | Jul 17, 2026 2:18pm | Jul 17, 2026 2:18pm | BrokenPole |  | Fair | No | Pole 0017593 brokenPole consist of street light, open secondary line and five customer take offRefer to maintenance to get pole changed
Non-Outage | J.E.26.07.19338 | C001857492 | Orville Lee | Portmore | Completed | Load_248660 | Naggo Head - 610 | Jul 17, 2026 8:50am | Jul 17, 2026 8:54am | Jul 17, 2026 9:21am | Jul 17, 2026 10:14am | Jul 17, 2026 10:35am | Jul 17, 2026 11:11am | Jul 17, 2026 11:14am | Jul 17, 2026 11:14am |  |  | Fair | No | Checks made and found pothead connection corroded One 1 bolt clamp and two pen union Voltage119v120v239v
Non-Outage | J.E.26.07.19848 | C001857490 | Orville Lee | Portmore | Completed | Load_256659 | Naggo Head - 610 | Jul 17, 2026 8:50am | Jul 17, 2026 8:55am | Jul 17, 2026 9:22am | Jul 17, 2026 9:23am | Jul 17, 2026 9:36am | Jul 17, 2026 9:43am | Jul 17, 2026 9:44am | Jul 17, 2026 9:44am | LeaningPole |  | Fair | No | Pole number 0078541rotten and needs to be changed immediately Refer maintenance department
Non-Outage | J.E.26.07.19824 | C001857452 | Selvin White | null | Completed | null | null | Jul 17, 2026 8:23am | Jul 17, 2026 9:26am | Jul 17, 2026 10:40am | Jul 17, 2026 10:44am | Jul 17, 2026 12:25pm | Jul 17, 2026 1:19pm | Jul 17, 2026 1:19pm | Jul 17, 2026 1:19pm |  |  | Fair | No | Isolate a 25 KVA transformer and tap up from 3 to tap 5. Voltage readings after tap up are 224,112,111 volts.
Non-Outage | J.E.26.06.39032 | C001857438 | Error Coore | Manchester | Completed | Load_264410 | Spur Tree - 310 | Jul 17, 2026 8:14am | Jul 17, 2026 8:15am | Jul 17, 2026 9:35am | Jul 17, 2026 9:35am | Jul 17, 2026 9:35am | Jul 17, 2026 9:35am | Jul 17, 2026 9:37am | Jul 17, 2026 9:37am |  |  | Fair | No | Premise found ok call customer said that she did not make any report
Non-Outage | J.E.26.07.01789 | C001857442 | Error Coore | Manchester | Completed | Load_242124 | Spur Tree - 310 | Jul 17, 2026 8:14am | Jul 17, 2026 8:15am | Jul 17, 2026 9:38am | Jul 17, 2026 9:38am | Jul 17, 2026 10:00am | Jul 17, 2026 10:16am | Jul 17, 2026 10:18am | Jul 17, 2026 10:18am |  |  | Fair | No | Premise not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.02027 | C001857441 | Error Coore | Manchester | Completed | Load_292265 | Spur Tree - 310 | Jul 17, 2026 8:14am | Jul 17, 2026 8:15am | Jul 17, 2026 8:30am | Jul 17, 2026 8:30am | Jul 17, 2026 9:18am | Jul 17, 2026 9:33am | Jul 17, 2026 9:34am | Jul 17, 2026 9:34am |  |  | Fair | No | Premise found ok voltage reading 116/115/231 volts
Non-Outage | J.E.26.07.02170 | C001857440 | Error Coore | Manchester | Completed | Load_248307 | Spur Tree - 310 | Jul 17, 2026 8:14am | Jul 17, 2026 8:15am | Jul 17, 2026 10:18am | Jul 17, 2026 10:19am | Jul 17, 2026 10:55am | Jul 17, 2026 11:00am | Jul 17, 2026 11:01am | Jul 17, 2026 11:01am |  |  | Fair | No | Premise not found not getting customer on phone effort to contact customer but was unsuccessful
Non-Outage | J.E.26.07.04563 | C001857443 | Error Coore | Manchester | Completed | Load_265696 | Spur Tree - 310 | Jul 17, 2026 8:14am | Jul 17, 2026 8:15am | Jul 17, 2026 11:01am | Jul 17, 2026 11:02am | Jul 17, 2026 11:16am | Jul 17, 2026 11:17am | Jul 17, 2026 11:18am | Jul 17, 2026 11:18am |  |  | Fair | No | Call customer and customer said that no will be there until after 4
Non-Outage | J.E.26.07.19059 | C001857439 | Edward Royal | null | Completed | null | null | Jul 17, 2026 8:14am | Jul 17, 2026 9:51am | Jul 17, 2026 11:11am | Jul 17, 2026 11:11am | Jul 17, 2026 11:11am | Jul 17, 2026 11:13am | Jul 17, 2026 11:16am | Jul 17, 2026 11:16am | Fire |  | Fair | No | Report is related to Torrington park outage
Non-Outage | J.E.26.07.18994 | C001857436 | Richard Samuda | Manchester | Completed | Load_262533 | Kendal - 210 | Jul 17, 2026 8:13am | Jul 17, 2026 8:15am | Jul 17, 2026 11:31am | Jul 17, 2026 11:31am | Jul 17, 2026 12:01pm | Jul 17, 2026 12:02pm | Jul 17, 2026 12:05pm | Jul 17, 2026 12:05pm | Fire |  | Fair | No | Customer say she bk to normal
Outage | J.E.26.07.19708 | C001857435 | Michael Christian | St.James | Completed | Load_261444 | Queens Drive - 710 | Jul 17, 2026 8:13am | Jul 17, 2026 8:13am | Jul 17, 2026 9:58am | Jul 17, 2026 9:58am | Jul 17, 2026 10:27am | Jul 17, 2026 10:34am | Jul 17, 2026 10:34am | Jul 17, 2026 10:34am | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Check and found okay voltage 110 109 221 at meter
Outage | J.E.26.07.18997 | C001857431 | Rusean Allen | KSAS | Completed | Load_266467 | Hunts Bay - 310 | Jul 17, 2026 8:09am | Jul 17, 2026 8:09am | Jul 17, 2026 8:59am | Jul 17, 2026 9:51am | Jul 17, 2026 11:17am | Jul 17, 2026 11:18am | Jul 17, 2026 11:18am | Jul 17, 2026 11:18am |  |  | Fair | No | Found okay
Outage | J.E.26.07.18715 | C001857429 | Rusean Allen | KSAS | Completed | Load_248008 | Rockfort - 410 | Jul 17, 2026 8:05am | Jul 17, 2026 8:06am | Jul 17, 2026 8:51pm | Jul 17, 2026 8:51pm | Jul 17, 2026 8:51pm | Jul 17, 2026 8:52pm | Jul 17, 2026 8:54pm | Jul 17, 2026 8:54pm | TreeContact |  | Fair | No | One span of secondary bushing needed Refer to bushing department
Outage | J.E.26.07.19110 | C001857428 | Rusean Allen | KSAS | Completed | Load_251755 | Rockfort - 410 | Jul 17, 2026 8:05am | Jul 17, 2026 8:06am | Jul 17, 2026 2:10pm | Jul 17, 2026 2:10pm | Jul 17, 2026 5:02pm | Jul 17, 2026 5:02pm | Jul 17, 2026 5:02pm | Jul 17, 2026 5:02pm |  |  | Fair | No | Reconnected wire at pole
Outage | J.E.26.07.19213 | C001857430 | Rusean Allen | KSAS | Completed | Load_253227 | Cane River - 610 | Jul 17, 2026 8:05am | Jul 17, 2026 8:06am | Jul 17, 2026 7:59pm | Jul 17, 2026 7:59pm | Jul 17, 2026 7:59pm | Jul 17, 2026 7:59pm | Jul 17, 2026 7:59pm | Jul 17, 2026 7:59pm |  |  | Fair | No
Outage | J.E.26.07.19063 | C001857423 | Collin Robinson | St.Mary | Completed | Load_262298 | Oracabessa - 210 | Jul 17, 2026 8:04am | Jul 17, 2026 8:05am | Jul 17, 2026 8:09am | Jul 17, 2026 8:09am | Jul 17, 2026 9:47am | Jul 17, 2026 10:00am | Jul 17, 2026 10:01am | Jul 17, 2026 10:01am |  |  | Fair | No | Remove bird from 25KVA transformer switch bottom and replace 3 amps fuse Voltage reading 120 v 120v 240v
Outage | J.E.26.07.19788 | C001857424 | Edward Royal | KSAS | Completed | Load_256488 | Greenwich - 310 | Jul 17, 2026 8:04am | Jul 17, 2026 8:10am | Jul 17, 2026 9:51am | Jul 17, 2026 9:52am | Jul 17, 2026 10:34am | Jul 17, 2026 11:01am | Jul 17, 2026 11:02am | Jul 17, 2026 11:02am |  |  | Fair | No | Replace junction 5A and fuse pole #0067821
Non-Outage | J.E.26.07.17763 | C001857422 | Nickolas Rodriques | null | Completed | null | null | Jul 17, 2026 8:03am | Jul 17, 2026 8:04am | Jul 17, 2026 8:38am | Jul 17, 2026 8:38am | Jul 17, 2026 9:13am | Jul 17, 2026 9:29am | Jul 17, 2026 9:31am | Jul 17, 2026 9:31am |  |  | Fair | No | Unable to locate or communicate with the specific customer on the contact number provided.
Outage | J.E.26.07.19527 | C001857421 | Nickolas Rodriques | Portmore | Completed | Load_257519 | Naggo Head - 610 | Jul 17, 2026 8:01am | Jul 17, 2026 8:04am | Jul 18, 2026 9:03am | Jul 18, 2026 9:19am | Jul 18, 2026 10:10am | Jul 18, 2026 10:33am | Jul 18, 2026 10:35am | Jul 18, 2026 10:35am |  |  | Fair | No | Unable to locate or communicate with the customer after several attempts. The area was patrolled and no noticeable outage was found.
Outage | J.E.26.07.19603 | C001857420 | Nickolas Rodriques | St.Catherine | Completed | Load_263800 | Twickenham - 210 | Jul 17, 2026 8:01am | Jul 17, 2026 8:04am | Jul 17, 2026 9:31am | Jul 17, 2026 11:12am | Jul 17, 2026 11:55am | Jul 17, 2026 12:24pm | Jul 17, 2026 12:37pm | Jul 17, 2026 12:37pm |  |  | Fair | No | Checked and found customer without electricity, reading found (116-117-233). Checks were done and it was found that the customer was disconnected. The escalation team was contacted and connected remotely.
Outage | J.E.26.07.19344 | C001857419 | Rayon Foster | Hanover | Completed | Load_243937 | Orange Bay - 210 | Jul 17, 2026 7:56am | Jul 17, 2026 7:56am | Jul 17, 2026 8:39am | Jul 17, 2026 8:40am | Jul 17, 2026 11:24am | Jul 17, 2026 11:29am | Jul 17, 2026 11:29am | Jul 17, 2026 11:29am |  |  | Fair | No | Found working ok voltage found in Meter socket 115/ 116 AB231
Non-Outage | J.E.26.07.18672 | C001857411 | Fredrick Hamilton | KSAN | Completed | Load_244680 | West Kings House - 310 | Jul 17, 2026 7:55am | Jul 17, 2026 7:56am | Jul 17, 2026 8:07am | Jul 17, 2026 11:21am | Jul 17, 2026 11:33am | Jul 17, 2026 11:56am | Jul 17, 2026 11:56am | Jul 17, 2026 11:56am |  |  | Fair | No | Emergency services required bucket truck required to rectify issue at pole Meter found burnt beyond recognition Switcher required Customer advised to do recertification Fire was in customer meter socket
Non-Outage | J.E.26.07.18743 | C001857410 | Fredrick Hamilton | KSAN | Completed | Load_240569 | Constant Spring - 210 | Jul 17, 2026 7:55am | Jul 17, 2026 7:56am | Jul 17, 2026 8:07am | Jul 17, 2026 9:55am | Jul 17, 2026 10:23am | Jul 17, 2026 10:29am | Jul 17, 2026 10:30am | Jul 17, 2026 10:30am |  |  | Fair | No | Please assign emergency to location secondary banging on flow cable wiresPole#39146
Non-Outage | J.E.26.07.18977 | C001857409 | Fredrick Hamilton | KSAN | Completed | Load_557735 | Washington Blvd - 610 | Jul 17, 2026 7:55am | Jul 17, 2026 7:56am | Jul 17, 2026 8:07am | Jul 17, 2026 10:30am | Jul 17, 2026 10:42am | Jul 17, 2026 11:21am | Jul 17, 2026 11:21am | Jul 17, 2026 11:21am |  |  | Fair | No | Burnt wires detected in meter socket customer advised No JPS issue at location
Non-Outage | J.E.26.07.19015 | C001857412 | Milton Charlton | KSAN | Completed | Load_259322 | Hope - 410 | Jul 17, 2026 7:55am | Jul 17, 2026 7:56am | Jul 17, 2026 9:19am | Jul 17, 2026 9:19am | Jul 17, 2026 11:00am | Jul 17, 2026 9:15am | Jul 17, 2026 11:04am | Jul 17, 2026 11:04am |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Non-Outage | J.E.26.07.13284 | C001857402 | Dwain Samuels | Westmoreland | Completed | Load_244638 | Paradise - 210 | Jul 17, 2026 7:50am | Jul 17, 2026 7:51am | Jul 17, 2026 8:06am | Jul 17, 2026 10:13am | Jul 17, 2026 10:13am | Jul 17, 2026 10:52am | Jul 17, 2026 10:54am | Jul 17, 2026 10:54am |  |  | Fair | No | Corrosion found at 3 wire pole. Corrosion clear use 3 one bolt clamp. Voltage check 113-113-226
Non-Outage | J.E.26.07.13591 | C001857408 | Dwain Samuels | Westmoreland | Completed | Load_247337 | Paradise - 210 | Jul 17, 2026 7:50am | Jul 17, 2026 7:51am | Jul 17, 2026 8:06am | Jul 17, 2026 11:25am | Jul 17, 2026 11:25am | Jul 17, 2026 11:34am | Jul 17, 2026 11:35am | Jul 17, 2026 11:35am |  |  | Fair | No | Customer said meter was changed yesterday. Supply is okay now
Outage | J.E.26.07.19375 | C001857401 | Michael Christian | St.James | Completed | Load_289860 | Queens Drive - 310 | Jul 17, 2026 7:49am | Jul 17, 2026 7:50am | Jul 17, 2026 9:57am | Jul 17, 2026 9:57am | Jul 17, 2026 9:57am | Jul 17, 2026 9:58am | Jul 17, 2026 9:58am | Jul 17, 2026 9:58am |  |  | Fair | No | 1 40 amp 1 30 amp replace
Non-Outage | J.E.26.07.13722 | C001857400 | Dwain Samuels | Westmoreland | Completed | Load_292064 | Paradise - 110 | Jul 17, 2026 7:48am | Jul 17, 2026 7:50am | Jul 17, 2026 8:06am | Jul 17, 2026 12:05pm | Jul 17, 2026 12:05pm | Jul 17, 2026 12:25pm | Jul 17, 2026 12:27pm | Jul 17, 2026 12:27pm |  |  | Fair | No | Corrosion found at 3 wire pot head. Corrosion clear use 3 pen union clamp. Voltage check 114-116-230
Non-Outage | J.E.26.07.14137 | C001857399 | Dwain Samuels | Westmoreland | Completed | Load_250735 | Paradise - 210 | Jul 17, 2026 7:48am | Jul 17, 2026 7:50am | Jul 17, 2026 8:06am | Jul 17, 2026 10:01am | Jul 17, 2026 10:04am | Jul 17, 2026 10:10am | Jul 17, 2026 10:10am | Jul 17, 2026 10:10am |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.07.16380 | C001857398 | Dwain Samuels | Westmoreland | Completed | Load_292305 | Paradise - 210 | Jul 17, 2026 7:48am | Jul 17, 2026 7:50am | Jul 17, 2026 8:06am | Jul 17, 2026 10:54am | Jul 17, 2026 10:54am | Jul 17, 2026 11:04am | Jul 17, 2026 11:05am | Jul 17, 2026 11:05am |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.07.19055 | C001857397 | Richman Whyte | Westmoreland | Completed | Load_263385 | Paradise - 310 | Jul 17, 2026 7:48am | Jul 17, 2026 7:50am | Jul 17, 2026 1:13pm | Jul 17, 2026 1:13pm | Jul 17, 2026 1:13pm | Jul 17, 2026 1:16pm | Jul 17, 2026 1:16pm | Jul 17, 2026 1:16pm |  |  | Fair | No | Check and found ok
Non-Outage | J.E.26.07.19273 | C001857395 | Dwain Samuels | null | Completed | null | null | Jul 17, 2026 7:48am | Jul 17, 2026 7:50am | Jul 17, 2026 8:06am | Jul 17, 2026 11:35am | Jul 17, 2026 11:35am | Jul 17, 2026 11:52am | Jul 17, 2026 11:54am | Jul 17, 2026 11:54am |  |  | Fair | No | Connected 3 wire meter. Used 3 one bolt clamp .
Non-Outage | J.E.26.07.17338 | C001857392 | Jermaine Williams | Clarendon | Completed | Load_295328 | Parnassus - 210 | Jul 17, 2026 7:47am | Jul 17, 2026 7:48am | Jul 17, 2026 9:55am | Jul 17, 2026 9:55am | Jul 17, 2026 11:06am | Jul 17, 2026 11:06am | Jul 17, 2026 11:09am | Jul 17, 2026 11:09am |  |  | SevereWind | No | Replaced blown 15amp at pad mounted xfmr.
Non-Outage | J.E.26.07.19283 | C001857394 | Dwain Samuels | Westmoreland | Completed | Load_269451 | Paradise - 210 | Jul 17, 2026 7:47am | Jul 17, 2026 7:50am | Jul 17, 2026 8:06am | Jul 17, 2026 11:06am | Jul 17, 2026 11:09am | Jul 17, 2026 11:16am | Jul 17, 2026 11:18am | Jul 17, 2026 11:18am | LowHangingWires |  | Fair | No | Found working okay. Voltage check 116-115-231
Outage | J.E.26.07.19626 | C001857393 | Kemark Slue | St.Catherine | Completed | Load_247665 | New Michelton - 210 | Jul 17, 2026 7:47am | Jul 17, 2026 7:48am | Jul 17, 2026 7:56am | Jul 17, 2026 7:56am | Jul 17, 2026 8:21am | Jul 17, 2026 8:00am | Jul 17, 2026 10:22am | Jul 17, 2026 10:22am |  |  | Fair | No | Upon arrival at the location the crew observer LCB6-993 was open, a patrol was done and nothing out of the ordinary was seen, return to device and liaison with control to attempt to normalize when the crew discovered that there is an issue with the device as it’s not closing and keeps going on and off, with the directives from the control the device was isolated and bypassed. Please refer to A. Murray to have the relevant authorities investigate this matter.
Non-Outage | J.E.26.07.19275 | C001857382 | Daniel Francis | null | Completed | null | null | Jul 17, 2026 7:41am | Jul 17, 2026 7:43am | Jul 17, 2026 9:10am | Jul 17, 2026 9:10am | Jul 17, 2026 9:48am | Jul 17, 2026 10:35am | Jul 17, 2026 10:36am | Jul 17, 2026 10:36am |  |  | Fair | No | Remade secondary jumper at pole #174962 using two 1bolt
Outage | J.E.26.07.19336 | C001857375 | Daniel Francis | St.Ann | Completed | Load_253537 | Upper White River - 210 | Jul 17, 2026 7:41am | Jul 17, 2026 7:43am | Jul 17, 2026 8:29am | Jul 17, 2026 8:29am | Jul 17, 2026 9:06am | Jul 17, 2026 9:09am | Jul 17, 2026 9:10am | Jul 17, 2026 9:10am |  |  | Fair | No | Found ok
Outage | J.E.26.07.19302 | C001857373 | Dwayne Samuels | Trelawny | Completed | Load_237701 | Greenwood - 110 | Jul 17, 2026 7:37am | Jul 17, 2026 7:38am | Jul 17, 2026 8:45am | Jul 17, 2026 8:49am | Jul 17, 2026 9:48am | Jul 17, 2026 11:32am | Jul 17, 2026 11:32am | Jul 17, 2026 11:32am |  |  | Fair | No | Patrol secondary line to find 2 pole span of broken secondary line open 1 50kva transformer pole#580052 to splice and retention secondary open span wire using about 50ft of number 2 conductor, 3 preform and 4 one bolt clamp to complete repairs and close voltage left on line 113v/115v/228v
Non-Outage | J.E.26.07.19117 | C001857364 | Stephen Taylor | null | Completed | null | null | Jul 17, 2026 7:33am | Jul 17, 2026 7:33am | Jul 17, 2026 11:31am | Jul 17, 2026 11:32am | Jul 17, 2026 11:32am | Jul 17, 2026 11:32am | Jul 17, 2026 11:32am | Jul 17, 2026 11:32am | BrokenWire |  | Fair | No | Splice and retention secondary wire use 6 clamps and close up back 25 kva transformer safely all customer is now okay
Outage | J.E.26.07.18869 | C001857365 | Stephen Taylor | St.Thomas | Completed | Load_556320 | Good Year - 210 | Jul 17, 2026 7:33am | Jul 17, 2026 7:33am | Jul 17, 2026 11:46am | Jul 17, 2026 11:46am | Jul 17, 2026 11:46am | Jul 17, 2026 11:46am | Jul 17, 2026 11:47am | Jul 17, 2026 11:47am |  |  | Fair | No | Need more information a lot of call to customer no one answered the phone
Outage | J.E.26.07.19198 | C001857362 | Stephen Taylor | St.Thomas | Completed | Load_269206 | Good Year - 210 | Jul 17, 2026 7:33am | Jul 17, 2026 7:33am | Jul 17, 2026 11:32am | Jul 17, 2026 11:32am | Jul 17, 2026 11:32am | Jul 17, 2026 11:32am | Jul 17, 2026 11:33am | Jul 17, 2026 11:33am | BrokenWire |  | Fair | No | Splice and retention secondary wire use 6 clamps and close up back 25 kva transformer safely all customer is now okay
Outage | J.E.26.07.19321 | C001857363 | Stephen Taylor | St.Thomas | Completed | Load_247908 | Good Year - 210 | Jul 17, 2026 7:33am | Jul 17, 2026 7:33am | Jul 17, 2026 5:59pm | Jul 17, 2026 5:59pm | Jul 17, 2026 5:59pm | Jul 17, 2026 5:59pm | Jul 17, 2026 6:00pm | Jul 17, 2026 6:00pm | BrokenWire |  | Fair | No | Patrol area and power is in the area but several calls to single customer and no one answering the phone failed to locate customer
Outage | J.E.26.07.19559 | C001857360 | Richman Whyte | Westmoreland | Completed | Load_254150 | Paradise - 310 | Jul 17, 2026 7:31am | Jul 17, 2026 7:33am | Jul 17, 2026 8:25am | Jul 17, 2026 10:51am | Jul 17, 2026 10:51am | Jul 17, 2026 11:04am | Jul 17, 2026 11:05am | Jul 17, 2026 11:05am |  |  | Fair | No | 25 kva transformer burned need to change
Outage | J.E.26.07.19611 | C001857353 | Clyde Brown | Clarendon | Completed | Load_568383 | May Pen - 110 | Jul 17, 2026 7:29am | Jul 17, 2026 7:32am | Jul 17, 2026 7:37am | Jul 17, 2026 10:30am | Jul 17, 2026 10:30am | Jul 17, 2026 10:20am | Jul 17, 2026 10:33am | Jul 17, 2026 10:33am |  |  | Fair | No | Blown 25 amps junction fuse at Rose hill,line patrolled and no fault seen,blown fuse replaced.
Outage | J.E.26.07.19612 | C001857352 | Jermaine Williams | Clarendon | Completed | Load_569950 | Monymusk - 210 | Jul 17, 2026 7:29am | Jul 17, 2026 7:31am | Jul 17, 2026 8:41am | Jul 17, 2026 8:41am | Jul 17, 2026 9:47am | Jul 17, 2026 9:47am | Jul 17, 2026 9:52am | Jul 17, 2026 9:52am |  |  | SevereWind | No | Hexing failure, collector was changed by field service technicians and customers restored.
Outage | J.E.26.07.19597 | C001857351 | Clyde Brown | Clarendon | Completed | Load_255025 | May Pen - 110 | Jul 17, 2026 7:28am | Jul 17, 2026 7:32am | Jul 17, 2026 7:37am | Jul 17, 2026 7:37am | Jul 17, 2026 9:44am | Jul 17, 2026 10:20am | Jul 17, 2026 10:30am | Jul 17, 2026 10:30am |  |  | Fair | No | Blown 25 amps junction fuse at Rose Hill line patrolled and no fault seen,blown fuse replaced
Outage | J.E.26.07.19007 | C001857349 | Cliton Henry | St.Mary | Completed | Load_252111 | Blackstonedge - 110 | Jul 17, 2026 7:27am | Jul 17, 2026 7:28am | Jul 17, 2026 7:45am | Jul 17, 2026 7:45am | Jul 17, 2026 9:14am | Jul 17, 2026 10:32am | Jul 17, 2026 10:42am | Jul 17, 2026 10:42am |  |  | Fair | No | A blown 25 amp junction fuse found at Goodwill Farm pole #0014106 and a blown 15 amp fuse found at Goshen entrance to lonigan property pole # 041315. Supply restored using 1-25 amp fuse at pole #0014106 and 1-15 at pole #041315 respectively.
Non-Outage | J.E.26.07.19605 | C001857342 | Jermaine Williams | Clarendon | Completed | Load_257105 | Monymusk - 410 | Jul 17, 2026 7:23am | Jul 17, 2026 7:27am | Jul 17, 2026 7:44am | Jul 17, 2026 7:44am | Jul 17, 2026 8:32am | Jul 17, 2026 8:40am | Jul 17, 2026 8:41am | Jul 17, 2026 8:41am |  |  | SevereWind | No | Replace 1-30A Junction Fuse, left ok.
Outage | J.E.26.07.19689 | C001857341 | Neckell Ormsby | St.Mary | Completed | Load_265280 | Highgate - 210 | Jul 17, 2026 7:23am | Jul 17, 2026 7:29am | Jul 17, 2026 7:33am | Jul 17, 2026 7:55am | Jul 17, 2026 8:54am | Jul 17, 2026 9:18am | Jul 17, 2026 9:18am | Jul 17, 2026 9:18am |  |  | Fair | No | Found 25kva transformer fuse blown patrol and found no permanent fault, replace 1-3 amp fuse no pole # seen
Outage | J.E.26.07.19405 | C001857339 | Oshane Warren | Hanover | Completed | Load_292400 | Orange Bay - 310 | Jul 17, 2026 7:21am | Jul 17, 2026 7:25am | Jul 17, 2026 8:29am | Jul 17, 2026 8:29am | Jul 17, 2026 8:29am | Jul 17, 2026 8:29am | Jul 17, 2026 8:30am | Jul 17, 2026 8:30am |  |  | Fair | No | Unable to locate or contact customer need direction
Outage | J.E.26.07.19410 | C001857340 | Oshane Warren | Hanover | Completed | Load_262801 | Orange Bay - 310 | Jul 17, 2026 7:21am | Jul 17, 2026 7:25am | Jul 17, 2026 8:30am | Jul 17, 2026 8:30am | Jul 17, 2026 8:30am | Jul 17, 2026 8:30am | Jul 17, 2026 8:31am | Jul 17, 2026 8:31am |  |  | Fair | No | Customer states that the power was restored
Outage | J.E.26.07.19607 | C001857338 | Selvin White | St.Elizabeth | Completed | Load_254061 | Maggotty - 210 | Jul 17, 2026 7:20am | Jul 17, 2026 7:21am | Jul 17, 2026 7:55am | Jul 17, 2026 8:11am | Jul 17, 2026 8:35am | Jul 17, 2026 9:22am | Jul 17, 2026 9:22am | Jul 17, 2026 9:22am |  |  | Fair | No | Replace a blown 20 amp junction fuse at the entrance to the National Irrigation Company pump after patrolling 3 phase primary line. Supply restored to th affected customers. No pole number found at location.
Outage | J.E.26.07.19326 | C001857335 | Andrew Powell | Manchester | Completed | Load_240930 | Spur Tree - 210 | Jul 17, 2026 7:13am | Jul 17, 2026 7:20am | Jul 17, 2026 7:26am | Jul 17, 2026 7:26am | Jul 17, 2026 7:41am | Jul 17, 2026 7:42am | Jul 17, 2026 7:44am | Jul 17, 2026 7:44am |  |  | Fair | No | Premises found okay customer stated that joint was burnt off at pothead electrician carried out repair work.
Non-Outage | J.E.26.07.18796 | C001857332 | Gregory Grossett | Portland | Completed | Load_263601 | Port Antonio - 310 | Jul 17, 2026 7:11am | Jul 17, 2026 3:15pm | Jul 17, 2026 3:19pm | Jul 17, 2026 3:19pm | Jul 17, 2026 3:58pm | Jul 17, 2026 4:59pm | Jul 17, 2026 5:01pm | Jul 17, 2026 5:01pm |  |  | Fair | No | Corrosion at 50kva transformer drop leads. Replace 4 one bolt clamps to correct corrosion. Voltage readings leave 120v, 120v & 241v.
Non-Outage | J.E.26.07.18966 | C001857333 | Gregory Grossett | Portland | Completed | Load_251558 | Port Antonio - 310 | Jul 17, 2026 7:11am | Jul 17, 2026 3:15pm | Jul 17, 2026 3:19pm | Jul 17, 2026 5:06pm | Jul 17, 2026 5:06pm | Jul 17, 2026 5:06pm | Jul 17, 2026 5:06pm | Jul 17, 2026 5:06pm |  |  | Fair | No | Corrosion at 50kva transformer drop leads. Replace 4 one bolt clamps to correct corrosion. Voltage readings leave 120v, 120v & 241v.
Non-Outage | J.E.26.07.19019 | C001857334 | Gregory Grossett | Portland | Completed | Load_263601 | Port Antonio - 310 | Jul 17, 2026 7:11am | Jul 17, 2026 3:15pm | Jul 17, 2026 3:19pm | Jul 17, 2026 5:07pm | Jul 17, 2026 5:07pm | Jul 17, 2026 5:08pm | Jul 17, 2026 5:08pm | Jul 17, 2026 5:08pm |  |  | Fair | No | Corrosion at 50kva transformer drop leads. Replace 4 one bolt clamps to correct corrosion. Voltage readings leave 120v, 120v & 241v.
Outage | J.E.26.07.19581 | C001857302 | Delano Gayle | St.Catherine | Completed | null | null | Jul 17, 2026 4:15am | Jul 17, 2026 4:15am | Jul 17, 2026 5:02am | Jul 17, 2026 5:02am | Jul 17, 2026 5:03am | Jul 17, 2026 6:48am | Jul 17, 2026 6:48am | Jul 17, 2026 6:48am |  |  | Fair | No | Open junction fuse on single T off line so fire fighters could out fire on Burke road,Burnt 40c6 pole with 25kva transformer scorched and badly leaking oil, burnt switch top connection, burnt transformer drop lead, broken/ burnt open secondary in 1 span, banging secondary in other spans, burnt service wires, burnt primary jumper clamp repair use 1 clamp close junction fuse, send call to maintenance urgent attention required
Outage | J.E.26.07.19371 | C001857293 | Michael Christian | St.James | Completed | Load_263183 | Queens Drive - 310 | Jul 17, 2026 1:43am | Jul 17, 2026 7:49am | Jul 17, 2026 9:55am | Jul 17, 2026 9:55am | Jul 17, 2026 9:55am | Jul 17, 2026 9:57am | Jul 17, 2026 9:57am | Jul 17, 2026 9:57am |  |  | Fair | No | Found 1 40 amp out and 1 30 amp no pole # replace 1 40 amp 1 30 amp
Outage | J.E.26.07.19383 | C001857292 | Derrick Dawkins | St.James | Completed | Load_260155 | Queens Drive - 710 | Jul 17, 2026 1:43am | Jul 17, 2026 1:50am | Jul 17, 2026 2:36am | Jul 17, 2026 6:41am | Jul 17, 2026 6:41am | Jul 17, 2026 6:22am | Jul 17, 2026 6:45am | Jul 17, 2026 6:45am |  |  | Fair | No | Found 50kva transformer defective need to replace refer to maintenance
Outage | J.E.26.07.19145 | C001857276 | Delano Gayle | St.Catherine | Completed | Load_263800 | Twickenham - 210 | Jul 16, 2026 11:05pm | Jul 16, 2026 11:08pm | Jul 17, 2026 12:12am | Jul 17, 2026 12:12am | Jul 17, 2026 12:55am | Jul 17, 2026 12:58am | Jul 17, 2026 12:58am | Jul 17, 2026 12:58am |  |  | Fair | No | Area found okay, single customer, premises not found
Outage | J.E.26.07.19191 | C001857275 | Delano Gayle | Portmore | Completed | Load_248667 | Naggo Head - 510 | Jul 16, 2026 11:05pm | Jul 16, 2026 11:08pm | Jul 17, 2026 12:59am | Jul 17, 2026 12:59am | Jul 17, 2026 1:46am | Jul 17, 2026 1:53am | Jul 17, 2026 1:54am | Jul 17, 2026 1:54am |  |  | Fair | No | Area found okay, single customer, premises not found
Outage | J.E.26.07.19341 | C001857274 | Nickolas Rodriques | Portmore | Completed | Load_239493 | Naggo Head - 610 | Jul 16, 2026 11:05pm | Jul 17, 2026 7:51am | Jul 17, 2026 4:47pm | Jul 17, 2026 5:30pm | Jul 17, 2026 6:10pm | Jul 17, 2026 6:19pm | Jul 17, 2026 6:24pm | Jul 17, 2026 6:24pm |  |  | Fair | No | Unable to locate or communicate with the specific customer. However, the area was patrolled and no noticeable outage was found.
Non-Outage | J.E.26.07.18948 | C001857273 | Edward Royal | null | Completed | null | null | Jul 16, 2026 10:56pm | Jul 16, 2026 10:58pm | Jul 17, 2026 11:59am | Jul 17, 2026 11:59am | Jul 17, 2026 2:34pm | Jul 17, 2026 3:25pm | Jul 17, 2026 3:33pm | Jul 17, 2026 3:33pm |  |  | Fair | No | Customer apply for new account there was a mixup with these two meter #2839317 the other meter number 2839318 advice customer to visit ruthven road to resolve the issue.
Non-Outage | J.E.26.07.19356 | C001857270 | Edward Royal | null | Completed | null | null | Jul 16, 2026 10:56pm | Jul 16, 2026 10:56pm | Jul 17, 2026 3:17am | Jul 17, 2026 3:17am | Jul 17, 2026 4:02am | Jul 17, 2026 4:04am | Jul 17, 2026 4:08am | Jul 17, 2026 4:08am |  |  | Fair | No | Premises not found unable to communicate with customer
Outage | J.E.26.07.19008 | C001857272 | Eric Williams | KSAS | Completed | Load_241282 | Duhaney - 310 | Jul 16, 2026 10:56pm | Jul 17, 2026 8:15am | Jul 17, 2026 8:51am | Jul 17, 2026 8:51am | Jul 17, 2026 9:13am | Jul 17, 2026 9:13am | Jul 17, 2026 9:13am | Jul 17, 2026 9:13am |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.19060 | C001857271 | Edward Royal | KSAN | Completed | Load_248397 | Constant Spring - 210 | Jul 16, 2026 10:56pm | Jul 16, 2026 10:57pm | Jul 17, 2026 2:41am | Jul 17, 2026 2:41am | Jul 17, 2026 3:13am | Jul 17, 2026 3:15am | Jul 17, 2026 3:16am | Jul 17, 2026 3:16am |  |  | Fair | No | Area have supply premises found ok
Outage | J.E.26.07.19092 | C001857268 | Edward Royal | KSAN | Completed | Load_259731 | Constant Spring - 210 | Jul 16, 2026 10:54pm | Jul 16, 2026 10:55pm | Jul 17, 2026 4:08am | Jul 17, 2026 4:08am | Jul 17, 2026 4:08am | Jul 17, 2026 4:11am | Jul 17, 2026 4:14am | Jul 17, 2026 4:14am | BrokenWire |  | Fair | No | Contact customer by phone Customer doesn’t have a pothead advice customer to a electrician to fix the pothead then contact customer care
Outage | J.E.26.07.19078 | C001857267 | Derrick Dawkins | St.James | Completed | Load_251673 | Bogue - 310 | Jul 16, 2026 10:52pm | Jul 16, 2026 10:54pm | Jul 17, 2026 1:13am | Jul 17, 2026 1:13am | Jul 17, 2026 1:44am | Jul 17, 2026 1:51am | Jul 17, 2026 2:27am | Jul 17, 2026 2:27am | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Customer service wire missing due to hurricane needs service wire for connection
Outage | J.E.26.07.19204 | C001857266 | Derrick Dawkins | St.James | Completed | Load_245170 | Queens Drive - 710 | Jul 16, 2026 10:52pm | Jul 16, 2026 10:53pm | Jul 17, 2026 12:00am | Jul 17, 2026 12:00am | Jul 17, 2026 12:31am | Jul 17, 2026 12:20am | Jul 17, 2026 1:13am | Jul 17, 2026 1:13am |  |  | Fair | No | Check and found customer with out supply. Customer meter has been disconnected refer to field service voltage left 118/117/236
Outage | J.E.26.07.19336 | C001857265 | Raymond Lewis | St.Ann | Completed | Load_253537 | Upper White River - 210 | Jul 16, 2026 10:51pm | Jul 16, 2026 10:51pm | Jul 17, 2026 4:23am | Jul 17, 2026 4:23am | Jul 17, 2026 4:26am | Jul 17, 2026 4:29am | Jul 17, 2026 4:30am | Jul 17, 2026 4:30am |  |  | Fair | No | Need daylight attention for a proper inspection
Outage | J.E.26.07.19335 | C001857261 | Derrick Dawkins | St.James | Completed | Load_243259 | Queens Drive - 710 | Jul 16, 2026 10:46pm | Jul 16, 2026 10:47pm | Jul 16, 2026 11:07pm | Jul 16, 2026 11:07pm | Jul 16, 2026 11:34pm | Jul 16, 2026 11:47pm | Jul 17, 2026 12:00am | Jul 17, 2026 12:00am |  |  | Fair | No | Found junction fuse blown due to defective switch. Replaced 8amp fuse Switch top burn out needs to replace no pole number available
Outage | J.E.26.07.19250 | C001857254 | Nickolas Rodriques | St.Catherine | Completed | Load_248434 | Twickenham - 210 | Jul 16, 2026 9:51pm | Jul 17, 2026 7:52am | Jul 17, 2026 2:07pm | Jul 17, 2026 3:01pm | Jul 17, 2026 3:26pm | Jul 17, 2026 3:44pm | Jul 17, 2026 3:55pm | Jul 17, 2026 3:55pm |  |  | Fair | No | Checked and found customer single phasing (119) caused by corroded connection. Repaired by replacing three service sleeves at pothead, current reading is (120-119-239).
Outage | J.E.26.07.19305 | C001857253 | Swon Miller | St.James | Completed | Load_249779 | Bogue - 310 | Jul 16, 2026 9:51pm | Jul 16, 2026 9:51pm | Jul 16, 2026 9:54pm | Jul 16, 2026 9:54pm | Jul 16, 2026 9:54pm | Jul 16, 2026 10:58pm | Jul 16, 2026 11:10pm | Jul 16, 2026 11:10pm | Fire |  | Fair | No | Found customer burnt off due to 1 bolt clamps kiss together at pothead voltage found 0.000 use about 70ft#6 2 linket red to red voltage left 115/114/232
Outage | J.E.26.07.19067 | C001857251 | Fitzroy Turner | KSAN | Completed | null | null | Jul 16, 2026 9:50pm | Jul 16, 2026 9:50pm | Jul 16, 2026 11:53pm | Jul 16, 2026 11:53pm | Jul 16, 2026 11:53pm | Jul 16, 2026 11:59pm | Jul 17, 2026 12:01am | Jul 17, 2026 12:01am |  |  | Fair | No | Reconnected customer after water commission completed work at underground cable
Outage | J.E.26.07.19251 | C001857249 | Donald Cunningham | St.Catherine | Completed | Load_252422 | Tredegar - 310 | Jul 16, 2026 8:57pm | Jul 17, 2026 7:45am | Jul 17, 2026 9:11am | Jul 17, 2026 9:11am | Jul 17, 2026 9:12am | Jul 17, 2026 9:14am | Jul 17, 2026 9:15am | Jul 17, 2026 9:15am |  |  | Fair | No | Supply restored call related to trip transformer
Outage | J.E.26.07.19292 | C001857247 | Javid Vernon | Hanover | Completed | Load_245791 | Orange Bay - 310 | Jul 16, 2026 8:54pm | Jul 16, 2026 8:54pm | Jul 16, 2026 9:42pm | Jul 16, 2026 9:42pm | Jul 16, 2026 10:02pm | Jul 16, 2026 10:04pm | Jul 16, 2026 10:04pm | Jul 16, 2026 10:04pm |  |  | Fair | No | Customer stated that the power was restored to the area and her premises
Non-Outage | J.E.26.07.19280 | C001857244 | Richard Samuda | null | Completed | null | null | Jul 16, 2026 8:52pm | Jul 17, 2026 7:07am | Jul 17, 2026 9:46am | Jul 17, 2026 9:46am | Jul 17, 2026 10:22am | Jul 17, 2026 11:30am | Jul 17, 2026 11:31am | Jul 17, 2026 11:31am | BrokenWire |  | Fair | No | Change customer service wire that was damaged by truck using 50 ft of #6 service wire and and three 1bolt clamps customer back to normal v
Outage | J.E.26.07.19228 | C001857242 | Richard Samuda | Manchester | Completed | Load_255863 | Kendal - 210 | Jul 16, 2026 8:52pm | Jul 17, 2026 7:06am | Jul 17, 2026 7:23am | Jul 17, 2026 7:23am | Jul 17, 2026 7:54am | Jul 17, 2026 9:41am | Jul 17, 2026 9:41am | Jul 17, 2026 9:41am | BrokenWire |  | Fair | No | Splice and reconnected customer service wire that was broken by truck using 4one bolt clamps and 10 ft of service neutral customer back to normal voltage 116/118/234
Outage | J.E.26.07.19231 | C001857243 | Ryan Richards | Manchester | Completed | Load_292080 | Kendal - 210 | Jul 16, 2026 8:52pm | Jul 16, 2026 8:53pm | Jul 16, 2026 9:46pm | Jul 16, 2026 9:46pm | Jul 16, 2026 11:09pm | Jul 16, 2026 11:35pm | Jul 17, 2026 1:05am | Jul 17, 2026 1:05am |  |  | Fair | No | Premises found ok customer meter broken and blank and needed to be replaced customer with out supply voltage 115/117/233 volts
Outage | J.E.26.07.19288 | C001857241 | Marlon Brown | Trelawny | Completed | Load_294556 | Duncans - 110 | Jul 16, 2026 8:50pm | Jul 16, 2026 8:51pm | Jul 16, 2026 9:59pm | Jul 16, 2026 9:59pm | Jul 16, 2026 10:28pm | Jul 16, 2026 10:41pm | Jul 16, 2026 10:41pm | Jul 16, 2026 10:41pm |  |  | Fair | No | Replaced 3amps 25kva transformer fuse Voltage found none Voltage leaving 120/120=240v.
Outage | J.E.26.07.19270 | C001857239 | Kemark Slue | St.Catherine | Completed | Load_250997 | New Michelton - 210 | Jul 16, 2026 8:47pm | Jul 17, 2026 12:07pm | Jul 17, 2026 1:00pm | Jul 17, 2026 1:36pm | Jul 17, 2026 1:36pm | Jul 17, 2026 2:21pm | Jul 17, 2026 2:27pm | Jul 17, 2026 2:27pm |  |  | Fair | No | Upon arrival at the location the crew discovered that x1 drop lead was burnt off at the joint from open secondary, isolate 25 kva 13.8 kv transformer at pole # 0103394, terminate conductor and remake joint using one 2/0-2/0 ampact and re-energized circuit.
Outage | J.E.26.07.19290 | C001857235 | Richard Grant | St.Catherine | Completed | Load_240104 | New Michelton - 210 | Jul 16, 2026 8:35pm | Jul 16, 2026 8:36pm | Jul 16, 2026 8:54pm | Jul 16, 2026 8:54pm | Jul 16, 2026 9:26pm | Jul 16, 2026 9:38pm | Jul 16, 2026 9:38pm | Jul 16, 2026 9:38pm |  |  | Fair | No | Defective meter seen at location. Kindly refer call to the field service department
Outage | J.E.26.07.19248 | C001857232 | Donald Cunningham | St.Catherine | Completed | Load_1001612 | Tredegar - 310 | Jul 16, 2026 8:23pm | Jul 17, 2026 7:45am | Jul 17, 2026 8:16am | Jul 17, 2026 8:16am | Jul 17, 2026 8:52am | Jul 17, 2026 9:06am | Jul 17, 2026 9:10am | Jul 17, 2026 9:10am |  |  | Fair | No | 25 kva transformer found trip same reset a lot of illegal connection in area need to be address urgently refer to losses personnel
Outage | J.E.26.07.19181 | C001857229 | Edward Royal | KSAN | Completed | Load_263284 | Washington Blvd - 510 | Jul 16, 2026 8:16pm | Jul 16, 2026 10:55pm | Jul 17, 2026 1:37am | Jul 17, 2026 1:37am | Jul 17, 2026 1:54am | Jul 17, 2026 2:26am | Jul 17, 2026 2:29am | Jul 17, 2026 2:29am | BrokenPole,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Tree cut on line 2 pole was broken the premises that responsible for is 1 benson avenue. 2 30 ft class 6 pole on them street lights 4 north triplex cable and third party cable no poles # referred to maintenance . ( line is energize) URGENT.
Outage | J.E.26.07.19178 | C001857223 | Hartley Chin | Clarendon | Completed | Load_268935 | Parnassus - 210 | Jul 16, 2026 7:52pm | Jul 16, 2026 7:53pm | Jul 16, 2026 8:36pm | Jul 16, 2026 8:36pm | Jul 16, 2026 8:36pm | Jul 16, 2026 8:37pm | Jul 16, 2026 8:39pm | Jul 16, 2026 8:39pm |  |  | Fair | No | Call related to job # 19175
Outage | J.E.26.07.19214 | C001857222 | Hartley Chin | Clarendon | Completed | Load_245821 | Monymusk - 410 | Jul 16, 2026 7:52pm | Jul 16, 2026 7:53pm | Jul 17, 2026 4:08pm | Jul 17, 2026 4:08pm | Jul 17, 2026 4:08pm | Jul 17, 2026 4:09pm | Jul 17, 2026 4:10pm | Jul 17, 2026 4:10pm |  |  | Fair | No | Found ok
Outage | J.E.26.07.19194 | C001857219 | Ricky Hall | St.Catherine | Completed | Load_305243 | Rhodens Pen - 210 | Jul 16, 2026 7:41pm | Jul 17, 2026 7:38am | Jul 17, 2026 7:56am | Jul 17, 2026 8:35am | Jul 17, 2026 9:26am | Jul 17, 2026 9:49am | Jul 17, 2026 9:50am | Jul 17, 2026 9:50am |  |  | Fair | No | Premises not found
Outage | J.E.26.07.19222 | C001857218 | Rayon Foster | Hanover | Completed | Load_244632 | Orange Bay - 210 | Jul 16, 2026 7:38pm | Jul 16, 2026 7:38pm | Jul 17, 2026 8:46am | Jul 17, 2026 11:30am | Jul 17, 2026 11:32am | Jul 17, 2026 11:59am | Jul 17, 2026 11:59am | Jul 17, 2026 11:59am |  |  | Fair | No | Low hanging 2/0 secondary wire pull down by passing truck retention 2/0 wire used one preform voltage after repair 116/117AB233
Outage | J.E.26.07.19063 | C001857217 | Raymond Carr | St.Mary | Completed | Load_262298 | Oracabessa - 210 | Jul 16, 2026 7:37pm | Jul 16, 2026 7:39pm | Jul 16, 2026 7:57pm | Jul 16, 2026 7:57pm | Jul 16, 2026 7:57pm | Jul 16, 2026 7:51pm | Jul 16, 2026 7:58pm | Jul 16, 2026 7:58pm |  |  | Fair | No | Kindly refer to Portland.
Non-Outage | J.E.26.07.19155 | C001857215 | Swon Miller | null | Completed | null | null | Jul 16, 2026 7:36pm | Jul 16, 2026 7:36pm | Jul 16, 2026 8:54pm | Jul 16, 2026 8:55pm | Jul 16, 2026 9:14pm | Jul 16, 2026 9:18am | Jul 16, 2026 9:21pm | Jul 16, 2026 9:21pm |  |  | Fair | No | Found 1,100 kva transformer fuse blown cause by contamination replace 8 amp in 100 kva transformer no pole number available
Non-Outage | J.E.26.07.18594 | C001857211 | Marlon Authors | St.Elizabeth | Completed | Load_269055 | Maggotty - 210 | Jul 16, 2026 7:28pm | Jul 16, 2026 7:28pm | Jul 16, 2026 7:33pm | Jul 16, 2026 7:33pm | Jul 16, 2026 9:03pm | Jul 16, 2026 9:23pm | Jul 16, 2026 9:23pm | Jul 16, 2026 9:23pm |  |  | Fair | No | Supply checked and found ampack that holds the neutral conductor from the transformer drop lead burnt. Isolate and close 100 kva transformers in bankers 3 to replace same. Supply leave working okay rdg 233v,241v and 231 volts
Outage | J.E.26.07.19229 | C001857210 | Milton Charlton | KSAN | Completed | Load_256672 | Hope - 410 | Jul 16, 2026 7:26pm | Jul 16, 2026 7:27pm | Jul 16, 2026 8:13pm | Jul 16, 2026 8:13pm | Jul 16, 2026 10:04pm | Jul 3, 2026 10:05pm | Jul 16, 2026 10:09pm | Jul 16, 2026 10:09pm |  |  | Fair | No | Bushing single phase 2-wire primary and refused and reclosed 15 amps junction at pole#0174847 and one 2- amps transformer switch at pole #0110253.
Outage | J.E.26.07.19177 | C001857206 | Stephen Taylor | St.Thomas | Completed | Load_269125 | Good Year - 110 | Jul 16, 2026 7:03pm | Jul 16, 2026 7:04pm | Jul 16, 2026 7:24pm | Jul 16, 2026 7:24pm | Jul 16, 2026 8:12pm | Jul 16, 2026 8:12pm | Jul 16, 2026 8:37pm | Jul 16, 2026 8:37pm |  |  | Fair | No | See junction down patrol see bird in line and use switch stick and clear line and close up back junction with a 10 amp fuse all customer is now okay
Outage | J.E.26.07.19048 | C001857201 | Hartley Chin | Clarendon | Completed | Load_245215 | Monymusk - 410 | Jul 16, 2026 6:44pm | Jul 16, 2026 6:45pm | Jul 17, 2026 4:10pm | Jul 17, 2026 4:10pm | Jul 17, 2026 4:10pm | Jul 17, 2026 4:11pm | Jul 17, 2026 4:11pm | Jul 17, 2026 4:11pm |  |  | Fair | No | Found ok
Outage | J.E.26.07.19170 | C001857202 | Hartley Chin | Clarendon | Completed | Load_294606 | Monymusk - 410 | Jul 16, 2026 6:44pm | Jul 16, 2026 6:45pm | Jul 17, 2026 4:10pm | Jul 17, 2026 4:10pm | Jul 17, 2026 4:10pm | Jul 17, 2026 4:10pm | Jul 17, 2026 4:10pm | Jul 17, 2026 4:10pm |  |  | Fair | No | Found ok
Outage | J.E.26.07.19175 | C001857200 | Hartley Chin | Clarendon | Completed | Load_237973 | Parnassus - 210 | Jul 16, 2026 6:44pm | Jul 16, 2026 6:45pm | Jul 16, 2026 7:07pm | Jul 16, 2026 7:07pm | Jul 16, 2026 7:57pm | Jul 16, 2026 8:08pm | Jul 16, 2026 8:35pm | Jul 16, 2026 8:35pm |  |  | Fair | No | Found 25 AMP junction fuse blown . line patrolled and refuse
Non-Outage | J.E.26.07.19151 | C001857199 | Edward Royal | KSAS | Completed | Load_263277 | Hunts Bay - 310 | Jul 16, 2026 6:43pm | Jul 17, 2026 12:05pm | Jul 17, 2026 3:33pm | Jul 17, 2026 3:33pm | Jul 17, 2026 3:51pm | Jul 17, 2026 4:18pm | Jul 17, 2026 4:26pm | Jul 17, 2026 4:26pm |  |  | Fair | No | Jumper burn off main primary line that supply lightening transformer referred to in-house crews pole# 0034371
Non-Outage | J.E.26.07.19112 | C001857198 | Fitzroy Turner | null | Completed | null | null | Jul 16, 2026 6:40pm | Jul 16, 2026 6:40pm | Jul 16, 2026 9:25pm | Jul 16, 2026 9:25pm | Jul 16, 2026 9:47pm | Jul 16, 2026 9:52pm | Jul 16, 2026 9:53pm | Jul 16, 2026 9:53pm | BrokenWire |  | Fair | No | No broken wire seeing at the location
Outage | J.E.26.07.17765 | C001857195 | Nickolas Rodriques | Portmore | Completed | Load_250261 | Naggo Head - 510 | Jul 16, 2026 6:38pm | Jul 17, 2026 8:22am | Jul 17, 2026 4:47pm | Jul 17, 2026 4:47pm | Jul 17, 2026 5:15pm | Jul 17, 2026 5:23pm | Jul 17, 2026 5:29pm | Jul 17, 2026 5:29pm |  |  | Fair | No | Customer confirmed that the issue was resolved.
Outage | J.E.26.07.18496 | C001857196 | Nickolas Rodriques | Portmore | Completed | Load_260088 | Naggo Head - 510 | Jul 16, 2026 6:38pm | Jul 17, 2026 7:53am | Jul 17, 2026 3:55pm | Jul 17, 2026 3:57pm | Jul 17, 2026 4:25pm | Jul 17, 2026 4:37pm | Jul 17, 2026 4:46pm | Jul 17, 2026 4:46pm |  |  | Fair | No | Found premises with electricity, reading found (118-115-233).
Outage | J.E.26.07.19039 | C001857194 | Delano Gayle | Portmore | Completed | Load_238584 | Naggo Head - 510 | Jul 16, 2026 6:38pm | Jul 16, 2026 11:12pm | Jul 17, 2026 1:55am | Jul 17, 2026 1:55am | Jul 17, 2026 2:53am | Jul 17, 2026 2:56am | Jul 17, 2026 2:56am | Jul 17, 2026 2:56am |  |  | Fair | No | Premises not located report indicating that customer made report for premises in kingston
Outage | J.E.26.07.19160 | C001857191 | Nickolas Rodriques | Portmore | Completed | Load_258219 | Naggo Head - 610 | Jul 16, 2026 6:28pm | Jul 16, 2026 6:30pm | Jul 16, 2026 7:47pm | Jul 16, 2026 7:47pm | Jul 16, 2026 8:21pm | Jul 16, 2026 8:43pm | Jul 16, 2026 9:03pm | Jul 16, 2026 9:03pm | BrokenWire |  | Fair | No | Checked and found customer without electricity caused by broken service wire at pole. Unable to connect due to defective customer meter wires in meter socket. The customer was advised to consult an electrician to do internal repair.
Outage | J.E.26.07.19076 | C001857186 | Floyd Taylor | Trelawny | Completed | Load_243668 | Greenwood - 210 | Jul 16, 2026 6:24pm | Jul 16, 2026 6:24pm | Jul 16, 2026 7:06pm | Jul 16, 2026 7:06pm | Jul 16, 2026 8:37pm | Jul 16, 2026 8:39pm | Jul 16, 2026 9:02pm | Jul 16, 2026 9:02pm |  |  | Fair | No | Unable to locate customer, several attempts were made
Outage | J.E.26.07.16258 | C001857164 | Richard Grant | St.Catherine | Completed | Load_256805 | New Michelton - 410 | Jul 16, 2026 5:37pm | Jul 16, 2026 5:38pm | Jul 16, 2026 5:59pm | Jul 16, 2026 5:59pm | Jul 16, 2026 6:45pm | Jul 16, 2026 7:03pm | Jul 16, 2026 7:03pm | Jul 16, 2026 7:03pm |  |  | Fair | No | Line section re-energized with 8amps fuse after bushing completed on line section by contractors
Non-Outage | J.E.26.07.11106 | C001857161 | Donald Cunningham | St.Catherine | Completed | Load_243121 | Tredegar - 310 | Jul 16, 2026 5:34pm | Jul 16, 2026 5:38pm | Jul 16, 2026 5:41pm | Jul 16, 2026 5:41pm | Jul 16, 2026 7:48pm | Jul 16, 2026 7:50pm | Jul 16, 2026 8:02pm | Jul 16, 2026 8:02pm | BrokenPole |  | Fair | No | Leaning 30 class 6 secondary pole with #2 triplex need to dig and straighten
Non-Outage | J.E.26.07.14906 | C001857160 | Richard Grant | St.Catherine | Completed | Load_247562 | New Michelton - 210 | Jul 16, 2026 5:34pm | Jul 16, 2026 5:35pm | Jul 16, 2026 7:03pm | Jul 16, 2026 7:03pm | Jul 16, 2026 7:49pm | Jul 16, 2026 7:50pm | Jul 16, 2026 7:50pm | Jul 16, 2026 7:50pm |  |  | Fair | No | Premises found okay. Customer complaint is about constant cycling of feeder
Non-Outage | J.E.26.07.18916 | C001857157 | Hartley Chin | Clarendon | Completed | Load_237834 | Parnassus - 210 | Jul 16, 2026 5:30pm | Jul 16, 2026 5:31pm | Jul 16, 2026 6:04pm | Jul 16, 2026 6:08pm | Jul 16, 2026 6:09pm | Jul 16, 2026 1:00am | Jul 16, 2026 6:12pm | Jul 16, 2026 6:12pm |  |  | Fair | No | Call related to job #18636
Non-Outage | J.E.26.07.18934 | C001857156 | Hartley Chin | Clarendon | Completed | Load_238199 | Parnassus - 310 | Jul 16, 2026 5:30pm | Jul 16, 2026 5:31pm | Jul 16, 2026 8:40pm | Jul 16, 2026 9:18pm | Jul 16, 2026 10:12pm | Jul 16, 2026 10:12pm | Jul 16, 2026 10:13pm | Jul 16, 2026 10:13pm |  |  | Fair | No | Require day light attention to troubleshoot properly
Non-Outage | J.E.26.07.18640 | C001857155 | Tajay Bernard | Hanover | Completed | Load_575279 | Orange Bay - 310 | Jul 16, 2026 5:26pm | Jul 16, 2026 5:26pm | Jul 16, 2026 5:41pm | Jul 16, 2026 5:44pm | Jul 16, 2026 6:32pm | Jul 16, 2026 6:49pm | Jul 16, 2026 6:49pm | Jul 16, 2026 6:49pm |  |  | Fair | No | Premises check and found okay
Non-Outage | J.E.26.07.14745 | C001857147 | Christopher Edwards | KSAN | Completed | Load_238001 | Constant Spring - 410 | Jul 16, 2026 5:06pm | Jul 16, 2026 5:06pm | Jul 16, 2026 6:12pm | Jul 16, 2026 6:28pm | Jul 16, 2026 7:14pm | Jul 17, 2026 7:19am | Jul 17, 2026 7:19am | Jul 17, 2026 7:19am | Fire |  | Fair | No | Check and found ok
Non-Outage | J.E.26.07.18627 | C001857149 | Christopher Edwards | KSAN | Completed | Load_246942 | Constant Spring - 410 | Jul 16, 2026 5:06pm | Jul 17, 2026 9:53am | Jul 17, 2026 12:41pm | Jul 17, 2026 12:41pm | Jul 17, 2026 1:44pm | Jul 17, 2026 1:57pm | Jul 17, 2026 1:58pm | Jul 17, 2026 1:58pm | BrokenPole |  | Fair | No | Rotten 35 ft wood polePole is already marked to be changed
Non-Outage | J.E.26.07.18730 | C001857148 | Christopher Edwards | KSAN | Completed | Load_261490 | Constant Spring - 410 | Jul 16, 2026 5:06pm | Jul 17, 2026 8:13am | Jul 17, 2026 8:50am | Jul 17, 2026 9:50am | Jul 17, 2026 10:42am | Jul 17, 2026 12:40pm | Jul 17, 2026 12:41pm | Jul 17, 2026 12:41pm |  |  | Fair | No | Isolate 50 kva transformer To remake burnt open secondary jumper joint Using (2) one bolt clamps Voltage:118,120,240v
Non-Outage | J.E.26.07.18974 | C001857146 | Milton Charlton | KSAN | Completed | Load_259322 | Hope - 410 | Jul 16, 2026 5:05pm | Jul 16, 2026 5:05pm | Jul 16, 2026 5:44pm | Jul 16, 2026 5:45pm | Jul 16, 2026 6:08pm | Jul 16, 2026 6:10pm | Jul 16, 2026 6:12pm | Jul 16, 2026 6:12pm |  |  | Fair | No | Customer service wire #6 triplex phase burn off at pole. Repair using one 1- bolt clamp.
Outage | J.E.26.07.19067 | C001857142 | Kaydon Taylor | KSAN | Completed | null | null | Jul 16, 2026 4:58pm | Jul 16, 2026 4:59pm | Jul 16, 2026 5:05pm | Jul 16, 2026 5:05pm | Jul 16, 2026 5:05pm | Jul 16, 2026 5:06pm | Jul 16, 2026 5:06pm | Jul 16, 2026 5:06pm |  |  | Fair | No | Isolation request at 35A cherry dr. Isolate single phase underground cable for newcomers to carry out repairs.
Outage | J.E.26.07.19033 | C001857141 | Richman Whyte | Westmoreland | Completed | Load_241338 | Paradise - 310 | Jul 16, 2026 4:57pm | Jul 16, 2026 4:57pm | Jul 16, 2026 6:24pm | Jul 16, 2026 6:24pm | Jul 16, 2026 6:25pm | Jul 16, 2026 6:58pm | Jul 16, 2026 6:59pm | Jul 16, 2026 6:59pm |  |  | Fair | No | Customer meter pole is still on the ground
Non-Outage | J.E.26.07.00941 | C001857139 | Kenroy Dale | Manchester | Completed | Load_237731 | Spur Tree - 310 | Jul 16, 2026 4:53pm | Jul 16, 2026 4:54pm | Jul 16, 2026 5:34pm | Jul 16, 2026 9:34pm | Jul 16, 2026 9:34pm | Jul 16, 2026 9:39pm | Jul 16, 2026 9:42pm | Jul 16, 2026 9:42pm |  |  | Fair | No | Customers were experiencing low voltage due to illegal connections. Top changer on transformer also leaking oil, illegal connections were removed transformer need to be replaced shorty due to oil leak. Voltage reading 118/116/234
Non-Outage | J.E.26.07.18761 | C001857137 | Fitzroy Turner | KSAS | Completed | Load_242005 | Rockfort - 410 | Jul 16, 2026 4:46pm | Jul 16, 2026 4:46pm | Jul 16, 2026 6:23pm | Jul 16, 2026 6:23pm | Jul 16, 2026 7:17pm | Jul 16, 2026 7:19pm | Jul 16, 2026 7:23pm | Jul 16, 2026 7:23pm |  |  | Fair | No | Customer having low voltage issues 102 / 98 /202 at pole and pothead customer advised
Outage | J.E.26.07.19007 | C001857127 | Raymond Carr | St.Mary | Completed | Load_252111 | Blackstonedge - 110 | Jul 16, 2026 4:40pm | Jul 16, 2026 4:53pm | Jul 16, 2026 5:09pm | Jul 16, 2026 5:09pm | Jul 16, 2026 6:48pm | Jul 16, 2026 7:00pm | Jul 16, 2026 6:51pm | Jul 16, 2026 6:51pm |  |  | Fair | No | Due to poor visibility and line running in heavy bushes. Daytime attention is needed.
Non-Outage | J.E.26.07.15087 | C001857126 | Fitzroy Turner | KSAS | Completed | Load_261828 | Up Park Camp - 510 | Jul 16, 2026 4:36pm | Jul 16, 2026 4:36pm | Jul 16, 2026 7:25pm | Jul 16, 2026 7:25pm | Jul 16, 2026 7:40pm | Jul 16, 2026 7:58pm | Jul 16, 2026 7:59pm | Jul 16, 2026 7:59pm |  |  | Fair | No | Tree wire service phase burnt off at pole use one linket to repair supply restored
Non-Outage | J.E.26.07.17125 | C001857123 | Omar King | St.Ann | Completed | Load_249379 | Roaring River - 210 | Jul 16, 2026 4:33pm | Jul 16, 2026 4:35pm | Jul 16, 2026 6:11pm | Jul 16, 2026 6:11pm | Jul 16, 2026 6:30pm | Jul 16, 2026 7:10pm | Jul 16, 2026 7:10pm | Jul 16, 2026 7:10pm |  |  | Fair | No | Found transformer drop lead one bolt connector with corrosion repair as been carry out customer is now with supply voltage reading 110-110-220
Non-Outage | J.E.26.07.18898 | C001857122 | Hartley Chin | null | Completed | null | null | Jul 16, 2026 4:32pm | Jul 16, 2026 4:49pm | Jul 16, 2026 8:47pm | Jul 16, 2026 9:02pm | Jul 16, 2026 9:09pm | Jul 16, 2026 9:17pm | Jul 16, 2026 9:18pm | Jul 16, 2026 9:18pm | LeakingTransformer |  | Fair | No | Found ok. Found 15 KVA transformer, no oil or leaking . Transformer operating normal. Voltage readings v115,v113,v228
Outage | J.E.26.07.19010 | C001857117 | Hartley Chin | Clarendon | Completed | Load_266129 | Parnassus - 210 | Jul 16, 2026 4:24pm | Jul 16, 2026 4:26pm | Jul 16, 2026 6:29pm | Jul 16, 2026 6:29pm | Jul 16, 2026 6:29pm | Jul 16, 2026 6:30pm | Jul 16, 2026 6:33pm | Jul 16, 2026 6:33pm |  |  | Fair | No | Premisis found ok. Customer stated that their supply is ok
Outage | J.E.26.07.18937 | C001857116 | Hartley Chin | Clarendon | Completed | Load_253488 | Monymusk - 210 | Jul 16, 2026 4:23pm | Jul 16, 2026 4:26pm | Jul 16, 2026 6:04pm | Jul 16, 2026 6:05pm | Jul 16, 2026 6:05pm | Jul 16, 2026 1:00am | Jul 16, 2026 6:08pm | Jul 16, 2026 6:08pm |  |  | Fair | No | Premisis found ok. Meter was connected by field service .
Outage | J.E.26.07.18972 | C001857112 | Ricky Hall | St.Catherine | Completed | Load_252781 | Tredegar - 210 | Jul 16, 2026 4:19pm | Jul 16, 2026 4:19pm | Jul 16, 2026 7:15pm | Jul 16, 2026 7:15pm | Jul 16, 2026 7:34pm | Jul 16, 2026 7:35pm | Jul 16, 2026 7:35pm | Jul 16, 2026 7:35pm |  |  | Fair | No | Premises closed
Non-Outage | J.E.26.07.18274 | C001857110 | Fitzroy Turner | KSAS | Completed | Load_251380 | Up Park Camp - 510 | Jul 16, 2026 4:13pm | Jul 16, 2026 4:14pm | Jul 16, 2026 7:59pm | Jul 16, 2026 7:59pm | Jul 16, 2026 8:11pm | Jul 16, 2026 8:53pm | Jul 16, 2026 8:54pm | Jul 16, 2026 8:54pm |  |  | Fair | No | Found tree wire service phase burnt off at pole use one clamp to carry out repair supply restored to customer
Outage | J.E.26.07.18963 | C001857106 | Ricky Hall | St.Catherine | Completed | Load_264996 | Tredegar - 210 | Jul 16, 2026 4:13pm | Jul 16, 2026 4:19pm | Jul 16, 2026 6:12pm | Jul 16, 2026 6:24pm | Jul 16, 2026 6:49pm | Jul 16, 2026 7:14pm | Jul 16, 2026 7:14pm | Jul 16, 2026 7:14pm |  |  | Fair | Yes | Clean and reconnect 3W service at pothead use 3 pen union 117*2/234
Outage | J.E.26.07.19016 | C001857107 | Swon Miller | St.James | Completed | Load_293172 | Queens Drive - 310 | Jul 16, 2026 4:13pm | Jul 16, 2026 4:14pm | Jul 16, 2026 7:55pm | Jul 16, 2026 7:55pm | Jul 16, 2026 7:56pm | Jul 8, 2026 7:58pm | Jul 16, 2026 7:58pm | Jul 16, 2026 7:58pm |  |  | Fair | No | Call related to previous
Outage | J.E.26.07.19017 | C001857108 | Swon Miller | St.James | Completed | Load_290370 | Queens Drive - 310 | Jul 16, 2026 4:13pm | Jul 16, 2026 4:14pm | Jul 16, 2026 7:53pm | Jul 16, 2026 7:53pm | Jul 16, 2026 7:53pm | Jul 14, 2026 7:54pm | Jul 16, 2026 7:55pm | Jul 16, 2026 7:55pm |  |  | Fair | No | Call related to previous
Outage | J.E.26.07.19020 | C001857109 | Swon Miller | St.James | Completed | Load_267183 | Rose Hall - 110 | Jul 16, 2026 4:13pm | Jul 16, 2026 4:14pm | Jul 16, 2026 6:23pm | Jul 16, 2026 6:23pm | Jul 16, 2026 6:45pm | Jul 22, 2026 7:52am | Jul 16, 2026 7:52pm | Jul 16, 2026 7:52pm |  |  | Fair | No | Found 30 amp junction fuse blown cause by contamination replace 30 amp junction fuse no pole number available
Outage | J.E.26.07.18882 | C001857101 | Ryan Richards | Manchester | Completed | Load_263434 | Kendal - 210 | Jul 16, 2026 4:10pm | Jul 16, 2026 4:12pm | Jul 16, 2026 6:14pm | Jul 16, 2026 6:14pm | Jul 16, 2026 7:36pm | Jul 16, 2026 8:36pm | Jul 16, 2026 8:43pm | Jul 16, 2026 8:43pm |  |  | Fair | No | No service wire found at the premises replaced 50ft#6 triplex 3 penunion 2 one bolt clamp voltage 114/112/227
Outage | J.E.26.07.18944 | C001857102 | Ryan Richards | Manchester | Completed | Load_262533 | Kendal - 210 | Jul 16, 2026 4:10pm | Jul 16, 2026 4:12pm | Jul 16, 2026 4:41pm | Jul 16, 2026 4:41pm | Jul 16, 2026 5:31pm | Jul 16, 2026 6:09pm | Jul 16, 2026 6:14pm | Jul 16, 2026 6:14pm |  |  | Fair | No | Burn off neutral found at pole for 3 wire meter remade burn off neutral 3ft#6 neutral 1 one bolt clamp voltage 115/117/233
Outage | J.E.26.07.18929 | C001857095 | Stephen Taylor | St.Thomas | Completed | Load_254904 | Good Year - 110 | Jul 16, 2026 4:03pm | Jul 16, 2026 4:03pm | Jul 16, 2026 8:37pm | Jul 16, 2026 9:31pm | Jul 16, 2026 10:16pm | Jul 16, 2026 10:16pm | Jul 16, 2026 10:25pm | Jul 16, 2026 10:25pm |  |  | Fair | No | Clean up single phase use 3 clamps customer is now okay
Outage | J.E.26.07.18971 | C001857094 | Nickolas Rodriques | St.Catherine | Completed | Load_244195 | Twickenham - 210 | Jul 16, 2026 4:03pm | Jul 17, 2026 8:19am | Jul 17, 2026 11:17am | Jul 17, 2026 12:38pm | Jul 17, 2026 12:49pm | Jul 17, 2026 1:11pm | Jul 17, 2026 1:17pm | Jul 17, 2026 1:17pm |  |  | Fair | No | Found premises with electricity. The maintenance team confirmed that the power was restored.
Outage | J.E.26.07.18804 | C001857092 | Damion Reid | Manchester | Completed | Load_245737 | Spur Tree - 310 | Jul 16, 2026 4:02pm | Jul 16, 2026 4:04pm | Jul 16, 2026 7:43pm | Jul 16, 2026 7:43pm | Jul 16, 2026 8:04pm | Jul 16, 2026 8:22pm | Jul 16, 2026 8:23pm | Jul 16, 2026 8:23pm |  |  | SevereWind | No | Remade corroded phase at secondary pole for 3 wire service using two one bolt clamp
Outage | J.E.26.07.18831 | C001857091 | Damion Reid | Manchester | Completed | Load_242017 | Spur Tree - 310 | Jul 16, 2026 4:02pm | Jul 16, 2026 4:04pm | Jul 16, 2026 10:20pm | Jul 16, 2026 10:21pm | Jul 16, 2026 10:50pm | Jul 17, 2026 12:32am | Jul 17, 2026 12:34am | Jul 17, 2026 12:34am |  |  | Fair | No | Blown 15amp junction fuse found cause by contamination line patrol nothing was found blown fuse replaced
Outage | J.E.26.07.18840 | C001857093 | Damion Reid | Manchester | Completed | Load_247599 | Spur Tree - 310 | Jul 16, 2026 4:02pm | Jul 16, 2026 4:04pm | Jul 16, 2026 5:46pm | Jul 16, 2026 5:46pm | Jul 16, 2026 6:53pm | Jul 16, 2026 7:41pm | Jul 16, 2026 7:42pm | Jul 16, 2026 7:42pm |  |  | SevereWind | No | Customer have internal problems customer have been advised voltage reading at meter socket phase to neutral 117v-116v across phase 234v
Outage | J.E.26.07.18785 | C001857090 | Damion Reid | Manchester | Completed | Load_244994 | Spur Tree - 310 | Jul 16, 2026 4:00pm | Jul 16, 2026 4:04pm | Jul 16, 2026 8:24pm | Jul 16, 2026 8:24pm | Jul 16, 2026 8:45pm | Jul 16, 2026 10:18pm | Jul 16, 2026 10:20pm | Jul 16, 2026 10:20pm |  |  | Fair | No | Blown 3amp fuse found for 25kva transformer cause by two span of broken secondary phase conductor splice an retention conductor using 10ft of 2/0 conductor two 2/0 preform two one bolt clamp and replace blown fuse
Non-Outage | J.E.26.07.18969 | C001857086 | Marlon Brown | null | Completed | null | null | Jul 16, 2026 3:57pm | Jul 16, 2026 3:57pm | Jul 16, 2026 4:51pm | Jul 16, 2026 4:51pm | Jul 16, 2026 4:59pm | Jul 16, 2026 5:03pm | Jul 16, 2026 5:03pm | Jul 16, 2026 5:03pm |  |  | Fair | No | No meter at premises, new installation refer to Field Service Department.
Non-Outage | J.E.26.07.17316 | C001857076 | Nickolas Rodriques | Portmore | Completed | Load_259274 | Naggo Head - 510 | Jul 16, 2026 3:48pm | Jul 16, 2026 3:48pm | Jul 16, 2026 6:54pm | Jul 16, 2026 7:27pm | Jul 16, 2026 7:40pm | Jul 16, 2026 7:42pm | Jul 16, 2026 7:46pm | Jul 16, 2026 7:46pm |  |  | Fair | No | Unable to locate or communicate with the customer after several attempts
Outage | J.E.26.07.18992 | C001857077 | Marlon Authors | Manchester | Completed | Load_239635 | Spur Tree - 210 | Jul 16, 2026 3:48pm | Jul 16, 2026 3:50pm | Jul 16, 2026 10:26pm | Jul 16, 2026 10:26pm | Jul 16, 2026 10:26pm | Jul 16, 2026 10:56pm | Jul 16, 2026 11:03pm | Jul 16, 2026 11:03pm |  |  | Fair | No | Patrol and found clear. Replace one blown 2 amp fuse that protects 15 kva transformer circuit no pole #. Restored supply ok
Outage | J.E.26.07.18852 | C001857075 | Javid Vernon | Hanover | Completed | Load_239031 | Orange Bay - 310 | Jul 16, 2026 3:46pm | Jul 16, 2026 3:47pm | Jul 16, 2026 6:29pm | Jul 16, 2026 6:29pm | Jul 16, 2026 7:52pm | Jul 16, 2026 8:06pm | Jul 16, 2026 8:06pm | Jul 16, 2026 8:06pm |  |  | Fair | No | Area check and found okay unable to locate customer and premises phone calls to customer number went unanswered
Outage | J.E.26.07.18845 | C001857063 | Richard Grant | St.Catherine | Completed | Load_257649 | New Michelton - 210 | Jul 16, 2026 3:44pm | Jul 16, 2026 3:46pm | Jul 16, 2026 3:59pm | Jul 16, 2026 3:59pm | Jul 16, 2026 5:34pm | Jul 16, 2026 5:35pm | Jul 16, 2026 5:35pm | Jul 16, 2026 5:35pm |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.18762 | C001857062 | Rayon Foster | Hanover | Completed | Load_244774 | Orange Bay - 310 | Jul 16, 2026 3:42pm | Jul 16, 2026 3:42pm | Jul 16, 2026 4:29pm | Jul 16, 2026 4:29pm | Jul 16, 2026 5:58pm | null | Jul 16, 2026 8:37pm | Jul 16, 2026 8:37pm |  |  | null |  | Crew found defective 50kVA transformer, refer to maintenance to replace.
Non-Outage | J.E.26.07.16956 | C001857059 | Tajay Bernard | null | Completed | null | null | Jul 16, 2026 3:40pm | Jul 16, 2026 3:40pm | Jul 16, 2026 3:51pm | Jul 16, 2026 4:49pm | Jul 16, 2026 4:49pm | Jul 16, 2026 4:50pm | Jul 16, 2026 4:50pm | Jul 16, 2026 4:50pm | BrokenWire |  | Fair | No | This call belongs to st James
Outage | J.E.26.07.18819 | C001857057 | Evan Spaulding | St.Mary | Completed | Load_264696 | Highgate - 210 | Jul 16, 2026 3:39pm | Jul 16, 2026 3:39pm | Jul 16, 2026 4:12pm | Jul 16, 2026 4:12pm | Jul 16, 2026 5:08pm | Jul 16, 2026 6:17pm | Jul 16, 2026 6:19pm | Jul 16, 2026 6:19pm |  |  | Fair | No | Truck pull an Flow cable cause fuse holder to drop out at pole number 0072344.
Outage | J.E.26.07.18810 | C001857055 | Javid Vernon | Westmoreland | Completed | Load_261764 | Paradise - 210 | Jul 16, 2026 3:38pm | Jul 16, 2026 3:39pm | Jul 16, 2026 3:44pm | Jul 16, 2026 3:44pm | Jul 16, 2026 4:17pm | Jul 16, 2026 4:35pm | Jul 16, 2026 4:36pm | Jul 16, 2026 4:36pm |  | Y | Fair | No | Remove tree limb refuse one 25kva transformer use 3amp fuse at pole number 557172
Outage | J.E.26.07.18825 | C001857054 | Raymond Carr | St.Mary | Completed | Load_268843 | Oracabessa - 210 | Jul 16, 2026 3:38pm | Jul 16, 2026 3:38pm | Jul 16, 2026 4:39pm | Jul 16, 2026 4:39pm | Jul 16, 2026 5:04pm | Jul 16, 2026 5:00pm | Jul 16, 2026 5:06pm | Jul 16, 2026 5:06pm |  |  | Fair | No | Customer reported that supply was restored.
Outage | J.E.26.07.18866 | C001857056 | Javid Vernon | Westmoreland | Completed | Load_292669 | Paradise - 210 | Jul 16, 2026 3:38pm | Jul 16, 2026 3:39pm | Jul 16, 2026 4:39pm | Jul 16, 2026 4:40pm | Jul 16, 2026 5:44pm | Jul 16, 2026 6:25pm | Jul 16, 2026 6:28pm | Jul 16, 2026 6:28pm |  |  | Fair | No | Clean and remake joints at JPS pole and customer pothead use two clamps voltage found 95/102/198 voltage left 114/109/223
Outage | J.E.26.07.18839 | C001857042 | Swon Miller | St.James | Completed | Load_257668 | Queens Drive - 710 | Jul 16, 2026 3:35pm | Jul 16, 2026 3:35pm | Jul 16, 2026 3:42pm | Jul 16, 2026 3:42pm | Jul 16, 2026 3:55pm | Jul 1, 2026 4:10am | Jul 16, 2026 4:09pm | Jul 16, 2026 4:09pm | LeaningPole |  | Fair | No | Found 2 30 ft class six pole with 2/o north twisted and street light leaning and urgently need to be straighten one of the lean and break a customer stantion please refer to maintenance/kerron Frazier
Outage | J.E.26.07.18949 | C001857041 | Hartley Chin | Clarendon | Completed | Load_294461 | Monymusk - 210 | Jul 16, 2026 3:33pm | Jul 16, 2026 3:33pm | Jul 16, 2026 6:14pm | Jul 16, 2026 6:14pm | Jul 16, 2026 6:14pm | Jul 16, 2026 6:15pm | Jul 16, 2026 6:17pm | Jul 16, 2026 6:17pm |  |  | Fair | No | Premisis found ok. Customer was connected by field service
Outage | J.E.26.07.18952 | C001857040 | Romeo Brissett | St.James | Completed | Load_267594 | Bogue - 310 | Jul 16, 2026 3:32pm | Jul 16, 2026 3:33pm | Jul 16, 2026 4:27pm | Jul 16, 2026 4:27pm | Jul 16, 2026 7:31pm | Jul 16, 2026 8:18pm | Jul 16, 2026 8:28pm | Jul 16, 2026 8:28pm |  |  | Fair | No | Reclosed (1)65amps tripsaver junction at pole #057919 which feed to maroon town, removed tree limb at sunderland and replaced (1)50amps junction at spring square which feed to sunderland
Non-Outage | J.E.26.07.17338 | C001857039 | Hartley Chin | Clarendon | Completed | Load_295328 | Parnassus - 210 | Jul 16, 2026 3:31pm | Jul 16, 2026 3:31pm | Jul 16, 2026 5:18pm | Jul 16, 2026 5:55pm | Jul 16, 2026 5:55pm | Jul 16, 2026 5:56pm | Jul 16, 2026 5:58pm | Jul 16, 2026 5:58pm |  |  | Fair | No | Premisis not found. Unable to contact customer .
Outage | J.E.26.07.18777 | C001857029 | Fitzroy Turner | KSAS | Completed | Load_251482 | Cane River - 610 | Jul 16, 2026 3:30pm | Jul 16, 2026 3:30pm | Jul 16, 2026 3:57pm | Jul 16, 2026 3:57pm | Jul 16, 2026 5:51pm | Jul 16, 2026 6:21pm | Jul 16, 2026 6:22pm | Jul 16, 2026 6:22pm |  |  | Fair | No | JDF have internal problems defective 100kva transformer at there private property
Outage | J.E.26.07.18522 | C001857028 | Fitzroy Turner | KSAS | Completed | Load_258621 | Greenwich - 410 | Jul 16, 2026 3:29pm | Jul 16, 2026 3:30pm | Jul 16, 2026 8:54pm | Jul 16, 2026 8:54pm | Jul 16, 2026 8:54pm | Jul 16, 2026 9:21pm | Jul 16, 2026 9:25pm | Jul 16, 2026 9:25pm |  |  | Fair | No | Found tree wire service disconnected reconnected service using trees linket and one clamp.when checked carry out and meter found meter defective not communicating please send email to field service department to have meter change
Outage | J.E.26.07.18828 | C001857025 | Marlon Authors | St.Elizabeth | Completed | Load_260221 | Maggotty - 210 | Jul 16, 2026 3:26pm | Jul 16, 2026 3:28pm | Jul 16, 2026 7:26pm | Jul 16, 2026 7:27pm | Jul 16, 2026 7:27pm | Jul 16, 2026 7:29pm | Jul 16, 2026 7:29pm | Jul 16, 2026 7:29pm | BrokenWire |  | Fair | No | Supply restored to the area
Outage | J.E.26.07.18848 | C001857026 | Marlon Authors | St.Elizabeth | Completed | Load_251764 | Maggotty - 210 | Jul 16, 2026 3:26pm | Jul 16, 2026 3:28pm | Jul 16, 2026 3:59pm | Jul 16, 2026 3:59pm | Jul 16, 2026 4:13pm | Jul 16, 2026 4:36pm | Jul 16, 2026 4:36pm | Jul 16, 2026 4:36pm |  |  | Fair | No | Supply checked and found disconnected at pole. Connect same using two clamps, supply leave working okay rdg 114v,113v and cross phased 227 volts
Non-Outage | J.E.26.07.18918 | C001857021 | Marlon Authors | null | Completed | null | null | Jul 16, 2026 3:25pm | Jul 16, 2026 3:28pm | Jul 16, 2026 4:44pm | Jul 16, 2026 4:44pm | Jul 16, 2026 5:05pm | Jul 16, 2026 5:51pm | Jul 16, 2026 5:51pm | Jul 16, 2026 5:51pm | BrokenWire |  | Fair | No | Patrol and found secondary phase and neutral bond together caused by vehicle accident. Separate same and replace one blown 2 amp fuse that protects 25 kva transformer circuit at pole #0168061. Restored supply ok
Non-Outage | J.E.26.07.18955 | C001857022 | Marlon Authors | null | Completed | null | null | Jul 16, 2026 3:25pm | Jul 16, 2026 3:28pm | Jul 16, 2026 3:51pm | Jul 16, 2026 3:51pm | Jul 16, 2026 3:51pm | Jul 16, 2026 3:54pm | Jul 16, 2026 3:54pm | Jul 16, 2026 3:54pm |  |  | Fair | No | Unable to connect supply, hexing system is in this area. Please refer same to the field services department for further assistance
Non-Outage | J.E.26.07.18794 | C001857019 | Wayne Dillion | null | Completed | null | null | Jul 16, 2026 3:24pm | Jul 16, 2026 3:25pm | Jul 16, 2026 6:30pm | Jul 16, 2026 6:30pm | Jul 16, 2026 6:30pm | Jul 16, 2026 6:30pm | Jul 16, 2026 6:30pm | Jul 16, 2026 6:30pm |  |  | Fair | No | Call related
Outage | J.E.26.07.18735 | C001857020 | Raymond Lewis | St.Ann | Completed | Load_238506 | Cardiff Hall - 310 | Jul 16, 2026 3:24pm | Jul 16, 2026 3:24pm | Jul 16, 2026 7:36pm | Jul 16, 2026 7:36pm | Jul 16, 2026 7:36pm | Jul 16, 2026 7:42pm | Jul 16, 2026 7:42pm | Jul 16, 2026 7:42pm |  |  | Fair | No | customers ask to return in the morning due to two golden age persons at home unable to come out at night
Outage | J.E.26.07.18784 | C001857018 | Tyrese Williams | St.Ann | Completed | Load_258982 | Ocho Rios - 310 | Jul 16, 2026 3:24pm | Jul 16, 2026 3:24pm | Jul 16, 2026 4:27pm | Jul 16, 2026 7:11pm | Jul 16, 2026 8:03pm | Jul 16, 2026 8:24pm | Jul 16, 2026 8:25pm | Jul 16, 2026 8:25pm |  |  | Fair | No | Prem found ok customer has internal problem
Outage | J.E.26.07.18927 | C001857017 | Raymond Lewis | St.Ann | Completed | Load_242725 | Cardiff Hall - 210 | Jul 16, 2026 3:23pm | Jul 16, 2026 3:23pm | Jul 16, 2026 3:54pm | Jul 16, 2026 3:55pm | Jul 16, 2026 5:34pm | Jul 16, 2026 5:36pm | Jul 16, 2026 5:36pm | Jul 16, 2026 5:36pm |  |  | Fair | No | Customer say supply restored
Outage | J.E.26.07.18932 | C001857016 | Raymond Lewis | St.Ann | Completed | Load_246982 | Cardiff Hall - 310 | Jul 16, 2026 3:23pm | Jul 16, 2026 3:23pm | Jul 16, 2026 6:06pm | Jul 16, 2026 6:06pm | Jul 16, 2026 7:24pm | Jul 16, 2026 7:28pm | Jul 16, 2026 7:28pm | Jul 16, 2026 7:28pm |  |  | Fair | No | Remade joint at pole 3 wire service 107,108,215
Non-Outage | J.E.26.07.18514 | C001857014 | Milton Charlton | KSAN | Completed | Load_244521 | Hope - 410 | Jul 16, 2026 3:21pm | Jul 16, 2026 3:21pm | Jul 16, 2026 5:34pm | Jul 16, 2026 5:34pm | Jul 16, 2026 5:34pm | Jul 16, 2026 5:30pm | Jul 16, 2026 5:38pm | Jul 16, 2026 5:38pm | LeaningPole |  | Fair | No | 30ft. Wooden pole #0081947 need to dig and straighten.
Outage | J.E.26.07.18585 | C001857012 | Wayne Dillion | St.Elizabeth | Completed | Load_248213 | Maggotty - 110 | Jul 16, 2026 3:17pm | Jul 16, 2026 3:19pm | Jul 16, 2026 6:30pm | Jul 16, 2026 6:31pm | Jul 16, 2026 6:31pm | Jul 16, 2026 6:31pm | Jul 16, 2026 6:31pm | Jul 16, 2026 6:31pm |  |  | Fair | No | Call related
Outage | J.E.26.07.18588 | C001857011 | Wayne Dillion | St.Elizabeth | Completed | Load_248731 | Maggotty - 110 | Jul 16, 2026 3:17pm | Jul 16, 2026 3:19pm | Jul 16, 2026 6:29pm | Jul 16, 2026 6:29pm | Jul 16, 2026 6:29pm | Jul 16, 2026 6:30pm | Jul 16, 2026 6:30pm | Jul 16, 2026 6:30pm |  |  | Fair | No | Call related
Outage | J.E.26.07.18792 | C001857010 | Wayne Dillion | St.Elizabeth | Completed | Load_249923 | Maggotty - 110 | Jul 16, 2026 3:16pm | Jul 16, 2026 3:19pm | Jul 16, 2026 5:03pm | Jul 16, 2026 5:03pm | Jul 16, 2026 5:03pm | Jul 16, 2026 6:28pm | Jul 16, 2026 6:28pm | Jul 16, 2026 6:28pm |  |  | Fair | No | Patrol and found clear replace one 15 amp junction no pole number one 10 amp junction no pole number and one 2 amp fuse that protect 10 KVA at pole number 531076 supply restore to area successfully
Non-Outage | J.E.26.07.18871 | C001857000 | Raymond Carr | null | Completed | null | null | Jul 16, 2026 3:13pm | Jul 16, 2026 3:14pm | Jul 16, 2026 3:26pm | Jul 16, 2026 3:26pm | Jul 16, 2026 4:13pm | Jul 16, 2026 4:25pm | Jul 16, 2026 4:39pm | Jul 16, 2026 4:39pm |  |  | Fair | No | Service wire was reconnected at JPS pole. Voltage readings 117/119/236.
Outage | J.E.26.07.18888 | C001856979 | Ricky Hall | St.Catherine | Completed | Load_255976 | Tredegar - 410 | Jul 16, 2026 2:48pm | Jul 16, 2026 2:56pm | Jul 16, 2026 5:29pm | Jul 16, 2026 5:29pm | Jul 16, 2026 5:44pm | Jul 16, 2026 5:56pm | Jul 16, 2026 5:56pm | Jul 16, 2026 5:56pm |  |  | Fair | No | Replaced blown 10 amps fuse in bank of 2*100 kva xfmr
Outage | J.E.26.07.18901 | C001856957 | Horace Malcolm | St.James | Completed | Load_238552 | Bogue - 310 | Jul 16, 2026 2:28pm | Jul 16, 2026 2:29pm | Jul 16, 2026 2:38pm | Jul 16, 2026 2:46pm | Jul 16, 2026 3:00pm | Jul 16, 2026 3:07pm | Jul 16, 2026 3:05pm | Jul 16, 2026 3:05pm |  |  | Fair | No | Check and found one 65amp trip saver open pole at pole number 057819 crew shift ended
Outage | J.E.26.07.18816 | C001856941 | Milton Charlton | KSAN | Completed | Load_254264 | Hope - 510 | Jul 16, 2026 2:03pm | Jul 16, 2026 2:05pm | Jul 16, 2026 3:28pm | Jul 16, 2026 3:28pm | Jul 16, 2026 4:18pm | Jul 16, 2026 5:15pm | Jul 16, 2026 4:21pm | Jul 16, 2026 4:21pm |  |  | Fair | No | Found okay upon arrival. Readings at meter socket 114-113-228volts.
Outage | J.E.26.07.18789 | C001856925 | Denton Williams | Portland | Completed | Load_268118 | Port Antonio - 410 | Jul 16, 2026 1:39pm | Jul 16, 2026 3:07pm | Jul 16, 2026 3:25pm | Jul 16, 2026 3:25pm | Jul 16, 2026 5:24pm | Jul 16, 2026 6:11pm | Jul 16, 2026 6:13pm | Jul 16, 2026 6:13pm |  |  | Fair | No | 110 service wire broken at pole repair and ok material use 2-one bolt clamps voltage reading 117v
Non-Outage | J.E.26.07.18600 | C001856923 | Roemello Brown | Trelawny | Completed | Load_293110 | Greenwood - 210 | Jul 16, 2026 1:32pm | Jul 16, 2026 1:32pm | Jul 17, 2026 8:50am | Jul 17, 2026 9:20am | Jul 17, 2026 9:50am | Jul 17, 2026 10:03am | Jul 17, 2026 10:08am | Jul 17, 2026 10:08am |  |  | Fair | No | Transformer overload lots of illegal connections in the area need strike force to assist Voltage found 102/103/205Voltage leave 102/103/205
Non-Outage | J.E.26.07.18714 | C001856924 | Roemello Brown | Trelawny | Completed | Load_261226 | Duncans - 210 | Jul 16, 2026 1:32pm | Jul 16, 2026 1:32pm | Jul 17, 2026 12:59pm | Jul 17, 2026 12:59pm | Jul 17, 2026 2:07pm | Jul 17, 2026 2:07pm | Jul 17, 2026 2:12pm | Jul 17, 2026 2:12pm |  |  | Fair | No | Corrosion at pothead have linkets installed Voltage found 116/112/228Voltage leave 115/113/228
Non-Outage | J.E.26.07.18803 | C001856920 | Floyd Taylor | null | Completed | null | null | Jul 16, 2026 1:29pm | Jul 16, 2026 3:48pm | Jul 16, 2026 6:12pm | Jul 16, 2026 6:12pm | Jul 16, 2026 6:55pm | Jul 16, 2026 7:06pm | Jul 16, 2026 7:06pm | Jul 16, 2026 7:06pm |  |  | Fair | No | 10kva transformer maxed out required upgrade base on customer count voltage readings from transformer 98v,97v,197vRefer to maintenance
Non-Outage | J.E.26.07.18344 | C001856919 | Omar King | null | Completed | null | null | Jul 16, 2026 1:28pm | Jul 16, 2026 3:19pm | Jul 16, 2026 3:50pm | Jul 16, 2026 3:50pm | Jul 16, 2026 4:25pm | Jul 16, 2026 4:25pm | Jul 16, 2026 4:25pm | Jul 16, 2026 4:25pm |  |  | Fair | No | Unable to find customer call several times no answer directions not sufficient
Outage | J.E.26.07.18455 | C001856918 | Omar King | St.Ann | Completed | Load_241505 | Cardiff Hall - 310 | Jul 16, 2026 1:28pm | Jul 16, 2026 3:20pm | Jul 16, 2026 4:35pm | Jul 16, 2026 4:35pm | Jul 16, 2026 4:56pm | Jul 16, 2026 4:56pm | Jul 16, 2026 4:56pm | Jul 16, 2026 4:56pm |  |  | Fair | No | Problem as been resolved
Outage | J.E.26.07.18797 | C001856917 | Dean Smith | Hanover | Completed | Load_230038 | Orange Bay - 310 | Jul 16, 2026 1:27pm | Jul 16, 2026 1:27pm | Jul 16, 2026 3:07pm | Jul 16, 2026 3:08pm | Jul 16, 2026 3:08pm | Jul 16, 2026 3:08pm | Jul 16, 2026 3:08pm | Jul 16, 2026 3:08pm | BrokenWire |  | Fair | No | Area was restored
Non-Outage | J.E.26.07.18761 | C001856916 | Rusean Allen | KSAS | Completed | Load_242005 | Rockfort - 410 | Jul 16, 2026 1:26pm | Jul 16, 2026 1:26pm | Jul 17, 2026 12:29pm | Jul 17, 2026 12:29pm | Jul 17, 2026 1:36pm | Jul 17, 2026 1:37pm | Jul 17, 2026 1:37pm | Jul 17, 2026 1:37pm |  |  | Fair | No | Found okay
Outage | J.E.26.07.18773 | C001856912 | Richard Samuda | Manchester | Completed | Load_261060 | Spur Tree - 310 | Jul 16, 2026 1:22pm | Jul 16, 2026 1:26pm | Jul 16, 2026 2:18pm | Jul 16, 2026 2:18pm | Jul 16, 2026 2:48pm | Jul 16, 2026 3:09pm | Jul 16, 2026 3:10pm | Jul 16, 2026 3:10pm | BrokenWire |  | Fair | No | Change corroded 1bolt clamp on service neutral that leads to customer premises that was corroded causing customer to experience low using 1bolt clamp customer back to normal voltage 114/114/228
Outage | J.E.26.07.18808 | C001856910 | Edward Royal | KSAS | Completed | Load_240820 | Greenwich - 310 | Jul 16, 2026 1:22pm | Jul 17, 2026 8:04am | Jul 17, 2026 9:26am | Jul 17, 2026 9:37am | Jul 17, 2026 9:37am | Jul 17, 2026 9:50am | Jul 17, 2026 9:51am | Jul 17, 2026 9:51am | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Premises found voltage reading 117v 118v 235v
Outage | J.E.26.07.18806 | C001856905 | Stephen Taylor | Portland | Completed | Load_264218 | Port Antonio - 310 | Jul 16, 2026 1:17pm | Jul 16, 2026 2:08pm | Jul 17, 2026 11:49am | Jul 17, 2026 11:49am | Jul 17, 2026 11:49am | Jul 17, 2026 11:51am | Jul 17, 2026 11:51am | Jul 17, 2026 11:51am |  |  | Fair | No | Premise lock with bad dog in yard
Outage | J.E.26.07.18788 | C001856894 | Swon Miller | St.James | Completed | Load_267952 | Rose Hall - 210 | Jul 16, 2026 12:57pm | Jul 16, 2026 3:35pm | Jul 16, 2026 4:11pm | Jul 16, 2026 4:11pm | Jul 16, 2026 4:50pm | Jul 28, 2026 6:03am | Jul 16, 2026 6:23pm | Jul 16, 2026 6:23pm |  |  | Fair | No | Check and found customer single phasing cause by truck pulling on cable wires banging on the secondary line which caused drop lead to burn off open 50 kva transformer use 3 ft #2AA and 2 pg to carry out repairs close up 50 kva transformer voltage found 116 voltage left 116/116/232
Non-Outage | J.E.26.07.18082 | C001856888 | Tyrese Williams | St.Ann | Completed | Load_243679 | Roaring River - 210 | Jul 16, 2026 12:52pm | Jul 16, 2026 3:35pm | Jul 16, 2026 4:27pm | Jul 16, 2026 8:34pm | Jul 16, 2026 9:37pm | Jul 16, 2026 9:51pm | Jul 16, 2026 9:55pm | Jul 16, 2026 9:55pm |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.07.18748 | C001856887 | Dean Smith | null | Completed | null | null | Jul 16, 2026 12:51pm | Jul 16, 2026 12:52pm | Jul 16, 2026 3:07pm | Jul 17, 2026 5:41pm | Jul 17, 2026 5:41pm | Jul 17, 2026 5:42pm | Jul 17, 2026 5:42pm | Jul 17, 2026 5:42pm |  |  | Fair | No | Check and found ok
Outage | J.E.26.07.18762 | C001856886 | Dean Smith | Hanover | Completed | Load_244774 | Orange Bay - 310 | Jul 16, 2026 12:51pm | Jul 16, 2026 12:52pm | Jul 16, 2026 1:52pm | Jul 17, 2026 5:41pm | Jul 17, 2026 5:41pm | Jul 17, 2026 5:41pm | Jul 17, 2026 5:41pm | Jul 17, 2026 5:41pm |  |  | Fair | No | Check and found ok
Outage | J.E.26.07.18774 | C001856881 | Stephen Taylor | St.Thomas | Completed | Load_351223 | Good Year - 110 | Jul 16, 2026 12:49pm | Jul 16, 2026 12:50pm | Jul 16, 2026 2:42pm | Jul 16, 2026 2:42pm | Jul 16, 2026 3:05pm | Jul 16, 2026 3:05pm | Jul 16, 2026 3:08pm | Jul 16, 2026 3:08pm | BrokenWire |  | Fair | No | Customer advise to get an electrician to replace meter socket wire. Wires are defective
Outage | J.E.26.07.18746 | C001856880 | Raymond Lewis | St.Ann | Completed | Load_575875 | Cardiff Hall - 210 | Jul 16, 2026 12:45pm | Jul 16, 2026 3:21pm | Jul 16, 2026 5:42pm | Jul 16, 2026 5:42pm | Jul 16, 2026 5:42pm | Jul 16, 2026 5:51pm | Jul 16, 2026 5:51pm | Jul 16, 2026 5:51pm |  |  | Fair | No | Customer say there is supply
Outage | J.E.26.07.18780 | C001856871 | Moses Elliston | St.Catherine | Completed | Load_264958 | Tredegar - 410 | Jul 16, 2026 12:45pm | Jul 16, 2026 12:48pm | Jul 17, 2026 4:01pm | Jul 17, 2026 4:01pm | Jul 17, 2026 4:01pm | Jul 17, 2026 1:15pm | Jul 17, 2026 4:02pm | Jul 17, 2026 4:02pm |  |  | Fair | No | Not located ,no answer from cell
Non-Outage | J.E.26.07.17340 | C001856870 | Daniel Francis | St.Ann | Completed | Load_251089 | Roaring River - 410 | Jul 16, 2026 12:41pm | Jul 16, 2026 12:41pm | Jul 16, 2026 2:24pm | Jul 16, 2026 2:24pm | Jul 16, 2026 2:42pm | Jul 16, 2026 2:51pm | Jul 16, 2026 2:54pm | Jul 16, 2026 2:54pm |  |  | Fair | No | Remade joint at pole 2. 1bolt clamp voltage 115/116/232
Outage | J.E.26.07.18739 | C001856863 | Derrick Dawkins | St.James | Completed | Load_261318 | Bogue - 610 | Jul 16, 2026 12:37pm | Jul 16, 2026 10:53pm | Jul 17, 2026 2:27am | Jul 17, 2026 2:27am | Jul 17, 2026 2:37am | Jul 17, 2026 2:40am | Jul 17, 2026 2:40am | Jul 17, 2026 2:40am |  |  | Fair | No | Cannot locate customer
Outage | J.E.26.07.18771 | C001856856 | Stephen Taylor | St.Thomas | Completed | Load_577217 | Good Year - 210 | Jul 16, 2026 12:33pm | Jul 16, 2026 12:35pm | Jul 17, 2026 9:11am | Jul 17, 2026 9:11am | Jul 17, 2026 11:28am | Jul 17, 2026 11:28am | Jul 17, 2026 11:31am | Jul 17, 2026 11:31am |  |  | Fair | No | Splice and retention secondary wire use 6 clamps and close up back 25 kva transformer safely all customer is now okay
Non-Outage | J.E.26.07.18642 | C001856831 | Odaine Johnson | Clarendon | Completed | Load_264346 | Parnassus - 210 | Jul 16, 2026 12:19pm | Jul 16, 2026 12:20pm | Jul 16, 2026 1:02pm | Jul 16, 2026 2:28pm | Jul 16, 2026 3:09pm | Jul 16, 2026 3:10pm | Jul 16, 2026 3:10pm | Jul 16, 2026 3:10pm |  |  | Fair | No | Premises found okay voltage reading 115/115/231
Non-Outage | J.E.26.07.18678 | C001856832 | Odaine Johnson | Clarendon | Completed | Load_265095 | Parnassus - 310 | Jul 16, 2026 12:19pm | Jul 16, 2026 12:20pm | Jul 16, 2026 1:02pm | Jul 16, 2026 2:23pm | Jul 16, 2026 2:23pm | Jul 16, 2026 2:24pm | Jul 16, 2026 2:24pm | Jul 16, 2026 2:24pm |  |  | Fair | No | Same area same issue
Non-Outage | J.E.26.07.18679 | C001856833 | Odaine Johnson | Clarendon | Completed | Load_265095 | Parnassus - 310 | Jul 16, 2026 12:19pm | Jul 16, 2026 12:20pm | Jul 16, 2026 1:02pm | Jul 16, 2026 2:16pm | Jul 16, 2026 2:22pm | Jul 16, 2026 2:23pm | Jul 16, 2026 2:23pm | Jul 16, 2026 2:23pm |  |  | Fair | No | Please refer this issue to a emergency team
Non-Outage | J.E.26.07.18686 | C001856834 | Odaine Johnson | Clarendon | Completed | Load_255380 | May Pen - 110 | Jul 16, 2026 12:19pm | Jul 16, 2026 12:20pm | Jul 16, 2026 1:02pm | Jul 17, 2026 1:12pm | Jul 17, 2026 1:13pm | Jul 17, 2026 1:13pm | Jul 17, 2026 1:14pm | Jul 17, 2026 1:14pm |  |  | Fair | No | Slack connections found at pole and tension voltage reading 120 volts
Non-Outage | J.E.26.07.18705 | C001856830 | Jermaine Williams | Clarendon | Completed | Load_268883 | Monymusk - 410 | Jul 16, 2026 12:19pm | Jul 16, 2026 12:19pm | Jul 16, 2026 1:01pm | Jul 16, 2026 1:02pm | Jul 16, 2026 1:27pm | Jul 16, 2026 2:04pm | Jul 16, 2026 2:05pm | Jul 16, 2026 2:05pm | Fire |  | SevereWind | No | Patrol and remade burnt off secondary jumper using two clamps.
Non-Outage | J.E.26.07.18648 | C001856829 | Odaine Johnson | St.Catherine | Completed | Load_256483 | Rhodens Pen - 310 | Jul 16, 2026 12:18pm | Jul 16, 2026 12:18pm | Jul 16, 2026 1:02pm | Jul 16, 2026 1:05pm | Jul 16, 2026 2:07pm | Jul 16, 2026 2:07pm | Jul 16, 2026 2:08pm | Jul 16, 2026 2:08pm |  |  | Fair | No | Burn off phase found at pole remade connection using 1 one bolt clamp voltage reading 111/113/224 volts
Outage | J.E.26.07.18701 | C001856828 | Rayon Foster | Hanover | Completed | Load_258609 | Orange Bay - 210 | Jul 16, 2026 12:16pm | Jul 16, 2026 12:51pm | Jul 16, 2026 1:40pm | Jul 16, 2026 1:42pm | Jul 16, 2026 2:54pm | Jul 16, 2026 4:06pm | Jul 16, 2026 4:06pm | Jul 16, 2026 4:06pm | LeaningPole |  | Fair | No | Leaning DV pole with two guy with street light attach pole # 459285 refer to maintenance crew to change pole
Outage | J.E.26.07.18719 | C001856823 | Dwayne Samuels | Trelawny | Completed | Load_264087 | Martha Brae - 110 | Jul 16, 2026 12:12pm | Jul 16, 2026 12:13pm | Jul 16, 2026 12:20pm | Jul 16, 2026 12:20pm | Jul 16, 2026 1:30pm | Jul 16, 2026 2:10pm | Jul 16, 2026 2:10pm | Jul 16, 2026 2:10pm | BrokenWire |  | Fair | No | Internal problem customer neighbor was advised to tell her same, after disconnecting other customer that’s is not ready for connection due to pole and pothead is damaged customer was for to have internal issues locking bad is on meter …
Outage | J.E.26.07.18603 | C001856806 | Daniel Francis | St.Ann | Completed | Load_242957 | Roaring River - 210 | Jul 16, 2026 12:04pm | Jul 16, 2026 12:04pm | Jul 16, 2026 12:30pm | Jul 16, 2026 12:30pm | Jul 16, 2026 1:55pm | Jul 16, 2026 2:22pm | Jul 16, 2026 2:23pm | Jul 16, 2026 2:23pm |  |  | Fair | No | Change one 5amp fuse
Outage | J.E.26.07.18646 | C001856807 | Tyrese Williams | St.Ann | Completed | Load_254445 | Roaring River - 210 | Jul 16, 2026 12:04pm | Jul 16, 2026 3:16pm | Jul 16, 2026 4:27pm | Jul 16, 2026 6:00pm | Jul 16, 2026 6:43pm | Jul 16, 2026 7:10pm | Jul 16, 2026 7:11pm | Jul 16, 2026 7:11pm |  |  | Fair | No | Remade service wire joint at pole and pothead
Outage | J.E.26.07.18707 | C001856804 | Neckell Ormsby | St.Mary | Completed | Load_257358 | Highgate -110 | Jul 16, 2026 12:01pm | Jul 16, 2026 12:02pm | Jul 16, 2026 12:12pm | Jul 16, 2026 12:12pm | Jul 16, 2026 1:31pm | Jul 16, 2026 1:00am | Jul 17, 2026 7:32am | Jul 17, 2026 7:32am |  |  | Fair | No | Open 10amp to cut bamboo. Remdae secondary jumper. Volatge 120 120 240. Use 2 one-bolt clamp to remade secondary jumper Call was resolved from yesterday but the tablet died Having charging issues
Outage | J.E.26.07.18718 | C001856791 | Cliton Henry | St.Mary | Completed | Load_267776 | Oracabessa - 210 | Jul 16, 2026 12:00pm | Jul 16, 2026 12:00pm | Jul 16, 2026 12:22pm | Jul 16, 2026 12:22pm | Jul 16, 2026 1:05pm | Jul 16, 2026 1:29pm | Jul 16, 2026 1:33pm | Jul 16, 2026 1:33pm | Fire |  | Fair | No | Two Illegal connections were removed from the 2/0 triplex secondary conductor.m
Outage | J.E.26.07.18720 | C001856790 | Nickolas Rodriques | Portmore | Completed | Load_238237 | Naggo Head - 610 | Jul 16, 2026 11:59am | Jul 16, 2026 11:59am | Jul 16, 2026 12:37pm | Jul 16, 2026 12:37pm | Jul 16, 2026 1:23pm | Jul 16, 2026 2:07pm | Jul 16, 2026 2:19pm | Jul 16, 2026 2:19pm | Fire |  | Fair | No | Checked and found one pole span of secondary neutral down caused by low banging wire. Isolate 50 KVA transformer for safety to repair. Repaired by splice and retention wire using 40 ft of #2 aluminum, one splicing sleeve, two clamps and replaced the fuse after completing patrol.
Non-Outage | J.E.26.07.18693 | C001856775 | Donald Cunningham | St.Catherine | Completed | Load_238458 | Rhodens Pen - 410 | Jul 16, 2026 11:52am | Jul 16, 2026 11:55am | Jul 16, 2026 2:59pm | Jul 16, 2026 3:04pm | Jul 16, 2026 4:26pm | Jul 16, 2026 4:32pm | Jul 16, 2026 4:33pm | Jul 16, 2026 4:33pm | LeaningPole |  | Fair | No | Single phase primary and secondary pole need to dig and straighten
Outage | J.E.26.07.18702 | C001856776 | Clyde Brown | Clarendon | Completed | Load_241943 | May Pen - 110 | Jul 16, 2026 11:52am | Jul 16, 2026 11:55am | Jul 16, 2026 12:12pm | Jul 16, 2026 12:12pm | Jul 16, 2026 12:12pm | Jul 16, 2026 1:40pm | Jul 16, 2026 1:54pm | Jul 16, 2026 1:54pm | BrokenWire |  | Fair | No | Broken secondary phase ,open bank of 2 kva transformer and repair secondary conductor with 8ft-#2/0,2-splicing sleeve,1- preform and 1- clamp
Outage | J.E.26.07.18467 | C001856744 | Raymond Lewis | St.Ann | Completed | Load_556416 | Roaring River - 210 | Jul 16, 2026 11:25am | Jul 16, 2026 10:52pm | Jul 17, 2026 4:14am | Jul 17, 2026 4:14am | Jul 17, 2026 4:14am | Jul 17, 2026 4:16am | Jul 17, 2026 4:17am | Jul 17, 2026 4:17am |  |  | Fair | No | Supply was restored
Outage | J.E.26.07.18669 | C001856727 | Ricky Hall | St.Catherine | Completed | Load_241136 | Tredegar - 210 | Jul 16, 2026 11:14am | Jul 16, 2026 11:16am | Jul 16, 2026 7:35pm | Jul 16, 2026 7:45pm | Jul 16, 2026 8:02pm | Jul 16, 2026 8:03pm | Jul 16, 2026 8:03pm | Jul 16, 2026 8:03pm |  |  | Fair | No | Site not located
Outage | J.E.26.07.18665 | C001856726 | Horace Malcolm | St.James | Completed | Load_303201 | Bogue - 310 | Jul 16, 2026 11:11am | Jul 16, 2026 11:12am | Jul 16, 2026 11:26am | Jul 16, 2026 11:27am | Jul 16, 2026 11:48am | Jul 16, 2026 11:49am | Jul 16, 2026 11:49am | Jul 16, 2026 11:49am |  |  | Fair | No | Check and found premises ok voltage 115-118-232
Outage | J.E.26.07.17662 | C001856720 | Shamour Haughton | St.James | Completed | Load_254484 | Bogue - 610 | Jul 16, 2026 11:09am | Jul 16, 2026 11:09am | Jul 16, 2026 12:16pm | Jul 16, 2026 12:22pm | Jul 16, 2026 2:20pm | Jul 16, 2026 2:20pm | Jul 16, 2026 2:24pm | Jul 16, 2026 2:24pm | BrokenPole,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Customer meter socket defective and needs to be change
Outage | J.E.26.07.18604 | C001856719 | Michael Christian | St.James | Completed | Load_245170 | Queens Drive - 710 | Jul 16, 2026 11:07am | Jul 16, 2026 11:11am | Jul 16, 2026 1:48pm | Jul 16, 2026 1:57pm | Jul 16, 2026 2:40pm | Jul 16, 2026 3:05pm | Jul 16, 2026 3:19pm | Jul 16, 2026 3:19pm |  |  | Fair | No | Internal fault
Non-Outage | J.E.26.07.14434 | C001856718 | Ricky Hall | St.Catherine | Completed | Load_256045 | Tredegar - 510 | Jul 16, 2026 11:05am | Jul 16, 2026 11:07am | Jul 16, 2026 11:25am | Jul 16, 2026 1:25pm | Jul 16, 2026 1:53pm | Jul 16, 2026 4:29pm | Jul 16, 2026 4:30pm | Jul 16, 2026 4:30pm |  |  | Fair | Yes | Rep Defective 3W service use 70’#6 triplex 3 clamps 3 pen union 118*2/236
Non-Outage | J.E.26.07.10704 | C001856709 | Kemark Slue | St.Catherine | Completed | Load_266494 | New Michelton - 210 | Jul 16, 2026 11:04am | Jul 16, 2026 11:05am | Jul 16, 2026 1:03pm | Jul 16, 2026 2:58pm | Jul 16, 2026 2:59pm | Jul 16, 2026 2:55pm | Jul 16, 2026 3:00pm | Jul 16, 2026 3:00pm | BrokenPole |  | Fair | No | Premises was checked and found okay.
Non-Outage | J.E.26.07.18652 | C001856708 | Edward Royal | null | Completed | null | null | Jul 16, 2026 11:04am | Jul 16, 2026 11:23am | Jul 16, 2026 1:16pm | Jul 16, 2026 1:34pm | Jul 16, 2026 1:34pm | Jul 16, 2026 2:49pm | Jul 16, 2026 2:50pm | Jul 16, 2026 2:50pm | LowHangingWires |  | SevereWind | No | Replaced 3 junction fuse (1) 15A (1) 30A (1) 50A
Non-Outage | J.E.26.07.18648 | C001856706 | Donald Cunningham | St.Catherine | Completed | Load_256483 | Rhodens Pen - 310 | Jul 16, 2026 11:03am | Jul 16, 2026 11:05am | Jul 16, 2026 11:19am | Jul 16, 2026 11:19am | Jul 16, 2026 12:17pm | Jul 16, 2026 12:18pm | Jul 16, 2026 12:19pm | Jul 16, 2026 12:19pm |  |  | Fair | No | Call is for Clarendon crew
Outage | J.E.26.07.18614 | C001856707 | Andre Williams | Trelawny | Completed | Load_262583 | Duncans - 210 | Jul 16, 2026 11:03am | Jul 16, 2026 11:05am | Jul 16, 2026 12:03pm | Jul 16, 2026 12:15pm | Jul 16, 2026 1:13pm | Jul 16, 2026 1:16pm | Jul 16, 2026 1:16pm | Jul 16, 2026 1:16pm |  |  | Fair | No | Customer meter turn on and off by meter center communication establish with meter customer was advice to check breaker (customer not at premises at the moment )
Non-Outage | J.E.26.07.18537 | C001856684 | Stephen Taylor | St.Thomas | Completed | Load_259414 | Good Year - 210 | Jul 16, 2026 10:44am | Jul 16, 2026 10:44am | Jul 16, 2026 3:08pm | Jul 16, 2026 3:08pm | Jul 16, 2026 4:05pm | Jul 16, 2026 4:05pm | Jul 16, 2026 4:20pm | Jul 16, 2026 4:20pm |  |  | Fair | No | Clean up single phase use 3 clamps reading 112,113,225 customer is now okay
Outage | J.E.26.07.18636 | C001856685 | Hartley Chin | Clarendon | Completed | Load_237834 | Parnassus - 210 | Jul 16, 2026 10:44am | Jul 16, 2026 3:32pm | Jul 16, 2026 3:47pm | Jul 16, 2026 3:47pm | Jul 16, 2026 5:02pm | Jul 16, 2026 1:00am | Jul 16, 2026 5:13pm | Jul 16, 2026 5:13pm | BrokenPole |  | Fair | No | Refer to maintenance. Broken 30 foot pole causing low hanging wires. Needs urgent attention .
Non-Outage | J.E.26.07.18623 | C001856680 | Nickolas Rodriques | null | Completed | null | null | Jul 16, 2026 10:39am | Jul 16, 2026 10:45am | Jul 16, 2026 3:57pm | Jul 16, 2026 3:57pm | Jul 16, 2026 4:01pm | Jul 16, 2026 4:04pm | Jul 16, 2026 4:15pm | Jul 16, 2026 4:15pm |  |  | Fair | No | Call relates to the 30 ft wooden pole that was found broken by vehicle accident. Customers are still without electricity.
Non-Outage | J.E.26.07.18580 | C001856668 | Richman Whyte | Westmoreland | Completed | Load_252942 | Paradise - 310 | Jul 16, 2026 10:29am | Jul 16, 2026 10:29am | Jul 16, 2026 12:57pm | Jul 16, 2026 12:57pm | Jul 16, 2026 12:57pm | Jul 16, 2026 12:57pm | Jul 16, 2026 12:58pm | Jul 16, 2026 12:58pm |  |  | EarthMovement | No | Repair broken service wire at secondary line voltage #110 109 220
Outage | J.E.26.07.18577 | C001856667 | Jermaine Williams | Clarendon | Completed | Load_570016 | Monymusk - 210 | Jul 16, 2026 10:27am | Jul 16, 2026 10:35am | Jul 16, 2026 11:58am | Jul 16, 2026 11:58am | Jul 16, 2026 12:59pm | Jul 16, 2026 12:59pm | Jul 16, 2026 1:00pm | Jul 16, 2026 1:00pm |  |  | SevereWind | No | Hexing failure, refer to Hopeton Daley from Field Service dept.
Outage | J.E.26.07.18265 | C001856666 | Moses Elliston | Portmore | Completed | Load_570190 | Naggo Head - 610 | Jul 16, 2026 10:26am | Jul 16, 2026 10:27am | Jul 16, 2026 4:50pm | Jul 16, 2026 4:50pm | Jul 16, 2026 5:55pm | Jul 16, 2026 5:56pm | Jul 16, 2026 5:59pm | Jul 16, 2026 5:59pm |  |  | Fair | No | Slack clamp on street light phase lead tightened
Outage | J.E.26.07.18553 | C001856662 | Damion Reid | Manchester | Completed | Load_256312 | Spur Tree - 310 | Jul 16, 2026 10:20am | Jul 16, 2026 4:05pm | Jul 16, 2026 4:49pm | Jul 16, 2026 4:49pm | Jul 16, 2026 5:25pm | Jul 16, 2026 5:42pm | Jul 16, 2026 5:45pm | Jul 16, 2026 5:45pm |  |  | SevereWind | No | Remade burnt off phase at secondary pole for 3 wire service using one 1 bolt clamp voltage reading at meter socket phase to neutral 114v-116v across phase 232v
Outage | J.E.26.07.18562 | C001856663 | Richard Samuda | Manchester | Completed | Load_258048 | Spur Tree - 310 | Jul 16, 2026 10:20am | Jul 16, 2026 10:21am | Jul 16, 2026 10:34am | Jul 16, 2026 10:34am | Jul 16, 2026 11:32am | Jul 16, 2026 1:16am | Jul 16, 2026 1:17pm | Jul 16, 2026 1:17pm |  |  | Fair | No | Change customer service wire that was defective causing customer to experience single phase using 25ft of #6 service wire customer back to normal 115/115 230
Non-Outage | J.E.26.07.14794 | C001856656 | Edward Royal | KSAS | Completed | Load_261030 | Rockfort - 410 | Jul 16, 2026 10:13am | Jul 16, 2026 10:13am | Jul 16, 2026 10:35am | Jul 16, 2026 10:35am | Jul 16, 2026 10:43am | Jul 16, 2026 1:03pm | Jul 16, 2026 1:03pm | Jul 16, 2026 1:03pm |  |  | Fair | No | We replace a coated cable with a number 2 triplex cable using 8 one bold clamps and two number preform.pole #0174878
Outage | J.E.26.07.18589 | C001856655 | Rusean Allen | KSAS | Completed | Load_239100 | Hunts Bay - 410 | Jul 16, 2026 10:11am | Jul 17, 2026 8:07am | Jul 17, 2026 8:58am | Jul 17, 2026 8:59am | Jul 17, 2026 9:50am | Jul 17, 2026 9:51am | Jul 17, 2026 9:51am | Jul 17, 2026 9:51am |  |  | Fair | No | Found okay
Outage | J.E.26.07.18559 | C001856637 | Selvin White | St.Elizabeth | Completed | Load_268564 | Maggotty - 110 | Jul 16, 2026 10:04am | Jul 16, 2026 10:04am | Jul 16, 2026 2:41pm | Jul 16, 2026 2:43pm | Jul 16, 2026 2:43pm | Jul 16, 2026 2:46pm | Jul 16, 2026 2:47pm | Jul 16, 2026 2:47pm |  |  | Fair | No | Order was referred to Simone Bicarie at the field service department who said an order for the field service technician to visit premises was generated.
Outage | J.E.26.07.18578 | C001856621 | Milton Charlton | KSAN | Completed | Load_254959 | West Kings House - 410 | Jul 16, 2026 9:54am | Jul 16, 2026 10:00am | Jul 16, 2026 12:24pm | Jul 16, 2026 1:04pm | Jul 16, 2026 1:04pm | Jul 16, 2026 12:55pm | Jul 16, 2026 1:09pm | Jul 16, 2026 1:09pm |  |  | Fair | No | Call belongs to Portland Parish district. Swift River.
Non-Outage | J.E.26.07.17048 | C001856619 | Error Coore | Manchester | Completed | Load_255183 | Spur Tree - 310 | Jul 16, 2026 9:52am | Jul 16, 2026 9:53am | Jul 16, 2026 11:39am | Jul 16, 2026 2:05pm | Jul 16, 2026 2:15pm | Jul 16, 2026 2:16pm | Jul 16, 2026 2:16pm | Jul 16, 2026 2:16pm |  |  | Fair | No | Premise found ok call customer and customer said that she did not make any report
Non-Outage | J.E.26.07.17268 | C001856618 | Error Coore | Manchester | Completed | Load_255680 | Spur Tree - 310 | Jul 16, 2026 9:52am | Jul 16, 2026 9:52am | Jul 16, 2026 2:17pm | Jul 16, 2026 2:17pm | Jul 16, 2026 2:17pm | Jul 16, 2026 2:18pm | Jul 16, 2026 2:19pm | Jul 16, 2026 2:19pm |  |  | Fair | No | Premise found ok call customer and customer said that she did not make any report
Non-Outage | J.E.26.07.18086 | C001856617 | Error Coore | Manchester | Completed | Load_264034 | Porus - 210 | Jul 16, 2026 9:52am | Jul 16, 2026 9:52am | Jul 16, 2026 11:43am | Jul 16, 2026 11:43am | Jul 16, 2026 12:05pm | Jul 16, 2026 12:36pm | Jul 16, 2026 12:38pm | Jul 16, 2026 12:38pm |  |  | Fair | No | Customer is having low voltage due illegal connection customer is at the end of the circuit voltage reading at xformer 117/118/235 volts
Non-Outage | J.E.26.07.18088 | C001856615 | Error Coore | Manchester | Completed | Load_1002521 | Kendal - 310 | Jul 16, 2026 9:52am | Jul 16, 2026 9:52am | Jul 16, 2026 10:06am | Jul 16, 2026 10:06am | Jul 16, 2026 10:16am | Jul 16, 2026 11:33am | Jul 16, 2026 11:37am | Jul 16, 2026 11:37am |  |  | Fair | No | Found customer with corroded phase and neutral at pothead and pothead remade corroded phase and neutral using 4 one bolt clamp and 2 service sleeve voltage reading 114/113/227 volts
Non-Outage | J.E.26.07.18548 | C001856616 | Error Coore | Manchester | Completed | Load_246031 | Spur Tree - 310 | Jul 16, 2026 9:52am | Jul 16, 2026 9:52am | Jul 16, 2026 12:41pm | Jul 16, 2026 12:41pm | Jul 16, 2026 12:57pm | Jul 16, 2026 2:03pm | Jul 16, 2026 2:05pm | Jul 16, 2026 2:05pm |  |  | Fair | No | Found customer with corroded phase and neutral using 3 one bolt clamp voltage reading 111/112/223 volt
Outage | J.E.26.07.18564 | C001856605 | Christopher Edwards | KSAN | Completed | Load_257226 | Constant Spring - 410 | Jul 16, 2026 9:43am | Jul 16, 2026 9:55am | Jul 16, 2026 4:13pm | Jul 16, 2026 4:59pm | Jul 16, 2026 5:34pm | Jul 16, 2026 6:11pm | Jul 16, 2026 6:12pm | Jul 16, 2026 6:12pm |  |  | Fair | No | Remake burnt phase joint At pole using (1) one bolt clamps Voltage:113,114,230v
Outage | J.E.26.07.18558 | C001856599 | Eric Williams | KSAS | Completed | Load_256936 | Greenwich - 710 | Jul 16, 2026 9:36am | Jul 16, 2026 9:37am | Jul 16, 2026 11:15am | Jul 16, 2026 11:15am | Jul 16, 2026 11:21am | Jul 16, 2026 11:24am | Jul 16, 2026 11:26am | Jul 16, 2026 11:26am |  |  | Fair | No | Customer applied to the wrong meter, customer advised to visit the office
Outage | J.E.26.07.18530 | C001856590 | Oshane Warren | Hanover | Completed | Load_263899 | Orange Bay - 310 | Jul 16, 2026 9:33am | Jul 16, 2026 9:33am | Jul 16, 2026 11:43am | Jul 16, 2026 11:43am | Jul 16, 2026 11:51am | Jul 16, 2026 12:11pm | Jul 16, 2026 12:12pm | Jul 16, 2026 12:12pm |  |  | Fair | No | Premises locked
Non-Outage | J.E.26.07.12188 | C001856589 | Daniel Francis | St.Ann | Completed | Load_261149 | Roaring River - 410 | Jul 16, 2026 9:32am | Jul 16, 2026 9:33am | Jul 16, 2026 10:53am | Jul 16, 2026 10:53am | Jul 16, 2026 11:09am | Jul 16, 2026 11:20am | Jul 16, 2026 11:21am | Jul 16, 2026 11:21am |  |  | Fair | No | Change 2 one bolt clamp 117 117 234 in all
Outage | J.E.26.07.18552 | C001856588 | Dean Smith | Hanover | Completed | Load_253054 | Orange Bay - 310 | Jul 16, 2026 9:31am | Jul 16, 2026 9:31am | Jul 16, 2026 2:59pm | Jul 16, 2026 2:59pm | Jul 16, 2026 2:59pm | Jul 16, 2026 3:02pm | Jul 16, 2026 3:03pm | Jul 16, 2026 3:03pm |  |  | Fair | No | Check and found ok
Outage | J.E.26.07.18550 | C001856582 | Eric Williams | KSAN | Completed | Load_245872 | Washington Blvd - 410 | Jul 16, 2026 9:28am | Jul 16, 2026 9:28am | Jul 16, 2026 10:50am | Jul 16, 2026 10:50am | Jul 16, 2026 11:11am | Jul 16, 2026 11:15am | Jul 16, 2026 11:15am | Jul 16, 2026 11:15am |  |  | Fair | No | Cx stated he is experiencing single phase readings at stantion checked and found okay 118 119 239 . Meter checked and found to be defective needs to be replaced urgent attention
Outage | J.E.26.07.18379 | C001856574 | Daniel Francis | Clarendon | Completed | Load_349775 | May Pen - 110 | Jul 16, 2026 9:24am | Jul 16, 2026 10:01am | Jul 17, 2026 1:04pm | Jul 17, 2026 1:04pm | Jul 17, 2026 1:04pm | Jul 17, 2026 1:05pm | Jul 17, 2026 1:06pm | Jul 17, 2026 1:06pm |  |  | Fair | No | We call customer and they say light come it’s okay now
Outage | J.E.26.07.18433 | C001856572 | Roxroy Needham | St.Ann | Completed | Load_266959 | Cardiff Hall - 210 | Jul 16, 2026 9:20am | Jul 16, 2026 9:20am | Jul 16, 2026 10:02am | Jul 16, 2026 10:02am | Jul 16, 2026 10:42am | Jul 16, 2026 10:43am | Jul 16, 2026 10:46am | Jul 16, 2026 10:46am |  | Y | Fair | No | Replace a 25 KVA transformer fuse with a 3 amps at pole
Outage | J.E.26.07.18523 | C001856566 | Richard Samuda | Manchester | Completed | Load_244019 | Spur Tree - 310 | Jul 16, 2026 9:19am | Jul 16, 2026 9:19am | Jul 16, 2026 1:17pm | Jul 16, 2026 1:55pm | Jul 16, 2026 1:55pm | Jul 16, 2026 1:57pm | Jul 16, 2026 1:56pm | Jul 16, 2026 1:56pm | Fire |  | Fair | No | Premises not located and call to check no answer
Outage | J.E.26.07.18524 | C001856568 | Kenroy Dale | Manchester | Completed | Load_240193 | Porus - 310 | Jul 16, 2026 9:19am | Jul 16, 2026 9:20am | Jul 16, 2026 10:37am | Jul 16, 2026 10:37am | Jul 16, 2026 12:21pm | Jul 16, 2026 12:42pm | Jul 16, 2026 12:46pm | Jul 16, 2026 12:46pm |  |  | Fair | No | Corroded phase found at pole remade connection using 1 one bolt clamp voltage reading 110
Outage | J.E.26.07.18529 | C001856567 | Kenroy Dale | Manchester | Completed | Load_263509 | Kendal - 310 | Jul 16, 2026 9:19am | Jul 16, 2026 9:20am | Jul 16, 2026 12:44pm | Jul 16, 2026 12:46pm | Jul 16, 2026 2:10pm | Jul 16, 2026 2:55pm | Jul 16, 2026 2:59pm | Jul 16, 2026 2:59pm |  |  | Fair | No | Blown 3 amp transformer fuse found for 25 kva transformer line patrol illegal wires causing feed back, illegal wires were removed and blown fuse replaced. Area now with supply
Outage | J.E.26.07.18540 | C001856565 | Daniel Francis | St.Ann | Completed | Load_267879 | Roaring River - 210 | Jul 16, 2026 9:17am | Jul 16, 2026 9:19am | Jul 16, 2026 10:07am | Jul 16, 2026 10:07am | Jul 16, 2026 10:07am | Jul 16, 2026 10:34am | Jul 16, 2026 10:34am | Jul 16, 2026 10:34am |  |  | Fair | No | Found junction blown two 20amp also 3amp for transformer 50kva
Non-Outage | J.E.26.07.18494 | C001856563 | Daniel Francis | null | Completed | null | null | Jul 16, 2026 9:14am | Jul 16, 2026 9:15am | Jul 16, 2026 10:48am | Jul 16, 2026 10:48am | Jul 16, 2026 10:48am | Jul 16, 2026 10:49am | Jul 16, 2026 10:51am | Jul 16, 2026 10:51am | TreeContact |  | Fair | No | Tree on the line JPS is there now working
Outage | J.E.26.07.18233 | C001856562 | Roxroy Needham | St.Ann | Completed | Load_256517 | Cardiff Hall - 310 | Jul 16, 2026 9:14am | Jul 16, 2026 9:14am | Jul 16, 2026 10:46am | Jul 16, 2026 10:46am | Jul 16, 2026 11:57am | Jul 16, 2026 12:34pm | Jul 16, 2026 12:37pm | Jul 16, 2026 12:37pm |  | Y | Fair | No | Replace a 25 KVA transformer fuse with a 3 amps at pole
Non-Outage | J.E.26.07.18511 | C001856557 | Ricky Hall | St.Catherine | Completed | Load_256243 | Tredegar - 510 | Jul 16, 2026 9:10am | Jul 16, 2026 11:03am | Jul 16, 2026 11:25am | Jul 16, 2026 12:04pm | Jul 16, 2026 12:39pm | Jul 16, 2026 1:24pm | Jul 16, 2026 1:25pm | Jul 16, 2026 1:25pm | BangingWires |  | Fair | No | Retention banging secondary lines
Outage | J.E.26.07.18522 | C001856555 | Rusean Allen | KSAS | Completed | Load_258621 | Greenwich - 410 | Jul 16, 2026 9:05am | Jul 16, 2026 9:09am | Jul 17, 2026 9:44am | Jul 17, 2026 1:40pm | Jul 17, 2026 1:54pm | Jul 17, 2026 1:57pm | Jul 17, 2026 1:57pm | Jul 17, 2026 1:57pm |  |  | Fair | No | Meter defective need to change Refer to field service
Outage | J.E.26.07.18507 | C001856550 | Stephen Taylor | St.Thomas | Completed | Load_259573 | Good Year - 210 | Jul 16, 2026 9:00am | Jul 16, 2026 9:02am | Jul 16, 2026 12:58pm | Jul 16, 2026 12:58pm | Jul 16, 2026 12:58pm | Jul 16, 2026 12:58pm | Jul 16, 2026 12:59pm | Jul 16, 2026 12:59pm |  |  | Fair | No | Patrol the area power is in the area a lot of call to customer single customer no one answered the phone need more information
Outage | J.E.26.07.18509 | C001856544 | Rusean Allen | KSAS | Completed | Load_239591 | Cane River - 610 | Jul 16, 2026 8:56am | Jul 16, 2026 9:00am | Jul 16, 2026 10:10am | Jul 16, 2026 10:10am | Jul 16, 2026 11:05am | Jul 16, 2026 11:05am | Jul 16, 2026 11:06am | Jul 16, 2026 11:06am |  |  | Fair | No | Found a 20 amps fuse Replace a 20 amps fuse
Non-Outage | J.E.26.07.16333 | C001856540 | Moses Elliston | St.Catherine | Completed | Load_556367 | Rhodens Pen - 210 | Jul 16, 2026 8:54am | Jul 16, 2026 11:22am | Jul 16, 2026 1:31pm | Jul 16, 2026 1:31pm | Jul 16, 2026 1:50pm | Jul 16, 2026 2:08pm | Jul 16, 2026 2:14pm | Jul 16, 2026 2:14pm |  |  | Fair | No | Meter changed to # 1365328 due to burnt terminals 117-117-234 volts
Non-Outage | J.E.26.07.18489 | C001856535 | Andrae Dawkins | St.James | Completed | Load_252666 | Bogue - 510 | Jul 16, 2026 8:48am | Jul 16, 2026 8:49am | Jul 16, 2026 9:08am | Jul 16, 2026 10:23am | Jul 16, 2026 11:01am | Jul 16, 2026 11:14am | Jul 16, 2026 11:33am | Jul 16, 2026 11:33am |  |  | Fair | No | Found customer experiencing low voltage due to corrosion at pothead clean and remade joints voltage left 116/117/211 233/232/233
Non-Outage | J.E.26.07.18498 | C001856534 | Andrae Dawkins | St.James | Completed | Load_255960 | Bogue - 510 | Jul 16, 2026 8:48am | Jul 16, 2026 8:49am | Jul 16, 2026 9:08am | Jul 16, 2026 11:34am | Jul 16, 2026 11:34am | Jul 16, 2026 12:55pm | Jul 16, 2026 12:59pm | Jul 16, 2026 12:59pm |  |  | SevereWind | No | Found customer experiencing low voltage due to corrosion at pole and pothead clean and remade joints voltage found 103/112/215 voltage left 110/112/222
Non-Outage | J.E.26.07.18502 | C001856533 | Floyd Taylor | St.James | Completed | Load_244424 | Bogue - 310 | Jul 16, 2026 8:48am | Jul 16, 2026 3:25pm | Jul 16, 2026 4:32pm | Jul 16, 2026 4:32pm | Jul 16, 2026 5:43pm | Jul 16, 2026 5:59pm | Jul 16, 2026 6:00pm | Jul 16, 2026 6:00pm |  |  | Fair | No | Defective meter, meter needs to be replaced. Meter# 2649390
Outage | J.E.26.07.18508 | C001856537 | Donald Cunningham | St.Catherine | Completed | Load_244378 | Rhodens Pen - 410 | Jul 16, 2026 8:48am | Jul 16, 2026 8:49am | Jul 16, 2026 2:12pm | Jul 16, 2026 2:12pm | Jul 16, 2026 2:55pm | Jul 16, 2026 2:56pm | Jul 16, 2026 2:59pm | Jul 16, 2026 2:59pm |  |  | Fair | No | Premises found ok supply restored
Non-Outage | J.E.26.07.16488 | C001856532 | Moses Elliston | St.Catherine | Completed | Load_238151 | Twickenham - 310 | Jul 16, 2026 8:46am | Jul 16, 2026 8:53am | Jul 16, 2026 4:48pm | Jul 16, 2026 4:49pm | Jul 16, 2026 4:49pm | Jul 16, 2026 4:49pm | Jul 16, 2026 4:50pm | Jul 16, 2026 4:50pm |  |  | Fair | No | Not located,no answer from cell service
Non-Outage | J.E.26.07.17371 | C001856529 | Junior Scarlett | St.James | Completed | Load_294645 | Queens Drive - 710 | Jul 16, 2026 8:44am | Jul 16, 2026 8:45am | Jul 16, 2026 9:14am | Jul 16, 2026 3:32pm | Jul 16, 2026 3:44pm | Jul 16, 2026 3:48pm | Jul 16, 2026 3:59pm | Jul 16, 2026 3:59pm |  |  | Fair | No | Install one lampVoltage found 115v 115v 230vVoltage leave 115v 115v 230
Non-Outage | J.E.26.07.17601 | C001856528 | Junior Scarlett | St.James | Completed | Load_266792 | Queens Drive - 710 | Jul 16, 2026 8:43am | Jul 16, 2026 8:45am | Jul 16, 2026 9:14am | Jul 16, 2026 1:22pm | Jul 16, 2026 1:37pm | Jul 16, 2026 2:28pm | Jul 16, 2026 2:29pm | Jul 16, 2026 2:29pm |  |  | Fair | No | Check and found Voltage found 115v 114v 229
Non-Outage | J.E.26.07.17619 | C001856525 | Junior Scarlett | St.James | Completed | Load_260155 | Queens Drive - 710 | Jul 16, 2026 8:43am | Jul 16, 2026 8:45am | Jul 16, 2026 9:14am | Jul 16, 2026 3:23pm | Jul 16, 2026 3:30pm | Jul 16, 2026 3:31pm | Jul 16, 2026 3:31pm | Jul 16, 2026 3:31pm |  |  | Fair | No | Check and found okVoltage found 115v 114v 229vJob completed
Non-Outage | J.E.26.07.17864 | C001856523 | Junior Scarlett | St.James | Completed | Load_252784 | Queens Drive - 710 | Jul 16, 2026 8:43am | Jul 16, 2026 8:45am | Jul 16, 2026 9:14am | Jul 16, 2026 9:48am | Jul 16, 2026 10:36am | Jul 16, 2026 10:44am | Jul 16, 2026 10:45am | Jul 16, 2026 10:45am |  |  | Fair | No | Check and found okCustomer meter socket have inproper groundingVoltage found 115v 116v 231v
Non-Outage | J.E.26.07.18003 | C001856526 | Junior Scarlett | St.James | Completed | Load_247384 | Queens Drive - 710 | Jul 16, 2026 8:43am | Jul 16, 2026 8:45am | Jul 16, 2026 9:14am | Jul 16, 2026 2:47pm | Jul 16, 2026 2:56pm | Jul 16, 2026 3:19pm | Jul 16, 2026 3:23pm | Jul 16, 2026 3:23pm |  |  | Fair | No | Install on clampVoltage found 115v 115v 230Voltage leave 115v 115v 230v
Non-Outage | J.E.26.07.18013 | C001856524 | Junior Scarlett | St.James | Completed | Load_258521 | Queens Drive - 710 | Jul 16, 2026 8:43am | Jul 16, 2026 8:45am | Jul 16, 2026 9:14am | Jul 16, 2026 9:14am | Jul 16, 2026 9:46am | Jul 16, 2026 9:47am | Jul 16, 2026 9:48am | Jul 16, 2026 9:48am |  |  | Fair | No | Check and found okVoltage found 112v 110v 221v
Non-Outage | J.E.26.07.18478 | C001856522 | Horace Malcolm | null | Completed | null | null | Jul 16, 2026 8:41am | Jul 16, 2026 8:42am | Jul 16, 2026 9:16am | Jul 16, 2026 9:16am | Jul 16, 2026 9:47am | Jul 16, 2026 10:16am | Jul 16, 2026 10:16am | Jul 16, 2026 10:16am |  |  | Fair | No | Customer have meter issues rami meter referred to field service department
Outage | J.E.26.07.18492 | C001856521 | Shamour Haughton | St.James | Completed | Load_263685 | Bogue - 610 | Jul 16, 2026 8:40am | Jul 16, 2026 8:41am | Jul 16, 2026 8:45am | Jul 16, 2026 8:45am | Jul 16, 2026 9:36am | Jul 16, 2026 9:46am | Jul 16, 2026 10:03am | Jul 16, 2026 10:03am |  |  | Fair | No | Found customer meter socket defective and meter burn,meter needs changing
Outage | J.E.26.07.16187 | C001856514 | Rayon Foster | Hanover | Completed | Load_239373 | Orange Bay - 210 | Jul 16, 2026 8:35am | Jul 16, 2026 8:35am | Jul 16, 2026 9:18am | Jul 16, 2026 9:45am | Jul 16, 2026 10:13am | Jul 16, 2026 10:18am | Jul 16, 2026 10:19am | Jul 16, 2026 10:19am |  |  | Fair | No | Customer reporting a street light that has not being working since the hurricane refer to the street light team to do repairs
Outage | J.E.26.07.18481 | C001856512 | Moses Elliston | St.Catherine | Completed | Load_266264 | Twickenham - 310 | Jul 16, 2026 8:28am | Jul 16, 2026 8:29am | Jul 16, 2026 3:56pm | Jul 16, 2026 3:56pm | Jul 16, 2026 3:56pm | Jul 16, 2026 3:56pm | Jul 16, 2026 3:57pm | Jul 16, 2026 3:57pm |  |  | Fair | No | Customer add credit to prepaid account.
Non-Outage | J.E.26.07.17338 | C001856504 | Odaine Johnson | Clarendon | Completed | Load_295328 | Parnassus - 210 | Jul 16, 2026 8:23am | Jul 16, 2026 8:24am | Jul 16, 2026 9:19am | Jul 16, 2026 11:06am | Jul 16, 2026 12:59pm | Jul 16, 2026 1:00pm | Jul 16, 2026 1:01pm | Jul 16, 2026 1:01pm |  |  | Fair | No | Please refer this issue to a emergency team asap
Non-Outage | J.E.26.07.17533 | C001856505 | Odaine Johnson | Clarendon | Completed | Load_241257 | May Pen - 110 | Jul 16, 2026 8:23am | Jul 16, 2026 8:24am | Jul 16, 2026 9:19am | Jul 16, 2026 11:00am | Jul 16, 2026 11:05am | Jul 16, 2026 11:06am | Jul 16, 2026 11:06am | Jul 16, 2026 11:06am |  |  | Fair | No | This location is not in Clarendon
Non-Outage | J.E.26.07.17320 | C001856494 | Roemello Brown | Trelawny | Completed | Load_255841 | Martha Brae - 110 | Jul 16, 2026 8:11am | Jul 16, 2026 8:12am | Jul 16, 2026 10:37am | Jul 16, 2026 10:37am | Jul 16, 2026 10:48am | Jul 16, 2026 10:48am | Jul 16, 2026 10:56am | Jul 16, 2026 10:56am |  |  | Fair | No | Premises found working okay Voltage found 117/116/233Voltage leave 116/117/233
Non-Outage | J.E.26.07.17485 | C001856495 | Roemello Brown | Trelawny | Completed | Load_294510 | Martha Brae - 110 | Jul 16, 2026 8:11am | Jul 16, 2026 8:12am | Jul 16, 2026 10:50am | Jul 16, 2026 10:58am | Jul 16, 2026 11:39am | Jul 16, 2026 11:39am | Jul 16, 2026 11:40am | Jul 16, 2026 11:40am |  |  | Fair | No | Premises found working okay Voltage found 115/116/231Voltage leave 115/116/231
Non-Outage | J.E.26.07.17827 | C001856496 | Roemello Brown | Trelawny | Completed | Load_249410 | Greenwood - 210 | Jul 16, 2026 8:11am | Jul 16, 2026 8:12am | Jul 16, 2026 11:02am | Jul 16, 2026 11:40am | Jul 16, 2026 12:51pm | Jul 16, 2026 12:51pm | Jul 16, 2026 1:10pm | Jul 16, 2026 1:10pm |  |  | Fair | No | Premises found working okay problem not from jps side inform the customer to get an private electrician to have premises check Voltage found 108/110/218Voltage leave 108/110/218
Non-Outage | J.E.26.07.17899 | C001856497 | Roemello Brown | Trelawny | Completed | Load_245327 | Duncans - 210 | Jul 16, 2026 8:11am | Jul 16, 2026 8:12am | Jul 17, 2026 8:46am | Jul 17, 2026 8:46am | Jul 17, 2026 8:46am | Jul 17, 2026 8:46am | Jul 17, 2026 8:48am | Jul 17, 2026 8:48am |  |  | Fair | No | This call is for st.james team please transfer to them please
Non-Outage | J.E.26.07.17906 | C001856492 | Roemello Brown | Trelawny | Completed | Load_261243 | Greenwood - 110 | Jul 16, 2026 8:11am | Jul 16, 2026 8:12am | Jul 17, 2026 9:20am | Jul 17, 2026 12:01pm | Jul 17, 2026 12:52pm | Jul 17, 2026 12:52pm | Jul 17, 2026 12:55pm | Jul 17, 2026 12:55pm |  |  | Fair | No | Customer needs to update proper directions an landmark also phone number provided went straight to voicemail
Non-Outage | J.E.26.07.18056 | C001856493 | Roemello Brown | Trelawny | Completed | Load_244909 | Greenwood - 110 | Jul 16, 2026 8:11am | Jul 16, 2026 8:12am | Jul 17, 2026 8:45am | Jul 17, 2026 10:11am | Jul 17, 2026 11:55am | Jul 17, 2026 11:55am | Jul 17, 2026 12:01pm | Jul 17, 2026 12:01pm |  |  | Fair | No | Premises found working okay however secondary lines banging up together please send emergency team to tension secondary please Voltage found 114/114/227Voltage leave 114/113/227
Non-Outage | J.E.26.07.18126 | C001856491 | Roemello Brown | Trelawny | Completed | Load_292751 | Greenwood - 210 | Jul 16, 2026 8:10am | Jul 16, 2026 8:12am | Jul 16, 2026 10:52am | Jul 16, 2026 1:11pm | Jul 16, 2026 1:20pm | Jul 16, 2026 1:21pm | Jul 16, 2026 3:08pm | Jul 16, 2026 3:08pm |  |  | Fair | No | Corrosion at the pole and at the pothead install clamps at the pole side and linkets at pothead Voltage found 111/30.29/141Voltage leave 112/116/228
Non-Outage | J.E.26.07.18193 | C001856490 | Roemello Brown | Trelawny | Completed | Load_246819 | Duncans - 210 | Jul 16, 2026 8:10am | Jul 16, 2026 8:12am | Jul 16, 2026 9:49am | Jul 16, 2026 9:49am | Jul 16, 2026 9:49am | Jul 16, 2026 9:55am | Jul 16, 2026 10:19am | Jul 16, 2026 10:19am |  |  | Fair | No | Premises found working okay Voltage found 114/116/230Voltage leave 114/116/230
Outage | J.E.26.07.17452 | C001856488 | Cliton Henry | St.Mary | Completed | Load_262786 | Blackstonedge - 110 | Jul 16, 2026 8:08am | Jul 16, 2026 8:09am | Jul 16, 2026 12:19pm | Jul 16, 2026 12:20pm | Jul 16, 2026 12:20pm | Jul 16, 2026 12:21pm | Jul 16, 2026 12:22pm | Jul 16, 2026 12:22pm | BrokenWire |  | Fair | No | A NWC personnel confirmed that the pump is up and running satisfactory
Outage | J.E.26.07.18038 | C001856489 | Michael Christian | St.James | Completed | Load_1002045 | Queens Drive - 710 | Jul 16, 2026 8:08am | Jul 16, 2026 8:08am | Jul 16, 2026 8:31am | Jul 16, 2026 8:31am | Jul 16, 2026 8:42am | Jul 16, 2026 8:47am | Jul 16, 2026 8:47am | Jul 16, 2026 8:47am |  |  | Fair | No | Check and found okay voltage 111 110 221 at meter
Outage | J.E.26.07.17886 | C001856486 | Horace Malcolm | St.James | Completed | Load_575863 | Bogue - 410 | Jul 16, 2026 8:07am | Jul 16, 2026 8:07am | Jul 16, 2026 8:28am | Jul 16, 2026 8:28am | Jul 16, 2026 8:30am | Jul 16, 2026 8:30am | Jul 16, 2026 8:30am | Jul 16, 2026 8:30am |  |  | Fair | No
Outage | J.E.26.07.17304 | C001856483 | Milton Charlton | KSAN | Completed | Load_255998 | Washington Blvd - 610 | Jul 16, 2026 8:06am | Jul 16, 2026 8:06am | Jul 16, 2026 11:43am | Jul 16, 2026 11:43am | Jul 16, 2026 12:17pm | Jul 16, 2026 12:15pm | Jul 16, 2026 12:21pm | Jul 16, 2026 12:21pm |  |  | Fair | No | Found okay upon arrival. Customer did not made a report.
Outage | J.E.26.07.18461 | C001856485 | Dwayne Samuels | St.James | Completed | Load_244424 | Bogue - 310 | Jul 16, 2026 8:06am | Jul 16, 2026 8:18am | Jul 16, 2026 8:23am | Jul 16, 2026 8:45am | Jul 16, 2026 8:45am | Jul 16, 2026 8:58am | Jul 16, 2026 8:58am | Jul 16, 2026 8:58am |  |  | Fair | No | Defective meter refer to field service voltage is 118v 118v 236v
Outage | J.E.26.07.17916 | C001856482 | Michael Christian | St.James | Completed | Load_257829 | Bogue - 610 | Jul 16, 2026 8:05am | Jul 16, 2026 8:26am | Jul 16, 2026 10:40am | Jul 16, 2026 10:40am | Jul 16, 2026 11:34am | Jul 16, 2026 11:51am | Jul 16, 2026 11:52am | Jul 16, 2026 11:52am |  |  | Fair | No | Use 1 clamp at customer service wire at pole voltage 112 110 223 at pothead
Outage | J.E.26.07.18341 | C001856481 | Horace Malcolm | St.James | Completed | Load_244963 | Bogue - 310 | Jul 16, 2026 8:05am | Jul 16, 2026 8:08am | Jul 16, 2026 8:23am | Jul 16, 2026 8:23am | Jul 16, 2026 8:23am | Jul 16, 2026 8:26am | Jul 16, 2026 8:27am | Jul 16, 2026 8:27am |  |  | Fair | No | Unable to locate customer or premises no directions given
Non-Outage | J.E.26.07.15400 | C001856479 | Oraine Minto | St.Ann | Completed | Load_244118 | Cardiff Hall - 310 | Jul 16, 2026 8:04am | Jul 16, 2026 8:05am | Jul 16, 2026 3:45pm | Jul 16, 2026 5:00pm | Jul 16, 2026 5:21pm | Jul 16, 2026 5:21pm | Jul 16, 2026 5:26pm | Jul 16, 2026 5:26pm |  |  | Fair | No | Refer to emergency Secondary neural burst above 3 times and customers are getting a floating neural Issue affecting 6 customers
Non-Outage | J.E.26.07.15419 | C001856478 | Oraine Minto | St.Ann | Completed | Load_252162 | Cardiff Hall - 310 | Jul 16, 2026 8:04am | Jul 16, 2026 8:05am | Jul 16, 2026 10:18am | Jul 16, 2026 10:18am | Jul 16, 2026 12:20pm | Jul 16, 2026 12:20pm | Jul 16, 2026 12:23pm | Jul 16, 2026 12:23pm |  |  | Fair | No | Refer to maintenance Customer is about 600 meters away from transformer an the voltage phase to phase is 218v 107v 111v Transformer need to turn up
Non-Outage | J.E.26.07.15924 | C001856477 | Oraine Minto | St.Ann | Completed | Load_269661 | Cardiff Hall - 310 | Jul 16, 2026 8:04am | Jul 16, 2026 8:05am | Jul 16, 2026 1:26pm | Jul 16, 2026 1:27pm | Jul 16, 2026 1:27pm | Jul 16, 2026 1:27pm | Jul 16, 2026 1:27pm | Jul 16, 2026 1:27pm |  |  | Fair | No | Issue resolved
Non-Outage | J.E.26.07.17007 | C001856476 | Oraine Minto | St.Ann | Completed | Load_304996 | Cardiff Hall - 310 | Jul 16, 2026 8:04am | Jul 16, 2026 8:05am | Jul 16, 2026 3:50pm | Jul 16, 2026 4:57pm | Jul 16, 2026 4:57pm | Jul 16, 2026 4:58pm | Jul 16, 2026 4:59pm | Jul 16, 2026 4:59pm |  |  | Fair | No | Issue fix Pole reconnection
Non-Outage | J.E.26.07.17282 | C001856475 | Oraine Minto | St.Ann | Completed | Load_262673 | Cardiff Hall - 310 | Jul 16, 2026 8:04am | Jul 16, 2026 8:05am | Jul 16, 2026 12:28pm | Jul 16, 2026 12:28pm | Jul 16, 2026 12:28pm | Jul 16, 2026 12:35pm | Jul 16, 2026 12:35pm | Jul 16, 2026 12:35pm |  |  | Fair | No | Refer to emergency Customer states that entire area is affected for 3 months now
Non-Outage | J.E.26.07.18305 | C001856473 | Oraine Minto | St.Ann | Completed | Load_252427 | Cardiff Hall - 310 | Jul 16, 2026 8:04am | Jul 16, 2026 8:05am | Jul 16, 2026 1:49pm | Jul 16, 2026 1:49pm | Jul 16, 2026 3:41pm | Jul 16, 2026 3:42pm | Jul 16, 2026 3:42pm | Jul 16, 2026 3:42pm |  |  | Fair | No | Issue resolved
Outage | J.E.26.07.18470 | C001856472 | Michael Christian | St.James | Completed | Load_245262 | Queens Drive - 710 | Jul 16, 2026 8:04am | Jul 16, 2026 8:04am | Jul 16, 2026 8:47am | Jul 16, 2026 8:47am | Jul 16, 2026 9:07am | Jul 16, 2026 9:14am | Jul 16, 2026 9:14am | Jul 16, 2026 9:14am |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.07.17502 | C001856467 | Royston Montague | St.Catherine | Completed | Load_263836 | Tredegar - 310 | Jul 16, 2026 8:03am | Jul 16, 2026 8:23am | Jul 16, 2026 8:27am | Jul 17, 2026 11:20am | Jul 17, 2026 11:32am | Jul 17, 2026 11:59am | Jul 17, 2026 11:59am | Jul 17, 2026 11:59am |  |  | Fair | No | Slack connection at pothead, same corrected. Voltage 232v 115v 116v
Outage | J.E.26.07.17965 | C001856468 | Michael Christian | St.James | Completed | Load_574038 | Queens Drive - 710 | Jul 16, 2026 8:03am | Jul 16, 2026 8:04am | Jul 16, 2026 11:52am | Jul 16, 2026 11:52am | Jul 16, 2026 12:44pm | Jul 16, 2026 12:52pm | Jul 16, 2026 12:52pm | Jul 16, 2026 12:52pm |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.18010 | C001856469 | Swon Miller | St.James | Completed | Load_247836 | Queens Drive - 710 | Jul 16, 2026 8:03am | Jul 16, 2026 3:38pm | Jul 16, 2026 7:58pm | Jul 16, 2026 7:58pm | Jul 16, 2026 8:45pm | Jul 21, 2026 8:50am | Jul 16, 2026 8:54pm | Jul 16, 2026 8:54pm |  |  | Fair | No | Check and found area okay voltage found 115/115/231 customer states that power supply was restored voltage left 115/115/231
Outage | J.E.26.07.18032 | C001856470 | Michael Christian | St.James | Completed | Load_239613 | Queens Drive - 710 | Jul 16, 2026 8:03am | Jul 16, 2026 8:04am | Jul 16, 2026 9:15am | Jul 16, 2026 9:15am | Jul 16, 2026 9:16am | Jul 16, 2026 10:17am | Jul 16, 2026 10:17am | Jul 16, 2026 10:17am |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.18066 | C001856471 | Michael Christian | St.James | Completed | Load_260155 | Queens Drive - 710 | Jul 16, 2026 8:03am | Jul 16, 2026 8:04am | Jul 16, 2026 10:17am | Jul 16, 2026 10:17am | Jul 16, 2026 10:38am | Jul 16, 2026 10:39am | Jul 16, 2026 10:39am | Jul 16, 2026 10:39am |  |  | Fair | No | Check and found okay voltage 112 110 223 at meter
Non-Outage | J.E.26.07.08535 | C001856456 | Milton Charlton | KSAN | Completed | Load_257150 | West Kings House - 210 | Jul 16, 2026 7:59am | Jul 16, 2026 7:59am | Jul 16, 2026 9:51am | Jul 16, 2026 9:51am | Jul 16, 2026 10:45am | Jul 16, 2026 10:40am | Jul 16, 2026 10:46am | Jul 16, 2026 10:46am |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Non-Outage | J.E.26.07.17156 | C001856454 | Milton Charlton | KSAN | Completed | Load_246866 | West Kings House - 310 | Jul 16, 2026 7:56am | Jul 16, 2026 7:56am | Jul 16, 2026 9:45am | Jul 16, 2026 9:46am | Jul 16, 2026 9:47am | Jul 16, 2026 9:47am | Jul 16, 2026 9:49am | Jul 16, 2026 9:49am |  |  | Fair | No | Call belongs to Mandeville District Manchester.
Non-Outage | J.E.26.07.17814 | C001856455 | Rochaine Hussey | KSAN | Completed | Load_567618 | Constant Spring - 310 | Jul 16, 2026 7:56am | Jul 16, 2026 7:56am | Jul 16, 2026 10:42am | Jul 16, 2026 10:42am | Jul 16, 2026 10:58am | Jul 16, 2026 10:58am | Jul 16, 2026 10:59am | Jul 16, 2026 10:59am |  |  | Fair | No | Customer was called multiple times no answer Unable to locate premises
Non-Outage | J.E.26.07.17903 | C001856453 | Dean Smith | null | Completed | null | null | Jul 16, 2026 7:55am | Jul 16, 2026 7:58am | Jul 16, 2026 8:40am | Jul 16, 2026 8:41am | Jul 16, 2026 9:51am | Jul 16, 2026 9:51am | Jul 16, 2026 10:49am | Jul 16, 2026 10:49am |  |  | Fair | No | Broken/leaning 30/6 pole , resulting banging and low hanging secondary conductors, direction; left turn at stand pipe in Egypt. Maintenance work is also needed in the area , please forward to maintenance dept to have area assess and plan work accordingly.Pole was temporarily guy to a tree and banging secondary conductors where corrected, replace 2amp transformer fuse.
Non-Outage | J.E.26.07.18188 | C001856450 | Dean Smith | null | Completed | null | null | Jul 16, 2026 7:51am | Jul 16, 2026 7:58am | Jul 16, 2026 12:12pm | Jul 16, 2026 12:12pm | Jul 16, 2026 1:46pm | Jul 16, 2026 1:46pm | Jul 16, 2026 1:47pm | Jul 16, 2026 1:47pm | Fire |  | Fair | No | Unable to locate
Outage | J.E.26.07.17833 | C001856444 | Nickolas Rodriques | Portmore | Completed | Load_255889 | Naggo Head - 610 | Jul 16, 2026 7:51am | Jul 16, 2026 7:51am | Jul 16, 2026 11:39am | Jul 16, 2026 11:39am | Jul 16, 2026 11:40am | Jul 16, 2026 11:42am | Jul 16, 2026 11:43am | Jul 16, 2026 11:43am |  |  | Fair | No | Power restored. Call relates to the 10 KVA transformer that was tripped.
Outage | J.E.26.07.18206 | C001856451 | Nickolas Rodriques | Portmore | Completed | Load_556172 | Naggo Head - 610 | Jul 16, 2026 7:51am | Jul 16, 2026 7:52am | Jul 16, 2026 7:46pm | Jul 16, 2026 9:03pm | Jul 16, 2026 9:26pm | Jul 16, 2026 9:28pm | Jul 16, 2026 9:31pm | Jul 16, 2026 9:31pm |  |  | Fair | No | Unable to communicate with the customer in order to gain access to the gated community. (Area has electricity)
Outage | J.E.26.07.18220 | C001856445 | Dean Smith | Hanover | Completed | Load_244774 | Orange Bay - 310 | Jul 16, 2026 7:51am | Jul 16, 2026 7:58am | Jul 16, 2026 10:51am | Jul 16, 2026 10:51am | Jul 16, 2026 11:32am | Jul 16, 2026 11:32am | Jul 16, 2026 12:04pm | Jul 16, 2026 12:04pm |  |  | Fair | No | Clear creeper from primary conductor, replace 10amp junction fuse. Pole number n/a.
Outage | J.E.26.07.18236 | C001856448 | Nickolas Rodriques | Portmore | Completed | Load_255889 | Naggo Head - 610 | Jul 16, 2026 7:51am | Jul 16, 2026 7:51am | Jul 16, 2026 6:18pm | Jul 16, 2026 6:18pm | Jul 16, 2026 6:45pm | Jul 16, 2026 6:49pm | Jul 16, 2026 6:53pm | Jul 16, 2026 6:53pm |  |  | Fair | No | Found customer with electricity. Call relates to the 10 KVA transformer that was tripped earlier today.
Outage | J.E.26.07.18355 | C001856446 | Nickolas Rodriques | Portmore | Completed | Load_570289 | Naggo Head - 510 | Jul 16, 2026 7:51am | Jul 16, 2026 7:51am | Jul 16, 2026 9:45am | Jul 16, 2026 9:47am | Jul 16, 2026 9:47am | Jul 16, 2026 9:54am | Jul 16, 2026 9:55am | Jul 16, 2026 9:55am |  |  | Fair | No | Power restored. Call relates to the junction fuses that was replaced.
Outage | J.E.26.07.18356 | C001856447 | Nickolas Rodriques | Portmore | Completed | Load_266551 | Naggo Head - 510 | Jul 16, 2026 7:51am | Jul 16, 2026 7:51am | Jul 16, 2026 8:29am | Jul 16, 2026 8:29am | Jul 16, 2026 8:59am | Jul 16, 2026 9:39am | Jul 16, 2026 9:45am | Jul 16, 2026 9:45am |  |  | Fair | No | Checked and found two junction fuses blown from same phase a (30 amp and a 25 amp). Patrol and found nothing on line. Repaired by replacing the fuses after completing patrol.
Outage | J.E.26.07.18420 | C001856449 | Moses Elliston | Portmore | Completed | Load_570198 | Naggo Head - 610 | Jul 16, 2026 7:51am | Jul 16, 2026 10:26am | Jul 16, 2026 3:35pm | Jul 16, 2026 3:35pm | Jul 16, 2026 3:35pm | Jul 16, 2026 3:35pm | Jul 16, 2026 3:36pm | Jul 16, 2026 3:36pm |  |  | Fair | No | Supply ok .Outage was in area
Outage | J.E.26.07.18224 | C001856443 | Cliton Henry | St.Mary | Completed | Load_251110 | Oracabessa - 110 | Jul 16, 2026 7:50am | Jul 16, 2026 7:50am | Jul 16, 2026 10:46am | Jul 16, 2026 10:46am | Jul 16, 2026 10:46am | Jul 16, 2026 10:47am | Jul 16, 2026 10:48am | Jul 16, 2026 10:48am |  |  | Fair | No | Supply restored, related outage #16218
Outage | J.E.26.07.18431 | C001856442 | Cliton Henry | St.Mary | Completed | Load_269033 | Oracabessa - 210 | Jul 16, 2026 7:50am | Jul 16, 2026 7:50am | Jul 16, 2026 9:46am | Jul 16, 2026 9:46am | Jul 16, 2026 9:46am | Jul 16, 2026 9:46am | Jul 16, 2026 9:46am | Jul 16, 2026 9:46am |  |  | Fair | No | The supply found ok
Outage | J.E.26.07.18218 | C001856439 | Cliton Henry | St.Mary | Completed | Load_247017 | Oracabessa - 110 | Jul 16, 2026 7:48am | Jul 16, 2026 7:48am | Jul 16, 2026 9:47am | Jul 16, 2026 9:47am | Jul 16, 2026 10:23am | Jul 16, 2026 10:40am | Jul 16, 2026 10:46am | Jul 16, 2026 10:46am |  |  | Fair | No | A blown 2 amp fuse found for a 25 kva transformer at pole #0013363. Supply restored using 1-2 amp fuse.
Outage | J.E.26.07.18201 | C001856438 | Neckell Ormsby | St.Mary | Completed | Load_341063 | Highgate -110 | Jul 16, 2026 7:47am | Jul 16, 2026 7:47am | Jul 16, 2026 8:05am | Jul 16, 2026 8:05am | Jul 16, 2026 9:33am | Jul 16, 2026 9:49am | Jul 16, 2026 9:49am | Jul 16, 2026 9:49am |  |  | Fair | No | Unable to locate customer after several calls however was told by other customers that supply went yesterday and came back
Non-Outage | J.E.26.07.18229 | C001856435 | Andre Williams | null | Completed | null | null | Jul 16, 2026 7:43am | Jul 16, 2026 7:46am | Jul 16, 2026 8:13am | Jul 16, 2026 8:13am | Jul 16, 2026 9:26am | Jul 16, 2026 10:26am | Jul 16, 2026 10:27am | Jul 16, 2026 10:27am |  |  | Fair | No | Open 50 kva transformer retention low hanging phase that was touching, remake burnt off neutral at transformer pole
Non-Outage | J.E.26.07.18284 | C001856436 | Andre Williams | null | Completed | null | null | Jul 16, 2026 7:43am | Jul 16, 2026 7:46am | Jul 16, 2026 10:28am | Jul 16, 2026 10:28am | Jul 16, 2026 10:28am | Jul 16, 2026 10:28am | Jul 16, 2026 10:29am | Jul 16, 2026 10:29am | Fire |  | Fair | No | Completed under job #18229
Non-Outage | J.E.26.07.12703 | C001856434 | Moses Elliston | St.Catherine | Completed | Load_290839 | Rhodens Pen - 210 | Jul 16, 2026 7:42am | Jul 16, 2026 7:43am | Jul 16, 2026 11:55am | Jul 16, 2026 11:55am | Jul 16, 2026 11:55am | Jul 16, 2026 1:01pm | Jul 16, 2026 1:04pm | Jul 16, 2026 1:04pm |  |  | Fair | No | 180’ # 6 defective triplex changed With 2. clamps,3 linkets 117-117-234 volts
Outage | J.E.26.07.18069 | C001856432 | Rusean Allen | KSAS | Completed | Load_246603 | Cane River - 610 | Jul 16, 2026 7:40am | Jul 16, 2026 10:40am | Jul 16, 2026 11:15am | Jul 16, 2026 11:15am | Jul 16, 2026 11:32am | Jul 16, 2026 11:34am | Jul 16, 2026 11:34am | Jul 16, 2026 11:34am |  |  | Fair | No | Found 2 20 amps fuse ReplaceReplace 2 20 amps fuse
Outage | J.E.26.07.18089 | C001856430 | Rusean Allen | KSAS | Completed | Load_245309 | Hunts Bay - 310 | Jul 16, 2026 7:40am | Jul 17, 2026 8:08am | Jul 17, 2026 1:57pm | Jul 17, 2026 1:57pm | Jul 17, 2026 1:57pm | Jul 17, 2026 2:09pm | Jul 17, 2026 2:10pm | Jul 17, 2026 2:10pm |  |  | Fair | No | Reconnected wire at pole Use 2 1bolt clamps
Non-Outage | J.E.26.07.13654 | C001856426 | Dwain Samuels | Hanover | Completed | Load_247476 | Orange Bay - 310 | Jul 16, 2026 7:39am | Jul 16, 2026 7:39am | Jul 16, 2026 8:10am | Jul 16, 2026 11:25am | Jul 16, 2026 11:40am | Jul 16, 2026 11:56am | Jul 16, 2026 11:58am | Jul 16, 2026 11:58am |  |  | Fair | No | Corrosion found at 3 wire pole. Voltage check 105-101-206. Corrosion clear use 2 one bolt clamp. Voltage check 125-116-231
Non-Outage | J.E.26.07.17959 | C001856424 | Dwain Samuels | Westmoreland | Completed | Load_241436 | Paradise - 310 | Jul 16, 2026 7:39am | Jul 16, 2026 7:39am | Jul 16, 2026 8:10am | Jul 16, 2026 12:45pm | Jul 16, 2026 12:56pm | Jul 16, 2026 1:06pm | Jul 16, 2026 1:07pm | Jul 16, 2026 1:07pm |  |  | Fair | No | Area affected by low voltage due to irregularities on the line
Non-Outage | J.E.26.07.18210 | C001856425 | Dwain Samuels | Westmoreland | Completed | Load_242418 | Paradise - 110 | Jul 16, 2026 7:39am | Jul 16, 2026 7:39am | Jul 16, 2026 8:10am | Jul 16, 2026 10:29am | Jul 16, 2026 11:09am | Jul 16, 2026 11:16am | Jul 16, 2026 11:17am | Jul 16, 2026 11:17am |  |  | Fair | No | Corrosion found at 3 wire pole. Corrosion clear use 3 one bolt clamp. Voltage check 114-114-228
Non-Outage | J.E.26.07.12061 | C001856422 | Donald Cunningham | St.Catherine | Completed | Load_252633 | Rhodens Pen - 310 | Jul 16, 2026 7:38am | Jul 16, 2026 7:39am | Jul 16, 2026 7:56am | Jul 16, 2026 8:50am | Jul 16, 2026 9:56am | Jul 16, 2026 10:19am | Jul 16, 2026 10:21am | Jul 16, 2026 10:21am |  |  | Fair | No | Blown junction to sports club replace 8 amp fuse voltage readings 120/2/240
Non-Outage | J.E.26.07.18259 | C001856423 | Dwain Samuels | Westmoreland | Completed | Load_242418 | Paradise - 110 | Jul 16, 2026 7:38am | Jul 16, 2026 7:39am | Jul 16, 2026 8:10am | Jul 16, 2026 11:21am | Jul 16, 2026 11:21am | Jul 16, 2026 11:22am | Jul 16, 2026 11:24am | Jul 16, 2026 11:24am |  |  | Fair | No | Corrosion found at 3 wire pole. Corrosion clear use 2 one bolt clamp. Voltage check 114-113-227
Outage | J.E.26.07.18457 | C001856421 | Ricky Hall | St.Catherine | Completed | Load_254672 | New Michelton - 210 | Jul 16, 2026 7:38am | Jul 16, 2026 7:40am | Jul 16, 2026 9:45am | Jul 16, 2026 9:51am | Jul 16, 2026 10:34am | Jul 16, 2026 10:34am | Jul 16, 2026 10:36am | Jul 16, 2026 10:36am | LowHangingWires |  | Fair | No | All Jps particular have already been transferred leaving cable wires customer advised
Non-Outage | J.E.26.07.11425 | C001856420 | Royston Montague | St.Catherine | Completed | Load_251630 | Rhodens Pen - 410 | Jul 16, 2026 7:37am | Jul 16, 2026 7:39am | Jul 16, 2026 8:16am | Jul 17, 2026 9:01am | Jul 17, 2026 9:36am | Jul 17, 2026 9:36am | Jul 17, 2026 9:37am | Jul 17, 2026 9:37am |  |  | Fair | No | Customer confirmed issue resolved.
Outage | J.E.26.07.17090 | C001856418 | Kaydon Taylor | KSAN | Completed | Load_255038 | Constant Spring - 410 | Jul 16, 2026 7:36am | Jul 16, 2026 3:06pm | Jul 16, 2026 5:07pm | Jul 16, 2026 6:03pm | Jul 16, 2026 6:39pm | Jul 16, 2026 9:00pm | Jul 16, 2026 9:00pm | Jul 16, 2026 9:00pm | BrokenWire |  | Fair | No | String 150’ of #2 triplex 6 clamps used
Non-Outage | J.E.26.07.14397 | C001856417 | Donald Cunningham | St.Catherine | Completed | Load_241272 | Rhodens Pen - 410 | Jul 16, 2026 7:35am | Jul 16, 2026 7:37am | Jul 16, 2026 4:34pm | Jul 16, 2026 4:34pm | Jul 16, 2026 5:37pm | Jul 16, 2026 5:38pm | Jul 16, 2026 5:40pm | Jul 16, 2026 5:40pm |  |  | Fair | No | Call is for the linstead crew no cell site at snake hill
Non-Outage | J.E.26.07.17975 | C001856414 | Donald Cunningham | St.Catherine | Completed | Load_290839 | Rhodens Pen - 210 | Jul 16, 2026 7:35am | Jul 16, 2026 7:37am | Jul 16, 2026 10:22am | Jul 16, 2026 10:22am | Jul 16, 2026 11:09am | Jul 16, 2026 11:13am | Jul 16, 2026 11:18am | Jul 16, 2026 11:18am |  |  | Fair | No | Premises found close
Outage | J.E.26.07.18442 | C001856415 | Barnett Brown | Manchester | Completed | Load_247253 | Kendal - 210 | Jul 16, 2026 7:35am | Jul 16, 2026 7:35am | Jul 16, 2026 7:48am | Jul 16, 2026 7:48am | Jul 16, 2026 10:46am | Jul 16, 2026 11:13am | Jul 16, 2026 11:14am | Jul 16, 2026 11:14am |  |  | Fair | No | Patrol line, found nothing, replace blown 10 and 15 amp junction fuse
Non-Outage | J.E.26.07.17360 | C001856413 | Donald Cunningham | St.Catherine | Completed | Load_240139 | Rhodens Pen - 310 | Jul 16, 2026 7:33am | Jul 16, 2026 7:34am | Jul 16, 2026 12:20pm | Jul 16, 2026 12:20pm | Jul 16, 2026 12:54pm | Jul 16, 2026 12:54pm | Jul 16, 2026 12:56pm | Jul 16, 2026 12:56pm | Fire |  | Fair | No | Premises not located
Non-Outage | J.E.26.07.15108 | C001856412 | Ricky Hall | St.Catherine | Completed | Load_238712 | Tredegar - 510 | Jul 16, 2026 7:29am | Jul 16, 2026 7:30am | Jul 16, 2026 9:16am | Jul 16, 2026 9:16am | Jul 16, 2026 9:44am | Jul 16, 2026 9:45am | Jul 16, 2026 9:45am | Jul 16, 2026 9:45am | Fire |  | Fair | No | Issue was resolved on previous shift
Outage | J.E.26.07.18351 | C001856410 | Richard Samuda | Manchester | Completed | Load_573440 | Spur Tree - 310 | Jul 16, 2026 7:28am | Jul 16, 2026 7:34am | Jul 16, 2026 9:19am | Jul 16, 2026 9:19am | Jul 16, 2026 9:45am | Jul 16, 2026 10:13am | Jul 16, 2026 10:14am | Jul 16, 2026 10:14am |  |  | Fair | No | Found 25 amps junction fuse blown patrol line found nothing replaced fuse close line customer back to normal
Outage | J.E.26.07.18352 | C001856409 | Richard Samuda | Manchester | Completed | Load_295434 | Spur Tree - 310 | Jul 16, 2026 7:28am | Jul 16, 2026 7:34am | Jul 16, 2026 2:02pm | Jul 16, 2026 2:02pm | Jul 16, 2026 2:15pm | Jul 16, 2026 2:15pm | Jul 16, 2026 2:16pm | Jul 16, 2026 2:16pm |  |  | Fair | No | Customer say he didn’t make a call
Outage | J.E.26.07.18400 | C001856407 | Richard Samuda | Manchester | Completed | Load_249942 | Spur Tree - 310 | Jul 16, 2026 7:28am | Jul 16, 2026 7:34am | Jul 16, 2026 1:57pm | Jul 16, 2026 1:57pm | Jul 16, 2026 2:01pm | Jul 16, 2026 2:02pm | Jul 16, 2026 2:02pm | Jul 16, 2026 2:02pm |  |  | Fair | No | Customer back to normal
Outage | J.E.26.07.18235 | C001856406 | Milton Charlton | KSAN | Completed | Load_263440 | Hope - 510 | Jul 16, 2026 7:27am | Jul 16, 2026 7:55am | Jul 16, 2026 10:51am | Jul 16, 2026 10:51am | Jul 16, 2026 11:40am | Jul 16, 2026 11:35am | Jul 16, 2026 11:43am | Jul 16, 2026 11:43am |  |  | Fair | No | Found okay upon arrival. Customer has an internal problem. Readings at meter socket 115-117-232 volts.
Outage | J.E.26.07.18410 | C001856405 | Elvis Trowers | KSAN | Completed | Load_244306 | Washington Blvd - 510 | Jul 16, 2026 7:27am | Jul 16, 2026 8:05am | Jul 16, 2026 10:21am | Jul 16, 2026 10:21am | Jul 16, 2026 10:45am | Jul 16, 2026 10:57am | Jul 16, 2026 10:57am | Jul 16, 2026 10:57am |  |  | Fair | Yes | Premises checked and found ok customer was also spoken with, however he suggested that the power supply was restored.
Non-Outage | J.E.26.07.18232 | C001856404 | Ricky Hall | St.Catherine | Completed | Load_241538 | Twickenham - 310 | Jul 16, 2026 7:26am | Jul 16, 2026 7:32am | Jul 16, 2026 5:57pm | Jul 16, 2026 5:57pm | Jul 16, 2026 6:11pm | Jul 16, 2026 6:11pm | Jul 16, 2026 6:12pm | Jul 16, 2026 6:12pm | LeakingTransformer |  | Fair | No | Premises not located
Outage | J.E.26.07.18353 | C001856403 | Kemark Slue | St.Catherine | Completed | Load_413079 | New Michelton - 210 | Jul 16, 2026 7:25am | Jul 16, 2026 7:26am | Jul 16, 2026 7:33am | Jul 16, 2026 7:33am | Jul 16, 2026 8:57am | Jul 16, 2026 8:10am | Jul 16, 2026 9:23am | Jul 16, 2026 9:23am |  |  | Fair | No | Upon arrival at the location the crew discovered that the premises electricity had been restored.
Outage | J.E.26.07.18412 | C001856402 | Ricky Hall | St.Catherine | Completed | Load_266216 | New Michelton - 210 | Jul 16, 2026 7:25am | Jul 16, 2026 7:26am | Jul 16, 2026 9:47am | Jul 16, 2026 10:59am | Jul 16, 2026 10:59am | Jul 16, 2026 10:59am | Jul 16, 2026 11:00am | Jul 16, 2026 11:00am |  |  | Fair | No | Call associated with outage #18264
Non-Outage | J.E.26.07.18168 | C001856398 | Christopher Edwards | null | Completed | null | null | Jul 16, 2026 7:24am | Jul 16, 2026 7:29am | Jul 16, 2026 4:10pm | Jul 16, 2026 4:10pm | Jul 16, 2026 4:10pm | Jul 16, 2026 4:12pm | Jul 16, 2026 4:13pm | Jul 16, 2026 4:13pm |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Outage | J.E.26.07.16985 | C001856397 | Christopher Edwards | KSAN | Completed | Load_244363 | Constant Spring - 210 | Jul 16, 2026 7:24am | Jul 16, 2026 7:32am | Jul 16, 2026 7:59am | Jul 16, 2026 10:14am | Jul 16, 2026 10:29am | Jul 16, 2026 11:41am | Jul 16, 2026 11:43am | Jul 16, 2026 11:43am |  |  | Fair | No | Isolate 50 kva transformer To bypass defective breaker in meter center Supply is now at the premises
Outage | J.E.26.07.17005 | C001856401 | Christopher Edwards | KSAN | Completed | Load_264959 | Constant Spring - 410 | Jul 16, 2026 7:24am | Jul 16, 2026 7:29am | Jul 16, 2026 2:32pm | Jul 16, 2026 2:32pm | Jul 16, 2026 2:32pm | Jul 16, 2026 3:11pm | Jul 16, 2026 3:13pm | Jul 16, 2026 3:13pm |  |  | Fair | No | Customer pothead is damaged and needs to be rectify Customer was advised to get electrician to rectify issue
Outage | J.E.26.07.17936 | C001856394 | Stephen Taylor | St.Thomas | Completed | Load_264218 | Lysson - 410 | Jul 16, 2026 7:24am | Jul 16, 2026 7:24am | Jul 16, 2026 11:48am | Jul 16, 2026 11:48am | Jul 16, 2026 11:48am | Jul 16, 2026 11:49am | Jul 16, 2026 11:49am | Jul 16, 2026 11:49am |  |  | Fair | No | Premises found closed a lot of bad dogs inside the yard
Outage | J.E.26.07.18084 | C001856396 | Stephen Taylor | St.Thomas | Completed | Load_248914 | Good Year - 210 | Jul 16, 2026 7:24am | Jul 16, 2026 7:24am | Jul 16, 2026 4:34pm | Jul 16, 2026 4:34pm | Jul 16, 2026 4:57pm | Jul 16, 2026 4:57pm | Jul 16, 2026 5:04pm | Jul 16, 2026 5:04pm | BrokenWire |  | Fair | No | Clean up single phase use 2 clamps customer is now okay reading 113,112,225
Outage | J.E.26.07.18139 | C001856395 | Stephen Taylor | St.Thomas | Completed | Load_247908 | Good Year - 210 | Jul 16, 2026 7:24am | Jul 16, 2026 7:24am | Jul 16, 2026 7:23pm | Jul 16, 2026 7:23pm | Jul 16, 2026 7:23pm | Jul 16, 2026 7:23pm | Jul 16, 2026 7:24pm | Jul 16, 2026 7:24pm | BrokenWire |  | Fair | No | Need more information a lot of call to customer no one answered the phone
Outage | J.E.26.07.18200 | C001856400 | Ricky Hall | St.Catherine | Completed | Load_265799 | New Michelton - 210 | Jul 16, 2026 7:24am | Jul 16, 2026 7:25am | Jul 16, 2026 11:22am | Jul 16, 2026 11:23am | Jul 16, 2026 12:04pm | Jul 16, 2026 12:04pm | Jul 16, 2026 12:04pm | Jul 16, 2026 12:04pm |  |  | Fair | No | Issue was resolved previously
Outage | J.E.26.07.18264 | C001856399 | Ricky Hall | St.Catherine | Completed | Load_1001536 | Tredegar - 510 | Jul 16, 2026 7:24am | Jul 16, 2026 7:25am | Jul 16, 2026 9:47am | Jul 16, 2026 10:36am | Jul 16, 2026 10:44am | Jul 16, 2026 10:58am | Jul 16, 2026 10:59am | Jul 16, 2026 10:59am |  |  | Fair | No | Replaced blown 15 amps junction fuse
Non-Outage | J.E.26.07.18179 | C001856393 | Stephen Taylor | null | Completed | null | null | Jul 16, 2026 7:23am | Jul 16, 2026 7:24am | Jul 16, 2026 10:26am | Jul 16, 2026 10:26am | Jul 16, 2026 10:57am | Jul 16, 2026 10:58am | Jul 16, 2026 10:58am | Jul 16, 2026 10:58am |  |  | Fair | No | Check with customer and customer said power is back from last night
Outage | J.E.26.07.18004 | C001856392 | Andrew Powell | Manchester | Completed | Load_252793 | Spur Tree - 210 | Jul 16, 2026 7:22am | Jul 16, 2026 7:27am | Jul 16, 2026 7:39am | Jul 16, 2026 7:41am | Jul 16, 2026 9:07am | Jul 16, 2026 10:14am | Jul 16, 2026 10:17am | Jul 16, 2026 10:17am |  |  | Fair | No | Isolate and close 25 kva transformer circuit to repair corroded secondary jumper joints using three clamps, voltage reading 116v-116v phase to neutral 232v cross phase, no pole number by switch location.
Outage | J.E.26.07.18291 | C001856391 | Selvin White | St.Elizabeth | Completed | Load_267211 | Maggotty - 210 | Jul 16, 2026 7:22am | Jul 16, 2026 7:27am | Jul 16, 2026 8:19am | Jul 16, 2026 8:19am | Jul 16, 2026 9:09am | Jul 16, 2026 9:17am | Jul 16, 2026 9:20am | Jul 16, 2026 9:20am | BrokenPole |  | Fair | No | Customer cannot be contacted or located however no broken pole was seen at location given by the customer.
Outage | J.E.26.07.17783 | C001856388 | Moses Elliston | St.Catherine | Completed | Load_289897 | Rhodens Pen - 210 | Jul 16, 2026 7:14am | Jul 16, 2026 7:22am | Jul 16, 2026 10:18am | Jul 16, 2026 10:18am | Jul 16, 2026 10:18am | Jul 16, 2026 11:40am | Jul 16, 2026 11:41am | Jul 16, 2026 11:41am |  |  | Fair | No | Supply reconnected at meter117-117-234 volts
Non-Outage | J.E.26.07.17870 | C001856387 | Eric Williams | KSAS | Completed | Load_246477 | Greenwich - 410 | Jul 16, 2026 7:13am | Jul 16, 2026 8:17am | Jul 16, 2026 8:55am | Jul 16, 2026 8:55am | Jul 16, 2026 9:30am | Jul 16, 2026 10:47am | Jul 16, 2026 10:50am | Jul 16, 2026 10:50am |  |  | Fair | No | Cx stated having high voltage . Cx pot head, meter socket , and at pole checked using voltmeter readings were okay 119 118 239
Outage | J.E.26.07.18392 | C001856375 | Rusean Allen | KSAS | Completed | Load_249201 | Cane River - 310 | Jul 16, 2026 5:32am | Jul 16, 2026 7:14am | Jul 16, 2026 1:12pm | Jul 16, 2026 1:12pm | Jul 16, 2026 1:12pm | Jul 16, 2026 2:28pm | Jul 16, 2026 2:29pm | Jul 16, 2026 2:29pm |  |  | Fair | No | Found 2 15 amps fuse ReplaceReplace 2 15 amps fuse
Outage | J.E.26.07.17833 | C001856369 | Delano Gayle | Portmore | Completed | Load_255889 | Naggo Head - 610 | Jul 16, 2026 2:42am | Jul 16, 2026 2:57am | Jul 16, 2026 3:59am | Jul 16, 2026 4:00am | Jul 16, 2026 4:32am | Jul 16, 2026 4:59am | Jul 16, 2026 4:59am | Jul 16, 2026 4:59am |  |  | Fair | No | Trip 25kva transformer no pole number, 25kva transformer open secondary line and found okay, reset transformer however after about a minute transformer trips once more, need daylight attention to properly assess situation
Outage | J.E.26.07.18206 | C001856368 | Delano Gayle | Portmore | Completed | Load_556172 | Naggo Head - 610 | Jul 16, 2026 2:38am | Jul 16, 2026 2:57am | Jul 16, 2026 3:43am | Jul 16, 2026 3:43am | Jul 16, 2026 3:54am | Jul 16, 2026 3:59am | Jul 16, 2026 3:59am | Jul 16, 2026 3:59am |  |  | Fair | No | Premises not found no answer from customer phone, no directions to locate customer
Outage | J.E.26.07.18265 | C001856366 | Delano Gayle | Portmore | Completed | Load_570190 | Naggo Head - 610 | Jul 16, 2026 2:38am | Jul 16, 2026 2:57am | Jul 16, 2026 5:02am | Jul 16, 2026 5:02am | Jul 16, 2026 5:31am | Jul 16, 2026 5:44am | Jul 16, 2026 5:44am | Jul 16, 2026 5:44am |  |  | Fair | No | Premises not found no answer from customer phone
Outage | J.E.26.07.18297 | C001856367 | Delano Gayle | Portmore | Completed | Load_255889 | Naggo Head - 610 | Jul 16, 2026 2:38am | Jul 16, 2026 2:57am | Jul 16, 2026 5:00am | Jul 16, 2026 5:00am | Jul 16, 2026 5:01am | Jul 16, 2026 5:02am | Jul 16, 2026 5:02am | Jul 16, 2026 5:02am |  |  | Fair | No | Related to call where trip 25kva transformer circuit needs daylight attention to properly assess as transformer keeps tripping a few minutes after being reset
Outage | J.E.26.07.18282 | C001856365 | Rusean Allen | KSAS | Completed | Load_253227 | Cane River - 610 | Jul 16, 2026 1:44am | Jul 16, 2026 2:19am | Jul 16, 2026 3:47am | Jul 16, 2026 3:47am | Jul 16, 2026 3:47am | Jul 16, 2026 3:48am | Jul 16, 2026 3:49am | Jul 16, 2026 3:49am |  |  | Fair | No | 1x 65amp fuse found 1x 65amp fuse replaced.
Outage | J.E.26.07.18289 | C001856364 | Rusean Allen | KSAS | Completed | Load_254610 | Cane River - 610 | Jul 16, 2026 1:44am | Jul 16, 2026 2:19am | Jul 16, 2026 3:49am | Jul 16, 2026 3:49am | Jul 16, 2026 3:49am | Jul 16, 2026 3:50am | Jul 16, 2026 3:50am | Jul 16, 2026 3:50am |  |  | Fair | No | Related to 16 Henry Morgan blvd
Outage | J.E.26.07.18290 | C001856363 | Rusean Allen | KSAS | Completed | Load_243254 | Cane River - 610 | Jul 16, 2026 1:44am | Jul 16, 2026 2:19am | Jul 16, 2026 3:50am | Jul 16, 2026 3:50am | Jul 16, 2026 3:50am | Jul 16, 2026 3:51am | Jul 16, 2026 3:51am | Jul 16, 2026 3:51am |  |  | Fair | No | Related to Henry Morgan blvd
Outage | J.E.26.07.18021 | C001856360 | Derrick Dawkins | St.James | Completed | Load_257587 | Queens Drive - 710 | Jul 16, 2026 12:05am | Jul 16, 2026 12:09am | Jul 16, 2026 4:35am | Jul 16, 2026 4:36am | Jul 16, 2026 4:36am | Jul 16, 2026 4:37am | Jul 16, 2026 4:44am | Jul 16, 2026 4:44am | BrokenWire |  | Fair | No | Cannot locate customer . Customer phone number short of one digit needed more information
Non-Outage | J.E.26.07.18124 | C001856358 | Derrick Dawkins | null | Completed | null | null | Jul 16, 2026 12:04am | Jul 16, 2026 12:09am | Jul 16, 2026 3:22am | Jul 16, 2026 3:22am | Jul 16, 2026 3:40am | Jul 16, 2026 3:53am | Jul 16, 2026 3:55am | Jul 16, 2026 3:55am | Fire |  | Fair | No | Check and found area ok
Outage | J.E.26.07.18045 | C001856359 | Derrick Dawkins | St.James | Completed | Load_267656 | Queens Drive - 710 | Jul 16, 2026 12:04am | Jul 16, 2026 12:09am | Jul 16, 2026 3:59am | Jul 16, 2026 3:59am | Jul 16, 2026 4:16am | Jul 16, 2026 4:19am | Jul 16, 2026 4:35am | Jul 16, 2026 4:35am | Fire |  | Fair | No | Check and found area ok cannot locate customer by phone
Outage | J.E.26.07.18198 | C001856357 | Delano Gayle | St.Catherine | Completed | Load_244050 | Tredegar - 410 | Jul 15, 2026 11:48pm | Jul 15, 2026 11:50pm | Jul 16, 2026 12:07am | Jul 16, 2026 2:56am | Jul 16, 2026 3:37am | Jul 16, 2026 3:40am | Jul 16, 2026 3:40am | Jul 16, 2026 3:40am |  |  | Fair | No | Trip 25kva transformer no pole number, reset transformer
Outage | J.E.26.07.18230 | C001856352 | Andre Williams | Trelawny | Completed | Load_258656 | Duncans - 210 | Jul 15, 2026 10:40pm | Jul 16, 2026 7:48am | Jul 16, 2026 8:11am | Jul 16, 2026 10:27am | Jul 16, 2026 10:27am | Jul 16, 2026 10:27am | Jul 16, 2026 10:27am | Jul 16, 2026 10:27am |  |  | Fair | No | Open 50 kva transformer retention low hanging phase that was touching, remake burnt off neutral at transformer pole
Outage | J.E.26.07.18150 | C001856328 | Swon Miller | St.James | Completed | Load_266001 | Queens Drive - 310 | Jul 15, 2026 8:58pm | Jul 15, 2026 8:59pm | Jul 15, 2026 9:31pm | Jul 15, 2026 9:31pm | Jul 15, 2026 10:12pm | Jul 21, 2026 10:20pm | Jul 15, 2026 10:20pm | Jul 15, 2026 10:20pm |  |  | Fair | No | Check and found okay voltage found 118/118/206/customer states power supply was restored earlier today voltage left 118/118/206/236/237/236
Outage | J.E.26.07.18145 | C001856325 | Raymond Carr | St.Mary | Completed | Load_240350 | Oracabessa - 210 | Jul 15, 2026 8:52pm | Jul 15, 2026 8:53pm | Jul 15, 2026 10:20pm | Jul 15, 2026 10:20pm | Jul 15, 2026 10:49pm | Jul 15, 2026 10:50pm | Jul 15, 2026 10:54pm | Jul 15, 2026 10:54pm | BrokenPole |  | Fair | No | Supply found okay, however customer needs leaning poles corrected. Refer to maintenance department.
Non-Outage | J.E.26.07.18134 | C001856322 | Andrae Clarke | Portland | Completed | Load_351947 | Port Antonio - 310 | Jul 15, 2026 8:51pm | Jul 16, 2026 9:36am | Jul 16, 2026 10:53am | Jul 16, 2026 10:53am | Jul 16, 2026 10:53am | Jul 16, 2026 10:59am | Jul 16, 2026 10:56am | Jul 16, 2026 10:56am |  |  | Fair | No | Meter burn refer to field service to change meterCheck voltage 118/121239
Outage | J.E.26.07.18172 | C001856320 | Milton Charlton | KSAN | Completed | Load_244680 | West Kings House - 310 | Jul 15, 2026 8:40pm | Jul 16, 2026 7:55am | Jul 16, 2026 12:23pm | Jul 16, 2026 12:23pm | Jul 16, 2026 12:51pm | Jul 16, 2026 12:55pm | Jul 16, 2026 12:58pm | Jul 16, 2026 12:58pm |  |  | Fair | No | Customer meter #2376933 and meter socket burn up. Customer need to repair meter socket and request a replacement.
Non-Outage | J.E.26.07.18047 | C001856319 | Omar King | St.Ann | Completed | Load_255760 | Cardiff Hall - 310 | Jul 15, 2026 8:39pm | Jul 15, 2026 8:40pm | Jul 15, 2026 11:00pm | Jul 15, 2026 11:00pm | Jul 15, 2026 11:46pm | Jul 15, 2026 11:47pm | Jul 15, 2026 11:47pm | Jul 15, 2026 11:47pm | BrokenWire |  | Fair | No | Unable to find customer customer call several times no answer directions not sufficient
Outage | J.E.26.07.18080 | C001856316 | Tyrese Williams | St.Ann | Completed | Load_254192 | Ocho Rios - 310 | Jul 15, 2026 8:31pm | Jul 15, 2026 8:31pm | Jul 15, 2026 8:36pm | Jul 15, 2026 9:02pm | Jul 15, 2026 9:02pm | Jul 15, 2026 9:13pm | Jul 15, 2026 9:14pm | Jul 15, 2026 9:14pm | TreeContact |  | Fair | No | Found a huge tree fell and burst span of primary and secondary line 1 span of primary run back, road way is blocked refer to maintenance bushing required
Outage | J.E.26.07.17851 | C001856312 | Stephen Taylor | St.Thomas | Completed | Load_265499 | Good Year - 210 | Jul 15, 2026 8:26pm | Jul 15, 2026 8:27pm | Jul 15, 2026 9:31pm | Jul 15, 2026 9:31pm | Jul 15, 2026 9:31pm | Jul 15, 2026 9:31pm | Jul 15, 2026 9:32pm | Jul 15, 2026 9:32pm |  |  | Fair | No | Check with customer and customer said power is back and okay
Outage | J.E.26.07.18132 | C001856310 | Stephen Taylor | St.Thomas | Completed | Load_238274 | Good Year - 210 | Jul 15, 2026 8:26pm | Jul 15, 2026 8:27pm | Jul 15, 2026 8:48pm | Jul 15, 2026 8:48pm | Jul 15, 2026 9:27pm | Jul 15, 2026 9:27pm | Jul 15, 2026 9:29pm | Jul 15, 2026 9:29pm |  |  | Fair | No | Patrol clear dead bird from line and close up back 25 kva transformer safely customer is now okay
Outage | J.E.26.07.18176 | C001856314 | Stephen Taylor | St.Thomas | Completed | Load_243904 | Good Year - 210 | Jul 15, 2026 8:26pm | Jul 15, 2026 8:27pm | Jul 15, 2026 9:32pm | Jul 15, 2026 9:32pm | Jul 15, 2026 9:33pm | Jul 15, 2026 9:33pm | Jul 15, 2026 9:34pm | Jul 15, 2026 9:34pm |  |  | Fair | No | Patrol clear dead bird from line and close up back 25 kva transformer safely all customer is now okay
Non-Outage | J.E.26.07.15886 | C001856309 | Romeo Brissett | St.James | Completed | Load_240799 | Bogue - 510 | Jul 15, 2026 8:25pm | Jul 15, 2026 8:25pm | Jul 15, 2026 8:47pm | Jul 15, 2026 8:47pm | Jul 15, 2026 8:56pm | Jul 15, 2026 9:00pm | Jul 15, 2026 9:01pm | Jul 15, 2026 9:01pm |  |  | Fair | No | Check and found ok customer stated issue was resolved earlier.V/R 118-121-206-236-236-238.
Outage | J.E.26.07.17515 | C001856307 | Jermaine Williams | St.Catherine | Completed | Load_293999 | Rhodens Pen - 310 | Jul 15, 2026 8:19pm | Jul 16, 2026 8:56am | Jul 16, 2026 9:21am | Jul 16, 2026 9:21am | Jul 16, 2026 9:41am | Jul 16, 2026 10:08am | Jul 16, 2026 10:18am | Jul 16, 2026 10:18am |  |  | SevereWind | No | Splice and retention broken service wire using 40’ #6 triplex and three clamps.
Non-Outage | J.E.26.07.17149 | C001856304 | Milton Charlton | KSAN | Completed | Load_557683 | West Kings House - 410 | Jul 15, 2026 8:16pm | Jul 16, 2026 8:00am | Jul 16, 2026 9:00am | Jul 16, 2026 9:00am | Jul 16, 2026 9:41am | Jul 15, 2026 10:25pm | Jul 16, 2026 9:43am | Jul 16, 2026 9:43am |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Non-Outage | J.E.26.07.17540 | C001856303 | Milton Charlton | KSAN | Completed | Load_245872 | Washington Blvd - 410 | Jul 15, 2026 8:16pm | Jul 15, 2026 8:16pm | Jul 15, 2026 8:37pm | Jul 15, 2026 8:37pm | Jul 15, 2026 8:49pm | Jul 15, 2026 8:50pm | Jul 15, 2026 8:56pm | Jul 15, 2026 8:56pm |  |  | Fair | No | Found okay upon arrival. Customer has an internal problem. Readings at meter socket 121-121-242 volts.
Outage | J.E.26.07.18111 | C001856301 | Elvis Trowers | KSAN | Completed | Load_253299 | Washington Blvd - 510 | Jul 15, 2026 8:15pm | Jul 16, 2026 7:27am | Jul 16, 2026 12:05pm | Jul 16, 2026 12:05pm | Jul 16, 2026 12:19pm | Jul 16, 2026 12:27pm | Jul 16, 2026 12:27pm | Jul 16, 2026 12:27pm |  |  | Fair | Yes | Premises checked and found ok upon arrival customer was also spoken with however she suggested that the power supply was restored.
Outage | J.E.26.07.18117 | C001856302 | Barrington Brown | St.James | Completed | Load_269643 | Rose Hall - 210 | Jul 15, 2026 8:15pm | Jul 15, 2026 8:17pm | Jul 15, 2026 10:40pm | Jul 15, 2026 10:40pm | Jul 15, 2026 10:59pm | Jul 15, 2026 11:43pm | Jul 15, 2026 11:43pm | Jul 15, 2026 11:43pm |  |  | Fair | No | Crew found 100kva transformer top blown off and 20k junction fuse blown on location. Crew isolated transformer and replaced junction fuse. Please refer to maintenance department to change defective transformer and replace damaged switch. Bank of three that servers one customer.
Outage | J.E.26.07.17894 | C001856298 | Kaydon Taylor | KSAN | Completed | null | null | Jul 15, 2026 8:14pm | Jul 15, 2026 9:55pm | Jul 15, 2026 10:00pm | Jul 15, 2026 10:00pm | Jul 15, 2026 10:31pm | Jul 16, 2026 12:05am | Jul 16, 2026 12:05am | Jul 16, 2026 12:05am | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Splice and retention broken #6 service wire, 3 clamps at pole. V 115-115-232
Outage | J.E.26.07.17838 | C001856297 | Moses Elliston | St.Catherine | Completed | Load_288554 | Rhodens Pen - 210 | Jul 15, 2026 8:12pm | Jul 15, 2026 8:13pm | Jul 16, 2026 1:18pm | Jul 16, 2026 1:18pm | Jul 16, 2026 1:18pm | Jul 16, 2026 1:29pm | Jul 16, 2026 1:31pm | Jul 16, 2026 1:31pm |  |  | Fair | No | Meter relay reset.117-117-234 volts.
Outage | J.E.26.07.18116 | C001856296 | Hartley Chin | Clarendon | Completed | Load_247516 | Monymusk - 210 | Jul 15, 2026 8:10pm | Jul 15, 2026 8:10pm | Jul 15, 2026 8:53pm | Jul 15, 2026 8:53pm | Jul 15, 2026 8:53pm | Jul 15, 2026 8:54pm | Jul 15, 2026 8:54pm | Jul 15, 2026 8:54pm |  |  | Fair | No | Customer now connected by field service
Outage | J.E.26.07.18118 | C001856295 | Hartley Chin | Clarendon | Completed | Load_248180 | Monymusk - 210 | Jul 15, 2026 8:10pm | Jul 15, 2026 8:10pm | Jul 15, 2026 8:33pm | Jul 15, 2026 8:33pm | Jul 15, 2026 8:33pm | Jul 15, 2026 8:33pm | Jul 15, 2026 8:33pm | Jul 15, 2026 8:33pm |  |  | Fair | No | Customer now connected Done by field service
Outage | J.E.26.07.18144 | C001856294 | Hartley Chin | Clarendon | Completed | Load_246879 | Monymusk - 210 | Jul 15, 2026 8:10pm | Jul 15, 2026 8:10pm | Jul 15, 2026 8:35pm | Jul 15, 2026 8:35pm | Jul 15, 2026 8:35pm | Jul 15, 2026 8:35pm | Jul 15, 2026 8:36pm | Jul 15, 2026 8:36pm |  |  | Fair | No | Customer now connected Done by field service
Outage | J.E.26.07.18034 | C001856286 | Floyd Taylor | Trelawny | Completed | Load_244909 | Greenwood - 110 | Jul 15, 2026 7:43pm | Jul 15, 2026 7:43pm | Jul 15, 2026 8:19pm | Jul 15, 2026 8:19pm | Jul 15, 2026 8:19pm | Jul 15, 2026 8:19pm | Jul 15, 2026 8:22pm | Jul 15, 2026 8:22pm |  |  | Fair | No | Customer advised that their service was restored.
Outage | J.E.26.07.17142 | C001856284 | Ryan Richards | Manchester | Completed | Load_252477 | Spur Tree - 310 | Jul 15, 2026 7:40pm | Jul 15, 2026 7:40pm | Jul 15, 2026 9:57pm | Jul 15, 2026 9:57pm | Jul 15, 2026 11:50pm | Jul 15, 2026 11:51pm | Jul 15, 2026 11:51pm | Jul 15, 2026 11:51pm |  |  | Fair | No | Area found ok customer made report about street lights that’s not working
Outage | J.E.26.07.17309 | C001856283 | Ryan Richards | Manchester | Completed | Load_248521 | Spur Tree - 310 | Jul 15, 2026 7:40pm | Jul 15, 2026 7:40pm | Jul 15, 2026 8:43pm | Jul 15, 2026 9:09pm | Jul 15, 2026 9:43pm | Jul 15, 2026 9:57pm | Jul 15, 2026 9:57pm | Jul 15, 2026 9:57pm | Fire |  | Fair | No | Corroded phase found at pole causing the customer to have single phase remade burn off phase using 2 one bolt clamps voltage 116/110/226 volts
Outage | J.E.26.07.17367 | C001856282 | Richard Samuda | Manchester | Completed | Load_254451 | Spur Tree - 310 | Jul 15, 2026 7:40pm | Jul 16, 2026 7:36am | Jul 16, 2026 7:45am | Jul 16, 2026 7:45am | Jul 16, 2026 7:59am | Jul 16, 2026 9:19am | Jul 16, 2026 9:19am | Jul 16, 2026 9:19am |  |  | Fair | No | Splice and reconnected customer service neutral that was broken causing customer to experience hi voltage using 3ft of #6service neutral and 1bolt clamp customer back to normal voltage 116/118/234
Outage | J.E.26.07.18050 | C001856280 | Raymond Carr | St.Mary | Completed | Load_350817 | Oracabessa - 110 | Jul 15, 2026 7:37pm | Jul 15, 2026 8:53pm | Jul 15, 2026 9:34pm | Jul 15, 2026 9:34pm | Jul 15, 2026 10:17pm | Jul 15, 2026 10:16pm | Jul 15, 2026 10:19pm | Jul 15, 2026 10:19pm |  |  | Fair | No | Several calls to contact number went unanswered.
Outage | J.E.26.07.18099 | C001856279 | Hartley Chin | Clarendon | Completed | Load_294623 | Monymusk - 210 | Jul 15, 2026 7:31pm | Jul 15, 2026 7:31pm | Jul 15, 2026 7:54pm | Jul 15, 2026 7:54pm | Jul 15, 2026 8:13pm | Jul 15, 2026 8:13pm | Jul 15, 2026 8:14pm | Jul 15, 2026 8:14pm |  |  | Fair | No | Customer was connected by field service
Non-Outage | J.E.26.07.10623 | C001856273 | Raymond Lewis | St.Ann | Completed | Load_268322 | Roaring River - 210 | Jul 15, 2026 7:21pm | Jul 15, 2026 7:23pm | Jul 15, 2026 7:52pm | Jul 15, 2026 7:52pm | Jul 15, 2026 9:20pm | Jul 15, 2026 10:40pm | Jul 15, 2026 10:40pm | Jul 15, 2026 10:40pm |  |  | Fair | No | Definitely 3 wire service 105ft
Outage | J.E.26.07.17910 | C001856272 | Barrington Brown | St.James | Completed | Load_268465 | Queens Drive - 710 | Jul 15, 2026 7:15pm | Jul 15, 2026 7:15pm | Jul 15, 2026 9:30pm | Jul 15, 2026 9:30pm | Jul 15, 2026 10:16pm | Jul 15, 2026 10:40pm | Jul 15, 2026 10:40pm | Jul 15, 2026 10:40pm |  |  | Fair | No | Crew found a burnt switch top jumper on location crew opened three junction fuses to remake jumper used 3 ft of #4 copper and 1 2- 2 ampact. Re energize circuit All customers restored.
Non-Outage | J.E.26.07.18068 | C001856270 | Fitzroy Turner | null | Completed | null | null | Jul 15, 2026 7:03pm | Jul 15, 2026 7:03pm | Jul 15, 2026 8:04pm | Jul 15, 2026 8:49pm | Jul 15, 2026 9:03pm | Jul 15, 2026 9:24pm | Jul 15, 2026 9:25pm | Jul 15, 2026 9:25pm | BrokenWire |  | Fair | No | Found tree service phase burnt off at pole use one clamp to carry out repair supply restored to customer
Outage | J.E.26.07.17994 | C001856264 | Richard Grant | St.Catherine | Completed | Load_255139 | New Michelton - 410 | Jul 15, 2026 6:47pm | Jul 15, 2026 7:07pm | Jul 15, 2026 9:37pm | Jul 15, 2026 9:37pm | Jul 15, 2026 10:44pm | Jul 15, 2026 10:45pm | Jul 15, 2026 10:48pm | Jul 15, 2026 10:48pm |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.16782 | C001856263 | Richard Grant | St.Catherine | Completed | Load_245525 | New Michelton - 410 | Jul 15, 2026 6:46pm | Jul 15, 2026 6:49pm | Jul 15, 2026 7:26pm | Jul 15, 2026 7:26pm | Jul 15, 2026 8:03pm | Jul 15, 2026 8:04pm | Jul 15, 2026 8:04pm | Jul 15, 2026 8:04pm |  |  | Fair | No | Premises not found. Calls to customer goes straight to voicemail. Insufficient direction
Outage | J.E.26.07.18027 | C001856261 | Tyrese Williams | St.Ann | Completed | Load_253537 | Upper White River - 210 | Jul 15, 2026 6:43pm | Jul 15, 2026 6:45pm | Jul 15, 2026 9:16pm | Jul 15, 2026 9:16pm | Jul 15, 2026 9:16pm | Jul 15, 2026 9:17pm | Jul 15, 2026 9:17pm | Jul 15, 2026 9:17pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.17993 | C001856259 | Selvin White | St.Elizabeth | Completed | Load_253295 | Maggotty - 110 | Jul 15, 2026 6:31pm | Jul 16, 2026 7:27am | Jul 16, 2026 2:30pm | Jul 16, 2026 2:30pm | Jul 16, 2026 2:30pm | Jul 16, 2026 12:58pm | Jul 16, 2026 2:36pm | Jul 16, 2026 2:36pm |  |  | Fair | No | Splice and retention approximately 50 ft of broken customer service wire phase and neutral conductors caused by a freak storm. Supply restored. Voltage readings left inside customer’s meter socket are 118,117,235 volts.
Non-Outage | J.E.26.07.18030 | C001856257 | Wayne Dillion | null | Completed | null | null | Jul 15, 2026 6:30pm | Jul 15, 2026 6:30pm | Jul 15, 2026 8:50pm | Jul 15, 2026 8:50pm | Jul 15, 2026 8:50pm | Jul 15, 2026 8:54pm | Jul 15, 2026 8:53pm | Jul 15, 2026 8:53pm |  |  | Fair | No | Customer said premises lock said team must visit in the morning
Outage | J.E.26.07.18011 | C001856258 | Wayne Dillion | St.Elizabeth | Completed | Load_241674 | Maggotty - 110 | Jul 15, 2026 6:30pm | Jul 15, 2026 6:30pm | Jul 15, 2026 6:52pm | Jul 15, 2026 6:52pm | Jul 15, 2026 6:52pm | Jul 15, 2026 6:53pm | Jul 15, 2026 6:53pm | Jul 15, 2026 6:53pm |  |  | Fair | No | Customer said problem has been resolved and supply working ok
Outage | J.E.26.07.17848 | C001856254 | Swon Miller | St.James | Completed | Load_576009 | Bogue - 310 | Jul 15, 2026 6:21pm | Jul 15, 2026 6:22pm | Jul 15, 2026 7:58pm | Jul 15, 2026 8:01pm | Jul 15, 2026 8:20pm | Jul 15, 2026 8:30am | Jul 15, 2026 8:31pm | Jul 15, 2026 8:31pm |  |  | Fair | No | Check and found customer without supply with the help of customer care agent Omar power was restored voltage found 0.000 voltage left 114/116/231
Outage | J.E.26.07.18000 | C001856253 | Swon Miller | St.James | Completed | Load_253178 | Bogue - 310 | Jul 15, 2026 6:21pm | Jul 15, 2026 6:22pm | Jul 15, 2026 7:31pm | Jul 15, 2026 10:21pm | Jul 15, 2026 10:55pm | Jul 15, 2026 11:01pm | Jul 15, 2026 11:01pm | Jul 15, 2026 11:01pm |  |  | Fair | No | Customer states that she did not make any report
Outage | J.E.26.07.18004 | C001856251 | Marlon Authors | Manchester | Completed | Load_252793 | Spur Tree - 210 | Jul 15, 2026 6:17pm | Jul 15, 2026 6:26pm | Jul 15, 2026 7:07pm | Jul 15, 2026 7:07pm | Jul 15, 2026 7:45pm | Jul 15, 2026 10:18pm | Jul 15, 2026 10:19pm | Jul 15, 2026 10:19pm |  |  | SevereWind | No | Unable to complete checks. Daylight attention is needed for better visibility
Non-Outage | J.E.26.02.36672 | C001856249 | Tajay Bernard | St.James | Completed | Load_238585 | Bogue - 510 | Jul 15, 2026 5:53pm | Jul 15, 2026 5:53pm | Jul 15, 2026 6:46pm | Jul 15, 2026 6:47pm | Jul 15, 2026 6:47pm | Jul 15, 2026 6:48pm | Jul 15, 2026 6:48pm | Jul 15, 2026 6:48pm |  |  | Fair | No | Customer stated that the issue has been resolved
Non-Outage | J.E.26.02.40028 | C001856246 | Tajay Bernard | St.James | Completed | Load_238585 | Bogue - 510 | Jul 15, 2026 5:53pm | Jul 15, 2026 5:53pm | Jul 15, 2026 7:09pm | Jul 15, 2026 7:09pm | Jul 15, 2026 7:10pm | Jul 15, 2026 7:10pm | Jul 15, 2026 7:10pm | Jul 15, 2026 7:10pm |  |  | Flood | No | Area check and found okay unable to locate customer on premises multiple phone call to customer number went unanswered
Non-Outage | J.E.26.02.45507 | C001856247 | Tajay Bernard | St.James | Completed | Load_250785 | Bogue - 510 | Jul 15, 2026 5:53pm | Jul 15, 2026 5:53pm | Jul 15, 2026 7:11pm | Jul 15, 2026 7:11pm | Jul 15, 2026 7:11pm | Jul 15, 2026 7:12pm | Jul 15, 2026 7:12pm | Jul 15, 2026 7:12pm | Fire |  | Fair | No | Customer stated that the issue has been resolved
Non-Outage | J.E.26.07.13846 | C001856248 | Tajay Bernard | St.James | Completed | Load_244420 | Bogue - 510 | Jul 15, 2026 5:53pm | Jul 15, 2026 5:53pm | Jul 15, 2026 6:48pm | Jul 15, 2026 6:49pm | Jul 15, 2026 7:07pm | Jul 15, 2026 7:07pm | Jul 15, 2026 7:07pm | Jul 15, 2026 7:07pm |  |  | Fair | No | Area check and found okay unable to locate customer on premises multiple phone call to customer number went unanswered
Outage | J.E.26.07.17987 | C001856243 | Richman Whyte | Westmoreland | Completed | Load_257430 | Paradise - 310 | Jul 15, 2026 5:45pm | Jul 15, 2026 6:14pm | Jul 15, 2026 9:33pm | Jul 15, 2026 9:33pm | Jul 15, 2026 10:30pm | Jul 15, 2026 10:31pm | Jul 15, 2026 10:32pm | Jul 15, 2026 10:32pm |  |  | Fair | No | Twenty five kva transformer burned need to change sand referral to maintenance department
Outage | J.E.26.07.17054 | C001856241 | Nickolas Rodriques | St.Catherine | Completed | Load_576126 | Twickenham - 210 | Jul 15, 2026 5:43pm | Jul 15, 2026 7:06pm | Jul 16, 2026 2:46pm | Jul 16, 2026 2:58pm | Jul 16, 2026 3:37pm | Jul 16, 2026 3:53pm | Jul 16, 2026 3:54pm | Jul 16, 2026 3:54pm |  |  | Fair | No | Checked and found a 10 KVA transformer fuse open. Patrol and found a 30 ft wooden pole broken caused by car accident. It’s a (T) pole with open secondary wires. Customers are still without power. Refer to maintenance.
Outage | J.E.26.07.17833 | C001856240 | Nickolas Rodriques | Portmore | Completed | Load_255889 | Naggo Head - 610 | Jul 15, 2026 5:41pm | Jul 15, 2026 7:38pm | Jul 16, 2026 9:57am | Jul 16, 2026 9:57am | Jul 16, 2026 10:29am | Jul 16, 2026 11:35am | Jul 16, 2026 11:38am | Jul 16, 2026 11:38am |  |  | Fair | No | Checked and found a 10 KVA transformer on tripped. All necessary checks were done and it was found that one customer is having internal electrical issues. Meter #(2627411) was disconnected in order to restore power. Unable to advise customer due to no one at the premises.
Outage | J.E.26.07.17859 | C001856239 | Kaydon Taylor | KSAN | Completed | Load_267152 | Constant Spring - 410 | Jul 15, 2026 5:26pm | Jul 15, 2026 5:27pm | Jul 15, 2026 7:04pm | Jul 15, 2026 7:04pm | Jul 15, 2026 8:06pm | Jul 15, 2026 8:19pm | Jul 15, 2026 8:19pm | Jul 15, 2026 8:19pm |  |  | Fair | No | Customer got disconnected then pay her bill but no supply . Reach out to escalation and they reset her meter. V 116 117 233
Outage | J.E.26.07.17297 | C001856238 | Neville Spencer | St.Ann | Completed | Load_242865 | Cardiff Hall - 310 | Jul 15, 2026 5:24pm | Jul 15, 2026 5:25pm | Jul 15, 2026 7:02pm | Jul 15, 2026 7:02pm | Jul 15, 2026 7:41pm | Jul 15, 2026 7:41pm | Jul 15, 2026 7:42pm | Jul 15, 2026 7:42pm |  |  | Fair | No | Found ok.
Outage | J.E.26.07.17901 | C001856237 | Neville Spencer | St.Ann | Completed | Load_239985 | Cardiff Hall - 310 | Jul 15, 2026 5:24pm | Jul 15, 2026 5:25pm | Jul 15, 2026 5:50pm | Jul 15, 2026 5:59pm | Jul 15, 2026 6:26pm | Jul 15, 2026 6:44pm | Jul 15, 2026 6:48pm | Jul 15, 2026 6:48pm | BrokenWire | Y | Fair | No | Cleared bamboo from secondary lines remade broken off phase joint at secondary on 3, wire service voltage reading 112 115 229 supply restored.
Outage | J.E.26.07.17893 | C001856235 | Fitzroy Turner | KSAS | Completed | Load_241461 | Rockfort - 410 | Jul 15, 2026 5:22pm | Jul 15, 2026 5:22pm | Jul 15, 2026 8:05pm | Jul 15, 2026 8:05pm | Jul 15, 2026 8:42pm | Jul 15, 2026 8:46pm | Jul 15, 2026 8:47pm | Jul 15, 2026 8:47pm | Fire |  | Fair | No | Found three wire service phase and neutral corroded at pothead use two one bolt clamps to carry out repair supply restored to customer
Outage | J.E.26.07.17923 | C001856234 | Romeo Brissett | St.James | Completed | Load_248714 | Bogue - 510 | Jul 15, 2026 5:20pm | Jul 15, 2026 5:21pm | Jul 15, 2026 7:32pm | Jul 15, 2026 7:32pm | Jul 15, 2026 7:32pm | Jul 15, 2026 7:30pm | Jul 15, 2026 7:33pm | Jul 15, 2026 7:33pm |  |  | Fair | No | Check and found ok, conductor was repaired and power restored. related to job#17258.
Outage | J.E.26.07.17924 | C001856233 | Neville Spencer | Clarendon | Completed | Load_251963 | May Pen - 110 | Jul 15, 2026 5:20pm | Jul 15, 2026 5:21pm | Jul 15, 2026 9:14pm | Jul 15, 2026 9:15pm | Jul 15, 2026 9:15pm | Jul 15, 2026 9:15pm | Jul 15, 2026 9:16pm | Jul 15, 2026 9:16pm |  |  | Fair | No | Not getting trough to customer.
Non-Outage | J.E.26.07.17299 | C001856228 | Wan Carlos Scarlett | null | Completed | null | null | Jul 15, 2026 5:07pm | Jul 15, 2026 6:21pm | Jul 15, 2026 9:43pm | Jul 15, 2026 9:43pm | Jul 15, 2026 10:44pm | Jul 15, 2026 10:44pm | Jul 15, 2026 10:45pm | Jul 15, 2026 10:45pm | BrokenWire |  | Fair | No | Found cable and wireless wires broken on the ground advised customer to contact cable provider for assistance
Non-Outage | J.E.26.07.17858 | C001856227 | Milton Charlton | null | Completed | null | null | Jul 15, 2026 5:07pm | Jul 15, 2026 5:23pm | Jul 15, 2026 6:10pm | Jul 15, 2026 6:10pm | Jul 15, 2026 6:10pm | Jul 15, 2026 6:05pm | Jul 15, 2026 6:13pm | Jul 15, 2026 6:13pm | BrokenWire |  | Fair | No | Call related to call at 8 Morinda Place Long Mountain.
Outage | J.E.26.07.17894 | C001856229 | Milton Charlton | KSAN | Completed | Load_239626 | Hope - 410 | Jul 15, 2026 5:07pm | Jul 15, 2026 5:23pm | Jul 15, 2026 5:52pm | Jul 15, 2026 5:52pm | Jul 15, 2026 6:06pm | Jul 15, 2026 6:05pm | Jul 15, 2026 6:10pm | Jul 15, 2026 6:10pm | BrokenWire |  | Fair | No | Customer service wire#6 triplex connected in mid-span damaged in motor vehicle accident. Need about 40ft #6 triplex to repair service wire. Need bucket truck.
Outage | J.E.26.07.17541 | C001856226 | Richard Grant | St.Catherine | Completed | Load_254302 | New Michelton - 210 | Jul 15, 2026 5:06pm | Jul 15, 2026 5:10pm | Jul 15, 2026 8:04pm | Jul 15, 2026 8:04pm | Jul 15, 2026 9:00pm | Jul 15, 2026 9:00pm | Jul 15, 2026 9:00pm | Jul 15, 2026 9:00pm |  |  | Fair | No | Premises found with supply and okay
Outage | J.E.26.07.17838 | C001856225 | Richard Nicholas | St.Catherine | Completed | Load_288554 | Rhodens Pen - 210 | Jul 15, 2026 5:06pm | Jul 15, 2026 5:07pm | Jul 15, 2026 7:56pm | Jul 15, 2026 7:56pm | Jul 15, 2026 8:09pm | Jul 15, 2026 8:09pm | Jul 15, 2026 8:10pm | Jul 15, 2026 8:10pm |  |  | Fair | No | EG system failure,please refer to Mr.moses.fault detected at EG box.
Outage | J.E.26.07.17861 | C001856224 | Richard Nicholas | St.Catherine | Completed | Load_262691 | Rhodens Pen - 210 | Jul 15, 2026 5:06pm | Jul 15, 2026 5:07pm | Jul 15, 2026 8:11pm | Jul 15, 2026 8:11pm | Jul 15, 2026 8:52pm | Jul 15, 2026 9:38pm | Jul 15, 2026 9:40pm | Jul 15, 2026 9:40pm | BangingWires |  | Fair | No | Splice and retention 2 span of broken secondary phase and neutral.10ft of #2aac and 2 clamp was used to completed the repair.
Non-Outage | J.E.26.07.17856 | C001856219 | Denton Williams | Portland | Completed | Load_268759 | Port Antonio - 410 | Jul 15, 2026 4:58pm | Jul 15, 2026 4:59pm | Jul 15, 2026 5:41pm | Jul 15, 2026 5:41pm | Jul 15, 2026 6:05pm | Jul 15, 2026 6:25pm | Jul 15, 2026 6:34pm | Jul 15, 2026 6:34pm | Fire |  | Fair | No | Primary jumper making contact with pole when it’s windy. Use a grip all stick to reposition jumper to safe distance from pole.
Non-Outage | J.E.26.07.17876 | C001856218 | Fitzroy Turner | KSAS | Completed | Load_269528 | Greenwich - 310 | Jul 15, 2026 4:56pm | Jul 15, 2026 4:57pm | Jul 15, 2026 6:11pm | Jul 15, 2026 6:11pm | Jul 15, 2026 6:11pm | Jul 15, 2026 7:53pm | Jul 15, 2026 8:03pm | Jul 15, 2026 8:03pm | Fire |  | Fair | No | Found 40/2 wooden pole top burnt off with drops out switch crossarm at transformer pole .use one insulator and one drops out switch and one switches brocket and one 3amps fuse and 4 machine bolt to carry out repair supply restored to areas. Cloae up 25 amps junction fuse at the intersection of Rae st paradise st
Outage | J.E.26.07.17565 | C001856216 | Barrington Brown | St.James | Completed | Load_301826 | Bogue - 310 | Jul 15, 2026 4:51pm | Jul 15, 2026 4:51pm | Jul 15, 2026 7:02pm | Jul 15, 2026 7:02pm | Jul 15, 2026 8:01pm | Jul 15, 2026 8:05pm | Jul 15, 2026 8:05pm | Jul 15, 2026 8:05pm |  |  | Fair | No | Checked and found ok
Outage | J.E.26.07.17291 | C001856213 | Barrington Brown | St.James | Completed | Load_265260 | Bogue - 310 | Jul 15, 2026 4:48pm | Jul 15, 2026 4:48pm | Jul 15, 2026 5:59pm | Jul 15, 2026 6:45pm | Jul 15, 2026 6:45pm | Jul 15, 2026 7:00pm | Jul 15, 2026 7:00pm | Jul 15, 2026 7:00pm |  |  | Fair | No | Crew found 2 blown 25 kva transformer fuse on location. Crew conducted patrol and re energized transformer. Customer restored.
Outage | J.E.26.07.17351 | C001856212 | Barrington Brown | St.James | Completed | Load_301755 | Bogue - 310 | Jul 15, 2026 4:48pm | Jul 15, 2026 4:48pm | Jul 15, 2026 6:44pm | Jul 15, 2026 6:44pm | Jul 15, 2026 6:44pm | Jul 15, 2026 6:44pm | Jul 15, 2026 6:45pm | Jul 15, 2026 6:45pm |  |  | Fair | No | Crew found 2 blown 167 transformer fuse on location. One switch barrel was found brunt as well. Crew replace Switch barrel and restored customer supply.
Non-Outage | J.E.26.07.17403 | C001856208 | Javid Vernon | null | Completed | null | null | Jul 15, 2026 4:43pm | Jul 15, 2026 4:44pm | Jul 15, 2026 6:02pm | Jul 15, 2026 6:02pm | Jul 15, 2026 6:02pm | Jul 15, 2026 6:02pm | Jul 15, 2026 6:03pm | Jul 15, 2026 6:03pm | TreeContact |  | Fair | No | This call belongs to st mary
Outage | J.E.26.07.17504 | C001856209 | Javid Vernon | Westmoreland | Completed | Load_256420 | Paradise - 110 | Jul 15, 2026 4:43pm | Jul 15, 2026 4:44pm | Jul 15, 2026 6:03pm | Jul 15, 2026 6:03pm | Jul 15, 2026 6:04pm | Jul 15, 2026 6:05pm | Jul 15, 2026 6:05pm | Jul 15, 2026 6:05pm |  |  | Fair | No | Customer stated that the power was restored
Outage | J.E.26.07.17617 | C001856210 | Oshane Warren | Hanover | Completed | Load_244025 | Orange Bay - 310 | Jul 15, 2026 4:43pm | Jul 16, 2026 7:25am | Jul 16, 2026 8:43am | Jul 16, 2026 8:43am | Jul 16, 2026 10:36am | Jul 16, 2026 10:42am | Jul 16, 2026 10:42am | Jul 16, 2026 10:42am | BrokenWire |  | Fair | No | Reconnected service wire to secondary line used 3pg clamps
Outage | J.E.26.07.14369 | C001856206 | Richard Grant | St.Catherine | Completed | Load_241272 | Rhodens Pen - 410 | Jul 15, 2026 4:41pm | Jul 15, 2026 4:41pm | Jul 15, 2026 5:02pm | Jul 15, 2026 7:02pm | Jul 15, 2026 7:25pm | Jul 15, 2026 7:25pm | Jul 15, 2026 7:25pm | Jul 15, 2026 7:25pm |  |  | Fair | No | Small unit required.
Outage | J.E.26.07.17046 | C001856207 | Damion Reid | Manchester | Completed | Load_293112 | Kendal - 210 | Jul 15, 2026 4:41pm | Jul 15, 2026 4:41pm | Jul 15, 2026 4:44pm | Jul 15, 2026 4:44pm | Jul 15, 2026 5:49pm | Jul 15, 2026 7:21pm | Jul 15, 2026 7:25pm | Jul 15, 2026 7:25pm | Fire |  | SevereWind | No | Blown 3amp fuse found for 25kva transformer cause by dislodge secondary phase an neutral conductor cut tree from line conductor reattach conductor and replace blown fuse
Outage | J.E.26.07.17828 | C001856205 | Barrington Brown | St.James | Completed | Load_261827 | Queens Drive - 710 | Jul 15, 2026 4:39pm | Jul 15, 2026 4:40pm | Jul 15, 2026 8:05pm | Jul 15, 2026 8:05pm | Jul 15, 2026 9:29pm | Jul 15, 2026 9:30pm | Jul 15, 2026 9:30pm | Jul 15, 2026 9:30pm |  |  | Fair | No | Checked and found ok
Non-Outage | J.E.26.07.15790 | C001856203 | Raymond Lewis | St.Ann | Completed | Load_253335 | Roaring River - 410 | Jul 15, 2026 4:38pm | Jul 15, 2026 4:40pm | Jul 15, 2026 6:43pm | Jul 15, 2026 6:44pm | Jul 15, 2026 7:34pm | Jul 15, 2026 7:37pm | Jul 15, 2026 7:37pm | Jul 15, 2026 7:37pm |  |  | Fair | No | Premises found ok voltage 107,
Non-Outage | J.E.26.07.15953 | C001856200 | Raymond Lewis | St.Ann | Completed | Load_318924 | Roaring River - 410 | Jul 15, 2026 4:38pm | Jul 15, 2026 4:40pm | Jul 15, 2026 6:40pm | Jul 15, 2026 6:40pm | Jul 15, 2026 6:40pm | Jul 15, 2026 6:43pm | Jul 15, 2026 6:43pm | Jul 15, 2026 6:43pm |  |  | Fair | No | Customer need to come in office
Non-Outage | J.E.26.07.15998 | C001856201 | Raymond Lewis | St.Ann | Completed | Load_266688 | Roaring River - 210 | Jul 15, 2026 4:38pm | Jul 15, 2026 4:40pm | Jul 15, 2026 7:50pm | Jul 15, 2026 7:50pm | Jul 15, 2026 7:50pm | Jul 15, 2026 7:52pm | Jul 15, 2026 7:52pm | Jul 15, 2026 7:52pm |  |  | Fair | No | Costume say light has restored
Non-Outage | J.E.26.07.16230 | C001856202 | Raymond Lewis | St.Ann | Completed | Load_266688 | Roaring River - 210 | Jul 15, 2026 4:38pm | Jul 15, 2026 4:40pm | Jul 15, 2026 7:37pm | Jul 15, 2026 7:37pm | Jul 15, 2026 7:47pm | Jul 15, 2026 7:49pm | Jul 15, 2026 7:50pm | Jul 15, 2026 7:50pm |  |  | Fair | No | Costume say that the light has restored
Non-Outage | J.E.26.07.17543 | C001856198 | Richard Nicholas | null | Completed | null | null | Jul 15, 2026 4:37pm | Jul 15, 2026 4:42pm | Jul 15, 2026 9:40pm | Jul 15, 2026 9:40pm | Jul 15, 2026 9:40pm | Jul 15, 2026 9:40pm | Jul 15, 2026 9:41pm | Jul 15, 2026 9:41pm | BangingWires |  | EarthMovement | No | Area found ok
Outage | J.E.26.07.17753 | C001856199 | Richard Nicholas | St.Catherine | Completed | Load_252827 | Rhodens Pen - 210 | Jul 15, 2026 4:37pm | Jul 15, 2026 4:42pm | Jul 15, 2026 4:50pm | Jul 15, 2026 4:50pm | Jul 15, 2026 6:58pm | Jul 15, 2026 7:09pm | Jul 15, 2026 7:09pm | Jul 15, 2026 7:09pm |  |  | Fair | No | Not located,more directions information needed.
Outage | J.E.26.07.17783 | C001856197 | Richard Nicholas | St.Catherine | Completed | Load_289897 | Rhodens Pen - 210 | Jul 15, 2026 4:37pm | Jul 15, 2026 4:42pm | Jul 15, 2026 9:41pm | Jul 15, 2026 9:41pm | Jul 15, 2026 10:12pm | Jul 15, 2026 10:46pm | Jul 15, 2026 10:48pm | Jul 15, 2026 10:48pm |  |  | Fair | No | Rammy system account dispute,please refer to the field service department.
Non-Outage | J.E.26.07.17554 | C001856194 | Raymond Carr | St.Mary | Completed | Load_262298 | Oracabessa - 210 | Jul 15, 2026 4:30pm | Jul 15, 2026 4:30pm | Jul 15, 2026 6:16pm | Jul 15, 2026 6:16pm | Jul 15, 2026 6:50pm | Jul 15, 2026 7:10pm | Jul 15, 2026 7:25pm | Jul 15, 2026 7:25pm |  |  | Fair | No | Defective clamp was replaced at pothead. Voltage readings 114/116/230.
Non-Outage | J.E.26.07.17258 | C001856188 | Romeo Brissett | null | Completed | null | null | Jul 15, 2026 4:28pm | Jul 15, 2026 4:29pm | Jul 15, 2026 4:51pm | Jul 15, 2026 4:51pm | Jul 15, 2026 5:26pm | Jul 15, 2026 7:22pm | Jul 15, 2026 7:30pm | Jul 15, 2026 7:30pm | BrokenWire | Y | Fair | No | Isolated (1)50 kva transformer, cut tree from line, spliced and retention 2 span of secondary. Used 50ft of 2/0 conductor (2)2/0 sleeve, (2)2/0 and 4 clamps.
Outage | J.E.26.07.17334 | C001856186 | Raymond Carr | St.Mary | Completed | Load_256845 | Blackstonedge - 110 | Jul 15, 2026 4:28pm | Jul 15, 2026 4:29pm | Jul 15, 2026 7:49pm | Jul 15, 2026 7:49pm | Jul 15, 2026 8:10pm | Jul 15, 2026 8:05pm | Jul 15, 2026 8:11pm | Jul 15, 2026 8:11pm |  |  | Fair | No | Customer reported that supply was restored earlier today.
Outage | J.E.26.07.17376 | C001856185 | Raymond Carr | St.Mary | Completed | Load_253640 | Oracabessa - 110 | Jul 15, 2026 4:28pm | Jul 15, 2026 4:29pm | Jul 15, 2026 7:29pm | Jul 15, 2026 7:29pm | Jul 15, 2026 7:40pm | Jul 15, 2026 9:00pm | Jul 15, 2026 7:49pm | Jul 15, 2026 7:49pm |  |  | Fair | No | No fire seen at this time.. Supply found okay.
Outage | J.E.26.07.17522 | C001856187 | Wan Carlos Scarlett | St.Catherine | Completed | Load_1000347 | Twickenham - 210 | Jul 15, 2026 4:28pm | Jul 15, 2026 4:42pm | Jul 15, 2026 5:13pm | Jul 15, 2026 5:47pm | Jul 15, 2026 6:11pm | Jul 15, 2026 6:23pm | Jul 15, 2026 6:23pm | Jul 15, 2026 6:23pm |  |  | Fair | No | Customer confirm that power supply has been restored
Outage | J.E.26.07.17509 | C001856184 | Raymond Carr | St.Mary | Completed | Load_268948 | Oracabessa - 210 | Jul 15, 2026 4:27pm | Jul 15, 2026 4:29pm | Jul 15, 2026 4:38pm | Jul 15, 2026 4:38pm | Jul 15, 2026 5:32pm | Jul 15, 2026 6:00pm | Jul 15, 2026 6:14pm | Jul 15, 2026 6:14pm |  |  | Fair | No | Blown junction fuse found, also 25 kva transformer in gully found blown. Line patrol okay however tree contact was suspected. A 10 amp fuse fuse for junction, plus a 3 amp fuse for transformer. Supply was restored.
Outage | J.E.26.07.17392 | C001856183 | Evan Spaulding | St.Mary | Completed | Load_260682 | Highgate - 210 | Jul 15, 2026 4:26pm | Jul 15, 2026 4:27pm | Jul 15, 2026 5:02pm | Jul 15, 2026 5:02pm | Jul 15, 2026 5:15pm | Jul 15, 2026 5:31pm | Jul 15, 2026 5:31pm | Jul 15, 2026 5:31pm |  |  | Fair | No | Disconnection
Outage | J.E.26.07.17496 | C001856182 | Evan Spaulding | St.Mary | Completed | Load_252445 | Highgate - 210 | Jul 15, 2026 4:26pm | Jul 15, 2026 4:27pm | Jul 15, 2026 5:31pm | Jul 15, 2026 5:31pm | Jul 15, 2026 6:29pm | Jul 15, 2026 8:40pm | Jul 15, 2026 8:42pm | Jul 15, 2026 8:42pm |  |  | Fair | No | Use 2-1 bolt clamps and 5 ft #2 AAAC conductor to jumper out neutral conductor mid span,117v,114v,231v.
Outage | J.E.26.07.17507 | C001856181 | Evan Spaulding | St.Mary | Completed | Load_266718 | Highgate -110 | Jul 15, 2026 4:26pm | Jul 15, 2026 4:27pm | Jul 15, 2026 8:44pm | Jul 15, 2026 8:44pm | Jul 15, 2026 9:09pm | Jul 15, 2026 10:30pm | Jul 15, 2026 10:31pm | Jul 15, 2026 10:31pm |  | Y | Fair | No | Cut tree off primary line and replace 1-10amps junction fuse at pole number 0005426.
Non-Outage | J.E.26.07.16240 | C001856179 | Ryan Richards | Manchester | Completed | Load_265753 | Spur Tree - 310 | Jul 15, 2026 4:23pm | Jul 15, 2026 4:24pm | Jul 15, 2026 6:37pm | Jul 15, 2026 6:37pm | Jul 15, 2026 7:49pm | Jul 15, 2026 8:43pm | Jul 15, 2026 8:43pm | Jul 15, 2026 8:43pm |  |  | Fair | No | Burn lower drop lead and corroded neutral lead found open 25 kva transformer replaced drop lead using 4ft#2/0 copper 2#2/0 ampac and reclose transformer voltage 119/120/240 all customers are now with supply
Outage | J.E.26.07.17238 | C001856178 | Ryan Richards | Manchester | Completed | Load_260536 | Spur Tree - 210 | Jul 15, 2026 4:23pm | Jul 15, 2026 4:24pm | Jul 15, 2026 4:37pm | Jul 15, 2026 4:50pm | Jul 15, 2026 6:01pm | Jul 15, 2026 6:37pm | Jul 15, 2026 6:37pm | Jul 15, 2026 6:37pm | BrokenWire |  | Fair | No | Area found ok customer that made report his unable to locate multiple efforts made to contact customer but unsuccessful
Outage | J.E.26.07.17474 | C001856176 | Wayne Dillion | St.Elizabeth | Completed | Load_292423 | Maggotty - 110 | Jul 15, 2026 4:21pm | Jul 15, 2026 4:21pm | Jul 15, 2026 5:04pm | Jul 15, 2026 5:04pm | Jul 15, 2026 5:05pm | Jul 15, 2026 5:08pm | Jul 15, 2026 5:08pm | Jul 15, 2026 5:08pm |  |  | Fair | No | Customer said supply ok
Outage | J.E.26.07.17566 | C001856175 | Wayne Dillion | St.Elizabeth | Completed | Load_267948 | Maggotty - 110 | Jul 15, 2026 4:21pm | Jul 15, 2026 4:21pm | Jul 15, 2026 8:25pm | Jul 15, 2026 8:25pm | Jul 15, 2026 8:25pm | Jul 15, 2026 8:49pm | Jul 15, 2026 8:50pm | Jul 15, 2026 8:50pm |  |  | Fair | No | Reconnect customer using 60 feet of number six triplex 3 linket 3 one bolt clamp voltage reading 112v 113v 226v supply working ok
Outage | J.E.26.07.17662 | C001856177 | Romeo Brissett | St.James | Completed | Load_254484 | Bogue - 610 | Jul 15, 2026 4:21pm | Jul 15, 2026 4:22pm | Jul 15, 2026 9:02pm | Jul 15, 2026 9:02pm | Jul 15, 2026 9:47pm | Jul 15, 2026 10:18pm | Jul 15, 2026 10:24pm | Jul 15, 2026 10:24pm |  |  | Fair | No | Found customer service wire disconnected on pole, unable to connect service wire due to defective pole, TA pole found severely rotten at the foot with over head guy pole fallen, pole is swaying wing the wind. Please send to maintenance, one customer found without supply.
Non-Outage | J.E.26.07.17781 | C001856174 | Nickolas Rodriques | null | Completed | null | null | Jul 15, 2026 4:20pm | Jul 15, 2026 4:21pm | Jul 15, 2026 4:35pm | Jul 15, 2026 4:36pm | Jul 15, 2026 5:30pm | Jul 15, 2026 7:12pm | Jul 15, 2026 7:21pm | Jul 15, 2026 7:21pm | BrokenWire |  | Fair | No | Checked and found one pole span of secondary lower phase down caused by slack connection where drop lead is connected to open secondary. Isolate 100 KVA transformer for safety to repair. Repaired by splice and retention wire using 20ft of 2-north aluminum, five one-bolt clamps and replaced the fuse after completing patrol.
Outage | J.E.26.07.13839 | C001856171 | Damion Reid | Manchester | Completed | Load_261772 | Kendal - 210 | Jul 15, 2026 4:20pm | Jul 15, 2026 4:25pm | Jul 15, 2026 9:24pm | Jul 15, 2026 9:24pm | Jul 15, 2026 9:53pm | Jul 15, 2026 10:24pm | Jul 15, 2026 10:24pm | Jul 15, 2026 10:24pm |  |  | Fair | No | Area found ok
Outage | J.E.26.07.14784 | C001856172 | Damion Reid | Manchester | Completed | Load_257714 | Kendal - 210 | Jul 15, 2026 4:20pm | Jul 15, 2026 4:25pm | Jul 15, 2026 7:25pm | Jul 15, 2026 7:25pm | Jul 15, 2026 8:26pm | Jul 15, 2026 8:38pm | Jul 15, 2026 8:41pm | Jul 15, 2026 8:41pm |  |  | Fair | No | Power is at line side of meter none is at the load side voltage reading at meter socket phase to neutral 113v-115v across phase 230v refer to field service
Outage | J.E.26.07.15861 | C001856173 | Damion Reid | Manchester | Completed | Load_256124 | Kendal - 210 | Jul 15, 2026 4:20pm | Jul 15, 2026 4:25pm | Jul 15, 2026 8:41pm | Jul 15, 2026 8:41pm | Jul 15, 2026 9:06pm | Jul 15, 2026 9:24pm | Jul 15, 2026 9:24pm | Jul 15, 2026 9:24pm |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.07.08890 | C001856170 | Stephen Taylor | St.Thomas | Completed | Load_246520 | Lysson - 410 | Jul 15, 2026 4:17pm | Jul 15, 2026 4:17pm | Jul 15, 2026 6:26pm | Jul 15, 2026 6:26pm | Jul 15, 2026 6:26pm | Jul 15, 2026 6:26pm | Jul 15, 2026 6:26pm | Jul 15, 2026 6:26pm |  |  | Fair | No | Premise found okay
Non-Outage | J.E.26.07.09197 | C001856169 | Stephen Taylor | St.Thomas | Completed | Load_256790 | Lysson - 410 | Jul 15, 2026 4:17pm | Jul 15, 2026 4:17pm | Jul 15, 2026 6:24pm | Jul 15, 2026 6:24pm | Jul 15, 2026 6:25pm | Jul 15, 2026 6:25pm | Jul 15, 2026 6:25pm | Jul 15, 2026 6:25pm |  |  | Fair | No | Check with customer and customer said that power is back
Non-Outage | J.E.26.07.10213 | C001856167 | Stephen Taylor | St.Thomas | Completed | Load_266801 | Lysson - 410 | Jul 15, 2026 4:17pm | Jul 15, 2026 4:17pm | Jul 15, 2026 6:32pm | Jul 15, 2026 6:32pm | Jul 15, 2026 6:59pm | Jul 15, 2026 7:00pm | Jul 15, 2026 7:00pm | Jul 15, 2026 7:00pm |  |  | Fair | No | Clean up single phase use 2 clamps reading 111,112,225 customer is now okay
Non-Outage | J.E.26.07.14178 | C001856164 | Stephen Taylor | St.Thomas | Completed | Load_577136 | Lysson - 410 | Jul 15, 2026 4:17pm | Jul 15, 2026 4:17pm | Jul 15, 2026 7:06pm | Jul 15, 2026 7:06pm | Jul 15, 2026 7:06pm | Jul 15, 2026 7:06pm | Jul 15, 2026 7:07pm | Jul 15, 2026 7:07pm |  |  | Fair | No | Clean up single phase use 1 clamp reading 112,113,225 customer is now okay
Non-Outage | J.E.26.07.15080 | C001856166 | Stephen Taylor | St.Thomas | Completed | Load_269082 | Lysson - 410 | Jul 15, 2026 4:17pm | Jul 15, 2026 4:17pm | Jul 15, 2026 5:04pm | Jul 15, 2026 5:04pm | Jul 15, 2026 5:10pm | Jul 15, 2026 5:10pm | Jul 15, 2026 5:12pm | Jul 15, 2026 5:12pm |  |  | Fair | No | Patrol the area power is in the area a lot of call to customer no one answered the phone
Non-Outage | J.E.26.07.15195 | C001856165 | Stephen Taylor | St.Thomas | Completed | Load_262609 | Lysson - 410 | Jul 15, 2026 4:17pm | Jul 15, 2026 4:17pm | Jul 15, 2026 4:43pm | Jul 15, 2026 4:43pm | Jul 15, 2026 4:57pm | Jul 15, 2026 4:58pm | Jul 15, 2026 5:02pm | Jul 15, 2026 5:02pm |  |  | Fair | No | Clean up single phase use 1 Linkeet customer is now okay reading 111,112,223
Non-Outage | J.E.26.07.16019 | C001856161 | Stephen Taylor | St.Thomas | Completed | Load_327665 | Lysson - 410 | Jul 15, 2026 4:17pm | Jul 15, 2026 4:17pm | Jul 15, 2026 9:35pm | Jul 15, 2026 9:35pm | Jul 16, 2026 9:13am | Jul 16, 2026 9:13am | Jul 16, 2026 9:15am | Jul 16, 2026 9:15am |  |  | Fair | No | Need more information a lot of call to customer no one answered the phone
Non-Outage | J.E.26.07.17114 | C001856163 | Stephen Taylor | St.Thomas | Completed | Load_238093 | Lysson - 410 | Jul 15, 2026 4:17pm | Jul 15, 2026 4:17pm | Jul 15, 2026 5:24pm | Jul 15, 2026 5:24pm | Jul 15, 2026 5:24pm | Jul 15, 2026 5:25pm | Jul 15, 2026 5:26pm | Jul 15, 2026 5:26pm | LowHangingWires |  | Fair | No | Customer advice get electrician to fix load side of service wire
Outage | J.E.26.07.17503 | C001856168 | Milton Charlton | KSAS | Completed | Load_568745 | Up Park Camp - 410 | Jul 15, 2026 4:17pm | Jul 15, 2026 4:27pm | Jul 15, 2026 4:37pm | Jul 15, 2026 4:37pm | Jul 15, 2026 5:35pm | Jul 15, 2026 5:30pm | Jul 15, 2026 5:37pm | Jul 15, 2026 5:37pm |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.07.17692 | C001856162 | Milton Charlton | KSAN | Completed | Load_248814 | Hope - 510 | Jul 15, 2026 4:17pm | Jul 15, 2026 4:27pm | Jul 15, 2026 6:13pm | Jul 15, 2026 6:13pm | Jul 15, 2026 6:48pm | Jul 15, 2026 6:05pm | Jul 15, 2026 6:52pm | Jul 15, 2026 6:52pm |  |  | Fair | No | Refused and reclosed 5amps junction at pole#0072810 using one 5amps fuse and reclosed junction switch.
Outage | J.E.26.07.17513 | C001856160 | Christopher Edwards | KSAN | Completed | Load_264240 | Constant Spring - 410 | Jul 15, 2026 4:16pm | Jul 16, 2026 7:28am | Jul 16, 2026 12:44pm | Jul 16, 2026 12:44pm | Jul 16, 2026 1:35pm | Jul 16, 2026 2:31pm | Jul 16, 2026 2:32pm | Jul 16, 2026 2:32pm |  |  | Fair | No | Customer is having an internal problem Voltage at meter pole114,113,230v Customer was advised to get electrician to rectify issue
Non-Outage | J.E.26.07.17770 | C001856158 | Kaydon Taylor | null | Completed | null | null | Jul 15, 2026 4:15pm | Jul 15, 2026 4:16pm | Jul 15, 2026 5:11pm | Jul 15, 2026 5:11pm | Jul 15, 2026 6:01pm | Jul 15, 2026 7:00pm | Jul 15, 2026 7:00pm | Jul 15, 2026 7:00pm | Fire |  | Fair | No | Defective steel rail found. the result of the pole to be extremely leaning towards the gully. Three phase cover conductor wire hangs about 15’ from from ground .Open secondary also needs to be splice and retention. 50kva transformer fuse found blown.
Outage | J.E.26.07.17559 | C001856159 | Elvis Trowers | KSAN | Completed | Load_253886 | Washington Blvd - 510 | Jul 15, 2026 4:15pm | Jul 16, 2026 7:26am | Jul 16, 2026 2:03pm | Jul 16, 2026 2:03pm | Jul 16, 2026 2:03pm | Jul 16, 2026 2:06pm | Jul 16, 2026 2:06pm | Jul 16, 2026 2:06pm | BrokenPole |  | Fair | Yes | Happened to be internal when checked customer was advised to contact an electrician to get the broken pole change, its their private pole.
Outage | J.E.26.07.14609 | C001856153 | Wan Carlos Scarlett | St.Catherine | Completed | Load_270057 | Tredegar - 210 | Jul 15, 2026 4:13pm | Jul 15, 2026 4:19pm | Jul 15, 2026 5:11pm | Jul 15, 2026 7:54pm | Jul 15, 2026 9:12pm | Jul 15, 2026 9:42pm | Jul 15, 2026 9:43pm | Jul 15, 2026 9:43pm | LeaningPole,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Customer confirm that power supply has been restored
Outage | J.E.26.07.17738 | C001856154 | Denton Williams | Portland | Completed | Load_268490 | Port Antonio - 410 | Jul 15, 2026 4:13pm | Jul 15, 2026 4:13pm | Jul 15, 2026 6:35pm | Jul 15, 2026 6:35pm | Jul 15, 2026 6:35pm | Jul 15, 2026 6:36pm | Jul 15, 2026 6:52pm | Jul 15, 2026 6:52pm |  |  | Fair | No | The customer stated that their service line was disconnected from last year. Please refer to field service.
Outage | J.E.26.07.16996 | C001856152 | Ricky Hall | St.Catherine | Completed | Load_249138 | Tredegar - 510 | Jul 15, 2026 4:12pm | Jul 16, 2026 7:25am | Jul 16, 2026 11:00am | Jul 16, 2026 11:01am | Jul 16, 2026 11:19am | Jul 16, 2026 11:23am | Jul 16, 2026 11:23am | Jul 16, 2026 11:23am |  |  | Fair | No | Premises closed
Outage | J.E.26.07.17516 | C001856151 | Wan Carlos Scarlett | St.Catherine | Completed | Load_239901 | Tredegar - 510 | Jul 15, 2026 4:12pm | Jul 15, 2026 4:13pm | Jul 15, 2026 4:18pm | Jul 15, 2026 4:18pm | Jul 15, 2026 5:17pm | Jul 15, 2026 5:39pm | Jul 15, 2026 5:45pm | Jul 15, 2026 5:45pm |  |  | Fair | No | Customer was reconnected from escalation department power supply has been restored
Outage | J.E.26.07.17524 | C001856149 | Denton Williams | Portland | Completed | Load_256491 | Port Antonio - 410 | Jul 15, 2026 4:12pm | Jul 15, 2026 4:13pm | Jul 15, 2026 4:25pm | Jul 15, 2026 4:25pm | Jul 15, 2026 5:00pm | Jul 15, 2026 5:36pm | Jul 15, 2026 5:40pm | Jul 15, 2026 5:40pm |  |  | Fair | No | Defective customer equipment bang together and caused lightning transformer drop lead to burnt off. Use six clamps to carry out repair. 120/120/240/206 volts
Outage | J.E.26.07.17785 | C001856148 | Fitzroy Turner | KSAN | Completed | Load_262237 | Washington Blvd - 310 | Jul 15, 2026 4:12pm | Jul 15, 2026 4:41pm | Jul 15, 2026 9:25pm | Jul 15, 2026 9:25pm | Jul 15, 2026 9:29pm | Jul 15, 2026 9:47pm | Jul 15, 2026 9:48pm | Jul 15, 2026 9:48pm |  |  | Fair | No | Customer premises found with electricity supply
Non-Outage | J.E.25.12.34216 | C001856141 | Tajay Bernard | St.James | Completed | Load_257317 | Bogue - 510 | Jul 15, 2026 3:59pm | Jul 15, 2026 3:59pm | Jul 15, 2026 5:24pm | Jul 15, 2026 5:24pm | Jul 15, 2026 5:24pm | Jul 15, 2026 5:25pm | Jul 15, 2026 5:25pm | Jul 15, 2026 5:25pm |  |  | Fair | No | Customer stated that the issue has been resolved
Non-Outage | J.E.26.02.20611 | C001856138 | Tajay Bernard | St.James | Completed | Load_260871 | Orange Bay - 310 | Jul 15, 2026 3:59pm | Jul 15, 2026 3:59pm | Jul 15, 2026 5:50pm | Jul 15, 2026 6:45pm | Jul 15, 2026 6:45pm | Jul 15, 2026 6:46pm | Jul 15, 2026 6:46pm | Jul 15, 2026 6:46pm |  |  | Fair | No | Area check and found okay unable to locate customer on premises multiple phone call to customer number went unanswered
Non-Outage | J.E.26.02.21295 | C001856140 | Tajay Bernard | St.James | Completed | Load_260871 | Orange Bay - 310 | Jul 15, 2026 3:59pm | Jul 15, 2026 3:59pm | Jul 15, 2026 5:27pm | Jul 15, 2026 5:27pm | Jul 15, 2026 5:27pm | Jul 15, 2026 5:27pm | Jul 15, 2026 5:27pm | Jul 15, 2026 5:27pm |  |  | Fair | No | Customer stated that the issue has been resolved
Non-Outage | J.E.26.02.35655 | C001856139 | Tajay Bernard | St.James | Completed | Load_238713 | Bogue - 510 | Jul 15, 2026 3:59pm | Jul 15, 2026 3:59pm | Jul 15, 2026 5:50pm | Jul 15, 2026 5:53pm | Jul 15, 2026 6:41pm | Jul 15, 2026 6:44pm | Jul 15, 2026 6:44pm | Jul 15, 2026 6:44pm |  |  | Fair | No | Area check and found okay unable to locate customer on premises multiple phone call to customer number went unanswered
Non-Outage | J.E.26.03.36573 | C001856137 | Tajay Bernard | St.James | Completed | Load_238713 | Bogue - 510 | Jul 15, 2026 3:58pm | Jul 15, 2026 3:59pm | Jul 15, 2026 5:50pm | Jul 15, 2026 6:44pm | Jul 15, 2026 6:45pm | Jul 15, 2026 6:45pm | Jul 15, 2026 6:45pm | Jul 15, 2026 6:45pm |  |  | Fair | No | Area check and found okay unable to locate customer on premises multiple phone call to customer number went unanswered
Non-Outage | J.E.26.04.03345 | C001856136 | Tajay Bernard | St.James | Completed | Load_243895 | Bogue - 510 | Jul 15, 2026 3:58pm | Jul 15, 2026 3:59pm | Jul 15, 2026 5:49pm | Jul 15, 2026 5:49pm | Jul 15, 2026 5:49pm | Jul 15, 2026 5:50pm | Jul 15, 2026 5:50pm | Jul 15, 2026 5:50pm |  |  | Fair | No | Customer stated that the issue has been resolved
Outage | J.E.26.07.17295 | C001856128 | Tajay Bernard | Hanover | Completed | Load_261296 | Orange Bay - 310 | Jul 15, 2026 3:45pm | Jul 15, 2026 3:46pm | Jul 15, 2026 3:52pm | Jul 15, 2026 3:52pm | Jul 15, 2026 4:38pm | Jul 15, 2026 5:09pm | Jul 15, 2026 5:17pm | Jul 15, 2026 5:17pm |  |  | Fair | No | Refuse 1 10kva transformer use 2amp fuse
Outage | J.E.26.07.17389 | C001856129 | Tajay Bernard | Hanover | Completed | Load_241841 | Orange Bay - 310 | Jul 15, 2026 3:45pm | Jul 15, 2026 3:46pm | Jul 15, 2026 5:18pm | Jul 15, 2026 5:18pm | Jul 15, 2026 5:19pm | Jul 15, 2026 5:20pm | Jul 15, 2026 5:20pm | Jul 15, 2026 5:20pm |  |  | Fair | No | Related to previous call job # 17295
Outage | J.E.26.07.17693 | C001856126 | Marlon Brown | Trelawny | Completed | Load_246391 | Martha Brae - 210 | Jul 15, 2026 3:44pm | Jul 15, 2026 3:46pm | Jul 15, 2026 3:50pm | Jul 15, 2026 3:50pm | Jul 15, 2026 3:53pm | Jul 15, 2026 3:56pm | Jul 15, 2026 3:56pm | Jul 15, 2026 3:56pm |  |  | Fair | No | Fixed by call center
Non-Outage | J.E.26.07.17271 | C001856124 | Hartley Chin | null | Completed | null | null | Jul 15, 2026 3:40pm | Jul 15, 2026 3:50pm | Jul 15, 2026 4:51pm | Jul 15, 2026 4:51pm | Jul 15, 2026 4:51pm | Jul 15, 2026 4:53pm | Jul 15, 2026 4:55pm | Jul 15, 2026 4:55pm |  |  | Fair | No | Wrong parish. Customer stated that it was Kingston.
Outage | J.E.26.07.17544 | C001856123 | Rayon Foster | Hanover | Completed | Load_240070 | Orange Bay - 210 | Jul 15, 2026 3:40pm | Jul 16, 2026 7:54am | Jul 15, 2026 8:25pm | Jul 15, 2026 8:25pm | Jul 15, 2026 8:25pm | Jul 15, 2026 8:27pm | Jul 15, 2026 8:28pm | Jul 15, 2026 8:28pm |  |  | Fair | No | Customer power supply was restored by emergency team earlier today voltage left on line 116v/115v/331v
Outage | J.E.26.07.17697 | C001856115 | Hartley Chin | Clarendon | Completed | Load_259406 | Parnassus - 310 | Jul 15, 2026 3:38pm | Jul 15, 2026 3:48pm | Jul 15, 2026 4:55pm | Jul 15, 2026 5:26pm | Jul 15, 2026 5:52pm | Jul 15, 2026 5:53pm | Jul 15, 2026 5:53pm | Jul 15, 2026 5:53pm |  |  | Fair | No | Found ok customer as internal issue Defective meter socket
Outage | J.E.26.07.17499 | C001856114 | Fitzroy Turner | KSAS | Completed | Load_256555 | Hunts Bay - 310 | Jul 15, 2026 3:36pm | Jul 15, 2026 3:37pm | Jul 15, 2026 9:48pm | Jul 15, 2026 9:49pm | Jul 15, 2026 10:24pm | Jul 15, 2026 10:24pm | Jul 15, 2026 10:25pm | Jul 15, 2026 10:25pm |  |  | Fair | No | Customer premises close at this time
Non-Outage | J.E.26.07.14672 | C001856105 | Romeo Brissett | St.James | Completed | Load_267492 | Bogue - 610 | Jul 15, 2026 3:29pm | Jul 15, 2026 3:29pm | Jul 15, 2026 10:24pm | Jul 15, 2026 10:24pm | Jul 15, 2026 10:24pm | Jul 15, 2026 10:36pm | Jul 15, 2026 11:09pm | Jul 15, 2026 11:09pm |  |  | Fair | No | Location was checked, V/R 103-105-207
Non-Outage | J.E.26.07.15504 | C001856103 | Romeo Brissett | St.James | Completed | Load_255716 | Bogue - 610 | Jul 15, 2026 3:29pm | Jul 15, 2026 3:29pm | Jul 15, 2026 7:34pm | Jul 15, 2026 9:01pm | Jul 15, 2026 9:01pm | Jul 15, 2026 9:00pm | Jul 15, 2026 9:02pm | Jul 15, 2026 9:02pm |  |  | Fair | No | Customer stated issue was resolved
Non-Outage | J.E.26.07.15551 | C001856104 | Romeo Brissett | St.James | Completed | Load_302163 | Bogue - 610 | Jul 15, 2026 3:29pm | Jul 15, 2026 3:29pm | Jul 15, 2026 3:40pm | Jul 15, 2026 3:40pm | Jul 15, 2026 4:48pm | Jul 15, 2026 4:38pm | Jul 15, 2026 4:50pm | Jul 15, 2026 4:50pm |  |  | Fair | No | Location was patrolled and no wire was found broken. Phone ring to voicemail.
Non-Outage | J.E.26.07.15717 | C001856102 | Romeo Brissett | St.James | Completed | Load_247713 | Bogue - 610 | Jul 15, 2026 3:29pm | Jul 15, 2026 3:29pm | Jul 15, 2026 7:34pm | Jul 15, 2026 7:34pm | Jul 15, 2026 7:49pm | Jul 15, 2026 8:45pm | Jul 15, 2026 8:47pm | Jul 15, 2026 8:47pm |  |  | Fair | No | Found transformer secondary connected to system. Repaired secondary neutral joint, used 1 clamp V/R before 132-100-232 after 116-116-232.
Outage | J.E.26.07.17471 | C001856098 | Tyrese Williams | St.Ann | Completed | Load_244460 | Ocho Rios - 310 | Jul 15, 2026 3:27pm | Jul 15, 2026 3:32pm | Jul 15, 2026 3:57pm | Jul 15, 2026 8:00pm | Jul 15, 2026 8:00pm | Jul 15, 2026 8:03pm | Jul 15, 2026 8:04pm | Jul 15, 2026 8:04pm |  |  | Fair | No | Prem found ok call related to 50amp junction fuse
Outage | J.E.26.07.17545 | C001856101 | Tyrese Williams | St.Ann | Completed | Load_238716 | Ocho Rios - 310 | Jul 15, 2026 3:27pm | Jul 15, 2026 3:32pm | Jul 15, 2026 3:57pm | Jul 15, 2026 7:48pm | Jul 15, 2026 7:56pm | Jul 15, 2026 7:58pm | Jul 15, 2026 8:00pm | Jul 15, 2026 8:00pm |  |  | Fair | No | Premises found ok call related to 50amp junction fuse
Outage | J.E.26.07.17104 | C001856096 | Moses Elliston | St.Catherine | Completed | Load_1001441 | Tredegar - 210 | Jul 15, 2026 3:26pm | Jul 15, 2026 3:26pm | Jul 15, 2026 4:03pm | Jul 15, 2026 4:03pm | Jul 15, 2026 4:03pm | Jul 15, 2026 4:04pm | Jul 15, 2026 4:06pm | Jul 15, 2026 4:06pm |  |  | Fair | No | Customer to add credit to prepaid account with-76.63 kwh
Outage | J.E.26.07.17466 | C001856097 | Tyrese Williams | St.Ann | Completed | Load_269408 | Ocho Rios - 310 | Jul 15, 2026 3:26pm | Jul 15, 2026 3:32pm | Jul 15, 2026 3:57pm | Jul 15, 2026 5:55pm | Jul 15, 2026 6:57pm | Jul 15, 2026 7:48pm | Jul 15, 2026 7:48pm | Jul 15, 2026 7:48pm |  |  | Fair | No | Replace a 50 amp junction fuse at pole
Outage | J.E.26.07.17241 | C001856093 | Swon Miller | St.James | Completed | Load_245091 | Bogue - 310 | Jul 15, 2026 3:21pm | Jul 15, 2026 3:21pm | Jul 15, 2026 3:34pm | Jul 15, 2026 3:35pm | Jul 15, 2026 4:22pm | Jul 20, 2026 5:15am | Jul 15, 2026 5:23pm | Jul 15, 2026 5:23pm |  |  | Fair | No | Found 50 amp junction fuse blown cause by contamination replace 50 amp junction fuse no pole number available
Outage | J.E.26.07.17411 | C001856088 | Swon Miller | St.James | Completed | Load_247062 | Bogue - 310 | Jul 15, 2026 3:21pm | Jul 15, 2026 3:21pm | Jul 15, 2026 5:23pm | Jul 15, 2026 5:23pm | Jul 15, 2026 5:55pm | Jul 28, 2026 7:10am | Jul 15, 2026 7:28pm | Jul 15, 2026 7:28pm |  |  | Fair | No | Check and found customer without supply cause by hurricane M use 15ft#6 triplex 2 linket red to red to carry out repairs voltage found 0.000 voltage left 0.000 plz refer to field service for customer to be reconnected
Outage | J.E.26.07.17435 | C001856087 | Swon Miller | St.James | Completed | Load_576009 | Bogue - 310 | Jul 15, 2026 3:21pm | Jul 15, 2026 3:21pm | Jul 15, 2026 8:31pm | Jul 15, 2026 8:31pm | Jul 15, 2026 8:33pm | Jul 20, 2026 9:10am | Jul 15, 2026 9:10pm | Jul 15, 2026 9:10pm |  |  | Fair | No | Check and found customer without supply contact customer care agent Omar and power supply was restored voltage found 0.000 voltage left 116/116/232
Outage | J.E.26.07.17520 | C001856085 | Horace Malcolm | St.James | Completed | Load_251673 | Bogue - 310 | Jul 15, 2026 3:21pm | Jul 16, 2026 11:08am | Jul 16, 2026 11:26am | Jul 16, 2026 11:50am | Jul 16, 2026 1:37pm | Jul 16, 2026 1:50pm | Jul 16, 2026 1:50pm | Jul 16, 2026 1:50pm | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Unable to locate premises from directions given multiple phone calls to customer unavailable
Non-Outage | J.E.26.07.17344 | C001856079 | Floyd Taylor | null | Completed | null | null | Jul 15, 2026 3:16pm | Jul 15, 2026 3:19pm | Jul 15, 2026 3:52pm | Jul 15, 2026 3:52pm | Jul 15, 2026 4:14pm | Jul 15, 2026 4:30pm | Jul 15, 2026 4:31pm | Jul 15, 2026 4:31pm |  |  | Fair | No | Unable to locate or contact customer. Directions poor
Outage | J.E.26.07.17397 | C001856080 | Floyd Taylor | Trelawny | Completed | Load_248121 | Greenwood - 110 | Jul 15, 2026 3:16pm | Jul 15, 2026 3:17pm | Jul 15, 2026 5:29pm | Jul 15, 2026 5:30pm | Jul 15, 2026 7:00pm | Jul 15, 2026 8:15pm | Jul 15, 2026 8:17pm | Jul 15, 2026 8:17pm | BrokenWire |  | Fair | No | Splice and retention customer service wire using 4 penunion. voltage readings left 113,117,232.
Non-Outage | J.E.26.07.17350 | C001856078 | Floyd Taylor | null | Completed | null | null | Jul 15, 2026 3:15pm | Jul 15, 2026 3:19pm | Jul 15, 2026 4:32pm | Jul 15, 2026 4:32pm | Jul 15, 2026 5:23pm | Jul 15, 2026 5:28pm | Jul 15, 2026 5:29pm | Jul 15, 2026 5:29pm |  |  | Fair | No | Customer say issues was resolved
Outage | J.E.26.07.17456 | C001856075 | Marlon Brown | Trelawny | Completed | Load_267431 | Duncans - 210 | Jul 15, 2026 3:15pm | Jul 15, 2026 3:16pm | Jul 15, 2026 4:01pm | Jul 15, 2026 4:01pm | Jul 15, 2026 5:28pm | Jul 15, 2026 6:32pm | Jul 15, 2026 6:32pm | Jul 15, 2026 6:32pm |  |  | Fair | No | Reset 10kva transformer Voltage found noneVoltage leaving 115/115=230
Outage | J.E.26.07.17468 | C001856077 | Marlon Brown | Trelawny | Completed | Load_255782 | Martha Brae - 210 | Jul 15, 2026 3:15pm | Jul 15, 2026 3:16pm | Jul 15, 2026 3:26pm | Jul 15, 2026 3:26pm | Jul 15, 2026 3:44pm | Jul 15, 2026 3:47pm | Jul 15, 2026 3:48pm | Jul 15, 2026 3:48pm |  |  | Fair | No | Fixed by call center.
Outage | J.E.26.07.17472 | C001856076 | Marlon Brown | Trelawny | Completed | Load_268993 | Duncans - 210 | Jul 15, 2026 3:15pm | Jul 15, 2026 3:16pm | Jul 15, 2026 3:57pm | Jul 15, 2026 3:58pm | Jul 15, 2026 3:58pm | Jul 15, 2026 4:01pm | Jul 15, 2026 4:01pm | Jul 15, 2026 4:01pm | BrokenPole |  | Fair | No | Customer report was for a premises in St Catherine not Trelawny.
Outage | J.E.26.07.17514 | C001856066 | Tyrese Williams | St.Ann | Completed | Load_257372 | Ocho Rios - 310 | Jul 15, 2026 3:09pm | Jul 15, 2026 3:32pm | Jul 15, 2026 3:57pm | Jul 15, 2026 8:04pm | Jul 15, 2026 8:35pm | Jul 15, 2026 9:00pm | Jul 15, 2026 9:01pm | Jul 15, 2026 9:01pm | BrokenWire |  | Fair | No | Found a huge tree fell and burst 1 span of primary and secondary line 1 span of primary run back, road way is blocked refer to maintenance bushing required
Non-Outage | J.E.26.07.17416 | C001856057 | Andrae Clarke | Portland | Completed | Load_267156 | Port Antonio - 410 | Jul 15, 2026 2:59pm | Jul 15, 2026 2:59pm | Jul 16, 2026 12:13pm | Jul 16, 2026 12:39pm | Jul 16, 2026 1:00pm | Jul 16, 2026 2:13pm | Jul 16, 2026 2:11pm | Jul 16, 2026 2:11pm |  |  | Fair | No | Repair burnt wires using three one bolt clamp and tape Check voltage 119/122/241Repair burnt clamps on transformer neutral Premises now okay
Non-Outage | J.E.26.07.17438 | C001856058 | Andrae Clarke | Portland | Completed | Load_263601 | Port Antonio - 310 | Jul 15, 2026 2:59pm | Jul 15, 2026 2:59pm | Jul 16, 2026 9:45am | Jul 16, 2026 9:45am | Jul 16, 2026 9:54am | Jul 16, 2026 9:59am | Jul 16, 2026 9:57am | Jul 16, 2026 9:57am |  |  | Fair | No | Refer to maintenance#2 wire oxidized needs to be changed 117/115 223
Outage | J.E.26.07.17233 | C001856053 | Rayon Foster | Hanover | Completed | Load_243094 | Orange Bay - 210 | Jul 15, 2026 2:52pm | Jul 16, 2026 7:51am | Jul 15, 2026 8:25pm | Jul 15, 2026 8:28pm | Jul 15, 2026 8:28pm | Jul 15, 2026 8:28pm | Jul 15, 2026 8:29pm | Jul 15, 2026 8:29pm |  |  | Fair | No | Customer power supply was restored by emergency team earlier today voltage left on line 116v/115v/331v
Non-Outage | J.E.26.07.09676 | C001856042 | Odaine Johnson | Clarendon | Completed | Load_248117 | Parnassus - 210 | Jul 15, 2026 2:42pm | Jul 15, 2026 2:42pm | Jul 15, 2026 2:59pm | Jul 15, 2026 2:59pm | Jul 15, 2026 3:10pm | Jul 15, 2026 3:11pm | Jul 15, 2026 3:12pm | Jul 15, 2026 3:12pm |  |  | Fair | No | Transformer drop leads corroded at bank of 2, switching needed
Outage | J.E.26.07.17452 | C001856041 | Raymond Carr | St.Mary | Completed | Load_262786 | Blackstonedge - 110 | Jul 15, 2026 2:41pm | Jul 15, 2026 4:36pm | Jul 15, 2026 8:11pm | Jul 15, 2026 8:11pm | Jul 15, 2026 8:27pm | Jul 15, 2026 8:26pm | Jul 15, 2026 8:29pm | Jul 15, 2026 8:29pm | BrokenWire |  | Fair | No | Due to no driving access to NWT pump, and poor visibility. Daytime attention is needed.
Non-Outage | J.E.26.07.11092 | C001856039 | Jermaine Williams | Clarendon | Completed | Load_263787 | May Pen - 110 | Jul 15, 2026 2:39pm | Jul 15, 2026 2:41pm | Jul 16, 2026 8:24am | Jul 16, 2026 8:24am | Jul 16, 2026 9:20am | Jul 16, 2026 9:20am | Jul 16, 2026 9:21am | Jul 16, 2026 9:21am | BrokenWire | Y | Fair | No | Isolate 10amp junction fuse to cut danger trees.
Non-Outage | J.E.26.07.17023 | C001856037 | Omar King | St.Ann | Completed | Load_266401 | Cardiff Hall - 210 | Jul 15, 2026 2:36pm | Jul 15, 2026 2:37pm | Jul 15, 2026 6:02pm | Jul 15, 2026 6:03pm | Jul 15, 2026 6:45pm | Jul 15, 2026 6:46pm | Jul 15, 2026 6:46pm | Jul 15, 2026 6:46pm |  |  | Fair | No | Unable to find customer call several times no answer directions not sufficient
Non-Outage | J.E.26.07.17235 | C001856036 | Omar King | St.Ann | Completed | Load_556862 | Cardiff Hall - 210 | Jul 15, 2026 2:36pm | Jul 15, 2026 2:37pm | Jul 15, 2026 9:51pm | Jul 15, 2026 9:51pm | Jul 15, 2026 10:54pm | Jul 15, 2026 10:54pm | Jul 15, 2026 10:55pm | Jul 15, 2026 10:55pm |  |  | Fair | No | Unable to find customer call several times no answer directions not sufficient
Non-Outage | J.E.26.07.17414 | C001856038 | Omar King | St.Ann | Completed | Load_264076 | Cardiff Hall - 210 | Jul 15, 2026 2:36pm | Jul 15, 2026 2:37pm | Jul 15, 2026 4:08pm | Jul 15, 2026 4:12pm | Jul 15, 2026 5:29pm | Jul 15, 2026 6:02pm | Jul 15, 2026 6:02pm | Jul 15, 2026 6:02pm | LowHangingWires |  | Fair | No | Found customer stantion defective I advise customer to I advise to replace
Outage | J.E.26.07.17467 | C001856019 | Hartley Chin | Clarendon | Completed | Load_269321 | May Pen - 210 | Jul 15, 2026 2:16pm | Jul 15, 2026 3:48pm | Jul 15, 2026 4:31pm | Jul 15, 2026 4:31pm | Jul 15, 2026 4:38pm | Jul 15, 2026 4:51pm | Jul 15, 2026 4:51pm | Jul 15, 2026 4:51pm | Fire |  | SevereWind | No | Found open secondary conductor was banging during heavy wind. Used spacer .
Outage | J.E.26.07.17461 | C001856016 | Richman Whyte | Hanover | Completed | Load_238992 | Orange Bay - 310 | Jul 15, 2026 2:12pm | Jul 15, 2026 2:14pm | Jul 15, 2026 2:31pm | Jul 15, 2026 2:31pm | Jul 15, 2026 3:45pm | Jul 15, 2026 3:49pm | Jul 15, 2026 3:54pm | Jul 15, 2026 3:54pm |  |  | Fair | No | Reconnect customer after hurricane use 30ft #6 triplex service wire voltage 113 115 230
Outage | J.E.26.07.17412 | C001855999 | Ricky Hall | St.Catherine | Completed | Load_263727 | Tredegar - 210 | Jul 15, 2026 1:48pm | Jul 15, 2026 2:05pm | Jul 15, 2026 2:11pm | Jul 15, 2026 2:11pm | Jul 15, 2026 2:33pm | Jul 15, 2026 3:02pm | Jul 15, 2026 3:06pm | Jul 15, 2026 3:06pm | BrokenWire |  | Fair | No | Defective 30’c6 DV secondary pole intersection of homestead blvd&dupont dr slack span sagging terribly gashes when wind blows heavily please have the same replaced
Outage | J.E.26.07.17226 | C001855954 | Richard Grant | St.Catherine | Completed | Load_257901 | New Michelton - 410 | Jul 15, 2026 1:08pm | Jul 15, 2026 3:42pm | Jul 15, 2026 5:01pm | Jul 15, 2026 5:02pm | Jul 15, 2026 6:11pm | Jul 15, 2026 7:02pm | Jul 15, 2026 7:02pm | Jul 15, 2026 7:02pm |  | Y | Fair | No | 20amps and 10d amps fuse found blown at separate single phase junction poles 053364 & 598153, respectively, caused by jps bushing contractor. Fuses replaced with same size fuses (10d replaced with 10k amps fuse) placed back at respective junction switches. Supply restored and area left okay.
Outage | J.E.26.07.17314 | C001855951 | Kemark Slue | St.Catherine | Completed | Load_239332 | New Michelton - 210 | Jul 15, 2026 1:07pm | Jul 16, 2026 7:25am | Jul 16, 2026 9:23am | Jul 16, 2026 9:23am | Jul 16, 2026 9:44am | Jul 16, 2026 9:00am | Jul 16, 2026 9:57am | Jul 16, 2026 9:57am | BrokenPole |  | Fair | No | Upon arrival at the location the crew discovered that a 30 ft cl 6 secondary DE pole is 98% rotten and leaning towards the main road, pole consisting of #2 triplex secondary and a #6 triplex service, please refer to A. Murray to effectively carry out repairs.
Non-Outage | J.E.26.07.17042 | C001855948 | Tyrese Williams | St.Ann | Completed | Load_246719 | Ocho Rios - 310 | Jul 15, 2026 1:02pm | Jul 16, 2026 3:36pm | Jul 16, 2026 4:27pm | Jul 16, 2026 4:35pm | Jul 16, 2026 5:35pm | Jul 16, 2026 6:00pm | Jul 16, 2026 6:00pm | Jul 16, 2026 6:00pm |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.07.17285 | C001855942 | Milton Charlton | KSAN | Completed | Load_243463 | Hope - 510 | Jul 15, 2026 12:56pm | Jul 15, 2026 12:57pm | Jul 15, 2026 1:01pm | Jul 15, 2026 1:53pm | Jul 15, 2026 1:57pm | Jul 15, 2026 2:05pm | Jul 15, 2026 2:01pm | Jul 15, 2026 2:01pm |  |  | Fair | No | Reconnect customer meter that was disconnected. Reconnection was done by JPS escalation.
Outage | J.E.26.07.17262 | C001855940 | Milton Charlton | KSAN | Completed | Load_572112 | Hope - 410 | Jul 15, 2026 12:55pm | Jul 15, 2026 12:56pm | Jul 15, 2026 1:01pm | Jul 15, 2026 1:02pm | Jul 15, 2026 1:48pm | Jul 15, 2026 1:40pm | Jul 15, 2026 1:51pm | Jul 15, 2026 1:51pm |  |  | Fair | No | Found okay upon arrival. Customer has an internal problem. Readings at meter socket 117-117-235 volts.
Outage | J.E.26.07.17284 | C001855941 | Elvis Trowers | KSAS | Completed | Load_248011 | Duhaney - 310 | Jul 15, 2026 12:55pm | Jul 15, 2026 12:56pm | Jul 15, 2026 1:52pm | Jul 15, 2026 1:52pm | Jul 15, 2026 1:54pm | Jul 15, 2026 2:22pm | Jul 15, 2026 2:22pm | Jul 15, 2026 2:22pm | BrokenWire |  | Fair | Yes | Reconnect dislodged twisted wire phase on pole with one clamp, voltage when checked was left at 118+117=235 volts.
Outage | J.E.26.07.17304 | C001855938 | Kaydon Taylor | KSAN | Completed | Load_255998 | Washington Blvd - 610 | Jul 15, 2026 12:53pm | Jul 15, 2026 4:16pm | Jul 15, 2026 8:22pm | Jul 15, 2026 9:11pm | Jul 15, 2026 9:51pm | Jul 15, 2026 9:52pm | Jul 15, 2026 9:53pm | Jul 15, 2026 9:53pm | BrokenWire |  | Fair | No | Broken wire at bamboo lodge Irish town. Daylight attention required
Outage | J.E.26.07.17239 | C001855935 | Oshane Warren | Westmoreland | Completed | Load_292373 | Paradise - 310 | Jul 15, 2026 12:52pm | Jul 15, 2026 12:52pm | Jul 15, 2026 1:01pm | Jul 15, 2026 1:01pm | Jul 15, 2026 2:39pm | Jul 15, 2026 2:42pm | Jul 15, 2026 2:44pm | Jul 15, 2026 2:44pm | BrokenWire |  | Rains | No | Replace 10 amp junction fuse heavy equipment working in the area suspect make in contact with the pole
Outage | J.E.26.07.17135 | C001855929 | Richard Samuda | Manchester | Completed | Load_266332 | Porus - 310 | Jul 15, 2026 12:49pm | Jul 15, 2026 12:51pm | Jul 15, 2026 1:01pm | Jul 15, 2026 1:19pm | Jul 15, 2026 1:42pm | Jul 15, 2026 2:08pm | Jul 15, 2026 2:12pm | Jul 15, 2026 2:12pm | BrokenPole |  | SevereWind | No | Ref call broken 40ft TA transformer pole broken by tractor Clearing land broken pole and damaged 25kva transformer over50 customer affected and customer doesn’t want to give information and tractor driver getting voicearous. Tractor is still on seen
Outage | J.E.26.07.17287 | C001855926 | Kenroy Dale | Manchester | Completed | Load_266526 | Porus - 310 | Jul 15, 2026 12:48pm | Jul 16, 2026 7:32am | Jul 16, 2026 9:37am | Jul 16, 2026 9:37am | Jul 16, 2026 10:06am | Jul 16, 2026 10:28am | Jul 16, 2026 10:36am | Jul 16, 2026 10:36am |  |  | Fair | No | Service wire from customer home to the meter pole defective customer was advised to get an electrician to replace defective wire before we can reconnect supply
Outage | J.E.26.07.17078 | C001855925 | Selvin White | St.Elizabeth | Completed | Load_265047 | Maggotty - 110 | Jul 15, 2026 12:47pm | Jul 15, 2026 12:47pm | Jul 15, 2026 1:07pm | Jul 15, 2026 1:42pm | Jul 15, 2026 1:42pm | Jul 15, 2026 1:45pm | Jul 15, 2026 1:45pm | Jul 15, 2026 1:45pm |  |  | Fair | No | Location complaint order was generated by Simone Bicarie for field service department technician to visit the premises already.
Non-Outage | J.E.26.07.17248 | C001855923 | Jermaine Williams | null | Completed | null | null | Jul 15, 2026 12:45pm | Jul 15, 2026 12:45pm | Jul 15, 2026 1:37pm | Jul 15, 2026 1:37pm | Jul 15, 2026 1:37pm | Jul 15, 2026 2:48pm | Jul 15, 2026 2:51pm | Jul 15, 2026 2:51pm | BangingWires |  | SevereWind | No | Single pole tripped at substation caused by badly leaning pole and banging wires on main line, N McLean was advised .
Non-Outage | J.E.26.07.17097 | C001855912 | Christopher Edwards | KSAN | Completed | Load_253819 | Constant Spring - 410 | Jul 15, 2026 12:42pm | Jul 16, 2026 7:58am | Jul 16, 2026 11:44am | Jul 16, 2026 11:44am | Jul 16, 2026 12:22pm | Jul 16, 2026 12:39pm | Jul 16, 2026 12:44pm | Jul 16, 2026 12:44pm | BrokenPole |  | Fair | No | Rotten 30 ft wood pole Consist of2/0 twisted wirePole is leaning extremely towards customer housePole needs to be changed Supply is in the areaVisit this location multiple times for the same rotten pole issue
Outage | J.E.26.07.15628 | C001855910 | Hartley Chin | Clarendon | Completed | Load_251963 | May Pen - 110 | Jul 15, 2026 12:35pm | Jul 15, 2026 12:36pm | Jul 15, 2026 2:00pm | Jul 15, 2026 2:00pm | Jul 15, 2026 2:05pm | Jul 15, 2026 3:27pm | Jul 15, 2026 3:28pm | Jul 15, 2026 3:28pm |  |  | Fair | No | Replace 250 ft # 2 triplex
Outage | J.E.26.07.17238 | C001855894 | Andrew Powell | Manchester | Completed | Load_260536 | Spur Tree - 210 | Jul 15, 2026 12:20pm | Jul 15, 2026 12:21pm | Jul 15, 2026 12:27pm | Jul 15, 2026 12:27pm | Jul 15, 2026 12:27pm | Jul 15, 2026 12:28pm | Jul 15, 2026 12:28pm | Jul 15, 2026 12:28pm | BrokenWire |  | Fair | No | Manchester called
Outage | J.E.26.07.17296 | C001855893 | Roxroy Needham | null | Completed | Load_243438 | Cardiff Hall - 310 | Jul 15, 2026 12:20pm | Jul 15, 2026 12:20pm | Jul 15, 2026 12:34pm | Jul 15, 2026 12:39pm | Jul 15, 2026 1:20pm | Jul 15, 2026 1:21pm | Jul 15, 2026 1:21pm | Jul 15, 2026 1:21pm | BrokenWire |  | Fair | No | Premises not found not getting customer on Phone
Non-Outage | J.E.26.07.17068 | C001855883 | Collin Robinson | Portland | Completed | Load_268898 | Port Antonio - 310 | Jul 15, 2026 12:10pm | Jul 15, 2026 12:10pm | Jul 15, 2026 12:13pm | Jul 15, 2026 12:13pm | Jul 15, 2026 1:41pm | Jul 15, 2026 1:43pm | Jul 15, 2026 2:13pm | Jul 15, 2026 2:13pm |  |  | Fair | No | Change corroded one bolt clamp at pothead Voltage reading 115v 115v 230v
Non-Outage | J.E.26.07.17117 | C001855884 | Andrae Clarke | Portland | Completed | Load_243136 | Port Antonio - 410 | Jul 15, 2026 12:10pm | Jul 15, 2026 12:11pm | Jul 15, 2026 12:30pm | Jul 15, 2026 12:34pm | Jul 15, 2026 12:49pm | Jul 15, 2026 12:57pm | Jul 15, 2026 12:54pm | Jul 15, 2026 12:54pm |  |  | Fair | No | Premises found ok118/122/240 customer needs to get an electrician to check inside
Outage | J.E.26.07.17269 | C001855882 | Dwayne Samuels | Trelawny | Completed | Load_262472 | Greenwood - 110 | Jul 15, 2026 12:10pm | Jul 15, 2026 12:10pm | Jul 15, 2026 1:15pm | Jul 15, 2026 1:15pm | Jul 15, 2026 1:18pm | Jul 15, 2026 1:30pm | Jul 15, 2026 1:30pm | Jul 15, 2026 1:30pm | Fire |  | Fair | No | Check and found area ok, Unable reach customer to fine her meter….
Outage | J.E.26.07.17220 | C001855881 | Dwain Samuels | Westmoreland | Completed | Load_238013 | Paradise - 110 | Jul 15, 2026 12:09pm | Jul 15, 2026 12:11pm | Jul 15, 2026 12:14pm | Jul 15, 2026 12:14pm | Jul 15, 2026 12:14pm | Jul 15, 2026 12:20pm | Jul 15, 2026 12:22pm | Jul 15, 2026 12:22pm |  |  | Fair | No | Connected 3 wire meter use 3 one bolt clamp
Non-Outage | J.E.26.07.17222 | C001855861 | Andre Williams | Trelawny | Completed | Load_247755 | Martha Brae - 210 | Jul 15, 2026 11:48am | Jul 15, 2026 11:48am | Jul 15, 2026 12:02pm | Jul 15, 2026 12:56pm | Jul 15, 2026 1:52pm | Jul 15, 2026 2:58pm | Jul 15, 2026 3:10pm | Jul 15, 2026 3:10pm |  |  | Fair | No | Re wire pothead on Jps side 113+113=226/108 volts
Non-Outage | J.E.26.07.14869 | C001855860 | Dwayne Samuels | Trelawny | Completed | Load_249410 | Greenwood - 210 | Jul 15, 2026 11:47am | Jul 15, 2026 11:48am | Jul 15, 2026 1:39pm | Jul 15, 2026 1:39pm | Jul 15, 2026 2:08pm | Jul 15, 2026 2:47pm | Jul 15, 2026 2:47pm | Jul 15, 2026 2:47pm |  |  | Fair | No | Voltage found at customer meter was 201v 202 voltage found at transformer is 116v 117v 233v after further checks and removing some illegal connections voltage at customer meter is now 110v 109v 119v customer is also at the end of the Jps line.
Outage | J.E.26.07.17213 | C001855854 | Cliton Henry | St.Mary | Completed | Load_261992 | Blackstonedge - 110 | Jul 15, 2026 11:43am | Jul 15, 2026 11:43am | Jul 15, 2026 12:39pm | Jul 15, 2026 12:40pm | Jul 15, 2026 1:40pm | Jul 15, 2026 2:33pm | Jul 15, 2026 2:37pm | Jul 15, 2026 2:37pm |  |  | Fair | No | A blown 20 amp junction fuse found at Derry crossing due to a clearance breach at Top Derry . The primary phase conductor was ret using 2 #2 preform. Supply restored using 1-20 amp fuse.
Outage | J.E.26.07.17163 | C001855838 | Nickolas Rodriques | Portmore | Completed | Load_260597 | Naggo Head - 610 | Jul 15, 2026 11:25am | Jul 15, 2026 4:44pm | Jul 15, 2026 8:24pm | Jul 15, 2026 8:25pm | Jul 15, 2026 9:00pm | Jul 15, 2026 9:25pm | Jul 15, 2026 9:29pm | Jul 15, 2026 9:29pm | BrokenPole |  | Fair | No | Checked and found a 30 ft wooden pole rotten and leading towards customer house. It’s a (T) pole which consists of open secondary, two guy wires and customer service wire. Refer to maintenance.
Outage | J.E.26.07.17212 | C001855836 | Michael Christian | St.James | Completed | Load_301741 | Bogue - 310 | Jul 15, 2026 11:24am | Jul 15, 2026 11:24am | Jul 15, 2026 1:56pm | Jul 15, 2026 1:56pm | Jul 15, 2026 2:37pm | Jul 15, 2026 2:39pm | Jul 15, 2026 2:39pm | Jul 15, 2026 2:39pm |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.17208 | C001855830 | Milton Charlton | KSAN | Completed | Load_265322 | Hope - 510 | Jul 15, 2026 11:19am | Jul 15, 2026 12:55pm | Jul 15, 2026 1:01pm | Jul 15, 2026 2:03pm | Jul 15, 2026 2:48pm | Jul 15, 2026 2:45pm | Jul 15, 2026 2:50pm | Jul 15, 2026 2:50pm |  |  | Fair | No | Refused and reclosed 2 amps transformer switch at pole #0057375.7
Outage | J.E.26.07.17160 | C001855829 | Michael Christian | St.James | Completed | Load_265607 | Bogue - 310 | Jul 15, 2026 11:17am | Jul 15, 2026 11:18am | Jul 15, 2026 12:43pm | Jul 15, 2026 12:43pm | Jul 15, 2026 1:05pm | Jul 15, 2026 1:11pm | Jul 15, 2026 1:11pm | Jul 15, 2026 1:11pm | BrokenWire |  | Fair | No | E N box send to field service
Outage | J.E.26.07.17172 | C001855828 | Stephen Taylor | St.Thomas | Completed | Load_243194 | Good Year - 210 | Jul 15, 2026 11:15am | Jul 15, 2026 11:16am | Jul 15, 2026 5:31pm | Jul 15, 2026 5:31pm | Jul 15, 2026 5:31pm | Jul 15, 2026 5:31pm | Jul 15, 2026 5:32pm | Jul 15, 2026 5:32pm |  |  | Fair | No | Check with customer and customer say that power is back
Outage | J.E.26.07.17167 | C001855827 | Stephen Taylor | St.Thomas | Completed | Load_241255 | Good Year - 210 | Jul 15, 2026 11:14am | Jul 15, 2026 11:16am | Jul 15, 2026 5:53pm | Jul 15, 2026 5:53pm | Jul 15, 2026 5:53pm | Jul 15, 2026 5:56pm | Jul 15, 2026 5:56pm | Jul 15, 2026 5:56pm |  |  | Fair | No | Need more information a lot of call to customer no one answered the phone
Outage | J.E.26.07.17058 | C001855823 | Daniel Francis | St.Ann | Completed | Load_238582 | Ocho Rios - 310 | Jul 15, 2026 11:12am | Jul 15, 2026 11:13am | Jul 15, 2026 11:25am | Jul 15, 2026 11:25am | Jul 15, 2026 12:05pm | Jul 15, 2026 1:17pm | Jul 15, 2026 1:22pm | Jul 15, 2026 1:22pm |  |  | Fair | No | Contact 110ft of service wire 118 118 236 in all
Outage | J.E.26.07.17154 | C001855822 | Daniel Francis | St.Ann | Completed | Load_245767 | Ocho Rios - 310 | Jul 15, 2026 11:12am | Jul 15, 2026 11:13am | Jul 15, 2026 1:46pm | Jul 15, 2026 1:46pm | Jul 15, 2026 1:59pm | Jul 15, 2026 2:29pm | Jul 15, 2026 2:30pm | Jul 15, 2026 2:30pm |  |  | Fair | No | Change 4 one bolt clamp 119 119 236 in all
Non-Outage | J.E.26.07.14453 | C001855813 | Cliton Henry | St.Mary | Completed | Load_260379 | Oracabessa - 110 | Jul 15, 2026 11:09am | Jul 15, 2026 11:09am | Jul 15, 2026 12:06pm | Jul 15, 2026 12:06pm | Jul 15, 2026 12:28pm | Jul 15, 2026 12:28pm | Jul 15, 2026 12:30pm | Jul 15, 2026 12:30pm |  |  | Fair | No | The customer supply found ok, the voltages found were at pothead 117-119/234 volts
Outage | J.E.26.07.17105 | C001855811 | Elvis Trowers | KSAN | Completed | Load_253886 | Washington Blvd - 510 | Jul 15, 2026 11:05am | Jul 15, 2026 12:54pm | Jul 15, 2026 2:25pm | Jul 15, 2026 2:25pm | Jul 15, 2026 2:49pm | Jul 15, 2026 2:54pm | Jul 15, 2026 2:54pm | Jul 15, 2026 2:54pm | BrokenPole |  | Fair | Yes | Happened to be internal when checked, customers private pole that leads to their appointment that is keeping the up from across the road and is broken, not JPS responsibility, customers were also advised.
Outage | J.E.26.07.17108 | C001855810 | Edward Royal | KSAS | Completed | Load_243865 | Up Park Camp - 410 | Jul 15, 2026 11:05am | Jul 15, 2026 11:19am | Jul 15, 2026 12:42pm | Jul 15, 2026 12:42pm | Jul 15, 2026 2:07pm | Jul 15, 2026 2:16pm | Jul 15, 2026 2:17pm | Jul 15, 2026 2:17pm |  |  | Fair | No | Defective meter need to be change reffered to field service
Non-Outage | J.E.26.07.17004 | C001855802 | Neckell Ormsby | St.Mary | Completed | Load_238714 | Highgate -110 | Jul 15, 2026 11:00am | Jul 15, 2026 11:01am | Jul 16, 2026 11:25am | Jul 16, 2026 11:25am | Jul 16, 2026 11:59am | Jul 16, 2026 12:11pm | Jul 16, 2026 12:11pm | Jul 16, 2026 12:11pm |  |  | Fair | No | Unable to locate customer after several calls also unable to locate gabby rd
Non-Outage | J.E.26.07.17132 | C001855798 | Edward Royal | null | Completed | null | null | Jul 15, 2026 11:00am | Jul 15, 2026 11:00am | Jul 15, 2026 11:30am | Jul 15, 2026 11:30am | Jul 15, 2026 11:51am | Jul 15, 2026 12:41pm | Jul 15, 2026 12:42pm | Jul 15, 2026 12:42pm |  |  | Fair | No | Replaced 2 one bolt clamps voltage reading 117v 116v 232v
Outage | J.E.26.07.17079 | C001855800 | Kenroy Dale | Manchester | Completed | Load_257134 | Kendal - 310 | Jul 15, 2026 11:00am | Jul 16, 2026 7:35am | Jul 16, 2026 7:49am | Jul 16, 2026 7:49am | Jul 16, 2026 9:14am | Jul 16, 2026 9:31am | Jul 16, 2026 9:36am | Jul 16, 2026 9:36am |  |  | Fair | No | Customer have internal problems, customer was advised to get an electrician to check the premises. Voltage reading 113/115/228
Outage | J.E.26.07.17122 | C001855799 | Kenroy Dale | Manchester | Completed | Load_265070 | Kendal - 210 | Jul 15, 2026 11:00am | Jul 15, 2026 12:16pm | Jul 15, 2026 1:02pm | Jul 15, 2026 1:46pm | Jul 15, 2026 2:28pm | Jul 15, 2026 2:52pm | Jul 15, 2026 2:54pm | Jul 15, 2026 2:54pm |  |  | Fair | No | Blown 3 amp transformer fuse for 25 kva transformer, line patrol bamboo found on secondary conductor bamboo was removed and blown fuse replaced area now with supply
Non-Outage | J.E.26.07.17100 | C001855789 | Neckell Ormsby | St.Mary | Completed | Load_253504 | Highgate -110 | Jul 15, 2026 10:59am | Jul 15, 2026 10:59am | Jul 16, 2026 9:50am | Jul 16, 2026 9:50am | Jul 16, 2026 10:21am | Jul 16, 2026 11:04am | Jul 16, 2026 11:06am | Jul 16, 2026 11:06am | Fire |  | Fair | No | Found tree limb on secondary open 25kva transformer to remove limb and retention secondary phase using 1-#2 preform reclose transformer (no pole number seen)
Outage | J.E.26.07.17080 | C001855787 | Neckell Ormsby | St.Mary | Completed | Load_238637 | Highgate - 210 | Jul 15, 2026 10:57am | Jul 15, 2026 10:57am | Jul 15, 2026 12:17pm | Jul 15, 2026 12:17pm | Jul 15, 2026 1:14pm | Jul 15, 2026 1:21pm | Jul 15, 2026 1:21pm | Jul 15, 2026 1:21pm |  |  | Fair | No | Related to previous Esther call
Outage | J.E.26.07.17137 | C001855788 | Andrew Powell | Manchester | Completed | Load_248901 | Spur Tree - 210 | Jul 15, 2026 10:57am | Jul 15, 2026 10:57am | Jul 15, 2026 11:50am | Jul 15, 2026 11:51am | Jul 15, 2026 11:51am | Jul 15, 2026 11:51am | Jul 15, 2026 11:52am | Jul 15, 2026 11:52am | Fire |  | Fair | No | Called related to banging conductor by Exton fault resolved supply restored.
Outage | J.E.26.07.17081 | C001855784 | Selvin White | St.Elizabeth | Completed | Load_305158 | Maggotty - 210 | Jul 15, 2026 10:56am | Jul 15, 2026 11:04am | Jul 15, 2026 11:53am | Jul 15, 2026 12:44pm | Jul 15, 2026 12:56pm | Jul 15, 2026 1:03pm | Jul 15, 2026 1:03pm | Jul 15, 2026 1:03pm | BrokenWire |  | Fair | No | Please refer to C. Johnson and Simone Bicarie as customer needs reconnection to a RAMI system to which only field service department have access to.
Outage | J.E.26.07.17083 | C001855786 | Cliton Henry | St.Mary | Completed | Load_352012 | Oracabessa - 110 | Jul 15, 2026 10:56am | Jul 15, 2026 10:56am | Jul 15, 2026 11:12am | Jul 15, 2026 11:12am | Jul 15, 2026 11:38am | Jul 15, 2026 12:03pm | Jul 15, 2026 12:05pm | Jul 15, 2026 12:05pm |  |  | Fair | No | Voltages found at the metering point were 116-117/233 volts. A dialog the the escalation team revealed that the meter was disconnected. The customer was advised.
Outage | J.E.26.07.17106 | C001855780 | Andrew Powell | Manchester | Completed | Load_269445 | Spur Tree - 210 | Jul 15, 2026 10:55am | Jul 15, 2026 10:56am | Jul 15, 2026 11:03am | Jul 15, 2026 11:03am | Jul 15, 2026 11:16am | Jul 15, 2026 11:49am | Jul 15, 2026 11:50am | Jul 15, 2026 11:50am | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Isolate and close 50 kva transformer circuit to retention two pole span of sagging secondary neutral conductor, no pole number by switch location, restore supply okay.
Outage | J.E.26.07.17107 | C001855782 | Romaine Roberts | St.Mary | Completed | Load_251410 | Annotto Bay - 210 | Jul 15, 2026 10:55am | Jul 15, 2026 10:56am | Jul 15, 2026 12:54pm | Jul 15, 2026 12:54pm | Jul 15, 2026 2:17pm | Jul 15, 2026 2:30pm | Jul 15, 2026 2:32pm | Jul 15, 2026 2:32pm |  |  | Fair | No | Corrosion at customer pothead clan and remake joints voltage 113-114-228
Non-Outage | J.E.26.06.28010 | C001855772 | Kemark Slue | St.Catherine | Completed | Load_238392 | New Michelton - 310 | Jul 15, 2026 10:53am | Jul 15, 2026 10:54am | Jul 15, 2026 1:10pm | Jul 15, 2026 2:26pm | Jul 15, 2026 2:26pm | Jul 15, 2026 2:58pm | Jul 15, 2026 2:58pm | Jul 15, 2026 2:58pm |  |  | Fair | No | Premises was checked and found okay.
Outage | J.E.26.07.17115 | C001855760 | Nickolas Rodriques | St.Catherine | Completed | Load_263069 | Twickenham - 210 | Jul 15, 2026 10:43am | Jul 15, 2026 10:56am | Jul 15, 2026 1:21pm | Jul 15, 2026 1:21pm | Jul 15, 2026 1:39pm | Jul 15, 2026 2:13pm | Jul 15, 2026 2:20pm | Jul 15, 2026 2:20pm | BrokenWire |  | Fair | No | Found customer without electricity due to fire that demolished meter and customer meter wires. Customer repair was done and awaiting a(110) meter. Also please note that no meter was found on the premises.
Outage | J.E.26.07.17090 | C001855757 | Christopher Edwards | KSAN | Completed | Load_255038 | Constant Spring - 410 | Jul 15, 2026 10:38am | Jul 15, 2026 10:38am | Jul 15, 2026 11:18am | Jul 15, 2026 11:18am | Jul 15, 2026 11:57am | Jul 15, 2026 12:44pm | Jul 15, 2026 12:45pm | Jul 15, 2026 12:45pm | BrokenWire |  | Fair | No | Required approximately 130ft #6 service wire to carry out repairs
Outage | J.E.26.07.17075 | C001855755 | Christopher Edwards | KSAN | Completed | Load_259084 | Constant Spring - 410 | Jul 15, 2026 10:35am | Jul 15, 2026 10:38am | Jul 15, 2026 12:45pm | Jul 15, 2026 12:45pm | Jul 15, 2026 3:28pm | Jul 15, 2026 3:51pm | Jul 15, 2026 3:53pm | Jul 15, 2026 3:53pm |  |  | Fair | No | Splice and retention broken open secondary wireUsing:80ft #2 AA conductor (4) #2 preforms(6) one bolt clamps Refuse blown 50 kva transformer Using (1) 5 amps
Outage | J.E.26.07.17103 | C001855756 | Elvis Trowers | KSAS | Completed | Load_248773 | Duhaney - 310 | Jul 15, 2026 10:35am | Jul 15, 2026 10:37am | Jul 15, 2026 12:57pm | Jul 15, 2026 12:57pm | Jul 15, 2026 1:47pm | Jul 15, 2026 1:51pm | Jul 15, 2026 1:51pm | Jul 15, 2026 1:51pm |  |  | Fair | Yes | Happened to be a disconnection when checked out and was reconnected with the assistant of escalation service department.
Outage | J.E.26.07.17028 | C001855725 | Michael Christian | St.James | Completed | Load_244480 | Bogue - 310 | Jul 15, 2026 10:18am | Jul 15, 2026 10:19am | Jul 15, 2026 1:11pm | Jul 15, 2026 1:11pm | Jul 15, 2026 1:46pm | Jul 15, 2026 1:56pm | Jul 15, 2026 1:56pm | Jul 15, 2026 1:56pm |  |  | Fair | No | Internal fault voltage 110 112 223 at pothead
Outage | J.E.26.07.17093 | C001855722 | Neville Spencer | Clarendon | Completed | Load_262048 | May Pen - 110 | Jul 15, 2026 10:13am | Jul 15, 2026 3:47pm | Jul 15, 2026 4:11pm | Jul 15, 2026 4:11pm | Jul 15, 2026 5:43pm | Jul 15, 2026 5:43pm | Jul 15, 2026 5:47pm | Jul 15, 2026 5:47pm | BrokenWire |  | Fair | No | Found ok call resolved.
Non-Outage | J.E.26.07.15665 | C001855719 | Kemark Slue | St.Catherine | Completed | Load_250536 | New Michelton - 410 | Jul 15, 2026 10:10am | Jul 15, 2026 10:11am | Jul 15, 2026 11:45am | Jul 15, 2026 1:39pm | Jul 15, 2026 2:17pm | Jul 15, 2026 2:00pm | Jul 15, 2026 2:26pm | Jul 15, 2026 2:26pm |  |  | Fair | No | Upon arrival at the location the crew discovered that several customers were experiencing high voltage, further troubleshooting revealed that there was a defective clamp along the secondary neutral, jumper the said clamp using two one bolt clamps and approximately 3ft of #2 aaac.
Non-Outage | J.E.26.07.12505 | C001855693 | Royston Montague | St.Catherine | Completed | Load_305202 | Rhodens Pen - 310 | Jul 15, 2026 9:50am | Jul 15, 2026 9:52am | Jul 15, 2026 9:55am | Jul 15, 2026 1:17pm | Jul 15, 2026 2:17pm | Jul 15, 2026 2:17pm | Jul 15, 2026 2:17pm | Jul 15, 2026 2:17pm |  |  | Fair | No | Customer confirmed issue resolved. Please update thanks
Non-Outage | J.E.26.07.13326 | C001855692 | Kemark Slue | St.Catherine | Completed | Load_267145 | New Michelton - 410 | Jul 15, 2026 9:50am | Jul 16, 2026 7:42am | Jul 16, 2026 9:57am | Jul 16, 2026 9:57am | Jul 16, 2026 10:10am | Jul 16, 2026 11:00am | Jul 16, 2026 12:22pm | Jul 16, 2026 12:22pm |  |  | Fair | No | Upon arrival at the location the crew discovered that the customer was experiencing a high voltage base on the reading obtain at customer’s line pothead which was 137,100,237v, further patrol revealed that the lower phase was making contacting with telephone catenary wire, installed a d-iron & spool and anchor phase, leaving a voltage reading of 118,118,236V.
Non-Outage | J.E.26.07.13706 | C001855691 | Royston Montague | St.Catherine | Completed | Load_249216 | Rhodens Pen - 310 | Jul 15, 2026 9:50am | Jul 15, 2026 9:52am | Jul 15, 2026 9:55am | Jul 15, 2026 2:17pm | Jul 15, 2026 3:59pm | Jul 15, 2026 3:59pm | Jul 15, 2026 4:00pm | Jul 15, 2026 4:00pm |  |  | Fair | No | Customer confirmed issue resolved
Non-Outage | J.E.26.07.14103 | C001855690 | Royston Montague | St.Catherine | Completed | Load_239074 | Rhodens Pen - 310 | Jul 15, 2026 9:50am | Jul 15, 2026 9:52am | Jul 15, 2026 9:55am | Jul 15, 2026 1:03pm | Jul 15, 2026 1:13pm | Jul 15, 2026 1:15pm | Jul 15, 2026 1:16pm | Jul 15, 2026 1:16pm |  |  | Fair | No | Customer said her electrician corrected issue. Voltage found 229v 113v 115v
Non-Outage | J.E.26.07.17065 | C001855687 | Neckell Ormsby | null | Completed | null | null | Jul 15, 2026 9:47am | Jul 15, 2026 9:47am | Jul 15, 2026 1:21pm | Jul 15, 2026 1:21pm | Jul 15, 2026 1:35pm | Jul 15, 2026 1:47pm | Jul 15, 2026 1:47pm | Jul 15, 2026 1:47pm | BrokenPole |  | Fair | No | No broken pole seen only leaning 35ft class 6 pole, cv construction carrying primary and secondary pole #0170177 please refer to maintenance department
Non-Outage | J.E.26.07.17053 | C001855686 | Neckell Ormsby | St.Mary | Completed | Load_266718 | Highgate -110 | Jul 15, 2026 9:46am | Jul 15, 2026 9:46am | Jul 15, 2026 1:48pm | Jul 15, 2026 1:48pm | Jul 15, 2026 2:18pm | Jul 15, 2026 2:31pm | Jul 15, 2026 2:50pm | Jul 15, 2026 2:50pm | Fire | Y | Fair | No | Unable to locate customer after several calls however patrol and found danger trees over hanging along line section no fire seen bushing requires
Non-Outage | J.E.26.07.14617 | C001855681 | Royston Montague | St.Catherine | Completed | Load_265022 | New Michelton - 410 | Jul 15, 2026 9:42am | Jul 15, 2026 9:44am | Jul 15, 2026 9:49am | Jul 16, 2026 11:31am | Jul 16, 2026 11:32am | Jul 16, 2026 11:35am | Jul 16, 2026 11:35am | Jul 16, 2026 11:35am |  |  | Fair | No | Faulty joints at completion customer take off point. Same corrected. Voltage found 122v voltage after job completion are 118v . Observed a lot of illegal connections on transformer circuit.
Non-Outage | J.E.26.07.14619 | C001855680 | Royston Montague | St.Catherine | Completed | Load_245855 | New Michelton - 210 | Jul 15, 2026 9:42am | Jul 15, 2026 9:44am | Jul 15, 2026 9:49am | Jul 16, 2026 2:33pm | Jul 16, 2026 2:56pm | Jul 16, 2026 3:41pm | Jul 16, 2026 3:41pm | Jul 16, 2026 3:41pm |  |  | Fair | No | Faulty neutral joint at pothead. Same corrected, voltage 230v 124v 101v , voltage after job completion are 230v 114v 114v
Non-Outage | J.E.26.07.14624 | C001855679 | Royston Montague | St.Catherine | Completed | Load_265022 | New Michelton - 410 | Jul 15, 2026 9:42am | Jul 15, 2026 9:44am | Jul 15, 2026 9:49am | Jul 16, 2026 8:54am | Jul 16, 2026 11:10am | Jul 16, 2026 11:29am | Jul 16, 2026 11:31am | Jul 16, 2026 11:31am |  |  | Fair | No | Faulty neutral joint at customer take off point, same corrected. Voltage voltage found 230v 122v 102v voltage after 230v 118v 108v , I observed a lot of illegal connections on transformer circuit.
Non-Outage | J.E.26.07.14680 | C001855678 | Royston Montague | St.Catherine | Completed | Load_568938 | Twickenham - 310 | Jul 15, 2026 9:41am | Jul 15, 2026 9:44am | Jul 15, 2026 9:49am | Jul 15, 2026 10:55am | Jul 15, 2026 11:39am | Jul 15, 2026 12:05pm | Jul 15, 2026 12:05pm | Jul 15, 2026 12:05pm |  |  | Fair | No | Damage twisted wire #6, same repair. Voltage found 114v voltage after job completion are 229v 114v 114v
Non-Outage | J.E.26.07.14729 | C001855677 | Royston Montague | St.Catherine | Completed | Load_301625 | New Michelton - 210 | Jul 15, 2026 9:41am | Jul 15, 2026 9:44am | Jul 15, 2026 9:49am | Jul 16, 2026 3:41pm | Jul 16, 2026 4:17pm | Jul 16, 2026 4:18pm | Jul 16, 2026 4:18pm | Jul 16, 2026 4:18pm |  |  | Fair | No | Full voltage found. Joints in great condition. 232v 114v 115v customer asked to get an electrician to check load side.
Non-Outage | J.E.26.07.14775 | C001855669 | Donald Cunningham | null | Completed | null | null | Jul 15, 2026 9:33am | Jul 15, 2026 9:44am | Jul 15, 2026 11:07am | Jul 15, 2026 11:07am | Jul 15, 2026 11:58am | Jul 15, 2026 11:58am | Jul 15, 2026 12:23pm | Jul 15, 2026 12:23pm | Fire |  | Fair | No | Issues already resolved there was banging conductors in area and tree on lines same removed and wire retention
Non-Outage | J.E.26.07.14779 | C001855668 | Donald Cunningham | null | Completed | null | null | Jul 15, 2026 9:33am | Jul 15, 2026 9:44am | Jul 15, 2026 11:09am | Jul 15, 2026 12:26pm | Jul 15, 2026 12:41pm | Jul 15, 2026 12:43pm | Jul 15, 2026 12:44pm | Jul 15, 2026 12:44pm | Fire |  | Fair | No | No fire seen
Outage | J.E.26.07.17030 | C001855667 | Selvin White | St.Elizabeth | Completed | Load_255287 | Maggotty - 110 | Jul 15, 2026 9:32am | Jul 15, 2026 9:33am | Jul 15, 2026 11:04am | Jul 15, 2026 11:04am | Jul 15, 2026 11:26am | Jul 15, 2026 11:53am | Jul 15, 2026 11:53am | Jul 15, 2026 11:53am |  |  | Fair | No | Order was referred to the field service department so premises can be inspected before reconnection can be carried out.
Non-Outage | J.E.26.07.15271 | C001855665 | Ricky Hall | St.Catherine | Completed | Load_238712 | Tredegar - 510 | Jul 15, 2026 9:31am | Jul 15, 2026 9:35am | Jul 15, 2026 10:44am | Jul 15, 2026 10:47am | Jul 15, 2026 11:11am | Jul 15, 2026 11:57am | Jul 15, 2026 11:57am | Jul 15, 2026 11:57am | Fire |  | Fair | No | Splice and retention broken secondary lines use 2 clamps 2 preform
Non-Outage | J.E.26.07.15365 | C001855664 | Ricky Hall | St.Catherine | Completed | Load_556349 | Rhodens Pen - 210 | Jul 15, 2026 9:31am | Jul 15, 2026 9:35am | Jul 15, 2026 11:58am | Jul 15, 2026 11:59am | Jul 15, 2026 12:53pm | Jul 15, 2026 12:54pm | Jul 15, 2026 12:54pm | Jul 15, 2026 12:54pm | Fire |  | Fair | No | Issue resolved by previous crew
Non-Outage | J.E.26.07.16333 | C001855660 | Royston Montague | St.Catherine | Completed | Load_556367 | Rhodens Pen - 210 | Jul 15, 2026 9:30am | Jul 15, 2026 9:35am | Jul 15, 2026 9:39am | Jul 16, 2026 8:53am | Jul 16, 2026 8:53am | Jul 16, 2026 8:54am | Jul 16, 2026 8:54am | Jul 16, 2026 8:54am |  |  | Fair | No | Rami box in area. Please assign to the relevant team thanks.
Non-Outage | J.E.26.07.16471 | C001855659 | Royston Montague | St.Catherine | Completed | Load_258329 | Rhodens Pen - 310 | Jul 15, 2026 9:30am | Jul 15, 2026 9:35am | Jul 15, 2026 9:39am | Jul 15, 2026 12:06pm | Jul 15, 2026 12:57pm | Jul 15, 2026 1:02pm | Jul 15, 2026 1:02pm | Jul 15, 2026 1:02pm |  |  | Fair | No | Faulty joints at pothead. Same corrected. Voltage found 100v 129v voltage after job completion are 112v 112v 229v
Non-Outage | J.E.26.07.16488 | C001855658 | Royston Montague | St.Catherine | Completed | Load_238151 | Twickenham - 310 | Jul 15, 2026 9:30am | Jul 15, 2026 9:35am | Jul 15, 2026 9:39am | Jul 16, 2026 8:16am | Jul 16, 2026 8:35am | Jul 16, 2026 8:37am | Jul 16, 2026 8:37am | Jul 16, 2026 8:37am |  |  | Fair | No | Customer having issue adding credit to prepaid account. Please inform the relevant team thanks.
Non-Outage | J.E.26.07.16943 | C001855654 | Royston Montague | St.Catherine | Completed | Load_261416 | Tredegar - 510 | Jul 15, 2026 9:29am | Jul 15, 2026 9:37am | Jul 15, 2026 9:39am | Jul 15, 2026 10:22am | Jul 15, 2026 10:28am | Jul 15, 2026 10:52am | Jul 15, 2026 10:52am | Jul 15, 2026 10:52am |  |  | Fair | No | Faulty joints at pothead. Same corrected. Voltage found 213v 104v 98v voltage after job completion are 222v 110v 110v
Non-Outage | J.E.26.07.16972 | C001855653 | Royston Montague | St.Catherine | Completed | Load_238151 | Twickenham - 310 | Jul 15, 2026 9:28am | Jul 15, 2026 9:37am | Jul 15, 2026 9:39am | Jul 15, 2026 4:00pm | Jul 15, 2026 5:11pm | Jul 15, 2026 5:11pm | Jul 15, 2026 5:11pm | Jul 15, 2026 5:11pm |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.07.17015 | C001855652 | Royston Montague | St.Catherine | Completed | Load_238151 | Twickenham - 310 | Jul 15, 2026 9:28am | Jul 15, 2026 9:37am | Jul 15, 2026 9:39am | Jul 15, 2026 9:49am | Jul 15, 2026 10:20am | Jul 15, 2026 10:20am | Jul 15, 2026 10:20am | Jul 15, 2026 10:20am |  |  | Fair | No | Customer confirmed issue resolved. Please update thanks.
Non-Outage | J.E.26.07.17034 | C001855650 | Royston Montague | St.Catherine | Completed | Load_246593 | New Michelton - 210 | Jul 15, 2026 9:28am | Jul 15, 2026 9:37am | Jul 15, 2026 9:39am | Jul 16, 2026 11:37am | Jul 16, 2026 12:35pm | Jul 16, 2026 1:06pm | Jul 16, 2026 1:06pm | Jul 16, 2026 1:06pm |  |  | Fair | No | Faulty joints at customer take off point. Same corrected. Voltage found 227v 111v 116v voltage after job completion are 227v 112v 113v
Non-Outage | J.E.26.07.17060 | C001855651 | Royston Montague | St.Catherine | Completed | Load_243611 | New Michelton - 410 | Jul 15, 2026 9:28am | Jul 15, 2026 9:37am | Jul 15, 2026 9:39am | Jul 16, 2026 1:07pm | Jul 16, 2026 2:23pm | Jul 16, 2026 2:32pm | Jul 16, 2026 2:32pm | Jul 16, 2026 2:32pm |  |  | Fair | No | Multiple calls to customer phone go without answer. GPS coordinate on job not working.
Outage | J.E.26.07.17040 | C001855647 | Rusean Allen | KSAS | Completed | Load_254739 | Cane River - 610 | Jul 15, 2026 9:25am | Jul 15, 2026 9:38am | Jul 15, 2026 2:30pm | Jul 15, 2026 2:30pm | Jul 15, 2026 2:30pm | Jul 15, 2026 2:31pm | Jul 15, 2026 2:31pm | Jul 15, 2026 2:31pm | BrokenWire |  | Fair | No | Reconnected wire at pole Use 3 1 bolt clamps
Outage | J.E.26.07.17050 | C001855648 | Fitzroy Turner | KSAS | Completed | Load_292068 | Duhaney - 410 | Jul 15, 2026 9:25am | Jul 15, 2026 5:23pm | Jul 15, 2026 6:09pm | Jul 15, 2026 6:09pm | Jul 15, 2026 6:09pm | Jul 15, 2026 6:10pm | Jul 15, 2026 6:10pm | Jul 15, 2026 6:10pm |  |  | Fair | No | Customer disconnected for none payment of bills
Non-Outage | J.E.26.07.13830 | C001855641 | Nickolas Rodriques | Portmore | Completed | Load_247269 | Naggo Head - 610 | Jul 15, 2026 9:21am | Jul 15, 2026 9:23am | Jul 15, 2026 3:28pm | Jul 15, 2026 3:29pm | Jul 15, 2026 4:01pm | Jul 15, 2026 4:27pm | Jul 15, 2026 4:29pm | Jul 15, 2026 4:29pm | Fire |  | Fair | No | No fire was seen upon arrival. The area was patrolled and no noticeable outage was found.
Non-Outage | J.E.26.07.14458 | C001855640 | Orville Lee | St.Catherine | Completed | Load_250212 | Twickenham - 210 | Jul 15, 2026 9:21am | Jul 15, 2026 9:24am | Jul 15, 2026 10:00am | Jul 15, 2026 10:00am | Jul 15, 2026 10:04am | Jul 15, 2026 10:27am | Jul 15, 2026 10:30am | Jul 15, 2026 10:30am |  |  | Fair | No | Checks made and found pothead and secondary connections corroded Two pen union one 1bolt clamp usedVoltage116V116v234v
Non-Outage | J.E.26.07.14818 | C001855639 | Orville Lee | St.Catherine | Completed | Load_262395 | Twickenham - 210 | Jul 15, 2026 9:20am | Jul 15, 2026 9:24am | Jul 15, 2026 9:46am | Jul 15, 2026 10:30am | Jul 15, 2026 10:36am | Jul 15, 2026 11:17am | Jul 15, 2026 11:19am | Jul 15, 2026 11:19am |  |  | Fair | No | Checks made and found pothead connections corroded Three pen union one1 bolt clampVoltage115v114v230v
Non-Outage | J.E.26.07.14880 | C001855638 | Nickolas Rodriques | Portmore | Completed | Load_576156 | Naggo Head - 610 | Jul 15, 2026 9:20am | Jul 15, 2026 9:22am | Jul 15, 2026 9:30pm | Jul 15, 2026 9:30pm | Jul 15, 2026 10:05pm | Jul 15, 2026 10:20pm | Jul 15, 2026 10:21pm | Jul 15, 2026 10:21pm | BrokenPole |  | Fair | No | Checked and found a 30 ft wooden pole rotten and leaning. Pole consists of customer service wire and one streetlight. Refer to maintenance.
Non-Outage | J.E.26.07.15329 | C001855636 | Orville Lee | St.Catherine | Completed | Load_249605 | Twickenham - 210 | Jul 15, 2026 9:19am | Jul 15, 2026 9:24am | Jul 15, 2026 9:46am | Jul 15, 2026 9:47am | Jul 15, 2026 9:56am | Jul 15, 2026 9:58am | Jul 15, 2026 9:59am | Jul 15, 2026 9:59am |  |  | Fair | No | team seen on site conducting repair
Non-Outage | J.E.26.07.15425 | C001855633 | Orville Lee | St.Catherine | Completed | Load_249744 | Twickenham - 210 | Jul 15, 2026 9:19am | Jul 15, 2026 9:24am | Jul 15, 2026 9:46am | Jul 15, 2026 12:43pm | Jul 15, 2026 12:57pm | Jul 15, 2026 1:13pm | Jul 15, 2026 1:14pm | Jul 15, 2026 1:14pm |  |  | Fair | No | No occupants seen at the premises Premises closedVoltage 115v116v231v
Non-Outage | J.E.26.07.15736 | C001855629 | Orville Lee | Portmore | Completed | Load_253463 | Naggo Head - 610 | Jul 15, 2026 9:19am | Jul 15, 2026 9:25am | Jul 15, 2026 2:25pm | Jul 15, 2026 2:32pm | Jul 15, 2026 2:32pm | Jul 15, 2026 2:58pm | Jul 15, 2026 3:00pm | Jul 15, 2026 3:00pm |  |  | Fair | No | Checks made and found secondary connections corrodedThree one bolt clamp usedVoltage118v118v237v
Non-Outage | J.E.26.07.16454 | C001855620 | Orville Lee | St.Catherine | Completed | Load_254928 | Twickenham - 210 | Jul 15, 2026 9:18am | Jul 15, 2026 9:25am | Jul 15, 2026 9:47am | Jul 15, 2026 1:15pm | Jul 15, 2026 1:19pm | Jul 15, 2026 1:52pm | Jul 15, 2026 1:53pm | Jul 15, 2026 1:53pm |  |  | Fair | No | Changed clamps on secondary line Voltag 116v117v233v
Outage | J.E.26.07.17038 | C001855615 | Jermaine Williams | Clarendon | Completed | Load_265262 | May Pen - 210 | Jul 15, 2026 9:14am | Jul 15, 2026 9:17am | Jul 15, 2026 9:58am | Jul 15, 2026 9:58am | Jul 15, 2026 10:27am | Jul 15, 2026 10:27am | Jul 15, 2026 10:29am | Jul 15, 2026 10:29am | BrokenPole |  | Fair | No | Splice and retention service wire… Left ok.
Non-Outage | J.E.26.07.11092 | C001855601 | Jermaine Williams | Clarendon | Completed | Load_263787 | May Pen - 110 | Jul 15, 2026 9:13am | Jul 15, 2026 9:13am | Jul 15, 2026 9:22am | Jul 15, 2026 9:22am | Jul 15, 2026 9:44am | Jul 15, 2026 9:45am | Jul 15, 2026 9:45am | Jul 15, 2026 9:45am | BrokenWire |  | Fair | No
Non-Outage | J.E.26.07.07022 | C001855590 | Odaine Johnson | Clarendon | Completed | Load_241598 | Parnassus - 310 | Jul 15, 2026 9:08am | Jul 15, 2026 9:09am | Jul 15, 2026 10:09am | Jul 15, 2026 12:26pm | Jul 15, 2026 12:40pm | Jul 15, 2026 12:40pm | Jul 15, 2026 12:41pm | Jul 15, 2026 12:41pm |  |  | Fair | No | Contacted customer and customer stated that the issue was resolved already
Non-Outage | J.E.26.07.07680 | C001855591 | Jermaine Williams | Clarendon | Completed | Load_301017 | Monymusk - 210 | Jul 15, 2026 9:08am | Jul 15, 2026 9:15am | Jul 15, 2026 10:42am | Jul 15, 2026 10:42am | Jul 15, 2026 12:47pm | Jul 15, 2026 12:47pm | Jul 15, 2026 12:49pm | Jul 15, 2026 12:49pm | LeaningPole |  | SevereWind | No | Broken 30’ class6 O/H guy pole.
Non-Outage | J.E.26.07.07386 | C001855589 | Odaine Johnson | Clarendon | Completed | Load_264974 | Monymusk - 210 | Jul 15, 2026 9:07am | Jul 15, 2026 9:09am | Jul 15, 2026 10:09am | Jul 15, 2026 11:56am | Jul 15, 2026 12:16pm | Jul 15, 2026 12:16pm | Jul 15, 2026 12:16pm | Jul 15, 2026 12:16pm |  |  | Fair | No | Contacted customer and customer stated that the issue was resolved already
Non-Outage | J.E.26.07.07887 | C001855588 | Jermaine Williams | Clarendon | Completed | Load_249360 | Parnassus - 310 | Jul 15, 2026 9:07am | Jul 15, 2026 9:08am | Jul 15, 2026 10:30am | Jul 15, 2026 10:30am | Jul 15, 2026 10:41am | Jul 15, 2026 10:41am | Jul 15, 2026 10:42am | Jul 15, 2026 10:42am | BrokenPole |  | Fair | No | Customer making reports for her meter pole, customer advised.
Non-Outage | J.E.26.07.08060 | C001855587 | Odaine Johnson | Clarendon | Completed | Load_301017 | Monymusk - 210 | Jul 15, 2026 9:06am | Jul 15, 2026 9:09am | Jul 15, 2026 10:09am | Jul 15, 2026 12:41pm | Jul 15, 2026 12:48pm | Jul 15, 2026 12:48pm | Jul 15, 2026 12:49pm | Jul 15, 2026 12:49pm |  |  | Fair | No | Contacted customer and customer stated that the issue was resolved from last week
Non-Outage | J.E.26.07.09695 | C001855585 | Odaine Johnson | Clarendon | Completed | Load_250524 | Parnassus - 310 | Jul 15, 2026 9:06am | Jul 15, 2026 9:09am | Jul 15, 2026 10:09am | Jul 15, 2026 1:32pm | Jul 15, 2026 1:47pm | Jul 15, 2026 1:47pm | Jul 15, 2026 1:47pm | Jul 15, 2026 1:47pm |  |  | Fair | No | Contacted customer and customer stated that the issue was resolved already
Non-Outage | J.E.26.07.10032 | C001855586 | Odaine Johnson | null | Completed | null | null | Jul 15, 2026 9:06am | Jul 15, 2026 9:09am | Jul 15, 2026 10:09am | Jul 15, 2026 2:58pm | Jul 15, 2026 2:58pm | Jul 15, 2026 2:58pm | Jul 15, 2026 2:58pm | Jul 15, 2026 2:58pm |  |  | Fair | No | Premises found okay voltage reading 110/110/221 volts
Non-Outage | J.E.26.07.10239 | C001855584 | Odaine Johnson | Clarendon | Completed | Load_262111 | Parnassus - 310 | Jul 15, 2026 9:06am | Jul 15, 2026 9:09am | Jul 15, 2026 10:09am | Jul 15, 2026 12:21pm | Jul 15, 2026 12:25pm | Jul 15, 2026 12:25pm | Jul 15, 2026 12:26pm | Jul 15, 2026 12:26pm |  |  | Fair | No | Contacted customer and customer stated that they did not make any report
Non-Outage | J.E.26.07.10766 | C001855582 | Odaine Johnson | Clarendon | Completed | Load_267585 | Parnassus - 310 | Jul 15, 2026 9:06am | Jul 15, 2026 9:09am | Jul 15, 2026 10:09am | Jul 16, 2026 2:24pm | Jul 16, 2026 2:24pm | Jul 16, 2026 2:24pm | Jul 16, 2026 2:24pm | Jul 16, 2026 2:24pm |  |  | Fair | No | Same area same issue
Non-Outage | J.E.26.07.11311 | C001855581 | Odaine Johnson | Clarendon | Completed | Load_239690 | Monymusk - 410 | Jul 15, 2026 9:06am | Jul 15, 2026 9:09am | Jul 15, 2026 10:09am | Jul 15, 2026 1:23pm | Jul 15, 2026 1:30pm | Jul 15, 2026 1:31pm | Jul 15, 2026 1:31pm | Jul 15, 2026 1:31pm |  |  | Fair | No | Contacted customer and customer stated that the issue was resolved already
Non-Outage | J.E.26.07.16415 | C001855580 | Clyde Brown | Clarendon | Completed | Load_238175 | May Pen - 110 | Jul 15, 2026 9:06am | Jul 16, 2026 7:48am | Jul 16, 2026 12:12pm | Jul 16, 2026 1:54pm | Jul 16, 2026 1:54pm | Jul 16, 2026 1:53pm | Jul 16, 2026 2:00pm | Jul 16, 2026 2:00pm |  |  | Fair | No | Cannot be located customer not answering phone
Outage | J.E.26.07.17024 | C001855583 | Barnett Brown | Manchester | Completed | Load_246177 | Spur Tree - 310 | Jul 15, 2026 9:06am | Jul 15, 2026 9:16am | Jul 15, 2026 12:37pm | Jul 15, 2026 12:38pm | Jul 15, 2026 1:50pm | Jul 15, 2026 2:48pm | Jul 15, 2026 2:52pm | Jul 15, 2026 2:52pm |  |  | Fair | No | Balance secondary line using spacers, reset 25 kva transformer
Non-Outage | J.E.26.07.16712 | C001855579 | Odaine Johnson | Clarendon | Completed | Load_267814 | Parnassus - 210 | Jul 15, 2026 9:05am | Jul 15, 2026 9:10am | Jul 15, 2026 10:09am | Jul 15, 2026 11:08am | Jul 15, 2026 11:08am | Jul 15, 2026 11:08am | Jul 15, 2026 11:09am | Jul 15, 2026 11:09am |  |  | Fair | No | Corrosion found at pole remade connection using 2 one bolt clamps voltage reading 116/116/232 volts
Non-Outage | J.E.26.07.16963 | C001855578 | Odaine Johnson | Clarendon | Completed | Load_1000130 | Parnassus - 210 | Jul 15, 2026 9:05am | Jul 15, 2026 9:10am | Jul 15, 2026 10:09am | Jul 15, 2026 3:55pm | Jul 15, 2026 4:06pm | Jul 15, 2026 4:06pm | Jul 15, 2026 4:11pm | Jul 15, 2026 4:11pm |  |  | Fair | No | Premises found okay voltage reading 112/115/228 volts primary line and secondary line need bushing
Non-Outage | J.E.26.07.17000 | C001855570 | Shamour Haughton | St.James | Completed | Load_266001 | Queens Drive - 310 | Jul 15, 2026 9:03am | Jul 15, 2026 9:04am | Jul 15, 2026 10:30am | Jul 15, 2026 10:30am | Jul 15, 2026 10:30am | Jul 15, 2026 10:30am | Jul 15, 2026 10:34am | Jul 15, 2026 10:34am |  |  | Fair | No | Found bank of 3 transformer open, customer states there was a white van that came to the premises and carry out work
Non-Outage | J.E.26.07.16348 | C001855557 | Neville Spencer | null | Completed | null | null | Jul 15, 2026 8:48am | Jul 15, 2026 3:50pm | Jul 15, 2026 6:48pm | Jul 15, 2026 6:48pm | Jul 15, 2026 7:01pm | Jul 15, 2026 7:01pm | Jul 15, 2026 7:02pm | Jul 15, 2026 7:02pm | BrokenWire |  | Fair | No | Found ok call resolved.
Outage | J.E.26.07.16980 | C001855556 | Stephen Taylor | St.Thomas | Completed | Load_247908 | Good Year - 210 | Jul 15, 2026 8:47am | Jul 15, 2026 8:48am | Jul 15, 2026 5:30pm | Jul 15, 2026 5:30pm | Jul 15, 2026 5:30pm | Jul 15, 2026 5:30pm | Jul 15, 2026 5:30pm | Jul 15, 2026 5:30pm | BrokenWire |  | Fair | No | Need more information a lot of call to customer no one answered the phone
Outage | J.E.26.07.16592 | C001855554 | Kemark Slue | Clarendon | Completed | Load_269136 | May Pen - 110 | Jul 15, 2026 8:46am | Jul 16, 2026 11:04am | Jul 16, 2026 12:26pm | Jul 16, 2026 12:26pm | Jul 16, 2026 1:14pm | Jul 16, 2026 1:46pm | Jul 16, 2026 2:42pm | Jul 16, 2026 2:42pm |  |  | Fair | No | Upon arrival at the location the crew discovered that one phase from 2/0 triplex secondary was burnt off resulting from illegal connections, remove illegal connections and remake joint using one, one bolt clamp.
Outage | J.E.26.07.16954 | C001855555 | Jermaine Williams | Clarendon | Completed | Load_259406 | Parnassus - 310 | Jul 15, 2026 8:46am | Jul 15, 2026 8:50am | Jul 15, 2026 9:21am | Jul 15, 2026 9:21am | Jul 15, 2026 9:21am | Jul 15, 2026 9:21am | Jul 15, 2026 9:21am | Jul 15, 2026 9:21am |  |  | Fair | No | Unable to locate customer
Outage | J.E.26.07.16987 | C001855553 | Rusean Allen | KSAS | Completed | Load_259300 | Hunts Bay - 510 | Jul 15, 2026 8:45am | Jul 15, 2026 8:46am | Jul 15, 2026 9:09am | Jul 15, 2026 9:10am | Jul 15, 2026 9:10am | Jul 15, 2026 9:15am | Jul 15, 2026 9:15am | Jul 15, 2026 9:15am | LeakingTransformer |  | Fair | No | 15 kva transformer defective need to change Eg box
Outage | J.E.26.07.16998 | C001855552 | Rusean Allen | KSAS | Completed | Load_246603 | Cane River - 610 | Jul 15, 2026 8:44am | Jul 15, 2026 8:46am | Jul 15, 2026 11:41am | Jul 15, 2026 11:41am | Jul 15, 2026 11:42am | Jul 15, 2026 2:30pm | Jul 15, 2026 2:30pm | Jul 15, 2026 2:30pm |  |  | Fair | No | Found a 65 amps fuse ReplacedReplace a 65 amps fuse
Outage | J.E.26.07.17018 | C001855549 | Christopher Edwards | KSAN | Completed | Load_250838 | Constant Spring - 310 | Jul 15, 2026 8:42am | Jul 15, 2026 8:44am | Jul 15, 2026 8:52am | Jul 15, 2026 9:26am | Jul 15, 2026 10:21am | Jul 15, 2026 11:17am | Jul 15, 2026 11:18am | Jul 15, 2026 11:18am | LeaningPole |  | Fair | No | Splice damage #6 service wire Using:30ft #6 service wire (3) one bolt clamps Voltage:114,113,230v
Non-Outage | J.E.26.06.30904 | C001855547 | Edward Royal | null | Completed | null | null | Jul 15, 2026 8:41am | Jul 15, 2026 8:42am | Jul 15, 2026 11:25am | Jul 15, 2026 11:25am | Jul 15, 2026 11:25am | Jul 15, 2026 11:28am | Jul 15, 2026 11:28am | Jul 15, 2026 11:28am | LeaningPole |  | Fair | No | Class 4 40 ft broken pole need to be change on it 2 phase primary line transformer with hexin service cable 3rd party cable reffered to maintenance
Outage | J.E.26.07.16912 | C001855546 | Horace Malcolm | St.James | Completed | Load_252666 | Bogue - 510 | Jul 15, 2026 8:39am | Jul 15, 2026 8:41am | Jul 15, 2026 8:48am | Jul 15, 2026 8:48am | Jul 15, 2026 9:10am | Jul 15, 2026 11:03am | Jul 15, 2026 11:03am | Jul 15, 2026 11:03am |  |  | Fair | No | Isolate two 50kva transformer to splice and retention two pole span secondary phase and nuetral used 50ft #2 conductor (1)#2 preform 30ft 2/0 conductor (1)2/0. Preform 3clamps voltage 115-118-233
Non-Outage | J.E.26.07.07642 | C001855544 | Shamour Haughton | Trelawny | Completed | Load_266091 | Greenwood - 110 | Jul 15, 2026 8:36am | Jul 15, 2026 8:37am | Jul 15, 2026 11:59am | Jul 15, 2026 11:59am | Jul 15, 2026 12:50pm | Jul 15, 2026 12:53pm | Jul 15, 2026 12:55pm | Jul 15, 2026 12:55pm | LowHangingWires |  | Fair | No | Unable to locate customer, phone number went voicemail after several attempts, conductors that are low hanging are conductors behind the meter
Non-Outage | J.E.26.07.10652 | C001855543 | Andre Williams | Trelawny | Completed | Load_1001485 | Duncans - 210 | Jul 15, 2026 8:36am | Jul 15, 2026 8:36am | Jul 15, 2026 9:01am | Jul 15, 2026 9:01am | Jul 15, 2026 10:18am | Jul 15, 2026 11:08am | Jul 15, 2026 11:08am | Jul 15, 2026 11:08am |  |  | Fair | No | Open 15 kva transformer, retention low hanging neutral that was touching phase
Non-Outage | J.E.26.07.07077 | C001855542 | Andrae Dawkins | St.James | Completed | Load_268851 | Queens Drive - 710 | Jul 15, 2026 8:34am | Jul 15, 2026 8:35am | Jul 15, 2026 11:39am | Jul 15, 2026 11:39am | Jul 15, 2026 11:42am | Jul 15, 2026 11:46am | Jul 15, 2026 11:47am | Jul 15, 2026 11:47am |  |  | Fair | No | Check and found ok customer said it was already resolved
Non-Outage | J.E.26.07.11972 | C001855539 | Andrae Dawkins | St.James | Completed | Load_257558 | Queens Drive - 710 | Jul 15, 2026 8:34am | Jul 15, 2026 8:35am | Jul 15, 2026 11:42am | Jul 15, 2026 11:54am | Jul 15, 2026 12:14pm | Jul 15, 2026 12:27pm | Jul 15, 2026 12:29pm | Jul 15, 2026 12:29pm |  |  | Fair | No | Check and found ok customer said the problem was already resolved voltage found 116/117/233
Non-Outage | J.E.26.07.15957 | C001855541 | Andrae Dawkins | St.James | Completed | Load_250410 | Queens Drive - 710 | Jul 15, 2026 8:34am | Jul 15, 2026 8:35am | Jul 15, 2026 11:34am | Jul 15, 2026 1:06pm | Jul 15, 2026 1:06pm | Jul 15, 2026 1:20pm | Jul 15, 2026 1:21pm | Jul 15, 2026 1:21pm |  |  | Fair | No | Check and found ok voltage found 113/116/229
Non-Outage | J.E.26.07.16170 | C001855537 | Andrae Dawkins | St.James | Completed | Load_243259 | Queens Drive - 710 | Jul 15, 2026 8:34am | Jul 15, 2026 8:35am | Jul 15, 2026 10:10am | Jul 15, 2026 10:11am | Jul 15, 2026 10:12am | Jul 15, 2026 10:12am | Jul 15, 2026 10:15am | Jul 15, 2026 10:15am |  |  | Fair | No | Check and found okay customer said that the power already came back
Non-Outage | J.E.26.07.15211 | C001855536 | Andrae Dawkins | St.James | Completed | Load_264461 | Bogue - 310 | Jul 15, 2026 8:33am | Jul 15, 2026 8:35am | Jul 15, 2026 12:45pm | Jul 15, 2026 12:45pm | Jul 15, 2026 12:45pm | Jul 15, 2026 12:55pm | Jul 15, 2026 1:04pm | Jul 15, 2026 1:04pm |  |  | Fair | No | Found multiple customers experiencing low voltage unable to make further checks due to rotten 30 foot class six dead end pole with twisted secondary and cables wires voltage found 101/103/205 pole needs to be replaced refer back to maintenance
Non-Outage | J.E.26.07.16007 | C001855535 | Andrae Dawkins | St.James | Completed | Load_242655 | Bogue - 310 | Jul 15, 2026 8:33am | Jul 15, 2026 8:35am | Jul 15, 2026 10:07am | Jul 15, 2026 10:15am | Jul 15, 2026 10:15am | Jul 15, 2026 10:34am | Jul 15, 2026 11:30am | Jul 15, 2026 11:30am |  |  | Fair | No | Found multiple customers in the area experiencing low voltage 9 pole span from transformer voltage found at customer pothead 103/108/211 voltage found at transformer pole 117/114/231 also found secondary line banging when heavy wind blows refer back to emergency crew
Non-Outage | J.E.26.07.16409 | C001855534 | Andrae Dawkins | St.James | Completed | Load_269249 | Bogue - 310 | Jul 15, 2026 8:33am | Jul 15, 2026 8:35am | Jul 15, 2026 1:24pm | Jul 15, 2026 1:26pm | Jul 15, 2026 1:43pm | Jul 15, 2026 2:48pm | Jul 15, 2026 2:49pm | Jul 15, 2026 2:49pm |  |  | Fair | No | Found multiple customers experiencing low voltage from the secondary line voltage found125/110/236 voltage fluctuates when the wind blows voltage stabilized when the wind stops 118/120/238 customer two pole span from transformer refer back to emergency crew
Non-Outage | J.E.26.07.15875 | C001855533 | Junior Scarlett | St.James | Completed | Load_260155 | Queens Drive - 710 | Jul 15, 2026 8:31am | Jul 15, 2026 8:31am | Jul 15, 2026 8:51am | Jul 15, 2026 2:57pm | Jul 15, 2026 3:22pm | Jul 15, 2026 3:40pm | Jul 15, 2026 3:41pm | Jul 15, 2026 3:41pm |  |  | Fair | No | Premesis lockVoltage found 114v 113v 225v
Non-Outage | J.E.26.07.10637 | C001855525 | Fredrick Hamilton | KSAN | Completed | Load_257446 | Constant Spring - 210 | Jul 15, 2026 8:29am | Jul 15, 2026 8:30am | Jul 15, 2026 8:37am | Jul 15, 2026 11:17am | Jul 15, 2026 11:17am | Jul 15, 2026 11:22am | Jul 15, 2026 11:22am | Jul 15, 2026 11:22am |  |  | Fair | No | Customer contacted and stated power was restored fully previously Premises is ok
Non-Outage | J.E.26.07.14439 | C001855526 | Junior Scarlett | St.James | Completed | Load_245262 | Queens Drive - 710 | Jul 15, 2026 8:29am | Jul 15, 2026 8:29am | Jul 15, 2026 8:51am | Jul 15, 2026 10:31am | Jul 15, 2026 10:31am | Jul 15, 2026 10:40am | Jul 15, 2026 11:41am | Jul 15, 2026 11:41am |  |  | Fair | No | Install pen unionInstall one clampVoltage found 114v 114v 228vVoltage leave 114v 114v 228b
Non-Outage | J.E.26.07.14445 | C001855527 | Junior Scarlett | St.James | Completed | Load_242423 | Queens Drive - 710 | Jul 15, 2026 8:29am | Jul 15, 2026 8:29am | Jul 15, 2026 8:51am | Jul 15, 2026 2:09pm | Jul 15, 2026 2:21pm | Jul 15, 2026 2:54pm | Jul 15, 2026 2:54pm | Jul 15, 2026 2:54pm |  |  | Fair | No | Defective meter socketAdvise customer to change meter socketVoltage found 115v 115v 230vVoltage leave 115v 115v 230v
Non-Outage | J.E.26.07.14608 | C001855529 | Junior Scarlett | St.James | Completed | Load_259518 | Queens Drive - 710 | Jul 15, 2026 8:29am | Jul 15, 2026 8:29am | Jul 15, 2026 8:51am | Jul 16, 2026 10:49am | Jul 16, 2026 11:46am | Jul 16, 2026 1:13pm | Jul 16, 2026 1:17pm | Jul 16, 2026 1:17pm |  |  | Fair | No | Install to clamp on poleInstall one crimpVoltage found 115v 0.33v 115v Voltage found 115v 115v 230vJob complete
Non-Outage | J.E.26.07.14739 | C001855530 | Junior Scarlett | St.James | Completed | Load_238066 | Queens Drive - 710 | Jul 15, 2026 8:29am | Jul 15, 2026 8:29am | Jul 15, 2026 8:51am | Jul 15, 2026 8:54am | Jul 15, 2026 9:32am | Jul 15, 2026 10:01am | Jul 15, 2026 10:02am | Jul 15, 2026 10:02am |  |  | Fair | No | Check and found okVoltage found 113v 113v 226vCustomer need to tension her wire
Non-Outage | J.E.26.07.16335 | C001855522 | Elvis Trowers | KSAS | Completed | Load_259244 | Duhaney - 310 | Jul 15, 2026 8:27am | Jul 15, 2026 8:29am | Jul 15, 2026 12:27pm | Jul 15, 2026 12:27pm | Jul 15, 2026 12:43pm | Jul 15, 2026 12:52pm | Jul 15, 2026 12:52pm | Jul 15, 2026 12:52pm | Fire |  | Fair | Yes | Premises checked and found ok, no sparks or fire was seen upon arrival.
Outage | J.E.26.07.16945 | C001855523 | Rayon Foster | Hanover | Completed | Load_303117 | Orange Bay - 210 | Jul 15, 2026 8:27am | Jul 15, 2026 8:28am | Jul 15, 2026 9:49am | Jul 15, 2026 1:49pm | Jul 15, 2026 2:27pm | Jul 15, 2026 5:05pm | Jul 15, 2026 5:09pm | Jul 15, 2026 5:09pm |  |  | Fair | No | One(167kva )transformer primary bushing damage /burnt off refer to Earl Vassle for imitate attention emergency no less than 60 customers are out of power in area pole #0221a at grand pineapple
Non-Outage | J.E.26.07.16501 | C001855519 | Edward Royal | KSAS | Completed | Load_578984 | Up Park Camp - 410 | Jul 15, 2026 8:26am | Jul 15, 2026 8:30am | Jul 15, 2026 9:32am | Jul 15, 2026 9:32am | Jul 15, 2026 9:32am | Jul 15, 2026 9:34am | Jul 15, 2026 9:34am | Jul 15, 2026 9:34am | LeaningPole |  | Fair | No | Premises found ok when arrived at location there is no leaning pole
Non-Outage | J.E.26.07.16589 | C001855517 | Rochaine Hussey | KSAN | Completed | Load_251210 | Washington Blvd - 610 | Jul 15, 2026 8:26am | Jul 15, 2026 8:33am | Jul 16, 2026 9:10am | Jul 16, 2026 9:10am | Jul 16, 2026 9:10am | Jul 16, 2026 9:12am | Jul 16, 2026 9:12am | Jul 16, 2026 9:12am |  |  | Fair | No | Visit premises and it’s closed , customer is requesting a team to visit in the night because during the day they are at work
Outage | J.E.26.07.13798 | C001855518 | Nickolas Rodriques | St.Catherine | Completed | Load_262435 | Twickenham - 210 | Jul 15, 2026 8:26am | Jul 15, 2026 8:27am | Jul 15, 2026 11:47am | Jul 15, 2026 11:53am | Jul 15, 2026 12:05pm | Jul 15, 2026 12:25pm | Jul 15, 2026 12:27pm | Jul 15, 2026 12:27pm |  |  | Fair | No | Issue resolved. Call relates to the 50 KVA transformer drop leads that was repaired.
Non-Outage | J.E.26.07.16182 | C001855515 | Rochaine Hussey | KSAN | Completed | Load_264325 | Washington Blvd - 510 | Jul 15, 2026 8:25am | Jul 15, 2026 8:34am | Jul 16, 2026 10:59am | Jul 16, 2026 10:59am | Jul 16, 2026 10:59am | Jul 16, 2026 11:50am | Jul 16, 2026 11:54am | Jul 16, 2026 11:54am |  |  | Fair | No | Slack connection in meter socket Issue resolved 120/120/241v
Outage | J.E.26.07.15207 | C001855514 | Nickolas Rodriques | St.Catherine | Completed | Load_248766 | Twickenham - 210 | Jul 15, 2026 8:25am | Jul 15, 2026 8:28am | Jul 15, 2026 10:05am | Jul 15, 2026 10:12am | Jul 15, 2026 10:48am | Jul 15, 2026 11:44am | Jul 15, 2026 11:51am | Jul 15, 2026 11:51am |  |  | Fair | No | Checked and found customer single phasing (118) caused by date meter socket burnt. Isolate 50 KVA transformer for safety to disconnect meter and connect transformer drop leads to aluminum and replaced the fuse after completing patrol, current reading is (118-120-238). Refer to field service for follow-up.
Outage | J.E.26.07.15756 | C001855513 | Nickolas Rodriques | Portmore | Completed | Load_557243 | Naggo Head - 510 | Jul 15, 2026 8:25am | Jul 15, 2026 8:27am | Jul 15, 2026 2:22pm | Jul 15, 2026 2:24pm | Jul 15, 2026 2:54pm | Jul 15, 2026 3:17pm | Jul 15, 2026 3:24pm | Jul 15, 2026 3:24pm |  |  | Fair | No | Checked and found customer without electricity. The escalation team was contacted in which they reconnected the customer remotely. Customer confirmed that all is well.
Outage | J.E.26.07.16099 | C001855512 | Nickolas Rodriques | St.Catherine | Completed | Load_265101 | Twickenham - 210 | Jul 15, 2026 8:25am | Jul 15, 2026 8:29am | Jul 16, 2026 11:44am | Jul 16, 2026 2:19pm | Jul 16, 2026 2:26pm | Jul 16, 2026 2:43pm | Jul 16, 2026 2:46pm | Jul 16, 2026 2:46pm |  |  | Fair | No | Found customer without electricity. Checks were done and it was found that a disconnection order was placed on the account for non-payment of bill.
Non-Outage | J.E.26.07.16161 | C001855504 | Horace Malcolm | St.James | Completed | Load_567728 | Bogue - 610 | Jul 15, 2026 8:24am | Jul 15, 2026 8:25am | Jul 16, 2026 9:04am | Jul 16, 2026 9:04am | Jul 16, 2026 9:13am | Jul 16, 2026 9:15am | Jul 16, 2026 9:15am | Jul 16, 2026 9:15am | LeaningPole |  | Fair | No | Found one 35ft wooden dead end pole leaning down in front of customer gateway with four customers service wires connected to pole
Non-Outage | J.E.26.07.16543 | C001855511 | Omar King | null | Completed | null | null | Jul 15, 2026 8:24am | Jul 15, 2026 2:27pm | Jul 15, 2026 8:45pm | Jul 15, 2026 8:45pm | Jul 15, 2026 9:40pm | Jul 15, 2026 9:41pm | Jul 15, 2026 9:41pm | Jul 15, 2026 9:41pm |  |  | Fair | No | Problem as been resolved
Outage | J.E.26.07.16131 | C001855510 | Nickolas Rodriques | Portmore | Completed | Load_257404 | Naggo Head - 510 | Jul 15, 2026 8:24am | Jul 15, 2026 8:29am | Jul 15, 2026 10:24pm | Jul 15, 2026 10:25pm | Jul 15, 2026 10:43pm | Jul 15, 2026 10:56pm | Jul 15, 2026 10:58pm | Jul 15, 2026 10:58pm |  |  | Fair | No | Found customer with electricity. Customer stated that he was disconnected due to non payment of bill.
Outage | J.E.26.07.16413 | C001855503 | Nickolas Rodriques | Portmore | Completed | Load_246829 | Naggo Head - 610 | Jul 15, 2026 8:24am | Jul 15, 2026 8:31am | Jul 16, 2026 5:22pm | Jul 16, 2026 5:23pm | Jul 16, 2026 6:07pm | Jul 16, 2026 6:14pm | Jul 16, 2026 6:15pm | Jul 16, 2026 6:15pm |  |  | Fair | No | Found customer with electricity. Call relates to the 10 KVA transformer that was tripped earlier this morning.
Outage | J.E.26.07.16469 | C001855502 | Nickolas Rodriques | St.Catherine | Completed | Load_253772 | Twickenham - 210 | Jul 15, 2026 8:24am | Jul 15, 2026 8:32am | Jul 16, 2026 4:16pm | Jul 16, 2026 4:18pm | Jul 16, 2026 5:08pm | Jul 16, 2026 5:15pm | Jul 16, 2026 5:21pm | Jul 16, 2026 5:21pm |  |  | Fair | No | Unable to locate or communicate with the customer after several attempts. However, the area was patrolled and no noticeable outage was found.
Outage | J.E.26.07.16511 | C001855501 | Nickolas Rodriques | St.Catherine | Completed | Load_263124 | Twickenham - 210 | Jul 15, 2026 8:24am | Jul 15, 2026 8:32am | Jul 15, 2026 12:32pm | Jul 15, 2026 12:32pm | Jul 15, 2026 1:02pm | Jul 15, 2026 1:13pm | Jul 15, 2026 1:19pm | Jul 15, 2026 1:19pm |  |  | Fair | No | Power restored. Customer was disconnected due to non payment of bill.
Non-Outage | J.E.26.04.30401 | C001855498 | Michael Christian | St.James | Completed | Load_267271 | Queens Drive - 810 | Jul 15, 2026 8:23am | Jul 16, 2026 8:25am | Jul 16, 2026 12:52pm | Jul 16, 2026 12:52pm | Jul 16, 2026 1:50pm | Jul 16, 2026 1:52pm | Jul 16, 2026 1:52pm | Jul 16, 2026 1:52pm |  |  | Fair | No | Premises found locked
Non-Outage | J.E.26.06.00757 | C001855500 | Shamour Haughton | St.James | Completed | Load_259452 | Queens Drive - 310 | Jul 15, 2026 8:23am | Jul 15, 2026 8:24am | Jul 15, 2026 11:03am | Jul 15, 2026 11:04am | Jul 15, 2026 11:16am | Jul 15, 2026 11:30am | Jul 15, 2026 11:33am | Jul 15, 2026 11:33am |  |  | Fair | No | Check and found customer experiencing internal problem, voltage found 119,111,221
Non-Outage | J.E.26.07.07197 | C001855497 | Shamour Haughton | St.James | Completed | Load_237816 | Rose Hall - 210 | Jul 15, 2026 8:23am | Jul 15, 2026 8:23am | Jul 15, 2026 10:34am | Jul 15, 2026 10:34am | Jul 15, 2026 10:45am | Jul 15, 2026 10:48am | Jul 15, 2026 10:53am | Jul 15, 2026 10:53am | BrokenPole |  | Fair | No | Found 30ft TA pole rotten at base,only secondary holding pole, pole needs to be changed urgently
Outage | J.E.26.07.16989 | C001855499 | Donald Cunningham | St.Catherine | Completed | Load_557371 | Tredegar - 210 | Jul 15, 2026 8:23am | Jul 15, 2026 8:23am | Jul 15, 2026 9:45am | Jul 15, 2026 9:45am | Jul 15, 2026 10:39am | Jul 15, 2026 11:04am | Jul 15, 2026 11:07am | Jul 15, 2026 11:07am |  |  | Fair | No | Defective meter socket in meter center need to replace urgently customer out for 7 weeks now notice that meter recently changed
Non-Outage | J.E.26.07.10804 | C001855494 | Cliton Henry | St.Mary | Completed | Load_243605 | Oracabessa - 110 | Jul 15, 2026 8:22am | Jul 15, 2026 8:22am | Jul 15, 2026 9:06am | Jul 15, 2026 9:06am | Jul 15, 2026 9:06am | Jul 15, 2026 9:07am | Jul 15, 2026 9:07am | Jul 15, 2026 9:07am |  |  | Fair | No | Supply restored, related to outage #12592
Non-Outage | J.E.26.07.10907 | C001855493 | Cliton Henry | St.Mary | Completed | Load_243605 | Oracabessa - 110 | Jul 15, 2026 8:22am | Jul 15, 2026 8:22am | Jul 15, 2026 9:07am | Jul 15, 2026 9:07am | Jul 15, 2026 9:07am | Jul 15, 2026 9:08am | Jul 15, 2026 9:08am | Jul 15, 2026 9:08am |  |  | Fair | No | Supply restored, related to outage #12592
Non-Outage | J.E.26.07.11882 | C001855495 | Cliton Henry | St.Mary | Completed | Load_243605 | Oracabessa - 110 | Jul 15, 2026 8:22am | Jul 15, 2026 8:22am | Jul 15, 2026 8:57am | Jul 15, 2026 8:57am | Jul 15, 2026 9:05am | Jul 15, 2026 9:06am | Jul 15, 2026 9:06am | Jul 15, 2026 9:06am |  |  | Fair | No | Supply restored, related to outage #12592
Non-Outage | J.E.26.07.14570 | C001855496 | Michael Christian | St.James | Completed | Load_302142 | Queens Drive - 710 | Jul 15, 2026 8:22am | Jul 16, 2026 8:25am | Jul 16, 2026 1:48pm | Jul 16, 2026 1:52pm | Jul 16, 2026 1:52pm | Jul 16, 2026 1:57pm | Jul 16, 2026 1:57pm | Jul 16, 2026 1:57pm | BrokenWire |  | Fair | No | Found broken wire replace 1 clamp at customer service wire at pole voltage 111 110 221 at pothead time 130 pm
Outage | J.E.26.07.16939 | C001855492 | Shamour Haughton | St.James | Completed | Load_259820 | Rose Hall - 210 | Jul 15, 2026 8:20am | Jul 15, 2026 8:22am | Jul 15, 2026 11:35am | Jul 15, 2026 11:35am | Jul 15, 2026 11:53am | Jul 15, 2026 11:53am | Jul 15, 2026 11:58am | Jul 15, 2026 11:58am |  |  | Fair | No | Customer experiencing internal issues,voltage left 119,117,238
Outage | J.E.26.07.16514 | C001855489 | Jermaine Williams | St.Catherine | Completed | Load_270222 | Rhodens Pen - 310 | Jul 15, 2026 8:16am | Jul 15, 2026 8:19am | Jul 15, 2026 8:29am | Jul 15, 2026 8:29am | Jul 15, 2026 8:53am | Jul 15, 2026 8:57am | Jul 15, 2026 8:58am | Jul 15, 2026 8:58am |  |  | Fair | No | Defective 3wire meter. Meter is off and unable to reconnect. Refer to Hopeton Daley to have meter change urgently as premises is a business establishment.
Non-Outage | J.E.26.07.15691 | C001855488 | Richman Whyte | Hanover | Completed | Load_253063 | Orange Bay - 310 | Jul 15, 2026 8:15am | Jul 15, 2026 8:16am | Jul 15, 2026 10:28am | Jul 15, 2026 10:28am | Jul 15, 2026 12:30pm | Jul 15, 2026 12:32pm | Jul 15, 2026 12:33pm | Jul 15, 2026 12:33pm |  |  | Fair | No | Repair burnt off service wire splice in midair voltage 108 108 216
Non-Outage | J.E.26.07.15811 | C001855486 | Richman Whyte | Westmoreland | Completed | Load_251345 | Paradise - 210 | Jul 15, 2026 8:15am | Jul 15, 2026 8:17am | Jul 15, 2026 2:05pm | Jul 15, 2026 2:05pm | Jul 15, 2026 2:05pm | Jul 15, 2026 2:29pm | Jul 15, 2026 2:30pm | Jul 15, 2026 2:30pm |  |  | Fair | No | Clean corrosion on service wire at pothead voltage 113 112 226 use two service connectors
Non-Outage | J.E.26.07.16930 | C001855487 | Richman Whyte | Westmoreland | Completed | Load_262009 | Paradise - 210 | Jul 15, 2026 8:15am | Jul 15, 2026 8:18am | Jul 15, 2026 12:37pm | Jul 15, 2026 12:37pm | Jul 15, 2026 12:37pm | Jul 15, 2026 12:37pm | Jul 15, 2026 12:39pm | Jul 15, 2026 12:39pm |  |  | Fair | No | Customer stated that he didn’t make any recent report the report he made was sometime ago and he is okay now
Non-Outage | J.E.26.07.16420 | C001855484 | Fredrick Hamilton | KSAN | Completed | Load_257226 | Constant Spring - 410 | Jul 15, 2026 8:14am | Jul 15, 2026 8:22am | Jul 15, 2026 8:27am | Jul 15, 2026 8:46am | Jul 15, 2026 8:46am | Jul 15, 2026 8:51am | Jul 15, 2026 8:51am | Jul 15, 2026 8:51am |  |  | Fair | No | Customer contacted and stated power was restored fully previously Premises is ok
Non-Outage | J.E.26.07.16394 | C001855483 | Roxroy Needham | null | Completed | null | null | Jul 15, 2026 8:12am | Jul 15, 2026 8:12am | Jul 15, 2026 8:39am | Jul 15, 2026 8:39am | Jul 15, 2026 10:34am | Jul 15, 2026 11:11am | Jul 15, 2026 11:12am | Jul 15, 2026 11:12am |  |  | Fair | No | Premises found ok voltage left at meter 116-115-237
Outage | J.E.26.07.16978 | C001855482 | Oshane Warren | Westmoreland | Completed | Load_292373 | Paradise - 310 | Jul 15, 2026 8:10am | Jul 15, 2026 8:11am | Jul 15, 2026 9:06am | Jul 15, 2026 9:07am | Jul 15, 2026 10:11am | Jul 15, 2026 10:12am | Jul 15, 2026 10:13am | Jul 15, 2026 10:13am |  |  | Fair | No | Unable to locate or contact customer need direction
Non-Outage | J.E.26.07.15334 | C001855479 | Nickolas Rodriques | null | Completed | null | null | Jul 15, 2026 8:08am | Jul 15, 2026 8:21am | Jul 15, 2026 8:27am | Jul 15, 2026 8:45am | Jul 15, 2026 9:29am | Jul 15, 2026 9:58am | Jul 15, 2026 10:04am | Jul 15, 2026 10:04am | Fire |  | Fair | No | Checked and found customer meter socket and wires burnt. Isolate service wire for safety to repair. The customer was advised to consult a licensed Electrician to do repairs.
Non-Outage | J.E.26.07.16970 | C001855476 | Cliton Henry | null | Completed | null | null | Jul 15, 2026 8:08am | Jul 15, 2026 8:14am | Jul 15, 2026 8:47am | Jul 15, 2026 8:47am | Jul 15, 2026 8:47am | Jul 15, 2026 8:48am | Jul 15, 2026 8:48am | Jul 15, 2026 8:48am |  |  | Fair | No | Supply restored, related to outage #16952
Outage | J.E.26.07.16304 | C001855477 | Jermaine Williams | St.Catherine | Completed | Load_265930 | Rhodens Pen - 310 | Jul 15, 2026 8:08am | Jul 15, 2026 8:18am | Jul 15, 2026 8:58am | Jul 15, 2026 9:19am | Jul 15, 2026 9:20am | Jul 15, 2026 9:20am | Jul 15, 2026 9:20am | Jul 15, 2026 9:20am |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.16977 | C001855478 | Rusean Allen | KSAS | Completed | Load_239591 | Cane River - 610 | Jul 15, 2026 8:08am | Jul 15, 2026 8:09am | Jul 15, 2026 9:54am | Jul 15, 2026 9:54am | Jul 15, 2026 10:27am | Jul 15, 2026 11:03am | Jul 15, 2026 11:03am | Jul 15, 2026 11:03am |  |  | Fair | No | Found a 20 amps fuse Replaced a 20 amps fuse
Non-Outage | J.E.26.07.15933 | C001855475 | Andre Williams | Trelawny | Completed | Load_302800 | Duncans - 110 | Jul 15, 2026 8:07am | Jul 15, 2026 8:08am | Jul 15, 2026 8:55am | Jul 15, 2026 11:09am | Jul 15, 2026 12:52pm | Jul 15, 2026 12:55am | Jul 15, 2026 12:55pm | Jul 15, 2026 12:55pm |  |  | Fair | No | Unable to locate with current phone number and directions community has more than one entrance
Non-Outage | J.E.26.07.16233 | C001855473 | Cliton Henry | St.Mary | Completed | Load_350817 | Oracabessa - 110 | Jul 15, 2026 8:07am | Jul 15, 2026 8:08am | Jul 15, 2026 9:08am | Jul 15, 2026 9:08am | Jul 15, 2026 9:25am | Jul 15, 2026 10:06am | Jul 15, 2026 10:06am | Jul 15, 2026 10:06am |  |  | Fair | No | A dislodge secondary neutral conductor found due rotten #2 preform caused by the salt air. A 25 kva transformer was de energized at pole #589543 to carryout repairs. Corrective work done to retension the secondary neutral conductor using 1-#2 preform. Supply restored to energized the 25 kva transformer at pole #589543. The customer service wire was also reconnected using 2#6-#2 pen union and 4 one bolt clamps.voltages118-118/236 volts
Non-Outage | J.E.26.07.16905 | C001855472 | Andre Williams | null | Completed | null | null | Jul 15, 2026 8:07am | Jul 15, 2026 8:08am | Jul 15, 2026 8:12am | Jul 15, 2026 8:22am | Jul 15, 2026 8:40am | Jul 15, 2026 8:51am | Jul 15, 2026 8:54am | Jul 15, 2026 8:54am | BrokenWire |  | Fair | No | Remake coroded joint at Jps pole on customer 2 wire service
Outage | J.E.26.07.16909 | C001855474 | Donald Cunningham | St.Catherine | Completed | Load_244050 | Tredegar - 410 | Jul 15, 2026 8:07am | Jul 15, 2026 8:13am | Jul 15, 2026 9:16am | Jul 15, 2026 9:16am | Jul 15, 2026 9:40am | Jul 15, 2026 9:42am | Jul 15, 2026 9:44am | Jul 15, 2026 9:44am |  | Y | Fair | No | 25 kva transformer found trip same reset illegal connection in area refer to losses crew also bushing required in area
Non-Outage | J.E.26.07.16175 | C001855468 | Roxroy Needham | St.Ann | Completed | Load_260368 | Cardiff Hall - 210 | Jul 15, 2026 8:06am | Jul 15, 2026 8:06am | Jul 15, 2026 12:35pm | Jul 15, 2026 12:38pm | Jul 15, 2026 12:38pm | Jul 15, 2026 12:38pm | Jul 15, 2026 12:39pm | Jul 15, 2026 12:39pm |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.07.16178 | C001855469 | Roxroy Needham | St.Ann | Completed | Load_260368 | Cardiff Hall - 210 | Jul 15, 2026 8:06am | Jul 15, 2026 8:06am | Jul 15, 2026 11:15am | Jul 15, 2026 11:15am | Jul 15, 2026 12:33pm | Jul 15, 2026 12:35pm | Jul 15, 2026 12:36pm | Jul 15, 2026 12:36pm |  |  | Fair | No | Remake joint at pole and pothead used 4 pg clamp voltage left at meter 118-117-241
Non-Outage | J.E.26.07.16257 | C001855470 | Omar King | St.Ann | Completed | Load_556920 | Cardiff Hall - 310 | Jul 15, 2026 8:06am | Jul 15, 2026 2:27pm | Jul 15, 2026 7:39pm | Jul 15, 2026 7:39pm | Jul 15, 2026 8:44pm | Jul 15, 2026 8:45pm | Jul 15, 2026 8:45pm | Jul 15, 2026 8:45pm |  |  | Fair | No | Problem as been resolved from yesterday
Outage | J.E.26.07.16876 | C001855471 | Elvis Trowers | KSAN | Completed | Load_246274 | Washington Blvd - 510 | Jul 15, 2026 8:06am | Jul 15, 2026 8:06am | Jul 15, 2026 9:57am | Jul 15, 2026 9:57am | Jul 15, 2026 10:21am | Jul 15, 2026 10:26am | Jul 15, 2026 10:26am | Jul 15, 2026 10:26am |  |  | Fair | Yes | Premises found closed upon arrival and customer could not be contacted by telephone either after several calls and voice messages were left, and which is a gated community.
Non-Outage | J.E.26.07.16422 | C001855467 | Omar King | St.Ann | Completed | Load_246935 | Cardiff Hall - 310 | Jul 15, 2026 8:05am | Jul 15, 2026 2:27pm | Jul 15, 2026 6:46pm | Jul 15, 2026 6:46pm | Jul 15, 2026 7:38pm | Jul 15, 2026 7:38pm | Jul 15, 2026 7:38pm | Jul 15, 2026 7:38pm |  |  | Fair | No | Problem as been resolved
Non-Outage | J.E.26.07.16491 | C001855466 | Roxroy Needham | St.Ann | Completed | Load_238147 | Cardiff Hall - 310 | Jul 15, 2026 8:05am | Jul 15, 2026 8:06am | Jul 15, 2026 1:22pm | Jul 15, 2026 1:22pm | Jul 15, 2026 3:30pm | Jul 15, 2026 3:32pm | Jul 15, 2026 3:35pm | Jul 15, 2026 3:35pm |  |  | Fair | No | Remake joint at pole used 2 pg clamp voltage left at meter 113-112-226
Outage | J.E.26.07.16953 | C001855465 | Horace Malcolm | St.James | Completed | Load_249034 | Bogue - 610 | Jul 15, 2026 8:05am | Jul 15, 2026 8:05am | Jul 15, 2026 11:43am | Jul 15, 2026 11:44am | Jul 15, 2026 12:37pm | Jul 15, 2026 1:54pm | Jul 15, 2026 1:54pm | Jul 15, 2026 1:54pm | BrokenWire |  | Fair | No | Isolate one 25kva transformer to splice and retention one pole span secondary phase and nuetral usd 30ft #2 conductor (2)#2 preforms 2clamps voltage 113-113-227
Outage | J.E.26.07.16967 | C001855461 | Daniel Francis | St.Ann | Completed | Load_239559 | Roaring River - 410 | Jul 15, 2026 8:04am | Jul 15, 2026 8:04am | Jul 15, 2026 9:20am | Jul 15, 2026 9:20am | Jul 15, 2026 9:36am | Jul 15, 2026 10:44am | Jul 15, 2026 10:49am | Jul 15, 2026 10:49am |  |  | Fair | No | Patrol and found junction blown at 044970 40amp replace
Outage | J.E.26.07.16968 | C001855462 | Daniel Francis | St.Ann | Completed | Load_258564 | Roaring River - 410 | Jul 15, 2026 8:04am | Jul 15, 2026 8:04am | Jul 15, 2026 10:49am | Jul 15, 2026 11:23am | Jul 15, 2026 11:23am | Jul 15, 2026 11:24am | Jul 15, 2026 11:24am | Jul 15, 2026 11:24am |  |  | Fair | No | Found okay
Outage | J.E.26.07.16733 | C001855459 | Kemark Slue | St.Catherine | Completed | Load_257901 | New Michelton - 410 | Jul 15, 2026 8:03am | Jul 15, 2026 8:06am | Jul 15, 2026 10:49am | Jul 15, 2026 1:15pm | Jul 15, 2026 1:15pm | Jul 15, 2026 12:00pm | Jul 15, 2026 1:29pm | Jul 15, 2026 1:29pm |  |  | Fair | No | Premises was checked and found okay.
Outage | J.E.26.07.16730 | C001855457 | Kemark Slue | St.Catherine | Completed | Load_240025 | New Michelton - 410 | Jul 15, 2026 8:02am | Jul 15, 2026 8:06am | Jul 15, 2026 10:34am | Jul 15, 2026 1:10pm | Jul 15, 2026 1:11pm | Jul 15, 2026 11:00am | Jul 15, 2026 1:15pm | Jul 15, 2026 1:15pm |  |  | Fair | No | Premises was checked and found okay.
Outage | J.E.26.07.16845 | C001855456 | Kemark Slue | St.Catherine | Completed | Load_260349 | New Michelton - 210 | Jul 15, 2026 8:02am | Jul 15, 2026 8:06am | Jul 15, 2026 10:33am | Jul 15, 2026 11:58am | Jul 15, 2026 11:58am | Jul 15, 2026 9:43am | Jul 15, 2026 12:10pm | Jul 15, 2026 12:10pm |  |  | Fair | No | Premises was checked and found okay.
Outage | J.E.26.07.16869 | C001855458 | Kemark Slue | St.Catherine | Completed | Load_242607 | New Michelton - 210 | Jul 15, 2026 8:02am | Jul 15, 2026 8:06am | Jul 15, 2026 11:43am | Jul 15, 2026 1:29pm | Jul 15, 2026 1:29pm | Jul 15, 2026 12:44pm | Jul 15, 2026 1:39pm | Jul 15, 2026 1:39pm |  |  | Fair | No | Unable to locate customer’s premises and all calls to number given were futile, the team however drove through the area which had supply.
Outage | J.E.26.07.16860 | C001855455 | Kemark Slue | St.Catherine | Completed | Load_255806 | New Michelton - 410 | Jul 15, 2026 8:01am | Jul 15, 2026 8:15am | Jul 15, 2026 10:31am | Jul 15, 2026 10:31am | Jul 15, 2026 11:57am | Jul 15, 2026 9:00am | Jul 15, 2026 11:58am | Jul 15, 2026 11:58am |  |  | Fair | No | Premises was checked and found okay.
Outage | J.E.26.07.15157 | C001855450 | Michael Christian | St.James | Completed | Load_262250 | Bogue - 310 | Jul 15, 2026 7:51am | Jul 15, 2026 7:51am | Jul 15, 2026 8:18am | Jul 15, 2026 8:18am | Jul 15, 2026 8:43am | Jul 15, 2026 8:49am | Jul 15, 2026 8:49am | Jul 15, 2026 8:49am | LowHangingWires |  | Fair | No | Check and found okay
Outage | J.E.26.07.15723 | C001855449 | Michael Christian | St.James | Completed | Load_1002490 | Bogue - 310 | Jul 15, 2026 7:51am | Jul 15, 2026 7:51am | Jul 15, 2026 10:12am | Jul 15, 2026 10:12am | Jul 15, 2026 10:50am | Jul 15, 2026 10:56am | Jul 15, 2026 10:56am | Jul 15, 2026 10:56am |  |  | Fair | No | No wire found send to field service
Outage | J.E.26.07.16908 | C001855447 | Michael Christian | St.James | Completed | Load_576009 | Bogue - 310 | Jul 15, 2026 7:51am | Jul 15, 2026 7:51am | Jul 15, 2026 9:55am | Jul 15, 2026 9:55am | Jul 15, 2026 10:11am | Jul 15, 2026 10:12am | Jul 15, 2026 10:12am | Jul 15, 2026 10:12am |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.16938 | C001855448 | Michael Christian | St.James | Completed | Load_576009 | Bogue - 310 | Jul 15, 2026 7:51am | Jul 15, 2026 7:51am | Jul 15, 2026 8:49am | Jul 15, 2026 8:50am | Jul 15, 2026 9:47am | Jul 15, 2026 9:55am | Jul 15, 2026 9:55am | Jul 15, 2026 9:55am |  |  | Fair | No | Check and found okay voltage 110 112 223 at pothead
Outage | J.E.26.07.16020 | C001855444 | Kenroy Dale | Manchester | Completed | Load_260683 | Kendal - 310 | Jul 15, 2026 7:48am | Jul 15, 2026 7:49am | Jul 15, 2026 8:35am | Jul 15, 2026 12:13pm | Jul 15, 2026 12:13pm | Jul 15, 2026 12:18pm | Jul 15, 2026 12:21pm | Jul 15, 2026 12:21pm |  |  | Fair | No | Customer said that supply was restored, area visited and found with supply. Was advised to write off call by dispatcher
Non-Outage | J.E.26.06.23839 | C001855439 | Andrew Powell | Manchester | Completed | Load_252763 | Spur Tree - 210 | Jul 15, 2026 7:40am | Jul 15, 2026 9:35am | Jul 15, 2026 9:44am | Jul 15, 2026 9:44am | Jul 15, 2026 9:53am | Jul 15, 2026 9:53am | Jul 15, 2026 9:54am | Jul 15, 2026 9:54am |  |  | Fair | No | Premises found okay customer stated that fault resolved supply restored.
Non-Outage | J.E.26.06.35638 | C001855440 | Selvin White | St.Elizabeth | Completed | Load_270243 | Maggotty - 210 | Jul 15, 2026 7:40am | Jul 15, 2026 7:41am | Jul 15, 2026 9:11am | Jul 15, 2026 9:11am | Jul 15, 2026 9:28am | Jul 15, 2026 9:37am | Jul 15, 2026 9:39am | Jul 15, 2026 9:39am | LeaningPole |  | Fair | No | A leaning 35 ft wooden pole found at location leaning towards the roadway needs to be straightened and a guy is to be installed. Please refer to the maintenance department so arrangements can be made for follow up.
Non-Outage | J.E.26.07.14550 | C001855442 | Selvin White | St.Elizabeth | Completed | Load_242892 | Maggotty - 110 | Jul 15, 2026 7:40am | Jul 15, 2026 7:42am | Jul 15, 2026 10:16am | Jul 15, 2026 10:16am | Jul 15, 2026 10:32am | Jul 15, 2026 11:03am | Jul 15, 2026 11:03am | Jul 15, 2026 11:03am |  |  | Fair | No | Supply found okay with voltage readings of 225 112,113 volts however customer meter is badly corroded and was advised to get the service of a licensed electrician to resolve the problem.
Non-Outage | J.E.26.07.15129 | C001855441 | Selvin White | St.Elizabeth | Completed | Load_269055 | Maggotty - 210 | Jul 15, 2026 7:40am | Jul 15, 2026 7:42am | Jul 15, 2026 8:49am | Jul 15, 2026 9:51am | Jul 15, 2026 9:52am | Jul 15, 2026 9:55am | Jul 15, 2026 10:03am | Jul 15, 2026 10:03am |  |  | Fair | No | Customer was contacted and said supply was restored. Problem was as a result of low voltage at the Moggotty substation.
Non-Outage | J.E.26.07.11576 | C001855438 | Neckell Ormsby | St.Mary | Completed | Load_238637 | Highgate - 210 | Jul 15, 2026 7:38am | Jul 15, 2026 7:38am | Jul 15, 2026 9:15am | Jul 15, 2026 9:15am | Jul 15, 2026 9:45am | Jul 15, 2026 10:32am | Jul 15, 2026 10:55am | Jul 15, 2026 10:55am |  |  | Fair | No | Troubleshoot and found corrosion at secondary jumper open 25kva transformer to clean and remade joint using 1- one bolt clamp voltage left 114v 112v 227v
Non-Outage | J.E.26.07.12460 | C001855436 | Neckell Ormsby | St.Mary | Completed | Load_264246 | Highgate - 210 | Jul 15, 2026 7:37am | Jul 15, 2026 7:38am | Jul 15, 2026 11:41am | Jul 15, 2026 11:41am | Jul 15, 2026 12:14pm | Jul 15, 2026 12:16pm | Jul 15, 2026 12:16pm | Jul 15, 2026 12:16pm |  |  | Fair | No | Found supply ok customer said issue was resolved
Non-Outage | J.E.26.07.12795 | C001855437 | Neckell Ormsby | St.Mary | Completed | Load_240452 | Highgate - 210 | Jul 15, 2026 7:37am | Jul 15, 2026 7:38am | Jul 15, 2026 8:09am | Jul 15, 2026 8:09am | Jul 15, 2026 8:53am | Jul 15, 2026 9:09am | Jul 15, 2026 9:10am | Jul 15, 2026 9:10am |  |  | Fair | No | Troubleshoot and found internal fault customer was advised voltage left at meter socket 114v 114v 228v
Non-Outage | J.E.26.07.14162 | C001855435 | Neckell Ormsby | St.Mary | Completed | Load_252384 | Highgate - 210 | Jul 15, 2026 7:37am | Jul 15, 2026 7:38am | Jul 15, 2026 10:55am | Jul 15, 2026 10:55am | Jul 15, 2026 11:17am | Jul 15, 2026 11:33am | Jul 15, 2026 11:37am | Jul 15, 2026 11:37am |  |  | Fair | No | Troubleshoot and found corrosion at pole used 1- one bolt clamp to correct issue voltage left 119v 117v 236vNB: Tablet keeps running out of charge after starting shift with %100 Needs a reliable charging source
Non-Outage | J.E.26.06.31818 | C001855434 | Andrew Powell | null | Completed | null | null | Jul 15, 2026 7:36am | Jul 15, 2026 7:36am | Jul 15, 2026 7:58am | Jul 15, 2026 7:58am | Jul 15, 2026 7:59am | Jul 15, 2026 8:01am | Jul 15, 2026 8:08am | Jul 15, 2026 8:08am | LeaningPole |  | Fair | No | Found defective 35 class 5 T construction wooden pole with 24 kv primary and open wire secondary attached, need urgent attention please refer to maintenance department for replacement.
Non-Outage | J.E.26.03.23563 | C001855433 | Andrew Powell | null | Completed | null | null | Jul 15, 2026 7:35am | Jul 15, 2026 7:36am | Jul 15, 2026 9:55am | Jul 15, 2026 9:55am | Jul 15, 2026 9:55am | Jul 15, 2026 9:55am | Jul 15, 2026 9:56am | Jul 15, 2026 9:56am | LeaningPole |  | Fair | No | Premises found okay customer stated that fault resolved.
Outage | J.E.26.07.16877 | C001855432 | Romaine Roberts | St.Mary | Completed | Load_262034 | Blackstonedge - 110 | Jul 15, 2026 7:35am | Jul 15, 2026 7:35am | Jul 15, 2026 8:28am | Jul 15, 2026 8:28am | Jul 15, 2026 9:33am | Jul 15, 2026 9:49am | Jul 15, 2026 9:49am | Jul 15, 2026 9:49am |  |  | Fair | No | Supply found in area customer said supply restore about 10;30pm 14/jul/26
Non-Outage | J.E.26.07.16947 | C001855431 | Richard Samuda | Manchester | Completed | Load_243321 | Porus - 310 | Jul 15, 2026 7:30am | Jul 15, 2026 7:30am | Jul 15, 2026 8:23am | Jul 15, 2026 8:23am | Jul 15, 2026 8:39am | Jul 15, 2026 8:46am | Jul 15, 2026 8:48am | Jul 15, 2026 8:48am | BrokenPole |  | Fair | No | Leaning primary T 40ft class 4 primary dislodge but floating primary in contact but pole leaning towards road customer concerns it may fall in road pole hole is already dig
Non-Outage | J.E.26.07.15127 | C001855429 | Richard Samuda | Manchester | Completed | Load_244820 | Porus - 210 | Jul 15, 2026 7:29am | Jul 15, 2026 7:31am | Jul 15, 2026 8:06am | Jul 15, 2026 8:06am | Jul 15, 2026 8:06am | Jul 15, 2026 8:06am | Jul 15, 2026 8:06am | Jul 15, 2026 8:06am | BrokenWire |  | Fair | No | Premises not located and call to check no answer
Non-Outage | J.E.26.07.16951 | C001855428 | Cliton Henry | null | Completed | null | null | Jul 15, 2026 7:27am | Jul 15, 2026 7:28am | Jul 15, 2026 8:50am | Jul 15, 2026 8:50am | Jul 15, 2026 8:50am | Jul 15, 2026 8:51am | Jul 15, 2026 8:51am | Jul 15, 2026 8:51am |  |  | Fair | No | Supply restored, related to outage #16952
Outage | J.E.26.07.16952 | C001855427 | Cliton Henry | St.Mary | Completed | Load_247017 | Oracabessa - 110 | Jul 15, 2026 7:27am | Jul 15, 2026 7:28am | Jul 15, 2026 7:46am | Jul 15, 2026 7:46am | Jul 15, 2026 8:17am | Jul 15, 2026 8:41am | Jul 15, 2026 8:42am | Jul 15, 2026 8:42am |  |  | Fair | No | A blown 2 amp fuse found for a 25 kva transformer at pole #0013363 at the entrance to America Alley due to birds. Supply restored using 1- 2amp fuse.
Outage | J.E.26.07.15639 | C001855425 | Barnett Brown | Manchester | Completed | Load_573618 | Spur Tree - 310 | Jul 15, 2026 7:19am | Jul 15, 2026 7:22am | Jul 15, 2026 7:34am | Jul 15, 2026 10:49am | Jul 15, 2026 10:49am | Jul 15, 2026 10:49am | Jul 15, 2026 10:53am | Jul 15, 2026 10:53am |  |  | Fair | No | Patrol line, found nothing, replace blown 8 amp junction fuse pole number 615944 and blown 3 amp transformer fuse
Non-Outage | J.E.26.07.16425 | C001855423 | Roemello Brown | Trelawny | Completed | Load_574709 | Greenwood - 210 | Jul 15, 2026 7:11am | Jul 15, 2026 7:11am | Jul 15, 2026 1:25pm | Jul 15, 2026 1:25pm | Jul 15, 2026 1:25pm | Jul 15, 2026 1:25pm | Jul 15, 2026 1:27pm | Jul 15, 2026 1:27pm |  |  | Fair | No | This call is for the st.james team please transfer to them please
Non-Outage | J.E.26.07.16915 | C001855424 | Roemello Brown | Trelawny | Completed | Load_255405 | Greenwood - 110 | Jul 15, 2026 7:11am | Jul 15, 2026 7:11am | Jul 15, 2026 9:13am | Jul 15, 2026 9:47am | Jul 15, 2026 10:38am | Jul 15, 2026 10:38am | Jul 15, 2026 10:54am | Jul 15, 2026 10:54am |  |  | Fair | No | Customer meter socket defective inform the customer to get an private electrician to have it change Voltage found 118/118/236Voltage leave 118/118/236
Outage | J.E.26.07.16377 | C001855421 | Clyde Brown | St.Ann | Completed | Load_250095 | Cardiff Hall - 310 | Jul 15, 2026 7:09am | Jul 15, 2026 8:11am | Jul 15, 2026 8:55am | Jul 15, 2026 8:55am | Jul 15, 2026 2:03pm | Jul 15, 2026 2:05pm | Jul 15, 2026 2:58pm | Jul 15, 2026 2:58pm | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards | Y | Fair | No | Blown 20 amps junction fuse caused by big tree torn down primary and secondary line 4 span same spliced and retention with 4 splicing sleeve,3preform 15ft-#2conductor and 6-clamp.blown 20 amps junction fuse at Works replaced
Outage | J.E.26.07.16434 | C001855422 | Clyde Brown | St.Ann | Completed | Load_264725 | Cardiff Hall - 310 | Jul 15, 2026 7:09am | Jul 15, 2026 8:12am | Jul 15, 2026 8:55am | Jul 15, 2026 2:59pm | Jul 15, 2026 2:59pm | Jul 15, 2026 2:48pm | Jul 15, 2026 3:09pm | Jul 15, 2026 3:09pm | BrokenPole |  | Fair | No | Blown 10 amps junction fuse caused by T35c6 pole broken At Burns Cedar caused by tree fell on line,line isolated and blown 15 amps junction at Silver spring replaced.
Outage | J.E.26.07.16878 | C001855420 | Collin Robinson | Portland | Completed | Load_239767 | Port Antonio - 310 | Jul 15, 2026 7:07am | Jul 15, 2026 7:07am | Jul 15, 2026 8:14am | Jul 15, 2026 8:14am | Jul 15, 2026 8:47am | Jul 15, 2026 9:31am | Jul 15, 2026 9:35am | Jul 15, 2026 9:35am |  |  | Fair | No | Replace 10 amps junction fuse and realize that 50 KVA transformer defective refer to maintenance
Outage | J.E.26.07.16920 | C001855417 | Denton Williams | Portland | Completed | Load_239767 | Port Antonio - 310 | Jul 15, 2026 7:05am | Jul 15, 2026 4:12pm | Jul 15, 2026 4:21pm | Jul 15, 2026 4:21pm | Jul 15, 2026 4:22pm | Jul 15, 2026 4:22pm | Jul 15, 2026 4:23pm | Jul 15, 2026 4:23pm | Fire |  | Fair | No | Customer stated that power is restored to area
Outage | J.E.26.07.16884 | C001855392 | Derrick Dawkins | St.James | Completed | Load_575161 | Bogue - 310 | Jul 15, 2026 12:15am | Jul 15, 2026 12:15am | Jul 15, 2026 12:46am | Jul 15, 2026 12:46am | Jul 15, 2026 12:46am | Jul 15, 2026 12:47am | Jul 15, 2026 12:47am | Jul 15, 2026 12:47am |  |  | Fair | No | Check and found premises ok
Outage | J.E.26.07.16886 | C001855391 | Delano Gayle | St.Catherine | Completed | Load_263727 | Tredegar - 210 | Jul 14, 2026 11:19pm | Jul 14, 2026 11:19pm | Jul 15, 2026 2:05am | Jul 15, 2026 2:19am | Jul 15, 2026 2:19am | Jul 15, 2026 2:25am | Jul 15, 2026 2:25am | Jul 15, 2026 2:25am | BrokenWire |  | Fair | No | Premises not found no answer from customer, area patrolled and found okay
Outage | J.E.26.07.16883 | C001855390 | Derrick Dawkins | St.James | Completed | Load_576009 | Bogue - 310 | Jul 14, 2026 11:13pm | Jul 14, 2026 11:14pm | Jul 15, 2026 12:01am | Jul 15, 2026 12:11am | Jul 15, 2026 12:11am | Jul 15, 2026 12:21am | Jul 15, 2026 12:46am | Jul 15, 2026 12:46am |  |  | Fair | No | Check and found premises ok
Outage | J.E.26.07.16337 | C001855385 | Daniel Francis | St.Ann | Completed | Load_246156 | Roaring River - 410 | Jul 14, 2026 10:53pm | Jul 15, 2026 7:32am | Jul 15, 2026 7:59am | Jul 15, 2026 7:59am | Jul 15, 2026 9:17am | Jul 15, 2026 9:18am | Jul 15, 2026 9:20am | Jul 15, 2026 9:20am |  |  | Fair | No | Found ok re connected from 14th
Outage | J.E.26.07.16865 | C001855375 | Richman Whyte | Westmoreland | Completed | Load_256238 | Paradise - 310 | Jul 14, 2026 10:08pm | Jul 14, 2026 10:09pm | Jul 14, 2026 10:53pm | Jul 14, 2026 10:53pm | Jul 14, 2026 10:54pm | Jul 14, 2026 10:54pm | Jul 14, 2026 10:58pm | Jul 14, 2026 10:58pm |  |  | Fair | No | Customer need to repair her line before it order for it to be connected
Outage | J.E.26.07.16709 | C001855373 | Richman Whyte | Westmoreland | Completed | Load_261287 | Paradise - 310 | Jul 14, 2026 9:55pm | Jul 14, 2026 9:56pm | Jul 14, 2026 10:20pm | Jul 14, 2026 10:20pm | Jul 14, 2026 10:20pm | Jul 14, 2026 10:21pm | Jul 14, 2026 10:31pm | Jul 14, 2026 10:31pm |  |  | Fair | No | Replace three amp twenty five kva transformer fuse voltage 113 114 226
Outage | J.E.26.07.16764 | C001855369 | Derrick Dawkins | St.James | Completed | Load_265607 | Bogue - 310 | Jul 14, 2026 9:41pm | Jul 14, 2026 11:12pm | Jul 14, 2026 11:43pm | Jul 14, 2026 11:43pm | Jul 14, 2026 11:49pm | Jul 14, 2026 11:52pm | Jul 14, 2026 11:54pm | Jul 14, 2026 11:54pm | BrokenWire |  | Fair | No | Cannot locate customer by mobile phone
Outage | J.E.26.07.16571 | C001855359 | Donald Cunningham | St.Catherine | Completed | Load_252422 | Tredegar - 310 | Jul 14, 2026 9:21pm | Jul 15, 2026 8:12am | Jul 15, 2026 8:15am | Jul 15, 2026 8:16am | Jul 15, 2026 9:00am | Jul 15, 2026 9:14am | Jul 15, 2026 9:16am | Jul 15, 2026 9:16am |  |  | Fair | No | 25 kva transformer found trip same reset illegal connection in area refer to loses crew
Outage | J.E.26.07.16586 | C001855360 | Delano Gayle | St.Catherine | Completed | Load_1001612 | Tredegar - 310 | Jul 14, 2026 9:21pm | Jul 14, 2026 11:21pm | Jul 14, 2026 11:26pm | Jul 14, 2026 11:26pm | Jul 15, 2026 1:35am | Jul 15, 2026 2:05am | Jul 15, 2026 2:05am | Jul 15, 2026 2:05am |  |  | Fair | No | Trip 25kva transformer no pole number, patrolled and found circuit okay reset transformer
Non-Outage | J.E.26.07.09592 | C001855355 | Evan Spaulding | null | Completed | null | null | Jul 14, 2026 9:16pm | Jul 14, 2026 9:16pm | Jul 14, 2026 9:59pm | Jul 14, 2026 9:59pm | Jul 14, 2026 10:18pm | Jul 14, 2026 10:22pm | Jul 14, 2026 10:23pm | Jul 14, 2026 10:23pm | LeaningPole |  | Fair | No | Leaning 10.5 m concrete pole with open wire secondary.
Outage | J.E.26.07.16652 | C001855354 | Evan Spaulding | St.Mary | Completed | Load_238714 | Highgate -110 | Jul 14, 2026 9:15pm | Jul 14, 2026 9:16pm | Jul 14, 2026 9:47pm | Jul 14, 2026 9:47pm | Jul 14, 2026 9:47pm | Jul 14, 2026 9:48pm | Jul 14, 2026 9:55pm | Jul 14, 2026 9:55pm |  |  | Fair | No | I refer this location two times already,there is a leaning concrete pole there,wires are low ,customer says the power is on and off in resents times ,please refer it again to maintenance,also you can send a in the the morning to check on the power.
Outage | J.E.26.07.16708 | C001855353 | Omar King | St.Ann | Completed | Load_251393 | Ocho Rios - 310 | Jul 14, 2026 9:09pm | Jul 14, 2026 9:09pm | Jul 14, 2026 9:21pm | Jul 14, 2026 10:40pm | Jul 14, 2026 10:49pm | Jul 14, 2026 11:37pm | Jul 14, 2026 11:37pm | Jul 14, 2026 11:37pm | Fire |  | Fair | No | Found customer service wire defective as been replaced 100 feet customer is now with supply
Outage | J.E.26.07.16582 | C001855351 | Derrick Dawkins | St.James | Completed | Load_264733 | Bogue - 310 | Jul 14, 2026 9:05pm | Jul 14, 2026 11:10pm | Jul 14, 2026 11:25pm | Jul 14, 2026 11:57pm | Jul 14, 2026 11:59pm | Jul 15, 2026 12:01am | Jul 15, 2026 12:01am | Jul 15, 2026 12:01am |  |  | Fair | No | Customer says dat light restored
Outage | J.E.26.07.16041 | C001855349 | Omar King | St.Ann | Completed | Load_253537 | Upper White River - 210 | Jul 14, 2026 9:03pm | Jul 14, 2026 9:04pm | Jul 14, 2026 9:15pm | Jul 14, 2026 9:15pm | Jul 14, 2026 9:20pm | Jul 14, 2026 9:20pm | Jul 14, 2026 9:21pm | Jul 14, 2026 9:21pm |  |  | Fair | No | Unable to locate customer call several times no answer directions not sufficient
Outage | J.E.26.07.16518 | C001855350 | Omar King | St.Ann | Completed | Load_266688 | Roaring River - 210 | Jul 14, 2026 9:03pm | Jul 14, 2026 9:04pm | Jul 14, 2026 11:38pm | Jul 14, 2026 11:38pm | Jul 15, 2026 12:08am | Jul 15, 2026 12:50am | Jul 15, 2026 12:50am | Jul 15, 2026 12:50am | TreeContact |  | Fair | No | Found secondary jumper open as been repaired customer is now with supply
Outage | J.E.26.07.16689 | C001855348 | Kaydon Taylor | KSAN | Completed | Load_256020 | Constant Spring - 310 | Jul 14, 2026 9:00pm | Jul 14, 2026 9:00pm | Jul 14, 2026 9:18pm | Jul 14, 2026 9:47pm | Jul 14, 2026 10:29pm | Jul 14, 2026 10:41pm | Jul 14, 2026 10:41pm | Jul 14, 2026 10:41pm |  |  | Fair | No | Reset customer breaker
Outage | J.E.26.07.16575 | C001855346 | Collin Robinson | Portland | Completed | Load_354679 | Port Antonio - 410 | Jul 14, 2026 8:56pm | Jul 14, 2026 8:57pm | Jul 15, 2026 9:36am | Jul 15, 2026 10:36am | Jul 15, 2026 10:36am | Jul 15, 2026 10:40am | Jul 15, 2026 10:40am | Jul 15, 2026 10:40am |  |  | Fair | No | Customer was disconnected for none payment
Outage | J.E.26.07.16158 | C001855339 | Raymond Lewis | St.Ann | Completed | Load_239328 | Cardiff Hall - 210 | Jul 14, 2026 8:32pm | Jul 14, 2026 8:32pm | Jul 14, 2026 10:01pm | Jul 14, 2026 10:01pm | Jul 14, 2026 10:01pm | Jul 14, 2026 10:02pm | Jul 14, 2026 10:02pm | Jul 14, 2026 10:02pm |  |  | SevereWind | No | Supply restored
Outage | J.E.26.07.16550 | C001855338 | Raymond Lewis | St.Ann | Completed | Load_239328 | Cardiff Hall - 210 | Jul 14, 2026 8:32pm | Jul 14, 2026 8:32pm | Jul 14, 2026 10:00pm | Jul 14, 2026 10:00pm | Jul 14, 2026 10:00pm | Jul 14, 2026 10:01pm | Jul 14, 2026 10:01pm | Jul 14, 2026 10:01pm |  |  | SevereWind | No | Supply restored
Outage | J.E.26.07.15637 | C001855335 | Raymond Lewis | St.Ann | Completed | Load_239328 | Cardiff Hall - 210 | Jul 14, 2026 8:27pm | Jul 14, 2026 8:28pm | Jul 14, 2026 8:42pm | Jul 14, 2026 8:42pm | Jul 14, 2026 9:13pm | Jul 14, 2026 9:59pm | Jul 14, 2026 9:59pm | Jul 14, 2026 9:59pm |  |  | SevereWind | No | Reset 10 kva x former
Outage | J.E.26.07.15845 | C001855336 | Raymond Lewis | St.Ann | Completed | Load_239328 | Cardiff Hall - 210 | Jul 14, 2026 8:27pm | Jul 14, 2026 8:28pm | Jul 14, 2026 9:59pm | Jul 14, 2026 9:59pm | Jul 14, 2026 9:59pm | Jul 14, 2026 10:00am | Jul 14, 2026 10:00pm | Jul 14, 2026 10:00pm |  |  | SevereWind | No | Supply restored
Outage | J.E.26.07.16207 | C001855331 | Rayon Foster | Hanover | Completed | Load_260650 | Orange Bay - 210 | Jul 14, 2026 8:19pm | Jul 14, 2026 8:20pm | Jul 14, 2026 8:28pm | Jul 14, 2026 8:30pm | Jul 14, 2026 10:46pm | Jul 14, 2026 11:11pm | Jul 14, 2026 11:22pm | Jul 14, 2026 11:22pm |  |  | Fair | No | Patrol primary line to find 2 blown junction fuse and 1 blown 15 kva transformer fuse complete line patrol before replacing 1 10 amp and 1 20amp junction fuse and 1 2 amp transformer fuse at same and close cause by lightning
Outage | J.E.26.07.16336 | C001855332 | Rayon Foster | Hanover | Completed | Load_303135 | Orange Bay - 210 | Jul 14, 2026 8:19pm | Jul 14, 2026 9:03pm | Jul 15, 2026 9:45am | Jul 15, 2026 9:50am | Jul 15, 2026 1:46pm | Jul 15, 2026 1:47pm | Jul 15, 2026 1:48pm | Jul 15, 2026 1:48pm | LeaningPole |  | Fair | No | Call is related to outage last night customer power supply was restored
Outage | J.E.26.07.16563 | C001855330 | Rayon Foster | Hanover | Completed | Load_253325 | Orange Bay - 210 | Jul 14, 2026 8:19pm | Jul 15, 2026 8:27am | Jul 14, 2026 11:22pm | Jul 14, 2026 11:22pm | Jul 14, 2026 11:22pm | Jul 14, 2026 11:58pm | Jul 14, 2026 11:59pm | Jul 14, 2026 11:59pm |  |  | Fair | No | Patrol secondary line to find damaged transformer drop lead open 1 25kva to change damage drop lead use about 6 ft of insulated copper wire and 1 one bolt clamp for repairs voltage left 116v/117v/231v
Outage | J.E.26.07.16523 | C001855326 | Richard Nicholas | St.Catherine | Completed | Load_260326 | Tredegar - 210 | Jul 14, 2026 8:13pm | Jul 14, 2026 8:56pm | Jul 14, 2026 10:24pm | Jul 14, 2026 10:24pm | Jul 14, 2026 11:22pm | Jul 14, 2026 11:22pm | Jul 14, 2026 11:24pm | Jul 14, 2026 11:24pm | BrokenWire |  | Fair | No | Remade broken 3w Rammy service phase joint at pothead,2 linket was used.voltage reading 118,117 and 235v.
Outage | J.E.26.07.15613 | C001855317 | Wan Carlos Scarlett | Portmore | Completed | Load_266600 | Naggo Head - 610 | Jul 14, 2026 7:50pm | Jul 14, 2026 7:51pm | Jul 14, 2026 8:34pm | Jul 14, 2026 9:41pm | Jul 14, 2026 9:41pm | Jul 14, 2026 9:42pm | Jul 14, 2026 9:42pm | Jul 14, 2026 9:42pm |  |  | Fair | No | Customer confirm that power supply has been restored
Non-Outage | J.E.26.07.13684 | C001855313 | Wayne Dillion | St.Elizabeth | Completed | Load_266444 | Maggotty - 110 | Jul 14, 2026 7:36pm | Jul 14, 2026 7:41pm | Jul 15, 2026 6:07pm | Jul 15, 2026 6:07pm | Jul 15, 2026 6:07pm | Jul 15, 2026 6:14pm | Jul 15, 2026 6:15pm | Jul 15, 2026 6:15pm |  |  | Fair | No | Please refer this call to field for a meter change meter showing error 3
Outage | J.E.26.07.16515 | C001855306 | Michael Christian | St.James | Completed | Load_258445 | Rose Hall - 110 | Jul 14, 2026 7:32pm | Jul 15, 2026 8:21am | Jul 15, 2026 10:50am | Jul 15, 2026 12:21pm | Jul 15, 2026 12:37pm | Jul 15, 2026 12:42pm | Jul 15, 2026 12:42pm | Jul 15, 2026 12:42pm |  |  | Fair | No | Check and found okay voltage 111 114 224 at pothead
Non-Outage | J.E.26.07.12025 | C001855293 | Marlon Authors | Manchester | Completed | Load_293011 | Spur Tree - 210 | Jul 14, 2026 7:20pm | Jul 14, 2026 7:23pm | Jul 14, 2026 8:52pm | Jul 14, 2026 8:52pm | Jul 14, 2026 9:10pm | Jul 14, 2026 9:11pm | Jul 14, 2026 9:12pm | Jul 14, 2026 9:12pm | Fire |  | Fair | No | Unable to locate and the customer not answering the phone
Non-Outage | J.E.26.07.12573 | C001855292 | Marlon Authors | St.Elizabeth | Completed | Load_1002214 | Maggotty - 210 | Jul 14, 2026 7:20pm | Jul 14, 2026 7:23pm | Jul 14, 2026 8:45pm | Jul 14, 2026 8:46pm | Jul 14, 2026 8:46pm | Jul 14, 2026 8:50pm | Jul 14, 2026 8:50pm | Jul 14, 2026 8:50pm | Fire |  | Fair | No | Customer said burnt meter was replaced by JPS technicians and the supply is okay
Outage | J.E.26.07.16548 | C001855288 | Floyd Taylor | Trelawny | Completed | Load_248121 | Greenwood - 110 | Jul 14, 2026 7:18pm | Jul 14, 2026 7:20pm | Jul 14, 2026 8:45pm | Jul 14, 2026 8:45pm | Jul 14, 2026 9:38pm | Jul 15, 2026 7:18am | Jul 15, 2026 7:19am | Jul 15, 2026 7:19am | Fire |  | Fair | No | Remove illegal connection from voltage readings left 109,110,218
Outage | J.E.26.07.16540 | C001855286 | Swon Miller | St.James | Completed | Load_269402 | Rose Hall - 210 | Jul 14, 2026 7:17pm | Jul 14, 2026 7:20pm | Jul 14, 2026 8:12pm | Jul 14, 2026 8:12pm | Jul 14, 2026 8:36pm | Jul 21, 2026 9:11am | Jul 14, 2026 9:13pm | Jul 14, 2026 9:13pm |  |  | Fair | No | Check and found okay voltage found 114/114/229 voltage left 114/114/229 customer was having internal problems which caused breaker to trip advise customer to reset breaker
Outage | J.E.26.07.16541 | C001855287 | Marlon Authors | Manchester | Completed | Load_244587 | Spur Tree - 210 | Jul 14, 2026 7:17pm | Jul 14, 2026 7:19pm | Jul 14, 2026 9:12pm | Jul 14, 2026 9:12pm | Jul 14, 2026 9:54pm | Jul 14, 2026 10:14pm | Jul 14, 2026 10:14pm | Jul 14, 2026 10:14pm | BrokenWire |  | Fair | No | Supply checked and found low voltage rdg at the transformer drop leads are 107v,108v and cross phased 217 volts. Isolate and close 25 kva transformer to check which has already maxed out to tap 5. Please refer same to the maintenance department for further assistance
Outage | J.E.26.07.16513 | C001855284 | Swon Miller | St.James | Completed | Load_255160 | Queens Drive - 710 | Jul 14, 2026 6:46pm | Jul 14, 2026 6:46pm | Jul 14, 2026 7:03pm | Jul 14, 2026 7:03pm | Jul 14, 2026 7:39pm | Jul 14, 2026 8:06pm | Jul 14, 2026 8:12pm | Jul 14, 2026 8:12pm |  |  | Fair | No | Found 25 kva transformer fuse blown and fuse barrel burnt up replace fuse barrel and 3 amp in a 25 kva transformer
Outage | J.E.26.07.16361 | C001855277 | Hartley Chin | St.Catherine | Completed | Load_567911 | Rhodens Pen - 310 | Jul 14, 2026 6:31pm | Jul 14, 2026 6:32pm | Jul 14, 2026 8:34pm | Jul 14, 2026 9:06pm | Jul 14, 2026 9:06pm | Jul 14, 2026 9:18pm | Jul 14, 2026 9:29pm | Jul 14, 2026 9:29pm | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Found 10 amp junction blown line patrolled found coconut tree on line remove and refused
Outage | J.E.26.07.16439 | C001855278 | Milton Charlton | KSAN | Completed | Load_262669 | West Kings House - 410 | Jul 14, 2026 6:31pm | Jul 14, 2026 6:32pm | Jul 14, 2026 7:38pm | Jul 14, 2026 7:38pm | Jul 14, 2026 8:10pm | Jul 14, 2026 7:50pm | Jul 14, 2026 8:12pm | Jul 14, 2026 8:12pm |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.07.16497 | C001855276 | Richard Grant | St.Catherine | Completed | Load_268207 | New Michelton - 210 | Jul 14, 2026 6:31pm | Jul 14, 2026 6:32pm | Jul 14, 2026 7:22pm | Jul 14, 2026 7:22pm | Jul 14, 2026 8:06pm | Jul 14, 2026 8:09pm | Jul 14, 2026 8:09pm | Jul 14, 2026 8:09pm |  |  | Fair | No | Calls to customer number goes unanswered. Insufficient direction given. Premises not found.
Outage | J.E.26.07.16215 | C001855275 | Kaydon Taylor | KSAS | Completed | Load_254879 | Duhaney - 310 | Jul 14, 2026 6:30pm | Jul 14, 2026 6:31pm | Jul 14, 2026 6:35pm | Jul 14, 2026 6:38pm | Jul 14, 2026 6:38pm | Jul 14, 2026 6:38pm | Jul 14, 2026 6:39pm | Jul 14, 2026 6:39pm |  |  | Fair | No | Found okay
Outage | J.E.26.07.16492 | C001855273 | Stephen Taylor | St.Thomas | Completed | Load_264218 | Lysson - 410 | Jul 14, 2026 6:28pm | Jul 15, 2026 8:01am | Jul 15, 2026 12:59pm | Jul 15, 2026 1:00pm | Jul 15, 2026 1:00pm | Jul 15, 2026 4:11pm | Jul 15, 2026 4:11pm | Jul 15, 2026 4:11pm |  |  | Fair | No
Outage | J.E.26.07.16475 | C001855272 | Romeo Brissett | St.James | Completed | Load_576009 | Bogue - 310 | Jul 14, 2026 6:12pm | Jul 14, 2026 6:13pm | Jul 14, 2026 7:16pm | Jul 14, 2026 8:58pm | Jul 14, 2026 9:27pm | Jul 14, 2026 10:00pm | Jul 14, 2026 10:08pm | Jul 14, 2026 10:08pm |  |  | Fair | No | Customers was connected individually by escalation technician
Outage | J.E.26.07.16401 | C001855270 | Collin Robinson | Portland | Completed | Load_247771 | Port Antonio - 310 | Jul 14, 2026 6:07pm | Jul 14, 2026 6:07pm | Jul 14, 2026 7:54pm | Jul 14, 2026 7:57pm | Jul 14, 2026 8:23pm | Jul 14, 2026 8:42pm | Jul 14, 2026 8:42pm | Jul 14, 2026 8:42pm | BrokenWire |  | Fair | No | Repair and retention broken #6 twisted wire Voltage reading 119v 120v 239v
Outage | J.E.26.07.16456 | C001855269 | Collin Robinson | Portland | Completed | Load_261023 | Port Antonio - 410 | Jul 14, 2026 6:07pm | Jul 14, 2026 6:07pm | Jul 14, 2026 7:14pm | Jul 14, 2026 7:14pm | Jul 14, 2026 7:48pm | Jul 14, 2026 7:54pm | Jul 14, 2026 7:54pm | Jul 14, 2026 7:54pm | BrokenWire |  | Fair | No | Reconnect one leg of broken #6 twisted wire Voltage reading 118v 117v 235v
Outage | J.E.26.07.16440 | C001855265 | Derrick Dawkins | St.James | Completed | Load_256241 | Bogue - 310 | Jul 14, 2026 6:00pm | Jul 14, 2026 11:11pm | Jul 14, 2026 11:21pm | Jul 14, 2026 11:54pm | Jul 14, 2026 11:55pm | Jul 14, 2026 11:56pm | Jul 14, 2026 11:57pm | Jul 14, 2026 11:57pm |  |  | Fair | No | Check and found premises ok
Outage | J.E.26.07.16435 | C001855263 | Romeo Brissett | St.James | Completed | Load_269068 | Bogue - 310 | Jul 14, 2026 5:58pm | Jul 14, 2026 6:00pm | Jul 14, 2026 7:29pm | Jul 14, 2026 7:29pm | Jul 14, 2026 7:54pm | Jul 14, 2026 8:53pm | Jul 14, 2026 8:57pm | Jul 14, 2026 8:57pm |  |  | Fair | No | Removed vegetation and replaced (1)10KVA transformer,
Outage | J.E.26.07.16465 | C001855262 | Tajay Bernard | Hanover | Completed | Load_265902 | Orange Bay - 310 | Jul 14, 2026 5:57pm | Jul 14, 2026 6:13pm | Jul 14, 2026 6:20pm | Jul 14, 2026 6:27pm | Jul 14, 2026 7:16pm | Jul 14, 2026 8:11pm | Jul 14, 2026 8:12pm | Jul 14, 2026 8:12pm |  |  | Fair | No | Check and found 1 pole span of secondary neutral broken, the section that was affected was isolated and approximately 3 customers are without power. Bushing has to be done before any work can be done refer to maintenance
Outage | J.E.26.07.16449 | C001855253 | Marlon Brown | Trelawny | Completed | Load_292205 | Duncans - 210 | Jul 14, 2026 5:47pm | Jul 14, 2026 5:54pm | Jul 14, 2026 6:47pm | Jul 14, 2026 6:47pm | Jul 14, 2026 7:06pm | Jul 14, 2026 7:31pm | Jul 14, 2026 7:31pm | Jul 14, 2026 7:31pm |  |  | Fair | No | Clean and remake joint at pole use 1 pg clamp. Voltage found at pothead 116Voltage leaving at pothead 116/116=232v.
Outage | J.E.26.07.16142 | C001855252 | Romeo Brissett | St.James | Completed | Load_257630 | Bogue - 310 | Jul 14, 2026 5:45pm | Jul 14, 2026 6:03pm | Jul 14, 2026 10:09pm | Jul 14, 2026 10:09pm | Jul 14, 2026 11:38pm | Jul 14, 2026 11:20pm | Jul 14, 2026 11:42pm | Jul 14, 2026 11:42pm |  |  | Fair | No | Customers was connected by escalation individually
Outage | J.E.26.07.15945 | C001855244 | Swon Miller | St.James | Completed | Load_267138 | Queens Drive - 710 | Jul 14, 2026 5:24pm | Jul 14, 2026 5:24pm | Jul 14, 2026 6:20pm | Jul 14, 2026 6:20pm | Jul 14, 2026 6:41pm | Jul 15, 2026 6:55am | Jul 14, 2026 7:03pm | Jul 14, 2026 7:03pm |  |  | Fair | No | Check and found premises closed advise customer to make another report stating when he’ will be home voltage found 0.000 voltage left 0.000
Outage | J.E.26.07.15964 | C001855246 | Swon Miller | St.James | Completed | Load_269145 | Queens Drive - 710 | Jul 14, 2026 5:24pm | Jul 14, 2026 6:20pm | Jul 14, 2026 9:13pm | Jul 14, 2026 9:28pm | Jul 14, 2026 9:31pm | Jul 27, 2026 9:41am | Jul 14, 2026 9:41pm | Jul 14, 2026 9:41pm |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.16027 | C001855245 | Swon Miller | St.James | Completed | Load_239386 | Queens Drive - 710 | Jul 14, 2026 5:24pm | Jul 14, 2026 5:24pm | Jul 14, 2026 5:33pm | Jul 14, 2026 5:33pm | Jul 14, 2026 6:10pm | Jul 29, 2026 6:20pm | Jul 14, 2026 6:20pm | Jul 14, 2026 6:20pm |  |  | Fair | No | Check and found okay voltage found 115/114/231 customer states that power supply has been restored voltage left 115/114/231
Non-Outage | J.E.26.07.16088 | C001855235 | Romeo Brissett | null | Completed | null | null | Jul 14, 2026 5:17pm | Jul 14, 2026 6:11pm | Jul 14, 2026 6:27pm | Jul 14, 2026 6:27pm | Jul 14, 2026 6:58pm | Jul 14, 2026 7:18pm | Jul 14, 2026 7:28pm | Jul 14, 2026 7:28pm | Fire |  | Fair | No | Premises was checked no fire was found, customer is unaware of report
Outage | J.E.26.07.14231 | C001855236 | Rayon Foster | St.James | Completed | Load_253569 | Bogue - 510 | Jul 14, 2026 5:17pm | Jul 15, 2026 8:42am | Jul 15, 2026 8:58am | Jul 15, 2026 8:58am | Jul 15, 2026 9:16am | Jul 15, 2026 9:50am | Jul 15, 2026 9:50am | Jul 15, 2026 9:50am |  |  | Fair | No | Found working ok customer said her power was restored few days ago after a power outage and was restored by a ps team
Outage | J.E.26.07.15797 | C001855238 | Tajay Bernard | Hanover | Completed | Load_575279 | Orange Bay - 310 | Jul 14, 2026 5:17pm | Jul 14, 2026 6:45pm | Jul 14, 2026 8:13pm | Jul 14, 2026 8:13pm | Jul 14, 2026 8:23pm | Jul 14, 2026 8:40pm | Jul 14, 2026 8:41pm | Jul 14, 2026 8:41pm |  |  | Fair | No | Area check and found okay unable to locate customer on premises. International number was given so we couldn’t get ahold of the customer
Outage | J.E.26.07.16307 | C001855237 | Barrington Brown | St.James | Completed | Load_266148 | Bogue - 510 | Jul 14, 2026 5:17pm | Jul 14, 2026 5:26pm | Jul 14, 2026 6:48pm | Jul 14, 2026 6:48pm | Jul 14, 2026 8:11pm | Jul 14, 2026 8:13pm | Jul 14, 2026 8:13pm | Jul 14, 2026 8:13pm |  |  | Fair | No | Customer has internal issues and was abvised to have electrician do checks
Outage | J.E.26.07.15723 | C001855234 | Derrick Dawkins | St.James | Completed | Load_1002490 | Bogue - 310 | Jul 14, 2026 5:16pm | Jul 14, 2026 11:11pm | Jul 15, 2026 12:47am | Jul 15, 2026 12:47am | Jul 15, 2026 1:03am | Jul 15, 2026 1:16am | Jul 15, 2026 1:18am | Jul 15, 2026 1:18am |  |  | Fair | No | Premises not found cannot locate customer
Outage | J.E.26.07.16416 | C001855225 | Javid Vernon | Westmoreland | Completed | Load_247337 | Paradise - 210 | Jul 14, 2026 5:07pm | Jul 14, 2026 5:12pm | Jul 14, 2026 8:25pm | Jul 14, 2026 8:25pm | Jul 14, 2026 9:36pm | Jul 14, 2026 9:56pm | Jul 14, 2026 10:06pm | Jul 14, 2026 10:06pm |  |  | Fair | No | Check and found customer meter single phase needs to be replaced voltage reading 116/119/235 customer requesting urgent assistance refer to field service
Outage | J.E.26.07.16381 | C001855222 | Hartley Chin | Clarendon | Completed | Load_256530 | Parnassus - 310 | Jul 14, 2026 5:01pm | Jul 14, 2026 5:05pm | Jul 14, 2026 5:27pm | Jul 14, 2026 5:27pm | Jul 14, 2026 5:48pm | Jul 14, 2026 5:57pm | Jul 14, 2026 5:58pm | Jul 14, 2026 5:58pm |  |  | Fair | No | Refer to field service , voltage reading v113 - v115 - v229 . Customer meter on the account does not match meter # on premise
Non-Outage | J.E.26.07.16224 | C001855217 | Marlon Brown | null | Completed | null | null | Jul 14, 2026 4:53pm | Jul 14, 2026 4:57pm | Jul 14, 2026 5:16pm | Jul 14, 2026 5:16pm | Jul 14, 2026 6:00pm | Jul 14, 2026 6:01pm | Jul 14, 2026 6:01pm | Jul 14, 2026 6:01pm |  |  | Fair | No | Check and found ok, internal issues. Voltage found at pothead 116/116=232vVoltage leaving at pothead 116/116=232v.
Outage | J.E.26.07.16246 | C001855214 | Floyd Taylor | Trelawny | Completed | Load_262658 | Greenwood - 110 | Jul 14, 2026 4:53pm | Jul 14, 2026 4:54pm | Jul 14, 2026 5:44pm | Jul 14, 2026 5:47pm | Jul 14, 2026 5:47pm | Jul 14, 2026 5:48pm | Jul 14, 2026 5:48pm | Jul 14, 2026 5:48pm |  |  | Fair | No | Customer power was restored
Outage | J.E.26.07.16346 | C001855212 | Marlon Brown | Trelawny | Completed | Load_262699 | Duncans - 210 | Jul 14, 2026 4:53pm | Jul 14, 2026 4:54pm | Jul 14, 2026 6:01pm | Jul 14, 2026 6:02pm | Jul 14, 2026 6:22pm | Jul 14, 2026 6:47pm | Jul 14, 2026 6:47pm | Jul 14, 2026 6:47pm | BrokenWire |  | Fair | No | Repair broken service wire neutral use 1 pg clamp. Voltage found at pothead 190/45=240Voltage leaving at pothead 120/120=240v.
Non-Outage | J.E.26.07.14523 | C001855211 | Collin Robinson | Portland | Completed | Load_254227 | Port Antonio - 410 | Jul 14, 2026 4:49pm | Jul 14, 2026 4:52pm | Jul 14, 2026 5:30pm | Jul 14, 2026 5:30pm | Jul 14, 2026 6:39pm | Jul 14, 2026 7:13pm | Jul 14, 2026 7:14pm | Jul 14, 2026 7:14pm |  |  | Rains | No | Change 3 corroded one bolt clamp at pole Voltage reading 116v 117v 233v
Non-Outage | J.E.26.07.15655 | C001855206 | Edward Royal | KSAS | Completed | Load_300798 | Cane River - 310 | Jul 14, 2026 4:44pm | Jul 14, 2026 5:01pm | Jul 15, 2026 9:28am | Jul 15, 2026 9:28am | Jul 15, 2026 9:28am | Jul 15, 2026 9:28am | Jul 15, 2026 9:28am | Jul 15, 2026 9:28am |  |  | Fair | No | Premises found close
Non-Outage | J.E.26.07.15688 | C001855204 | Edward Royal | KSAS | Completed | Load_264749 | Rockfort - 210 | Jul 14, 2026 4:44pm | Jul 14, 2026 5:01pm | Jul 14, 2026 8:19pm | Jul 14, 2026 8:19pm | Jul 14, 2026 8:25pm | Jul 14, 2026 9:08pm | Jul 14, 2026 9:08pm | Jul 14, 2026 9:08pm |  |  | Fair | No | Customer have internal problems customer have faulty wiring advise customer to get a electrician to fix the problem voltage reading 117 v
Non-Outage | J.E.26.07.15950 | C001855205 | Fitzroy Turner | KSAS | Completed | Load_243713 | Three Miles - 510 | Jul 14, 2026 4:44pm | Jul 14, 2026 5:01pm | Jul 14, 2026 8:14pm | Jul 14, 2026 8:14pm | Jul 14, 2026 9:29pm | Jul 14, 2026 9:29pm | Jul 14, 2026 9:31pm | Jul 14, 2026 9:31pm |  |  | Fair | No | Found three wire service neutral corroded at pothead use one clamp to carry out repair supply restored
Non-Outage | J.E.26.07.16217 | C001855203 | Edward Royal | KSAS | Completed | Load_575222 | Hunts Bay - 310 | Jul 14, 2026 4:44pm | Jul 14, 2026 5:01pm | Jul 14, 2026 6:45pm | Jul 14, 2026 6:45pm | Jul 14, 2026 6:48pm | Jul 14, 2026 7:03pm | Jul 14, 2026 7:04pm | Jul 14, 2026 7:04pm |  |  | Fair | No | When contacted customer by phone customer said that nobody is at the premises at the time she is requesting a visit for tomorrow at 10am
Non-Outage | J.E.26.07.16271 | C001855202 | Edward Royal | KSAS | Completed | Load_261313 | Rockfort - 210 | Jul 14, 2026 4:44pm | Jul 14, 2026 5:01pm | Jul 14, 2026 7:04pm | Jul 14, 2026 7:04pm | Jul 14, 2026 7:24pm | Jul 14, 2026 7:41pm | Jul 14, 2026 7:42pm | Jul 14, 2026 7:42pm |  |  | Fair | No | Customer have internal problems customer defective meter socket advise customer to get a electrician to fix the problem voltage reading 118 v
Non-Outage | J.E.26.07.16329 | C001855201 | Edward Royal | KSAS | Completed | Load_249935 | Rockfort - 410 | Jul 14, 2026 4:44pm | Jul 14, 2026 5:01pm | Jul 14, 2026 9:31pm | Jul 14, 2026 9:31pm | Jul 14, 2026 9:37pm | Jul 14, 2026 10:02pm | Jul 14, 2026 10:04pm | Jul 14, 2026 10:04pm |  |  | Fair | No | Spliced and reconnected service phase using 2 single bolt clamp
Non-Outage | J.E.26.07.13196 | C001855189 | Edward Royal | KSAS | Completed | Load_255768 | Hunts Bay - 310 | Jul 14, 2026 4:41pm | Jul 14, 2026 4:41pm | Jul 14, 2026 4:55pm | Jul 14, 2026 4:55pm | Jul 14, 2026 4:56pm | Jul 14, 2026 6:43pm | Jul 14, 2026 6:43pm | Jul 14, 2026 6:43pm |  |  | Fair | No | Spliced and reconnected service cable using 3 single bolt clamp
Non-Outage | J.E.26.07.08140 | C001855180 | Fitzroy Turner | KSAS | Completed | Load_262511 | Three Miles - 410 | Jul 14, 2026 4:35pm | Jul 14, 2026 4:36pm | Jul 14, 2026 4:47pm | Jul 14, 2026 4:48pm | Jul 14, 2026 5:25pm | Jul 14, 2026 5:34pm | Jul 14, 2026 5:35pm | Jul 14, 2026 5:35pm | BrokenWire |  | Fair | No | Found premises found with electricity supply
Non-Outage | J.E.26.07.15910 | C001855179 | Edward Royal | KSAS | Completed | Load_253437 | Cane River - 410 | Jul 14, 2026 4:35pm | Jul 14, 2026 4:36pm | Jul 14, 2026 10:06pm | Jul 14, 2026 10:06pm | Jul 14, 2026 10:09pm | Jul 14, 2026 10:11pm | Jul 14, 2026 10:13pm | Jul 14, 2026 10:13pm | BrokenWire |  | Fair | No | This report is for richman st mart
Non-Outage | J.E.26.07.16062 | C001855178 | Fitzroy Turner | KSAN | Completed | Load_269199 | Washington Blvd - 310 | Jul 14, 2026 4:35pm | Jul 14, 2026 4:37pm | Jul 14, 2026 5:40pm | Jul 14, 2026 5:40pm | Jul 14, 2026 8:13pm | Jul 14, 2026 8:13pm | Jul 14, 2026 8:14pm | Jul 14, 2026 8:14pm | BrokenWire |  | Fair | No | Customer premises not found
Non-Outage | J.E.26.07.16109 | C001855165 | Edward Royal | KSAS | Completed | Load_254960 | Cane River - 410 | Jul 14, 2026 4:31pm | Jul 14, 2026 4:34pm | Jul 15, 2026 9:34am | Jul 15, 2026 9:34am | Jul 15, 2026 9:34am | Jul 15, 2026 9:35am | Jul 15, 2026 9:35am | Jul 15, 2026 9:35am | Fire |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.07.16371 | C001855163 | Stephen Taylor | null | Completed | null | null | Jul 14, 2026 4:28pm | Jul 14, 2026 4:31pm | Jul 14, 2026 5:35pm | Jul 14, 2026 5:35pm | Jul 14, 2026 5:35pm | Jul 14, 2026 5:35pm | Jul 14, 2026 5:36pm | Jul 14, 2026 5:36pm |  |  | Fair | No | Clean primary line with switch stick and close up back junction with a 20 amp fuse all customer is now okay no number on pole
Non-Outage | J.E.26.07.16355 | C001855148 | Richman Whyte | null | Completed | null | null | Jul 14, 2026 4:23pm | Jul 14, 2026 4:25pm | Jul 14, 2026 4:31pm | Jul 14, 2026 4:31pm | Jul 14, 2026 4:31pm | Jul 14, 2026 4:44pm | Jul 14, 2026 4:45pm | Jul 14, 2026 4:45pm | Fire |  | Rains | No | Replace 15 amp junction fuse
Outage | J.E.26.07.15837 | C001855144 | Barrington Brown | St.James | Completed | Load_268282 | Bogue - 610 | Jul 14, 2026 4:20pm | Jul 14, 2026 4:45pm | Jul 14, 2026 8:13pm | Jul 14, 2026 8:13pm | Jul 14, 2026 9:37pm | Jul 14, 2026 10:23pm | Jul 14, 2026 10:24pm | Jul 14, 2026 10:24pm |  |  | Fair | No | Crew replaced two clamps at pot head. Customer has defective breakers on location crew abvised customer to get electrician to do checks and changed breakers. Customer meter is also burnt please refer to field service department to have meter changed.
Outage | J.E.26.07.16090 | C001855146 | Barrington Brown | St.James | Completed | Load_264282 | Bogue - 610 | Jul 14, 2026 4:20pm | Jul 14, 2026 4:45pm | Jul 14, 2026 5:23pm | Jul 14, 2026 5:23pm | Jul 14, 2026 6:10pm | Jul 14, 2026 6:48pm | Jul 14, 2026 6:48pm | Jul 14, 2026 6:48pm |  |  | Fair | No | Checked and found ok
Outage | J.E.26.07.16212 | C001855147 | Barrington Brown | St.James | Completed | Load_267953 | Bogue - 610 | Jul 14, 2026 4:20pm | Jul 14, 2026 4:45pm | Jul 14, 2026 10:24pm | Jul 14, 2026 10:24pm | Jul 14, 2026 11:18pm | Jul 14, 2026 11:19pm | Jul 14, 2026 11:19pm | Jul 14, 2026 11:19pm |  |  | Fair | No | Crew found downed unused service wires on location. Crew isolated wires and removed Area made safe.
Non-Outage | J.E.26.07.15684 | C001855133 | Wayne Dillion | St.Elizabeth | Completed | Load_244822 | Maggotty - 110 | Jul 14, 2026 4:08pm | Jul 14, 2026 4:24pm | Jul 14, 2026 4:53pm | Jul 14, 2026 4:53pm | Jul 14, 2026 4:53pm | Jul 14, 2026 4:57pm | Jul 14, 2026 4:57pm | Jul 14, 2026 4:57pm |  |  | Fair | No | Patrol and found clear replace 2 15 amp junction fuse no pole number supply restore to customer successfully
Non-Outage | J.E.26.07.12329 | C001855131 | Marlon Authors | St.Elizabeth | Completed | Load_246111 | Maggotty - 210 | Jul 14, 2026 4:07pm | Jul 14, 2026 4:09pm | Jul 14, 2026 7:02pm | Jul 14, 2026 7:02pm | Jul 14, 2026 7:03pm | Jul 14, 2026 7:07pm | Jul 14, 2026 7:07pm | Jul 14, 2026 7:07pm | BrokenWire |  | Fair | No | Customer said supply is okay
Non-Outage | J.E.26.07.12565 | C001855130 | Marlon Authors | St.Elizabeth | Completed | Load_246111 | Maggotty - 210 | Jul 14, 2026 4:07pm | Jul 14, 2026 4:09pm | Jul 14, 2026 7:07pm | Jul 14, 2026 7:07pm | Jul 14, 2026 7:07pm | Jul 14, 2026 7:09pm | Jul 14, 2026 7:09pm | Jul 14, 2026 7:09pm |  |  | Fair | No | Customer said supply is okay
Non-Outage | J.E.26.07.12998 | C001855132 | Marlon Authors | St.Elizabeth | Completed | Load_245279 | Maggotty - 210 | Jul 14, 2026 4:07pm | Jul 14, 2026 4:09pm | Jul 14, 2026 7:11pm | Jul 14, 2026 7:11pm | Jul 14, 2026 7:11pm | Jul 14, 2026 7:13pm | Jul 14, 2026 7:13pm | Jul 14, 2026 7:13pm | BrokenWire |  | Fair | No | Customer said supply is okay
Outage | J.E.26.07.15739 | C001855127 | Horace Malcolm | St.James | Completed | Load_249034 | Bogue - 610 | Jul 14, 2026 4:06pm | Jul 15, 2026 8:04am | Jul 15, 2026 8:13am | Jul 15, 2026 1:54pm | Jul 15, 2026 1:54pm | Jul 15, 2026 1:55pm | Jul 15, 2026 1:55pm | Jul 15, 2026 1:55pm | Fire |  | Fair | No | Related to previous call job number 16953
Outage | J.E.26.07.16073 | C001855123 | Raymond Carr | St.Mary | Completed | Load_257590 | Oracabessa - 210 | Jul 14, 2026 4:01pm | Jul 14, 2026 4:02pm | Jul 14, 2026 4:38pm | Jul 14, 2026 4:38pm | Jul 14, 2026 5:46pm | Jul 14, 2026 5:53pm | Jul 14, 2026 5:50pm | Jul 14, 2026 5:50pm | Fire |  | Fair | No | Supply found okay. No broken wire seen at this time of visit.
Outage | J.E.26.07.16120 | C001855118 | Raymond Carr | St.Ann | Completed | Load_265764 | Upper White River - 110 | Jul 14, 2026 4:01pm | Jul 14, 2026 4:02pm | Jul 14, 2026 8:16pm | Jul 14, 2026 8:16pm | Jul 14, 2026 8:16pm | Jul 14, 2026 8:05pm | Jul 14, 2026 8:18pm | Jul 14, 2026 8:18pm |  |  | Fair | No | Line runs in bushes. No driving access. Daytime attention is needed.
Outage | J.E.26.07.16120 | C001855122 | Raymond Carr | St.Ann | Completed | Load_265764 | Upper White River - 110 | Jul 14, 2026 4:01pm | Jul 14, 2026 4:02pm | Jul 14, 2026 8:02pm | Jul 14, 2026 8:02pm | Jul 14, 2026 8:02pm | Jul 14, 2026 8:00pm | Jul 14, 2026 8:16pm | Jul 14, 2026 8:16pm |  |  | Fair | No | Line runs in bushes. No driving access, daytime attention is needed.
Outage | J.E.26.07.16151 | C001855120 | Raymond Carr | St.Mary | Completed | Load_352012 | Oracabessa - 110 | Jul 14, 2026 4:01pm | Jul 14, 2026 4:02pm | Jul 14, 2026 5:50pm | Jul 14, 2026 5:50pm | Jul 14, 2026 5:53pm | Jul 14, 2026 5:59pm | Jul 14, 2026 5:58pm | Jul 14, 2026 5:58pm |  |  | Fair | No | Customer was advised that account is disconnected.
Outage | J.E.26.07.16272 | C001855119 | Raymond Carr | St.Mary | Completed | Load_268843 | Oracabessa - 210 | Jul 14, 2026 4:01pm | Jul 14, 2026 4:02pm | Jul 14, 2026 5:58pm | Jul 14, 2026 5:58pm | Jul 14, 2026 7:21pm | Jul 14, 2026 7:54am | Jul 14, 2026 7:57pm | Jul 14, 2026 7:57pm | BrokenWire |  | Fair | No | Supply was reconnected at JPS pole.
Outage | J.E.26.07.16195 | C001855117 | Tyrese Williams | St.Ann | Completed | Load_241654 | Cardiff Hall - 310 | Jul 14, 2026 3:59pm | Jul 14, 2026 4:02pm | Jul 14, 2026 4:09pm | Jul 14, 2026 7:29pm | Jul 14, 2026 7:29pm | Jul 14, 2026 7:31pm | Jul 14, 2026 7:31pm | Jul 14, 2026 7:31pm |  |  | Fair | No | Not getting customer on phone
Outage | J.E.26.07.16242 | C001855116 | Tyrese Williams | St.Ann | Completed | Load_238506 | Cardiff Hall - 310 | Jul 14, 2026 3:59pm | Jul 14, 2026 3:59pm | Jul 14, 2026 4:09pm | Jul 14, 2026 7:31pm | Jul 14, 2026 7:55pm | Jul 14, 2026 7:56pm | Jul 14, 2026 7:57pm | Jul 14, 2026 7:57pm |  |  | Fair | No | Remade joint at pothead use 2 pg. clamp
Outage | J.E.26.07.16261 | C001855114 | Tyrese Williams | St.Ann | Completed | Load_556920 | Cardiff Hall - 310 | Jul 14, 2026 3:59pm | Jul 14, 2026 3:59pm | Jul 14, 2026 4:09pm | Jul 14, 2026 4:15pm | Jul 14, 2026 6:21pm | Jul 14, 2026 7:26pm | Jul 14, 2026 7:26pm | Jul 14, 2026 7:26pm |  |  | Fair | No | Open a 50kva transformer fuse at pole Splice and retention 2 span of secondary neutral use 3 pg clamp and 20ft of #2AA
Outage | J.E.26.07.16278 | C001855115 | Tyrese Williams | St.Ann | Completed | Load_238147 | Cardiff Hall - 310 | Jul 14, 2026 3:59pm | Jul 14, 2026 3:59pm | Jul 14, 2026 4:09pm | Jul 14, 2026 7:26pm | Jul 14, 2026 7:28pm | Jul 14, 2026 7:28pm | Jul 14, 2026 7:28pm | Jul 14, 2026 7:28pm |  |  | Fair | No | Call related to the secondary neutral wire that was broken
Outage | J.E.26.07.15904 | C001855109 | Raymond Lewis | St.Ann | Completed | Load_262693 | Cardiff Hall - 210 | Jul 14, 2026 3:58pm | Jul 14, 2026 3:58pm | Jul 14, 2026 7:09pm | Jul 14, 2026 7:09pm | Jul 14, 2026 7:09pm | Jul 14, 2026 7:10pm | Jul 14, 2026 7:10pm | Jul 14, 2026 7:10pm |  |  | Fair | No | Supply restored
Outage | J.E.26.07.16279 | C001855108 | Raymond Lewis | St.Ann | Completed | Load_266748 | Cardiff Hall - 210 | Jul 14, 2026 3:58pm | Jul 14, 2026 3:58pm | Jul 14, 2026 6:37pm | Jul 14, 2026 6:37pm | Jul 14, 2026 6:37pm | Jul 14, 2026 7:05pm | Jul 14, 2026 7:05pm | Jul 14, 2026 7:05pm |  |  | Fair | No | Supply restored
Outage | J.E.26.07.16280 | C001855103 | Raymond Lewis | St.Ann | Completed | Load_1003794 | Cardiff Hall - 210 | Jul 14, 2026 3:58pm | Jul 14, 2026 3:58pm | Jul 14, 2026 6:29pm | Jul 14, 2026 6:29pm | Jul 14, 2026 6:29pm | Jul 14, 2026 6:30pm | Jul 14, 2026 6:32pm | Jul 14, 2026 6:32pm |  |  | Fair | No | Supply restored
Outage | J.E.26.07.16281 | C001855110 | Raymond Lewis | St.Ann | Completed | Load_263239 | Cardiff Hall - 210 | Jul 14, 2026 3:58pm | Jul 14, 2026 3:58pm | Jul 14, 2026 7:08pm | Jul 14, 2026 7:08pm | Jul 14, 2026 7:08pm | Jul 14, 2026 7:09pm | Jul 14, 2026 7:09pm | Jul 14, 2026 7:09pm |  |  | Fair | No | Supply restored
Outage | J.E.26.07.16284 | C001855107 | Raymond Lewis | St.Ann | Completed | Load_258184 | Cardiff Hall - 210 | Jul 14, 2026 3:58pm | Jul 14, 2026 3:58pm | Jul 14, 2026 6:35pm | Jul 14, 2026 6:35pm | Jul 14, 2026 6:35pm | Jul 14, 2026 6:36pm | Jul 14, 2026 6:37pm | Jul 14, 2026 6:37pm |  |  | Fair | No | Supply restored
Outage | J.E.26.07.16286 | C001855106 | Raymond Lewis | St.Ann | Completed | Load_244612 | Cardiff Hall - 210 | Jul 14, 2026 3:58pm | Jul 14, 2026 3:58pm | Jul 14, 2026 6:34pm | Jul 14, 2026 6:34pm | Jul 14, 2026 6:34pm | Jul 14, 2026 6:35pm | Jul 14, 2026 6:35pm | Jul 14, 2026 6:35pm |  |  | Fair | No | Supply restored
Outage | J.E.26.07.16287 | C001855105 | Raymond Lewis | St.Ann | Completed | Load_265058 | Cardiff Hall - 210 | Jul 14, 2026 3:58pm | Jul 14, 2026 3:58pm | Jul 14, 2026 6:32pm | Jul 14, 2026 6:32pm | Jul 14, 2026 6:32pm | Jul 14, 2026 6:33pm | Jul 14, 2026 6:33pm | Jul 14, 2026 6:33pm |  |  | Fair | No | Supply restored
Outage | J.E.26.07.16289 | C001855102 | Raymond Lewis | St.Ann | Completed | Load_248151 | Cardiff Hall - 210 | Jul 14, 2026 3:58pm | Jul 14, 2026 3:58pm | Jul 14, 2026 6:28pm | Jul 14, 2026 6:28pm | Jul 14, 2026 6:28pm | Jul 14, 2026 6:29pm | Jul 14, 2026 6:29pm | Jul 14, 2026 6:29pm |  |  | Fair | No | Supply restored
Outage | J.E.26.07.16290 | C001855104 | Raymond Lewis | St.Ann | Completed | Load_412864 | Cardiff Hall - 210 | Jul 14, 2026 3:58pm | Jul 14, 2026 3:58pm | Jul 14, 2026 4:09pm | Jul 14, 2026 4:09pm | Jul 14, 2026 6:20pm | Jul 14, 2026 6:21pm | Jul 14, 2026 6:22pm | Jul 14, 2026 6:22pm |  |  | Fair | No | Customer say that supply has returned
Outage | J.E.26.07.16114 | C001855101 | Javid Vernon | Westmoreland | Completed | Load_260320 | Paradise - 210 | Jul 14, 2026 3:57pm | Jul 14, 2026 4:00pm | Jul 15, 2026 4:37pm | Jul 15, 2026 4:38pm | Jul 15, 2026 5:29pm | Jul 15, 2026 6:01pm | Jul 15, 2026 6:02pm | Jul 15, 2026 6:02pm |  |  | Fair | No | Replace 70ft #6 triplex wire and 3 clamps voltage reading 113/115/228
Outage | J.E.26.07.16197 | C001855100 | Javid Vernon | Westmoreland | Completed | Load_292305 | Paradise - 210 | Jul 14, 2026 3:57pm | Jul 14, 2026 4:00pm | Jul 14, 2026 5:22pm | Jul 14, 2026 5:22pm | Jul 14, 2026 6:22pm | Jul 14, 2026 6:42pm | Jul 14, 2026 6:53pm | Jul 14, 2026 6:53pm |  |  | Fair | No | Remove vegetation and refuse one 25kva transformer use 3amp fuse
Outage | J.E.26.07.16219 | C001855099 | Javid Vernon | Westmoreland | Completed | Load_247022 | Paradise - 210 | Jul 14, 2026 3:57pm | Jul 14, 2026 4:00pm | Jul 14, 2026 6:53pm | Jul 14, 2026 6:53pm | Jul 14, 2026 7:48pm | Jul 14, 2026 8:21pm | Jul 14, 2026 8:25pm | Jul 14, 2026 8:25pm |  |  | Fair | No | Cut and remove vegetation from transformer switch bottom and refuse one 25kva transformer use 3amp fuse
Outage | J.E.26.07.16245 | C001855098 | Javid Vernon | Westmoreland | Completed | Load_238357 | Paradise - 210 | Jul 14, 2026 3:57pm | Jul 14, 2026 4:00pm | Jul 14, 2026 4:18pm | Jul 14, 2026 4:18pm | Jul 14, 2026 4:18pm | Jul 14, 2026 5:20pm | Jul 14, 2026 5:22pm | Jul 14, 2026 5:22pm |  |  | Rains | No | Isolate three 15amp junction fuse to disconnect defective lighting arrester and reclose three junction fuse
Non-Outage | J.E.26.07.13033 | C001855091 | Clyde Brown | Clarendon | Completed | Load_241942 | May Pen - 110 | Jul 14, 2026 3:53pm | Jul 14, 2026 3:55pm | Jul 14, 2026 4:37pm | Jul 14, 2026 7:01pm | Jul 14, 2026 8:47pm | Jul 14, 2026 9:43pm | Jul 14, 2026 8:52pm | Jul 14, 2026 8:52pm |  |  | Fair | No | Customer said this was corrected since yesterday
Non-Outage | J.E.26.07.15937 | C001855089 | Clyde Brown | Clarendon | Completed | Load_268174 | May Pen - 110 | Jul 14, 2026 3:53pm | Jul 14, 2026 3:55pm | Jul 14, 2026 4:37pm | Jul 14, 2026 4:37pm | Jul 14, 2026 6:36pm | Jul 14, 2026 6:58pm | Jul 14, 2026 7:01pm | Jul 14, 2026 7:01pm |  |  | Fair | No | Secondary neutral for 25kva transformer neutral lead burnt off open transformer and and replaced with 4ft-bare copper .
Non-Outage | J.E.26.07.16079 | C001855092 | Stephen Taylor | null | Completed | null | null | Jul 14, 2026 3:53pm | Jul 14, 2026 3:54pm | Jul 14, 2026 5:36pm | Jul 14, 2026 5:36pm | Jul 14, 2026 5:36pm | Jul 14, 2026 5:36pm | Jul 14, 2026 5:36pm | Jul 14, 2026 5:36pm |  |  | Fair | No | Clean primary line with switch stick and close up back junction with a 20 amp fuse all customer is now okay no number on pole
Non-Outage | J.E.26.07.16185 | C001855090 | Stephen Taylor | null | Completed | null | null | Jul 14, 2026 3:53pm | Jul 14, 2026 3:54pm | Jul 14, 2026 9:45pm | Jul 14, 2026 9:45pm | Jul 14, 2026 9:45pm | Jul 14, 2026 9:45pm | Jul 14, 2026 9:54pm | Jul 14, 2026 9:54pm |  |  | Fair | No | Patrol and see nothing and close up back junction with a 7 amp fuse customer is now ok
Outage | J.E.26.07.16186 | C001855088 | Kaydon Taylor | KSAN | Completed | Load_247926 | Constant Spring - 410 | Jul 14, 2026 3:52pm | Jul 14, 2026 3:53pm | Jul 14, 2026 4:02pm | Jul 14, 2026 4:09pm | Jul 14, 2026 4:20pm | Jul 14, 2026 4:20pm | Jul 14, 2026 4:21pm | Jul 14, 2026 4:21pm | BrokenWire |  | Fair | No | Found okay
Outage | J.E.26.07.16210 | C001855087 | Milton Charlton | KSAN | Completed | Load_241152 | Hope - 410 | Jul 14, 2026 3:51pm | Jul 14, 2026 3:52pm | Jul 14, 2026 5:02pm | Jul 14, 2026 5:02pm | Jul 14, 2026 5:04pm | Jul 14, 2026 5:05pm | Jul 14, 2026 5:10pm | Jul 14, 2026 5:10pm |  |  | Fair | No | Customer meter #2444775 disconnected for debt The bill was paid but meter remain disconnected.
Outage | J.E.26.07.16234 | C001855086 | Wayne Dillion | St.Elizabeth | Completed | Load_265227 | Maggotty - 110 | Jul 14, 2026 3:49pm | Jul 14, 2026 3:56pm | Jul 14, 2026 6:05pm | Jul 14, 2026 6:05pm | Jul 14, 2026 6:23pm | Jul 14, 2026 6:46pm | Jul 14, 2026 6:46pm | Jul 14, 2026 6:46pm |  |  | Fair | No | Reconnect customer using 30 feet of number 6 triplex 3 linket 3 one bolt clamp voltage reading 112v 111v 224v supply working ok
Non-Outage | J.E.26.07.15871 | C001855079 | Marlon Authors | St.Elizabeth | Completed | Load_265219 | Maggotty - 210 | Jul 14, 2026 3:45pm | Jul 14, 2026 3:56pm | Jul 14, 2026 5:58pm | Jul 14, 2026 5:58pm | Jul 14, 2026 6:48pm | Jul 14, 2026 6:55pm | Jul 14, 2026 6:55pm | Jul 14, 2026 6:55pm | BrokenPole |  | Fair | No | Patrol and found one 40 feet TA wooden pole broken close to the base caused by vehicle accident. Please refer same to the maintenance department for replacement
Outage | J.E.26.07.15839 | C001855071 | Omar King | St.Ann | Completed | Load_251934 | Ocho Rios - 310 | Jul 14, 2026 3:43pm | Jul 14, 2026 3:46pm | Jul 14, 2026 5:01pm | Jul 14, 2026 5:01pm | Jul 14, 2026 5:38pm | Jul 14, 2026 6:00pm | Jul 14, 2026 6:01pm | Jul 14, 2026 6:01pm |  |  | Fair | No | Found 50 amp junction fuse blow cause by tree contact fuse as been replaced area is now with supply
Outage | J.E.26.07.15856 | C001855069 | Omar King | St.Ann | Completed | Load_245767 | Ocho Rios - 310 | Jul 14, 2026 3:43pm | Jul 14, 2026 3:46pm | Jul 14, 2026 4:50pm | Jul 14, 2026 4:50pm | Jul 14, 2026 5:00pm | Jul 14, 2026 5:01pm | Jul 14, 2026 5:01pm | Jul 14, 2026 5:01pm |  |  | Fair | No | Premises check and found
Outage | J.E.26.07.16056 | C001855070 | Omar King | St.Ann | Completed | Load_252506 | Ocho Rios - 310 | Jul 14, 2026 3:43pm | Jul 14, 2026 3:46pm | Jul 14, 2026 6:01pm | Jul 14, 2026 6:01pm | Jul 14, 2026 6:18pm | Jul 14, 2026 6:25pm | Jul 14, 2026 6:26pm | Jul 14, 2026 6:26pm |  |  | Fair | No | Plan outage found in the area
Non-Outage | J.E.26.07.15108 | C001855055 | Richard Nicholas | St.Catherine | Completed | Load_238712 | Tredegar - 510 | Jul 14, 2026 3:33pm | Jul 14, 2026 4:32pm | Jul 14, 2026 9:16pm | Jul 14, 2026 9:16pm | Jul 14, 2026 9:49pm | Jul 14, 2026 10:20pm | Jul 14, 2026 10:24pm | Jul 14, 2026 10:24pm | Fire |  | Fair | No | Up on arrival the crew observed a low hanging insulated secondary phase that was loosen from the D-iron.wire was already make safe when found however the area is very difficult and unsafe to work at night therefore it is recommended to do repair on the morning shift.
Outage | J.E.26.07.16201 | C001855052 | Marlon Authors | St.Elizabeth | Completed | Load_292683 | Maggotty - 210 | Jul 14, 2026 3:31pm | Jul 14, 2026 3:32pm | Jul 14, 2026 8:29pm | Jul 14, 2026 8:29pm | Jul 14, 2026 8:29pm | Jul 14, 2026 8:30pm | Jul 14, 2026 8:30pm | Jul 14, 2026 8:30pm |  |  | Fair | No | Unable to locate and the customer not answering the phone
Outage | J.E.26.07.15733 | C001855051 | Ryan Richards | Manchester | Completed | Load_270083 | Kendal - 210 | Jul 14, 2026 3:29pm | Jul 14, 2026 3:32pm | Jul 14, 2026 6:07pm | Jul 14, 2026 7:45pm | Jul 14, 2026 9:14pm | Jul 14, 2026 10:09pm | Jul 14, 2026 10:09pm | Jul 14, 2026 10:09pm |  |  | Fair | No | Burn off phase found at pole remade burn off phase using 1 one bolt clamps voltage 116/118/235 volts
Outage | J.E.26.07.15821 | C001855046 | Richard Nicholas | St.Catherine | Completed | Load_251534 | Rhodens Pen - 410 | Jul 14, 2026 3:28pm | Jul 14, 2026 3:59pm | Jul 14, 2026 4:09pm | Jul 14, 2026 4:09pm | Jul 14, 2026 6:50pm | Jul 14, 2026 7:14pm | Jul 14, 2026 7:19pm | Jul 14, 2026 7:19pm |  |  | Fair | No | Customer meter socket found defective,customer advised.voltage reading 113,116 and 239v
Outage | J.E.26.07.16066 | C001855045 | Nickolas Rodriques | St.Catherine | Completed | Load_267832 | Twickenham - 410 | Jul 14, 2026 3:25pm | Jul 14, 2026 3:59pm | Jul 14, 2026 9:34pm | Jul 14, 2026 9:36pm | Jul 14, 2026 10:25pm | Jul 14, 2026 10:57pm | Jul 15, 2026 12:16am | Jul 15, 2026 12:16am | BrokenWire |  | Fair | No | Checked and found customer service wire neutral broken caused by truck. Repaired by splice and retention wire using two clamps, current reading is (117).
Non-Outage | J.E.26.07.15349 | C001855041 | Collin Robinson | null | Completed | null | null | Jul 14, 2026 3:24pm | Jul 14, 2026 3:26pm | Jul 14, 2026 3:52pm | Jul 14, 2026 3:52pm | Jul 14, 2026 3:52pm | Jul 14, 2026 3:54pm | Jul 14, 2026 3:54pm | Jul 14, 2026 3:54pm |  |  | Fair | No | Information received from customer that supply was restored from yesterday
Outage | J.E.26.07.15371 | C001855043 | Collin Robinson | Portland | Completed | Load_246850 | Port Antonio - 410 | Jul 14, 2026 3:24pm | Jul 14, 2026 3:26pm | Jul 14, 2026 3:56pm | Jul 14, 2026 3:56pm | Jul 14, 2026 3:56pm | Jul 14, 2026 3:57pm | Jul 14, 2026 3:57pm | Jul 14, 2026 3:57pm |  |  | Fair | Yes | Information received from customer that supply was restored
Outage | J.E.26.07.15646 | C001855040 | Ryan Richards | Manchester | Completed | Load_247253 | Kendal - 210 | Jul 14, 2026 3:24pm | Jul 14, 2026 3:28pm | Jul 14, 2026 6:07pm | Jul 14, 2026 6:07pm | Jul 14, 2026 7:10pm | Jul 14, 2026 7:43pm | Jul 14, 2026 7:43pm | Jul 14, 2026 7:43pm |  |  | Fair | No | Premises found ok site found running ok voltage 115/117/233 volts
Outage | J.E.26.07.16209 | C001855042 | Nickolas Rodriques | St.Catherine | Completed | Load_263727 | Tredegar - 210 | Jul 14, 2026 3:24pm | Jul 14, 2026 3:29pm | Jul 14, 2026 5:24pm | Jul 14, 2026 5:30pm | Jul 14, 2026 6:16pm | Jul 14, 2026 7:04pm | Jul 14, 2026 7:08pm | Jul 14, 2026 7:08pm | BrokenWire |  | Fair | No | Unable to locate or communicate with the customer after several attempts. No broken wire/ outage was observed while patrolling the area.
Outage | J.E.26.07.16262 | C001855044 | Nickolas Rodriques | St.Catherine | Completed | Load_268971 | Tredegar - 210 | Jul 14, 2026 3:24pm | Jul 14, 2026 3:59pm | Jul 14, 2026 7:37pm | Jul 14, 2026 7:38pm | Jul 14, 2026 8:33pm | Jul 14, 2026 9:30pm | Jul 14, 2026 9:31pm | Jul 14, 2026 9:31pm |  |  | Fair | No | Checked and found customer without electricity caused by corroded connection. Repaired by replacing two clamps at pothead and pole, current reading is (114). Customer confirmed that all is well now.
Non-Outage | J.E.26.07.15799 | C001855038 | Ryan Richards | null | Completed | null | null | Jul 14, 2026 3:22pm | Jul 14, 2026 3:24pm | Jul 14, 2026 3:49pm | Jul 14, 2026 3:49pm | Jul 14, 2026 5:27pm | Jul 14, 2026 6:07pm | Jul 14, 2026 6:07pm | Jul 14, 2026 6:07pm | Fire |  | Fair | No | Area found ok flow pole found on fire no jps line his on the pole
Outage | J.E.26.07.15943 | C001855036 | Damion Reid | Manchester | Completed | Load_268344 | Spur Tree - 310 | Jul 14, 2026 3:20pm | Jul 14, 2026 3:22pm | Jul 14, 2026 6:23pm | Jul 14, 2026 6:23pm | Jul 14, 2026 6:44pm | Jul 14, 2026 6:49pm | Jul 14, 2026 6:49pm | Jul 14, 2026 6:49pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.16118 | C001855037 | Richard Nicholas | St.Catherine | Completed | Load_247071 | Rhodens Pen - 210 | Jul 14, 2026 3:20pm | Jul 14, 2026 3:58pm | Jul 14, 2026 7:19pm | Jul 14, 2026 7:20pm | Jul 14, 2026 8:16pm | Jul 14, 2026 8:34pm | Jul 14, 2026 8:34pm | Jul 14, 2026 8:34pm |  |  | Fair | No | Area found ok
Non-Outage | J.E.26.07.16124 | C001855028 | Richard Samuda | Manchester | Completed | Load_250211 | Porus - 210 | Jul 14, 2026 3:19pm | Jul 15, 2026 7:31am | Jul 15, 2026 9:54am | Jul 15, 2026 9:54am | Jul 15, 2026 9:54am | Jul 15, 2026 10:00am | Jul 15, 2026 10:00am | Jul 15, 2026 10:00am |  |  | Fair | No | Splice and reconnected customer service neutral that was broken causing customer to experience hi voltage using one 1bolt clamp and two feet of #6 wire customer back to normal 115/114/229
Outage | J.E.26.07.16005 | C001855033 | Hartley Chin | St.Catherine | Completed | Load_293999 | Rhodens Pen - 310 | Jul 14, 2026 3:19pm | Jul 14, 2026 4:00pm | Jul 14, 2026 5:26pm | Jul 14, 2026 5:26pm | Jul 14, 2026 5:26pm | Jul 14, 2026 5:26pm | Jul 14, 2026 5:26pm | Jul 14, 2026 5:26pm |  |  | Fair | No | Customer disconnected due to non payment
Outage | J.E.26.07.16162 | C001855031 | Damion Reid | Manchester | Completed | Load_261393 | Spur Tree - 310 | Jul 14, 2026 3:19pm | Jul 14, 2026 3:22pm | Jul 14, 2026 3:37pm | Jul 14, 2026 3:37pm | Jul 14, 2026 5:06pm | Jul 14, 2026 6:19pm | Jul 14, 2026 6:21pm | Jul 14, 2026 6:21pm |  |  | Fair | No | Replace 80ft of defective #6 triplex service wire for 3 wire service using 3 one bolt clamp and 3 pen union
Outage | J.E.26.07.16176 | C001855032 | Kenroy Dale | Manchester | Completed | Load_238510 | Kendal - 310 | Jul 14, 2026 3:19pm | Jul 15, 2026 7:48am | Jul 15, 2026 8:46am | Jul 15, 2026 9:09am | Jul 15, 2026 11:00am | Jul 15, 2026 11:14am | Jul 15, 2026 11:15am | Jul 15, 2026 11:15am |  |  | Fair | No | Customer have internal problems, customer was advised to get an electrician to check the premises. Voltage reading 112/112/224
Outage | J.E.26.07.16225 | C001855030 | Damion Reid | Manchester | Completed | Load_257171 | Spur Tree - 310 | Jul 14, 2026 3:19pm | Jul 14, 2026 3:22pm | Jul 14, 2026 6:59pm | Jul 14, 2026 6:59pm | Jul 14, 2026 7:40pm | Jul 14, 2026 8:25pm | Jul 14, 2026 8:28pm | Jul 14, 2026 8:28pm |  |  | SevereWind | No | Remade corroded phase at pothead and in meter socket for 3 wire service using two pen union voltage reading at meter socket phase to neutral 113v-115v across phase 229v
Outage | J.E.26.07.16258 | C001855029 | Richard Grant | St.Catherine | Completed | Load_256805 | New Michelton - 410 | Jul 14, 2026 3:19pm | Jul 14, 2026 3:19pm | Jul 14, 2026 8:09pm | Jul 14, 2026 8:09pm | Jul 14, 2026 8:39pm | Jul 14, 2026 8:41pm | Jul 14, 2026 8:41pm | Jul 14, 2026 8:41pm |  |  | Fair | No | Daylight attention. Small unit required.
Outage | J.E.26.07.10463 | C001855024 | Richard Grant | St.Catherine | Completed | Load_568270 | New Michelton - 410 | Jul 14, 2026 3:16pm | Jul 14, 2026 3:18pm | Jul 14, 2026 3:42pm | Jul 14, 2026 3:42pm | Jul 14, 2026 5:10pm | Jul 14, 2026 5:31pm | Jul 14, 2026 5:31pm | Jul 14, 2026 5:31pm |  |  | Fair | No | 3amps fuse for 10kva transformer found blown. No visible cause seen after inspection performed. 3amps fuse replaced with 2amps fuse, supply restored and area left okay.
Outage | J.E.26.07.16045 | C001855023 | Richard Grant | St.Catherine | Completed | Load_250409 | New Michelton - 210 | Jul 14, 2026 3:16pm | Jul 14, 2026 3:17pm | Jul 14, 2026 5:32pm | Jul 14, 2026 5:32pm | Jul 14, 2026 6:59pm | Jul 14, 2026 7:22pm | Jul 14, 2026 7:22pm | Jul 14, 2026 7:22pm | BrokenWire |  | Fair | No | Wire for abandon building found dangling. Wire disconnected and isolated. Area left secured and okay.
Outage | J.E.26.07.16036 | C001855020 | Nickolas Rodriques | St.Catherine | Completed | Load_1000333 | Twickenham - 210 | Jul 14, 2026 3:14pm | Jul 14, 2026 3:18pm | Jul 14, 2026 3:31pm | Jul 14, 2026 3:41pm | Jul 14, 2026 4:49pm | Jul 14, 2026 5:10pm | Jul 14, 2026 5:22pm | Jul 14, 2026 5:22pm | BrokenPole |  | Fair | No | Call relates to a 30 ft wooden pole that is broken at the base and needs to be replaced. The pole is laying on the ground and consists of open secondary wires, one streetlight and service wire. The open secondary wires were found isolated. Refer to maintenance.
Outage | J.E.26.07.16248 | C001855019 | Wan Carlos Scarlett | Portmore | Completed | Load_239685 | Naggo Head - 610 | Jul 14, 2026 3:14pm | Jul 14, 2026 3:15pm | Jul 14, 2026 4:19pm | Jul 14, 2026 4:51pm | Jul 14, 2026 5:09pm | Jul 14, 2026 5:37pm | Jul 14, 2026 5:39pm | Jul 14, 2026 5:39pm | BrokenWire |  | Fair | No | Found one span of open secondary line neutral burn out use 2 one bolt clamps at pole readings 116-117-234
Outage | J.E.26.07.16121 | C001855013 | Hartley Chin | Clarendon | Completed | Load_239834 | Parnassus - 210 | Jul 14, 2026 3:12pm | Jul 14, 2026 3:13pm | Jul 14, 2026 5:58pm | Jul 14, 2026 5:58pm | Jul 14, 2026 6:57pm | Jul 14, 2026 8:06pm | Jul 14, 2026 8:07pm | Jul 14, 2026 8:07pm |  |  | Fair | No | Found 15 amp Tripsaver open due to tree on line remove tree and close tripsaver
Outage | J.E.26.07.16134 | C001855011 | Hartley Chin | Clarendon | Completed | Load_269637 | Monymusk - 210 | Jul 14, 2026 3:12pm | Jul 14, 2026 3:13pm | Jul 14, 2026 3:34pm | Jul 14, 2026 3:35pm | Jul 14, 2026 4:40pm | Jul 14, 2026 5:23pm | Jul 14, 2026 5:25pm | Jul 14, 2026 5:25pm | BrokenWire | Y | Fair | No | Found broken wire due to tree contact open 15 amp junction remove tree repair broken phase the close 15 amp junction
Outage | J.E.26.07.16149 | C001855012 | Hartley Chin | Clarendon | Completed | Load_246426 | May Pen - 210 | Jul 14, 2026 3:12pm | Jul 14, 2026 3:13pm | Jul 14, 2026 10:10pm | Jul 14, 2026 10:10pm | Jul 14, 2026 10:10pm | Jul 14, 2026 10:11pm | Jul 14, 2026 10:11pm | Jul 14, 2026 10:11pm |  |  | Fair | No | Found ok
Outage | J.E.26.07.16038 | C001855010 | Tajay Bernard | Hanover | Completed | Load_242835 | Orange Bay - 310 | Jul 14, 2026 3:10pm | Jul 14, 2026 3:23pm | Jul 14, 2026 3:33pm | Jul 14, 2026 3:33pm | Jul 14, 2026 4:05pm | Jul 14, 2026 4:07pm | Jul 14, 2026 4:08pm | Jul 14, 2026 4:08pm |  |  | Fair | No | Area check and found okay unable to locate customer on premises multiple phone call to customer number went unanswered
Non-Outage | J.E.26.07.14777 | C001855005 | Richman Whyte | null | Completed | null | null | Jul 14, 2026 3:06pm | Jul 14, 2026 3:31pm | Jul 14, 2026 5:19pm | Jul 14, 2026 5:19pm | Jul 14, 2026 7:13pm | Jul 14, 2026 7:20pm | Jul 14, 2026 7:21pm | Jul 14, 2026 7:21pm |  |  | Fair | No | Connect back customer after hurricane use 73 feet #6 triplex voltage 112 112 224
Outage | J.E.26.07.15749 | C001855003 | Richman Whyte | Westmoreland | Completed | Load_248174 | Paradise - 310 | Jul 14, 2026 3:05pm | Jul 14, 2026 3:05pm | Jul 14, 2026 7:52pm | Jul 14, 2026 7:52pm | Jul 14, 2026 7:52pm | Jul 14, 2026 7:52pm | Jul 14, 2026 7:54pm | Jul 14, 2026 7:54pm |  |  | Fair | No | Unable to locate and call to customer went unanswered customer need to provide a good phone number and better direction to premises
Outage | J.E.26.07.15948 | C001855004 | Richman Whyte | Westmoreland | Completed | Load_291995 | Paradise - 310 | Jul 14, 2026 3:05pm | Jul 14, 2026 3:05pm | Jul 14, 2026 5:07pm | Jul 14, 2026 5:07pm | Jul 14, 2026 5:07pm | Jul 14, 2026 5:07pm | Jul 14, 2026 5:18pm | Jul 14, 2026 5:18pm |  |  | Rains | No | There is a secondary line on customer private property witch was built by customer.customer move his meter from burn ground to mile town road and connect it to the secondary line that line blow down in the hurricane and it didn’t restore
Outage | J.E.26.07.16220 | C001855002 | Richman Whyte | Westmoreland | Completed | Load_262006 | Paradise - 310 | Jul 14, 2026 3:04pm | Jul 14, 2026 3:05pm | Jul 14, 2026 4:47pm | Jul 14, 2026 4:47pm | Jul 14, 2026 4:47pm | Jul 14, 2026 4:48pm | Jul 14, 2026 4:49pm | Jul 14, 2026 4:49pm |  |  | Rains | No | Replace 15 amp junction fuse
Outage | J.E.26.07.16110 | C001854998 | Swon Miller | St.James | Completed | Load_243259 | Queens Drive - 710 | Jul 14, 2026 3:01pm | Jul 14, 2026 3:13pm | Jul 14, 2026 3:41pm | Jul 14, 2026 3:41pm | Jul 14, 2026 3:50pm | Jul 21, 2026 4:31am | Jul 14, 2026 4:32pm | Jul 14, 2026 4:32pm |  |  | Fair | No | Found 1,8 amp junction fuse blown cause by contamination replace 8 amp junction fuse voltage found 0.000 voltage left 115/115/231
Outage | J.E.26.07.15656 | C001854958 | Richard Samuda | Manchester | Completed | Load_257611 | Spur Tree - 310 | Jul 14, 2026 2:33pm | Jul 14, 2026 2:33pm | Jul 14, 2026 3:09pm | Jul 14, 2026 3:09pm | Jul 14, 2026 3:09pm | Jul 14, 2026 3:09pm | Jul 14, 2026 3:34pm | Jul 14, 2026 3:34pm |  |  | Fair | No | Found transformer tripped reset transformer customer back to normal
Outage | J.E.26.07.15817 | C001854916 | Edward Royal | KSAS | Completed | Load_255178 | Up Park Camp - 410 | Jul 14, 2026 1:59pm | Jul 14, 2026 1:59pm | Jul 14, 2026 2:31pm | Jul 14, 2026 2:31pm | Jul 14, 2026 2:31pm | Jul 14, 2026 2:33pm | Jul 14, 2026 2:33pm | Jul 14, 2026 2:33pm | TreeContact |  | Fair | No | Referred to secondary bushing crew
Non-Outage | J.E.26.07.16140 | C001854910 | Dwain Samuels | null | Completed | null | null | Jul 14, 2026 1:53pm | Jul 14, 2026 1:54pm | Jul 14, 2026 2:42pm | Jul 14, 2026 2:54pm | Jul 14, 2026 3:41pm | Jul 14, 2026 3:45pm | Jul 14, 2026 3:48pm | Jul 14, 2026 3:48pm |  |  | Fair | No | Connect 3 wire meter .use 75feet of #6 service wire . Use 6 one bolt clamp.
Outage | J.E.26.07.16031 | C001854909 | Moses Elliston | St.Catherine | Completed | Load_568941 | Twickenham - 310 | Jul 14, 2026 1:50pm | Jul 14, 2026 1:51pm | Jul 14, 2026 1:54pm | Jul 14, 2026 1:54pm | Jul 14, 2026 1:55pm | Jul 14, 2026 1:56pm | Jul 14, 2026 1:56pm | Jul 14, 2026 1:56pm |  |  | Fair | No | Credit added to prepaid account
Outage | J.E.26.07.16107 | C001854908 | Moses Elliston | St.Catherine | Completed | Load_248875 | Tredegar - 510 | Jul 14, 2026 1:50pm | Jul 14, 2026 1:51pm | Jul 14, 2026 2:34pm | Jul 14, 2026 2:34pm | Jul 14, 2026 3:06pm | Jul 14, 2026 3:49pm | Jul 14, 2026 3:59pm | Jul 14, 2026 3:59pm |  |  | Fair | No | Wrong account signed for .Should be meter # 2937162.Customer advised.
Outage | J.E.26.07.15835 | C001854902 | Wayne Dillion | St.Elizabeth | Completed | Load_239461 | Maggotty - 110 | Jul 14, 2026 1:48pm | Jul 14, 2026 1:48pm | Jul 14, 2026 3:24pm | Jul 14, 2026 3:24pm | Jul 14, 2026 3:27pm | Jul 14, 2026 3:50pm | Jul 14, 2026 3:50pm | Jul 14, 2026 3:50pm |  |  | Fair | No | Supply check on found customer low voltage.reading 93v remade joint at pole using 2 one bolt clamp voltage leave at premises 112v supply working ok
Outage | J.E.26.07.15848 | C001854901 | Wayne Dillion | St.Elizabeth | Completed | Load_1002160 | Maggotty - 110 | Jul 14, 2026 1:48pm | Jul 14, 2026 1:48pm | Jul 14, 2026 5:17pm | Jul 14, 2026 5:17pm | Jul 14, 2026 5:46pm | Jul 14, 2026 6:02pm | Jul 14, 2026 6:03pm | Jul 14, 2026 6:03pm |  |  | Fair | No | Patrol and found one blown 2 amp fuse that protects 10 KVA transformer no pole number cause by bird replace the same supply restore ok
Outage | J.E.26.07.16152 | C001854903 | Kaydon Taylor | KSAN | Completed | Load_239178 | Constant Spring - 410 | Jul 14, 2026 1:48pm | Jul 14, 2026 6:42pm | Jul 14, 2026 6:47pm | Jul 14, 2026 6:48pm | Jul 14, 2026 7:29pm | Jul 14, 2026 7:30pm | Jul 14, 2026 7:30pm | Jul 14, 2026 7:30pm |  |  | Fair | No | Found okay
Outage | J.E.26.07.16127 | C001854900 | Wayne Dillion | St.Elizabeth | Completed | Load_239911 | Maggotty - 110 | Jul 14, 2026 1:47pm | Jul 14, 2026 1:48pm | Jul 14, 2026 6:53pm | Jul 14, 2026 6:53pm | Jul 14, 2026 6:53pm | Jul 14, 2026 6:54pm | Jul 14, 2026 6:55pm | Jul 14, 2026 6:55pm |  |  | Fair | No | Customer was disconnected call customer care to reconnect customer supply was restored to customer successfully
Outage | J.E.26.07.16137 | C001854896 | Christopher Edwards | KSAN | Completed | Load_256340 | Constant Spring - 410 | Jul 14, 2026 1:41pm | Jul 14, 2026 1:42pm | Jul 14, 2026 2:31pm | Jul 14, 2026 2:31pm | Jul 14, 2026 3:12pm | Jul 14, 2026 3:47pm | Jul 14, 2026 3:47pm | Jul 14, 2026 3:47pm |  |  | Fair | No | Reset 25 kva transformer
Outage | J.E.26.07.16122 | C001854888 | Andre Williams | Trelawny | Completed | Load_241450 | Martha Brae - 210 | Jul 14, 2026 1:34pm | Jul 14, 2026 1:34pm | Jul 14, 2026 1:54pm | Jul 14, 2026 1:54pm | Jul 14, 2026 2:08pm | Jul 14, 2026 2:36pm | Jul 14, 2026 2:38pm | Jul 14, 2026 2:38pm |  |  | Fair | No | Patrol 3phase line re fuse 30 amp junction on duke street across from Jps.hospital now with full supply
Outage | J.E.26.07.16125 | C001854889 | Andre Williams | Trelawny | Completed | Load_255782 | Martha Brae - 210 | Jul 14, 2026 1:34pm | Jul 14, 2026 1:34pm | Jul 14, 2026 1:41pm | Jul 14, 2026 1:41pm | Jul 14, 2026 1:41pm | Jul 14, 2026 1:51pm | Jul 14, 2026 1:53pm | Jul 14, 2026 1:53pm |  |  | Fair | No | Unable to locate customer wire from hexing box reffer to field service customer only one on plaza experience low voltage.
Outage | J.E.26.07.16126 | C001854890 | Andre Williams | Trelawny | Completed | Load_253495 | Martha Brae - 210 | Jul 14, 2026 1:34pm | Jul 14, 2026 1:34pm | Jul 14, 2026 2:39pm | Jul 14, 2026 2:39pm | Jul 14, 2026 2:48pm | Jul 14, 2026 2:48pm | Jul 14, 2026 2:48pm | Jul 14, 2026 2:48pm |  |  | Fair | No | Premises ok and with supply call related to earlier outage
Outage | J.E.26.07.15971 | C001854884 | Donald Cunningham | St.Catherine | Completed | Load_240390 | Twickenham - 210 | Jul 14, 2026 1:32pm | Jul 14, 2026 1:35pm | Jul 14, 2026 2:01pm | Jul 14, 2026 2:01pm | Jul 14, 2026 2:07pm | Jul 14, 2026 2:07pm | Jul 14, 2026 2:11pm | Jul 14, 2026 2:11pm | BrokenPole |  | Fair | No | Broken secondary pole 30 class 6 removed from out of road and isolate by transformer pole by train line by dyke road refer to maintenance for replacement
Outage | J.E.26.07.16075 | C001854880 | Elvis Trowers | KSAN | Completed | Load_262669 | West Kings House - 410 | Jul 14, 2026 1:25pm | Jul 14, 2026 1:30pm | Jul 14, 2026 1:52pm | Jul 14, 2026 1:52pm | Jul 14, 2026 2:27pm | Jul 14, 2026 2:33pm | Jul 14, 2026 2:33pm | Jul 14, 2026 2:33pm |  |  | Fair | Yes | Happened to be a disconnection and was reconnected with the assistant of escalation service department after being checked.
Non-Outage | J.E.26.07.15863 | C001854865 | Rochaine Hussey | KSAS | Completed | Load_259281 | Duhaney - 310 | Jul 14, 2026 1:06pm | Jul 14, 2026 1:08pm | Jul 15, 2026 11:02am | Jul 15, 2026 11:03am | Jul 15, 2026 11:13am | Jul 15, 2026 11:42am | Jul 15, 2026 11:42am | Jul 15, 2026 11:42am |  |  | Fair | No | Voltage found at Premesis is okay 118/118/237v however the customer saying they power is in and out hence the the twisted is connected it needs bushing so I’m requesting a team to do the bushing , no pole number is visible on pole
Non-Outage | J.E.26.07.15825 | C001854862 | Elvis Trowers | KSAN | Completed | Load_253886 | Washington Blvd - 510 | Jul 14, 2026 1:05pm | Jul 14, 2026 1:09pm | Jul 14, 2026 1:24pm | Jul 14, 2026 1:24pm | Jul 14, 2026 1:45pm | Jul 14, 2026 1:51pm | Jul 14, 2026 1:51pm | Jul 14, 2026 1:51pm | BrokenPole |  | Fair | Yes | Happened to be internal when checked, customer private pole with their twisted wire broken and needs to be changed, was also advised to contact an electrician.
Non-Outage | J.E.26.07.15888 | C001854864 | Rochaine Hussey | KSAS | Completed | Load_259468 | Duhaney - 310 | Jul 14, 2026 1:05pm | Jul 14, 2026 1:08pm | Jul 15, 2026 11:43am | Jul 15, 2026 11:43am | Jul 15, 2026 11:49am | Jul 15, 2026 12:19pm | Jul 15, 2026 12:20pm | Jul 15, 2026 12:20pm |  |  | Fair | No | Corrosion on pole1clamp usedIssue resolved 110/113/223v
Non-Outage | J.E.26.07.16029 | C001854860 | Fredrick Hamilton | KSAN | Completed | Load_247998 | Constant Spring - 210 | Jul 14, 2026 1:05pm | Jul 14, 2026 1:07pm | Jul 14, 2026 1:55pm | Jul 14, 2026 2:34pm | Jul 14, 2026 2:39pm | Jul 14, 2026 2:47pm | Jul 14, 2026 2:47pm | Jul 14, 2026 2:47pm |  |  | Fair | No | 119.3v obtained premises checked and found okNo issue detected on JPS supply
Non-Outage | J.E.26.07.16059 | C001854861 | Fredrick Hamilton | KSAN | Completed | Load_250041 | Washington Blvd - 510 | Jul 14, 2026 1:05pm | Jul 14, 2026 1:06pm | Jul 14, 2026 1:55pm | Jul 14, 2026 2:23pm | Jul 14, 2026 2:24pm | Jul 14, 2026 2:33pm | Jul 14, 2026 2:33pm | Jul 14, 2026 2:33pm |  |  | Fair | No | 239.7v/121.4v/117.3v obtained No issue detected on the JPS supply Premises is ok
Non-Outage | J.E.26.07.15939 | C001854858 | Christopher Edwards | KSAN | Completed | Load_243315 | Constant Spring - 410 | Jul 14, 2026 1:04pm | Jul 14, 2026 1:07pm | Jul 14, 2026 1:14pm | Jul 14, 2026 1:14pm | Jul 14, 2026 1:29pm | Jul 14, 2026 2:29pm | Jul 14, 2026 2:31pm | Jul 14, 2026 2:31pm | BrokenPole |  | Fair | No | Rotten 35 ft wood poleConsist of single phase primary Open secondary wirePole is rotten and needs to be replaced
Non-Outage | J.E.26.07.16004 | C001854859 | Fredrick Hamilton | KSAN | Completed | Load_252041 | Constant Spring - 410 | Jul 14, 2026 1:04pm | Jul 14, 2026 1:07pm | Jul 14, 2026 1:55pm | Jul 15, 2026 9:08am | Jul 15, 2026 10:34am | Jul 15, 2026 11:17am | Jul 15, 2026 11:17am | Jul 15, 2026 11:17am | Defective customer pole |  | Fair | No | 223.8v/113.4v/110.3v obtained Corrosion detected at pothead however unable to correct issue due to a Defective customer pole Customer advised
Outage | J.E.26.07.15866 | C001854851 | Richman Whyte | Hanover | Completed | Load_238992 | Orange Bay - 310 | Jul 14, 2026 1:03pm | Jul 14, 2026 1:03pm | Jul 14, 2026 1:46pm | Jul 14, 2026 1:46pm | Jul 14, 2026 1:46pm | Jul 14, 2026 1:46pm | Jul 14, 2026 1:47pm | Jul 14, 2026 1:47pm | BrokenWire |  | Fair | No | Customer have internal problem advise to fix
Outage | J.E.26.07.15912 | C001854852 | Javid Vernon | Westmoreland | Completed | Load_241658 | Paradise - 210 | Jul 14, 2026 1:03pm | Jul 14, 2026 4:02pm | Jul 14, 2026 10:06pm | Jul 14, 2026 10:06pm | Jul 14, 2026 10:45pm | Jul 14, 2026 10:53pm | Jul 14, 2026 10:54pm | Jul 14, 2026 10:54pm |  |  | Fair | No | Customer requesting a disconnection due to damage of property because she is still getting bills
Outage | J.E.26.07.15801 | C001854850 | Richman Whyte | Hanover | Completed | Load_239491 | Orange Bay - 310 | Jul 14, 2026 1:02pm | Jul 14, 2026 1:03pm | Jul 14, 2026 1:49pm | Jul 14, 2026 1:49pm | Jul 14, 2026 2:40pm | Jul 14, 2026 2:42pm | Jul 14, 2026 2:43pm | Jul 14, 2026 2:43pm |  |  | Fair | No | Customer have internal problem advise to fix voltage 110 110 220
Outage | J.E.26.07.16023 | C001854836 | Romeo Brissett | St.James | Completed | Load_230013 | Bogue - 310 | Jul 14, 2026 12:50pm | Jul 14, 2026 12:51pm | Jul 14, 2026 1:34pm | Jul 14, 2026 1:34pm | Jul 14, 2026 1:34pm | Jul 14, 2026 2:00pm | Jul 14, 2026 2:00pm | Jul 14, 2026 2:00pm |  |  | Fair | No | Replaced (2)20amps junction and (2)100kva transformer fuse, used (2)10amps and (2)20amps
Outage | J.E.26.07.16026 | C001854828 | Dwayne Samuels | Trelawny | Completed | Load_262658 | Greenwood - 110 | Jul 14, 2026 12:48pm | Jul 14, 2026 12:49pm | Jul 14, 2026 1:55pm | Jul 14, 2026 1:55pm | Jul 14, 2026 3:23pm | Jul 14, 2026 3:28pm | Jul 14, 2026 3:33pm | Jul 14, 2026 3:33pm |  |  | Fair | No | Open 1 25kva transformer to splice and retention customer service wire to jps pole using 3 one bolt clamp, 3 linkets and about 100ft of number 6 wire voltage left after reconnection 114v/115v/229v
Outage | J.E.26.07.16032 | C001854827 | Floyd Taylor | Trelawny | Completed | Load_239232 | Greenwood - 110 | Jul 14, 2026 12:48pm | Jul 14, 2026 4:55pm | Jul 14, 2026 5:21pm | Jul 14, 2026 5:21pm | Jul 14, 2026 5:43pm | Jul 14, 2026 5:46pm | Jul 14, 2026 5:46pm | Jul 14, 2026 5:46pm |  |  | Fair | No | Call belong to mobay
Outage | J.E.26.07.15682 | C001854825 | Neckell Ormsby | St.Mary | Completed | null | null | Jul 14, 2026 12:45pm | Jul 14, 2026 12:46pm | Jul 14, 2026 2:11pm | Jul 14, 2026 2:11pm | Jul 14, 2026 2:11pm | Jul 14, 2026 2:12pm | Jul 14, 2026 2:12pm | Jul 14, 2026 2:12pm |  |  | Fair | No | Nothing in call
Non-Outage | J.E.26.07.16022 | C001854812 | Cliton Henry | St.Mary | Completed | Load_268843 | Oracabessa - 210 | Jul 14, 2026 12:29pm | Jul 14, 2026 12:29pm | Jul 14, 2026 1:25pm | Jul 14, 2026 1:26pm | Jul 14, 2026 1:56pm | Jul 14, 2026 2:14pm | Jul 14, 2026 2:17pm | Jul 14, 2026 2:17pm | BrokenWire |  | Fair | No | The customer service wire hanging low and the pothead need repairs to be done. The service wire was disconnected and the customer advised to carryout repairs and call upon completion to be reconnected.
Outage | J.E.26.07.16011 | C001854804 | Stephen Taylor | St.Thomas | Completed | Load_243194 | Good Year - 210 | Jul 14, 2026 12:28pm | Jul 14, 2026 12:29pm | Jul 14, 2026 5:37pm | Jul 14, 2026 5:37pm | Jul 14, 2026 5:37pm | Jul 14, 2026 5:37pm | Jul 14, 2026 5:37pm | Jul 14, 2026 5:37pm |  |  | Fair | No | Clean primary line with switch stick and close up back junction with a 20 amp fuse all customer is now okay no number on pole
Outage | J.E.26.07.15895 | C001854803 | Stephen Taylor | St.Thomas | Completed | Load_260209 | Lysson - 410 | Jul 14, 2026 12:27pm | Jul 14, 2026 12:29pm | Jul 14, 2026 2:44pm | Jul 14, 2026 2:53pm | Jul 14, 2026 3:09pm | Jul 14, 2026 3:09pm | Jul 14, 2026 3:13pm | Jul 14, 2026 3:13pm |  |  | Fair | No | Clean up single phase line use 3onebolt clamp customer is now ok…Rdg 112-113-225
Outage | J.E.26.07.15969 | C001854782 | Collin Robinson | Portland | Completed | Load_244022 | Port Antonio - 310 | Jul 14, 2026 12:03pm | Jul 14, 2026 12:03pm | Jul 14, 2026 1:20pm | Jul 14, 2026 1:20pm | Jul 14, 2026 2:23pm | Jul 14, 2026 2:30pm | Jul 14, 2026 2:30pm | Jul 14, 2026 2:30pm |  |  | Fair | No | Meter burn refer to field service
Outage | J.E.26.07.15852 | C001854771 | Moses Elliston | Portmore | Completed | Load_576148 | Naggo Head - 610 | Jul 14, 2026 11:57am | Jul 14, 2026 11:57am | Jul 14, 2026 12:58pm | Jul 14, 2026 12:58pm | Jul 14, 2026 12:58pm | Jul 14, 2026 12:59pm | Jul 14, 2026 1:04pm | Jul 14, 2026 1:04pm |  |  | Fair | No | Meter changed to # 3069139.Relay stuck in off position
Outage | J.E.26.07.15891 | C001854767 | Roxroy Needham | St.Ann | Completed | Load_556217 | Cardiff Hall - 210 | Jul 14, 2026 11:50am | Jul 14, 2026 11:50am | Jul 14, 2026 12:14pm | Jul 14, 2026 12:14pm | Jul 14, 2026 12:14pm | Jul 14, 2026 12:15pm | Jul 14, 2026 12:16pm | Jul 14, 2026 12:16pm |  |  | Fair | No | Call customer and customer say she don’t make a report and the light is ok
Outage | J.E.26.07.15894 | C001854766 | Roxroy Needham | St.Ann | Completed | Load_258184 | Cardiff Hall - 210 | Jul 14, 2026 11:50am | Jul 14, 2026 11:50am | Jul 14, 2026 12:16pm | Jul 14, 2026 12:16pm | Jul 14, 2026 2:10pm | Jul 14, 2026 2:11pm | Jul 14, 2026 2:12pm | Jul 14, 2026 2:12pm |  |  | Fair | No | Replace a 8 amps junction fuse at pole
Outage | J.E.26.07.15929 | C001854761 | Dean Smith | Hanover | Completed | Load_253025 | Orange Bay - 210 | Jul 14, 2026 11:44am | Jul 14, 2026 11:45am | Jul 14, 2026 1:14pm | Jul 14, 2026 1:14pm | Jul 14, 2026 1:49pm | Jul 14, 2026 1:49pm | Jul 14, 2026 1:50pm | Jul 14, 2026 1:50pm |  |  | Fair | No | Area was restored
Outage | J.E.26.07.15868 | C001854748 | Michael Christian | St.James | Completed | Load_237906 | Rose Hall - 210 | Jul 14, 2026 11:29am | Jul 15, 2026 8:20am | Jul 15, 2026 10:56am | Jul 15, 2026 10:56am | Jul 15, 2026 12:00pm | Jul 15, 2026 12:21pm | Jul 15, 2026 12:21pm | Jul 15, 2026 12:21pm |  |  | Fair | No | Check and found okay voltage 110 111 223 at pothead
Non-Outage | J.E.26.07.08641 | C001854725 | Jermaine Williams | Clarendon | Completed | Load_266996 | Monymusk - 210 | Jul 14, 2026 11:13am | Jul 14, 2026 11:16am | Jul 14, 2026 12:47pm | Jul 14, 2026 12:47pm | Jul 14, 2026 1:10pm | Jul 14, 2026 1:33pm | Jul 14, 2026 1:34pm | Jul 14, 2026 1:34pm | Fire |  | Fair | No | Remade joints at secondary using three clamps.
Non-Outage | J.E.26.07.15782 | C001854723 | Roemello Brown | Trelawny | Completed | Load_302479 | Duncans - 210 | Jul 14, 2026 11:11am | Jul 14, 2026 11:11am | Jul 14, 2026 1:02pm | Jul 14, 2026 1:39pm | Jul 14, 2026 2:52pm | Jul 14, 2026 3:26pm | Jul 14, 2026 3:31pm | Jul 14, 2026 3:31pm |  |  | Fair | No | Meter socket defective inform the customer to get an private electrician to have meter socket change Voltage found 110/108/218Voltage leave 110/108/218
Outage | J.E.26.07.15893 | C001854724 | Kemark Slue | St.Catherine | Completed | Load_250891 | Tredegar - 310 | Jul 14, 2026 11:11am | Jul 14, 2026 11:11am | Jul 14, 2026 11:59am | Jul 14, 2026 12:13pm | Jul 14, 2026 12:32pm | Jul 14, 2026 12:47pm | Jul 14, 2026 12:47pm | Jul 14, 2026 12:47pm |  |  | Fair | No | Premises was checked and found okay.
Outage | J.E.26.07.15849 | C001854716 | Edward Royal | KSAS | Completed | Load_258279 | Three Miles - 510 | Jul 14, 2026 11:05am | Jul 14, 2026 11:05am | Jul 14, 2026 12:03pm | Jul 14, 2026 12:03pm | Jul 14, 2026 12:03pm | Jul 14, 2026 12:03pm | Jul 14, 2026 12:04pm | Jul 14, 2026 12:04pm |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.07.15851 | C001854707 | Neckell Ormsby | St.Mary | Completed | Load_264348 | Highgate -110 | Jul 14, 2026 10:59am | Jul 14, 2026 10:59am | Jul 14, 2026 12:58pm | Jul 14, 2026 12:58pm | Jul 14, 2026 12:58pm | Jul 14, 2026 12:55pm | Jul 14, 2026 12:59pm | Jul 14, 2026 12:59pm | BrokenWire |  | Fair | No | Troubleshoot and found corrosion at pothead, clean and remade joints using 2- one bolt clamps voltage left 111v 114v 225v
Non-Outage | J.E.26.07.14523 | C001854698 | Collin Robinson | Portland | Completed | Load_254227 | Port Antonio - 410 | Jul 14, 2026 10:58am | Jul 14, 2026 10:58am | Jul 14, 2026 12:14pm | Jul 14, 2026 12:14pm | Jul 14, 2026 1:42pm | Jul 14, 2026 1:19pm | Jul 14, 2026 1:19pm | Jul 14, 2026 1:19pm |  |  | Fair | No | Unable to locate customer
Outage | J.E.26.07.15702 | C001854697 | Michael Christian | St.James | Completed | Load_269402 | Rose Hall - 210 | Jul 14, 2026 10:57am | Jul 14, 2026 10:57am | Jul 14, 2026 1:01pm | Jul 14, 2026 1:02pm | Jul 14, 2026 1:20pm | Jul 14, 2026 1:21pm | Jul 14, 2026 1:21pm | Jul 14, 2026 1:21pm |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.07.15847 | C001854696 | Andrae Clarke | Portland | Completed | Load_243136 | Port Antonio - 410 | Jul 14, 2026 10:56am | Jul 15, 2026 7:11am | Jul 15, 2026 8:18am | Jul 15, 2026 9:16am | Jul 15, 2026 10:02am | Jul 15, 2026 10:03am | Jul 15, 2026 10:07am | Jul 15, 2026 10:07am |  |  | Fair | No | Check meter found meter burnt check voltage 118/117/236 Refer to field service for meter to get change
Non-Outage | J.E.26.07.15239 | C001854694 | Edward Royal | null | Completed | null | null | Jul 14, 2026 10:55am | Jul 14, 2026 11:02am | Jul 14, 2026 12:06pm | Jul 14, 2026 12:06pm | Jul 14, 2026 12:06pm | Jul 14, 2026 12:07pm | Jul 14, 2026 12:07pm | Jul 14, 2026 12:07pm |  |  | Fair | No | When contacted customer said that there is no at the premises
Outage | J.E.26.07.15826 | C001854686 | Moses Elliston | St.Catherine | Completed | Load_573851 | Tredegar - 210 | Jul 14, 2026 10:52am | Jul 14, 2026 10:53am | Jul 14, 2026 11:42am | Jul 14, 2026 11:42am | Jul 14, 2026 11:43am | Jul 14, 2026 11:43am | Jul 14, 2026 11:44am | Jul 14, 2026 11:44am |  |  | Fair | No | Credit added to prepaid account.
Non-Outage | J.E.26.07.15428 | C001854668 | Jermaine Williams | Clarendon | Completed | Load_239131 | May Pen - 110 | Jul 14, 2026 10:43am | Jul 15, 2026 9:12am | Jul 15, 2026 9:46am | Jul 15, 2026 9:46am | Jul 15, 2026 9:55am | Jul 15, 2026 9:55am | Jul 15, 2026 9:56am | Jul 15, 2026 9:56am | BrokenPole |  | Fair | No | Broken 35 c/6 Pole, needs urgent attention. Maintenance team already aware of issue.
Non-Outage | J.E.26.07.15535 | C001854669 | Jermaine Williams | Clarendon | Completed | Load_242454 | Monymusk - 410 | Jul 14, 2026 10:43am | Jul 14, 2026 10:44am | Jul 14, 2026 1:35pm | Jul 14, 2026 1:35pm | Jul 14, 2026 1:54pm | Jul 14, 2026 1:53pm | Jul 14, 2026 1:55pm | Jul 14, 2026 1:55pm | BrokenWire |  | Fair | No | Low hanging cable wires, not property of JPS.
Non-Outage | J.E.26.07.15669 | C001854660 | Collin Robinson | Portland | Completed | Load_253648 | Port Antonio - 410 | Jul 14, 2026 10:38am | Jul 14, 2026 10:39am | Jul 14, 2026 11:23am | Jul 14, 2026 11:23am | Jul 14, 2026 12:07pm | Jul 14, 2026 12:09pm | Jul 14, 2026 12:09pm | Jul 14, 2026 12:09pm | BrokenWire |  | Fair | No | Reconnect #6 twisted neutral wire at pole Voltage reading 119v 120v 239v
Outage | J.E.26.07.15829 | C001854657 | Daniel Francis | St.Ann | Completed | Load_241237 | Roaring River - 410 | Jul 14, 2026 10:35am | Jul 14, 2026 10:36am | Jul 14, 2026 12:32pm | Jul 14, 2026 12:38pm | Jul 14, 2026 12:57pm | Jul 14, 2026 1:07pm | Jul 14, 2026 1:08pm | Jul 14, 2026 1:08pm | BrokenWire |  | Fair | No | Change 2 one clamp 116 116 232 in all
Outage | J.E.26.07.15721 | C001854648 | Andrew Powell | Manchester | Completed | Load_1002274 | Spur Tree - 210 | Jul 14, 2026 10:28am | Jul 14, 2026 10:33am | Jul 14, 2026 10:40am | Jul 14, 2026 10:40am | Jul 14, 2026 10:55am | Jul 14, 2026 11:11am | Jul 14, 2026 11:16am | Jul 14, 2026 11:16am | BrokenWire |  | Fair | No | Disconnect and remove 100 feet burnt up #6 triplex service wire from secondary line, customer leaves without service due to repair work required on customer private side burnt up service entry wire meter #2660674, advise customer.
Outage | J.E.26.07.15775 | C001854647 | Edward Royal | KSAN | Completed | Load_266121 | Washington Blvd - 610 | Jul 14, 2026 10:28am | Jul 14, 2026 10:53am | Jul 14, 2026 12:14pm | Jul 14, 2026 12:14pm | Jul 14, 2026 12:14pm | Jul 14, 2026 12:15pm | Jul 14, 2026 12:15pm | Jul 14, 2026 12:15pm |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.07.15816 | C001854649 | Selvin White | St.Elizabeth | Completed | Load_292267 | Maggotty - 210 | Jul 14, 2026 10:28am | Jul 14, 2026 10:33am | Jul 14, 2026 10:58am | Jul 14, 2026 11:25am | Jul 14, 2026 11:37am | Jul 14, 2026 11:43am | Jul 14, 2026 11:45am | Jul 14, 2026 11:45am |  |  | Fair | No | Customer was found to be disconnected for non payment of bills more than a year ago . Escalation department was contacted and said premises will need recertification.
Outage | J.E.26.07.15823 | C001854652 | Edward Royal | KSAS | Completed | Load_257249 | Up Park Camp - 410 | Jul 14, 2026 10:28am | Jul 14, 2026 10:53am | Jul 14, 2026 2:03pm | Jul 14, 2026 2:03pm | Jul 14, 2026 2:03pm | Jul 14, 2026 2:30pm | Jul 14, 2026 2:31pm | Jul 14, 2026 2:31pm |  |  | Fair | No | Premises found ok voltage reading 119 v 118v 236.8
Outage | J.E.26.07.15752 | C001854645 | Milton Charlton | KSAN | Completed | Load_240009 | Hope - 410 | Jul 14, 2026 10:27am | Jul 14, 2026 10:28am | Jul 14, 2026 1:25pm | Jul 14, 2026 1:25pm | Jul 14, 2026 2:49pm | Jul 14, 2026 2:40pm | Jul 14, 2026 2:51pm | Jul 14, 2026 2:51pm |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.07.15785 | C001854646 | Milton Charlton | KSAN | Completed | Load_242001 | Hope - 510 | Jul 14, 2026 10:27am | Jul 14, 2026 10:28am | Jul 14, 2026 1:16pm | Jul 14, 2026 1:16pm | Jul 14, 2026 1:21pm | Jul 14, 2026 1:20pm | Jul 14, 2026 1:24pm | Jul 14, 2026 1:24pm |  |  | Fair | No | Unable to locate customer by telephone. No one answering telephone number on report.
Outage | J.E.26.07.15818 | C001854644 | Neckell Ormsby | St.Mary | Completed | Load_266816 | Highgate -110 | Jul 14, 2026 10:27am | Jul 14, 2026 10:27am | Jul 14, 2026 10:39am | Jul 14, 2026 10:39am | Jul 14, 2026 10:39am | Jul 14, 2026 11:00am | Jul 14, 2026 11:21am | Jul 14, 2026 11:21am | Fire |  | Fair | No | Related to previous Richmond rd call
Outage | J.E.26.07.15771 | C001854643 | Wayne Dillion | St.Elizabeth | Completed | Load_245955 | Maggotty - 110 | Jul 14, 2026 10:26am | Jul 14, 2026 10:27am | Jul 14, 2026 1:24pm | Jul 14, 2026 1:24pm | Jul 14, 2026 1:24pm | Jul 14, 2026 1:30pm | Jul 14, 2026 1:30pm | Jul 14, 2026 1:30pm |  |  | Fair | No | Patrol and found customer experiencing high voltage reading 153v 134v other check found transformer neutral drop lead burn isolate 25 KVA transformer repair drop lead using 5 feet of #2 capper 2 one bolt clamp recluse transformer voltage reading 115v 115v 232v supply working ok
Outage | J.E.26.07.15814 | C001854628 | Hartley Chin | Clarendon | Completed | Load_242599 | Parnassus - 310 | Jul 14, 2026 10:16am | Jul 14, 2026 3:13pm | Jul 14, 2026 10:11pm | Jul 14, 2026 10:11pm | Jul 14, 2026 10:11pm | Jul 14, 2026 10:11pm | Jul 14, 2026 10:12pm | Jul 14, 2026 10:12pm |  |  | Fair | No | Found ok
Outage | J.E.26.07.15821 | C001854630 | Ricky Hall | St.Catherine | Completed | Load_251534 | Rhodens Pen - 410 | Jul 14, 2026 10:16am | Jul 14, 2026 10:17am | Jul 14, 2026 10:26am | Jul 14, 2026 10:26am | Jul 14, 2026 11:16am | Aug 7, 2026 11:16am | Jul 14, 2026 11:17am | Jul 14, 2026 11:17am |  |  | Fair | No | Premises closed
Non-Outage | J.E.26.07.14794 | C001854615 | Rusean Allen | KSAS | Completed | Load_261030 | Rockfort - 410 | Jul 14, 2026 10:07am | Jul 14, 2026 10:08am | Jul 14, 2026 12:51pm | Jul 14, 2026 12:51pm | Jul 14, 2026 2:08pm | Jul 14, 2026 2:10pm | Jul 14, 2026 2:10pm | Jul 14, 2026 2:10pm |  |  | Fair | No | The concentric cable need to change it defective Refer to field service department
Non-Outage | J.E.26.07.13365 | C001854595 | Richard Samuda | null | Completed | null | null | Jul 14, 2026 9:49am | Jul 14, 2026 9:49am | Jul 14, 2026 10:05am | Jul 14, 2026 10:05am | Jul 14, 2026 10:05am | Jul 14, 2026 10:05am | Jul 14, 2026 10:09am | Jul 14, 2026 10:09am |  |  | Fair | No | Customer say he back to normal
Non-Outage | J.E.26.07.15216 | C001854593 | Barnett Brown | null | Completed | null | null | Jul 14, 2026 9:49am | Jul 15, 2026 7:28am | Jul 15, 2026 11:01am | Jul 15, 2026 11:02am | Jul 15, 2026 12:03pm | Jul 15, 2026 12:26pm | Jul 15, 2026 12:35pm | Jul 15, 2026 12:35pm | Fire |  | Fair | No | Use switch stick to clear tree branch
Non-Outage | J.E.26.07.15512 | C001854592 | Barnett Brown | null | Completed | null | null | Jul 14, 2026 9:48am | Jul 14, 2026 10:03am | Jul 14, 2026 12:19pm | Jul 14, 2026 12:19pm | Jul 14, 2026 12:41pm | Jul 14, 2026 1:18pm | Jul 14, 2026 1:22pm | Jul 14, 2026 1:22pm |  |  | Fair | No | Patrol line, found nothing, replace blown 10 amp junction fuse
Non-Outage | J.E.26.07.15751 | C001854580 | Ricky Hall | null | Completed | null | null | Jul 14, 2026 9:40am | Jul 14, 2026 9:40am | Jul 14, 2026 12:16pm | Jul 14, 2026 12:29pm | Jul 14, 2026 12:38pm | Jul 14, 2026 12:39pm | Jul 14, 2026 12:40pm | Jul 14, 2026 12:40pm |  |  | Fair | No | Premises closed
Non-Outage | J.E.26.07.15762 | C001854581 | Moses Elliston | null | Completed | null | null | Jul 14, 2026 9:40am | Jul 14, 2026 9:40am | Jul 14, 2026 10:32am | Jul 14, 2026 10:32am | Jul 14, 2026 10:47am | Jul 14, 2026 10:48am | Jul 14, 2026 10:49am | Jul 14, 2026 10:49am |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.07.15709 | C001854574 | Kemark Slue | St.Catherine | Completed | Load_257996 | Tredegar - 510 | Jul 14, 2026 9:39am | Jul 14, 2026 9:39am | Jul 14, 2026 10:30am | Jul 14, 2026 10:31am | Jul 14, 2026 10:54am | Jul 14, 2026 10:54am | Jul 14, 2026 10:55am | Jul 14, 2026 10:55am |  |  | Fair | No | Premises was checked and found okay.
Outage | J.E.26.07.15744 | C001854573 | Dwain Samuels | Westmoreland | Completed | Load_256357 | Paradise - 310 | Jul 14, 2026 9:38am | Jul 14, 2026 9:38am | Jul 14, 2026 9:53am | Jul 14, 2026 1:31pm | Jul 14, 2026 2:02pm | Jul 14, 2026 2:03pm | Jul 14, 2026 2:11pm | Jul 14, 2026 2:11pm |  |  | Fair | No | Connect 3 wire meter use 3 one bolt clamp and 3 pen union
Outage | J.E.26.07.15738 | C001854568 | Cliton Henry | St.Mary | Completed | Load_352012 | Oracabessa - 110 | Jul 14, 2026 9:31am | Jul 14, 2026 10:27am | Jul 14, 2026 11:30am | Jul 14, 2026 11:30am | Jul 14, 2026 12:00pm | Jul 14, 2026 12:11pm | Jul 14, 2026 12:11pm | Jul 14, 2026 12:11pm |  |  | Fair | No | The voltages found at the metering point were 114-120/235 volts. The customer was advised to get a licensed electrician to check internally.
Outage | J.E.26.07.15710 | C001854564 | Daniel Francis | St.Ann | Completed | Load_243992 | Ocho Rios - 310 | Jul 14, 2026 9:28am | Jul 14, 2026 9:29am | Jul 14, 2026 11:27am | Jul 14, 2026 11:27am | Jul 14, 2026 11:27am | Jul 14, 2026 11:28am | Jul 14, 2026 11:28am | Jul 14, 2026 11:28am |  |  | Fair | No | Found okay customer say light come
Outage | J.E.26.07.15696 | C001854563 | Daniel Francis | St.Ann | Completed | Load_265738 | Ocho Rios - 310 | Jul 14, 2026 9:27am | Jul 14, 2026 9:27am | Jul 14, 2026 10:36am | Jul 14, 2026 10:36am | Jul 14, 2026 10:51am | Jul 14, 2026 11:23am | Jul 14, 2026 11:26am | Jul 14, 2026 11:26am |  |  | Fair | No | Change two 30amp fuse no pole # next one 10amp and one 15amp pole #0098817
Outage | J.E.26.07.15689 | C001854559 | Neckell Ormsby | St.Mary | Completed | Load_241528 | Highgate -110 | Jul 14, 2026 9:22am | Jul 14, 2026 9:22am | Jul 14, 2026 10:43am | Jul 14, 2026 11:22am | Jul 14, 2026 11:22am | Jul 14, 2026 11:33am | Jul 14, 2026 11:34am | Jul 14, 2026 11:34am |  |  | Fair | No | Related to previous Richmond road call broken wire
Outage | J.E.26.07.15708 | C001854552 | Romeo Brissett | St.James | Completed | Load_240006 | Bogue - 310 | Jul 14, 2026 9:14am | Jul 14, 2026 9:15am | Jul 14, 2026 3:07pm | Jul 14, 2026 3:07pm | Jul 14, 2026 3:07pm | Jul 14, 2026 2:40pm | Jul 14, 2026 3:11pm | Jul 14, 2026 3:11pm |  |  | Fair | No | Removed vegetation and replaced (1)20amps junction
Outage | J.E.26.07.15711 | C001854553 | Romeo Brissett | St.James | Completed | Load_238410 | Bogue - 310 | Jul 14, 2026 9:14am | Jul 14, 2026 9:15am | Jul 14, 2026 2:00pm | Jul 14, 2026 2:00pm | Jul 14, 2026 2:26pm | Jul 14, 2026 2:27pm | Jul 14, 2026 3:07pm | Jul 14, 2026 3:07pm |  |  | Fair | No | Cut and removed vegetation, replaced (1)40amps junction
Non-Outage | J.E.26.07.11331 | C001854550 | Marlon Authors | Manchester | Completed | Load_262620 | Spur Tree - 210 | Jul 14, 2026 9:13am | Jul 14, 2026 4:04pm | Jul 14, 2026 5:42pm | Jul 14, 2026 5:42pm | Jul 14, 2026 5:42pm | Jul 14, 2026 5:54pm | Jul 14, 2026 5:55pm | Jul 14, 2026 5:55pm |  |  | Fair | No | Supply checked and found low voltage, rdg 103v,103v and cross phased 206 volts. Further checks revealed that the transformer is tapped at max 5 . Please refer same to the maintenance department for further assistance
Outage | J.E.26.07.15672 | C001854549 | Edward Royal | KSAS | Completed | Load_259251 | Greenwich - 410 | Jul 14, 2026 9:12am | Jul 14, 2026 9:13am | Jul 14, 2026 9:41am | Jul 14, 2026 9:52am | Jul 14, 2026 9:52am | Jul 14, 2026 9:58am | Jul 14, 2026 9:59am | Jul 14, 2026 9:59am | LowHangingWires |  | Fair | No | Premises found ok customer was referring about 3rd party cable
Outage | J.E.26.07.15701 | C001854548 | Horace Malcolm | St.James | Completed | Load_269952 | Bogue - 610 | Jul 14, 2026 9:11am | Jul 14, 2026 9:11am | Jul 14, 2026 1:08pm | Jul 14, 2026 1:08pm | Jul 14, 2026 1:45pm | Jul 14, 2026 2:24pm | Jul 14, 2026 2:24pm | Jul 14, 2026 2:24pm | BrokenWire |  | Fair | No | Splice and retention customer service wire used 10ft #6 triplex wire one clamp voltage 113-115-228
Non-Outage | J.E.26.07.15473 | C001854531 | Rochaine Hussey | KSAN | Completed | Load_251210 | Washington Blvd - 610 | Jul 14, 2026 8:53am | Jul 14, 2026 8:54am | Jul 14, 2026 1:02pm | Jul 14, 2026 1:02pm | Jul 14, 2026 1:09pm | Jul 14, 2026 1:22pm | Jul 14, 2026 1:22pm | Jul 14, 2026 1:22pm |  |  | Fair | No | Premises closed Customer is at workUnable to access meter
Non-Outage | J.E.26.07.14183 | C001854524 | Rayon Foster | Hanover | Completed | Load_292572 | Orange Bay - 310 | Jul 14, 2026 8:42am | Jul 14, 2026 8:42am | Jul 14, 2026 10:21am | Jul 14, 2026 10:31am | Jul 14, 2026 10:31am | Jul 14, 2026 11:48am | Jul 14, 2026 11:48am | Jul 14, 2026 11:48am |  |  | Fair | No | Dislocated of neutral wire on customer pathead was the causes of low voltage,voltage found when arrived on location 94/101 voltage after repair 110/111AB221 volts use four one bolt clamp to complete repair
Non-Outage | J.E.26.07.15089 | C001854525 | Dean Smith | Hanover | Completed | Load_262475 | Orange Bay - 210 | Jul 14, 2026 8:42am | Jul 14, 2026 8:42am | Jul 14, 2026 2:30pm | Jul 14, 2026 2:30pm | Jul 14, 2026 2:30pm | Jul 14, 2026 2:30pm | Jul 14, 2026 2:53pm | Jul 14, 2026 2:53pm | LowHangingWires |  | Fair | No | Jps wires and apparatus Check and found ok. Telephone provider wire on fence.
Non-Outage | J.E.26.07.14371 | C001854521 | Rayon Foster | Hanover | Completed | Load_269776 | Orange Bay - 310 | Jul 14, 2026 8:40am | Jul 14, 2026 8:41am | Jul 14, 2026 12:18pm | Jul 14, 2026 12:18pm | Jul 14, 2026 12:36pm | Jul 14, 2026 3:14pm | Jul 14, 2026 3:15pm | Jul 14, 2026 3:15pm |  |  | Fair | No | Voltage check at transformer pole 120/121AB241 volts voltage check at customer meter socket 94/101 customer is 14 pole span from transformer pole damage 25 kva transformer that was redundant need to be replace refer to earl vassle And randy brown to have it replace customer said a jps van come with a transformer few weeks ago but did not change transformer need to replace asap to resolved low voltage issue affecting customer
Non-Outage | J.E.26.04.15550 | C001854519 | Richman Whyte | Hanover | Completed | Load_268845 | Orange Bay - 310 | Jul 14, 2026 8:37am | Jul 14, 2026 8:38am | Jul 14, 2026 11:16am | Jul 14, 2026 11:16am | Jul 14, 2026 11:16am | Jul 14, 2026 11:46am | Jul 14, 2026 11:57am | Jul 14, 2026 11:57am |  |  | Fair | No | Open twenty five kva transformer fuse and change defective clamps on transformer drop leads use three one bolt clamps voltage 113 112 226
Non-Outage | J.E.26.04.16621 | C001854518 | Richman Whyte | Hanover | Completed | Load_266395 | Orange Bay - 310 | Jul 14, 2026 8:37am | Jul 14, 2026 8:38am | Jul 14, 2026 12:16pm | Jul 14, 2026 12:16pm | Jul 14, 2026 12:16pm | Jul 14, 2026 12:17pm | Jul 14, 2026 12:18pm | Jul 14, 2026 12:18pm |  |  | Fair | No | Customer stated that problem was resolved
Non-Outage | J.E.26.04.24254 | C001854516 | Richman Whyte | Hanover | Completed | Load_268845 | Orange Bay - 310 | Jul 14, 2026 8:37am | Jul 14, 2026 8:38am | Jul 14, 2026 11:58am | Jul 14, 2026 11:58am | Jul 14, 2026 11:58am | Jul 14, 2026 11:58am | Jul 14, 2026 12:00pm | Jul 14, 2026 12:00pm |  |  | Fair | No | Change defective clamps on transformer drop leads
Non-Outage | J.E.26.05.03599 | C001854517 | Richman Whyte | Hanover | Completed | Load_268845 | Orange Bay - 310 | Jul 14, 2026 8:37am | Jul 14, 2026 8:38am | Jul 14, 2026 12:12pm | Jul 14, 2026 12:12pm | Jul 14, 2026 12:13pm | Jul 14, 2026 12:13pm | Jul 14, 2026 12:14pm | Jul 14, 2026 12:14pm |  |  | Fair | No | Replace defective clamps on transformer drop leads voltage 113 112 226
Non-Outage | J.E.26.05.07221 | C001854515 | Richman Whyte | Westmoreland | Completed | Load_261865 | Paradise - 110 | Jul 14, 2026 8:37am | Jul 14, 2026 8:38am | Jul 14, 2026 10:58pm | Jul 14, 2026 10:58pm | Jul 14, 2026 10:58pm | Jul 14, 2026 10:58pm | Jul 14, 2026 10:59pm | Jul 14, 2026 10:59pm |  |  | Fair | No | Unable to locate or contact customer on the phone
Non-Outage | J.E.26.05.07281 | C001854514 | Richman Whyte | Hanover | Completed | Load_293095 | Orange Bay - 310 | Jul 14, 2026 8:37am | Jul 14, 2026 8:38am | Jul 14, 2026 12:25pm | Jul 14, 2026 12:25pm | Jul 14, 2026 12:25pm | Jul 14, 2026 12:25pm | Jul 14, 2026 12:27pm | Jul 14, 2026 12:27pm |  |  | Fair | No | Customer stated that problem was resolved from some time ago there was a defective transformer in the area
Non-Outage | J.E.26.05.24452 | C001854513 | Richman Whyte | Hanover | Completed | Load_293095 | Orange Bay - 310 | Jul 14, 2026 8:37am | Jul 14, 2026 8:38am | Jul 14, 2026 12:18pm | Jul 14, 2026 12:18pm | Jul 14, 2026 12:18pm | Jul 14, 2026 12:22pm | Jul 14, 2026 12:23pm | Jul 14, 2026 12:23pm |  |  | Fair | No | Area found okay however unable to locate or contact this customer
Non-Outage | J.E.26.07.15040 | C001854512 | Dean Smith | null | Completed | null | null | Jul 14, 2026 8:35am | Jul 14, 2026 8:36am | Jul 14, 2026 12:45pm | Jul 14, 2026 12:45pm | Jul 14, 2026 12:45pm | Jul 14, 2026 12:57pm | Jul 14, 2026 1:14pm | Jul 14, 2026 1:14pm |  |  | Fair | No | Unable to locate customer, area was check and found ok.
Non-Outage | J.E.26.07.14908 | C001854509 | Oshane Warren | Westmoreland | Completed | Load_253644 | Paradise - 310 | Jul 14, 2026 8:33am | Jul 14, 2026 8:33am | Jul 14, 2026 1:00pm | Jul 14, 2026 1:00pm | Jul 14, 2026 2:42pm | Jul 14, 2026 4:17pm | Jul 14, 2026 4:19pm | Jul 14, 2026 4:19pm |  |  | Rains | No | Open 25kva xformer fuse and change defective clamps from xformer drop leads
Non-Outage | J.E.26.07.15619 | C001854507 | Oshane Warren | Westmoreland | Completed | Load_245346 | Paradise - 310 | Jul 14, 2026 8:33am | Jul 14, 2026 8:33am | Jul 14, 2026 12:50pm | Jul 14, 2026 12:50pm | Jul 14, 2026 12:50pm | Jul 14, 2026 12:51pm | Jul 14, 2026 12:53pm | Jul 14, 2026 12:53pm | Fire |  | Rains | No | Cross arm break off and miss logged conductor reattached miss logged conductor cross arm needs to be changed however no customer is without power refer to maintenance
Non-Outage | J.E.26.07.15658 | C001854508 | Oshane Warren | Westmoreland | Completed | Load_260004 | Paradise - 310 | Jul 14, 2026 8:33am | Jul 14, 2026 8:33am | Jul 14, 2026 11:55am | Jul 14, 2026 11:55am | Jul 14, 2026 11:55am | Jul 14, 2026 12:47pm | Jul 14, 2026 12:49pm | Jul 14, 2026 12:49pm | BrokenWire |  | Rains | No | Cross arm brake off conductor miss lodge retention and reattach conductor however no one is without power cross arm needs to be change refer to maintenance
Outage | J.E.26.07.15574 | C001854510 | Richman Whyte | Westmoreland | Completed | Load_251449 | Paradise - 310 | Jul 14, 2026 8:33am | Jul 14, 2026 3:06pm | Jul 14, 2026 7:55pm | Jul 14, 2026 7:55pm | Jul 14, 2026 7:55pm | Jul 14, 2026 7:55pm | Jul 14, 2026 7:56pm | Jul 14, 2026 7:56pm |  |  | Fair | No | Unable to locate and call to customer went unanswered
Outage | J.E.26.07.15651 | C001854506 | Floyd Taylor | St.James | Completed | Load_244424 | Bogue - 310 | Jul 14, 2026 8:33am | Jul 14, 2026 5:52pm | Jul 14, 2026 6:30pm | Jul 14, 2026 6:30pm | Jul 14, 2026 7:55pm | Jul 14, 2026 8:44pm | Jul 14, 2026 8:45pm | Jul 14, 2026 8:45pm |  |  | Fair | No | Replace 1-8amp junction fused
Outage | J.E.26.07.15673 | C001854505 | Romeo Brissett | St.James | Completed | Load_269249 | Bogue - 310 | Jul 14, 2026 8:33am | Jul 14, 2026 8:33am | Jul 14, 2026 5:14pm | Jul 14, 2026 5:14pm | Jul 14, 2026 6:15pm | Jul 14, 2026 6:10pm | Jul 14, 2026 6:16pm | Jul 14, 2026 6:16pm |  |  | Fair | No | Check and found ok, Customer stated issue is already resolved.
Outage | J.E.26.07.15609 | C001854504 | Richman Whyte | Hanover | Completed | Load_238910 | Orange Bay - 310 | Jul 14, 2026 8:32am | Jul 14, 2026 8:33am | Jul 14, 2026 9:15am | Jul 14, 2026 9:15am | Jul 14, 2026 10:36am | Jul 14, 2026 10:55am | Jul 14, 2026 10:59am | Jul 14, 2026 10:59am |  |  | Fair | No | Open twenty five kva transformer fuse and repair burnt off neutral jumper use three one bolt clamps voltage 114 116 230
Non-Outage | J.E.26.07.14125 | C001854503 | Andre Williams | Trelawny | Completed | Load_267205 | Duncans - 210 | Jul 14, 2026 8:31am | Jul 14, 2026 8:31am | Jul 14, 2026 10:17am | Jul 14, 2026 10:17am | Jul 14, 2026 10:45am | Jul 14, 2026 10:58am | Jul 14, 2026 10:59am | Jul 14, 2026 10:59am |  |  | Fair | No | Open 25 kva transformer, remake neutral joint that was burning off voltage in area now steady 117+117=234
Outage | J.E.26.07.15467 | C001854502 | Edward Royal | KSAN | Completed | Load_575407 | Washington Blvd - 710 | Jul 14, 2026 8:30am | Jul 14, 2026 8:30am | Jul 14, 2026 9:11am | Jul 14, 2026 9:17am | Jul 14, 2026 9:17am | Jul 14, 2026 9:18am | Jul 14, 2026 9:18am | Jul 14, 2026 9:18am |  |  | Fair | No | Customer was reconnected by escalation
Outage | J.E.26.07.15662 | C001854501 | Damion Reid | Manchester | Completed | Load_241325 | Spur Tree - 310 | Jul 14, 2026 8:30am | Jul 14, 2026 3:21pm | Jul 14, 2026 8:28pm | Jul 14, 2026 8:28pm | Jul 14, 2026 9:39pm | Jul 14, 2026 10:07pm | Jul 14, 2026 10:08pm | Jul 14, 2026 10:08pm | Fire |  | Fair | No | Premises found ok
Outage | J.E.26.07.12580 | C001854498 | Kenroy Dale | Manchester | Completed | Load_253217 | Kendal - 210 | Jul 14, 2026 8:28am | Jul 14, 2026 8:28am | Jul 14, 2026 1:17pm | Jul 14, 2026 1:17pm | Jul 14, 2026 1:17pm | Jul 14, 2026 2:31pm | Jul 14, 2026 2:32pm | Jul 14, 2026 2:32pm | BrokenWire |  | Fair | No | Approximately 500 feet of #6 triplex was used to replace defective service wire that was causing 2 customers to experience single phase, area was also de-bushed to carry out task and customers now with supply. Voltage reading 115/115/230
Outage | J.E.26.07.15046 | C001854499 | Edward Royal | KSAS | Completed | Load_248613 | Hunts Bay - 310 | Jul 14, 2026 8:28am | Jul 14, 2026 8:28am | Jul 14, 2026 9:08am | Jul 14, 2026 9:08am | Jul 14, 2026 9:13am | Jul 14, 2026 9:16am | Jul 14, 2026 9:16am | Jul 14, 2026 9:16am |  |  | Fair | No | Premises found ok customer was query about her bill
Outage | J.E.26.07.14801 | C001854496 | Richard Samuda | Manchester | Completed | Load_301393 | Porus - 210 | Jul 14, 2026 8:27am | Jul 15, 2026 7:27am | Jul 15, 2026 7:54am | Jul 15, 2026 7:55am | Jul 15, 2026 7:55am | Jul 15, 2026 7:55am | Jul 15, 2026 7:58am | Jul 15, 2026 7:58am |  |  | Fair | No | Customer say he’s back to normal
Outage | J.E.26.07.14842 | C001854491 | Barnett Brown | Manchester | Completed | Load_301405 | Porus - 310 | Jul 14, 2026 8:27am | Jul 14, 2026 8:28am | Jul 14, 2026 12:15pm | Jul 14, 2026 12:15pm | Jul 14, 2026 12:15pm | Jul 14, 2026 12:16pm | Jul 14, 2026 12:18pm | Jul 14, 2026 12:18pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.14884 | C001854494 | Richard Samuda | Manchester | Completed | Load_292439 | Porus - 210 | Jul 14, 2026 8:27am | Jul 15, 2026 7:27am | Jul 15, 2026 8:04am | Jul 15, 2026 8:04am | Jul 15, 2026 8:04am | Jul 15, 2026 8:04am | Jul 15, 2026 8:05am | Jul 15, 2026 8:05am |  |  | Fair | No | Customer service was restored
Outage | J.E.26.07.15049 | C001854489 | Barnett Brown | Manchester | Completed | Load_249527 | Porus - 310 | Jul 14, 2026 8:27am | Jul 14, 2026 8:28am | Jul 14, 2026 11:40am | Jul 14, 2026 11:40am | Jul 14, 2026 11:50am | Jul 14, 2026 12:07pm | Jul 14, 2026 12:10pm | Jul 14, 2026 12:10pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.15070 | C001854495 | Barnett Brown | Manchester | Completed | Load_244426 | Porus - 210 | Jul 14, 2026 8:27am | Jul 14, 2026 8:28am | Jul 14, 2026 10:41am | Jul 14, 2026 10:41am | Jul 14, 2026 11:14am | Jul 14, 2026 11:39am | Jul 14, 2026 11:39am | Jul 14, 2026 11:39am |  |  | Fair | No | Patrol line, found nothing, replace blown 10 amp junction fuse, pole number 0184584
Outage | J.E.26.07.15152 | C001854490 | Barnett Brown | Manchester | Completed | Load_301405 | Porus - 310 | Jul 14, 2026 8:27am | Jul 14, 2026 8:28am | Jul 14, 2026 12:10pm | Jul 14, 2026 12:10pm | Jul 14, 2026 12:10pm | Jul 14, 2026 12:10pm | Jul 14, 2026 12:11pm | Jul 14, 2026 12:11pm |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.07.14123 | C001854486 | Roemello Brown | Trelawny | Completed | Load_241533 | Greenwood - 210 | Jul 14, 2026 8:26am | Jul 14, 2026 8:26am | Jul 15, 2026 9:08am | Jul 15, 2026 11:42am | Jul 15, 2026 1:11pm | Jul 15, 2026 1:11pm | Jul 15, 2026 1:24pm | Jul 15, 2026 1:24pm |  |  | Fair | No | Corrosion at the pothead an at pole side has both clamps change Voltage found 114/77/191Voltage leave 114/116/230
Non-Outage | J.E.26.07.14869 | C001854487 | Roemello Brown | Trelawny | Completed | Load_249410 | Greenwood - 210 | Jul 14, 2026 8:26am | Jul 14, 2026 8:26am | Jul 15, 2026 9:47am | Jul 15, 2026 10:54am | Jul 15, 2026 11:26am | Jul 15, 2026 11:26am | Jul 15, 2026 11:42am | Jul 15, 2026 11:42am |  |  | Fair | No | Secondary line fluctuating please send emergency team to assist getting 99volts on one leg Voltage found 110/99/209Voltage leave 110/99/209
Outage | J.E.26.07.15131 | C001854488 | Edward Royal | KSAS | Completed | Load_240053 | Duhaney - 410 | Jul 14, 2026 8:26am | Jul 14, 2026 8:27am | Jul 14, 2026 12:20pm | Jul 14, 2026 12:20pm | Jul 14, 2026 12:31pm | Jul 14, 2026 12:45pm | Jul 14, 2026 12:46pm | Jul 14, 2026 12:46pm |  |  | Fair | No | Customer having internal problems advice customer to a electrician to fix problem voltage reading 120v 118 v 238
Non-Outage | J.E.26.07.14437 | C001854485 | Dwayne Samuels | Trelawny | Completed | Load_291988 | Greenwood - 210 | Jul 14, 2026 8:25am | Jul 14, 2026 8:26am | Jul 14, 2026 9:53am | Jul 14, 2026 9:54am | Jul 14, 2026 10:16am | Jul 14, 2026 10:26am | Jul 14, 2026 10:27am | Jul 14, 2026 10:27am |  |  | Fair | No | Check and found voltage working ok voltage found at customer meter was 113/115/228 customer was advised to get a electrician to do some internal checks customer has a internal issue
Outage | J.E.26.07.12879 | C001854483 | Andre Williams | Trelawny | Completed | Load_265828 | Duncans - 110 | Jul 14, 2026 8:24am | Jul 14, 2026 8:24am | Jul 14, 2026 8:28am | Jul 14, 2026 8:28am | Jul 14, 2026 8:55am | Jul 14, 2026 10:04am | Jul 14, 2026 10:04am | Jul 14, 2026 10:04am |  |  | Fair | No | Roughly 200 ft #two twisted burn customer was advice to replace line before calling Jps ( private line leading to meter pole
Non-Outage | J.E.26.07.10142 | C001854478 | Christopher Edwards | KSAN | Completed | Load_256340 | Constant Spring - 410 | Jul 14, 2026 8:21am | Jul 14, 2026 8:22am | Jul 14, 2026 9:19am | Jul 14, 2026 9:19am | Jul 14, 2026 9:19am | Jul 14, 2026 11:03am | Jul 14, 2026 11:03am | Jul 14, 2026 11:03am |  |  | Fair | No | Burnt neutral joint at poleRemake joint Using (1) one bolt clamps Voltage:114,115,230v
Outage | J.E.26.07.15393 | C001854477 | Rusean Allen | KSAS | Completed | Load_249853 | Cane River - 310 | Jul 14, 2026 8:20am | Jul 14, 2026 8:20am | Jul 14, 2026 10:31am | Jul 14, 2026 10:31am | Jul 14, 2026 11:55am | Jul 14, 2026 12:51pm | Jul 14, 2026 12:51pm | Jul 14, 2026 12:51pm |  |  | Fair | No | No meter found at premises Customer states that a team come to the location yesterday and remove meter Refer to field service department
Non-Outage | J.E.26.07.15661 | C001854474 | Daniel Francis | St.Ann | Completed | Load_266688 | Roaring River - 210 | Jul 14, 2026 8:19am | Jul 14, 2026 8:19am | Jul 14, 2026 1:10pm | Jul 14, 2026 1:10pm | Jul 14, 2026 2:05pm | Jul 14, 2026 2:46pm | Jul 14, 2026 2:46pm | Jul 14, 2026 2:46pm | BrokenWire |  | Fair | No | Found secondary neutral broken opening 100kva splice and retention 1 span of 1 wire
Outage | J.E.26.07.15387 | C001854476 | Rusean Allen | KSAS | Completed | Load_255914 | Cane River - 310 | Jul 14, 2026 8:19am | Jul 14, 2026 8:20am | Jul 14, 2026 9:18am | Jul 14, 2026 9:41am | Jul 14, 2026 10:30am | Jul 14, 2026 10:31am | Jul 14, 2026 10:31am | Jul 14, 2026 10:31am |  |  | Fair | No | Found disconnected customer premises under investigation
Outage | J.E.26.07.15652 | C001854475 | Stephen Taylor | St.Thomas | Completed | Load_259221 | Lysson - 410 | Jul 14, 2026 8:19am | Jul 15, 2026 8:02am | Jul 15, 2026 12:30pm | Jul 15, 2026 12:30pm | Jul 15, 2026 12:41pm | Jul 15, 2026 12:41pm | Jul 15, 2026 12:46pm | Jul 15, 2026 12:46pm |  |  | Fair | No | Customer meter socket defective and need to change and contact back jps for connection
Non-Outage | J.E.26.07.10943 | C001854463 | Andre Williams | Trelawny | Completed | Load_240468 | Duncans - 110 | Jul 14, 2026 8:18am | Jul 14, 2026 8:20am | Jul 14, 2026 8:23am | Jul 14, 2026 10:09am | Jul 14, 2026 10:09am | Jul 14, 2026 10:13am | Jul 14, 2026 10:13am | Jul 14, 2026 10:13am | LeaningPole |  | Fair | No | 30 class 4 pole leaning on customer wall with single phase primary and open secondary, pole not broken just resting on customer wall, fourth time reporting same pole ,reffer to maintenance for follow up
Non-Outage | J.E.26.07.12049 | C001854466 | Cliton Henry | St.Mary | Completed | Load_243605 | Oracabessa - 110 | Jul 14, 2026 8:18am | Jul 14, 2026 8:18am | Jul 14, 2026 1:23pm | Jul 14, 2026 1:23pm | Jul 14, 2026 1:23pm | Jul 14, 2026 1:23pm | Jul 14, 2026 1:25pm | Jul 14, 2026 1:25pm |  |  | Fair | No | Supply restored, related report # 12592
Non-Outage | J.E.26.07.12145 | C001854469 | Cliton Henry | St.Mary | Completed | Load_256173 | Oracabessa - 210 | Jul 14, 2026 8:18am | Jul 14, 2026 8:18am | Jul 14, 2026 11:13am | Jul 14, 2026 11:14am | Jul 14, 2026 11:16am | Jul 14, 2026 11:16am | Jul 14, 2026 11:18am | Jul 14, 2026 11:18am |  |  | Fair | No | The customer stated that a team came yesterday and corrected the problem.
Non-Outage | J.E.26.07.12402 | C001854470 | Cliton Henry | St.Mary | Completed | Load_256173 | Oracabessa - 210 | Jul 14, 2026 8:18am | Jul 14, 2026 8:18am | Jul 14, 2026 11:25am | Jul 14, 2026 11:25am | Jul 14, 2026 11:28am | Jul 14, 2026 11:28am | Jul 14, 2026 11:29am | Jul 14, 2026 11:29am |  |  | Fair | No | The customer stated that the supply was corrected yesterday.
Non-Outage | J.E.26.07.12592 | C001854471 | Cliton Henry | St.Mary | Completed | Load_243605 | Oracabessa - 110 | Jul 14, 2026 8:18am | Jul 14, 2026 8:19am | Jul 14, 2026 12:12pm | Jul 14, 2026 12:12pm | Jul 14, 2026 12:26pm | Jul 14, 2026 12:51pm | Jul 14, 2026 1:14pm | Jul 14, 2026 1:14pm |  |  | Fair | No | The transformer drop lead found corrroded at pole. A 50 kva transformer was de energized to carryout repairs. Corrective work done to cut, clean and reconnected the transformer drop lead using 2 one bot clamp. Supply restored to energized the 50 kva transformer. Voltages left 120-120/240 volts
Non-Outage | J.E.26.07.13644 | C001854465 | Cliton Henry | St.Mary | Completed | Load_259971 | Oracabessa - 210 | Jul 14, 2026 8:18am | Jul 14, 2026 8:18am | Jul 14, 2026 10:58am | Jul 14, 2026 10:58am | Jul 14, 2026 10:58am | Jul 14, 2026 10:59am | Jul 14, 2026 11:04am | Jul 14, 2026 11:04am | Fire |  | Fair | No | Supply restored, related to outage 13652
Non-Outage | J.E.26.07.13652 | C001854464 | Cliton Henry | St.Mary | Completed | Load_259971 | Oracabessa - 210 | Jul 14, 2026 8:18am | Jul 14, 2026 8:18am | Jul 14, 2026 9:07am | Jul 14, 2026 9:07am | Jul 14, 2026 9:31am | Jul 14, 2026 10:56am | Jul 14, 2026 10:58am | Jul 14, 2026 10:58am | Fire |  | Fair | No | The secondary conductors found sagging and a tree in close proximity to the secondary line, burnt drop leads and corroded secondary jumpers. A 50 kva transformer was de energized to carryout repairs. Corrective work done to retension one span of secondary conductors using 2#2 and 2 2/0 preform,replace transformer drop lead and reconnected secondary jumper using 5 feet 2/0 pvc copper, two foot #2 AA conductor and 9 one bolt. Clamps. Supply restored to energized the 50 kva transformer.
Non-Outage | J.E.26.07.14578 | C001854467 | Cliton Henry | St.Mary | Completed | Load_256173 | Oracabessa - 210 | Jul 14, 2026 8:18am | Jul 14, 2026 8:18am | Jul 14, 2026 11:20am | Jul 14, 2026 11:20am | Jul 14, 2026 11:20am | Jul 14, 2026 11:23am | Jul 14, 2026 11:24am | Jul 14, 2026 11:24am |  |  | Fair | No | The customer with contact number provided stated that she didn’t make a report and she is in St. Catherine
Outage | J.E.26.07.15608 | C001854468 | Elvis Trowers | KSAN | Completed | Load_256020 | Constant Spring - 310 | Jul 14, 2026 8:18am | Jul 14, 2026 8:18am | Jul 14, 2026 8:58am | Jul 14, 2026 8:58am | Jul 14, 2026 9:42am | Jul 14, 2026 10:34am | Jul 14, 2026 10:34am | Jul 14, 2026 10:34am |  | Y | Fair | Yes | Areas was found without electricity supply when checked and a blown 5 amp transformer fuse was found and replaced after patrol was completed at pole #0001413 and trees contact was cut away, primary and secondary bushings still required.
Outage | J.E.26.07.15650 | C001854472 | Milton Charlton | KSAN | Completed | Load_253182 | Hope - 510 | Jul 14, 2026 8:18am | Jul 14, 2026 8:19am | Jul 14, 2026 10:39am | Jul 14, 2026 10:39am | Jul 14, 2026 1:13pm | Jul 14, 2026 12:50pm | Jul 14, 2026 1:16pm | Jul 14, 2026 1:16pm | Fire |  | Fair | No | Unable to locate customer by telephone.
Non-Outage | J.E.26.07.06188 | C001854461 | Andre Williams | Trelawny | Completed | Load_266884 | Duncans - 210 | Jul 14, 2026 8:17am | Jul 14, 2026 8:40am | Jul 14, 2026 10:05am | Jul 14, 2026 12:01pm | Jul 14, 2026 12:01pm | Jul 14, 2026 12:04pm | Jul 14, 2026 12:05pm | Jul 14, 2026 12:05pm | LeaningPole |  | Fair | No | Premises not found numbers not working unable to locate even with the help of dispatch
Non-Outage | J.E.26.07.07750 | C001854462 | Andre Williams | Trelawny | Completed | Load_250145 | Duncans - 210 | Jul 14, 2026 8:17am | Jul 14, 2026 8:20am | Jul 14, 2026 10:59am | Jul 14, 2026 10:59am | Jul 14, 2026 11:15am | Jul 14, 2026 11:35am | Jul 14, 2026 11:36am | Jul 14, 2026 11:36am | LeaningPole |  | Fair | No | Pole leaning on property has no jps hardware pole belong to flow , customer wants to build fence but runs risk of going near secondary line due to land being on embankment where fence is to be built.customer was advice to seek advice from Jps regarding relocation of pole as to clear line from property.
Non-Outage | J.E.26.07.14699 | C001854460 | Dwayne Samuels | Trelawny | Completed | Load_239112 | Greenwood - 110 | Jul 14, 2026 8:17am | Jul 14, 2026 11:34am | Jul 14, 2026 11:39am | Jul 14, 2026 11:53am | Jul 14, 2026 12:29pm | Jul 14, 2026 12:46pm | Jul 14, 2026 12:51pm | Jul 14, 2026 12:51pm |  |  | Fair | No | Top phase of customer service wire is disconnected from Jps pole that was the cause of customer single phasings reconnect phase to secondary line using 1 one bolt clamp voltage left after repair 112v/113v/225v
Non-Outage | J.E.26.07.07471 | C001854455 | Oraine Minto | St.Ann | Completed | Load_249305 | Ocho Rios - 510 | Jul 14, 2026 8:16am | Jul 14, 2026 8:16am | Jul 14, 2026 3:18pm | Jul 14, 2026 3:18pm | Jul 14, 2026 3:18pm | Jul 14, 2026 3:19pm | Jul 14, 2026 3:19pm | Jul 14, 2026 3:19pm |  |  | Fair | No | 234v 116v 17v
Non-Outage | J.E.26.07.12900 | C001854458 | Oraine Minto | St.Ann | Completed | Load_255814 | Ocho Rios - 510 | Jul 14, 2026 8:16am | Jul 14, 2026 8:16am | Jul 14, 2026 12:20pm | Jul 14, 2026 12:20pm | Jul 14, 2026 12:20pm | Jul 14, 2026 12:21pm | Jul 14, 2026 12:21pm | Jul 14, 2026 12:21pm |  |  | Fair | No | Customer states that they came yesterday and all her issues was resolved
Non-Outage | J.E.26.07.14511 | C001854456 | Oraine Minto | St.Ann | Completed | Load_249305 | Ocho Rios - 510 | Jul 14, 2026 8:16am | Jul 14, 2026 8:16am | Jul 14, 2026 1:44pm | Jul 14, 2026 2:46pm | Jul 14, 2026 2:46pm | Jul 14, 2026 2:47pm | Jul 14, 2026 3:18pm | Jul 14, 2026 3:18pm |  |  | Fair | No | 234v 117v 116v 3 one bolt clamp
Outage | J.E.26.07.15544 | C001854454 | Milton Charlton | KSAN | Completed | Load_572060 | Hope - 410 | Jul 14, 2026 8:16am | Jul 14, 2026 8:16am | Jul 14, 2026 10:15am | Jul 14, 2026 10:15am | Jul 14, 2026 10:32am | Jul 14, 2026 10:35am | Jul 14, 2026 10:34am | Jul 14, 2026 10:34am |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Non-Outage | J.E.26.07.07858 | C001854452 | Daniel Francis | St.Ann | Completed | Load_267230 | Ocho Rios - 410 | Jul 14, 2026 8:15am | Jul 14, 2026 8:15am | Jul 14, 2026 11:28am | Jul 14, 2026 11:28am | Jul 14, 2026 11:37am | Jul 14, 2026 11:50am | Jul 14, 2026 11:54am | Jul 14, 2026 11:54am |  |  | Fair | No | Found okay
Non-Outage | J.E.26.07.07865 | C001854450 | Daniel Francis | St.Ann | Completed | Load_267230 | Ocho Rios - 410 | Jul 14, 2026 8:15am | Jul 14, 2026 8:15am | Jul 14, 2026 11:54am | Jul 14, 2026 11:54am | Jul 14, 2026 11:54am | Jul 14, 2026 11:55am | Jul 14, 2026 11:55am | Jul 14, 2026 11:55am |  |  | Fair | No | Found okay
Outage | J.E.26.07.15621 | C001854453 | Dwayne Samuels | Trelawny | Completed | Load_556059 | Martha Brae - 110 | Jul 14, 2026 8:15am | Jul 14, 2026 8:16am | Jul 14, 2026 8:41am | Jul 14, 2026 8:41am | Jul 14, 2026 8:42am | Jul 14, 2026 9:20am | Jul 14, 2026 9:21am | Jul 14, 2026 9:21am |  |  | Fair | No | Patrol primary line to find 2 blown 15 amp junction fuse and 1 blown 4amp transformer fuse cause by birds complete line patrol before replacing 2 15amp junction and 4amp transformer fuse at same and close
Outage | J.E.26.07.15634 | C001854451 | Dwayne Samuels | Trelawny | Completed | Load_258614 | Greenwood - 110 | Jul 14, 2026 8:15am | Jul 14, 2026 8:16am | Jul 14, 2026 10:27am | Jul 14, 2026 10:27am | Jul 14, 2026 10:37am | Jul 14, 2026 10:38am | Jul 14, 2026 10:38am | Jul 14, 2026 10:38am |  |  | Fair | No | When spoke with customer they stated that they are located in Manchester
Non-Outage | J.E.26.07.07346 | C001854448 | Daniel Francis | St.Ann | Completed | Load_257505 | Ocho Rios - 310 | Jul 14, 2026 8:14am | Jul 14, 2026 8:14am | Jul 14, 2026 12:07pm | Jul 14, 2026 12:07pm | Jul 14, 2026 12:10pm | Jul 14, 2026 12:11pm | Jul 14, 2026 12:11pm | Jul 14, 2026 12:11pm |  |  | Fair | No | We call customer she say she is okay for now
Non-Outage | J.E.26.07.15475 | C001854445 | Michael Christian | St.James | Completed | Load_269402 | Rose Hall - 210 | Jul 14, 2026 8:13am | Jul 14, 2026 8:13am | Jul 14, 2026 11:04am | Jul 14, 2026 11:04am | Jul 14, 2026 11:39am | Jul 14, 2026 11:57am | Jul 14, 2026 11:57am | Jul 14, 2026 11:57am |  |  | Fair | No | Found defective clamp replace at pole voltage 111 113 224 at pothead
Outage | J.E.26.07.15644 | C001854444 | Michael Christian | St.James | Completed | Load_246358 | Rose Hall - 210 | Jul 14, 2026 8:13am | Jul 14, 2026 8:13am | Jul 14, 2026 9:13am | Jul 14, 2026 9:19am | Jul 14, 2026 9:54am | Jul 14, 2026 10:56am | Jul 14, 2026 11:04am | Jul 14, 2026 11:04am |  |  | Fair | No | Found secondary jumper bun off cause by banging wire open 100 kava to work replace 3 clamps voltage 111 113 at pothead
Non-Outage | J.E.26.07.14479 | C001854443 | Neckell Ormsby | St.Mary | Completed | Load_266601 | Highgate - 210 | Jul 14, 2026 8:11am | Jul 14, 2026 8:11am | Jul 14, 2026 10:43am | Jul 14, 2026 1:41pm | Jul 14, 2026 2:01pm | Jul 14, 2026 2:11pm | Jul 14, 2026 2:11pm | Jul 14, 2026 2:11pm |  |  | Fair | No | Unable to locate customer after several calls, no directions
Non-Outage | J.E.26.07.14773 | C001854442 | Fredrick Hamilton | KSAN | Completed | Load_246783 | Constant Spring - 410 | Jul 14, 2026 8:11am | Jul 14, 2026 8:12am | Jul 14, 2026 8:15am | Jul 14, 2026 11:00am | Jul 14, 2026 11:00am | Jul 14, 2026 11:02am | Jul 14, 2026 11:02am | Jul 14, 2026 11:02am |  |  | Fair | No | Customer contacted and stated power was restored fully previously Premises is ok
Non-Outage | J.E.26.07.15118 | C001854440 | Fredrick Hamilton | KSAN | Completed | Load_258520 | Constant Spring - 410 | Jul 14, 2026 8:11am | Jul 14, 2026 8:12am | Jul 14, 2026 8:15am | Jul 14, 2026 8:20am | Jul 14, 2026 8:20am | Jul 14, 2026 8:22am | Jul 14, 2026 8:22am | Jul 14, 2026 8:22am |  |  | Fair | No | Customer contacted and stated that it was a customer defect which was rectified by there electrician Premises is ok
Non-Outage | J.E.26.07.15161 | C001854441 | Fredrick Hamilton | KSAN | Completed | Load_264129 | Constant Spring - 210 | Jul 14, 2026 8:11am | Jul 14, 2026 8:12am | Jul 14, 2026 8:15am | Jul 14, 2026 12:33pm | Jul 14, 2026 1:35pm | Jul 14, 2026 1:49pm | Jul 14, 2026 1:49pm | Jul 14, 2026 1:49pm |  |  | Fair | No | Premises checked and found no JPS defect detected 238v/119v/118v obtained Bushing required in area
Non-Outage | J.E.26.07.15169 | C001854437 | Romaine Roberts | St.Mary | Completed | Load_260240 | Annotto Bay - 310 | Jul 14, 2026 8:11am | Jul 14, 2026 8:11am | Jul 14, 2026 11:27am | Jul 14, 2026 11:27am | Jul 14, 2026 12:16pm | Jul 14, 2026 12:33pm | Jul 14, 2026 12:38pm | Jul 14, 2026 12:38pm |  |  | Fair | No | Corrosion at pole clean and remake connection power restore voltage 113-114-228
Outage | J.E.26.07.15492 | C001854439 | Michael Christian | St.James | Completed | Load_243259 | Queens Drive - 710 | Jul 14, 2026 8:11am | Jul 14, 2026 8:12am | Jul 14, 2026 8:27am | Jul 14, 2026 8:27am | Jul 14, 2026 8:48am | Jul 14, 2026 9:06am | Jul 14, 2026 9:06am | Jul 14, 2026 9:06am |  |  | Fair | No | Found 1 15 amp out replace 1 15 amp no pole #
Outage | J.E.26.07.15509 | C001854438 | Michael Christian | St.James | Completed | Load_267418 | Queens Drive - 710 | Jul 14, 2026 8:11am | Jul 14, 2026 8:12am | Jul 14, 2026 9:15am | Jul 14, 2026 9:15am | Jul 14, 2026 9:18am | Jul 14, 2026 9:18am | Jul 14, 2026 9:18am | Jul 14, 2026 9:18am |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.07.10762 | C001854430 | Neckell Ormsby | St.Mary | Completed | Load_243697 | Highgate -110 | Jul 14, 2026 8:10am | Jul 14, 2026 8:10am | Jul 14, 2026 10:43am | Jul 14, 2026 11:35am | Jul 14, 2026 11:51am | Jul 14, 2026 12:00pm | Jul 14, 2026 12:00pm | Jul 14, 2026 12:00pm |  |  | Fair | No | We called customer and she said the issue was resolved
Non-Outage | J.E.26.07.14561 | C001854431 | Odaine Johnson | Clarendon | Completed | Load_237753 | Monymusk - 410 | Jul 14, 2026 8:10am | Jul 14, 2026 8:17am | Jul 14, 2026 9:11am | Jul 14, 2026 11:59am | Jul 14, 2026 12:20pm | Jul 14, 2026 12:20pm | Jul 14, 2026 12:22pm | Jul 14, 2026 12:22pm |  |  | Fair | No | Corroded neutral found at pothead remade connection using one pen union voltage reading 113/113/227 volts
Non-Outage | J.E.26.07.14612 | C001854432 | Odaine Johnson | Clarendon | Completed | Load_249266 | May Pen - 110 | Jul 14, 2026 8:10am | Jul 14, 2026 8:17am | Jul 14, 2026 9:11am | Jul 14, 2026 2:32pm | Jul 14, 2026 2:34pm | Jul 14, 2026 2:34pm | Jul 14, 2026 2:35pm | Jul 14, 2026 2:35pm |  |  | Fair | No | Premises found okay customer has internal problem
Non-Outage | J.E.26.07.14721 | C001854433 | Odaine Johnson | Clarendon | Completed | Load_574468 | Parnassus - 310 | Jul 14, 2026 8:10am | Jul 14, 2026 8:17am | Jul 14, 2026 9:11am | Jul 14, 2026 11:29am | Jul 14, 2026 11:55am | Jul 14, 2026 11:56am | Jul 14, 2026 11:57am | Jul 14, 2026 11:57am |  |  | Fair | No | Corrosion was found at pothead remade connection using one pen union voltage reading 117/117/234 volts
Non-Outage | J.E.26.07.15045 | C001854435 | Odaine Johnson | Clarendon | Completed | Load_405661 | Parnassus - 210 | Jul 14, 2026 8:10am | Jul 14, 2026 8:17am | Jul 14, 2026 9:11am | Jul 14, 2026 2:35pm | Jul 14, 2026 3:48pm | Jul 14, 2026 3:48pm | Jul 14, 2026 3:57pm | Jul 14, 2026 3:57pm |  |  | Fair | No | Both phase found corroded at pole remade connections using 2 one bolt clamps voltage reading 113/110/224 volts
Non-Outage | J.E.26.07.15155 | C001854434 | Odaine Johnson | Clarendon | Completed | Load_248257 | Monymusk - 410 | Jul 14, 2026 8:10am | Jul 14, 2026 8:17am | Jul 14, 2026 9:11am | Jul 14, 2026 12:22pm | Jul 14, 2026 12:43pm | Jul 14, 2026 12:54pm | Jul 14, 2026 12:55pm | Jul 14, 2026 12:55pm |  |  | Fair | No | Burn off phase found at pole remade connection using 1 one bolt clamp voltage reading 117 volts
Non-Outage | J.E.26.07.15344 | C001854436 | Odaine Johnson | Clarendon | Completed | Load_301192 | Monymusk - 210 | Jul 14, 2026 8:10am | Jul 14, 2026 8:17am | Jul 14, 2026 9:11am | Jul 14, 2026 10:57am | Jul 14, 2026 10:57am | Jul 14, 2026 11:11am | Jul 14, 2026 11:11am | Jul 14, 2026 11:11am |  |  | Fair | No | Burn off phase found at pole remade connection using 1 one bolt clamp voltage reading 113/113/227 volts
Non-Outage | J.E.26.07.10003 | C001854429 | Neckell Ormsby | St.Mary | Completed | Load_264348 | Highgate -110 | Jul 14, 2026 8:09am | Jul 14, 2026 8:09am | Jul 14, 2026 10:43am | Jul 14, 2026 12:00pm | Jul 14, 2026 12:25pm | Jul 14, 2026 12:50pm | Jul 14, 2026 12:57pm | Jul 14, 2026 12:57pm |  |  | Fair | No | Troubleshoot and found corrosion at pothead, clean and remade joints using 2- one bolt clamps voltage left 111v 114v 225v
Non-Outage | J.E.26.07.11608 | C001854428 | Neckell Ormsby | St.Mary | Completed | Load_242166 | Highgate -110 | Jul 14, 2026 8:09am | Jul 14, 2026 8:09am | Jul 14, 2026 10:43am | Jul 14, 2026 12:59pm | Jul 14, 2026 1:22pm | Jul 14, 2026 1:35pm | Jul 14, 2026 1:41pm | Jul 14, 2026 1:41pm |  |  | Fair | No | Unable to locate customer after several calls also no proper directions
Outage | J.E.26.07.14456 | C001854427 | Romeo Brissett | St.James | Completed | Load_252646 | Bogue - 410 | Jul 14, 2026 8:09am | Jul 14, 2026 8:09am | Jul 14, 2026 9:19am | Jul 14, 2026 9:19am | Jul 14, 2026 9:29am | Jul 14, 2026 12:40pm | Jul 14, 2026 12:49pm | Jul 14, 2026 12:49pm | Fire |  | Fair | No | Found 4/0 quad twisted conductor damage due to big units vehicles and heavy duty equipments passing resulting chafe fire, isolated (2)50 kva transformer, dislodged 4/0 twisted, repaired and retention 4/0 twisted Conductor.
Outage | J.E.26.07.15402 | C001854426 | Romeo Brissett | St.James | Completed | Load_241551 | Bogue - 310 | Jul 14, 2026 8:09am | Jul 14, 2026 8:09am | Jul 14, 2026 3:26pm | Jul 14, 2026 3:26pm | Jul 14, 2026 3:26pm | Jul 14, 2026 4:00pm | Jul 14, 2026 4:04pm | Jul 14, 2026 4:04pm |  |  | Fair | No | Check and found rammy connection, no power coming from box to service wire.
Non-Outage | J.E.26.07.15072 | C001854424 | Orville Lee | Portmore | Completed | Load_251353 | Naggo Head - 510 | Jul 14, 2026 8:08am | Jul 14, 2026 8:09am | Jul 14, 2026 8:44am | Jul 14, 2026 8:44am | Jul 14, 2026 9:43am | Jul 14, 2026 10:19am | Jul 14, 2026 10:21am | Jul 14, 2026 10:21am |  |  | Fair | No | Checks made and found clamps corroded at secondary Two 1 bolt clampVoltage118v119v237v
Non-Outage | J.E.26.07.15309 | C001854423 | Orville Lee | Portmore | Completed | Load_557413 | Naggo Head - 610 | Jul 14, 2026 8:08am | Jul 14, 2026 8:09am | Jul 14, 2026 10:21am | Jul 14, 2026 10:21am | Jul 14, 2026 10:39am | Jul 14, 2026 12:27pm | Jul 14, 2026 12:30pm | Jul 14, 2026 12:30pm |  |  | Fair | No | Checks made and found sliced joints defective Joints was corrected and customer service wire changed Voltage before160V55VVoltage after122V121V243V
Non-Outage | J.E.26.07.15422 | C001854422 | Orville Lee | St.Catherine | Completed | Load_261612 | Twickenham - 210 | Jul 14, 2026 8:08am | Jul 14, 2026 8:09am | Jul 14, 2026 1:24pm | Jul 15, 2026 8:59am | Jul 15, 2026 9:19am | Jul 15, 2026 9:44am | Jul 15, 2026 9:44am | Jul 15, 2026 9:44am |  |  | Fair | No | Checks made and found pothead corroded Three pen union used.Voltage 116v116v233v
Outage | J.E.26.07.15633 | C001854425 | Romeo Brissett | St.James | Completed | Load_557023 | Bogue - 310 | Jul 14, 2026 8:08am | Jul 14, 2026 8:10am | Jul 14, 2026 4:04pm | Jul 14, 2026 4:04pm | Jul 14, 2026 4:04pm | Jul 14, 2026 5:02pm | Jul 14, 2026 5:14pm | Jul 14, 2026 5:14pm | BrokenWire |  | Fair | No | Spliced and retention customer service wire, used 20ft of #6 and 2 clamps. V/R 114-15-230
Outage | J.E.26.07.15545 | C001854419 | Horace Malcolm | St.James | Completed | Load_302163 | Bogue - 610 | Jul 14, 2026 8:05am | Jul 15, 2026 8:04am | Jul 15, 2026 8:17am | Jul 15, 2026 8:20am | Jul 15, 2026 8:39am | Jul 15, 2026 8:43am | Jul 15, 2026 8:43am | Jul 15, 2026 8:43am |  |  | Fair | No | Check and found ok issue resolved 115-117-232
Non-Outage | J.E.26.07.14574 | C001854415 | Andrae Clarke | Portland | Completed | Load_250879 | Port Antonio - 310 | Jul 14, 2026 8:04am | Jul 14, 2026 8:04am | Jul 14, 2026 11:39am | Jul 14, 2026 11:39am | Jul 14, 2026 1:05pm | Jul 14, 2026 1:08pm | Jul 14, 2026 1:06pm | Jul 14, 2026 1:06pm |  |  | Fair | No | Made several phone calls to the customer and got no response
Non-Outage | J.E.26.07.14748 | C001854416 | Andrae Clarke | Portland | Completed | Load_265666 | Port Antonio - 310 | Jul 14, 2026 8:04am | Jul 14, 2026 8:04am | Jul 14, 2026 8:36am | Jul 14, 2026 10:37am | Jul 14, 2026 10:47am | Jul 14, 2026 11:22am | Jul 14, 2026 11:37am | Jul 14, 2026 11:37am |  |  | Fair | No | Replace burnt wireUse tape and 50ft wireCheck voltage 121/119/240
Non-Outage | J.E.26.07.14749 | C001854417 | Andrae Clarke | Portland | Completed | Load_265666 | Port Antonio - 310 | Jul 14, 2026 8:04am | Jul 14, 2026 8:04am | Jul 14, 2026 11:37am | Jul 14, 2026 11:37am | Jul 14, 2026 11:37am | Jul 14, 2026 11:29am | Jul 14, 2026 11:38am | Jul 14, 2026 11:38am |  |  | Fair | No | Check voltage 121/119/240Premises okay
Non-Outage | J.E.26.07.15374 | C001854418 | Andrae Clarke | Portland | Completed | Load_253681 | Port Antonio - 310 | Jul 14, 2026 8:04am | Jul 14, 2026 8:04am | Jul 14, 2026 10:28am | Jul 14, 2026 10:28am | Jul 14, 2026 10:28am | Jul 14, 2026 10:00am | Jul 14, 2026 10:36am | Jul 14, 2026 10:36am |  |  | Fair | No | Check voltage 117/119/236 Check meter meter burn needs to be changed refer to field service
Outage | J.E.26.07.11248 | C001854414 | Horace Malcolm | St.James | Completed | Load_238758 | Bogue - 610 | Jul 14, 2026 8:04am | Jul 14, 2026 8:04am | Jul 14, 2026 12:03pm | Jul 14, 2026 12:03pm | Jul 14, 2026 1:05pm | Jul 14, 2026 1:06pm | Jul 14, 2026 1:06pm | Jul 14, 2026 1:06pm |  |  | Fair | No | Check and found ok issue resolved 113-115-228
Non-Outage | J.E.26.07.15642 | C001854411 | Moses Elliston | null | Completed | null | null | Jul 14, 2026 8:03am | Jul 14, 2026 8:03am | Jul 14, 2026 11:47am | Jul 14, 2026 11:47am | Jul 14, 2026 11:47am | Jul 14, 2026 11:26am | Jul 14, 2026 11:50am | Jul 14, 2026 11:50am |  |  | Fair | No | Supply connected from Twickenham Office.New Installation
Outage | J.E.26.07.15587 | C001854412 | Horace Malcolm | St.James | Completed | Load_245547 | Bogue - 610 | Jul 14, 2026 8:03am | Jul 14, 2026 8:03am | Jul 14, 2026 8:56am | Jul 14, 2026 8:56am | Jul 14, 2026 9:58am | Jul 14, 2026 11:54am | Jul 14, 2026 11:54am | Jul 14, 2026 11:54am |  | Y | Fair | No | Refused one 50amp junction fuse
Outage | J.E.26.07.15610 | C001854410 | Horace Malcolm | St.James | Completed | Load_260210 | Bogue - 610 | Jul 14, 2026 8:03am | Jul 14, 2026 8:03am | Jul 14, 2026 11:57am | Jul 14, 2026 11:57am | Jul 14, 2026 11:57am | Jul 14, 2026 11:58am | Jul 14, 2026 11:58am | Jul 14, 2026 11:58am |  |  | Fair | No | Related to previous call job number 15587
Outage | J.E.26.07.15616 | C001854409 | Horace Malcolm | St.James | Completed | Load_246802 | Bogue - 610 | Jul 14, 2026 8:02am | Jul 14, 2026 8:03am | Jul 14, 2026 11:56am | Jul 14, 2026 11:56am | Jul 14, 2026 11:56am | Jul 14, 2026 11:57am | Jul 14, 2026 11:57am | Jul 14, 2026 11:57am |  |  | Fair | No | Related to previous call job number 15587
Non-Outage | J.E.26.07.14461 | C001854408 | Neckell Ormsby | St.Mary | Completed | Load_266816 | Highgate -110 | Jul 14, 2026 8:00am | Jul 14, 2026 8:01am | Jul 14, 2026 8:49am | Jul 14, 2026 8:49am | Jul 14, 2026 9:47am | Jul 14, 2026 10:36am | Jul 14, 2026 10:37am | Jul 14, 2026 10:37am | BrokenWire |  | Rains | No | Unable to locate customer after several calls however patrol and found broken secondary phase open 50 kva transformer new number seen splice and retention 2- pole span secondary phase using approximately 25ft #2-AA,2- one bolt clamps and 1- #2 preform reclose 50 kva transformer
Non-Outage | J.E.26.07.15389 | C001854407 | Dean Smith | Hanover | Completed | Load_556372 | Orange Bay - 210 | Jul 14, 2026 7:59am | Jul 14, 2026 8:37am | Jul 14, 2026 12:16pm | Jul 14, 2026 12:16pm | Jul 14, 2026 12:16pm | Jul 14, 2026 12:16pm | Jul 14, 2026 12:27pm | Jul 14, 2026 12:27pm |  |  | Fair | No | Found transformer drop lead joint Burt off, same was repaired. However customer breaker trip when reset . Internal fault, customer was advised.
Non-Outage | J.E.26.07.11616 | C001854406 | Ricky Hall | St.Catherine | Completed | Load_290839 | Rhodens Pen - 210 | Jul 14, 2026 7:58am | Jul 14, 2026 8:00am | Jul 14, 2026 12:16pm | Jul 14, 2026 12:16pm | Jul 14, 2026 12:28pm | Jul 14, 2026 12:28pm | Jul 14, 2026 12:29pm | Jul 14, 2026 12:29pm |  |  | Fair | No | Premises closed
Non-Outage | J.E.26.07.15502 | C001854405 | Roxroy Needham | St.Ann | Completed | Load_269661 | Cardiff Hall - 310 | Jul 14, 2026 7:58am | Jul 14, 2026 8:00am | Jul 14, 2026 9:23am | Jul 14, 2026 9:23am | Jul 14, 2026 10:21am | Jul 14, 2026 10:46am | Jul 14, 2026 10:48am | Jul 14, 2026 10:48am |  |  | Fair | No | Open a 25 KVA transformer at pole to repair transformer leed used 2 pg clamp voltage left at meter 113-114-229
Non-Outage | J.E.26.07.12225 | C001854403 | Ricky Hall | St.Catherine | Completed | Load_251630 | Rhodens Pen - 410 | Jul 14, 2026 7:57am | Jul 14, 2026 7:57am | Jul 14, 2026 8:57am | Jul 14, 2026 9:14am | Jul 14, 2026 9:58am | Jul 14, 2026 10:24am | Jul 14, 2026 10:25am | Jul 14, 2026 10:25am |  |  | Fair | No | Clean and reconnect 3W service at pole use 2 clamps 111/110/220
Outage | J.E.26.07.15287 | C001854404 | Dean Smith | Hanover | Completed | Load_573745 | Orange Bay - 210 | Jul 14, 2026 7:57am | Jul 14, 2026 8:37am | Jul 14, 2026 10:56am | Jul 14, 2026 10:56am | Jul 14, 2026 10:56am | Jul 14, 2026 10:56am | Jul 14, 2026 10:57am | Jul 14, 2026 10:57am |  |  | Fair | No | Unable to locate
Outage | J.E.26.07.15629 | C001854401 | Neckell Ormsby | St.Mary | Completed | Load_243461 | Highgate - 210 | Jul 14, 2026 7:56am | Jul 14, 2026 7:56am | Jul 14, 2026 8:02am | Jul 14, 2026 8:02am | Jul 14, 2026 8:30am | Jul 14, 2026 8:49am | Jul 14, 2026 8:49am | Jul 14, 2026 8:49am |  |  | Fair | No | Troubleshoot and found burnt joint at pole, remade joint using 2- one bolt clamps voltage left 120v 120v 240v
Outage | J.E.26.07.15104 | C001854397 | Andrew Powell | St.Elizabeth | Completed | Load_292683 | Maggotty - 210 | Jul 14, 2026 7:55am | Jul 14, 2026 7:55am | Jul 14, 2026 9:35am | Jul 14, 2026 9:35am | Jul 14, 2026 9:35am | Jul 14, 2026 9:48am | Jul 14, 2026 9:50am | Jul 14, 2026 9:50am | BrokenWire |  | SevereWind | No | Remade broken service wire phase joint at secondary line 3 wire using one clamp, voltage reading 112v - 114v phase to neutral 226v cross phase.
Outage | J.E.26.07.15409 | C001854398 | Andrew Powell | Manchester | Completed | Load_262703 | Spur Tree - 210 | Jul 14, 2026 7:55am | Jul 14, 2026 7:55am | Jul 14, 2026 8:11am | Jul 14, 2026 8:11am | Jul 14, 2026 8:13am | Jul 14, 2026 8:13am | Jul 14, 2026 8:15am | Jul 14, 2026 8:15am |  |  | Fair | No | Customer made report for Holland Village stated that supply restored last night.
Outage | J.E.26.07.15627 | C001854400 | Romaine Roberts | St.Mary | Completed | Load_251410 | Annotto Bay - 210 | Jul 14, 2026 7:55am | Jul 14, 2026 7:55am | Jul 14, 2026 8:20am | Jul 14, 2026 8:20am | Jul 14, 2026 11:25am | Jul 14, 2026 11:26am | Jul 14, 2026 11:26am | Jul 14, 2026 11:26am |  |  | Fair | No | Junction fuse found blown patrol line nothing found replace 10 amp and 15 amp junction power restore
Outage | J.E.26.07.15585 | C001854395 | Rayon Foster | Hanover | Completed | Load_302811 | Orange Bay - 310 | Jul 14, 2026 7:51am | Jul 14, 2026 7:53am | Jul 14, 2026 8:37am | Jul 14, 2026 8:47am | Jul 14, 2026 9:23am | Jul 14, 2026 10:19am | Jul 14, 2026 10:19am | Jul 14, 2026 10:19am |  |  | Fair | No | Patrol primary line to find one 8 amps junction fuse blow line was clear after patrolling replace with fuse and closed
Outage | J.E.26.07.15420 | C001854394 | Daniel Francis | St.Ann | Completed | Load_255026 | Ocho Rios - 310 | Jul 14, 2026 7:50am | Jul 14, 2026 7:50am | Jul 14, 2026 10:16am | Jul 14, 2026 10:16am | Jul 14, 2026 10:19am | Jul 14, 2026 10:29am | Jul 14, 2026 10:33am | Jul 14, 2026 10:33am |  |  | Fair | No | Found okay 117 118 236 in all customer need to work on meter box
Non-Outage | J.E.26.07.15623 | C001854392 | Roxroy Needham | St.Ann | Completed | Load_251763 | Cardiff Hall - 310 | Jul 14, 2026 7:49am | Jul 14, 2026 7:49am | Jul 14, 2026 10:48am | Jul 14, 2026 10:48am | Jul 14, 2026 11:50am | Jul 14, 2026 12:12pm | Jul 14, 2026 12:14pm | Jul 14, 2026 12:14pm | Fire | Y | Fair | No | Remove illegal connections from line and retention a span of secondary line
Outage | J.E.26.07.15604 | C001854393 | Wayne Dillion | St.Elizabeth | Completed | Load_255428 | Maggotty - 110 | Jul 14, 2026 7:49am | Jul 14, 2026 7:50am | Jul 14, 2026 10:28am | Jul 14, 2026 10:28am | Jul 14, 2026 11:41am | Jul 14, 2026 12:33pm | Jul 14, 2026 12:33pm | Jul 14, 2026 12:33pm |  |  | Fair | No | Reconnect customer using 30 feet of number 6 triplex 3 linket 3 one bolt clamp close one two amp fuse that protects 25 KVA transformer that was leave open from hurricane voltage reading 120v 121v 243v supply restore successfully
Outage | J.E.26.07.14797 | C001854389 | Donald Cunningham | St.Catherine | Completed | Load_245608 | Twickenham - 210 | Jul 14, 2026 7:48am | Jul 14, 2026 7:49am | Jul 14, 2026 2:14pm | Jul 14, 2026 2:14pm | Jul 14, 2026 3:01pm | Jul 14, 2026 3:14pm | Jul 14, 2026 3:14pm | Jul 14, 2026 3:14pm |  |  | Fair | No | Premises not located customer not reachable
Outage | J.E.26.07.14567 | C001854388 | Moses Elliston | St.Catherine | Completed | Load_270251 | Twickenham - 210 | Jul 14, 2026 7:46am | Jul 14, 2026 7:47am | Jul 15, 2026 1:10pm | Jul 15, 2026 1:10pm | Jul 15, 2026 1:53pm | Jul 15, 2026 1:53pm | Jul 15, 2026 1:54pm | Jul 15, 2026 1:54pm |  |  | Fair | No | Supply ok at premises.
Outage | J.E.26.07.15620 | C001854385 | Donald Cunningham | Portmore | Completed | Load_264640 | Naggo Head - 610 | Jul 14, 2026 7:44am | Jul 14, 2026 7:45am | Jul 14, 2026 8:25am | Jul 14, 2026 8:25am | Jul 14, 2026 10:31am | Jul 14, 2026 11:48am | Jul 14, 2026 12:44pm | Jul 14, 2026 12:44pm |  |  | Fair | No | Corroded secondary phase and neural by 50 kva transformer dahlia ave u using 12 clamps and one 2/0 preform voltage readings 119 / 2/240
Outage | J.E.26.07.15626 | C001854386 | Wan Carlos Scarlett | Portmore | Completed | Load_261040 | Naggo Head - 610 | Jul 14, 2026 7:44am | Jul 14, 2026 3:15pm | Jul 14, 2026 4:19pm | Jul 14, 2026 4:36pm | Jul 14, 2026 4:36pm | Jul 14, 2026 4:50pm | Jul 14, 2026 4:51pm | Jul 14, 2026 4:51pm |  |  | Fair | No | Refuse 10amp junction no pole # was found clear bird from off single phase primary line
Outage | J.E.26.07.15630 | C001854387 | Wan Carlos Scarlett | Portmore | Completed | Load_243215 | Naggo Head - 510 | Jul 14, 2026 7:44am | Jul 14, 2026 3:15pm | Jul 14, 2026 7:04pm | Jul 14, 2026 7:05pm | Jul 14, 2026 7:38pm | Jul 14, 2026 7:50pm | Jul 14, 2026 7:50pm | Jul 14, 2026 7:50pm |  |  | Fair | No | Customer was reconnected from escalation department power supply has been restored
Outage | J.E.26.07.15577 | C001854382 | Wan Carlos Scarlett | St.Catherine | Completed | Load_249744 | Twickenham - 210 | Jul 14, 2026 7:43am | Jul 14, 2026 3:15pm | Jul 14, 2026 4:45pm | Jul 14, 2026 9:42pm | Jul 14, 2026 10:27pm | Jul 15, 2026 12:16am | Jul 15, 2026 12:17am | Jul 15, 2026 12:17am |  |  | Fair | No | Reset customer breaker power supply has been restored
Non-Outage | J.E.26.07.15625 | C001854378 | Jermaine Williams | null | Completed | null | null | Jul 14, 2026 7:42am | Jul 14, 2026 7:42am | Jul 14, 2026 8:05am | Jul 14, 2026 8:05am | Jul 14, 2026 8:42am | Jul 14, 2026 8:55am | Jul 14, 2026 9:02am | Jul 14, 2026 9:02am |  |  | Fair | No | Defective 10kva need to be replaced, cct tied to adjacent cct . Readings found 98v, 101,199 40’ class 4 xfmr pole also broken at root and badly leaning. Refe4 to N McLean.
Outage | J.E.26.07.15605 | C001854379 | Romaine Roberts | St.Mary | Completed | Load_264075 | Annotto Bay - 210 | Jul 14, 2026 7:42am | Jul 14, 2026 7:42am | Jul 14, 2026 11:26am | Jul 14, 2026 11:26am | Jul 14, 2026 11:26am | Jul 14, 2026 11:26am | Jul 14, 2026 11:27am | Jul 14, 2026 11:27am |  |  | Fair | No | Junction fuse found blown patrol line nothing found replace 10 amp and 15 amp junction power restore
Outage | J.E.26.07.15628 | C001854380 | Clyde Brown | Clarendon | Completed | Load_251963 | May Pen - 110 | Jul 14, 2026 7:42am | Jul 14, 2026 7:43am | Jul 14, 2026 8:54am | Jul 14, 2026 10:29am | Jul 14, 2026 1:20pm | Jul 14, 2026 1:13pm | Jul 14, 2026 1:35pm | Jul 14, 2026 1:35pm |  |  | Fair | No | Defective 3wire service #2- 250ft line isolated about 25 customers are left without supply,maintenance department to replaced defective 3wire service
Outage | J.E.26.07.15538 | C001854377 | Jermaine Williams | Clarendon | Completed | Load_258028 | Monymusk - 210 | Jul 14, 2026 7:41am | Jul 14, 2026 7:42am | Jul 14, 2026 10:23am | Jul 14, 2026 10:23am | Jul 14, 2026 10:52am | Jul 14, 2026 10:56am | Jul 14, 2026 10:54am | Jul 14, 2026 10:54am |  |  | Fair | No | Remade joint at secondary using one clamp.
Outage | J.E.26.07.15539 | C001854376 | Jermaine Williams | Clarendon | Completed | Load_242454 | Monymusk - 410 | Jul 14, 2026 7:41am | Jul 14, 2026 7:42am | Jul 14, 2026 9:04am | Jul 14, 2026 9:04am | Jul 14, 2026 9:55am | Jul 14, 2026 10:26am | Jul 14, 2026 10:22am | Jul 14, 2026 10:22am |  |  | Fair | No | Replaced 100’ #6 triplex.
Outage | J.E.26.07.15600 | C001854375 | Clyde Brown | Clarendon | Completed | Load_265903 | May Pen - 110 | Jul 14, 2026 7:40am | Jul 14, 2026 7:41am | Jul 14, 2026 8:54am | Jul 14, 2026 8:55am | Jul 14, 2026 9:19am | Jul 14, 2026 9:49am | Jul 14, 2026 9:55am | Jul 14, 2026 9:55am | Fire |  | Fair | No | Defective 3 wire service burnt up same repaired and supply now ok.
Outage | J.E.26.07.15520 | C001854366 | Daniel Francis | St.Ann | Completed | Load_248125 | Ocho Rios - 310 | Jul 14, 2026 7:29am | Jul 14, 2026 7:29am | Jul 14, 2026 8:46am | Jul 14, 2026 8:46am | Jul 14, 2026 9:02am | Jul 14, 2026 9:07am | Jul 14, 2026 9:08am | Jul 14, 2026 9:08am |  |  | Fair | No | Found customer stantion lean customer need to get repair done on stantion
Outage | J.E.26.07.15602 | C001854369 | Daniel Francis | St.Ann | Completed | Load_245789 | Roaring River - 210 | Jul 14, 2026 7:29am | Jul 14, 2026 7:29am | Jul 14, 2026 11:56am | Jul 14, 2026 11:56am | Jul 14, 2026 12:04pm | Jul 14, 2026 12:05pm | Jul 14, 2026 12:06pm | Jul 14, 2026 12:06pm |  |  | Fair | No | Found okay customer say light come them good
Outage | J.E.26.07.14781 | C001854361 | Kenroy Dale | Manchester | Completed | Load_263539 | Kendal - 210 | Jul 14, 2026 7:23am | Jul 14, 2026 8:26am | Jul 15, 2026 9:09am | Jul 15, 2026 12:22pm | Jul 15, 2026 1:14pm | Jul 15, 2026 1:39pm | Jul 15, 2026 1:42pm | Jul 15, 2026 1:42pm | BrokenPole |  | Fair | No | 40 foot class 6 TA pole found with top burned out, pole need urgent attention
Non-Outage | J.E.26.07.15353 | C001854355 | Collin Robinson | null | Completed | null | null | Jul 14, 2026 7:22am | Jul 14, 2026 7:23am | Jul 14, 2026 9:43am | Jul 14, 2026 9:43am | Jul 14, 2026 9:47am | Jul 14, 2026 9:50am | Jul 14, 2026 9:50am | Jul 14, 2026 9:50am |  |  | Rains | No | Information received from customer that supply was restored back from last night
Outage | J.E.26.07.14848 | C001854358 | Kenroy Dale | Manchester | Completed | Load_261877 | Kendal - 210 | Jul 14, 2026 7:22am | Jul 14, 2026 8:26am | Jul 14, 2026 2:33pm | Jul 14, 2026 2:34pm | Jul 14, 2026 3:00pm | Jul 14, 2026 3:02pm | Jul 14, 2026 3:02pm | Jul 14, 2026 3:02pm |  |  | Fair | No | Burned off phase found at pole, remade connection using one 1bolt clamp. Voltage reading 110/112/222
Outage | J.E.26.07.15312 | C001854356 | Ryan Richards | Manchester | Completed | Load_247253 | Kendal - 210 | Jul 14, 2026 7:22am | Jul 14, 2026 3:29pm | Jul 14, 2026 6:07pm | Jul 14, 2026 7:43pm | Jul 14, 2026 7:43pm | Jul 14, 2026 7:44pm | Jul 14, 2026 7:44pm | Jul 14, 2026 7:44pm |  |  | Fair | No | Same as the other
Outage | J.E.26.07.15314 | C001854357 | Kenroy Dale | Manchester | Completed | Load_303044 | Kendal - 210 | Jul 14, 2026 7:22am | Jul 15, 2026 7:50am | Jul 15, 2026 1:49pm | Jul 15, 2026 2:54pm | Jul 15, 2026 3:41pm | Jul 15, 2026 3:42pm | Jul 15, 2026 3:44pm | Jul 15, 2026 3:44pm |  |  | Fair | No | Customer meter lost single call center was contacted and customer now with supply
Outage | J.E.26.07.15612 | C001854354 | Collin Robinson | Portland | Completed | Load_242465 | Port Antonio - 310 | Jul 14, 2026 7:22am | Jul 14, 2026 7:22am | Jul 14, 2026 8:35am | Jul 14, 2026 8:35am | Jul 14, 2026 9:09am | Jul 14, 2026 9:29am | Jul 14, 2026 9:29am | Jul 14, 2026 9:29am |  |  | Rains | No | Replace 20 amps junction fuse at pole 0053273
Outage | J.E.26.07.14581 | C001854346 | Richard Samuda | Manchester | Completed | Load_244975 | Spur Tree - 310 | Jul 14, 2026 7:18am | Jul 14, 2026 7:19am | Jul 14, 2026 12:37pm | Jul 14, 2026 12:38pm | Jul 14, 2026 12:38pm | Jul 14, 2026 12:38pm | Jul 14, 2026 12:40pm | Jul 14, 2026 12:40pm | LeaningPole |  | Fair | No | Customer say he didn’t make a call
Outage | J.E.26.07.14795 | C001854347 | Richard Samuda | Manchester | Completed | Load_256312 | Spur Tree - 310 | Jul 14, 2026 7:18am | Jul 14, 2026 7:19am | Jul 14, 2026 12:40pm | Jul 14, 2026 1:52pm | Jul 14, 2026 1:52pm | Jul 14, 2026 2:58pm | Jul 14, 2026 1:59pm | Jul 14, 2026 1:59pm |  |  | Fair | No | Change customer service wire that was damaged customer customer to experience low voltage using 40 of #6 service wire and 4 one bolt clamps voltage 114/116/230
Outage | J.E.26.07.15017 | C001854345 | Richard Samuda | Manchester | Completed | Load_238520 | Spur Tree - 310 | Jul 14, 2026 7:18am | Jul 14, 2026 7:19am | Jul 14, 2026 7:42am | Jul 14, 2026 7:42am | Jul 14, 2026 7:43am | Jul 14, 2026 7:43am | Jul 14, 2026 8:19am | Jul 14, 2026 8:19am |  |  | Fair | No | Found 10 amps junction blown patrol area found nothing replaced fuse close line customer back to normal
Outage | J.E.26.07.15051 | C001854341 | Richard Samuda | Manchester | Completed | Load_302769 | Spur Tree - 210 | Jul 14, 2026 7:18am | Jul 14, 2026 7:19am | Jul 14, 2026 9:32am | Jul 14, 2026 9:32am | Jul 14, 2026 9:32am | Jul 14, 2026 9:40am | Jul 14, 2026 9:40am | Jul 14, 2026 9:40am |  |  | Fair | No | Found okay
Non-Outage | J.E.26.07.15438 | C001854339 | Stephen Taylor | null | Completed | null | null | Jul 14, 2026 7:17am | Jul 14, 2026 7:18am | Jul 14, 2026 12:58pm | Jul 14, 2026 12:58pm | Jul 14, 2026 2:46pm | Jul 14, 2026 2:46pm | Jul 14, 2026 2:49pm | Jul 14, 2026 2:49pm |  |  | Fair | No | Clean up single phase line use 3 one bolts clamp
Outage | J.E.26.07.15182 | C001854340 | Stephen Taylor | St.Thomas | Completed | Load_338587 | Lysson - 410 | Jul 14, 2026 7:17am | Jul 14, 2026 7:18am | Jul 14, 2026 9:01am | Jul 14, 2026 9:25am | Jul 14, 2026 9:25am | Jul 14, 2026 9:25am | Jul 14, 2026 9:27am | Jul 14, 2026 9:27am |  |  | Fair | No | Junction fuse no number and pole patrol clear line with switch stick and close up back junction fuse safely with a 15 amp fuse all customer is now okay
Outage | J.E.26.07.15546 | C001854337 | Stephen Taylor | St.Thomas | Completed | Load_240667 | Good Year - 110 | Jul 14, 2026 7:17am | Jul 14, 2026 7:18am | Jul 14, 2026 10:24am | Jul 14, 2026 10:24am | Jul 14, 2026 12:26pm | Jul 14, 2026 12:26pm | Jul 14, 2026 12:54pm | Jul 14, 2026 12:54pm |  |  | Fair | No | Junction fuse out patrol clear line and close up back junction fuse with a 7 amp fuse safely customer is now okay
Outage | J.E.26.07.15580 | C001854338 | Stephen Taylor | St.Thomas | Completed | Load_261507 | Good Year - 210 | Jul 14, 2026 7:17am | Jul 14, 2026 7:18am | Jul 14, 2026 6:05pm | Jul 14, 2026 6:05pm | Jul 14, 2026 6:32pm | Jul 14, 2026 6:32pm | Jul 14, 2026 6:34pm | Jul 14, 2026 6:34pm |  |  | Fair | No | Contact customer and customer say that power was restored and now okay
Outage | J.E.26.07.15527 | C001854271 | Omar King | St.Ann | Completed | Load_266228 | Roaring River - 410 | Jul 14, 2026 12:31am | Jul 14, 2026 12:37am | Jul 14, 2026 12:57am | Jul 14, 2026 12:57am | Jul 14, 2026 1:09am | Jul 14, 2026 1:40am | Jul 14, 2026 1:40am | Jul 14, 2026 1:40am |  |  | Fair | No | Found a 25 KVA transformer fuse blow cause by vegetation fuse as been replaced area is now with supply . Area need severe bushing please refer to maintenance
Outage | J.E.26.07.14567 | C001854269 | Delano Gayle | St.Catherine | Completed | Load_270251 | Twickenham - 210 | Jul 14, 2026 12:24am | Jul 14, 2026 12:25am | Jul 14, 2026 1:46am | Jul 14, 2026 1:46am | Jul 14, 2026 1:54am | Jul 14, 2026 1:56am | Jul 14, 2026 1:57am | Jul 14, 2026 1:57am |  |  | Fair | No | Single customer, premises not found, area patrolled and found okay, Eg system in area
Outage | J.E.26.07.15341 | C001854270 | Delano Gayle | St.Catherine | Completed | Load_260470 | Twickenham - 210 | Jul 14, 2026 12:24am | Jul 14, 2026 12:25am | Jul 14, 2026 1:57am | Jul 14, 2026 1:57am | Jul 14, 2026 2:02am | Jul 14, 2026 2:05am | Jul 14, 2026 2:05am | Jul 14, 2026 2:05am |  |  | Fair | No | Non outage call, area found okay, premises not found
Outage | J.E.26.07.15439 | C001854268 | Delano Gayle | St.Catherine | Completed | Load_249744 | Twickenham - 210 | Jul 14, 2026 12:24am | Jul 14, 2026 12:25am | Jul 14, 2026 1:18am | Jul 14, 2026 1:18am | Jul 14, 2026 1:39am | Jul 14, 2026 1:45am | Jul 14, 2026 1:46am | Jul 14, 2026 1:46am |  |  | Fair | No | Premises not found no answer from customer phone, single customer, area found okay
Outage | J.E.26.07.15465 | C001854266 | Delano Gayle | St.Catherine | Completed | Load_244050 | Tredegar - 410 | Jul 14, 2026 12:15am | Jul 14, 2026 12:23am | Jul 14, 2026 12:28am | Jul 14, 2026 12:28am | Jul 14, 2026 1:14am | Jul 14, 2026 1:16am | Jul 14, 2026 1:16am | Jul 14, 2026 1:16am |  |  | Fair | No | Trip 25kva transformer no pole number patrolled line section and found okay for closure, reset transformer, illegal connections causing transformer to trip
Outage | J.E.26.07.14757 | C001854264 | Elvis Trowers | KSAN | Completed | Load_247843 | Constant Spring - 210 | Jul 13, 2026 11:23pm | Jul 14, 2026 8:25am | Jul 14, 2026 10:47am | Jul 14, 2026 10:47am | Jul 14, 2026 11:10am | Jul 14, 2026 11:16am | Jul 14, 2026 11:16am | Jul 14, 2026 11:16am |  |  | Fair | Yes | Customer was contacted and she suggested that the power supply was restored from last night.
Outage | J.E.26.07.15167 | C001854263 | Rusean Allen | KSAN | Completed | Load_238001 | Constant Spring - 410 | Jul 13, 2026 11:23pm | Jul 13, 2026 11:27pm | Jul 14, 2026 1:32am | Jul 14, 2026 1:32am | Jul 14, 2026 3:42am | Jul 14, 2026 3:46am | Jul 14, 2026 3:46am | Jul 14, 2026 3:46am | BrokenPole,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Broken 30ft pole containing open secondary wires found, pole needs to be changed, refer to maintenance department.
Non-Outage | J.E.26.07.15239 | C001854262 | Rusean Allen | null | Completed | null | null | Jul 13, 2026 11:22pm | Jul 13, 2026 11:27pm | Jul 14, 2026 3:47am | Jul 14, 2026 3:47am | Jul 14, 2026 3:48am | Jul 14, 2026 3:49am | Jul 14, 2026 3:49am | Jul 14, 2026 3:49am |  |  | Fair | No | Meter center locked
Outage | J.E.26.07.15272 | C001854251 | Wayne Dillion | St.Elizabeth | Completed | Load_260427 | Maggotty - 110 | Jul 13, 2026 9:50pm | Jul 14, 2026 7:50am | Jul 14, 2026 9:48am | Jul 14, 2026 9:48am | Jul 14, 2026 9:48am | Jul 14, 2026 10:22am | Jul 14, 2026 10:22am | Jul 14, 2026 10:22am |  |  | Fair | No | Patrol and found 1 blown 3 amp fuse that protects 25 KVA transformer no pole number and one dislodge conductor.reattach conductor and replace fuse supply restore to customer successfully
Outage | J.E.26.07.15316 | C001854252 | Selvin White | St.Elizabeth | Completed | Load_253396 | Maggotty - 110 | Jul 13, 2026 9:50pm | Jul 14, 2026 7:51am | Jul 14, 2026 8:07am | Jul 14, 2026 8:07am | Jul 14, 2026 8:32am | Jul 14, 2026 8:35am | Jul 14, 2026 8:36am | Jul 14, 2026 8:36am |  |  | Fair | No | Customer says supply was restored from last night .
Outage | J.E.26.07.15184 | C001854249 | Fitzroy Turner | KSAS | Completed | Load_258279 | Three Miles - 510 | Jul 13, 2026 9:37pm | Jul 13, 2026 9:37pm | Jul 13, 2026 10:04pm | Jul 13, 2026 10:04pm | Jul 13, 2026 10:34pm | Jul 13, 2026 10:35pm | Jul 13, 2026 10:35pm | Jul 13, 2026 10:35pm |  |  | Fair | No | Customer premises close at this time
Outage | J.E.26.07.15469 | C001854248 | Stephen Taylor | St.Thomas | Completed | Load_577151 | Lysson - 410 | Jul 13, 2026 9:33pm | Jul 13, 2026 9:33pm | Jul 14, 2026 9:28am | Jul 14, 2026 9:28am | Jul 14, 2026 9:59am | Jul 14, 2026 10:00am | Jul 14, 2026 10:23am | Jul 14, 2026 10:23am |  |  | Fair | No | Junction fuse out patrol and clear dead bird from line and close up back junction with a 10 amp fuse safely customer is now okay
Outage | J.E.26.07.15383 | C001854243 | Collin Robinson | Portland | Completed | Load_247400 | Port Antonio - 410 | Jul 13, 2026 9:17pm | Jul 13, 2026 9:17pm | Jul 13, 2026 10:18pm | Jul 13, 2026 10:18pm | Jul 13, 2026 10:29pm | Jul 13, 2026 10:40pm | Jul 13, 2026 10:42pm | Jul 13, 2026 10:42pm |  |  | Rains | No | Replace 10 amps junction fuse
Outage | J.E.26.07.15292 | C001854239 | Richard Samuda | Manchester | Completed | Load_336391 | Spur Tree - 210 | Jul 13, 2026 9:12pm | Jul 14, 2026 7:29am | Jul 14, 2026 8:19am | Jul 14, 2026 8:19am | Jul 14, 2026 8:54am | Jul 14, 2026 9:31am | Jul 14, 2026 9:32am | Jul 14, 2026 9:32am |  |  | Fair | No | Found 30 amps junction blown patrol line found nothing replaced fuse close line customer back to normal
Outage | J.E.26.07.15426 | C001854240 | Marlon Authors | Manchester | Completed | Load_567626 | Spur Tree - 210 | Jul 13, 2026 9:12pm | Jul 13, 2026 9:14pm | Jul 13, 2026 10:38pm | Jul 13, 2026 10:38pm | Jul 13, 2026 10:38pm | Jul 13, 2026 10:47pm | Jul 13, 2026 10:47pm | Jul 13, 2026 10:47pm |  |  | Fair | No | Patrol and found clear. Replace one blown 20 amp junction fuse no pole #. Restored supply okay
Outage | J.E.26.07.15051 | C001854235 | Marlon Authors | Manchester | Completed | Load_302769 | Spur Tree - 210 | Jul 13, 2026 9:07pm | Jul 13, 2026 9:07pm | Jul 13, 2026 10:47pm | Jul 13, 2026 10:47pm | Jul 13, 2026 10:48pm | Jul 13, 2026 10:49pm | Jul 13, 2026 10:49pm | Jul 13, 2026 10:49pm |  |  | Fair | No | Manchester call
Outage | J.E.26.07.15104 | C001854234 | Marlon Brown | St.Elizabeth | Completed | Load_292683 | Maggotty - 210 | Jul 13, 2026 9:07pm | Jul 13, 2026 9:13pm | Jul 13, 2026 9:40pm | Jul 13, 2026 9:40pm | Jul 13, 2026 9:40pm | Jul 13, 2026 9:41pm | Jul 13, 2026 9:41pm | Jul 13, 2026 9:41pm | BrokenWire |  | Fair | No | St Elizabeth call
Outage | J.E.26.07.15091 | C001854229 | Oshane Warren | Westmoreland | Completed | Load_259377 | Paradise - 310 | Jul 13, 2026 9:06pm | Jul 14, 2026 8:33am | Jul 14, 2026 8:49am | Jul 14, 2026 8:49am | Jul 14, 2026 10:39am | Jul 14, 2026 10:42am | Jul 14, 2026 10:42am | Jul 14, 2026 10:42am |  |  | Fair | No | Check and find ok
Outage | J.E.26.07.15228 | C001854230 | Richman Whyte | Westmoreland | Completed | Load_248327 | Paradise - 210 | Jul 13, 2026 9:06pm | Jul 13, 2026 9:07pm | Jul 13, 2026 9:53pm | Jul 13, 2026 9:53pm | Jul 13, 2026 9:53pm | Jul 13, 2026 9:53pm | Jul 13, 2026 9:54pm | Jul 13, 2026 9:54pm |  |  | Fair | No | Customer stated that power was restored earlier
Outage | J.E.26.07.15242 | C001854231 | Javid Vernon | Westmoreland | Completed | Load_264156 | Paradise - 310 | Jul 13, 2026 9:06pm | Jul 13, 2026 9:07pm | Jul 13, 2026 9:45pm | Jul 13, 2026 9:45pm | Jul 13, 2026 10:27pm | Jul 13, 2026 10:35pm | Jul 13, 2026 10:35pm | Jul 13, 2026 10:35pm |  |  | Fair | No | Area check and found okay unable to locate customer phone calls to number went unanswered
Outage | J.E.26.07.15446 | C001854227 | Fitzroy Turner | KSAS | Completed | Load_252001 | Duhaney - 410 | Jul 13, 2026 9:00pm | Jul 13, 2026 9:01pm | Jul 13, 2026 9:50pm | Jul 13, 2026 9:50pm | Jul 13, 2026 9:55pm | Jul 13, 2026 10:03pm | Jul 13, 2026 10:03pm | Jul 13, 2026 10:03pm | Fire |  | Fair | No | No fire seeing at this location
Non-Outage | J.E.26.07.14903 | C001854223 | Moses Elliston | null | Completed | null | null | Jul 13, 2026 8:57pm | Jul 13, 2026 9:00pm | Jul 14, 2026 10:14am | Jul 14, 2026 10:14am | Jul 14, 2026 10:14am | Jul 14, 2026 10:30am | Jul 14, 2026 10:31am | Jul 14, 2026 10:31am | BrokenWire |  | Fair | No | Broken 3 wire service neutral repaired with 2 clamps.
Outage | J.E.26.07.15401 | C001854214 | Floyd Taylor | Trelawny | Completed | Load_264455 | Greenwood - 110 | Jul 13, 2026 8:45pm | Jul 13, 2026 8:47pm | Jul 13, 2026 9:06pm | Jul 13, 2026 9:07pm | Jul 13, 2026 10:45pm | Jul 13, 2026 10:46pm | Jul 13, 2026 10:46pm | Jul 13, 2026 10:46pm |  |  | Fair | No | Found ok, contacted customer and customer advised power was restored
Non-Outage | J.E.26.07.14762 | C001854209 | Omar King | St.Ann | Completed | Load_259648 | Cardiff Hall - 210 | Jul 13, 2026 8:32pm | Jul 13, 2026 11:04pm | Jul 13, 2026 11:18pm | Jul 13, 2026 11:19pm | Jul 14, 2026 12:13am | Jul 14, 2026 12:26am | Jul 14, 2026 12:27am | Jul 14, 2026 12:27am |  |  | Fair | No | Found transformer switch top broken from main line unable to carry out repair due to safety measures and to avoid numbers of outage in the Dumbarton and Minard area I was advise by D Willis refer call to maintenance
Outage | J.E.26.07.15420 | C001854210 | Omar King | St.Ann | Completed | Load_255026 | Ocho Rios - 310 | Jul 13, 2026 8:32pm | Jul 13, 2026 8:32pm | Jul 13, 2026 8:47pm | Jul 13, 2026 8:47pm | Jul 13, 2026 9:46pm | Jul 13, 2026 9:47pm | Jul 13, 2026 9:48pm | Jul 13, 2026 9:48pm |  |  | Fair | No | Area need daylight attention unsafe area
Outage | J.E.26.07.15209 | C001854206 | Raymond Lewis | St.Ann | Completed | Load_265779 | Cardiff Hall - 310 | Jul 13, 2026 8:27pm | Jul 13, 2026 8:27pm | Jul 13, 2026 9:15pm | Jul 13, 2026 9:15pm | Jul 13, 2026 9:42pm | Jul 13, 2026 11:02pm | Jul 13, 2026 11:03pm | Jul 13, 2026 11:03pm | Fire |  | Fair | No | Need feel service to attend to box enclosure ( burnt out ) 05842 two or more customer out of supply
Outage | J.E.26.07.15191 | C001854196 | Tyrese Williams | St.Ann | Completed | Load_249052 | Cardiff Hall - 310 | Jul 13, 2026 8:01pm | Jul 13, 2026 8:01pm | Jul 13, 2026 8:08pm | Jul 13, 2026 8:09pm | Jul 13, 2026 8:09pm | Jul 13, 2026 8:11pm | Jul 13, 2026 8:11pm | Jul 13, 2026 8:11pm |  |  | Fair | No | Premises found ok call related to the 50amp junction fuse
Outage | J.E.26.07.15192 | C001854194 | Tyrese Williams | St.Ann | Completed | Load_251950 | Cardiff Hall - 310 | Jul 13, 2026 8:01pm | Jul 13, 2026 8:01pm | Jul 13, 2026 8:09pm | Jul 13, 2026 8:12pm | Jul 13, 2026 8:13pm | Jul 13, 2026 8:13pm | Jul 13, 2026 8:13pm | Jul 13, 2026 8:13pm |  |  | Fair | No | Premises found ok call related to the 50amp junction fuse
Outage | J.E.26.07.15286 | C001854193 | Tyrese Williams | St.Ann | Completed | Load_262044 | Cardiff Hall - 310 | Jul 13, 2026 8:01pm | Jul 13, 2026 8:01pm | Jul 13, 2026 8:09pm | Jul 13, 2026 8:13pm | Jul 13, 2026 8:13pm | Jul 13, 2026 8:14pm | Jul 13, 2026 8:14pm | Jul 13, 2026 8:14pm |  |  | Fair | No | Premises found ok call related to the 50amp junction fuse
Outage | J.E.26.07.15357 | C001854195 | Tyrese Williams | St.Ann | Completed | Load_243053 | Cardiff Hall - 310 | Jul 13, 2026 8:01pm | Jul 13, 2026 8:01pm | Jul 13, 2026 8:08pm | Jul 13, 2026 8:11pm | Jul 13, 2026 8:11pm | Jul 13, 2026 8:12pm | Jul 13, 2026 8:12pm | Jul 13, 2026 8:12pm |  |  | Fair | No | Premises found ok call related to the 50amp junction fuse
Non-Outage | J.E.26.07.15281 | C001854191 | Milton Charlton | KSAN | Completed | Load_574898 | Washington Blvd - 810 | Jul 13, 2026 7:59pm | Jul 13, 2026 8:01pm | Jul 13, 2026 8:24pm | Jul 13, 2026 8:24pm | Jul 13, 2026 8:44pm | Jul 13, 2026 8:45pm | Jul 13, 2026 8:50pm | Jul 13, 2026 8:50pm | BrokenPole |  | Fair | No | 30ft wooden pole # 052805 rotten at the foot and broken and leaning towards customer property pole is held up by open wire secondary conductor. Pole has on open wire secondary, one streetlight, service wire and D/Guy. Need immediate attention.
Outage | J.E.26.07.15376 | C001854192 | Edward Royal | KSAN | Completed | Load_252893 | Constant Spring - 410 | Jul 13, 2026 7:59pm | Jul 13, 2026 8:01pm | Jul 13, 2026 8:51pm | Jul 13, 2026 8:51pm | Jul 13, 2026 8:51pm | Jul 13, 2026 8:52pm | Jul 13, 2026 8:52pm | Jul 13, 2026 8:52pm |  |  | Fair | No | Premises not found unable to communicate with customer
Non-Outage | J.E.26.07.15392 | C001854190 | Milton Charlton | null | Completed | null | null | Jul 13, 2026 7:58pm | Jul 13, 2026 8:00pm | Jul 13, 2026 8:50pm | Jul 13, 2026 8:50pm | Jul 13, 2026 10:01pm | Jul 13, 2026 10:20pm | Jul 13, 2026 10:04pm | Jul 13, 2026 10:04pm | Fire |  | Fair | No | Found okay upon arrival. Customer complaining that the street light on section of Miraflores Drive is not working.
Outage | J.E.26.07.13806 | C001854156 | Tajay Bernard | Hanover | Completed | Load_245732 | Orange Bay - 310 | Jul 13, 2026 7:17pm | Jul 13, 2026 7:18pm | Jul 13, 2026 7:21pm | Jul 13, 2026 7:23pm | Jul 13, 2026 8:49pm | Jul 13, 2026 9:19pm | Jul 13, 2026 9:21pm | Jul 13, 2026 9:21pm |  |  | Fair | No | Reconnect customer service wire use 3 clamps voltage reading 113/113/226
Outage | J.E.26.07.15339 | C001854154 | Ricky Hall | St.Catherine | Completed | Load_556339 | Rhodens Pen - 210 | Jul 13, 2026 7:15pm | Jul 14, 2026 7:52am | Jul 14, 2026 11:17am | Jul 14, 2026 11:17am | Jul 14, 2026 11:49am | Jul 14, 2026 12:15pm | Jul 14, 2026 12:15pm | Jul 14, 2026 12:15pm | LowHangingWires |  | Fair | No | Retention low hanging secondary use 1 preform
Outage | J.E.26.07.15345 | C001854155 | Nickolas Rodriques | St.Catherine | Completed | Load_556350 | Rhodens Pen - 210 | Jul 13, 2026 7:15pm | Jul 13, 2026 7:16pm | Jul 13, 2026 9:35pm | Jul 13, 2026 9:36pm | Jul 13, 2026 9:56pm | Jul 13, 2026 10:18pm | Jul 13, 2026 10:18pm | Jul 13, 2026 10:18pm |  |  | Fair | No | Call relates to the 3 amp fuse that was replaced. Power restored.
Outage | J.E.26.07.15288 | C001854152 | Hartley Chin | Clarendon | Completed | Load_259916 | Parnassus - 310 | Jul 13, 2026 7:14pm | Jul 13, 2026 7:15pm | Jul 13, 2026 8:10pm | Jul 13, 2026 10:13pm | Jul 13, 2026 10:49pm | Jul 13, 2026 10:53pm | Jul 13, 2026 10:53pm | Jul 13, 2026 10:53pm |  |  | Fair | No | Prem not found … unable to contact customer… unable to find meter ..
Outage | J.E.26.07.15173 | C001854151 | Romeo Brissett | St.James | Completed | Load_244449 | Bogue - 610 | Jul 13, 2026 7:13pm | Jul 13, 2026 7:14pm | Jul 13, 2026 8:09pm | Jul 13, 2026 8:10pm | Jul 13, 2026 8:46pm | Jul 13, 2026 9:20pm | Jul 13, 2026 9:24pm | Jul 13, 2026 9:24pm |  |  | Fair | No | Spliced and retention customer service wire, used 50ft of #6. V/R 113-114-227
Outage | J.E.26.07.15213 | C001854150 | Michael Christian | St.James | Completed | Load_252288 | Queens Drive - 710 | Jul 13, 2026 7:13pm | Jul 14, 2026 8:12am | Jul 14, 2026 11:04am | Jul 14, 2026 1:21pm | Jul 14, 2026 1:58pm | Jul 14, 2026 1:59pm | Jul 14, 2026 1:59pm | Jul 14, 2026 1:59pm |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.15337 | C001854147 | Michael Christian | St.James | Completed | Load_242943 | Rose Hall - 210 | Jul 13, 2026 7:12pm | Jul 14, 2026 8:12am | Jul 14, 2026 11:58am | Jul 14, 2026 11:58am | Jul 14, 2026 12:54pm | Jul 14, 2026 12:59pm | Jul 14, 2026 12:59pm | Jul 14, 2026 12:59pm |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.15258 | C001854145 | Rayon Foster | Hanover | Completed | Load_303135 | Orange Bay - 210 | Jul 13, 2026 7:05pm | Jul 13, 2026 7:05pm | Jul 13, 2026 7:12pm | Jul 13, 2026 7:59pm | Jul 13, 2026 7:59pm | Jul 13, 2026 8:10pm | Jul 13, 2026 8:11pm | Jul 13, 2026 8:11pm | Fire |  | Fair | No | Patrol primary and secondary line to find one blow 10 amps junction fuse and one 15 KVA transformer fuse blow cause by lightning replace with same after patrolling lines and close
Outage | J.E.26.07.15188 | C001854144 | Collin Robinson | Portland | Completed | Load_349214 | Port Antonio - 410 | Jul 13, 2026 7:01pm | Jul 13, 2026 7:02pm | Jul 13, 2026 10:42pm | Jul 13, 2026 10:42pm | Jul 13, 2026 11:01pm | Jul 13, 2026 11:04pm | Jul 13, 2026 11:07pm | Jul 13, 2026 11:07pm | LeaningPole |  | Fair | No | Premises found with supply Meter socket voltage reading 117v 118v 235v
Outage | J.E.26.07.15245 | C001854143 | Collin Robinson | Portland | Completed | Load_270105 | Port Antonio - 410 | Jul 13, 2026 7:01pm | Jul 13, 2026 7:02pm | Jul 13, 2026 9:43pm | Jul 13, 2026 9:43pm | Jul 13, 2026 9:43pm | Jul 13, 2026 10:17pm | Jul 13, 2026 10:17pm | Jul 13, 2026 10:17pm |  |  | Fair | No | Bush one pole of single primary conductor and replace 10 amps junction fuse
Outage | J.E.26.07.15301 | C001854142 | Collin Robinson | Portland | Completed | Load_244763 | Port Antonio - 410 | Jul 13, 2026 7:01pm | Jul 13, 2026 7:02pm | Jul 14, 2026 9:39am | Jul 14, 2026 9:39am | Jul 14, 2026 9:42am | Jul 14, 2026 9:43am | Jul 14, 2026 9:43am | Jul 14, 2026 9:43am |  |  | Rains | No | Information received from customer that supply was restored
Outage | J.E.26.07.15066 | C001854141 | Hartley Chin | Clarendon | Completed | Load_263846 | May Pen - 210 | Jul 13, 2026 7:00pm | Jul 13, 2026 7:10pm | Jul 13, 2026 8:10pm | Jul 13, 2026 8:11pm | Jul 13, 2026 9:17pm | Jul 13, 2026 10:13pm | Jul 13, 2026 10:13pm | Jul 13, 2026 10:13pm | TreeContact | Y | Fair | No | Cut tree from line .. repair service phase …
Outage | J.E.26.07.15305 | C001854135 | Richard Nicholas | St.Catherine | Completed | Load_263382 | Twickenham - 310 | Jul 13, 2026 6:51pm | Jul 13, 2026 6:52pm | Jul 13, 2026 7:20pm | Jul 13, 2026 7:20pm | Jul 13, 2026 7:42pm | Jul 13, 2026 7:49pm | Jul 13, 2026 7:49pm | Jul 13, 2026 7:49pm |  |  | EarthMovement | No | Area found ok
Outage | J.E.26.07.15306 | C001854134 | Richard Nicholas | St.Catherine | Completed | Load_257433 | Twickenham - 310 | Jul 13, 2026 6:50pm | Jul 13, 2026 6:52pm | Jul 13, 2026 8:45pm | Jul 13, 2026 8:45pm | Jul 13, 2026 9:08pm | Jul 13, 2026 9:12pm | Jul 13, 2026 9:16pm | Jul 13, 2026 9:16pm |  |  | Fair | No | Found ok.communicate with customer by telephone however customer said ,supply in the area is ok and she did not make any report to JPS.co
Outage | J.E.26.07.15317 | C001854133 | Nickolas Rodriques | St.Catherine | Completed | Load_556367 | Rhodens Pen - 210 | Jul 13, 2026 6:49pm | Jul 13, 2026 6:52pm | Jul 13, 2026 6:56pm | Jul 13, 2026 7:05pm | Jul 13, 2026 8:33pm | Jul 13, 2026 9:28pm | Jul 13, 2026 9:33pm | Jul 13, 2026 9:33pm | Fire |  | Fair | No | Checked and found a 3 amp transformer fuse blown caused by defective fuse holder. Repaired by replacing the fuse after completing patrol. No fire was seen upon arrival.
Non-Outage | J.E.26.07.12831 | C001854130 | Raymond Carr | St.Mary | Completed | Load_262298 | Oracabessa - 210 | Jul 13, 2026 6:43pm | Jul 13, 2026 6:43pm | Jul 13, 2026 8:08pm | Jul 13, 2026 8:08pm | Jul 13, 2026 9:26pm | Jul 13, 2026 7:16am | Jul 13, 2026 9:28pm | Jul 13, 2026 9:28pm |  |  | Fair | No | Customer couldn’t be contacted.
Outage | J.E.26.07.15197 | C001854129 | Raymond Carr | St.Mary | Completed | Load_256173 | Oracabessa - 210 | Jul 13, 2026 6:42pm | Jul 13, 2026 6:43pm | Jul 13, 2026 9:28pm | Jul 13, 2026 9:28pm | Jul 13, 2026 9:33pm | Jul 13, 2026 9:26pm | Jul 13, 2026 9:35pm | Jul 13, 2026 9:35pm |  |  | Fair | No | Supply was already restored.
Outage | J.E.26.07.15176 | C001854128 | Tyrese Williams | St.Ann | Completed | Load_244653 | Cardiff Hall - 310 | Jul 13, 2026 6:39pm | Jul 13, 2026 6:42pm | Jul 13, 2026 6:58pm | Jul 13, 2026 8:05pm | Jul 13, 2026 8:05pm | Jul 13, 2026 8:08pm | Jul 13, 2026 8:08pm | Jul 13, 2026 8:08pm |  |  | Fair | No | Premises found ok call related to the 50amp junction fuse
Outage | J.E.26.07.15230 | C001854127 | Omar King | St.Ann | Completed | Load_413085 | Ocho Rios - 310 | Jul 13, 2026 6:38pm | Jul 13, 2026 6:38pm | Jul 13, 2026 6:48pm | Jul 13, 2026 6:48pm | Jul 13, 2026 7:10pm | Jul 13, 2026 7:57pm | Jul 13, 2026 7:58pm | Jul 13, 2026 7:58pm |  |  | Fair | No | Found customer meter socket defective I advise customer to a electrician to resolve matter
Outage | J.E.26.07.15259 | C001854126 | Omar King | St.Ann | Completed | Load_245789 | Roaring River - 210 | Jul 13, 2026 6:38pm | Jul 13, 2026 6:38pm | Jul 13, 2026 7:58pm | Jul 13, 2026 7:58pm | Jul 13, 2026 8:42pm | Jul 13, 2026 8:43pm | Jul 13, 2026 8:43pm | Jul 13, 2026 8:43pm |  |  | Fair | No | Unable to find customer customer call several times no answer directions not sufficient
Outage | J.E.26.07.15274 | C001854125 | Raymond Lewis | St.Ann | Completed | Load_257880 | Roaring River - 410 | Jul 13, 2026 6:38pm | Jul 13, 2026 8:03pm | Jul 13, 2026 8:26pm | Jul 13, 2026 8:26pm | Jul 13, 2026 8:26pm | Jul 13, 2026 9:09pm | Jul 13, 2026 9:09pm | Jul 13, 2026 9:09pm |  |  | Fair | No | Remove vegetation from x former bank of tree/50 close
Non-Outage | J.E.26.07.15120 | C001854115 | Damion Reid | null | Completed | null | null | Jul 13, 2026 6:16pm | Jul 13, 2026 6:16pm | Jul 13, 2026 7:39pm | Jul 13, 2026 7:39pm | Jul 13, 2026 8:45pm | Jul 13, 2026 9:38pm | Jul 13, 2026 9:43pm | Jul 13, 2026 9:43pm | BrokenWire |  | SevereWind | No | Blown 8amp junction fuse found cause by broken 35ft TA construction pole isolate broken pole leaving approximately 20 customer out of power pole needs to replace as soon as possible
Outage | J.E.26.07.15082 | C001854113 | Floyd Taylor | Trelawny | Completed | Load_264455 | Greenwood - 110 | Jul 13, 2026 6:11pm | Jul 13, 2026 6:15pm | Jul 13, 2026 6:36pm | Jul 13, 2026 6:37pm | Jul 13, 2026 6:37pm | Jul 13, 2026 6:38pm | Jul 13, 2026 6:39pm | Jul 13, 2026 6:39pm |  |  | Fair | No | Customer service was restored.
Outage | J.E.26.07.15180 | C001854109 | Rayon Foster | Hanover | Completed | Load_303117 | Orange Bay - 210 | Jul 13, 2026 6:05pm | Jul 13, 2026 6:09pm | Jul 13, 2026 8:11pm | Jul 13, 2026 8:11pm | Jul 13, 2026 8:16pm | Jul 13, 2026 8:20pm | Jul 13, 2026 8:21pm | Jul 13, 2026 8:21pm |  |  | Fair | No | Damaged meter refer to field service to have meter change
Outage | J.E.26.07.15218 | C001854108 | Rayon Foster | Hanover | Completed | Load_264990 | Orange Bay - 210 | Jul 13, 2026 6:05pm | Jul 13, 2026 6:09pm | Jul 13, 2026 8:28pm | Jul 13, 2026 8:28pm | Jul 13, 2026 8:28pm | Jul 13, 2026 10:05pm | Jul 13, 2026 10:05pm | Jul 13, 2026 10:05pm |  |  | Fair | No | Car crash into concrete pole causing fuse to dislocate from switch Reclose after patrolling line
Outage | J.E.26.07.15177 | C001854094 | Collin Robinson | Portland | Completed | Load_263127 | Port Antonio - 310 | Jul 13, 2026 5:34pm | Jul 13, 2026 5:35pm | Jul 13, 2026 7:22pm | Jul 13, 2026 7:22pm | Jul 13, 2026 7:44pm | Jul 13, 2026 8:13pm | Jul 13, 2026 8:15pm | Jul 13, 2026 8:15pm | BrokenWire |  | Flood | No | Change 60 ft of #6 twisted wire six one bolt clamp Voltage reading 118v 118v 236v
Outage | J.E.26.07.15065 | C001854092 | Tyrese Williams | St.Ann | Completed | Load_255835 | Cardiff Hall - 310 | Jul 13, 2026 5:32pm | Jul 13, 2026 8:28pm | Jul 13, 2026 8:46pm | Jul 13, 2026 8:47pm | Jul 13, 2026 9:34pm | Jul 13, 2026 9:35pm | Jul 13, 2026 9:36pm | Jul 13, 2026 9:36pm | BrokenWire |  | Fair | No | Service wire needed
Outage | J.E.26.07.15176 | C001854091 | Tyrese Williams | St.Ann | Completed | Load_244653 | Cardiff Hall - 310 | Jul 13, 2026 5:32pm | Jul 13, 2026 6:39pm | Jul 13, 2026 6:58pm | Jul 13, 2026 6:58pm | Jul 13, 2026 8:02pm | Jul 13, 2026 8:04pm | Jul 13, 2026 8:04pm | Jul 13, 2026 8:04pm |  |  | Fair | No | Replace a 50amp junction fuse at pole
Outage | J.E.26.07.15171 | C001854086 | Omar King | St.Ann | Completed | Load_248125 | Ocho Rios - 310 | Jul 13, 2026 5:17pm | Jul 13, 2026 5:18pm | Jul 13, 2026 6:38pm | Jul 13, 2026 6:38pm | Jul 13, 2026 6:46pm | Jul 13, 2026 6:47pm | Jul 13, 2026 6:48pm | Jul 13, 2026 6:48pm |  |  | Fair | No | Unable to find customer call several times no answer directions not sufficient
Outage | J.E.26.07.15156 | C001854083 | Stephen Taylor | St.Thomas | Completed | Load_261596 | Good Year - 210 | Jul 13, 2026 5:04pm | Jul 13, 2026 5:13pm | Jul 13, 2026 8:52pm | Jul 13, 2026 8:52pm | Jul 13, 2026 8:52pm | Jul 13, 2026 8:52pm | Jul 13, 2026 8:54pm | Jul 13, 2026 8:54pm | BrokenWire |  | Fair | No | When in the area and light is in the area but several calls to single customer and no one answering the phone need more information to locate customer
Non-Outage | J.E.26.07.14764 | C001854074 | Richman Whyte | null | Completed | null | null | Jul 13, 2026 4:54pm | Jul 13, 2026 5:43pm | Jul 13, 2026 5:58pm | Jul 13, 2026 5:58pm | Jul 13, 2026 6:49pm | Jul 13, 2026 7:23pm | Jul 13, 2026 7:24pm | Jul 13, 2026 7:24pm |  |  | Fair | No | Check and found okay voltage 115 116 230
Non-Outage | J.E.26.07.15140 | C001854067 | Wan Carlos Scarlett | null | Completed | null | null | Jul 13, 2026 4:43pm | Jul 13, 2026 4:44pm | Jul 13, 2026 7:01pm | Jul 14, 2026 5:42pm | Jul 14, 2026 6:09pm | Jul 14, 2026 6:58pm | Jul 14, 2026 6:59pm | Jul 14, 2026 6:59pm |  |  | Fair | No | Found tree growing in to secondary line need bushing team assistance
Outage | J.E.26.07.15010 | C001854055 | Richard Nicholas | St.Catherine | Completed | Load_238529 | Twickenham - 310 | Jul 13, 2026 4:37pm | Jul 13, 2026 4:39pm | Jul 13, 2026 6:37pm | Jul 13, 2026 6:37pm | Jul 13, 2026 7:01pm | Jul 13, 2026 7:19pm | Jul 13, 2026 7:20pm | Jul 13, 2026 7:20pm |  |  | Fair | No
Non-Outage | J.E.26.07.09807 | C001854054 | Richard Grant | null | Completed | null | null | Jul 13, 2026 4:35pm | Jul 13, 2026 4:37pm | Jul 13, 2026 7:15pm | Jul 13, 2026 7:15pm | Jul 13, 2026 8:51pm | Jul 13, 2026 8:52pm | Jul 13, 2026 8:52pm | Jul 13, 2026 8:52pm |  |  | Fair | No | Pretty found okay
Outage | J.E.26.07.15059 | C001854053 | Barrington Brown | St.James | Completed | Load_260850 | Rose Hall - 210 | Jul 13, 2026 4:33pm | Jul 13, 2026 4:34pm | Jul 13, 2026 5:19pm | Jul 13, 2026 5:19pm | Jul 13, 2026 8:14pm | Jul 13, 2026 10:41pm | Jul 13, 2026 10:41pm | Jul 13, 2026 10:41pm | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Crew found customer service wires tore down by pass excavator truck. Crew opened 50kva transformer and conducted repairs using 200ft of #2 triplex, 15 one bolt clamps 4 ampacts, #2 splicing sleeve, 4 #2 preform. Crew also remade burnt jumpers at pole. Customer supply now restored
Non-Outage | J.E.26.07.14588 | C001854047 | Rayon Foster | Hanover | Completed | Load_261941 | Orange Bay - 210 | Jul 13, 2026 4:32pm | Jul 13, 2026 4:33pm | Jul 13, 2026 6:47pm | Jul 13, 2026 6:47pm | Jul 13, 2026 6:47pm | Jul 13, 2026 6:53pm | Jul 13, 2026 6:53pm | Jul 13, 2026 6:53pm |  |  | Fair | No | Electrician completed work and no longer need power to be disconnected
Non-Outage | J.E.26.07.14903 | C001854049 | Richard Nicholas | null | Completed | null | null | Jul 13, 2026 4:32pm | Jul 13, 2026 4:35pm | Jul 13, 2026 7:49pm | Jul 13, 2026 7:49pm | Jul 13, 2026 8:36pm | Jul 13, 2026 8:43pm | Jul 13, 2026 8:45pm | Jul 13, 2026 8:45pm | BrokenWire |  | Fair | No | Premises found locked,however Rammy system installed in the area.please refer to the rammy department.
Non-Outage | J.E.26.07.08569 | C001854045 | Evan Spaulding | null | Completed | null | null | Jul 13, 2026 4:29pm | Jul 13, 2026 4:29pm | Jul 13, 2026 10:08pm | Jul 13, 2026 10:08pm | Jul 13, 2026 10:08pm | Jul 13, 2026 10:08pm | Jul 13, 2026 10:08pm | Jul 13, 2026 10:08pm | BangingWires |  | Fair | No | Premises not found.
Non-Outage | J.E.26.07.15120 | C001854046 | Marlon Brown | null | Completed | null | null | Jul 13, 2026 4:29pm | Jul 13, 2026 4:34pm | Jul 13, 2026 4:39pm | Jul 13, 2026 4:39pm | Jul 13, 2026 4:39pm | Jul 13, 2026 4:40pm | Jul 13, 2026 4:40pm | Jul 13, 2026 4:40pm | BrokenWire |  | Fair | No | Manchester call
Non-Outage | J.E.26.07.15057 | C001854044 | Richard Nicholas | null | Completed | null | null | Jul 13, 2026 4:28pm | Jul 13, 2026 4:28pm | Jul 13, 2026 9:16pm | Jul 13, 2026 9:16pm | Jul 13, 2026 9:39pm | Jul 13, 2026 10:23pm | Jul 13, 2026 10:25pm | Jul 13, 2026 10:25pm | Fire | Y | Fair | No | Spot bushing done.retention and balance 1 span of banging secondary neutral at mid span.2 clamp was used.
Outage | J.E.26.07.10463 | C001854036 | Richard Grant | St.Catherine | Completed | Load_568270 | New Michelton - 410 | Jul 13, 2026 4:27pm | Jul 13, 2026 4:28pm | Jul 13, 2026 10:00pm | Jul 13, 2026 10:00pm | Jul 13, 2026 10:35pm | Jul 13, 2026 10:36pm | Jul 13, 2026 10:36pm | Jul 13, 2026 10:36pm |  |  | Fair | No | Daylight attention, area unsafe
Outage | J.E.26.07.14665 | C001854032 | Richard Grant | St.Catherine | Completed | Load_257724 | New Michelton - 210 | Jul 13, 2026 4:27pm | Jul 13, 2026 4:28pm | Jul 13, 2026 8:53pm | Jul 13, 2026 8:53pm | Jul 13, 2026 9:59pm | Jul 13, 2026 9:59pm | Jul 13, 2026 10:00pm | Jul 13, 2026 10:00pm | BrokenPole |  | Fair | No | Rotten pole needs to be removed and spot bushing done please refer to maintenance department
Outage | J.E.26.07.14735 | C001854033 | Richard Grant | St.Catherine | Completed | Load_244952 | New Michelton - 210 | Jul 13, 2026 4:27pm | Jul 13, 2026 4:28pm | Jul 13, 2026 5:59pm | Jul 13, 2026 5:59pm | Jul 13, 2026 7:05pm | Jul 13, 2026 7:15pm | Jul 13, 2026 7:15pm | Jul 13, 2026 7:15pm |  |  | Fair | No | Premises found okay.
Outage | J.E.26.07.14900 | C001854034 | Richard Grant | St.Catherine | Completed | Load_264133 | New Michelton - 210 | Jul 13, 2026 4:27pm | Jul 13, 2026 4:28pm | Jul 13, 2026 5:09pm | Jul 13, 2026 5:09pm | Jul 13, 2026 5:49pm | Jul 13, 2026 5:58pm | Jul 13, 2026 5:58pm | Jul 13, 2026 5:58pm | BrokenWire |  | Fair | No | No broken wire seen, premises found closed.
Outage | J.E.26.07.15081 | C001854035 | Milton Charlton | KSAN | Completed | Load_264577 | Constant Spring - 210 | Jul 13, 2026 4:27pm | Jul 13, 2026 4:29pm | Jul 13, 2026 6:12pm | Jul 13, 2026 6:12pm | Jul 13, 2026 6:34pm | Jul 13, 2026 6:45pm | Jul 13, 2026 6:39pm | Jul 13, 2026 6:39pm |  |  | Fair | No | Found one 2 amps transformer fuse blown at pole #( no pole #). Refused using one 2 amps fuse and reclosed transformer switch.
Outage | J.E.26.07.15055 | C001854031 | Milton Charlton | KSAN | Completed | Load_574799 | Washington Blvd - 610 | Jul 13, 2026 4:26pm | Jul 13, 2026 4:29pm | Jul 13, 2026 5:05pm | Jul 13, 2026 5:05pm | Jul 13, 2026 6:11pm | Jul 13, 2026 6:05pm | Jul 13, 2026 6:12pm | Jul 13, 2026 6:12pm |  |  | Fair | No | Reconnect customer by J.P.S. Escalation.
Outage | J.E.26.07.09356 | C001854019 | Gregory Grossett | Portland | Completed | Load_349214 | Port Antonio - 410 | Jul 13, 2026 4:14pm | Jul 13, 2026 4:14pm | Jul 13, 2026 4:18pm | Jul 13, 2026 4:18pm | Jul 13, 2026 4:25pm | Jul 13, 2026 5:52pm | Jul 13, 2026 5:53pm | Jul 13, 2026 5:53pm |  | Y | Fair | No | Open secondary conductors burst down across river splice and retention several pole span of conductors then close transformer fuse to restore supply to the area.Material use 100ft aa conductor 4 one bolt clamps 2 number 2 preform.
Outage | J.E.26.07.14892 | C001854007 | Marlon Authors | Manchester | Completed | Load_302767 | Spur Tree - 210 | Jul 13, 2026 4:02pm | Jul 13, 2026 4:03pm | Jul 13, 2026 6:25pm | Jul 13, 2026 6:25pm | Jul 13, 2026 6:25pm | Jul 13, 2026 6:26pm | Jul 13, 2026 6:26pm | Jul 13, 2026 6:26pm |  |  | Fair | No | Manchester call
Outage | J.E.26.07.14985 | C001854008 | Marlon Authors | Manchester | Completed | Load_573423 | Spur Tree - 210 | Jul 13, 2026 4:02pm | Jul 13, 2026 4:03pm | Jul 13, 2026 5:20pm | Jul 13, 2026 5:20pm | Jul 13, 2026 5:31pm | Jul 13, 2026 5:39pm | Jul 13, 2026 5:39pm | Jul 13, 2026 5:39pm |  |  | Fair | No | Patrol and found clear. Replace one blown 20 amp junction fuse no pole #. Restored supply ok
Outage | J.E.26.07.14998 | C001854009 | Marlon Authors | Manchester | Completed | Load_268371 | Spur Tree - 210 | Jul 13, 2026 4:02pm | Jul 13, 2026 4:04pm | Jul 13, 2026 6:26pm | Jul 13, 2026 6:26pm | Jul 13, 2026 6:40pm | Jul 13, 2026 6:56pm | Jul 13, 2026 6:56pm | Jul 13, 2026 6:56pm |  |  | Fair | No | Meter appears to be burnt, unable to check same as meter is barrel locked. Customer is still with supply. Please refer same to the field services department for further assistance
Outage | J.E.26.07.15043 | C001854010 | Marlon Authors | Manchester | Completed | Load_246292 | Spur Tree - 210 | Jul 13, 2026 4:02pm | Jul 13, 2026 4:04pm | Jul 13, 2026 6:22pm | Jul 13, 2026 6:22pm | Jul 13, 2026 6:22pm | Jul 13, 2026 6:25pm | Jul 13, 2026 6:24pm | Jul 13, 2026 6:24pm |  |  | Fair | No | Manchester call
Outage | J.E.26.07.14885 | C001854006 | Marlon Authors | Manchester | Completed | Load_1002209 | Spur Tree - 210 | Jul 13, 2026 4:01pm | Jul 13, 2026 4:03pm | Jul 13, 2026 5:42pm | Jul 13, 2026 5:42pm | Jul 13, 2026 5:42pm | Jul 13, 2026 5:44pm | Jul 13, 2026 5:44pm | Jul 13, 2026 5:44pm |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.07.14814 | C001854001 | Fitzroy Turner | KSAS | Completed | Load_261035 | Duhaney - 410 | Jul 13, 2026 3:55pm | Jul 13, 2026 3:55pm | Jul 14, 2026 4:02pm | Jul 14, 2026 4:02pm | Jul 14, 2026 4:36pm | Jul 14, 2026 4:40pm | Jul 14, 2026 4:41pm | Jul 14, 2026 4:41pm |  |  | Fair | No | Found tree wire service phase burnt mid span use one clamp to carry out repair supply restored to customer
Outage | J.E.26.07.14609 | C001854000 | Kemark Slue | St.Catherine | Completed | Load_270057 | Tredegar - 210 | Jul 13, 2026 3:53pm | Jul 14, 2026 9:39am | Jul 14, 2026 10:30am | Jul 14, 2026 10:55am | Jul 14, 2026 11:21am | Jul 14, 2026 11:47am | Jul 14, 2026 12:13pm | Jul 14, 2026 12:13pm | LeaningPole |  | Fair | No | Upon arrival at the location the crew discovered that a 30 ft cl 6 sec. TDE construction pole is 95% rotten at pole # 0063579, pole consisting of three, 3-wire service, two 2-wire service, streetlight and telecommunications cable, please refer to A. Murray to have pole changed asap.
Outage | J.E.26.07.14485 | C001853993 | Richard Nicholas | St.Catherine | Completed | Load_248181 | Tredegar - 410 | Jul 13, 2026 3:48pm | Jul 13, 2026 3:49pm | Jul 13, 2026 10:25pm | Jul 13, 2026 10:25pm | Jul 13, 2026 10:39pm | Jul 14, 2026 1:37am | Jul 14, 2026 1:38am | Jul 14, 2026 1:38am |  |  | Fair | No | Found ok
Outage | J.E.26.07.14708 | C001853992 | Richard Nicholas | St.Catherine | Completed | Load_257313 | Tredegar - 510 | Jul 13, 2026 3:48pm | Jul 13, 2026 3:49pm | Jul 13, 2026 4:27pm | Jul 13, 2026 4:27pm | Jul 13, 2026 5:04pm | Jul 13, 2026 5:20pm | Jul 13, 2026 5:20pm | Jul 13, 2026 5:20pm |  |  | Fair | No | Found ok
Outage | J.E.26.07.14992 | C001853988 | Richard Nicholas | St.Catherine | Completed | Load_238583 | Twickenham - 310 | Jul 13, 2026 3:47pm | Jul 13, 2026 3:49pm | Jul 13, 2026 5:22pm | Jul 13, 2026 5:22pm | Jul 13, 2026 5:52pm | Jul 13, 2026 6:33pm | Jul 13, 2026 6:36pm | Jul 13, 2026 6:36pm | BrokenWire |  | Fair | No | Replaced blown 25amp junctions fuse on pole #045009
Outage | J.E.26.07.14889 | C001853980 | Ryan Richards | Manchester | Completed | Load_302243 | Spur Tree - 310 | Jul 13, 2026 3:46pm | Jul 13, 2026 3:47pm | Jul 13, 2026 6:42pm | Jul 13, 2026 6:42pm | Jul 13, 2026 8:29pm | Jul 13, 2026 8:35pm | Jul 13, 2026 8:36pm | Jul 13, 2026 8:36pm | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | 1 span of broken secondary neutral found cause by almond and cedar tree op 25kva transformer carry out one span of spot bushing cutting tree’s splice and retention using 60ft#2 aluminum 1#2 preform 2 one bolt clamps and reclose transformer all customers are now with supply
Outage | J.E.26.07.14964 | C001853985 | Damion Reid | Manchester | Completed | Load_244820 | Porus - 210 | Jul 13, 2026 3:46pm | Jul 13, 2026 3:47pm | Jul 13, 2026 4:16pm | Jul 13, 2026 4:16pm | Jul 13, 2026 5:41pm | Jul 13, 2026 7:36pm | Jul 13, 2026 7:39pm | Jul 13, 2026 7:39pm | BrokenWire |  | Rains | No | Two span of broken secondary phase conductor found cause by illegal connection open 25kva transformer fuse link splice an retention conductor using 30ft of 2/0 aluminum conductor two 2/0 preform three one bolt clamp and restore power
Outage | J.E.26.07.15061 | C001853981 | Richard Samuda | Manchester | Completed | Load_248630 | Spur Tree - 310 | Jul 13, 2026 3:46pm | Jul 14, 2026 7:19am | Jul 14, 2026 10:12am | Jul 14, 2026 10:12am | Jul 14, 2026 11:37am | Jul 14, 2026 11:37am | Jul 14, 2026 12:37pm | Jul 14, 2026 12:37pm | BrokenWire |  | Fair | No | Splice and reconnected lower phase of secondary line that was broken using 40 ft of #2 aluminum wire and one #2 preform and two 1bolt clamps
Outage | J.E.26.07.15067 | C001853983 | Dean Smith | Hanover | Completed | Load_262588 | Orange Bay - 210 | Jul 13, 2026 3:46pm | Jul 14, 2026 8:37am | Jul 14, 2026 8:49am | Jul 14, 2026 8:49am | Jul 14, 2026 10:03am | Jul 14, 2026 10:03am | Jul 14, 2026 10:41am | Jul 14, 2026 10:41am |  |  | Fair | No | Defective D/O Switch at raiser pole, replace same. Opened and closed main aD/O Switches for isolation/ re-energize at pole number (624090)
Outage | J.E.26.07.15069 | C001853982 | Ryan Richards | Manchester | Completed | Load_302234 | Spur Tree - 310 | Jul 13, 2026 3:46pm | Jul 13, 2026 3:47pm | Jul 13, 2026 4:03pm | Jul 13, 2026 4:03pm | Jul 13, 2026 5:21pm | Jul 13, 2026 6:38pm | Jul 13, 2026 6:38pm | Jul 13, 2026 6:38pm |  |  | Rains | No | Blown 20 amp junction fuse found line patrol pear tree limb found an the primary chop tree limb and replaced blown 20 amp junction fuse all customers are now with supply
Outage | J.E.26.07.15074 | C001853984 | Ryan Richards | Manchester | Completed | Load_268712 | Spur Tree - 310 | Jul 13, 2026 3:46pm | Jul 13, 2026 3:47pm | Jul 13, 2026 8:29pm | Jul 13, 2026 8:36pm | Jul 13, 2026 9:42pm | Jul 13, 2026 11:38pm | Jul 13, 2026 11:38pm | Jul 13, 2026 11:38pm |  |  | Fair | No | Blown 40 &30 amp junction fuse found line patrol nothing found blown fuse was replaced all customers are now with supply lighting suspected to be the cause
Outage | J.E.26.07.14849 | C001853973 | Floyd Taylor | Trelawny | Completed | Load_242087 | Greenwood - 110 | Jul 13, 2026 3:40pm | Jul 13, 2026 3:47pm | Jul 13, 2026 6:01pm | Jul 13, 2026 6:01pm | Jul 13, 2026 6:32pm | Jul 13, 2026 6:36pm | Jul 13, 2026 6:36pm | Jul 13, 2026 6:36pm |  |  | Fair | No | Found ok
Outage | J.E.26.07.15035 | C001853960 | Romeo Brissett | St.James | Completed | Load_557427 | Bogue - 610 | Jul 13, 2026 3:34pm | Jul 13, 2026 3:47pm | Jul 13, 2026 5:01pm | Jul 13, 2026 5:01pm | Jul 13, 2026 6:18pm | Jul 13, 2026 6:30pm | Jul 13, 2026 6:33pm | Jul 13, 2026 6:33pm |  |  | Fair | No | Cut and removed vegetation and replaced (1)8amps junction fuse.
Outage | J.E.26.07.15002 | C001853946 | Richard Watson | St.Elizabeth | Completed | Load_264361 | Maggotty - 110 | Jul 13, 2026 3:32pm | Jul 13, 2026 3:32pm | Jul 13, 2026 5:34pm | Jul 13, 2026 6:11pm | Jul 13, 2026 6:11pm | Jul 13, 2026 5:59pm | Jul 13, 2026 6:12pm | Jul 13, 2026 6:12pm |  |  | Rains | No | Found tripsaver saver road phase operated at LAB 6-747, tripsaver closed after patrol line to next switching point at RAHEEN, no visible fault found reports of heavy rain, lightning and severe winds in the area, supply restored to affected customers.
Outage | J.E.26.07.15003 | C001853947 | Richard Watson | St.Elizabeth | Completed | Load_557648 | Maggotty - 110 | Jul 13, 2026 3:32pm | Jul 13, 2026 3:32pm | Jul 13, 2026 4:11pm | Jul 13, 2026 6:12pm | Jul 13, 2026 6:12pm | Jul 13, 2026 5:59pm | Jul 13, 2026 6:13pm | Jul 13, 2026 6:13pm |  |  | Rains | No | Found tripsaver saver road phase operated at LAB 6-747, tripsaver closed after patrol line to next switching point at RAHEEN, no visible fault found reports of heavy rain, lightning and severe winds in the area, supply restored to affected customers.
Outage | J.E.26.07.15025 | C001853948 | Richard Watson | St.Elizabeth | Completed | Load_242044 | Maggotty - 110 | Jul 13, 2026 3:32pm | Jul 13, 2026 3:32pm | Jul 13, 2026 4:15pm | Jul 13, 2026 4:25pm | Jul 13, 2026 5:58pm | Jul 13, 2026 5:59pm | Jul 13, 2026 6:07pm | Jul 13, 2026 6:07pm |  |  | Rains | No | Found tripsaver saver road phase operated at LAB 6-747, tripsaver closed after patrol line to next switching point at RAHEEN, no visible fault found reports of heavy rain, lightning and severe winds in the area, supply restored to affected customers.
Outage | J.E.26.07.14752 | C001853941 | Rayon Foster | Hanover | Completed | Load_241281 | Orange Bay - 310 | Jul 13, 2026 3:31pm | Jul 13, 2026 3:31pm | Jul 13, 2026 3:59pm | Jul 13, 2026 4:56pm | Jul 13, 2026 5:45pm | Jul 13, 2026 6:13pm | Jul 13, 2026 6:13pm | Jul 13, 2026 6:13pm |  |  | Fair | No | Blow 25 kva transformer cause by lightning remove fuse link patrol secondary line line was clear replace with 2amps fuse voltage after closing 118/117AB235
Outage | J.E.26.07.14936 | C001853944 | Richard Watson | St.Elizabeth | Completed | Load_255947 | Maggotty - 110 | Jul 13, 2026 3:31pm | Jul 13, 2026 3:32pm | Jul 13, 2026 5:34pm | Jul 13, 2026 6:08pm | Jul 13, 2026 6:08pm | Jul 13, 2026 5:59pm | Jul 13, 2026 6:09pm | Jul 13, 2026 6:09pm |  |  | LandSlide | No | Found tripsaver saver road phase operated at LAB 6-747, tripsaver closed after patrol line to next switching point at RAHEEN, no visible fault found reports of heavy rain, lightning and severe winds in the area, supply restored to affected customers.
Outage | J.E.26.07.14955 | C001853943 | Marlon Authors | Manchester | Completed | Load_240436 | Spur Tree - 210 | Jul 13, 2026 3:31pm | Jul 13, 2026 3:32pm | Jul 13, 2026 5:50pm | Jul 13, 2026 5:50pm | Jul 13, 2026 6:10pm | Jul 13, 2026 6:22pm | Jul 13, 2026 6:22pm | Jul 13, 2026 6:22pm | Fire |  | Fair | No | Patrol and found clear. Replace one blown 10 amp junction fuse no pole #. Restored supply ok
Outage | J.E.26.07.14986 | C001853942 | Richard Watson | St.Elizabeth | Completed | Load_247338 | Maggotty - 110 | Jul 13, 2026 3:31pm | Jul 13, 2026 3:33pm | Jul 13, 2026 6:21pm | Jul 13, 2026 7:25pm | Jul 13, 2026 7:26pm | Jul 13, 2026 7:26pm | Jul 13, 2026 7:35pm | Jul 13, 2026 7:35pm | Fire |  | Fair | No | Customer contacted by phone and stated that a cable wire caught fire and burned down and electricity is in the area and normal, customer advised to call back if problem happens again.
Outage | J.E.26.07.15000 | C001853945 | Richard Watson | St.Elizabeth | Completed | Load_252313 | Maggotty - 110 | Jul 13, 2026 3:31pm | Jul 13, 2026 3:32pm | Jul 13, 2026 5:34pm | Jul 13, 2026 6:09pm | Jul 13, 2026 6:09pm | Jul 13, 2026 5:59pm | Jul 13, 2026 6:11pm | Jul 13, 2026 6:11pm |  |  | Rains | No | Found tripsaver saver road phase operated at LAB 6-747, tripsaver closed after patrol line to next switching point at RAHEEN, no visible fault found reports of heavy rain, lightning and severe winds in the area, supply restored to affected customers.
Outage | J.E.26.07.13151 | C001853936 | Evan Spaulding | St.Mary | Completed | Load_257699 | Highgate -110 | Jul 13, 2026 3:30pm | Jul 13, 2026 3:30pm | Jul 13, 2026 10:09pm | Jul 13, 2026 10:09pm | Jul 13, 2026 10:47pm | Jul 13, 2026 10:47pm | Jul 13, 2026 10:47pm | Jul 13, 2026 10:47pm | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Customer says issue was resolved.
Outage | J.E.26.07.14625 | C001853937 | Evan Spaulding | St.Mary | Completed | Load_267351 | Annotto Bay - 210 | Jul 13, 2026 3:30pm | Jul 13, 2026 3:30pm | Jul 13, 2026 3:54pm | Jul 13, 2026 3:54pm | Jul 13, 2026 5:04pm | Jul 13, 2026 5:24pm | Jul 13, 2026 5:25pm | Jul 13, 2026 5:25pm |  |  | Fair | No | Replace 2-5 amps Transformer fuse at pole number 0005256.
Outage | J.E.26.07.14670 | C001853938 | Evan Spaulding | St.Mary | Completed | Load_260358 | Annotto Bay - 210 | Jul 13, 2026 3:30pm | Jul 13, 2026 3:30pm | Jul 13, 2026 5:26pm | Jul 13, 2026 5:26pm | Jul 13, 2026 5:42pm | Jul 13, 2026 5:45pm | Jul 13, 2026 6:05pm | Jul 13, 2026 6:05pm | LeakingTransformer |  | Fair | No | 25kva Transformer leaking oil ,pole rotten and leaning as well,refer to maintenance.
Outage | J.E.26.07.14997 | C001853934 | Rayon Foster | Hanover | Completed | Load_260650 | Orange Bay - 210 | Jul 13, 2026 3:28pm | Jul 13, 2026 3:29pm | Jul 13, 2026 3:59pm | Jul 13, 2026 10:56pm | Jul 13, 2026 10:56pm | Jul 13, 2026 11:10pm | Jul 13, 2026 11:12pm | Jul 13, 2026 11:12pm |  |  | Fair | No | Found working ok power was restored early today by a technician team
Outage | J.E.26.07.04911 | C001853933 | Raymond Lewis | Clarendon | Completed | Load_242425 | May Pen - 110 | Jul 13, 2026 3:27pm | Jul 13, 2026 3:28pm | Jul 13, 2026 4:10pm | Jul 13, 2026 4:11pm | Jul 13, 2026 4:16pm | Jul 13, 2026 5:18pm | Jul 13, 2026 4:19pm | Jul 13, 2026 4:19pm |  |  | Fair | No | No direction plus phone number out of service
Outage | J.E.26.07.15042 | C001853924 | Neville Spencer | Clarendon | Completed | Load_245557 | May Pen - 110 | Jul 13, 2026 3:27pm | Jul 13, 2026 3:27pm | Jul 13, 2026 5:09pm | Jul 13, 2026 5:09pm | Jul 13, 2026 6:24pm | Jul 13, 2026 6:24pm | Jul 13, 2026 6:25pm | Jul 13, 2026 6:25pm |  |  | Fair | No | Found ok.
Non-Outage | J.E.26.07.14693 | C001853923 | Raymond Carr | null | Completed | null | null | Jul 13, 2026 3:26pm | Jul 13, 2026 3:27pm | Jul 13, 2026 6:02pm | Jul 13, 2026 6:03pm | Jul 13, 2026 6:53pm | Jul 13, 2026 6:38pm | Jul 13, 2026 6:58pm | Jul 13, 2026 6:58pm |  |  | Fair | No | Several calls to contact number went unanswered.
Outage | J.E.26.07.14451 | C001853922 | Raymond Carr | St.Mary | Completed | Load_243605 | Oracabessa - 110 | Jul 13, 2026 3:26pm | Jul 13, 2026 3:27pm | Jul 13, 2026 6:59pm | Jul 13, 2026 6:59pm | Jul 13, 2026 8:06pm | Jul 13, 2026 8:00pm | Jul 13, 2026 8:07pm | Jul 13, 2026 8:07pm |  |  | Fair | No | Several calls to contact number went straight to voicemail.
Outage | J.E.26.07.14737 | C001853921 | Raymond Carr | St.Mary | Completed | Load_256173 | Oracabessa - 210 | Jul 13, 2026 3:26pm | Jul 13, 2026 3:27pm | Jul 13, 2026 4:53pm | Jul 13, 2026 4:53pm | Jul 13, 2026 5:05pm | Jul 13, 2026 6:28pm | Jul 13, 2026 6:02pm | Jul 13, 2026 6:02pm | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Transformer drop lead was reconnected, also one span of lagging secondary conductor was tensioned. Normal supply was restored.
Outage | J.E.26.07.14429 | C001853920 | Jermaine Williams | Clarendon | Completed | Load_292535 | Parnassus - 310 | Jul 13, 2026 3:24pm | Jul 14, 2026 7:41am | Jul 14, 2026 10:55am | Jul 14, 2026 10:56am | Jul 14, 2026 12:27pm | Jul 14, 2026 12:40pm | Jul 14, 2026 12:47pm | Jul 14, 2026 12:47pm |  |  | SevereWind | No | Remade joints at secondary using two clamps.
Outage | J.E.26.07.14651 | C001853914 | Fitzroy Turner | KSAN | Completed | Load_266737 | Washington Blvd - 310 | Jul 13, 2026 3:23pm | Jul 13, 2026 3:23pm | Jul 13, 2026 6:52pm | Jul 13, 2026 6:52pm | Jul 13, 2026 7:36pm | Jul 13, 2026 7:36pm | Jul 13, 2026 7:37pm | Jul 13, 2026 7:37pm |  |  | Fair | No | Customer premises close at this time
Outage | J.E.26.07.14730 | C001853915 | Fitzroy Turner | KSAN | Completed | Load_293820 | Washington Blvd - 710 | Jul 13, 2026 3:23pm | Jul 13, 2026 3:23pm | Jul 13, 2026 7:38pm | Jul 13, 2026 7:38pm | Jul 13, 2026 7:56pm | Jul 13, 2026 8:32pm | Jul 13, 2026 8:33pm | Jul 13, 2026 8:33pm |  |  | Fair | No | Customer meter is not communicating.please send email to field service department to have issues resolved
Outage | J.E.26.07.14769 | C001853913 | Fitzroy Turner | KSAN | Completed | Load_268902 | Greenwich - 710 | Jul 13, 2026 3:23pm | Jul 13, 2026 3:23pm | Jul 13, 2026 6:23pm | Jul 13, 2026 6:23pm | Jul 13, 2026 6:49pm | Jul 13, 2026 6:50pm | Jul 13, 2026 6:50pm | Jul 13, 2026 6:50pm |  |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.07.14991 | C001853916 | Hartley Chin | Clarendon | Completed | Load_254405 | Parnassus - 210 | Jul 13, 2026 3:23pm | Jul 13, 2026 3:24pm | Jul 13, 2026 3:31pm | Jul 13, 2026 3:31pm | Jul 13, 2026 4:19pm | Jul 13, 2026 5:50pm | Jul 13, 2026 5:50pm | Jul 13, 2026 5:50pm |  |  | SevereWind | No | Found open 15 amp trip saver @ pole # 0208607 due to tree contact , cut tree from line , close trip saver …
Outage | J.E.26.07.15027 | C001853917 | Hartley Chin | Clarendon | Completed | Load_246945 | Parnassus - 210 | Jul 13, 2026 3:23pm | Jul 13, 2026 3:24pm | Jul 13, 2026 3:51pm | Jul 13, 2026 6:42pm | Jul 13, 2026 6:42pm | Jul 13, 2026 6:42pm | Jul 13, 2026 6:43pm | Jul 13, 2026 6:43pm |  |  | Fair | No | Call related to job # 14796 ..
Outage | J.E.26.07.15036 | C001853919 | Hartley Chin | Clarendon | Completed | Load_260256 | Parnassus - 210 | Jul 13, 2026 3:23pm | Jul 13, 2026 3:24pm | Jul 13, 2026 6:43pm | Jul 13, 2026 6:43pm | Jul 13, 2026 7:12pm | Jul 13, 2026 7:33pm | Jul 13, 2026 7:36pm | Jul 13, 2026 7:36pm |  |  | Fair | No | Found blown 8 amp junction fuse @ pole # 041801 line patrolled and found okay , junction refused…
Outage | J.E.26.07.14830 | C001853902 | Floyd Taylor | Trelawny | Completed | Load_261119 | Greenwood - 110 | Jul 13, 2026 3:22pm | Jul 13, 2026 3:24pm | Jul 13, 2026 3:33pm | Jul 13, 2026 3:37pm | Jul 13, 2026 5:17pm | Jul 13, 2026 5:56pm | Jul 13, 2026 6:00pm | Jul 13, 2026 6:00pm |  |  | Fair | No | Replace 1- 15amp junction fuse after line was patrol and nothing found, voltage readings left 114,117,232.
Outage | J.E.26.07.14567 | C001853899 | Wan Carlos Scarlett | St.Catherine | Completed | Load_270251 | Twickenham - 210 | Jul 13, 2026 3:20pm | Jul 13, 2026 3:21pm | Jul 13, 2026 7:03pm | Jul 13, 2026 9:45pm | Jul 13, 2026 10:14pm | Jul 14, 2026 3:00pm | Jul 14, 2026 3:00pm | Jul 14, 2026 3:00pm |  |  | Fair | No | Customer was reconnected from escalation department power supply has been restored
Outage | J.E.26.07.14688 | C001853900 | Tajay Bernard | Hanover | Completed | Load_302811 | Orange Bay - 310 | Jul 13, 2026 3:20pm | Jul 13, 2026 3:20pm | Jul 13, 2026 3:43pm | Jul 13, 2026 3:43pm | Jul 13, 2026 4:14pm | Jul 13, 2026 4:36pm | Jul 13, 2026 4:37pm | Jul 13, 2026 4:37pm |  |  | Fair | No | Area check and found okay customer stated that power was restored
Outage | J.E.26.07.14367 | C001853895 | Raymond Lewis | St.Ann | Completed | Load_254204 | Roaring River - 410 | Jul 13, 2026 3:19pm | Jul 13, 2026 4:15pm | Jul 13, 2026 5:11pm | Jul 13, 2026 5:11pm | Jul 13, 2026 5:22pm | Jul 13, 2026 5:25pm | Jul 13, 2026 5:26pm | Jul 13, 2026 5:26pm |  |  | Fair | No | Customer need local number to complete job
Outage | J.E.26.07.14475 | C001853896 | Omar King | St.Ann | Completed | Load_574282 | Roaring River - 210 | Jul 13, 2026 3:19pm | Jul 13, 2026 3:19pm | Jul 13, 2026 3:30pm | Jul 13, 2026 3:33pm | Jul 13, 2026 4:27pm | Jul 13, 2026 4:32pm | Jul 13, 2026 4:32pm | Jul 13, 2026 4:32pm |  |  | Fair | No | On arrival at the location I observed that a team from field service is on site doing a meter change at the premises I further contact dispatch and tell him the situation
Outage | J.E.26.07.14668 | C001853897 | Omar King | St.Ann | Completed | Load_246620 | Roaring River - 210 | Jul 13, 2026 3:19pm | Jul 13, 2026 3:19pm | Jul 13, 2026 5:19pm | Jul 13, 2026 5:19pm | Jul 13, 2026 6:37pm | Jul 13, 2026 6:38pm | Jul 13, 2026 6:38pm | Jul 13, 2026 6:38pm |  |  | Fair | No | Found customer # 6 service wire neutral broken as been repaired customer is now with supply voltage reading 120 volts
Outage | J.E.26.07.15021 | C001853894 | Richman Whyte | Westmoreland | Completed | Load_257539 | Paradise - 210 | Jul 13, 2026 3:19pm | Jul 13, 2026 3:20pm | Jul 13, 2026 5:20pm | Jul 13, 2026 5:20pm | Jul 13, 2026 5:20pm | Jul 13, 2026 5:20pm | Jul 13, 2026 5:21pm | Jul 13, 2026 5:21pm | BrokenPole |  | Rains | No | Hanover call
Outage | J.E.26.07.14411 | C001853892 | Wan Carlos Scarlett | Portmore | Completed | Load_256681 | Naggo Head - 510 | Jul 13, 2026 3:18pm | Jul 13, 2026 3:22pm | Jul 13, 2026 6:50pm | Jul 13, 2026 7:00pm | Jul 13, 2026 7:44pm | Jul 13, 2026 8:11pm | Jul 13, 2026 8:14pm | Jul 13, 2026 8:14pm | BrokenWire |  | Fair | No | Found customer 3 wire service at pole with one of the phase broken off use one bolt clamp at open secondary line phase readings 116-117-234
Outage | J.E.26.07.14950 | C001853890 | Wan Carlos Scarlett | Portmore | Completed | Load_252141 | Naggo Head - 510 | Jul 13, 2026 3:18pm | Jul 13, 2026 3:18pm | Jul 13, 2026 6:00pm | Jul 13, 2026 6:00pm | Jul 13, 2026 6:26pm | Jul 13, 2026 6:56pm | Jul 13, 2026 7:00pm | Jul 13, 2026 7:00pm |  |  | Fair | No | Replace a fuse line Refuse 20 Amp junction no pole # was found nothing was found on primary line
Outage | J.E.26.07.14428 | C001853876 | Raymond Lewis | St.Ann | Completed | Load_260720 | Cardiff Hall - 210 | Jul 13, 2026 3:15pm | Jul 13, 2026 3:16pm | Jul 13, 2026 5:26pm | Jul 13, 2026 5:26pm | Jul 13, 2026 6:27pm | Jul 13, 2026 6:30pm | Jul 13, 2026 6:30pm | Jul 13, 2026 6:30pm |  |  | Fair | No | Premises not found and phone not answering
Outage | J.E.26.07.14658 | C001853875 | Raymond Lewis | St.Ann | Completed | Load_265779 | Cardiff Hall - 310 | Jul 13, 2026 3:15pm | Jul 13, 2026 3:16pm | Jul 13, 2026 4:19pm | Jul 13, 2026 4:20pm | Jul 13, 2026 5:05pm | Jul 13, 2026 5:08pm | Jul 13, 2026 5:10pm | Jul 13, 2026 5:10pm | BrokenWire |  | Fair | No | Directions not proper phone not answering
Outage | J.E.26.07.14723 | C001853874 | Tyrese Williams | St.Ann | Completed | Load_294431 | Cardiff Hall - 210 | Jul 13, 2026 3:15pm | Jul 13, 2026 3:15pm | Jul 13, 2026 4:13pm | Jul 13, 2026 4:14pm | Jul 13, 2026 4:38pm | Jul 13, 2026 4:43pm | Jul 13, 2026 4:43pm | Jul 13, 2026 4:43pm | Fire |  | Fair | No | Premises found ok customer said she didn’t make any report
Outage | J.E.26.07.14844 | C001853872 | Tyrese Williams | St.Ann | Completed | Load_261736 | Cardiff Hall - 310 | Jul 13, 2026 3:15pm | Jul 13, 2026 3:15pm | Jul 13, 2026 4:13pm | Jul 13, 2026 6:24pm | Jul 13, 2026 6:24pm | Jul 13, 2026 6:24pm | Jul 13, 2026 6:24pm | Jul 13, 2026 6:24pm |  |  | Fair | No | Call isn’t for st.ann Team
Outage | J.E.26.07.14916 | C001853873 | Tyrese Williams | St.Ann | Completed | Load_258189 | Cardiff Hall - 210 | Jul 13, 2026 3:15pm | Jul 13, 2026 3:15pm | Jul 13, 2026 4:13pm | Jul 13, 2026 4:43pm | Jul 13, 2026 5:42pm | Jul 13, 2026 6:20pm | Jul 13, 2026 6:22pm | Jul 13, 2026 6:22pm | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Open a 50 kva transformer fuse to remove illegal connections, splice and retention 3 span of secondary phase and neutral
Outage | J.E.26.07.14660 | C001853870 | Wan Carlos Scarlett | St.Catherine | Completed | Load_245565 | Twickenham - 210 | Jul 13, 2026 3:14pm | Jul 13, 2026 3:17pm | Jul 13, 2026 4:23pm | Jul 13, 2026 4:23pm | Jul 13, 2026 5:04pm | Jul 13, 2026 5:58pm | Jul 13, 2026 5:59pm | Jul 13, 2026 5:59pm |  |  | Fair | No | Refuse 30amp junction no pole # was found clear bird from off transformer bushing
Non-Outage | J.E.26.07.10898 | C001853857 | Raymond Carr | St.Mary | Completed | Load_269033 | Oracabessa - 210 | Jul 13, 2026 3:12pm | Jul 13, 2026 3:12pm | Jul 13, 2026 3:18pm | Jul 13, 2026 3:18pm | Jul 13, 2026 3:57pm | Jul 13, 2026 3:31pm | Jul 13, 2026 4:49pm | Jul 13, 2026 4:49pm |  |  | Fair | No | Three defective clamps replaced, at JPS. Meter socket is barrel locked, supply is normal now.
Outage | J.E.26.07.14430 | C001853856 | Derrick Dawkins | St.James | Completed | Load_239445 | Queens Drive - 710 | Jul 13, 2026 3:12pm | Jul 13, 2026 3:14pm | Jul 13, 2026 6:05pm | Jul 13, 2026 6:05pm | Jul 13, 2026 6:22pm | Jul 13, 2026 6:54pm | Jul 13, 2026 6:54pm | Jul 13, 2026 6:54pm |  |  | Fair | No | Only customer without light out of the EG refer back to field service kadian
Outage | J.E.26.07.14788 | C001853855 | Barrington Brown | St.James | Completed | Load_259820 | Rose Hall - 210 | Jul 13, 2026 3:11pm | Jul 13, 2026 3:17pm | Jul 13, 2026 10:42pm | Jul 13, 2026 10:42pm | Jul 13, 2026 10:42pm | Jul 14, 2026 12:04am | Jul 14, 2026 12:04am | Jul 14, 2026 12:04am |  |  | Fair | No | Crew found burnt secondary jumper at transformer pole . Crew used 2one bolt clamps and 5 ft of aluminum to make repairs. All customers restored.
Outage | J.E.26.07.14874 | C001853852 | Derrick Dawkins | St.James | Completed | Load_249682 | Bogue - 310 | Jul 13, 2026 3:11pm | Jul 13, 2026 3:14pm | Jul 13, 2026 6:55pm | Jul 13, 2026 6:55pm | Jul 13, 2026 7:13pm | Jul 13, 2026 7:42pm | Jul 13, 2026 7:44pm | Jul 13, 2026 7:44pm | BrokenWire |  | Fair | No | Customer service wire broken due to illegal connection splice and retention customer service wire voltage 118/119=237
Outage | J.E.26.07.14876 | C001853853 | Derrick Dawkins | St.James | Completed | Load_252646 | Bogue - 410 | Jul 13, 2026 3:11pm | Jul 13, 2026 3:16pm | Jul 13, 2026 3:26pm | Jul 13, 2026 3:26pm | Jul 13, 2026 5:08pm | Jul 13, 2026 6:04pm | Jul 13, 2026 6:05pm | Jul 13, 2026 6:05pm |  |  | Fair | No | Found customers without light due to restoration transformer drop lead disconnected clean and remade joint used 2 pg clamp voltage 119/119=239
Non-Outage | J.E.26.07.14808 | C001853849 | Collin Robinson | null | Completed | null | null | Jul 13, 2026 3:09pm | Jul 13, 2026 7:01pm | Jul 14, 2026 9:30am | Jul 14, 2026 9:30am | Jul 14, 2026 9:31am | Jul 14, 2026 9:32am | Jul 14, 2026 9:32am | Jul 14, 2026 9:32am | Fire |  | Rains | No | Information received from customer that issue was resolved from yesterday
Outage | J.E.26.07.14697 | C001853851 | Collin Robinson | Portland | Completed | Load_252093 | Port Antonio - 310 | Jul 13, 2026 3:09pm | Jul 13, 2026 5:34pm | Jul 13, 2026 6:40pm | Jul 13, 2026 6:40pm | Jul 13, 2026 7:13pm | Jul 13, 2026 6:53pm | Jul 13, 2026 7:16pm | Jul 13, 2026 7:16pm | BrokenWire |  | Rains | No | Reconnect one leg # 6 twisted wire at pole Voltage reading 115v 115v 230v
Outage | J.E.26.07.14893 | C001853848 | Collin Robinson | Portland | Completed | Load_268318 | Port Antonio - 410 | Jul 13, 2026 3:09pm | Jul 13, 2026 7:01pm | Jul 13, 2026 8:23pm | Jul 13, 2026 8:23pm | Jul 13, 2026 9:13pm | Jul 13, 2026 9:35pm | Jul 13, 2026 9:43pm | Jul 13, 2026 9:43pm |  |  | Fair | No | Change 1 corroded one bolt clamp at pole Voltage reading 115v 115v 230v
Outage | J.E.26.07.14914 | C001853850 | Collin Robinson | Portland | Completed | Load_257953 | Port Antonio - 310 | Jul 13, 2026 3:09pm | Jul 13, 2026 5:34pm | Jul 13, 2026 7:21pm | Jul 13, 2026 7:21pm | Jul 13, 2026 7:21pm | Jul 13, 2026 7:22pm | Jul 13, 2026 7:22pm | Jul 13, 2026 7:22pm |  |  | Rains | No | Information received from customer that supply was restored
Outage | J.E.26.07.15014 | C001853847 | Edward Royal | KSAS | Completed | Load_579129 | Duhaney - 310 | Jul 13, 2026 3:08pm | Jul 13, 2026 3:22pm | Jul 13, 2026 5:32pm | Jul 13, 2026 5:32pm | Jul 13, 2026 5:44pm | Jul 13, 2026 6:35pm | Jul 13, 2026 6:35pm | Jul 13, 2026 6:35pm | Fire |  | Fair | No | Spliced and reconnected service cable using 2 single bolt clamp
Outage | J.E.26.07.14759 | C001853835 | Neville Spencer | St.Ann | Completed | Load_265251 | Cardiff Hall - 310 | Jul 13, 2026 3:04pm | Jul 13, 2026 3:28pm | Jul 13, 2026 3:47pm | Jul 13, 2026 3:47pm | Jul 13, 2026 5:08pm | Jul 13, 2026 5:08pm | Jul 13, 2026 5:09pm | Jul 13, 2026 5:09pm | Fire |  | Fair | No | Unable to locate customer.
Outage | J.E.26.07.15009 | C001853838 | Stephen Taylor | St.Thomas | Completed | Load_262086 | Good Year - 110 | Jul 13, 2026 3:04pm | Jul 13, 2026 3:04pm | Jul 13, 2026 3:24pm | Jul 13, 2026 3:24pm | Jul 13, 2026 4:48pm | Jul 13, 2026 4:48pm | Jul 13, 2026 5:11pm | Jul 13, 2026 5:11pm |  |  | Fair | No | Clean up single phase use 3 clamps and customer is now okay
Outage | J.E.26.07.14947 | C001853811 | Stephen Taylor | St.Thomas | Completed | Load_259369 | Lysson - 410 | Jul 13, 2026 2:39pm | Jul 13, 2026 2:39pm | Jul 13, 2026 5:12pm | Jul 13, 2026 5:12pm | Jul 13, 2026 5:42pm | Jul 13, 2026 5:42pm | Jul 13, 2026 5:43pm | Jul 13, 2026 5:43pm | BrokenWire |  | Fair | No | Clean secondary line and close up back 25 kva transformer all customer is now okay
Non-Outage | J.E.26.07.14883 | C001853790 | Fitzroy Turner | null | Completed | null | null | Jul 13, 2026 2:25pm | Jul 13, 2026 3:22pm | Jul 13, 2026 5:01pm | Jul 13, 2026 5:01pm | Jul 13, 2026 5:11pm | Jul 13, 2026 6:18pm | Jul 13, 2026 6:23pm | Jul 13, 2026 6:23pm | Fire |  | Fair | No | Found crossarm burnt cause by rain and dust.use one crossarm and t3 insulator and machine bolts and one 25 amps fuse to restore power to the areas
Non-Outage | J.E.26.07.14474 | C001853787 | Moses Elliston | null | Completed | null | null | Jul 13, 2026 2:24pm | Jul 13, 2026 2:26pm | Jul 14, 2026 10:54am | Jul 14, 2026 10:54am | Jul 14, 2026 10:54am | Jul 14, 2026 10:54am | Jul 14, 2026 10:56am | Jul 14, 2026 10:56am |  |  | Fair | No | Credit added to prepaid account (Duplication)
Outage | J.E.26.07.14392 | C001853789 | Moses Elliston | St.Catherine | Completed | Load_238151 | Twickenham - 310 | Jul 13, 2026 2:24pm | Jul 13, 2026 2:26pm | Jul 13, 2026 4:43pm | Jul 13, 2026 4:43pm | Jul 13, 2026 4:43pm | Jul 13, 2026 4:44pm | Jul 13, 2026 4:44pm | Jul 13, 2026 4:44pm |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.07.14785 | C001853788 | Richman Whyte | Westmoreland | Completed | Load_238357 | Paradise - 210 | Jul 13, 2026 2:24pm | Jul 13, 2026 2:36pm | Jul 13, 2026 5:00pm | Jul 13, 2026 5:00pm | Jul 13, 2026 5:10pm | Jul 13, 2026 5:19pm | Jul 13, 2026 5:20pm | Jul 13, 2026 5:20pm | Fire |  | Rains | No | Replace two 15 amp junction fuse
Outage | J.E.26.07.14867 | C001853780 | Barnett Brown | Manchester | Completed | Load_265468 | Kendal - 310 | Jul 13, 2026 2:21pm | Jul 14, 2026 8:28am | Jul 14, 2026 9:01am | Jul 14, 2026 9:01am | Jul 14, 2026 9:51am | Jul 14, 2026 10:34am | Jul 14, 2026 10:36am | Jul 14, 2026 10:36am |  |  | Fair | No | Patrol line, found nothing, replace blown 15 amp junction fuse, pole number 040054
Outage | J.E.26.07.14846 | C001853778 | Collin Robinson | Portland | Completed | Load_251770 | Port Antonio - 310 | Jul 13, 2026 2:19pm | Jul 13, 2026 2:19pm | Jul 13, 2026 2:50pm | Jul 13, 2026 2:50pm | Jul 13, 2026 2:51pm | Jul 13, 2026 3:16pm | Jul 13, 2026 3:21pm | Jul 13, 2026 3:21pm | Fire |  | Rains | No | Cut and clear tree from primary conductor and replace 15 amps junction fuse at pole 0014418 .and also found two 35 ft t pole rotten refer to maintenance
Outage | J.E.26.07.14850 | C001853775 | Stephen Taylor | St.Thomas | Completed | Load_247908 | Good Year - 210 | Jul 13, 2026 2:17pm | Jul 13, 2026 2:18pm | Jul 14, 2026 5:43pm | Jul 14, 2026 5:44pm | Jul 14, 2026 5:44pm | Jul 14, 2026 5:44pm | Jul 14, 2026 5:46pm | Jul 14, 2026 5:46pm |  |  | Fair | No | Patrol the area a lot of call to single customer no one answered the phone
Non-Outage | J.E.26.07.14097 | C001853774 | Rusean Allen | KSAS | Completed | Load_249201 | Cane River - 310 | Jul 13, 2026 2:15pm | Jul 13, 2026 2:19pm | Jul 14, 2026 3:47am | Jul 14, 2026 3:49am | Jul 14, 2026 3:49am | Jul 14, 2026 3:49am | Jul 14, 2026 3:50am | Jul 14, 2026 3:50am |  |  | Fair | No | Hexing failure, refer to field service department.
Outage | J.E.26.07.14865 | C001853764 | Edward Royal | KSAN | Completed | Load_244103 | Washington Blvd - 610 | Jul 13, 2026 2:11pm | Jul 13, 2026 2:19pm | Jul 13, 2026 3:04pm | Jul 13, 2026 3:04pm | Jul 13, 2026 3:04pm | Jul 13, 2026 3:54pm | Jul 13, 2026 3:54pm | Jul 13, 2026 3:54pm |  |  | Fair | No | Remake primary jumper replaced 2 junction fuse 40A 15A
Outage | J.E.26.07.14853 | C001853763 | Richard Watson | St.Elizabeth | Completed | Load_292260 | Maggotty - 110 | Jul 13, 2026 2:08pm | Jul 13, 2026 5:52pm | Jul 13, 2026 6:21pm | Jul 13, 2026 6:23pm | Jul 13, 2026 6:35pm | Jul 13, 2026 7:19pm | Jul 13, 2026 7:22pm | Jul 13, 2026 7:22pm | BrokenWire |  | Fair | No | Splice and retention broken service wire use approximately 15ft of #6 triplex service wire and three 1bolt clamps, voltage left in meter socket 111v, 119v, 230v.
Outage | J.E.26.07.14838 | C001853761 | Edward Royal | KSAN | Completed | Load_266172 | Washington Blvd - 610 | Jul 13, 2026 2:03pm | Jul 13, 2026 2:06pm | Jul 13, 2026 3:55pm | Jul 13, 2026 3:55pm | Jul 13, 2026 4:17pm | Jul 13, 2026 4:18pm | Jul 13, 2026 4:18pm | Jul 13, 2026 4:18pm |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.07.14796 | C001853759 | Hartley Chin | Clarendon | Completed | Load_253859 | Parnassus - 210 | Jul 13, 2026 1:58pm | Jul 13, 2026 3:25pm | Jul 13, 2026 3:30pm | Jul 13, 2026 5:50pm | Jul 13, 2026 6:07pm | Jul 13, 2026 6:41pm | Jul 13, 2026 6:42pm | Jul 13, 2026 6:42pm |  | Y | Fair | No | Found 2 of 3 blown 30 amp junction fuse (no pole #) due to tree contact, cut tree from line , refused junction ..
Outage | J.E.26.07.14816 | C001853744 | Edward Royal | KSAS | Completed | Load_270125 | Duhaney - 410 | Jul 13, 2026 1:53pm | Jul 14, 2026 8:27am | Jul 14, 2026 9:59am | Jul 14, 2026 10:00am | Jul 14, 2026 10:20am | Jul 14, 2026 10:32am | Jul 14, 2026 10:33am | Jul 14, 2026 10:33am |  |  | Fair | No | Spliced reconnected #6 service cable using one bolt clamp voltage reading 123 v
Outage | J.E.26.07.14704 | C001853742 | Horace Malcolm | St.James | Completed | Load_248690 | Bogue - 610 | Jul 13, 2026 1:51pm | Jul 13, 2026 1:52pm | Jul 13, 2026 2:03pm | Jul 13, 2026 2:03pm | Jul 13, 2026 2:31pm | Jul 14, 2026 7:54am | Jul 14, 2026 7:54am | Jul 14, 2026 7:54am | BrokenPole |  | Fair | No | Check and found old broken pole with cable wires no jps wires attached to pole
Outage | J.E.26.07.14811 | C001853741 | Edward Royal | KSAN | Completed | Load_557728 | Washington Blvd - 610 | Jul 13, 2026 1:51pm | Jul 13, 2026 1:51pm | Jul 13, 2026 3:55pm | Jul 13, 2026 3:55pm | Jul 13, 2026 3:55pm | Jul 13, 2026 3:55pm | Jul 13, 2026 3:55pm | Jul 13, 2026 3:55pm |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.07.14683 | C001853739 | Romeo Brissett | St.James | Completed | Load_249034 | Bogue - 610 | Jul 13, 2026 1:50pm | Jul 13, 2026 3:26pm | Jul 13, 2026 9:24pm | Jul 13, 2026 9:24pm | Jul 13, 2026 10:53pm | Jul 13, 2026 11:25pm | Jul 14, 2026 6:19am | Jul 14, 2026 6:19am | Fire |  | Fair | No | Removed illegal connections, repaired secondary jumper
Outage | J.E.26.07.14810 | C001853740 | Milton Charlton | KSAN | Completed | Load_254841 | West Kings House - 310 | Jul 13, 2026 1:50pm | Jul 13, 2026 1:51pm | Jul 13, 2026 2:26pm | Jul 13, 2026 2:26pm | Jul 13, 2026 3:14pm | Jul 13, 2026 3:25pm | Jul 13, 2026 3:21pm | Jul 13, 2026 3:21pm |  |  | Fair | No | Reset customer circuit breakers.
Non-Outage | J.E.26.07.09042 | C001853722 | Stephen Taylor | St.Thomas | Completed | Load_263695 | Good Year - 110 | Jul 13, 2026 1:41pm | Jul 13, 2026 1:41pm | Jul 13, 2026 2:25pm | Jul 13, 2026 2:25pm | Jul 13, 2026 2:26pm | Jul 13, 2026 2:26pm | Jul 13, 2026 2:35pm | Jul 13, 2026 2:35pm |  |  | Fair | No | Close up back 25 kva transformer safely customer is now okay
Non-Outage | J.E.26.07.14719 | C001853714 | Christopher Edwards | null | Completed | null | null | Jul 13, 2026 1:32pm | Jul 13, 2026 1:33pm | Jul 13, 2026 3:05pm | Jul 13, 2026 3:05pm | Jul 13, 2026 3:20pm | Jul 13, 2026 4:04pm | Jul 13, 2026 4:07pm | Jul 13, 2026 4:07pm | BrokenPole |  | Fair | No | Isolate 25 kva transformer to create dead end on open secondary WiresBroken 30 ft wood poleConsist of open secondary wires Pole needs to be replaced Dead end was created one pole span before reaching broken poleApproximately 15 customers are without supply as a result of broken pole
Outage | J.E.26.07.14760 | C001853703 | Milton Charlton | KSAS | Completed | Load_267534 | Greenwich - 410 | Jul 13, 2026 1:15pm | Jul 14, 2026 8:21am | Jul 14, 2026 10:03am | Jul 14, 2026 10:03am | Jul 14, 2026 10:10am | Jul 14, 2026 10:05am | Jul 14, 2026 10:14am | Jul 14, 2026 10:14am |  |  | Fair | No | Reset customer circuit breaker tripped at meter. Readings at meter socket 118-118-239volts.
Outage | J.E.26.07.14752 | C001853695 | Dean Smith | Hanover | Completed | Load_241281 | Orange Bay - 310 | Jul 13, 2026 1:10pm | Jul 13, 2026 1:11pm | Jul 13, 2026 2:41pm | Jul 13, 2026 2:42pm | Jul 13, 2026 2:42pm | Jul 13, 2026 2:42pm | Jul 13, 2026 2:42pm | Jul 13, 2026 2:42pm |  |  | Rains | No | Shift ended
Outage | J.E.26.07.14717 | C001853694 | Wan Carlos Scarlett | Portmore | Completed | Load_266484 | Naggo Head - 610 | Jul 13, 2026 1:09pm | Jul 13, 2026 3:17pm | Jul 13, 2026 8:15pm | Jul 13, 2026 8:15pm | Jul 13, 2026 8:43pm | Jul 13, 2026 9:16pm | Jul 13, 2026 9:17pm | Jul 13, 2026 9:17pm | Fire |  | Fair | No | Found customer 3 wire service at pothead with phase and neutral corroded use 3 Penn union at service wire phase and neutral readings 115-114-230
Outage | J.E.26.07.14688 | C001853676 | Dean Smith | Hanover | Completed | Load_302811 | Orange Bay - 310 | Jul 13, 2026 12:52pm | Jul 13, 2026 12:52pm | Jul 13, 2026 2:41pm | Jul 13, 2026 2:41pm | Jul 13, 2026 2:41pm | Jul 13, 2026 2:41pm | Jul 13, 2026 2:41pm | Jul 13, 2026 2:41pm |  |  | Rains | No | Shift ended
Outage | J.E.26.07.14682 | C001853675 | Marlon Authors | Manchester | Completed | Load_265454 | Spur Tree - 210 | Jul 13, 2026 12:51pm | Jul 13, 2026 4:01pm | Jul 13, 2026 5:13pm | Jul 13, 2026 5:14pm | Jul 13, 2026 5:14pm | Jul 13, 2026 5:18pm | Jul 13, 2026 5:18pm | Jul 13, 2026 5:18pm |  |  | Fair | No | Unable to locate, I’m not seeing where the issue is
Non-Outage | J.E.26.07.14701 | C001853643 | Fredrick Hamilton | KSAN | Completed | Load_258520 | Constant Spring - 410 | Jul 13, 2026 12:29pm | Jul 14, 2026 8:09am | Jul 14, 2026 8:15am | Jul 14, 2026 12:00pm | Jul 14, 2026 12:21pm | Jul 14, 2026 12:31pm | Jul 14, 2026 12:31pm | Jul 14, 2026 12:31pm |  |  | Fair | No | Burnt meter at location recommend meter change Customer had defective socket which was rectified Please follow upMeter damaged and in single phase condition
Outage | J.E.26.07.14626 | C001853642 | Cliton Henry | St.Mary | Completed | Load_350780 | Blackstonedge - 110 | Jul 13, 2026 12:28pm | Jul 13, 2026 12:28pm | Jul 13, 2026 1:24pm | Jul 13, 2026 1:24pm | Jul 13, 2026 1:48pm | Jul 13, 2026 2:19pm | Jul 13, 2026 2:19pm | Jul 13, 2026 2:19pm | BrokenWire | Y | Fair | No | The secondary conductors found entangled due to bamboo tree fell on the secondary line. A 50 kva transformer was de energized to cut and remove bamboo trees from the secondary lines and retension 1 span of secondary conductors.Supply restored to energized the 50 kva transformer.
Outage | J.E.26.07.14674 | C001853629 | Kemark Slue | St.Catherine | Completed | Load_568938 | Twickenham - 310 | Jul 13, 2026 12:21pm | Jul 13, 2026 12:22pm | Jul 13, 2026 2:27pm | Jul 13, 2026 2:27pm | Jul 13, 2026 3:21pm | Jul 13, 2026 3:12pm | Jul 13, 2026 3:27pm | Jul 13, 2026 3:27pm |  |  | Fair | No | Upon arrival at the location the crew discovered that bush 20 amps junction from three phases was blown at pole # 0028363, further patrol revealed that creepers was the caused, remove creepers, refuse links and re-energized line section.
Outage | J.E.26.07.14666 | C001853618 | Oshane Warren | Westmoreland | Completed | Load_238440 | Paradise - 310 | Jul 13, 2026 12:12pm | Jul 13, 2026 12:14pm | Jul 13, 2026 1:26pm | Jul 13, 2026 1:26pm | Jul 13, 2026 2:10pm | Jul 13, 2026 2:21pm | Jul 13, 2026 2:30pm | Jul 13, 2026 2:30pm | Fire |  | Rains | No | Replace 5amp Junction fuse
Outage | J.E.26.07.14669 | C001853605 | Edward Royal | KSAN | Completed | Load_239622 | Constant Spring - 410 | Jul 13, 2026 12:06pm | Jul 13, 2026 5:16pm | Jul 13, 2026 8:07pm | Jul 13, 2026 8:07pm | Jul 13, 2026 8:07pm | Jul 13, 2026 8:09pm | Jul 13, 2026 8:09pm | Jul 13, 2026 8:09pm | BrokenWire |  | Fair | No | Premises not found unable to communicate with customer
Outage | J.E.26.07.13213 | C001853592 | Wayne Dillion | St.Elizabeth | Completed | Load_243601 | Maggotty - 210 | Jul 13, 2026 12:02pm | Jul 13, 2026 12:02pm | Jul 13, 2026 12:25pm | Jul 13, 2026 12:25pm | Jul 13, 2026 12:25pm | Jul 13, 2026 12:29pm | Jul 13, 2026 12:29pm | Jul 13, 2026 12:29pm |  |  | Fair | No | Please refer same to the maintenance department for extension of secondary so that customer can get reconnected.
Non-Outage | J.E.26.07.14603 | C001853590 | Christopher Edwards | KSAN | Completed | Load_246783 | Constant Spring - 410 | Jul 13, 2026 11:58am | Jul 13, 2026 11:59am | Jul 13, 2026 1:00pm | Jul 13, 2026 1:00pm | Jul 13, 2026 1:51pm | Jul 13, 2026 3:04pm | Jul 13, 2026 3:05pm | Jul 13, 2026 3:05pm | Fire |  | Fair | No | Splice and retention broken open secondary wireUsing:40ft #2 AA conductor (2) #2 preform 2 one bolt clamps Refuse blown 25 kva transformer Using (1) 2 amp
Outage | J.E.26.07.14637 | C001853549 | Christopher Edwards | KSAN | Completed | Load_255109 | Constant Spring - 310 | Jul 13, 2026 11:35am | Jul 13, 2026 11:36am | Jul 13, 2026 11:46am | Jul 13, 2026 11:56am | Jul 13, 2026 11:56am | Jul 13, 2026 12:59pm | Jul 13, 2026 1:00pm | Jul 13, 2026 1:00pm | LeakingTransformer |  | Fair | No | Supply is at the premises 25 kva transformer is slightly leaking oil from the x3 secondary bushing
Outage | J.E.26.07.14633 | C001853548 | Richman Whyte | Westmoreland | Completed | Load_267763 | Paradise - 210 | Jul 13, 2026 11:33am | Jul 13, 2026 11:38am | Jul 13, 2026 12:30pm | Jul 13, 2026 12:30pm | Jul 13, 2026 12:30pm | Jul 13, 2026 12:30pm | Jul 13, 2026 12:32pm | Jul 13, 2026 12:32pm | BrokenPole |  | Fair | No | Concrete pole fell in the church yard during the hurricane customer want it to move
Outage | J.E.26.07.14627 | C001853542 | Edward Royal | KSAN | Completed | Load_268902 | Washington Blvd - 710 | Jul 13, 2026 11:32am | Jul 13, 2026 12:20pm | Jul 13, 2026 1:05pm | Jul 13, 2026 1:05pm | Jul 13, 2026 1:05pm | Jul 13, 2026 1:06pm | Jul 13, 2026 1:06pm | Jul 13, 2026 1:06pm |  |  | Fair | No | Premises found ok related to outage
Non-Outage | J.E.26.07.14598 | C001853534 | Rusean Allen | KSAS | Completed | Load_573580 | Cane River - 410 | Jul 13, 2026 11:26am | Jul 13, 2026 11:41am | Jul 13, 2026 12:39pm | Jul 13, 2026 12:39pm | Jul 13, 2026 1:26pm | Jul 13, 2026 2:01pm | Jul 13, 2026 2:01pm | Jul 13, 2026 2:01pm |  |  | Fair | No | Burnt #2 wire found at intermediate pole, wire was spliced and reconnected.
Outage | J.E.26.07.14596 | C001853533 | Michael Christian | St.James | Completed | Load_267418 | Queens Drive - 710 | Jul 13, 2026 11:23am | Jul 14, 2026 8:12am | Jul 14, 2026 9:06am | Jul 14, 2026 9:06am | Jul 14, 2026 9:13am | Jul 14, 2026 9:14am | Jul 14, 2026 9:14am | Jul 14, 2026 9:14am |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.14563 | C001853522 | Javid Vernon | Westmoreland | Completed | Load_265674 | Paradise - 310 | Jul 13, 2026 11:18am | Jul 13, 2026 3:21pm | Jul 13, 2026 3:45pm | Jul 13, 2026 3:45pm | Jul 13, 2026 4:00pm | Jul 13, 2026 4:45pm | Jul 13, 2026 4:45pm | Jul 13, 2026 4:45pm |  |  | Fair | No | Refuse one 10am junction fuse
Outage | J.E.26.07.14601 | C001853512 | Rusean Allen | KSAS | Completed | Load_244086 | Rockfort - 410 | Jul 13, 2026 11:12am | Jul 13, 2026 11:14am | Jul 13, 2026 2:01pm | Jul 13, 2026 2:02pm | Jul 13, 2026 2:23pm | Jul 13, 2026 2:23pm | Jul 13, 2026 2:23pm | Jul 13, 2026 2:23pm |  |  | Fair | No | Premises okay
Outage | J.E.26.07.14481 | C001853509 | Moses Elliston | Portmore | Completed | Load_238728 | Naggo Head - 610 | Jul 13, 2026 11:11am | Jul 13, 2026 11:11am | Jul 13, 2026 12:10pm | Jul 13, 2026 12:10pm | Jul 13, 2026 1:24pm | Jul 13, 2026 2:02pm | Jul 13, 2026 2:08pm | Jul 13, 2026 2:08pm |  |  | Fair | No | Burnt 2 wire service phase and neutral repaired with 2 clamps.120 volts.
Outage | J.E.26.07.11374 | C001853508 | Daniel Francis | St.Elizabeth | Completed | Load_246153 | Maggotty - 210 | Jul 13, 2026 11:08am | Jul 13, 2026 11:10am | Jul 13, 2026 2:41pm | Jul 13, 2026 2:41pm | Jul 13, 2026 3:41pm | Jul 13, 2026 3:42pm | Jul 13, 2026 3:43pm | Jul 13, 2026 3:43pm |  |  | Fair | No | Found okay customer say light come back
Outage | J.E.26.07.14590 | C001853507 | Selvin White | St.Elizabeth | Completed | Load_245279 | Maggotty - 210 | Jul 13, 2026 11:08am | Jul 13, 2026 11:09am | Jul 13, 2026 11:19am | Jul 13, 2026 12:36pm | Jul 13, 2026 12:37pm | Jul 13, 2026 1:52pm | Jul 13, 2026 1:52pm | Jul 13, 2026 1:52pm | BrokenWire |  | SevereWind | No | Splice and retention 3 pole spans of broken secondary phase and neutral conductors after isolation of a 25 KVA transformer with no pole number at location. Supply restored to the affected customers. Heavy wind and over sagging conductors were said to be the cause.
Outage | J.E.26.07.14568 | C001853503 | Wayne Dillion | St.Elizabeth | Completed | Load_238493 | Maggotty - 110 | Jul 13, 2026 11:07am | Jul 13, 2026 11:10am | Jul 13, 2026 1:19pm | Jul 13, 2026 1:19pm | Jul 13, 2026 1:19pm | Jul 13, 2026 1:50pm | Jul 13, 2026 1:56pm | Jul 13, 2026 1:56pm |  |  | Rains | No | Supply check and found no service wire. Connect same using 50ft of #6 triplex service wire, 3 clamps and 3 linkets. Supply leave working okay reading 111v, 112v and cross phase 223volts.
Non-Outage | J.E.26.07.14588 | C001853502 | Lancelot Brown | Hanover | Completed | Load_261941 | Orange Bay - 210 | Jul 13, 2026 11:05am | Jul 13, 2026 11:05am | Jul 13, 2026 11:15am | Jul 13, 2026 11:15am | Jul 13, 2026 1:27pm | Jul 13, 2026 1:38pm | Jul 13, 2026 1:38pm | Jul 13, 2026 1:38pm |  |  | Rains | No | Cannot locate customer no answer from contact number need proper direction
Non-Outage | J.E.26.07.04967 | C001853501 | Andrew Powell | Manchester | Completed | Load_256355 | Spur Tree - 210 | Jul 13, 2026 11:03am | Jul 13, 2026 11:04am | Jul 13, 2026 11:09am | Jul 13, 2026 11:10am | Jul 13, 2026 11:48am | Jul 13, 2026 12:48pm | Jul 13, 2026 12:50pm | Jul 13, 2026 12:50pm |  |  | Fair | No | Remade corroded service wire joints at meter pothead 3 wire using two clamps, voltage reading 112v - 116v phase to neutral 228v cross phase.
Non-Outage | J.E.26.07.14566 | C001853490 | Odeanie Davis | KSAS | Completed | Load_256814 | Greenwich - 710 | Jul 13, 2026 10:52am | Jul 13, 2026 10:58am | Jul 13, 2026 12:23pm | Jul 13, 2026 12:23pm | Jul 13, 2026 12:35pm | Jul 13, 2026 12:51pm | Jul 13, 2026 12:54pm | Jul 13, 2026 12:54pm |  |  | Fair | No | 118v/0V at arrival, open circuit at secondary corrected, 1 one bolt clamp, 119v/118v & 238v after correction
Outage | J.E.26.07.14564 | C001853489 | Edward Royal | KSAN | Completed | Load_293297 | Washington Blvd - 710 | Jul 13, 2026 10:52am | Jul 13, 2026 12:19pm | Jul 13, 2026 12:22pm | Jul 13, 2026 12:22pm | Jul 13, 2026 12:35pm | Jul 13, 2026 1:05pm | Jul 13, 2026 1:05pm | Jul 13, 2026 1:05pm |  |  | Fair | No | Replaced 2 junction fuse 25a 20A pole #0022153
Outage | J.E.26.07.14562 | C001853487 | Edward Royal | KSAN | Completed | Load_249728 | West Kings House - 410 | Jul 13, 2026 10:50am | Jul 13, 2026 12:22pm | Jul 13, 2026 1:06pm | Jul 13, 2026 1:06pm | Jul 13, 2026 1:30pm | Jul 13, 2026 1:52pm | Jul 13, 2026 1:53pm | Jul 13, 2026 1:53pm |  |  | Fair | No | Customer have internal problems customer breaker trip problem was resolved
Non-Outage | J.E.26.07.14552 | C001853486 | Christopher Edwards | KSAN | Completed | Load_246783 | Constant Spring - 410 | Jul 13, 2026 10:48am | Jul 13, 2026 10:49am | Jul 13, 2026 11:04am | Jul 13, 2026 11:08am | Jul 13, 2026 11:08am | Jul 13, 2026 11:48am | Jul 13, 2026 11:49am | Jul 13, 2026 11:49am |  |  | Fair | No | Premises closed No one is at location to give access Customer request a visit at 4:00pm Today
Non-Outage | J.E.26.07.14556 | C001853481 | Andre Smith | null | Completed | null | null | Jul 13, 2026 10:47am | Jul 13, 2026 10:47am | Jul 13, 2026 12:33pm | Jul 13, 2026 12:33pm | Jul 13, 2026 12:35pm | Jul 13, 2026 12:35pm | Jul 13, 2026 12:35pm | Jul 13, 2026 12:35pm | Fire |  | Fair | No | Premises found okay supply restored already
Non-Outage | J.E.26.07.14540 | C001853480 | Stephen Taylor | null | Completed | null | null | Jul 13, 2026 10:44am | Jul 13, 2026 10:45am | Jul 13, 2026 8:57pm | Jul 13, 2026 8:57pm | Jul 13, 2026 9:56pm | Jul 13, 2026 9:57pm | Jul 13, 2026 9:58pm | Jul 13, 2026 9:58pm |  |  | Fair | No | Clean up single phase use 2 clamps reading 111,112,224 customer is now okay
Outage | J.E.26.07.14435 | C001853479 | Stephen Taylor | St.Thomas | Completed | Load_247908 | Good Year - 210 | Jul 13, 2026 10:44am | Jul 13, 2026 10:45am | Jul 13, 2026 11:45am | Jul 13, 2026 11:45am | Jul 13, 2026 11:45am | Jul 13, 2026 11:45am | Jul 13, 2026 11:46am | Jul 13, 2026 11:46am |  |  | Fair | No | Need more information a lot of call to customer no one answered the phone
Outage | J.E.26.07.14553 | C001853478 | Selvin White | St.Elizabeth | Completed | Load_263523 | Maggotty - 110 | Jul 13, 2026 10:44am | Jul 13, 2026 11:05am | Jul 13, 2026 11:21am | Jul 13, 2026 11:21am | Jul 13, 2026 11:34am | Jul 13, 2026 11:46am | Jul 13, 2026 11:46am | Jul 13, 2026 11:46am |  |  | Fair | No | Meter center found padlock and cannot be currently accessed however escalation department was contacted and said an order has been generated for the field service department to visit.
Non-Outage | J.E.26.07.06658 | C001853477 | Collin Robinson | Portland | Completed | Load_238553 | Port Antonio - 310 | Jul 13, 2026 10:43am | Jul 13, 2026 10:44am | Jul 13, 2026 11:17am | Jul 13, 2026 11:17am | Jul 13, 2026 11:38am | Jul 13, 2026 11:41am | Jul 13, 2026 11:41am | Jul 13, 2026 11:41am |  |  | Fair | No | Premises found okMeter socket voltage reading 118v 117v 235v
Non-Outage | J.E.26.07.14395 | C001853470 | Collin Robinson | Portland | Completed | Load_351343 | Port Antonio - 410 | Jul 13, 2026 10:42am | Jul 13, 2026 10:43am | Jul 13, 2026 11:41am | Jul 13, 2026 11:41am | Jul 13, 2026 12:07pm | Jul 13, 2026 12:21pm | Jul 13, 2026 12:21pm | Jul 13, 2026 12:21pm |  |  | Fair | No | Change one corroded one bolt clamp at pothead Voltage reading 115v 115v 230v
Outage | J.E.26.07.14526 | C001853469 | Floyd Taylor | Trelawny | Completed | Load_294629 | Greenwood - 110 | Jul 13, 2026 10:41am | Jul 13, 2026 3:24pm | Jul 13, 2026 7:02pm | Jul 13, 2026 7:02pm | Jul 13, 2026 7:02pm | Jul 13, 2026 7:24pm | Jul 13, 2026 7:25pm | Jul 13, 2026 7:25pm |  |  | Fair | No | Replace 2-30 amp junction fuse.
Outage | J.E.26.07.14507 | C001853468 | Dwayne Samuels | Trelawny | Completed | Load_263248 | Greenwood - 110 | Jul 13, 2026 10:40am | Jul 13, 2026 10:41am | Jul 13, 2026 12:36pm | Jul 13, 2026 12:37pm | Jul 13, 2026 1:24pm | Jul 13, 2026 2:18pm | Jul 13, 2026 2:18pm | Jul 13, 2026 2:18pm | Fire |  | Fair | No | Check and found ok voltage found is 240v 238v 236v 415v 422v 410v
Outage | J.E.26.07.11869 | C001853449 | Barnett Brown | Manchester | Completed | Load_246108 | Spur Tree - 210 | Jul 13, 2026 10:29am | Jul 13, 2026 10:30am | Jul 13, 2026 11:00am | Jul 13, 2026 11:00am | Jul 13, 2026 12:34pm | Jul 13, 2026 12:47pm | Jul 13, 2026 12:49pm | Jul 13, 2026 12:49pm |  |  | Rains | No | Premises found ok
Outage | J.E.26.07.14520 | C001853448 | Romeo Brissett | St.James | Completed | Load_261318 | Bogue - 610 | Jul 13, 2026 10:29am | Jul 13, 2026 3:26pm | Jul 13, 2026 6:27pm | Jul 13, 2026 6:33pm | Jul 13, 2026 7:44pm | Jul 13, 2026 7:14pm | Jul 13, 2026 7:57pm | Jul 13, 2026 7:57pm |  |  | Fair | No | Unable to locate customer phone ring to voicemail, lane patrolled premises did not found.
Non-Outage | J.E.26.07.14421 | C001853436 | Horace Malcolm | St.James | Completed | Load_251206 | Rose Hall - 110 | Jul 13, 2026 10:26am | Jul 13, 2026 11:07am | Jul 13, 2026 11:39am | Jul 13, 2026 11:39am | Jul 13, 2026 11:59am | Jul 13, 2026 1:57pm | Jul 13, 2026 1:58pm | Jul 13, 2026 1:58pm |  |  | Fair | No | Not authorized to open advised by Mr Richards
Outage | J.E.26.07.14516 | C001853427 | Andre Smith | KSAS | Completed | Load_263218 | Hunts Bay - 210 | Jul 13, 2026 10:19am | Jul 13, 2026 10:25am | Jul 13, 2026 12:39pm | Jul 13, 2026 12:39pm | Jul 13, 2026 1:28pm | Jul 13, 2026 1:43pm | Jul 13, 2026 1:43pm | Jul 13, 2026 1:43pm |  |  | Fair | No | Service wire #6triplex remove from premises because of disconnection field service department required to replace 60ft of Same
Outage | J.E.26.07.14462 | C001853419 | Wayne Dillion | St.Elizabeth | Completed | Load_265227 | Maggotty - 110 | Jul 13, 2026 10:16am | Jul 13, 2026 10:32am | Jul 13, 2026 10:47am | Jul 13, 2026 10:47am | Jul 13, 2026 10:47am | Jul 13, 2026 10:50am | Jul 13, 2026 10:51am | Jul 13, 2026 10:51am |  |  | Fair | No | Repairs are not fully completed at the customer’s premises
Non-Outage | J.E.26.07.12548 | C001853417 | Neckell Ormsby | St.Mary | Completed | Load_252159 | Highgate - 210 | Jul 13, 2026 10:14am | Jul 13, 2026 10:14am | Jul 13, 2026 2:17pm | Jul 13, 2026 2:17pm | Jul 13, 2026 2:17pm | Jul 13, 2026 2:00pm | Jul 13, 2026 2:22pm | Jul 13, 2026 2:22pm |  |  | Fair | No | Troubleshoot and found corrosion at pothead clean and remade joints using 2- one bolt clamps voltage left 112v 113v 226v NB Tablet battery died in middle of shift and started shift at %100
Non-Outage | J.E.26.07.14443 | C001853403 | Andre Smith | KSAS | Completed | Load_246477 | Greenwich - 410 | Jul 13, 2026 10:03am | Jul 13, 2026 10:04am | Jul 13, 2026 2:22pm | Jul 13, 2026 2:22pm | Jul 13, 2026 3:47pm | Jul 13, 2026 3:49pm | Jul 13, 2026 3:52pm | Jul 13, 2026 3:52pm |  |  | Fair | No | Replace defective one bolt clamp at pole on neutral supply restored
Non-Outage | J.E.26.07.14447 | C001853402 | Andre Smith | KSAS | Completed | Load_244061 | Greenwich - 410 | Jul 13, 2026 10:03am | Jul 13, 2026 10:04am | Jul 13, 2026 1:43pm | Jul 13, 2026 1:43pm | Jul 13, 2026 2:04pm | Jul 13, 2026 2:21pm | Jul 13, 2026 2:22pm | Jul 13, 2026 2:22pm | LowHangingWires |  | Fair | No | Repair burnt neutral service wire using one bolt clamp mid span supply restored
Outage | J.E.26.07.14487 | C001853377 | Edward Royal | KSAS | Completed | Load_251395 | Duhaney - 310 | Jul 13, 2026 9:57am | Jul 13, 2026 9:57am | Jul 13, 2026 11:12am | Jul 13, 2026 11:12am | Jul 13, 2026 11:52am | Jul 13, 2026 12:17pm | Jul 13, 2026 12:17pm | Jul 13, 2026 12:17pm | BrokenWire |  | Fair | No | Spliced and reconnected service neutral using 2 single bolt clamp
Outage | J.E.26.07.14470 | C001853376 | Kenroy Dale | Manchester | Completed | Load_301461 | Kendal - 310 | Jul 13, 2026 9:56am | Jul 13, 2026 10:10am | Jul 13, 2026 2:15pm | Jul 13, 2026 2:15pm | Jul 13, 2026 3:09pm | Jul 13, 2026 3:10pm | Jul 13, 2026 3:11pm | Jul 13, 2026 3:11pm |  |  | Fair | No | Area checked and found with supply, customer also confirmed that supply has been restored
Non-Outage | J.E.26.07.14474 | C001853374 | Kemark Slue | null | Completed | null | null | Jul 13, 2026 9:54am | Jul 13, 2026 9:55am | Jul 13, 2026 11:07am | Jul 13, 2026 11:07am | Jul 13, 2026 11:44am | Jul 13, 2026 10:27am | Jul 13, 2026 2:19pm | Jul 13, 2026 2:19pm |  |  | Fair | No | Upon arrival at the location the crew discovered that the customer is unable to add credit to CIU, please refer to Field service to assist asap.
Outage | J.E.26.07.14459 | C001853372 | Ricky Hall | St.Catherine | Completed | Load_557387 | Rhodens Pen - 410 | Jul 13, 2026 9:54am | Jul 13, 2026 9:55am | Jul 13, 2026 12:54pm | Jul 13, 2026 12:54pm | Jul 13, 2026 1:44pm | Jul 13, 2026 2:02pm | Jul 13, 2026 2:04pm | Jul 13, 2026 2:04pm |  |  | Fair | No | Defective 3W meter #2467162 plz refer to field service
Outage | J.E.26.07.14463 | C001853373 | Ricky Hall | St.Catherine | Completed | Load_251255 | Rhodens Pen - 410 | Jul 13, 2026 9:54am | Jul 13, 2026 9:55am | Jul 13, 2026 10:55am | Jul 13, 2026 10:55am | Jul 13, 2026 11:01am | Jul 13, 2026 11:06am | Jul 13, 2026 11:06am | Jul 13, 2026 11:06am |  |  | Fair | No | Premises closed
Outage | J.E.26.07.14356 | C001853363 | Oraine Minto | St.Ann | Completed | Load_239981 | Roaring River - 410 | Jul 13, 2026 9:49am | Jul 13, 2026 9:49am | Jul 13, 2026 11:23am | Jul 13, 2026 1:03pm | Jul 13, 2026 1:03pm | Jul 13, 2026 1:04pm | Jul 13, 2026 1:08pm | Jul 13, 2026 1:08pm | BrokenWire |  | Fair | No | Reconnection done 228v 111v 116v 2 one bolt clamp 2 red to red
Outage | J.E.26.07.14464 | C001853355 | Dean Smith | Hanover | Completed | Load_264386 | Orange Bay - 310 | Jul 13, 2026 9:42am | Jul 13, 2026 11:25am | Jul 13, 2026 12:30pm | Jul 13, 2026 12:30pm | Jul 13, 2026 2:20pm | Jul 13, 2026 2:20pm | Jul 13, 2026 2:40pm | Jul 13, 2026 2:40pm |  |  | Fair | No | Customer service wire was removed during hurricane restoration for repair. Replace about 80’ of number six triplex, used (3) red-orange service connectors and (3) one bolt clamp.
Outage | J.E.26.07.14472 | C001853354 | Andre Smith | KSAS | Completed | Load_258279 | Three Miles - 510 | Jul 13, 2026 9:41am | Jul 13, 2026 9:42am | Jul 13, 2026 10:46am | Jul 13, 2026 10:46am | Jul 13, 2026 12:02pm | Jul 13, 2026 12:18pm | Jul 13, 2026 12:32pm | Jul 13, 2026 12:32pm |  |  | Fair | No | Replace blown transformer fuses 10A/3 cause by truck making contact with pole supply
Outage | J.E.26.07.14413 | C001853353 | Michael Christian | St.James | Completed | Load_240769 | Bogue - 510 | Jul 13, 2026 9:39am | Jul 13, 2026 9:39am | Jul 13, 2026 1:52pm | Jul 13, 2026 1:52pm | Jul 13, 2026 2:50pm | Jul 13, 2026 3:47pm | Jul 13, 2026 3:47pm | Jul 13, 2026 3:47pm |  |  | Fair | No | Reconnection customer service wire at pole voltage 111 113 225 at meter
Outage | J.E.26.07.14449 | C001853352 | Michael Christian | St.James | Completed | Load_243432 | Bogue - 610 | Jul 13, 2026 9:38am | Jul 13, 2026 9:39am | Jul 13, 2026 11:19am | Jul 13, 2026 11:19am | Jul 13, 2026 12:55pm | Jul 13, 2026 1:14pm | Jul 13, 2026 1:15pm | Jul 13, 2026 1:15pm |  |  | Fair | No | Found 1 10 kava out cause by banging wire replace 1 1 amp no pole #
Outage | J.E.26.07.09718 | C001853346 | Moses Elliston | St.Catherine | Completed | Load_263911 | Tredegar - 410 | Jul 13, 2026 9:37am | Jul 13, 2026 9:37am | Jul 13, 2026 3:34pm | Jul 13, 2026 3:34pm | Jul 13, 2026 3:34pm | Jul 11, 2026 8:45am | Jul 13, 2026 3:36pm | Jul 13, 2026 3:36pm |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.07.14417 | C001853345 | Gregory Grossett | Portland | Completed | Load_244673 | Port Antonio - 410 | Jul 13, 2026 9:36am | Jul 13, 2026 9:39am | Jul 13, 2026 11:08am | Jul 13, 2026 11:08am | Jul 13, 2026 11:59am | Jul 13, 2026 12:35pm | Jul 13, 2026 12:44pm | Jul 13, 2026 12:44pm |  |  | Fair | No | 110 service wire corroded at pole and pothead repair and ok material use 2 penunion sleeves 1-one bolt clamp voltage reading 115v.
Outage | J.E.26.07.14456 | C001853341 | Junior Scarlett | St.James | Completed | Load_252646 | Bogue - 410 | Jul 13, 2026 9:32am | Jul 13, 2026 9:35am | Jul 13, 2026 2:00pm | Jul 13, 2026 2:07pm | Jul 13, 2026 2:24pm | Jul 13, 2026 2:32pm | Jul 13, 2026 2:32pm | Jul 13, 2026 2:32pm | Fire |  | Fair | No | Refer to emergency teamJumper burn off cause by truckVoltage found 115v 0.22v 115v
Non-Outage | J.E.26.07.07046 | C001853339 | Daniel Francis | St.Ann | Completed | Load_253537 | Upper White River - 210 | Jul 13, 2026 9:31am | Jul 13, 2026 9:32am | Jul 13, 2026 11:07am | Jul 13, 2026 11:07am | Jul 13, 2026 1:05pm | Jul 13, 2026 2:40pm | Jul 13, 2026 2:40pm | Jul 13, 2026 2:40pm |  |  | Fair | No | At prospect office remade neutral joint at transformer pole also service wire found broken splice and reconnect at manager quarter
Non-Outage | J.E.26.06.19124 | C001853323 | Error Coore | Manchester | Completed | Load_263063 | Kendal - 210 | Jul 13, 2026 9:30am | Jul 13, 2026 9:32am | Jul 13, 2026 3:08pm | Jul 13, 2026 3:08pm | Jul 13, 2026 3:30pm | Jul 13, 2026 3:57pm | Jul 13, 2026 3:59pm | Jul 13, 2026 3:59pm |  |  | Fair | No | Premise not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.06.19568 | C001853324 | Error Coore | Manchester | Completed | Load_252632 | Kendal - 210 | Jul 13, 2026 9:30am | Jul 13, 2026 9:32am | Jul 13, 2026 1:53pm | Jul 13, 2026 1:53pm | Jul 13, 2026 2:42pm | Jul 13, 2026 3:03pm | Jul 13, 2026 3:08pm | Jul 13, 2026 3:08pm |  |  | Fair | No | Premise not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.06.19630 | C001853329 | Error Coore | Manchester | Completed | Load_241328 | Kendal - 210 | Jul 13, 2026 9:30am | Jul 13, 2026 9:32am | Jul 13, 2026 10:08am | Jul 13, 2026 1:06pm | Jul 13, 2026 1:33pm | Jul 13, 2026 1:50pm | Jul 13, 2026 1:52pm | Jul 13, 2026 1:52pm |  |  | Rains | No | Premise not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.06.20143 | C001853327 | Error Coore | Manchester | Completed | Load_240750 | Kendal - 210 | Jul 13, 2026 9:30am | Jul 13, 2026 9:32am | Jul 13, 2026 10:08am | Jul 13, 2026 10:15am | Jul 13, 2026 11:47am | Jul 13, 2026 12:06pm | Jul 13, 2026 12:07pm | Jul 13, 2026 12:07pm |  |  | Fair | No | Premise found ok voltage reading 116/115/231 volts
Non-Outage | J.E.26.06.20188 | C001853332 | Error Coore | Manchester | Completed | Load_248685 | Kendal - 210 | Jul 13, 2026 9:30am | Jul 13, 2026 9:32am | Jul 14, 2026 3:49pm | Jul 14, 2026 3:49pm | Jul 14, 2026 3:49pm | Jul 14, 2026 3:49pm | Jul 14, 2026 3:50pm | Jul 14, 2026 3:50pm |  |  | Fair | No | Premise not found not getting customer on phone
Non-Outage | J.E.26.06.20672 | C001853336 | Error Coore | Manchester | Completed | Load_261106 | Spur Tree - 310 | Jul 13, 2026 9:30am | Jul 13, 2026 9:32am | Jul 14, 2026 1:15pm | Jul 14, 2026 1:15pm | Jul 14, 2026 2:33pm | Jul 14, 2026 2:53pm | Jul 14, 2026 2:54pm | Jul 14, 2026 2:54pm |  |  | Fair | No | Premise not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.12676 | C001853337 | Orville Lee | St.Catherine | Completed | Load_246022 | Twickenham - 210 | Jul 13, 2026 9:30am | Jul 13, 2026 9:31am | Jul 13, 2026 9:50am | Jul 13, 2026 9:51am | Jul 13, 2026 10:33am | Jul 13, 2026 11:10am | Jul 13, 2026 11:11am | Jul 13, 2026 11:11am |  |  | Fair | No | Premises closed Costumer request for a technician to visit july(18)
Non-Outage | J.E.26.07.14145 | C001853334 | Orville Lee | St.Catherine | Completed | Load_557084 | Twickenham - 210 | Jul 13, 2026 9:30am | Jul 13, 2026 9:31am | Jul 13, 2026 9:50am | Jul 14, 2026 4:02pm | Jul 14, 2026 4:39pm | Jul 14, 2026 4:42pm | Jul 14, 2026 4:42pm | Jul 14, 2026 4:42pm |  |  | Fair | No | Checks made and found transformer drop lead connection burn Voltage 88v115VUnable to carry out repair because I’m unable to reach the connectionsRefer to a bucket truck team
Non-Outage | J.E.26.07.14197 | C001853333 | Orville Lee | Portmore | Completed | Load_246794 | Naggo Head - 610 | Jul 13, 2026 9:30am | Jul 13, 2026 9:31am | Jul 13, 2026 9:50am | Jul 13, 2026 11:14am | Jul 13, 2026 11:50am | Jul 13, 2026 11:51am | Jul 13, 2026 11:52am | Jul 13, 2026 11:52am |  |  | Fair | No | Pot head connection corroded Three pen union and one 1bolt clamp usedVoltage120v
Non-Outage | J.E.26.07.14266 | C001853331 | Orville Lee | St.Catherine | Completed | Load_576105 | Twickenham - 210 | Jul 13, 2026 9:30am | Jul 13, 2026 9:31am | Jul 13, 2026 9:50am | Jul 13, 2026 11:53am | Jul 13, 2026 12:13pm | Jul 13, 2026 1:06pm | Jul 13, 2026 1:06pm | Jul 13, 2026 1:06pm |  |  | Fair | No | Service wire defective Two pen union, two one bolt clamp and 30ft #6 service wire usedVoltage 115V
Non-Outage | J.E.26.07.14342 | C001853330 | Orville Lee | St.Catherine | Completed | Load_248766 | Twickenham - 210 | Jul 13, 2026 9:30am | Jul 13, 2026 9:31am | Jul 13, 2026 9:50am | Jul 13, 2026 4:03pm | Jul 13, 2026 4:27pm | Jul 13, 2026 5:05pm | Jul 13, 2026 5:10pm | Jul 13, 2026 5:10pm |  |  | Fair | No | Checks made and found drop lead wire burn at meter on pole Unable to reach to carry out repair Bucket truck recommend Voltage 115V80V
Non-Outage | J.E.26.07.14355 | C001853325 | Orville Lee | Portmore | Completed | Load_254077 | Naggo Head - 510 | Jul 13, 2026 9:30am | Jul 13, 2026 9:31am | Jul 13, 2026 9:50am | Jul 13, 2026 1:11pm | Jul 13, 2026 1:23pm | Jul 13, 2026 1:36pm | Jul 13, 2026 1:38pm | Jul 13, 2026 1:38pm |  |  | Fair | No | Upon arrival no visible fire on secondary line Customer show where fire was and mentioned a team visited before
Non-Outage | J.E.26.06.15476 | C001853317 | Error Coore | Manchester | Completed | Load_253163 | Spur Tree - 310 | Jul 13, 2026 9:29am | Jul 13, 2026 9:34am | Jul 14, 2026 9:10am | Jul 14, 2026 9:19am | Jul 14, 2026 9:56am | Jul 14, 2026 10:05am | Jul 14, 2026 10:09am | Jul 14, 2026 10:09am |  |  | Fair | No | Premise not found found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.06.18577 | C001853318 | Error Coore | Manchester | Completed | Load_265918 | Spur Tree - 310 | Jul 13, 2026 9:29am | Jul 13, 2026 9:34am | Jul 14, 2026 10:10am | Jul 14, 2026 10:10am | Jul 14, 2026 11:02am | Jul 14, 2026 11:13am | Jul 14, 2026 11:14am | Jul 14, 2026 11:14am |  |  | Fair | No | Premise not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.06.18814 | C001853321 | Error Coore | Manchester | Completed | Load_243616 | Spur Tree - 310 | Jul 13, 2026 9:29am | Jul 13, 2026 9:34am | Jul 14, 2026 11:14am | Jul 14, 2026 11:50am | Jul 14, 2026 12:59pm | Jul 14, 2026 1:13pm | Jul 14, 2026 1:14pm | Jul 14, 2026 1:14pm |  |  | Fair | No | Premise not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.06.19080 | C001853322 | Error Coore | Manchester | Completed | Load_262584 | Kendal - 210 | Jul 13, 2026 9:29am | Jul 13, 2026 9:34am | Jul 13, 2026 10:13am | Jul 13, 2026 12:07pm | Jul 13, 2026 12:39pm | Jul 13, 2026 1:05pm | Jul 13, 2026 1:06pm | Jul 13, 2026 1:06pm |  |  | Fair | No | Premise found ok voltage reading 110/111/221 volts
Non-Outage | J.E.26.07.10297 | C001853320 | Rochaine Hussey | KSAN | Completed | Load_256340 | Constant Spring - 410 | Jul 13, 2026 9:29am | Jul 13, 2026 9:29am | Jul 13, 2026 9:40am | Jul 13, 2026 12:34pm | Jul 13, 2026 12:35pm | Jul 13, 2026 12:36pm | Jul 13, 2026 12:36pm | Jul 13, 2026 12:36pm |  |  | Fair | No | Customer said issue was already resolved
Non-Outage | J.E.26.07.10321 | C001853319 | Rochaine Hussey | KSAN | Completed | Load_247395 | Constant Spring - 410 | Jul 13, 2026 9:29am | Jul 13, 2026 9:29am | Jul 13, 2026 9:42am | Jul 13, 2026 4:49pm | Jul 13, 2026 4:49pm | Jul 13, 2026 4:50pm | Jul 13, 2026 4:50pm | Jul 13, 2026 4:50pm |  |  | Fair | No | Customer say the issue was resolved
Non-Outage | J.E.26.07.10519 | C001853315 | Rochaine Hussey | KSAN | Completed | Load_240948 | Constant Spring - 410 | Jul 13, 2026 9:29am | Jul 13, 2026 9:29am | Jul 13, 2026 9:37am | Jul 13, 2026 1:08pm | Jul 13, 2026 1:09pm | Jul 13, 2026 1:09pm | Jul 13, 2026 1:09pm | Jul 13, 2026 1:09pm |  |  | Fair | No | Customer say the issue was already resolved
Non-Outage | J.E.26.07.11588 | C001853316 | Rochaine Hussey | KSAN | Completed | Load_244992 | Constant Spring - 410 | Jul 13, 2026 9:29am | Jul 13, 2026 9:29am | Jul 13, 2026 9:39am | Jul 13, 2026 4:51pm | Jul 13, 2026 4:51pm | Jul 13, 2026 4:51pm | Jul 13, 2026 4:51pm | Jul 13, 2026 4:51pm |  |  | Fair | No | Customer say the issue was resolved
Non-Outage | J.E.26.07.12306 | C001853312 | Rochaine Hussey | KSAN | Completed | Load_260089 | West Kings House - 310 | Jul 13, 2026 9:29am | Jul 13, 2026 9:29am | Jul 13, 2026 9:44am | Jul 13, 2026 1:01pm | Jul 13, 2026 1:01pm | Jul 13, 2026 1:02pm | Jul 13, 2026 1:03pm | Jul 13, 2026 1:03pm |  |  | Fair | No | Customer say the issue was already resolved
Non-Outage | J.E.26.07.11498 | C001853304 | Neckell Ormsby | St.Mary | Completed | Load_252125 | Highgate -110 | Jul 13, 2026 9:28am | Jul 13, 2026 9:28am | Jul 13, 2026 10:25am | Jul 13, 2026 10:25am | Jul 13, 2026 10:52am | Jul 13, 2026 12:03pm | Jul 13, 2026 12:19pm | Jul 13, 2026 12:19pm |  |  | Fair | No | Found broken secondary neutral open 25 kva transformer no pole number seen to splice and retention conductor using approximately 40ft #2 AA,1-#2 sleeve and 2- one bolt clamps voltage left 114v 116v 229v
Non-Outage | J.E.26.07.12495 | C001853311 | Rochaine Hussey | KSAN | Completed | Load_264345 | Constant Spring - 410 | Jul 13, 2026 9:28am | Jul 13, 2026 9:29am | Jul 13, 2026 9:50am | Jul 13, 2026 12:40pm | Jul 13, 2026 12:41pm | Jul 13, 2026 12:41pm | Jul 13, 2026 12:41pm | Jul 13, 2026 12:41pm |  |  | Fair | No | Customer said issue was already resolved
Non-Outage | J.E.26.07.13729 | C001853308 | Rochaine Hussey | KSAN | Completed | Load_1001730 | Constant Spring - 410 | Jul 13, 2026 9:28am | Jul 13, 2026 9:29am | Jul 13, 2026 11:14am | Jul 13, 2026 11:15am | Jul 13, 2026 11:35am | Jul 13, 2026 12:22pm | Jul 13, 2026 12:23pm | Jul 13, 2026 12:23pm |  |  | Fair | No | Neutral wire burnt off poleWire was reconnected Issue resolved 114v
Outage | J.E.26.07.14412 | C001853303 | Neckell Ormsby | St.Mary | Completed | Load_263217 | Highgate -110 | Jul 13, 2026 9:28am | Jul 13, 2026 9:28am | Jul 13, 2026 12:19pm | Jul 13, 2026 12:19pm | Jul 13, 2026 12:45pm | Jul 13, 2026 12:38pm | Jul 13, 2026 2:17pm | Jul 13, 2026 2:17pm |  |  | Rains | No | Troubleshoot and found internal fault customer was advised
Non-Outage | J.E.26.07.12703 | C001853294 | Royston Montague | St.Catherine | Completed | Load_290839 | Rhodens Pen - 210 | Jul 13, 2026 9:27am | Jul 13, 2026 9:29am | Jul 13, 2026 10:05am | Jul 13, 2026 4:11pm | Jul 13, 2026 5:20pm | Jul 13, 2026 5:21pm | Jul 13, 2026 5:21pm | Jul 13, 2026 5:21pm |  |  | Fair | No | Customer only getting one hot leg from box , hex box in area. Please assign to sir Moses thanks.
Non-Outage | J.E.26.07.12975 | C001853291 | Royston Montague | St.Catherine | Completed | Load_245775 | New Michelton - 210 | Jul 13, 2026 9:27am | Jul 13, 2026 9:29am | Jul 13, 2026 10:05am | Jul 13, 2026 12:41pm | Jul 13, 2026 2:19pm | Jul 13, 2026 2:22pm | Jul 13, 2026 2:23pm | Jul 13, 2026 2:23pm |  |  | Rains | No | Faulty joints at pothead, same corrected, voltage 232v 116v 115v
Non-Outage | J.E.26.07.13648 | C001853288 | Royston Montague | St.Catherine | Completed | Load_238392 | New Michelton - 410 | Jul 13, 2026 9:27am | Jul 13, 2026 9:29am | Jul 13, 2026 10:05am | Jul 13, 2026 3:32pm | Jul 13, 2026 4:07pm | Jul 13, 2026 4:08pm | Jul 13, 2026 4:09pm | Jul 13, 2026 4:09pm |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.07.00792 | C001853283 | Ricky Hall | St.Catherine | Completed | Load_260519 | Rhodens Pen - 410 | Jul 13, 2026 9:25am | Jul 13, 2026 9:25am | Jul 13, 2026 10:20am | Jul 13, 2026 10:20am | Jul 13, 2026 10:40am | Jul 13, 2026 10:55am | Jul 13, 2026 10:55am | Jul 13, 2026 10:55am |  |  | Fair | No | Clean and reconnect 3W service at pothead use 3 pen union 115/115/230
Outage | J.E.26.07.14441 | C001853284 | Moses Elliston | St.Catherine | Completed | Load_263562 | New Michelton - 210 | Jul 13, 2026 9:25am | Jul 13, 2026 9:25am | Jul 13, 2026 11:27am | Jul 13, 2026 11:27am | Jul 13, 2026 11:27am | Jul 13, 2026 11:28am | Jul 13, 2026 11:28am | Jul 13, 2026 11:28am |  |  | Fair | No | Credit added to prepaid account.
Non-Outage | J.E.26.01.26707 | C001853268 | Dwain Samuels | Hanover | Completed | Load_246147 | Orange Bay - 310 | Jul 13, 2026 9:22am | Jul 13, 2026 9:24am | Jul 13, 2026 10:21am | Jul 14, 2026 12:20pm | Jul 14, 2026 12:20pm | Jul 14, 2026 12:23pm | Jul 14, 2026 12:23pm | Jul 14, 2026 12:23pm |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.01.26845 | C001853261 | Dwain Samuels | Westmoreland | Completed | Load_292403 | Paradise - 310 | Jul 13, 2026 9:21am | Jul 13, 2026 9:24am | Jul 13, 2026 10:21am | Jul 13, 2026 11:14am | Jul 13, 2026 11:14am | Jul 13, 2026 11:15am | Jul 13, 2026 11:16am | Jul 13, 2026 11:16am |  |  | Fair | No | Need proper contact and directions called and got no answer
Non-Outage | J.E.26.01.26864 | C001853262 | Dwain Samuels | Hanover | Completed | Load_265619 | Paradise - 210 | Jul 13, 2026 9:21am | Jul 13, 2026 9:24am | Jul 13, 2026 10:21am | Jul 13, 2026 11:39am | Jul 13, 2026 11:39am | Jul 13, 2026 11:39am | Jul 13, 2026 11:42am | Jul 13, 2026 11:42am |  |  | Fair | No | Found working okay. Voltage check 114-116-230
Non-Outage | J.E.26.01.26886 | C001853263 | Dwain Samuels | Westmoreland | Completed | Load_256923 | Paradise - 110 | Jul 13, 2026 9:21am | Jul 13, 2026 9:24am | Jul 13, 2026 10:21am | Jul 13, 2026 12:12pm | Jul 13, 2026 12:12pm | Jul 13, 2026 12:18pm | Jul 13, 2026 12:18pm | Jul 13, 2026 12:18pm |  |  | Fair | No | Customer complained is of high light bills
Non-Outage | J.E.26.01.26901 | C001853264 | Dwain Samuels | Westmoreland | Completed | Load_241486 | Paradise - 210 | Jul 13, 2026 9:21am | Jul 13, 2026 9:24am | Jul 13, 2026 10:21am | Jul 13, 2026 11:20am | Jul 13, 2026 11:20am | Jul 13, 2026 11:26am | Jul 13, 2026 11:27am | Jul 13, 2026 11:27am |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.01.26637 | C001853256 | Dwain Samuels | Westmoreland | Completed | Load_301650 | Paradise - 110 | Jul 13, 2026 9:20am | Jul 13, 2026 9:25am | Jul 13, 2026 10:21am | Jul 13, 2026 10:22am | Jul 13, 2026 10:23am | Jul 13, 2026 10:28am | Jul 13, 2026 10:29am | Jul 13, 2026 10:29am |  |  | Fair | No | Called and customer said supply was restored
Non-Outage | J.E.26.01.26649 | C001853255 | Dwain Samuels | Westmoreland | Completed | Load_292066 | Orange Bay - 310 | Jul 13, 2026 9:20am | Jul 13, 2026 9:25am | Jul 13, 2026 10:21am | Jul 14, 2026 12:47pm | Jul 14, 2026 12:47pm | Jul 14, 2026 1:00pm | Jul 14, 2026 1:01pm | Jul 14, 2026 1:01pm |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.01.26653 | C001853254 | Dwain Samuels | Hanover | Completed | Load_257353 | Orange Bay - 310 | Jul 13, 2026 9:20am | Jul 13, 2026 9:25am | Jul 13, 2026 10:21am | Jul 14, 2026 9:49am | Jul 14, 2026 9:49am | Jul 14, 2026 9:52am | Jul 14, 2026 9:53am | Jul 14, 2026 9:53am |  |  | Fair | No | Found working okay. Voltage check 119
Non-Outage | J.E.26.01.26709 | C001853260 | Dwain Samuels | Westmoreland | Completed | Load_266123 | Paradise - 210 | Jul 13, 2026 9:20am | Jul 13, 2026 9:25am | Jul 13, 2026 10:21am | Jul 13, 2026 11:07am | Jul 13, 2026 11:08am | Jul 13, 2026 11:11am | Jul 13, 2026 11:11am | Jul 13, 2026 11:11am |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.01.26782 | C001853258 | Dwain Samuels | Hanover | Completed | Load_238992 | Orange Bay - 310 | Jul 13, 2026 9:20am | Jul 13, 2026 9:25am | Jul 13, 2026 10:21am | Jul 14, 2026 9:35am | Jul 14, 2026 9:35am | Jul 14, 2026 9:46am | Jul 14, 2026 9:46am | Jul 14, 2026 9:46am |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.01.26834 | C001853259 | Dwain Samuels | Westmoreland | Completed | Load_253394 | Orange Bay - 310 | Jul 13, 2026 9:20am | Jul 13, 2026 9:25am | Jul 13, 2026 10:21am | Jul 14, 2026 12:39pm | Jul 14, 2026 12:39pm | Jul 14, 2026 12:42pm | Jul 14, 2026 12:42pm | Jul 14, 2026 12:42pm |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.01.26372 | C001853247 | Dwain Samuels | Hanover | Completed | Load_263899 | Orange Bay - 310 | Jul 13, 2026 9:19am | Jul 13, 2026 9:25am | Jul 13, 2026 10:21am | Jul 14, 2026 12:24pm | Jul 14, 2026 12:24pm | Jul 14, 2026 12:30pm | Jul 14, 2026 12:33pm | Jul 14, 2026 12:33pm |  |  | Fair | No | Corrosion found at 3 wire pole. Voltage check 101-100-201. Corrosion clear use 3 one bolt clamp 113-114-227
Non-Outage | J.E.26.01.26576 | C001853249 | Dwain Samuels | Westmoreland | Completed | Load_556870 | Paradise - 210 | Jul 13, 2026 9:19am | Jul 13, 2026 9:25am | Jul 13, 2026 10:21am | Jul 13, 2026 11:50am | Jul 13, 2026 11:55am | Jul 13, 2026 12:10pm | Jul 13, 2026 12:12pm | Jul 13, 2026 12:12pm |  |  | Fair | No | Found working okay. Voltage check 117-117-234. Customer has internal problems
Non-Outage | J.E.26.01.26590 | C001853250 | Dwain Samuels | Westmoreland | Completed | Load_249211 | Paradise - 110 | Jul 13, 2026 9:19am | Jul 13, 2026 9:25am | Jul 13, 2026 10:21am | Jul 13, 2026 10:34am | Jul 13, 2026 10:56am | Jul 13, 2026 11:03am | Jul 13, 2026 11:04am | Jul 13, 2026 11:04am |  |  | Fair | No | Meter room close cannot access area
Non-Outage | J.E.26.01.26594 | C001853251 | Dwain Samuels | Hanover | Completed | Load_246407 | Orange Bay - 310 | Jul 13, 2026 9:19am | Jul 13, 2026 9:25am | Jul 13, 2026 10:21am | Jul 14, 2026 11:17am | Jul 14, 2026 11:17am | Jul 14, 2026 11:22am | Jul 14, 2026 11:23am | Jul 14, 2026 11:23am |  |  | Fair | No | Found working okay. Voltage check 114-114-228
Non-Outage | J.E.26.01.26611 | C001853252 | Dwain Samuels | Hanover | Completed | Load_259364 | Orange Bay - 310 | Jul 13, 2026 9:19am | Jul 13, 2026 9:25am | Jul 13, 2026 10:21am | Jul 14, 2026 9:59am | Jul 14, 2026 10:34am | Jul 14, 2026 10:37am | Jul 14, 2026 10:39am | Jul 14, 2026 10:39am |  |  | Fair | No | No one lives at the premises. House was damaged from hurricane
Non-Outage | J.E.26.01.26622 | C001853253 | Dwain Samuels | Westmoreland | Completed | Load_260069 | Paradise - 310 | Jul 13, 2026 9:19am | Jul 13, 2026 9:25am | Jul 13, 2026 10:21am | Jul 13, 2026 12:27pm | Jul 13, 2026 12:27pm | Jul 13, 2026 12:30pm | Jul 13, 2026 12:31pm | Jul 13, 2026 12:31pm |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.01.26259 | C001853245 | Dwain Samuels | Hanover | Completed | Load_249606 | Orange Bay - 310 | Jul 13, 2026 9:18am | Jul 13, 2026 9:25am | Jul 13, 2026 10:21am | Jul 14, 2026 10:44am | Jul 14, 2026 10:57am | Jul 14, 2026 11:14am | Jul 14, 2026 11:16am | Jul 14, 2026 11:16am |  |  | Fair | No | Corrosion found at one 3 wire pole. Corrosion clear use 3 one bolt clamp. Voltage check 114-115-229
Non-Outage | J.E.26.01.26563 | C001853246 | Dwain Samuels | Westmoreland | Completed | Load_292843 | Paradise - 110 | Jul 13, 2026 9:18am | Jul 13, 2026 9:25am | Jul 13, 2026 10:21am | Jul 13, 2026 12:39pm | Jul 13, 2026 12:39pm | Jul 13, 2026 12:46pm | Jul 13, 2026 12:46pm | Jul 13, 2026 12:46pm |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.07.14390 | C001853232 | Dwain Samuels | null | Completed | null | null | Jul 13, 2026 9:16am | Jul 13, 2026 9:17am | Jul 13, 2026 9:23am | Jul 13, 2026 12:52pm | Jul 13, 2026 12:59pm | Jul 13, 2026 1:04pm | Jul 13, 2026 1:05pm | Jul 13, 2026 1:05pm |  |  | Fair | No | Meter damaged from Mellisa . Meter has no display
Outage | J.E.26.07.14374 | C001853231 | Dean Smith | Hanover | Completed | Load_250522 | Orange Bay - 310 | Jul 13, 2026 9:15am | Jul 13, 2026 9:43am | Jul 13, 2026 10:20am | Jul 13, 2026 10:20am | Jul 13, 2026 11:05am | Jul 13, 2026 11:05am | Jul 13, 2026 11:11am | Jul 13, 2026 11:11am |  |  | EarthMovement | No | Removed broken tree limb from primary conductor. Replace 8amp junction fuse. Pole number n/a.
Outage | J.E.26.07.14331 | C001853230 | Lancelot Brown | Hanover | Completed | Load_260507 | Orange Bay - 310 | Jul 13, 2026 9:14am | Jul 13, 2026 9:15am | Jul 13, 2026 10:11am | Jul 13, 2026 10:11am | Jul 13, 2026 10:43am | Jul 13, 2026 11:02am | Jul 13, 2026 11:03am | Jul 13, 2026 11:03am |  |  | Fair | No | Found junction fuse blown patroll found nothing replace 1-15amps junction at pole number 212169 supply restore
Non-Outage | J.E.26.07.14434 | C001853229 | Royston Montague | St.Catherine | Completed | Load_256045 | Tredegar - 510 | Jul 13, 2026 9:13am | Jul 13, 2026 9:14am | Jul 13, 2026 9:20am | Jul 13, 2026 10:14am | Jul 13, 2026 11:04am | Jul 13, 2026 11:24am | Jul 13, 2026 11:25am | Jul 13, 2026 11:25am |  |  | Fair | No | Damage twisted wire, mid span connection unable to use ladder to change same, voltage found 115v bucket truck required.
Non-Outage | J.E.26.07.10879 | C001853218 | Christopher Edwards | KSAN | Completed | Load_257052 | Constant Spring - 410 | Jul 13, 2026 9:12am | Jul 13, 2026 9:15am | Jul 13, 2026 9:50am | Jul 13, 2026 10:01am | Jul 13, 2026 10:01am | Jul 13, 2026 11:03am | Jul 13, 2026 11:04am | Jul 13, 2026 11:04am | BangingWires |  | Fair | No | Related to illegal connections that was removed off open secondary that was causing wire to bang
Outage | J.E.26.07.14431 | C001853216 | Edward Royal | KSAN | Completed | Load_293203 | Washington Blvd - 710 | Jul 13, 2026 9:09am | Jul 14, 2026 8:29am | Jul 14, 2026 10:35am | Jul 14, 2026 10:35am | Jul 14, 2026 11:42am | Jul 14, 2026 11:55am | Jul 14, 2026 11:55am | Jul 14, 2026 11:55am |  |  | Fair | No | Meter not responding need to be check reffered to field service box #YP03915 pole#0114964
Outage | J.E.26.07.14392 | C001853208 | Kemark Slue | St.Catherine | Completed | Load_238151 | Twickenham - 310 | Jul 13, 2026 9:07am | Jul 13, 2026 9:07am | Jul 13, 2026 2:01pm | Jul 13, 2026 2:20pm | Jul 13, 2026 2:20pm | Jul 13, 2026 11:28am | Jul 13, 2026 2:21pm | Jul 13, 2026 2:21pm |  |  | Fair | No | Upon arrival at the location the crew discovered that the customer is unable to add credit to CIU, please refer to Field service to assist asap.
Outage | J.E.26.07.14422 | C001853207 | Kemark Slue | St.Catherine | Completed | Load_247477 | Tredegar - 410 | Jul 13, 2026 9:07am | Jul 13, 2026 9:07am | Jul 13, 2026 11:44am | Jul 13, 2026 2:21pm | Jul 13, 2026 2:21pm | Jul 13, 2026 12:00pm | Jul 13, 2026 2:26pm | Jul 13, 2026 2:26pm |  |  | Fair | No | Upon arrival at the location the crew is assuming the labeling for the meter socket is incorrect and the meter is installed in the wrong socket or there’s a burnt off joint on the load side as the meter that corresponds with the given account is on and left a voltage reading of 120,120,240V, but customers is still without supply, customer was advised to contact an licensed electrician to effectively carry out repairs.
Non-Outage | J.E.26.07.13023 | C001853205 | Andrae Dawkins | St.James | Completed | Load_292067 | Bogue - 610 | Jul 13, 2026 9:04am | Jul 13, 2026 9:04am | Jul 13, 2026 1:38pm | Jul 13, 2026 4:16pm | Jul 13, 2026 4:16pm | Jul 13, 2026 3:24pm | Jul 13, 2026 4:19pm | Jul 13, 2026 4:19pm |  |  | Rains | No | Found customer meter socket defective advised customer to get an electrician
Non-Outage | J.E.26.07.11226 | C001853197 | Andrae Dawkins | St.James | Completed | Load_257601 | Bogue - 610 | Jul 13, 2026 9:02am | Jul 13, 2026 9:02am | Jul 13, 2026 1:35pm | Jul 13, 2026 1:57pm | Jul 13, 2026 3:36pm | Jul 13, 2026 2:14pm | Jul 13, 2026 3:41pm | Jul 13, 2026 3:41pm |  |  | Fair | No | Check and found okay customer said that the problem was already resolved
Non-Outage | J.E.26.07.10824 | C001853186 | Jermaine Williams | null | Completed | null | null | Jul 13, 2026 8:56am | Jul 13, 2026 9:08am | Jul 13, 2026 1:19pm | Jul 13, 2026 1:19pm | Jul 14, 2026 7:37am | Jul 14, 2026 7:37am | Jul 14, 2026 7:38am | Jul 14, 2026 7:38am | BrokenWire |  | Fair | No | Premises found ok.
Non-Outage | J.E.26.07.11795 | C001853185 | Jermaine Williams | Clarendon | Completed | Load_256095 | Monymusk - 410 | Jul 13, 2026 8:56am | Jul 13, 2026 8:56am | Jul 13, 2026 10:38am | Jul 13, 2026 10:39am | Jul 13, 2026 11:17am | Jul 13, 2026 11:37am | Jul 13, 2026 11:35am | Jul 13, 2026 11:35am | BrokenWire |  | SevereWind | No | Isolate 50kva xfmr to splice and retention two spans broken #4 bare copper.
Non-Outage | J.E.26.07.14406 | C001853184 | Dean Smith | Hanover | Completed | Load_575279 | Orange Bay - 310 | Jul 13, 2026 8:55am | Jul 13, 2026 8:55am | Jul 13, 2026 12:16pm | Jul 13, 2026 12:16pm | Jul 13, 2026 12:16pm | Jul 13, 2026 12:27pm | Jul 13, 2026 12:28pm | Jul 13, 2026 12:28pm |  |  | Fair | No | House number found , unable to locate meter that correspond with lot number.
Non-Outage | J.E.26.07.05359 | C001853183 | Dean Smith | Hanover | Completed | Load_574024 | Bogue - 510 | Jul 13, 2026 8:54am | Jul 13, 2026 8:55am | Jul 13, 2026 12:29pm | Jul 13, 2026 12:29pm | Jul 13, 2026 12:29pm | Jul 13, 2026 12:29pm | Jul 13, 2026 12:29pm | Jul 13, 2026 12:29pm |  |  | Fair | No | Unable to locate
Non-Outage | J.E.26.07.13676 | C001853182 | Dean Smith | Hanover | Completed | Load_575279 | Orange Bay - 310 | Jul 13, 2026 8:53am | Jul 13, 2026 8:54am | Jul 13, 2026 12:28pm | Jul 13, 2026 12:28pm | Jul 13, 2026 12:28pm | Jul 13, 2026 12:28pm | Jul 13, 2026 12:29pm | Jul 13, 2026 12:29pm |  |  | Fair | No | Unable to locate
Non-Outage | J.E.26.07.14381 | C001853178 | Edward Royal | KSAS | Completed | Load_259281 | Duhaney - 310 | Jul 13, 2026 8:52am | Jul 13, 2026 9:16am | Jul 13, 2026 10:08am | Jul 13, 2026 10:08am | Jul 13, 2026 10:08am | Jul 13, 2026 10:09am | Jul 13, 2026 10:09am | Jul 13, 2026 10:09am |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.07.13593 | C001853177 | Dean Smith | St.James | Completed | Load_257440 | Bogue - 510 | Jul 13, 2026 8:52am | Jul 13, 2026 8:52am | Jul 13, 2026 8:56am | Jul 13, 2026 9:47am | Jul 13, 2026 10:19am | Jul 13, 2026 10:20am | Jul 13, 2026 10:20am | Jul 13, 2026 10:20am |  |  | Fair | No | Check and found ok
Non-Outage | J.E.26.07.09650 | C001853176 | Romeo Brissett | St.James | Completed | Load_557023 | Bogue - 310 | Jul 13, 2026 8:50am | Jul 13, 2026 8:51am | Jul 13, 2026 11:08am | Jul 13, 2026 11:08am | Jul 13, 2026 11:34am | Jul 13, 2026 11:50am | Jul 13, 2026 11:52am | Jul 13, 2026 11:52am | BrokenWire |  | Fair | No | Unable to locate customer, phone ring to voicemail
Non-Outage | J.E.26.07.10892 | C001853175 | Romeo Brissett | St.James | Completed | Load_244921 | Bogue - 310 | Jul 13, 2026 8:50am | Jul 13, 2026 8:50am | Jul 13, 2026 11:53am | Jul 13, 2026 11:53am | Jul 13, 2026 12:34pm | Jul 13, 2026 12:50pm | Jul 13, 2026 12:53pm | Jul 13, 2026 12:53pm | BrokenWire |  | Fair | No | Check and found internal fault customer stanchion
Non-Outage | J.E.26.07.12711 | C001853172 | Junior Scarlett | St.James | Completed | Load_239243 | Queens Drive - 710 | Jul 13, 2026 8:48am | Jul 13, 2026 8:49am | Jul 13, 2026 8:53am | Jul 13, 2026 1:33pm | Jul 13, 2026 1:59pm | Jul 13, 2026 1:06pm | Jul 13, 2026 2:07pm | Jul 13, 2026 2:07pm |  |  | Fair | No | Check and found okVoltage found 115v 115v 230v
Non-Outage | J.E.26.07.12720 | C001853173 | Junior Scarlett | St.James | Completed | Load_257668 | Queens Drive - 710 | Jul 13, 2026 8:48am | Jul 13, 2026 8:48am | Jul 13, 2026 8:53am | Jul 13, 2026 2:51pm | Jul 13, 2026 4:09pm | Jul 13, 2026 4:09am | Jul 13, 2026 4:14pm | Jul 13, 2026 4:14pm |  |  | Fair | No | Install two clampVoltage found 115v 101v 207v Voltage leave 115v 15v 230v
Non-Outage | J.E.26.07.13835 | C001853168 | Stephen Taylor | St.Thomas | Completed | Load_267393 | Good Year - 210 | Jul 13, 2026 8:45am | Jul 13, 2026 8:47am | Jul 13, 2026 10:39am | Jul 13, 2026 10:39am | Jul 13, 2026 10:45am | Jul 13, 2026 10:49am | Jul 13, 2026 10:49am | Jul 13, 2026 10:49am |  |  | Fair | No | Customer is single phase from the rami box need filed service technician to restore power to customer
Non-Outage | J.E.26.07.14149 | C001853167 | Stephen Taylor | St.Thomas | Completed | Load_241389 | Lysson - 410 | Jul 13, 2026 8:45am | Jul 13, 2026 8:47am | Jul 13, 2026 8:55pm | Jul 13, 2026 8:55pm | Jul 13, 2026 8:55pm | Jul 13, 2026 8:55pm | Jul 13, 2026 8:56pm | Jul 13, 2026 8:56pm |  |  | Fair | No | Check with customer and customer said power is back now and okay
Non-Outage | J.E.26.07.14212 | C001853169 | Stephen Taylor | St.Thomas | Completed | Load_253956 | Good Year - 210 | Jul 13, 2026 8:45am | Jul 13, 2026 8:47am | Jul 13, 2026 1:19pm | Jul 13, 2026 1:19pm | Jul 13, 2026 1:19pm | Jul 13, 2026 1:19pm | Jul 13, 2026 1:20pm | Jul 13, 2026 1:20pm |  |  | Fair | No | Need more information a lot of call to customer no one answered the phone
Outage | J.E.26.07.14290 | C001853165 | Barrington Brown | St.James | Completed | Load_263681 | Queens Drive - 710 | Jul 13, 2026 8:45am | Jul 13, 2026 3:18pm | Jul 13, 2026 3:50pm | Jul 13, 2026 3:50pm | Jul 13, 2026 4:35pm | Jul 13, 2026 4:56pm | Jul 13, 2026 5:19pm | Jul 13, 2026 5:19pm |  |  | Fair | No | Checked and found ok
Outage | J.E.26.07.14357 | C001853164 | Romeo Brissett | St.James | Completed | Load_567828 | Bogue - 610 | Jul 13, 2026 8:45am | Jul 13, 2026 3:26pm | Jul 13, 2026 3:43pm | Jul 13, 2026 3:43pm | Jul 13, 2026 4:30pm | Jul 13, 2026 4:48pm | Jul 13, 2026 5:01pm | Jul 13, 2026 5:01pm |  |  | Fair | No | Check and found no supply coming from the rammy box. Please send to field service.
Non-Outage | J.E.26.07.14304 | C001853163 | Stephen Taylor | St.Thomas | Completed | Load_256512 | Good Year - 110 | Jul 13, 2026 8:44am | Jul 13, 2026 8:47am | Jul 13, 2026 1:21pm | Jul 13, 2026 3:15pm | Jul 13, 2026 3:15pm | Jul 13, 2026 3:15pm | Jul 13, 2026 3:16pm | Jul 13, 2026 3:16pm |  |  | Fair | No | Clean up single phase customer is now okay
Non-Outage | J.E.26.07.14390 | C001853161 | Oshane Warren | null | Completed | null | null | Jul 13, 2026 8:40am | Jul 13, 2026 8:41am | Jul 13, 2026 9:12am | Jul 13, 2026 9:12am | Jul 13, 2026 9:12am | Jul 13, 2026 9:13am | Jul 13, 2026 9:13am | Jul 13, 2026 9:13am |  |  | Fair | No | Unable to locate or contact customer
Outage | J.E.26.07.14388 | C001853160 | Elvis Trowers | KSAN | Completed | Load_264577 | Constant Spring - 210 | Jul 13, 2026 8:40am | Jul 13, 2026 8:51am | Jul 13, 2026 2:39pm | Jul 13, 2026 2:39pm | Jul 13, 2026 3:11pm | Jul 13, 2026 3:15pm | Jul 13, 2026 3:15pm | Jul 13, 2026 3:15pm |  |  | Fair | Yes | Premises not located and customer could not be contacted by telephone either after several calls, even though several voice messages was left.
Non-Outage | J.E.26.07.13030 | C001853158 | Junior Scarlett | St.James | Completed | Load_253530 | Queens Drive - 710 | Jul 13, 2026 8:36am | Jul 13, 2026 8:48am | Jul 13, 2026 8:53am | Jul 13, 2026 12:33pm | Jul 13, 2026 12:38pm | Jul 13, 2026 1:27pm | Jul 13, 2026 1:28pm | Jul 13, 2026 1:28pm |  |  | Fair | No | Install two clampVoltage found 114v 24v 114vVoltage leave 14v 114v 228vJob complete
Non-Outage | J.E.26.07.13093 | C001853157 | Junior Scarlett | St.James | Completed | Load_253530 | Queens Drive - 710 | Jul 13, 2026 8:36am | Jul 13, 2026 8:47am | Jul 13, 2026 8:53am | Jul 13, 2026 11:57am | Jul 13, 2026 11:57am | Jul 13, 2026 12:22pm | Jul 13, 2026 12:22pm | Jul 13, 2026 12:22pm |  |  | Fair | No | Install two clamp on potheadVoltage found 114v 22v 114vVoltage leave 114v 114v 228vJob complete
Non-Outage | J.E.26.07.13200 | C001853152 | Donald Cunningham | null | Completed | null | null | Jul 13, 2026 8:35am | Jul 13, 2026 8:36am | Jul 13, 2026 1:52pm | Jul 13, 2026 1:52pm | Jul 13, 2026 2:29pm | Jul 13, 2026 2:30pm | Jul 13, 2026 2:38pm | Jul 13, 2026 2:38pm |  |  | Fair | No | Internal issues customer advised
Non-Outage | J.E.26.07.14288 | C001853154 | Junior Scarlett | St.James | Completed | Load_263681 | Queens Drive - 710 | Jul 13, 2026 8:35am | Jul 13, 2026 8:41am | Jul 13, 2026 8:53am | Jul 13, 2026 10:25am | Jul 13, 2026 11:22am | Jul 13, 2026 11:21am | Jul 13, 2026 11:27am | Jul 13, 2026 11:27am |  |  | Fair | No | Corrosion at pole and pothead wire burn offWire burn off reattach wireInstall tow clamp on poleInstal 3 pen union on PotheadVoltage found 113v 67v 181vVoltage leave 113v 113v 226vJob complete
Non-Outage | J.E.26.07.14377 | C001853153 | Junior Scarlett | St.James | Completed | Load_248827 | Queens Drive - 710 | Jul 13, 2026 8:35am | Jul 13, 2026 8:40am | Jul 13, 2026 8:53am | Jul 13, 2026 8:58am | Jul 13, 2026 9:37am | Jul 13, 2026 10:19am | Jul 13, 2026 10:21am | Jul 13, 2026 10:21am |  |  | Fair | No | Improper metter socket wire Advise customer correct issueVoltage found 110v 111v 221vVoltage leave 110v 111v 221vUnable to complete until customer fix issue
Outage | J.E.26.07.14339 | C001853151 | Donald Cunningham | Portmore | Completed | Load_263652 | Naggo Head - 510 | Jul 13, 2026 8:33am | Jul 13, 2026 8:33am | Jul 13, 2026 11:49am | Jul 13, 2026 11:50am | Jul 13, 2026 11:59am | Jul 13, 2026 12:00pm | Jul 13, 2026 12:00pm | Jul 13, 2026 12:00pm |  |  | Fair | No | Supply restored
Outage | J.E.26.07.14340 | C001853148 | Richman Whyte | Westmoreland | Completed | Load_244638 | Paradise - 210 | Jul 13, 2026 8:31am | Jul 13, 2026 8:38am | Jul 13, 2026 10:55am | Jul 13, 2026 10:55am | Jul 13, 2026 10:55am | Jul 13, 2026 10:56am | Jul 13, 2026 10:57am | Jul 13, 2026 10:57am |  |  | Fair | No | Twenty five kva transformer burned need to change sand referral to maintenance
Non-Outage | J.E.26.07.12462 | C001853140 | Odaine Johnson | Clarendon | Completed | Load_245076 | Parnassus - 310 | Jul 13, 2026 8:30am | Jul 13, 2026 8:31am | Jul 13, 2026 10:09am | Jul 13, 2026 2:42pm | Jul 13, 2026 4:32pm | Jul 13, 2026 4:33pm | Jul 13, 2026 4:33pm | Jul 13, 2026 4:33pm |  |  | Fair | No | Unable to locate customer
Non-Outage | J.E.26.07.12764 | C001853146 | Jermaine Williams | Clarendon | Completed | Load_268157 | Parnassus - 210 | Jul 13, 2026 8:30am | Jul 13, 2026 11:10am | Jul 13, 2026 11:35am | Jul 13, 2026 11:35am | Jul 13, 2026 12:51pm | Jul 13, 2026 1:00pm | Jul 13, 2026 1:15pm | Jul 13, 2026 1:15pm |  |  | SevereWind | No | De energize and isolate three 100kva xfmr, Customer requested disconnection.
Non-Outage | J.E.26.07.12818 | C001853144 | Odaine Johnson | Clarendon | Completed | Load_256639 | Parnassus - 210 | Jul 13, 2026 8:30am | Jul 13, 2026 8:31am | Jul 13, 2026 10:09am | Jul 14, 2026 9:22am | Jul 14, 2026 9:41am | Jul 14, 2026 9:55am | Jul 14, 2026 9:56am | Jul 14, 2026 9:56am |  |  | Fair | No | Corroded phase found at pole remade connection using 1 one bolt clamp voltage reading 118/116/234 volts
Non-Outage | J.E.26.07.12892 | C001853145 | Odaine Johnson | Clarendon | Completed | Load_257855 | Monymusk - 210 | Jul 13, 2026 8:30am | Jul 13, 2026 8:31am | Jul 13, 2026 10:09am | Jul 13, 2026 1:02pm | Jul 13, 2026 1:02pm | Jul 13, 2026 1:04am | Jul 13, 2026 1:06pm | Jul 13, 2026 1:06pm |  |  | Fair | No | Damaged service wire causing on and off supply, services wire was replaced and problem was fixed Voltage reading before A115 B0 AB115Voltage reading after A114 B116 AB230
Non-Outage | J.E.26.07.13011 | C001853143 | Odaine Johnson | Clarendon | Completed | Load_247305 | Parnassus - 210 | Jul 13, 2026 8:30am | Jul 13, 2026 8:31am | Jul 13, 2026 10:09am | Jul 13, 2026 2:41pm | Jul 13, 2026 2:41pm | Jul 13, 2026 2:41pm | Jul 13, 2026 2:42pm | Jul 13, 2026 2:42pm |  |  | Fair | No | Contacted customer and customer stated that the issue was resolved already
Non-Outage | J.E.26.07.13026 | C001853142 | Odaine Johnson | Clarendon | Completed | Load_256749 | Monymusk - 410 | Jul 13, 2026 8:30am | Jul 13, 2026 8:31am | Jul 13, 2026 10:09am | Jul 13, 2026 2:13pm | Jul 13, 2026 2:13pm | Jul 13, 2026 2:13pm | Jul 13, 2026 2:13pm | Jul 13, 2026 2:13pm |  |  | Fair | No | Premises found okay voltage reading 110/119/220 volts
Non-Outage | J.E.26.07.13193 | C001853141 | Odaine Johnson | Clarendon | Completed | Load_246032 | Monymusk - 410 | Jul 13, 2026 8:30am | Jul 13, 2026 8:31am | Jul 13, 2026 10:09am | Jul 13, 2026 1:17pm | Jul 13, 2026 1:17pm | Jul 13, 2026 1:18pm | Jul 13, 2026 1:18pm | Jul 13, 2026 1:18pm |  |  | Fair | No | Premises found okay customer said problem was resolved
Non-Outage | J.E.26.07.13713 | C001853138 | Odaine Johnson | Clarendon | Completed | Load_259676 | Monymusk - 210 | Jul 13, 2026 8:30am | Jul 13, 2026 8:31am | Jul 13, 2026 10:09am | Jul 13, 2026 11:21am | Jul 13, 2026 11:22am | Jul 13, 2026 11:22am | Jul 13, 2026 11:23am | Jul 13, 2026 11:23am |  |  | Fair | No | Burn off phase found at pole remade connection using 1 one bolt clamp voltage reading 118/116/234 volts
Non-Outage | J.E.26.07.14151 | C001853139 | Odaine Johnson | Clarendon | Completed | Load_243769 | Parnassus - 210 | Jul 13, 2026 8:30am | Jul 13, 2026 8:31am | Jul 13, 2026 10:09am | Jul 13, 2026 2:37pm | Jul 13, 2026 2:37pm | Jul 13, 2026 2:37pm | Jul 13, 2026 2:38pm | Jul 13, 2026 2:38pm |  |  | Fair | No | Try contact customer but no one answer and try to follow direction given and still did find location
Non-Outage | J.E.26.07.12484 | C001853137 | Roemello Brown | Trelawny | Completed | Load_261734 | Duncans - 210 | Jul 13, 2026 8:27am | Jul 13, 2026 8:27am | Jul 14, 2026 8:05am | Jul 14, 2026 8:10am | Jul 14, 2026 8:45am | Jul 14, 2026 8:46am | Jul 14, 2026 8:51am | Jul 14, 2026 8:51am |  |  | Fair | No | Premises found working okay Voltage found 116/117/233Voltage leave 116/117/233
Non-Outage | J.E.26.07.13238 | C001853136 | Roemello Brown | Trelawny | Completed | Load_556269 | Duncans - 210 | Jul 13, 2026 8:27am | Jul 13, 2026 8:28am | Jul 14, 2026 8:07am | Jul 14, 2026 9:39am | Jul 14, 2026 10:03am | Jul 14, 2026 10:03am | Jul 14, 2026 10:06am | Jul 14, 2026 10:06am |  |  | Fair | No | Premises found working okay Voltage found 114/114/228Voltage leave 114/114/228
Non-Outage | J.E.26.07.13766 | C001853133 | Roemello Brown | Trelawny | Completed | Load_241073 | Duncans - 210 | Jul 13, 2026 8:27am | Jul 14, 2026 8:31am | Jul 14, 2026 8:56am | Jul 14, 2026 8:56am | Jul 14, 2026 9:31am | Jul 14, 2026 9:31am | Jul 14, 2026 9:38am | Jul 14, 2026 9:38am |  |  | Fair | No | Meter burn needs please send field service team to have meter change please Voltage found 123/123/246Voltage leave 123/123/246
Non-Outage | J.E.26.07.14052 | C001853134 | Roemello Brown | Trelawny | Completed | Load_302800 | Duncans - 110 | Jul 13, 2026 8:27am | Jul 13, 2026 8:29am | Jul 13, 2026 10:22am | Jul 13, 2026 3:09pm | Jul 13, 2026 3:26pm | Jul 13, 2026 3:28pm | Jul 13, 2026 4:34pm | Jul 13, 2026 4:34pm |  |  | Fair | No | Premises found working okay Voltage found 109/108/217Voltage leave 109/108/217
Non-Outage | J.E.26.07.14125 | C001853135 | Roemello Brown | Trelawny | Completed | Load_267205 | Duncans - 210 | Jul 13, 2026 8:27am | Jul 13, 2026 8:31am | Jul 13, 2026 10:31am | Jul 13, 2026 12:44pm | Jul 13, 2026 3:02pm | Jul 13, 2026 3:02pm | Jul 13, 2026 3:08pm | Jul 13, 2026 3:08pm |  |  | Fair | No | Customers are having high voltage please send this to the emergency team problem coming from transformer drop lead Voltage found 121/104/225Voltage leave 121/104/225
Non-Outage | J.E.26.07.14155 | C001853132 | Roemello Brown | Trelawny | Completed | Load_240708 | Duncans - 210 | Jul 13, 2026 8:26am | Jul 13, 2026 8:32am | Jul 13, 2026 10:29am | Jul 13, 2026 10:31am | Jul 13, 2026 10:45am | Jul 13, 2026 11:52am | Jul 13, 2026 12:44pm | Jul 13, 2026 12:44pm |  |  | Fair | No | Corroded neutral clamp have it change Voltage found 113/109/222Voltage leave 113/111/224
Non-Outage | J.E.26.07.14230 | C001853131 | Roemello Brown | Trelawny | Completed | Load_247464 | Duncans - 210 | Jul 13, 2026 8:26am | Jul 13, 2026 8:31am | Jul 14, 2026 9:39am | Jul 14, 2026 10:11am | Jul 14, 2026 12:33pm | Jul 14, 2026 12:34pm | Jul 14, 2026 12:54pm | Jul 14, 2026 12:54pm |  |  | Fair | No | Premises found working okay problem not from jps side Voltage found 115/115/231Voltage leave 115/115/231
Non-Outage | J.E.26.07.08559 | C001853130 | Jermaine Williams | null | Completed | null | null | Jul 13, 2026 8:25am | Jul 13, 2026 8:25am | Jul 14, 2026 7:47am | Jul 14, 2026 7:47am | Jul 14, 2026 7:47am | Jul 14, 2026 7:47am | Jul 14, 2026 7:48am | Jul 14, 2026 7:48am |  |  | Fair | No | Premises found ok.
Non-Outage | J.E.26.07.11254 | C001853129 | Marlon Brown | Trelawny | Completed | Load_249132 | Martha Brae - 110 | Jul 13, 2026 8:23am | Jul 13, 2026 1:13pm | Jul 13, 2026 4:41pm | Jul 13, 2026 5:47pm | Jul 13, 2026 6:06pm | Jul 13, 2026 6:07pm | Jul 13, 2026 6:07pm | Jul 13, 2026 6:07pm |  |  | Fair | No | Customer not at home.
Non-Outage | J.E.26.07.12422 | C001853127 | Andre Williams | Trelawny | Completed | Load_555930 | Martha Brae - 210 | Jul 13, 2026 8:23am | Jul 13, 2026 1:15pm | Jul 13, 2026 1:29pm | Jul 13, 2026 1:34pm | Jul 13, 2026 1:53pm | Jul 13, 2026 2:16pm | Jul 13, 2026 2:19pm | Jul 13, 2026 2:19pm |  |  | Fair | No | Clean corroded joints at Jps pole on customer #6 wire. Voltage before 90+107=197 voltage fire 110+110=220
Non-Outage | J.E.26.07.12895 | C001853128 | Andre Williams | Trelawny | Completed | Load_555893 | Martha Brae - 210 | Jul 13, 2026 8:23am | Jul 13, 2026 1:15pm | Jul 13, 2026 1:29pm | Jul 13, 2026 2:20pm | Jul 13, 2026 2:46pm | Jul 13, 2026 2:47pm | Jul 13, 2026 2:47pm | Jul 13, 2026 2:47pm |  |  | Fair | No | Premises ok and with supply confirm by visit
Non-Outage | J.E.26.07.13843 | C001853125 | Marlon Brown | Trelawny | Completed | Load_294510 | Martha Brae - 110 | Jul 13, 2026 8:22am | Jul 13, 2026 3:32pm | Jul 13, 2026 5:25pm | Jul 13, 2026 5:26pm | Jul 13, 2026 5:26pm | Jul 13, 2026 5:46pm | Jul 13, 2026 5:47pm | Jul 13, 2026 5:47pm |  |  | Fair | No | Check and found ok at pothead and pole. Voltage found 116/116=232vVoltage leaving at pothead 116/116=232v.
Outage | J.E.26.07.14368 | C001853120 | Horace Malcolm | St.James | Completed | Load_261979 | Queens Drive - 310 | Jul 13, 2026 8:20am | Jul 13, 2026 8:21am | Jul 13, 2026 9:30am | Jul 13, 2026 9:30am | Jul 13, 2026 10:38am | Jul 13, 2026 10:49am | Jul 13, 2026 10:49am | Jul 13, 2026 10:49am |  |  | Fair | No | Check and found customer have internal issues incoming voltage from jps side 117-117-235 outgoing from meter to customer 117-116-234
Outage | J.E.26.07.14372 | C001853118 | Kenroy Dale | Manchester | Completed | Load_255268 | Porus - 310 | Jul 13, 2026 8:18am | Jul 13, 2026 8:23am | Jul 13, 2026 10:05am | Jul 13, 2026 10:05am | Jul 13, 2026 11:54am | Jul 13, 2026 11:59am | Jul 13, 2026 12:00pm | Jul 13, 2026 12:00pm |  |  | Fair | No | 25 kva transformer found trip. Line patrol nothing found, transformer was reset and area now with supply
Non-Outage | J.E.26.07.14214 | C001853116 | Odeanie Davis | KSAN | Completed | Load_244392 | Washington Blvd - 710 | Jul 13, 2026 8:16am | Jul 13, 2026 8:19am | Jul 13, 2026 9:12am | Jul 13, 2026 11:35am | Jul 13, 2026 11:35am | Jul 13, 2026 11:37am | Jul 13, 2026 11:37am | Jul 13, 2026 11:37am |  |  | Fair | No | 111v/0V at location from rammi box, rammi team needed, customer currently getting single phase, othe customer’s in the area having the same issue
Outage | J.E.26.07.14360 | C001853114 | Dwayne Samuels | Trelawny | Completed | Load_302923 | Greenwood - 110 | Jul 13, 2026 8:12am | Jul 13, 2026 8:30am | Jul 13, 2026 8:56am | Jul 13, 2026 8:56am | Jul 13, 2026 11:51am | Jul 13, 2026 12:32pm | Jul 13, 2026 12:34pm | Jul 13, 2026 12:34pm | BrokenWire |  | Fair | No | Reconnect customer service wire to system used 3 obc at same voltage left is 114v 116v 230
Non-Outage | J.E.26.07.14024 | C001853113 | Horace Malcolm | null | Completed | null | null | Jul 13, 2026 8:08am | Jul 13, 2026 8:09am | Jul 13, 2026 8:20am | Jul 13, 2026 8:20am | Jul 13, 2026 9:22am | Jul 13, 2026 9:23am | Jul 13, 2026 9:23am | Jul 13, 2026 9:23am |  |  | Fair | No | Checked and found premises ok supply restored
Non-Outage | J.E.26.07.12237 | C001853111 | Elvis Trowers | KSAN | Completed | Load_258089 | Constant Spring - 210 | Jul 13, 2026 8:07am | Jul 13, 2026 8:07am | Jul 13, 2026 9:19am | Jul 13, 2026 9:19am | Jul 13, 2026 9:54am | Jul 13, 2026 10:11am | Jul 13, 2026 10:11am | Jul 13, 2026 10:11am |  |  | Fair | Yes | Premises found closed upon arrival and when customer was contacted she said that she was expecting to be at home but she had was to leave for work.
Non-Outage | J.E.26.07.12554 | C001853110 | Fredrick Hamilton | KSAN | Completed | Load_264129 | Constant Spring - 210 | Jul 13, 2026 8:07am | Jul 14, 2026 8:10am | Jul 14, 2026 8:15am | Jul 14, 2026 1:50pm | Jul 14, 2026 1:50pm | Jul 14, 2026 1:52pm | Jul 14, 2026 1:52pm | Jul 14, 2026 1:52pm |  |  | Fair | No | Premises checked and found ok no JPS issue detected 238v/119v/118v obtained Bushing required in area
Non-Outage | J.E.26.07.10579 | C001853107 | Fredrick Hamilton | KSAS | Completed | Load_246230 | Up Park Camp - 410 | Jul 13, 2026 8:06am | Jul 13, 2026 8:06am | Jul 13, 2026 8:09am | Jul 13, 2026 12:07pm | Jul 13, 2026 12:07pm | Jul 13, 2026 12:08pm | Jul 13, 2026 12:08pm | Jul 13, 2026 12:08pm |  |  | Fair | No | Customer contacted and stated that power was restored fully previously Premises is ok
Non-Outage | J.E.26.07.10673 | C001853109 | Fredrick Hamilton | KSAN | Completed | Load_249262 | Hope - 510 | Jul 13, 2026 8:06am | Jul 13, 2026 8:06am | Jul 13, 2026 8:09am | Jul 13, 2026 8:24am | Jul 13, 2026 8:24am | Jul 13, 2026 8:25am | Jul 13, 2026 8:25am | Jul 13, 2026 8:25am | Fire |  | Fair | No | Customer contacted and stated that premises is ok no loss of powerPremises ok
Non-Outage | J.E.26.07.10691 | C001853106 | Fredrick Hamilton | KSAS | Completed | Load_246230 | Up Park Camp - 410 | Jul 13, 2026 8:06am | Jul 13, 2026 8:06am | Jul 13, 2026 8:09am | Jul 13, 2026 12:08pm | Jul 13, 2026 12:08pm | Jul 13, 2026 12:09pm | Jul 13, 2026 12:10pm | Jul 13, 2026 12:10pm |  |  | Fair | No | Customer contacted and stated power was restored fully previously Premises is ok
Non-Outage | J.E.26.07.10788 | C001853108 | Fredrick Hamilton | KSAS | Completed | Load_263693 | Duhaney - 310 | Jul 13, 2026 8:06am | Jul 13, 2026 8:06am | Jul 13, 2026 8:09am | Jul 13, 2026 9:10am | Jul 13, 2026 9:32am | Jul 13, 2026 9:43am | Jul 13, 2026 9:43am | Jul 13, 2026 9:43am |  |  | Fair | No | 235v/116v/117v obtained Defective meter at location recommend meter change Meter in single phase condition
Non-Outage | J.E.26.07.10926 | C001853105 | Fredrick Hamilton | KSAS | Completed | Load_246230 | Up Park Camp - 410 | Jul 13, 2026 8:06am | Jul 13, 2026 8:06am | Jul 13, 2026 8:09am | Jul 13, 2026 12:10pm | Jul 13, 2026 12:10pm | Jul 13, 2026 12:12pm | Jul 13, 2026 12:12pm | Jul 13, 2026 12:12pm |  |  | EarthMovement | No | Customer contacted and stated power was restored fully previously Premises is ok
Non-Outage | J.E.26.07.10973 | C001853103 | Fredrick Hamilton | KSAN | Completed | Load_245677 | West Kings House - 210 | Jul 13, 2026 8:06am | Jul 13, 2026 8:06am | Jul 13, 2026 8:09am | Jul 13, 2026 10:13am | Jul 13, 2026 10:22am | Jul 13, 2026 10:26am | Jul 13, 2026 10:26am | Jul 13, 2026 10:26am |  |  | Fair | No | Power was restored fully to customer previously Premises is ok
Non-Outage | J.E.26.07.11190 | C001853104 | Fredrick Hamilton | KSAS | Completed | Load_246230 | Up Park Camp - 410 | Jul 13, 2026 8:06am | Jul 13, 2026 8:06am | Jul 13, 2026 8:09am | Jul 13, 2026 12:12pm | Jul 13, 2026 12:12pm | Jul 13, 2026 12:13pm | Jul 13, 2026 12:13pm | Jul 13, 2026 12:13pm |  |  | Fair | No | Customer contacted and stated power was restored fully previously Premises is ok
Non-Outage | J.E.26.07.11360 | C001853102 | Fredrick Hamilton | KSAN | Completed | Load_267043 | Washington Blvd - 410 | Jul 13, 2026 8:05am | Jul 13, 2026 8:06am | Jul 13, 2026 8:09am | Jul 13, 2026 10:05am | Jul 13, 2026 10:05am | Jul 13, 2026 10:07am | Jul 13, 2026 10:07am | Jul 13, 2026 10:07am |  |  | Fair | No | Multiple calls to customer went to voicemail
Non-Outage | J.E.26.07.13894 | C001853100 | Fredrick Hamilton | KSAN | Completed | Load_557436 | West Kings House - 310 | Jul 13, 2026 8:04am | Jul 13, 2026 8:06am | Jul 13, 2026 8:09am | Jul 13, 2026 10:55am | Jul 13, 2026 10:55am | Jul 13, 2026 10:56am | Jul 13, 2026 10:56am | Jul 13, 2026 10:56am |  |  | Fair | No | Customer contacted and stated power was restored fully previously Premises is ok
Non-Outage | J.E.26.07.14090 | C001853101 | Fredrick Hamilton | KSAS | Completed | Load_245377 | Up Park Camp - 410 | Jul 13, 2026 8:04am | Jul 13, 2026 8:06am | Jul 13, 2026 8:09am | Jul 13, 2026 10:57am | Jul 13, 2026 11:18am | Jul 13, 2026 11:25am | Jul 13, 2026 11:56am | Jul 13, 2026 11:56am |  |  | Fair | No | 238v/119v/117v obtained Meter #3019797 found burnt at location recommend meter changeAlso meter# 2342642 seen burnt and damage at location Burnt meter socket seen customer advised
Non-Outage | J.E.26.07.11834 | C001853092 | Royston Montague | St.Catherine | Completed | Load_250128 | Tredegar - 510 | Jul 13, 2026 8:03am | Jul 13, 2026 8:04am | Jul 13, 2026 9:16am | Jul 13, 2026 11:30am | Jul 13, 2026 11:50am | Jul 13, 2026 12:41pm | Jul 13, 2026 12:41pm | Jul 13, 2026 12:41pm |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.07.11956 | C001853099 | Odeanie Davis | KSAS | Completed | Load_291482 | Greenwich - 510 | Jul 13, 2026 8:03am | Jul 13, 2026 8:04am | Jul 13, 2026 9:13am | Jul 13, 2026 9:18am | Jul 13, 2026 9:18am | Jul 13, 2026 9:47am | Jul 13, 2026 9:47am | Jul 13, 2026 9:47am |  |  | Fair | No | 123v/20v at location from rammi box, rammi team needed, customer it currently getting a single phase at location.
Non-Outage | J.E.26.07.12079 | C001853096 | Odeanie Davis | KSAS | Completed | Load_240797 | Rockfort - 410 | Jul 13, 2026 8:03am | Jul 13, 2026 8:04am | Jul 13, 2026 12:56pm | Jul 13, 2026 2:00pm | Jul 13, 2026 2:02pm | Jul 13, 2026 2:25pm | Jul 13, 2026 2:13pm | Jul 13, 2026 2:13pm |  |  | Fair | No | 113v/113v & 227v at location, no power issues found. Premises found okay
Non-Outage | J.E.26.07.12512 | C001853082 | Royston Montague | St.Catherine | Completed | Load_240043 | Tredegar - 210 | Jul 13, 2026 8:03am | Jul 13, 2026 8:04am | Jul 13, 2026 9:16am | Jul 13, 2026 2:23pm | Jul 13, 2026 3:29pm | Jul 13, 2026 3:30pm | Jul 13, 2026 3:30pm | Jul 13, 2026 3:30pm |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.07.12568 | C001853098 | Odeanie Davis | KSAS | Completed | Load_259746 | Rockfort - 410 | Jul 13, 2026 8:03am | Jul 13, 2026 8:04am | Jul 13, 2026 12:55pm | Jul 13, 2026 1:58pm | Jul 13, 2026 1:58pm | Jul 13, 2026 2:16pm | Jul 13, 2026 2:00pm | Jul 13, 2026 2:00pm |  |  | Fair | No | 98v at arrival, open circuit at pothead and secondary corrected. 2 one bolt clamps & 2 penn union, 114v after correction.
Non-Outage | J.E.26.07.12570 | C001853097 | Odeanie Davis | KSAS | Completed | Load_259746 | Rockfort - 410 | Jul 13, 2026 8:03am | Jul 13, 2026 8:04am | Jul 13, 2026 12:56pm | Jul 13, 2026 1:19pm | Jul 13, 2026 1:19pm | Jul 13, 2026 1:58pm | Jul 13, 2026 1:58pm | Jul 13, 2026 1:58pm |  |  | Fair | No | 98v at arrival, open circuit at pothead and secondary corrected. 2 one bolt clamps & 2 penn union, 114v after correction.
Non-Outage | J.E.26.07.12605 | C001853080 | Royston Montague | St.Catherine | Completed | Load_257732 | Tredegar - 510 | Jul 13, 2026 8:03am | Jul 13, 2026 8:04am | Jul 13, 2026 9:16am | Jul 13, 2026 10:09am | Jul 13, 2026 10:09am | Jul 13, 2026 10:09am | Jul 13, 2026 10:09am | Jul 13, 2026 10:09am |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.07.12725 | C001853078 | Royston Montague | St.Catherine | Completed | Load_240043 | Tredegar - 210 | Jul 13, 2026 8:03am | Jul 13, 2026 8:04am | Jul 13, 2026 9:16am | Jul 13, 2026 3:30pm | Jul 13, 2026 3:31pm | Jul 13, 2026 3:31pm | Jul 13, 2026 3:32pm | Jul 13, 2026 3:32pm |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.07.12823 | C001853094 | Odeanie Davis | KSAS | Completed | Load_250688 | Hunts Bay - 310 | Jul 13, 2026 8:03am | Jul 13, 2026 8:04am | Jul 14, 2026 9:55am | Jul 14, 2026 9:55am | Jul 14, 2026 9:55am | Jul 14, 2026 9:59am | Jul 14, 2026 9:57am | Jul 14, 2026 9:57am |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.07.12987 | C001853088 | Odeanie Davis | KSAN | Completed | Load_268663 | Washington Blvd - 710 | Jul 13, 2026 8:03am | Jul 13, 2026 8:04am | Jul 13, 2026 9:12am | Jul 13, 2026 11:42am | Jul 13, 2026 11:52am | Jul 13, 2026 12:19pm | Jul 13, 2026 12:19pm | Jul 13, 2026 12:19pm |  |  | Fair | No | 111v/95v on secondary line, field service needed, bucket truck needed.
Non-Outage | J.E.26.07.13168 | C001853081 | Odeanie Davis | KSAN | Completed | Load_244392 | Washington Blvd - 710 | Jul 13, 2026 8:03am | Jul 13, 2026 8:04am | Jul 13, 2026 9:12am | Jul 13, 2026 11:12am | Jul 13, 2026 11:14am | Jul 13, 2026 11:27am | Jul 13, 2026 11:29am | Jul 13, 2026 11:29am |  |  | Fair | No | 111v/0V at location from rammi box, customer currently getting single phase at location, field service team needed. Multiple customers having the same issue in area
Non-Outage | J.E.26.07.13184 | C001853075 | Royston Montague | St.Catherine | Completed | Load_257089 | Twickenham - 310 | Jul 13, 2026 8:03am | Jul 13, 2026 8:04am | Jul 13, 2026 9:16am | Jul 13, 2026 9:16am | Jul 13, 2026 10:07am | Jul 13, 2026 10:08am | Jul 13, 2026 10:08am | Jul 13, 2026 10:08am |  |  | Fair | No | customer confirmed issue resolved.
Non-Outage | J.E.26.07.13610 | C001853079 | Odeanie Davis | KSAN | Completed | Load_567704 | Washington Blvd - 310 | Jul 13, 2026 8:03am | Jul 13, 2026 8:04am | Jul 13, 2026 9:12am | Jul 13, 2026 10:55am | Jul 13, 2026 10:55am | Jul 13, 2026 11:04am | Jul 13, 2026 11:04am | Jul 13, 2026 11:04am |  |  | Fair | No | Premises found okay, customer stated that issue was resolved.
Non-Outage | J.E.26.07.13877 | C001853089 | Odeanie Davis | KSAS | Completed | Load_247391 | Rockfort - 410 | Jul 13, 2026 8:03am | Jul 13, 2026 8:04am | Jul 13, 2026 12:30pm | Jul 13, 2026 2:13pm | Jul 13, 2026 2:14pm | Jul 13, 2026 4:05pm | Jul 13, 2026 4:05pm | Jul 13, 2026 4:05pm |  |  | Fair | No | 99v/0V at arrival, open circuit at pothead and secondary corrected, 3 one bolt clamps, 6 penn union & 60ft twisted wire, 100v/115v & 215v after correction, transformer needs to check and Analog meter at location needs to be changed.
Non-Outage | J.E.26.07.13891 | C001853076 | Odeanie Davis | KSAN | Completed | Load_244711 | Washington Blvd - 710 | Jul 13, 2026 8:03am | Jul 13, 2026 8:04am | Jul 13, 2026 9:12am | Jul 13, 2026 10:00am | Jul 13, 2026 10:08am | Jul 13, 2026 10:53am | Jul 13, 2026 10:53am | Jul 13, 2026 10:53am |  |  | Fair | No | 98v at arrival, open circuit at pothead corrected, 2 penn union . 115v after correction,
Non-Outage | J.E.26.07.14076 | C001853077 | Odeanie Davis | KSAN | Completed | Load_251848 | Washington Blvd - 710 | Jul 13, 2026 8:03am | Jul 13, 2026 8:04am | Jul 13, 2026 9:12am | Jul 13, 2026 11:31am | Jul 13, 2026 11:31am | Jul 13, 2026 11:42am | Jul 13, 2026 11:34am | Jul 13, 2026 11:34am |  |  | Fair | No | Customer stated that issue was resolved by their electrician
Non-Outage | J.E.26.07.14116 | C001853074 | Rusean Allen | KSAS | Completed | Load_254739 | Cane River - 610 | Jul 13, 2026 8:02am | Jul 13, 2026 9:05am | Jul 13, 2026 11:02am | Jul 13, 2026 11:02am | Jul 13, 2026 11:16am | Jul 13, 2026 11:25am | Jul 13, 2026 11:26am | Jul 13, 2026 11:26am |  |  | Fair | No | Broken intermediate pole, broken stanchion, broken pothead wires found Wires were disconnected at transformer pole, Customer was advised to contact electrician to conduct repairs.
Non-Outage | J.E.26.07.14366 | C001853073 | Rusean Allen | null | Completed | null | null | Jul 13, 2026 8:01am | Jul 13, 2026 8:08am | Jul 13, 2026 9:02am | Jul 13, 2026 9:27am | Jul 13, 2026 9:57am | Jul 13, 2026 9:58am | Jul 13, 2026 9:59am | Jul 13, 2026 9:59am |  |  | Fair | No | Found okay at time of visit. Customer complains of low voltage, customer is feed by #6 conductor with numerous splicing. Recommended that customer wire be replaced and upgraded. 500 feet of #2 triplex required.
Non-Outage | J.E.26.07.08530 | C001853072 | Gregory Grossett | Portland | Completed | Load_251129 | Port Antonio - 410 | Jul 13, 2026 7:58am | Jul 13, 2026 7:58am | Jul 13, 2026 9:03am | Jul 13, 2026 9:03am | Jul 13, 2026 9:35am | Jul 13, 2026 11:00am | Jul 13, 2026 11:08am | Jul 13, 2026 11:08am |  | Y | Fair | No | Open secondary conductors banging and transformer drop leads corroded open 15kva transformer fuse then cut tree that was entangled with conductors and retention several pole span of conductors then repair drop leads close transformer fuse to restore normal supply to the area.Material use 3 one bolt clamps.
Outage | J.E.26.07.09612 | C001853068 | Moses Elliston | St.Catherine | Completed | Load_243890 | New Michelton - 210 | Jul 13, 2026 7:58am | Jul 13, 2026 7:59am | Jul 13, 2026 8:13am | Jul 13, 2026 8:13am | Jul 13, 2026 8:13am | Jul 12, 2026 12:15pm | Jul 13, 2026 8:16am | Jul 13, 2026 8:16am |  |  | Fair | No | Credit added to prepaid account.
Non-Outage | J.E.26.07.11920 | C001853067 | Gregory Grossett | Portland | Completed | Load_268118 | Port Antonio - 410 | Jul 13, 2026 7:57am | Jul 13, 2026 7:57am | Jul 13, 2026 8:58am | Jul 13, 2026 8:58am | Jul 13, 2026 8:58am | Jul 13, 2026 9:02am | Jul 13, 2026 9:02am | Jul 13, 2026 9:02am |  |  | Fair | No | After calling customer he said that the issue was resolved.
Non-Outage | J.E.26.07.13211 | C001853066 | Gregory Grossett | Portland | Completed | Load_243136 | Port Antonio - 410 | Jul 13, 2026 7:57am | Jul 13, 2026 7:57am | Jul 13, 2026 1:53pm | Jul 13, 2026 1:53pm | Jul 13, 2026 2:23pm | Jul 13, 2026 3:15pm | Jul 13, 2026 3:20pm | Jul 13, 2026 3:20pm |  |  | Fair | No | 220 service neutral corrode and phase broken at pole repair and ok material use 2 one bolt clamps 5ft of service neutral.
Outage | J.E.26.07.13824 | C001853064 | Richard Samuda | Manchester | Completed | Load_251048 | Kendal - 210 | Jul 13, 2026 7:56am | Jul 13, 2026 8:04am | Jul 13, 2026 3:56pm | Jul 13, 2026 3:56pm | Jul 13, 2026 3:56pm | Jul 13, 2026 3:56pm | Jul 13, 2026 3:57pm | Jul 13, 2026 3:57pm |  |  | Fair | No | Premises not located and call to check no answer
Outage | J.E.26.07.13825 | C001853063 | Richard Samuda | Manchester | Completed | Load_268263 | Kendal - 210 | Jul 13, 2026 7:56am | Jul 13, 2026 8:04am | Jul 13, 2026 8:32am | Jul 13, 2026 12:22pm | Jul 13, 2026 12:22pm | Jul 13, 2026 12:22pm | Jul 13, 2026 12:23pm | Jul 13, 2026 12:23pm |  |  | Fair | No | Customer back to normal
Outage | J.E.26.07.14262 | C001853060 | Richard Samuda | Manchester | Completed | Load_270122 | Kendal - 210 | Jul 13, 2026 7:56am | Jul 13, 2026 8:01am | Jul 13, 2026 8:58am | Jul 13, 2026 8:58am | Jul 13, 2026 8:58am | Jul 13, 2026 8:58am | Jul 13, 2026 9:00am | Jul 13, 2026 9:00am |  |  | Fair | No | Found ok
Non-Outage | J.E.26.07.07830 | C001853057 | Locksley Allen | St.Mary | Completed | Load_576739 | Annotto Bay - 210 | Jul 13, 2026 7:55am | Jul 13, 2026 7:55am | Jul 13, 2026 3:09pm | Jul 13, 2026 3:09pm | Jul 13, 2026 3:09pm | Jul 13, 2026 3:10pm | Jul 13, 2026 3:11pm | Jul 13, 2026 3:11pm |  |  | Fair | No | Customer said JPS corrected the problem from last week
Non-Outage | J.E.26.07.08405 | C001853056 | Locksley Allen | St.Mary | Completed | Load_242932 | Annotto Bay - 210 | Jul 13, 2026 7:55am | Jul 13, 2026 7:55am | Jul 13, 2026 1:45pm | Jul 13, 2026 2:48pm | Jul 13, 2026 2:49pm | Jul 13, 2026 2:58pm | Jul 13, 2026 2:59pm | Jul 13, 2026 2:59pm |  |  | Fair | No | The neutral in the service wire is broken,underneath the transformerThere are about ten service wire connected at the pole(Cobwebs) and the pole is too high for the Ladder A bucket truck would be safer to do the repairs Voltage at meter socket phase to phase 230v. Phase
Non-Outage | J.E.26.07.08578 | C001853058 | Locksley Allen | St.Mary | Completed | Load_265547 | Annotto Bay - 210 | Jul 13, 2026 7:55am | Jul 13, 2026 7:55am | Jul 13, 2026 12:01pm | Jul 13, 2026 12:27pm | Jul 13, 2026 12:35pm | Jul 13, 2026 12:57pm | Jul 13, 2026 12:58pm | Jul 13, 2026 12:58pm |  |  | Fair | No | Pothead found corroded,clean up connectors at pothead Voltage at meter socket phase to phase 223v. Phase to neutral 111&110vMeter left working
Outage | J.E.26.07.07132 | C001853059 | Moses Elliston | St.Catherine | Completed | Load_569915 | Twickenham - 410 | Jul 13, 2026 7:55am | Jul 13, 2026 7:56am | Jul 13, 2026 8:18am | Jul 13, 2026 8:18am | Jul 13, 2026 8:18am | Jul 8, 2026 3:45pm | Jul 13, 2026 8:20am | Jul 13, 2026 8:20am |  |  | Fair | No | Credit added to prepaid account
Non-Outage | J.E.26.07.08580 | C001853055 | Locksley Allen | St.Mary | Completed | Load_265547 | Annotto Bay - 210 | Jul 13, 2026 7:54am | Jul 13, 2026 7:55am | Jul 13, 2026 1:08pm | Jul 13, 2026 1:08pm | Jul 13, 2026 1:08pm | Jul 13, 2026 1:24pm | Jul 13, 2026 1:22pm | Jul 13, 2026 1:22pm |  |  | Fair | No | Clean up connectors at pothead. Voltage at meter socket phase to phase 223v. Phase to neutral 112&108vThe secondary line at end of Hill Side Dr is low and is covered with bushes and they are touching
Non-Outage | J.E.26.07.08582 | C001853054 | Locksley Allen | St.Mary | Completed | Load_265547 | Annotto Bay - 210 | Jul 13, 2026 7:54am | Jul 13, 2026 7:55am | Jul 13, 2026 1:31pm | Jul 13, 2026 1:32pm | Jul 13, 2026 1:32pm | Jul 13, 2026 1:34am | Jul 13, 2026 1:33pm | Jul 13, 2026 1:33pm |  |  | Fair | No | Duplicate
Non-Outage | J.E.26.07.09293 | C001853050 | Locksley Allen | St.Mary | Completed | Load_249878 | Annotto Bay - 310 | Jul 13, 2026 7:54am | Jul 13, 2026 7:55am | Jul 13, 2026 10:34am | Jul 13, 2026 11:41am | Jul 13, 2026 11:41am | Jul 13, 2026 11:59am | Jul 13, 2026 11:58am | Jul 13, 2026 11:58am |  |  | Fair | No | Problem was corrected from last week. Voltage at meter panel phase to phase 229v. Phase to neutral 116&115This area is Rami
Non-Outage | J.E.26.07.11145 | C001853053 | Locksley Allen | St.Mary | Completed | Load_265547 | Annotto Bay - 210 | Jul 13, 2026 7:54am | Jul 13, 2026 7:55am | Jul 13, 2026 1:29pm | Jul 13, 2026 1:29pm | Jul 13, 2026 1:30pm | Jul 13, 2026 1:32pm | Jul 13, 2026 1:31pm | Jul 13, 2026 1:31pm |  |  | Fair | No | Secondary line covered with bushes
Non-Outage | J.E.26.07.11148 | C001853051 | Locksley Allen | St.Mary | Completed | Load_265547 | Annotto Bay - 210 | Jul 13, 2026 7:54am | Jul 13, 2026 7:55am | Jul 13, 2026 1:23pm | Jul 13, 2026 1:23pm | Jul 13, 2026 1:23pm | Jul 13, 2026 1:27pm | Jul 13, 2026 1:26pm | Jul 13, 2026 1:26pm |  |  | Fair | No | Clean up pothead. Voltage at meter socket phase to phase 223vPhase to neutral 110&111v. Secondary line covered with bushes
Non-Outage | J.E.26.07.11150 | C001853052 | Locksley Allen | St.Mary | Completed | Load_265547 | Annotto Bay - 210 | Jul 13, 2026 7:54am | Jul 13, 2026 7:55am | Jul 13, 2026 1:26pm | Jul 13, 2026 1:26pm | Jul 13, 2026 1:27pm | Jul 13, 2026 1:30pm | Jul 13, 2026 1:29pm | Jul 13, 2026 1:29pm |  |  | Fair | No | Clean up pothead. Voltage at meter socket phase to phase 223vPhase to neutral 113&108. Secondary line covered with bushes
Non-Outage | J.E.26.07.11167 | C001853048 | Locksley Allen | St.Mary | Completed | Load_265547 | Annotto Bay - 210 | Jul 13, 2026 7:54am | Jul 13, 2026 7:56am | Jul 13, 2026 1:34pm | Jul 13, 2026 1:41pm | Jul 13, 2026 1:41pm | Jul 13, 2026 1:45pm | Jul 13, 2026 1:44pm | Jul 13, 2026 1:44pm | Fire |  | Fair | No | Conductors are hanging low and are covered with bushes and they are touching. Voltage at meter socket phase to phase 217vPhase to neutral 110&107v
Outage | J.E.26.07.10491 | C001853049 | Moses Elliston | St.Catherine | Completed | Load_557183 | Tredegar - 410 | Jul 13, 2026 7:54am | Jul 13, 2026 7:54am | Jul 13, 2026 3:53pm | Jul 13, 2026 3:53pm | Jul 13, 2026 3:53pm | Jul 13, 2026 3:45pm | Jul 13, 2026 3:55pm | Jul 13, 2026 3:55pm |  |  | Fair | No | Supply ok at premises
Outage | J.E.26.07.11823 | C001853047 | Moses Elliston | St.Catherine | Completed | Load_254572 | Tredegar - 210 | Jul 13, 2026 7:53am | Jul 13, 2026 7:54am | Jul 13, 2026 10:07am | Jul 13, 2026 10:07am | Jul 13, 2026 10:07am | Jul 13, 2026 10:16am | Jul 13, 2026 10:17am | Jul 13, 2026 10:17am | BrokenPole |  | Fair | No | Meter found dislodged,same replaced.
Non-Outage | J.E.26.07.07359 | C001853044 | Gregory Grossett | null | Completed | null | null | Jul 13, 2026 7:52am | Jul 13, 2026 10:43am | Jul 13, 2026 12:44pm | Jul 13, 2026 12:45pm | Jul 13, 2026 1:06pm | Jul 13, 2026 1:45pm | Jul 13, 2026 1:53pm | Jul 13, 2026 1:53pm |  |  | Fair | No | 220 service wire corroded at pothead joints repair and ok material use 2 one bolt clamps voltage readings 115/116/231 on both phase.
Non-Outage | J.E.26.07.09116 | C001853045 | Collin Robinson | Portland | Completed | Load_256564 | Port Antonio - 310 | Jul 13, 2026 7:52am | Jul 13, 2026 7:52am | Jul 13, 2026 9:19am | Jul 13, 2026 9:19am | Jul 13, 2026 9:19am | Jul 13, 2026 9:21am | Jul 13, 2026 9:22am | Jul 13, 2026 9:22am |  |  | Fair | No | Information received from customer that issue was resolved from last week
Outage | J.E.26.07.14108 | C001853046 | Moses Elliston | St.Catherine | Completed | Load_239334 | Tredegar - 410 | Jul 13, 2026 7:52am | Jul 13, 2026 7:52am | Jul 13, 2026 10:18am | Jul 13, 2026 10:18am | Jul 13, 2026 10:45am | Jul 13, 2026 11:02am | Jul 13, 2026 11:02am | Jul 13, 2026 11:02am |  |  | Fair | No | Credit added to prepaid account
Non-Outage | J.E.26.07.05397 | C001853043 | Collin Robinson | Portland | Completed | Load_268491 | Port Antonio - 310 | Jul 13, 2026 7:51am | Jul 13, 2026 7:52am | Jul 13, 2026 9:32am | Jul 13, 2026 9:32am | Jul 13, 2026 9:32am | Jul 13, 2026 9:33am | Jul 13, 2026 9:34am | Jul 13, 2026 9:34am | LeaningPole |  | Fair | No | Unable to locate customer for better direction
Outage | J.E.26.07.14300 | C001853041 | Ricky Hall | St.Catherine | Completed | Load_239309 | Rhodens Pen - 410 | Jul 13, 2026 7:51am | Jul 13, 2026 7:51am | Jul 13, 2026 9:02am | Jul 13, 2026 11:07am | Jul 13, 2026 11:59am | Jul 13, 2026 12:54pm | Jul 13, 2026 12:54pm | Jul 13, 2026 12:54pm |  |  | Fair | No | Conduct spot bushing clear secondary lines
Non-Outage | J.E.26.07.06309 | C001853038 | Oraine Minto | St.Ann | Completed | Load_238582 | Ocho Rios - 310 | Jul 13, 2026 7:47am | Jul 13, 2026 7:48am | Jul 14, 2026 11:05am | Jul 14, 2026 11:45am | Jul 14, 2026 11:45am | Jul 14, 2026 11:45am | Jul 14, 2026 11:48am | Jul 14, 2026 11:48am |  |  | Fair | No | 235v 117v 117v Customer states that the issue happened this morning but it’s ok now
Non-Outage | J.E.26.07.06651 | C001853039 | Oraine Minto | St.Ann | Completed | Load_238582 | Ocho Rios - 310 | Jul 13, 2026 7:47am | Jul 13, 2026 7:48am | Jul 14, 2026 11:48am | Jul 14, 2026 11:48am | Jul 14, 2026 11:48am | Jul 14, 2026 11:49am | Jul 14, 2026 11:49am | Jul 14, 2026 11:49am |  |  | Fair | No | 235v 117v 117v
Non-Outage | J.E.26.07.06720 | C001853040 | Oraine Minto | St.Ann | Completed | Load_238582 | Ocho Rios - 310 | Jul 13, 2026 7:47am | Jul 13, 2026 7:48am | Jul 13, 2026 1:25pm | Jul 13, 2026 1:25pm | Jul 13, 2026 1:25pm | Jul 13, 2026 1:26pm | Jul 13, 2026 1:26pm | Jul 13, 2026 1:26pm |  |  | Fair | No | Customer states that the issue has been resolved
Non-Outage | J.E.26.07.07346 | C001853035 | Oraine Minto | St.Ann | Completed | Load_257505 | Ocho Rios - 310 | Jul 13, 2026 7:46am | Jul 13, 2026 7:47am | Jul 13, 2026 1:56pm | Jul 13, 2026 1:56pm | Jul 13, 2026 1:56pm | Jul 13, 2026 1:57pm | Jul 13, 2026 1:57pm | Jul 13, 2026 1:57pm |  |  | Fair | No | Refer to emergency Open fuse
Non-Outage | J.E.26.07.09332 | C001853034 | Oraine Minto | St.Ann | Completed | Load_248125 | Ocho Rios - 310 | Jul 13, 2026 7:46am | Jul 13, 2026 7:47am | Jul 13, 2026 1:35pm | Jul 13, 2026 1:35pm | Jul 13, 2026 1:35pm | Jul 13, 2026 1:35pm | Jul 13, 2026 1:36pm | Jul 13, 2026 1:36pm |  |  | Fair | No
Non-Outage | J.E.26.07.10855 | C001853031 | Oraine Minto | St.Ann | Completed | Load_266688 | Roaring River - 210 | Jul 13, 2026 7:46am | Jul 13, 2026 7:47am | Jul 13, 2026 1:15pm | Jul 13, 2026 1:15pm | Jul 13, 2026 1:15pm | Jul 13, 2026 1:15pm | Jul 13, 2026 1:16pm | Jul 13, 2026 1:16pm |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.07.11343 | C001853030 | Oraine Minto | St.Ann | Completed | Load_238508 | Roaring River - 210 | Jul 13, 2026 7:46am | Jul 13, 2026 7:47am | Jul 13, 2026 2:42pm | Jul 13, 2026 2:42pm | Jul 13, 2026 2:43pm | Jul 13, 2026 2:44pm | Jul 13, 2026 2:48pm | Jul 13, 2026 2:48pm |  |  | Fair | No | Need better directions and contact number
Non-Outage | J.E.26.07.14168 | C001853029 | Milton Charlton | null | Completed | null | null | Jul 13, 2026 7:46am | Jul 13, 2026 7:47am | Jul 13, 2026 8:49am | Jul 13, 2026 8:52am | Jul 13, 2026 10:21am | Jul 13, 2026 10:10am | Jul 13, 2026 10:28am | Jul 13, 2026 10:28am |  |  | Fair | No | Bank of 3- 50 kva transformer at pole #0098227 on the ground of Devon House feeding Devon House I cream one of the power transformer is defective 50 kva secondary bushing burn out . Defective 50 kva transformer at pole #0098227.
Outage | J.E.26.07.14220 | C001853028 | Rusean Allen | KSAS | Completed | Load_253227 | Cane River - 610 | Jul 13, 2026 7:45am | Jul 13, 2026 7:47am | Jul 13, 2026 11:26am | Jul 13, 2026 11:26am | Jul 13, 2026 12:22pm | Jul 13, 2026 12:24pm | Jul 13, 2026 12:24pm | Jul 13, 2026 12:24pm |  |  | Fair | No | Corroded clamp found at pole and pothead, clamps were changed.
Non-Outage | J.E.26.07.13581 | C001853025 | Neckell Ormsby | null | Completed | null | null | Jul 13, 2026 7:42am | Jul 13, 2026 9:27am | Jul 13, 2026 9:32am | Jul 13, 2026 9:32am | Jul 13, 2026 9:37am | Jul 13, 2026 10:20am | Jul 13, 2026 10:20am | Jul 13, 2026 10:20am |  |  | Fair | No | Found corrosion at pole and pothead clean and remade joints using 4- one bolt clamps voltage left 120v 1110v 230v
Outage | J.E.26.07.13771 | C001853027 | Cliton Henry | St.Mary | Completed | Load_253313 | Oracabessa - 210 | Jul 13, 2026 7:42am | Jul 13, 2026 7:43am | Jul 13, 2026 8:49am | Jul 13, 2026 8:49am | Jul 13, 2026 9:55am | Jul 13, 2026 10:33am | Jul 13, 2026 10:39am | Jul 13, 2026 10:39am |  |  | Fair | No | A corroded neutral joint found at the secondary dead was reconnected using 2 one bolt clamps. Voltages left. Voltages left 119-119/238 volts
Outage | J.E.26.07.14305 | C001853026 | Daniel Francis | St.Ann | Completed | Load_264963 | Upper White River - 110 | Jul 13, 2026 7:42am | Jul 13, 2026 7:43am | Jul 13, 2026 10:28am | Jul 13, 2026 10:28am | Jul 13, 2026 11:03am | Jul 13, 2026 11:06am | Jul 13, 2026 11:07am | Jul 13, 2026 11:07am |  |  | Fair | No | Customer need to work on meter box
Non-Outage | J.E.26.07.06329 | C001853022 | Cliton Henry | St.Mary | Completed | Load_248681 | Blackstonedge - 110 | Jul 13, 2026 7:41am | Jul 13, 2026 7:43am | Jul 13, 2026 10:51am | Jul 13, 2026 10:53am | Jul 13, 2026 12:32pm | Jul 13, 2026 1:09pm | Jul 13, 2026 1:12pm | Jul 13, 2026 1:12pm |  | Y | Fair | No | The customer supply found ok however the customer complaint of bamboo trees touching the secondary conductors when the wind blows. A 10 kva transformer was de energized and corrective work done to cut and remove bamboo trees. Supply restored the energized the 10 kva transformer.
Non-Outage | J.E.26.07.06444 | C001853024 | Cliton Henry | St.Mary | Completed | Load_262038 | Blackstonedge - 110 | Jul 13, 2026 7:41am | Jul 13, 2026 7:43am | Jul 13, 2026 1:19pm | Jul 13, 2026 1:19pm | Jul 13, 2026 1:19pm | Jul 13, 2026 1:19pm | Jul 13, 2026 1:21pm | Jul 13, 2026 1:21pm |  |  | Fair | No | The customer stated that the supply is now ok. This may related the a feeder cycling .
Non-Outage | J.E.26.07.06579 | C001853023 | Cliton Henry | St.Mary | Completed | Load_251509 | Blackstonedge - 110 | Jul 13, 2026 7:41am | Jul 13, 2026 7:43am | Jul 13, 2026 1:22pm | Jul 13, 2026 1:22pm | Jul 13, 2026 1:22pm | Jul 13, 2026 1:24pm | Jul 13, 2026 1:24pm | Jul 13, 2026 1:24pm |  |  | Fair | No | The customer stated that the supply is ok now
Outage | J.E.26.07.14117 | C001853020 | Romeo Brissett | St.James | Completed | Load_256834 | Bogue - 610 | Jul 13, 2026 7:35am | Jul 13, 2026 3:26pm | Jul 13, 2026 8:00pm | Jul 13, 2026 8:00pm | Jul 13, 2026 8:00pm | Jul 13, 2026 8:08pm | Jul 13, 2026 8:09pm | Jul 13, 2026 8:09pm |  |  | Fair | No | Removed bamboo and Replaced (1)10amps junction fuse.
Non-Outage | J.E.26.07.13787 | C001853017 | Jermaine Williams | Clarendon | Completed | Load_247306 | Monymusk - 410 | Jul 13, 2026 7:34am | Jul 13, 2026 7:34am | Jul 14, 2026 1:55pm | Jul 14, 2026 1:55pm | Jul 14, 2026 2:33pm | Jul 14, 2026 2:33pm | Jul 14, 2026 2:34pm | Jul 14, 2026 2:34pm |  |  | Fair | No | Premises found ok.
Non-Outage | J.E.26.07.13865 | C001853018 | Jermaine Williams | Clarendon | Completed | Load_246032 | Monymusk - 410 | Jul 13, 2026 7:34am | Jul 13, 2026 7:34am | Jul 13, 2026 8:26am | Jul 13, 2026 8:26am | Jul 13, 2026 10:25am | Jul 13, 2026 10:35am | Jul 13, 2026 10:36am | Jul 13, 2026 10:36am |  | Y | SevereWind | No | Isolate 10kva xfmr to repair defective #2 twisted secondary. Broken 30’ class 6 Tsec pole at location, refer to N McLean. Urgent attention required
Non-Outage | J.E.26.07.14080 | C001853016 | Jermaine Williams | Clarendon | Completed | Load_247305 | Parnassus - 210 | Jul 13, 2026 7:34am | Jul 13, 2026 7:34am | Jul 13, 2026 8:25am | Jul 13, 2026 8:25am | Jul 13, 2026 8:25am | Jul 13, 2026 8:25am | Jul 13, 2026 8:26am | Jul 13, 2026 8:26am |  |  | Fair | No | Premises found ok.
Outage | J.E.26.07.14223 | C001853015 | Michael Christian | St.James | Completed | Load_261201 | Bogue - 610 | Jul 13, 2026 7:33am | Jul 13, 2026 7:33am | Jul 13, 2026 1:15pm | Jul 13, 2026 1:15pm | Jul 13, 2026 1:46pm | Jul 13, 2026 1:51pm | Jul 13, 2026 1:51pm | Jul 13, 2026 1:51pm |  |  | Fair | No | Reset 1 25 kava cause by cable wire no pole # voltage 111 112 223 at pothead
Outage | J.E.26.07.10120 | C001853013 | Romaine Roberts | St.Mary | Completed | Load_241211 | Highgate - 210 | Jul 13, 2026 7:32am | Jul 13, 2026 7:33am | Jul 13, 2026 12:34pm | Jul 13, 2026 12:34pm | Jul 13, 2026 2:03pm | Jul 13, 2026 2:21pm | Jul 13, 2026 2:23pm | Jul 13, 2026 2:23pm | BrokenWire |  | Fair | No | Bamboo fall on secondary line and burst down one span of neutral splice and retention conductor open and close 25 kva transformer to carryout repairs
Outage | J.E.26.07.10597 | C001853009 | Wayne Dillion | St.Elizabeth | Completed | Load_249402 | Maggotty - 110 | Jul 13, 2026 7:32am | Jul 13, 2026 7:34am | Jul 13, 2026 9:10am | Jul 13, 2026 9:10am | Jul 13, 2026 9:10am | Jul 13, 2026 9:10am | Jul 13, 2026 9:11am | Jul 13, 2026 9:11am |  |  | Fair | No | Problem has been resolved from yesterday
Outage | J.E.26.07.14131 | C001853011 | Romaine Roberts | St.Mary | Completed | Load_242488 | Highgate - 210 | Jul 13, 2026 7:32am | Jul 13, 2026 7:33am | Jul 13, 2026 9:29am | Jul 13, 2026 9:29am | Jul 13, 2026 12:06pm | Jul 13, 2026 12:29pm | Jul 13, 2026 12:30pm | Jul 13, 2026 12:30pm | BrokenWire |  | Fair | No | Truck. Rust down customer service main splice and replace 6 3 wire suing 250 foot of number 6 triplex open and close 25 kva to carryout repairs
Outage | J.E.26.07.14330 | C001853008 | Jermaine Williams | Clarendon | Completed | Load_247305 | Parnassus - 210 | Jul 13, 2026 7:31am | Jul 13, 2026 7:31am | Jul 13, 2026 7:35am | Jul 13, 2026 7:35am | Jul 13, 2026 8:19am | Jul 13, 2026 8:24am | Jul 13, 2026 8:25am | Jul 13, 2026 8:25am | Fire |  | Fair | No | Premises found ok.
Non-Outage | J.E.26.07.12450 | C001853007 | Wayne Dillion | null | Completed | null | null | Jul 13, 2026 7:28am | Jul 13, 2026 10:34am | Jul 13, 2026 2:46pm | Jul 13, 2026 2:46pm | Jul 13, 2026 2:46pm | Jul 13, 2026 2:47pm | Jul 13, 2026 2:47pm | Jul 13, 2026 2:47pm |  |  | Rains | No | Unable to locate and customer not answering the phone.
Non-Outage | J.E.26.07.12668 | C001853006 | Selvin White | null | Completed | null | null | Jul 13, 2026 7:28am | Jul 13, 2026 7:29am | Jul 13, 2026 9:56am | Jul 13, 2026 9:56am | Jul 13, 2026 9:57am | Jul 13, 2026 9:59am | Jul 13, 2026 9:59am | Jul 13, 2026 9:59am |  |  | Fair | No | Customer says supply was restored from yesterday by an emergency crew.
Non-Outage | J.E.26.07.11088 | C001853005 | Elvis Trowers | KSAN | Completed | Load_262377 | Constant Spring - 210 | Jul 13, 2026 7:26am | Jul 13, 2026 8:07am | Jul 13, 2026 10:34am | Jul 13, 2026 10:34am | Jul 13, 2026 11:25am | Jul 13, 2026 12:16pm | Jul 13, 2026 12:17pm | Jul 13, 2026 12:17pm |  |  | Fair | Yes | Happened to be internal when checked, customer was also advised to contact an electrician to complete checks on the inside.
Non-Outage | J.E.26.07.14294 | C001853004 | Fredrick Hamilton | KSAN | Completed | Load_256846 | Constant Spring - 210 | Jul 13, 2026 7:26am | Jul 14, 2026 8:10am | Jul 14, 2026 8:15am | Jul 14, 2026 11:19am | Jul 14, 2026 11:47am | Jul 14, 2026 11:59am | Jul 14, 2026 11:59am | Jul 14, 2026 11:59am |  |  | Fair | No | 243v121v/121v obtained Premises checked and found okNo JPS issue detected
Non-Outage | J.E.26.07.06163 | C001852999 | Daniel Francis | St.Ann | Completed | Load_264883 | Ocho Rios - 510 | Jul 13, 2026 7:22am | Jul 13, 2026 7:23am | Jul 13, 2026 8:48am | Jul 13, 2026 8:48am | Jul 13, 2026 8:48am | Jul 13, 2026 8:48am | Jul 13, 2026 8:49am | Jul 13, 2026 8:49am |  |  | Fair | No | Found ok
Non-Outage | J.E.26.07.07979 | C001853000 | Daniel Francis | St.Ann | Completed | Load_264883 | Ocho Rios - 510 | Jul 13, 2026 7:22am | Jul 13, 2026 7:23am | Jul 13, 2026 8:46am | Jul 13, 2026 8:46am | Jul 13, 2026 8:46am | Jul 13, 2026 8:47am | Jul 13, 2026 8:47am | Jul 13, 2026 8:47am |  |  | Fair | No | Found ok
Non-Outage | J.E.26.07.11363 | C001853002 | Daniel Francis | St.Ann | Completed | Load_246719 | Ocho Rios - 310 | Jul 13, 2026 7:22am | Jul 13, 2026 7:23am | Jul 13, 2026 10:14am | Jul 13, 2026 10:14am | Jul 13, 2026 10:26am | Jul 13, 2026 10:27am | Jul 13, 2026 10:27am | Jul 13, 2026 10:27am |  |  | Fair | No | Found okay
Non-Outage | J.E.26.07.11483 | C001853001 | Daniel Francis | St.Ann | Completed | Load_244282 | Ocho Rios - 310 | Jul 13, 2026 7:22am | Jul 13, 2026 7:23am | Jul 13, 2026 8:50am | Jul 13, 2026 8:50am | Jul 13, 2026 9:57am | Jul 13, 2026 9:57am | Jul 13, 2026 9:59am | Jul 13, 2026 9:59am |  |  | Fair | No | Found okay customer say someone come there from the 10th and it’s okay now
Non-Outage | J.E.26.07.11627 | C001853003 | Daniel Francis | St.Ann | Completed | Load_246719 | Ocho Rios - 310 | Jul 13, 2026 7:22am | Jul 13, 2026 7:23am | Jul 13, 2026 10:00am | Jul 13, 2026 10:00am | Jul 13, 2026 10:10am | Jul 13, 2026 10:12am | Jul 13, 2026 10:14am | Jul 13, 2026 10:14am |  |  | Fair | No | Found okay we do this work from the 10th
Non-Outage | J.E.26.07.07046 | C001852997 | Daniel Francis | St.Ann | Completed | Load_253537 | Upper White River - 210 | Jul 13, 2026 7:18am | Jul 13, 2026 7:23am | Jul 13, 2026 8:18am | Jul 13, 2026 8:18am | Jul 13, 2026 8:45am | Jul 13, 2026 8:45am | Jul 13, 2026 8:46am | Jul 13, 2026 8:46am |  |  | Fair | No | Found okay 116 117 233 in all
Non-Outage | J.E.26.07.10536 | C001852996 | Roxroy Needham | St.Ann | Completed | Load_259557 | Cardiff Hall - 210 | Jul 13, 2026 7:13am | Jul 13, 2026 7:14am | Jul 13, 2026 7:52am | Jul 13, 2026 7:52am | Jul 13, 2026 9:34am | Jul 13, 2026 9:37am | Jul 13, 2026 9:39am | Jul 13, 2026 9:39am |  |  | Fair | No | Open a 50 KVA transformer at pole to repair transformer leed use 2 pg clamp
Non-Outage | J.E.26.07.10706 | C001852994 | Roxroy Needham | St.Ann | Completed | Load_259557 | Cardiff Hall - 210 | Jul 13, 2026 7:13am | Jul 13, 2026 7:14am | Jul 13, 2026 11:31am | Jul 13, 2026 11:32am | Jul 13, 2026 12:45pm | Jul 13, 2026 1:00pm | Jul 13, 2026 1:04pm | Jul 13, 2026 1:04pm |  |  | Fair | No | Remake joint at pothead used 3 pg clamp voltage left at meter 115-116-234
Non-Outage | J.E.26.07.11933 | C001852993 | Roxroy Needham | St.Ann | Completed | Load_269955 | Duncans - 210 | Jul 13, 2026 7:13am | Jul 13, 2026 7:14am | Jul 13, 2026 11:25am | Jul 13, 2026 11:27am | Jul 13, 2026 11:27am | Jul 13, 2026 11:27am | Jul 13, 2026 11:28am | Jul 13, 2026 11:28am |  |  | Fair | No | Premises found ok call customer and customer say that the light is ok
Non-Outage | J.E.26.07.11944 | C001852991 | Roxroy Needham | St.Ann | Completed | Load_264977 | Duncans - 210 | Jul 13, 2026 7:13am | Jul 13, 2026 7:14am | Jul 13, 2026 11:26am | Jul 13, 2026 11:28am | Jul 13, 2026 11:28am | Jul 13, 2026 11:30am | Jul 13, 2026 11:29am | Jul 13, 2026 11:29am |  |  | Fair | No | Premises found ok call customer and customer say that the light is ok
Non-Outage | J.E.26.07.11944 | C001852992 | Roxroy Needham | St.Ann | Completed | Load_264977 | Duncans - 210 | Jul 13, 2026 7:13am | Jul 13, 2026 7:14am | Jul 13, 2026 11:26am | Jul 13, 2026 11:30am | Jul 13, 2026 11:30am | Jul 13, 2026 11:30am | Jul 13, 2026 11:31am | Jul 13, 2026 11:31am |  |  | Fair | No | Premises found ok call customer and customer say that the light is ok
Non-Outage | J.E.26.07.13727 | C001852988 | Roxroy Needham | St.Ann | Completed | Load_244223 | Cardiff Hall - 210 | Jul 13, 2026 7:13am | Jul 13, 2026 7:14am | Jul 13, 2026 9:40am | Jul 13, 2026 9:40am | Jul 13, 2026 10:20am | Jul 13, 2026 11:23am | Jul 13, 2026 11:25am | Jul 13, 2026 11:25am |  | Y | Fair | No | Open a 25 KVA transformer at pole to repair transformer Leeds use 4 pg clamp voltage left at meter 113-114-228
Non-Outage | J.E.26.07.11911 | C001852983 | Andrew Powell | null | Completed | null | null | Jul 13, 2026 7:07am | Jul 13, 2026 7:09am | Jul 13, 2026 10:12am | Jul 13, 2026 10:12am | Jul 13, 2026 10:12am | Jul 13, 2026 10:13am | Jul 13, 2026 10:13am | Jul 13, 2026 10:13am |  |  | Fair | No | Premises found okay customer stated that fault resolved supply restored.
Outage | J.E.26.07.14216 | C001852982 | Selvin White | St.Elizabeth | Completed | Load_292190 | Maggotty - 210 | Jul 13, 2026 7:06am | Jul 13, 2026 9:47am | Jul 13, 2026 9:59am | Jul 13, 2026 9:59am | Jul 13, 2026 11:05am | Jul 13, 2026 11:12am | Jul 13, 2026 11:12am | Jul 13, 2026 11:12am |  |  | Fair | No | Customer cannot be contacted however the escalation department was contacted and said the meter was not communicating so please refer to Simone Bicarie and C. Johnson at the field service department so an order can be generated.
Outage | J.E.26.07.14282 | C001852981 | Andrew Powell | Manchester | Completed | Load_292494 | Spur Tree - 210 | Jul 13, 2026 7:05am | Jul 13, 2026 7:10am | Jul 13, 2026 7:29am | Jul 13, 2026 7:29am | Jul 13, 2026 9:14am | Jul 13, 2026 9:58am | Jul 13, 2026 10:03am | Jul 13, 2026 10:03am | Fire |  | Fair | No | Repair burnt off 35 class 6 TA construction wooden pole head using one 35 kv post type insulator with pole top lop, replace blown 8 amp junction fuse by pot of gold restaurant and larch, no pole number by switch location, restore supply okay.
Outage | J.E.26.07.14313 | C001852980 | Andrew Powell | Manchester | Completed | Load_293096 | Spur Tree - 210 | Jul 13, 2026 7:05am | Jul 13, 2026 7:11am | Jul 13, 2026 10:08am | Jul 13, 2026 10:09am | Jul 13, 2026 10:09am | Jul 13, 2026 10:09am | Jul 13, 2026 10:10am | Jul 13, 2026 10:10am |  |  | Fair | No | Called related to burnt off wooden pole head in Yardley Chase fault resolved supply restored.
Non-Outage | J.E.26.07.14312 | C001852978 | Javid Vernon | null | Completed | null | null | Jul 13, 2026 7:04am | Jul 13, 2026 3:22pm | Jul 13, 2026 6:32pm | Jul 13, 2026 6:32pm | Jul 13, 2026 6:32pm | Jul 13, 2026 6:34pm | Jul 13, 2026 6:35pm | Jul 13, 2026 6:35pm | Fire |  | Fair | No | This call belongs to st james
Non-Outage | J.E.26.07.14321 | C001852979 | Andrew Powell | null | Completed | null | null | Jul 13, 2026 7:04am | Jul 13, 2026 7:12am | Jul 13, 2026 10:03am | Jul 13, 2026 10:03am | Jul 13, 2026 10:03am | Jul 13, 2026 10:03am | Jul 13, 2026 10:05am | Jul 13, 2026 10:05am | Fire |  | Fair | No | Called related to burnt off pole head in Yardley Chase, fault resolved supply restored.
Outage | J.E.26.07.14272 | C001852977 | Oshane Warren | Westmoreland | Completed | Load_264630 | Paradise - 310 | Jul 13, 2026 7:04am | Jul 13, 2026 8:42am | Jul 13, 2026 12:32pm | Jul 13, 2026 12:33pm | Jul 13, 2026 1:16pm | Jul 13, 2026 1:18pm | Jul 13, 2026 1:21pm | Jul 13, 2026 1:21pm |  |  | Rains | No | Customer needs to relocate pole in order to get reconnection
Outage | J.E.26.07.14308 | C001852976 | Michael Christian | St.James | Completed | Load_573589 | Bogue - 610 | Jul 13, 2026 7:03am | Jul 13, 2026 7:05am | Jul 13, 2026 7:34am | Jul 13, 2026 7:34am | Jul 13, 2026 8:10am | Jul 13, 2026 8:55am | Jul 13, 2026 8:55am | Jul 13, 2026 8:55am |  |  | Fair | No | Found 1 20 amp 1 30 amp 1 2 amp out cause by bird replace 1 30 amp at pole # 589517
Outage | J.E.26.07.14318 | C001852974 | Michael Christian | St.James | Completed | Load_249034 | Bogue - 610 | Jul 13, 2026 7:03am | Jul 13, 2026 7:05am | Jul 13, 2026 8:57am | Jul 13, 2026 8:57am | Jul 13, 2026 11:14am | Jul 13, 2026 11:18am | Jul 13, 2026 11:18am | Jul 13, 2026 11:18am | Fire |  | Fair | No | Check and found okay no fire found
Non-Outage | J.E.26.07.14130 | C001852971 | Andre Williams | null | Completed | null | null | Jul 13, 2026 7:02am | Jul 13, 2026 8:31am | Jul 13, 2026 8:40am | Jul 13, 2026 8:40am | Jul 13, 2026 9:27am | Jul 13, 2026 9:29am | Jul 13, 2026 9:34am | Jul 13, 2026 9:34am |  |  | Fair | No | Premises ok customer was advice to switch on breaker premises now with supply.
Outage | J.E.26.07.14329 | C001852972 | Lancelot Brown | Hanover | Completed | Load_302811 | Orange Bay - 310 | Jul 13, 2026 7:02am | Jul 13, 2026 8:18am | Jul 13, 2026 8:37am | Jul 13, 2026 9:00am | Jul 13, 2026 9:13am | Jul 13, 2026 10:08am | Jul 13, 2026 10:08am | Jul 13, 2026 10:08am |  |  | SevereWind | No | Found junction fuse blown patroll found nothing replace 1-8amps junction fuse no pole number supply restore
Outage | J.E.26.07.14297 | C001852969 | Donald Cunningham | Portmore | Completed | Load_248603 | Naggo Head - 510 | Jul 13, 2026 5:38am | Jul 13, 2026 8:33am | Jul 13, 2026 10:27am | Jul 13, 2026 10:27am | Jul 13, 2026 11:19am | Jul 13, 2026 11:45am | Jul 13, 2026 11:49am | Jul 13, 2026 11:49am |  |  | Fair | No | Blown transformer fuse by north edgewater ave replace 8 amp for 100 kva transformer in front of Yvette crescent
Outage | J.E.26.07.14188 | C001852960 | Delano Gayle | Portmore | Completed | Load_1004124 | Naggo Head - 510 | Jul 12, 2026 11:18pm | Jul 12, 2026 11:18pm | Jul 13, 2026 12:27am | Jul 13, 2026 12:27am | Jul 13, 2026 1:11am | Jul 13, 2026 1:36am | Jul 13, 2026 1:36am | Jul 13, 2026 1:36am | Fire |  | Fair | No | Premises not found no answer from customer phone no fire seen
Outage | J.E.26.07.14110 | C001852958 | Swon Miller | St.James | Completed | Load_259739 | Bogue - 310 | Jul 12, 2026 11:15pm | Jul 12, 2026 11:15pm | Jul 13, 2026 4:56am | Jul 13, 2026 4:56am | Jul 13, 2026 5:25am | Jul 13, 2026 5:46am | Jul 13, 2026 5:59am | Jul 13, 2026 5:59am | Fire |  | Fair | No | Check and found okay no fire found
Outage | J.E.26.07.14232 | C001852957 | Swon Miller | St.James | Completed | Load_573589 | Bogue - 610 | Jul 12, 2026 11:14pm | Jul 12, 2026 11:14pm | Jul 13, 2026 2:36am | Jul 13, 2026 2:36am | Jul 13, 2026 3:54am | Jul 13, 2026 3:53am | Jul 13, 2026 4:56am | Jul 13, 2026 4:56am |  |  | Fair | No | Found 10 amp junction fuse blown 50 kva transformer fuse blown cause by contamination replace 10 amp junction fuse no pole number available and replace 5 amp in a 50 kva transformer
Non-Outage | J.E.26.07.14218 | C001852956 | Delano Gayle | null | Completed | null | null | Jul 12, 2026 10:59pm | Jul 12, 2026 11:00pm | Jul 12, 2026 11:06pm | Jul 12, 2026 11:14pm | Jul 13, 2026 12:03am | Jul 13, 2026 12:27am | Jul 13, 2026 12:27am | Jul 13, 2026 12:27am | Fire |  | Fair | No | Premises and area found okay no fire seen
Outage | J.E.26.07.14234 | C001852955 | Delano Gayle | St.Catherine | Completed | Load_244050 | Tredegar - 410 | Jul 12, 2026 10:59pm | Jul 12, 2026 11:00pm | Jul 13, 2026 1:36am | Jul 13, 2026 4:05am | Jul 13, 2026 4:10am | Jul 13, 2026 4:15am | Jul 13, 2026 4:15am | Jul 13, 2026 4:15am |  |  | Fair | No | Premises found okay via phone call power restored
Outage | J.E.26.07.14127 | C001852954 | Swon Miller | St.James | Completed | Load_255507 | Bogue - 610 | Jul 12, 2026 10:53pm | Jul 12, 2026 10:59pm | Jul 13, 2026 12:32am | Jul 13, 2026 12:32am | Jul 13, 2026 1:50am | Jul 13, 2026 2:31am | Jul 13, 2026 2:35am | Jul 13, 2026 2:35am |  |  | Fair | No | Found 15 amp junction fuse blown cause by contamination replace 15 amp junction fuse no pole number available
Outage | J.E.26.07.14239 | C001852953 | Swon Miller | St.James | Completed | Load_245936 | Queens Drive - 710 | Jul 12, 2026 10:53pm | Jul 12, 2026 10:59pm | Jul 12, 2026 11:07pm | Jul 12, 2026 11:08pm | Jul 12, 2026 11:37pm | Jul 28, 2026 12:30am | Jul 13, 2026 12:31am | Jul 13, 2026 12:31am |  |  | Fair | No | Found 50 kva transformer fuse blown cause by illegal connections remove illegal connections and replace 5 amp in 50 kva transformer no pole number available voltage found 0.000 voltage left 115/116/232
Outage | J.E.26.07.14209 | C001852935 | Richman Whyte | Westmoreland | Completed | Load_257466 | Paradise - 210 | Jul 12, 2026 9:17pm | Jul 12, 2026 9:18pm | Jul 12, 2026 10:50pm | Jul 12, 2026 10:50pm | Jul 12, 2026 11:32pm | Jul 12, 2026 11:38pm | Jul 12, 2026 11:38pm | Jul 12, 2026 11:38pm |  |  | Fair | No | Replace two amp twenty five kva transformer fuse
Outage | J.E.26.07.14060 | C001852933 | Edward Royal | KSAN | Completed | Load_251201 | Washington Blvd - 610 | Jul 12, 2026 8:55pm | Jul 12, 2026 8:56pm | Jul 12, 2026 9:08pm | Jul 12, 2026 9:08pm | Jul 12, 2026 9:37pm | Jul 12, 2026 9:43pm | Jul 12, 2026 9:44pm | Jul 12, 2026 9:44pm |  |  | Fair | No | Replaced 20A junction fuse
Non-Outage | J.E.26.07.14180 | C001852931 | Andrew Powell | null | Completed | null | null | Jul 12, 2026 8:38pm | Jul 12, 2026 8:39pm | Jul 12, 2026 10:02pm | Jul 12, 2026 10:02pm | Jul 12, 2026 10:02pm | Jul 12, 2026 10:03pm | Jul 12, 2026 10:03pm | Jul 12, 2026 10:03pm | Fire |  | Fair | No | Found okay fault resolved supply restored.
Outage | J.E.26.07.14128 | C001852930 | Andrew Powell | St.Elizabeth | Completed | Load_1002214 | Maggotty - 210 | Jul 12, 2026 8:38pm | Jul 12, 2026 8:38pm | Jul 12, 2026 8:57pm | Jul 12, 2026 8:57pm | Jul 12, 2026 9:52pm | Jul 12, 2026 9:55pm | Jul 12, 2026 10:02pm | Jul 12, 2026 10:02pm | BrokenWire |  | SevereWind | No | Found three damage 3 wire AMI smart meter #2875797 and 2932281 unable access meter # 3 bush fire damage meter screen, no customer affected, please refer to field service department for replacement.
Outage | J.E.26.07.14200 | C001852929 | Lancelot Brown | Hanover | Completed | Load_244685 | Orange Bay - 310 | Jul 12, 2026 8:36pm | Jul 12, 2026 8:36pm | Jul 12, 2026 8:46pm | Jul 12, 2026 8:47pm | Jul 12, 2026 9:46pm | Jul 12, 2026 10:10pm | Jul 12, 2026 10:11pm | Jul 12, 2026 10:11pm |  |  | Rains | No | Found junction fuse blown patroll found nothing customer said rain was falling and lightning strike and supply went replace 1-15amps junction fuse no pole number supply restore
Non-Outage | J.E.26.07.14164 | C001852928 | Oshane Warren | null | Completed | null | null | Jul 12, 2026 8:35pm | Jul 12, 2026 8:36pm | Jul 12, 2026 9:11pm | Jul 12, 2026 9:11pm | Jul 12, 2026 9:11pm | Jul 12, 2026 9:36pm | Jul 12, 2026 9:39pm | Jul 12, 2026 9:39pm | Fire |  | Fair | No | Open 10 amp junction fuse and cut off pole top from line section
Non-Outage | J.E.26.07.14194 | C001852927 | Romeo Brissett | St.James | Completed | Load_248322 | Bogue - 310 | Jul 12, 2026 8:35pm | Jul 13, 2026 8:08am | Jul 13, 2026 8:12am | Jul 13, 2026 8:12am | Jul 13, 2026 10:05am | Jul 13, 2026 10:39am | Jul 13, 2026 11:07am | Jul 13, 2026 11:07am |  |  | Fair | No | Found customer service wire broken due to fallen tree across main road spliced and retention customer service wire.
Non-Outage | J.E.26.07.14038 | C001852922 | Edward Royal | null | Completed | null | null | Jul 12, 2026 8:16pm | Jul 12, 2026 8:16pm | Jul 12, 2026 8:55pm | Jul 12, 2026 8:55pm | Jul 12, 2026 9:05pm | Jul 12, 2026 9:06pm | Jul 12, 2026 9:06pm | Jul 12, 2026 9:06pm | BrokenPole |  | Fair | No | Customer was reconnected by escalation
Non-Outage | J.E.26.07.14054 | C001852921 | Edward Royal | null | Completed | null | null | Jul 12, 2026 8:16pm | Jul 12, 2026 8:16pm | Jul 12, 2026 9:06pm | Jul 12, 2026 9:06pm | Jul 12, 2026 9:06pm | Jul 12, 2026 9:06pm | Jul 12, 2026 9:06pm | Jul 12, 2026 9:06pm | BrokenPole |  | Fair | No | Call related
Outage | J.E.26.07.13997 | C001852920 | Ryan Richards | Manchester | Completed | Load_1002477 | Kendal - 210 | Jul 12, 2026 8:14pm | Jul 12, 2026 8:14pm | Jul 12, 2026 10:32pm | Jul 12, 2026 10:32pm | Jul 12, 2026 10:32pm | Jul 13, 2026 12:15am | Jul 13, 2026 12:15am | Jul 13, 2026 12:15am |  |  | Rains | No | Blow. 8 amp junction fuse found line patrol nothing was lighting suspected to be the cause blown fuse was replaced and all customers are now with supply
Outage | J.E.26.07.14165 | C001852917 | Marlon Brown | Trelawny | Completed | Load_263884 | Duncans - 210 | Jul 12, 2026 8:07pm | Jul 12, 2026 8:09pm | Jul 12, 2026 8:15pm | Jul 12, 2026 8:15pm | Jul 12, 2026 8:33pm | Jul 12, 2026 8:34pm | Jul 12, 2026 8:34pm | Jul 12, 2026 8:34pm |  |  | Fair | No | Unable to locate customer via telephone nor direction.
Outage | J.E.26.07.14143 | C001852915 | Clyde Brown | Clarendon | Completed | Load_247305 | Parnassus - 210 | Jul 12, 2026 7:54pm | Jul 12, 2026 7:55pm | Jul 12, 2026 8:28pm | Jul 12, 2026 8:28pm | Jul 12, 2026 9:05pm | Jul 12, 2026 10:40pm | Jul 12, 2026 10:50pm | Jul 12, 2026 10:50pm | Fire |  | Fair | No | Broken secondary phase and neutral caused by truck open 25 kva transformer and repaired with 16ft-#2/0 conductor,3-splicing sleeve 2-preform and 3 clamp.
Outage | J.E.26.07.14153 | C001852914 | Clyde Brown | Clarendon | Completed | Load_244072 | Parnassus - 210 | Jul 12, 2026 7:54pm | Jul 12, 2026 7:55pm | Jul 12, 2026 10:50pm | Jul 12, 2026 10:50pm | Jul 12, 2026 10:50pm | Jul 12, 2026 10:40pm | Jul 12, 2026 10:54pm | Jul 12, 2026 10:54pm | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Broken secondary phase and neutral caused by truck open 25 kva transformer and repaired with 16ft-#2 conductor,3-preform,3-clamp and 3-splicing sleeve
Non-Outage | J.E.26.07.14095 | C001852907 | Horace Malcolm | St.James | Completed | Load_266674 | Bogue - 410 | Jul 12, 2026 6:54pm | Jul 12, 2026 6:55pm | Jul 12, 2026 7:29pm | Jul 12, 2026 8:06pm | Jul 12, 2026 8:06pm | Jul 12, 2026 8:48pm | Jul 12, 2026 8:48pm | Jul 12, 2026 8:48pm |  |  | Fair | No | Clean and remake joints at transformer drop lead use 1clamp voltage 234–236-238-414-417-418
Outage | J.E.26.07.13625 | C001852906 | Wan Carlos Scarlett | St.Catherine | Completed | Load_576209 | Twickenham - 210 | Jul 12, 2026 6:52pm | Jul 12, 2026 7:03pm | Jul 12, 2026 8:08pm | Jul 12, 2026 8:08pm | Jul 12, 2026 9:11pm | Jul 12, 2026 9:16pm | Jul 12, 2026 9:17pm | Jul 12, 2026 9:17pm |  |  | Fair | No | Customer was reconnected from escalation department power supply has been restored
Non-Outage | J.E.26.07.14105 | C001852904 | Edward Royal | null | Completed | null | null | Jul 12, 2026 6:47pm | Jul 12, 2026 6:48pm | Jul 12, 2026 8:10pm | Jul 12, 2026 8:10pm | Jul 12, 2026 8:10pm | Jul 12, 2026 8:10pm | Jul 12, 2026 8:10pm | Jul 12, 2026 8:10pm | BrokenPole |  | Fair | No | Premises not found unable to communicate with customer
Outage | J.E.26.07.14070 | C001852903 | Rusean Allen | KSAN | Completed | Load_242236 | Washington Blvd - 310 | Jul 12, 2026 6:47pm | Jul 12, 2026 6:49pm | Jul 12, 2026 10:15pm | Jul 12, 2026 10:15pm | Jul 12, 2026 10:15pm | Jul 12, 2026 10:21pm | Jul 12, 2026 10:21pm | Jul 12, 2026 10:21pm | Fire |  | Fair | No | Burnt transformer with rami rami enclosure found, transformer needs to be changed. Refer to maintenance department.
Outage | J.E.26.07.13309 | C001852899 | Wan Carlos Scarlett | St.Catherine | Completed | Load_240767 | Twickenham - 210 | Jul 12, 2026 6:37pm | Jul 12, 2026 6:40pm | Jul 12, 2026 6:53pm | Jul 12, 2026 6:53pm | Jul 12, 2026 7:52pm | Jul 12, 2026 8:07pm | Jul 12, 2026 8:08pm | Jul 12, 2026 8:08pm |  |  | Fair | No | Reach at location been calling customer but no answer premises closed
Outage | J.E.26.07.14078 | C001852900 | Donald Cunningham | Portmore | Completed | Load_253186 | Naggo Head - 610 | Jul 12, 2026 6:37pm | Jul 13, 2026 8:34am | Jul 13, 2026 12:56pm | Jul 13, 2026 12:56pm | Jul 13, 2026 1:47pm | Jul 13, 2026 1:50pm | Jul 13, 2026 1:51pm | Jul 13, 2026 1:51pm |  |  | Fair | No | Premises closed
Non-Outage | J.E.26.07.14093 | C001852897 | Clyde Brown | null | Completed | null | null | Jul 12, 2026 6:31pm | Jul 12, 2026 6:34pm | Jul 12, 2026 7:40pm | Jul 12, 2026 7:40pm | Jul 12, 2026 7:46pm | Jul 12, 2026 7:35pm | Jul 12, 2026 7:50pm | Jul 12, 2026 7:50pm | BangingWires |  | Fair | No | Cannot be located customer not answering phone
Outage | J.E.26.07.14085 | C001852898 | Clyde Brown | Clarendon | Completed | Load_238412 | May Pen - 210 | Jul 12, 2026 6:31pm | Jul 12, 2026 6:34pm | Jul 12, 2026 6:44pm | Jul 12, 2026 6:44pm | Jul 12, 2026 7:32pm | Jul 12, 2026 7:30pm | Jul 12, 2026 7:38pm | Jul 12, 2026 7:38pm | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Blown 3 amps fuse for 25 kva transformer caused by motor vehicle accident causing phase and neutral to entangled same cleared and blown fuse replaced.
Outage | J.E.26.07.14063 | C001852895 | Shamour Haughton | St.James | Completed | Load_555724 | Bogue - 310 | Jul 12, 2026 6:24pm | Jul 12, 2026 6:24pm | Jul 12, 2026 7:53pm | Jul 12, 2026 7:53pm | Jul 12, 2026 8:33pm | Jul 12, 2026 8:33pm | Jul 12, 2026 8:35pm | Jul 12, 2026 8:35pm |  |  | Fair | No | Found 1,10amp junction fuse blown, refuse 10amp junction
Outage | J.E.26.07.14064 | C001852896 | Michael Christian | St.James | Completed | Load_241009 | Bogue - 510 | Jul 12, 2026 6:24pm | Jul 12, 2026 6:24pm | Jul 12, 2026 9:52pm | Jul 12, 2026 9:52pm | Jul 12, 2026 10:55pm | Jul 12, 2026 10:58pm | Jul 12, 2026 10:58pm | Jul 12, 2026 10:58pm |  |  | Fair | No | Check and found okay voltage 110 109 at meter
Outage | J.E.26.07.13699 | C001852894 | Donald Cunningham | St.Catherine | Completed | Load_1001347 | Tredegar - 210 | Jul 12, 2026 6:15pm | Jul 12, 2026 6:30pm | Jul 12, 2026 6:50pm | Jul 12, 2026 6:50pm | Jul 12, 2026 9:07pm | Jul 12, 2026 9:07pm | Jul 12, 2026 9:13pm | Jul 12, 2026 9:13pm |  |  | Fair | No | Premises not found
Outage | J.E.26.07.14072 | C001852893 | Collin Robinson | Portland | Completed | Load_249013 | Port Antonio - 310 | Jul 12, 2026 6:00pm | Jul 12, 2026 6:03pm | Jul 12, 2026 7:25pm | Jul 12, 2026 7:25pm | Jul 12, 2026 7:25pm | Jul 12, 2026 7:26pm | Jul 12, 2026 7:26pm | Jul 12, 2026 7:26pm |  |  | Fair | No | Unable to locate customer for better direction
Outage | J.E.26.07.12451 | C001852890 | Andrew Powell | Manchester | Completed | Load_556606 | Spur Tree - 210 | Jul 12, 2026 5:38pm | Jul 12, 2026 5:38pm | Jul 12, 2026 5:54pm | Jul 12, 2026 5:54pm | Jul 12, 2026 5:54pm | Jul 12, 2026 5:54pm | Jul 12, 2026 5:55pm | Jul 12, 2026 5:55pm |  |  | Fair | No | Premises found okay customer stated that supply restored.
Outage | J.E.26.07.14056 | C001852889 | Richard Nicholas | St.Catherine | Completed | Load_260121 | New Michelton - 210 | Jul 12, 2026 5:37pm | Jul 12, 2026 6:05pm | Jul 12, 2026 8:40pm | Jul 12, 2026 8:40pm | Jul 12, 2026 9:07pm | Jul 12, 2026 9:07pm | Jul 12, 2026 9:08pm | Jul 12, 2026 9:08pm | BrokenWire |  | Fair | No | Found ok
Outage | J.E.26.07.14065 | C001852888 | Richard Nicholas | St.Catherine | Completed | Load_266494 | New Michelton - 210 | Jul 12, 2026 5:37pm | Jul 12, 2026 6:05pm | Jul 12, 2026 9:08pm | Jul 12, 2026 9:08pm | Jul 12, 2026 10:26pm | Jul 12, 2026 10:51pm | Jul 12, 2026 10:53pm | Jul 12, 2026 10:53pm |  |  | Fair | No | Replaced blown 25kva transformer 3amp fuse at the nwc water pump.
Outage | J.E.26.07.14019 | C001852887 | Andrew Powell | St.Elizabeth | Completed | Load_292231 | Maggotty - 210 | Jul 12, 2026 5:34pm | Jul 12, 2026 6:45pm | Jul 12, 2026 7:08pm | Jul 12, 2026 7:09pm | Jul 12, 2026 8:10pm | Jul 12, 2026 8:48pm | Jul 12, 2026 8:52pm | Jul 12, 2026 8:52pm |  |  | SevereWind | No | No service wire found at location. Replace broken service wire using 60 feet #6 triplex, three clamps and three service sleeves, voltage leave 114v-114v phase to neutral 228v cross phase, meter #2541285
Outage | J.E.26.07.14041 | C001852886 | Wayne Dillion | St.Elizabeth | Completed | Load_255608 | Maggotty - 110 | Jul 12, 2026 5:34pm | Jul 12, 2026 5:34pm | Jul 12, 2026 7:43pm | Jul 12, 2026 7:44pm | Jul 12, 2026 7:44pm | Jul 12, 2026 8:10pm | Jul 12, 2026 8:12pm | Jul 12, 2026 8:12pm |  |  | Fair | No | Patrol and found one blown 10amp junction fuse no pole #. Replace same and restored supply okay.
Non-Outage | J.E.26.07.07822 | C001852885 | Omar King | St.Ann | Completed | Load_267230 | Ocho Rios - 410 | Jul 12, 2026 5:28pm | Jul 12, 2026 5:28pm | Jul 12, 2026 5:35pm | Jul 12, 2026 5:35pm | Jul 12, 2026 6:14pm | Jul 12, 2026 6:21pm | Jul 12, 2026 6:22pm | Jul 12, 2026 6:22pm |  |  | Fair | No | Problem as been resolved two days ago
Outage | J.E.26.07.13715 | C001852884 | Damion Reid | Manchester | Completed | Load_300881 | Porus - 310 | Jul 12, 2026 5:27pm | Jul 12, 2026 5:28pm | Jul 12, 2026 5:36pm | Jul 12, 2026 5:36pm | Jul 12, 2026 7:42pm | Jul 12, 2026 8:48pm | Jul 12, 2026 8:49pm | Jul 12, 2026 8:49pm |  |  | Fair | No | Blown 8amp junction fuse found cause by contamination line patrol and replace blown fuse
Non-Outage | J.E.26.07.11871 | C001852878 | Omar King | St.Ann | Completed | Load_267464 | Ocho Rios - 310 | Jul 12, 2026 5:26pm | Jul 12, 2026 5:27pm | Jul 12, 2026 7:56pm | Jul 12, 2026 7:56pm | Jul 12, 2026 8:31pm | Jul 12, 2026 8:33pm | Jul 12, 2026 8:33pm | Jul 12, 2026 8:33pm |  |  | Fair | No | Problem as been resolved
Non-Outage | J.E.26.07.11986 | C001852879 | Omar King | St.Ann | Completed | Load_243953 | Ocho Rios - 310 | Jul 12, 2026 5:26pm | Jul 12, 2026 5:27pm | Jul 12, 2026 8:52pm | Jul 12, 2026 8:52pm | Jul 12, 2026 9:25pm | Jul 12, 2026 9:25pm | Jul 12, 2026 9:26pm | Jul 12, 2026 9:26pm |  |  | Fair | No | Problem as been resolved
Non-Outage | J.E.26.07.12740 | C001852880 | Omar King | St.Ann | Completed | Load_252833 | Ocho Rios - 310 | Jul 12, 2026 5:26pm | Jul 12, 2026 5:27pm | Jul 12, 2026 8:34pm | Jul 12, 2026 8:34pm | Jul 12, 2026 8:51pm | Jul 12, 2026 8:52pm | Jul 12, 2026 8:52pm | Jul 12, 2026 8:52pm |  |  | Fair | No | Problem as been resolved
Non-Outage | J.E.26.07.13040 | C001852881 | Omar King | St.Ann | Completed | Load_575117 | Ocho Rios - 310 | Jul 12, 2026 5:26pm | Jul 12, 2026 5:27pm | Jul 12, 2026 6:22pm | Jul 12, 2026 6:22pm | Jul 12, 2026 6:37pm | Jul 12, 2026 6:55pm | Jul 12, 2026 6:55pm | Jul 12, 2026 6:55pm |  |  | Fair | No | Unable to find customer call several times no answer directions not sufficient
Non-Outage | J.E.26.07.13072 | C001852882 | Omar King | St.Ann | Completed | Load_264624 | Ocho Rios - 310 | Jul 12, 2026 5:26pm | Jul 12, 2026 5:27pm | Jul 12, 2026 7:03pm | Jul 12, 2026 7:03pm | Jul 12, 2026 7:35pm | Jul 12, 2026 7:54pm | Jul 12, 2026 7:54pm | Jul 12, 2026 7:54pm |  |  | Fair | No | Problem as been resolved said customer
Outage | J.E.26.07.14020 | C001852883 | Ryan Richards | Manchester | Completed | Load_303123 | Kendal - 210 | Jul 12, 2026 5:26pm | Jul 12, 2026 5:27pm | Jul 12, 2026 6:35pm | Jul 12, 2026 8:29pm | Jul 12, 2026 10:05pm | Jul 12, 2026 10:32pm | Jul 12, 2026 10:32pm | Jul 12, 2026 10:32pm |  |  | Fair | No | Banging secondary phase and neutral found cause by tree limb open 25 kva transformer chop tree limb and reclose Transformer fuse all customers are now with
Outage | J.E.26.07.12520 | C001852877 | Andrew Powell | Manchester | Completed | Load_1002209 | Spur Tree - 210 | Jul 12, 2026 5:24pm | Jul 12, 2026 5:25pm | Jul 12, 2026 5:35pm | Jul 12, 2026 5:37pm | Jul 12, 2026 5:37pm | Jul 12, 2026 5:38pm | Jul 12, 2026 5:38pm | Jul 12, 2026 5:38pm |  |  | Fair | No | Premises found okay customer stated that supply restored.
Outage | J.E.26.07.13375 | C001852876 | Andrew Powell | Manchester | Completed | Load_258651 | Spur Tree - 210 | Jul 12, 2026 5:24pm | Jul 12, 2026 5:25pm | Jul 12, 2026 5:34pm | Jul 12, 2026 5:34pm | Jul 12, 2026 5:36pm | Jul 12, 2026 5:36pm | Jul 12, 2026 5:37pm | Jul 12, 2026 5:37pm |  |  | Fair | No | Premises found okay customer stated that supply restored.
Non-Outage | J.E.26.07.14016 | C001852875 | Edward Royal | null | Completed | null | null | Jul 12, 2026 5:23pm | Jul 12, 2026 5:24pm | Jul 12, 2026 7:30pm | Jul 12, 2026 7:30pm | Jul 12, 2026 7:30pm | Jul 12, 2026 7:31pm | Jul 12, 2026 7:32pm | Jul 12, 2026 7:32pm | Fire |  | Fair | No | Premises not found unable communicate with customer
Outage | J.E.26.07.14010 | C001852874 | Edward Royal | KSAN | Completed | Load_266813 | Hope - 510 | Jul 12, 2026 5:23pm | Jul 12, 2026 5:24pm | Jul 12, 2026 7:23pm | Jul 12, 2026 7:23pm | Jul 12, 2026 7:23pm | Jul 12, 2026 7:28pm | Jul 12, 2026 7:29pm | Jul 12, 2026 7:29pm | BrokenWire |  | Fair | No | Premises not found unable communicate with customer
Outage | J.E.26.07.14039 | C001852870 | Clyde Brown | Clarendon | Completed | Load_239043 | Parnassus - 310 | Jul 12, 2026 5:09pm | Jul 12, 2026 5:10pm | Jul 12, 2026 5:37pm | Jul 12, 2026 5:37pm | Jul 12, 2026 6:12pm | Jul 12, 2026 6:24pm | Jul 12, 2026 6:29pm | Jul 12, 2026 6:29pm |  |  | Fair | No | Blown 15 amps junction fuse at Birds hill,line patrolled and no fault seen ,blown fuse replaced.
Outage | J.E.26.07.14048 | C001852871 | Clyde Brown | Clarendon | Completed | Load_242359 | Parnassus - 310 | Jul 12, 2026 5:09pm | Jul 12, 2026 5:10pm | Jul 12, 2026 6:33pm | Jul 12, 2026 6:33pm | Jul 12, 2026 6:34pm | Jul 12, 2026 6:33pm | Jul 12, 2026 6:35pm | Jul 12, 2026 6:35pm |  |  | Fair | No | Found ok at Chatteau primary school
Outage | J.E.26.07.14034 | C001852868 | Raymond Carr | St.Mary | Completed | Load_352988 | Blackstonedge - 110 | Jul 12, 2026 4:59pm | Jul 12, 2026 5:00pm | Jul 12, 2026 5:12pm | Jul 12, 2026 5:12pm | Jul 12, 2026 6:43pm | Jul 12, 2026 6:58pm | Jul 12, 2026 7:03pm | Jul 12, 2026 7:03pm |  |  | Fair | No | Blown junction fuse found line patrol and found okay, however tree contact. A 10 amp fuse was used to renew supply was restored.
Outage | J.E.26.07.13216 | C001852867 | Clyde Brown | St.Catherine | Completed | Load_265801 | Rhodens Pen - 310 | Jul 12, 2026 4:48pm | Jul 12, 2026 6:13pm | Jul 12, 2026 6:35pm | Jul 12, 2026 6:36pm | Jul 12, 2026 6:37pm | Jul 12, 2026 6:37pm | Jul 12, 2026 6:42pm | Jul 12, 2026 6:42pm |  |  | Fair | No | Customer said he did not make call to JPS
Outage | J.E.26.07.13996 | C001852864 | Michael Christian | St.James | Completed | Load_240742 | Bogue - 610 | Jul 12, 2026 4:22pm | Jul 12, 2026 4:22pm | Jul 12, 2026 8:31pm | Jul 12, 2026 8:31pm | Jul 12, 2026 9:44pm | Jul 12, 2026 9:52pm | Jul 12, 2026 9:52pm | Jul 12, 2026 9:52pm |  |  | Fair | No | Premises not found
Outage | J.E.26.07.14002 | C001852865 | Michael Christian | St.James | Completed | Load_302380 | Bogue - 510 | Jul 12, 2026 4:22pm | Jul 12, 2026 4:22pm | Jul 12, 2026 5:50pm | Jul 12, 2026 5:50pm | Jul 12, 2026 5:50pm | Jul 12, 2026 5:52pm | Jul 12, 2026 5:52pm | Jul 12, 2026 5:52pm |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.14008 | C001852866 | Michael Christian | St.James | Completed | Load_261335 | Bogue - 610 | Jul 12, 2026 4:22pm | Jul 12, 2026 4:22pm | Jul 12, 2026 6:46pm | Jul 12, 2026 6:46pm | Jul 12, 2026 7:47pm | Jul 12, 2026 8:30pm | Jul 12, 2026 8:30pm | Jul 12, 2026 8:30pm |  |  | Rains | No | Reset 1 25 kava transformer cause banging wire
Outage | J.E.26.07.13925 | C001852863 | Horace Malcolm | St.James | Completed | Load_259820 | Rose Hall - 210 | Jul 12, 2026 4:19pm | Jul 12, 2026 4:22pm | Jul 12, 2026 4:41pm | Jul 12, 2026 4:41pm | Jul 12, 2026 5:31pm | Jul 12, 2026 6:11pm | Jul 12, 2026 6:11pm | Jul 12, 2026 6:11pm |  |  | Fair | No | Unable to locate customer multiple calls to customer unavailable check and found area ok
Non-Outage | J.E.26.07.10559 | C001852860 | Oshane Warren | Westmoreland | Completed | Load_240662 | Paradise - 310 | Jul 12, 2026 3:57pm | Jul 12, 2026 6:43pm | Jul 13, 2026 9:52am | Jul 13, 2026 9:52am | Jul 13, 2026 12:25pm | Jul 13, 2026 12:25pm | Jul 13, 2026 12:26pm | Jul 13, 2026 12:26pm |  |  | Fair | No | Internal problem advice to fix
Non-Outage | J.E.26.07.11601 | C001852861 | Oshane Warren | Westmoreland | Completed | Load_266994 | Paradise - 310 | Jul 12, 2026 3:57pm | Jul 12, 2026 6:43pm | Jul 12, 2026 7:47pm | Jul 12, 2026 9:39pm | Jul 12, 2026 11:02pm | Jul 12, 2026 11:04pm | Jul 12, 2026 11:04pm | Jul 12, 2026 11:04pm |  |  | Fair | No | Unable to locate or contact customer
Outage | J.E.26.07.13959 | C001852858 | Shamour Haughton | St.James | Completed | Load_267594 | Bogue - 310 | Jul 12, 2026 3:55pm | Jul 12, 2026 3:59pm | Jul 12, 2026 7:34pm | Jul 12, 2026 7:34pm | Jul 12, 2026 7:34pm | Jul 12, 2026 7:34pm | Jul 12, 2026 7:35pm | Jul 12, 2026 7:35pm |  |  | Fair | No | Related to previous call
Outage | J.E.26.07.13984 | C001852857 | Shamour Haughton | St.James | Completed | Load_263567 | Bogue - 310 | Jul 12, 2026 3:55pm | Jul 12, 2026 3:56pm | Jul 12, 2026 4:00pm | Jul 12, 2026 4:00pm | Jul 12, 2026 4:18pm | Jul 12, 2026 7:26pm | Jul 12, 2026 7:28pm | Jul 12, 2026 7:28pm |  |  | Fair | No | Found 2,65amp tripsaver down, reclose 2,65amp tripsaver at pole number 057819
Outage | J.E.26.07.13990 | C001852856 | Michael Christian | St.James | Completed | Load_1001324 | Bogue - 510 | Jul 12, 2026 3:55pm | Jul 12, 2026 3:56pm | Jul 12, 2026 4:28pm | Jul 12, 2026 4:28pm | Jul 12, 2026 5:17pm | Jul 12, 2026 5:50pm | Jul 12, 2026 5:50pm | Jul 12, 2026 5:50pm | Fire |  | Fair | No | Found 1 20 1 8 amps junction out cause by house top replace 1 20 amp %%aaa
Non-Outage | J.E.26.07.12285 | C001852854 | Andrew Powell | null | Completed | null | null | Jul 12, 2026 3:54pm | Jul 12, 2026 3:55pm | Jul 12, 2026 3:58pm | Jul 12, 2026 3:58pm | Jul 12, 2026 3:58pm | Jul 12, 2026 3:58pm | Jul 12, 2026 3:59pm | Jul 12, 2026 3:59pm |  |  | Fair | No | Premises found okay customer stated that supply restored.
Outage | J.E.26.07.13852 | C001852853 | Horace Malcolm | St.James | Completed | Load_267491 | Queens Drive - 710 | Jul 12, 2026 3:54pm | Jul 12, 2026 3:55pm | Jul 12, 2026 4:30pm | Jul 12, 2026 4:30pm | Jul 12, 2026 4:30pm | Jul 12, 2026 4:33pm | Jul 12, 2026 4:33pm | Jul 12, 2026 4:33pm |  |  | Fair | No | Related to previous call job number 13656 both customers on same premises Clean and reamake joints at pole used 2clamps voltage 117-116-233
Outage | J.E.26.07.13920 | C001852855 | Shamour Haughton | St.James | Completed | Load_301657 | Bogue - 310 | Jul 12, 2026 3:54pm | Jul 12, 2026 3:56pm | Jul 12, 2026 7:33pm | Jul 12, 2026 7:33pm | Jul 12, 2026 7:33pm | Jul 12, 2026 7:33pm | Jul 12, 2026 7:34pm | Jul 12, 2026 7:34pm |  |  | Fair | No | Related to previous call
Outage | J.E.26.07.12488 | C001852851 | Andrew Powell | Manchester | Completed | Load_302821 | Spur Tree - 210 | Jul 12, 2026 3:53pm | Jul 12, 2026 3:53pm | Jul 12, 2026 4:04pm | Jul 12, 2026 4:04pm | Jul 12, 2026 4:04pm | Jul 12, 2026 4:04pm | Jul 12, 2026 4:05pm | Jul 12, 2026 4:05pm |  |  | Fair | No | Premises found okay supply restored.
Outage | J.E.26.07.12550 | C001852849 | Andrew Powell | Manchester | Completed | Load_302852 | Spur Tree - 210 | Jul 12, 2026 3:45pm | Jul 12, 2026 3:52pm | Jul 12, 2026 4:05pm | Jul 12, 2026 4:05pm | Jul 12, 2026 4:06pm | Jul 12, 2026 4:06pm | Jul 12, 2026 4:07pm | Jul 12, 2026 4:07pm |  |  | Fair | No | Premises found okay customer stated that supply restored.
Outage | J.E.26.07.12576 | C001852848 | Andrew Powell | Manchester | Completed | Load_244872 | Spur Tree - 210 | Jul 12, 2026 3:42pm | Jul 12, 2026 3:42pm | Jul 12, 2026 3:50pm | Jul 12, 2026 3:50pm | Jul 12, 2026 3:50pm | Jul 12, 2026 3:50pm | Jul 12, 2026 3:51pm | Jul 12, 2026 3:51pm |  |  | Fair | No | Premises found okay customer stated that supply restored yesterday.
Outage | J.E.26.07.12552 | C001852847 | Andrew Powell | Manchester | Completed | Load_252404 | Spur Tree - 210 | Jul 12, 2026 3:39pm | Jul 12, 2026 5:37pm | Jul 12, 2026 5:55pm | Jul 12, 2026 5:55pm | Jul 12, 2026 6:32pm | Jul 12, 2026 7:04pm | Jul 12, 2026 7:06pm | Jul 12, 2026 7:06pm |  |  | SevereWind | No | Isolate and close 25 kva transformer circuit by pole number 036575 to repair one pole span of broken secondary neutral conductor using one automatic splicing sleeves and 30 feet #2 AA conductor, restore supply okay.
Outage | J.E.26.07.13213 | C001852846 | Wayne Dillion | St.Elizabeth | Completed | Load_243601 | Maggotty - 210 | Jul 12, 2026 3:39pm | Jul 12, 2026 3:53pm | Jul 12, 2026 6:38pm | Jul 12, 2026 6:38pm | Jul 12, 2026 6:38pm | Jul 12, 2026 6:41pm | Jul 12, 2026 6:41pm | Jul 12, 2026 6:41pm |  |  | Fair | No | Please refer to maintenance for a extension of the secondary for customer to get connected.
Outage | J.E.26.07.13907 | C001852845 | Edward Royal | KSAN | Completed | Load_557436 | West Kings House - 310 | Jul 12, 2026 3:37pm | Jul 12, 2026 3:41pm | Jul 12, 2026 6:20pm | Jul 12, 2026 6:20pm | Jul 12, 2026 6:47pm | Jul 12, 2026 6:48pm | Jul 12, 2026 6:57pm | Jul 12, 2026 6:57pm |  |  | Fair | No | Spliced and reconnected secondary phase using 2 single bolt clamp
Non-Outage | J.E.26.07.13693 | C001852844 | Wayne Dillion | null | Completed | null | null | Jul 12, 2026 3:22pm | Jul 12, 2026 6:45pm | Jul 12, 2026 9:04pm | Jul 12, 2026 9:04pm | Jul 12, 2026 9:04pm | Jul 12, 2026 9:24pm | Jul 12, 2026 9:24pm | Jul 12, 2026 9:24pm | BrokenWire |  | Fair | No | Supply check and found disconnected at pole. Connect same using 2 clamps. Supply leave working okay reading 113v, 114v and cross phase 227volts.
Non-Outage | J.E.26.07.13855 | C001852843 | Daniel Francis | null | Completed | null | null | Jul 12, 2026 3:21pm | Jul 12, 2026 3:23pm | Jul 12, 2026 4:19pm | Jul 12, 2026 4:19pm | Jul 12, 2026 5:14pm | Jul 12, 2026 7:19pm | Jul 12, 2026 7:33pm | Jul 12, 2026 7:33pm | Fire |  | Fair | No | Found secondary phase broken cause illegal connections removed service line from secondary no meter and removed multiple connections
Outage | J.E.26.07.13431 | C001852841 | Andrew Powell | Manchester | Completed | Load_263960 | Spur Tree - 210 | Jul 12, 2026 3:21pm | Jul 12, 2026 3:38pm | Jul 12, 2026 3:45pm | Jul 12, 2026 3:46pm | Jul 12, 2026 3:46pm | Jul 12, 2026 3:46pm | Jul 12, 2026 3:47pm | Jul 12, 2026 3:47pm |  |  | Fair | No | Premises found okay customers stated that supply restored.
Outage | J.E.26.07.13900 | C001852840 | Wayne Dillion | St.Elizabeth | Completed | Load_237725 | Maggotty - 110 | Jul 12, 2026 3:21pm | Jul 12, 2026 3:22pm | Jul 12, 2026 6:31pm | Jul 12, 2026 6:31pm | Jul 12, 2026 6:31pm | Jul 12, 2026 6:33pm | Jul 12, 2026 6:33pm | Jul 12, 2026 6:33pm |  |  | Fair | No | Customer said supply was restored.
Outage | J.E.26.07.13915 | C001852839 | Wayne Dillion | St.Elizabeth | Completed | Load_263203 | Maggotty - 110 | Jul 12, 2026 3:21pm | Jul 12, 2026 3:22pm | Jul 12, 2026 4:58pm | Jul 12, 2026 5:27pm | Jul 12, 2026 5:27pm | Jul 12, 2026 6:25am | Jul 12, 2026 6:30pm | Jul 12, 2026 6:30pm |  |  | Fair | No | Patrol and found one blown 30amp junction fuse no pole # and 2 blown 15amp junction fuse no pole #. Replace same and supply restored okay.
Non-Outage | J.E.26.07.13810 | C001852837 | Richman Whyte | null | Completed | null | null | Jul 12, 2026 3:18pm | Jul 12, 2026 3:20pm | Jul 12, 2026 6:33pm | Jul 12, 2026 6:33pm | Jul 12, 2026 6:33pm | Jul 12, 2026 6:35pm | Jul 12, 2026 6:35pm | Jul 12, 2026 6:35pm |  |  | Fair | No | Premises not found
Outage | J.E.26.07.13769 | C001852836 | Richard Nicholas | St.Catherine | Completed | Load_260121 | New Michelton - 210 | Jul 12, 2026 3:18pm | Jul 12, 2026 3:23pm | Jul 12, 2026 6:15pm | Jul 12, 2026 6:15pm | Jul 12, 2026 7:11pm | Jul 12, 2026 8:36pm | Jul 12, 2026 8:38pm | Jul 12, 2026 8:38pm |  |  | Fair | No | Retention 1 span of banging secondary phase and neutral conductors.replaced blown10amp junctions fuse near to pole #213557 and blown 10kva transformer 2amp fuse on pole #0103342.
Outage | J.E.26.07.13801 | C001852838 | Richman Whyte | Westmoreland | Completed | Load_240095 | Paradise - 210 | Jul 12, 2026 3:18pm | Jul 12, 2026 3:47pm | Jul 12, 2026 6:35pm | Jul 12, 2026 6:35pm | Jul 12, 2026 7:54pm | Jul 12, 2026 7:55pm | Jul 12, 2026 7:55pm | Jul 12, 2026 7:55pm |  |  | Fair | No | Close back twenty five kva transformer fuse
Outage | J.E.26.07.13620 | C001852835 | Clyde Brown | Clarendon | Completed | Load_249758 | Parnassus - 210 | Jul 12, 2026 3:13pm | Jul 12, 2026 3:13pm | Jul 12, 2026 3:35pm | Jul 12, 2026 3:35pm | Jul 12, 2026 3:35pm | Jul 12, 2026 3:36pm | Jul 12, 2026 3:40pm | Jul 12, 2026 3:40pm | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Found ok,supply restored
Outage | J.E.26.07.13871 | C001852831 | Neville Spencer | Clarendon | Completed | Load_237763 | May Pen - 110 | Jul 12, 2026 3:11pm | Jul 12, 2026 3:12pm | Jul 12, 2026 3:21pm | Jul 12, 2026 3:21pm | Jul 12, 2026 4:19pm | Jul 12, 2026 4:42pm | Jul 12, 2026 4:44pm | Jul 12, 2026 4:44pm |  |  | Fair | No | Renew blown 25 amp j/ fuse area restored
Outage | J.E.26.07.13878 | C001852833 | Neville Spencer | Clarendon | Completed | Load_241942 | May Pen - 110 | Jul 12, 2026 3:11pm | Jul 12, 2026 3:12pm | Jul 12, 2026 4:47pm | Jul 12, 2026 4:47pm | Jul 12, 2026 6:11pm | Jul 12, 2026 6:43pm | Jul 12, 2026 6:44pm | Jul 12, 2026 6:44pm |  |  | Fair | No | Found defective meter socket temporary repair voltage reading 112 customer advised.
Outage | J.E.26.07.13889 | C001852832 | Neville Spencer | Clarendon | Completed | Load_253095 | May Pen - 110 | Jul 12, 2026 3:11pm | Jul 12, 2026 3:12pm | Jul 12, 2026 4:45pm | Jul 12, 2026 4:45pm | Jul 12, 2026 4:46pm | Jul 12, 2026 4:46pm | Jul 12, 2026 4:47pm | Jul 12, 2026 4:47pm |  |  | Fair | No | Renew blown 25 amp j/ fuse area restored.
Non-Outage | J.E.26.07.13886 | C001852830 | Floyd Taylor | Trelawny | Completed | Load_292361 | Greenwood - 210 | Jul 12, 2026 3:02pm | Jul 12, 2026 3:02pm | Jul 12, 2026 3:43pm | Jul 12, 2026 3:43pm | Jul 12, 2026 4:11pm | Jul 12, 2026 4:12pm | Jul 12, 2026 4:12pm | Jul 12, 2026 4:12pm |  |  | Fair | No | Customer had an electrician fix the issue
Outage | J.E.26.07.13868 | C001852827 | Raymond Carr | St.Mary | Completed | Load_352775 | Blackstonedge - 110 | Jul 12, 2026 2:52pm | Jul 12, 2026 3:34pm | Jul 12, 2026 7:03pm | Jul 12, 2026 7:03pm | Jul 12, 2026 7:03pm | Jul 12, 2026 6:56pm | Jul 12, 2026 7:05pm | Jul 12, 2026 7:05pm |  |  | Fair | No | Supply was restored.
Outage | J.E.26.07.11248 | C001852826 | Michael Christian | St.James | Completed | Load_238758 | Bogue - 610 | Jul 12, 2026 2:49pm | Jul 12, 2026 3:49pm | Jul 12, 2026 5:53pm | Jul 12, 2026 5:53pm | Jul 12, 2026 6:41pm | Jul 12, 2026 6:45pm | Jul 12, 2026 6:45pm | Jul 12, 2026 6:45pm |  |  | Fair | No | No wire found send to field service need 110 ft
Outage | J.E.26.07.09542 | C001852825 | Floyd Taylor | St.James | Completed | Load_252748 | Rose Hall - 210 | Jul 12, 2026 2:45pm | Jul 12, 2026 2:46pm | Jul 12, 2026 4:12pm | Jul 12, 2026 4:12pm | Jul 12, 2026 5:09pm | Jul 12, 2026 5:49pm | Jul 12, 2026 5:53pm | Jul 12, 2026 5:53pm |  |  | Fair | No | Mixing up of meter please refer to field service
Outage | J.E.26.07.13828 | C001852824 | Collin Robinson | Portland | Completed | Load_262308 | Port Antonio - 310 | Jul 12, 2026 2:44pm | Jul 12, 2026 2:44pm | Jul 12, 2026 4:08pm | Jul 12, 2026 4:08pm | Jul 12, 2026 4:36pm | Jul 12, 2026 4:36pm | Jul 12, 2026 4:51pm | Jul 12, 2026 4:51pm |  |  | Fair | No | Entangle open secondary conductor and reset 10 KVA transformer
Outage | J.E.26.07.13847 | C001852823 | Richard Nicholas | St.Catherine | Completed | Load_568289 | New Michelton - 410 | Jul 12, 2026 2:37pm | Jul 12, 2026 2:39pm | Jul 12, 2026 3:46pm | Jul 12, 2026 3:46pm | Jul 12, 2026 5:37pm | Jul 12, 2026 6:09pm | Jul 12, 2026 6:11pm | Jul 12, 2026 6:11pm |  |  | Fair | No | Replaced defective drop out switch with a 80amp fuse,on the primary dead under ground pole.
Outage | J.E.26.07.13860 | C001852822 | Rusean Allen | KSAS | Completed | Load_264323 | Greenwich - 310 | Jul 12, 2026 2:31pm | Jul 13, 2026 7:48am | Jul 13, 2026 9:59am | Jul 13, 2026 10:00am | Jul 13, 2026 10:13am | Jul 13, 2026 10:14am | Jul 13, 2026 10:15am | Jul 13, 2026 10:15am |  |  | Fair | No | Power was restored
Outage | J.E.26.07.13857 | C001852821 | Stephen Taylor | St.Thomas | Completed | Load_247886 | Lysson - 410 | Jul 12, 2026 2:29pm | Jul 12, 2026 2:31pm | Jul 12, 2026 8:36pm | Jul 12, 2026 8:36pm | Jul 12, 2026 9:36pm | Jul 12, 2026 9:36pm | Jul 12, 2026 9:39pm | Jul 12, 2026 9:39pm |  |  | Fair | No | Check was make and found out that 25kva transformer was defective
Outage | J.E.26.07.13656 | C001852819 | Horace Malcolm | St.James | Completed | Load_292531 | Queens Drive - 710 | Jul 12, 2026 2:24pm | Jul 12, 2026 2:24pm | Jul 12, 2026 3:28pm | Jul 12, 2026 3:28pm | Jul 12, 2026 4:16pm | Jul 12, 2026 4:30pm | Jul 12, 2026 4:30pm | Jul 12, 2026 4:30pm |  |  | Fair | No | Clean and remake joints at pole used 2clamps voltage 117-116-233
Outage | J.E.26.07.13833 | C001852817 | Raymond Carr | St.Mary | Completed | Load_261992 | Blackstonedge - 110 | Jul 12, 2026 2:21pm | Jul 12, 2026 2:33pm | Jul 12, 2026 7:05pm | Jul 12, 2026 7:05pm | Jul 12, 2026 7:14pm | Jul 12, 2026 7:35pm | Jul 12, 2026 7:48pm | Jul 12, 2026 7:48pm |  |  | Fair | No | Blown junction fuse found at pole number 0014181, line patrol and found ok, still unable to ascertain cause of outage. A 20 amp fuse was used to renew supply was restored. Nb. Refer to maintenance department for a detailed patrol on line section.
Outage | J.E.26.07.13805 | C001852813 | Rayon Foster | Hanover | Completed | Load_1001393 | Orange Bay - 310 | Jul 12, 2026 1:52pm | Jul 12, 2026 1:56pm | Jul 12, 2026 2:06pm | Jul 12, 2026 2:06pm | Jul 12, 2026 3:02pm | Jul 12, 2026 3:15pm | Jul 12, 2026 3:15pm | Jul 12, 2026 3:15pm |  |  | Fair | No | Check and found working ok voltage found at pothead 114v/114v/228v on load and line side customer was advised to get a electrician to do some internal checks
Outage | J.E.26.07.13813 | C001852809 | Stephen Taylor | St.Thomas | Completed | Load_242361 | Good Year - 110 | Jul 12, 2026 1:42pm | Jul 12, 2026 1:43pm | Jul 12, 2026 2:23pm | Jul 12, 2026 2:23pm | Jul 12, 2026 4:19pm | Jul 12, 2026 4:19pm | Jul 12, 2026 5:29pm | Jul 12, 2026 5:29pm | BrokenWire |  | Fair | No | Transformer fuse down patrol secondary line and found tree and line clear the line and close up transformer with 3ams fuse
Outage | J.E.26.07.13817 | C001852808 | Stephen Taylor | St.Thomas | Completed | Load_263676 | Good Year - 110 | Jul 12, 2026 1:42pm | Jul 12, 2026 1:43pm | Jul 12, 2026 5:30pm | Jul 12, 2026 5:30pm | Jul 12, 2026 5:30pm | Jul 12, 2026 5:31pm | Jul 12, 2026 5:31pm | Jul 12, 2026 5:31pm |  |  | Fair | No | Check with customer and customer say power is back
Outage | J.E.26.07.13791 | C001852807 | Horace Malcolm | St.James | Completed | Load_258936 | Queens Drive - 710 | Jul 12, 2026 1:26pm | Jul 12, 2026 1:29pm | Jul 12, 2026 2:20pm | Jul 12, 2026 2:20pm | Jul 12, 2026 3:18pm | Jul 12, 2026 3:20pm | Jul 12, 2026 3:20pm | Jul 12, 2026 3:20pm |  |  | Fair | No | Unable to locate premises no directions given multiple calls to customer unavailable
Outage | J.E.26.07.13802 | C001852806 | Rusean Allen | KSAS | Completed | Load_244328 | Cane River - 610 | Jul 12, 2026 1:24pm | Jul 12, 2026 1:24pm | Jul 12, 2026 2:19pm | Jul 12, 2026 2:19pm | Jul 12, 2026 3:31pm | Jul 12, 2026 3:31pm | Jul 12, 2026 3:32pm | Jul 12, 2026 3:32pm |  |  | Fair | No | Found okay
Outage | J.E.26.07.13803 | C001852804 | Stephen Taylor | St.Thomas | Completed | Load_249841 | Cane River - 310 | Jul 12, 2026 1:22pm | Jul 12, 2026 1:24pm | Jul 13, 2026 12:10pm | Jul 13, 2026 12:10pm | Jul 13, 2026 12:30pm | Jul 13, 2026 12:30pm | Jul 13, 2026 12:31pm | Jul 13, 2026 12:31pm | BrokenWire |  | Fair | No | Clean up single phase use 2 clamps reading 112,113.225 customer is now okay
Non-Outage | J.E.26.07.12310 | C001852801 | Elvis Trowers | KSAN | Completed | Load_252653 | West Kings House - 310 | Jul 12, 2026 1:19pm | Jul 12, 2026 1:25pm | Jul 12, 2026 2:40pm | Jul 12, 2026 2:40pm | Jul 12, 2026 2:53pm | Jul 12, 2026 2:57pm | Jul 12, 2026 2:57pm | Jul 12, 2026 2:57pm |  |  | Fair | Yes | Premises checked and found ok upon arrival, customer was also spoken with, however she suggested that the situation was resolved by another crew from yesterday.
Non-Outage | J.E.26.07.12381 | C001852800 | Fredrick Hamilton | KSAN | Completed | Load_246913 | West Kings House - 210 | Jul 12, 2026 1:19pm | Jul 13, 2026 8:05am | Jul 13, 2026 8:09am | Jul 13, 2026 10:28am | Jul 13, 2026 10:32am | Jul 13, 2026 10:35am | Jul 13, 2026 10:36am | Jul 13, 2026 10:36am |  |  | Fair | No | Premises visited and customer power was restored fully previously Premises is ok
Non-Outage | J.E.26.07.12924 | C001852799 | Christopher Edwards | KSAN | Completed | Load_238308 | Constant Spring - 310 | Jul 12, 2026 1:19pm | Jul 12, 2026 1:19pm | Jul 12, 2026 2:03pm | Jul 12, 2026 2:03pm | Jul 12, 2026 2:03pm | Jul 12, 2026 2:03pm | Jul 12, 2026 2:04pm | Jul 12, 2026 2:04pm |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Non-Outage | J.E.26.07.13732 | C001852798 | Elvis Trowers | KSAN | Completed | Load_557436 | West Kings House - 310 | Jul 12, 2026 1:19pm | Jul 12, 2026 1:20pm | Jul 12, 2026 2:19pm | Jul 12, 2026 2:19pm | Jul 12, 2026 2:29pm | Jul 12, 2026 2:38pm | Jul 12, 2026 2:38pm | Jul 12, 2026 2:38pm |  |  | Fair | Yes | Happened to be internal when checked, electrician was also on the location, voltage when checked was left at 118 +119=237 volts.
Non-Outage | J.E.26.07.11328 | C001852797 | Christopher Edwards | KSAN | Completed | Load_257052 | Constant Spring - 410 | Jul 12, 2026 1:18pm | Jul 12, 2026 1:19pm | Jul 12, 2026 2:04pm | Jul 12, 2026 2:04pm | Jul 12, 2026 2:37pm | Jul 12, 2026 3:00pm | Jul 12, 2026 3:00pm | Jul 12, 2026 3:00pm | Fire |  | Fair | No | Clear illegal connections off open secondary that was causing wire to bang
Non-Outage | J.E.26.07.12664 | C001852796 | Raymond Carr | null | Completed | null | null | Jul 12, 2026 1:18pm | Jul 12, 2026 1:20pm | Jul 12, 2026 2:49pm | Jul 12, 2026 2:49pm | Jul 12, 2026 3:34pm | Jul 12, 2026 3:13pm | Jul 12, 2026 3:36pm | Jul 12, 2026 3:36pm | LowHangingWires |  | Fair | No | Supply found okay, however customer couldn’t be contacted.
Outage | J.E.26.07.13799 | C001852795 | Lancelot Brown | Hanover | Completed | Load_302749 | Orange Bay - 310 | Jul 12, 2026 1:17pm | Jul 12, 2026 1:17pm | Jul 12, 2026 1:47pm | Jul 12, 2026 1:47pm | Jul 12, 2026 3:54pm | Jul 12, 2026 3:58pm | Jul 12, 2026 3:59pm | Jul 12, 2026 3:59pm |  |  | SevereWind | No | Isolate bank of 2-50kva remake corroded dropleed joint used three pg clamps at pothead 110-110-202-220-221–230 customer has internal trouble advise customer to get electrician
Non-Outage | J.E.26.07.12343 | C001852789 | Rusean Allen | null | Completed | null | null | Jul 12, 2026 1:11pm | Jul 12, 2026 1:20pm | Jul 12, 2026 4:54pm | Jul 12, 2026 4:54pm | Jul 12, 2026 5:55pm | Jul 12, 2026 6:00pm | Jul 12, 2026 6:00pm | Jul 12, 2026 6:00pm | Fire |  | Fair | No | Broken secondary wire found, wire was spliced retention and reconnected.
Outage | J.E.26.07.12816 | C001852792 | Fitzroy Turner | KSAS | Completed | Load_291482 | Greenwich - 510 | Jul 12, 2026 1:11pm | Jul 12, 2026 1:20pm | Jul 12, 2026 4:19pm | Jul 12, 2026 4:19pm | Jul 12, 2026 4:21pm | Jul 12, 2026 4:22pm | Jul 12, 2026 4:25pm | Jul 12, 2026 4:25pm |  |  | Fair | No | Customer meter not communicating please email to field service department to have issues resolved
Outage | J.E.26.07.13764 | C001852793 | Ryan Richards | Manchester | Completed | Load_239884 | Kendal - 210 | Jul 12, 2026 1:11pm | Jul 12, 2026 1:12pm | Jul 12, 2026 1:59pm | Jul 12, 2026 1:59pm | Jul 12, 2026 3:35pm | Jul 12, 2026 6:32pm | Jul 12, 2026 6:32pm | Jul 12, 2026 6:32pm |  |  | Rains | No | 2 blown 40 amp junction fuse found line patrol nothing found blown 40 amp fuses was replaced further check made where one 50 amp junction fuse found fuse was replaced and all customers are now with supply
Outage | J.E.26.07.13767 | C001852794 | Ryan Richards | Manchester | Completed | Load_261672 | Kendal - 210 | Jul 12, 2026 1:11pm | Jul 12, 2026 1:12pm | Jul 12, 2026 3:52pm | Jul 12, 2026 6:32pm | Jul 12, 2026 6:32pm | Jul 12, 2026 6:33pm | Jul 12, 2026 6:33pm | Jul 12, 2026 6:33pm |  |  | Rains | No | Same as the other 40&50 amp junction fuse replaced
Outage | J.E.26.07.13775 | C001852790 | Ryan Richards | Manchester | Completed | Load_245077 | Kendal - 210 | Jul 12, 2026 1:11pm | Jul 12, 2026 1:12pm | Jul 12, 2026 5:15pm | Jul 12, 2026 6:34pm | Jul 12, 2026 8:27pm | Jul 12, 2026 8:28pm | Jul 12, 2026 8:29pm | Jul 12, 2026 8:29pm |  |  | Rains | No | Blown 40&50 mp junction fuse replaced
Outage | J.E.26.07.13784 | C001852791 | Ryan Richards | Manchester | Completed | Load_259484 | Kendal - 210 | Jul 12, 2026 1:11pm | Jul 12, 2026 1:12pm | Jul 12, 2026 3:52pm | Jul 12, 2026 6:33pm | Jul 12, 2026 6:33pm | Jul 12, 2026 6:34pm | Jul 12, 2026 6:34pm | Jul 12, 2026 6:34pm |  |  | Rains | No | Same as the other 40&50 amp junction fuses was replaced
Outage | J.E.26.07.13788 | C001852788 | Richard Samuda | Manchester | Completed | Load_265440 | Kendal - 210 | Jul 12, 2026 1:11pm | Jul 13, 2026 8:01am | Jul 13, 2026 12:27pm | Jul 13, 2026 1:57pm | Jul 13, 2026 3:54pm | Jul 13, 2026 3:54pm | Jul 13, 2026 3:54pm | Jul 13, 2026 3:54pm |  |  | Fair | No | Found ok
Outage | J.E.26.07.13790 | C001852785 | Lancelot Brown | Hanover | Completed | Load_254570 | Orange Bay - 310 | Jul 12, 2026 1:05pm | Jul 12, 2026 1:07pm | Jul 12, 2026 1:47pm | Jul 12, 2026 4:03pm | Jul 12, 2026 6:03pm | Jul 12, 2026 6:14pm | Jul 12, 2026 7:46pm | Jul 12, 2026 7:46pm | BrokenWire |  | Rains | No | Splice and retention triplex service line used twenty five feet #6 three pg clamps vl at meter socket 112-114-226 supply restore
Outage | J.E.26.07.13700 | C001852780 | Donald Cunningham | Portmore | Completed | Load_576148 | Naggo Head - 610 | Jul 12, 2026 12:51pm | Jul 13, 2026 8:34am | Jul 13, 2026 2:38pm | Jul 13, 2026 2:39pm | Jul 13, 2026 3:08pm | Jul 13, 2026 3:09pm | Jul 13, 2026 3:09pm | Jul 13, 2026 3:09pm |  |  | Fair | No | Premises closed
Outage | J.E.26.07.13717 | C001852779 | Donald Cunningham | Portmore | Completed | Load_269534 | Naggo Head - 510 | Jul 12, 2026 12:51pm | Jul 13, 2026 8:34am | Jul 13, 2026 12:00pm | Jul 13, 2026 12:00pm | Jul 13, 2026 12:32pm | Jul 13, 2026 12:33pm | Jul 13, 2026 12:55pm | Jul 13, 2026 12:55pm | BrokenWire |  | Fair | No | Disconnect 3 wire service broken down stanchion abandon building
Outage | J.E.26.07.12648 | C001852778 | Fitzroy Turner | KSAS | Completed | Load_238916 | Three Miles - 410 | Jul 12, 2026 12:50pm | Jul 12, 2026 1:11pm | Jul 12, 2026 4:29pm | Jul 12, 2026 4:29pm | Jul 12, 2026 4:35pm | Jul 12, 2026 4:42pm | Jul 12, 2026 5:23pm | Jul 12, 2026 5:23pm |  |  | Fair | No | Customer meter not communicating field service needs to visit this location
Non-Outage | J.E.26.07.12825 | C001852777 | Edward Royal | KSAS | Completed | Load_252263 | Duhaney - 310 | Jul 12, 2026 12:49pm | Jul 12, 2026 12:50pm | Jul 12, 2026 1:19pm | Jul 12, 2026 1:19pm | Jul 12, 2026 1:27pm | Jul 12, 2026 1:41pm | Jul 12, 2026 1:41pm | Jul 12, 2026 1:41pm |  |  | Fair | No | Premises found ok voltage reading 236 117 118 v
Non-Outage | J.E.26.07.13760 | C001852776 | Edward Royal | KSAS | Completed | Load_251395 | Duhaney - 310 | Jul 12, 2026 12:49pm | Jul 12, 2026 12:50pm | Jul 12, 2026 1:41pm | Jul 12, 2026 1:41pm | Jul 12, 2026 2:16pm | Jul 12, 2026 2:17pm | Jul 12, 2026 2:17pm | Jul 12, 2026 2:17pm |  |  | Fair | No | Premises found close
Outage | J.E.26.07.13733 | C001852775 | Rayon Foster | Hanover | Completed | Load_259699 | Orange Bay - 310 | Jul 12, 2026 12:48pm | Jul 12, 2026 1:05pm | Jul 12, 2026 3:15pm | Jul 12, 2026 3:15pm | Jul 12, 2026 3:49pm | Jul 12, 2026 4:42pm | Jul 12, 2026 4:45pm | Jul 12, 2026 4:45pm |  |  | Fair | No | Patrol secondary line to find 1 tripped 25kva transformer complete line patrol before resetting tripped 25kva transformer
Outage | J.E.26.07.13735 | C001852774 | Lancelot Brown | Hanover | Completed | Load_1001636 | Orange Bay - 310 | Jul 12, 2026 12:42pm | Jul 12, 2026 1:04pm | Jul 12, 2026 1:47pm | Jul 12, 2026 4:00pm | Jul 12, 2026 4:00pm | Jul 12, 2026 4:01pm | Jul 12, 2026 4:02pm | Jul 12, 2026 4:02pm |  |  | Fair | No | This call related to isolation of bank of 2-50kva
Outage | J.E.26.07.13762 | C001852772 | Shamour Haughton | St.James | Completed | Load_556983 | Bogue - 310 | Jul 12, 2026 12:40pm | Jul 12, 2026 1:26pm | Jul 12, 2026 7:35pm | Jul 12, 2026 7:35pm | Jul 12, 2026 7:51pm | Jul 12, 2026 7:51pm | Jul 12, 2026 7:53pm | Jul 12, 2026 7:53pm |  |  | Fair | No | Found 15kva fuse blown, refuse 15kva use 1,2amp fuse
Outage | J.E.26.07.13779 | C001852773 | Swon Miller | St.James | Completed | Load_249682 | Bogue - 310 | Jul 12, 2026 12:40pm | Jul 12, 2026 11:41pm | Jul 13, 2026 5:59am | Jul 13, 2026 5:59am | Jul 13, 2026 6:38am | Jul 13, 2026 6:50am | Jul 13, 2026 6:50am | Jul 13, 2026 6:50am | BrokenWire |  | Fair | No | Unable to locate customer phone calls to customer number went unanswered
Non-Outage | J.E.26.07.12563 | C001852771 | Collin Robinson | Portland | Completed | Load_265666 | Port Antonio - 310 | Jul 12, 2026 12:39pm | Jul 12, 2026 12:39pm | Jul 12, 2026 5:47pm | Jul 12, 2026 7:48pm | Jul 12, 2026 7:48pm | Jul 12, 2026 7:49pm | Jul 12, 2026 7:50pm | Jul 12, 2026 7:50pm |  |  | Fair | No | Unable to locate customer
Non-Outage | J.E.26.07.08118 | C001852767 | Collin Robinson | Portland | Completed | Load_238553 | Port Antonio - 310 | Jul 12, 2026 12:38pm | Jul 12, 2026 12:39pm | Jul 12, 2026 4:52pm | Jul 12, 2026 4:52pm | Jul 12, 2026 5:45pm | Jul 12, 2026 5:47pm | Jul 12, 2026 5:47pm | Jul 12, 2026 5:47pm |  |  | Fair | No | Premises found okMeter socket Voltage reading 117v 118v 235v
Non-Outage | J.E.26.07.08571 | C001852768 | Collin Robinson | Portland | Completed | Load_249141 | Port Antonio - 310 | Jul 12, 2026 12:38pm | Jul 12, 2026 12:39pm | Jul 12, 2026 1:19pm | Jul 12, 2026 1:19pm | Jul 12, 2026 3:03pm | Jul 12, 2026 3:09pm | Jul 12, 2026 3:09pm | Jul 12, 2026 3:09pm | LowHangingWires |  | Fair | No | Low hanging wire that customer reported does not belong jps
Non-Outage | J.E.26.07.10494 | C001852770 | Collin Robinson | Portland | Completed | Load_257634 | Port Antonio - 310 | Jul 12, 2026 12:38pm | Jul 12, 2026 12:39pm | Jul 12, 2026 3:15pm | Jul 12, 2026 3:15pm | Jul 12, 2026 4:04pm | Jul 12, 2026 4:06pm | Jul 12, 2026 4:06pm | Jul 12, 2026 4:06pm |  |  | Fair | No | Information received from customer that Issue was resolved
Outage | J.E.26.07.12870 | C001852769 | Rusean Allen | KSAS | Completed | Load_241830 | Rockfort - 210 | Jul 12, 2026 12:38pm | Jul 12, 2026 12:38pm | Jul 12, 2026 4:25pm | Jul 12, 2026 4:25pm | Jul 12, 2026 4:31pm | Jul 12, 2026 4:32pm | Jul 12, 2026 4:32pm | Jul 12, 2026 4:32pm |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.12377 | C001852766 | Barnett Brown | Manchester | Completed | Load_237860 | Spur Tree - 210 | Jul 12, 2026 12:37pm | Jul 13, 2026 7:25am | Jul 13, 2026 7:51am | Jul 13, 2026 7:55am | Jul 13, 2026 10:08am | Jul 13, 2026 10:44am | Jul 13, 2026 10:47am | Jul 13, 2026 10:47am |  |  | Fair | No | Remade service joint at secondary line, voltage 116
Outage | J.E.26.07.13687 | C001852765 | Hartley Chin | Clarendon | Completed | Load_255474 | Parnassus - 210 | Jul 12, 2026 12:34pm | Jul 12, 2026 12:36pm | Jul 12, 2026 12:50pm | Jul 12, 2026 2:29pm | Jul 12, 2026 2:29pm | Jul 12, 2026 2:30pm | Jul 12, 2026 2:31pm | Jul 12, 2026 2:31pm | Fire |  | SevereWind | No | Premisis found ok. Call related to job #13623
Non-Outage | J.E.26.07.13141 | C001852764 | Clyde Brown | null | Completed | null | null | Jul 12, 2026 12:32pm | Jul 12, 2026 3:14pm | Jul 12, 2026 3:49pm | Jul 12, 2026 3:49pm | Jul 12, 2026 3:49pm | Jul 12, 2026 3:49pm | Jul 12, 2026 3:55pm | Jul 12, 2026 3:55pm |  |  | Fair | No | Found ok ,customer said supply was restored from yesterday
Outage | J.E.26.07.13529 | C001852763 | Andrew Powell | Manchester | Completed | Load_1002348 | Spur Tree - 210 | Jul 12, 2026 12:30pm | Jul 12, 2026 12:31pm | Jul 12, 2026 12:39pm | Jul 12, 2026 12:39pm | Jul 12, 2026 12:39pm | Jul 12, 2026 12:40pm | Jul 12, 2026 12:40pm | Jul 12, 2026 12:40pm |  |  | Fair | No | Manchester called.
Outage | J.E.26.07.12168 | C001852761 | Andrew Powell | Manchester | Completed | Load_556606 | Spur Tree - 210 | Jul 12, 2026 12:26pm | Jul 12, 2026 12:27pm | Jul 12, 2026 12:49pm | Jul 12, 2026 12:49pm | Jul 12, 2026 12:49pm | Jul 12, 2026 12:49pm | Jul 12, 2026 12:50pm | Jul 12, 2026 12:50pm |  |  | Fair | No | Premises found okay customer stated that supply restored.
Outage | J.E.26.07.12366 | C001852760 | Andrew Powell | Manchester | Completed | Load_1002209 | Spur Tree - 210 | Jul 12, 2026 12:26pm | Jul 12, 2026 12:27pm | Jul 12, 2026 12:47pm | Jul 12, 2026 12:47pm | Jul 12, 2026 12:47pm | Jul 12, 2026 12:48pm | Jul 12, 2026 12:48pm | Jul 12, 2026 12:48pm |  |  | Fair | No | Premises found okay customer stated that supply restored.
Outage | J.E.26.07.13669 | C001852758 | Damion Reid | Manchester | Completed | Load_295313 | Spur Tree - 310 | Jul 12, 2026 12:22pm | Jul 12, 2026 12:24pm | Jul 12, 2026 2:21pm | Jul 12, 2026 2:21pm | Jul 12, 2026 2:36pm | Jul 12, 2026 3:25pm | Jul 12, 2026 3:27pm | Jul 12, 2026 3:27pm |  |  | Fair | No | Two blown 30amp junction fuse found line patrol nothing was found blown fuse replaced
Outage | J.E.26.07.11869 | C001852757 | Andrew Powell | Manchester | Completed | Load_246108 | Spur Tree - 210 | Jul 12, 2026 12:20pm | Jul 12, 2026 12:22pm | Jul 12, 2026 12:38pm | Jul 12, 2026 12:38pm | Jul 12, 2026 12:38pm | Jul 12, 2026 12:38pm | Jul 12, 2026 12:38pm | Jul 12, 2026 12:38pm |  |  | Fair | No | Manchester called.
Outage | J.E.26.07.12509 | C001852756 | Andrew Powell | Manchester | Completed | Load_556608 | Spur Tree - 210 | Jul 12, 2026 12:20pm | Jul 12, 2026 12:22pm | Jul 12, 2026 12:45pm | Jul 12, 2026 12:45pm | Jul 12, 2026 12:45pm | Jul 12, 2026 12:45pm | Jul 12, 2026 12:46pm | Jul 12, 2026 12:46pm |  |  | Fair | No | Premises found okay customer’s stated that supply restored .
Outage | J.E.26.07.13718 | C001852755 | Andrew Powell | Manchester | Completed | Load_292433 | Spur Tree - 210 | Jul 12, 2026 12:20pm | Jul 12, 2026 12:22pm | Jul 12, 2026 12:33pm | Jul 12, 2026 12:53pm | Jul 12, 2026 12:53pm | Jul 12, 2026 12:54pm | Jul 12, 2026 12:54pm | Jul 12, 2026 12:54pm |  |  | Fair | No | Premises not located inadequately direction contact customer by telephone unsuccessful.
Outage | J.E.26.07.13736 | C001852752 | Richman Whyte | Westmoreland | Completed | Load_292064 | Paradise - 110 | Jul 12, 2026 12:12pm | Jul 12, 2026 12:13pm | Jul 12, 2026 12:31pm | Jul 12, 2026 12:31pm | Jul 12, 2026 1:04pm | Jul 12, 2026 1:04pm | Jul 12, 2026 1:06pm | Jul 12, 2026 1:06pm |  |  | Fair | No | Restore earlier
Outage | J.E.26.07.13752 | C001852751 | Edward Royal | KSAN | Completed | Load_252722 | Washington Blvd - 710 | Jul 12, 2026 12:08pm | Jul 12, 2026 12:45pm | Jul 12, 2026 1:18pm | Jul 12, 2026 1:18pm | Jul 12, 2026 1:18pm | Jul 12, 2026 1:18pm | Jul 12, 2026 1:18pm | Jul 12, 2026 1:18pm |  |  | Fair | No | Meter not responding meter need to be check reffered to field service
Outage | J.E.26.07.13689 | C001852748 | Romaine Roberts | St.Mary | Completed | Load_250104 | Highgate -110 | Jul 12, 2026 12:00pm | Jul 12, 2026 12:01pm | Jul 12, 2026 4:58pm | Jul 12, 2026 4:58pm | Jul 12, 2026 6:23pm | Jul 12, 2026 7:14pm | Jul 12, 2026 7:23pm | Jul 12, 2026 7:23pm |  | Y | Fair | No | Bamboo Fall on secondary line and trip 25 kva transformer fuse patrol and clear line and restore supply
Outage | J.E.26.07.13656 | C001852745 | Marlon Brown | St.James | Completed | Load_292531 | Queens Drive - 710 | Jul 12, 2026 11:20am | Jul 12, 2026 11:21am | Jul 12, 2026 11:55am | Jul 12, 2026 11:55am | Jul 12, 2026 11:55am | Jul 12, 2026 11:56am | Jul 12, 2026 11:56am | Jul 12, 2026 11:56am |  |  | Fair | No | St James call
Outage | J.E.26.07.13710 | C001852746 | Shamour Haughton | St.James | Completed | Load_249876 | Bogue - 310 | Jul 12, 2026 11:20am | Jul 12, 2026 11:22am | Jul 12, 2026 11:37am | Jul 12, 2026 11:37am | Jul 12, 2026 2:37pm | Jul 12, 2026 2:46pm | Jul 12, 2026 2:48pm | Jul 12, 2026 2:48pm |  |  | Fair | No | Found 1,8amp junction fuse blown caused vehicle accident, line was cleared, refuse 8amp junction
Outage | J.E.26.07.13716 | C001852744 | Elvis Trowers | KSAN | Completed | Load_557436 | West Kings House - 310 | Jul 12, 2026 11:16am | Jul 12, 2026 11:16am | Jul 12, 2026 1:14pm | Jul 12, 2026 1:14pm | Jul 12, 2026 2:15pm | Jul 12, 2026 2:18pm | Jul 12, 2026 2:18pm | Jul 12, 2026 2:18pm |  |  | Fair | Yes | Premises checked and found ok upon arrival, customer was also spoken with however he suggested that the power supply was restored from earlier today.
Non-Outage | J.E.26.07.12798 | C001852743 | Tyrese Williams | St.Ann | Completed | Load_258093 | Roaring River - 410 | Jul 12, 2026 11:14am | Jul 12, 2026 11:15am | Jul 12, 2026 11:36am | Jul 12, 2026 12:48pm | Jul 12, 2026 1:16pm | Jul 12, 2026 1:58pm | Jul 12, 2026 1:58pm | Jul 12, 2026 1:58pm | BangingWires |  | Fair | No | Open a 25kva transformer fuse to remove secondary twisted wire that was stuck in zinc roof and wire had to splice and repair
Outage | J.E.26.07.13708 | C001852742 | Edward Royal | KSAN | Completed | Load_269393 | West Kings House - 310 | Jul 12, 2026 11:08am | Jul 12, 2026 3:42pm | Jul 12, 2026 5:15pm | Jul 12, 2026 5:15pm | Jul 12, 2026 5:39pm | Jul 12, 2026 6:19pm | Jul 12, 2026 6:19pm | Jul 12, 2026 6:19pm |  |  | Fair | No | There is no maintenance personnel at premises to assist us to do our check
Outage | J.E.26.07.13707 | C001852741 | Edward Royal | KSAS | Completed | Load_240610 | Duhaney - 310 | Jul 12, 2026 10:58am | Jul 12, 2026 11:02am | Jul 12, 2026 12:47pm | Jul 12, 2026 12:47pm | Jul 12, 2026 1:00pm | Jul 12, 2026 1:12pm | Jul 12, 2026 1:12pm | Jul 12, 2026 1:12pm |  |  | Fair | No | Customer have internal problems customer have faulty breaker advise customer to get a electrician to fix the problem voltage reading 234 116 115 v
Non-Outage | J.E.26.07.13001 | C001852740 | Edward Royal | KSAS | Completed | Load_249310 | Duhaney - 310 | Jul 12, 2026 10:57am | Jul 12, 2026 11:02am | Jul 12, 2026 12:45pm | Jul 12, 2026 12:45pm | Jul 12, 2026 12:46pm | Jul 12, 2026 12:46pm | Jul 12, 2026 12:47pm | Jul 12, 2026 12:47pm | BrokenPole |  | Fair | No | Rotten guy pole need to change referred to maintenance pole is leaning on customer wall need to be addressed urgently
Outage | J.E.26.07.13698 | C001852739 | Fitzroy Turner | KSAS | Completed | Load_261241 | Hunts Bay - 310 | Jul 12, 2026 10:56am | Jul 12, 2026 10:58am | Jul 12, 2026 12:21pm | Jul 12, 2026 12:21pm | Jul 12, 2026 12:51pm | Jul 12, 2026 12:51pm | Jul 12, 2026 12:54pm | Jul 12, 2026 12:54pm |  |  | Fair | No | Found b Off two 50 kva transformer fuse blown cause switch top blown off use one drop out switch and one 5amps fuse damaged fuse defective arrester.supply restored to areas
Non-Outage | J.E.26.07.13074 | C001852738 | Neville Spencer | Clarendon | Completed | Load_250911 | May Pen - 110 | Jul 12, 2026 10:51am | Jul 12, 2026 11:00am | Jul 12, 2026 11:04am | Jul 12, 2026 11:04am | Jul 12, 2026 11:47am | Jul 12, 2026 11:53am | Jul 12, 2026 11:53am | Jul 12, 2026 11:53am |  |  | Fair | No | Remade corrded netural joint at pothead on 3 , wire service used 1, 2/6; sleeves voltage reading 114 117 232. supply restored.
Outage | J.E.26.07.13666 | C001852737 | Richard Nicholas | St.Catherine | Completed | Load_238392 | New Michelton - 410 | Jul 12, 2026 10:50am | Jul 12, 2026 10:52am | Jul 12, 2026 2:40pm | Jul 12, 2026 2:40pm | Jul 12, 2026 3:24pm | Jul 12, 2026 3:44pm | Jul 12, 2026 3:44pm | Jul 12, 2026 3:44pm |  |  | Fair | No | Area found ok
Outage | J.E.26.07.12932 | C001852731 | Edward Royal | KSAS | Completed | Load_239353 | Hunts Bay - 810 | Jul 12, 2026 10:47am | Jul 12, 2026 10:48am | Jul 12, 2026 12:05pm | Jul 12, 2026 12:05pm | Jul 12, 2026 12:16pm | Jul 12, 2026 12:45pm | Jul 12, 2026 12:45pm | Jul 12, 2026 12:45pm |  |  | Fair | No | Remake primary jumper using 2 single bolt clamp
Outage | J.E.26.07.13690 | C001852730 | Edward Royal | KSAS | Completed | Load_290800 | Hunts Bay - 810 | Jul 12, 2026 10:46am | Jul 12, 2026 10:48am | Jul 12, 2026 12:45pm | Jul 12, 2026 12:45pm | Jul 12, 2026 12:45pm | Jul 12, 2026 12:45pm | Jul 12, 2026 12:45pm | Jul 12, 2026 12:45pm |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.07.13688 | C001852729 | Hartley Chin | Clarendon | Completed | Load_267175 | Parnassus - 210 | Jul 12, 2026 10:39am | Jul 12, 2026 10:41am | Jul 12, 2026 12:22pm | Jul 12, 2026 2:27pm | Jul 12, 2026 2:27pm | Jul 12, 2026 2:27pm | Jul 12, 2026 2:29pm | Jul 12, 2026 2:29pm |  |  | SevereWind | No | Premisis found ok. Call related to job #13623
Outage | J.E.26.07.13662 | C001852728 | Donald Cunningham | St.Catherine | Completed | Load_240043 | Tredegar - 210 | Jul 12, 2026 10:31am | Jul 12, 2026 10:40am | Jul 12, 2026 1:10pm | Jul 12, 2026 1:10pm | Jul 12, 2026 2:18pm | Jul 12, 2026 2:20pm | Jul 12, 2026 2:37pm | Jul 12, 2026 2:37pm | Fire |  | Fair | No | Burnt off phase by pole by pole one clamp use voltage readings 119/2/240
Outage | J.E.26.07.13665 | C001852727 | Raymond Lewis | St.Ann | Completed | Load_257310 | Ocho Rios - 310 | Jul 12, 2026 10:22am | Jul 12, 2026 10:31am | Jul 12, 2026 11:14am | Jul 12, 2026 11:14am | Jul 12, 2026 1:18pm | Jul 12, 2026 1:41pm | Jul 12, 2026 1:42pm | Jul 12, 2026 1:42pm |  |  | Fair | No | Remade joint at pothead 2 wire service voltages 120 customer have internal fault
Outage | J.E.26.07.13657 | C001852726 | Christopher Edwards | KSAN | Completed | Load_244288 | Constant Spring - 410 | Jul 12, 2026 10:12am | Jul 12, 2026 10:14am | Jul 12, 2026 1:08pm | Jul 12, 2026 1:09pm | Jul 12, 2026 1:36pm | Jul 12, 2026 2:01pm | Jul 12, 2026 2:03pm | Jul 12, 2026 2:03pm |  |  | Fair | No | Refuse blown 25 kva transformer fuseUsing (1) 3 amps
Non-Outage | J.E.26.07.12399 | C001852725 | Stephen Taylor | null | Completed | null | null | Jul 12, 2026 9:55am | Jul 12, 2026 10:07am | Jul 12, 2026 11:28am | Jul 12, 2026 11:28am | Jul 12, 2026 11:28am | Jul 12, 2026 11:29am | Jul 12, 2026 11:29am | Jul 12, 2026 11:29am |  |  | Fair | No | Call to customer and customer said power is back now
Non-Outage | J.E.26.07.13057 | C001852724 | Stephen Taylor | null | Completed | null | null | Jul 12, 2026 9:55am | Jul 12, 2026 10:07am | Jul 12, 2026 11:25am | Jul 12, 2026 11:25am | Jul 12, 2026 11:26am | Jul 12, 2026 11:26am | Jul 12, 2026 11:27am | Jul 12, 2026 11:27am |  |  | Fair | No | Check with customer and customer said power is back from yesterday
Outage | J.E.26.07.12541 | C001852723 | Stephen Taylor | KSAS | Completed | Load_264625 | Good Year - 210 | Jul 12, 2026 9:55am | Jul 12, 2026 10:07am | Jul 13, 2026 12:04pm | Jul 13, 2026 12:04pm | Jul 13, 2026 12:04pm | Jul 13, 2026 12:04pm | Jul 13, 2026 12:04pm | Jul 13, 2026 12:04pm |  |  | Fair | No | Premise found ok
Outage | J.E.26.07.13260 | C001852722 | Stephen Taylor | St.Thomas | Completed | Load_258338 | Good Year - 210 | Jul 12, 2026 9:55am | Jul 12, 2026 10:07am | Jul 13, 2026 12:44pm | Jul 13, 2026 12:44pm | Jul 13, 2026 12:44pm | Jul 13, 2026 12:44pm | Jul 13, 2026 12:46pm | Jul 13, 2026 12:46pm |  |  | Fair | No | Clean up single phase use 3 clamps 111,112,224 customer is now okay
Outage | J.E.26.07.11232 | C001852721 | Tyrese Williams | St.Ann | Completed | Load_244028 | Roaring River - 410 | Jul 12, 2026 9:54am | Jul 12, 2026 9:59am | Jul 12, 2026 10:11am | Jul 12, 2026 12:39pm | Jul 12, 2026 12:39pm | Jul 12, 2026 12:40pm | Jul 12, 2026 12:41pm | Jul 12, 2026 12:41pm |  |  | Fair | No | Premises found ok voltage check 120/120/240/205
Outage | J.E.26.07.13632 | C001852720 | Romaine Roberts | St.Mary | Completed | Load_247804 | Blackstonedge - 110 | Jul 12, 2026 9:45am | Jul 12, 2026 12:03pm | Jul 12, 2026 4:11pm | Jul 12, 2026 4:11pm | Jul 12, 2026 4:11pm | Jul 12, 2026 4:12pm | Jul 12, 2026 4:13pm | Jul 12, 2026 4:13pm |  |  | Fair | Yes | Found defective 25 kva transformer after test carry maintenance work needed. No pole number
Non-Outage | J.E.26.07.13646 | C001852719 | Marlon Brown | null | Completed | null | null | Jul 12, 2026 9:44am | Jul 12, 2026 10:24am | Jul 12, 2026 10:58am | Jul 12, 2026 10:58am | Jul 12, 2026 11:33am | Jul 12, 2026 11:55am | Jul 12, 2026 11:55am | Jul 12, 2026 11:55am |  |  | Fair | No | Clear vegetation from transformer pole Replaced 10amps fuse @ 100kva transformer Voltage found at meter 235/235/0=235/235/406vVoltage leaving at meter 236/238/239=407/411/412v
Outage | J.E.26.07.12776 | C001852718 | Wan Carlos Scarlett | KSAS | Completed | Load_250337 | Duhaney - 210 | Jul 12, 2026 9:17am | Jul 12, 2026 9:18am | Jul 12, 2026 12:10pm | Jul 12, 2026 1:43pm | Jul 12, 2026 2:08pm | Jul 12, 2026 3:05pm | Jul 12, 2026 3:05pm | Jul 12, 2026 3:05pm |  |  | Fair | No | Customer confirm that power supply has has been restored
Outage | J.E.26.07.13618 | C001852717 | Richard Nicholas | St.Catherine | Completed | Load_261450 | New Michelton - 210 | Jul 12, 2026 9:17am | Jul 12, 2026 9:18am | Jul 12, 2026 1:31pm | Jul 12, 2026 1:31pm | Jul 12, 2026 1:42pm | Jul 12, 2026 1:42pm | Jul 12, 2026 1:42pm | Jul 12, 2026 1:42pm |  |  | Fair | No | Area found ok
Outage | J.E.26.07.13623 | C001852716 | Hartley Chin | Clarendon | Completed | Load_249758 | Parnassus - 210 | Jul 12, 2026 9:17am | Jul 12, 2026 9:18am | Jul 12, 2026 12:22pm | Jul 12, 2026 12:22pm | Jul 12, 2026 1:29pm | Jul 12, 2026 2:25pm | Jul 12, 2026 2:26pm | Jul 12, 2026 2:26pm | Fire |  | SevereWind | No | Found blown 20 amp junction fuse @ pole # 055817 line patrolled and found blown 3 amp fuse on 25 KVA transformer @ pole # 0113147 line patrolled and okay ..junction refused.. then refused transformer..
Outage | J.E.26.07.13112 | C001852713 | Romaine Roberts | St.Mary | Completed | Load_241528 | Highgate -110 | Jul 12, 2026 8:59am | Jul 12, 2026 9:00am | Jul 12, 2026 7:24pm | Jul 12, 2026 7:24pm | Jul 12, 2026 9:31pm | Jul 12, 2026 9:41pm | Jul 12, 2026 9:41pm | Jul 12, 2026 9:41pm | BrokenWire | Y | Fair | No | Junction fuse found blown patrol line found bamboo on line,clear bamboo from line and replace 10 amp no pole number power restore
Outage | J.E.26.07.13577 | C001852711 | Romaine Roberts | St.Mary | Completed | Load_248573 | Blackstonedge - 110 | Jul 12, 2026 8:59am | Jul 12, 2026 9:00am | Jul 12, 2026 3:01pm | Jul 12, 2026 3:01pm | Jul 12, 2026 4:07pm | Jul 12, 2026 4:10pm | Jul 12, 2026 4:11pm | Jul 12, 2026 4:11pm |  |  | Fair | No | Found defective 25 kva transformer after test carry maintenance work needed. No pole number
Outage | J.E.26.07.10414 | C001852709 | Romaine Roberts | St.Mary | Completed | Load_261325 | Blackstonedge - 110 | Jul 12, 2026 8:58am | Jul 12, 2026 1:09pm | Jul 12, 2026 1:50pm | Jul 12, 2026 1:51pm | Jul 12, 2026 2:56pm | Jul 12, 2026 3:01pm | Jul 12, 2026 3:01pm | Jul 12, 2026 3:01pm | BangingWires | Y | Fair | No | Open and close 25 kva transformer to clear out one span of secondary conductor bushing carry out power restore w
Outage | J.E.26.07.11538 | C001852707 | Fitzroy Turner | KSAS | Completed | Load_237939 | Hunts Bay - 310 | Jul 12, 2026 8:58am | Jul 12, 2026 12:15pm | Jul 12, 2026 12:54pm | Jul 12, 2026 12:54pm | Jul 12, 2026 12:54pm | Jul 12, 2026 12:55pm | Jul 12, 2026 12:55pm | Jul 12, 2026 12:55pm |  |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.07.11815 | C001852708 | Fitzroy Turner | KSAS | Completed | Load_247391 | Rockfort - 410 | Jul 12, 2026 8:58am | Jul 12, 2026 9:02am | Jul 12, 2026 1:06pm | Jul 12, 2026 1:06pm | Jul 12, 2026 1:36pm | Jul 12, 2026 2:03pm | Jul 12, 2026 2:04pm | Jul 12, 2026 2:04pm | BrokenWire |  | Fair | No | Found two wires service corroded at pole use one clamp to carry out repair supply restored to customer
Outage | J.E.26.07.13069 | C001852710 | Romaine Roberts | St.Mary | Completed | Load_259870 | Blackstonedge - 110 | Jul 12, 2026 8:58am | Jul 12, 2026 9:00am | Jul 12, 2026 1:14pm | Jul 12, 2026 1:29pm | Jul 12, 2026 1:29pm | Jul 12, 2026 1:30pm | Jul 12, 2026 1:31pm | Jul 12, 2026 1:31pm | BrokenWire |  | Fair | No | High wind bang and burst down 2 span of secondary neutral open and close 25 kva transformer to splice and retention conductor
Non-Outage | J.E.26.07.12855 | C001852706 | Rusean Allen | null | Completed | null | null | Jul 12, 2026 8:57am | Jul 12, 2026 12:17pm | Jul 12, 2026 12:44pm | Jul 12, 2026 12:44pm | Jul 12, 2026 2:13pm | Jul 12, 2026 2:14pm | Jul 12, 2026 2:14pm | Jul 12, 2026 2:14pm | LowHangingWires |  | Fair | No | Not Found
Non-Outage | J.E.26.07.13021 | C001852705 | Fitzroy Turner | null | Completed | null | null | Jul 12, 2026 8:56am | Jul 12, 2026 9:02am | Jul 12, 2026 9:23am | Jul 12, 2026 9:23am | Jul 12, 2026 11:03am | Jul 12, 2026 12:05pm | Jul 12, 2026 12:12pm | Jul 12, 2026 12:12pm |  |  | EarthMovement | No | Found three phases primary switches to top burnt off and up park camp compound cause by heavy win.remove hot line clamps at the intersection of camp road and camp gate to carry out repair.use 3one bolt clamp to repair switches to and 3ft of #4 copper and 3 25 amps fuse at the junction and one 15 amp at the bank of three 167 transformer supply restored to customer .
Outage | J.E.26.07.13602 | C001852704 | Donald Cunningham | St.Catherine | Completed | Load_252934 | Rhodens Pen - 210 | Jul 12, 2026 8:41am | Jul 12, 2026 8:42am | Jul 12, 2026 2:37pm | Jul 12, 2026 2:37pm | Jul 12, 2026 2:37pm | Jul 12, 2026 3:47pm | Jul 12, 2026 3:53pm | Jul 12, 2026 3:53pm |  |  | Fair | No | Blown junction fuse by entrance to sharper lane replace 25 amp fuse
Outage | J.E.26.07.13611 | C001852703 | Donald Cunningham | St.Catherine | Completed | Load_1001569 | Tredegar - 510 | Jul 12, 2026 8:41am | Jul 12, 2026 8:41am | Jul 12, 2026 12:08pm | Jul 12, 2026 12:08pm | Jul 12, 2026 1:05pm | Jul 12, 2026 1:07pm | Jul 12, 2026 1:08pm | Jul 12, 2026 1:08pm | BrokenWire |  | Fair | No | Premises closed
Outage | J.E.26.07.13615 | C001852702 | Marlon Brown | Trelawny | Completed | Load_302540 | Martha Brae - 210 | Jul 12, 2026 8:41am | Jul 12, 2026 8:41am | Jul 12, 2026 11:56am | Jul 12, 2026 11:56am | Jul 12, 2026 12:35pm | Jul 12, 2026 12:36pm | Jul 12, 2026 12:36pm | Jul 12, 2026 12:36pm |  |  | Fair | No | Refer to Field Service Department as premises was destroyed by fire, hence no electricity there.
Outage | J.E.26.07.12982 | C001852701 | Nickolas Rodriques | Portmore | Completed | Load_243381 | Naggo Head - 610 | Jul 12, 2026 8:40am | Jul 12, 2026 8:41am | Jul 12, 2026 12:07pm | Jul 12, 2026 12:12pm | Jul 12, 2026 12:48pm | Jul 12, 2026 2:02pm | Jul 12, 2026 2:12pm | Jul 12, 2026 2:12pm |  |  | Fair | No | Checked and found customer single phasing (114) caused by broken service wire at pothead. Repaired by connecting wire using one service sleeve, current reading (114-115-239).
Outage | J.E.26.07.13607 | C001852700 | Shamour Haughton | St.James | Completed | Load_261335 | Bogue - 610 | Jul 12, 2026 8:39am | Jul 12, 2026 8:40am | Jul 12, 2026 9:10am | Jul 12, 2026 9:10am | Jul 12, 2026 10:46am | Jul 12, 2026 10:56am | Jul 12, 2026 10:59am | Jul 12, 2026 10:59am |  |  | Fair | No | Found 25kva transformer tripped, reset 25kva
Non-Outage | J.E.26.07.13537 | C001852699 | Roxroy Needham | null | Completed | null | null | Jul 12, 2026 8:37am | Jul 12, 2026 8:40am | Jul 12, 2026 9:52am | Jul 12, 2026 9:55am | Jul 12, 2026 10:52am | Jul 12, 2026 12:19pm | Jul 12, 2026 12:21pm | Jul 12, 2026 12:21pm |  |  | Fair | No | Remove illegal and retention 2 span of secondary phase voltage readings left 111,114,225
Outage | J.E.26.07.13597 | C001852698 | Nickolas Rodriques | Portmore | Completed | Load_255528 | Naggo Head - 510 | Jul 12, 2026 8:36am | Jul 12, 2026 8:37am | Jul 12, 2026 8:48am | Jul 12, 2026 9:00am | Jul 12, 2026 9:50am | Jul 12, 2026 10:25am | Jul 12, 2026 10:27am | Jul 12, 2026 10:27am |  |  | Fair | No | Customer is reporting a defective streetlight. Refer to streetlight department.
Outage | J.E.26.07.12347 | C001852696 | Tyrese Williams | St.Ann | Completed | Load_266688 | Roaring River - 210 | Jul 12, 2026 8:35am | Jul 12, 2026 8:35am | Jul 12, 2026 8:48am | Jul 12, 2026 12:47pm | Jul 12, 2026 12:47pm | Jul 12, 2026 12:47pm | Jul 12, 2026 12:48pm | Jul 12, 2026 12:48pm |  |  | Fair | No | Premises found ok customer said it was a internal problem
Outage | J.E.26.07.13333 | C001852697 | Tyrese Williams | null | Completed | Load_268042 | Ocho Rios - 310 | Jul 12, 2026 8:35am | Jul 12, 2026 8:35am | Jul 12, 2026 8:47am | Jul 12, 2026 8:50am | Jul 12, 2026 9:43am | Jul 12, 2026 10:37am | Jul 12, 2026 10:51am | Jul 12, 2026 10:51am |  |  | Fair | No | Splice and repair service wire use 4ft of #6 service wire
Outage | J.E.26.07.13547 | C001852695 | Tyrese Williams | St.Ann | Completed | Load_239479 | Ocho Rios - 310 | Jul 12, 2026 8:34am | Jul 12, 2026 8:35am | Jul 12, 2026 8:51am | Jul 12, 2026 10:52am | Jul 12, 2026 12:20pm | Jul 12, 2026 12:38pm | Jul 12, 2026 12:39pm | Jul 12, 2026 12:39pm |  |  | Fair | No | Remade service wire joint at pothead 110 connection
Outage | J.E.26.07.13593 | C001852694 | Shamour Haughton | St.James | Completed | Load_257440 | Bogue - 510 | Jul 12, 2026 8:25am | Jul 12, 2026 9:17am | Jul 12, 2026 11:01am | Jul 12, 2026 11:01am | Jul 12, 2026 11:01am | Jul 12, 2026 11:01am | Jul 12, 2026 11:02am | Jul 12, 2026 11:02am |  |  | Fair | No | Hanover call
Outage | J.E.26.07.12984 | C001852693 | Donald Cunningham | St.Catherine | Completed | Load_259897 | Rhodens Pen - 210 | Jul 12, 2026 8:24am | Jul 12, 2026 8:24am | Jul 12, 2026 3:55pm | Jul 12, 2026 3:55pm | Jul 12, 2026 4:46pm | Jul 12, 2026 4:54pm | Jul 12, 2026 4:54pm | Jul 12, 2026 4:54pm |  |  | Fair | No | Supply in area customer premises closed
Outage | J.E.26.07.06919 | C001852692 | Neville Spencer | St.Ann | Completed | Load_248136 | Cardiff Hall - 310 | Jul 12, 2026 8:23am | Jul 12, 2026 8:24am | Jul 12, 2026 11:53am | Jul 12, 2026 11:53am | Jul 12, 2026 12:22pm | Jul 12, 2026 12:22pm | Jul 12, 2026 12:24pm | Jul 12, 2026 12:24pm | BrokenWire |  | Fair | No | Unable to locate customer.
Outage | J.E.26.07.11982 | C001852691 | Elvis Trowers | KSAN | Completed | Load_244190 | Hope - 510 | Jul 12, 2026 8:22am | Jul 12, 2026 9:02am | Jul 12, 2026 10:47am | Jul 12, 2026 10:47am | Jul 12, 2026 12:12pm | Jul 12, 2026 1:10pm | Jul 12, 2026 1:10pm | Jul 12, 2026 1:10pm | LeaningPole |  | Fair | Yes | Customer was found without electricity supply when checked, and broken twisted wire was found where about 30’ feet was used for splicing and reconnect, voltage when checked was left at 112+113=225 volts.
Outage | J.E.26.07.13087 | C001852690 | Raymond Lewis | Clarendon | Completed | Load_568418 | May Pen - 110 | Jul 12, 2026 8:22am | Jul 12, 2026 8:22am | Jul 12, 2026 10:59am | Jul 12, 2026 10:59am | Jul 12, 2026 10:59am | Jul 12, 2026 11:00am | Jul 12, 2026 11:01am | Jul 12, 2026 11:01am |  |  | Fair | No | Supply restored
Outage | J.E.26.07.13121 | C001852689 | Raymond Lewis | Clarendon | Completed | Load_568412 | May Pen - 110 | Jul 12, 2026 8:22am | Jul 12, 2026 8:22am | Jul 12, 2026 11:01am | Jul 12, 2026 11:01am | Jul 12, 2026 11:02am | Jul 12, 2026 11:03am | Jul 12, 2026 11:05am | Jul 12, 2026 11:05am |  |  | Fair | No | Supply restored
Outage | J.E.26.07.13226 | C001852688 | Raymond Lewis | Clarendon | Completed | Load_241634 | May Pen - 110 | Jul 12, 2026 8:22am | Jul 12, 2026 8:22am | Jul 12, 2026 11:08am | Jul 12, 2026 11:08am | Jul 12, 2026 11:12am | Jul 12, 2026 11:13am | Jul 12, 2026 11:14am | Jul 12, 2026 11:14am |  |  | Fair | No | Supply restored
Outage | J.E.26.07.13314 | C001852686 | Richman Whyte | Westmoreland | Completed | Load_292064 | Paradise - 110 | Jul 12, 2026 8:20am | Jul 12, 2026 8:23am | Jul 12, 2026 8:32am | Jul 12, 2026 8:32am | Jul 12, 2026 10:50am | Jul 12, 2026 11:47am | Jul 12, 2026 11:48am | Jul 12, 2026 11:48am |  |  | Fair | No | Repair burnt off secondary jumper use three one bolt clamps voltage 115 115 230
Outage | J.E.26.07.13516 | C001852687 | Richman Whyte | Hanover | Completed | Load_244663 | Orange Bay - 310 | Jul 12, 2026 8:20am | Jul 12, 2026 8:23am | Jul 12, 2026 11:48am | Jul 12, 2026 11:48am | Jul 12, 2026 12:14pm | Jul 12, 2026 12:30pm | Jul 12, 2026 12:30pm | Jul 12, 2026 12:30pm |  |  | Fair | No | Replace two 8 amp junction fuse
Outage | J.E.26.07.12931 | C001852684 | Damion Reid | Manchester | Completed | Load_267101 | Spur Tree - 310 | Jul 12, 2026 8:19am | Jul 12, 2026 8:19am | Jul 12, 2026 8:41am | Jul 12, 2026 8:41am | Jul 12, 2026 10:07am | Jul 12, 2026 2:12pm | Jul 12, 2026 2:16pm | Jul 12, 2026 2:16pm | BrokenWire |  | Fair | No | Two span of broken secondary phase an neutral conductor found cause by tree limb open 25kva transformer fuse link cut tree limb from secondary line splice an retention conductor using 30ft of #2 aluminum conductor 3 one bolt clamp and restore power
Outage | J.E.26.07.13548 | C001852685 | Damion Reid | Manchester | Completed | Load_295272 | Spur Tree - 310 | Jul 12, 2026 8:19am | Jul 12, 2026 8:19am | Jul 12, 2026 3:28pm | Jul 12, 2026 3:28pm | Jul 12, 2026 4:07pm | Jul 12, 2026 4:08pm | Jul 12, 2026 4:12pm | Jul 12, 2026 4:12pm |  |  | Fair | No | Call related to one done at moorlands earlier ref
Outage | J.E.26.07.12850 | C001852683 | Rusean Allen | KSAS | Completed | Load_245879 | Rockfort - 210 | Jul 12, 2026 8:15am | Jul 12, 2026 12:42pm | Jul 12, 2026 3:45pm | Jul 12, 2026 3:45pm | Jul 12, 2026 4:21pm | Jul 12, 2026 4:24pm | Jul 12, 2026 4:25pm | Jul 12, 2026 4:25pm |  |  | Fair | No | Premises found okay, customer reset breaker.
Outage | J.E.26.07.13262 | C001852681 | Wayne Dillion | St.Elizabeth | Completed | Load_263142 | Maggotty - 110 | Jul 12, 2026 8:11am | Jul 12, 2026 8:12am | Jul 12, 2026 11:19am | Jul 12, 2026 11:19am | Jul 12, 2026 11:19am | Jul 12, 2026 11:19am | Jul 12, 2026 11:20am | Jul 12, 2026 11:20am |  |  | Fair | No | Customer said supply was restored.
Outage | J.E.26.07.13366 | C001852682 | Wayne Dillion | St.Elizabeth | Completed | Load_266366 | Maggotty - 110 | Jul 12, 2026 8:11am | Jul 12, 2026 8:12am | Jul 12, 2026 1:32pm | Jul 12, 2026 1:32pm | Jul 12, 2026 1:32pm | Jul 12, 2026 1:33pm | Jul 12, 2026 1:34pm | Jul 12, 2026 1:34pm |  |  | Fair | No | Please refer this call to the Westmoreland team.
Non-Outage | J.E.26.07.13240 | C001852680 | Edward Royal | null | Completed | null | null | Jul 12, 2026 8:05am | Jul 12, 2026 8:06am | Jul 12, 2026 10:20am | Jul 12, 2026 10:20am | Jul 12, 2026 10:20am | Jul 12, 2026 10:21am | Jul 12, 2026 10:21am | Jul 12, 2026 10:21am | Fire |  | Fair | No | Premises found ok related to outage
Non-Outage | J.E.26.07.12952 | C001852677 | Fitzroy Turner | null | Completed | null | null | Jul 12, 2026 8:03am | Jul 12, 2026 8:56am | Jul 12, 2026 2:04pm | Jul 12, 2026 2:04pm | Jul 12, 2026 2:04pm | Jul 12, 2026 2:11pm | Jul 12, 2026 2:15pm | Jul 12, 2026 2:15pm |  |  | Fair | No | Found two wires service corroded at pothead use one clamp to carry out repair supply restored to stoplights
Non-Outage | J.E.26.07.13164 | C001852678 | Edward Royal | null | Completed | null | null | Jul 12, 2026 8:03am | Jul 12, 2026 8:05am | Jul 12, 2026 10:24am | Jul 12, 2026 10:24am | Jul 12, 2026 10:24am | Jul 12, 2026 10:26am | Jul 12, 2026 10:26am | Jul 12, 2026 10:26am | BrokenWire |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.07.13166 | C001852679 | Edward Royal | null | Completed | null | null | Jul 12, 2026 8:03am | Jul 12, 2026 8:05am | Jul 12, 2026 10:24am | Jul 12, 2026 10:24am | Jul 12, 2026 10:24am | Jul 12, 2026 10:24am | Jul 12, 2026 10:24am | Jul 12, 2026 10:24am | BrokenWire |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.07.13157 | C001852673 | Wayne Dillion | St.Elizabeth | Completed | Load_292313 | Maggotty - 110 | Jul 12, 2026 8:03am | Jul 12, 2026 8:07am | Jul 12, 2026 11:17am | Jul 12, 2026 11:17am | Jul 12, 2026 11:17am | Jul 12, 2026 11:17am | Jul 12, 2026 11:18am | Jul 12, 2026 11:18am |  |  | Fair | No | Customer said supply was restored.
Outage | J.E.26.07.13171 | C001852671 | Wayne Dillion | St.Elizabeth | Completed | Load_263142 | Maggotty - 110 | Jul 12, 2026 8:03am | Jul 12, 2026 8:07am | Jul 12, 2026 11:14am | Jul 12, 2026 11:14am | Jul 12, 2026 11:14am | Jul 12, 2026 11:15am | Jul 12, 2026 11:15am | Jul 12, 2026 11:15am |  |  | Fair | No | Customer said supply was restored.
Outage | J.E.26.07.13185 | C001852676 | Edward Royal | KSAN | Completed | Load_244392 | Washington Blvd - 710 | Jul 12, 2026 8:03am | Jul 12, 2026 8:04am | Jul 12, 2026 10:39am | Jul 12, 2026 10:39am | Jul 12, 2026 11:02am | Jul 12, 2026 11:03am | Jul 12, 2026 11:03am | Jul 12, 2026 11:03am |  |  | Fair | No | Meter not responding meter need to check reffered to field service
Outage | J.E.26.07.13188 | C001852672 | Wayne Dillion | St.Elizabeth | Completed | Load_257518 | Maggotty - 110 | Jul 12, 2026 8:03am | Jul 12, 2026 8:07am | Jul 12, 2026 11:16am | Jul 12, 2026 11:16am | Jul 12, 2026 11:16am | Jul 12, 2026 11:16am | Jul 12, 2026 11:16am | Jul 12, 2026 11:16am |  |  | Fair | No | Customer said supply was restored.
Outage | J.E.26.07.13584 | C001852674 | Wayne Dillion | St.Elizabeth | Completed | Load_263142 | Maggotty - 110 | Jul 12, 2026 8:03am | Jul 12, 2026 8:07am | Jul 12, 2026 11:18am | Jul 12, 2026 11:18am | Jul 12, 2026 11:18am | Jul 12, 2026 11:18am | Jul 12, 2026 11:19am | Jul 12, 2026 11:19am |  |  | Fair | No | Customer said supply was restored.
Outage | J.E.26.07.13586 | C001852675 | Edward Royal | KSAN | Completed | Load_238567 | Washington Blvd - 310 | Jul 12, 2026 8:03am | Jul 12, 2026 8:04am | Jul 12, 2026 10:29am | Jul 12, 2026 10:29am | Jul 12, 2026 10:35am | Jul 12, 2026 10:38am | Jul 12, 2026 10:38am | Jul 12, 2026 10:38am |  |  | Fair | No | Meter not responding meter need to be check reffered to field service no box number no pole number it a EN box
Outage | J.E.26.07.12681 | C001852667 | Wayne Dillion | St.Elizabeth | Completed | Load_292191 | Maggotty - 110 | Jul 12, 2026 8:02am | Jul 13, 2026 7:41am | Jul 13, 2026 2:43pm | Jul 13, 2026 2:43pm | Jul 13, 2026 2:43pm | Jul 13, 2026 2:46pm | Jul 13, 2026 2:46pm | Jul 13, 2026 2:46pm |  |  | Rains | No | Unable to locate and customer not answering the phone.
Outage | J.E.26.07.12853 | C001852668 | Wayne Dillion | St.Elizabeth | Completed | Load_263142 | Maggotty - 110 | Jul 12, 2026 8:02am | Jul 12, 2026 8:07am | Jul 12, 2026 11:11am | Jul 12, 2026 11:11am | Jul 12, 2026 11:11am | Jul 12, 2026 11:12am | Jul 12, 2026 11:13am | Jul 12, 2026 11:13am |  |  | Fair | No | Customer said supply was restored.
Outage | J.E.26.07.12888 | C001852670 | Wayne Dillion | St.Elizabeth | Completed | Load_292313 | Maggotty - 110 | Jul 12, 2026 8:02am | Jul 12, 2026 8:07am | Jul 12, 2026 9:12am | Jul 12, 2026 9:12am | Jul 12, 2026 10:37am | Jul 12, 2026 10:55am | Jul 12, 2026 11:06am | Jul 12, 2026 11:06am |  |  | Fair | No | Patrol and found one blown 20amp junction fuse no pole #. Replace same and restored supply okay.
Outage | J.E.26.07.13024 | C001852669 | Wayne Dillion | St.Elizabeth | Completed | Load_265377 | Maggotty - 110 | Jul 12, 2026 8:02am | Jul 12, 2026 8:07am | Jul 12, 2026 11:13am | Jul 12, 2026 11:13am | Jul 12, 2026 11:13am | Jul 12, 2026 11:14am | Jul 12, 2026 11:14am | Jul 12, 2026 11:14am |  |  | Fair | No | Customer said supply was restored.
Outage | J.E.26.07.13588 | C001852665 | Lancelot Brown | Hanover | Completed | Load_265958 | Orange Bay - 310 | Jul 12, 2026 8:01am | Jul 12, 2026 8:01am | Jul 12, 2026 8:28am | Jul 12, 2026 10:08am | Jul 12, 2026 10:08am | Jul 12, 2026 10:10am | Jul 12, 2026 10:10am | Jul 12, 2026 10:10am |  |  | SevereWind | No | This call related to 2amps fuse at 25kva supply restore
Outage | J.E.26.07.12779 | C001852664 | Rusean Allen | KSAS | Completed | Load_252659 | Rockfort - 410 | Jul 12, 2026 8:00am | Jul 12, 2026 8:03am | Jul 12, 2026 11:14am | Jul 12, 2026 3:32pm | Jul 12, 2026 3:32pm | Jul 12, 2026 3:32pm | Jul 12, 2026 3:33pm | Jul 12, 2026 3:33pm |  |  | Fair | No | No access to premises
Outage | J.E.26.07.13179 | C001852663 | Rusean Allen | KSAS | Completed | Load_259327 | Rockfort - 410 | Jul 12, 2026 8:00am | Jul 12, 2026 8:03am | Jul 12, 2026 3:35pm | Jul 13, 2026 12:27pm | Jul 13, 2026 12:27pm | Jul 13, 2026 12:28pm | Jul 13, 2026 12:28pm | Jul 13, 2026 12:28pm |  |  | Fair | No | St Mary
Outage | J.E.26.07.13236 | C001852662 | Edward Royal | KSAN | Completed | Load_244711 | Washington Blvd - 710 | Jul 12, 2026 7:58am | Jul 12, 2026 8:03am | Jul 12, 2026 8:33am | Jul 12, 2026 8:33am | Jul 12, 2026 9:17am | Jul 12, 2026 10:19am | Jul 12, 2026 10:19am | Jul 12, 2026 10:19am | Fire |  | Fair | No | Spliced and reconnected drop lead to secondary phase using 20 ft 2 north cable 4 single bolt clamp
Outage | J.E.26.07.13294 | C001852660 | Rusean Allen | KSAS | Completed | Load_254610 | Cane River - 610 | Jul 12, 2026 7:58am | Jul 12, 2026 8:03am | Jul 12, 2026 12:21pm | Jul 12, 2026 12:21pm | Jul 12, 2026 12:21pm | Jul 12, 2026 12:22pm | Jul 12, 2026 12:22pm | Jul 12, 2026 12:22pm |  |  | Fair | No | Related to Henry Morgan blvd
Outage | J.E.26.07.13298 | C001852661 | Rusean Allen | KSAS | Completed | Load_253227 | Cane River - 610 | Jul 12, 2026 7:58am | Jul 12, 2026 8:03am | Jul 12, 2026 8:49am | Jul 12, 2026 8:49am | Jul 12, 2026 10:21am | Jul 12, 2026 12:20pm | Jul 12, 2026 12:20pm | Jul 12, 2026 12:20pm |  |  | Fair | No | 2x 65amp fuse found 2x 65amp fuse replaced
Outage | J.E.26.07.13135 | C001852655 | Donald Cunningham | St.Catherine | Completed | Load_1001612 | Tredegar - 310 | Jul 12, 2026 7:55am | Jul 12, 2026 7:57am | Jul 12, 2026 10:14am | Jul 12, 2026 10:14am | Jul 12, 2026 11:47am | Jul 12, 2026 12:05pm | Jul 12, 2026 12:06pm | Jul 12, 2026 12:06pm |  |  | Fair | No | 25 kva transformer found trip same reset illegal connection
Outage | J.E.26.07.13221 | C001852657 | Donald Cunningham | St.Catherine | Completed | Load_244050 | Tredegar - 410 | Jul 12, 2026 7:55am | Jul 12, 2026 7:57am | Jul 12, 2026 8:34am | Jul 12, 2026 8:34am | Jul 12, 2026 9:56am | Jul 12, 2026 10:12am | Jul 12, 2026 10:13am | Jul 12, 2026 10:13am |  |  | Fair | No | 25 kva transformer found trip same reset cause by illegal connection
Outage | J.E.26.07.13542 | C001852656 | Richard Nicholas | St.Catherine | Completed | Load_257347 | New Michelton - 210 | Jul 12, 2026 7:55am | Jul 12, 2026 7:57am | Jul 12, 2026 8:05am | Jul 12, 2026 8:05am | Jul 12, 2026 12:26pm | Jul 12, 2026 1:29pm | Jul 12, 2026 1:31pm | Jul 12, 2026 1:31pm | BrokenWire |  | Fair | No | Cut and splice damaged #6 triplex 3w service wire.replaced blown 15amp junctions fuse on pole #0180242.
Outage | J.E.26.07.13556 | C001852659 | Richard Nicholas | St.Catherine | Completed | Load_250336 | New Michelton - 210 | Jul 12, 2026 7:55am | Jul 12, 2026 7:57am | Jul 12, 2026 1:42pm | Jul 12, 2026 1:42pm | Jul 12, 2026 2:19pm | Jul 12, 2026 2:39pm | Jul 12, 2026 2:39pm | Jul 12, 2026 2:39pm |  |  | Fair | No | Area found ok
Non-Outage | J.E.26.07.11540 | C001852654 | Neville Spencer | null | Completed | null | null | Jul 12, 2026 7:53am | Jul 12, 2026 7:54am | Jul 12, 2026 12:24pm | Jul 12, 2026 12:24pm | Jul 12, 2026 2:28pm | Jul 12, 2026 2:28pm | Jul 12, 2026 2:29pm | Jul 12, 2026 2:29pm |  |  | Fair | No | Found supply in area.
Outage | J.E.26.07.13055 | C001852653 | Hartley Chin | Clarendon | Completed | Load_264818 | Parnassus - 310 | Jul 12, 2026 7:52am | Jul 12, 2026 7:53am | Jul 12, 2026 8:13am | Jul 12, 2026 8:37am | Jul 12, 2026 9:16am | Jul 12, 2026 9:17am | Jul 12, 2026 9:17am | Jul 12, 2026 9:17am |  |  | SevereWind | No | Call related to job # 11808 ..
Outage | J.E.26.07.13316 | C001852652 | Neville Spencer | Clarendon | Completed | Load_1003286 | May Pen - 110 | Jul 12, 2026 7:52am | Jul 12, 2026 7:53am | Jul 12, 2026 8:19am | Jul 12, 2026 8:24am | Jul 12, 2026 10:11am | Jul 12, 2026 10:40am | Jul 12, 2026 10:44am | Jul 12, 2026 10:44am |  |  | Fair | No | Remade corroded phase and neutral joints at pothead on 2 wire service used 2, 6/6 sleeves voltage reading 114.
Non-Outage | J.E.26.07.10760 | C001852651 | Hartley Chin | null | Completed | null | null | Jul 12, 2026 7:51am | Jul 12, 2026 7:51am | Jul 12, 2026 11:06am | Jul 12, 2026 12:20pm | Jul 12, 2026 12:20pm | Jul 12, 2026 12:21pm | Jul 12, 2026 12:22pm | Jul 12, 2026 12:22pm |  |  | SevereWind | No | Call related to job # 12288 ..
Outage | J.E.26.07.12246 | C001852648 | Hartley Chin | Clarendon | Completed | Load_267468 | Parnassus - 310 | Jul 12, 2026 7:51am | Jul 12, 2026 7:51am | Jul 12, 2026 8:07am | Jul 12, 2026 11:05am | Jul 12, 2026 11:05am | Jul 12, 2026 11:05am | Jul 12, 2026 11:06am | Jul 12, 2026 11:06am |  |  | SevereWind | No | Contacted customer… she stated that issue was resolved …
Outage | J.E.26.07.12288 | C001852649 | Hartley Chin | Clarendon | Completed | Load_247306 | Monymusk - 410 | Jul 12, 2026 7:51am | Jul 12, 2026 7:51am | Jul 12, 2026 11:06am | Jul 12, 2026 11:07am | Jul 12, 2026 12:11pm | Jul 12, 2026 12:19pm | Jul 12, 2026 12:20pm | Jul 12, 2026 12:20pm |  |  | SevereWind | No | Isolate 10 KVA transformer (no pole #) due to burnt X1 drop lead found , replace x1 drop lead , re-energize transformer … use : 1 clamp , 5ft copper …
Outage | J.E.26.07.13530 | C001852650 | Hartley Chin | Clarendon | Completed | Load_245215 | Monymusk - 410 | Jul 12, 2026 7:51am | Jul 12, 2026 7:51am | Jul 12, 2026 9:52am | Jul 12, 2026 9:52am | Jul 12, 2026 10:34am | Jul 12, 2026 11:02am | Jul 12, 2026 11:04am | Jul 12, 2026 11:04am | BrokenWire |  | SevereWind | No | Isolate 25 KVA transformer @ pole # 551246 due to broken open secondary phase found in 1 span , repair broken phase , re-energize transformer… use 1 clamp , 10ft #2 conductor..
Non-Outage | J.E.26.07.12621 | C001852647 | Fitzroy Turner | null | Completed | null | null | Jul 12, 2026 7:45am | Jul 12, 2026 8:56am | Jul 12, 2026 12:15pm | Jul 12, 2026 12:16pm | Jul 12, 2026 12:16pm | Jul 12, 2026 12:16pm | Jul 12, 2026 12:20pm | Jul 12, 2026 12:20pm |  |  | Fair | No | Customer supply restored after repair burnt off switches top retention premises line 3 25 amps junction fuse replaced
Non-Outage | J.E.26.07.13521 | C001852645 | Collin Robinson | null | Completed | null | null | Jul 12, 2026 7:36am | Jul 12, 2026 7:36am | Jul 12, 2026 8:08am | Jul 12, 2026 9:00am | Jul 12, 2026 9:18am | Jul 12, 2026 10:03am | Jul 12, 2026 10:03am | Jul 12, 2026 10:03am | BrokenWire |  | Fair | No | Cut tree branch near primary conductor and replace 8 amps junction fuse
Outage | J.E.26.07.13573 | C001852644 | Lancelot Brown | Hanover | Completed | Load_265958 | Orange Bay - 310 | Jul 12, 2026 7:34am | Jul 12, 2026 8:02am | Jul 12, 2026 8:28am | Jul 12, 2026 9:49am | Jul 12, 2026 9:49am | Jul 12, 2026 10:05am | Jul 12, 2026 10:06am | Jul 12, 2026 10:06am |  |  | EarthMovement | No | Found 25kva fuse blown patroll found bird contact with primary line and switch bracket removed bird from primary line replace 1-2amps fuse at 25kva no pole number supply restore
Outage | J.E.26.07.13219 | C001852643 | Roxroy Needham | St.Ann | Completed | Load_254165 | Cardiff Hall - 210 | Jul 12, 2026 7:32am | Jul 12, 2026 7:33am | Jul 12, 2026 7:47am | Jul 12, 2026 7:47am | Jul 12, 2026 8:03am | Jul 12, 2026 8:04am | Jul 12, 2026 8:04am | Jul 12, 2026 8:04am |  |  | Fair | No | Meter is on PMC need field service to check meter
Outage | J.E.26.07.13209 | C001852640 | Daniel Francis | St.Ann | Completed | Load_267692 | Cardiff Hall - 210 | Jul 12, 2026 7:31am | Jul 12, 2026 7:49pm | Jul 12, 2026 7:59pm | Jul 12, 2026 7:59pm | Jul 12, 2026 7:59pm | Jul 12, 2026 8:02pm | Jul 12, 2026 8:02pm | Jul 12, 2026 8:02pm |  |  | Fair | No | Unable to find customer no dereliction customer not answering
Outage | J.E.26.07.13220 | C001852641 | Roxroy Needham | St.Ann | Completed | Load_250632 | Cardiff Hall - 210 | Jul 12, 2026 7:31am | Jul 12, 2026 7:33am | Jul 12, 2026 12:47pm | Jul 12, 2026 12:47pm | Jul 12, 2026 12:47pm | Jul 12, 2026 12:47pm | Jul 12, 2026 12:48pm | Jul 12, 2026 12:48pm |  |  | Fair | No | Customer issue was resolved
Outage | J.E.26.07.13512 | C001852642 | Roxroy Needham | St.Ann | Completed | Load_268637 | Cardiff Hall - 210 | Jul 12, 2026 7:31am | Jul 12, 2026 7:33am | Jul 12, 2026 7:47am | Jul 12, 2026 12:23pm | Jul 12, 2026 12:23pm | Jul 12, 2026 12:37pm | Jul 12, 2026 12:45pm | Jul 12, 2026 12:45pm | Fire |  | Fair | No | Splice and retention 1 span of secondary neutral used 2 pg clamp and replace 1- 3 amp transformer fuse
Outage | J.E.26.07.08322 | C001852637 | Roxroy Needham | St.Ann | Completed | Load_252066 | Cardiff Hall - 310 | Jul 12, 2026 7:30am | Jul 12, 2026 7:33am | Jul 12, 2026 7:59am | Jul 12, 2026 8:04am | Jul 12, 2026 9:49am | Jul 12, 2026 9:49am | Jul 12, 2026 9:51am | Jul 12, 2026 9:51am |  |  | Fair | No | Meter found with locked need kee to open lock
Outage | J.E.26.07.13004 | C001852638 | Roxroy Needham | St.Ann | Completed | Load_243889 | Cardiff Hall - 210 | Jul 12, 2026 7:30am | Jul 12, 2026 7:33am | Jul 12, 2026 12:49pm | Jul 12, 2026 12:49pm | Jul 12, 2026 1:36pm | Jul 12, 2026 2:33pm | Jul 12, 2026 2:33pm | Jul 12, 2026 2:33pm | Fire | Y | Fair | No | Open a 25 KVA transformer at pole to repair 2 jumper used 4 pg clamp
Outage | J.E.26.07.13070 | C001852639 | Roxroy Needham | St.Ann | Completed | Load_268637 | Cardiff Hall - 210 | Jul 12, 2026 7:30am | Jul 12, 2026 7:33am | Jul 12, 2026 7:47am | Jul 12, 2026 12:45pm | Jul 12, 2026 12:45pm | Jul 12, 2026 12:37pm | Jul 12, 2026 12:46pm | Jul 12, 2026 12:46pm | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Splice and retention 1 span of secondary neutral used 2 pg clamp and replace 1- 3 amp transformer
Non-Outage | J.E.26.07.12546 | C001852635 | Stephen Taylor | null | Completed | null | null | Jul 12, 2026 7:27am | Jul 12, 2026 7:29am | Jul 12, 2026 9:30am | Jul 12, 2026 9:30am | Jul 12, 2026 9:30am | Jul 12, 2026 9:30am | Jul 12, 2026 9:31am | Jul 12, 2026 9:31am |  |  | Fair | No | Call to customer and customer said power is back and okay now
Outage | J.E.26.07.12556 | C001852634 | Stephen Taylor | St.Thomas | Completed | Load_266441 | Lysson - 410 | Jul 12, 2026 7:27am | Jul 12, 2026 7:27am | Jul 12, 2026 9:14am | Jul 12, 2026 9:14am | Jul 12, 2026 9:14am | Jul 12, 2026 9:14am | Jul 12, 2026 9:15am | Jul 12, 2026 9:15am |  |  | Fair | No | Call to customer and customer said power was restored last night
Outage | J.E.26.07.12662 | C001852632 | Stephen Taylor | KSAS | Completed | Load_269603 | Good Year - 210 | Jul 12, 2026 7:27am | Jul 12, 2026 7:27am | Jul 12, 2026 9:44am | Jul 12, 2026 9:44am | Jul 12, 2026 9:44am | Jul 12, 2026 9:44am | Jul 12, 2026 9:46am | Jul 12, 2026 9:46am |  |  | Fair | No | Call to customer and customer said power is working okay now
Outage | J.E.26.07.12805 | C001852633 | Stephen Taylor | St.Thomas | Completed | Load_238855 | Good Year - 210 | Jul 12, 2026 7:27am | Jul 12, 2026 7:27am | Jul 12, 2026 9:35am | Jul 12, 2026 9:35am | Jul 12, 2026 9:35am | Jul 12, 2026 9:35am | Jul 12, 2026 9:36am | Jul 12, 2026 9:36am |  |  | Fair | No | Call to customer and customer said light is back now a okay
Outage | J.E.26.07.12858 | C001852631 | Stephen Taylor | St.Thomas | Completed | Load_247908 | Good Year - 210 | Jul 12, 2026 7:26am | Jul 12, 2026 7:27am | Jul 13, 2026 9:14am | Jul 13, 2026 11:35am | Jul 13, 2026 11:40am | Jul 13, 2026 11:40am | Jul 13, 2026 11:44am | Jul 13, 2026 11:44am |  |  | Fair | No | Patrol the area power is in the area a lot of call to single customer no one answered the phone
Outage | J.E.26.07.13031 | C001852630 | Stephen Taylor | St.Thomas | Completed | Load_243194 | Good Year - 210 | Jul 12, 2026 7:26am | Jul 12, 2026 7:27am | Jul 12, 2026 9:40am | Jul 12, 2026 9:40am | Jul 12, 2026 9:40am | Jul 12, 2026 9:40am | Jul 12, 2026 9:41am | Jul 12, 2026 9:41am |  |  | Fair | No | Call to customer and customer said light is back now and okay
Outage | J.E.26.07.13120 | C001852628 | Stephen Taylor | KSAS | Completed | Load_249841 | Good Year - 210 | Jul 12, 2026 7:26am | Jul 12, 2026 7:27am | Jul 12, 2026 9:52am | Jul 12, 2026 9:52am | Jul 12, 2026 9:52am | Jul 12, 2026 9:53am | Jul 12, 2026 9:57am | Jul 12, 2026 9:57am | BrokenWire |  | Fair | No | Call to customer and customer said it the rong number but she have light now
Outage | J.E.26.07.13306 | C001852629 | Stephen Taylor | St.Thomas | Completed | Load_267447 | Good Year - 210 | Jul 12, 2026 7:26am | Jul 12, 2026 7:27am | Jul 12, 2026 5:57pm | Jul 12, 2026 5:57pm | Jul 12, 2026 8:04pm | Jul 12, 2026 8:04pm | Jul 12, 2026 8:36pm | Jul 12, 2026 8:36pm | BrokenWire |  | Fair | No | Clean up transformer drop lead and use 3 one bolts clamp
Outage | J.E.26.07.13525 | C001852627 | Stephen Taylor | KSAS | Completed | Load_348616 | Good Year - 210 | Jul 12, 2026 7:26am | Jul 12, 2026 7:27am | Jul 12, 2026 9:24am | Jul 12, 2026 9:24am | Jul 12, 2026 9:24am | Jul 12, 2026 9:24am | Jul 12, 2026 9:25am | Jul 12, 2026 9:25am |  |  | Fair | No | Check with customer and customer said power is back now and okay
Outage | J.E.26.07.13527 | C001852626 | Stephen Taylor | KSAS | Completed | Load_351021 | Good Year - 210 | Jul 12, 2026 7:26am | Jul 12, 2026 7:27am | Jul 12, 2026 9:21am | Jul 12, 2026 9:21am | Jul 12, 2026 9:21am | Jul 12, 2026 9:21am | Jul 12, 2026 9:22am | Jul 12, 2026 9:22am |  |  | Fair | No | Call to customer and customer said power is back now and okay
Non-Outage | J.E.26.07.13275 | C001852625 | Horace Malcolm | null | Completed | null | null | Jul 12, 2026 7:25am | Jul 12, 2026 7:25am | Jul 12, 2026 8:03am | Jul 12, 2026 8:03am | Jul 12, 2026 8:14am | Jul 12, 2026 8:51am | Jul 12, 2026 8:51am | Jul 12, 2026 8:51am | Fire |  | Fair | No | Check found no fire on pole area check and found ok unable to locate customer phone calls to customer unavailable
Outage | J.E.26.07.12526 | C001852620 | Raymond Carr | St.Mary | Completed | Load_260493 | Blackstonedge - 110 | Jul 12, 2026 7:16am | Jul 12, 2026 7:17am | Jul 12, 2026 7:36am | Jul 12, 2026 7:36am | Jul 12, 2026 10:22am | Jul 12, 2026 10:31am | Jul 12, 2026 10:38am | Jul 12, 2026 10:38am |  |  | Fair | No | Tripp saver found operated at pole number 400571, line patrol and found okay, tree contact was suspected. Tripp saver reset and supply was restored.
Outage | J.E.26.07.13508 | C001852619 | Marlon Brown | Trelawny | Completed | Load_556269 | Duncans - 210 | Jul 12, 2026 7:12am | Jul 12, 2026 7:13am | Jul 12, 2026 9:32am | Jul 12, 2026 9:32am | Jul 12, 2026 10:10am | Jul 12, 2026 10:58am | Jul 12, 2026 10:58am | Jul 12, 2026 10:58am |  |  | Fair | No | Isolated 25kva transformer to repair drop lead, use 3 pg clamps Voltage found 118Voltage leaving 118/118=236
Outage | J.E.26.07.12864 | C001852611 | Daniel Francis | St.Ann | Completed | Load_252833 | Ocho Rios - 310 | Jul 12, 2026 1:27am | Jul 12, 2026 1:27am | Jul 12, 2026 2:26am | Jul 12, 2026 2:27am | Jul 12, 2026 2:33am | Jul 12, 2026 2:35am | Jul 12, 2026 2:35am | Jul 12, 2026 2:35am |  |  | Fair | No | Not found customer not answering phone
Outage | J.E.26.07.13065 | C001852613 | Daniel Francis | St.Ann | Completed | Load_239479 | Ocho Rios - 310 | Jul 12, 2026 1:27am | Jul 12, 2026 1:27am | Jul 12, 2026 2:35am | Jul 12, 2026 2:35am | Jul 12, 2026 3:18am | Jul 12, 2026 3:20am | Jul 12, 2026 3:21am | Jul 12, 2026 3:21am |  |  | Fair | No | Unable to locate. Customer not answering phone
Outage | J.E.26.07.13102 | C001852612 | Daniel Francis | St.Ann | Completed | Load_243953 | Ocho Rios - 310 | Jul 12, 2026 1:27am | Jul 12, 2026 1:27am | Jul 12, 2026 1:48am | Jul 12, 2026 1:48am | Jul 12, 2026 2:20am | Jul 12, 2026 2:22am | Jul 12, 2026 2:23am | Jul 12, 2026 2:23am |  |  | Fair | No | Found okay customer say someone came there yesterday
Outage | J.E.26.07.12245 | C001852608 | Fitzroy Turner | KSAS | Completed | Load_256501 | Hunts Bay - 310 | Jul 12, 2026 1:23am | Jul 12, 2026 12:19pm | Jul 12, 2026 12:57pm | Jul 12, 2026 12:59pm | Jul 12, 2026 1:04pm | Jul 12, 2026 1:05pm | Jul 12, 2026 1:05pm | Jul 12, 2026 1:05pm |  |  | Fair | No | Customer premises close at this time
Outage | J.E.26.07.12832 | C001852609 | Christopher Edwards | KSAS | Completed | Load_256908 | Hunts Bay - 310 | Jul 12, 2026 1:23am | Jul 12, 2026 1:24am | Jul 12, 2026 3:41am | Jul 12, 2026 3:41am | Jul 12, 2026 3:41am | Jul 12, 2026 6:37am | Jul 12, 2026 6:38am | Jul 12, 2026 6:38am |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Outage | J.E.26.07.12981 | C001852606 | Swon Miller | St.James | Completed | Load_254099 | Bogue - 310 | Jul 12, 2026 1:13am | Jul 12, 2026 1:14am | Jul 12, 2026 1:17am | Jul 12, 2026 1:17am | Jul 12, 2026 3:26am | Jul 12, 2026 3:58am | Jul 12, 2026 3:59am | Jul 12, 2026 3:59am |  |  | Fair | No | Found 5 kva transformer fuse blown cause by contamination replace 1 amp in a 5 kva transformer
Outage | J.E.26.07.11211 | C001852604 | Delano Gayle | St.Catherine | Completed | Load_253711 | New Michelton - 410 | Jul 12, 2026 1:05am | Jul 12, 2026 1:06am | Jul 12, 2026 5:00am | Jul 12, 2026 5:00am | Jul 12, 2026 6:05am | Jul 12, 2026 6:11am | Jul 12, 2026 6:11am | Jul 12, 2026 6:11am |  |  | Fair | No | Blown 25kva transformer fuse no pole number replace 3amps
Outage | J.E.26.07.13269 | C001852597 | Delano Gayle | St.Catherine | Completed | Load_259906 | New Michelton - 210 | Jul 11, 2026 11:05pm | Jul 11, 2026 11:05pm | Jul 12, 2026 12:25am | Jul 12, 2026 12:25am | Jul 12, 2026 12:28am | Jul 12, 2026 12:28am | Jul 12, 2026 12:28am | Jul 12, 2026 12:28am |  |  | Fair | No | Premises found related to call where 25amps junction fuse was replaced
Outage | J.E.26.07.13276 | C001852598 | Delano Gayle | St.Catherine | Completed | Load_252447 | New Michelton - 210 | Jul 11, 2026 11:05pm | Jul 11, 2026 11:05pm | Jul 11, 2026 11:18pm | Jul 11, 2026 11:18pm | Jul 12, 2026 12:01am | Jul 12, 2026 12:25am | Jul 12, 2026 12:25am | Jul 12, 2026 12:25am |  |  | Fair | No | Blown junction on single phase T-off line to cassava pond, patrolled line section and found okay for closure replace 25amps
Outage | J.E.26.07.13267 | C001852596 | Swon Miller | St.James | Completed | Load_270234 | Queens Drive - 710 | Jul 11, 2026 10:55pm | Jul 11, 2026 10:56pm | Jul 11, 2026 11:03pm | Jul 11, 2026 11:03pm | Jul 11, 2026 11:37pm | Jul 22, 2026 12:33am | Jul 12, 2026 12:33am | Jul 12, 2026 12:33am | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Found 10 amp junction fuse blown cause by secondary insulator dislodged from rack replace insulator and replace 8 amp junction fuse
Outage | J.E.26.07.13227 | C001852594 | Raymond Lewis | Clarendon | Completed | Load_269181 | May Pen - 110 | Jul 11, 2026 10:28pm | Jul 12, 2026 8:22am | Jul 12, 2026 8:36am | Jul 12, 2026 8:36am | Jul 12, 2026 10:11am | Jul 12, 2026 10:57am | Jul 12, 2026 10:59am | Jul 12, 2026 10:59am |  |  | Fair | No | Refuse and close 20 A junction fuse
Outage | J.E.26.07.13139 | C001852593 | Wan Carlos Scarlett | St.Catherine | Completed | Load_244063 | Twickenham - 210 | Jul 11, 2026 10:02pm | Jul 12, 2026 7:59am | Jul 12, 2026 8:48am | Jul 12, 2026 9:36am | Jul 12, 2026 10:33am | Jul 12, 2026 12:39pm | Jul 12, 2026 12:41pm | Jul 12, 2026 12:41pm |  | Y | Fair | No | Refuse 50KVA transformer with a 5amp fuse no pole # was found clear tree lim from off open secondary line
Outage | J.E.26.07.12727 | C001852585 | Fitzroy Turner | KSAS | Completed | Load_293369 | Hunts Bay - 810 | Jul 11, 2026 9:02pm | Jul 12, 2026 8:57am | Jul 12, 2026 2:15pm | Jul 12, 2026 5:24pm | Jul 12, 2026 5:57pm | Jul 12, 2026 6:04pm | Jul 12, 2026 6:06pm | Jul 12, 2026 6:06pm |  |  | Fair | No | Customer service restored after service reconnected
Non-Outage | J.E.26.01.24030 | C001852583 | Tajay Bernard | null | Completed | null | null | Jul 11, 2026 9:01pm | Jul 11, 2026 9:02pm | Jul 11, 2026 9:57pm | Jul 11, 2026 9:57pm | Jul 11, 2026 10:20pm | Jul 11, 2026 10:42pm | Jul 11, 2026 10:42pm | Jul 11, 2026 10:42pm |  |  | Fair | No | Clean and remake joints at jps pole use 2 clamps voltage readings 112/112 224
Non-Outage | J.E.26.07.13036 | C001852580 | Tajay Bernard | Hanover | Completed | Load_257115 | Orange Bay - 310 | Jul 11, 2026 9:00pm | Jul 11, 2026 9:02pm | Jul 11, 2026 9:13pm | Jul 11, 2026 9:13pm | Jul 11, 2026 9:35pm | Jul 11, 2026 9:56pm | Jul 11, 2026 9:57pm | Jul 11, 2026 9:57pm |  |  | Fair | No | Clean and remake transformer neutral drop led use 1 clamps voltage reading 114/115/230
Outage | J.E.26.07.13215 | C001852579 | Rayon Foster | Hanover | Completed | Load_257564 | Orange Bay - 310 | Jul 11, 2026 8:58pm | Jul 12, 2026 7:35am | Jul 12, 2026 7:59am | Jul 12, 2026 7:59am | Jul 12, 2026 9:33am | Jul 12, 2026 10:35am | Jul 12, 2026 10:35am | Jul 12, 2026 10:35am | BrokenWire |  | Fair | No | Open one 25 kva transformer to repair Broken down neutral in one span cause by banging wires splic and retention neutral and secondary top phase using about 50 feet of #2 wire voltage after closing 25 kva transformer 118/117AB235
Outage | J.E.26.07.13028 | C001852578 | Michael Christian | St.James | Completed | Load_253530 | Queens Drive - 710 | Jul 11, 2026 8:50pm | Jul 11, 2026 8:51pm | Jul 11, 2026 9:46pm | Jul 11, 2026 9:49pm | Jul 11, 2026 10:21pm | Jul 11, 2026 10:27pm | Jul 11, 2026 10:27pm | Jul 11, 2026 10:27pm |  |  | Fair | No | Check and found okay voltage 111 110 222 at meter
Outage | J.E.26.07.13148 | C001852576 | Michael Christian | St.James | Completed | Load_258936 | Queens Drive - 710 | Jul 11, 2026 8:50pm | Jul 11, 2026 8:51pm | Jul 11, 2026 9:05pm | Jul 11, 2026 9:05pm | Jul 11, 2026 9:46pm | Jul 11, 2026 9:49pm | Jul 11, 2026 9:49pm | Jul 11, 2026 9:49pm |  |  | Fair | No | Check and found okay customer needs street lights to work and
Outage | J.E.26.07.13156 | C001852577 | Michael Christian | St.James | Completed | Load_292055 | Bogue - 310 | Jul 11, 2026 8:50pm | Jul 11, 2026 8:51pm | Jul 11, 2026 10:27pm | Jul 11, 2026 10:27pm | Jul 11, 2026 10:53pm | Jul 11, 2026 10:53pm | Jul 11, 2026 10:54pm | Jul 11, 2026 10:54pm |  |  | Fair | No | Premises not found
Non-Outage | J.E.26.07.11653 | C001852575 | Oshane Warren | Westmoreland | Completed | Load_260812 | Paradise - 110 | Jul 11, 2026 8:45pm | Jul 11, 2026 8:45pm | Jul 11, 2026 10:24pm | Jul 11, 2026 10:24pm | Jul 11, 2026 10:55pm | Jul 11, 2026 10:57pm | Jul 11, 2026 10:58pm | Jul 11, 2026 10:58pm |  |  | Fair | No | Unable to locate or contact customer on the phone
Non-Outage | J.E.26.07.12320 | C001852574 | Oshane Warren | Westmoreland | Completed | Load_245695 | Paradise - 210 | Jul 11, 2026 8:45pm | Jul 11, 2026 8:45pm | Jul 11, 2026 10:59pm | Jul 11, 2026 10:59pm | Jul 11, 2026 10:59pm | Jul 11, 2026 10:59pm | Jul 11, 2026 11:00pm | Jul 11, 2026 11:00pm |  |  | Fair | No | Unable to locate or contact customer on the phone
Outage | J.E.26.07.13111 | C001852572 | Eric Williams | KSAN | Completed | Load_248378 | Hope - 410 | Jul 11, 2026 8:43pm | Jul 11, 2026 8:43pm | Jul 11, 2026 9:16pm | Jul 11, 2026 9:17pm | Jul 11, 2026 10:01pm | Jul 11, 2026 10:12pm | Jul 11, 2026 10:13pm | Jul 11, 2026 10:13pm | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Premises found okay, cable wires
Outage | J.E.26.07.13149 | C001852568 | Barnett Brown | Manchester | Completed | Load_265119 | Kendal - 310 | Jul 11, 2026 7:37pm | Jul 11, 2026 7:37pm | Jul 11, 2026 7:51pm | Jul 11, 2026 8:07pm | Jul 11, 2026 9:11pm | Jul 11, 2026 9:15pm | Jul 11, 2026 9:16pm | Jul 11, 2026 9:16pm |  |  | Fair | No
Outage | J.E.26.07.13113 | C001852565 | Andre Williams | Trelawny | Completed | Load_292472 | Duncans - 110 | Jul 11, 2026 7:05pm | Jul 11, 2026 7:05pm | Jul 11, 2026 7:12pm | Jul 11, 2026 8:26pm | Jul 11, 2026 8:26pm | Jul 11, 2026 8:27pm | Jul 11, 2026 8:29pm | Jul 11, 2026 8:29pm |  |  | Fair | No | Caller problem is located in Portland not trelawny wrong address a sign to call
Outage | J.E.26.07.12879 | C001852562 | Andre Williams | Trelawny | Completed | Load_265828 | Duncans - 110 | Jul 11, 2026 6:48pm | Jul 11, 2026 6:49pm | Jul 11, 2026 7:18pm | Jul 11, 2026 7:50pm | Jul 11, 2026 7:50pm | Jul 11, 2026 7:52pm | Jul 11, 2026 7:57pm | Jul 11, 2026 7:57pm |  |  | Fair | No | Defective #6 conductor feeding two customer, span more than 100 ft wire is isolated due to wire being burnt reffer to field service.
Outage | J.E.26.07.13066 | C001852563 | Floyd Taylor | Trelawny | Completed | Load_261734 | Duncans - 210 | Jul 11, 2026 6:48pm | Jul 11, 2026 7:55pm | Jul 11, 2026 8:33pm | Jul 11, 2026 8:33pm | Jul 11, 2026 9:09pm | Jul 11, 2026 10:17pm | Jul 11, 2026 10:19pm | Jul 11, 2026 10:19pm |  |  | Fair | No | 15kva transformer fuse blown, one 1 amp was replaced with a 2Amp after line was patrolled and nothing was found, voltage reading 115,117,233
Outage | J.E.26.07.12874 | C001852558 | Floyd Taylor | Trelawny | Completed | Load_250348 | Greenwood - 210 | Jul 11, 2026 6:47pm | Jul 11, 2026 6:48pm | Jul 11, 2026 7:05pm | Jul 11, 2026 7:05pm | Jul 11, 2026 7:48pm | Jul 11, 2026 8:17pm | Jul 11, 2026 8:18pm | Jul 11, 2026 8:18pm |  |  | Fair | No | Clean and remake joints at pole using 2pg clamps voltage readings left 116,118,235
Outage | J.E.26.07.12934 | C001852560 | Marlon Brown | Trelawny | Completed | Load_255782 | Martha Brae - 210 | Jul 11, 2026 6:47pm | Jul 12, 2026 7:14am | Jul 12, 2026 7:57am | Jul 12, 2026 7:57am | Jul 12, 2026 8:02am | Jul 12, 2026 9:31am | Jul 12, 2026 9:31am | Jul 12, 2026 9:31am |  |  | Fair | No | Premises closed
Outage | J.E.26.07.12939 | C001852559 | Floyd Taylor | Trelawny | Completed | Load_244229 | Greenwood - 110 | Jul 11, 2026 6:47pm | Jul 11, 2026 6:48pm | Jul 12, 2026 7:57am | Jul 12, 2026 7:57am | Jul 12, 2026 8:29am | Jul 12, 2026 9:24am | Jul 12, 2026 9:27am | Jul 12, 2026 9:27am |  |  | Fair | No | Customer is not home, currently at work however will be returning in the evening .
Outage | J.E.26.07.13018 | C001852561 | Floyd Taylor | Trelawny | Completed | Load_294629 | Greenwood - 110 | Jul 11, 2026 6:47pm | Jul 11, 2026 6:48pm | Jul 11, 2026 10:20pm | Jul 11, 2026 10:20pm | Jul 12, 2026 6:16am | Jul 12, 2026 6:17am | Jul 12, 2026 6:17am | Jul 12, 2026 6:17am | TreeContact |  | Fair | No | Customer breaker trip
Outage | J.E.26.07.13008 | C001852551 | Lancelot Brown | Hanover | Completed | Load_257800 | Orange Bay - 310 | Jul 11, 2026 6:09pm | Jul 11, 2026 6:09pm | Jul 11, 2026 7:20pm | Jul 11, 2026 7:20pm | Jul 11, 2026 7:59pm | Jul 11, 2026 8:54pm | Jul 11, 2026 8:55pm | Jul 11, 2026 8:55pm |  |  | Fair | No | Found junction fuse blown patroll found nothing carry out test closed and it hold supply restore
Outage | J.E.26.07.13012 | C001852552 | Lancelot Brown | Hanover | Completed | Load_253661 | Orange Bay - 310 | Jul 11, 2026 6:09pm | Jul 11, 2026 6:09pm | Jul 11, 2026 7:19pm | Jul 11, 2026 9:08pm | Jul 11, 2026 9:08pm | Jul 11, 2026 9:08pm | Jul 11, 2026 9:09pm | Jul 11, 2026 9:09pm |  |  | Fair | No | This call related to 25amps junction fuse supply restore
Non-Outage | J.E.26.07.12971 | C001852550 | Richard Samuda | null | Completed | null | null | Jul 11, 2026 5:54pm | Jul 11, 2026 5:54pm | Jul 11, 2026 6:01pm | Jul 11, 2026 6:57pm | Jul 11, 2026 7:35pm | Jul 11, 2026 9:25am | Jul 11, 2026 9:25pm | Jul 11, 2026 9:25pm | BrokenWire |  | Fair | No | Splice and reconnected span of secondary line that was broken using 20ft of aluminum wire , number 2 preform and one bolt clamp customer back to normal
Outage | J.E.26.07.12938 | C001852549 | Richard Samuda | Manchester | Completed | Load_267614 | Spur Tree - 310 | Jul 11, 2026 5:53pm | Jul 11, 2026 5:54pm | Jul 11, 2026 6:08pm | Jul 11, 2026 6:08pm | Jul 11, 2026 6:56pm | Jul 11, 2026 6:57pm | Jul 11, 2026 6:57pm | Jul 11, 2026 6:57pm |  |  | Fair | No | Found ok power was restored
Outage | J.E.26.07.13005 | C001852545 | Marlon Authors | Manchester | Completed | Load_555886 | Spur Tree - 210 | Jul 11, 2026 5:50pm | Jul 11, 2026 5:54pm | Jul 11, 2026 6:52pm | Jul 11, 2026 6:52pm | Jul 11, 2026 7:32pm | Jul 11, 2026 7:51pm | Jul 11, 2026 7:51pm | Jul 11, 2026 7:51pm | BrokenWire |  | Fair | No | Supply checked and found service wire neutral burnt off caused by severe winds. Splice and retention same using 10 feet of #6 conductor and two clamps. Supply leave working okay rdg 113 volts
Non-Outage | J.E.26.07.13003 | C001852544 | Oshane Warren | null | Completed | null | null | Jul 11, 2026 5:49pm | Jul 11, 2026 5:55pm | Jul 11, 2026 6:10pm | Jul 11, 2026 6:10pm | Jul 11, 2026 7:05pm | Jul 11, 2026 7:06pm | Jul 11, 2026 7:07pm | Jul 11, 2026 7:07pm |  |  | Fair | No | Hanover call
Outage | J.E.26.07.12937 | C001852543 | Richman Whyte | Westmoreland | Completed | Load_253644 | Paradise - 310 | Jul 11, 2026 5:49pm | Jul 11, 2026 5:55pm | Jul 11, 2026 8:29pm | Jul 11, 2026 8:29pm | Jul 11, 2026 8:49pm | Jul 11, 2026 8:50pm | Jul 11, 2026 8:51pm | Jul 11, 2026 8:51pm |  |  | Fair | No | Check and found ok 115 115 230
Outage | J.E.26.07.12902 | C001852542 | Elvis Trowers | KSAN | Completed | Load_265279 | Hope - 510 | Jul 11, 2026 5:45pm | Jul 12, 2026 7:36am | Jul 12, 2026 9:48am | Jul 12, 2026 9:48am | Jul 12, 2026 10:34am | Jul 12, 2026 10:41am | Jul 12, 2026 10:41am | Jul 12, 2026 10:41am |  |  | Fair | Yes | Customer was found with regular electricity supply, but he’s requesting that the illegal connections be removed that is causing him the inconvenience.
Outage | J.E.26.07.12775 | C001852540 | Hartley Chin | Clarendon | Completed | Load_248640 | Parnassus - 310 | Jul 11, 2026 5:27pm | Jul 11, 2026 5:28pm | Jul 11, 2026 6:08pm | Jul 11, 2026 6:59pm | Jul 11, 2026 7:00pm | Jul 11, 2026 7:01pm | Jul 11, 2026 7:01pm | Jul 11, 2026 7:01pm |  |  | SevereWind | No | Call related t job # 12914 ..
Non-Outage | J.E.26.07.12958 | C001852537 | Shamour Haughton | null | Completed | null | null | Jul 11, 2026 5:25pm | Jul 12, 2026 7:31am | Jul 12, 2026 8:11am | Jul 12, 2026 8:11am | Jul 12, 2026 8:11am | Jul 12, 2026 8:11am | Jul 12, 2026 8:16am | Jul 12, 2026 8:16am |  |  | Fair | No | Unable to locate customer, cell number went voicemail after several calls
Outage | J.E.26.07.12499 | C001852535 | Ricky Hall | St.Catherine | Completed | Load_244401 | Rhodens Pen - 210 | Jul 11, 2026 5:25pm | Jul 11, 2026 5:25pm | Jul 11, 2026 7:26pm | Jul 11, 2026 7:26pm | Jul 11, 2026 8:03pm | Jul 11, 2026 8:34pm | Jul 11, 2026 8:34pm | Jul 11, 2026 8:34pm |  |  | Fair | No | Customer found with supply
Outage | J.E.26.07.12859 | C001852538 | Richard Nicholas | St.Catherine | Completed | Load_240550 | Tredegar - 210 | Jul 11, 2026 5:25pm | Jul 11, 2026 5:26pm | Jul 11, 2026 6:04pm | Jul 11, 2026 6:04pm | Jul 11, 2026 8:45pm | Jul 11, 2026 10:29pm | Jul 11, 2026 10:31pm | Jul 11, 2026 10:31pm |  |  | Fair | No | Replaced blown 30amp near to pole #0053480 and blown 20amp across from the foot ball field.
Outage | J.E.26.07.12925 | C001852536 | Romeo Brissett | St.James | Completed | Load_264886 | Bogue - 310 | Jul 11, 2026 5:25pm | Jul 11, 2026 5:26pm | Jul 11, 2026 7:10pm | Jul 11, 2026 7:11pm | Jul 11, 2026 7:37pm | Jul 11, 2026 8:31pm | Jul 11, 2026 9:53pm | Jul 11, 2026 9:53pm | BrokenWire |  | Fair | No | Line patrolled and found power in the area.
Outage | J.E.26.07.12776 | C001852534 | Nickolas Rodriques | KSAS | Completed | Load_250337 | Duhaney - 210 | Jul 11, 2026 5:24pm | Jul 11, 2026 5:24pm | Jul 11, 2026 7:15pm | Jul 11, 2026 7:37pm | Jul 11, 2026 8:19pm | Jul 11, 2026 9:02pm | Jul 11, 2026 9:10pm | Jul 11, 2026 9:10pm |  |  | Fair | No | Customer stated that they are single phasing. While patrolling, a loud explosion (sounding like gunshot) was heard across the bushes and the team was unable to proceed with further checks due to safety concerns. However, it was observed that all three fuses were intact. Daylight attention required.
Outage | J.E.26.07.12417 | C001852533 | Wan Carlos Scarlett | St.Catherine | Completed | Load_261363 | Twickenham - 210 | Jul 11, 2026 5:22pm | Jul 11, 2026 5:22pm | Jul 12, 2026 1:20pm | Jul 12, 2026 1:20pm | Jul 12, 2026 1:40pm | Jul 12, 2026 1:40pm | Jul 12, 2026 1:43pm | Jul 12, 2026 1:43pm |  |  | Fair | No | Found customer service wire defective use 100ft of # 6 service wire use 3 Penn union at pothead use 3 one bolt clamps at open secondary line readings 114-115-231
Outage | J.E.26.07.12044 | C001852532 | Wan Carlos Scarlett | Portmore | Completed | Load_261040 | Naggo Head - 610 | Jul 11, 2026 5:19pm | Jul 11, 2026 5:20pm | Jul 11, 2026 8:56pm | Jul 11, 2026 8:56pm | Jul 11, 2026 9:36pm | Jul 11, 2026 10:10pm | Jul 11, 2026 10:11pm | Jul 11, 2026 10:11pm |  |  | Fair | No | Customer confirm that power supply has been restored
Outage | J.E.26.07.12718 | C001852531 | Wan Carlos Scarlett | Portmore | Completed | Load_239523 | Naggo Head - 610 | Jul 11, 2026 5:15pm | Jul 11, 2026 5:20pm | Jul 11, 2026 6:38pm | Jul 11, 2026 7:42pm | Jul 11, 2026 8:31pm | Jul 11, 2026 8:51pm | Jul 11, 2026 8:56pm | Jul 11, 2026 8:56pm |  |  | Fair | No | Customer was reconnected from escalation department power supply has been restored
Outage | J.E.26.07.12618 | C001852530 | Ricky Hall | St.Catherine | Completed | Load_1000369 | Rhodens Pen - 410 | Jul 11, 2026 5:02pm | Jul 11, 2026 5:02pm | Jul 11, 2026 6:58pm | Jul 11, 2026 6:58pm | Jul 11, 2026 7:24pm | Jul 11, 2026 7:25pm | Jul 11, 2026 7:26pm | Jul 11, 2026 7:26pm |  |  | Fair | No | Premises not found customer unreachable
Outage | J.E.26.07.12655 | C001852529 | Ricky Hall | St.Catherine | Completed | Load_1000356 | Rhodens Pen - 310 | Jul 11, 2026 5:00pm | Jul 11, 2026 5:01pm | Jul 11, 2026 6:30pm | Jul 11, 2026 6:30pm | Jul 11, 2026 6:42pm | Jul 11, 2026 6:58pm | Jul 11, 2026 6:58pm | Jul 11, 2026 6:58pm |  |  | Fair | No | Replaced blown 50 amps junction fuse
Non-Outage | J.E.26.07.10395 | C001852528 | Delano Gayle | null | Completed | null | null | Jul 11, 2026 4:59pm | Jul 11, 2026 4:59pm | Jul 11, 2026 7:22pm | Jul 11, 2026 7:22pm | Jul 11, 2026 7:46pm | Jul 11, 2026 8:01pm | Jul 11, 2026 8:01pm | Jul 11, 2026 8:01pm | BrokenWire |  | Fair | No | Area found okay premises not found no answer from customer phone
Outage | J.E.26.07.11843 | C001852524 | Ricky Hall | null | Completed | Load_265244 | Twickenham - 210 | Jul 11, 2026 4:44pm | Jul 11, 2026 4:45pm | Jul 11, 2026 6:14pm | Jul 11, 2026 6:15pm | Jul 11, 2026 6:29pm | Jul 11, 2026 6:29pm | Jul 11, 2026 6:29pm | Jul 11, 2026 6:29pm |  |  | Fair | No | Issue was resolved previously
Outage | J.E.26.07.12586 | C001852523 | Ricky Hall | St.Catherine | Completed | Load_305202 | Rhodens Pen - 310 | Jul 11, 2026 4:44pm | Jul 11, 2026 5:00pm | Jul 11, 2026 4:51pm | null | Jul 11, 2026 5:52pm | Jul 11, 2026 6:13pm | Jul 11, 2026 6:14pm | Jul 11, 2026 6:14pm |  |  | SevereWind | No | Repair burnt off 25 kva xfmr drop lead use 2 clamps 118/118/236
Outage | J.E.26.07.12927 | C001852522 | Roxroy Needham | St.Ann | Completed | Load_254165 | Cardiff Hall - 210 | Jul 11, 2026 4:41pm | Jul 11, 2026 4:42pm | Jul 11, 2026 6:46pm | Jul 11, 2026 6:46pm | Jul 11, 2026 6:47pm | Jul 11, 2026 6:48pm | Jul 11, 2026 6:49pm | Jul 11, 2026 6:49pm |  |  | Fair | No | Not getting customer on phone
Outage | J.E.26.07.12835 | C001852520 | Hartley Chin | Clarendon | Completed | Load_256530 | Parnassus - 310 | Jul 11, 2026 4:31pm | Jul 11, 2026 4:31pm | Jul 11, 2026 4:40pm | Jul 11, 2026 7:01pm | Jul 11, 2026 7:02pm | Jul 11, 2026 7:02pm | Jul 11, 2026 7:03pm | Jul 11, 2026 7:03pm |  |  | SevereWind | No | Prem not fond … unable to contact customer … direction inconclusive….
Outage | J.E.26.07.12845 | C001852521 | Hartley Chin | Clarendon | Completed | Load_246356 | Parnassus - 310 | Jul 11, 2026 4:31pm | Jul 11, 2026 4:31pm | Jul 11, 2026 4:40pm | Jul 11, 2026 6:58pm | Jul 11, 2026 6:58pm | Jul 11, 2026 6:58pm | Jul 11, 2026 6:58pm | Jul 11, 2026 6:58pm |  |  | SevereWind | No | Call related to job # 12914 ..
Outage | J.E.26.07.12914 | C001852519 | Hartley Chin | Clarendon | Completed | Load_248927 | Parnassus - 310 | Jul 11, 2026 4:31pm | Jul 11, 2026 4:31pm | Jul 11, 2026 4:41pm | Jul 11, 2026 6:31pm | Jul 11, 2026 6:50pm | Jul 11, 2026 6:51pm | Jul 11, 2026 6:57pm | Jul 11, 2026 6:57pm |  |  | SevereWind | No | Found 1 of 3 fuse barrel fall out of drop out switch … remove fuse barrel from drop out switch @ pole # 550872 .. string fused and close junction … Note: spring in switch top is loose … 1 of 3 junction is now string fused .. …
Outage | J.E.26.07.11493 | C001852517 | Clyde Brown | Clarendon | Completed | Load_257140 | Monymusk - 410 | Jul 11, 2026 4:24pm | Jul 11, 2026 4:25pm | Jul 11, 2026 8:51pm | Jul 11, 2026 8:51pm | Jul 11, 2026 8:52pm | Jul 11, 2026 6:03pm | Jul 11, 2026 8:57pm | Jul 11, 2026 8:57pm | BrokenWire |  | SevereWind | No | Broken secondary neutral open 25 kva transformer and repaired with 2-splicing sleeve ,1-preform 8ft-#2 conductor and 1- clamp.
Outage | J.E.26.07.12901 | C001852516 | Tyrese Williams | St.Ann | Completed | Load_268228 | Cardiff Hall - 210 | Jul 11, 2026 4:23pm | Jul 11, 2026 4:24pm | Jul 11, 2026 8:02pm | Jul 11, 2026 8:02pm | Jul 11, 2026 8:50pm | Jul 11, 2026 8:59pm | Jul 11, 2026 9:02pm | Jul 11, 2026 9:02pm | Fire |  | Fair | No | Open a junction fuse to Remake primary line jumper use 1 pg clamp
Outage | J.E.26.07.12877 | C001852514 | Clyde Brown | Clarendon | Completed | Load_248494 | Monymusk - 410 | Jul 11, 2026 4:21pm | Jul 11, 2026 4:22pm | Jul 11, 2026 7:40pm | Jul 11, 2026 7:40pm | Jul 11, 2026 8:44pm | Jul 11, 2026 8:42pm | Jul 11, 2026 8:51pm | Jul 11, 2026 8:51pm | BrokenWire |  | Fair | No | Broken 2 wire service spliced and retention with 8ft-#6 duplex
Outage | J.E.26.07.12909 | C001852515 | Daniel Francis | St.Ann | Completed | Load_267462 | Upper White River - 210 | Jul 11, 2026 4:21pm | Jul 11, 2026 4:23pm | Jul 11, 2026 7:23pm | Jul 11, 2026 7:23pm | Jul 11, 2026 7:32pm | Jul 11, 2026 8:24pm | Jul 11, 2026 8:26pm | Jul 11, 2026 8:26pm | BrokenWire |  | Fair | No | Found secondary phase conducter broken splice and retention 2span of nuert
Outage | J.E.26.07.12466 | C001852512 | Hartley Chin | Clarendon | Completed | Load_405841 | Parnassus - 310 | Jul 11, 2026 4:20pm | Jul 11, 2026 4:21pm | Jul 11, 2026 4:40pm | Jul 11, 2026 5:06pm | Jul 11, 2026 6:14pm | Jul 11, 2026 6:28pm | Jul 11, 2026 6:31pm | Jul 11, 2026 6:31pm |  |  | SevereWind | No | Found corrosion on 1 phase clamp @ service pole , Change 2 phase clamp …
Outage | J.E.26.07.12626 | C001852509 | Hartley Chin | St.Catherine | Completed | Load_247304 | Rhodens Pen - 310 | Jul 11, 2026 4:20pm | Jul 11, 2026 4:21pm | Jul 11, 2026 7:51pm | Jul 11, 2026 7:51pm | Jul 11, 2026 8:59pm | Jul 11, 2026 9:40pm | Jul 11, 2026 9:41pm | Jul 11, 2026 9:41pm |  |  | Fair | No | Repair broken service phase found @ service pole …
Outage | J.E.26.07.12655 | C001852510 | Hartley Chin | St.Catherine | Completed | Load_1000356 | Rhodens Pen - 310 | Jul 11, 2026 4:20pm | Jul 11, 2026 4:21pm | Jul 11, 2026 5:00pm | Jul 11, 2026 5:01pm | Jul 11, 2026 5:01pm | Jul 11, 2026 5:01pm | Jul 11, 2026 5:01pm | Jul 11, 2026 5:01pm |  |  | SevereWind | No | Wrong parish … St . Catherine..
Non-Outage | J.E.26.07.12638 | C001852508 | Clyde Brown | null | Completed | null | null | Jul 11, 2026 4:18pm | Jul 11, 2026 4:19pm | Jul 11, 2026 4:34pm | Jul 11, 2026 4:34pm | Jul 11, 2026 5:21pm | Jul 11, 2026 6:03pm | Jul 11, 2026 6:17pm | Jul 11, 2026 6:17pm | BrokenWire |  | SevereWind | No | Broken secondary neutral,open 25 kva transformer and repaired with 6ft-#2 conductor,2- splicing sleeve and 1-clamp and 1- preform.
Outage | J.E.26.07.12658 | C001852507 | Clyde Brown | Clarendon | Completed | Load_238377 | Monymusk - 410 | Jul 11, 2026 4:18pm | Jul 11, 2026 4:19pm | Jul 11, 2026 6:58pm | Jul 11, 2026 6:58pm | Jul 11, 2026 6:58pm | Jul 11, 2026 6:56pm | Jul 11, 2026 7:04pm | Jul 11, 2026 7:04pm | BrokenWire |  | Fair | No | Corroded phase at secondary line connection remade with 1- clamp,voltage left 112V
Outage | J.E.26.07.12477 | C001852505 | Delano Gayle | St.Catherine | Completed | Load_243468 | New Michelton - 410 | Jul 11, 2026 4:15pm | Jul 11, 2026 4:16pm | Jul 11, 2026 4:41pm | Jul 11, 2026 4:41pm | Jul 11, 2026 7:01pm | Jul 11, 2026 7:21pm | Jul 11, 2026 7:22pm | Jul 11, 2026 7:22pm | BrokenWire |  | Fair | No | Premises found okay power restored voltage readings 113-112-226
Outage | J.E.26.07.12742 | C001852504 | Hartley Chin | Clarendon | Completed | Load_301017 | Monymusk - 210 | Jul 11, 2026 3:59pm | Jul 11, 2026 4:23pm | Jul 11, 2026 7:02pm | Jul 11, 2026 7:03pm | Jul 11, 2026 7:30pm | Jul 11, 2026 7:50pm | Jul 11, 2026 7:51pm | Jul 11, 2026 7:51pm | BrokenWire |  | Fair | No | Replace 70ft damage service wire … voltage read 111v …
Outage | J.E.26.07.11101 | C001852503 | Roxroy Needham | St.Ann | Completed | Load_245275 | Cardiff Hall - 310 | Jul 11, 2026 3:58pm | Jul 11, 2026 4:00pm | Jul 11, 2026 4:36pm | Jul 11, 2026 4:36pm | Jul 11, 2026 5:33pm | Jul 11, 2026 5:24pm | Jul 11, 2026 5:35pm | Jul 11, 2026 5:35pm |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.07.12758 | C001852502 | Tyrese Williams | St.Ann | Completed | Load_258385 | Cardiff Hall - 210 | Jul 11, 2026 3:58pm | Jul 11, 2026 4:02pm | Jul 11, 2026 7:44pm | Jul 11, 2026 7:44pm | Jul 11, 2026 8:01pm | Jul 11, 2026 8:02pm | Jul 11, 2026 8:02pm | Jul 11, 2026 8:02pm |  |  | Fair | No | Reset a 25kva transformer at pole
Outage | J.E.26.07.12871 | C001852499 | Roxroy Needham | St.Ann | Completed | Load_263508 | Cardiff Hall - 210 | Jul 11, 2026 3:56pm | Jul 11, 2026 3:57pm | Jul 11, 2026 5:35pm | Jul 11, 2026 5:39pm | Jul 11, 2026 6:43pm | Jul 11, 2026 6:45pm | Jul 11, 2026 6:46pm | Jul 11, 2026 6:46pm |  |  | Fair | No | Not getting customer on phone
Non-Outage | J.E.26.07.12863 | C001852498 | Marlon Authors | null | Completed | null | null | Jul 11, 2026 3:53pm | Jul 11, 2026 3:54pm | Jul 11, 2026 4:45pm | Jul 11, 2026 4:45pm | Jul 11, 2026 5:27pm | Jul 11, 2026 6:38pm | Jul 11, 2026 6:38pm | Jul 11, 2026 6:38pm | BrokenWire |  | Fair | No | Patrol and found two pole spans of secondary neutral burnt off,caused by illegal connections. Isolate and close 50 kva transformer circuit no pole # to splice and retention same using 60 feet of #2 conductor, two #2 preforms and two clamps. Restored supply ok
Non-Outage | J.E.26.07.12558 | C001852491 | Edward Royal | null | Completed | null | null | Jul 11, 2026 3:39pm | Jul 12, 2026 8:06am | Jul 12, 2026 11:03am | Jul 12, 2026 11:03am | Jul 12, 2026 11:03am | Jul 12, 2026 11:03am | Jul 12, 2026 11:04am | Jul 12, 2026 11:04am | Fire |  | Fair | No | Premises not found unable to communicate with customer
Non-Outage | J.E.26.07.12590 | C001852493 | Eric Williams | null | Completed | null | null | Jul 11, 2026 3:39pm | Jul 11, 2026 6:43pm | Jul 11, 2026 7:11pm | Jul 11, 2026 7:11pm | Jul 11, 2026 7:48pm | Jul 11, 2026 7:50pm | Jul 11, 2026 7:52pm | Jul 11, 2026 7:52pm | Fire | Y | Fair | No | Major/ urgent bushing required, refer to maintenance department
Outage | J.E.26.07.12440 | C001852494 | Eric Williams | KSAN | Completed | Load_244896 | West Kings House - 310 | Jul 11, 2026 3:39pm | Jul 11, 2026 3:39pm | Jul 11, 2026 5:11pm | Jul 11, 2026 5:11pm | Jul 11, 2026 5:23pm | Jul 11, 2026 6:03pm | Jul 11, 2026 6:04pm | Jul 11, 2026 6:04pm |  |  | Fair | No | Internal problem readings check at pole and pothead 116,115,232volts
Outage | J.E.26.07.12693 | C001852495 | Christopher Edwards | KSAN | Completed | Load_240919 | Constant Spring - 410 | Jul 11, 2026 3:39pm | Jul 12, 2026 7:31am | Jul 12, 2026 9:35am | Jul 12, 2026 9:35am | Jul 12, 2026 10:16am | Jul 12, 2026 1:08pm | Jul 12, 2026 1:08pm | Jul 12, 2026 1:08pm | BrokenWire |  | Fair | No | Isolate 25 kva transformer To splice and retention broken open secondary wiresUsing: 80ft #2 AA conductor 4 #2 preforms6- one bolt clamps Also clear bamboo off open secondary lines
Outage | J.E.26.07.11114 | C001852489 | Eric Williams | KSAS | Completed | Load_256079 | Up Park Camp - 410 | Jul 11, 2026 3:35pm | Jul 11, 2026 3:35pm | Jul 11, 2026 6:04pm | Jul 11, 2026 6:04pm | Jul 11, 2026 6:17pm | Jul 11, 2026 6:20pm | Jul 11, 2026 6:21pm | Jul 11, 2026 6:21pm | TreeContact |  | Fair | No | No problem at location, customer reports for somewhere else
Outage | J.E.26.07.12291 | C001852490 | Eric Williams | KSAN | Completed | Load_578782 | Washington Blvd - 510 | Jul 11, 2026 3:35pm | Jul 11, 2026 3:35pm | Jul 11, 2026 3:39pm | Jul 11, 2026 3:51pm | Jul 11, 2026 5:07pm | Jul 11, 2026 5:10pm | Jul 11, 2026 5:11pm | Jul 11, 2026 5:11pm |  |  | Fair | No | Calls to customer went unanswered, check with meter indicates meter on
Outage | J.E.26.07.12530 | C001852488 | Stephen Taylor | St.Thomas | Completed | Load_254306 | Lysson - 410 | Jul 11, 2026 3:33pm | Jul 11, 2026 3:34pm | Jul 12, 2026 9:17am | Jul 12, 2026 9:17am | Jul 12, 2026 9:17am | Jul 12, 2026 9:17am | Jul 12, 2026 9:18am | Jul 12, 2026 9:18am |  |  | Fair | No | Call to customer and customer said light is back now and okay
Outage | J.E.26.07.12551 | C001852487 | Hopeton Henry | St.Thomas | Completed | Load_259076 | Good Year - 210 | Jul 11, 2026 3:33pm | Jul 11, 2026 3:34pm | Jul 11, 2026 4:26pm | Jul 11, 2026 7:48pm | Jul 11, 2026 7:48pm | Jul 11, 2026 7:48pm | Jul 11, 2026 7:48pm | Jul 11, 2026 7:48pm |  |  | Fair | No | Found ok
Outage | J.E.26.07.12619 | C001852486 | Hopeton Henry | St.Thomas | Completed | Load_260408 | Good Year - 110 | Jul 11, 2026 3:33pm | Jul 11, 2026 3:34pm | Jul 11, 2026 4:26pm | Jul 11, 2026 7:48pm | Jul 11, 2026 7:49pm | Jul 11, 2026 7:49pm | Jul 11, 2026 7:49pm | Jul 11, 2026 7:49pm |  |  | Fair | No | Found ok , power restored earlier today
Outage | J.E.26.07.12599 | C001852483 | Rusean Allen | KSAS | Completed | Load_269212 | Rockfort - 410 | Jul 11, 2026 3:31pm | Jul 11, 2026 3:34pm | Jul 11, 2026 8:40pm | Jul 12, 2026 3:34pm | Jul 12, 2026 3:44pm | Jul 12, 2026 3:44pm | Jul 12, 2026 3:44pm | Jul 12, 2026 3:44pm | Fire |  | Fair | No | Customer phone went unanswered
Non-Outage | J.E.26.07.11182 | C001852482 | Tyrese Williams | St.Ann | Completed | Load_237638 | Roaring River - 410 | Jul 11, 2026 3:29pm | Jul 11, 2026 3:43pm | Jul 11, 2026 3:48pm | Jul 11, 2026 3:54pm | Jul 11, 2026 4:00pm | Jul 11, 2026 5:33pm | Jul 11, 2026 5:33pm | Jul 11, 2026 5:33pm |  |  | Fair | No | Splice and retention secondary twisted service wire voltage check 115/115/230
Outage | J.E.26.07.08854 | C001852481 | Daniel Francis | St.Ann | Completed | Load_259444 | Upper White River - 110 | Jul 11, 2026 3:27pm | Jul 11, 2026 3:44pm | Jul 11, 2026 11:40pm | Jul 11, 2026 11:40pm | Jul 12, 2026 12:15am | Jul 12, 2026 12:17am | Jul 12, 2026 12:17am | Jul 12, 2026 12:17am |  |  | Fair | No | Unable to located customer not answering phone
Outage | J.E.26.07.09845 | C001852479 | Cliton Henry | St.Mary | Completed | Load_354886 | Blackstonedge - 110 | Jul 11, 2026 3:26pm | Jul 11, 2026 3:33pm | Jul 11, 2026 9:01pm | Jul 11, 2026 9:01pm | Jul 11, 2026 9:01pm | Jul 11, 2026 9:02pm | Jul 11, 2026 9:03pm | Jul 11, 2026 9:03pm |  |  | Fair | No | Supply found ok
Outage | J.E.26.07.10670 | C001852478 | Daniel Francis | St.Ann | Completed | Load_265764 | Upper White River - 110 | Jul 11, 2026 3:26pm | Jul 11, 2026 3:47pm | Jul 11, 2026 9:07pm | Jul 11, 2026 9:07pm | Jul 11, 2026 9:15pm | Jul 11, 2026 9:15pm | Jul 11, 2026 9:17pm | Jul 11, 2026 9:17pm |  |  | Fair | No | Not found customer not answering phone
Outage | J.E.26.07.12722 | C001852477 | Raymond Carr | St.Mary | Completed | Load_261992 | Blackstonedge - 110 | Jul 11, 2026 3:26pm | Jul 12, 2026 7:19am | Jul 12, 2026 10:39am | Jul 12, 2026 10:39am | Jul 12, 2026 10:58am | Jul 12, 2026 11:30am | Jul 12, 2026 11:39am | Jul 12, 2026 11:39am |  |  | Fair | No | Blown junction fuse found at pole number 0014181, line patrol and found okay, however, unable to ascertain cause of frequent outages. A 20 amp fuse was used to renew supply was restored. Kindly refer to maintenance department for a detailed patrol.
Outage | J.E.26.07.12846 | C001852475 | Michael Christian | St.James | Completed | Load_253637 | Queens Drive - 310 | Jul 11, 2026 3:22pm | Jul 11, 2026 3:22pm | Jul 11, 2026 5:08pm | Jul 11, 2026 5:08pm | Jul 11, 2026 5:08pm | Jul 11, 2026 5:09pm | Jul 11, 2026 5:09pm | Jul 11, 2026 5:09pm |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.12849 | C001852476 | Michael Christian | St.James | Completed | Load_293361 | Queens Drive - 310 | Jul 11, 2026 3:22pm | Jul 11, 2026 3:22pm | Jul 11, 2026 3:30pm | Jul 11, 2026 3:30pm | Jul 11, 2026 4:28pm | Jul 11, 2026 4:39pm | Jul 11, 2026 4:40pm | Jul 11, 2026 4:40pm |  |  | Fair | No | Found 1 30 amp out replace 1 30 amp no pole #
Outage | J.E.26.07.12405 | C001852473 | Floyd Grant | St.Mary | Completed | Load_257079 | Blackstonedge - 110 | Jul 11, 2026 2:56pm | Jul 11, 2026 2:57pm | Jul 11, 2026 3:27pm | Jul 11, 2026 3:27pm | Jul 11, 2026 3:27pm | Jul 11, 2026 3:57am | Jul 11, 2026 3:57pm | Jul 11, 2026 3:57pm |  |  | Fair | No | Open 25kva TRF. Splice an retention 2/0 conductor use one #2/0 splicing sleeve and one bolt clamp
Outage | J.E.26.07.12790 | C001852470 | Floyd Taylor | Trelawny | Completed | Load_574629 | Greenwood - 110 | Jul 11, 2026 2:42pm | Jul 11, 2026 2:46pm | Jul 11, 2026 3:33pm | Jul 11, 2026 3:33pm | Jul 11, 2026 4:42pm | Jul 11, 2026 5:48pm | Jul 11, 2026 5:52pm | Jul 11, 2026 5:52pm |  |  | Fair | No | Replaced one 20Amp junction fuse after line was patrolled and nothing was found
Outage | J.E.26.07.12796 | C001852469 | Daniel Francis | St.Ann | Completed | Load_255547 | Roaring River - 210 | Jul 11, 2026 2:38pm | Jul 11, 2026 4:25pm | Jul 11, 2026 8:39pm | Jul 11, 2026 11:31pm | Jul 11, 2026 11:34pm | Jul 11, 2026 11:37pm | Jul 11, 2026 11:37pm | Jul 11, 2026 11:37pm |  |  | Fair | No | Found okay 117 117 234 in all
Outage | J.E.26.07.12759 | C001852465 | Richard Samuda | Manchester | Completed | Load_1002553 | Kendal - 310 | Jul 11, 2026 2:16pm | Jul 11, 2026 2:16pm | Jul 11, 2026 2:24pm | Jul 11, 2026 2:24pm | Jul 11, 2026 2:41pm | Jul 11, 2026 3:23am | Jul 11, 2026 3:23pm | Jul 11, 2026 3:23pm | Fire |  | SevereWind | No | Remake joint at customer pothead that was burnt out causing customer to experience single phase voltage: 115,115 230
Outage | J.E.26.07.12670 | C001852460 | Wan Carlos Scarlett | Portmore | Completed | Load_1003655 | Naggo Head - 610 | Jul 11, 2026 1:36pm | Jul 11, 2026 1:36pm | Jul 11, 2026 2:49pm | Jul 11, 2026 2:49pm | Jul 11, 2026 2:51pm | Jul 11, 2026 4:58pm | Jul 11, 2026 4:59pm | Jul 11, 2026 4:59pm |  |  | Fair | No | Refuse 50amp junction no pole # was found clear bird from off transformer bushing
Outage | J.E.26.07.12044 | C001852459 | Wan Carlos Scarlett | Portmore | Completed | Load_261040 | Naggo Head - 610 | Jul 11, 2026 1:35pm | Jul 11, 2026 1:36pm | Jul 11, 2026 4:59pm | Jul 11, 2026 5:00pm | Jul 11, 2026 6:13pm | Jul 11, 2026 7:34pm | Jul 11, 2026 7:36pm | Jul 11, 2026 7:36pm |  |  | Fair | No | Found customer with internal problem advised customer to get a licensed electrician to fix the problem pothead wire to meter socket defective isolate 2 wire service at pothead
Outage | J.E.26.07.12647 | C001852458 | Rusean Allen | KSAS | Completed | Load_254739 | Cane River - 610 | Jul 11, 2026 1:34pm | Jul 11, 2026 1:36pm | Jul 11, 2026 2:53pm | Jul 11, 2026 2:53pm | Jul 11, 2026 3:50pm | Jul 11, 2026 4:04pm | Jul 11, 2026 4:05pm | Jul 11, 2026 4:05pm |  |  | Fair | No | 1x 40amp fuse found 1x 40amp fuse replaced.1x 3amp fuse found 1x 3amp fuse replaced.
Outage | J.E.26.07.12375 | C001852457 | Richard Nicholas | St.Catherine | Completed | Load_1001432 | Tredegar - 210 | Jul 11, 2026 1:33pm | Jul 11, 2026 1:33pm | Jul 11, 2026 2:35pm | Jul 11, 2026 2:35pm | Jul 11, 2026 2:48pm | Jul 11, 2026 4:49pm | Jul 11, 2026 4:50pm | Jul 11, 2026 4:50pm |  |  | Fair | No | Replaced blown 30amp x2 junctions fuse on pole #040609.
Non-Outage | J.E.26.07.12651 | C001852455 | Romeo Brissett | null | Completed | null | null | Jul 11, 2026 1:22pm | Jul 11, 2026 1:26pm | Jul 11, 2026 5:06pm | Jul 11, 2026 5:06pm | Jul 11, 2026 5:56pm | Jul 11, 2026 7:01pm | Jul 11, 2026 7:10pm | Jul 11, 2026 7:10pm |  |  | Fair | No | Found customer service wire single phasing, one leg coming from the box V/R 114-25. Please send to field service.
Outage | J.E.26.07.11271 | C001852449 | Nickolas Rodriques | Portmore | Completed | Load_240613 | Naggo Head - 610 | Jul 11, 2026 1:02pm | Jul 12, 2026 8:38am | Jul 12, 2026 2:12pm | Jul 12, 2026 2:31pm | Jul 12, 2026 2:51pm | Jul 12, 2026 3:12pm | Jul 12, 2026 3:13pm | Jul 12, 2026 3:13pm |  |  | Fair | No | Unable to locate or communicate with the customer after several attempts. Cell number does not work.
Outage | J.E.26.07.12244 | C001852450 | Wan Carlos Scarlett | St.Catherine | Completed | Load_252984 | Twickenham - 210 | Jul 11, 2026 1:02pm | Jul 11, 2026 1:02pm | Jul 12, 2026 12:41pm | Jul 12, 2026 12:42pm | Jul 12, 2026 12:53pm | Jul 12, 2026 1:19pm | Jul 12, 2026 1:20pm | Jul 12, 2026 1:20pm |  |  | Fair | No | Reach at location been calling customer but no answer premises closed
Outage | J.E.26.07.12641 | C001852451 | Andre Smith | KSAN | Completed | Load_247843 | Constant Spring - 210 | Jul 11, 2026 1:02pm | Jul 11, 2026 1:06pm | Jul 11, 2026 1:10pm | Jul 11, 2026 1:10pm | Jul 11, 2026 2:21pm | Jul 11, 2026 2:56pm | Jul 11, 2026 2:56pm | Jul 11, 2026 2:56pm |  |  | Fair | No | Install one post type insulator and tension primary conductor replace blown junction fuse 10A supply restored
Outage | J.E.26.07.12629 | C001852447 | Wan Carlos Scarlett | Portmore | Completed | Load_266299 | Naggo Head - 510 | Jul 11, 2026 1:01pm | Jul 11, 2026 1:05pm | Jul 11, 2026 5:17pm | Jul 11, 2026 7:36pm | Jul 11, 2026 7:36pm | Jul 11, 2026 7:37pm | Jul 11, 2026 7:41pm | Jul 11, 2026 7:41pm |  |  | Fair | No | Refuse 20amp junction pole # 006610 suspect bird take out power supply
Outage | J.E.26.07.12631 | C001852446 | Roxroy Needham | St.Ann | Completed | Load_239011 | Cardiff Hall - 210 | Jul 11, 2026 1:00pm | Jul 11, 2026 1:01pm | Jul 11, 2026 2:22pm | Jul 11, 2026 2:22pm | Jul 11, 2026 2:22pm | Jul 11, 2026 2:24pm | Jul 11, 2026 2:25pm | Jul 11, 2026 2:25pm |  |  | Fair | No | Call customer and customer say it was an internal problem
Outage | J.E.26.07.12636 | C001852444 | Collin Robinson | Portland | Completed | Load_257633 | Port Antonio - 310 | Jul 11, 2026 12:57pm | Jul 11, 2026 12:58pm | Jul 11, 2026 5:33pm | Jul 11, 2026 5:33pm | Jul 11, 2026 7:58pm | Jul 11, 2026 7:33pm | Jul 11, 2026 8:07pm | Jul 11, 2026 8:07pm |  |  | Fair | No | Defective 25 KVA transformer found at location leaking oil Refer to maintenance
Outage | J.E.26.07.12615 | C001852440 | Andre Williams | Trelawny | Completed | Load_294514 | Duncans - 110 | Jul 11, 2026 12:47pm | Jul 11, 2026 12:53pm | Jul 11, 2026 1:45pm | Jul 11, 2026 1:57pm | Jul 11, 2026 2:24pm | Jul 11, 2026 2:26pm | Jul 11, 2026 2:38pm | Jul 11, 2026 2:38pm | BrokenWire |  | Fair | No | Remake burnt off joint on #6 wire at Jps pole use one 1 bolt clamp voltage 116+114=230
Outage | J.E.26.07.12622 | C001852439 | Kenroy Dale | Manchester | Completed | Load_262141 | Kendal - 210 | Jul 11, 2026 12:37pm | Jul 11, 2026 12:43pm | Jul 11, 2026 12:54pm | Jul 11, 2026 12:54pm | Jul 11, 2026 2:54pm | Jul 11, 2026 4:29pm | Jul 11, 2026 4:30pm | Jul 11, 2026 4:30pm |  |  | Fair | No | Blown 3 amp transformer fuse found. Line patrol one span of secondary neutral found slack, conductor was retention and blown fuse replaced. Area now with supply
Outage | J.E.26.07.12580 | C001852437 | Kenroy Dale | Manchester | Completed | Load_253217 | Kendal - 210 | Jul 11, 2026 12:35pm | Jul 11, 2026 12:35pm | Jul 11, 2026 4:30pm | Jul 11, 2026 4:30pm | Jul 11, 2026 6:39pm | Jul 11, 2026 6:44pm | Jul 11, 2026 6:47pm | Jul 11, 2026 6:47pm | BrokenWire |  | Fair | No | Approximately 500-600 feet of #6 triplex needed to give back customers full supply, we found approximately 500-600 feet of 2/0 twisted down in the ground with an old car on it. It’s been like this for several months according to surrounding citizens, 2 customers are left single phasing until the #6 triplex is procured. Mr.Crew was advised
Outage | J.E.26.07.12555 | C001852436 | Barnett Brown | Manchester | Completed | Load_266697 | Kendal - 310 | Jul 11, 2026 12:34pm | Jul 11, 2026 12:35pm | Jul 11, 2026 12:55pm | Jul 11, 2026 2:20pm | Jul 11, 2026 3:58pm | Jul 11, 2026 3:58pm | Jul 11, 2026 4:39pm | Jul 11, 2026 4:39pm |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.07.12602 | C001852435 | Hartley Chin | null | Completed | null | null | Jul 11, 2026 12:30pm | Jul 11, 2026 12:30pm | Jul 11, 2026 2:08pm | Jul 11, 2026 2:08pm | Jul 11, 2026 2:08pm | Jul 11, 2026 2:08pm | Jul 11, 2026 2:09pm | Jul 11, 2026 2:09pm |  |  | SevereWind | No | Found okay… call related to job # 11808 …
Non-Outage | J.E.26.07.11456 | C001852434 | Derrick Dawkins | St.James | Completed | Load_302398 | Bogue - 610 | Jul 11, 2026 12:22pm | Jul 11, 2026 12:22pm | Jul 11, 2026 3:17pm | Jul 11, 2026 3:17pm | Jul 11, 2026 3:30pm | Jul 11, 2026 5:45pm | Jul 11, 2026 5:45pm | Jul 11, 2026 5:45pm |  |  | Fair | No | Voltage found 240/254/221. 408/421/423 Found transformer drop lead corroded clean and remade joint used 1 2/0-2/0 amp pack voltage left 249/240/243. 419/424/420
Non-Outage | J.E.26.07.09817 | C001852431 | Tyrese Williams | St.Ann | Completed | Load_270119 | Ocho Rios - 510 | Jul 11, 2026 12:08pm | Jul 11, 2026 12:10pm | Jul 11, 2026 2:24pm | Jul 11, 2026 2:24pm | Jul 11, 2026 2:36pm | Jul 11, 2026 3:06pm | Jul 11, 2026 3:10pm | Jul 11, 2026 3:10pm |  |  | Fair | No | Remade service wire joint at pole use 1 pg clamp voltage Left 120/120/240
Outage | J.E.26.07.12510 | C001852429 | Raymond Lewis | St.Ann | Completed | Load_263912 | Roaring River - 210 | Jul 11, 2026 11:56am | Jul 11, 2026 11:57am | Jul 11, 2026 12:57pm | Jul 11, 2026 12:57pm | Jul 11, 2026 12:57pm | Jul 11, 2026 12:58pm | Jul 11, 2026 12:58pm | Jul 11, 2026 12:58pm | LowHangingWires |  | Fair | No | Phone not answering
Outage | J.E.26.07.12518 | C001852430 | Raymond Lewis | St.Ann | Completed | Load_252442 | Roaring River - 210 | Jul 11, 2026 11:56am | Jul 11, 2026 11:57am | Jul 11, 2026 12:08pm | Jul 11, 2026 12:08pm | Jul 11, 2026 12:50pm | Jul 11, 2026 12:52pm | Jul 11, 2026 12:52pm | Jul 11, 2026 12:52pm |  |  | Fair | No | Supply found in area
Non-Outage | J.E.26.07.09704 | C001852428 | Wan Carlos Scarlett | Portmore | Completed | Load_266484 | Naggo Head - 610 | Jul 11, 2026 11:55am | Jul 11, 2026 11:56am | Jul 12, 2026 5:03pm | Jul 12, 2026 5:03pm | Jul 12, 2026 6:22pm | Jul 12, 2026 6:52pm | Jul 12, 2026 6:53pm | Jul 12, 2026 6:53pm |  |  | Fair | No | Found one span of open secondary line phase jumper burn out use 2 one bolt clamps at pole readings 117-118-234
Outage | J.E.26.07.12430 | C001852423 | Clyde Brown | Clarendon | Completed | Load_568663 | May Pen - 210 | Jul 11, 2026 11:47am | Jul 11, 2026 11:50am | Jul 11, 2026 12:58pm | Jul 11, 2026 12:58pm | Jul 11, 2026 12:58pm | Jul 11, 2026 12:53pm | Jul 11, 2026 1:00pm | Jul 11, 2026 1:00pm |  |  | SevereWind | No | Found ok,customer supply was repaired from this morning
Outage | J.E.26.07.12286 | C001852421 | Tyrese Williams | St.Ann | Completed | Load_265738 | Ocho Rios - 310 | Jul 11, 2026 11:39am | Jul 11, 2026 11:40am | Jul 11, 2026 11:43am | Jul 11, 2026 1:57pm | Jul 11, 2026 2:13pm | Jul 11, 2026 2:14pm | Jul 11, 2026 2:15pm | Jul 11, 2026 2:15pm |  |  | Fair | No | Replace a 25kva transformer fuse with a 2amp at pole
Outage | J.E.26.07.12458 | C001852420 | Roxroy Needham | St.Ann | Completed | Load_246466 | Cardiff Hall - 210 | Jul 11, 2026 11:35am | Jul 11, 2026 11:40am | Jul 11, 2026 11:52am | Jul 11, 2026 12:36pm | Jul 11, 2026 1:13pm | Jul 11, 2026 1:18pm | Jul 11, 2026 1:22pm | Jul 11, 2026 1:22pm |  |  | Fair | No | Splice and retention two spans of secondary phase use about 5 ft of No.2 conductor, 1 pg clamp and 1 preformed
Non-Outage | J.E.26.07.10211 | C001852419 | Michael Christian | null | Completed | null | null | Jul 11, 2026 11:33am | Jul 11, 2026 11:42am | Jul 11, 2026 4:28pm | Jul 11, 2026 5:09pm | Jul 11, 2026 5:38pm | Jul 11, 2026 5:40pm | Jul 11, 2026 5:41pm | Jul 11, 2026 5:41pm |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.12363 | C001852417 | Hopeton Henry | St.Thomas | Completed | Load_575858 | Good Year - 110 | Jul 11, 2026 11:32am | Jul 11, 2026 11:35am | Jul 11, 2026 3:27pm | Jul 11, 2026 3:27pm | Jul 11, 2026 3:27pm | Jul 11, 2026 3:27pm | Jul 11, 2026 3:29pm | Jul 11, 2026 3:29pm |  |  | Fair | No | Refuse 7 amp fuse , issue unresolved, customer having frequent outages Refer to maintenance for bushing
Outage | J.E.26.07.12525 | C001852418 | Stephen Taylor | St.Thomas | Completed | Load_343333 | Lysson - 410 | Jul 11, 2026 11:32am | Jul 11, 2026 11:35am | Jul 12, 2026 8:10am | Jul 12, 2026 8:10am | Jul 12, 2026 9:08am | Jul 12, 2026 9:08am | Jul 12, 2026 9:09am | Jul 12, 2026 9:09am |  |  | Fair | No | Check with customer and customer said power is back now and okay
Outage | J.E.26.07.12374 | C001852416 | Edward Royal | KSAN | Completed | Load_268837 | West Kings House - 310 | Jul 11, 2026 11:27am | Jul 11, 2026 11:28am | Jul 11, 2026 11:45am | Jul 11, 2026 11:45am | Jul 11, 2026 11:45am | Jul 11, 2026 12:26pm | Jul 11, 2026 12:26pm | Jul 11, 2026 12:26pm |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.07.12516 | C001852415 | Barnett Brown | Manchester | Completed | Load_255369 | Kendal - 310 | Jul 11, 2026 11:27am | Jul 11, 2026 11:28am | Jul 11, 2026 11:34am | Jul 11, 2026 12:51pm | Jul 11, 2026 12:51pm | Jul 11, 2026 12:54pm | Jul 11, 2026 12:55pm | Jul 11, 2026 12:55pm |  |  | Fair | No | Call already dealt with
Outage | J.E.26.07.12479 | C001852411 | Ricky Hall | St.Catherine | Completed | Load_251630 | Rhodens Pen - 410 | Jul 11, 2026 11:14am | Jul 11, 2026 11:15am | Jul 11, 2026 1:14pm | Jul 11, 2026 1:14pm | Jul 11, 2026 2:16pm | Jul 11, 2026 2:29pm | Jul 11, 2026 2:30pm | Jul 11, 2026 2:30pm |  |  | Fair | No | Area found with supply ( issue was resolved previously)
Outage | J.E.26.07.12489 | C001852408 | Raymond Carr | St.Mary | Completed | Load_265293 | Blackstonedge - 110 | Jul 11, 2026 11:06am | Jul 12, 2026 7:19am | Jul 12, 2026 11:40am | Jul 12, 2026 11:40am | Jul 12, 2026 2:36pm | Jul 12, 2026 2:33pm | Jul 12, 2026 2:45pm | Jul 12, 2026 2:45pm | BrokenWire |  | Fair | No | Spliced and retention Four spans of broken secondary conductors, caused by a almond tree fallen on same. Five clamps , 50 ft#2 aa, 2#2 preforms 2. 2/0 preforms. Supply was restored.
Outage | J.E.26.07.12455 | C001852407 | Christopher Edwards | KSAN | Completed | Load_265361 | Constant Spring - 410 | Jul 11, 2026 11:03am | Jul 11, 2026 11:06am | Jul 11, 2026 12:26pm | Jul 11, 2026 12:26pm | Jul 11, 2026 1:11pm | Jul 11, 2026 1:58pm | Jul 11, 2026 2:03pm | Jul 11, 2026 2:03pm |  |  | Fair | No | Remake burnt neutral joint Using (1) one bolt clamps Voltage:113,114,230vHowever customer was advised to get electrician to check service line from meter pole to house has JPS side was fixed
Outage | J.E.26.07.12371 | C001852406 | Christopher Edwards | KSAN | Completed | Load_244992 | Constant Spring - 410 | Jul 11, 2026 10:59am | Jul 11, 2026 11:06am | Jul 11, 2026 2:03pm | Jul 11, 2026 2:03pm | Jul 11, 2026 2:17pm | Jul 11, 2026 2:51pm | Jul 11, 2026 2:53pm | Jul 11, 2026 2:53pm | Fire | Y | Fair | No | Clear bamboo off open secondary wiresThat was causing wires to bang Reset 50 kva transformer
Outage | J.E.26.07.12469 | C001852405 | Roxroy Needham | St.Ann | Completed | Load_258093 | Roaring River - 410 | Jul 11, 2026 10:58am | Jul 11, 2026 11:42am | Jul 11, 2026 2:09pm | Jul 11, 2026 2:09pm | Jul 11, 2026 2:09pm | Jul 11, 2026 2:10pm | Jul 11, 2026 2:10pm | Jul 11, 2026 2:10pm | Fire |  | Fair | No | Call customer and customer say light restored from last night
Outage | J.E.26.07.12472 | C001852404 | Clyde Brown | Clarendon | Completed | Load_405349 | Parnassus - 210 | Jul 11, 2026 10:54am | Jul 11, 2026 10:54am | Jul 11, 2026 1:01pm | Jul 11, 2026 1:01pm | Jul 11, 2026 1:01pm | Jul 11, 2026 1:02pm | Jul 11, 2026 1:04pm | Jul 11, 2026 1:04pm |  |  | SevereWind | No | Found ok,area was restored since this morning
Outage | J.E.26.07.12470 | C001852403 | Lancelot Brown | Hanover | Completed | Load_1001393 | Orange Bay - 310 | Jul 11, 2026 10:48am | Jul 11, 2026 10:49am | Jul 11, 2026 11:48am | Jul 11, 2026 11:48am | Jul 11, 2026 1:02pm | Jul 11, 2026 1:06pm | Jul 11, 2026 1:06pm | Jul 11, 2026 1:06pm |  |  | Fair | No | Check and found ok customer turn off breaker transformer was diffective customer did not know transformer had change supply restore
Outage | J.E.26.07.12443 | C001852401 | Marlon Authors | Manchester | Completed | Load_251724 | Spur Tree - 210 | Jul 11, 2026 10:46am | Jul 11, 2026 10:51am | Jul 11, 2026 12:17pm | Jul 11, 2026 3:07pm | Jul 11, 2026 4:16pm | Jul 11, 2026 4:40pm | Jul 11, 2026 4:40pm | Jul 11, 2026 4:40pm | Fire |  | SevereWind | No | Patrol and found one pole span of secondary conductors banging together whenever the wind blows. Isolate and close 25 kva transformer circuit no pole # to retention same. Supply leave working okay
Outage | J.E.26.07.12451 | C001852402 | Marlon Authors | Manchester | Completed | Load_556606 | Spur Tree - 210 | Jul 11, 2026 10:46am | Jul 11, 2026 10:51am | Jul 11, 2026 12:17pm | Jul 11, 2026 1:47pm | Jul 11, 2026 1:47pm | Jul 11, 2026 1:49pm | Jul 11, 2026 1:49pm | Jul 11, 2026 1:49pm |  |  | SevereWind | No | Supply restored to the area
Outage | J.E.26.07.11248 | C001852399 | Derrick Dawkins | St.James | Completed | Load_238758 | Bogue - 610 | Jul 11, 2026 10:44am | Jul 11, 2026 11:08am | Jul 11, 2026 12:32pm | Jul 11, 2026 12:32pm | Jul 11, 2026 12:32pm | Jul 11, 2026 1:27pm | Jul 11, 2026 1:28pm | Jul 11, 2026 1:28pm |  |  | Fair | No | Reconnected customer service service wire missing due to hurricane used 38 feet #2 duplex 2 linket voltage left 119
Outage | J.E.26.07.08394 | C001852398 | Michael Christian | St.James | Completed | Load_267491 | Queens Drive - 710 | Jul 11, 2026 10:42am | Jul 11, 2026 10:43am | Jul 11, 2026 1:45pm | Jul 11, 2026 1:45pm | Jul 11, 2026 3:16pm | Jul 11, 2026 3:27pm | Jul 11, 2026 3:27pm | Jul 11, 2026 3:27pm |  |  | Fair | No | Found 1 25 kava out replace 1 2 amp in 1 25 kava no pole #
Outage | J.E.26.07.12429 | C001852395 | Romeo Brissett | St.James | Completed | Load_264886 | Bogue - 310 | Jul 11, 2026 10:40am | Jul 11, 2026 10:43am | Jul 11, 2026 12:30pm | Jul 11, 2026 12:30pm | Jul 11, 2026 12:53pm | Jul 11, 2026 3:10pm | Jul 11, 2026 3:20pm | Jul 11, 2026 3:20pm |  |  | Fair | No | Isolated (2)20amps junction for safety clearance, spliced and retention 1 span span of single phase Primary, Then replaced (1)20amps,junction.
Outage | J.E.26.07.12452 | C001852396 | Derrick Dawkins | St.James | Completed | Load_247569 | Bogue - 610 | Jul 11, 2026 10:40am | Jul 11, 2026 10:42am | Jul 11, 2026 11:43am | Jul 11, 2026 1:28pm | Jul 11, 2026 1:50pm | Jul 11, 2026 2:44pm | Jul 11, 2026 2:45pm | Jul 11, 2026 2:45pm | BrokenWire |  | Fair | No | Found one span secondary neutral burn off due to vehicle accident, 25 kva transformer fuse blown 3 amp splice and retention replace transformer fuse 3 amp used one #2 splicing sleeve and 2 pg clamp
Outage | J.E.26.07.12257 | C001852394 | Elvis Trowers | KSAN | Completed | Load_238164 | Hope - 510 | Jul 11, 2026 10:30am | Jul 11, 2026 10:31am | Jul 11, 2026 2:52pm | Jul 11, 2026 2:52pm | Jul 11, 2026 3:12pm | Jul 11, 2026 3:29pm | Jul 11, 2026 3:30pm | Jul 11, 2026 3:30pm |  |  | SevereWind | Yes | Areas was found without electricity supply when checked and a blown 15 amp junction fuse was found and replaced after patrol was completed at pole #0175000.
Outage | J.E.26.07.12419 | C001852393 | Elvis Trowers | KSAN | Completed | Load_247067 | Hope - 510 | Jul 11, 2026 10:30am | Jul 11, 2026 10:31am | Jul 11, 2026 10:47am | Jul 11, 2026 10:47am | Jul 11, 2026 12:39pm | Jul 11, 2026 2:51pm | Jul 11, 2026 2:51pm | Jul 11, 2026 2:51pm | BrokenWire | Y | Fair | Yes | Broken secondary wires was found and a 25 kva transformer was isolated at pole #0214395 to repair broken wires, about 60’ feet of #2 AA wire, 2 preforms and 4 one bolt clamps along with temporary bushings to complete repairs then reclose the transformer at the above pole number.
Outage | J.E.26.07.12377 | C001852385 | Andrew Powell | Manchester | Completed | Load_237860 | Spur Tree - 210 | Jul 11, 2026 10:14am | Jul 12, 2026 7:45am | Jul 12, 2026 8:08am | Jul 12, 2026 8:08am | Jul 12, 2026 8:08am | Jul 12, 2026 8:08am | Jul 12, 2026 8:08am | Jul 12, 2026 8:08am |  |  | Fair | No | Manchester called.
Outage | J.E.26.07.12412 | C001852386 | Marlon Authors | Manchester | Completed | Load_248909 | Spur Tree - 210 | Jul 11, 2026 10:14am | Jul 11, 2026 10:14am | Jul 11, 2026 12:17pm | Jul 11, 2026 1:59pm | Jul 11, 2026 2:39pm | Jul 11, 2026 2:49pm | Jul 11, 2026 2:49pm | Jul 11, 2026 2:49pm |  |  | SevereWind | No | Patrol and found clear. Reset trip type transformer at pole #085150. Restored supply ok
Outage | J.E.26.07.12366 | C001852384 | Marlon Authors | Manchester | Completed | Load_1002209 | Spur Tree - 210 | Jul 11, 2026 10:13am | Jul 11, 2026 10:14am | Jul 11, 2026 12:17pm | Jul 11, 2026 1:51pm | Jul 11, 2026 1:51pm | Jul 11, 2026 1:52pm | Jul 11, 2026 1:53pm | Jul 11, 2026 1:53pm |  |  | SevereWind | No
Outage | J.E.26.07.12415 | C001852383 | Tyrese Williams | St.Ann | Completed | Load_245204 | Ocho Rios - 410 | Jul 11, 2026 10:10am | Jul 11, 2026 10:20am | Jul 11, 2026 11:43am | Jul 11, 2026 12:15pm | Jul 11, 2026 12:15pm | Jul 11, 2026 12:15pm | Jul 11, 2026 12:16pm | Jul 11, 2026 12:16pm |  |  | Fair | No | Refer to field service technician
Outage | J.E.26.07.12414 | C001852382 | Collin Robinson | Portland | Completed | Load_268490 | Port Antonio - 410 | Jul 11, 2026 10:08am | Jul 11, 2026 11:15am | Jul 11, 2026 12:15pm | Jul 11, 2026 12:15pm | Jul 11, 2026 12:22pm | Jul 11, 2026 12:25pm | Jul 11, 2026 12:25pm | Jul 11, 2026 12:25pm |  |  | Fair | No | Information received from customer that issue was resolved
Outage | J.E.26.07.12304 | C001852381 | Andre Smith | KSAN | Completed | Load_253996 | Washington Blvd - 710 | Jul 11, 2026 10:04am | Jul 11, 2026 10:34am | Jul 11, 2026 10:49am | Jul 11, 2026 10:49am | Jul 11, 2026 11:11am | Jul 11, 2026 11:12am | Jul 11, 2026 11:12am | Jul 11, 2026 11:12am |  |  | Fair | No | Defective 15kva transformer found maintenance department required
Outage | J.E.26.07.12378 | C001852380 | Lancelot Brown | Hanover | Completed | Load_249767 | Orange Bay - 310 | Jul 11, 2026 10:03am | Jul 11, 2026 11:59am | Jul 11, 2026 1:07pm | Jul 11, 2026 3:24pm | Jul 11, 2026 3:24pm | Jul 11, 2026 3:27pm | Jul 11, 2026 3:27pm | Jul 11, 2026 3:27pm |  |  | Fair | No | This call related to isolation carry out on bank of 2-100 and 1-50kva to repair one span of broken secondary neutral supply restore
Outage | J.E.26.07.12350 | C001852379 | Richard Samuda | Manchester | Completed | Load_292172 | Spur Tree - 310 | Jul 11, 2026 9:57am | Jul 11, 2026 9:58am | Jul 11, 2026 10:09am | Jul 11, 2026 10:09am | Jul 11, 2026 10:09am | Jul 11, 2026 10:10am | Jul 11, 2026 10:10am | Jul 11, 2026 10:10am |  |  | Fair | No | Found 25kva transformer blown patrol line found nothing replaced fuse customer back to normal
Outage | J.E.26.07.12361 | C001852364 | Raymond Lewis | St.Ann | Completed | Load_240361 | Roaring River - 210 | Jul 11, 2026 9:25am | Jul 11, 2026 9:27am | Jul 11, 2026 10:21am | Jul 11, 2026 10:21am | Jul 11, 2026 12:02pm | Jul 11, 2026 12:06pm | Jul 11, 2026 12:06pm | Jul 11, 2026 12:06pm |  |  | SevereWind | No | Cut and remove trees from line, refuse and close 5A junction fuse
Outage | J.E.26.07.12346 | C001852358 | Tyrese Williams | St.Ann | Completed | Load_242978 | Cardiff Hall - 210 | Jul 11, 2026 9:10am | Jul 11, 2026 4:01pm | Jul 11, 2026 4:36pm | Jul 11, 2026 9:51pm | Jul 11, 2026 9:51pm | Jul 11, 2026 9:51pm | Jul 11, 2026 9:52pm | Jul 11, 2026 9:52pm |  |  | Fair | No | Found. Defective 25kva transformer recommend to be change at pole 031152/ 0171297
Non-Outage | J.E.26.07.12034 | C001852357 | Collin Robinson | null | Completed | null | null | Jul 11, 2026 9:08am | Jul 11, 2026 9:13am | Jul 11, 2026 11:39am | Jul 11, 2026 11:41am | Jul 11, 2026 12:14pm | Jul 11, 2026 12:15pm | Jul 11, 2026 12:15pm | Jul 11, 2026 12:15pm |  |  | Fair | No | Information received from customer that issue was resolved
Outage | J.E.26.07.12168 | C001852354 | Marlon Authors | Manchester | Completed | Load_556606 | Spur Tree - 210 | Jul 11, 2026 8:56am | Jul 11, 2026 8:57am | Jul 11, 2026 12:17pm | Jul 11, 2026 1:05pm | Jul 11, 2026 1:05pm | Jul 11, 2026 1:45pm | Jul 11, 2026 1:45pm | Jul 11, 2026 1:45pm |  |  | SevereWind | No | Patrol and found clear. Replace one blown 20 amp junction fuse no pole #. Restored supply okay
Outage | J.E.26.07.12217 | C001852355 | Marlon Authors | Manchester | Completed | Load_248909 | Spur Tree - 210 | Jul 11, 2026 8:56am | Jul 11, 2026 8:57am | Jul 11, 2026 12:17pm | Jul 11, 2026 2:52pm | Jul 11, 2026 2:52pm | Jul 11, 2026 2:53pm | Jul 11, 2026 2:53pm | Jul 11, 2026 2:53pm |  |  | SevereWind | No | Supply restored to the area
Outage | J.E.26.07.12280 | C001852356 | Marlon Authors | Manchester | Completed | Load_265698 | Spur Tree - 210 | Jul 11, 2026 8:56am | Jul 11, 2026 8:57am | Jul 11, 2026 9:33am | Jul 11, 2026 9:33am | Jul 11, 2026 9:44am | Jul 11, 2026 12:21pm | Jul 11, 2026 12:21pm | Jul 11, 2026 12:21pm |  |  | Fair | No | Supply checked and found low voltage 108v,107v and cross phased 206 volts. Isolate and close 100 kva transformers in bankers two to tap up same to tap five and repair pothead and pole using two linkets and four clamps. Supply leave working okay rdg 113v,112v and cross phased 226 volts
Outage | J.E.26.07.10597 | C001852352 | Wayne Dillion | St.Elizabeth | Completed | Load_249402 | Maggotty - 110 | Jul 11, 2026 8:53am | Jul 12, 2026 11:03am | Jul 12, 2026 11:56am | Jul 12, 2026 11:56am | Jul 12, 2026 11:56am | Jul 12, 2026 12:30pm | Jul 12, 2026 12:41pm | Jul 12, 2026 12:41pm |  |  | Fair | No | Supply check and found no service wire connect same using 60ft of #6 triplex service wire, 3 clamps and 3 linkets. Supply leave working okay reading 115v, 115v and cross phase 230volts.
Outage | J.E.26.07.12235 | C001852353 | Andrew Powell | St.Elizabeth | Completed | Load_244573 | Maggotty - 110 | Jul 11, 2026 8:53am | Jul 12, 2026 7:45am | Jul 12, 2026 10:56am | Jul 12, 2026 10:56am | Jul 12, 2026 10:56am | Jul 12, 2026 10:56am | Jul 12, 2026 10:59am | Jul 12, 2026 10:59am |  |  | SevereWind | No | Found customer out of supply since Hurricane Mellisa no service wire found at location property damaged customer complained of getting light bill, please refer to field service department for investigation.
Outage | J.E.26.07.12011 | C001852350 | Wayne Dillion | St.Elizabeth | Completed | Load_268522 | Maggotty - 110 | Jul 11, 2026 8:52am | Jul 12, 2026 11:04am | Jul 12, 2026 11:29am | Jul 12, 2026 11:29am | Jul 12, 2026 11:29am | Jul 12, 2026 11:32am | Jul 12, 2026 11:32am | Jul 12, 2026 11:32am |  |  | Fair | No | Unable to locate and customer’s not answering the phone.
Outage | J.E.26.07.11774 | C001852347 | Marlon Authors | Manchester | Completed | Load_248909 | Spur Tree - 210 | Jul 11, 2026 8:51am | Jul 11, 2026 8:52am | Jul 11, 2026 12:17pm | Jul 11, 2026 3:00pm | Jul 11, 2026 3:00pm | Jul 11, 2026 3:01pm | Jul 11, 2026 3:01pm | Jul 11, 2026 3:01pm |  |  | SevereWind | No | Supply restored to the area
Outage | J.E.26.07.11868 | C001852348 | Andrew Powell | Manchester | Completed | Load_1002350 | Spur Tree - 210 | Jul 11, 2026 8:51am | Jul 12, 2026 7:45am | Jul 12, 2026 8:06am | Jul 12, 2026 8:06am | Jul 12, 2026 8:06am | Jul 12, 2026 8:06am | Jul 12, 2026 8:07am | Jul 12, 2026 8:07am |  |  | Fair | No | Premises found okay customer stated that supply restored.
Outage | J.E.26.07.12110 | C001852349 | Marlon Authors | Manchester | Completed | Load_248909 | Spur Tree - 210 | Jul 11, 2026 8:51am | Jul 11, 2026 8:52am | Jul 11, 2026 12:17pm | Jul 11, 2026 2:55pm | Jul 11, 2026 2:55pm | Jul 11, 2026 2:57pm | Jul 11, 2026 2:57pm | Jul 11, 2026 2:57pm |  |  | SevereWind | No | Customer said supply was restored
Outage | J.E.26.07.11374 | C001852344 | Andrew Powell | St.Elizabeth | Completed | Load_246153 | Maggotty - 210 | Jul 11, 2026 8:50am | Jul 12, 2026 7:45am | Jul 12, 2026 8:03am | Jul 12, 2026 8:03am | Jul 12, 2026 8:04am | Jul 12, 2026 8:04am | Jul 12, 2026 8:05am | Jul 12, 2026 8:05am |  |  | Fair | No | Customer made report for Dunnsville in St Ann.
Outage | J.E.26.07.12232 | C001852345 | Marlon Authors | Manchester | Completed | Load_265170 | Spur Tree - 210 | Jul 11, 2026 8:50am | Jul 11, 2026 8:52am | Jul 11, 2026 12:17pm | Jul 11, 2026 8:01pm | Jul 11, 2026 8:01pm | Jul 11, 2026 8:05pm | Jul 11, 2026 8:05pm | Jul 11, 2026 8:05pm |  |  | Fair | No | Supply checked and found service wire neutral bonded with secondary lower phase conductor. Remove same and supply leave working ok, rdg 114v,115v and cross phased 229 volts
Non-Outage | J.E.26.07.12007 | C001852343 | Collin Robinson | Portland | Completed | Load_268118 | Port Antonio - 410 | Jul 11, 2026 8:49am | Jul 11, 2026 8:59am | Jul 11, 2026 12:29pm | Jul 11, 2026 12:29pm | Jul 11, 2026 1:15pm | Jul 11, 2026 1:19pm | Jul 11, 2026 1:19pm | Jul 11, 2026 1:19pm |  |  | Fair | No | Information received from customer that issue was resolved
Non-Outage | J.E.26.07.12065 | C001852341 | Collin Robinson | Portland | Completed | Load_260238 | Port Antonio - 410 | Jul 11, 2026 8:49am | Jul 11, 2026 8:59am | Jul 11, 2026 1:20pm | Jul 11, 2026 1:20pm | Jul 11, 2026 1:36pm | Jul 11, 2026 1:37pm | Jul 11, 2026 1:37pm | Jul 11, 2026 1:37pm |  |  | Fair | No | Unable to locate customer
Non-Outage | J.E.26.07.12072 | C001852342 | Collin Robinson | Portland | Completed | Load_268490 | Port Antonio - 410 | Jul 11, 2026 8:49am | Jul 11, 2026 8:59am | Jul 11, 2026 1:42pm | Jul 11, 2026 1:42pm | Jul 11, 2026 4:49pm | Jul 11, 2026 5:26pm | Jul 11, 2026 5:28pm | Jul 11, 2026 5:28pm |  |  | Fair | No | Change corroded clamp that connect transformer drop lead Voltage reading 120v 120v 240v
Non-Outage | J.E.26.07.11995 | C001852339 | Lancelot Brown | Hanover | Completed | Load_249767 | Orange Bay - 310 | Jul 11, 2026 8:48am | Jul 11, 2026 8:48am | Jul 11, 2026 10:09am | Jul 11, 2026 10:10am | Jul 11, 2026 10:10am | Jul 11, 2026 10:12am | Jul 11, 2026 10:13am | Jul 11, 2026 10:13am |  |  | Fair | No | Isolate bank of 2-100kva and 1-50kva splice and retention one span secondary neutral used sixty feet #2 conductor one #2 preform two pg clamps energise bank of 2-100and 1-50kva supply restore
Outage | J.E.26.07.11255 | C001852340 | Michael Christian | St.James | Completed | Load_256990 | Queens Drive - 710 | Jul 11, 2026 8:48am | Jul 11, 2026 8:49am | Jul 11, 2026 11:22am | Jul 11, 2026 11:22am | Jul 11, 2026 11:51am | Jul 11, 2026 12:19pm | Jul 11, 2026 12:19pm | Jul 11, 2026 12:19pm |  |  | Fair | No | Check and found okay voltage 110 111 222 at pothead
Outage | J.E.26.07.11552 | C001852336 | Rusean Allen | KSAS | Completed | Load_291495 | Greenwich - 510 | Jul 11, 2026 8:44am | Jul 11, 2026 8:44am | Jul 11, 2026 11:51am | Jul 11, 2026 12:16pm | Jul 11, 2026 1:21pm | Jul 11, 2026 1:23pm | Jul 11, 2026 1:24pm | Jul 11, 2026 1:24pm |  |  | Fair | No | Rami failure, about 3 customers are without power, refer to field service department.
Outage | J.E.26.07.11768 | C001852338 | Rusean Allen | KSAS | Completed | Load_252190 | Rockfort - 210 | Jul 11, 2026 8:44am | Jul 11, 2026 8:44am | Jul 11, 2026 4:23pm | Jul 11, 2026 6:58pm | Jul 11, 2026 6:59pm | Jul 11, 2026 6:59pm | Jul 11, 2026 6:59pm | Jul 11, 2026 6:59pm |  |  | Fair | No | Not found
Outage | J.E.26.07.11815 | C001852334 | Rusean Allen | KSAS | Completed | Load_247391 | Rockfort - 410 | Jul 11, 2026 8:44am | Jul 11, 2026 8:44am | Jul 11, 2026 11:57am | Jul 11, 2026 11:57am | Jul 11, 2026 12:13pm | Jul 11, 2026 12:16pm | Jul 11, 2026 12:16pm | Jul 11, 2026 12:16pm |  |  | Fair | No | Illegal connections needs to be removed before repairs can be done.
Outage | J.E.26.07.11880 | C001852337 | Rusean Allen | KSAS | Completed | Load_1002669 | Cane River - 410 | Jul 11, 2026 8:44am | Jul 11, 2026 8:44am | Jul 11, 2026 10:08am | Jul 11, 2026 10:08am | Jul 11, 2026 10:30am | Jul 11, 2026 10:31am | Jul 11, 2026 10:31am | Jul 11, 2026 10:31am |  |  | Fair | No
Outage | J.E.26.07.12084 | C001852335 | Rusean Allen | KSAS | Completed | Load_412792 | Hunts Bay - 810 | Jul 11, 2026 8:44am | Jul 11, 2026 8:44am | Jul 11, 2026 10:33am | Jul 11, 2026 10:33am | Jul 11, 2026 11:01am | Jul 11, 2026 11:04am | Jul 11, 2026 11:05am | Jul 11, 2026 11:05am |  |  | Fair | No | Broken service wire found at pole, wire was reconnected.
Outage | J.E.26.07.12185 | C001852332 | Stephen Taylor | St.Thomas | Completed | Load_343333 | Lysson - 410 | Jul 11, 2026 8:37am | Jul 11, 2026 8:38am | Jul 11, 2026 11:34am | Jul 11, 2026 11:34am | Jul 11, 2026 11:34am | Jul 11, 2026 11:35am | Jul 11, 2026 11:35am | Jul 11, 2026 11:35am |  |  | Fair | No | Transformer link down and click was made and found out that 25 kva transformer defective and need to change by the jps maintenance team
Outage | J.E.26.07.12282 | C001852333 | Stephen Taylor | St.Thomas | Completed | Load_268030 | Lysson - 410 | Jul 11, 2026 8:37am | Jul 11, 2026 8:38am | Jul 11, 2026 1:02pm | Jul 11, 2026 1:02pm | Jul 11, 2026 1:44pm | Jul 11, 2026 2:20pm | Jul 11, 2026 2:20pm | Jul 11, 2026 2:20pm |  |  | Fair | No | Clean up single phase line-3- clamp 3 p/ union
Outage | J.E.26.07.12175 | C001852329 | Stephen Taylor | St.Thomas | Completed | Load_252161 | Good Year - 110 | Jul 11, 2026 8:35am | Jul 11, 2026 10:08am | Jul 11, 2026 11:35am | Jul 11, 2026 11:35am | Jul 11, 2026 11:36am | Jul 11, 2026 11:36am | Jul 11, 2026 11:36am | Jul 11, 2026 11:36am |  |  | Fair | No | Transformer link down and click was made and found out that 25 kva transformer defective and need to change by the jps maintenance team
Outage | J.E.26.07.12183 | C001852331 | Hopeton Henry | St.Thomas | Completed | Load_354593 | Good Year - 210 | Jul 11, 2026 8:35am | Jul 11, 2026 8:36am | Jul 11, 2026 9:16am | Jul 11, 2026 7:50pm | Jul 11, 2026 8:23pm | Jul 11, 2026 8:23pm | Jul 11, 2026 8:24pm | Jul 11, 2026 8:24pm |  |  | Fair | No | Check and found ok
Outage | J.E.26.07.12195 | C001852328 | Hopeton Henry | St.Thomas | Completed | Load_267955 | Good Year - 110 | Jul 11, 2026 8:35am | Jul 11, 2026 8:36am | Jul 11, 2026 9:16am | Jul 11, 2026 3:30pm | Jul 11, 2026 4:26pm | Jul 11, 2026 7:47pm | Jul 11, 2026 7:47pm | Jul 11, 2026 7:47pm | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Change defective use holder at 25 kva transformer
Outage | J.E.26.07.12220 | C001852326 | Stephen Taylor | St.Thomas | Completed | Load_254161 | Good Year - 110 | Jul 11, 2026 8:35am | Jul 11, 2026 10:09am | Jul 11, 2026 11:36am | Jul 11, 2026 11:37am | Jul 11, 2026 11:37am | Jul 11, 2026 11:37am | Jul 11, 2026 11:38am | Jul 11, 2026 11:38am |  |  | Fair | No | Transformer link down and click was made and found out that 25 kva transformer defective and need to change by the jps maintenance team
Outage | J.E.26.07.12227 | C001852327 | Hopeton Henry | St.Thomas | Completed | Load_269308 | Good Year - 210 | Jul 11, 2026 8:35am | Jul 11, 2026 8:36am | Jul 11, 2026 9:16am | Jul 11, 2026 8:24pm | Jul 11, 2026 9:20pm | Jul 11, 2026 9:22pm | Jul 11, 2026 9:26pm | Jul 11, 2026 9:26pm |  |  | Flood | No | Customer not located
Outage | J.E.26.07.12279 | C001852325 | Hopeton Henry | St.Thomas | Completed | Load_238855 | Good Year - 210 | Jul 11, 2026 8:35am | Jul 11, 2026 8:36am | Jul 11, 2026 9:16am | Jul 11, 2026 11:11am | Jul 11, 2026 11:11am | Jul 11, 2026 11:11am | Jul 11, 2026 11:15am | Jul 11, 2026 11:15am |  |  | Fair | No | Found ok , power restored
Non-Outage | J.E.26.03.08958 | C001852324 | Dwain Samuels | Westmoreland | Completed | Load_252796 | Paradise - 210 | Jul 11, 2026 8:34am | Jul 11, 2026 8:35am | Jul 11, 2026 8:43am | Jul 11, 2026 12:10pm | Jul 11, 2026 12:10pm | Jul 11, 2026 12:10pm | Jul 11, 2026 12:12pm | Jul 11, 2026 12:12pm |  |  | Fair | No | Corrosion found at 3 wire pole. Voltage check 116-41-157. Corrosion clear use 1 one bolt clamp. Voltage check 116-115-231
Non-Outage | J.E.26.03.12549 | C001852321 | Dwain Samuels | Westmoreland | Completed | Load_239830 | Paradise - 210 | Jul 11, 2026 8:34am | Jul 11, 2026 8:35am | Jul 11, 2026 8:43am | Jul 11, 2026 11:03am | Jul 11, 2026 11:03am | Jul 11, 2026 11:08am | Jul 11, 2026 11:08am | Jul 11, 2026 11:08am | LeaningPole |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.07.10355 | C001852318 | Collin Robinson | Portland | Completed | Load_259756 | Port Antonio - 410 | Jul 11, 2026 8:34am | Jul 11, 2026 8:35am | Jul 11, 2026 9:15pm | Jul 11, 2026 9:15pm | Jul 11, 2026 9:27pm | Jul 11, 2026 9:28pm | Jul 11, 2026 9:29pm | Jul 11, 2026 9:29pm | LowHangingWires |  | Fair | No | Unable to locate customer
Non-Outage | J.E.26.03.19500 | C001852313 | Dwain Samuels | Westmoreland | Completed | Load_237679 | Paradise - 210 | Jul 11, 2026 8:33am | Jul 11, 2026 8:35am | Jul 11, 2026 8:43am | Jul 11, 2026 10:08am | Jul 11, 2026 10:09am | Jul 11, 2026 10:15am | Jul 11, 2026 10:16am | Jul 11, 2026 10:16am |  |  | Fair | No | Premises is closed
Non-Outage | J.E.26.03.19915 | C001852308 | Dwain Samuels | Westmoreland | Completed | Load_239066 | Orange Bay - 210 | Jul 11, 2026 8:33am | Jul 11, 2026 8:36am | Jul 11, 2026 8:43am | Jul 11, 2026 9:49am | Jul 11, 2026 9:49am | Jul 11, 2026 9:51am | Jul 11, 2026 9:52am | Jul 11, 2026 9:52am |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.03.25728 | C001852309 | Dwain Samuels | Westmoreland | Completed | Load_262557 | Paradise - 210 | Jul 11, 2026 8:33am | Jul 11, 2026 8:36am | Jul 11, 2026 8:43am | Jul 11, 2026 9:53am | Jul 11, 2026 9:54am | Jul 11, 2026 10:01am | Jul 11, 2026 10:04am | Jul 11, 2026 10:04am |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.07.09367 | C001852314 | Collin Robinson | Portland | Completed | Load_268759 | Port Antonio - 410 | Jul 11, 2026 8:33am | Jul 11, 2026 8:35am | Jul 11, 2026 8:21pm | Jul 11, 2026 8:21pm | Jul 11, 2026 9:13pm | Jul 11, 2026 9:15pm | Jul 11, 2026 9:15pm | Jul 11, 2026 9:15pm | Fire |  | Fair | No | No access to premises gate lock
Non-Outage | J.E.26.07.10077 | C001852316 | Collin Robinson | Portland | Completed | Load_237806 | Port Antonio - 410 | Jul 11, 2026 8:33am | Jul 11, 2026 8:35am | Jul 11, 2026 9:22am | Jul 11, 2026 9:22am | Jul 11, 2026 11:37am | Jul 11, 2026 11:39am | Jul 11, 2026 11:39am | Jul 11, 2026 11:39am | Fire |  | Fair | No | Information received from customer that issue was resolved
Non-Outage | J.E.26.07.11842 | C001852310 | Christopher Edwards | KSAN | Completed | Load_257186 | Constant Spring - 410 | Jul 11, 2026 8:33am | Jul 11, 2026 8:33am | Jul 11, 2026 9:19am | Jul 11, 2026 9:19am | Jul 11, 2026 10:20am | Jul 11, 2026 12:21pm | Jul 11, 2026 12:25pm | Jul 11, 2026 12:25pm |  |  | Fair | No | Clear vegetation to get access to transformer poleIsolate bank of three transformer to step down transformer Transformer is now in position 3 Voltage:238,240,248,422,418,447v
Outage | J.E.26.07.10806 | C001852306 | Richard Samuda | Manchester | Completed | Load_237860 | Spur Tree - 210 | Jul 11, 2026 8:30am | Jul 11, 2026 8:31am | Jul 11, 2026 1:40pm | Jul 11, 2026 1:40pm | Jul 11, 2026 1:50pm | Jul 11, 2026 2:24am | Jul 11, 2026 2:24pm | Jul 11, 2026 2:24pm |  |  | SevereWind | No | Reconnect customer service wire one phase that was broken causing customer to experience single phasing voltage: 115, 115 230
Outage | J.E.26.07.12283 | C001852307 | Richman Whyte | Westmoreland | Completed | Load_257048 | Paradise - 310 | Jul 11, 2026 8:30am | Jul 11, 2026 8:31am | Jul 11, 2026 1:37pm | Jul 11, 2026 1:37pm | Jul 11, 2026 1:38pm | Jul 11, 2026 1:38pm | Jul 11, 2026 1:46pm | Jul 11, 2026 1:46pm |  |  | Fair | No | Run an connected #80ft #6 triplex service wire #3 service connectors #3 clamps voltage #114 114 228
Outage | J.E.26.07.12199 | C001852304 | Andre Smith | KSAN | Completed | Load_253996 | Washington Blvd - 710 | Jul 11, 2026 8:20am | Jul 11, 2026 8:30am | Jul 11, 2026 8:37am | Jul 11, 2026 8:37am | Jul 11, 2026 9:26am | Jul 11, 2026 10:10am | Jul 11, 2026 10:10am | Jul 11, 2026 10:10am |  |  | Fair | No | Defective 15kva hexing transformer found maintenance department required
Outage | J.E.26.07.08657 | C001852303 | Michael Christian | St.James | Completed | Load_292531 | Queens Drive - 710 | Jul 11, 2026 8:19am | Jul 11, 2026 8:49am | Jul 11, 2026 3:28pm | Jul 11, 2026 3:28pm | Jul 11, 2026 3:28pm | Jul 11, 2026 3:28pm | Jul 11, 2026 3:28pm | Jul 11, 2026 3:28pm |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.10503 | C001852301 | Michael Christian | St.James | Completed | Load_266001 | Queens Drive - 310 | Jul 11, 2026 8:19am | Jul 11, 2026 8:49am | Jul 11, 2026 10:33am | Jul 11, 2026 4:40pm | Jul 11, 2026 5:05pm | Jul 11, 2026 5:05pm | Jul 11, 2026 5:06pm | Jul 11, 2026 5:06pm |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.10841 | C001852302 | Michael Christian | St.James | Completed | Load_241044 | Queens Drive - 710 | Jul 11, 2026 8:19am | Jul 11, 2026 8:49am | Jul 11, 2026 12:19pm | Jul 11, 2026 12:19pm | Jul 11, 2026 12:37pm | Jul 11, 2026 12:51pm | Jul 11, 2026 12:51pm | Jul 11, 2026 12:51pm |  |  | Fair | No | Check and found okay voltage 111 110 221 at meter
Outage | J.E.26.07.05836 | C001852299 | Romeo Brissett | St.James | Completed | Load_1002490 | Bogue - 310 | Jul 11, 2026 8:18am | Jul 11, 2026 8:18am | Jul 11, 2026 3:20pm | Jul 11, 2026 9:54pm | Jul 11, 2026 11:07pm | Jul 11, 2026 11:00pm | Jul 11, 2026 11:09pm | Jul 11, 2026 11:09pm |  |  | Fair | No | Check and found closed.
Non-Outage | J.E.26.07.11213 | C001852290 | Tyrese Williams | St.Ann | Completed | Load_259557 | Cardiff Hall - 210 | Jul 11, 2026 8:16am | Jul 11, 2026 8:17am | Jul 11, 2026 8:59am | Jul 11, 2026 10:18am | Jul 11, 2026 10:34am | Jul 11, 2026 10:36am | Jul 11, 2026 10:36am | Jul 11, 2026 10:36am |  |  | Fair | No | Premises found ok problem was resolved from yesterday
Non-Outage | J.E.26.07.11217 | C001852289 | Tyrese Williams | St.Ann | Completed | Load_246384 | Cardiff Hall - 310 | Jul 11, 2026 8:16am | Jul 11, 2026 8:17am | Jul 11, 2026 8:59am | Jul 11, 2026 9:01am | Jul 11, 2026 9:48am | Jul 11, 2026 10:15am | Jul 11, 2026 10:18am | Jul 11, 2026 10:18am |  |  | Fair | No | Premises found ok at the time of visit voltage check 118/116/234 customer meter is in hexing box
Non-Outage | J.E.26.07.11242 | C001852288 | Daniel Francis | St.Ann | Completed | Load_252857 | Roaring River - 210 | Jul 11, 2026 8:16am | Jul 11, 2026 4:05pm | Jul 11, 2026 9:27pm | Jul 11, 2026 9:27pm | Jul 11, 2026 11:04pm | Jul 11, 2026 11:30pm | Jul 11, 2026 11:31pm | Jul 11, 2026 11:31pm |  |  | Fair | No | Pole #044573 change one 25amp fuse
Outage | J.E.26.07.10832 | C001852287 | Derrick Dawkins | St.James | Completed | Load_258788 | Bogue - 610 | Jul 11, 2026 8:16am | Jul 11, 2026 8:17am | Jul 11, 2026 2:45pm | Jul 11, 2026 2:46pm | Jul 11, 2026 3:15pm | Jul 11, 2026 3:16pm | Jul 11, 2026 3:16pm | Jul 11, 2026 3:16pm |  |  | Fair | No | Customer meter burn refer back to customer service 117/118=235
Outage | J.E.26.07.10924 | C001852286 | Derrick Dawkins | St.James | Completed | Load_259585 | Bogue - 510 | Jul 11, 2026 8:16am | Jul 11, 2026 8:17am | Jul 11, 2026 10:59am | Jul 11, 2026 10:59am | Jul 11, 2026 11:28am | Jul 11, 2026 11:32am | Jul 11, 2026 11:32am | Jul 11, 2026 11:32am |  |  | Fair | No | Premises checked and found ok
Outage | J.E.26.07.12252 | C001852284 | Derrick Dawkins | St.James | Completed | Load_269407 | Bogue - 510 | Jul 11, 2026 8:16am | Jul 11, 2026 8:17am | Jul 11, 2026 8:55am | Jul 11, 2026 8:55am | Jul 11, 2026 10:38am | Jul 11, 2026 10:58am | Jul 11, 2026 10:59am | Jul 11, 2026 10:59am | BrokenWire |  | Fair | No | Customer service wire torn down due to vehicle accident customer sanction damaged advise customer to get sanction repaired
Outage | J.E.26.07.11643 | C001852282 | Romaine Roberts | St.Mary | Completed | Load_252214 | Highgate -110 | Jul 11, 2026 8:15am | Jul 11, 2026 8:16am | Jul 11, 2026 8:30am | Jul 11, 2026 8:30am | Jul 11, 2026 9:44am | Jul 11, 2026 11:02am | Jul 11, 2026 11:02am | Jul 11, 2026 11:02am |  |  | Fair | No | 3 wire service Corrosion at pole and pothead clean and remake joints 112-112 -224
Outage | J.E.26.07.11667 | C001852277 | Stephen Taylor | St.Thomas | Completed | Load_238021 | Lysson - 410 | Jul 11, 2026 8:14am | Jul 11, 2026 8:15am | Jul 11, 2026 9:29am | Jul 11, 2026 9:29am | Jul 11, 2026 10:01am | Jul 11, 2026 10:01am | Jul 11, 2026 10:02am | Jul 11, 2026 10:02am |  |  | Fair | No | Contact customer and customer say that power was restored and now okay
Outage | J.E.26.07.12160 | C001852278 | Romaine Roberts | St.Mary | Completed | Load_267975 | Highgate - 210 | Jul 11, 2026 8:14am | Jul 11, 2026 8:15am | Jul 11, 2026 11:03am | Jul 11, 2026 11:49am | Jul 11, 2026 11:49am | Jul 11, 2026 11:57am | Jul 11, 2026 12:00pm | Jul 11, 2026 12:00pm |  |  | Fair | No | High wind bang secondary conductor and trip 25 kva transformer clear cline and retention one span of conductor phase And neutral reset 25 kva power restore
Outage | J.E.26.07.12264 | C001852276 | Romaine Roberts | St.Mary | Completed | Load_264246 | Highgate - 210 | Jul 11, 2026 8:14am | Jul 11, 2026 8:15am | Jul 11, 2026 5:39pm | Jul 11, 2026 5:44pm | Jul 11, 2026 7:16pm | Jul 11, 2026 7:18pm | Jul 11, 2026 7:21pm | Jul 11, 2026 7:21pm |  |  | Fair | No | High wind bang 3 span of secondary phase and neutral open and close 50 kva transformer to retention conductor power restore
Outage | J.E.26.07.12270 | C001852275 | Cliton Henry | St.Mary | Completed | Load_239913 | Blackstonedge - 110 | Jul 11, 2026 8:13am | Jul 11, 2026 8:15am | Jul 11, 2026 10:36am | Jul 11, 2026 10:36am | Jul 11, 2026 11:53am | Jul 11, 2026 12:56pm | Jul 11, 2026 1:03pm | Jul 11, 2026 1:03pm | BrokenWire |  | Fair | No | A broken secondary neutral conductor found due bamboo tree fell on line. A 25 kva transformer was de energized at pole #0014198 to carryout repairs. Corrective work done to cut and remove bamboo trees, spliced and retention secondary neutral conductor using approximately 5 feet #2 AA conductor, 2 #2 splicing sleeves, 1#2 preform and 2 one bolt clamps. Supply restored to energized the 25 kva transformer. Voltages left 119-119/238 volts.
Non-Outage | J.E.26.07.12098 | C001852274 | Michael Christian | St.James | Completed | Load_250164 | Rose Hall - 210 | Jul 11, 2026 8:12am | Jul 11, 2026 8:13am | Jul 11, 2026 8:22am | Jul 11, 2026 8:22am | Jul 11, 2026 9:41am | Jul 11, 2026 10:13am | Jul 11, 2026 10:14am | Jul 11, 2026 10:14am |  |  | Fair | No | Found 1 50 amp junction out replace no pole #
Outage | J.E.26.07.12177 | C001852272 | Hopeton Henry | St.Thomas | Completed | Load_243194 | Good Year - 210 | Jul 11, 2026 8:06am | Jul 11, 2026 8:07am | Jul 11, 2026 9:16am | Jul 11, 2026 3:29pm | Jul 11, 2026 3:29pm | Jul 11, 2026 3:29pm | Jul 11, 2026 3:30pm | Jul 11, 2026 3:30pm |  |  | Fair | No | Power restored
Outage | J.E.26.07.12184 | C001852270 | Stephen Taylor | St.Thomas | Completed | Load_256230 | Lysson - 410 | Jul 11, 2026 8:03am | Jul 11, 2026 8:04am | Jul 11, 2026 10:16am | Jul 11, 2026 10:16am | Jul 11, 2026 10:24am | Jul 11, 2026 10:24am | Jul 11, 2026 11:33am | Jul 11, 2026 11:33am |  |  | Fair | No | Transformer link down and click was made and found out that 25 kva transformer defective and need to change by the jps maintenance team
Outage | J.E.26.07.12221 | C001852271 | Elvis Trowers | KSAN | Completed | Load_252171 | Hope - 510 | Jul 11, 2026 8:03am | Jul 11, 2026 8:06am | Jul 11, 2026 3:34pm | Jul 11, 2026 3:34pm | Jul 11, 2026 3:37pm | Jul 11, 2026 4:13pm | Jul 11, 2026 4:13pm | Jul 11, 2026 4:13pm |  |  | SevereWind | Yes | A section was found without electricity supply when checked and a blown 3 amp transformer fuse was found and replaced after patrol was completed at pole #————.missing.
Non-Outage | J.E.26.07.07350 | C001852269 | Nickolas Rodriques | St.Catherine | Completed | Load_264996 | Tredegar - 210 | Jul 11, 2026 7:59am | Jul 11, 2026 8:10am | Jul 11, 2026 1:06pm | Jul 11, 2026 1:17pm | Jul 11, 2026 1:53pm | Jul 11, 2026 2:03pm | Jul 11, 2026 2:20pm | Jul 11, 2026 2:20pm |  |  | Fair | No | Found premises locked. The customer was contacted and stated that no one is currently home to accommodate the team and he is requesting a team tomorrow July 12, 2026.
Non-Outage | J.E.26.07.08589 | C001852265 | Nickolas Rodriques | St.Catherine | Completed | Load_255345 | Twickenham - 310 | Jul 11, 2026 7:58am | Jul 11, 2026 7:59am | Jul 11, 2026 10:30am | Jul 11, 2026 10:30am | Jul 11, 2026 11:09am | Jul 11, 2026 11:43am | Jul 11, 2026 11:52am | Jul 11, 2026 11:52am | BrokenWire |  | Fair | No | Checked and found customer service wire broken caused by heavy winds. Repaired by splice and retention wire using three service sleeves, current reading is (114-117-231). Customer confirmed all is well now.
Outage | J.E.26.07.10779 | C001852260 | Romeo Brissett | St.James | Completed | Load_292055 | Bogue - 310 | Jul 11, 2026 7:57am | Jul 11, 2026 8:01am | Jul 11, 2026 8:09am | Jul 11, 2026 8:09am | Jul 11, 2026 9:12am | Jul 11, 2026 9:20am | Jul 11, 2026 9:38am | Jul 11, 2026 9:38am | BrokenPole |  | Fair | No | Found (1)30ft pole Broken with open secondary and streetlight no customer is without supply, please send to maintenance.
Outage | J.E.26.07.11100 | C001852261 | Romeo Brissett | St.James | Completed | Load_301642 | Bogue - 310 | Jul 11, 2026 7:57am | Jul 11, 2026 8:01am | Jul 11, 2026 11:35am | Jul 11, 2026 11:35am | Jul 11, 2026 11:59am | Jul 11, 2026 12:27pm | Jul 11, 2026 12:30pm | Jul 11, 2026 12:30pm |  |  | Fair | No | Removed bamboo, replaced (1)8amps junction fuse.
Outage | J.E.26.07.12128 | C001852262 | Romeo Brissett | St.James | Completed | Load_238410 | Bogue - 310 | Jul 11, 2026 7:57am | Jul 11, 2026 8:01am | Jul 11, 2026 11:34am | Jul 11, 2026 11:34am | Jul 11, 2026 11:34am | Jul 11, 2026 11:34am | Jul 11, 2026 11:35am | Jul 11, 2026 11:35am |  |  | Fair | No | Check and found ok
Outage | J.E.26.07.12128 | C001852263 | Romeo Brissett | St.James | Completed | Load_238410 | Bogue - 310 | Jul 11, 2026 7:57am | Jul 11, 2026 8:01am | Jul 11, 2026 9:39am | Jul 11, 2026 9:39am | Jul 11, 2026 10:49am | Jul 11, 2026 11:23am | Jul 11, 2026 11:33am | Jul 11, 2026 11:33am |  |  | Fair | No | Line patrolled and found power in the area. Resident stated power was restored earlier.
Outage | J.E.26.07.12173 | C001852264 | Romeo Brissett | St.James | Completed | Load_238410 | Bogue - 310 | Jul 11, 2026 7:57am | Jul 11, 2026 8:01am | Jul 11, 2026 11:33am | Jul 11, 2026 11:33am | Jul 11, 2026 11:33am | Jul 11, 2026 11:30am | Jul 11, 2026 11:34am | Jul 11, 2026 11:34am |  |  | Fair | No | Check and found ok
Outage | J.E.26.07.10548 | C001852259 | Romeo Brissett | St.James | Completed | Load_246427 | Bogue - 310 | Jul 11, 2026 7:56am | Jul 11, 2026 8:02am | Jul 11, 2026 3:43pm | Jul 11, 2026 3:43pm | Jul 11, 2026 4:01pm | Jul 11, 2026 5:00pm | Jul 11, 2026 5:06pm | Jul 11, 2026 5:06pm |  |  | Fair | No | Changed customer service wire, used 50ft of #6. V/R 118-120-238
Outage | J.E.26.07.12186 | C001852255 | Cliton Henry | St.Mary | Completed | Load_257277 | Blackstonedge - 110 | Jul 11, 2026 7:56am | Jul 11, 2026 7:56am | Jul 11, 2026 1:50pm | Jul 11, 2026 1:50pm | Jul 11, 2026 2:07pm | Jul 11, 2026 2:28pm | Jul 11, 2026 2:30pm | Jul 11, 2026 2:30pm |  |  | Fair | No | A blown 10 junction fuse found at pole pole # 0014123. Supply restored using 1 10 amp fuse.
Outage | J.E.26.06.22564 | C001852253 | Richman Whyte | Westmoreland | Completed | Load_255620 | Paradise - 310 | Jul 11, 2026 7:52am | Jul 11, 2026 7:52am | Jul 11, 2026 10:18am | Jul 11, 2026 10:18am | Jul 11, 2026 10:18am | Jul 11, 2026 10:18am | Jul 11, 2026 10:18am | Jul 11, 2026 10:18am |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.07.11779 | C001852251 | Tyrese Williams | null | Completed | null | null | Jul 11, 2026 7:51am | Jul 11, 2026 4:28pm | Jul 11, 2026 4:35pm | Jul 11, 2026 9:09pm | Jul 11, 2026 9:36pm | Jul 11, 2026 9:56pm | Jul 11, 2026 9:51pm | Jul 11, 2026 9:51pm | Fire |  | Fair | No | Found. Defective 25kva transformer recommend to be change at pole 031152/ 0171297
Outage | J.E.26.07.04815 | C001852252 | Richman Whyte | Westmoreland | Completed | Load_241093 | Paradise - 310 | Jul 11, 2026 7:51am | Jul 11, 2026 7:52am | Jul 11, 2026 10:12am | Jul 11, 2026 10:12am | Jul 11, 2026 10:12am | Jul 11, 2026 10:13am | Jul 11, 2026 10:13am | Jul 11, 2026 10:13am |  |  | Fair | No | Found already connected
Outage | J.E.26.07.07591 | C001852250 | Richman Whyte | Westmoreland | Completed | Load_270211 | Paradise - 310 | Jul 11, 2026 7:51am | Jul 11, 2026 7:52am | Jul 11, 2026 1:35pm | Jul 11, 2026 1:35pm | Jul 11, 2026 1:35pm | Jul 11, 2026 1:35pm | Jul 11, 2026 1:36pm | Jul 11, 2026 1:36pm |  |  | Fair | No | Found already connected
Non-Outage | J.E.26.07.09664 | C001852249 | Nickolas Rodriques | St.Catherine | Completed | Load_255976 | Tredegar - 410 | Jul 11, 2026 7:50am | Jul 11, 2026 7:51am | Jul 11, 2026 10:15am | Jul 11, 2026 10:15am | Jul 11, 2026 10:27am | Jul 11, 2026 10:28am | Jul 11, 2026 10:29am | Jul 11, 2026 10:29am |  |  | Fair | No | Unable to communicate with the customer after several attempts.
Non-Outage | J.E.26.07.09670 | C001852246 | Nickolas Rodriques | St.Catherine | Completed | Load_1001354 | Tredegar - 210 | Jul 11, 2026 7:50am | Jul 11, 2026 7:51am | Jul 11, 2026 3:42pm | Jul 11, 2026 3:57pm | Jul 11, 2026 3:57pm | Jul 11, 2026 4:00pm | Jul 11, 2026 4:02pm | Jul 11, 2026 4:02pm |  |  | Fair | No | Customer stated that she is having single phasing. Reading found (112-114-226). All necessary checks were done and it was found that the customer is having internal issue. The customer was advised to consult an electrician to do repairs.
Non-Outage | J.E.26.07.09670 | C001852248 | Nickolas Rodriques | St.Catherine | Completed | Load_1001354 | Tredegar - 210 | Jul 11, 2026 7:50am | Jul 11, 2026 7:51am | Jul 11, 2026 2:20pm | Jul 11, 2026 2:24pm | Jul 11, 2026 3:06pm | Jul 11, 2026 3:35pm | Jul 11, 2026 3:36pm | Jul 11, 2026 3:36pm |  |  | Fair | No | Customer stated that she is having single phasing. Reading found (112-114-226). All necessary checks were done and it was found that the customer is having internal issue. The customer was advised to consult an electrician to do repairs.
Non-Outage | J.E.26.07.09854 | C001852247 | Nickolas Rodriques | St.Catherine | Completed | Load_256045 | Tredegar - 510 | Jul 11, 2026 7:50am | Jul 11, 2026 7:51am | Jul 11, 2026 5:31pm | Jul 11, 2026 5:32pm | Jul 11, 2026 6:12pm | Jul 11, 2026 6:39pm | Jul 11, 2026 6:59pm | Jul 11, 2026 6:59pm |  |  | Fair | No | Checked and found customer single phasing (118) caused by defective service wire that runs through a mango tree. Unable to proceed with repair due to the huge mango tree that needs to be cut. The customer was advised to cut the tree before repair can be done.
Non-Outage | J.E.26.07.10439 | C001852245 | Nickolas Rodriques | St.Catherine | Completed | Load_255976 | Tredegar - 410 | Jul 11, 2026 7:50am | Jul 11, 2026 7:51am | Jul 11, 2026 8:49am | Jul 11, 2026 9:07am | Jul 11, 2026 10:00am | Jul 11, 2026 10:13am | Jul 11, 2026 10:14am | Jul 11, 2026 10:14am |  |  | Fair | No | Unable to communicate with the customer after several attempts.
Non-Outage | J.E.26.07.11237 | C001852243 | Nickolas Rodriques | St.Catherine | Completed | Load_244358 | Tredegar - 410 | Jul 11, 2026 7:49am | Jul 11, 2026 7:51am | Jul 11, 2026 4:05pm | Jul 11, 2026 4:05pm | Jul 11, 2026 5:08pm | Jul 11, 2026 5:24pm | Jul 11, 2026 5:30pm | Jul 11, 2026 5:30pm |  |  | Fair | No | Unable to locate or communicate with the customer after several attempts.
Non-Outage | J.E.26.07.11580 | C001852241 | Nickolas Rodriques | St.Catherine | Completed | Load_267523 | Tredegar - 410 | Jul 11, 2026 7:49am | Jul 11, 2026 7:51am | Jul 11, 2026 12:00pm | Jul 11, 2026 12:01pm | Jul 11, 2026 12:34pm | Jul 11, 2026 12:52pm | Jul 11, 2026 1:06pm | Jul 11, 2026 1:06pm |  |  | Fair | No | Checked and found customer with unstable voltage caused by corroded connection. Repaired by placing three service sleeves and three clamps at pothead and pole, current reading is (113-111-224).
Non-Outage | J.E.26.07.04486 | C001852239 | Donald Cunningham | St.Catherine | Completed | Load_244637 | New Michelton - 210 | Jul 11, 2026 7:48am | Jul 11, 2026 7:51am | Jul 12, 2026 4:56pm | Jul 12, 2026 4:56pm | Jul 12, 2026 4:56pm | Jul 12, 2026 4:56pm | Jul 12, 2026 4:57pm | Jul 12, 2026 4:57pm |  |  | Fair | No
Non-Outage | J.E.26.07.05878 | C001852240 | Donald Cunningham | St.Catherine | Completed | Load_262099 | New Michelton - 210 | Jul 11, 2026 7:48am | Jul 11, 2026 7:51am | Jul 11, 2026 9:44am | Jul 11, 2026 9:44am | Jul 11, 2026 11:33am | Jul 11, 2026 11:36am | Jul 11, 2026 11:36am | Jul 11, 2026 11:36am |  |  | Fair | No | Premises closed
Non-Outage | J.E.26.07.06025 | C001852238 | Donald Cunningham | St.Catherine | Completed | Load_237877 | New Michelton - 210 | Jul 11, 2026 7:48am | Jul 11, 2026 7:48am | Jul 12, 2026 4:57pm | Jul 12, 2026 4:57pm | Jul 12, 2026 4:57pm | Jul 12, 2026 4:58pm | Jul 12, 2026 4:59pm | Jul 12, 2026 4:59pm | LowHangingWires |  | Fair | No
Non-Outage | J.E.26.07.08194 | C001852236 | Donald Cunningham | St.Catherine | Completed | Load_260206 | New Michelton - 310 | Jul 11, 2026 7:48am | Jul 11, 2026 7:48am | Jul 11, 2026 1:16pm | Jul 11, 2026 1:16pm | Jul 11, 2026 2:33pm | Jul 11, 2026 2:50pm | Jul 11, 2026 2:53pm | Jul 11, 2026 2:53pm | BrokenWire |  | Fair | No | Issues resolved conductors were banging bushing required in area
Non-Outage | J.E.26.07.08814 | C001852237 | Donald Cunningham | St.Catherine | Completed | Load_252028 | New Michelton - 210 | Jul 11, 2026 7:48am | Jul 11, 2026 7:48am | Jul 11, 2026 11:40am | Jul 11, 2026 11:41am | Jul 11, 2026 1:04pm | Jul 11, 2026 1:15pm | Jul 11, 2026 1:16pm | Jul 11, 2026 1:16pm |  |  | Fair | No | Premises not located customer not reachable
Non-Outage | J.E.26.07.09048 | C001852235 | Donald Cunningham | St.Catherine | Completed | Load_245848 | New Michelton - 210 | Jul 11, 2026 7:48am | Jul 11, 2026 7:48am | Jul 12, 2026 4:59pm | Jul 12, 2026 4:59pm | Jul 12, 2026 4:59pm | Jul 12, 2026 4:59pm | Jul 12, 2026 5:00pm | Jul 12, 2026 5:00pm |  |  | EarthMovement | No
Non-Outage | J.E.26.07.09425 | C001852234 | Donald Cunningham | St.Catherine | Completed | Load_568285 | New Michelton - 410 | Jul 11, 2026 7:47am | Jul 11, 2026 7:48am | Jul 11, 2026 8:04am | Jul 11, 2026 8:04am | Jul 11, 2026 9:39am | Jul 11, 2026 9:43am | Jul 11, 2026 9:44am | Jul 11, 2026 9:44am |  |  | Fair | No | Premises closed
Non-Outage | J.E.26.07.10694 | C001852233 | Donald Cunningham | St.Catherine | Completed | Load_267869 | New Michelton - 410 | Jul 11, 2026 7:47am | Jul 11, 2026 7:48am | Jul 12, 2026 5:00pm | Jul 12, 2026 5:00pm | Jul 12, 2026 5:00pm | Jul 12, 2026 5:00pm | Jul 12, 2026 5:00pm | Jul 12, 2026 5:00pm | LeaningPole |  | Fair | No
Non-Outage | J.E.26.07.10951 | C001852232 | Donald Cunningham | St.Catherine | Completed | Load_568317 | New Michelton - 410 | Jul 11, 2026 7:47am | Jul 11, 2026 7:48am | Jul 12, 2026 5:01pm | Jul 12, 2026 5:01pm | Jul 12, 2026 5:02pm | Jul 12, 2026 5:02pm | Jul 12, 2026 5:02pm | Jul 12, 2026 5:02pm |  |  | Fair | No
Non-Outage | J.E.26.07.12059 | C001852231 | Donald Cunningham | St.Catherine | Completed | Load_238392 | New Michelton - 410 | Jul 11, 2026 7:46am | Jul 11, 2026 7:48am | Jul 12, 2026 5:04pm | Jul 12, 2026 5:04pm | Jul 12, 2026 5:04pm | Jul 12, 2026 5:04pm | Jul 12, 2026 5:04pm | Jul 12, 2026 5:04pm |  |  | Fair | No
Outage | J.E.26.07.10491 | C001852230 | Richard Nicholas | St.Catherine | Completed | Load_557183 | Tredegar - 410 | Jul 11, 2026 7:42am | Jul 11, 2026 7:43am | Jul 11, 2026 4:52pm | Jul 11, 2026 4:52pm | Jul 11, 2026 5:45pm | Jul 11, 2026 6:02pm | Jul 11, 2026 6:03pm | Jul 11, 2026 6:03pm |  |  | Fair | No | Rammy system failure.
Outage | J.E.26.07.10650 | C001852226 | Richard Nicholas | St.Catherine | Completed | Load_247419 | New Michelton - 410 | Jul 11, 2026 7:42am | Jul 11, 2026 7:43am | Jul 11, 2026 8:48am | Jul 11, 2026 8:48am | Jul 11, 2026 11:40am | Jul 11, 2026 12:13pm | Jul 11, 2026 12:13pm | Jul 11, 2026 12:13pm | BrokenWire |  | Fair | No | Found ok
Outage | J.E.26.07.10809 | C001852227 | Richard Nicholas | St.Catherine | Completed | Load_557854 | Tredegar - 310 | Jul 11, 2026 7:42am | Jul 11, 2026 7:43am | Jul 11, 2026 1:22pm | Jul 11, 2026 1:23pm | Jul 11, 2026 2:16pm | Jul 11, 2026 2:34pm | Jul 11, 2026 2:35pm | Jul 11, 2026 2:35pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.11211 | C001852228 | Donald Cunningham | St.Catherine | Completed | Load_253711 | New Michelton - 410 | Jul 11, 2026 7:42am | Jul 11, 2026 12:47pm | Jul 12, 2026 5:04pm | Jul 12, 2026 5:04pm | Jul 12, 2026 5:05pm | Jul 12, 2026 5:05pm | Jul 12, 2026 5:05pm | Jul 12, 2026 5:05pm |  |  | EarthMovement | No
Non-Outage | J.E.26.07.11500 | C001852221 | Tyrese Williams | null | Completed | null | null | Jul 11, 2026 7:40am | Jul 11, 2026 4:34pm | Jul 11, 2026 5:48pm | Jul 11, 2026 6:56pm | Jul 11, 2026 7:41pm | Jul 11, 2026 7:43pm | Jul 11, 2026 7:43pm | Jul 11, 2026 7:43pm |  |  | Fair | No | Premises not found not getting customer on phone
Non-Outage | J.E.26.07.11731 | C001852225 | Ricky Hall | null | Completed | null | null | Jul 11, 2026 7:40am | Jul 11, 2026 7:41am | Jul 11, 2026 2:30pm | Jul 11, 2026 3:00pm | Jul 11, 2026 3:22pm | Jul 11, 2026 3:45pm | Jul 11, 2026 3:46pm | Jul 11, 2026 3:46pm |  |  | Fair | No | Issue was resolved on previous shift
Non-Outage | J.E.26.07.11874 | C001852223 | Ricky Hall | null | Completed | null | null | Jul 11, 2026 7:40am | Jul 11, 2026 7:41am | Jul 11, 2026 2:30pm | Jul 11, 2026 3:46pm | Jul 11, 2026 3:46pm | Jul 11, 2026 3:46pm | Jul 11, 2026 3:46pm | Jul 11, 2026 3:46pm |  |  | Fair | No | Issue was resolved on previous shift
Non-Outage | J.E.26.07.11903 | C001852222 | Ricky Hall | null | Completed | null | null | Jul 11, 2026 7:40am | Jul 11, 2026 7:41am | Jul 11, 2026 2:30pm | Jul 11, 2026 3:46pm | Jul 11, 2026 3:46pm | Jul 11, 2026 3:47pm | Jul 11, 2026 3:47pm | Jul 11, 2026 3:47pm |  |  | Fair | No | Issue was resolved on previous shift
Non-Outage | J.E.26.07.12215 | C001852216 | Omar King | null | Completed | null | null | Jul 11, 2026 7:40am | Jul 11, 2026 7:41am | Jul 11, 2026 11:01am | Jul 11, 2026 11:02am | Jul 11, 2026 11:26am | Jul 11, 2026 11:47am | Jul 11, 2026 11:48am | Jul 11, 2026 11:48am | BrokenWire |  | SevereWind | No | Found two span of secondary secondary phase and neutral broken as been repaired customer is now with supply
Outage | J.E.26.07.11691 | C001852224 | Ricky Hall | St.Catherine | Completed | Load_258187 | Rhodens Pen - 410 | Jul 11, 2026 7:40am | Jul 11, 2026 7:41am | Jul 11, 2026 11:14am | Jul 11, 2026 12:59pm | Jul 11, 2026 12:59pm | Jul 11, 2026 12:59pm | Jul 11, 2026 1:00pm | Jul 11, 2026 1:00pm | BrokenWire |  | Fair | No | Call associated with outage #12005
Outage | J.E.26.07.12005 | C001852219 | Ricky Hall | St.Catherine | Completed | Load_258187 | Rhodens Pen - 410 | Jul 11, 2026 7:40am | Jul 11, 2026 7:41am | Jul 11, 2026 11:14am | Jul 11, 2026 11:14am | Jul 11, 2026 12:24pm | Jul 11, 2026 12:59pm | Jul 11, 2026 12:59pm | Jul 11, 2026 12:59pm |  |  | SevereWind | No | Replaced blown 2 amps fuse 25 kva xfmr
Outage | J.E.26.07.12073 | C001852220 | Ricky Hall | St.Catherine | Completed | Load_254991 | Rhodens Pen - 410 | Jul 11, 2026 7:40am | Jul 11, 2026 7:41am | Jul 11, 2026 8:56am | Jul 11, 2026 11:13am | Jul 11, 2026 11:13am | Jul 11, 2026 11:14am | Jul 11, 2026 11:14am | Jul 11, 2026 11:14am |  |  | Fair | No | Call associated with outage #11247
Outage | J.E.26.07.12124 | C001852215 | Omar King | St.Ann | Completed | Load_258385 | Cardiff Hall - 210 | Jul 11, 2026 7:40am | Jul 11, 2026 7:41am | Jul 11, 2026 12:18pm | Jul 11, 2026 12:18pm | Jul 11, 2026 1:02pm | Jul 11, 2026 1:13pm | Jul 11, 2026 1:39pm | Jul 11, 2026 1:39pm |  |  | SevereWind | No | Found 25 KVA transformer trip cause by banging wire transformer as been reset customer is now with supply
Outage | J.E.26.07.12126 | C001852218 | Omar King | St.Ann | Completed | Load_267823 | Cardiff Hall - 210 | Jul 11, 2026 7:40am | Jul 11, 2026 7:41am | Jul 11, 2026 11:51am | Jul 11, 2026 11:51am | Jul 11, 2026 11:51am | Jul 11, 2026 12:17pm | Jul 11, 2026 12:17pm | Jul 11, 2026 12:17pm |  |  | SevereWind | No | Found 25 KVA transformer trip cause by banging wire transformer as been reset customer is now with supply
Outage | J.E.26.07.12222 | C001852214 | Omar King | St.Ann | Completed | Load_245873 | Cardiff Hall - 210 | Jul 11, 2026 7:40am | Jul 11, 2026 7:41am | Jul 11, 2026 8:40am | Jul 11, 2026 8:40am | Jul 11, 2026 9:57am | Jul 11, 2026 10:28am | Jul 11, 2026 10:28am | Jul 11, 2026 10:28am |  |  | Fair | No | Found a 30 amp junction fuse blow cause by tree contact fuse as been replaced area is now with supply
Non-Outage | J.E.26.07.11742 | C001852212 | Tyrese Williams | null | Completed | null | null | Jul 11, 2026 7:37am | Jul 11, 2026 12:39pm | Jul 11, 2026 2:19pm | Jul 11, 2026 2:19pm | Jul 11, 2026 2:20pm | Jul 11, 2026 2:20pm | Jul 11, 2026 2:20pm | Jul 11, 2026 2:20pm |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.07.11232 | C001852205 | Roxroy Needham | St.Ann | Completed | Load_244028 | Roaring River - 410 | Jul 11, 2026 7:37am | Jul 11, 2026 11:45am | Jul 11, 2026 1:25pm | Jul 11, 2026 1:40pm | Jul 11, 2026 1:46pm | Jul 11, 2026 1:47pm | Jul 11, 2026 1:50pm | Jul 11, 2026 1:50pm |  |  | Fair | No | Road need cut to access property heavy bushing to be done
Outage | J.E.26.07.11400 | C001852208 | Daniel Francis | St.Ann | Completed | Load_253537 | Upper White River - 210 | Jul 11, 2026 7:37am | Jul 11, 2026 3:41pm | Jul 11, 2026 9:17pm | Jul 11, 2026 9:17pm | Jul 11, 2026 9:26pm | Jul 11, 2026 9:26pm | Jul 11, 2026 9:27pm | Jul 11, 2026 9:27pm |  |  | Fair | No | Premises lock
Outage | J.E.26.07.11598 | C001852207 | Roxroy Needham | St.Ann | Completed | Load_255731 | Roaring River - 410 | Jul 11, 2026 7:37am | Jul 11, 2026 11:44am | Jul 11, 2026 1:22pm | Jul 11, 2026 1:22pm | Jul 11, 2026 1:22pm | Jul 11, 2026 1:22pm | Jul 11, 2026 1:23pm | Jul 11, 2026 1:23pm |  |  | Fair | No | Not getting customer on phone
Outage | J.E.26.07.11659 | C001852209 | Daniel Francis | St.Ann | Completed | Load_258794 | Ocho Rios - 510 | Jul 11, 2026 7:37am | Jul 11, 2026 3:41pm | Jul 11, 2026 8:57pm | Jul 11, 2026 8:57pm | Jul 11, 2026 9:05pm | Jul 11, 2026 9:04pm | Jul 11, 2026 9:07pm | Jul 11, 2026 9:07pm |  |  | Fair | No | Not found not answering phone
Outage | J.E.26.07.11673 | C001852210 | Daniel Francis | St.Ann | Completed | Load_264396 | Upper White River - 210 | Jul 11, 2026 7:37am | Jul 11, 2026 3:41pm | Jul 11, 2026 6:35pm | Jul 11, 2026 6:35pm | Jul 11, 2026 7:07pm | Jul 11, 2026 7:10pm | Jul 11, 2026 7:23pm | Jul 11, 2026 7:23pm |  |  | Fair | No | Not found
Outage | J.E.26.07.12218 | C001852203 | Tyrese Williams | St.Ann | Completed | Load_237805 | Ocho Rios - 310 | Jul 11, 2026 7:36am | Jul 11, 2026 11:39am | Jul 11, 2026 11:43am | Jul 11, 2026 1:31pm | Jul 11, 2026 1:44pm | Jul 11, 2026 1:53pm | Jul 11, 2026 1:55pm | Jul 11, 2026 1:55pm |  |  | Fair | No | Replace a 8amp junction fuse at pole
Non-Outage | J.E.26.07.07299 | C001852201 | Neville Spencer | Clarendon | Completed | Load_354364 | May Pen - 110 | Jul 11, 2026 7:35am | Jul 11, 2026 7:36am | Jul 11, 2026 11:55am | Jul 11, 2026 11:55am | Jul 11, 2026 11:55am | Jul 11, 2026 11:55am | Jul 11, 2026 11:56am | Jul 11, 2026 11:56am |  |  | Fair | No | Call belong to ST Ann’s.
Non-Outage | J.E.26.07.10336 | C001852198 | Neville Spencer | Clarendon | Completed | Load_352838 | May Pen - 110 | Jul 11, 2026 7:35am | Jul 11, 2026 7:36am | Jul 11, 2026 8:33am | Jul 11, 2026 8:33am | Jul 11, 2026 9:48am | Jul 11, 2026 11:37am | Jul 11, 2026 11:38am | Jul 11, 2026 11:38am | O |  | Fair | No | Open 25 kva xmfr cleared tree limb from secondary line . Also repair burnt out clamp on secondary neutral jumper used 1, clamp voltage reading 119.
Non-Outage | J.E.26.07.10642 | C001852199 | Neville Spencer | Clarendon | Completed | Load_250911 | May Pen - 110 | Jul 11, 2026 7:35am | Jul 11, 2026 7:36am | Jul 11, 2026 11:42am | Jul 11, 2026 11:42am | Jul 11, 2026 11:53am | Jul 11, 2026 11:54am | Jul 11, 2026 11:54am | Jul 11, 2026 11:54am |  |  | Fair | No | Found ok call resolved.
Non-Outage | J.E.26.07.10850 | C001852196 | Neville Spencer | Clarendon | Completed | Load_352838 | May Pen - 110 | Jul 11, 2026 7:35am | Jul 11, 2026 7:36am | Jul 11, 2026 11:39am | Jul 11, 2026 11:39am | Jul 11, 2026 11:39am | Jul 11, 2026 11:39am | Jul 11, 2026 11:42am | Jul 11, 2026 11:42am |  |  | Fair | No | Open 25 25 kva xmfr cleared cleared tree limb from secondary lines.Also repair burnt out clamp on secondary neutral jumper used 1, clamp voltage reading 119. Supply restored.
Non-Outage | J.E.26.07.12090 | C001852195 | Clyde Brown | Clarendon | Completed | Load_568663 | May Pen - 210 | Jul 11, 2026 7:33am | Jul 11, 2026 7:34am | Jul 11, 2026 11:27am | Jul 11, 2026 11:27am | Jul 11, 2026 11:27am | Jul 11, 2026 11:11am | Jul 11, 2026 11:29am | Jul 11, 2026 11:29am |  | Y | SevereWind | No | Broken secondary phase caused by tree contact,open 25 kva transformer and repaired with 7ft-#2/0 ,1- preform and 3- clamp.
Non-Outage | J.E.26.07.10082 | C001852194 | Clyde Brown | Clarendon | Completed | Load_251131 | Parnassus - 210 | Jul 11, 2026 7:32am | Jul 11, 2026 7:34am | Jul 11, 2026 11:30am | Jul 11, 2026 11:30am | Jul 11, 2026 12:19pm | Jul 11, 2026 12:40pm | Jul 11, 2026 12:55pm | Jul 11, 2026 12:55pm |  |  | SevereWind | No | Burnt off phase wire at pothead for 3 wire service connection remade with one clamp,voltage left 111/112 224V
Non-Outage | J.E.26.07.11658 | C001852193 | Clyde Brown | Clarendon | Completed | Load_295328 | Parnassus - 210 | Jul 11, 2026 7:32am | Jul 11, 2026 7:34am | Jul 11, 2026 9:43am | Jul 11, 2026 9:43am | Jul 11, 2026 9:43am | Jul 11, 2026 9:25am | Jul 11, 2026 9:45am | Jul 11, 2026 9:45am |  |  | SevereWind | No | Blown 30 amps junction fuse at St.Jago road,line patrolled and no fault seen,blown fuse replaced
Outage | J.E.26.07.12092 | C001852192 | Clyde Brown | Clarendon | Completed | Load_568663 | May Pen - 210 | Jul 11, 2026 7:31am | Jul 11, 2026 7:34am | Jul 11, 2026 9:46am | Jul 11, 2026 9:46am | Jul 11, 2026 10:58am | Jul 11, 2026 11:11am | Jul 11, 2026 11:26am | Jul 11, 2026 11:26am |  | Y | SevereWind | No | Broken secondary phase caused by tree contact,open 25 kva transformer and repaired with 2-clamp,7ft-2/0 conductor and 1- preform
Outage | J.E.26.07.12001 | C001852190 | Hartley Chin | Clarendon | Completed | Load_254372 | Monymusk - 410 | Jul 11, 2026 7:29am | Jul 11, 2026 7:31am | Jul 11, 2026 11:47am | Jul 11, 2026 12:58pm | Jul 11, 2026 1:50pm | Jul 11, 2026 2:07pm | Jul 11, 2026 2:08pm | Jul 11, 2026 2:08pm |  |  | SevereWind | No | Found okay … customer stated issue was resolved yesterday..
Outage | J.E.26.07.12038 | C001852191 | Hartley Chin | Clarendon | Completed | Load_257029 | Parnassus - 310 | Jul 11, 2026 7:29am | Jul 11, 2026 7:31am | Jul 11, 2026 8:55am | Jul 11, 2026 9:49am | Jul 11, 2026 10:01am | Jul 11, 2026 10:11am | Jul 11, 2026 10:11am | Jul 11, 2026 10:11am |  |  | Fair | No | Unable to contact customer…. Area patrolled and Found 15 KVA transformer @ pole # 0125632 breaker on trip line patrolled and found oaky , reset transformer…
Outage | J.E.26.07.11901 | C001852189 | Hartley Chin | Clarendon | Completed | Load_244499 | Parnassus - 310 | Jul 11, 2026 7:27am | Jul 11, 2026 7:30am | Jul 11, 2026 7:41am | Jul 11, 2026 11:46am | Jul 11, 2026 11:47am | Jul 11, 2026 11:47am | Jul 11, 2026 11:47am | Jul 11, 2026 11:47am |  |  | SevereWind | No | Call related to job # 11808 ..
Outage | J.E.26.07.12147 | C001852188 | Clyde Brown | Clarendon | Completed | Load_264199 | Parnassus - 210 | Jul 11, 2026 7:26am | Jul 11, 2026 7:30am | Jul 11, 2026 9:40am | Jul 11, 2026 9:40am | Jul 11, 2026 9:40am | Jul 11, 2026 9:24am | Jul 11, 2026 9:42am | Jul 11, 2026 9:42am |  |  | SevereWind | No | Blown 30 amps junction fuse at St.Jago road ,line patrolled and no fault seen,blown fuse replaced.
Outage | J.E.26.07.12172 | C001852187 | Hartley Chin | Clarendon | Completed | Load_250524 | Parnassus - 310 | Jul 11, 2026 7:26am | Jul 11, 2026 7:30am | Jul 11, 2026 7:42am | Jul 11, 2026 7:42am | Jul 11, 2026 9:15am | Jul 11, 2026 9:47am | Jul 11, 2026 9:48am | Jul 11, 2026 9:48am |  | Y | Fair | No | Found blown 3 amp fuse on 25 KVA transformer @ pole # 0125683 due to tree falling on open secondary circuit, cut tree from line , refused transformer…
Outage | J.E.26.07.11808 | C001852184 | Hartley Chin | Clarendon | Completed | Load_248927 | Parnassus - 310 | Jul 11, 2026 7:25am | Jul 11, 2026 7:30am | Jul 11, 2026 7:40am | Jul 11, 2026 10:12am | Jul 11, 2026 10:31am | Jul 11, 2026 11:41am | Jul 11, 2026 11:45am | Jul 11, 2026 11:45am |  |  | SevereWind | No | Found 2 of 3 blown 30 amp junction 550872 line patrolled and found okay , junction refused… note : CHNAGE 1 burnt fuse barrel .. note : severe wind speeds …
Outage | J.E.26.07.11895 | C001852183 | Hartley Chin | Clarendon | Completed | Load_264818 | Parnassus - 310 | Jul 11, 2026 7:25am | Jul 11, 2026 7:30am | Jul 11, 2026 7:40am | Jul 11, 2026 11:45am | Jul 11, 2026 11:45am | Jul 11, 2026 11:46am | Jul 11, 2026 11:46am | Jul 11, 2026 11:46am |  |  | Fair | No | Call related to job # 11808 ..
Outage | J.E.26.07.12154 | C001852185 | Clyde Brown | Clarendon | Completed | Load_251474 | Parnassus - 210 | Jul 11, 2026 7:25am | Jul 11, 2026 7:30am | Jul 11, 2026 8:33am | Jul 11, 2026 8:33am | Jul 11, 2026 9:08am | Jul 11, 2026 9:23am | Jul 11, 2026 9:39am | Jul 11, 2026 9:39am |  |  | SevereWind | No | Blown 30 amps junction fuse on St.Jago road,line patrolled and no fault seen,blown fuse replaced.
Outage | J.E.26.07.12139 | C001852182 | Collin Robinson | Portland | Completed | Load_245949 | Port Antonio - 410 | Jul 11, 2026 7:24am | Jul 11, 2026 7:25am | Jul 11, 2026 12:25pm | Jul 11, 2026 12:25pm | Jul 11, 2026 12:25pm | Jul 11, 2026 12:27pm | Jul 11, 2026 12:27pm | Jul 11, 2026 12:27pm | Fire |  | Fair | No | Unable to locate customer for better direction to premises
Outage | J.E.26.07.08746 | C001852181 | Cliton Henry | St.Mary | Completed | Load_270005 | Blackstonedge - 110 | Jul 11, 2026 7:22am | Jul 11, 2026 7:24am | Jul 11, 2026 10:26am | Jul 11, 2026 10:26am | Jul 11, 2026 10:27am | Jul 11, 2026 10:27am | Jul 11, 2026 10:30am | Jul 11, 2026 10:30am |  |  | Fair | No | Supply found ok. The customer stated that he the supply was restored.
Non-Outage | J.E.26.07.12190 | C001852180 | Richard Samuda | null | Completed | null | null | Jul 11, 2026 7:21am | Jul 11, 2026 7:22am | Jul 11, 2026 9:13am | Jul 11, 2026 9:13am | Jul 11, 2026 9:18am | Jul 11, 2026 9:37am | Jul 11, 2026 9:37am | Jul 11, 2026 9:37am | Fire |  | Fair | No | Pole number: 0113810 Refer call broken 40 ft TA pole pole needs to be replaced now causing secondary to bang out causing fire in area refer call to maintenance pole beside andrews memorial church urgent attention had to isolate transformer on broken pole that is causing secondary line to bang out causing fire funeral at church
Non-Outage | J.E.26.07.10620 | C001852177 | Richard Samuda | null | Completed | null | null | Jul 11, 2026 7:20am | Jul 11, 2026 7:22am | Jul 11, 2026 12:35pm | Jul 11, 2026 12:35pm | Jul 11, 2026 1:38pm | Jul 11, 2026 1:39pm | Jul 11, 2026 1:39pm | Jul 11, 2026 1:39pm |  |  | SevereWind | No | Found ok customer said issue was resolved
Non-Outage | J.E.26.07.10659 | C001852178 | Richard Samuda | null | Completed | null | null | Jul 11, 2026 7:20am | Jul 11, 2026 7:22am | Jul 11, 2026 4:52pm | Jul 11, 2026 4:53pm | Jul 11, 2026 4:53pm | Jul 11, 2026 4:53am | Jul 11, 2026 4:54pm | Jul 11, 2026 4:54pm |  |  | SevereWind | No | Found ok power was restored
Non-Outage | J.E.26.07.11703 | C001852179 | Richard Samuda | null | Completed | null | null | Jul 11, 2026 7:20am | Jul 11, 2026 7:26am | Jul 11, 2026 11:31am | Jul 11, 2026 11:31am | Jul 11, 2026 12:34pm | Jul 11, 2026 12:34pm | Jul 11, 2026 12:35pm | Jul 11, 2026 12:35pm |  |  | Fair | No | Found ok power was restored
Outage | J.E.26.07.10634 | C001852175 | Cliton Henry | St.Mary | Completed | Load_260286 | Blackstonedge - 110 | Jul 11, 2026 7:20am | Jul 11, 2026 7:23am | Jul 11, 2026 1:06pm | Jul 11, 2026 1:06pm | Jul 11, 2026 1:22pm | Jul 11, 2026 1:45pm | Jul 11, 2026 1:50pm | Jul 11, 2026 1:50pm |  |  | Fair | No | A single phase condition found due to a burnt off service wire phase conductor at pole. The derive wire was reconnected using 1 one bolt clamp. Voltages left were 119-119/238 volts
Outage | J.E.26.07.11079 | C001852174 | Cliton Henry | St.Mary | Completed | Load_259008 | Blackstonedge - 110 | Jul 11, 2026 7:20am | Jul 11, 2026 7:23am | Jul 11, 2026 10:22am | Jul 11, 2026 10:22am | Jul 11, 2026 10:22am | Jul 11, 2026 10:23am | Jul 11, 2026 10:23am | Jul 11, 2026 10:23am |  |  | Fair | No | The customer stated that the supply was restored last night.
Outage | J.E.26.07.12182 | C001852176 | Tajay Bernard | Hanover | Completed | Load_253054 | Orange Bay - 310 | Jul 11, 2026 7:20am | Jul 11, 2026 7:22am | Jul 11, 2026 7:42am | Jul 11, 2026 7:47am | Jul 11, 2026 8:57am | Jul 11, 2026 9:49am | Jul 11, 2026 9:49am | Jul 11, 2026 9:49am |  |  | Fair | No | Premises check and found okay customer has internal problems voltage reading 115/115/230
Non-Outage | J.E.26.07.11813 | C001852173 | Cliton Henry | null | Completed | null | null | Jul 11, 2026 7:19am | Jul 11, 2026 7:23am | Jul 11, 2026 10:31am | Jul 11, 2026 10:31am | Jul 11, 2026 10:31am | Jul 11, 2026 10:32am | Jul 11, 2026 10:32am | Jul 11, 2026 10:32am |  |  | Fair | No | Supply restored last night
Non-Outage | J.E.26.07.12229 | C001852168 | Andre Williams | null | Completed | null | null | Jul 11, 2026 7:19am | Jul 11, 2026 7:20am | Jul 11, 2026 8:13am | Jul 11, 2026 9:54am | Jul 11, 2026 9:54am | Jul 11, 2026 9:54am | Jul 11, 2026 9:55am | Jul 11, 2026 9:55am |  |  | Fair | No | Customer disconnected for none payment
Outage | J.E.26.07.12104 | C001852172 | Cliton Henry | St.Mary | Completed | Load_352622 | Oracabessa - 110 | Jul 11, 2026 7:19am | Jul 11, 2026 7:23am | Jul 11, 2026 8:50am | Jul 11, 2026 8:50am | Jul 11, 2026 9:48am | Jul 11, 2026 10:14am | Jul 11, 2026 10:18am | Jul 11, 2026 10:18am |  |  | Fair | No | The customer service wire found corroded at pole was reconnected using 3 one bolt clamps. Voltages left were 118-119/237 volts
Outage | J.E.26.07.12161 | C001852170 | Floyd Grant | St.Mary | Completed | Load_262319 | Blackstonedge - 110 | Jul 11, 2026 7:19am | Jul 11, 2026 1:43pm | Jul 11, 2026 1:46pm | Jul 11, 2026 1:46pm | Jul 11, 2026 2:34pm | Jul 11, 2026 2:57pm | Jul 11, 2026 3:00pm | Jul 11, 2026 3:00pm |  |  | Fair | Yes | Transformer circuit was moved to another phase of the primary
Outage | J.E.26.07.12223 | C001852169 | Cliton Henry | St.Mary | Completed | Load_262319 | Blackstonedge - 110 | Jul 11, 2026 7:19am | Jul 11, 2026 7:23am | Jul 11, 2026 10:19am | Jul 11, 2026 10:24am | Jul 11, 2026 10:24am | Jul 11, 2026 10:25am | Jul 11, 2026 10:26am | Jul 11, 2026 10:26am |  |  | Fair | No | The customer stated that he live at Brown Town not Waterford
Outage | J.E.26.07.12002 | C001852166 | Richard Samuda | Manchester | Completed | Load_292975 | Spur Tree - 310 | Jul 11, 2026 7:12am | Jul 11, 2026 7:12am | Jul 11, 2026 7:28am | Jul 11, 2026 7:28am | Jul 11, 2026 7:28am | Jul 11, 2026 7:29am | Jul 11, 2026 7:29am | Jul 11, 2026 7:29am |  |  | Fair | No | Customer said power was restored
Outage | J.E.26.07.12101 | C001852165 | Richard Samuda | Manchester | Completed | Load_240206 | Spur Tree - 310 | Jul 11, 2026 7:11am | Jul 11, 2026 7:12am | Jul 11, 2026 1:39pm | Jul 11, 2026 1:39pm | Jul 11, 2026 1:39pm | Jul 11, 2026 1:39pm | Jul 11, 2026 1:40pm | Jul 11, 2026 1:40pm |  |  | SevereWind | No | Found ok power was restored
Outage | J.E.26.07.12149 | C001852164 | Richard Samuda | Manchester | Completed | Load_248110 | Spur Tree - 310 | Jul 11, 2026 7:11am | Jul 11, 2026 7:12am | Jul 11, 2026 9:53am | Jul 11, 2026 10:11am | Jul 11, 2026 10:31am | Jul 11, 2026 11:26am | Jul 11, 2026 11:26am | Jul 11, 2026 11:26am |  |  | SevereWind | No | Found 25kva transformer blown patrol line found nothing replaced fuse customer back to normal
Outage | J.E.26.07.12165 | C001852163 | Richard Samuda | Manchester | Completed | Load_244291 | Spur Tree - 310 | Jul 11, 2026 7:11am | Jul 11, 2026 7:12am | Jul 11, 2026 7:25am | Jul 11, 2026 7:25am | Jul 11, 2026 7:26am | Jul 11, 2026 7:27am | Jul 11, 2026 7:27am | Jul 11, 2026 7:27am |  |  | Fair | No | Customer said they are back to normal
Outage | J.E.26.07.12159 | C001852162 | Richard Samuda | Manchester | Completed | Load_292172 | Spur Tree - 310 | Jul 11, 2026 7:09am | Jul 11, 2026 7:10am | Jul 11, 2026 7:15am | Jul 11, 2026 7:29am | Jul 11, 2026 7:36am | Jul 11, 2026 8:39am | Jul 11, 2026 8:39am | Jul 11, 2026 8:39am |  |  | Fair | No | Found 20 amp junction blown patrol line found 25va transformer patrol line found nothing closed junction then transformer customer back to normal
Outage | J.E.26.07.10614 | C001852155 | Wan Carlos Scarlett | Portmore | Completed | Load_254803 | Naggo Head - 610 | Jul 11, 2026 7:07am | Jul 11, 2026 7:10am | Jul 11, 2026 7:25am | Jul 11, 2026 7:25am | Jul 11, 2026 9:04am | Jul 11, 2026 9:34am | Jul 11, 2026 9:36am | Jul 11, 2026 9:36am |  |  | Fair | No | Found 25KVA transformer defective leaking oil no pole # was found
Outage | J.E.26.07.11137 | C001852160 | Wan Carlos Scarlett | Portmore | Completed | Load_244381 | Naggo Head - 610 | Jul 11, 2026 7:07am | Jul 11, 2026 7:10am | Jul 11, 2026 10:59am | Jul 11, 2026 10:59am | Jul 11, 2026 11:52am | Jul 11, 2026 12:37pm | Jul 11, 2026 12:38pm | Jul 11, 2026 12:38pm |  |  | Fair | No | Found customer 3 wire service with one of the phase broken off use one bolt clamp at open secondary line readings 115-114-230
Outage | J.E.26.07.11744 | C001852159 | Wan Carlos Scarlett | Portmore | Completed | Load_570083 | Naggo Head - 610 | Jul 11, 2026 7:07am | Jul 11, 2026 7:10am | Jul 11, 2026 9:45am | Jul 11, 2026 9:45am | Jul 11, 2026 10:36am | Jul 11, 2026 10:59am | Jul 11, 2026 10:59am | Jul 11, 2026 10:59am |  |  | Fair | No | Customer was reconnected from escalation department power supply has been restored
Outage | J.E.26.07.11894 | C001852158 | Wan Carlos Scarlett | St.Catherine | Completed | Load_576216 | Twickenham - 210 | Jul 11, 2026 7:07am | Jul 11, 2026 7:10am | Jul 11, 2026 12:39pm | Jul 11, 2026 12:39pm | Jul 11, 2026 1:03pm | Jul 11, 2026 2:00pm | Jul 11, 2026 2:02pm | Jul 11, 2026 2:02pm |  |  | Fair | No | Found customer with internal problem advised customer to get a licensed electrician to fix the problem.pothead wire defective
Outage | J.E.26.07.12194 | C001852153 | Swon Miller | St.James | Completed | Load_1002073 | Bogue - 310 | Jul 11, 2026 6:21am | Jul 11, 2026 6:21am | Jul 11, 2026 6:32am | Jul 11, 2026 6:32am | Jul 11, 2026 6:56am | Jul 11, 2026 7:25am | Jul 11, 2026 7:26am | Jul 11, 2026 7:26am |  |  | Fair | No | Found eg fuse blown cause by contamination replace 1.5 in a eg 01105
Outage | J.E.26.07.12191 | C001852151 | Tyrese Williams | St.Ann | Completed | Load_243953 | Ocho Rios - 310 | Jul 11, 2026 6:19am | Jul 11, 2026 11:39am | Jul 11, 2026 11:43am | Jul 11, 2026 12:48pm | Jul 11, 2026 12:48pm | Jul 11, 2026 1:31pm | Jul 11, 2026 1:31pm | Jul 11, 2026 1:31pm |  |  | Fair | No | Refer to maintenance team for rehabilitation and strike force due to multiple illegal connections in area
Outage | J.E.26.07.11963 | C001852149 | Roxroy Needham | St.Ann | Completed | Load_557883 | Roaring River - 410 | Jul 11, 2026 1:03am | Jul 11, 2026 11:44am | Jul 11, 2026 1:56pm | Jul 11, 2026 2:07pm | Jul 11, 2026 2:07pm | Jul 11, 2026 2:08pm | Jul 11, 2026 2:09pm | Jul 11, 2026 2:09pm |  |  | Fair | No | Call customer and customer say light restored from last night
Outage | J.E.26.07.11494 | C001852147 | Swon Miller | St.James | Completed | Load_254132 | Bogue - 610 | Jul 10, 2026 11:36pm | Jul 10, 2026 11:36pm | Jul 11, 2026 2:01am | Jul 11, 2026 2:01am | Jul 11, 2026 2:56am | Jul 11, 2026 3:15am | Jul 11, 2026 3:49am | Jul 11, 2026 3:49am |  |  | Fair | No | Check and found area okay unable to locate customer phone calls to customer number went unanswered
Outage | J.E.26.07.11520 | C001852146 | Swon Miller | St.James | Completed | Load_250782 | Queens Drive - 710 | Jul 10, 2026 11:35pm | Jul 10, 2026 11:35pm | Jul 11, 2026 12:19am | Jul 11, 2026 12:19am | Jul 11, 2026 12:53am | Jul 28, 2026 1:10am | Jul 11, 2026 1:11am | Jul 11, 2026 1:11am |  |  | Fair | No | Check and found area okay unable to locate customer
Outage | J.E.26.07.12032 | C001852145 | Edward Royal | KSAN | Completed | Load_238689 | Hope - 510 | Jul 10, 2026 11:33pm | Jul 10, 2026 11:33pm | Jul 10, 2026 11:38pm | Jul 10, 2026 11:38pm | Jul 10, 2026 11:38pm | Jul 10, 2026 11:39pm | Jul 10, 2026 11:39pm | Jul 10, 2026 11:39pm |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.07.11958 | C001852144 | Edward Royal | KSAN | Completed | Load_248967 | Washington Blvd - 810 | Jul 10, 2026 11:32pm | Jul 10, 2026 11:32pm | Jul 11, 2026 7:03am | Jul 11, 2026 7:03am | Jul 11, 2026 7:03am | Jul 11, 2026 7:03am | Jul 11, 2026 7:03am | Jul 11, 2026 7:03am |  |  | Fair | No | Premises found close
Outage | J.E.26.07.11893 | C001852142 | Delano Gayle | St.Catherine | Completed | Load_256805 | New Michelton - 410 | Jul 10, 2026 11:30pm | Jul 10, 2026 11:31pm | Jul 11, 2026 3:27am | Jul 11, 2026 3:27am | Jul 11, 2026 4:31am | Jul 11, 2026 4:39am | Jul 11, 2026 4:39am | Jul 11, 2026 4:39am |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.10616 | C001852140 | Delano Gayle | St.Catherine | Completed | Load_263287 | Tredegar - 410 | Jul 10, 2026 11:18pm | Jul 10, 2026 11:18pm | Jul 11, 2026 5:28am | Jul 11, 2026 5:28am | Jul 11, 2026 5:47am | Jul 11, 2026 7:06am | Jul 11, 2026 7:06am | Jul 11, 2026 7:06am | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Blown junction no pole#, tree contact, heavy spot bushing replace 10amps
Outage | J.E.26.07.10994 | C001852138 | Delano Gayle | St.Catherine | Completed | Load_250727 | New Michelton - 210 | Jul 10, 2026 11:05pm | Jul 10, 2026 11:06pm | Jul 10, 2026 11:31pm | Jul 10, 2026 11:38pm | Jul 11, 2026 3:01am | Jul 11, 2026 3:26am | Jul 11, 2026 3:26am | Jul 11, 2026 3:26am |  |  | Fair | No | Blown junction no pole number patrolled line section and found okay for closure replace 10amps
Outage | J.E.26.07.11934 | C001852137 | Swon Miller | St.James | Completed | Load_248745 | Bogue - 310 | Jul 10, 2026 11:02pm | Jul 10, 2026 11:04pm | Jul 10, 2026 11:14pm | Jul 10, 2026 11:14pm | Jul 10, 2026 11:35pm | Jul 11, 2026 12:04am | Jul 11, 2026 12:12am | Jul 11, 2026 12:12am |  |  | Fair | No | Found customer single phasing due to contamination at pole voltage found 114 clean and remake joint use 1pg voltage left 115/114/232
Non-Outage | J.E.26.07.11687 | C001852136 | Andre Williams | null | Completed | null | null | Jul 10, 2026 10:59pm | Jul 11, 2026 7:18am | Jul 11, 2026 8:47am | Jul 11, 2026 8:48am | Jul 11, 2026 8:48am | Jul 11, 2026 8:51am | Jul 11, 2026 8:52am | Jul 11, 2026 8:52am |  |  | Fair | No | Multiple Illegal connections in area causing low voltage near end of line voltage 113+90=203 voltage ok up to two pole span from transformer reffer to field service to rectify
Outage | J.E.26.07.12118 | C001852135 | Edward Royal | KSAN | Completed | Load_252236 | Washington Blvd - 310 | Jul 10, 2026 10:52pm | Jul 10, 2026 10:53pm | Jul 11, 2026 12:16am | Jul 11, 2026 12:16am | Jul 11, 2026 12:28am | Jul 11, 2026 12:46am | Jul 11, 2026 12:46am | Jul 11, 2026 12:46am |  |  | Fair | No | Defective 25kva transformer need to be change reffered to bucket truck
Outage | J.E.26.07.11864 | C001852134 | Edward Royal | KSAN | Completed | Load_247699 | Washington Blvd - 310 | Jul 10, 2026 10:51pm | Jul 10, 2026 10:52pm | Jul 11, 2026 7:04am | Jul 11, 2026 7:04am | Jul 11, 2026 7:04am | Jul 11, 2026 7:04am | Jul 11, 2026 7:04am | Jul 11, 2026 7:04am |  |  | Fair | No | Premises not found unable to communicate with customer
Non-Outage | J.E.26.07.12113 | C001852133 | Edward Royal | null | Completed | null | null | Jul 10, 2026 10:46pm | Jul 10, 2026 10:47pm | Jul 11, 2026 1:25am | Jul 11, 2026 1:25am | Jul 11, 2026 1:25am | Jul 11, 2026 1:26am | Jul 11, 2026 1:26am | Jul 11, 2026 1:26am |  |  | Fair | No | Premises not found unable to communicate with customer
Outage | J.E.26.07.11772 | C001852132 | Daniel Francis | St.Ann | Completed | Load_249991 | Roaring River - 210 | Jul 10, 2026 10:26pm | Jul 11, 2026 2:58am | Jul 11, 2026 3:40am | Jul 11, 2026 3:40am | Jul 11, 2026 3:44am | Jul 11, 2026 3:57am | Jul 11, 2026 4:11am | Jul 11, 2026 4:11am |  |  | Fair | No | Found junction blown at Total Energies and scohies
Outage | J.E.26.07.10392 | C001852129 | Tajay Bernard | St.James | Completed | Load_267526 | Bogue - 510 | Jul 10, 2026 9:41pm | Jul 11, 2026 7:51am | Jul 11, 2026 9:49am | Jul 11, 2026 9:49am | Jul 11, 2026 11:24am | Jul 11, 2026 11:58am | Jul 11, 2026 11:59am | Jul 11, 2026 11:59am | Fire |  | Fair | No | Refuse 1 10amp junction fuse
Outage | J.E.26.07.12075 | C001852128 | Swon Miller | St.James | Completed | Load_292055 | Bogue - 310 | Jul 10, 2026 9:41pm | Jul 10, 2026 11:04pm | Jul 11, 2026 1:11am | Jul 11, 2026 1:11am | Jul 11, 2026 1:31am | Jul 11, 2026 1:52am | Jul 11, 2026 2:01am | Jul 11, 2026 2:01am | BrokenPole |  | Fair | No | Found 35ft class6 pole broken for than two weeks with secondary lines cable wires hanging very low across customers gate pole needs replacing plz refer to k.frazer operations
Outage | J.E.26.07.11708 | C001852126 | Gregory Grossett | Portland | Completed | Load_239999 | Port Antonio - 410 | Jul 10, 2026 9:39pm | Jul 10, 2026 9:51pm | Jul 10, 2026 10:10pm | Jul 10, 2026 10:10pm | Jul 10, 2026 10:23pm | Jul 10, 2026 10:24pm | Jul 10, 2026 10:25pm | Jul 10, 2026 10:25pm |  |  | Fair | No | The customer stated that their supply has been restored. Customer okay.
Outage | J.E.26.07.11722 | C001852127 | Collin Robinson | Portland | Completed | Load_257634 | Port Antonio - 310 | Jul 10, 2026 9:39pm | Jul 10, 2026 9:50pm | Jul 10, 2026 10:25pm | Jul 10, 2026 10:25pm | Jul 10, 2026 10:34pm | Jul 10, 2026 10:40pm | Jul 10, 2026 10:40pm | Jul 10, 2026 10:40pm |  |  | Fair | No | Unable to locate customer
Outage | J.E.26.07.12063 | C001852125 | Collin Robinson | Portland | Completed | Load_268118 | Port Antonio - 410 | Jul 10, 2026 9:38pm | Jul 11, 2026 7:24am | Jul 11, 2026 7:56am | Jul 11, 2026 7:56am | Jul 11, 2026 9:19am | Jul 11, 2026 9:20am | Jul 11, 2026 9:20am | Jul 11, 2026 9:20am |  |  | Fair | No | Unable to locate customer
Outage | J.E.26.07.11740 | C001852123 | Stephen Taylor | St.Thomas | Completed | Load_405559 | Lysson - 410 | Jul 10, 2026 9:20pm | Jul 10, 2026 9:29pm | Jul 11, 2026 12:11pm | Jul 11, 2026 6:36pm | Jul 11, 2026 6:37pm | Jul 11, 2026 6:37pm | Jul 11, 2026 6:37pm | Jul 11, 2026 6:37pm |  |  | Fair | No | Need more information
Outage | J.E.26.07.12056 | C001852121 | Stephen Taylor | St.Thomas | Completed | Load_267178 | Lysson - 410 | Jul 10, 2026 9:15pm | Jul 10, 2026 9:29pm | Jul 11, 2026 11:34am | Jul 11, 2026 11:34am | Jul 11, 2026 11:34am | Jul 11, 2026 11:34am | Jul 11, 2026 11:34am | Jul 11, 2026 11:34am |  |  | Fair | No | Transformer link down and click was made and found out that 25 kva transformer defective and need to change by the jps maintenance team
Outage | J.E.26.07.11818 | C001852120 | Hopeton Henry | St.Thomas | Completed | Load_243194 | Good Year - 210 | Jul 10, 2026 9:13pm | Jul 10, 2026 9:30pm | Jul 10, 2026 9:58pm | Jul 11, 2026 11:10am | Jul 11, 2026 11:10am | Jul 11, 2026 11:10am | Jul 11, 2026 11:11am | Jul 11, 2026 11:11am |  |  | Fair | No | Found ok , power restored
Outage | J.E.26.07.11845 | C001852119 | Stephen Taylor | St.Thomas | Completed | Load_264975 | Lysson - 410 | Jul 10, 2026 9:12pm | Jul 10, 2026 9:29pm | Jul 11, 2026 7:25am | Jul 11, 2026 7:25am | Jul 11, 2026 7:25am | Jul 11, 2026 7:25am | Jul 11, 2026 7:26am | Jul 11, 2026 7:26am |  |  | Fair | No | Call to customer and customer said power is back on okay from last night
Outage | J.E.26.07.11851 | C001852118 | Hopeton Henry | St.Thomas | Completed | Load_238855 | Good Year - 210 | Jul 10, 2026 9:12pm | Jul 10, 2026 9:30pm | Jul 10, 2026 9:58pm | Jul 11, 2026 9:19am | Jul 11, 2026 10:40am | Jul 11, 2026 11:07am | Jul 11, 2026 11:10am | Jul 11, 2026 11:10am |  |  | Fair | No | Issue unresolved, refer to maintenance department, drop out link blowing every day
Outage | J.E.26.07.11866 | C001852117 | Stephen Taylor | St.Thomas | Completed | Load_254105 | Lysson - 410 | Jul 10, 2026 9:12pm | Jul 10, 2026 9:29pm | Jul 11, 2026 2:21pm | Jul 11, 2026 4:25pm | Jul 11, 2026 4:26pm | Jul 11, 2026 4:26pm | Jul 11, 2026 4:26pm | Jul 11, 2026 4:26pm | Fire |  | Fair | No | Premise found okay
Outage | J.E.26.07.11736 | C001852116 | Rusean Allen | KSAS | Completed | Load_257789 | Hunts Bay - 310 | Jul 10, 2026 9:11pm | Jul 10, 2026 9:11pm | Jul 10, 2026 9:26pm | Jul 10, 2026 9:26pm | Jul 10, 2026 10:04pm | Jul 10, 2026 10:26pm | Jul 10, 2026 10:26pm | Jul 10, 2026 10:26pm |  |  | Fair | No | Premises okay
Outage | J.E.26.07.12053 | C001852115 | Milton Charlton | KSAS | Completed | Load_576839 | Up Park Camp - 510 | Jul 10, 2026 9:08pm | Jul 10, 2026 9:11pm | Jul 10, 2026 9:41pm | Jul 10, 2026 9:41pm | Jul 10, 2026 10:11pm | Jul 10, 2026 10:25pm | Jul 10, 2026 10:45pm | Jul 10, 2026 10:45pm |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.07.11538 | C001852114 | Eric Williams | KSAS | Completed | Load_255768 | Hunts Bay - 310 | Jul 10, 2026 9:05pm | Jul 10, 2026 9:05pm | Jul 10, 2026 9:31pm | Jul 10, 2026 9:31pm | Jul 10, 2026 10:05pm | Jul 10, 2026 10:10pm | Jul 10, 2026 10:11pm | Jul 10, 2026 10:11pm |  |  | Fair | No | Premises found okay, customer stated there breaker trip,
Non-Outage | J.E.26.07.11689 | C001852113 | Evan Spaulding | null | Completed | null | null | Jul 10, 2026 9:04pm | Jul 10, 2026 9:05pm | Jul 10, 2026 9:53pm | Jul 10, 2026 9:53pm | Jul 10, 2026 9:53pm | Jul 10, 2026 9:53pm | Jul 10, 2026 9:54pm | Jul 10, 2026 9:54pm | BrokenWire |  | Fair | No | Customer says issue was resolved.
Outage | J.E.26.07.12046 | C001852112 | Raymond Carr | St.Mary | Completed | Load_252727 | Oracabessa - 110 | Jul 10, 2026 9:03pm | Jul 10, 2026 9:46pm | Jul 10, 2026 10:03pm | Jul 10, 2026 10:03pm | Jul 10, 2026 11:15pm | Jul 10, 2026 10:00am | Jul 10, 2026 11:17pm | Jul 10, 2026 11:17pm |  |  | Fair | No | Customer couldn’t be contacted,
Outage | J.E.26.07.12018 | C001852108 | Lancelot Brown | Hanover | Completed | Load_269202 | Orange Bay - 310 | Jul 10, 2026 8:53pm | Jul 10, 2026 8:56pm | Jul 10, 2026 9:14pm | Jul 10, 2026 9:15pm | Jul 10, 2026 10:18pm | Jul 10, 2026 10:48pm | Jul 10, 2026 10:48pm | Jul 10, 2026 10:48pm | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Isolate 50kva no pole number replace burnt off dropleed used seven feet 2/0 copper one pg clamp energise 50kva supply restore voltage leave at secondary 117-117-234
Outage | J.E.26.07.11950 | C001852104 | Daniel Francis | St.Ann | Completed | Load_269248 | Roaring River - 410 | Jul 10, 2026 8:39pm | Jul 11, 2026 1:15am | Jul 11, 2026 1:41am | Jul 11, 2026 1:41am | Jul 11, 2026 1:53am | Jul 11, 2026 2:49am | Jul 11, 2026 2:55am | Jul 11, 2026 2:55am | Fire |  | Fair | No | Found secondary making contact with flow strand cables open bank of two transformer pole # 0121171 and retention 2span of secondary phase conducter
Outage | J.E.26.07.12017 | C001852099 | Raymond Carr | St.Mary | Completed | Load_256173 | Oracabessa - 210 | Jul 10, 2026 8:30pm | Jul 10, 2026 8:31pm | Jul 10, 2026 9:28pm | Jul 10, 2026 9:29pm | Jul 10, 2026 10:01pm | Jul 10, 2026 9:46pm | Jul 10, 2026 10:02pm | Jul 10, 2026 10:02pm |  |  | Fair | No | Several calls to contact number went straight to voicemail.
Outage | J.E.26.07.10256 | C001852095 | Ricky Hall | St.Catherine | Completed | Load_256389 | Rhodens Pen - 210 | Jul 10, 2026 8:24pm | Jul 10, 2026 8:25pm | Jul 11, 2026 8:56am | Jul 11, 2026 11:13am | Jul 11, 2026 11:13am | Jul 11, 2026 11:13am | Jul 11, 2026 11:13am | Jul 11, 2026 11:13am | BrokenWire |  | Fair | No | Call associated with outage #11247
Outage | J.E.26.07.11887 | C001852088 | Richard Samuda | Manchester | Completed | Load_259688 | Spur Tree - 310 | Jul 10, 2026 8:06pm | Jul 11, 2026 2:34pm | Jul 11, 2026 3:23pm | Jul 11, 2026 3:23pm | Jul 11, 2026 4:10pm | Jul 11, 2026 4:48pm | Jul 11, 2026 4:48pm | Jul 11, 2026 4:48pm |  |  | SevereWind | No | Found 25 kva transformer blown patrol line found nothing replaced fuse customer back
Outage | J.E.26.07.11966 | C001852087 | Raymond Lewis | St.Ann | Completed | Load_267783 | Roaring River - 210 | Jul 10, 2026 8:06pm | Jul 10, 2026 8:06pm | Jul 10, 2026 9:01pm | Jul 10, 2026 9:01pm | Jul 10, 2026 10:10pm | Jul 10, 2026 11:02pm | Jul 10, 2026 11:03pm | Jul 10, 2026 11:03pm |  |  | SevereWind | No | Remove tree from primary but tree need to be cut from secondary bucket truck unable to reach but customer is left with supply and refuse and close 15 amp junction
Outage | J.E.26.07.11732 | C001852085 | Andre Williams | Trelawny | Completed | Load_292442 | Greenwood - 210 | Jul 10, 2026 7:59pm | Jul 10, 2026 8:56pm | Jul 10, 2026 9:14pm | Jul 10, 2026 9:52pm | Jul 10, 2026 9:57pm | Jul 10, 2026 9:57pm | Jul 10, 2026 11:04pm | Jul 10, 2026 11:04pm |  |  | Fair | No | Premises ok and with supply.
Outage | J.E.26.07.11940 | C001852084 | Oshane Warren | Westmoreland | Completed | Load_257268 | Paradise - 210 | Jul 10, 2026 7:58pm | Jul 10, 2026 7:59pm | Jul 10, 2026 9:35pm | Jul 10, 2026 9:35pm | Jul 10, 2026 11:13pm | Jul 10, 2026 11:17pm | Jul 10, 2026 11:18pm | Jul 10, 2026 11:18pm | BrokenWire |  | Rains | No | Open 25 kva xformer and splice and retention 1 spand secondary conductor
Outage | J.E.26.07.10597 | C001852083 | Selvin White | St.Elizabeth | Completed | Load_249402 | Maggotty - 110 | Jul 10, 2026 7:57pm | Jul 10, 2026 8:25pm | Jul 10, 2026 8:58pm | Jul 10, 2026 9:38pm | Jul 10, 2026 9:54pm | Jul 10, 2026 10:00pm | Jul 10, 2026 10:01pm | Jul 10, 2026 10:01pm |  |  | Fair | No | Daylight attention is needed due to poor lighting and busy roadway and conductor to string across roadway. Please refer to the morning crew.
Non-Outage | J.E.26.07.11842 | C001852073 | Christopher Edwards | KSAN | Completed | Load_257186 | Constant Spring - 410 | Jul 10, 2026 7:43pm | Jul 10, 2026 7:43pm | Jul 10, 2026 8:07pm | Jul 10, 2026 8:07pm | Jul 10, 2026 9:01pm | Jul 10, 2026 9:49pm | Jul 10, 2026 9:50pm | Jul 10, 2026 9:50pm |  |  | Fair | No | Required daylight attention Unable to access transformer poleDue to thick vegetation
Outage | J.E.26.07.11300 | C001852066 | Michael Christian | St.James | Completed | Load_250268 | Queens Drive - 710 | Jul 10, 2026 7:34pm | Jul 10, 2026 7:35pm | Jul 11, 2026 10:14am | Jul 11, 2026 10:14am | Jul 11, 2026 10:33am | Jul 11, 2026 11:21am | Jul 11, 2026 11:21am | Jul 11, 2026 11:21am |  |  | Fair | No | Internal fault
Outage | J.E.26.07.11384 | C001852063 | Milton Charlton | KSAS | Completed | Load_248613 | Hunts Bay - 310 | Jul 10, 2026 7:31pm | Jul 10, 2026 7:36pm | Jul 10, 2026 8:37pm | Jul 10, 2026 8:37pm | Jul 10, 2026 9:05pm | Jul 10, 2026 9:10pm | Jul 10, 2026 9:06pm | Jul 10, 2026 9:06pm |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.07.10928 | C001852062 | Ricky Hall | St.Catherine | Completed | Load_406084 | Rhodens Pen - 210 | Jul 10, 2026 7:27pm | Jul 10, 2026 7:27pm | Jul 11, 2026 2:30pm | Jul 11, 2026 2:30pm | Jul 11, 2026 2:58pm | Jul 11, 2026 2:59pm | Jul 11, 2026 2:59pm | Jul 11, 2026 2:59pm |  |  | Fair | No | Premises not located due to incorrect details
Outage | J.E.26.07.11247 | C001852061 | Ricky Hall | St.Catherine | Completed | Load_251630 | Rhodens Pen - 410 | Jul 10, 2026 7:27pm | Jul 10, 2026 7:27pm | Jul 11, 2026 8:57am | Jul 11, 2026 9:34am | Jul 11, 2026 10:40am | Jul 11, 2026 11:12am | Jul 11, 2026 11:12am | Jul 11, 2026 11:12am | BrokenWire |  | Fair | No | Splice and retention broken secondary phase conductor use 1 automatic splice
Outage | J.E.26.07.11860 | C001852059 | Ricky Hall | St.Catherine | Completed | Load_260736 | Rhodens Pen - 410 | Jul 10, 2026 7:25pm | Jul 10, 2026 7:25pm | Jul 10, 2026 9:38pm | Jul 10, 2026 9:38pm | Jul 10, 2026 10:24pm | Jul 10, 2026 10:33pm | Jul 10, 2026 10:34pm | Jul 10, 2026 10:34pm |  |  | Fair | No | Issue was resolved previously
Non-Outage | J.E.26.07.11788 | C001852058 | Michael Christian | St.James | Completed | Load_248976 | Queens Drive - 710 | Jul 10, 2026 7:24pm | Jul 10, 2026 7:25pm | Jul 10, 2026 10:07pm | Jul 10, 2026 10:10pm | Jul 10, 2026 10:27pm | Jul 10, 2026 10:28pm | Jul 10, 2026 10:28pm | Jul 10, 2026 10:28pm | Fire |  | Fair | No | Check and found okay no fire found
Non-Outage | J.E.26.07.11916 | C001852057 | Raymond Lewis | null | Completed | null | null | Jul 10, 2026 7:24pm | Jul 10, 2026 7:24pm | Jul 11, 2026 12:59pm | Jul 11, 2026 12:59pm | Jul 11, 2026 2:52pm | Jul 11, 2026 2:56pm | Jul 11, 2026 2:56pm | Jul 11, 2026 2:56pm | BrokenPole |  | SevereWind | No | Open 25kva x former to open secondary jumper due to tree fall on line one 30 ft pole dead end and over head pole
Outage | J.E.26.07.11879 | C001852055 | Michael Christian | St.James | Completed | Load_264164 | Queens Drive - 310 | Jul 10, 2026 7:22pm | Jul 10, 2026 7:25pm | Jul 10, 2026 10:08pm | Jul 10, 2026 10:08pm | Jul 10, 2026 10:08pm | Jul 10, 2026 10:09pm | Jul 10, 2026 10:09pm | Jul 10, 2026 10:09pm | Fire |  | Fair | No | Check and found okay
Outage | J.E.26.07.11888 | C001852050 | Horace Malcolm | St.James | Completed | Load_244546 | Bogue - 310 | Jul 10, 2026 7:19pm | Jul 10, 2026 7:20pm | Jul 10, 2026 8:59pm | Jul 10, 2026 10:04pm | Jul 10, 2026 10:04pm | Jul 10, 2026 11:05pm | Jul 10, 2026 11:06pm | Jul 10, 2026 11:06pm |  |  | SevereWind | No | Check and found one 50 kva transformer defective
Outage | J.E.26.07.11541 | C001852049 | Michael Christian | St.James | Completed | Load_263606 | Queens Drive - 310 | Jul 10, 2026 7:18pm | Jul 10, 2026 7:20pm | Jul 10, 2026 9:55pm | Jul 10, 2026 9:55pm | Jul 10, 2026 10:08pm | Jul 10, 2026 10:08pm | Jul 10, 2026 10:08pm | Jul 10, 2026 10:08pm |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.11672 | C001852044 | Ricky Hall | St.Catherine | Completed | Load_289138 | Rhodens Pen - 210 | Jul 10, 2026 7:08pm | Jul 10, 2026 7:08pm | Jul 10, 2026 7:19pm | Jul 10, 2026 7:20pm | Jul 10, 2026 7:20pm | Jul 10, 2026 7:22pm | Jul 10, 2026 7:22pm | Jul 10, 2026 7:22pm |  |  | Fair | No | Replaced 2 blown 50 amps junction fuse
Outage | J.E.26.07.10216 | C001852040 | Donald Cunningham | St.Catherine | Completed | Load_262911 | Tredegar - 510 | Jul 10, 2026 7:04pm | Jul 10, 2026 7:05pm | Jul 10, 2026 7:45pm | Jul 10, 2026 7:45pm | Jul 10, 2026 8:18pm | Jul 10, 2026 8:18pm | Jul 10, 2026 8:26pm | Jul 10, 2026 8:26pm | LowHangingWires |  | Fair | No | No low wire seen customer not reachable
Outage | J.E.26.07.10522 | C001852038 | Donald Cunningham | St.Catherine | Completed | Load_246786 | Tredegar - 410 | Jul 10, 2026 7:04pm | Jul 10, 2026 7:05pm | Jul 10, 2026 10:04pm | Jul 10, 2026 10:04pm | Jul 10, 2026 10:46pm | Jul 10, 2026 10:46pm | Jul 10, 2026 10:51pm | Jul 10, 2026 10:51pm | TreeContact |  | Fair | No | Bushing crew required
Outage | J.E.26.07.10616 | C001852039 | Donald Cunningham | St.Catherine | Completed | Load_263287 | Tredegar - 410 | Jul 10, 2026 7:04pm | Jul 10, 2026 7:05pm | Jul 10, 2026 9:34pm | Jul 10, 2026 9:34pm | Jul 10, 2026 9:57pm | Jul 10, 2026 10:02pm | Jul 10, 2026 10:04pm | Jul 10, 2026 10:04pm | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Rotten and broken pole top lap need to replace bucket truck required with pole tap lap
Outage | J.E.26.07.11823 | C001852037 | Donald Cunningham | St.Catherine | Completed | Load_254572 | Tredegar - 210 | Jul 10, 2026 7:04pm | Jul 10, 2026 7:05pm | Jul 10, 2026 8:27pm | Jul 10, 2026 8:27pm | Jul 10, 2026 9:02pm | Jul 10, 2026 9:04pm | Jul 10, 2026 9:34pm | Jul 10, 2026 9:34pm |  |  | Fair | No | Rami system need to be checked refer to mr Ellison urgently customer medication on fridge
Outage | J.E.26.07.11355 | C001852036 | Ricky Hall | St.Catherine | Completed | Load_289138 | Rhodens Pen - 210 | Jul 10, 2026 7:03pm | Jul 10, 2026 7:04pm | Jul 10, 2026 7:19pm | Jul 10, 2026 7:22pm | Jul 10, 2026 7:22pm | Jul 10, 2026 7:22pm | Jul 10, 2026 7:23pm | Jul 10, 2026 7:23pm |  |  | Fair | No | Call associated with outage #11672
Non-Outage | J.E.26.07.11695 | C001852033 | Damion Reid | null | Completed | null | null | Jul 10, 2026 6:58pm | Jul 10, 2026 6:58pm | Jul 10, 2026 8:49pm | Jul 10, 2026 8:49pm | Jul 10, 2026 8:55pm | Jul 10, 2026 9:45pm | Jul 10, 2026 9:48pm | Jul 10, 2026 9:48pm | Fire |  | SevereWind | No | Blown 2amp fuse found for 25kva transformer cause by banging secondary phase an neutral conductor line patrol replace 2/0 preform and blown fuse
Outage | J.E.26.07.11676 | C001852027 | Marlon Brown | Trelawny | Completed | Load_267431 | Duncans - 210 | Jul 10, 2026 6:51pm | Jul 10, 2026 6:52pm | Jul 10, 2026 7:43pm | Jul 10, 2026 7:43pm | Jul 10, 2026 8:59pm | Jul 10, 2026 9:00pm | Jul 10, 2026 9:00pm | Jul 10, 2026 9:00pm |  |  | Fair | No | Reset 10kva transformer
Outage | J.E.26.07.11729 | C001852026 | Oshane Warren | Westmoreland | Completed | Load_239357 | Paradise - 210 | Jul 10, 2026 6:51pm | Jul 10, 2026 6:52pm | Jul 10, 2026 9:34pm | Jul 10, 2026 9:34pm | Jul 10, 2026 9:34pm | Jul 10, 2026 9:35pm | Jul 10, 2026 9:35pm | Jul 10, 2026 9:35pm |  |  | Rains | No | Check and find ok
Outage | J.E.26.07.11840 | C001852022 | Omar King | St.Ann | Completed | null | null | Jul 10, 2026 6:47pm | Jul 10, 2026 6:48pm | Jul 10, 2026 7:43pm | Jul 10, 2026 7:43pm | Jul 10, 2026 7:54pm | Jul 10, 2026 10:28pm | Jul 10, 2026 10:28pm | Jul 10, 2026 10:28pm |  |  | Fair | No | Found two span of secondary phase broken as been repaired customer is now with supply
Non-Outage | J.E.26.07.11386 | C001852008 | Kemark Slue | null | Completed | null | null | Jul 10, 2026 6:44pm | Jul 10, 2026 6:45pm | Jul 10, 2026 10:20pm | Jul 10, 2026 10:20pm | Jul 10, 2026 10:20pm | Jul 10, 2026 9:00pm | Jul 10, 2026 10:21pm | Jul 10, 2026 10:21pm | BrokenWire |  | Fair | No | Premises was checked and found okay.
Outage | J.E.26.07.10457 | C001852007 | Kemark Slue | St.Catherine | Completed | Load_252984 | Twickenham - 210 | Jul 10, 2026 6:44pm | Jul 10, 2026 6:45pm | Jul 10, 2026 8:18pm | Jul 10, 2026 8:26pm | Jul 10, 2026 9:05pm | Jul 10, 2026 8:35pm | Jul 10, 2026 10:19pm | Jul 10, 2026 10:19pm | Fire |  | Fair | No | Upon arrival at the location the crew didn’t see any form of electrical fire, all calls to number given were futile however area is with supply.
Outage | J.E.26.07.10715 | C001852009 | Kemark Slue | St.Catherine | Completed | Load_261722 | Twickenham - 210 | Jul 10, 2026 6:44pm | Jul 10, 2026 6:45pm | Jul 10, 2026 7:41pm | Jul 10, 2026 7:41pm | Jul 10, 2026 8:24pm | Jul 10, 2026 8:25pm | Jul 10, 2026 8:26pm | Jul 10, 2026 8:26pm | BrokenWire |  | Fair | No | Premises was checked and found okay, broken conductor that customer is making reference is on the load side, the electrician on site was advised.
Outage | J.E.26.07.11740 | C001851996 | Stephen Taylor | St.Thomas | Completed | Load_405559 | Lysson - 410 | Jul 10, 2026 6:21pm | Jul 10, 2026 6:28pm | Jul 10, 2026 7:33pm | Jul 10, 2026 7:33pm | Jul 10, 2026 7:33pm | Jul 10, 2026 7:35pm | Jul 10, 2026 7:35pm | Jul 10, 2026 7:35pm |  |  | Fair | No | Check with customer and say power is back and they are now ok
Outage | J.E.26.07.11715 | C001851995 | Hopeton Henry | St.Thomas | Completed | Load_242327 | Good Year - 210 | Jul 10, 2026 6:20pm | Jul 10, 2026 6:29pm | Jul 10, 2026 8:07pm | Jul 10, 2026 8:07pm | Jul 10, 2026 8:59pm | Jul 10, 2026 9:10pm | Jul 10, 2026 9:10pm | Jul 10, 2026 9:10pm |  |  | Fair | No | Check and found ok
Non-Outage | J.E.26.07.11701 | C001851994 | Kaydon Taylor | null | Completed | null | null | Jul 10, 2026 6:12pm | Jul 10, 2026 6:13pm | Jul 10, 2026 8:33pm | Jul 10, 2026 8:38pm | Jul 10, 2026 10:03pm | Jul 10, 2026 10:05pm | Jul 10, 2026 10:05pm | Jul 10, 2026 10:05pm | Fire |  | Fair | No | Found okay
Outage | J.E.26.07.11199 | C001851982 | Michael Christian | St.James | Completed | Load_259518 | Queens Drive - 710 | Jul 10, 2026 6:01pm | Jul 10, 2026 6:10pm | Jul 11, 2026 12:59pm | Jul 11, 2026 12:59pm | Jul 11, 2026 1:34pm | Jul 11, 2026 1:43pm | Jul 11, 2026 1:43pm | Jul 11, 2026 1:43pm |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.11165 | C001851981 | Michael Christian | St.James | Completed | Load_265992 | Queens Drive - 710 | Jul 10, 2026 6:00pm | Jul 10, 2026 6:10pm | Jul 10, 2026 9:33pm | Jul 10, 2026 9:33pm | Jul 10, 2026 9:51pm | Jul 10, 2026 9:53pm | Jul 10, 2026 9:53pm | Jul 10, 2026 9:53pm |  |  | Fair | No | Check and found voltage 110 109 221 at meter
Outage | J.E.26.07.11475 | C001851979 | Michael Christian | St.James | Completed | Load_264164 | Queens Drive - 310 | Jul 10, 2026 6:00pm | Jul 10, 2026 6:10pm | Jul 10, 2026 7:48pm | Jul 10, 2026 7:48pm | Jul 10, 2026 8:24pm | Jul 10, 2026 8:45pm | Jul 10, 2026 8:45pm | Jul 10, 2026 8:45pm | Q |  | Fair | No | Found 1 20 amp out and 1 15 amp cause by bird replace 1 20 1 2 amp
Outage | J.E.26.07.11479 | C001851980 | Michael Christian | St.James | Completed | Load_248507 | Queens Drive - 710 | Jul 10, 2026 6:00pm | Jul 10, 2026 6:10pm | Jul 10, 2026 10:28pm | Jul 10, 2026 10:28pm | Jul 10, 2026 10:41pm | Jul 10, 2026 10:57pm | Jul 10, 2026 10:57pm | Jul 10, 2026 10:57pm |  |  | Fair | No | Replace 1 clamp at customer service wire at pole voltage 110 109 221 at pothead
Outage | J.E.26.07.11582 | C001851977 | Ricky Hall | St.Catherine | Completed | Load_1000334 | Tredegar - 210 | Jul 10, 2026 6:00pm | Jul 10, 2026 6:03pm | Jul 10, 2026 7:25pm | Jul 10, 2026 7:25pm | Jul 10, 2026 8:48pm | Jul 10, 2026 9:37pm | Jul 10, 2026 9:37pm | Jul 10, 2026 9:37pm |  |  | Fair | No | Repair slack 3W service at pole use 3 clamps 17/117/235
Outage | J.E.26.07.11698 | C001851978 | Michael Christian | St.James | Completed | Load_263808 | Rose Hall - 210 | Jul 10, 2026 6:00pm | Jul 10, 2026 6:02pm | Jul 10, 2026 6:57pm | Jul 10, 2026 6:57pm | Jul 10, 2026 7:40pm | Jul 10, 2026 7:47pm | Jul 10, 2026 7:48pm | Jul 10, 2026 7:48pm | BrokenPole |  | Fair | No | Found 1 30 ft pole broken down open 1 25 kava needed 1 30 ft pole
Outage | J.E.26.07.11260 | C001851975 | Milton Charlton | KSAS | Completed | Load_246230 | Up Park Camp - 410 | Jul 10, 2026 5:59pm | Jul 10, 2026 6:06pm | Jul 10, 2026 7:22pm | Jul 10, 2026 7:22pm | Jul 10, 2026 7:34pm | Jul 10, 2026 7:40pm | Jul 10, 2026 7:38pm | Jul 10, 2026 7:38pm |  |  | Fair | No | Found one 5 amps transformer fuse blown at pole #0098089. Refused using one 5 amps fuse and reclosed transformer switch.
Outage | J.E.26.07.11536 | C001851974 | Kaydon Taylor | KSAN | Completed | Load_301911 | Constant Spring - 210 | Jul 10, 2026 5:59pm | Jul 10, 2026 6:06pm | Jul 10, 2026 7:20pm | Jul 10, 2026 8:30pm | Jul 10, 2026 8:30pm | Jul 10, 2026 8:31pm | Jul 10, 2026 8:31pm | Jul 10, 2026 8:31pm |  |  | Fair | No | Premises closed
Outage | J.E.26.07.11663 | C001851976 | Christopher Edwards | KSAN | Completed | Load_243434 | Constant Spring - 410 | Jul 10, 2026 5:59pm | Jul 10, 2026 6:05pm | Jul 10, 2026 9:50pm | Jul 10, 2026 9:50pm | Jul 10, 2026 10:44pm | Jul 10, 2026 10:55pm | Jul 10, 2026 10:57pm | Jul 10, 2026 10:57pm |  |  | Fair | No | Refuse blown 50 kva transformer Using (1) 5 amps
Non-Outage | J.E.26.07.11015 | C001851972 | Tyrese Williams | null | Completed | null | null | Jul 10, 2026 5:50pm | Jul 11, 2026 4:31pm | Jul 11, 2026 4:35pm | Jul 11, 2026 5:33pm | Jul 11, 2026 5:34pm | Jul 11, 2026 5:36pm | Jul 11, 2026 5:36pm | Jul 11, 2026 5:36pm | Fire |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.07.10555 | C001851971 | Kaydon Taylor | KSAN | Completed | Load_240558 | Washington Blvd - 510 | Jul 10, 2026 5:49pm | Jul 10, 2026 5:53pm | Jul 10, 2026 5:57pm | Jul 10, 2026 5:57pm | Jul 10, 2026 6:21pm | Jul 10, 2026 7:16pm | Jul 10, 2026 7:16pm | Jul 10, 2026 7:16pm |  |  | Fair | No | Bank of 3 transformer two 1 100kva and two 50 kva transformer. Two 50kva transformer fuse found blown and replace
Outage | J.E.26.07.10895 | C001851965 | Evan Spaulding | St.Mary | Completed | Load_249898 | Highgate - 210 | Jul 10, 2026 5:37pm | Jul 10, 2026 5:39pm | Jul 10, 2026 8:50pm | Jul 10, 2026 8:50pm | Jul 10, 2026 8:50pm | Jul 10, 2026 8:50pm | Jul 10, 2026 8:50pm | Jul 10, 2026 8:50pm |  |  | Fair | No | Customer says power was restored.
Outage | J.E.26.07.11178 | C001851964 | Richman Whyte | Westmoreland | Completed | Load_259377 | Paradise - 310 | Jul 10, 2026 5:36pm | Jul 10, 2026 6:51pm | Jul 10, 2026 7:15pm | Jul 10, 2026 7:15pm | Jul 10, 2026 7:15pm | Jul 10, 2026 7:21pm | Jul 10, 2026 7:21pm | Jul 10, 2026 7:21pm |  |  | Fair | No | Replace two twenty amp junction fuse
Outage | J.E.26.07.11636 | C001851963 | Gregory Grossett | Portland | Completed | Load_257113 | Port Antonio - 410 | Jul 10, 2026 5:29pm | Jul 10, 2026 5:32pm | Jul 10, 2026 6:42pm | Jul 10, 2026 6:42pm | Jul 10, 2026 6:42pm | Jul 10, 2026 6:43pm | Jul 10, 2026 6:45pm | Jul 10, 2026 6:45pm |  |  | Fair | No | Check and found Mill Bank police station okay
Outage | J.E.26.07.11665 | C001851962 | Gregory Grossett | Portland | Completed | Load_239047 | Port Antonio - 410 | Jul 10, 2026 5:29pm | Jul 10, 2026 5:32pm | Jul 10, 2026 6:47pm | Jul 10, 2026 6:47pm | Jul 10, 2026 8:09pm | Jul 10, 2026 8:09pm | Jul 10, 2026 8:10pm | Jul 10, 2026 8:10pm |  |  | Fair | No | After calling the customer he said the power came back
Outage | J.E.26.07.09082 | C001851961 | Cliton Henry | St.Mary | Completed | Load_354886 | Blackstonedge - 110 | Jul 10, 2026 5:26pm | Jul 10, 2026 5:27pm | Jul 10, 2026 6:35pm | Jul 10, 2026 6:35pm | Jul 10, 2026 6:52pm | Jul 10, 2026 7:03pm | Jul 10, 2026 7:04pm | Jul 10, 2026 7:04pm |  |  | Fair | No | A blown 7 amp junction fuse found at pole #596567 due tree contact. The branches were removed and supply restored using 1-7 amp fuse.
Outage | J.E.26.07.11667 | C001851960 | Stephen Taylor | St.Thomas | Completed | Load_238021 | Lysson - 410 | Jul 10, 2026 5:26pm | Jul 10, 2026 5:55pm | Jul 10, 2026 6:53pm | Jul 10, 2026 6:53pm | Jul 10, 2026 6:53pm | Jul 10, 2026 6:55pm | Jul 10, 2026 6:57pm | Jul 10, 2026 6:57pm |  |  | Fair | No | Splice and retention secondary wire with 6one bolt clamp and 60 feet of wire customer are now back in service
Outage | J.E.26.07.11670 | C001851959 | Hopeton Henry | St.Thomas | Completed | Load_238731 | Good Year - 210 | Jul 10, 2026 5:25pm | Jul 10, 2026 5:27pm | Jul 10, 2026 5:43pm | Jul 10, 2026 5:43pm | Jul 10, 2026 5:43pm | Jul 10, 2026 5:45pm | Jul 10, 2026 5:45pm | Jul 10, 2026 5:45pm |  |  | Fair | No | Found ok , power restored
Non-Outage | J.E.26.07.11594 | C001851952 | Rusean Allen | KSAS | Completed | Load_255768 | Hunts Bay - 310 | Jul 10, 2026 5:12pm | Jul 10, 2026 5:22pm | Jul 10, 2026 8:14pm | Jul 10, 2026 8:14pm | Jul 10, 2026 8:21pm | Jul 10, 2026 8:46pm | Jul 10, 2026 8:46pm | Jul 10, 2026 8:46pm |  |  | Fair | No | Broken service wire found, wire was spliced and reconnected.50KVA transformer pushing out high voltage and needs to be checked.Refer to in-house team. Voltage: 125 125 250
Outage | J.E.26.07.11556 | C001851950 | Selvin White | St.Elizabeth | Completed | Load_259919 | Maggotty - 110 | Jul 10, 2026 5:10pm | Jul 10, 2026 5:10pm | Jul 10, 2026 7:30pm | Jul 10, 2026 7:31pm | Jul 10, 2026 7:37pm | Jul 10, 2026 8:49pm | Jul 10, 2026 8:52pm | Jul 10, 2026 8:52pm |  |  | Fair | No | Replace a defective 2 amp fuse for a 25 KVA transformer circuit at pole number 025197 after patrolling. Supply restored to the affected customers.
Outage | J.E.26.07.11583 | C001851951 | Andrew Powell | St.Elizabeth | Completed | Load_262656 | Maggotty - 210 | Jul 10, 2026 5:10pm | Jul 10, 2026 5:11pm | Jul 10, 2026 5:49pm | Jul 10, 2026 5:49pm | Jul 10, 2026 6:05pm | Jul 10, 2026 7:09pm | Jul 10, 2026 7:12pm | Jul 10, 2026 7:12pm | BrokenWire |  | SevereWind | No | Replace broken service wire using 30 feet #6 triplex, three clamps and three service sleeves, voltage reading 112v-114v phase to neutral 226v cross phase, meter #2838631.
Outage | J.E.26.07.11630 | C001851948 | Andre Williams | Trelawny | Completed | Load_262472 | Greenwood - 110 | Jul 10, 2026 5:01pm | Jul 10, 2026 5:06pm | Jul 10, 2026 5:45pm | Jul 10, 2026 5:45pm | Jul 10, 2026 6:51pm | Jul 10, 2026 7:01pm | Jul 10, 2026 7:05pm | Jul 10, 2026 7:05pm | BrokenWire |  | Fair | No | Remake burnt off neutral on customer 3 wire service at Jps pole voltage 113+114=227
Outage | J.E.26.07.10821 | C001851944 | Eric Williams | KSAN | Completed | Load_243825 | Washington Blvd - 310 | Jul 10, 2026 4:45pm | Jul 10, 2026 5:02pm | Jul 10, 2026 5:45pm | Jul 10, 2026 5:45pm | Jul 10, 2026 7:49pm | Jul 10, 2026 8:50pm | Jul 10, 2026 8:52pm | Jul 10, 2026 8:52pm | Fire |  | Fair | No | Defective 10KVA replace by 15kva transformer and 2amps fuse
Outage | J.E.26.07.10894 | C001851942 | Hartley Chin | Clarendon | Completed | Load_238908 | Parnassus - 210 | Jul 10, 2026 4:42pm | Jul 10, 2026 4:42pm | Jul 10, 2026 6:14pm | Jul 10, 2026 7:31pm | Jul 10, 2026 7:53pm | Jul 10, 2026 8:02pm | Jul 10, 2026 8:02pm | Jul 10, 2026 8:02pm | LowHangingWires |  | Fair | No | Unable to contact customer… area patrolled and found okay …
Outage | J.E.26.07.11605 | C001851943 | Hartley Chin | Clarendon | Completed | Load_241995 | Parnassus - 210 | Jul 10, 2026 4:42pm | Jul 10, 2026 4:42pm | Jul 10, 2026 4:48pm | Jul 10, 2026 6:14pm | Jul 10, 2026 6:58pm | Jul 10, 2026 7:30pm | Jul 10, 2026 7:31pm | Jul 10, 2026 7:31pm |  |  | SevereWind | No | Found 1 of 3 blown 40 amp junction fuse @ pole # 0177669 line patrolled and found okay , junction refused …
Non-Outage | J.E.26.07.07689 | C001851941 | Clyde Brown | Clarendon | Completed | Load_251508 | May Pen - 110 | Jul 10, 2026 4:38pm | Jul 10, 2026 4:38pm | Jul 10, 2026 4:48pm | Jul 10, 2026 4:48pm | Jul 10, 2026 4:54pm | Jul 10, 2026 5:41pm | Jul 10, 2026 5:55pm | Jul 10, 2026 5:55pm |  |  | Fair | No | Corroded clamp at pothead for 3 wire service,clamp replaced,voltage now reading 111/115 and 227V
Non-Outage | J.E.26.07.11564 | C001851940 | Andre Williams | null | Completed | null | null | Jul 10, 2026 4:36pm | Jul 11, 2026 7:16am | Jul 11, 2026 7:25am | Jul 11, 2026 7:25am | Jul 11, 2026 7:56am | Jul 11, 2026 7:09am | Jul 11, 2026 8:11am | Jul 11, 2026 8:11am |  |  | Fair | No | Patrol line section re fuse and close close 25 amp fuse on three phase line at pole 02948 o visible fault seen on line , fuse facing cow pasture always out whenever when ever outage is reported other two always fine primary also hanging low from take off pole reffer to maintenance for follow up
Outage | J.E.26.07.11548 | C001851938 | Floyd Grant | St.Mary | Completed | Load_257079 | Blackstonedge - 110 | Jul 10, 2026 4:34pm | Jul 10, 2026 7:18pm | Jul 10, 2026 9:57pm | Jul 10, 2026 9:57pm | Jul 10, 2026 10:07pm | Jul 10, 2026 10:10pm | Jul 10, 2026 10:11pm | Jul 10, 2026 10:11pm | BrokenWire |  | SevereWind | No | Customer reported that the issue was resolved from yesterday
Outage | J.E.26.07.11589 | C001851939 | Raymond Carr | St.Mary | Completed | Load_257590 | Oracabessa - 210 | Jul 10, 2026 4:34pm | Jul 10, 2026 4:34pm | Jul 10, 2026 6:47pm | Jul 10, 2026 6:47pm | Jul 10, 2026 7:21pm | Jul 10, 2026 7:00pm | Jul 10, 2026 7:24pm | Jul 10, 2026 7:24pm | BrokenWire |  | Fair | No | Premises already visited. Customer was advised to fix pothead and stanchion.
Outage | J.E.26.07.10133 | C001851937 | Cliton Henry | St.Mary | Completed | Load_257387 | Blackstonedge - 110 | Jul 10, 2026 4:33pm | Jul 10, 2026 4:34pm | Jul 10, 2026 8:27pm | Jul 10, 2026 8:27pm | Jul 10, 2026 8:32pm | Jul 10, 2026 8:52pm | Jul 10, 2026 8:52pm | Jul 10, 2026 8:52pm | BangingWires |  | Fair | No | The secondary conductors found making contact when the wind blow creating a clearance breach. A 10 kva transformer was de energized at pole #045920 to carryout repairs. Corrective work done to retention the secondary neutral conductor. Supply restored to energized the 10 kva transformer at pole #045920.
Non-Outage | J.E.26.07.11456 | C001851936 | Shamour Haughton | St.James | Completed | Load_302398 | Bogue - 610 | Jul 10, 2026 4:32pm | Jul 10, 2026 4:37pm | Jul 10, 2026 6:46pm | Jul 10, 2026 6:46pm | Jul 10, 2026 6:55pm | Jul 10, 2026 6:55pm | Jul 10, 2026 6:57pm | Jul 10, 2026 6:57pm |  |  | Fair | No | Directions not clear, phone number went voicemail after several attempts, unable to locate customer
Outage | J.E.26.07.11538 | C001851933 | Rusean Allen | KSAS | Completed | Load_255768 | Hunts Bay - 310 | Jul 10, 2026 4:30pm | Jul 10, 2026 4:38pm | Jul 10, 2026 8:46pm | Jul 10, 2026 8:46pm | Jul 10, 2026 9:00pm | Jul 10, 2026 9:01pm | Jul 10, 2026 9:01pm | Jul 10, 2026 9:01pm |  |  | Fair | No | Premises okay
Outage | J.E.26.07.11200 | C001851931 | Rusean Allen | KSAS | Completed | Load_261241 | Hunts Bay - 310 | Jul 10, 2026 4:28pm | Jul 10, 2026 4:38pm | Jul 10, 2026 9:01pm | Jul 10, 2026 9:01pm | Jul 10, 2026 9:02pm | Jul 10, 2026 9:02pm | Jul 10, 2026 9:02pm | Jul 10, 2026 9:02pm |  |  | Fair | No | Premises okay
Outage | J.E.26.07.11050 | C001851929 | Rusean Allen | KSAS | Completed | Load_253374 | Hunts Bay - 310 | Jul 10, 2026 4:27pm | Jul 10, 2026 4:38pm | Jul 10, 2026 5:24pm | Jul 10, 2026 5:24pm | Jul 10, 2026 6:17pm | Jul 10, 2026 6:23pm | Jul 10, 2026 6:23pm | Jul 10, 2026 6:23pm |  |  | Fair | No | Premises locked
Outage | J.E.26.07.11256 | C001851930 | Rusean Allen | KSAS | Completed | Load_263200 | Hunts Bay - 310 | Jul 10, 2026 4:27pm | Jul 10, 2026 4:38pm | Jul 10, 2026 6:26pm | Jul 10, 2026 6:29pm | Jul 10, 2026 6:39pm | Jul 10, 2026 7:20pm | Jul 10, 2026 7:20pm | Jul 10, 2026 7:20pm |  |  | Fair | No | 2x 50amp fuse found 2x 50amp fuse replaced.2x 40amp fuse found 2x 50amp fuse replaced
Outage | J.E.26.07.11272 | C001851928 | Eric Williams | KSAS | Completed | Load_253996 | Greenwich - 710 | Jul 10, 2026 4:27pm | Jul 10, 2026 4:40pm | Jul 10, 2026 5:25pm | Jul 10, 2026 5:25pm | Jul 10, 2026 5:36pm | Jul 10, 2026 5:41pm | Jul 10, 2026 5:45pm | Jul 10, 2026 5:45pm | Fire |  | Fair | No | No fire seeing, calls to customer went unanswered
Outage | J.E.26.07.11325 | C001851927 | Rusean Allen | KSAS | Completed | Load_251712 | Hunts Bay - 510 | Jul 10, 2026 4:27pm | Jul 10, 2026 4:38pm | Jul 10, 2026 5:25pm | Jul 10, 2026 6:25pm | Jul 10, 2026 6:25pm | Jul 10, 2026 6:25pm | Jul 10, 2026 6:25pm | Jul 10, 2026 6:25pm |  |  | Fair | No | Found okay
Outage | J.E.26.07.10969 | C001851921 | Rusean Allen | KSAS | Completed | Load_237939 | Hunts Bay - 310 | Jul 10, 2026 4:25pm | Jul 10, 2026 4:40pm | Jul 10, 2026 9:03pm | Jul 10, 2026 9:03pm | Jul 10, 2026 9:03pm | Jul 10, 2026 9:04pm | Jul 10, 2026 9:04pm | Jul 10, 2026 9:04pm |  |  | Fair | No | Premises okay
Outage | J.E.26.07.11016 | C001851920 | Rusean Allen | KSAS | Completed | Load_254508 | Hunts Bay - 310 | Jul 10, 2026 4:25pm | Jul 10, 2026 4:44pm | Jul 10, 2026 7:21pm | Jul 10, 2026 7:21pm | Jul 10, 2026 8:14pm | Jul 10, 2026 8:14pm | Jul 10, 2026 8:14pm | Jul 10, 2026 8:14pm |  |  | Fair | No | Found okay
Outage | J.E.26.07.11443 | C001851919 | Ricky Hall | St.Catherine | Completed | Load_269657 | Tredegar - 410 | Jul 10, 2026 4:25pm | Jul 10, 2026 4:25pm | Jul 10, 2026 5:49pm | Jul 10, 2026 7:23pm | Jul 10, 2026 7:23pm | Jul 10, 2026 7:23pm | Jul 10, 2026 7:23pm | Jul 10, 2026 7:23pm |  |  | Fair | No | Call associated with outage #11672
Outage | J.E.26.07.11523 | C001851918 | Ricky Hall | St.Catherine | Completed | Load_270021 | Tredegar - 210 | Jul 10, 2026 4:25pm | Jul 10, 2026 4:25pm | Jul 10, 2026 4:30pm | Jul 10, 2026 4:30pm | Jul 10, 2026 4:56pm | Jul 10, 2026 5:48pm | Jul 10, 2026 5:48pm | Jul 10, 2026 5:48pm |  |  | Fair | No | Replaced blown 25 amps junction fuse
Outage | J.E.26.07.11507 | C001851917 | Andre Williams | Trelawny | Completed | Load_292876 | Greenwood - 210 | Jul 10, 2026 4:24pm | Jul 10, 2026 4:26pm | Jul 10, 2026 4:50pm | Jul 10, 2026 5:15pm | Jul 10, 2026 5:15pm | Jul 10, 2026 5:40pm | Jul 10, 2026 5:41pm | Jul 10, 2026 5:41pm |  |  | Fair | No | Patrol line section remove primary that was touching pole close 30 amp junctIon fuse
Outage | J.E.26.07.11413 | C001851908 | Rusean Allen | KSAS | Completed | Load_251392 | Greenwich - 310 | Jul 10, 2026 4:18pm | Jul 10, 2026 4:46pm | Jul 10, 2026 10:27pm | Jul 10, 2026 10:27pm | Jul 10, 2026 10:27pm | Jul 10, 2026 10:28pm | Jul 10, 2026 10:28pm | Jul 10, 2026 10:28pm | Fire |  | Fair | No | New meter to be installed, refer to field service department.
Outage | J.E.26.07.11533 | C001851909 | Evan Spaulding | St.Mary | Completed | Load_247519 | Highgate - 210 | Jul 10, 2026 4:18pm | Jul 10, 2026 4:19pm | Jul 10, 2026 7:44pm | Jul 10, 2026 7:44pm | Jul 10, 2026 7:44pm | Jul 10, 2026 7:44pm | Jul 10, 2026 7:45pm | Jul 10, 2026 7:45pm | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Associated with the Oxford call.
Outage | J.E.26.07.11534 | C001851907 | Evan Spaulding | St.Mary | Completed | Load_264935 | Highgate - 210 | Jul 10, 2026 4:18pm | Jul 10, 2026 4:19pm | Jul 10, 2026 5:39pm | Jul 10, 2026 5:39pm | Jul 10, 2026 6:08pm | Jul 10, 2026 7:38pm | Jul 10, 2026 7:41pm | Jul 10, 2026 7:41pm | BrokenWire |  | SevereWind | No | Splice and retention two spans secondary conductors using 110ft #2 AAAC ,90ft 2/0 AAAC conductor,2-2/0 & 1-#2 splicing sleeves 2-2/0 preforms and replace 1- 5 amps Transformer fuse at pole number 0013035.
Outage | J.E.26.07.11009 | C001851906 | Milton Charlton | KSAN | Completed | Load_261591 | Hope - 510 | Jul 10, 2026 4:17pm | Jul 10, 2026 4:17pm | Jul 10, 2026 4:26pm | Jul 10, 2026 4:31pm | Jul 10, 2026 4:31pm | Jul 10, 2026 4:40pm | Jul 10, 2026 4:32pm | Jul 10, 2026 4:32pm | BrokenWire |  | Fair | No | Call related to call at Constitution Hill.
Outage | J.E.26.07.11440 | C001851900 | Oshane Warren | Westmoreland | Completed | Load_239357 | Paradise - 210 | Jul 10, 2026 4:16pm | Jul 10, 2026 4:17pm | Jul 10, 2026 4:24pm | Jul 10, 2026 4:24pm | Jul 10, 2026 6:22pm | Jul 10, 2026 6:26pm | Jul 10, 2026 6:29pm | Jul 10, 2026 6:29pm | Fire |  | Fair | No | Replace 3 pg clamps from transformer drop lead and replace 2amp 25 kva transformer fuse
Outage | J.E.26.07.11442 | C001851899 | Kenroy Dale | Manchester | Completed | Load_249527 | Porus - 310 | Jul 10, 2026 4:15pm | Jul 10, 2026 4:16pm | Jul 10, 2026 5:06pm | Jul 10, 2026 8:59pm | Jul 10, 2026 10:46pm | Jul 10, 2026 10:46pm | Jul 10, 2026 10:49pm | Jul 10, 2026 10:49pm |  |  | Fair | No | Blown 2 amp transformer fuse found for 25 kva transformer one patrol nothing found (twisted secondary) blown fuse was replaced and area now with supply
Non-Outage | J.E.26.07.10565 | C001851897 | Milton Charlton | KSAS | Completed | Load_246230 | Up Park Camp - 410 | Jul 10, 2026 4:12pm | Jul 10, 2026 6:09pm | Jul 10, 2026 7:38pm | Jul 10, 2026 7:38pm | Jul 10, 2026 7:39pm | Jul 10, 2026 7:40pm | Jul 10, 2026 7:41pm | Jul 10, 2026 7:41pm |  |  | Fair | No | Call related to call at unity 26- 2 Seymour Avenue.
Outage | J.E.26.07.11526 | C001851893 | Daniel Francis | St.Ann | Completed | Load_246719 | Ocho Rios - 310 | Jul 10, 2026 4:10pm | Jul 10, 2026 4:10pm | Jul 10, 2026 6:05pm | Jul 10, 2026 6:05pm | Jul 10, 2026 6:38pm | Jul 10, 2026 7:01pm | Jul 10, 2026 7:05pm | Jul 10, 2026 7:05pm |  |  | Fair | No | Remade joint transformer leads using 6 one bolt clamp pe
Outage | J.E.26.07.11364 | C001851892 | Richard Samuda | Manchester | Completed | Load_263434 | Kendal - 210 | Jul 10, 2026 4:09pm | Jul 10, 2026 4:10pm | Jul 10, 2026 5:56pm | Jul 10, 2026 6:35pm | Jul 10, 2026 7:07pm | Jul 10, 2026 7:40pm | Jul 10, 2026 7:40pm | Jul 10, 2026 7:40pm | LeaningPole |  | Fair | No | Refer call to maintenance Leaning 40ft concrete pole customer concerned pole is going fall pole need guy wire
Outage | J.E.26.07.11514 | C001851890 | Daniel Francis | St.Ann | Completed | Load_260482 | Ocho Rios - 510 | Jul 10, 2026 4:07pm | Jul 10, 2026 4:07pm | Jul 10, 2026 5:23pm | Jul 10, 2026 5:23pm | Jul 10, 2026 5:23pm | Jul 10, 2026 5:30pm | Jul 10, 2026 5:40pm | Jul 10, 2026 5:40pm |  |  | Fair | No | Change one 3amp fuse no pole #
Outage | J.E.26.07.10752 | C001851884 | Hopeton Henry | St.Thomas | Completed | Load_238731 | Good Year - 210 | Jul 10, 2026 4:04pm | Jul 10, 2026 4:06pm | Jul 10, 2026 4:32pm | Jul 10, 2026 4:33pm | Jul 10, 2026 5:41pm | Jul 10, 2026 5:41pm | Jul 10, 2026 5:42pm | Jul 10, 2026 5:42pm | BrokenWire |  | Fair | No | Reconnect secondary conductors and reset 25 kva transformer
Outage | J.E.26.07.11002 | C001851882 | Raymond Lewis | St.Ann | Completed | Load_259193 | Roaring River - 210 | Jul 10, 2026 4:04pm | Jul 10, 2026 4:04pm | Jul 10, 2026 5:34pm | Jul 10, 2026 5:35pm | Jul 10, 2026 6:06pm | Jul 10, 2026 6:10pm | Jul 10, 2026 6:10pm | Jul 10, 2026 6:10pm |  |  | SevereWind | No | Install switch on line refuse and close 25 amp junction
Outage | J.E.26.07.11097 | C001851883 | Hopeton Henry | St.Thomas | Completed | Load_258375 | Good Year - 210 | Jul 10, 2026 4:04pm | Jul 10, 2026 4:06pm | Jul 10, 2026 4:32pm | Jul 10, 2026 5:45pm | Jul 10, 2026 5:47pm | Jul 10, 2026 5:47pm | Jul 10, 2026 5:47pm | Jul 10, 2026 5:47pm |  |  | Fair | No | Check and found ok
Outage | J.E.26.07.11510 | C001851881 | Hopeton Henry | St.Thomas | Completed | Load_252203 | Good Year - 210 | Jul 10, 2026 4:03pm | Jul 10, 2026 4:06pm | Jul 10, 2026 4:32pm | Jul 10, 2026 5:48pm | Jul 10, 2026 5:54pm | Jul 10, 2026 6:07pm | Jul 10, 2026 6:08pm | Jul 10, 2026 6:08pm |  |  | Fair | No | Check and found ok
Outage | J.E.26.07.11467 | C001851880 | Milton Charlton | KSAN | Completed | Load_245329 | Hope - 510 | Jul 10, 2026 4:02pm | Jul 10, 2026 4:02pm | Jul 10, 2026 4:33pm | Jul 10, 2026 4:33pm | Jul 10, 2026 5:28pm | Jul 10, 2026 5:30pm | Jul 10, 2026 5:30pm | Jul 10, 2026 5:30pm |  |  | Fair | No | Found one 15 amps junction fuse blown at pole #041094. Refused using one 15 amps fuse and reclosed junction switch.
Outage | J.E.26.07.11135 | C001851878 | Donald Cunningham | St.Catherine | Completed | Load_262150 | Tredegar - 510 | Jul 10, 2026 4:01pm | Jul 10, 2026 4:02pm | Jul 10, 2026 4:31pm | Jul 10, 2026 4:31pm | Jul 10, 2026 5:57pm | Jul 10, 2026 6:42pm | Jul 10, 2026 6:46pm | Jul 10, 2026 6:46pm | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Broken secondary neural cause by falling tree on line have same removed splice and retention secondary phase and neural using 1 automatic splice 4 clamps 1 #2 preform for repair also replace blown junction fuse with 10 amp fuse
Outage | J.E.26.07.11117 | C001851875 | Kaydon Taylor | KSAN | Completed | Load_247559 | Constant Spring - 210 | Jul 10, 2026 3:59pm | Jul 10, 2026 4:00pm | Jul 10, 2026 10:05pm | Jul 10, 2026 10:05pm | Jul 10, 2026 10:06pm | Jul 10, 2026 10:07pm | Jul 10, 2026 10:07pm | Jul 10, 2026 10:07pm | BrokenWire |  | Fair | No | Premises closed customer request a crew to return at 8:00am Saturday
Outage | J.E.26.07.11340 | C001851873 | Christopher Edwards | KSAN | Completed | Load_250815 | Constant Spring - 410 | Jul 10, 2026 3:59pm | Jul 10, 2026 4:00pm | Jul 10, 2026 6:15pm | Jul 10, 2026 6:15pm | Jul 10, 2026 6:15pm | Jul 10, 2026 7:32pm | Jul 10, 2026 7:33pm | Jul 10, 2026 7:33pm |  |  | Fair | No | Remake burnt joint at pole Using (2) one bolt clamps AlsoVoltage:115,114,230v
Outage | J.E.26.07.11358 | C001851872 | Selvin White | St.Elizabeth | Completed | Load_255287 | Maggotty - 110 | Jul 10, 2026 3:59pm | Jul 10, 2026 4:05pm | Jul 10, 2026 5:56pm | Jul 10, 2026 5:56pm | Jul 10, 2026 6:20pm | Jul 10, 2026 6:50pm | Jul 10, 2026 6:51pm | Jul 10, 2026 6:51pm |  |  | Fair | No | Customer cannot be reconnected due to corrections that needs to be done at customer pothead. Customer was advised..
Outage | J.E.26.07.10729 | C001851867 | Kaydon Taylor | KSAN | Completed | Load_256025 | Constant Spring - 210 | Jul 10, 2026 3:56pm | Jul 10, 2026 3:57pm | Jul 10, 2026 4:14pm | Jul 10, 2026 10:07pm | Jul 10, 2026 10:37pm | Jul 10, 2026 10:37pm | Jul 10, 2026 10:38pm | Jul 10, 2026 10:38pm |  |  | Fair | No | Found okay
Outage | J.E.26.07.11230 | C001851866 | Kaydon Taylor | KSAN | Completed | Load_247843 | Constant Spring - 210 | Jul 10, 2026 3:56pm | Jul 10, 2026 3:57pm | Jul 10, 2026 4:26pm | Jul 10, 2026 4:26pm | Jul 10, 2026 5:35pm | Jul 10, 2026 5:53pm | Jul 10, 2026 5:53pm | Jul 10, 2026 5:53pm |  |  | Fair | No | 15 amp fuse found blown and replace at pole #539171
Outage | J.E.26.07.10648 | C001851864 | Jermaine Williams | Clarendon | Completed | Load_247306 | Monymusk - 410 | Jul 10, 2026 3:54pm | Jul 10, 2026 3:54pm | Jul 10, 2026 9:36pm | Jul 10, 2026 9:36pm | Jul 10, 2026 9:36pm | Jul 10, 2026 9:30pm | Jul 10, 2026 9:37pm | Jul 10, 2026 9:37pm | BrokenWire |  | SevereWind | No | Patrol and replaced two blown 40amp junction fuse at Clifton sq.
Outage | J.E.26.07.10862 | C001851865 | Jermaine Williams | Clarendon | Completed | Load_252198 | Monymusk - 410 | Jul 10, 2026 3:54pm | Jul 10, 2026 3:54pm | Jul 10, 2026 8:05pm | Jul 10, 2026 8:05pm | Jul 10, 2026 8:58pm | Jul 10, 2026 9:01pm | Jul 10, 2026 9:06pm | Jul 10, 2026 9:06pm | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | SevereWind | No | Isolate 25kva xfmr to splice and retention broken secondary neutral conductor using 30’ #2aaa, two sleeves and row clamps.
Outage | J.E.26.07.11071 | C001851860 | Clyde Brown | Clarendon | Completed | Load_253095 | May Pen - 110 | Jul 10, 2026 3:50pm | Jul 10, 2026 3:51pm | Jul 10, 2026 4:28pm | Jul 10, 2026 4:28pm | Jul 10, 2026 4:41pm | Jul 10, 2026 4:37pm | Jul 10, 2026 4:46pm | Jul 10, 2026 4:46pm | BrokenWire |  | Fair | No | Customer said issue was resolve
Outage | J.E.26.07.10091 | C001851859 | Gregory Grossett | Portland | Completed | Load_241333 | Port Antonio - 410 | Jul 10, 2026 3:47pm | Jul 10, 2026 3:49pm | Jul 10, 2026 8:11pm | Jul 10, 2026 8:11pm | Jul 10, 2026 8:47pm | Jul 10, 2026 9:04pm | Jul 10, 2026 9:23pm | Jul 10, 2026 9:23pm |  |  | Fair | No | The customer stated that their power supply has been restored. Customer okay.
Outage | J.E.26.07.10913 | C001851851 | Jermaine Williams | Clarendon | Completed | Load_257029 | Parnassus - 310 | Jul 10, 2026 3:44pm | Jul 10, 2026 3:45pm | Jul 10, 2026 5:53pm | Jul 10, 2026 5:53pm | Jul 10, 2026 6:27pm | Jul 10, 2026 6:36pm | Jul 10, 2026 6:35pm | Jul 10, 2026 6:35pm | BangingWires |  | SevereWind | No | Splice and retention two spans broken secondary phase conductor using 10’ 2/0aaa, one sleeve and two clamps and reset tripped 10kva xfmr.
Outage | J.E.26.07.10979 | C001851849 | Jermaine Williams | Clarendon | Completed | Load_245051 | Parnassus - 310 | Jul 10, 2026 3:44pm | Jul 10, 2026 3:45pm | Jul 10, 2026 6:35pm | Jul 10, 2026 6:35pm | Jul 10, 2026 6:36pm | Jul 10, 2026 6:36pm | Jul 10, 2026 6:38pm | Jul 10, 2026 6:38pm |  |  | SevereWind | No | Splice and retention two spans broken phase conductor 10’ 2/0aaa, one sleeve and two clamps and reset tripped 10kva xfmr.
Outage | J.E.26.07.11083 | C001851850 | Jermaine Williams | Clarendon | Completed | Load_258269 | Parnassus - 310 | Jul 10, 2026 3:44pm | Jul 10, 2026 3:45pm | Jul 10, 2026 4:13pm | Jul 10, 2026 4:13pm | Jul 10, 2026 4:44pm | Jul 10, 2026 5:10pm | Jul 10, 2026 5:34pm | Jul 10, 2026 5:34pm |  |  | SevereWind | No | Defective 25kva xfmr , N McLean was advised.
Outage | J.E.26.07.11120 | C001851852 | Jermaine Williams | Clarendon | Completed | Load_239411 | Parnassus - 310 | Jul 10, 2026 3:44pm | Jul 10, 2026 3:45pm | Jul 10, 2026 10:40pm | Jul 10, 2026 10:40pm | Jul 10, 2026 10:40pm | Jul 10, 2026 10:40pm | Jul 10, 2026 10:40pm | Jul 10, 2026 10:40pm |  |  | Fair | No | Premises found ok.
Outage | J.E.26.07.10667 | C001851848 | Gregory Grossett | Portland | Completed | Load_240240 | Port Antonio - 410 | Jul 10, 2026 3:43pm | Jul 10, 2026 3:44pm | Jul 10, 2026 9:24pm | Jul 10, 2026 9:24pm | Jul 10, 2026 9:24pm | Jul 10, 2026 9:25pm | Jul 10, 2026 9:26pm | Jul 10, 2026 9:26pm |  |  | Fair | No | The customer stated that their power supply has been after 3pm today. Customer okay.
Outage | J.E.26.07.11248 | C001851846 | Shamour Haughton | St.James | Completed | Load_238758 | Bogue - 610 | Jul 10, 2026 3:40pm | Jul 10, 2026 3:41pm | Jul 10, 2026 6:41pm | Jul 10, 2026 6:41pm | Jul 10, 2026 6:41pm | Jul 10, 2026 6:41pm | Jul 10, 2026 6:45pm | Jul 10, 2026 6:45pm |  |  | Fair | No | Area needs 110ft of #6 triplex
Outage | J.E.26.07.11377 | C001851843 | Shamour Haughton | St.James | Completed | Load_248957 | Bogue - 610 | Jul 10, 2026 3:38pm | Jul 10, 2026 3:39pm | Jul 10, 2026 4:56pm | Jul 10, 2026 5:11pm | Jul 10, 2026 5:11pm | Jul 10, 2026 5:25pm | Jul 10, 2026 5:53pm | Jul 10, 2026 5:53pm |  |  | Fair | No | Found customer meter defective, meter needs to change urgently, voltage left 111,112,223
Non-Outage | J.E.26.07.10875 | C001851840 | Marlon Brown | Trelawny | Completed | Load_257002 | Duncans - 210 | Jul 10, 2026 3:35pm | Jul 10, 2026 3:38pm | Jul 10, 2026 3:42pm | Jul 10, 2026 3:42pm | Jul 10, 2026 3:42pm | Jul 10, 2026 4:18pm | Jul 10, 2026 4:18pm | Jul 10, 2026 4:18pm | Fire |  | SevereWind | No | 20ft #6 triplex 3pg & 3 linkers Voltage found noneVoltage leaving 118/118=236v.
Outage | J.E.26.07.11407 | C001851839 | Marlon Brown | Trelawny | Completed | Load_257987 | Duncans - 210 | Jul 10, 2026 3:35pm | Jul 10, 2026 3:35pm | Jul 10, 2026 7:00pm | Jul 10, 2026 7:01pm | Jul 10, 2026 7:27pm | Jul 10, 2026 7:43pm | Jul 10, 2026 7:43pm | Jul 10, 2026 7:43pm |  |  | Fair | No | Reset 25kva transformer Voltage found noneVoltage leaving 115/114=229 Fire lit burning bushes causing secondary to bang.
Outage | J.E.26.07.11414 | C001851838 | Lancelot Brown | Hanover | Completed | Load_238848 | Orange Bay - 310 | Jul 10, 2026 3:34pm | Jul 10, 2026 3:35pm | Jul 10, 2026 4:39pm | Jul 10, 2026 5:54pm | Jul 10, 2026 7:34pm | Jul 10, 2026 7:35pm | Jul 10, 2026 7:36pm | Jul 10, 2026 7:36pm |  |  | Fair | No | Check and found ok fix by private electrician
Non-Outage | J.E.26.07.11228 | C001851835 | Michael Christian | null | Completed | null | null | Jul 10, 2026 3:32pm | Jul 10, 2026 3:33pm | Jul 10, 2026 3:47pm | Jul 10, 2026 3:48pm | Jul 10, 2026 4:57pm | Jul 10, 2026 5:25pm | Jul 10, 2026 5:25pm | Jul 10, 2026 5:25pm | Fire |  | Fair | No | Check and found okay no fire found
Outage | J.E.26.07.10600 | C001851834 | Michael Christian | St.James | Completed | Load_261444 | Queens Drive - 710 | Jul 10, 2026 3:32pm | Jul 10, 2026 3:33pm | Jul 10, 2026 3:47pm | Jul 10, 2026 5:25pm | Jul 10, 2026 5:25pm | Jul 10, 2026 6:25pm | Jul 10, 2026 6:25pm | Jul 10, 2026 6:25pm | BrokenWire |  | Fair | No | Reconnection customer service wire at pole voltage 110
Outage | J.E.26.07.11273 | C001851836 | Shamour Haughton | St.James | Completed | Load_239376 | Bogue - 510 | Jul 10, 2026 3:32pm | Jul 10, 2026 3:33pm | Jul 10, 2026 4:07pm | Jul 10, 2026 4:08pm | Jul 10, 2026 4:49pm | Jul 10, 2026 4:49pm | Jul 10, 2026 4:54pm | Jul 10, 2026 4:54pm |  |  | Fair | No | Check and found okay, voltage left 114,114,198,222,228,228
Outage | J.E.26.07.10145 | C001851833 | Gregory Grossett | Portland | Completed | Load_254246 | Port Antonio - 410 | Jul 10, 2026 3:31pm | Jul 10, 2026 3:33pm | Jul 10, 2026 9:27pm | Jul 10, 2026 9:27pm | Jul 10, 2026 9:27pm | Jul 10, 2026 9:27pm | Jul 10, 2026 9:28pm | Jul 10, 2026 9:28pm |  |  | Fair | No | Duplicated report. Customer supply has been restored.
Outage | J.E.26.07.11168 | C001851826 | Roxroy Needham | St.Ann | Completed | Load_574936 | Cardiff Hall - 210 | Jul 10, 2026 3:31pm | Jul 10, 2026 3:31pm | Jul 10, 2026 5:13pm | Jul 10, 2026 5:13pm | Jul 10, 2026 5:13pm | Jul 10, 2026 5:25pm | Jul 10, 2026 5:25pm | Jul 10, 2026 5:25pm |  |  | Fair | No | Found light in the are
Outage | J.E.26.07.11361 | C001851828 | Roxroy Needham | St.Ann | Completed | Load_248752 | Cardiff Hall - 210 | Jul 10, 2026 3:31pm | Jul 10, 2026 3:31pm | Jul 10, 2026 5:25pm | Jul 10, 2026 5:25pm | Jul 10, 2026 5:26pm | Jul 10, 2026 5:26pm | Jul 10, 2026 5:30pm | Jul 10, 2026 5:30pm |  |  | Fair | No | Found the area with light
Outage | J.E.26.07.10872 | C001851822 | Michael Christian | St.James | Completed | Load_267138 | Queens Drive - 710 | Jul 10, 2026 3:30pm | Jul 10, 2026 3:31pm | Jul 10, 2026 3:47pm | Jul 10, 2026 6:25pm | Jul 10, 2026 6:49pm | Jul 10, 2026 6:56pm | Jul 10, 2026 6:56pm | Jul 10, 2026 6:56pm | BrokenWire |  | Fair | No | Found secondary dislodged form cross an needle 1 6 ft and bucket truck and line
Outage | J.E.26.07.10947 | C001851823 | Michael Christian | St.James | Completed | Load_268563 | Queens Drive - 710 | Jul 10, 2026 3:30pm | Jul 10, 2026 3:31pm | Jul 10, 2026 3:47pm | Jul 10, 2026 8:54pm | Jul 10, 2026 9:22pm | Jul 10, 2026 9:32pm | Jul 10, 2026 9:32pm | Jul 10, 2026 9:32pm | BrokenWire |  | Fair | No | Replace 1 clamp at customer service wire at pole voltage 112 114 223 at pothead
Outage | J.E.26.07.10980 | C001851824 | Gregory Grossett | Portland | Completed | Load_260585 | Port Antonio - 410 | Jul 10, 2026 3:30pm | Jul 10, 2026 3:33pm | Jul 10, 2026 6:38pm | Jul 10, 2026 6:38pm | Jul 10, 2026 6:39pm | Jul 10, 2026 6:31pm | Jul 10, 2026 6:40pm | Jul 10, 2026 6:40pm |  | Y | Fair | No | 10 amps junction fuse blown no pole number at location, cause by bamboo fall on line clear and restore area, material used 1-10 amps fuse
Outage | J.E.26.07.11221 | C001851825 | Roxroy Needham | St.Ann | Completed | Load_248242 | Cardiff Hall - 210 | Jul 10, 2026 3:30pm | Jul 10, 2026 3:31pm | Jul 10, 2026 5:03pm | Jul 10, 2026 5:03pm | Jul 10, 2026 5:04pm | Jul 10, 2026 5:13pm | Jul 10, 2026 5:13pm | Jul 10, 2026 5:13pm |  |  | Fair | No | Found the area with light not getting customer on phone
Outage | J.E.26.07.11152 | C001851820 | Lancelot Brown | Hanover | Completed | Load_246952 | Orange Bay - 310 | Jul 10, 2026 3:29pm | Jul 10, 2026 3:30pm | Jul 10, 2026 4:39pm | Jul 10, 2026 4:39pm | Jul 10, 2026 5:28pm | Jul 10, 2026 5:53pm | Jul 10, 2026 5:54pm | Jul 10, 2026 5:54pm |  |  | Fair | No | Remake corroded joint at pothead used three connectors further checks found customer disconnected advise customer
Outage | J.E.26.07.11086 | C001851818 | Horace Malcolm | St.James | Completed | Load_268004 | Bogue - 310 | Jul 10, 2026 3:28pm | Jul 10, 2026 3:29pm | Jul 10, 2026 7:15pm | Jul 10, 2026 7:15pm | Jul 10, 2026 7:15pm | Jul 10, 2026 7:16pm | Jul 10, 2026 7:16pm | Jul 10, 2026 7:16pm | BrokenWire |  | Fair | No | Related to previous call job number 11367
Outage | J.E.26.07.11139 | C001851817 | Horace Malcolm | St.James | Completed | Load_576009 | Bogue - 310 | Jul 10, 2026 3:27pm | Jul 10, 2026 3:29pm | Jul 10, 2026 4:13pm | Jul 10, 2026 4:13pm | Jul 10, 2026 4:45pm | Jul 10, 2026 5:03pm | Jul 10, 2026 5:03pm | Jul 10, 2026 5:03pm |  |  | SevereWind | No | Refused one 30amp junction fuse
Outage | J.E.26.07.11366 | C001851816 | Gregory Grossett | Portland | Completed | Load_353091 | Port Antonio - 410 | Jul 10, 2026 3:27pm | Jul 10, 2026 3:30pm | Jul 10, 2026 6:37pm | Jul 10, 2026 6:37pm | Jul 10, 2026 6:37pm | Jul 10, 2026 6:31pm | Jul 10, 2026 6:38pm | Jul 10, 2026 6:38pm | Fire | Y | Fair | No | 10 amps junction fuse blown no pole number at location, cause by bamboo fall on line clear and restore area, material used 1-10 amps fuse
Outage | J.E.26.07.11367 | C001851815 | Horace Malcolm | St.James | Completed | Load_302873 | Bogue - 310 | Jul 10, 2026 3:27pm | Jul 10, 2026 3:29pm | Jul 10, 2026 5:05pm | Jul 10, 2026 5:05pm | Jul 10, 2026 5:54pm | Jul 10, 2026 7:15pm | Jul 10, 2026 7:15pm | Jul 10, 2026 7:15pm |  |  | Fair | No | Clear primary nuetral wire from primary line and replace one 50amp junction fuse
Outage | J.E.26.07.11234 | C001851810 | Andre Williams | Trelawny | Completed | Load_261046 | Greenwood - 110 | Jul 10, 2026 3:22pm | Jul 10, 2026 3:22pm | Jul 10, 2026 3:39pm | Jul 10, 2026 7:06pm | Jul 10, 2026 7:20pm | Jul 10, 2026 7:21pm | Jul 10, 2026 7:22pm | Jul 10, 2026 7:22pm |  |  | Fair | No | Premises not found, phone going to voicemail and number in voicemail also not working
Outage | J.E.26.07.11154 | C001851802 | Richman Whyte | Westmoreland | Completed | Load_292085 | Paradise - 310 | Jul 10, 2026 3:15pm | Jul 10, 2026 3:54pm | Jul 10, 2026 5:02pm | Jul 10, 2026 5:02pm | Jul 10, 2026 5:02pm | Jul 10, 2026 5:03pm | Jul 10, 2026 5:04pm | Jul 10, 2026 5:04pm |  |  | Fair | No | Restoration work is required refer to maintenance
Outage | J.E.26.07.11131 | C001851801 | Selvin White | St.Elizabeth | Completed | Load_292274 | Maggotty - 210 | Jul 10, 2026 3:13pm | Jul 10, 2026 3:14pm | Jul 10, 2026 5:39pm | Jul 10, 2026 5:39pm | Jul 10, 2026 5:40pm | Jul 10, 2026 5:45pm | Jul 10, 2026 5:45pm | Jul 10, 2026 5:45pm |  |  | Fair | No | Please refer to Simone Bicarie and C. Johnson at the field service department as System at location is RAMI and connection is dealt with by that department.
Outage | J.E.26.07.11222 | C001851800 | Wayne Dillion | Manchester | Completed | Load_302929 | Spur Tree - 210 | Jul 10, 2026 3:12pm | Jul 10, 2026 3:53pm | Jul 10, 2026 4:51pm | Jul 10, 2026 4:51pm | Jul 10, 2026 5:10pm | Jul 10, 2026 6:15pm | Jul 10, 2026 6:16pm | Jul 10, 2026 6:16pm |  |  | Fair | No | Patrol and found switch top jumper brunt off. Isolate 20amp chip saver at pole #041099 to repair same using 1 hot line clamp. Re-close chip saver and supply restored okay.
Outage | J.E.26.07.11095 | C001851795 | Richard Samuda | Manchester | Completed | Load_269497 | Kendal - 210 | Jul 10, 2026 3:07pm | Jul 10, 2026 3:08pm | Jul 10, 2026 3:42pm | Jul 10, 2026 3:42pm | Jul 10, 2026 4:50pm | Jul 10, 2026 4:51pm | Jul 10, 2026 4:51pm | Jul 10, 2026 4:51pm |  |  | Fair | No | Call to phone no answer premises not located
Outage | J.E.26.07.10985 | C001851791 | Christopher Edwards | KSAN | Completed | Load_238744 | Constant Spring - 410 | Jul 10, 2026 3:05pm | Jul 10, 2026 3:09pm | Jul 10, 2026 5:38pm | Jul 10, 2026 5:38pm | Jul 10, 2026 5:45pm | Jul 10, 2026 6:13pm | Jul 10, 2026 6:14pm | Jul 10, 2026 6:14pm | LeaningPole |  | Fair | No | Rotten 40ft wood poleConsist of single phase primary Open secondary wiresPole needs to be replaced Supply is in the area
Outage | J.E.26.07.10915 | C001851789 | Hopeton Henry | St.Thomas | Completed | Load_239959 | Good Year - 210 | Jul 10, 2026 3:03pm | Jul 10, 2026 3:08pm | Jul 10, 2026 4:32pm | Jul 10, 2026 5:42pm | Jul 10, 2026 5:42pm | Jul 10, 2026 1:00am | Jul 10, 2026 5:43pm | Jul 10, 2026 5:43pm |  |  | Fair | No | Found ok , power restored
Outage | J.E.26.07.11209 | C001851788 | Hopeton Henry | St.Thomas | Completed | Load_243194 | Good Year - 210 | Jul 10, 2026 3:03pm | Jul 10, 2026 3:08pm | Jul 10, 2026 4:32pm | Jul 10, 2026 6:09pm | Jul 10, 2026 8:02pm | Jul 10, 2026 8:03pm | Jul 10, 2026 8:06pm | Jul 10, 2026 8:06pm |  |  | SevereWind | No | Power restored, refer to maintenance department to do detail patrol
Outage | J.E.26.07.11287 | C001851787 | Hopeton Henry | St.Thomas | Completed | Load_260408 | Good Year - 110 | Jul 10, 2026 3:02pm | Jul 10, 2026 3:08pm | Jul 10, 2026 4:32pm | Jul 10, 2026 9:10pm | Jul 11, 2026 9:16am | Jul 11, 2026 9:17am | Jul 11, 2026 9:18am | Jul 11, 2026 9:18am |  |  | Fair | No | Check and found ok
Outage | J.E.26.07.09124 | C001851784 | Cliton Henry | St.Mary | Completed | Load_241396 | Blackstonedge - 110 | Jul 10, 2026 2:57pm | Jul 10, 2026 2:58pm | Jul 10, 2026 8:54pm | Jul 10, 2026 8:54pm | Jul 10, 2026 9:05pm | Jul 10, 2026 10:36pm | Jul 10, 2026 10:36pm | Jul 10, 2026 10:36pm |  |  | Fair | No | A primary switch jumper burnt off at pole #0014115.The other 2 switches were de energized to carryout repairs. Corrective work done to reconnected the jumper using 1- one bolt clamp. Supply restored to energized the 3 drop switches.
Outage | J.E.26.07.09534 | C001851778 | Cliton Henry | St.Mary | Completed | Load_261992 | Blackstonedge - 110 | Jul 10, 2026 2:54pm | Jul 10, 2026 2:55pm | Jul 10, 2026 4:16pm | Jul 10, 2026 4:16pm | Jul 10, 2026 4:36pm | Jul 10, 2026 6:23pm | Jul 10, 2026 6:34pm | Jul 10, 2026 6:34pm |  |  | Fair | No | A blown amp junction fuse found at Wood Park towards Derry and a blown 25 amp fuse found at Derry Square towards Top Derry/ Hazard Dist. Due tree contact. Corrective work done to cut and remove tree branch and vines form the primary line. Supply restored using 1- 20 amp fuse at Derry Square and 1-30 amp fuse at Wood Park respectively
Outage | J.E.26.07.09629 | C001851766 | Richard Nicholas | St.Catherine | Completed | Load_256805 | New Michelton - 410 | Jul 10, 2026 2:33pm | Jul 10, 2026 2:34pm | Jul 10, 2026 3:30pm | Jul 10, 2026 3:31pm | Jul 10, 2026 4:35pm | Jul 10, 2026 5:08pm | Jul 10, 2026 5:10pm | Jul 10, 2026 5:10pm |  |  | Fair | No | Replaced blown 20amp x2 junctions fuse on pole #0126175 and blown 15amp on pole #47402.
Outage | J.E.26.07.11201 | C001851754 | Marlon Brown | Trelawny | Completed | Load_555692 | Duncans - 210 | Jul 10, 2026 2:19pm | Jul 10, 2026 2:19pm | Jul 10, 2026 6:13pm | Jul 10, 2026 6:13pm | Jul 10, 2026 6:17pm | Jul 10, 2026 6:18pm | Jul 10, 2026 6:18pm | Jul 10, 2026 6:18pm |  |  | Fair | No | Unable to locate customer via telephone nor direction
Outage | J.E.26.07.10992 | C001851752 | Edward Royal | KSAS | Completed | Load_260446 | Hunts Bay - 310 | Jul 10, 2026 2:14pm | Jul 10, 2026 2:14pm | Jul 10, 2026 11:42pm | Jul 10, 2026 11:42pm | Jul 10, 2026 11:42pm | Jul 10, 2026 11:43pm | Jul 10, 2026 11:43pm | Jul 10, 2026 11:43pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.10458 | C001851743 | Floyd Grant | St.Mary | Completed | Load_262319 | Blackstonedge - 110 | Jul 10, 2026 1:58pm | Jul 10, 2026 7:18pm | Jul 10, 2026 7:33pm | Jul 10, 2026 7:33pm | Jul 10, 2026 8:30pm | Jul 10, 2026 9:56pm | Jul 10, 2026 9:57pm | Jul 10, 2026 9:57pm |  |  | SevereWind | No | Lightning arrester bottom was disconnected and the junction fuse reclosed.
Non-Outage | J.E.26.07.09456 | C001851741 | Andrae Dawkins | St.James | Completed | Load_267138 | Queens Drive - 710 | Jul 10, 2026 1:57pm | Jul 10, 2026 1:57pm | Jul 10, 2026 3:14pm | Jul 10, 2026 3:14pm | Jul 10, 2026 3:24pm | Jul 10, 2026 3:26pm | Jul 10, 2026 3:26pm | Jul 10, 2026 3:26pm |  |  | Fair | No | Found customer meter defective needs to be replaced refer back to field service kaydian
Non-Outage | J.E.26.07.09676 | C001851738 | Hartley Chin | Clarendon | Completed | Load_248117 | Parnassus - 210 | Jul 10, 2026 1:46pm | Jul 10, 2026 1:52pm | Jul 10, 2026 8:02pm | Jul 10, 2026 8:02pm | Jul 10, 2026 8:52pm | Jul 10, 2026 8:57pm | Jul 10, 2026 8:57pm | Jul 10, 2026 8:57pm |  |  | Fair | No | Requires daylight attention…Prem currently closed… will be able to access Prem when school is in session…
Outage | J.E.26.07.11085 | C001851734 | Andre Williams | Trelawny | Completed | Load_257144 | Greenwood - 110 | Jul 10, 2026 1:42pm | Jul 10, 2026 3:23pm | Jul 10, 2026 3:43pm | Jul 10, 2026 3:56pm | Jul 10, 2026 4:33pm | Jul 10, 2026 4:34pm | Jul 10, 2026 4:50pm | Jul 10, 2026 4:50pm |  |  | Fair | No | Reconnect customer with help Fromm meter center.
Outage | J.E.26.07.10848 | C001851702 | Tajay Bernard | Hanover | Completed | Load_250849 | Orange Bay - 310 | Jul 10, 2026 1:16pm | Jul 10, 2026 1:16pm | Jul 10, 2026 1:45pm | Jul 10, 2026 1:48pm | Jul 10, 2026 2:26pm | Jul 10, 2026 2:33pm | Jul 10, 2026 2:33pm | Jul 10, 2026 2:33pm |  |  | Fair | No | Premises check and found okay customer has internal problems voltage reading 115/115/230
Outage | J.E.26.07.10905 | C001851697 | Stephen Taylor | St.Thomas | Completed | Load_254225 | Lysson - 410 | Jul 10, 2026 1:13pm | Jul 10, 2026 1:14pm | Jul 10, 2026 10:28pm | Jul 10, 2026 10:28pm | Jul 11, 2026 7:22am | Jul 11, 2026 7:22am | Jul 11, 2026 7:23am | Jul 11, 2026 7:23am |  |  | Fair | No | Call to customer and customer said power is back now and okay
Outage | J.E.26.07.11051 | C001851698 | Stephen Taylor | St.Thomas | Completed | Load_238021 | Lysson - 410 | Jul 10, 2026 1:13pm | Jul 10, 2026 1:14pm | Jul 10, 2026 2:20pm | Jul 10, 2026 2:20pm | Jul 10, 2026 5:58pm | Jul 10, 2026 6:51pm | Jul 10, 2026 6:52pm | Jul 10, 2026 6:52pm | BangingWires |  | Fair | No | Clear line and close up 25kva transformer customer are now ok
Non-Outage | J.E.26.07.10700 | C001851695 | Marlon Brown | Trelawny | Completed | Load_244451 | Duncans - 210 | Jul 10, 2026 1:12pm | Jul 10, 2026 1:13pm | Jul 10, 2026 6:19pm | Jul 10, 2026 6:19pm | Jul 10, 2026 6:57pm | Jul 10, 2026 7:00pm | Jul 10, 2026 7:00pm | Jul 10, 2026 7:00pm | Fire |  | Fair | No | No broken wire seen
Non-Outage | J.E.26.07.10956 | C001851696 | Marlon Brown | Trelawny | Completed | Load_258326 | Duncans - 210 | Jul 10, 2026 1:12pm | Jul 10, 2026 1:13pm | Jul 10, 2026 3:26pm | Jul 10, 2026 4:18pm | Jul 10, 2026 5:01pm | Jul 10, 2026 6:11pm | Jul 10, 2026 6:11pm | Jul 10, 2026 6:11pm |  |  | Fair | No | Voltage found at pothead 165/5=170Voltage leaving at pothead 112/116=228vDisconnected illegal connections @ a pothead that had burnt up wires in it, column, no meter at the premises meter socket bridge out. Service wire removed.
Non-Outage | J.E.26.07.10875 | C001851694 | Marlon Brown | Trelawny | Completed | Load_257002 | Duncans - 210 | Jul 10, 2026 1:11pm | Jul 10, 2026 1:13pm | Jul 10, 2026 3:23pm | Jul 10, 2026 3:24pm | Jul 10, 2026 3:25pm | Jul 10, 2026 3:25pm | Jul 10, 2026 3:25pm | Jul 10, 2026 3:25pm | Fire |  | Fair | No | Unable to locate customer via telephone nor direction
Outage | J.E.26.07.11017 | C001851693 | Marlon Brown | Trelawny | Completed | Load_572246 | Duncans - 210 | Jul 10, 2026 1:11pm | Jul 10, 2026 1:13pm | Jul 10, 2026 1:26pm | Jul 10, 2026 1:26pm | Jul 10, 2026 2:07pm | Jul 10, 2026 3:23pm | Jul 10, 2026 3:23pm | Jul 10, 2026 3:23pm |  |  | SevereWind | No | Primary conductor contact on overhead guy, retention 1 span primarySee permit number 11030 for details. Replaced 15amps junction fuse @ pole number 027392.
Outage | J.E.26.07.10945 | C001851689 | Richard Samuda | Manchester | Completed | Load_258501 | Porus - 310 | Jul 10, 2026 1:09pm | Jul 11, 2026 8:01am | Jul 11, 2026 9:12am | Jul 11, 2026 9:12am | Jul 11, 2026 9:12am | Jul 11, 2026 9:12am | Jul 11, 2026 9:13am | Jul 11, 2026 9:13am | BrokenPole |  | Fair | No | Customer said situation was resolved
Non-Outage | J.E.26.07.11021 | C001851672 | Lancelot Brown | null | Completed | null | null | Jul 10, 2026 1:06pm | Jul 11, 2026 7:55am | Jul 11, 2026 10:09am | Jul 11, 2026 10:13am | Jul 11, 2026 11:42am | Jul 11, 2026 11:46am | Jul 11, 2026 11:46am | Jul 11, 2026 11:46am | BrokenPole |  | Fair | No | 35c4 wooden pole broke leaning more and more in the road also causing service line hanging low pole need to replace ergent please pass on to maintenance department in Hanover mr Richards need ergent attention
Outage | J.E.26.07.10583 | C001851673 | Andre Williams | Trelawny | Completed | Load_247877 | Greenwood - 110 | Jul 10, 2026 1:06pm | Jul 10, 2026 3:24pm | Jul 10, 2026 5:43pm | Jul 10, 2026 5:43pm | Jul 10, 2026 5:43pm | Jul 10, 2026 5:43pm | Jul 10, 2026 5:44pm | Jul 10, 2026 5:44pm |  |  | Fair | No | Unable to locate #not in use
Outage | J.E.26.07.10927 | C001851670 | Raymond Carr | St.Mary | Completed | Load_258412 | Oracabessa - 210 | Jul 10, 2026 1:02pm | Jul 10, 2026 1:58pm | Jul 10, 2026 4:28pm | Jul 10, 2026 4:28pm | Jul 10, 2026 4:53pm | Jul 10, 2026 6:39pm | Jul 10, 2026 6:46pm | Jul 10, 2026 6:46pm |  |  | SevereWind | No | Spliced and retention two spans of broken secondary conductors using 50 ft#2 a, 1#2 preforms, also two spans of sagging conductors were tensioned. Supply restored.
Outage | J.E.26.07.10816 | C001851660 | Jermaine Williams | St.Catherine | Completed | Load_244805 | Rhodens Pen - 310 | Jul 10, 2026 1:00pm | Jul 10, 2026 4:46pm | Jul 10, 2026 10:38pm | Jul 10, 2026 10:38pm | Jul 10, 2026 10:38pm | Jul 10, 2026 6:17pm | Jul 10, 2026 10:39pm | Jul 10, 2026 10:39pm |  |  | SevereWind | No | Repair defective service wire.
Outage | J.E.26.07.11012 | C001851659 | Tyrese Williams | St.Ann | Completed | Load_240260 | Cardiff Hall - 210 | Jul 10, 2026 12:59pm | Jul 10, 2026 1:05pm | Jul 10, 2026 2:23pm | Jul 10, 2026 3:02pm | Jul 10, 2026 3:02pm | Jul 10, 2026 3:03pm | Jul 10, 2026 3:03pm | Jul 10, 2026 3:03pm | BrokenPole |  | Fair | No | Premises found ok
Outage | J.E.26.07.10880 | C001851437 | Romaine Roberts | St.Mary | Completed | Load_329897 | Highgate -110 | Jul 10, 2026 12:58pm | Jul 10, 2026 12:58pm | Jul 10, 2026 2:21pm | Jul 10, 2026 2:21pm | Jul 10, 2026 2:22pm | Jul 10, 2026 2:27pm | Jul 10, 2026 2:27pm | Jul 10, 2026 2:27pm | Fire |  | Fair | No | High wind bang sagging secondary conductor open and close 25 kva transformer to retention conductor also clean and remake joints at transformer drop lead
Outage | J.E.26.07.10993 | C001851434 | Daniel Francis | St.Ann | Completed | Load_253965 | Ocho Rios - 310 | Jul 10, 2026 12:53pm | Jul 10, 2026 3:51pm | Jul 10, 2026 5:41pm | Jul 10, 2026 5:41pm | Jul 10, 2026 6:03pm | Jul 10, 2026 6:05pm | Jul 10, 2026 6:05pm | Jul 10, 2026 6:05pm |  |  | Fair | No | Premises lock no one at the house
Outage | J.E.26.07.10980 | C001851228 | Gregory Grossett | Portland | Completed | Load_260585 | Port Antonio - 410 | Jul 10, 2026 12:49pm | Jul 10, 2026 3:26pm | Jul 10, 2026 5:45pm | Jul 10, 2026 5:45pm | Jul 10, 2026 6:26pm | Jul 10, 2026 6:30pm | Jul 10, 2026 6:36pm | Jul 10, 2026 6:36pm |  | Y | Fair | No | 10 amps junction fuse blown no pole number at location, cause by bamboo fall on line clear and restore area, material used 1-10 amps fuse
Non-Outage | J.E.26.07.10976 | C001850244 | Locksley Allen | St.Mary | Completed | Load_241220 | Highgate - 210 | Jul 10, 2026 12:44pm | Jul 10, 2026 12:46pm | Jul 10, 2026 1:27pm | Jul 10, 2026 1:27pm | Jul 10, 2026 1:27pm | Jul 10, 2026 1:30pm | Jul 10, 2026 1:30pm | Jul 10, 2026 1:30pm |  |  | Fair | No | Secondary line lying on the ground. Bucket truck is needed
Non-Outage | J.E.26.07.10815 | C001850239 | Tyrese Williams | St.Ann | Completed | Load_258297 | Cardiff Hall - 210 | Jul 10, 2026 12:37pm | Jul 10, 2026 12:43pm | Jul 10, 2026 1:04pm | Jul 10, 2026 2:23pm | Jul 10, 2026 3:01pm | Jul 10, 2026 3:01pm | Jul 10, 2026 3:01pm | Jul 10, 2026 3:01pm |  |  | Fair | No | Remade 2 service wire joints at pole use 1 pg clamp
Outage | J.E.26.07.10936 | C001850114 | Omar King | St.Ann | Completed | Load_246929 | Ocho Rios - 410 | Jul 10, 2026 12:31pm | Jul 10, 2026 12:32pm | Jul 10, 2026 1:36pm | Jul 10, 2026 1:36pm | Jul 10, 2026 1:39pm | Jul 10, 2026 1:39pm | Jul 10, 2026 1:41pm | Jul 10, 2026 1:41pm | BrokenWire |  | Fair | No | Problem as been resolved said customer P Davis
Non-Outage | J.E.26.07.10933 | C001849838 | Tyrese Williams | St.Ann | Completed | Load_267462 | Upper White River - 210 | Jul 10, 2026 12:30pm | Jul 11, 2026 8:17am | Jul 11, 2026 8:59am | Jul 11, 2026 2:15pm | Jul 11, 2026 2:15pm | Jul 11, 2026 2:16pm | Jul 11, 2026 2:17pm | Jul 11, 2026 2:17pm | Fire |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.07.10742 | C001849730 | Derrick Dawkins | St.James | Completed | Load_1001863 | Bogue - 310 | Jul 10, 2026 12:29pm | Jul 10, 2026 12:34pm | Jul 10, 2026 1:23pm | Jul 10, 2026 1:23pm | Jul 10, 2026 2:07pm | Jul 10, 2026 2:37pm | Jul 10, 2026 2:38pm | Jul 10, 2026 2:38pm |  |  | Fair | No | Found 65 trip saver down patrol and found nothing on the line did a test close and hold at pole lab6-677
Outage | J.E.26.07.10888 | C001849729 | Calvin Poorman | St.Ann | Completed | Load_267596 | Roaring River - 410 | Jul 10, 2026 12:26pm | Jul 10, 2026 12:34pm | Jul 10, 2026 12:37pm | Jul 10, 2026 12:37pm | Jul 10, 2026 12:52pm | Jul 10, 2026 1:20am | Jul 10, 2026 1:20pm | Jul 10, 2026 1:20pm | Fire |  | Fair | No | Splice n retention one span of secondary neutral using two clamp and 3ft no2 conductor
Outage | J.E.26.07.10889 | C001849719 | Raymond Lewis | St.Ann | Completed | Load_259193 | Roaring River - 210 | Jul 10, 2026 12:19pm | Jul 10, 2026 12:22pm | Jul 10, 2026 1:47pm | Jul 10, 2026 1:47pm | Jul 10, 2026 2:10pm | Jul 10, 2026 2:11pm | Jul 10, 2026 2:11pm | Jul 10, 2026 2:11pm |  |  | SevereWind | No | Refuse and close 25amp junction
Outage | J.E.26.07.10638 | C001849716 | Andrew Powell | St.Elizabeth | Completed | Load_264265 | Maggotty - 210 | Jul 10, 2026 12:16pm | Jul 10, 2026 3:16pm | Jul 10, 2026 5:44pm | Jul 10, 2026 5:44pm | Jul 10, 2026 5:44pm | Jul 10, 2026 5:46pm | Jul 10, 2026 5:46pm | Jul 10, 2026 5:46pm |  |  | SevereWind | No | Called related to blown fuse by Kildare to Hounslow, supply restored.
Outage | J.E.26.07.10751 | C001849714 | Edward Royal | KSAS | Completed | Load_269362 | Hunts Bay - 210 | Jul 10, 2026 12:14pm | Jul 10, 2026 12:14pm | Jul 10, 2026 1:49pm | Jul 10, 2026 1:49pm | Jul 10, 2026 1:49pm | Jul 10, 2026 2:29pm | Jul 10, 2026 2:29pm | Jul 10, 2026 2:29pm | BrokenWire |  | Fair | No | Spliced and reconnected service cable using 80 ft service cable 6 single bolt clamp
Outage | J.E.26.07.10538 | C001849560 | Cliton Henry | St.Mary | Completed | Load_354886 | Blackstonedge - 110 | Jul 10, 2026 12:05pm | Jul 10, 2026 12:06pm | Jul 10, 2026 8:23pm | Jul 10, 2026 8:23pm | Jul 10, 2026 8:23pm | Jul 10, 2026 8:24pm | Jul 10, 2026 8:25pm | Jul 10, 2026 8:25pm |  |  | Fair | No | Supply restored, related to outage #09082. The customer confirmed supply available.
Outage | J.E.26.07.10474 | C001849459 | Andrew Powell | Manchester | Completed | Load_246108 | Spur Tree - 210 | Jul 10, 2026 12:01pm | Jul 10, 2026 3:16pm | Jul 10, 2026 3:27pm | Jul 10, 2026 3:27pm | Jul 10, 2026 3:27pm | Jul 10, 2026 3:28pm | Jul 10, 2026 3:28pm | Jul 10, 2026 3:28pm |  |  | Fair | No | Manchester called.
Outage | J.E.26.07.10821 | C001848509 | Andre Smith | KSAN | Completed | Load_265970 | Washington Blvd - 310 | Jul 10, 2026 11:58am | Jul 10, 2026 11:58am | Jul 10, 2026 12:55pm | Jul 10, 2026 12:55pm | Jul 10, 2026 12:55pm | Jul 10, 2026 12:55pm | Jul 10, 2026 12:55pm | Jul 10, 2026 12:55pm |  |  | Fair | No | 15 kva defective transformer found maintenance department required to replace same
Outage | J.E.26.07.10831 | C001848510 | Andre Smith | KSAN | Completed | Load_243825 | Washington Blvd - 310 | Jul 10, 2026 11:58am | Jul 10, 2026 11:58am | Jul 10, 2026 12:06pm | Jul 10, 2026 12:06pm | Jul 10, 2026 12:53pm | Jul 10, 2026 12:54pm | Jul 10, 2026 12:55pm | Jul 10, 2026 12:55pm | Fire |  | Fair | No | 15 kva defective transformer found maintenance department required to replace same
Non-Outage | J.E.26.07.09058 | C001848508 | Romaine Roberts | null | Completed | null | null | Jul 10, 2026 11:56am | Jul 10, 2026 11:57am | Jul 10, 2026 2:27pm | Jul 10, 2026 2:27pm | Jul 10, 2026 4:15pm | Jul 10, 2026 4:42pm | Jul 10, 2026 4:46pm | Jul 10, 2026 4:46pm |  |  | Fair | No | Bamboo fall on secondary line and burn down 3 span of secondary phase clear line and splice and retention conductor open and close 25 kva transformer power restore
Outage | J.E.26.07.10415 | C001848506 | Wan Carlos Scarlett | St.Catherine | Completed | Load_576216 | Twickenham - 210 | Jul 10, 2026 11:54am | Jul 10, 2026 11:55am | Jul 10, 2026 1:01pm | Jul 10, 2026 1:01pm | Jul 10, 2026 2:27pm | Jul 10, 2026 2:40pm | Jul 10, 2026 2:41pm | Jul 10, 2026 2:41pm |  |  | Fair | No | Found customer 2 wire service at pole with phase and neutral corroded use 2 one bolt clamps at open secondary line phase and neutral readings 114
Outage | J.E.26.07.10835 | C001848505 | Collin Robinson | Portland | Completed | Load_250952 | Port Antonio - 310 | Jul 10, 2026 11:54am | Jul 10, 2026 3:27pm | Jul 10, 2026 4:50pm | Jul 10, 2026 4:50pm | Jul 10, 2026 5:28pm | Jul 10, 2026 5:31pm | Jul 10, 2026 5:31pm | Jul 10, 2026 5:31pm |  |  | Fair | No | Replace two corroded pen union at pot head voltage 117 118 235v
Outage | J.E.26.07.10838 | C001848504 | Collin Robinson | Portland | Completed | Load_257634 | Port Antonio - 310 | Jul 10, 2026 11:54am | Jul 10, 2026 3:27pm | Jul 10, 2026 5:37pm | Jul 10, 2026 5:37pm | Jul 10, 2026 6:02pm | Jul 10, 2026 6:50pm | Jul 10, 2026 6:51pm | Jul 10, 2026 6:51pm |  |  | Fair | No | Isolate 25KVA transformer to replace corroded clamps on transformer drop lead voltage 120 v 120v 240v
Outage | J.E.26.07.10842 | C001848503 | Tyrese Williams | St.Ann | Completed | Load_259598 | Cardiff Hall - 210 | Jul 10, 2026 11:54am | Jul 10, 2026 11:56am | Jul 10, 2026 12:31pm | Jul 10, 2026 2:21pm | Jul 10, 2026 2:22pm | Jul 10, 2026 2:23pm | Jul 10, 2026 2:23pm | Jul 10, 2026 2:23pm |  |  | Fair | No | Premises found ok call related to defective transformer drop Leeds
Outage | J.E.26.07.10822 | C001848501 | Raymond Carr | St.Mary | Completed | Load_269166 | Oracabessa - 210 | Jul 10, 2026 11:49am | Jul 10, 2026 11:49am | Jul 10, 2026 2:43pm | Jul 10, 2026 2:43pm | Jul 10, 2026 4:16pm | Jul 10, 2026 3:15pm | Jul 10, 2026 4:27pm | Jul 10, 2026 4:27pm | BrokenWire |  | Fair | No | One leg of dislodged service wire was reconnected at JPS pole. Voltage readings 117/115/232.
Outage | J.E.26.07.10721 | C001848500 | Elvis Trowers | KSAN | Completed | Load_246651 | Constant Spring - 210 | Jul 10, 2026 11:48am | Jul 10, 2026 11:48am | Jul 10, 2026 12:56pm | Jul 10, 2026 12:56pm | Jul 10, 2026 1:36pm | Jul 10, 2026 2:22pm | Jul 10, 2026 2:22pm | Jul 10, 2026 2:22pm |  | Y | Fair | Yes | Areas was found without electricity supply when checked and a blown 30 amp junction fuse was found during patrol and was replaced after at pole #0011261. This is over by coopers hill.
Outage | J.E.26.07.10709 | C001847995 | Marlon Authors | Manchester | Completed | Load_246385 | Spur Tree - 210 | Jul 10, 2026 11:38am | Jul 10, 2026 11:47am | Jul 10, 2026 1:03pm | Jul 10, 2026 1:03pm | Jul 10, 2026 1:37pm | Jul 10, 2026 2:31pm | Jul 10, 2026 2:31pm | Jul 10, 2026 2:31pm | Fire |  | SevereWind | No | Patrol and found one pole span of primary neutral banging on the secondary upper phase conductor at the intermediate pole caused by severe winds. Isolate and close 25 kva transformer circuit no pole #, to affix same to intermediate pole using one D iron, bolt, spool. Restored supply ok
Outage | J.E.26.07.10753 | C001847937 | Richard Samuda | Manchester | Completed | Load_254861 | Kendal - 210 | Jul 10, 2026 11:36am | Jul 10, 2026 4:10pm | Jul 10, 2026 5:56pm | Jul 10, 2026 6:05pm | Jul 10, 2026 6:05pm | Jul 10, 2026 6:35pm | Jul 10, 2026 6:35pm | Jul 10, 2026 6:35pm |  |  | Fair | No | Remake joint at customer pothead that was corroded causing customer to experience low voltage voltage: 113, 113 225
Non-Outage | J.E.26.07.10756 | C001847528 | Marlon Authors | Manchester | Completed | Load_246385 | Spur Tree - 210 | Jul 10, 2026 11:31am | Jul 10, 2026 11:31am | Jul 10, 2026 2:33pm | Jul 10, 2026 2:33pm | Jul 10, 2026 2:33pm | Jul 10, 2026 2:32pm | Jul 10, 2026 2:34pm | Jul 10, 2026 2:34pm | Fire |  | SevereWind | No | Supply restored to the area
Outage | J.E.26.07.10471 | C001847525 | Evan Spaulding | St.Mary | Completed | Load_258507 | Highgate - 210 | Jul 10, 2026 11:29am | Jul 10, 2026 11:32am | Jul 10, 2026 12:54pm | Jul 10, 2026 12:54pm | Jul 10, 2026 12:54pm | Jul 10, 2026 12:55pm | Jul 10, 2026 12:57pm | Jul 10, 2026 12:57pm |  |  | SevereWind | No | Operation team on location carrying out repairs
Outage | J.E.26.07.10501 | C001847522 | Evan Spaulding | St.Mary | Completed | Load_265280 | Highgate - 210 | Jul 10, 2026 11:29am | Jul 10, 2026 11:31am | Jul 10, 2026 11:54am | Jul 10, 2026 11:54am | Jul 10, 2026 12:06pm | Jul 10, 2026 12:44pm | Jul 10, 2026 12:48pm | Jul 10, 2026 12:48pm |  |  | SevereWind | No | Line section from Knutsfield to Robins Bay badly needs some maintenance work,leaning poles,sagging conductors bushing,Replace 1-20 amps junction fuse at pole number 0010851.
Outage | J.E.26.07.10562 | C001847523 | Evan Spaulding | St.Mary | Completed | Load_262285 | Highgate - 210 | Jul 10, 2026 11:29am | Jul 10, 2026 11:30am | Jul 10, 2026 12:58pm | Jul 10, 2026 12:58pm | Jul 10, 2026 12:58pm | Jul 10, 2026 12:59pm | Jul 10, 2026 12:59pm | Jul 10, 2026 12:59pm |  |  | Fair | No | Customer says issue was internal and was corrected.
Outage | J.E.26.07.10570 | C001847526 | Evan Spaulding | St.Mary | Completed | Load_267975 | Highgate - 210 | Jul 10, 2026 11:29am | Jul 10, 2026 11:54am | Jul 10, 2026 1:09pm | Jul 10, 2026 1:09pm | Jul 10, 2026 2:17pm | Jul 10, 2026 2:45pm | Jul 10, 2026 2:46pm | Jul 10, 2026 2:46pm |  | Y | Fair | No | Remove Bamboo from primary line and replace 1-10 amps junction fuse,no pole number.
Outage | J.E.26.07.10647 | C001847527 | Richard Samuda | Manchester | Completed | Load_255195 | Kendal - 310 | Jul 10, 2026 11:29am | Jul 11, 2026 7:25am | Jul 11, 2026 8:59am | Jul 11, 2026 8:59am | Jul 11, 2026 9:12am | Jul 11, 2026 9:12am | Jul 11, 2026 9:12am | Jul 11, 2026 9:12am | BrokenPole |  | Fair | No | Customer said power was restored
Outage | J.E.26.07.10757 | C001847524 | Evan Spaulding | St.Mary | Completed | Load_252911 | Highgate - 210 | Jul 10, 2026 11:29am | Jul 10, 2026 11:30am | Jul 10, 2026 11:44am | Jul 10, 2026 1:02pm | Jul 10, 2026 1:02pm | Jul 10, 2026 1:02pm | Jul 10, 2026 1:02pm | Jul 10, 2026 1:02pm | Fire |  | SevereWind | No | Customer says issue was resolved.
Non-Outage | J.E.26.06.35222 | C001847094 | Orville Lee | Portmore | Completed | Load_248619 | Naggo Head - 510 | Jul 10, 2026 11:26am | Jul 10, 2026 11:27am | Jul 10, 2026 11:33am | Jul 10, 2026 1:03pm | Jul 10, 2026 1:03pm | Jul 10, 2026 1:05pm | Jul 10, 2026 1:05pm | Jul 10, 2026 1:05pm |  |  | Fair | No | Premises found ok Issue was resolved by a technician Voltage 116V117V233V
Non-Outage | J.E.26.06.39742 | C001847092 | Orville Lee | Portmore | Completed | Load_257303 | Naggo Head - 510 | Jul 10, 2026 11:26am | Jul 10, 2026 11:27am | Jul 10, 2026 11:33am | Jul 10, 2026 2:38pm | Jul 10, 2026 2:38pm | Jul 10, 2026 2:38pm | Jul 10, 2026 2:39pm | Jul 10, 2026 2:39pm |  |  | Fair | No | Customer connected to Hexing boxMultiple customer affected with voltage fluctuation Refer to maintenance
Non-Outage | J.E.26.07.01959 | C001847090 | Orville Lee | Portmore | Completed | Load_257303 | Naggo Head - 510 | Jul 10, 2026 11:26am | Jul 10, 2026 11:27am | Jul 10, 2026 11:33am | Jul 10, 2026 2:05pm | Jul 10, 2026 2:05pm | Jul 10, 2026 2:36pm | Jul 10, 2026 2:38pm | Jul 10, 2026 2:38pm |  |  | Fair | No | Customer connected to Hexing boxMultiple customer affected with voltage fluctuation Refer to maintenance
Non-Outage | J.E.26.07.02569 | C001847091 | Orville Lee | Portmore | Completed | Load_266997 | Naggo Head - 510 | Jul 10, 2026 11:26am | Jul 10, 2026 11:27am | Jul 10, 2026 11:33am | Jul 10, 2026 11:41am | Jul 10, 2026 11:42am | Jul 10, 2026 11:50am | Jul 10, 2026 11:51am | Jul 10, 2026 11:51am |  |  | Fair | No | Premises closed Voltage119v120v239vCall to costumer unanswered
Non-Outage | J.E.26.07.05101 | C001847089 | Orville Lee | Portmore | Completed | Load_248619 | Naggo Head - 510 | Jul 10, 2026 11:26am | Jul 10, 2026 11:27am | Jul 10, 2026 11:33am | Jul 10, 2026 12:16pm | Jul 10, 2026 12:41pm | Jul 10, 2026 1:03pm | Jul 10, 2026 1:03pm | Jul 10, 2026 1:03pm |  |  | Fair | No | Premises found ok Issue was resolved by a technician Voltage 116V117V233V
Non-Outage | J.E.26.07.10576 | C001847088 | Neville Spencer | Clarendon | Completed | Load_243522 | May Pen - 110 | Jul 10, 2026 11:23am | Jul 10, 2026 11:23am | Jul 10, 2026 11:30am | Jul 10, 2026 11:30am | Jul 10, 2026 12:54pm | Jul 10, 2026 12:54pm | Jul 10, 2026 1:46pm | Jul 10, 2026 1:46pm |  |  | Fair | No | Remade defective phase and neutral joints at pothead on 3, wire service used 3,6/6 sleeves voltage reading 113=114 229 supply restored.
Outage | J.E.26.07.10421 | C001846131 | Hartley Chin | Clarendon | Completed | Load_294684 | Monymusk - 210 | Jul 10, 2026 11:20am | Jul 10, 2026 11:21am | Jul 10, 2026 12:46pm | Jul 10, 2026 1:07pm | Jul 10, 2026 1:18pm | Jul 10, 2026 1:25pm | Jul 10, 2026 1:34pm | Jul 10, 2026 1:34pm |  |  | SevereWind | No | Ref to maintenance!!! Found defective 15 KVA transformer (no pole #) transformer supply’s customer to HX 27121979 … transformer was found with H1 , H2 bushings dislodged from transformer … maintenance to repair urgently…
Outage | J.E.26.07.10454 | C001846129 | Hartley Chin | Clarendon | Completed | Load_268927 | Monymusk - 210 | Jul 10, 2026 11:20am | Jul 10, 2026 11:21am | Jul 10, 2026 1:35pm | Jul 10, 2026 1:35pm | Jul 10, 2026 1:35pm | Jul 10, 2026 1:40pm | Jul 10, 2026 1:50pm | Jul 10, 2026 1:50pm |  |  | SevereWind | No | Found blown 10 amp junction fuse , cause by defective 15 KAV transformer found on line related to (job # 10421) .. line patrolled and found okay … refused junction…
Outage | J.E.26.07.10465 | C001846130 | Hartley Chin | Clarendon | Completed | Load_252389 | Parnassus - 210 | Jul 10, 2026 11:20am | Jul 10, 2026 11:21am | Jul 10, 2026 8:58pm | Jul 10, 2026 8:58pm | Jul 10, 2026 11:11pm | Jul 10, 2026 11:11pm | Jul 10, 2026 11:12pm | Jul 10, 2026 11:12pm |  |  | Fair | No | Found okay … voltage read 111v , 112v .
Outage | J.E.26.07.10645 | C001846132 | Hartley Chin | Clarendon | Completed | Load_301017 | Monymusk - 210 | Jul 10, 2026 11:20am | Jul 10, 2026 11:21am | Jul 10, 2026 1:51pm | Jul 10, 2026 3:17pm | Jul 10, 2026 3:26pm | Jul 10, 2026 3:27pm | Jul 10, 2026 3:29pm | Jul 10, 2026 3:29pm | BangingWires |  | SevereWind | No | Found okay , voltage read 110 v … customer has internal issue…
Outage | J.E.26.07.10739 | C001846133 | Hartley Chin | Clarendon | Completed | Load_260226 | Parnassus - 210 | Jul 10, 2026 11:20am | Jul 10, 2026 11:21am | Jul 10, 2026 4:50pm | Jul 10, 2026 5:04pm | Jul 10, 2026 5:47pm | Jul 10, 2026 6:13pm | Jul 10, 2026 6:14pm | Jul 10, 2026 6:14pm | TreeContact |  | SevereWind | No | Repair service phase found @ customer pot head … use 2 clamp … voltage read 113v , 114v ..
Outage | J.E.26.07.07234 | C001846128 | Neville Spencer | Clarendon | Completed | Load_352557 | May Pen - 110 | Jul 10, 2026 11:18am | Jul 10, 2026 11:18am | Jul 11, 2026 11:59am | Jul 11, 2026 11:59am | Jul 11, 2026 12:55pm | Jul 11, 2026 12:55pm | Jul 11, 2026 1:30pm | Jul 11, 2026 1:30pm | BrokenWire |  | Fair | No | Splice and retention broken 2, wire service usedv 50 ft #6 triplex, 2 clamps voltage reading 116 .
Non-Outage | J.E.26.07.10724 | C001846127 | Edward Royal | KSAS | Completed | Load_261035 | Duhaney - 410 | Jul 10, 2026 11:16am | Jul 10, 2026 11:17am | Jul 10, 2026 11:41pm | Jul 10, 2026 11:41pm | Jul 10, 2026 11:41pm | Jul 10, 2026 11:42pm | Jul 10, 2026 11:42pm | Jul 10, 2026 11:42pm |  |  | Fair | No | Premises found close
Outage | J.E.26.07.09118 | C001846126 | Neville Spencer | Clarendon | Completed | Load_257707 | May Pen - 110 | Jul 10, 2026 11:15am | Jul 10, 2026 11:16am | Jul 10, 2026 1:48pm | Jul 10, 2026 1:48pm | Jul 10, 2026 2:25pm | Jul 10, 2026 2:25pm | Jul 10, 2026 2:26pm | Jul 10, 2026 2:26pm | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Found ok call resolved yesterday.
Non-Outage | J.E.26.01.34768 | C001845619 | Floyd Taylor | null | Completed | null | null | Jul 10, 2026 10:59am | Jul 10, 2026 11:00am | Jul 10, 2026 3:02pm | Jul 10, 2026 3:02pm | Jul 10, 2026 3:03pm | Jul 10, 2026 3:03pm | Jul 10, 2026 3:04pm | Jul 10, 2026 3:04pm |  |  | Fair | No | Unable to locate or contact customer phone number invalid
Non-Outage | J.E.26.03.11951 | C001845617 | Floyd Taylor | null | Completed | null | null | Jul 10, 2026 10:59am | Jul 10, 2026 11:00am | Jul 10, 2026 12:54pm | Jul 10, 2026 12:54pm | Jul 10, 2026 1:52pm | Jul 10, 2026 1:57pm | Jul 10, 2026 1:58pm | Jul 10, 2026 1:58pm | BrokenPole |  | Fair | No | Pole belongs to cable company
Non-Outage | J.E.26.04.05804 | C001845615 | Floyd Taylor | St.James | Completed | Load_241873 | Queens Drive - 710 | Jul 10, 2026 10:59am | Jul 10, 2026 11:00am | Jul 10, 2026 1:58pm | Jul 10, 2026 1:59pm | Jul 10, 2026 2:39pm | Jul 10, 2026 3:01pm | Jul 10, 2026 3:01pm | Jul 10, 2026 3:01pm |  |  | Fair | No | Unable to locate or contact customer, directions poor
Outage | J.E.26.07.10567 | C001845611 | Milton Charlton | KSAS | Completed | Load_246230 | Up Park Camp - 410 | Jul 10, 2026 10:55am | Jul 10, 2026 10:55am | Jul 10, 2026 5:37pm | Jul 10, 2026 5:37pm | Jul 10, 2026 6:54pm | Jul 10, 2026 6:35pm | Jul 10, 2026 6:58pm | Jul 10, 2026 6:58pm |  |  | Fair | No | Premises closed. No one answering knock at the door.
Outage | J.E.26.07.10665 | C001845610 | Milton Charlton | KSAS | Completed | Load_245377 | Up Park Camp - 410 | Jul 10, 2026 10:55am | Jul 10, 2026 10:55am | Jul 10, 2026 6:59pm | Jul 10, 2026 6:59pm | Jul 10, 2026 6:59pm | Jul 10, 2026 7:00pm | Jul 10, 2026 7:02pm | Jul 10, 2026 7:02pm |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.07.10631 | C001845605 | Hopeton Henry | St.Thomas | Completed | Load_252203 | Good Year - 210 | Jul 10, 2026 10:50am | Jul 10, 2026 3:09pm | Jul 10, 2026 4:32pm | Jul 10, 2026 8:06pm | Jul 10, 2026 8:06pm | Jul 10, 2026 8:06pm | Jul 10, 2026 8:07pm | Jul 10, 2026 8:07pm |  |  | Fair | No | Check and found ok
Non-Outage | J.E.26.07.10613 | C001845603 | Edward Royal | null | Completed | null | null | Jul 10, 2026 10:49am | Jul 10, 2026 10:50am | Jul 10, 2026 11:31am | Jul 10, 2026 11:31am | Jul 10, 2026 11:31am | Jul 10, 2026 12:23pm | Jul 10, 2026 12:23pm | Jul 10, 2026 12:23pm |  |  | Fair | No | Customer have internal problems customer breaker trip problem was resolved
Outage | J.E.26.07.10635 | C001845604 | Edward Royal | KSAN | Completed | Load_252722 | Washington Blvd - 710 | Jul 10, 2026 10:49am | Jul 10, 2026 10:50am | Jul 10, 2026 12:23pm | Jul 10, 2026 12:23pm | Jul 10, 2026 12:23pm | Jul 10, 2026 12:24pm | Jul 10, 2026 12:24pm | Jul 10, 2026 12:24pm |  |  | Fair | No | Meter not responding meter need to be check reffered to field service
Non-Outage | J.E.26.07.10657 | C001845599 | Roemello Brown | Trelawny | Completed | Load_258502 | Greenwood - 110 | Jul 10, 2026 10:45am | Jul 10, 2026 10:45am | Jul 10, 2026 11:05am | Jul 10, 2026 11:05am | Jul 10, 2026 11:11am | Jul 10, 2026 11:11am | Jul 10, 2026 11:14am | Jul 10, 2026 11:14am |  |  | Fair | No | Meter burn needs field service team to assist please Voltage found 117/118/235Voltage leave 117/118/235
Outage | J.E.26.07.09195 | C001845596 | Christopher West | St.Catherine | Completed | Load_239309 | Rhodens Pen - 410 | Jul 10, 2026 10:45am | Jul 10, 2026 10:46am | Jul 10, 2026 10:52am | Jul 10, 2026 10:52am | Jul 10, 2026 1:38pm | Jul 10, 2026 2:40pm | Jul 10, 2026 3:22pm | Jul 10, 2026 3:22pm | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Dislodged neutral at pole#0143965 came in contact with the lower phase of the open secondary, a 25kva transformer was de-energized, used 1 D-iron, one #2 preform and one 12’ bolt to effect repairs, transformer was re-energized, area now ok. NB. Pole mentioned above, 40’ C4 single phase primary, D/V construction is 98% rotten and leaning towards the roadway, requesting a memo be sent to Mr. A. Murray to have pole replaced ASAP.
Outage | J.E.26.07.10481 | C001845598 | Christopher West | St.Catherine | Completed | Load_239309 | Rhodens Pen - 410 | Jul 10, 2026 10:45am | Jul 10, 2026 10:46am | Jul 10, 2026 3:22pm | Jul 10, 2026 3:22pm | Jul 10, 2026 3:22pm | Jul 10, 2026 2:40pm | Jul 10, 2026 3:23pm | Jul 10, 2026 3:23pm | BrokenPole |  | Fair | No | Dislodged neutral at pole#0143965 came in contact with the lower phase of the open secondary, a 25kva transformer was de-energized, used 1 D-iron, one #2 preform and one 12’ bolt to effect repairs, transformer was re-energized, area now ok. NB. Pole mentioned above, 40’ C4 single phase primary, D/V construction is 98% rotten and leaning towards the roadway, requesting a memo be sent to Mr. A. Murray to have pole replaced ASAP.
Non-Outage | J.E.26.07.09297 | C001845595 | Tajay Bernard | Hanover | Completed | Load_260959 | Orange Bay - 210 | Jul 10, 2026 10:43am | Jul 10, 2026 10:44am | Jul 10, 2026 10:49am | Jul 10, 2026 10:50am | Jul 10, 2026 11:37am | Jul 10, 2026 11:52am | Jul 10, 2026 11:52am | Jul 10, 2026 11:52am | BrokenPole |  | Fair | No | Customer has internal problems
Non-Outage | J.E.26.07.10232 | C001845594 | Tajay Bernard | Hanover | Completed | Load_573746 | Orange Bay - 210 | Jul 10, 2026 10:43am | Jul 10, 2026 10:44am | Jul 10, 2026 11:52am | Jul 10, 2026 11:52am | Jul 10, 2026 12:13pm | Jul 10, 2026 12:33pm | Jul 10, 2026 12:35pm | Jul 10, 2026 12:35pm |  |  | Fair | No | Check and found customer meter burned need to be replaced urgently refer to field service voltage found 115/113/228
Outage | J.E.26.07.10166 | C001845592 | Rusean Allen | KSAS | Completed | Load_242532 | Cane River - 610 | Jul 10, 2026 10:42am | Jul 10, 2026 10:45am | Jul 10, 2026 11:12am | Jul 10, 2026 11:12am | Jul 10, 2026 11:30am | Jul 10, 2026 12:01pm | Jul 10, 2026 12:01pm | Jul 10, 2026 12:01pm |  |  | Fair | No | 1x 30amp fuse found 1x 30amp fuse replaced
Outage | J.E.26.07.10611 | C001845588 | Richard Samuda | Manchester | Completed | Load_244436 | Kendal - 210 | Jul 10, 2026 10:41am | Jul 10, 2026 4:11pm | Jul 10, 2026 4:51pm | Jul 10, 2026 4:51pm | Jul 10, 2026 5:35pm | Jul 10, 2026 5:52pm | Jul 10, 2026 5:53pm | Jul 10, 2026 5:53pm |  |  | Fair | No | Pole number 551361 found 25kva transformer blown patrol line found nothing replaced fuse customer back
Outage | J.E.26.07.10605 | C001845582 | Omar King | St.Ann | Completed | Load_243936 | Ocho Rios - 410 | Jul 10, 2026 10:34am | Jul 10, 2026 10:34am | Jul 10, 2026 11:18am | Jul 10, 2026 11:18am | Jul 10, 2026 11:32am | Jul 10, 2026 11:34am | Jul 10, 2026 11:35am | Jul 10, 2026 11:35am |  |  | Fair | No | Found a 50 amp junction fuse blow cause by tree contact fuse as been replaced area is now with supply
Outage | J.E.26.07.10615 | C001845581 | Omar King | St.Ann | Completed | Load_255452 | Ocho Rios - 410 | Jul 10, 2026 10:34am | Jul 10, 2026 10:34am | Jul 10, 2026 11:35am | Jul 10, 2026 11:35am | Jul 10, 2026 11:35am | Jul 10, 2026 11:35am | Jul 10, 2026 11:36am | Jul 10, 2026 11:36am |  |  | Fair | No | Found a 50 amp junction fuse blow cause by tree contact fuse as been replaced area is now with supply
Outage | J.E.26.07.10627 | C001845580 | Tyrese Williams | St.Ann | Completed | Load_259557 | Cardiff Hall - 210 | Jul 10, 2026 10:33am | Jul 10, 2026 10:34am | Jul 10, 2026 12:31pm | Jul 10, 2026 2:19pm | Jul 10, 2026 2:19pm | Jul 10, 2026 2:20pm | Jul 10, 2026 2:20pm | Jul 10, 2026 2:20pm |  |  | Fair | No | Premises found ok call related to defective transformer drop leed
Outage | J.E.26.07.10588 | C001845576 | Denton Williams | Portland | Completed | Load_261023 | Port Antonio - 410 | Jul 10, 2026 10:18am | Jul 10, 2026 10:18am | Jul 10, 2026 11:49am | Jul 10, 2026 11:49am | Jul 10, 2026 1:04pm | Jul 10, 2026 1:04pm | Jul 10, 2026 1:07pm | Jul 10, 2026 1:07pm | BrokenWire |  | Fair | No | Corrosion at 25kva transformer drop leads. Open transformer switch and replaced 8 one bolt clamps to fix corrosion issue. Voltage readings leave 118v, 118v & 239v.
Outage | J.E.26.07.10549 | C001845571 | Andrew Powell | Manchester | Completed | Load_265170 | Spur Tree - 210 | Jul 10, 2026 10:14am | Jul 10, 2026 3:16pm | Jul 10, 2026 7:13pm | Jul 10, 2026 7:13pm | Jul 10, 2026 7:17pm | Jul 10, 2026 7:17pm | Jul 10, 2026 7:18pm | Jul 10, 2026 7:18pm |  |  | SevereWind | No | Premises not located inadequately direction contact customer by telephone unsuccessful.
Outage | J.E.26.07.10560 | C001845572 | Andrew Powell | St.Elizabeth | Completed | Load_237865 | Maggotty - 210 | Jul 10, 2026 10:14am | Jul 10, 2026 3:16pm | Jul 10, 2026 3:37pm | Jul 10, 2026 3:38pm | Jul 10, 2026 5:18pm | Jul 10, 2026 5:39pm | Jul 10, 2026 5:43pm | Jul 10, 2026 5:43pm |  |  | SevereWind | No | Patrol and found clear, replace one blown 40 amp junction fuse by Kildare to Hounslow, no pole number by switch location, restore supply okay.
Outage | J.E.26.07.10555 | C001845569 | Elvis Trowers | KSAN | Completed | Load_240558 | Washington Blvd - 510 | Jul 10, 2026 10:12am | Jul 10, 2026 11:59am | Jul 11, 2026 9:38am | Jul 11, 2026 9:38am | Jul 11, 2026 10:06am | Jul 11, 2026 10:46am | Jul 11, 2026 10:46am | Jul 11, 2026 10:46am |  |  | Fair | Yes | Happened to be internal when checked customer was advised to contact an electrician, voltage when checked was left at R=116 +B =115 and Y=197,R-B =235,Y-B =236.
Outage | J.E.26.07.10486 | C001845565 | Marlon Authors | Manchester | Completed | Load_573534 | Spur Tree - 210 | Jul 10, 2026 10:07am | Jul 10, 2026 10:08am | Jul 10, 2026 11:28am | Jul 10, 2026 11:28am | Jul 10, 2026 12:37pm | Jul 10, 2026 12:55pm | Jul 10, 2026 12:58pm | Jul 10, 2026 12:58pm |  |  | SevereWind | No | Supply checked and found two blown 10 amp fuses that protects 100kva transformers in bankers 3 caused by birds. Replace same and supply restored ok
Outage | J.E.26.07.09629 | C001845559 | Richard Nicholas | St.Catherine | Completed | Load_256805 | New Michelton - 410 | Jul 10, 2026 10:06am | Jul 10, 2026 10:06am | Jul 10, 2026 1:33pm | Jul 10, 2026 1:33pm | Jul 10, 2026 1:33pm | Jul 10, 2026 1:48pm | Jul 10, 2026 1:49pm | Jul 10, 2026 1:49pm |  |  | Fair | No | Area found ok,supply was restored yesterday.
Outage | J.E.26.07.10580 | C001845557 | Omar King | St.Ann | Completed | Load_238796 | Ocho Rios - 410 | Jul 10, 2026 10:04am | Jul 10, 2026 10:04am | Jul 10, 2026 11:36am | Jul 10, 2026 11:36am | Jul 10, 2026 11:43am | Jul 10, 2026 11:43am | Jul 10, 2026 11:45am | Jul 10, 2026 11:45am |  |  | Fair | No | Found a 50 amp junction fuse blow cause by tree contact fuse as been replaced area is now with supply
Outage | J.E.26.07.10509 | C001845554 | Raymond Carr | St.Mary | Completed | Load_262298 | Oracabessa - 210 | Jul 10, 2026 10:03am | Jul 10, 2026 10:04am | Jul 10, 2026 12:43pm | Jul 10, 2026 12:43pm | Jul 10, 2026 12:43pm | Jul 10, 2026 12:28pm | Jul 10, 2026 12:45pm | Jul 10, 2026 12:45pm |  |  | Fair | No | Supply was restored. Related to back street Boscobell.
Outage | J.E.26.07.10533 | C001845555 | Raymond Carr | St.Mary | Completed | Load_252304 | Oracabessa - 210 | Jul 10, 2026 10:03am | Jul 10, 2026 10:03am | Jul 10, 2026 11:43am | Jul 10, 2026 11:43am | Jul 10, 2026 11:43am | Jul 10, 2026 11:44am | Jul 10, 2026 11:44am | Jul 10, 2026 11:44am |  |  | Fair | No | Supply was restored.
Outage | J.E.26.07.09095 | C001845540 | Cliton Henry | St.Mary | Completed | Load_252471 | Blackstonedge - 110 | Jul 10, 2026 10:00am | Jul 10, 2026 12:06pm | Jul 10, 2026 12:14pm | Jul 10, 2026 12:14pm | Jul 10, 2026 1:48pm | Jul 10, 2026 4:13pm | Jul 10, 2026 4:16pm | Jul 10, 2026 4:16pm |  |  | Fair | No | A 20 amp trip saver found tripped at Pembroke Hall main Rd. toward Cox Piece due to clearance breach and tree contacts. Corrective work done to retensioned 3 spans of single phase primary conductor and carryout spot bushing to include cutting of Bamboo trees. Supply restored to energized to 20 amp trip saver.
Non-Outage | J.E.26.07.10554 | C001845539 | Andrae Dawkins | St.James | Completed | Load_301824 | Bogue - 310 | Jul 10, 2026 9:56am | Jul 10, 2026 9:57am | Jul 10, 2026 10:01am | Jul 10, 2026 10:01am | Jul 10, 2026 10:34am | Jul 10, 2026 11:55am | Jul 10, 2026 12:02pm | Jul 10, 2026 12:02pm |  |  | Fair | No | Found customer single phasing due to slack connection at pole clean and remade joint used 1 pg clamp also found customer pothead corroded cleaned and remade joints used 2 pg clamp
Outage | J.E.26.07.10530 | C001845512 | Elvis Trowers | KSAN | Completed | Load_557730 | Washington Blvd - 610 | Jul 10, 2026 9:43am | Jul 10, 2026 9:44am | Jul 10, 2026 10:26am | Jul 10, 2026 10:26am | Jul 10, 2026 10:42am | Jul 10, 2026 11:12am | Jul 10, 2026 11:12am | Jul 10, 2026 11:12am |  |  | Fair | Yes | Happened to be internal when checked, customer was assisted by resetting her breakers.
Outage | J.E.26.07.10541 | C001845504 | Raymond Lewis | St.Ann | Completed | Load_252442 | Roaring River - 210 | Jul 10, 2026 9:40am | Jul 10, 2026 9:52am | Jul 10, 2026 12:20pm | Jul 10, 2026 12:20pm | Jul 10, 2026 12:20pm | Jul 10, 2026 12:23pm | Jul 10, 2026 12:23pm | Jul 10, 2026 12:23pm |  |  | SevereWind | No | Voltage found 117/117/234
Outage | J.E.26.07.10506 | C001845491 | Tyrese Williams | St.Ann | Completed | Load_556106 | Cardiff Hall - 210 | Jul 10, 2026 9:35am | Jul 10, 2026 9:53am | Jul 10, 2026 10:45am | Jul 10, 2026 12:30pm | Jul 10, 2026 12:30pm | Jul 10, 2026 12:30pm | Jul 10, 2026 12:31pm | Jul 10, 2026 12:31pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.10378 | C001845480 | Elvis Trowers | KSAN | Completed | Load_302283 | Washington Blvd - 510 | Jul 10, 2026 9:29am | Jul 10, 2026 9:29am | Jul 10, 2026 11:19am | Jul 10, 2026 11:19am | Jul 10, 2026 11:39am | Jul 10, 2026 11:45am | Jul 10, 2026 11:45am | Jul 10, 2026 11:45am |  |  | Fair | Yes | Premises checked and found ok upon arrival, customer was also spoken with however she suggested that the power supply was restored from last night early morning.
Outage | J.E.26.07.10452 | C001845481 | Milton Charlton | KSAN | Completed | Load_261591 | Hope - 510 | Jul 10, 2026 9:29am | Jul 10, 2026 9:29am | Jul 10, 2026 1:32pm | Jul 10, 2026 1:32pm | Jul 10, 2026 4:26pm | Jul 10, 2026 4:30pm | Jul 10, 2026 4:31pm | Jul 10, 2026 4:31pm |  |  | Fair | No | Isolate 25 kva transformer at pole#0110202 and repair broken open secondary neutral using 50ft #2AA conductor, two #2 preform and six 1- bolt clamps. And reclosed transformer switch.
Non-Outage | J.E.26.07.08730 | C001845447 | Oraine Minto | St.Ann | Completed | Load_261926 | Cardiff Hall - 310 | Jul 10, 2026 9:08am | Jul 10, 2026 9:13am | Jul 11, 2026 2:16pm | Jul 11, 2026 4:30pm | Jul 11, 2026 4:30pm | Jul 11, 2026 4:31pm | Jul 11, 2026 4:34pm | Jul 11, 2026 4:34pm |  |  | Fair | No | 2 one bolt clamp 234v 118v 115v
Non-Outage | J.E.26.07.09546 | C001845450 | Oraine Minto | St.Ann | Completed | Load_252112 | Cardiff Hall - 310 | Jul 10, 2026 9:08am | Jul 10, 2026 9:13am | Jul 11, 2026 9:58am | Jul 11, 2026 11:47am | Jul 11, 2026 11:47am | Jul 11, 2026 11:47am | Jul 11, 2026 11:48am | Jul 11, 2026 11:48am |  |  | Fair | No | Issue was fix 234v 117v 116v
Non-Outage | J.E.26.07.09621 | C001845451 | Oraine Minto | St.Ann | Completed | Load_252162 | Cardiff Hall - 310 | Jul 10, 2026 9:08am | Jul 10, 2026 9:13am | Jul 10, 2026 3:13pm | Jul 10, 2026 3:13pm | Jul 10, 2026 4:09pm | Jul 10, 2026 4:10pm | Jul 10, 2026 4:10pm | Jul 10, 2026 4:10pm |  |  | Fair | No | Refer to emergency No power in area
Outage | J.E.26.07.10490 | C001845452 | Romeo Brissett | St.James | Completed | Load_267621 | Bogue - 610 | Jul 10, 2026 9:08am | Jul 10, 2026 9:09am | Jul 10, 2026 11:23am | Jul 10, 2026 11:28am | Jul 10, 2026 12:40pm | Jul 10, 2026 2:12pm | Jul 10, 2026 2:13pm | Jul 10, 2026 2:13pm | BrokenWire |  | Fair | No | Removed several illegal connections, spliced and retention 2 span of secondary, replaced (1)25 kva transformer fuse. Used 50ft of #2 (1)#2 sleeve, (1)#2 preformed and 4 clamps
Non-Outage | J.E.26.07.05920 | C001845436 | Odeanie Davis | KSAS | Completed | Load_240573 | Three Miles - 410 | Jul 10, 2026 9:06am | Jul 10, 2026 9:07am | Jul 10, 2026 9:11am | Jul 10, 2026 12:11pm | Jul 10, 2026 12:23pm | Jul 10, 2026 12:31pm | Jul 10, 2026 12:41pm | Jul 10, 2026 12:41pm |  |  | Fair | No | 101v/103v & 205v on secondary line from transformer, field service team needed,
Non-Outage | J.E.26.07.05927 | C001845438 | Odeanie Davis | KSAS | Completed | Load_261195 | Hunts Bay - 810 | Jul 10, 2026 9:06am | Jul 10, 2026 9:07am | Jul 10, 2026 9:11am | Jul 10, 2026 12:41pm | Jul 10, 2026 12:50pm | Jul 10, 2026 1:25pm | Jul 10, 2026 1:30pm | Jul 10, 2026 1:30pm |  |  | Fair | No | 118v/114v at arrival, open circuit at pothead corrected, 3 penn union, 117v/116v & 233v after correction
Non-Outage | J.E.26.07.07493 | C001845437 | Odeanie Davis | KSAS | Completed | Load_242523 | Greenwich - 310 | Jul 10, 2026 9:06am | Jul 10, 2026 9:07am | Jul 10, 2026 9:11am | Jul 10, 2026 10:17am | Jul 10, 2026 10:22am | Jul 10, 2026 10:55am | Jul 10, 2026 10:52am | Jul 10, 2026 10:52am |  |  | Fair | No | 111v/119v at arrival, open circuit at secondary corrected, 2 one bolt clamps, 112v/119v & 230v after correction,
Non-Outage | J.E.26.07.08841 | C001845439 | Odeanie Davis | KSAS | Completed | Load_266654 | Hunts Bay - 510 | Jul 10, 2026 9:06am | Jul 10, 2026 9:07am | Jul 10, 2026 9:11am | Jul 10, 2026 9:27am | Jul 10, 2026 9:31am | Jul 10, 2026 10:00am | Jul 10, 2026 9:59am | Jul 10, 2026 9:59am |  |  | Fair | No | 110v/118v at arrival, open circuit at pothead corrected, 3 penn union, 119v/118v & 238v after correction
Non-Outage | J.E.26.07.10437 | C001845441 | Odeanie Davis | KSAS | Completed | Load_255166 | Greenwich - 710 | Jul 10, 2026 9:06am | Jul 10, 2026 9:07am | Jul 10, 2026 9:11am | Jul 10, 2026 11:07am | Jul 10, 2026 11:32am | Jul 10, 2026 12:00pm | Jul 10, 2026 12:03pm | Jul 10, 2026 12:03pm |  |  | Fair | No | 111v/124v at location from secondary line, field service team needed.
Outage | J.E.26.07.10487 | C001845442 | Tyrese Williams | St.Ann | Completed | Load_568224 | Cardiff Hall - 210 | Jul 10, 2026 9:06am | Jul 10, 2026 9:13am | Jul 10, 2026 9:33am | Jul 10, 2026 12:29pm | Jul 10, 2026 12:29pm | Jul 10, 2026 12:29pm | Jul 10, 2026 12:29pm | Jul 10, 2026 12:29pm |  |  | Fair | No | Premises found ok call related to the 15 amp junction fuse
Outage | J.E.26.07.10461 | C001845434 | Elvis Trowers | KSAN | Completed | Load_266226 | Constant Spring - 210 | Jul 10, 2026 9:04am | Jul 10, 2026 9:04am | Jul 10, 2026 11:50am | Jul 10, 2026 11:50am | Jul 10, 2026 12:34pm | Jul 10, 2026 12:56pm | Jul 10, 2026 12:56pm | Jul 10, 2026 12:56pm |  |  | Fair | Yes | Areas found without electricity supply when checked and a blown 20 amp junction fuse was found and replaced after patrol was completed at pole #0011374.
Non-Outage | J.E.26.07.08439 | C001845431 | Rochaine Hussey | KSAN | Completed | Load_240919 | Constant Spring - 410 | Jul 10, 2026 9:01am | Jul 10, 2026 9:04am | Jul 10, 2026 9:31am | Jul 10, 2026 1:36pm | Jul 10, 2026 1:36pm | Jul 10, 2026 1:37pm | Jul 10, 2026 1:37pm | Jul 10, 2026 1:37pm |  |  | Fair | No | Unable to locate Customer was called multiple times no answer
Non-Outage | J.E.26.07.09281 | C001845432 | Rochaine Hussey | KSAS | Completed | Load_243498 | Duhaney - 310 | Jul 10, 2026 9:01am | Jul 10, 2026 9:04am | Jul 10, 2026 11:23am | Jul 10, 2026 11:39am | Jul 10, 2026 11:39am | Jul 10, 2026 12:02pm | Jul 10, 2026 12:03pm | Jul 10, 2026 12:03pm |  |  | Fair | No | Premises found ok119/119/238v
Non-Outage | J.E.26.07.09638 | C001845433 | Rochaine Hussey | KSAN | Completed | Load_258637 | Constant Spring - 210 | Jul 10, 2026 9:01am | Jul 10, 2026 9:04am | Jul 10, 2026 12:40pm | Jul 10, 2026 12:40pm | Jul 10, 2026 12:40pm | Jul 10, 2026 12:43pm | Jul 10, 2026 12:43pm | Jul 10, 2026 12:43pm |  |  | Fair | No | Customer said issue was already resolved
Non-Outage | J.E.26.07.08847 | C001845423 | Oraine Minto | St.Ann | Completed | Load_556218 | Cardiff Hall - 210 | Jul 10, 2026 8:58am | Jul 10, 2026 8:59am | Jul 10, 2026 1:18pm | Jul 10, 2026 1:18pm | Jul 10, 2026 1:18pm | Jul 10, 2026 2:30pm | Jul 10, 2026 2:31pm | Jul 10, 2026 2:31pm |  |  | Fair | No | Issue was resolved
Non-Outage | J.E.26.07.09580 | C001845421 | Oraine Minto | St.Ann | Completed | Load_254196 | Cardiff Hall - 210 | Jul 10, 2026 8:58am | Jul 10, 2026 8:59am | Jul 10, 2026 2:36pm | Jul 10, 2026 2:36pm | Jul 10, 2026 2:36pm | Jul 10, 2026 2:37pm | Jul 10, 2026 2:37pm | Jul 10, 2026 2:37pm |  |  | Fair | No | Refer to emergency
Non-Outage | J.E.26.07.09786 | C001845422 | Tyrese Williams | St.Ann | Completed | Load_259557 | Cardiff Hall - 210 | Jul 10, 2026 8:58am | Jul 10, 2026 10:13am | Jul 10, 2026 12:31pm | Jul 10, 2026 12:31pm | Jul 10, 2026 2:14pm | Jul 10, 2026 2:16pm | Jul 10, 2026 2:18pm | Jul 10, 2026 2:18pm |  |  | Fair | No | Open a bank of 2() 25kva transformer fuse to repair transformer drop leed use 2 pg clamp
Outage | J.E.26.07.10472 | C001845420 | Raymond Lewis | St.Ann | Completed | Load_267761 | Roaring River - 210 | Jul 10, 2026 8:57am | Jul 10, 2026 8:58am | Jul 10, 2026 9:30am | Jul 10, 2026 9:30am | Jul 10, 2026 11:10am | Jul 10, 2026 12:09pm | Jul 10, 2026 12:20pm | Jul 10, 2026 12:20pm | BrokenWire |  | SevereWind | No | Open 25 kva x former to splice and retention 4 span secondary neutral
Outage | J.E.26.07.10441 | C001845417 | Oraine Minto | St.Ann | Completed | Load_242214 | Cardiff Hall - 210 | Jul 10, 2026 8:53am | Jul 10, 2026 8:59am | Jul 10, 2026 2:38pm | Jul 10, 2026 2:38pm | Jul 10, 2026 2:38pm | Jul 10, 2026 3:01pm | Jul 10, 2026 3:09pm | Jul 10, 2026 3:09pm |  |  | Fair | No | Refer to emergency At the entrance of crusts city
Non-Outage | J.E.26.07.09396 | C001845415 | Ryan Richards | Manchester | Completed | Load_238224 | Kendal - 310 | Jul 10, 2026 8:52am | Jul 10, 2026 8:53am | Jul 10, 2026 8:58am | Jul 10, 2026 12:13pm | Jul 10, 2026 1:43pm | Jul 10, 2026 2:08pm | Jul 10, 2026 2:08pm | Jul 10, 2026 2:08pm |  |  | Fair | No | Blown 3 amp fuse found for 25 kva transformer line patrol nothing found blown fuse was replaced and all customers are now with supply
Outage | J.E.26.07.10435 | C001845402 | Damion Reid | Manchester | Completed | Load_269829 | Spur Tree - 310 | Jul 10, 2026 8:42am | Jul 10, 2026 8:42am | Jul 10, 2026 6:15pm | Jul 10, 2026 6:15pm | Jul 10, 2026 8:45pm | Jul 10, 2026 8:47pm | Jul 10, 2026 8:48pm | Jul 10, 2026 8:48pm |  |  | SevereWind | No | Call was already done by the operations team
Non-Outage | J.E.26.07.09945 | C001845390 | Fredrick Hamilton | KSAN | Completed | Load_238618 | Hope - 510 | Jul 10, 2026 8:26am | Jul 10, 2026 8:29am | Jul 10, 2026 8:35am | Jul 10, 2026 9:54am | Jul 10, 2026 9:55am | Jul 10, 2026 9:57am | Jul 10, 2026 9:57am | Jul 10, 2026 9:57am |  |  | Fair | No | Customer contacted and stated that power is fully at premises however previous team may have meter socket cover in there possession by mistake Premises is ok
Non-Outage | J.E.26.07.10186 | C001845389 | Fredrick Hamilton | KSAN | Completed | Load_238339 | Hope - 410 | Jul 10, 2026 8:26am | Jul 10, 2026 8:29am | Jul 10, 2026 8:35am | Jul 10, 2026 8:38am | Jul 10, 2026 9:20am | Jul 10, 2026 9:49am | Jul 10, 2026 9:49am | Jul 10, 2026 9:49am |  |  | Fair | No | Emergency crew required single phase coming from Exim box 118v/11.38v obtained please follow upPole#0110089
Non-Outage | J.E.26.03.42884 | C001845382 | Junior Scarlett | St.James | Completed | Load_246868 | Rose Hall - 210 | Jul 10, 2026 8:22am | Jul 10, 2026 8:23am | Jul 10, 2026 8:26am | Jul 10, 2026 11:49am | Jul 10, 2026 11:49am | Jul 10, 2026 12:10pm | Jul 10, 2026 12:11pm | Jul 10, 2026 12:11pm |  |  | Fair | No | Premesis lock Voltage found 113v 114v 227v
Non-Outage | J.E.26.07.09171 | C001845380 | Christopher Edwards | KSAN | Completed | Load_250006 | Constant Spring - 410 | Jul 10, 2026 8:22am | Jul 10, 2026 8:23am | Jul 10, 2026 2:44pm | Jul 10, 2026 2:44pm | Jul 10, 2026 4:03pm | Jul 10, 2026 5:04pm | Jul 10, 2026 5:09pm | Jul 10, 2026 5:09pm |  |  | Fair | No | Remake burnt neutral joint At poleUsing (1) one bolt clampVoltage:115,114,230v
Non-Outage | J.E.26.07.09483 | C001845381 | Junior Scarlett | St.James | Completed | Load_269700 | Rose Hall - 210 | Jul 10, 2026 8:22am | Jul 10, 2026 8:23am | Jul 10, 2026 8:26am | Jul 10, 2026 8:37am | Jul 10, 2026 8:56am | Jul 10, 2026 10:01am | Jul 10, 2026 10:02am | Jul 10, 2026 10:02am |  |  | Fair | No | Check and found okVoltage found 115v 115v 230v 208v
Non-Outage | J.E.26.07.09655 | C001845378 | Junior Scarlett | St.James | Completed | Load_250922 | Rose Hall - 210 | Jul 10, 2026 8:22am | Jul 10, 2026 8:23am | Jul 10, 2026 8:26am | Jul 10, 2026 10:11am | Jul 10, 2026 10:52am | Jul 10, 2026 11:12am | Jul 10, 2026 11:12am | Jul 10, 2026 11:12am |  |  | Fair | No | Install two clampVoltage found 114v 117v 229v Voltage leave 114v 114v 228v
Non-Outage | J.E.26.07.10220 | C001845377 | Junior Scarlett | St.James | Completed | Load_264270 | Rose Hall - 210 | Jul 10, 2026 8:22am | Jul 10, 2026 8:23am | Jul 10, 2026 8:26am | Jul 10, 2026 3:13pm | Jul 10, 2026 3:19pm | Jul 10, 2026 3:21pm | Jul 10, 2026 3:22pm | Jul 10, 2026 3:22pm |  |  | Fair | No | Premess lockVoltage found 115 v 115 v 230v
Non-Outage | J.E.26.07.10225 | C001845379 | Junior Scarlett | St.James | Completed | Load_264270 | Rose Hall - 210 | Jul 10, 2026 8:22am | Jul 10, 2026 8:23am | Jul 10, 2026 8:26am | Jul 10, 2026 3:22pm | Jul 10, 2026 3:22pm | Jul 10, 2026 3:22pm | Jul 10, 2026 3:24pm | Jul 10, 2026 3:24pm |  |  | Fair | No | Premesis lockVoltage from pole 115v 115v 230v
Outage | J.E.26.07.10422 | C001845376 | Tyrese Williams | St.Ann | Completed | Load_556116 | Cardiff Hall - 210 | Jul 10, 2026 8:22am | Jul 10, 2026 8:22am | Jul 10, 2026 8:28am | Jul 10, 2026 9:36am | Jul 10, 2026 10:27am | Jul 10, 2026 10:40am | Jul 10, 2026 10:40am | Jul 10, 2026 10:40am |  |  | Fair | No | Replace a 20amp junction fuse at pole
Outage | J.E.26.07.09449 | C001845370 | Rusean Allen | KSAS | Completed | Load_255914 | Cane River - 310 | Jul 10, 2026 8:21am | Jul 10, 2026 9:34am | Jul 10, 2026 12:01pm | Jul 10, 2026 12:01pm | Jul 10, 2026 1:18pm | Jul 10, 2026 1:21pm | Jul 10, 2026 1:21pm | Jul 10, 2026 1:21pm |  |  | Fair | No | Premises under investigation. Refer to field service department
Outage | J.E.26.07.09645 | C001845369 | Rusean Allen | KSAS | Completed | Load_252659 | Rockfort - 410 | Jul 10, 2026 8:20am | Jul 10, 2026 9:34am | Jul 10, 2026 9:46am | Jul 10, 2026 9:46am | Jul 10, 2026 10:00am | Jul 10, 2026 10:03am | Jul 10, 2026 10:03am | Jul 10, 2026 10:03am | TreeContact |  | Fair | No | Premises found locked
Non-Outage | J.E.26.07.07928 | C001845359 | Andrae Dawkins | St.James | Completed | Load_270234 | Queens Drive - 710 | Jul 10, 2026 8:19am | Jul 10, 2026 8:21am | Jul 10, 2026 1:53pm | Jul 10, 2026 2:28pm | Jul 10, 2026 2:33pm | Jul 10, 2026 2:37pm | Jul 10, 2026 2:38pm | Jul 10, 2026 2:38pm | Fire |  | Fair | No | Found secondary line banging due to heavy winds secondary line needs tensioning urgent attention required refer back to emergency crew.
Non-Outage | J.E.26.07.08270 | C001845356 | Andrae Dawkins | St.James | Completed | Load_249352 | Queens Drive - 710 | Jul 10, 2026 8:19am | Jul 10, 2026 8:21am | Jul 10, 2026 8:30am | Jul 10, 2026 2:06pm | Jul 10, 2026 2:06pm | Jul 10, 2026 1:56pm | Jul 10, 2026 2:07pm | Jul 10, 2026 2:07pm |  |  | Fair | No | Cannot locate customer unable to reach customer mobile phone
Non-Outage | J.E.26.07.08459 | C001845357 | Andrae Dawkins | St.James | Completed | Load_254425 | Queens Drive - 710 | Jul 10, 2026 8:19am | Jul 10, 2026 8:21am | Jul 10, 2026 8:30am | Jul 10, 2026 3:38pm | Jul 10, 2026 3:38pm | Jul 10, 2026 1:07pm | Jul 10, 2026 3:40pm | Jul 10, 2026 3:40pm |  |  | Fair | No | Found multiple customers experiencing low voltage 14 pole span from transformer voltage found at customer 109/104/213 voltage found at transformer 115/115/231 also found transformer installed but not connected one pole span of secondary and Primary with drop lead required refer back to maintenance
Non-Outage | J.E.26.07.09564 | C001845355 | Andrae Dawkins | St.James | Completed | Load_267342 | Queens Drive - 710 | Jul 10, 2026 8:19am | Jul 10, 2026 8:21am | Jul 10, 2026 8:30am | Jul 10, 2026 9:48am | Jul 10, 2026 9:49am | Jul 10, 2026 9:28am | Jul 10, 2026 9:51am | Jul 10, 2026 9:51am |  |  | Fair | No | Check and found ok customer said that they don’t have any problem with the light
Non-Outage | J.E.26.07.09753 | C001845354 | Andrae Dawkins | St.James | Completed | Load_263634 | Queens Drive - 710 | Jul 10, 2026 8:19am | Jul 10, 2026 8:21am | Jul 10, 2026 8:30am | Jul 10, 2026 12:04pm | Jul 10, 2026 12:04pm | Jul 10, 2026 12:05pm | Jul 10, 2026 12:09pm | Jul 10, 2026 12:09pm |  |  | Fair | No | Check and found ok customer said that the power came back
Outage | J.E.26.07.09968 | C001845353 | Edward Royal | KSAS | Completed | Load_293369 | Hunts Bay - 810 | Jul 10, 2026 8:19am | Jul 10, 2026 8:19am | Jul 10, 2026 10:48am | Jul 10, 2026 10:48am | Jul 10, 2026 10:48am | Jul 10, 2026 10:59am | Jul 10, 2026 10:59am | Jul 10, 2026 10:59am |  |  | Fair | No | Defective 15kva transformer need to be change it a rami system YP Box reffered to bucket truck
Outage | J.E.26.07.10146 | C001845352 | Rusean Allen | KSAS | Completed | Load_246366 | Cane River - 310 | Jul 10, 2026 8:17am | Jul 10, 2026 9:34am | Jul 10, 2026 12:01pm | Jul 10, 2026 1:21pm | Jul 10, 2026 2:58pm | Jul 10, 2026 2:59pm | Jul 10, 2026 2:59pm | Jul 10, 2026 2:59pm |  |  | Fair | No | Power was restored
Non-Outage | J.E.26.05.34776 | C001845349 | Royston Montague | St.Catherine | Completed | Load_264950 | New Michelton - 310 | Jul 10, 2026 8:16am | Jul 10, 2026 10:07am | Jul 10, 2026 10:16am | Jul 10, 2026 12:12pm | Jul 10, 2026 12:33pm | Jul 10, 2026 12:48pm | Jul 10, 2026 12:48pm | Jul 10, 2026 12:48pm |  |  | Fair | No | Customer confirmed issue resolved few weeks ago. 229v 114v 113v
Non-Outage | J.E.26.06.24811 | C001845350 | Royston Montague | St.Catherine | Completed | Load_244944 | New Michelton - 310 | Jul 10, 2026 8:16am | Jul 10, 2026 10:07am | Jul 10, 2026 10:16am | Jul 10, 2026 3:05pm | Jul 10, 2026 3:46pm | Jul 10, 2026 3:47pm | Jul 10, 2026 3:47pm | Jul 10, 2026 3:47pm |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.07.07649 | C001845351 | Royston Montague | St.Catherine | Completed | Load_252397 | New Michelton - 310 | Jul 10, 2026 8:16am | Jul 10, 2026 10:07am | Jul 10, 2026 10:16am | Jul 10, 2026 3:47pm | Jul 10, 2026 4:58pm | Jul 10, 2026 4:58pm | Jul 10, 2026 4:58pm | Jul 10, 2026 4:58pm |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.07.08239 | C001845347 | Royston Montague | St.Catherine | Completed | Load_250536 | New Michelton - 310 | Jul 10, 2026 8:16am | Jul 10, 2026 10:07am | Jul 10, 2026 10:16am | Jul 10, 2026 2:11pm | Jul 10, 2026 2:31pm | Jul 10, 2026 3:05pm | Jul 10, 2026 3:05pm | Jul 10, 2026 3:05pm |  |  | Fair | No | Bucket truck required. Faulty splice in neutral. Affected side voltage 124v 103 v 229v , transformer drop lead 230v 114v 115v
Non-Outage | J.E.26.07.09177 | C001845348 | Royston Montague | St.Catherine | Completed | Load_239113 | New Michelton - 410 | Jul 10, 2026 8:16am | Jul 10, 2026 10:07am | Jul 10, 2026 10:16am | Jul 10, 2026 12:49pm | Jul 10, 2026 12:58pm | Jul 10, 2026 1:05pm | Jul 10, 2026 1:05pm | Jul 10, 2026 1:05pm |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.07.09421 | C001845346 | Royston Montague | St.Catherine | Completed | Load_568285 | New Michelton - 410 | Jul 10, 2026 8:16am | Jul 10, 2026 10:07am | Jul 10, 2026 10:16am | Jul 10, 2026 1:06pm | Jul 10, 2026 1:15pm | Jul 10, 2026 2:10pm | Jul 10, 2026 2:11pm | Jul 10, 2026 2:11pm |  |  | Fair | No | Faulty meter socket. Customer asked to get an electrician to repair same , observed also that meter burn same needs to change. Please inform field service department thank. Voltage 229v 113v 114v
Outage | J.E.26.07.10420 | C001845345 | Oshane Warren | Westmoreland | Completed | Load_292929 | Paradise - 210 | Jul 10, 2026 8:16am | Jul 10, 2026 8:16am | Jul 10, 2026 10:48am | Jul 10, 2026 10:48am | Jul 10, 2026 11:46am | Jul 10, 2026 11:47am | Jul 10, 2026 11:48am | Jul 10, 2026 11:48am |  |  | Rains | No | Replace 8amp junction fuse
Outage | J.E.26.07.10410 | C001845344 | Oshane Warren | Westmoreland | Completed | Load_253700 | Paradise - 210 | Jul 10, 2026 8:15am | Jul 10, 2026 8:16am | Jul 10, 2026 11:48am | Jul 10, 2026 11:48am | Jul 10, 2026 11:48am | Jul 10, 2026 11:49am | Jul 10, 2026 11:49am | Jul 10, 2026 11:49am |  |  | Rains | No | Replace 8amp junction fuse
Non-Outage | J.E.26.07.09955 | C001845343 | Floyd Taylor | Trelawny | Completed | Load_262457 | Greenwood - 110 | Jul 10, 2026 8:14am | Jul 10, 2026 8:14am | Jul 10, 2026 8:38am | Jul 10, 2026 8:40am | Jul 10, 2026 9:22am | Jul 10, 2026 10:30am | Jul 10, 2026 10:31am | Jul 10, 2026 10:31am |  |  | Fair | No | Remake joint at pole using 2pg clamps . Voltage readings left 117,119,204,238,237,237.
Outage | J.E.26.07.09659 | C001845342 | Floyd Taylor | St.James | Completed | Load_244424 | Bogue - 310 | Jul 10, 2026 8:13am | Jul 10, 2026 8:14am | Jul 10, 2026 10:58am | Jul 10, 2026 10:58am | Jul 10, 2026 11:48am | Jul 10, 2026 12:23pm | Jul 10, 2026 12:46pm | Jul 10, 2026 12:46pm |  |  | Fair | No | Replace 1 8amp junction fuse, also meter defective refer to field service.
Non-Outage | J.E.26.07.07767 | C001845339 | Marlon Brown | Trelawny | Completed | Load_237635 | Duncans - 210 | Jul 10, 2026 8:12am | Jul 10, 2026 8:12am | Jul 10, 2026 8:45am | Jul 10, 2026 12:53pm | Jul 10, 2026 12:53pm | Jul 10, 2026 12:55pm | Jul 10, 2026 12:55pm | Jul 10, 2026 12:55pm |  |  | Fair | No | Unable to locate customer via telephone nor direction
Non-Outage | J.E.26.07.08138 | C001845340 | Marlon Brown | Trelawny | Completed | Load_246819 | Duncans - 210 | Jul 10, 2026 8:12am | Jul 10, 2026 8:13am | Jul 10, 2026 12:55pm | Jul 10, 2026 12:55pm | Jul 10, 2026 12:55pm | Jul 10, 2026 12:56pm | Jul 10, 2026 12:56pm | Jul 10, 2026 12:56pm |  |  | Fair | No | Fixed on the 9/07/2026 by A. Williams.
Non-Outage | J.E.26.07.08865 | C001845341 | Marlon Brown | Trelawny | Completed | Load_248221 | Duncans - 210 | Jul 10, 2026 8:12am | Jul 10, 2026 8:13am | Jul 10, 2026 12:56pm | Jul 10, 2026 12:56pm | Jul 10, 2026 12:56pm | Jul 10, 2026 1:00pm | Jul 10, 2026 1:00pm | Jul 10, 2026 1:00pm | Fire |  | Fair | No | Found ok, customer says the issue has been restored by electrician. Voltage found at pothead 120/120/207v=240/238/237v. Voltage leaving at pothead 120/120/207=238/237/240
Outage | J.E.26.07.10205 | C001845338 | Marlon Brown | Trelawny | Completed | Load_265828 | Duncans - 110 | Jul 10, 2026 8:11am | Jul 10, 2026 8:12am | Jul 10, 2026 8:47am | Jul 10, 2026 8:47am | Jul 10, 2026 9:21am | Jul 10, 2026 11:46am | Jul 10, 2026 11:46am | Jul 10, 2026 11:46am |  |  | Fair | No | Replaced 5amps fuse @ 50kva transformer Load readings @ transformer drop leads are as follow X1 voltage 111v & 504ampsX3 voltage 112v & 468amps Across phase 225v X3 Neutral 30ampsThese reading are as a result of a ton of illegal connections on the secondary line
Outage | J.E.26.07.10407 | C001845337 | Raymond Lewis | St.Ann | Completed | Load_250195 | Roaring River - 210 | Jul 10, 2026 8:11am | Jul 10, 2026 8:51am | Jul 10, 2026 12:24pm | Jul 10, 2026 12:24pm | Jul 10, 2026 12:49pm | Jul 10, 2026 1:46pm | Jul 10, 2026 1:46pm | Jul 10, 2026 1:46pm |  |  | SevereWind | No | Refuse and close 25kva x former
Non-Outage | J.E.26.07.07623 | C001845332 | Roemello Brown | Trelawny | Completed | Load_261797 | Martha Brae - 210 | Jul 10, 2026 8:10am | Jul 10, 2026 8:11am | Jul 10, 2026 8:27am | Jul 10, 2026 8:27am | Jul 10, 2026 8:59am | Jul 10, 2026 9:00am | Jul 10, 2026 9:07am | Jul 10, 2026 9:07am | LowHangingWires |  | Fair | No | Have service wire re-tension Voltage found 115/116/231Voltage leave 115/116/231
Non-Outage | J.E.26.07.08343 | C001845335 | Marlon Brown | Trelawny | Completed | Load_230035 | Duncans - 110 | Jul 10, 2026 8:10am | Jul 10, 2026 8:12am | Jul 10, 2026 1:00pm | Jul 10, 2026 1:00pm | Jul 10, 2026 1:00pm | Jul 10, 2026 1:01pm | Jul 10, 2026 1:01pm | Jul 10, 2026 1:01pm |  |  | Fair | No | Found ok fixed on the 9/07/2026 by M. Brown.
Non-Outage | J.E.26.07.08587 | C001845334 | Roemello Brown | Trelawny | Completed | Load_294295 | Duncans - 110 | Jul 10, 2026 8:10am | Jul 10, 2026 8:11am | Jul 10, 2026 12:25pm | Jul 10, 2026 2:13pm | Jul 10, 2026 2:13pm | Jul 10, 2026 2:13pm | Jul 10, 2026 3:04pm | Jul 10, 2026 3:04pm | LowHangingWires |  | Fair | No | Have service wire relocated Voltage found 118/118/236Voltage leave 118/118/236
Non-Outage | J.E.26.07.09512 | C001845333 | Roemello Brown | Trelawny | Completed | Load_247321 | Martha Brae - 110 | Jul 10, 2026 8:10am | Jul 10, 2026 8:11am | Jul 10, 2026 11:25am | Jul 10, 2026 11:25am | Jul 10, 2026 12:15pm | Jul 10, 2026 12:15pm | Jul 10, 2026 12:22pm | Jul 10, 2026 12:22pm |  |  | Fair | No | Meter socket burn up inform the customer to get an private electrician to get meter socket repair Voltage found 124/114/114/228Voltage leave 114/114/124/228
Non-Outage | J.E.26.07.05487 | C001845326 | Richard Watson | St.Elizabeth | Completed | Load_243863 | Maggotty - 110 | Jul 10, 2026 8:09am | Jul 10, 2026 8:10am | Jul 10, 2026 10:36am | Jul 10, 2026 10:36am | Jul 10, 2026 11:45am | Jul 10, 2026 1:00pm | Jul 10, 2026 1:05pm | Jul 10, 2026 1:05pm |  |  | Fair | No | Replace blown 20amp junction fuse no pole#, also replaced two blown 5amp fuse for two 50kva transformers in bank of three, suspected cause lightning, supply restored.
Non-Outage | J.E.26.07.06560 | C001845325 | Dwain Samuels | St.Elizabeth | Completed | Load_265987 | Maggotty - 110 | Jul 10, 2026 8:09am | Jul 10, 2026 8:54am | Jul 10, 2026 9:27am | Jul 10, 2026 12:08pm | Jul 10, 2026 12:09pm | Jul 10, 2026 12:10pm | Jul 10, 2026 12:12pm | Jul 10, 2026 12:12pm |  |  | Fair | No | Meter room gate is locked cannot access area
Non-Outage | J.E.26.07.07788 | C001845329 | Richard Watson | St.Elizabeth | Completed | Load_292191 | Maggotty - 110 | Jul 10, 2026 8:09am | Jul 10, 2026 8:10am | Jul 10, 2026 1:25pm | Jul 10, 2026 1:25pm | Jul 10, 2026 1:27pm | Jul 10, 2026 1:29pm | Jul 10, 2026 1:32pm | Jul 10, 2026 1:32pm |  |  | Fair | No | Unable to reach customer by phone, however checks were made on the system and it was determined that electricity is at the premises.
Non-Outage | J.E.26.07.09378 | C001845324 | Odaine Johnson | Clarendon | Completed | Load_259354 | Parnassus - 310 | Jul 10, 2026 8:09am | Jul 10, 2026 8:09am | Jul 10, 2026 8:48am | Jul 10, 2026 11:30am | Jul 10, 2026 11:30am | Jul 10, 2026 11:30am | Jul 10, 2026 11:31am | Jul 10, 2026 11:31am | BrokenPole |  | Fair | No | Please refer this issue to a maintenance team to go and change damaged pole
Non-Outage | J.E.26.07.09491 | C001845328 | Richard Watson | St.Elizabeth | Completed | Load_245393 | Maggotty - 110 | Jul 10, 2026 8:09am | Jul 10, 2026 8:10am | Jul 10, 2026 1:32pm | Jul 10, 2026 1:32pm | Jul 10, 2026 2:21pm | Jul 10, 2026 3:33pm | Jul 10, 2026 3:39pm | Jul 10, 2026 3:39pm |  |  | Fair | No | Remade secondary neutral jumper, also remade secondary phase jumper, use two 1bolt clamps, voltage found 86v, 144v 230v and voltage left 116v, 116v, 232v
Non-Outage | J.E.26.07.09676 | C001845323 | Odaine Johnson | Clarendon | Completed | Load_248117 | Parnassus - 210 | Jul 10, 2026 8:09am | Jul 10, 2026 8:09am | Jul 10, 2026 8:48am | Jul 10, 2026 1:41pm | Jul 10, 2026 1:41pm | Jul 10, 2026 1:42pm | Jul 10, 2026 1:43pm | Jul 10, 2026 1:43pm |  |  | Fair | No | Bank of two found with corroded phase and neutral, switcher need
Non-Outage | J.E.26.07.10093 | C001845331 | Richard Watson | St.Elizabeth | Completed | Load_244065 | Maggotty - 110 | Jul 10, 2026 8:09am | Jul 10, 2026 8:10am | Jul 10, 2026 8:32am | Jul 10, 2026 8:32am | Jul 10, 2026 9:13am | Jul 10, 2026 9:53am | Jul 10, 2026 9:59am | Jul 10, 2026 9:59am |  |  | Fair | No | Corrosion found at secondary pole and pothead, corrected use one 1bolt clamp and three #6-#6 service sleeves, voltages left inside meter socket 108v, 108v, 216v.
Non-Outage | J.E.26.07.07453 | C001845320 | Odaine Johnson | Clarendon | Completed | Load_267981 | Parnassus - 310 | Jul 10, 2026 8:08am | Jul 10, 2026 8:09am | Jul 10, 2026 8:48am | Jul 10, 2026 10:36am | Jul 10, 2026 10:36am | Jul 10, 2026 10:36am | Jul 10, 2026 10:40am | Jul 10, 2026 10:40am |  |  | Fair | No | Damaged transformer drop lead causing single phase in the area when the wind blow and customer meter need to be changed. So please refer this issue to the authorized personnel to come change meter and check transformer
Non-Outage | J.E.26.07.07702 | C001845318 | Odaine Johnson | Clarendon | Completed | Load_267981 | Parnassus - 310 | Jul 10, 2026 8:08am | Jul 10, 2026 8:09am | Jul 10, 2026 8:48am | Jul 10, 2026 10:48am | Jul 10, 2026 10:48am | Jul 10, 2026 10:49am | Jul 10, 2026 10:49am | Jul 10, 2026 10:49am |  |  | Fair | No | Premises was found working ok voltage reading is A115 B116 AB231
Non-Outage | J.E.26.07.08518 | C001845321 | Odaine Johnson | Clarendon | Completed | Load_252867 | Parnassus - 310 | Jul 10, 2026 8:08am | Jul 10, 2026 8:09am | Jul 10, 2026 8:48am | Jul 10, 2026 10:22am | Jul 10, 2026 10:22am | Jul 10, 2026 10:27am | Jul 10, 2026 10:27am | Jul 10, 2026 10:27am |  |  | Fair | No | Corrosion was found at service pole 3 one bolt clamps was replaced and problem was fixed A115 B115 AB 230
Non-Outage | J.E.26.07.08751 | C001845319 | Odaine Johnson | Clarendon | Completed | Load_260282 | Parnassus - 310 | Jul 10, 2026 8:08am | Jul 10, 2026 8:09am | Jul 10, 2026 8:48am | Jul 10, 2026 10:42am | Jul 10, 2026 10:42am | Jul 10, 2026 10:42am | Jul 10, 2026 10:43am | Jul 10, 2026 10:43am | BrokenPole |  | EarthMovement | No | Try contact customer but no one answer and try to follow direction given and still did not find location
Non-Outage | J.E.26.07.09315 | C001845322 | Odaine Johnson | Clarendon | Completed | Load_259757 | Parnassus - 310 | Jul 10, 2026 8:08am | Jul 10, 2026 8:09am | Jul 10, 2026 8:48am | Jul 10, 2026 11:26am | Jul 10, 2026 11:26am | Jul 10, 2026 11:26am | Jul 10, 2026 11:27am | Jul 10, 2026 11:27am |  |  | Fair | No | Premises was found working ok voltage reading is A112 B112 AB225
Non-Outage | J.E.26.07.07962 | C001845317 | Locksley Allen | St.Mary | Completed | Load_267206 | Highgate - 210 | Jul 10, 2026 8:07am | Jul 10, 2026 8:08am | Jul 10, 2026 12:44pm | Jul 10, 2026 12:44pm | Jul 10, 2026 12:44pm | Jul 10, 2026 12:47pm | Jul 10, 2026 12:47pm | Jul 10, 2026 12:47pm |  |  | Fair | No | JPS corrected the problem yesterday. Meter working okay
Non-Outage | J.E.26.07.08237 | C001845316 | Locksley Allen | St.Mary | Completed | Load_267206 | Highgate - 210 | Jul 10, 2026 8:07am | Jul 10, 2026 8:08am | Jul 10, 2026 12:13pm | Jul 10, 2026 12:33pm | Jul 10, 2026 12:33pm | Jul 10, 2026 12:39pm | Jul 10, 2026 12:38pm | Jul 10, 2026 12:38pm |  |  | Fair | No | JPS corrected the problem from yesterday.Voltage at meter socket phase to phase 234v. Phase to neutral 117&117vMeter working okay
Non-Outage | J.E.26.07.08295 | C001845315 | Locksley Allen | St.Mary | Completed | Load_267206 | Highgate - 210 | Jul 10, 2026 8:07am | Jul 10, 2026 12:45pm | Jul 10, 2026 12:52pm | Jul 10, 2026 12:55pm | Jul 10, 2026 12:55pm | Jul 10, 2026 12:58pm | Jul 10, 2026 12:57pm | Jul 10, 2026 12:57pm |  |  | Fair | No | No low voltage problem found at premises,JPS corrected the problem yesterday. Voltage at meter socket phase to phase 220v.Phase to neutral 112&107v. Meter left working
Non-Outage | J.E.26.07.09980 | C001845312 | Locksley Allen | St.Mary | Completed | Load_252482 | Highgate - 210 | Jul 10, 2026 8:07am | Jul 10, 2026 8:09am | Jul 10, 2026 11:02am | Jul 10, 2026 12:09pm | Jul 10, 2026 12:09pm | Jul 10, 2026 12:11pm | Jul 10, 2026 12:12pm | Jul 10, 2026 12:12pm |  |  | Fair | No | Meter socket defective. Customer was advised to change socket urgently
Non-Outage | J.E.26.07.10090 | C001845314 | Locksley Allen | St.Mary | Completed | Load_260677 | Highgate - 210 | Jul 10, 2026 8:07am | Jul 10, 2026 8:10am | Jul 10, 2026 9:29am | Jul 10, 2026 9:56am | Jul 10, 2026 9:56am | Jul 10, 2026 9:59am | Jul 10, 2026 10:00am | Jul 10, 2026 10:00am |  |  | Fair | No | No low voltage problem found at premises. Voltage at meter socket phase to phase 225v. Phase to neutral 108&117vSupply was disconnected for nonpayment of bill. Meter left
Non-Outage | J.E.26.07.10106 | C001845311 | Locksley Allen | St.Mary | Completed | Load_252445 | Highgate - 210 | Jul 10, 2026 8:06am | Jul 10, 2026 8:10am | Jul 10, 2026 10:01am | Jul 10, 2026 10:57am | Jul 10, 2026 10:57am | Jul 10, 2026 10:00am | Jul 10, 2026 11:02am | Jul 10, 2026 11:02am |  |  | Fair | No | Low voltage problem found at premises. Several customer in this area is having the same problem. Customer said that from the transformer was moved from the cross road,they are having this problem.
Outage | J.E.26.07.10406 | C001845309 | Rusean Allen | KSAS | Completed | Load_574050 | Cane River - 410 | Jul 10, 2026 8:05am | Jul 10, 2026 9:34am | Jul 10, 2026 10:50am | Jul 10, 2026 3:20pm | Jul 10, 2026 3:20pm | Jul 10, 2026 3:20pm | Jul 10, 2026 3:21pm | Jul 10, 2026 3:21pm |  |  | Fair | No | Found okay
Non-Outage | J.E.26.06.30534 | C001845306 | Royston Montague | St.Catherine | Completed | Load_261993 | New Michelton - 310 | Jul 10, 2026 8:04am | Jul 10, 2026 8:05am | Jul 10, 2026 8:13am | Jul 10, 2026 8:41am | Jul 10, 2026 11:50am | Jul 10, 2026 12:10pm | Jul 10, 2026 12:10pm | Jul 10, 2026 12:10pm |  |  | Fair | No | Full voltage at premises, pen union replace at pothead, meter socket in great condition, likewise service wire and transformer drop lead joints, voltage 233v 115v 115v
Non-Outage | J.E.26.07.10184 | C001845307 | Andrae Clarke | Portland | Completed | Load_243638 | Port Antonio - 410 | Jul 10, 2026 8:04am | Jul 10, 2026 8:05am | Jul 10, 2026 2:45pm | Jul 10, 2026 2:45pm | Jul 10, 2026 2:45pm | Jul 10, 2026 3:00pm | Jul 10, 2026 3:03pm | Jul 10, 2026 3:03pm |  |  | Fair | No | Premises okay to meter Customer need to get a electrian to repair damaged wires to house Check voltage 236/118/119
Non-Outage | J.E.26.07.10192 | C001845305 | Andrae Clarke | Portland | Completed | Load_351343 | Port Antonio - 410 | Jul 10, 2026 8:04am | Jul 10, 2026 8:05am | Jul 10, 2026 9:54am | Jul 10, 2026 9:54am | Jul 10, 2026 10:59am | Jul 10, 2026 10:34am | Jul 10, 2026 11:00am | Jul 10, 2026 11:00am |  |  | Fair | No | Made several phone calls to the customer and got no response
Non-Outage | J.E.26.07.10390 | C001845304 | Rusean Allen | null | Completed | null | null | Jul 10, 2026 8:04am | Jul 10, 2026 9:34am | Jul 10, 2026 10:14am | Jul 10, 2026 3:21pm | Jul 10, 2026 3:21pm | Jul 10, 2026 3:22pm | Jul 10, 2026 3:22pm | Jul 10, 2026 3:22pm | Fire |  | Fair | No | Okay found
Outage | J.E.26.07.10405 | C001845308 | Rusean Allen | KSAS | Completed | Load_257065 | Cane River - 410 | Jul 10, 2026 8:04am | Jul 10, 2026 9:34am | Jul 10, 2026 10:14am | Jul 10, 2026 10:14am | Jul 10, 2026 11:09am | Jul 10, 2026 11:11am | Jul 10, 2026 11:12am | Jul 10, 2026 11:12am |  |  | Fair | No | Broken wire at switch top, wire was reconnected.
Outage | J.E.26.07.09890 | C001845303 | Christopher Edwards | KSAN | Completed | Load_250649 | Constant Spring - 410 | Jul 10, 2026 8:03am | Jul 10, 2026 8:03am | Jul 10, 2026 5:09pm | Jul 10, 2026 5:09pm | Jul 10, 2026 5:23pm | Jul 10, 2026 5:37pm | Jul 10, 2026 5:38pm | Jul 10, 2026 5:38pm | LowHangingWires |  | Fair | No | Splice and retention broken #6 service wire Using 30ft #6 wire(3) one bolt clamps
Outage | J.E.26.07.09926 | C001845302 | Elvis Trowers | KSAS | Completed | Load_251395 | Duhaney - 310 | Jul 10, 2026 8:03am | Jul 10, 2026 8:03am | Jul 10, 2026 9:04am | Jul 10, 2026 9:04am | Jul 10, 2026 9:42am | Jul 10, 2026 9:52am | Jul 10, 2026 9:52am | Jul 10, 2026 9:52am | BrokenWire |  | Fair | Yes | Premises found closed upon arrival and customer could not be contacted by telephone, even though voice messages were left, the only broken wires found are those of C/W.
Non-Outage | J.E.26.07.09116 | C001845300 | Andrae Clarke | Portland | Completed | Load_256564 | Port Antonio - 310 | Jul 10, 2026 8:02am | Jul 10, 2026 8:05am | Jul 10, 2026 11:52am | Jul 10, 2026 11:52am | Jul 10, 2026 12:28pm | Jul 10, 2026 1:00pm | Jul 10, 2026 1:00pm | Jul 10, 2026 1:00pm |  |  | Fair | No | Check voltage 101/102/203Transformer leads need to be cleaned Emergency crew needed
Non-Outage | J.E.26.07.09157 | C001845301 | Andrae Clarke | Portland | Completed | Load_265439 | Port Antonio - 310 | Jul 10, 2026 8:02am | Jul 10, 2026 8:05am | Jul 10, 2026 11:07am | Jul 10, 2026 11:07am | Jul 10, 2026 11:48am | Jul 10, 2026 11:47am | Jul 10, 2026 11:51am | Jul 10, 2026 11:51am |  |  | Fair | No | Check voltage 122/122/244Premises okay
Non-Outage | J.E.26.07.09307 | C001845299 | Andrae Clarke | Portland | Completed | Load_351343 | Port Antonio - 410 | Jul 10, 2026 8:02am | Jul 10, 2026 8:05am | Jul 10, 2026 9:06am | Jul 10, 2026 9:06am | Jul 10, 2026 9:51am | Jul 10, 2026 9:53am | Jul 10, 2026 9:53am | Jul 10, 2026 9:53am |  |  | Fair | No | Premises found okay check voltage 117/119/236
Non-Outage | J.E.26.07.09329 | C001845296 | Romeo Brissett | St.James | Completed | Load_239961 | Bogue - 610 | Jul 10, 2026 8:02am | Jul 10, 2026 8:09am | Jul 10, 2026 11:23am | Jul 10, 2026 11:27am | Jul 10, 2026 11:27am | Jul 10, 2026 11:25am | Jul 10, 2026 11:28am | Jul 10, 2026 11:28am |  |  | Fair | No | Check and found ok
Non-Outage | J.E.26.07.09387 | C001845297 | Romeo Brissett | St.James | Completed | Load_239961 | Bogue - 610 | Jul 10, 2026 8:02am | Jul 10, 2026 8:09am | Jul 10, 2026 9:05am | Jul 10, 2026 9:05am | Jul 10, 2026 11:21am | Jul 10, 2026 11:18am | Jul 10, 2026 11:27am | Jul 10, 2026 11:27am |  |  | Fair | No | Found secondary neutral joints contaminated, repaired secondary neutral joints. Used 4 clamps, 130-105-233 After 113-117-235
Outage | J.E.26.07.10312 | C001845298 | Milton Charlton | KSAN | Completed | Load_557720 | West Kings House - 410 | Jul 10, 2026 8:02am | Jul 10, 2026 8:02am | Jul 10, 2026 7:02pm | Jul 10, 2026 7:02pm | Jul 10, 2026 7:05pm | Jul 10, 2026 7:10pm | Jul 10, 2026 7:08pm | Jul 10, 2026 7:08pm |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.07.10200 | C001845295 | Derrick Dawkins | Trelawny | Completed | Load_266091 | Greenwood - 110 | Jul 10, 2026 8:00am | Jul 10, 2026 8:00am | Jul 10, 2026 8:31am | Jul 10, 2026 8:31am | Jul 10, 2026 8:31am | Jul 10, 2026 9:07am | Jul 10, 2026 10:04am | Jul 10, 2026 10:04am |  |  | Fair | No | Checked and found ok
Outage | J.E.26.07.10334 | C001845293 | Milton Charlton | KSAN | Completed | Load_266979 | Hope - 510 | Jul 10, 2026 7:58am | Jul 10, 2026 8:00am | Jul 10, 2026 12:29pm | Jul 10, 2026 12:29pm | Jul 10, 2026 1:29pm | Jul 10, 2026 1:30pm | Jul 10, 2026 1:31pm | Jul 10, 2026 1:31pm |  |  | Fair | No | Found okay upon arrival.matter was resolved.
Outage | J.E.26.07.10392 | C001845292 | Shamour Haughton | St.James | Completed | Load_267526 | Bogue - 510 | Jul 10, 2026 7:58am | Jul 10, 2026 3:31pm | Jul 10, 2026 7:55pm | Jul 10, 2026 7:55pm | Jul 10, 2026 7:55pm | Jul 10, 2026 7:55pm | Jul 10, 2026 7:56pm | Jul 10, 2026 7:56pm | Fire |  | Fair | No | Hanover call
Outage | J.E.26.07.10402 | C001845294 | Milton Charlton | KSAN | Completed | Load_568475 | Hope - 510 | Jul 10, 2026 7:58am | Jul 10, 2026 8:00am | Jul 10, 2026 9:08am | Jul 10, 2026 9:08am | Jul 10, 2026 12:24pm | Jul 10, 2026 12:25pm | Jul 10, 2026 12:26pm | Jul 10, 2026 12:26pm |  |  | Fair | No | Found one 3 amps transformer fuse blown at pole#0112576. Refused using one 3 amps fuse and reclosed transformer switch
Outage | J.E.26.07.10397 | C001845291 | Marlon Authors | Manchester | Completed | Load_249196 | Spur Tree - 210 | Jul 10, 2026 7:55am | Jul 10, 2026 7:56am | Jul 10, 2026 8:50am | Jul 10, 2026 8:51am | Jul 10, 2026 9:36am | Jul 10, 2026 9:53am | Jul 10, 2026 9:53am | Jul 10, 2026 9:53am | BrokenWire |  | SevereWind | No | Supply checked and found service wire broken at pole caused by tree contact. Cut and remove same and connect supply using one clamp. Supply leave working ok rdg 115v,114v and cross phased 229 volts
Outage | J.E.26.07.08630 | C001845285 | Richard Nicholas | St.Catherine | Completed | Load_268326 | New Michelton - 210 | Jul 10, 2026 7:52am | Jul 10, 2026 7:52am | Jul 10, 2026 8:06am | Jul 10, 2026 5:10pm | Jul 10, 2026 6:42pm | Jul 10, 2026 7:20pm | Jul 10, 2026 7:24pm | Jul 10, 2026 7:24pm |  |  | Fair | No | Meter socket lug found broken,2w supply left working temporary.customer advised.voltage reading 120v
Outage | J.E.26.07.08651 | C001845286 | Richard Nicholas | St.Catherine | Completed | Load_249847 | New Michelton - 210 | Jul 10, 2026 7:52am | Jul 10, 2026 7:52am | Jul 10, 2026 8:05pm | Jul 10, 2026 8:05pm | Jul 10, 2026 8:34pm | Jul 10, 2026 8:52pm | Jul 10, 2026 8:53pm | Jul 10, 2026 8:53pm |  |  | Fair | No | Cannot locate,directions needed.
Outage | J.E.26.07.09270 | C001845287 | Richard Nicholas | St.Catherine | Completed | Load_269938 | New Michelton - 210 | Jul 10, 2026 7:52am | Jul 10, 2026 7:52am | Jul 10, 2026 7:24pm | Jul 10, 2026 7:24pm | Jul 10, 2026 8:03pm | Jul 10, 2026 8:03pm | Jul 10, 2026 8:05pm | Jul 10, 2026 8:05pm |  |  | Fair | No | This calls is for Kingston and not st.catherine.
Outage | J.E.26.07.09612 | C001845288 | Richard Nicholas | St.Catherine | Completed | Load_243890 | New Michelton - 210 | Jul 10, 2026 7:52am | Jul 10, 2026 7:52am | Jul 10, 2026 8:53pm | Jul 10, 2026 8:53pm | Jul 10, 2026 11:00pm | Jul 10, 2026 11:00pm | Jul 10, 2026 11:02pm | Jul 10, 2026 11:02pm |  |  | Fair | No | Rammy prepaid system
Outage | J.E.26.07.09909 | C001845289 | Richard Nicholas | St.Catherine | Completed | Load_253711 | New Michelton - 410 | Jul 10, 2026 7:52am | Jul 10, 2026 7:52am | Jul 10, 2026 12:56pm | Jul 10, 2026 12:57pm | Jul 10, 2026 12:57pm | Jul 10, 2026 1:15pm | Jul 10, 2026 1:17pm | Jul 10, 2026 1:17pm |  |  | Fair | No | Remade burnt off 4w service phase joint at pothead.1 clamp was used.voltage reading 235,243,240,415,414 and 417v.
Outage | J.E.26.07.10119 | C001845290 | Richard Nicholas | St.Catherine | Completed | Load_243610 | New Michelton - 210 | Jul 10, 2026 7:52am | Jul 10, 2026 7:53am | Jul 10, 2026 1:49pm | Jul 10, 2026 1:49pm | Jul 10, 2026 3:07pm | Jul 10, 2026 3:30pm | Jul 10, 2026 3:30pm | Jul 10, 2026 3:30pm | BrokenWire |  | Fair | No | Premises found locked.
Outage | J.E.26.07.10343 | C001845284 | Damion Reid | Manchester | Completed | Load_1002348 | Spur Tree - 210 | Jul 10, 2026 7:51am | Jul 10, 2026 7:52am | Jul 10, 2026 12:40pm | Jul 10, 2026 12:40pm | Jul 10, 2026 12:40pm | Jul 10, 2026 12:41pm | Jul 10, 2026 12:43pm | Jul 10, 2026 12:43pm |  |  | SevereWind | No | Call related to one done at spur tree earlier
Non-Outage | J.E.26.07.09429 | C001845279 | Wan Carlos Scarlett | null | Completed | null | null | Jul 10, 2026 7:50am | Jul 10, 2026 7:50am | Jul 10, 2026 8:49am | Jul 10, 2026 8:49am | Jul 10, 2026 9:43am | Jul 10, 2026 10:16am | Jul 10, 2026 10:18am | Jul 10, 2026 10:18am |  |  | Fair | No | Found customer 3 wire service at pothead with one of the phase broken off use one Penn union at service wire phase readings 115-116-231
Outage | J.E.26.07.10143 | C001845280 | Wan Carlos Scarlett | St.Catherine | Completed | Load_260470 | Twickenham - 210 | Jul 10, 2026 7:50am | Jul 10, 2026 7:50am | Jul 10, 2026 7:53am | Jul 10, 2026 7:53am | Jul 10, 2026 8:35am | Jul 10, 2026 8:48am | Jul 10, 2026 8:49am | Jul 10, 2026 8:49am |  |  | Fair | No | Customer not available at this time premises closed
Outage | J.E.26.07.10193 | C001845281 | Selvin White | St.Elizabeth | Completed | Load_258087 | Maggotty - 210 | Jul 10, 2026 7:50am | Jul 10, 2026 3:52pm | Jul 10, 2026 10:02pm | Jul 10, 2026 10:03pm | Jul 10, 2026 10:22pm | Jul 10, 2026 10:24pm | Jul 10, 2026 10:24pm | Jul 10, 2026 10:24pm |  |  | Fair | No | Customer cannot be contacted or located as calls to the number goes straight to voicemail.
Outage | J.E.26.07.10361 | C001845282 | Marlon Authors | Manchester | Completed | Load_268017 | Spur Tree - 210 | Jul 10, 2026 7:50am | Jul 10, 2026 7:52am | Jul 10, 2026 10:43am | Jul 10, 2026 10:43am | Jul 10, 2026 10:43am | Jul 10, 2026 11:26am | Jul 10, 2026 11:27am | Jul 10, 2026 11:27am |  |  | SevereWind | No | Patrol and found defective primary lightning arrester neutral blowing to the primary, severe winds. Use hot stick to remove same and replace one blown 10 amp junction fuse no pole #. Restored supply okay
Outage | J.E.26.07.10139 | C001845276 | Raymond Carr | St.Mary | Completed | Load_259633 | Highgate - 210 | Jul 10, 2026 7:49am | Jul 10, 2026 8:05am | Jul 10, 2026 12:50pm | Jul 10, 2026 12:50pm | Jul 10, 2026 1:15pm | Jul 10, 2026 1:59pm | Jul 10, 2026 2:00pm | Jul 10, 2026 2:00pm |  |  | Fair | No | JPS maintenance crew working on line.
Outage | J.E.26.07.10168 | C001845274 | Evan Spaulding | St.Mary | Completed | Load_242674 | Highgate - 210 | Jul 10, 2026 7:49am | Jul 10, 2026 7:51am | Jul 10, 2026 9:59am | Jul 10, 2026 9:59am | Jul 10, 2026 10:28am | Jul 10, 2026 11:41am | Jul 10, 2026 11:43am | Jul 10, 2026 11:43am |  |  | SevereWind | No | Retention two spans secondary conductors and replace 1-10amps junction fuse at pole number 004326
Outage | J.E.26.07.10214 | C001845275 | Evan Spaulding | St.Mary | Completed | Load_572640 | Highgate - 210 | Jul 10, 2026 7:49am | Jul 10, 2026 7:52am | Jul 10, 2026 8:28am | Jul 10, 2026 8:28am | Jul 10, 2026 9:21am | Jul 10, 2026 9:53am | Jul 10, 2026 9:53am | Jul 10, 2026 9:53am |  | Y | Rains | No | Carry spot bushing and replace 1-20 amps junction fuse at pole number 0010716.
Outage | J.E.26.07.10380 | C001845277 | Evan Spaulding | St.Mary | Completed | Load_266596 | Highgate - 210 | Jul 10, 2026 7:49am | Jul 10, 2026 7:52am | Jul 10, 2026 9:56am | Jul 10, 2026 9:56am | Jul 10, 2026 9:56am | Jul 10, 2026 9:56am | Jul 10, 2026 9:56am | Jul 10, 2026 9:56am | TreeContact |  | Fair | No | Customer says she live in Portland and not st Mary.
Outage | J.E.26.07.07969 | C001845269 | Nickolas Rodriques | St.Catherine | Completed | Load_1004021 | Twickenham - 310 | Jul 10, 2026 7:48am | Jul 10, 2026 7:48am | Jul 10, 2026 12:08pm | Jul 10, 2026 12:09pm | Jul 10, 2026 12:36pm | Jul 10, 2026 1:36pm | Jul 10, 2026 1:42pm | Jul 10, 2026 1:42pm |  |  | Fair | No | Customer confirmed that the area outage was already restored.
Outage | J.E.26.07.08286 | C001845268 | Nickolas Rodriques | St.Catherine | Completed | Load_568924 | Twickenham - 310 | Jul 10, 2026 7:48am | Jul 10, 2026 7:48am | Jul 10, 2026 10:31am | Jul 10, 2026 10:36am | Jul 10, 2026 10:48am | Jul 10, 2026 10:49am | Jul 10, 2026 10:57am | Jul 10, 2026 10:57am |  |  | Fair | No | Power restored. Call relates to the 25 amp junction fuse 5hat was replaced earlier.
Outage | J.E.26.07.09733 | C001845266 | Nickolas Rodriques | St.Catherine | Completed | Load_247812 | Twickenham - 310 | Jul 10, 2026 7:48am | Jul 10, 2026 7:48am | Jul 10, 2026 10:57am | Jul 10, 2026 10:57am | Jul 10, 2026 11:35am | Jul 10, 2026 12:06pm | Jul 10, 2026 12:08pm | Jul 10, 2026 12:08pm |  |  | Fair | No | Found premises with electricity. Call relates to the 25 amp junction fuse that was replaced.
Outage | J.E.26.07.09998 | C001845265 | Nickolas Rodriques | St.Catherine | Completed | Load_568932 | Twickenham - 310 | Jul 10, 2026 7:48am | Jul 10, 2026 7:48am | Jul 10, 2026 9:26am | Jul 10, 2026 9:26am | Jul 10, 2026 9:50am | Jul 10, 2026 10:30am | Jul 10, 2026 10:31am | Jul 10, 2026 10:31am |  |  | Fair | No | Checked and found a 25 amp junction fuse blown. Patrol and found nothing on line. Repaired by replacing the fuse after completing patrol.
Outage | J.E.26.07.10000 | C001845267 | Nickolas Rodriques | St.Catherine | Completed | Load_256165 | Twickenham - 310 | Jul 10, 2026 7:48am | Jul 10, 2026 7:48am | Jul 10, 2026 8:16am | Jul 10, 2026 8:37am | Jul 10, 2026 9:10am | Jul 10, 2026 9:24am | Jul 10, 2026 9:26am | Jul 10, 2026 9:26am |  |  | Fair | No | Customer was located and confirmed that the power was restored.
Outage | J.E.26.07.10120 | C001845270 | Evan Spaulding | St.Mary | Completed | Load_241211 | Highgate - 210 | Jul 10, 2026 7:48am | Jul 10, 2026 7:50am | Jul 10, 2026 8:46pm | Jul 10, 2026 8:46pm | Jul 10, 2026 8:46pm | Jul 10, 2026 8:47pm | Jul 10, 2026 8:48pm | Jul 10, 2026 8:48pm | BrokenWire |  | Fair | No | Daylight attention needed,old fowl farm Brimmer hall .
Outage | J.E.26.07.10280 | C001845271 | Damion Reid | Manchester | Completed | Load_255995 | Spur Tree - 210 | Jul 10, 2026 7:48am | Jul 10, 2026 7:49am | Jul 10, 2026 12:45pm | Jul 10, 2026 12:45pm | Jul 10, 2026 12:45pm | Jul 10, 2026 12:45pm | Jul 10, 2026 12:46pm | Jul 10, 2026 12:46pm |  |  | SevereWind | No | Call related to one done at spur tree earlier
Outage | J.E.26.07.10281 | C001845272 | Damion Reid | Manchester | Completed | Load_265815 | Spur Tree - 210 | Jul 10, 2026 7:48am | Jul 10, 2026 7:49am | Jul 10, 2026 8:01am | Jul 10, 2026 8:01am | Jul 10, 2026 10:34am | Jul 10, 2026 12:36pm | Jul 10, 2026 12:40pm | Jul 10, 2026 12:40pm |  |  | SevereWind | No | Burnt off primary phase conductor found cause by banging of conductor open trip saver splice an retention conductor using 10ft of #2 aluminum conductor two #2 preform 3 one bolt clamp and restore power
Outage | J.E.26.07.10284 | C001845273 | Damion Reid | Manchester | Completed | Load_1002349 | Spur Tree - 210 | Jul 10, 2026 7:48am | Jul 10, 2026 7:49am | Jul 10, 2026 12:43pm | Jul 10, 2026 12:43pm | Jul 10, 2026 12:43pm | Jul 10, 2026 12:44pm | Jul 10, 2026 12:45pm | Jul 10, 2026 12:45pm |  |  | SevereWind | No | Call related to one done at spur tree earlier
Non-Outage | J.E.26.01.27455 | C001845263 | Derrick Dawkins | St.James | Completed | Load_259554 | Queens Drive - 710 | Jul 10, 2026 7:47am | Jul 10, 2026 7:57am | Jul 10, 2026 10:05am | Jul 10, 2026 10:05am | Jul 10, 2026 11:15am | Jul 10, 2026 11:16am | Jul 10, 2026 11:20am | Jul 10, 2026 11:20am |  |  | Fair | No | Premises not found cannot locate calls to customer went unanswered
Non-Outage | J.E.26.07.07219 | C001845262 | Derrick Dawkins | null | Completed | null | null | Jul 10, 2026 7:46am | Jul 10, 2026 7:57am | Jul 10, 2026 11:21am | Jul 10, 2026 11:21am | Jul 10, 2026 11:27am | Jul 10, 2026 11:28am | Jul 10, 2026 11:29am | Jul 10, 2026 11:29am |  |  | Fair | No | Calls to customer went unanswered not enough information to locate customer
Outage | J.E.26.07.10323 | C001845254 | Derrick Dawkins | St.James | Completed | Load_254869 | Bogue - 310 | Jul 10, 2026 7:45am | Jul 10, 2026 7:57am | Jul 10, 2026 11:29am | Jul 10, 2026 11:29am | Jul 10, 2026 1:08pm | Jul 10, 2026 1:22pm | Jul 10, 2026 1:23pm | Jul 10, 2026 1:23pm |  |  | Fair | No | Found a junction fuse blow 8 amp due to bird replaced an 8 am junction fuse no pole # available
Outage | J.E.26.07.09062 | C001845248 | Romaine Roberts | St.Mary | Completed | Load_254403 | Highgate -110 | Jul 10, 2026 7:41am | Jul 10, 2026 7:41am | Jul 10, 2026 8:02am | Jul 10, 2026 8:02am | Jul 10, 2026 10:47am | Jul 10, 2026 11:00am | Jul 10, 2026 11:02am | Jul 10, 2026 11:02am |  |  | Fair | No | Junction fuse found blown patrol line and clear bamboo from line and replace 15 amp junction power restore
Outage | J.E.26.07.09087 | C001845247 | Romaine Roberts | St.Mary | Completed | Load_248621 | Highgate -110 | Jul 10, 2026 7:41am | Jul 10, 2026 7:41am | Jul 10, 2026 10:58am | Jul 10, 2026 4:49pm | Jul 10, 2026 7:52pm | Jul 10, 2026 7:54pm | Jul 10, 2026 7:55pm | Jul 10, 2026 7:55pm |  |  | Fair | No | Bamboo fall down on secondary line burst down 3 spans of phase and neutral splice and retention conductor replace 3 amp fuse power restore
Outage | J.E.26.07.10374 | C001845249 | Tyrese Williams | St.Ann | Completed | Load_251147 | Cardiff Hall - 210 | Jul 10, 2026 7:41am | Jul 10, 2026 7:42am | Jul 10, 2026 8:12am | Jul 10, 2026 11:38am | Jul 10, 2026 12:02pm | Jul 10, 2026 12:28pm | Jul 10, 2026 12:28pm | Jul 10, 2026 12:28pm |  |  | Fair | No | Replace a 15 amp junction fuse at pole
Non-Outage | J.E.26.07.06944 | C001845243 | Rayon Foster | Hanover | Completed | Load_302811 | Orange Bay - 310 | Jul 10, 2026 7:40am | Jul 10, 2026 7:40am | Jul 10, 2026 8:18am | Jul 10, 2026 8:20am | Jul 10, 2026 9:48am | Jul 10, 2026 10:13am | Jul 10, 2026 10:13am | Jul 10, 2026 10:13am |  |  | Fair | No | Check and found voltage working ok voltage working ok voltage found at pothead line side 116/10/226 load side 116v/110v/226v meter is locking band customer was advised get a electrician to do internal checks
Non-Outage | J.E.26.07.10367 | C001845239 | Rayon Foster | Hanover | Completed | Load_242732 | Orange Bay - 310 | Jul 10, 2026 7:40am | Jul 10, 2026 7:40am | Jul 10, 2026 8:18am | Jul 10, 2026 11:30am | Jul 10, 2026 12:47pm | Jul 10, 2026 1:02pm | Jul 10, 2026 1:11pm | Jul 10, 2026 1:11pm |  |  | Fair | No | Corrosion at pothead was the cause of customer low voltage customer has a 120v supply meter voltage found at pothead 104v customer is 7 pole span from 25 transformer use 2 one bolt clamp at pothead to restore corroded neutral and corroded phase voltage left after repair 109v
Outage | J.E.26.07.09337 | C001845244 | Romaine Roberts | St.Mary | Completed | Load_249623 | Highgate -110 | Jul 10, 2026 7:40am | Jul 10, 2026 7:40am | Jul 10, 2026 10:58am | Jul 10, 2026 11:34am | Jul 10, 2026 11:34am | Jul 10, 2026 12:28pm | Jul 10, 2026 12:30pm | Jul 10, 2026 12:30pm | TreeContact | Y | Fair | No | Bamboo fall on secondary line and blow 25 kva transformer fuse clear bamboo from line and splice and retention phase and neutral conductor 25 kva open and close
Outage | J.E.26.07.09486 | C001845245 | Javid Vernon | Westmoreland | Completed | Load_265309 | Paradise - 310 | Jul 10, 2026 7:40am | Jul 10, 2026 7:40am | Jul 10, 2026 8:23am | Jul 10, 2026 8:23am | Jul 10, 2026 9:38am | Jul 10, 2026 10:33am | Jul 10, 2026 10:36am | Jul 10, 2026 10:36am |  |  | Fair | No | Replace 80ft #6 triplex service wire an use 6 clamp voltage reading 115/112/228
Outage | J.E.26.07.09960 | C001845242 | Hartley Chin | Clarendon | Completed | Load_406198 | Parnassus - 310 | Jul 10, 2026 7:40am | Jul 10, 2026 7:41am | Jul 10, 2026 9:41am | Jul 10, 2026 9:41am | Jul 10, 2026 12:21pm | Jul 10, 2026 12:45pm | Jul 10, 2026 12:45pm | Jul 10, 2026 12:45pm | BrokenWire |  | Fair | No | Replace 120 ft service wire … use 4 clamp … voltage read 111v , 110v …
Outage | J.E.26.07.10046 | C001845246 | Hartley Chin | Clarendon | Completed | Load_251409 | Parnassus - 310 | Jul 10, 2026 7:40am | Jul 10, 2026 7:41am | Jul 10, 2026 8:06am | Jul 10, 2026 8:08am | Jul 10, 2026 9:20am | Jul 10, 2026 9:39am | Jul 10, 2026 9:40am | Jul 10, 2026 9:40am |  |  | Fair | No | Found okay …voltage read 114v , 115v …
Outage | J.E.26.07.10255 | C001845240 | Hartley Chin | Clarendon | Completed | Load_266671 | Monymusk - 210 | Jul 10, 2026 7:40am | Jul 10, 2026 7:41am | Jul 10, 2026 1:34pm | Jul 10, 2026 2:33pm | Jul 10, 2026 2:53pm | Jul 10, 2026 3:08pm | Jul 10, 2026 3:17pm | Jul 10, 2026 3:17pm |  |  | SevereWind | No | Repair broken phase @ service pole … voltage read 111v ..
Outage | J.E.26.07.10368 | C001845241 | Hartley Chin | Clarendon | Completed | Load_239774 | Parnassus - 310 | Jul 10, 2026 7:40am | Jul 10, 2026 7:41am | Jul 10, 2026 12:29pm | Jul 10, 2026 1:51pm | Jul 10, 2026 2:24pm | Jul 10, 2026 2:26pm | Jul 10, 2026 2:33pm | Jul 10, 2026 2:33pm | BrokenWire |  | Fair | No | Ref to field service!!!! Found 2 customers currently without supply due to dislodged service wire from HEX02516 … unable to repair service wire .. customer meter unknown ..
Non-Outage | J.E.26.07.10174 | C001845238 | Rayon Foster | Hanover | Completed | Load_242763 | Orange Bay - 310 | Jul 10, 2026 7:39am | Jul 10, 2026 7:40am | Jul 10, 2026 10:15am | Jul 10, 2026 10:17am | Jul 10, 2026 10:39am | Jul 10, 2026 11:26am | Jul 10, 2026 11:30am | Jul 10, 2026 11:30am |  |  | Fair | No | Check and found voltage work ok voltage found at pothead 109v/110v/219v Customer meter is in locking
Non-Outage | J.E.26.07.10318 | C001845236 | Stephen Taylor | null | Completed | null | null | Jul 10, 2026 7:38am | Jul 10, 2026 7:39am | Jul 10, 2026 11:59am | Jul 10, 2026 11:59am | Jul 10, 2026 11:59am | Jul 10, 2026 11:59am | Jul 10, 2026 12:00pm | Jul 10, 2026 12:00pm |  |  | SevereWind | No | Patrol clear bush off line with switch stick and close up back junction fuse with a 25 amp fuse safely all customer is now okay pole # 0003768
Outage | J.E.26.07.10245 | C001845233 | Stephen Taylor | St.Thomas | Completed | Load_243194 | Good Year - 210 | Jul 10, 2026 7:38am | Jul 10, 2026 7:39am | Jul 10, 2026 8:49am | Jul 10, 2026 8:49am | Jul 10, 2026 10:38am | Jul 10, 2026 11:49am | Jul 10, 2026 11:59am | Jul 10, 2026 11:59am |  |  | SevereWind | No | Patrol clear bush off line with switch stick and close up back junction fuse with a 25 amp fuse safely all customer is now okay pole # 0003768
Outage | J.E.26.07.10302 | C001845234 | Stephen Taylor | St.Thomas | Completed | Load_243194 | Good Year - 210 | Jul 10, 2026 7:38am | Jul 10, 2026 7:39am | Jul 10, 2026 12:00pm | Jul 10, 2026 12:00pm | Jul 10, 2026 12:00pm | Jul 10, 2026 12:00pm | Jul 10, 2026 12:00pm | Jul 10, 2026 12:00pm |  |  | SevereWind | No | Patrol clear bush off line with switch stick and close up back junction fuse with a 25 amp fuse safely all customer is now okay pole # 0003768
Outage | J.E.26.07.10370 | C001845235 | Stephen Taylor | St.Thomas | Completed | Load_238731 | Good Year - 210 | Jul 10, 2026 7:38am | Jul 10, 2026 7:39am | Jul 10, 2026 1:06pm | Jul 10, 2026 1:06pm | Jul 10, 2026 1:07pm | Jul 10, 2026 1:08pm | Jul 10, 2026 1:45pm | Jul 10, 2026 1:45pm | BrokenWire |  | Fair | No | Patrol the area power is in the area no hanging wire seen a lot of call to customer customer no one answered the call
Outage | J.E.26.07.09970 | C001845232 | Raymond Carr | St.Mary | Completed | Load_266413 | Oracabessa - 210 | Jul 10, 2026 7:36am | Jul 10, 2026 7:36am | Jul 10, 2026 7:58am | Jul 10, 2026 7:58am | Jul 10, 2026 8:51am | Jul 10, 2026 8:25am | Jul 10, 2026 8:52am | Jul 10, 2026 8:52am |  |  | Fair | No | Customer reported that supply was restored yesterday evening.
Non-Outage | J.E.26.06.17672 | C001845229 | Tajay Bernard | null | Completed | null | null | Jul 10, 2026 7:35am | Jul 10, 2026 7:36am | Jul 10, 2026 8:23am | Jul 10, 2026 12:35pm | Jul 10, 2026 1:11pm | Jul 10, 2026 1:12pm | Jul 10, 2026 1:12pm | Jul 10, 2026 1:12pm | LeaningPole |  | Fair | No | Area and premises check and found okay unable to locate customer on premises multiple phone calls to customer number went unanswered
Non-Outage | J.E.26.07.04124 | C001845231 | Tajay Bernard | Hanover | Completed | Load_258270 | Orange Bay - 310 | Jul 10, 2026 7:35am | Jul 10, 2026 7:36am | Jul 10, 2026 7:41am | Jul 10, 2026 7:41am | Jul 10, 2026 8:21am | Jul 10, 2026 8:29am | Jul 10, 2026 8:29am | Jul 10, 2026 8:29am |  |  | Fair | No | Area check and found okay unable to locate customer on premises multiple phone calls to customer number went unanswered
Non-Outage | J.E.26.07.08843 | C001845230 | Tajay Bernard | Hanover | Completed | Load_257388 | Orange Bay - 310 | Jul 10, 2026 7:35am | Jul 10, 2026 7:36am | Jul 10, 2026 8:23am | Jul 10, 2026 8:30am | Jul 10, 2026 8:53am | Jul 10, 2026 9:17am | Jul 10, 2026 9:17am | Jul 10, 2026 9:17am |  |  | Fair | No | Area check and found okay unable to locate customer on premises multiple phone to customer number went unanswered
Outage | J.E.26.07.10058 | C001845228 | Tajay Bernard | Hanover | Completed | Load_253920 | Orange Bay - 310 | Jul 10, 2026 7:35am | Jul 10, 2026 7:36am | Jul 10, 2026 8:23am | Jul 10, 2026 9:28am | Jul 10, 2026 9:28am | Jul 10, 2026 10:06am | Jul 10, 2026 10:08am | Jul 10, 2026 10:08am |  |  | Fair | No | Clean and remake joints at customer pothead use 3 clamps Voltage found 103/107/210Voltage left 112/115/227
Outage | J.E.26.07.10182 | C001845227 | Raymond Carr | St.Mary | Completed | Load_269849 | Oracabessa - 210 | Jul 10, 2026 7:34am | Jul 10, 2026 7:35am | Jul 10, 2026 9:00am | Jul 10, 2026 9:00am | Jul 10, 2026 10:04am | Jul 10, 2026 10:00am | Jul 10, 2026 10:05am | Jul 10, 2026 10:05am |  |  | Fair | No | Customer couldn’t be contacted.
Non-Outage | J.E.26.07.10373 | C001845224 | Gregory Grossett | null | Completed | null | null | Jul 10, 2026 7:33am | Jul 10, 2026 3:45pm | Jul 10, 2026 9:28pm | Jul 10, 2026 9:28pm | Jul 10, 2026 10:06pm | Jul 10, 2026 10:07pm | Jul 10, 2026 10:09pm | Jul 10, 2026 10:09pm | LeakingTransformer |  | Fair | No | Completed. Maintenance team attended to this report today. Customer okay.
Outage | J.E.26.07.09600 | C001845222 | Neville Spencer | Clarendon | Completed | Load_241634 | May Pen - 110 | Jul 10, 2026 7:33am | Jul 10, 2026 7:34am | Jul 10, 2026 10:01am | Jul 10, 2026 10:01am | Jul 10, 2026 10:41am | Jul 10, 2026 10:41am | Jul 10, 2026 10:42am | Jul 10, 2026 10:42am |  |  | Fair | No | Call belong to ST Ann’s.
Outage | J.E.26.07.10033 | C001845221 | Neville Spencer | Clarendon | Completed | Load_260045 | May Pen - 110 | Jul 10, 2026 7:33am | Jul 10, 2026 7:34am | Jul 10, 2026 8:30am | Jul 10, 2026 8:30am | Jul 10, 2026 9:40am | Jul 10, 2026 9:41am | Jul 10, 2026 10:00am | Jul 10, 2026 10:00am |  |  | Fair | No | Reconnect 3 , wire service voltage reading 112 116 229 supply restored.
Outage | J.E.26.07.10324 | C001845223 | Raymond Carr | St.Mary | Completed | Load_262298 | Oracabessa - 210 | Jul 10, 2026 7:33am | Jul 10, 2026 7:33am | Jul 10, 2026 12:46pm | Jul 10, 2026 12:46pm | Jul 10, 2026 12:46pm | Jul 10, 2026 12:00am | Jul 10, 2026 12:48pm | Jul 10, 2026 12:48pm | BrokenWire |  | Fair | No | Supply was restored. Related to back street boscobell.
Outage | J.E.26.07.08643 | C001845216 | Tyrese Williams | St.Ann | Completed | Load_250632 | Cardiff Hall - 310 | Jul 10, 2026 7:31am | Jul 10, 2026 7:32am | Jul 10, 2026 8:19am | Jul 10, 2026 9:34am | Jul 10, 2026 9:34am | Jul 10, 2026 9:35am | Jul 10, 2026 9:35am | Jul 10, 2026 9:35am |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.08860 | C001845215 | Tyrese Williams | St.Ann | Completed | Load_242498 | Cardiff Hall - 310 | Jul 10, 2026 7:31am | Jul 10, 2026 7:31am | Jul 10, 2026 8:12am | Jul 10, 2026 8:20am | Jul 10, 2026 8:21am | Jul 10, 2026 8:21am | Jul 10, 2026 8:21am | Jul 10, 2026 8:21am |  |  | Fair | No | Customer said he didn’t make any report
Outage | J.E.26.07.08919 | C001845214 | Tyrese Williams | St.Ann | Completed | Load_245275 | Cardiff Hall - 310 | Jul 10, 2026 7:31am | Jul 10, 2026 7:31am | Jul 10, 2026 8:12am | Jul 10, 2026 8:22am | Jul 10, 2026 9:32am | Jul 10, 2026 9:33am | Jul 10, 2026 9:33am | Jul 10, 2026 9:33am |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.09111 | C001845212 | Tyrese Williams | St.Ann | Completed | Load_264409 | Cardiff Hall - 310 | Jul 10, 2026 7:31am | Jul 10, 2026 7:31am | Jul 10, 2026 8:16am | Jul 10, 2026 8:17am | Jul 10, 2026 8:17am | Jul 10, 2026 8:17am | Jul 10, 2026 8:18am | Jul 10, 2026 8:18am |  |  | Fair | No | Premises not four not getting customer on phone
Outage | J.E.26.07.10344 | C001845218 | Raymond Carr | St.Mary | Completed | Load_252304 | Oracabessa - 210 | Jul 10, 2026 7:31am | Jul 10, 2026 7:33am | Jul 10, 2026 10:52am | Jul 10, 2026 10:52am | Jul 10, 2026 11:24am | Jul 10, 2026 11:38am | Jul 10, 2026 11:42am | Jul 10, 2026 11:42am |  |  | SevereWind | No | Blown 50 kva transformer fuse found at pole number 0013615, line patrol and found okay, however lightening was suspected. A 5 amp fuse fuse was used to renew supply was restored.
Non-Outage | J.E.26.07.09958 | C001845210 | Damion Reid | Manchester | Completed | Load_240206 | Spur Tree - 310 | Jul 10, 2026 7:30am | Jul 10, 2026 7:31am | Jul 10, 2026 4:33pm | Jul 10, 2026 4:33pm | Jul 10, 2026 5:26pm | Jul 10, 2026 6:13pm | Jul 10, 2026 6:15pm | Jul 10, 2026 6:15pm |  |  | SevereWind | No | Remade corroded phase at secondary pole for 3 wire service using one 1 bolt clamp voltage reading at meter socket phase to neutral 113-v114v access phase 229v
Outage | J.E.26.07.09370 | C001845211 | Tyrese Williams | St.Ann | Completed | Load_254202 | Cardiff Hall - 310 | Jul 10, 2026 7:30am | Jul 10, 2026 7:31am | Jul 10, 2026 8:12am | Jul 10, 2026 10:41am | Jul 10, 2026 11:05am | Jul 10, 2026 11:29am | Jul 10, 2026 11:38am | Jul 10, 2026 11:38am | BrokenWire |  | Fair | No | Install 100ft of #6 service wire at pole use 5 pg clamp
Outage | J.E.26.07.10365 | C001845207 | Christopher Edwards | KSAN | Completed | Load_249864 | Constant Spring - 410 | Jul 10, 2026 7:30am | Jul 10, 2026 7:43am | Jul 10, 2026 7:57am | Jul 10, 2026 8:41am | Jul 10, 2026 8:41am | Jul 10, 2026 9:28am | Jul 10, 2026 9:29am | Jul 10, 2026 9:29am |  |  | Fair | No | Customer breaker was tripped Supply is now at the premises
Non-Outage | J.E.26.07.10355 | C001845206 | Denton Williams | Portland | Completed | Load_259756 | Port Antonio - 410 | Jul 10, 2026 7:29am | Jul 10, 2026 9:14am | Jul 10, 2026 2:00pm | Jul 10, 2026 2:00pm | Jul 10, 2026 3:02pm | Jul 10, 2026 3:02pm | Jul 10, 2026 3:03pm | Jul 10, 2026 3:03pm | LowHangingWires |  | Fair | No | Premises not found
Outage | J.E.26.07.09294 | C001845205 | Calvin Poorman | St.Ann | Completed | Load_249379 | Roaring River - 210 | Jul 10, 2026 7:29am | Jul 10, 2026 9:52am | Jul 10, 2026 10:50am | Jul 10, 2026 10:52am | Jul 10, 2026 10:52am | Jul 10, 2026 10:53am | Jul 10, 2026 10:53am | Jul 10, 2026 10:53am |  |  | Fair | No
Outage | J.E.26.07.09681 | C001845204 | Daniel Francis | St.Ann | Completed | Load_269944 | Roaring River - 210 | Jul 10, 2026 7:29am | Jul 11, 2026 4:05pm | Jul 11, 2026 6:30pm | Jul 11, 2026 6:30pm | Jul 11, 2026 6:33pm | Jul 11, 2026 6:33pm | Jul 11, 2026 6:34pm | Jul 11, 2026 6:34pm |  |  | Fair | No | Fond okay
Non-Outage | J.E.26.07.09865 | C001845202 | Oshane Warren | Westmoreland | Completed | Load_258899 | Paradise - 310 | Jul 10, 2026 7:28am | Jul 10, 2026 7:28am | Jul 10, 2026 9:23am | Jul 10, 2026 9:23am | Jul 10, 2026 9:47am | Jul 10, 2026 10:03am | Jul 10, 2026 10:08am | Jul 10, 2026 10:08am |  |  | Rains | No | Open 25 kva transformer and top down transformer for position 3 to position 2 voltage 116 116 232
Non-Outage | J.E.26.07.09885 | C001845203 | Oshane Warren | Westmoreland | Completed | Load_258899 | Paradise - 310 | Jul 10, 2026 7:28am | Jul 10, 2026 7:28am | Jul 10, 2026 10:08am | Jul 10, 2026 10:08am | Jul 10, 2026 10:09am | Jul 10, 2026 10:09am | Jul 10, 2026 10:11am | Jul 10, 2026 10:11am |  |  | Rains | No | Open 25kva xformer and top down xformer from 3 to 2 voltage 116 116 232
Non-Outage | J.E.26.07.05471 | C001845201 | Barrington Brown | St.James | Completed | Load_249760 | Queens Drive - 310 | Jul 10, 2026 7:27am | Jul 10, 2026 7:27am | Jul 10, 2026 9:06am | Jul 10, 2026 9:06am | Jul 10, 2026 9:36am | Jul 10, 2026 12:03pm | Jul 10, 2026 12:03pm | Jul 10, 2026 12:03pm |  |  | Fair | No | Crewfound 2 blown 100kva transformer fuse on location. Crew also found two burnt joints at transformer drop lead. Crew used two 394 amp acts to remake joints. Crew changed two switch barrels and re energized circuit. Customer supply now restored.
Non-Outage | J.E.26.07.05883 | C001845200 | Barrington Brown | St.James | Completed | Load_1002436 | Queens Drive - 810 | Jul 10, 2026 7:27am | Jul 10, 2026 7:27am | Jul 10, 2026 12:04pm | Jul 10, 2026 12:04pm | Jul 10, 2026 12:47pm | Jul 10, 2026 12:50pm | Jul 10, 2026 12:50pm | Jul 10, 2026 12:50pm |  |  | Fair | No | Checked and found ok issue was resolved.
Non-Outage | J.E.26.07.07543 | C001845198 | Barrington Brown | St.James | Completed | Load_266844 | Queens Drive - 710 | Jul 10, 2026 7:27am | Jul 10, 2026 7:27am | Jul 10, 2026 12:51pm | Jul 10, 2026 12:51pm | Jul 10, 2026 1:17pm | Jul 10, 2026 1:19pm | Jul 10, 2026 1:19pm | Jul 10, 2026 1:19pm |  |  | Fair | No | Checked and found ok
Non-Outage | J.E.26.07.09541 | C001845197 | Barrington Brown | St.James | Completed | Load_248827 | Queens Drive - 710 | Jul 10, 2026 7:27am | Jul 10, 2026 7:27am | Jul 10, 2026 2:53pm | Jul 10, 2026 2:53pm | Jul 10, 2026 3:31pm | Jul 10, 2026 3:36pm | Jul 10, 2026 3:36pm | Jul 10, 2026 3:36pm |  |  | Fair | No | Crew found blown found 100kva transformer fuse on location. Crew refused and all customers restored.
Outage | J.E.26.07.08902 | C001845193 | Calvin Poorman | St.Ann | Completed | Load_264817 | Roaring River - 210 | Jul 10, 2026 7:26am | Jul 10, 2026 9:58am | Jul 10, 2026 10:34am | Jul 10, 2026 10:34am | Jul 10, 2026 10:49am | Jul 10, 2026 10:50am | Jul 10, 2026 10:50am | Jul 10, 2026 10:50am |  |  | Fair | No
Outage | J.E.26.07.09723 | C001845196 | Raymond Lewis | St.Ann | Completed | Load_263260 | Roaring River - 410 | Jul 10, 2026 7:26am | Jul 10, 2026 7:26am | Jul 10, 2026 8:03am | Jul 10, 2026 8:03am | Jul 10, 2026 9:05am | Jul 10, 2026 9:07am | Jul 10, 2026 9:08am | Jul 10, 2026 9:08am |  |  | Fair | No | Refuse and close 20A junction fuse
Non-Outage | J.E.26.07.10339 | C001845192 | Javid Vernon | null | Completed | null | null | Jul 10, 2026 7:25am | Jul 10, 2026 10:43am | Jul 10, 2026 10:52am | Jul 10, 2026 10:52am | Jul 10, 2026 12:08pm | Jul 10, 2026 1:10pm | Jul 10, 2026 1:11pm | Jul 10, 2026 1:11pm |  |  | Fair | No | Isolate one 25kva transformer to reconnect secondary jumper use one #2 preform and one clamp voltage reading 117/116/234
Outage | J.E.26.07.10039 | C001845191 | Oshane Warren | Westmoreland | Completed | Load_267905 | Paradise - 210 | Jul 10, 2026 7:25am | Jul 10, 2026 7:25am | Jul 10, 2026 10:11am | Jul 10, 2026 10:11am | Jul 10, 2026 10:32am | Jul 10, 2026 10:44am | Jul 10, 2026 10:45am | Jul 10, 2026 10:45am |  |  | Rains | No | Meter Defective needs to be change refer to feel service
Outage | J.E.26.07.10310 | C001845190 | Javid Vernon | Westmoreland | Completed | Load_253644 | Paradise - 310 | Jul 10, 2026 7:24am | Jul 10, 2026 7:24am | Jul 10, 2026 10:48am | Jul 10, 2026 10:48am | Jul 10, 2026 10:48am | Jul 10, 2026 10:48am | Jul 10, 2026 10:49am | Jul 10, 2026 10:49am |  |  | Fair | No | Related to previous call job #08564
Outage | J.E.26.07.08816 | C001845189 | Kenroy Dale | Manchester | Completed | Load_242004 | Porus - 310 | Jul 10, 2026 7:23am | Jul 10, 2026 7:23am | Jul 10, 2026 8:39am | Jul 10, 2026 10:21am | Jul 10, 2026 10:21am | Jul 10, 2026 10:22am | Jul 10, 2026 10:23am | Jul 10, 2026 10:23am | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Defective 10 kva transformer found, transformer was isolated andapproximately 10-15 customers are affected (circuit was unable to tie in) transformer need to be replaced
Outage | J.E.26.07.09054 | C001845186 | Omar King | St.Ann | Completed | Load_244721 | Ocho Rios - 310 | Jul 10, 2026 7:22am | Jul 10, 2026 7:23am | Jul 10, 2026 9:18am | Jul 10, 2026 9:18am | Jul 10, 2026 9:18am | Jul 10, 2026 9:18am | Jul 10, 2026 9:18am | Jul 10, 2026 9:18am |  |  | Fair | No | Problem as been resolved
Outage | J.E.26.07.09454 | C001845188 | Omar King | St.Ann | Completed | Load_250046 | Ocho Rios - 310 | Jul 10, 2026 7:22am | Jul 10, 2026 7:23am | Jul 10, 2026 8:56am | Jul 10, 2026 8:56am | Jul 10, 2026 9:17am | Jul 10, 2026 9:17am | Jul 10, 2026 9:18am | Jul 10, 2026 9:18am |  |  | Fair | No | Problem as been resolved
Outage | J.E.26.07.10157 | C001845187 | Tajay Bernard | Hanover | Completed | Load_253054 | Orange Bay - 310 | Jul 10, 2026 7:22am | Jul 10, 2026 7:25am | Jul 10, 2026 7:29am | Jul 10, 2026 7:35am | Jul 10, 2026 7:35am | Jul 10, 2026 7:36am | Jul 10, 2026 7:37am | Jul 10, 2026 7:37am |  |  | Fair | No | Customer stated that the issue has been resolved
Non-Outage | J.E.26.07.05874 | C001845178 | Kenroy Dale | Manchester | Completed | Load_254918 | Porus - 310 | Jul 10, 2026 7:19am | Jul 10, 2026 7:20am | Jul 10, 2026 10:30am | Jul 10, 2026 2:36pm | Jul 10, 2026 4:17pm | Jul 10, 2026 4:52pm | Jul 10, 2026 5:01pm | Jul 10, 2026 5:01pm |  |  | Fair | No | Corroded phase found at pole, remade connection using one 1bolt clamp. Voltage reading 111/113/224
Non-Outage | J.E.26.07.09929 | C001845181 | Kenroy Dale | Manchester | Completed | Load_251477 | Porus - 310 | Jul 10, 2026 7:19am | Jul 10, 2026 7:20am | Jul 10, 2026 11:04am | Jul 10, 2026 12:32pm | Jul 10, 2026 2:12pm | Jul 10, 2026 2:34pm | Jul 10, 2026 2:35pm | Jul 10, 2026 2:35pm |  |  | Fair | No | Burned off phase found at pole, remade connection using one 1bolt clamp voltage reading 113/115/228
Outage | J.E.26.07.07550 | C001845174 | Barrington Brown | St.James | Completed | Load_247384 | Queens Drive - 710 | Jul 10, 2026 7:16am | Jul 10, 2026 7:16am | Jul 10, 2026 1:19pm | Jul 10, 2026 1:19pm | Jul 10, 2026 2:09pm | Jul 10, 2026 2:11pm | Jul 10, 2026 2:11pm | Jul 10, 2026 2:11pm |  |  | Fair | No
Outage | J.E.26.07.07718 | C001845175 | Barrington Brown | St.James | Completed | Load_243105 | Queens Drive - 710 | Jul 10, 2026 7:16am | Jul 10, 2026 7:16am | Jul 10, 2026 2:13pm | Jul 10, 2026 2:13pm | Jul 10, 2026 2:52pm | Jul 10, 2026 2:52pm | Jul 10, 2026 2:53pm | Jul 10, 2026 2:53pm | BrokenWire |  | Fair | No | Checked and found ok
Outage | J.E.26.07.10162 | C001845170 | Calvin Poorman | St.Ann | Completed | Load_249772 | Roaring River - 410 | Jul 10, 2026 7:15am | Jul 10, 2026 9:54am | Jul 10, 2026 10:10am | Jul 10, 2026 10:10am | Jul 10, 2026 10:28am | Jul 10, 2026 10:32am | Jul 10, 2026 10:33am | Jul 10, 2026 10:33am |  |  | Fair | No
Outage | J.E.26.07.10145 | C001845169 | Gregory Grossett | Portland | Completed | Load_254246 | Port Antonio - 410 | Jul 10, 2026 7:13am | Jul 10, 2026 3:26pm | Jul 10, 2026 4:11pm | Jul 10, 2026 4:11pm | Jul 10, 2026 5:14pm | Jul 10, 2026 5:30pm | Jul 10, 2026 5:44pm | Jul 10, 2026 5:44pm |  |  | Fair | No | 8 amps junction fuse blown no pole number at location cause by bamboo on line, clear bamboo and restore line section, also repair 220 service at pothead,material used 1-8 amps fuse, 2 pen union sleeves, 1 one bolt clamp, voltage left 120-120-240 volts in meter socket is defective.
Non-Outage | J.E.26.07.09321 | C001845168 | Denton Williams | null | Completed | null | null | Jul 10, 2026 7:12am | Jul 10, 2026 7:14am | Jul 10, 2026 10:09am | Jul 10, 2026 10:10am | Jul 10, 2026 10:28am | Jul 10, 2026 10:53am | Jul 10, 2026 11:01am | Jul 10, 2026 11:01am |  |  | Rains | No | The customer confirmed that their power supply was restored yesterday. Customer okay.
Outage | J.E.26.07.09356 | C001845166 | Denton Williams | Portland | Completed | Load_349214 | Port Antonio - 410 | Jul 10, 2026 7:12am | Jul 10, 2026 7:14am | Jul 10, 2026 1:08pm | Jul 10, 2026 1:08pm | Jul 10, 2026 1:09pm | Jul 10, 2026 1:24pm | Jul 10, 2026 1:39pm | Jul 10, 2026 1:39pm |  | Y | Fair | No | Broken open secondary neutral wire across river. Tree engulfed secondary lines. Heavy vegetation is required and conductor needs to be splice and retention. Recommend no. 2 twisted conductor to replace open secondary wire. Approximately 300ft is needed.
Outage | J.E.26.07.09825 | C001845167 | Collin Robinson | Portland | Completed | Load_246653 | Port Antonio - 310 | Jul 10, 2026 7:12am | Jul 10, 2026 3:27pm | Jul 10, 2026 4:00pm | Jul 10, 2026 4:01pm | Jul 10, 2026 4:48pm | Jul 10, 2026 4:49pm | Jul 10, 2026 4:50pm | Jul 10, 2026 4:50pm |  |  | Fair | No | Information received from customer that supply was restored from yesterday
Outage | J.E.26.07.10314 | C001845165 | Denton Williams | Portland | Completed | Load_260425 | Port Antonio - 410 | Jul 10, 2026 7:12am | Jul 10, 2026 7:14am | Jul 10, 2026 7:37am | Jul 10, 2026 7:37am | Jul 10, 2026 8:08am | Jul 10, 2026 10:01am | Jul 10, 2026 10:09am | Jul 10, 2026 10:09am |  | Y | Rains | No | Tree fell on line and caused secondary to burn down, use 10 feet of #2 aluminum wire to carry out repair. One 3 amp fuse
Non-Outage | J.E.26.07.10364 | C001845163 | Denton Williams | null | Completed | null | null | Jul 10, 2026 7:11am | Jul 10, 2026 7:14am | Jul 10, 2026 11:03am | Jul 10, 2026 11:03am | Jul 10, 2026 11:03am | Jul 10, 2026 11:03am | Jul 10, 2026 11:04am | Jul 10, 2026 11:04am | BrokenWire |  | Rains | No | Broken wire was repaired this morning. Area is back to normalcy.
Outage | J.E.26.07.10303 | C001845142 | Christopher Edwards | KSAN | Completed | Load_256340 | Constant Spring - 410 | Jul 10, 2026 5:25am | Jul 10, 2026 7:32am | Jul 10, 2026 9:30am | Jul 10, 2026 9:30am | Jul 10, 2026 10:25am | Jul 10, 2026 11:59am | Jul 10, 2026 12:05pm | Jul 10, 2026 12:05pm | Fire | Y | Fair | No | Isolate 50 kva transformer To Splice and retention broken open secondary wireUsing:60ft #2 AA conductor (2) #2 preform (4) one bolt clamps Also clear bamboo off open secondary lines
Outage | J.E.26.07.10202 | C001845138 | Swon Miller | St.James | Completed | Load_292296 | Rose Hall - 210 | Jul 10, 2026 4:55am | Jul 10, 2026 4:55am | Jul 10, 2026 5:04am | Jul 10, 2026 5:04am | Jul 10, 2026 6:06am | Jul 10, 2026 6:21am | Jul 10, 2026 6:28am | Jul 10, 2026 6:28am |  |  | Fair | No | Check and found area okay voltage found 117/116/234 customer states that power supply has been restored
Outage | J.E.26.07.10237 | C001845139 | Swon Miller | St.James | Completed | Load_261029 | Rose Hall - 210 | Jul 10, 2026 4:55am | Jul 10, 2026 4:55am | Jul 10, 2026 6:28am | Jul 10, 2026 6:28am | Jul 10, 2026 6:47am | Jul 10, 2026 6:57am | Jul 10, 2026 7:00am | Jul 10, 2026 7:00am |  |  | Fair | No | Check and found area okay voltage found 117/116/234 customer states that power supply has been restored
Outage | J.E.26.07.10235 | C001845136 | Delano Gayle | St.Catherine | Completed | Load_258734 | Twickenham - 310 | Jul 10, 2026 4:46am | Jul 10, 2026 4:47am | Jul 10, 2026 4:57am | Jul 10, 2026 4:57am | Jul 10, 2026 5:55am | Jul 10, 2026 6:19am | Jul 10, 2026 6:19am | Jul 10, 2026 6:19am |  |  | Fair | No | Broken secondary phase in 1span , blown 25kva transformer fuse no pole number, splice and retention secondary phase use 1 2/0 preform 2 clamps replace 3amps voltage readings 113-114-227
Outage | J.E.26.07.10260 | C001845135 | Edward Royal | KSAN | Completed | Load_254870 | Constant Spring - 210 | Jul 10, 2026 4:45am | Jul 10, 2026 4:47am | Jul 10, 2026 6:45am | Jul 10, 2026 6:45am | Jul 10, 2026 6:45am | Jul 10, 2026 7:39am | Jul 10, 2026 7:40am | Jul 10, 2026 7:40am |  |  | Fair | No | Replaced 30A junction fuse pole # 0012921
Outage | J.E.26.07.10273 | C001845134 | Edward Royal | KSAN | Completed | Load_243485 | Constant Spring - 210 | Jul 10, 2026 4:44am | Jul 10, 2026 4:47am | Jul 10, 2026 7:40am | Jul 10, 2026 7:40am | Jul 10, 2026 7:40am | Jul 10, 2026 7:41am | Jul 10, 2026 7:43am | Jul 10, 2026 7:43am |  |  | Fair | No | Premises found ok call related to outage
Outage | J.E.26.07.10275 | C001845133 | Raymond Carr | St.Mary | Completed | Load_262298 | Oracabessa - 210 | Jul 10, 2026 4:44am | Jul 10, 2026 7:34am | Jul 10, 2026 11:44am | Jul 10, 2026 11:44am | Jul 10, 2026 11:57am | Jul 10, 2026 12:30pm | Jul 10, 2026 12:43pm | Jul 10, 2026 12:43pm |  |  | SevereWind | No | Blown junction fuse found at pole number 005005, line patrol and found okay lightening was suspected. A 15 amp fuse was used to renew supply was restored.
Outage | J.E.26.07.09813 | C001845125 | Edward Royal | KSAN | Completed | Load_264523 | Constant Spring - 410 | Jul 9, 2026 11:15pm | Jul 9, 2026 11:17pm | Jul 10, 2026 6:10am | Jul 10, 2026 6:10am | Jul 10, 2026 6:10am | Jul 10, 2026 6:10am | Jul 10, 2026 6:11am | Jul 10, 2026 6:11am |  |  | Fair | No | Premises not found unable to communicate with customer
Outage | J.E.26.07.10221 | C001845124 | Edward Royal | KSAN | Completed | Load_256340 | Constant Spring - 410 | Jul 9, 2026 11:14pm | Jul 9, 2026 11:17pm | Jul 9, 2026 11:40pm | Jul 9, 2026 11:40pm | Jul 10, 2026 12:38am | Jul 10, 2026 12:38am | Jul 10, 2026 12:39am | Jul 10, 2026 12:39am | Fire |  | Fair | No | Premises not found daylight attention
Outage | J.E.26.07.10198 | C001845121 | Swon Miller | St.James | Completed | Load_244260 | Rose Hall - 210 | Jul 9, 2026 10:52pm | Jul 9, 2026 11:12pm | Jul 10, 2026 12:40am | Jul 10, 2026 12:40am | Jul 10, 2026 12:46am | Jul 22, 2026 12:42am | Jul 10, 2026 12:49am | Jul 10, 2026 12:49am |  |  | Fair | No | Call related to previous
Outage | J.E.26.07.10199 | C001845120 | Swon Miller | St.James | Completed | Load_239852 | Rose Hall - 210 | Jul 9, 2026 10:52pm | Jul 9, 2026 11:12pm | Jul 9, 2026 11:20pm | Jul 9, 2026 11:20pm | Jul 10, 2026 12:05am | Jul 15, 2026 12:39am | Jul 10, 2026 12:40am | Jul 10, 2026 12:40am |  |  | Fair | No | Found 1,30 amp junction fuse blown cause by contamination replace 30 amp junction fuse no pole number available voltage found 0.000 voltage left 115/116/232
Outage | J.E.26.07.09311 | C001845115 | Shamour Haughton | St.James | Completed | Load_237918 | Bogue - 310 | Jul 9, 2026 10:22pm | Jul 9, 2026 10:23pm | Jul 9, 2026 11:32pm | Jul 9, 2026 11:32pm | Jul 9, 2026 11:41pm | Jul 9, 2026 11:41pm | Jul 9, 2026 11:43pm | Jul 9, 2026 11:43pm |  |  | Fair | No | Found 1,10amp junction fuse blown, refuse 10amp junction
Outage | J.E.26.07.10189 | C001845112 | Daniel Francis | St.Ann | Completed | Load_237638 | Roaring River - 410 | Jul 9, 2026 10:09pm | Jul 9, 2026 10:22pm | Jul 9, 2026 11:09pm | Jul 9, 2026 11:09pm | Jul 9, 2026 11:16pm | Jul 9, 2026 11:17pm | Jul 9, 2026 11:17pm | Jul 9, 2026 11:17pm | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Rains | No | Not answering phone
Outage | J.E.26.07.10111 | C001845101 | Horace Malcolm | St.James | Completed | Load_250268 | Queens Drive - 710 | Jul 9, 2026 9:22pm | Jul 9, 2026 9:44pm | Jul 9, 2026 10:29pm | Jul 9, 2026 10:29pm | Jul 9, 2026 10:50pm | Jul 9, 2026 11:06pm | Jul 9, 2026 11:06pm | Jul 9, 2026 11:06pm |  |  | Fair | No | Check and found ok unable to locate customer multiple calls to customer unavailable
Outage | J.E.26.07.10157 | C001845100 | Dean Smith | Hanover | Completed | Load_253054 | Orange Bay - 310 | Jul 9, 2026 9:21pm | Jul 9, 2026 9:22pm | Jul 9, 2026 10:29pm | Jul 9, 2026 10:30pm | Jul 9, 2026 10:30pm | Jul 9, 2026 10:30pm | Jul 9, 2026 10:31pm | Jul 9, 2026 10:31pm |  |  | Rains | No | Please forward to morning team. Reason this call would run into overtime base on the distance.
Outage | J.E.26.07.10140 | C001845098 | Selvin White | St.Elizabeth | Completed | Load_251946 | Maggotty - 110 | Jul 9, 2026 9:13pm | Jul 10, 2026 3:52pm | Jul 10, 2026 4:12pm | Jul 10, 2026 4:12pm | Jul 10, 2026 4:56pm | Jul 10, 2026 5:33pm | Jul 10, 2026 5:36pm | Jul 10, 2026 5:36pm |  |  | Fair | No | Replace approximately 50 ft of number six triplex service wire that was damaged and removed after the hurricane. Supply restored with voltage readings left inside customer’s meter socket of 223,111,112 volts.
Outage | J.E.26.07.10124 | C001845097 | Selvin White | St.Elizabeth | Completed | Load_574150 | Maggotty - 110 | Jul 9, 2026 9:12pm | Jul 9, 2026 9:14pm | Jul 9, 2026 10:10pm | Jul 9, 2026 10:10pm | Jul 9, 2026 10:10pm | Jul 9, 2026 10:17pm | Jul 9, 2026 10:17pm | Jul 9, 2026 10:17pm |  |  | Fair | No | Customer was contacted and said no supply is at premises since hurricane Melissa as premises was damaged and needs repair however bill is being sent out. So please refer to the field service department for further investigation.
Outage | J.E.26.07.10113 | C001845096 | Cliton Henry | St.Mary | Completed | Load_262319 | Blackstonedge - 110 | Jul 9, 2026 9:10pm | Jul 9, 2026 9:11pm | Jul 9, 2026 9:15pm | Jul 9, 2026 9:15pm | Jul 9, 2026 9:40pm | Jul 9, 2026 9:55pm | Jul 9, 2026 9:55pm | Jul 9, 2026 9:55pm |  |  | Fair | No | A blown 20 junction fuse found at Waterford pole #091352. Supply restored using 1-20 amp fuse.
Outage | J.E.26.07.10027 | C001845093 | Daniel Francis | St.Ann | Completed | Load_310933 | Roaring River - 410 | Jul 9, 2026 8:58pm | Jul 9, 2026 10:21pm | Jul 9, 2026 10:40pm | Jul 9, 2026 10:40pm | Jul 9, 2026 10:43pm | Jul 9, 2026 11:03pm | Jul 9, 2026 11:07pm | Jul 9, 2026 11:07pm |  |  | Rains | No | Patrol and found junction blown at Lignum Vitae. avenue 10amp renew
Outage | J.E.26.07.09897 | C001845089 | Michael Christian | St.James | Completed | Load_557019 | Bogue - 310 | Jul 9, 2026 8:53pm | Jul 9, 2026 8:53pm | Jul 9, 2026 9:41pm | Jul 9, 2026 9:41pm | Jul 9, 2026 10:43pm | Jul 9, 2026 11:04pm | Jul 9, 2026 11:04pm | Jul 9, 2026 11:04pm |  |  | Fair | No | Premises not found
Outage | J.E.26.07.10118 | C001845088 | Andre Williams | Trelawny | Completed | Load_1001526 | Duncans - 110 | Jul 9, 2026 8:52pm | Jul 9, 2026 8:53pm | Jul 9, 2026 9:03pm | Jul 9, 2026 9:51pm | Jul 9, 2026 10:32pm | Jul 9, 2026 10:33pm | Jul 9, 2026 10:33pm | Jul 9, 2026 10:33pm |  |  | Rains | No | Premises ok and with supply confirm by call power was restored earlier in the day
Outage | J.E.26.07.10103 | C001845087 | Omar King | St.Ann | Completed | Load_252531 | Ocho Rios - 310 | Jul 9, 2026 8:48pm | Jul 10, 2026 7:22am | Jul 10, 2026 7:53am | Jul 10, 2026 7:53am | Jul 10, 2026 8:23am | Jul 10, 2026 8:24am | Jul 10, 2026 8:25am | Jul 10, 2026 8:25am | BrokenWire |  | Fair | No | Problem as been resolved customer is with supply
Non-Outage | J.E.26.07.10065 | C001845083 | Hopeton Henry | St.Thomas | Completed | Load_239900 | Good Year - 210 | Jul 9, 2026 8:35pm | Jul 9, 2026 8:37pm | Jul 9, 2026 8:55pm | Jul 9, 2026 10:09pm | Jul 9, 2026 10:27pm | Jul 9, 2026 10:32pm | Jul 9, 2026 10:33pm | Jul 9, 2026 10:33pm |  |  | Rains | No | On and off supply dus to circling feeder
Outage | J.E.26.07.10050 | C001845077 | Lancelot Brown | Hanover | Completed | Load_1001380 | Orange Bay - 310 | Jul 9, 2026 8:13pm | Jul 9, 2026 8:13pm | Jul 9, 2026 9:31pm | Jul 9, 2026 9:57pm | Jul 9, 2026 9:57pm | Jul 9, 2026 9:58pm | Jul 9, 2026 9:59pm | Jul 9, 2026 9:59pm |  |  | Fair | No | Check and found ok customer said supply went but it came back
Outage | J.E.26.07.10039 | C001845076 | Oshane Warren | Westmoreland | Completed | Load_267905 | Paradise - 210 | Jul 9, 2026 8:04pm | Jul 9, 2026 8:04pm | Jul 9, 2026 11:35pm | Jul 9, 2026 11:35pm | Jul 9, 2026 11:35pm | Jul 9, 2026 11:35pm | Jul 9, 2026 11:36pm | Jul 9, 2026 11:36pm |  |  | Rains | No | Need daylight attention to carry out repair
Outage | J.E.26.07.10075 | C001845075 | Daniel Francis | St.Ann | Completed | null | null | Jul 9, 2026 8:03pm | Jul 9, 2026 8:04pm | Jul 9, 2026 8:59pm | Jul 9, 2026 9:15pm | Jul 9, 2026 9:15pm | Jul 9, 2026 9:16pm | Jul 9, 2026 9:19pm | Jul 9, 2026 9:19pm |  |  | Rains | No | Found defective 50kva transformer at pole#0121213
Outage | J.E.26.07.09661 | C001845074 | Daniel Francis | St.Ann | Completed | Load_254491 | Roaring River - 410 | Jul 9, 2026 8:00pm | Jul 9, 2026 8:00pm | Jul 9, 2026 9:22pm | Jul 9, 2026 9:22pm | Jul 9, 2026 9:23pm | Jul 9, 2026 9:24pm | Jul 9, 2026 9:26pm | Jul 9, 2026 9:26pm |  |  | Rains | No | Change one 30 fuse no pole #
Outage | J.E.26.07.09913 | C001845073 | Gregory Grossett | Portland | Completed | Load_247607 | Port Antonio - 410 | Jul 9, 2026 7:52pm | Jul 9, 2026 7:53pm | Jul 9, 2026 8:40pm | Jul 9, 2026 8:40pm | Jul 9, 2026 8:40pm | Jul 9, 2026 8:44pm | Jul 9, 2026 8:45pm | Jul 9, 2026 8:45pm |  |  | SevereWind | No | 1 of 2-20amp junction fuse blown cause by heavy rain and lightning in area patrol line section then restore to the area.Material use 20amps fuse 2amp fuse
Outage | J.E.26.07.10056 | C001845070 | Christopher Edwards | KSAN | Completed | Load_567714 | Washington Blvd - 310 | Jul 9, 2026 7:51pm | Jul 9, 2026 8:34pm | Jul 9, 2026 10:27pm | Jul 9, 2026 10:28pm | Jul 9, 2026 10:34pm | Jul 9, 2026 11:23pm | Jul 9, 2026 11:44pm | Jul 9, 2026 11:44pm |  |  | Fair | No | Check and found okSupply is in the area
Outage | J.E.26.07.10057 | C001845072 | Milton Charlton | KSAN | Completed | Load_258947 | Washington Blvd - 510 | Jul 9, 2026 7:51pm | Jul 9, 2026 7:55pm | Jul 9, 2026 8:02pm | Jul 9, 2026 8:23pm | Jul 9, 2026 8:29pm | Jul 9, 2026 8:30pm | Jul 9, 2026 8:42pm | Jul 9, 2026 8:42pm |  |  | Fair | No | Found one 30 amps junction fuse at pole #( no pole#). Refused using one 30 amps fuse and reclosed junction switch.
Non-Outage | J.E.26.07.10055 | C001845069 | Hopeton Henry | St.Thomas | Completed | Load_266155 | Good Year - 210 | Jul 9, 2026 7:50pm | Jul 9, 2026 7:50pm | Jul 9, 2026 8:25pm | Jul 9, 2026 8:25pm | Jul 9, 2026 8:57pm | Jul 9, 2026 8:57pm | Jul 9, 2026 8:58pm | Jul 9, 2026 8:58pm |  |  | Rains | No | Feeder circling causing on and off supply
Outage | J.E.26.07.10053 | C001845068 | Hopeton Henry | St.Thomas | Completed | Load_238731 | Good Year - 210 | Jul 9, 2026 7:50pm | Jul 9, 2026 7:50pm | Jul 9, 2026 8:55pm | Jul 9, 2026 8:59pm | Jul 9, 2026 9:26pm | Jul 9, 2026 10:08pm | Jul 9, 2026 10:09pm | Jul 9, 2026 10:09pm | Fire |  | Rains | No | No spark seen
Outage | J.E.26.07.09987 | C001845062 | Horace Malcolm | St.James | Completed | Load_269145 | Queens Drive - 710 | Jul 9, 2026 7:36pm | Jul 9, 2026 7:37pm | Jul 9, 2026 9:09pm | Jul 9, 2026 9:10pm | Jul 9, 2026 10:14pm | Jul 9, 2026 10:28pm | Jul 9, 2026 10:29pm | Jul 9, 2026 10:29pm |  |  | Fair | No | Refused one 50kva transformer due to banging wires transformer switch top burn out switch need replacement
Outage | J.E.26.07.10008 | C001845061 | Clyde Brown | Clarendon | Completed | Load_245804 | May Pen - 110 | Jul 9, 2026 7:33pm | Jul 9, 2026 7:34pm | Jul 9, 2026 10:34pm | Jul 9, 2026 10:34pm | Jul 9, 2026 10:34pm | Jul 9, 2026 10:28pm | Jul 9, 2026 10:37pm | Jul 9, 2026 10:37pm | Fire |  | Fair | No | Blown 3 amps fuse for 25 kva transformer caused by broken phase conductor same repaired with 7ft-#2/0,2-preform,2-clamp and blown fuse replaced.
Outage | J.E.26.07.09965 | C001845060 | Horace Malcolm | St.James | Completed | Load_263606 | Queens Drive - 310 | Jul 9, 2026 7:31pm | Jul 9, 2026 7:47pm | Jul 9, 2026 9:09pm | Jul 9, 2026 9:09pm | Jul 9, 2026 9:09pm | Jul 9, 2026 9:10pm | Jul 9, 2026 9:10pm | Jul 9, 2026 9:10pm |  |  | Fair | No | Related to previous call job number 10005
Outage | J.E.26.07.10005 | C001845059 | Horace Malcolm | St.James | Completed | Load_248780 | Queens Drive - 310 | Jul 9, 2026 7:31pm | Jul 9, 2026 7:46pm | Jul 9, 2026 8:38pm | Jul 9, 2026 8:38pm | Jul 9, 2026 8:40pm | Jul 9, 2026 8:46pm | Jul 9, 2026 8:46pm | Jul 9, 2026 8:46pm |  |  | Fair | No | Refused one 15amp junction fuse
Outage | J.E.26.07.09969 | C001845058 | Roxroy Needham | St.Ann | Completed | Load_259557 | Cardiff Hall - 210 | Jul 9, 2026 7:30pm | Jul 9, 2026 7:30pm | Jul 9, 2026 8:29pm | Jul 9, 2026 8:29pm | Jul 9, 2026 8:29pm | Jul 9, 2026 8:31pm | Jul 9, 2026 8:31pm | Jul 9, 2026 8:31pm |  |  | Fair | No | Call customer and customer say light is back
Outage | J.E.26.07.10007 | C001845057 | Raymond Carr | St.Ann | Completed | Load_412802 | Upper White River - 210 | Jul 9, 2026 7:30pm | Jul 10, 2026 8:44am | Jul 10, 2026 10:05am | Jul 10, 2026 10:05am | Jul 10, 2026 10:23am | Jul 10, 2026 10:40am | Jul 10, 2026 10:49am | Jul 10, 2026 10:49am |  |  | Fair | No | Blown junction fuse found at pole number 0013713, line patrol and found okay, lightening was suspected. A 10 amp fuse was used to renew supply was restored.
Outage | J.E.26.07.09967 | C001845053 | Richard Samuda | Manchester | Completed | Load_303059 | Kendal - 210 | Jul 9, 2026 7:23pm | Jul 9, 2026 7:25pm | Jul 9, 2026 9:42pm | Jul 9, 2026 9:46pm | Jul 9, 2026 10:25pm | Jul 9, 2026 10:25pm | Jul 9, 2026 10:25pm | Jul 9, 2026 10:25pm |  |  | Fair | No | Customer back to normal
Outage | J.E.26.07.09977 | C001845054 | Richard Samuda | Manchester | Completed | Load_241796 | Kendal - 210 | Jul 9, 2026 7:23pm | Jul 9, 2026 7:25pm | Jul 9, 2026 8:13pm | Jul 9, 2026 8:13pm | Jul 9, 2026 9:21pm | Jul 9, 2026 9:21pm | Jul 9, 2026 9:40pm | Jul 9, 2026 9:40pm |  |  | Fair | No | Customer had a trip breaker voltage
Outage | J.E.26.07.10015 | C001845055 | Kenroy Dale | Manchester | Completed | Load_256540 | Porus - 310 | Jul 9, 2026 7:23pm | Jul 9, 2026 7:24pm | Jul 10, 2026 8:40am | Jul 10, 2026 10:42am | Jul 10, 2026 10:42am | Jul 10, 2026 10:43am | Jul 10, 2026 10:43am | Jul 10, 2026 10:43am |  |  | Fair | No | Call related to defective 10 kva transformer
Outage | J.E.26.07.10016 | C001845052 | Milton Charlton | KSAN | Completed | Load_1000589 | Washington Blvd - 510 | Jul 9, 2026 7:22pm | Jul 9, 2026 7:24pm | Jul 9, 2026 8:42pm | Jul 9, 2026 8:42pm | Jul 9, 2026 9:30pm | Jul 9, 2026 9:35pm | Jul 9, 2026 9:34pm | Jul 9, 2026 9:34pm |  |  | Rains | No | Reconnect about 25 customers by J.P.S. Escalation. And a lot more is still without power escalation states the rest of to call customer care.
Outage | J.E.26.07.10012 | C001845050 | Milton Charlton | KSAN | Completed | Load_242285 | Washington Blvd - 510 | Jul 9, 2026 7:20pm | Jul 9, 2026 7:24pm | Jul 9, 2026 9:34pm | Jul 9, 2026 9:34pm | Jul 10, 2026 9:02am | Jul 9, 2026 9:35pm | Jul 10, 2026 9:06am | Jul 10, 2026 9:06am |  |  | Fair | No | Found okay upon y. Matter was resolved.
Outage | J.E.26.07.09843 | C001845048 | Michael Christian | St.James | Completed | Load_259739 | Bogue - 310 | Jul 9, 2026 7:16pm | Jul 9, 2026 7:16pm | Jul 9, 2026 9:36pm | Jul 9, 2026 9:36pm | Jul 9, 2026 9:40pm | Jul 9, 2026 9:41pm | Jul 9, 2026 9:41pm | Jul 9, 2026 9:41pm |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.08676 | C001845045 | Lloyd Lugg | St.Ann | Completed | Load_262327 | Cardiff Hall - 310 | Jul 9, 2026 7:14pm | Jul 9, 2026 7:14pm | Jul 9, 2026 9:32pm | Jul 9, 2026 9:32pm | Jul 9, 2026 9:32pm | Jul 9, 2026 9:33pm | Jul 9, 2026 9:33pm | Jul 9, 2026 9:33pm |  |  | Rains | No | Area found with supply..... customer said power was restored earlier
Outage | J.E.26.07.09070 | C001845046 | Lloyd Lugg | St.Ann | Completed | Load_246197 | Roaring River - 210 | Jul 9, 2026 7:14pm | Jul 9, 2026 7:14pm | Jul 9, 2026 8:19pm | Jul 9, 2026 8:19pm | Jul 9, 2026 9:03pm | Jul 9, 2026 9:04pm | Jul 9, 2026 9:04pm | Jul 9, 2026 9:04pm |  |  | Rains | No | Area found with supply..... customer said power was restored earlier
Outage | J.E.26.07.09742 | C001845044 | Lloyd Lugg | St.Ann | Completed | Load_262327 | Cardiff Hall - 310 | Jul 9, 2026 7:14pm | Jul 9, 2026 7:15pm | Jul 9, 2026 9:10pm | Jul 9, 2026 9:15pm | Jul 9, 2026 9:15pm | Jul 9, 2026 9:15pm | Jul 9, 2026 9:16pm | Jul 9, 2026 9:16pm |  |  | Rains | No | Area found with supply..... customer said power was restored earlier
Outage | J.E.26.07.09811 | C001845047 | Michael Christian | St.James | Completed | Load_240626 | Bogue - 310 | Jul 9, 2026 7:14pm | Jul 9, 2026 7:14pm | Jul 9, 2026 9:01pm | Jul 9, 2026 9:01pm | Jul 9, 2026 9:31pm | Jul 9, 2026 9:36pm | Jul 9, 2026 9:36pm | Jul 9, 2026 9:36pm |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.07.09899 | C001845042 | Romeo Brissett | St.James | Completed | Load_240799 | Bogue - 510 | Jul 9, 2026 7:04pm | Jul 9, 2026 7:05pm | Jul 9, 2026 8:41pm | Jul 9, 2026 8:41pm | Jul 9, 2026 8:41pm | Jul 9, 2026 7:14pm | Jul 9, 2026 8:44pm | Jul 9, 2026 8:44pm |  |  | Fair | No | Check and found internal fault V/R at Breaker point 115-121-212-236-237-244
Outage | J.E.26.07.08805 | C001845040 | Evan Spaulding | St.Mary | Completed | Load_265280 | Highgate - 210 | Jul 9, 2026 7:03pm | Jul 10, 2026 7:50am | Jul 10, 2026 12:52pm | Jul 10, 2026 12:52pm | Jul 10, 2026 12:52pm | Jul 10, 2026 12:53pm | Jul 10, 2026 12:53pm | Jul 10, 2026 12:53pm |  |  | SevereWind | No | Associated call
Outage | J.E.26.07.08836 | C001845041 | Evan Spaulding | St.Mary | Completed | Load_260746 | Highgate - 210 | Jul 9, 2026 7:03pm | Jul 10, 2026 7:49am | Jul 10, 2026 12:51pm | Jul 10, 2026 12:51pm | Jul 10, 2026 12:51pm | Jul 10, 2026 12:51pm | Jul 10, 2026 12:52pm | Jul 10, 2026 12:52pm |  |  | SevereWind | No | Associated call
Outage | J.E.26.07.09992 | C001845039 | Oshane Warren | Hanover | Completed | Load_248706 | Orange Bay - 310 | Jul 9, 2026 7:02pm | Jul 9, 2026 7:03pm | Jul 9, 2026 8:36pm | Jul 9, 2026 8:36pm | Jul 9, 2026 11:21pm | Jul 9, 2026 11:24pm | Jul 9, 2026 11:25pm | Jul 9, 2026 11:25pm | BrokenWire |  | Rains | No | Open 25kva xformer and splice and retention one spand of secondary conductor
Outage | J.E.26.07.09910 | C001845035 | Edward Royal | KSAS | Completed | Load_293431 | Hunts Bay - 810 | Jul 9, 2026 6:49pm | Jul 10, 2026 8:15am | Jul 10, 2026 11:00am | Jul 10, 2026 11:00am | Jul 10, 2026 11:00am | Jul 10, 2026 11:01am | Jul 10, 2026 11:02am | Jul 10, 2026 11:02am |  |  | Fair | No | Call related to outage
Outage | J.E.26.07.08771 | C001845033 | Raymond Lewis | St.Ann | Completed | Load_268753 | Ocho Rios - 310 | Jul 9, 2026 6:42pm | Jul 9, 2026 6:43pm | Jul 9, 2026 8:12pm | Jul 9, 2026 8:12pm | Jul 9, 2026 8:15pm | Jul 9, 2026 8:16pm | Jul 9, 2026 8:16pm | Jul 9, 2026 8:16pm |  |  | Fair | No | Phone not working
Outage | J.E.26.07.09737 | C001845032 | Daniel Francis | St.Ann | Completed | Load_261043 | Roaring River - 410 | Jul 9, 2026 6:39pm | Jul 9, 2026 6:39pm | Jul 9, 2026 6:47pm | Jul 9, 2026 6:47pm | Jul 9, 2026 6:55pm | Jul 9, 2026 7:08pm | Jul 9, 2026 7:10pm | Jul 9, 2026 7:10pm |  |  | Fair | No | Change one 30amp fuse no pole #
Outage | J.E.26.07.09930 | C001845031 | Andrew Powell | Manchester | Completed | Load_302904 | Spur Tree - 210 | Jul 9, 2026 6:33pm | Jul 9, 2026 6:55pm | Jul 9, 2026 8:12pm | Jul 9, 2026 8:12pm | Jul 9, 2026 8:49pm | Jul 9, 2026 10:03pm | Jul 9, 2026 10:05pm | Jul 9, 2026 10:05pm | BrokenWire |  | Fair | No | Remade burnt off phase joints inside PMC box #0073 using two service sleeves, voltage reading 112v-112v phase to neutral 224v cross phase.
Outage | J.E.26.07.09964 | C001845030 | Andrew Powell | Manchester | Completed | Load_257702 | Spur Tree - 210 | Jul 9, 2026 6:32pm | Jul 9, 2026 6:40pm | Jul 9, 2026 6:52pm | Jul 9, 2026 6:58pm | Jul 9, 2026 7:47pm | Jul 9, 2026 8:08pm | Jul 9, 2026 8:10pm | Jul 9, 2026 8:10pm | BrokenWire |  | Fair | No | Remade corroded service wire joints at secondary line 3 wire using three clamps, voltage reading 113v-115v phase to neutral 228v cross phase.
Outage | J.E.26.07.09943 | C001845026 | Roxroy Needham | St.Ann | Completed | Load_248462 | Cardiff Hall - 210 | Jul 9, 2026 6:23pm | Jul 9, 2026 6:24pm | Jul 9, 2026 7:00pm | Jul 9, 2026 8:32pm | Jul 9, 2026 9:28pm | Jul 9, 2026 10:21pm | Jul 9, 2026 10:23pm | Jul 9, 2026 10:23pm |  |  | Fair | No | Remake joint at pole used 1 pg clamp
Outage | J.E.26.07.09036 | C001845022 | Omar King | St.Ann | Completed | Load_261002 | Ocho Rios - 510 | Jul 9, 2026 6:19pm | Jul 9, 2026 6:19pm | Jul 9, 2026 7:06pm | Jul 9, 2026 7:06pm | Jul 9, 2026 7:36pm | Jul 9, 2026 7:55pm | Jul 9, 2026 7:55pm | Jul 9, 2026 7:55pm |  |  | Fair | No | Problem as been resolved customer
Non-Outage | J.E.26.07.09260 | C001845019 | Roxroy Needham | null | Completed | null | null | Jul 9, 2026 6:18pm | Jul 9, 2026 6:18pm | Jul 9, 2026 8:31pm | Jul 9, 2026 8:31pm | Jul 9, 2026 8:31pm | Jul 9, 2026 8:32pm | Jul 9, 2026 8:32pm | Jul 9, 2026 8:32pm |  |  | Fair | No | Call customer and customer say light is back
Outage | J.E.26.07.09127 | C001845021 | Roxroy Needham | St.Ann | Completed | Load_263361 | Cardiff Hall - 310 | Jul 9, 2026 6:18pm | Jul 9, 2026 6:19pm | Jul 9, 2026 7:04pm | Jul 9, 2026 8:25pm | Jul 9, 2026 8:26pm | Jul 9, 2026 8:26pm | Jul 9, 2026 8:26pm | Jul 9, 2026 8:26pm |  |  | Fair | No | Call customer and customer say light is back
Outage | J.E.26.07.09953 | C001845020 | Christopher Edwards | KSAS | Completed | Load_293827 | Greenwich - 710 | Jul 9, 2026 6:18pm | Jul 9, 2026 6:24pm | Jul 9, 2026 8:42pm | Jul 9, 2026 8:42pm | Jul 9, 2026 9:05pm | Jul 9, 2026 10:25pm | Jul 9, 2026 10:27pm | Jul 9, 2026 10:27pm |  |  | Fair | No | Required field service Rami box # 01988 is having issues
Non-Outage | J.E.26.07.09348 | C001845018 | Roxroy Needham | null | Completed | null | null | Jul 9, 2026 6:17pm | Jul 9, 2026 6:17pm | Jul 9, 2026 7:02pm | Jul 9, 2026 10:24pm | Jul 9, 2026 10:24pm | Jul 9, 2026 10:42pm | Jul 10, 2026 3:31pm | Jul 10, 2026 3:31pm |  |  | Fair | No | Remake service wire used 5 ft of # 6 service wire
Outage | J.E.26.07.09706 | C001845014 | Omar King | St.Ann | Completed | Load_258422 | Ocho Rios - 310 | Jul 9, 2026 6:16pm | Jul 9, 2026 6:16pm | Jul 9, 2026 8:08pm | Jul 9, 2026 8:08pm | Jul 9, 2026 8:28pm | Jul 9, 2026 8:31pm | Jul 9, 2026 8:32pm | Jul 9, 2026 8:32pm | BrokenWire |  | Rains | No | After visiting location a voltage reading as been taken. Reading show 116-116-232 Volts premises found ok
Outage | J.E.26.07.09834 | C001845012 | Daniel Francis | St.Ann | Completed | Load_256557 | Cardiff Hall - 310 | Jul 9, 2026 6:13pm | Jul 9, 2026 6:14pm | Jul 9, 2026 10:23pm | Jul 9, 2026 10:23pm | Jul 9, 2026 10:28pm | Jul 9, 2026 10:29pm | Jul 9, 2026 10:32pm | Jul 9, 2026 10:32pm |  |  | Rains | No | Costumer not answering phone
Outage | J.E.26.07.09829 | C001845011 | Roxroy Needham | St.Ann | Completed | Load_245873 | Cardiff Hall - 210 | Jul 9, 2026 6:11pm | Jul 9, 2026 6:11pm | Jul 9, 2026 7:03pm | Jul 9, 2026 8:24pm | Jul 9, 2026 8:24pm | Jul 9, 2026 8:25pm | Jul 9, 2026 8:25pm | Jul 9, 2026 8:25pm |  |  | Fair | No | Found premises ok
Outage | J.E.26.07.09862 | C001845010 | Omar King | St.Ann | Completed | Load_240065 | Ocho Rios - 510 | Jul 9, 2026 6:10pm | Jul 9, 2026 6:11pm | Jul 9, 2026 7:56pm | Jul 9, 2026 7:56pm | Jul 9, 2026 7:57pm | Jul 9, 2026 8:08pm | Jul 9, 2026 8:08pm | Jul 9, 2026 8:08pm |  |  | Fair | No | Found 25 amp junction fuse blow cause by lightning fuse as replace area is now with supply
Non-Outage | J.E.26.07.09822 | C001845005 | Ricky Hall | null | Completed | null | null | Jul 9, 2026 6:03pm | Jul 9, 2026 6:05pm | Jul 9, 2026 6:46pm | Jul 9, 2026 7:23pm | Jul 9, 2026 7:23pm | Jul 9, 2026 7:23pm | Jul 9, 2026 8:12pm | Jul 9, 2026 8:12pm | BrokenPole |  | Fair | No | Isolate defective line section due to broken 40’c6 TDEwr pole replaced blown 30 amps junction fuse
Non-Outage | J.E.26.07.09925 | C001845006 | Ricky Hall | null | Completed | null | null | Jul 9, 2026 6:03pm | Jul 9, 2026 6:05pm | Jul 9, 2026 6:45pm | Jul 9, 2026 6:45pm | Jul 9, 2026 6:46pm | Jul 9, 2026 7:16pm | Jul 9, 2026 7:23pm | Jul 9, 2026 7:23pm | BrokenPole |  | Fair | No | Broken 40’c4 pole TDE w/r presently blocking rdwy need assistance of crane truck to facilitate clearance line section confirmed insulated plz refer to maintenance ( material needed for repairs (1)8’ cross arm6 D/E polymer 6 D/E clamp
Outage | J.E.26.07.09824 | C001845008 | Clyde Brown | Clarendon | Completed | Load_256737 | May Pen - 110 | Jul 9, 2026 6:03pm | Jul 9, 2026 6:03pm | Jul 9, 2026 7:52pm | Jul 9, 2026 7:52pm | Jul 9, 2026 10:14pm | Jul 9, 2026 10:28pm | Jul 9, 2026 10:34pm | Jul 9, 2026 10:34pm | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Illegal connection caused secondary phase to be broken and blown 3 amps fuse for 25 kva transformer used 7ft-#2/0 conductor,2-clamp and 2preform and blown fuse replaced.
Outage | J.E.26.07.09855 | C001845007 | Jermaine Williams | St.Catherine | Completed | Load_255385 | Rhodens Pen - 310 | Jul 9, 2026 6:03pm | Jul 9, 2026 6:04pm | Jul 9, 2026 8:55pm | Jul 9, 2026 8:55pm | Jul 9, 2026 10:02pm | Jul 9, 2026 10:31pm | Jul 9, 2026 10:32pm | Jul 9, 2026 10:32pm |  | Y | SevereWind | No | Patrol secondary cct and replaced blown 25kva 5amp xfmr fuse. Extensive bushing required on line section.
Outage | J.E.26.07.09674 | C001845003 | Raymond Lewis | St.Ann | Completed | Load_242451 | Ocho Rios - 310 | Jul 9, 2026 6:02pm | Jul 9, 2026 6:03pm | Jul 9, 2026 6:25pm | Jul 9, 2026 6:25pm | Jul 9, 2026 7:39pm | Jul 9, 2026 8:09pm | Jul 9, 2026 8:10pm | Jul 9, 2026 8:10pm |  |  | SevereWind | No | Remade joint at pothead 3 wire service
Outage | J.E.26.07.09835 | C001845004 | Nickolas Rodriques | St.Catherine | Completed | Load_248390 | Twickenham - 310 | Jul 9, 2026 6:02pm | Jul 9, 2026 6:35pm | Jul 9, 2026 6:43pm | Jul 9, 2026 7:18pm | Jul 9, 2026 8:03pm | Jul 9, 2026 8:36pm | Jul 9, 2026 8:53pm | Jul 9, 2026 8:53pm | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Checked and found two 30 amp junction fuses blown caused by truck contact with guy wire. The guy wire was cleared accordingly and the fuses were replaced after completing patrol in order to restore supply.
Outage | J.E.26.07.09926 | C001844999 | Edward Royal | KSAS | Completed | Load_251395 | Duhaney - 310 | Jul 9, 2026 5:51pm | Jul 10, 2026 4:50am | Jul 10, 2026 6:06am | Jul 10, 2026 6:06am | Jul 10, 2026 6:06am | Jul 10, 2026 6:09am | Jul 10, 2026 6:09am | Jul 10, 2026 6:09am | BrokenWire |  | Fair | No | Premises not found unable to communicate with customer
Outage | J.E.26.07.09266 | C001844994 | Richman Whyte | Westmoreland | Completed | Load_259377 | Paradise - 310 | Jul 9, 2026 5:33pm | Jul 9, 2026 5:35pm | Jul 9, 2026 7:37pm | Jul 9, 2026 7:37pm | Jul 9, 2026 7:37pm | Jul 9, 2026 7:37pm | Jul 9, 2026 7:38pm | Jul 9, 2026 7:38pm |  |  | Fair | No | Customer stated that power was restored from last night
Non-Outage | J.E.26.07.09892 | C001844993 | Eric Williams | KSAN | Completed | Load_245677 | West Kings House - 210 | Jul 9, 2026 5:31pm | Jul 9, 2026 5:31pm | Jul 9, 2026 6:33pm | Jul 9, 2026 6:33pm | Jul 9, 2026 7:14pm | Jul 9, 2026 9:02pm | Jul 9, 2026 9:05pm | Jul 9, 2026 9:05pm |  |  | Fair | No | 4 wire service, corroded transformer droplead, used 8feet 2/0 copper and 4 onebolt clamps
Outage | J.E.26.07.08767 | C001844991 | Romeo Brissett | St.James | Completed | Load_263300 | Bogue - 610 | Jul 9, 2026 5:30pm | Jul 9, 2026 5:37pm | Jul 9, 2026 6:48pm | Jul 9, 2026 6:48pm | Jul 9, 2026 6:48pm | Jul 9, 2026 6:49pm | Jul 9, 2026 6:50pm | Jul 9, 2026 6:50pm |  |  | Fair | No | Issue is resolved, customer stated power restored. Related to job#08907.
Outage | J.E.26.07.09876 | C001844989 | Selvin White | St.Elizabeth | Completed | Load_570258 | Maggotty - 110 | Jul 9, 2026 5:24pm | Jul 9, 2026 5:26pm | Jul 9, 2026 6:53pm | Jul 9, 2026 7:07pm | Jul 9, 2026 7:38pm | Jul 9, 2026 7:58pm | Jul 9, 2026 7:58pm | Jul 9, 2026 7:58pm | BrokenWire |  | Fair | No | Remade broken off connections at secondary for customer’s service phases conductors that was damaged during the hurricane. Supply restored to the affected customer. Voltage readings found at customer pothead are 221, 110,111 volts. Meter socket was found barrel locked.
Outage | J.E.26.07.09870 | C001844977 | Andre Williams | Trelawny | Completed | Load_239166 | Duncans - 110 | Jul 9, 2026 5:11pm | Jul 9, 2026 5:12pm | Jul 9, 2026 5:16pm | Jul 9, 2026 5:55pm | Jul 9, 2026 5:55pm | Jul 9, 2026 6:06pm | Jul 9, 2026 6:06pm | Jul 9, 2026 6:06pm | BrokenWire |  | Fair | No | Remake burnt off joint on customer #6 wire service at Jps pole voltage 113+115=228
Outage | J.E.26.07.08954 | C001844975 | Cliton Henry | St.Mary | Completed | Load_245290 | Blackstonedge - 110 | Jul 9, 2026 5:03pm | Jul 9, 2026 5:03pm | Jul 9, 2026 5:15pm | Jul 9, 2026 5:16pm | Jul 9, 2026 5:51pm | Jul 9, 2026 6:25pm | Jul 9, 2026 6:29pm | Jul 9, 2026 6:29pm |  |  | Fair | No | The supply found ok, the voltages at the metering point were 117-117/234 volts. The customer was advised to get a licensed electrician to change the meter socket,
Outage | J.E.26.07.09688 | C001844976 | Cliton Henry | St.Mary | Completed | Load_256631 | Blackstonedge - 110 | Jul 9, 2026 5:03pm | Jul 9, 2026 5:03pm | Jul 9, 2026 6:32pm | Jul 9, 2026 6:32pm | Jul 9, 2026 7:20pm | Jul 9, 2026 9:04pm | Jul 9, 2026 9:04pm | Jul 9, 2026 9:04pm | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | A blown 7 amp junction fuse at Rock Spring due to a broken single phase primary conductor caused by a fallen tree. Corrective work done to cut and remove tree from the primary line, spliced and retention primary conductor using approximately 20 #2 AA conductor, 2 s2 preform and 2 one bolt clamp. Supply restored using 1-7 amp fuse
Outage | J.E.26.07.09440 | C001844971 | Milton Charlton | KSAN | Completed | Load_270241 | Washington Blvd - 410 | Jul 9, 2026 4:54pm | Jul 9, 2026 6:33pm | Jul 9, 2026 7:25pm | Jul 9, 2026 7:28pm | Jul 9, 2026 7:28pm | Jul 9, 2026 7:45pm | Jul 9, 2026 7:59pm | Jul 9, 2026 7:59pm |  |  | Fair | No | Found okay upon arrival. Customer has an internal problem.
Outage | J.E.26.07.09562 | C001844970 | Eric Williams | KSAN | Completed | Load_265029 | Washington Blvd - 810 | Jul 9, 2026 4:53pm | Jul 9, 2026 5:00pm | Jul 9, 2026 9:33pm | Jul 9, 2026 9:33pm | Jul 9, 2026 9:36pm | Jul 9, 2026 9:37pm | Jul 9, 2026 9:38pm | Jul 9, 2026 9:38pm |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.09707 | C001844969 | Eric Williams | KSAN | Completed | Load_260304 | Washington Blvd - 810 | Jul 9, 2026 4:53pm | Jul 9, 2026 5:00pm | Jul 9, 2026 9:05pm | Jul 9, 2026 9:05pm | Jul 9, 2026 9:30pm | Jul 9, 2026 9:32pm | Jul 9, 2026 9:33pm | Jul 9, 2026 9:33pm |  |  | Fair | No | Premises found okay,
Outage | J.E.26.07.09848 | C001844966 | Lancelot Brown | Hanover | Completed | Load_292101 | Orange Bay - 310 | Jul 9, 2026 4:52pm | Jul 9, 2026 4:53pm | Jul 9, 2026 5:39pm | Jul 9, 2026 6:11pm | Jul 9, 2026 7:03pm | Jul 9, 2026 7:05pm | Jul 9, 2026 7:05pm | Jul 9, 2026 7:05pm |  |  | Fair | No | Check and found area ok customer said supply went and it restore
Outage | J.E.26.07.09830 | C001844964 | Raymond Carr | St.Ann | Completed | Load_244643 | Upper White River - 210 | Jul 9, 2026 4:51pm | Jul 9, 2026 4:52pm | Jul 9, 2026 4:59pm | Jul 9, 2026 4:59pm | Jul 9, 2026 4:59pm | Jul 9, 2026 5:34am | Jul 9, 2026 5:37pm | Jul 9, 2026 5:37pm |  |  | Fair | No | Blown junction fuse found at pole number 0013685, line patrol and found okay, however lightening was suspected. A 25 amp fuse was used to renew supply was restored.
Outage | J.E.26.07.09844 | C001844965 | Andre Williams | Trelawny | Completed | Load_250518 | Duncans - 110 | Jul 9, 2026 4:51pm | Jul 9, 2026 4:53pm | Jul 9, 2026 6:06pm | Jul 9, 2026 6:06pm | Jul 9, 2026 6:40pm | Jul 9, 2026 6:43pm | Jul 9, 2026 6:44pm | Jul 9, 2026 6:44pm |  |  | Fair | No | Patrol secondary re fuse and close close 4 amp on 50 kva transformer
Outage | J.E.26.07.09812 | C001844960 | Kenroy Dale | Manchester | Completed | Load_269775 | Porus - 310 | Jul 9, 2026 4:46pm | Jul 9, 2026 4:47pm | Jul 10, 2026 10:34am | Jul 10, 2026 10:44am | Jul 10, 2026 12:04pm | Jul 10, 2026 12:30pm | Jul 10, 2026 12:32pm | Jul 10, 2026 12:32pm |  |  | Fair | No | Effort to contact customer was unsuccessful however area checked and found with supply
Outage | J.E.26.07.09819 | C001844961 | Kenroy Dale | Manchester | Completed | Load_256540 | Porus - 310 | Jul 9, 2026 4:46pm | Jul 9, 2026 4:47pm | Jul 10, 2026 8:38am | Jul 10, 2026 10:39am | Jul 10, 2026 10:39am | Jul 10, 2026 10:41am | Jul 10, 2026 10:42am | Jul 10, 2026 10:42am |  |  | Fair | No | Call related to defective 10 kva transformer
Outage | J.E.26.07.09771 | C001844958 | Lancelot Brown | Hanover | Completed | Load_256837 | Orange Bay - 210 | Jul 9, 2026 4:43pm | Jul 9, 2026 5:10pm | Jul 9, 2026 5:39pm | Jul 9, 2026 6:10pm | Jul 9, 2026 6:10pm | Jul 9, 2026 6:10pm | Jul 9, 2026 6:11pm | Jul 9, 2026 6:11pm |  |  | Rains | No | Check and found ok customer said supply restore
Outage | J.E.26.07.09827 | C001844959 | Dean Smith | Hanover | Completed | Load_261296 | Orange Bay - 310 | Jul 9, 2026 4:43pm | Jul 9, 2026 5:10pm | Jul 9, 2026 5:22pm | Jul 9, 2026 5:22pm | Jul 9, 2026 6:22pm | Jul 9, 2026 7:58pm | Jul 9, 2026 7:59pm | Jul 9, 2026 7:59pm |  |  | Rains | No | Replace 1amp 10kva transformer fuse. Pole number n/a
Outage | J.E.26.07.09266 | C001844957 | Romeo Brissett | Westmoreland | Completed | Load_259377 | Paradise - 310 | Jul 9, 2026 4:42pm | Jul 9, 2026 4:42pm | Jul 9, 2026 5:34pm | Jul 9, 2026 5:34pm | Jul 9, 2026 5:34pm | Jul 9, 2026 5:28pm | Jul 9, 2026 5:34pm | Jul 9, 2026 5:34pm |  |  | Fair | No | Westmoreland call
Outage | J.E.26.07.09810 | C001844954 | Selvin White | St.Elizabeth | Completed | Load_292412 | Maggotty - 210 | Jul 9, 2026 4:38pm | Jul 9, 2026 4:54pm | Jul 9, 2026 5:49pm | Jul 9, 2026 5:49pm | Jul 9, 2026 6:07pm | Jul 9, 2026 6:50pm | Jul 9, 2026 6:53pm | Jul 9, 2026 6:53pm |  |  | Fair | No | Replace approximately 60 ft of number six triplex service wire that was damaged and removed after the hurricane. Supply restored with voltage readings of 225, 112,113 volts left inside customer’s meter socket.
Outage | J.E.26.07.09823 | C001844953 | Richman Whyte | St.Elizabeth | Completed | Load_269458 | Maggotty - 110 | Jul 9, 2026 4:37pm | Jul 9, 2026 4:39pm | Jul 9, 2026 6:28pm | Jul 9, 2026 6:28pm | Jul 9, 2026 6:28pm | Jul 9, 2026 6:49pm | Jul 9, 2026 6:51pm | Jul 9, 2026 6:51pm |  |  | Fair | No | Connect back customer after hurricane use 100 feet #6 triplex and 6 one bolt clamps voltage 115 116 232
Outage | J.E.26.07.09815 | C001844948 | Richman Whyte | Westmoreland | Completed | Load_245482 | Paradise - 310 | Jul 9, 2026 4:32pm | Jul 9, 2026 4:36pm | Jul 9, 2026 5:35pm | Jul 9, 2026 5:35pm | Jul 9, 2026 5:35pm | Jul 9, 2026 5:36pm | Jul 9, 2026 5:37pm | Jul 9, 2026 5:37pm |  |  | Fair | No | Customer is reporting street light not working
Outage | J.E.26.07.09820 | C001844949 | Oshane Warren | Westmoreland | Completed | Load_238357 | Paradise - 210 | Jul 9, 2026 4:32pm | Jul 9, 2026 4:36pm | Jul 9, 2026 6:39pm | Jul 9, 2026 6:39pm | Jul 9, 2026 6:39pm | Jul 9, 2026 6:49pm | Jul 9, 2026 6:56pm | Jul 9, 2026 6:56pm |  |  | Rains | No | Replace two 10amps junction fuse
Outage | J.E.26.07.09516 | C001844938 | Romaine Roberts | St.Mary | Completed | Load_238502 | Highgate -110 | Jul 9, 2026 4:26pm | Jul 10, 2026 7:38am | Jul 10, 2026 10:58am | Jul 10, 2026 4:47pm | Jul 10, 2026 4:47pm | Jul 10, 2026 4:48pm | Jul 10, 2026 4:49pm | Jul 10, 2026 4:49pm |  |  | Fair | No | Found ok power was restore
Outage | J.E.26.07.09556 | C001844926 | Richman Whyte | Westmoreland | Completed | Load_239292 | Paradise - 310 | Jul 9, 2026 4:19pm | Jul 9, 2026 4:23pm | Jul 9, 2026 5:42pm | Jul 9, 2026 5:42pm | Jul 9, 2026 6:25pm | Jul 9, 2026 6:25pm | Jul 9, 2026 6:27pm | Jul 9, 2026 6:27pm |  |  | Fair | No | Due to the length of wire Mr Richard advise to refer back to field service about 200 feet of wire it’s a wide read way
Outage | J.E.26.07.09768 | C001844925 | Oshane Warren | Hanover | Completed | Load_245791 | Orange Bay - 310 | Jul 9, 2026 4:19pm | Jul 9, 2026 4:34pm | Jul 9, 2026 5:06pm | Jul 9, 2026 5:06pm | Jul 9, 2026 5:06pm | Jul 9, 2026 5:07pm | Jul 9, 2026 5:07pm | Jul 9, 2026 5:07pm |  |  | Fair | No | Check and find ok
Outage | J.E.26.07.09793 | C001844924 | Oshane Warren | Westmoreland | Completed | Load_242476 | Paradise - 210 | Jul 9, 2026 4:19pm | Jul 9, 2026 4:24pm | Jul 9, 2026 5:08pm | Jul 9, 2026 5:09pm | Jul 9, 2026 6:33pm | Jul 9, 2026 6:38pm | Jul 9, 2026 6:39pm | Jul 9, 2026 6:39pm | BrokenWire |  | Fair | No | Replace 15 amps junction fuse and replace 3amps xformer fuse
Outage | J.E.26.07.07763 | C001844919 | Romaine Roberts | St.Mary | Completed | Load_262607 | Annotto Bay - 310 | Jul 9, 2026 4:15pm | Jul 9, 2026 4:16pm | Jul 9, 2026 6:54pm | Jul 9, 2026 6:54pm | Jul 9, 2026 8:11pm | Jul 9, 2026 8:50pm | Jul 9, 2026 8:57pm | Jul 9, 2026 8:57pm |  | Y | Fair | No | Tree lim fall on primary line and blow junction fuse patrol and clear lim from line and replace 30 amp and 40 amp junction to restore supply
Outage | J.E.26.07.09502 | C001844915 | Romaine Roberts | St.Mary | Completed | Load_249878 | Annotto Bay - 310 | Jul 9, 2026 4:15pm | Jul 9, 2026 4:16pm | Jul 9, 2026 4:49pm | Jul 9, 2026 4:49pm | Jul 9, 2026 5:40pm | Jul 9, 2026 6:54pm | Jul 9, 2026 6:54pm | Jul 9, 2026 6:54pm |  |  | Fair | No | After carrying out several checks found burnt clamp at pole on customer service main clean and remake joints
Outage | J.E.26.07.08728 | C001844909 | Neckell Ormsby | St.Mary | Completed | Load_268580 | Highgate - 210 | Jul 9, 2026 4:13pm | Jul 9, 2026 4:14pm | Jul 9, 2026 6:16pm | Jul 9, 2026 6:16pm | Jul 9, 2026 7:01pm | Jul 9, 2026 7:07pm | Jul 9, 2026 7:08pm | Jul 9, 2026 7:08pm |  |  | Rains | No | Found junction fuse blown at pole number 138766 patrol and found broken primary conductor in cross country location requires bushing and additional assistance due to conductor goes across river please refer to maintenance department
Outage | J.E.26.07.08926 | C001844911 | Neckell Ormsby | St.Mary | Completed | Load_243069 | Highgate - 210 | Jul 9, 2026 4:13pm | Jul 9, 2026 4:14pm | Jul 9, 2026 9:40pm | Jul 9, 2026 9:40pm | Jul 9, 2026 9:40pm | Jul 9, 2026 9:41pm | Jul 9, 2026 9:41pm | Jul 9, 2026 9:41pm |  |  | Rains | No | Found blown fuse for transformer unable to see size, patrol and found 2- pole span broken secondary phase and neutral (heavy rain in area) splice and retention conductors using approximately 50 ft #2 AA ,2-# sleeves and 3- one bolt clamps voltage left 119v 119v 238v
Outage | J.E.26.07.09485 | C001844908 | Neckell Ormsby | St.Mary | Completed | Load_240575 | Highgate - 210 | Jul 9, 2026 4:13pm | Jul 9, 2026 4:14pm | Jul 9, 2026 9:41pm | Jul 9, 2026 9:41pm | Jul 9, 2026 9:41pm | Jul 9, 2026 9:42pm | Jul 9, 2026 9:42pm | Jul 9, 2026 9:42pm | BrokenWire |  | Rains | No | Found blown fuse for transformer unable to see size, patrol and found 2- pole span broken secondary phase and neutral (heavy rain in area) splice and retention conductors using approximately 50 ft #2 AA ,2-# sleeves and 3- one bolt clamps voltage left 119v 119v 238v
Non-Outage | J.E.26.07.08000 | C001844903 | Wayne Dillion | null | Completed | null | null | Jul 9, 2026 4:10pm | Jul 9, 2026 4:11pm | Jul 9, 2026 6:56pm | Jul 9, 2026 6:56pm | Jul 9, 2026 7:08pm | Jul 9, 2026 7:10pm | Jul 9, 2026 7:10pm | Jul 9, 2026 7:10pm | BrokenWire |  | Fair | No | Patrol and found no outage in area and no broken wire.
Outage | J.E.26.07.09574 | C001844902 | Daniel Francis | St.Ann | Completed | Load_262500 | Roaring River - 210 | Jul 9, 2026 4:08pm | Jul 9, 2026 4:08pm | Jul 9, 2026 9:27pm | Jul 9, 2026 9:27pm | Jul 9, 2026 10:03pm | Jul 9, 2026 10:04pm | Jul 9, 2026 10:05pm | Jul 9, 2026 10:05pm |  |  | Rains | No | Power restored
Outage | J.E.26.07.09625 | C001844901 | Milton Charlton | KSAN | Completed | Load_258637 | Constant Spring - 210 | Jul 9, 2026 4:07pm | Jul 9, 2026 4:09pm | Jul 9, 2026 4:30pm | Jul 9, 2026 5:01pm | Jul 9, 2026 5:53pm | Jul 9, 2026 6:25pm | Jul 9, 2026 6:26pm | Jul 9, 2026 6:26pm |  |  | Fair | No | Customer service wire #6 triplex phase corroded at pole. Repair using one 1- bolt clamp.
Outage | J.E.26.07.09097 | C001844900 | Horace Malcolm | St.James | Completed | Load_240761 | Rose Hall - 210 | Jul 9, 2026 4:06pm | Jul 9, 2026 5:35pm | Jul 9, 2026 6:16pm | Jul 9, 2026 6:16pm | Jul 9, 2026 6:16pm | Jul 9, 2026 7:28pm | Jul 9, 2026 7:29pm | Jul 9, 2026 7:29pm |  |  | Fair | No | Splice and retention one pole span secondary neutral use one #2 preform one clamp and refuse two 30amp junction fuse (the three phase line section going up towards sugar mill road need retention line saggy
Outage | J.E.26.07.09216 | C001844891 | Daniel Francis | St.Ann | Completed | Load_247617 | Roaring River - 210 | Jul 9, 2026 4:06pm | Jul 9, 2026 4:06pm | Jul 9, 2026 11:18pm | Jul 9, 2026 11:18pm | Jul 10, 2026 12:15am | Jul 10, 2026 12:16am | Jul 10, 2026 12:17am | Jul 10, 2026 12:17am |  |  | Rains | No | Power restored earlier Thursday
Outage | J.E.26.07.08642 | C001844890 | Gregory Grossett | Portland | Completed | Load_1003532 | Port Antonio - 410 | Jul 9, 2026 4:05pm | Jul 9, 2026 4:05pm | Jul 9, 2026 7:23pm | Jul 9, 2026 7:23pm | Jul 9, 2026 7:23pm | Jul 9, 2026 7:24pm | Jul 9, 2026 7:24pm | Jul 9, 2026 7:24pm |  |  | Rains | No | 20amp junction fuse blown patrol line section then restore supply to the area suspected cause heavy rain and high wind.
Outage | J.E.26.07.09488 | C001844889 | Omar King | St.Ann | Completed | Load_574409 | Roaring River - 210 | Jul 9, 2026 4:04pm | Jul 9, 2026 4:05pm | Jul 9, 2026 4:43pm | Jul 9, 2026 4:43pm | Jul 9, 2026 5:14pm | Jul 9, 2026 5:15pm | Jul 9, 2026 5:16pm | Jul 9, 2026 5:16pm |  |  | Fair | No | Found 25 amp junction fuse blow cause by lightning fuse as been replaced area is now with supply
Non-Outage | J.E.26.07.09748 | C001844888 | Christopher Edwards | null | Completed | null | null | Jul 9, 2026 4:03pm | Jul 9, 2026 4:03pm | Jul 9, 2026 7:49pm | Jul 9, 2026 7:49pm | Jul 9, 2026 7:49pm | Jul 9, 2026 8:39pm | Jul 9, 2026 8:41pm | Jul 9, 2026 8:41pm | Fire |  | Fair | No | Isolate 50 kva transformer Splice and retention broken open secondary phaseUsing:40ft #2AA conductor (1) # preform(2) one bolt clamps
Non-Outage | J.E.26.07.08697 | C001844884 | Hopeton Henry | null | Completed | null | null | Jul 9, 2026 4:02pm | Jul 9, 2026 4:03pm | Jul 9, 2026 6:04pm | Jul 9, 2026 7:36pm | Jul 9, 2026 7:36pm | Jul 9, 2026 7:50pm | Jul 9, 2026 7:51pm | Jul 9, 2026 7:51pm |  |  | Fair | No | Check and found ok
Outage | J.E.26.07.08663 | C001844886 | Hopeton Henry | St.Thomas | Completed | Load_577138 | Lysson - 410 | Jul 9, 2026 4:02pm | Jul 9, 2026 4:03pm | Jul 9, 2026 6:04pm | Jul 9, 2026 6:31pm | Jul 9, 2026 6:31pm | Jul 9, 2026 7:33pm | Jul 9, 2026 7:35pm | Jul 9, 2026 7:35pm |  |  | Fair | No | Reconnect service at pole and pot head , 119-120-240 volts
Outage | J.E.26.07.09164 | C001844885 | Hopeton Henry | St.Thomas | Completed | Load_577233 | Good Year - 210 | Jul 9, 2026 4:02pm | Jul 9, 2026 4:03pm | Jul 9, 2026 6:04pm | Jul 9, 2026 7:35pm | Jul 9, 2026 7:35pm | Jul 9, 2026 7:35pm | Jul 9, 2026 7:36pm | Jul 9, 2026 7:36pm |  |  | Fair | No | Area found ok
Outage | J.E.26.07.09369 | C001844887 | Richard Samuda | Manchester | Completed | Load_302243 | Spur Tree - 310 | Jul 9, 2026 4:02pm | Jul 9, 2026 4:45pm | Jul 9, 2026 5:58pm | Jul 9, 2026 5:59pm | Jul 9, 2026 5:59pm | Jul 9, 2026 6:06pm | Jul 9, 2026 6:08pm | Jul 9, 2026 6:08pm | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Carry out spot bushing in area and balance line area needs extensive bushing refer call
Non-Outage | J.E.26.07.09628 | C001844883 | Hopeton Henry | null | Completed | null | null | Jul 9, 2026 4:01pm | Jul 9, 2026 4:03pm | Jul 9, 2026 6:04pm | Jul 9, 2026 7:51pm | Jul 9, 2026 8:23pm | Jul 9, 2026 8:23pm | Jul 9, 2026 8:25pm | Jul 9, 2026 8:25pm |  |  | Rains | No | Found disconnected for nonpayment
Outage | J.E.26.07.08595 | C001844875 | Richard Samuda | Manchester | Completed | Load_246581 | Spur Tree - 310 | Jul 9, 2026 4:00pm | Jul 9, 2026 4:45pm | Jul 9, 2026 7:11pm | Jul 9, 2026 7:11pm | Jul 9, 2026 7:11pm | Jul 9, 2026 7:11pm | Jul 9, 2026 8:06pm | Jul 9, 2026 8:06pm | BrokenWire |  | Fair | No | Splice and reconnect customer service wire using 30ft of#6service wire voltage 118/120/238 but meter is defective 0 consumption since 2023 refer
Outage | J.E.26.07.09505 | C001844874 | Raymond Lewis | St.Ann | Completed | Load_263102 | Roaring River - 210 | Jul 9, 2026 4:00pm | Jul 9, 2026 6:03pm | Jul 9, 2026 6:13pm | Jul 9, 2026 6:13pm | Jul 9, 2026 6:13pm | Jul 9, 2026 6:24pm | Jul 9, 2026 6:24pm | Jul 9, 2026 6:24pm |  |  | Fair | No | Refuse and close 20amp junction
Outage | J.E.26.07.09577 | C001844872 | Daniel Francis | St.Ann | Completed | Load_295224 | Roaring River - 210 | Jul 9, 2026 4:00pm | Jul 9, 2026 4:02pm | Jul 9, 2026 5:32pm | Jul 9, 2026 5:32pm | Jul 9, 2026 6:11pm | Jul 9, 2026 6:21pm | Jul 9, 2026 6:23pm | Jul 9, 2026 6:23pm |  |  | Fair | No | Change one 10am fuse no pole #
Outage | J.E.26.07.08575 | C001844871 | Donald Cunningham | St.Catherine | Completed | Load_250553 | Tredegar - 410 | Jul 9, 2026 3:59pm | Jul 9, 2026 4:00pm | Jul 9, 2026 8:21pm | Jul 9, 2026 8:25pm | Jul 9, 2026 9:50pm | Jul 9, 2026 9:59pm | Jul 9, 2026 10:00pm | Jul 9, 2026 10:00pm |  |  | Fair | No | Premises closed
Outage | J.E.26.07.08664 | C001844867 | Donald Cunningham | St.Catherine | Completed | Load_243118 | Rhodens Pen - 410 | Jul 9, 2026 3:59pm | Jul 9, 2026 4:00pm | Jul 9, 2026 5:11pm | Jul 9, 2026 5:11pm | Jul 9, 2026 6:15pm | Jul 9, 2026 6:17pm | Jul 9, 2026 6:23pm | Jul 9, 2026 6:23pm |  |  | Fair | No | No response from customer more directions required
Outage | J.E.26.07.08844 | C001844870 | Donald Cunningham | St.Catherine | Completed | Load_257526 | Tredegar - 210 | Jul 9, 2026 3:59pm | Jul 9, 2026 4:00pm | Jul 9, 2026 10:01pm | Jul 9, 2026 10:01pm | Jul 9, 2026 10:35pm | Jul 9, 2026 10:43pm | Jul 9, 2026 10:49pm | Jul 9, 2026 10:49pm |  |  | Fair | No | Customer service was disconnected but supply is restored
Outage | J.E.26.07.08927 | C001844868 | Donald Cunningham | St.Catherine | Completed | Load_239310 | Rhodens Pen - 210 | Jul 9, 2026 3:59pm | Jul 9, 2026 4:00pm | Jul 9, 2026 6:24pm | Jul 9, 2026 6:24pm | Jul 9, 2026 8:09pm | Jul 9, 2026 8:11pm | Jul 9, 2026 8:20pm | Jul 9, 2026 8:20pm |  |  | Fair | No | Broken 30 class 6 secondary pole need to replace cause by motor vehicle accident
Outage | J.E.26.07.09696 | C001844865 | Donald Cunningham | St.Catherine | Completed | Load_239309 | Rhodens Pen - 410 | Jul 9, 2026 3:59pm | Jul 9, 2026 4:00pm | Jul 9, 2026 4:17pm | Jul 9, 2026 4:17pm | Jul 9, 2026 5:05pm | Jul 9, 2026 5:05pm | Jul 9, 2026 5:09pm | Jul 9, 2026 5:09pm | Fire |  | Fair | No | Need more directions customer not reachable
Outage | J.E.26.07.09183 | C001844860 | Barnett Brown | Manchester | Completed | Load_265494 | Spur Tree - 310 | Jul 9, 2026 3:58pm | Jul 9, 2026 3:59pm | Jul 9, 2026 9:02pm | Jul 9, 2026 9:02pm | Jul 9, 2026 9:02pm | Jul 9, 2026 9:02pm | Jul 9, 2026 9:05pm | Jul 9, 2026 9:05pm |  |  | Fair | No | Related to Wood Lawn call where 10 amp fuse was replaced
Outage | J.E.26.07.09618 | C001844862 | Christopher Edwards | KSAS | Completed | Load_244305 | Greenwich - 710 | Jul 9, 2026 3:58pm | Jul 9, 2026 4:00pm | Jul 9, 2026 5:50pm | Jul 9, 2026 5:50pm | Jul 9, 2026 6:02pm | Jul 9, 2026 6:24pm | Jul 9, 2026 6:25pm | Jul 9, 2026 6:25pm |  |  | Fair | No | Reset 100 kva transformer
Outage | J.E.26.07.09642 | C001844863 | Edward Royal | KSAS | Completed | Load_575430 | Greenwich - 710 | Jul 9, 2026 3:58pm | Jul 10, 2026 8:15am | Jul 10, 2026 9:33am | Jul 10, 2026 9:33am | Jul 10, 2026 9:33am | Jul 10, 2026 9:33am | Jul 10, 2026 9:33am | Jul 10, 2026 9:33am |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.07.09689 | C001844861 | Eric Williams | KSAS | Completed | Load_247678 | Duhaney - 410 | Jul 9, 2026 3:58pm | Jul 9, 2026 3:59pm | Jul 9, 2026 4:59pm | Jul 9, 2026 4:59pm | Jul 9, 2026 5:10pm | Jul 9, 2026 6:29pm | Jul 9, 2026 6:33pm | Jul 9, 2026 6:33pm | BrokenWire |  | Fair | No | Broken primary conductor and 2 25amps blown junction fuse and 1 15amps transformer fuse, wire cut and splice using 2 onebolt clamps and 2 25amps fuse, 1 15amps fuse
Non-Outage | J.E.26.07.09362 | C001844857 | Collin Robinson | null | Completed | null | null | Jul 9, 2026 3:57pm | Jul 9, 2026 3:58pm | Jul 9, 2026 7:36pm | Jul 9, 2026 7:36pm | Jul 9, 2026 8:21pm | Jul 9, 2026 8:23pm | Jul 9, 2026 8:23pm | Jul 9, 2026 8:23pm | TreeContact |  | Rains | No | Information received from customer that issue was resolved
Non-Outage | J.E.26.07.09443 | C001844855 | Collin Robinson | null | Completed | null | null | Jul 9, 2026 3:57pm | Jul 9, 2026 3:58pm | Jul 9, 2026 4:45pm | Jul 9, 2026 4:46pm | Jul 9, 2026 6:00pm | Jul 9, 2026 6:12pm | Jul 9, 2026 6:13pm | Jul 9, 2026 6:13pm |  |  | Rains | No | Replace 3 amps fuse at pole 557026
Non-Outage | J.E.26.07.09531 | C001844854 | Collin Robinson | null | Completed | null | null | Jul 9, 2026 3:57pm | Jul 9, 2026 3:58pm | Jul 9, 2026 7:03pm | Jul 9, 2026 7:03pm | Jul 9, 2026 7:04pm | Jul 9, 2026 7:08pm | Jul 9, 2026 7:08pm | Jul 9, 2026 7:08pm |  |  | Rains | No | Information received from customer that supply was restored
Non-Outage | J.E.26.07.09582 | C001844848 | Christopher Edwards | null | Completed | null | null | Jul 9, 2026 3:57pm | Jul 9, 2026 3:59pm | Jul 9, 2026 6:28pm | Jul 9, 2026 6:28pm | Jul 9, 2026 6:43pm | Jul 9, 2026 6:44pm | Jul 9, 2026 6:45pm | Jul 9, 2026 6:45pm | LeakingTransformer |  | Fair | No | Check and found okIssue was already resolved
Outage | J.E.26.07.07376 | C001844859 | Barnett Brown | Manchester | Completed | Load_245137 | Spur Tree - 310 | Jul 9, 2026 3:57pm | Jul 9, 2026 3:59pm | Jul 9, 2026 6:09pm | Jul 9, 2026 6:09pm | Jul 9, 2026 7:02pm | Jul 9, 2026 7:07pm | Jul 9, 2026 7:11pm | Jul 9, 2026 7:11pm | BrokenPole |  | Fair | No | 40 class 4 TA with return, 3phase is rotten at root but was treated and stubbed.
Outage | J.E.26.07.08549 | C001844856 | Barnett Brown | Manchester | Completed | Load_251145 | Spur Tree - 310 | Jul 9, 2026 3:57pm | Jul 9, 2026 3:59pm | Jul 9, 2026 6:03pm | Jul 9, 2026 6:03pm | Jul 9, 2026 6:03pm | Jul 9, 2026 6:04pm | Jul 9, 2026 6:06pm | Jul 9, 2026 6:06pm |  |  | Fair | No | Related to previous Manings field call where secondary line was retention and fuse and fuse holder were replaced
Outage | J.E.26.07.08725 | C001844852 | Collin Robinson | Portland | Completed | Load_245297 | Port Antonio - 410 | Jul 9, 2026 3:57pm | Jul 9, 2026 3:58pm | Jul 9, 2026 6:16pm | Jul 9, 2026 6:16pm | Jul 9, 2026 6:49pm | Jul 9, 2026 6:56pm | Jul 9, 2026 6:56pm | Jul 9, 2026 6:56pm |  |  | Rains | No | Entangle open secondary conductor and replace 2 amps fuse no pole number at location
Outage | J.E.26.07.09439 | C001844851 | Collin Robinson | Portland | Completed | Load_242277 | Port Antonio - 410 | Jul 9, 2026 3:57pm | Jul 9, 2026 3:58pm | Jul 9, 2026 8:23pm | Jul 9, 2026 8:23pm | Jul 9, 2026 8:50pm | Jul 9, 2026 8:55pm | Jul 9, 2026 8:55pm | Jul 9, 2026 8:55pm |  |  | Rains | No | Premises found with supply Meter socket voltage reading 118v 117v 235v
Outage | J.E.26.07.09461 | C001844853 | Collin Robinson | Portland | Completed | Load_353584 | Port Antonio - 310 | Jul 9, 2026 3:57pm | Jul 9, 2026 3:58pm | Jul 9, 2026 9:03pm | Jul 9, 2026 9:03pm | Jul 9, 2026 10:18pm | Jul 9, 2026 10:20pm | Jul 9, 2026 10:48pm | Jul 9, 2026 10:48pm |  |  | Rains | No | Replace 15 amps junction fuse
Outage | J.E.26.07.08893 | C001844841 | Gregory Grossett | Portland | Completed | Load_239589 | Port Antonio - 410 | Jul 9, 2026 3:53pm | Jul 9, 2026 3:55pm | Jul 9, 2026 7:25pm | Jul 9, 2026 7:25pm | Jul 9, 2026 8:20pm | Jul 9, 2026 8:40pm | Jul 9, 2026 8:40pm | Jul 9, 2026 8:40pm |  |  | SevereWind | No | 1 of 2-20amps junction fuse blown and a transformer fuse cause by heavy rain and lightning in area patrol line section then restore supply to area.Material use 20amps fuse 2amps fuse.
Outage | J.E.26.07.09159 | C001844840 | Gregory Grossett | Portland | Completed | Load_248851 | Port Antonio - 410 | Jul 9, 2026 3:53pm | Jul 9, 2026 3:55pm | Jul 9, 2026 5:49pm | Jul 9, 2026 5:49pm | Jul 9, 2026 5:54pm | Jul 9, 2026 6:06pm | Jul 9, 2026 6:07pm | Jul 9, 2026 6:07pm |  |  | Fair | No | Customer meter socket is defective we advise customer to get on certified electrician to change meter socket.Voltage reading 114/111/228 on both phase.
Outage | J.E.26.07.09224 | C001844839 | Gregory Grossett | Portland | Completed | Load_260238 | Port Antonio - 410 | Jul 9, 2026 3:53pm | Jul 9, 2026 3:55pm | Jul 9, 2026 6:07pm | Jul 9, 2026 6:07pm | Jul 9, 2026 7:17pm | Jul 9, 2026 7:21pm | Jul 9, 2026 7:22pm | Jul 9, 2026 7:22pm |  |  | Rains | No | 20amp junction fuse blown patrol line section then restore supply to the area suspected cause heavy rain and high wind.
Outage | J.E.26.07.09356 | C001844838 | Gregory Grossett | Portland | Completed | Load_349214 | Port Antonio - 410 | Jul 9, 2026 3:53pm | Jul 9, 2026 3:55pm | Jul 9, 2026 8:47pm | Jul 9, 2026 8:47pm | Jul 9, 2026 8:52pm | Jul 9, 2026 9:04pm | Jul 9, 2026 9:04pm | Jul 9, 2026 9:04pm |  |  | SevereWind | No | Heavy rain and lightning in area needs daylight attention to carry out work.
Outage | J.E.26.07.09507 | C001844837 | Gregory Grossett | Portland | Completed | Load_256491 | Port Antonio - 410 | Jul 9, 2026 3:53pm | Jul 9, 2026 3:55pm | Jul 9, 2026 9:04pm | Jul 9, 2026 9:04pm | Jul 9, 2026 9:12pm | Jul 9, 2026 10:04pm | Jul 9, 2026 10:05pm | Jul 9, 2026 10:05pm |  |  | Rains | No | Check and found ok at meter socket however customer has internal issue we advise customer to get on certified electrician and make checks voltage reading at meter socket 112/114/226 on both phase.
Non-Outage | J.E.26.07.09458 | C001844824 | Barnett Brown | null | Completed | null | null | Jul 9, 2026 3:51pm | Jul 9, 2026 3:55pm | Jul 9, 2026 9:22pm | Jul 9, 2026 9:22pm | Jul 9, 2026 10:55pm | Jul 10, 2026 11:20pm | Jul 10, 2026 1:00am | Jul 10, 2026 1:00am | Fire |  | Fair | No | Premises not found, direction not clear, customer not answering phone
Outage | J.E.26.07.09355 | C001844822 | Barnett Brown | Manchester | Completed | Load_256785 | Spur Tree - 310 | Jul 9, 2026 3:50pm | Jul 9, 2026 3:54pm | Jul 9, 2026 7:13pm | Jul 9, 2026 7:13pm | Jul 9, 2026 8:14pm | Jul 9, 2026 8:54pm | Jul 9, 2026 8:59pm | Jul 9, 2026 8:59pm |  |  | Fair | No | Patrol line found nothing, replace blown 10 amp junction fuse
Outage | J.E.26.07.09103 | C001844819 | Shamour Haughton | St.James | Completed | Load_243105 | Queens Drive - 710 | Jul 9, 2026 3:49pm | Jul 9, 2026 3:49pm | Jul 9, 2026 4:00pm | Jul 9, 2026 4:05pm | Jul 9, 2026 4:51pm | Jul 9, 2026 5:39pm | Jul 9, 2026 5:44pm | Jul 9, 2026 5:44pm | BrokenWire | Y | Fair | No | Found 3,25amp tripsaver down, caused by tree falling on primary, remove tree limb from primary and reclose 3,25amp tripsaver at pole number 586204
Non-Outage | J.E.26.06.32171 | C001844814 | Rodclif Dawkins | Portmore | Completed | Load_252357 | Naggo Head - 510 | Jul 9, 2026 3:46pm | Jul 9, 2026 3:47pm | Jul 9, 2026 6:13pm | Jul 9, 2026 7:06pm | Jul 9, 2026 7:14pm | Jul 9, 2026 7:31pm | Jul 9, 2026 7:35pm | Jul 9, 2026 7:35pm |  |  | Fair | No | At location crew observed other customers experiencing the same problem, which led to crew doing checks at 25kva transformer. Crew observed x3 to lower phase of open secondary joint with burnt marks. 25kva transformer was de-energized. All three joints were changed us in ampact. Transformer energized and voltage reading collected at open secondary joint with. 121*2v,241v . Area okay
Outage | J.E.26.07.08797 | C001844807 | Kenroy Dale | Manchester | Completed | Load_266332 | Porus - 310 | Jul 9, 2026 3:44pm | Jul 9, 2026 3:44pm | Jul 9, 2026 8:32pm | Jul 10, 2026 8:40am | Jul 10, 2026 8:40am | Jul 10, 2026 9:32am | Jul 10, 2026 9:42am | Jul 10, 2026 9:42am |  |  | Fair | No | Defective 10 kva transformer found, transformer was isolated and approximately 10-15 customers are affected (circuit was unable to tie in) transformer need to be replaced
Outage | J.E.26.07.08917 | C001844810 | Raymond Carr | St.Mary | Completed | Load_246515 | Oracabessa - 210 | Jul 9, 2026 3:44pm | Jul 9, 2026 3:44pm | Jul 9, 2026 7:26pm | Jul 9, 2026 7:26pm | Jul 9, 2026 7:35pm | Jul 9, 2026 7:49pm | Jul 9, 2026 7:59pm | Jul 9, 2026 7:59pm | LeakingTransformer |  | Rains | No | Blown junction fuse found, line patrol and found okay, however lightening was suspected. A 15 amp fuse was used to renew supply was restored.
Outage | J.E.26.07.09317 | C001844809 | Raymond Carr | St.Mary | Completed | Load_252304 | Oracabessa - 210 | Jul 9, 2026 3:44pm | Jul 9, 2026 3:44pm | Jul 9, 2026 7:59pm | Jul 9, 2026 7:59pm | Jul 9, 2026 8:00pm | Jul 9, 2026 7:54pm | Jul 9, 2026 8:01pm | Jul 9, 2026 8:01pm |  |  | Rains | No | Supply was restored . Related to ocean ridge.
Outage | J.E.26.07.09381 | C001844808 | Raymond Carr | St.Mary | Completed | Load_253185 | Oracabessa - 210 | Jul 9, 2026 3:44pm | Jul 9, 2026 3:44pm | Jul 9, 2026 5:40pm | Jul 9, 2026 5:40pm | Jul 9, 2026 5:40pm | Jul 9, 2026 5:39pm | Jul 9, 2026 5:42pm | Jul 9, 2026 5:42pm |  |  | Fair | No | Customer made request for new installation.
Outage | J.E.26.07.09739 | C001844811 | Omar King | St.Ann | Completed | Load_269255 | Upper White River - 210 | Jul 9, 2026 3:44pm | Jul 9, 2026 3:44pm | Jul 9, 2026 5:21pm | Jul 9, 2026 5:21pm | Jul 9, 2026 5:21pm | Jul 9, 2026 5:23pm | Jul 9, 2026 5:23pm | Jul 9, 2026 5:23pm |  |  | Fair | No | Related to middle street outage that as been resolved
Outage | J.E.26.07.08816 | C001844804 | Kenroy Dale | Manchester | Completed | Load_242004 | Porus - 310 | Jul 9, 2026 3:43pm | Jul 9, 2026 3:44pm | Jul 9, 2026 3:56pm | Jul 9, 2026 4:10pm | Jul 9, 2026 5:23pm | Jul 9, 2026 10:46pm | Jul 9, 2026 11:03pm | Jul 9, 2026 11:03pm | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Blow 10 amp and 3 amp transformer fuse found line patrol 2 different span of secondary neutral and two span of phase found broken conductors was splice and retention, blown 10 amp junction fuse was replaced and 90% of customer now with supply. The other 10% which is about 8-10 customers remain out of supply due to defective switch, please refer to daylight attention to replace switch safely
Outage | J.E.26.07.09583 | C001844805 | Raymond Carr | St.Mary | Completed | Load_257590 | Oracabessa - 210 | Jul 9, 2026 3:43pm | Jul 10, 2026 7:37am | Jul 10, 2026 2:00pm | Jul 10, 2026 2:00pm | Jul 10, 2026 2:26pm | Jul 10, 2026 2:40am | Jul 10, 2026 2:42pm | Jul 10, 2026 2:42pm | BrokenWire |  | Fair | No | Line broken service wire was disconnected, also customer was advised to repair pothead and stanchion.
Outage | J.E.26.07.09602 | C001844803 | Jermaine Williams | Clarendon | Completed | Load_1002788 | Monymusk - 410 | Jul 9, 2026 3:43pm | Jul 9, 2026 3:44pm | Jul 9, 2026 5:12pm | Jul 9, 2026 5:12pm | Jul 9, 2026 6:09pm | Jul 9, 2026 6:31pm | Jul 9, 2026 6:32pm | Jul 9, 2026 6:32pm | BrokenWire |  | SevereWind | No | Splice and retention broken service wire.
Outage | J.E.26.07.09631 | C001844806 | Raymond Carr | St.Mary | Completed | Load_266413 | Oracabessa - 210 | Jul 9, 2026 3:43pm | Jul 9, 2026 3:44pm | Jul 9, 2026 5:47pm | Jul 9, 2026 5:47pm | Jul 9, 2026 6:06pm | Jul 9, 2026 7:27pm | Jul 9, 2026 7:25pm | Jul 9, 2026 7:25pm |  |  | Fair | No | Blown junction 0012884, line patrol and okay, however a 25 kva transformer fuse found blown also. A 15 amp & 3 amp fuse were used to energize line , also several bushes were removed from transformer pole.
Outage | J.E.26.07.09698 | C001844802 | Jermaine Williams | Clarendon | Completed | Load_249523 | May Pen - 210 | Jul 9, 2026 3:43pm | Jul 9, 2026 3:44pm | Jul 9, 2026 6:33pm | Jul 9, 2026 6:33pm | Jul 9, 2026 8:37pm | Jul 9, 2026 8:06pm | Jul 9, 2026 8:39pm | Jul 9, 2026 8:39pm | BrokenWire |  | SevereWind | No | Splice and retention broken service wires using 60’ #6 triplex.
Outage | J.E.26.07.09662 | C001844801 | Barnett Brown | Manchester | Completed | Load_251145 | Spur Tree - 310 | Jul 9, 2026 3:42pm | Jul 9, 2026 3:45pm | Jul 9, 2026 3:51pm | Jul 9, 2026 3:51pm | Jul 9, 2026 5:11pm | Jul 9, 2026 5:58pm | Jul 9, 2026 6:02pm | Jul 9, 2026 6:02pm |  |  | Fair | No | Retention secondary neutral, replace blown 3 amp transformer fuse and fuse holder
Outage | J.E.26.07.09668 | C001844800 | Barnett Brown | Manchester | Completed | Load_256785 | Spur Tree - 310 | Jul 9, 2026 3:42pm | Jul 9, 2026 3:45pm | Jul 9, 2026 9:06pm | Jul 9, 2026 9:08pm | Jul 9, 2026 9:08pm | Jul 9, 2026 9:09pm | Jul 9, 2026 9:21pm | Jul 9, 2026 9:21pm | Fire |  | Fair | No | Related to Wood Lawn call where 10 amp fuse was replaced
Outage | J.E.26.07.08593 | C001844789 | Clyde Brown | Clarendon | Completed | Load_257707 | May Pen - 110 | Jul 9, 2026 3:41pm | Jul 9, 2026 3:41pm | Jul 9, 2026 5:25pm | Jul 9, 2026 5:25pm | Jul 9, 2026 6:54pm | Jul 9, 2026 6:54pm | Jul 9, 2026 7:04pm | Jul 9, 2026 7:04pm | BrokenWire |  | Fair | No | Broken secondary neutral,open 25 kva transformer and repaired with 6ft-#2 conductor,2-splicing sleeve,1-preform and 1- clamp.
Outage | J.E.26.07.07990 | C001844787 | Christopher Edwards | KSAS | Completed | Load_262511 | Three Miles - 410 | Jul 9, 2026 3:40pm | Jul 9, 2026 3:46pm | Jul 9, 2026 3:50pm | Jul 9, 2026 3:57pm | Jul 9, 2026 3:57pm | Jul 9, 2026 5:47pm | Jul 9, 2026 5:50pm | Jul 9, 2026 5:50pm |  |  | Fair | No | Isolate 2 phase primary junction fuse’To disconnect burnt rami box switch Refuse blown 15 amps transformer Using (2) 2 amps
Outage | J.E.26.07.08999 | C001844786 | Daniel Francis | St.Ann | Completed | Load_242133 | Roaring River - 410 | Jul 9, 2026 3:40pm | Jul 9, 2026 6:38pm | Jul 9, 2026 7:10pm | Jul 9, 2026 7:10pm | Jul 9, 2026 7:16pm | Jul 9, 2026 7:35pm | Jul 9, 2026 7:35pm | Jul 9, 2026 7:35pm |  |  | Fair | No | Change one 10amp fuse no pole #
Outage | J.E.26.07.09112 | C001844785 | Roxroy Needham | St.Ann | Completed | Load_264468 | Roaring River - 410 | Jul 9, 2026 3:39pm | Jul 9, 2026 3:39pm | Jul 9, 2026 3:51pm | Jul 9, 2026 3:55pm | Jul 9, 2026 4:54pm | Jul 9, 2026 4:51pm | Jul 9, 2026 4:55pm | Jul 9, 2026 4:55pm |  |  | Fair | No | Replace a 20 amps junction fuse at pole
Outage | J.E.26.07.09566 | C001844784 | Lancelot Brown | Hanover | Completed | Load_258804 | Orange Bay - 310 | Jul 9, 2026 3:39pm | Jul 9, 2026 3:39pm | Jul 9, 2026 3:51pm | Jul 9, 2026 3:51pm | Jul 9, 2026 3:51pm | Jul 9, 2026 4:20pm | Jul 9, 2026 4:20pm | Jul 9, 2026 4:20pm |  |  | SevereWind | No | Found junction fuse blown patroll found tree lim on primary line cut and remove tree lim from primary line replace 1-8amps junction fuse no pole number supply restore
Outage | J.E.26.07.06947 | C001844777 | Horace Malcolm | St.James | Completed | Load_557046 | Bogue - 310 | Jul 9, 2026 3:38pm | Jul 9, 2026 3:39pm | Jul 9, 2026 3:46pm | Jul 9, 2026 3:46pm | Jul 9, 2026 4:16pm | Jul 9, 2026 4:27pm | Jul 9, 2026 4:27pm | Jul 9, 2026 4:27pm |  |  | Fair | No | Check and found premises closed no occupant
Outage | J.E.26.07.08656 | C001844778 | Horace Malcolm | St.James | Completed | Load_261979 | Queens Drive - 310 | Jul 9, 2026 3:38pm | Jul 9, 2026 3:39pm | Jul 9, 2026 5:14pm | Jul 9, 2026 5:14pm | Jul 9, 2026 6:07pm | Jul 9, 2026 6:08pm | Jul 9, 2026 6:08pm | Jul 9, 2026 6:08pm |  |  | Fair | No | Check and found ok supply restored
Outage | J.E.26.07.09659 | C001844780 | Horace Malcolm | St.James | Completed | Load_244424 | Bogue - 310 | Jul 9, 2026 3:38pm | Jul 9, 2026 3:39pm | Jul 9, 2026 5:13pm | Jul 9, 2026 5:13pm | Jul 9, 2026 5:13pm | Jul 9, 2026 5:14pm | Jul 9, 2026 5:14pm | Jul 9, 2026 5:14pm |  |  | Fair | No | Call belongs to trelawny
Outage | J.E.26.07.09692 | C001844779 | Horace Malcolm | St.James | Completed | Load_1002108 | Bogue - 310 | Jul 9, 2026 3:38pm | Jul 9, 2026 3:39pm | Jul 9, 2026 4:27pm | Jul 9, 2026 4:27pm | Jul 9, 2026 4:42pm | Jul 9, 2026 4:50pm | Jul 9, 2026 4:50pm | Jul 9, 2026 4:50pm |  |  | Fair | No | Check and found customer the only one without supply coming from rami meter referred to field service
Outage | J.E.26.07.09693 | C001844782 | Horace Malcolm | St.James | Completed | Load_556938 | Bogue - 310 | Jul 9, 2026 3:38pm | Jul 9, 2026 3:39pm | Jul 9, 2026 4:50pm | Jul 9, 2026 4:50pm | Jul 9, 2026 5:04pm | Jul 9, 2026 5:13pm | Jul 9, 2026 5:13pm | Jul 9, 2026 5:13pm |  |  | Fair | No | Check and ok supply restored
Outage | J.E.26.07.07890 | C001844763 | Romeo Brissett | St.James | Completed | Load_302420 | Bogue - 510 | Jul 9, 2026 3:34pm | Jul 9, 2026 4:05pm | Jul 9, 2026 6:51pm | Jul 9, 2026 6:51pm | Jul 9, 2026 7:56pm | Jul 9, 2026 8:38pm | Jul 9, 2026 8:41pm | Jul 9, 2026 8:41pm |  |  | Fair | No | Line patrolled and found power in the area.
Outage | J.E.26.07.08639 | C001844761 | Romeo Brissett | St.James | Completed | Load_241154 | Bogue - 510 | Jul 9, 2026 3:34pm | Jul 9, 2026 4:05pm | Jul 9, 2026 5:34pm | Jul 9, 2026 5:34pm | Jul 9, 2026 6:21pm | Jul 9, 2026 6:35pm | Jul 9, 2026 6:48pm | Jul 9, 2026 6:48pm |  |  | Fair | No | Check and found ok, V/R 113-117-231
Outage | J.E.26.07.09125 | C001844762 | Michael Christian | St.James | Completed | Load_1000603 | Bogue - 510 | Jul 9, 2026 3:34pm | Jul 9, 2026 3:34pm | Jul 9, 2026 3:43pm | Jul 9, 2026 3:43pm | Jul 9, 2026 4:13pm | Jul 9, 2026 5:20pm | Jul 9, 2026 5:20pm | Jul 9, 2026 5:20pm |  |  | Fair | No | Found 1 20 amp 1 2 amp out cause by banging wires replace 1 20 amp at junction and 1 2 amp in 25 kava
Outage | J.E.26.07.09630 | C001844760 | Roxroy Needham | St.Ann | Completed | Load_242214 | Cardiff Hall - 210 | Jul 9, 2026 3:34pm | Jul 9, 2026 3:34pm | Jul 9, 2026 4:45pm | Jul 9, 2026 7:02pm | Jul 9, 2026 8:11pm | Jul 9, 2026 8:23pm | Jul 9, 2026 8:23pm | Jul 9, 2026 8:23pm |  |  | Fair | No | Replace 1- 20 amp junction fuse at pole
Outage | J.E.26.07.08897 | C001844758 | Clyde Brown | Clarendon | Completed | Load_237763 | May Pen - 110 | Jul 9, 2026 3:32pm | Jul 9, 2026 3:34pm | Jul 9, 2026 3:46pm | Jul 9, 2026 3:46pm | Jul 9, 2026 4:44pm | Jul 9, 2026 5:12pm | Jul 9, 2026 5:23pm | Jul 9, 2026 5:23pm |  |  | Fair | No | Secondary phase conductor touching flow guy wire,guy wire removed and tripped transformer reset.
Outage | J.E.26.07.09353 | C001844759 | Jermaine Williams | Clarendon | Completed | Load_246032 | Monymusk - 410 | Jul 9, 2026 3:32pm | Jul 9, 2026 3:34pm | Jul 9, 2026 4:36pm | Jul 9, 2026 4:36pm | Jul 9, 2026 4:44pm | Jul 9, 2026 5:10pm | Jul 9, 2026 5:12pm | Jul 9, 2026 5:12pm | BrokenWire |  | SevereWind | No | Isolate 25kva xfmr to splice and retention two spans broken secondary conductors using two 2/0 sleeve, one preform and two clamps.
Outage | J.E.26.07.08135 | C001844751 | Andre Williams | Trelawny | Completed | Load_246819 | Duncans - 210 | Jul 9, 2026 3:27pm | Jul 9, 2026 3:28pm | Jul 9, 2026 3:35pm | Jul 9, 2026 4:04pm | Jul 9, 2026 5:01pm | Jul 9, 2026 5:14pm | Jul 9, 2026 5:14pm | Jul 9, 2026 5:14pm |  |  | Fair | No | Remake burnt off joint on customer 3 wire service at jps pole voltage 116+114=230
Outage | J.E.26.07.09138 | C001844750 | Floyd Taylor | Trelawny | Completed | Load_302922 | Greenwood - 110 | Jul 9, 2026 3:26pm | Jul 9, 2026 3:28pm | Jul 9, 2026 4:07pm | Jul 9, 2026 4:07pm | Jul 9, 2026 5:38pm | Jul 9, 2026 6:22pm | Jul 9, 2026 6:22pm | Jul 9, 2026 6:22pm |  |  | Fair | No | Replace 1-20amp and 1-25amp junction fused
Outage | J.E.26.07.09160 | C001844740 | Andre Williams | Trelawny | Completed | Load_253461 | Duncans - 210 | Jul 9, 2026 3:26pm | Jul 9, 2026 3:28pm | Jul 9, 2026 6:47pm | Jul 9, 2026 7:33pm | Jul 9, 2026 7:33pm | Jul 9, 2026 7:33pm | Jul 9, 2026 7:33pm | Jul 9, 2026 7:33pm |  |  | Fair | No | Power was restored to area.
Outage | J.E.26.07.09658 | C001844745 | Andre Williams | Trelawny | Completed | Load_269195 | Martha Brae - 210 | Jul 9, 2026 3:26pm | Jul 9, 2026 6:19pm | Jul 9, 2026 7:33pm | Jul 9, 2026 9:10pm | Jul 9, 2026 9:35pm | Jul 9, 2026 9:50pm | Jul 9, 2026 9:51pm | Jul 9, 2026 9:51pm | BrokenWire |  | Fair | No | Splice and retention broken #6 conductor on customer 3 wire service. Voltage 115+115=230
Outage | J.E.26.07.09354 | C001844739 | Andrew Powell | St.Elizabeth | Completed | Load_264146 | Maggotty - 210 | Jul 9, 2026 3:21pm | Jul 9, 2026 3:26pm | Jul 9, 2026 3:31pm | Jul 9, 2026 3:34pm | Jul 9, 2026 4:23pm | Jul 9, 2026 4:45pm | Jul 9, 2026 4:48pm | Jul 9, 2026 4:48pm |  |  | Fair | No | Found internal fault at customer premises lower phase joints disconnect inside meter socket 3 wire, voltage reading 113v-116v phase to neutral 229v cross phase. Advise customer.
Outage | J.E.26.07.09003 | C001844735 | Selvin White | St.Elizabeth | Completed | Load_1002137 | Maggotty - 110 | Jul 9, 2026 3:20pm | Jul 9, 2026 3:28pm | Jul 9, 2026 4:14pm | Jul 9, 2026 4:14pm | Jul 9, 2026 4:40pm | Jul 9, 2026 4:52pm | Jul 9, 2026 4:53pm | Jul 9, 2026 4:53pm |  |  | Rains | No | Approximately 80 ft of number six triplex service wire along with a 3 wire 240 volts meter which was damaged during the recent hurricane will be required to reconnect customer which has been out of supply since. Please advise C. Johnson and Simone Bicarie at the field service department so customer can be reconnected.
Outage | J.E.26.07.09480 | C001844734 | Wayne Dillion | St.Elizabeth | Completed | Load_239722 | Maggotty - 210 | Jul 9, 2026 3:20pm | Jul 9, 2026 3:25pm | Jul 9, 2026 7:48pm | Jul 9, 2026 9:02pm | Jul 9, 2026 9:02pm | Jul 9, 2026 9:07pm | Jul 9, 2026 9:14pm | Jul 9, 2026 9:14pm |  |  | Fair | No | Customer is concerned about getting light bills and there is no supply at premises. Customer has not yet completed any repairs to the premises since hurricane Melissa.
Outage | J.E.26.07.09680 | C001844733 | Milton Charlton | KSAN | Completed | Load_241804 | Hope - 410 | Jul 9, 2026 3:20pm | Jul 9, 2026 3:22pm | Jul 9, 2026 3:54pm | Jul 9, 2026 3:54pm | Jul 9, 2026 4:27pm | Jul 9, 2026 4:30pm | Jul 9, 2026 4:31pm | Jul 9, 2026 4:31pm |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.07.09578 | C001844732 | Selvin White | St.Elizabeth | Completed | Load_257416 | Maggotty - 110 | Jul 9, 2026 3:19pm | Jul 9, 2026 3:28pm | Jul 9, 2026 4:59pm | Jul 9, 2026 4:59pm | Jul 9, 2026 5:38pm | Jul 9, 2026 5:47pm | Jul 9, 2026 5:47pm | Jul 9, 2026 5:47pm |  |  | Rains | No | Customer supply was upgraded from 2 wire to 3 wire service was passed by inspector. Escalation department was contacted and said no certificate was submitted as yet so customer was advised to submit certificate before an order can be generated for customer to be reconnected. Customer was advised.
Outage | J.E.26.07.09643 | C001844731 | Wayne Dillion | St.Elizabeth | Completed | Load_270140 | Maggotty - 110 | Jul 9, 2026 3:19pm | Jul 9, 2026 4:18pm | Jul 9, 2026 6:33pm | Jul 9, 2026 6:33pm | Jul 9, 2026 6:49pm | Jul 9, 2026 6:50pm | Jul 9, 2026 6:54pm | Jul 9, 2026 6:54pm |  |  | Fair | No | Supply check and found single phasing. Repair at pole using 1 clamp. Supply leave working okay reading 109v, 110v and cross phase 220volts.
Outage | J.E.26.07.09667 | C001844730 | Wayne Dillion | Manchester | Completed | Load_261504 | Spur Tree - 210 | Jul 9, 2026 3:19pm | Jul 9, 2026 3:25pm | Jul 9, 2026 4:35pm | Jul 9, 2026 4:35pm | Jul 9, 2026 4:35pm | Jul 9, 2026 5:28pm | Jul 9, 2026 5:36pm | Jul 9, 2026 5:36pm |  |  | Fair | No | Supply check and found single phasing. Repair at pole and pot head using 3 clamps and 3:linkets. Supply leave working okay reading 110v, 110v and cross phase 221volts.
Outage | J.E.26.07.09214 | C001844729 | Raymond Carr | St.Ann | Completed | Load_241946 | Upper White River - 210 | Jul 9, 2026 3:17pm | Jul 9, 2026 3:18pm | Jul 9, 2026 3:21pm | Jul 9, 2026 3:21pm | Jul 9, 2026 4:21pm | Jul 9, 2026 4:32pm | Jul 9, 2026 4:34pm | Jul 9, 2026 4:34pm |  |  | Fair | No | Blown junction fuse found at pole number 0913685, line patrol and found okay, lightening was suspected. A 25 amp fuse was used to renew supply was restored.
Outage | J.E.26.07.09495 | C001844671 | Milton Charlton | KSAN | Completed | Load_266887 | West Kings House - 210 | Jul 9, 2026 2:41pm | Jul 9, 2026 3:56pm | Jul 9, 2026 4:30pm | Jul 9, 2026 6:26pm | Jul 9, 2026 6:47pm | Jul 9, 2026 7:20pm | Jul 9, 2026 7:25pm | Jul 9, 2026 7:25pm |  |  | Fair | No | Meter # 2514882 is connected to customer meter socket this meter is disconnected meter that is assigned to customer is 1513057 which is connected to a deferent customer so meter mix up. Refer to field service.
Outage | J.E.26.07.09147 | C001844614 | Lloyd Lugg | St.Ann | Completed | Load_252272 | Roaring River - 410 | Jul 9, 2026 1:58pm | Jul 9, 2026 7:16pm | Jul 9, 2026 7:46pm | Jul 9, 2026 7:46pm | Jul 9, 2026 8:03pm | Jul 9, 2026 8:18pm | Jul 9, 2026 8:19pm | Jul 9, 2026 8:19pm | BrokenWire |  | Rains | No | Unable to locate customer ...... no broken JPS wire seen in area
Outage | J.E.26.07.09103 | C001844612 | Barrington Brown | St.James | Completed | Load_243105 | Queens Drive - 710 | Jul 9, 2026 1:56pm | Jul 9, 2026 1:56pm | Jul 9, 2026 2:13pm | Jul 9, 2026 2:13pm | Jul 9, 2026 2:54pm | Jul 9, 2026 3:21pm | Jul 9, 2026 3:21pm | Jul 9, 2026 3:21pm | BrokenWire |  | Fair | No | Crew found downed phase on location. Crew isolated fault @ pole#586204. Crew also found down tripsaver on glendevon road no pole number. Crew re energized circuit up to isolation point.
Outage | J.E.26.07.09518 | C001844610 | Jermaine Williams | Clarendon | Completed | Load_262809 | May Pen - 110 | Jul 9, 2026 1:55pm | Jul 9, 2026 3:57pm | Jul 9, 2026 8:39pm | Jul 9, 2026 8:39pm | Jul 9, 2026 8:39pm | Jul 9, 2026 8:51pm | Jul 9, 2026 8:55pm | Jul 9, 2026 8:55pm | BrokenWire |  | SevereWind | No | Isolate 25kva xfmr to splice and retention two spans broken secondary phase Conductor using 30’ 2/0aaa,one sleeve and one clamp
Outage | J.E.26.07.09391 | C001844607 | Andre Williams | Trelawny | Completed | Load_1001517 | Duncans - 110 | Jul 9, 2026 1:54pm | Jul 9, 2026 3:30pm | Jul 9, 2026 3:39pm | Jul 9, 2026 3:40pm | Jul 9, 2026 4:01pm | Jul 9, 2026 4:04pm | Jul 9, 2026 4:04pm | Jul 9, 2026 4:04pm | LeakingTransformer |  | Fair | No | 25 kva transformer slightly leaking at the log and on the side, area still with supply, oil causing damage to customer plants and fruit tree at pole reffer to maintenance lot 848
Outage | J.E.26.07.09397 | C001844608 | Neville Spencer | Clarendon | Completed | Load_260045 | May Pen - 110 | Jul 9, 2026 1:54pm | Jul 9, 2026 1:55pm | Jul 9, 2026 1:58pm | Jul 9, 2026 1:58pm | Jul 9, 2026 2:41pm | Jul 9, 2026 2:48pm | Jul 9, 2026 2:51pm | Jul 9, 2026 2:51pm |  |  | Fair | No | Disconnect 3 , wire service in meter socket # 3020084 reset trip 25 kva xmfr area restored customer advised.
Outage | J.E.26.07.09469 | C001844603 | Marlon Brown | Trelawny | Completed | Load_250518 | Duncans - 110 | Jul 9, 2026 1:54pm | Jul 9, 2026 1:55pm | Jul 9, 2026 1:59pm | Jul 9, 2026 1:59pm | Jul 9, 2026 2:11pm | Jul 9, 2026 3:28pm | Jul 9, 2026 3:28pm | Jul 9, 2026 3:28pm |  |  | Fair | No | 15amps junction fuse, replaced defective insulator clear tree limbs see permit # 11029.
Outage | J.E.26.07.08764 | C001844602 | Tajay Bernard | St.James | Completed | Load_267526 | Bogue - 510 | Jul 9, 2026 1:53pm | Jul 9, 2026 1:53pm | Jul 9, 2026 1:56pm | Jul 9, 2026 1:56pm | Jul 9, 2026 2:24pm | Jul 9, 2026 2:51pm | Jul 9, 2026 2:53pm | Jul 9, 2026 2:53pm | Fire |  | Fair | No | Refuse 1 10amp junction fuse Meter close to the pole(3036226)
Outage | J.E.26.07.09108 | C001844601 | Lancelot Brown | Hanover | Completed | Load_257747 | Orange Bay - 310 | Jul 9, 2026 1:52pm | Jul 9, 2026 3:32pm | Jul 9, 2026 4:20pm | Jul 9, 2026 5:58pm | Jul 9, 2026 5:58pm | Jul 9, 2026 6:04pm | Jul 9, 2026 6:04pm | Jul 9, 2026 6:04pm |  |  | Rains | No | Get direction from security to premises check voltage at pothead 114-115-230 no one at premises also both meter number not corresponding with meter at location
Outage | J.E.26.07.08907 | C001844599 | Romeo Brissett | St.James | Completed | Load_257396 | Bogue - 610 | Jul 9, 2026 1:51pm | Jul 9, 2026 1:51pm | Jul 9, 2026 1:57pm | Jul 9, 2026 1:57pm | Jul 9, 2026 3:21pm | Jul 9, 2026 5:00pm | Jul 9, 2026 5:21pm | Jul 9, 2026 5:21pm |  |  | Fair | No | Disconnected and isolated defective pothead reset (1)10KVA transformer
Outage | J.E.26.07.09481 | C001844600 | Romeo Brissett | St.James | Completed | Load_266838 | Bogue - 610 | Jul 9, 2026 1:51pm | Jul 9, 2026 1:51pm | Jul 9, 2026 5:22pm | Jul 9, 2026 5:23pm | Jul 9, 2026 5:32pm | Jul 9, 2026 5:33pm | Jul 9, 2026 5:34pm | Jul 9, 2026 5:34pm |  |  | Fair | No | Unable to locate customer, directions unclear, phone ring to voicemail.
Outage | J.E.26.07.09501 | C001844588 | Cliton Henry | St.Mary | Completed | Load_247804 | Blackstonedge - 110 | Jul 9, 2026 1:39pm | Jul 9, 2026 1:39pm | Jul 9, 2026 2:57pm | Jul 9, 2026 2:57pm | Jul 9, 2026 3:09pm | Jul 9, 2026 4:29pm | Jul 9, 2026 4:29pm | Jul 9, 2026 4:29pm | BrokenWire |  | Fair | No | A broken secondary neutral conductor found on the ground. A 25 kva transformer was de energized to carryout repairs. Corrective work done to to spliced and retention secondary neutral conductor using approximately 70 feet #2 AA, 1#2 preform and 2one bolt clamps. Voltages left 119-119/238 volts.
Non-Outage | J.E.26.07.08622 | C001844581 | Cliton Henry | null | Completed | null | null | Jul 9, 2026 1:15pm | Jul 9, 2026 1:16pm | Jul 9, 2026 4:32pm | Jul 9, 2026 4:32pm | Jul 9, 2026 4:32pm | Jul 9, 2026 4:32pm | Jul 9, 2026 4:33pm | Jul 9, 2026 4:33pm | BrokenWire |  | Fair | No | Supply restored, related to outage #09501
Outage | J.E.26.07.09407 | C001844566 | Evan Spaulding | St.Mary | Completed | Load_269277 | Highgate -110 | Jul 9, 2026 12:56pm | Jul 9, 2026 12:57pm | Jul 9, 2026 4:42pm | Jul 9, 2026 4:42pm | Jul 9, 2026 5:40pm | Jul 9, 2026 10:56pm | Jul 9, 2026 10:59pm | Jul 9, 2026 10:59pm | BrokenWire |  | SevereWind | No | Straighten 35ft wooden,splice and retention 5 spans secondary conductors using 150ft 2/0 AAAC conductor,6-2/0 splicing sleeves,4-2/0 preforms and 8-1 bolt clamps.
Outage | J.E.26.07.09418 | C001844565 | Neckell Ormsby | St.Mary | Completed | Load_267975 | Highgate - 210 | Jul 9, 2026 12:56pm | Jul 9, 2026 4:12pm | Jul 9, 2026 7:09pm | Jul 9, 2026 7:09pm | Jul 9, 2026 7:56pm | Jul 9, 2026 9:40pm | Jul 9, 2026 9:40pm | Jul 9, 2026 9:40pm | BrokenWire |  | Rains | No | Found blown fuse for transformer unable to see size, patrol and found 2- pole span broken secondary phase and neutral (heavy rain in area) splice and retention conductors using approximately 50 ft #2 AA ,2-# sleeves and 3- one bolt clamps voltage left 119v 119v 238v
Outage | J.E.26.07.08039 | C001844559 | Edward Royal | KSAS | Completed | Load_249689 | Three Miles - 410 | Jul 9, 2026 12:54pm | Jul 9, 2026 12:58pm | Jul 9, 2026 1:30pm | Jul 9, 2026 1:30pm | Jul 9, 2026 1:30pm | Jul 9, 2026 1:30pm | Jul 9, 2026 1:30pm | Jul 9, 2026 1:30pm |  |  | Fair | No | Meter not responding meter need to be check reffered to field
Outage | J.E.26.07.09370 | C001844555 | Tyrese Williams | St.Ann | Completed | Load_254202 | Cardiff Hall - 310 | Jul 9, 2026 12:51pm | Jul 9, 2026 12:52pm | Jul 9, 2026 1:44pm | Jul 9, 2026 6:11pm | Jul 9, 2026 7:41pm | Jul 9, 2026 7:41pm | Jul 9, 2026 7:41pm | Jul 9, 2026 7:41pm | BrokenWire |  | Fair | No | 100 ft of Service wire recommended
Outage | J.E.26.07.09415 | C001844554 | Omar King | St.Ann | Completed | Load_264396 | Upper White River - 210 | Jul 9, 2026 12:51pm | Jul 9, 2026 12:52pm | Jul 9, 2026 5:17pm | Jul 9, 2026 5:18pm | Jul 9, 2026 5:18pm | Jul 9, 2026 5:18pm | Jul 9, 2026 5:19pm | Jul 9, 2026 5:19pm |  |  | Fair | No | Found 25 amp junction fuse blow cause by lightning fuse as been replaced area is now with supply related call
Outage | J.E.26.07.09444 | C001844553 | Omar King | St.Ann | Completed | Load_248659 | Upper White River - 210 | Jul 9, 2026 12:51pm | Jul 9, 2026 3:00pm | Jul 9, 2026 3:03pm | Jul 9, 2026 3:03pm | Jul 9, 2026 4:41pm | Jul 9, 2026 4:42pm | Jul 9, 2026 4:43pm | Jul 9, 2026 4:43pm | Fire |  | Fair | No | Found 25 amp junction fuse blow cause by lightning fuse as been replaced area is now with supply
Non-Outage | J.E.26.06.32171 | C001844550 | Wan Carlos Scarlett | Portmore | Completed | Load_252357 | Naggo Head - 510 | Jul 9, 2026 12:48pm | Jul 9, 2026 12:49pm | Jul 9, 2026 1:42pm | Jul 9, 2026 1:42pm | Jul 9, 2026 2:20pm | Jul 9, 2026 3:05pm | Jul 9, 2026 3:07pm | Jul 9, 2026 3:07pm |  |  | Fair | No | Found 3 phase primary line junction with one of the switch top jumper burn off pole 011891 need maintenance team assistance
Non-Outage | J.E.26.07.07081 | C001844541 | Evan Spaulding | St.Mary | Completed | Load_252310 | Highgate -110 | Jul 9, 2026 12:37pm | Jul 9, 2026 12:37pm | Jul 9, 2026 3:05pm | Jul 9, 2026 3:05pm | Jul 9, 2026 3:05pm | Jul 9, 2026 3:06pm | Jul 9, 2026 3:07pm | Jul 9, 2026 3:07pm | Fire |  | Fair | No | Associated call.
Outage | J.E.26.07.09262 | C001844544 | Ryan Richards | Manchester | Completed | Load_239116 | Kendal - 310 | Jul 9, 2026 12:37pm | Jul 9, 2026 12:38pm | Jul 9, 2026 12:42pm | Jul 9, 2026 3:56pm | Jul 9, 2026 3:56pm | Jul 9, 2026 3:57pm | Jul 9, 2026 3:57pm | Jul 9, 2026 3:57pm |  |  | Fair | No | Same as the other blown 50 amp junction fuse replaced
Outage | J.E.26.07.09373 | C001844542 | Ryan Richards | Manchester | Completed | Load_265411 | Kendal - 310 | Jul 9, 2026 12:37pm | Jul 9, 2026 12:38pm | Jul 9, 2026 12:42pm | Jul 9, 2026 3:57pm | Jul 9, 2026 3:57pm | Jul 9, 2026 3:58pm | Jul 9, 2026 3:58pm | Jul 9, 2026 3:58pm |  |  | Fair | No | Same as the other blown 50 amp junction fuse replaced
Outage | J.E.26.07.09380 | C001844543 | Ryan Richards | Manchester | Completed | Load_1002494 | Kendal - 310 | Jul 9, 2026 12:37pm | Jul 9, 2026 12:38pm | Jul 9, 2026 12:42pm | Jul 9, 2026 12:42pm | Jul 9, 2026 2:01pm | Jul 9, 2026 3:56pm | Jul 9, 2026 3:56pm | Jul 9, 2026 3:56pm |  |  | Fair | No | Blown 50 amp junction fuse found line patrol nothing found blown fuse was replaced and all customers are now with supply
Outage | J.E.26.07.07489 | C001844536 | Moses Elliston | St.Catherine | Completed | Load_557299 | Tredegar - 410 | Jul 9, 2026 12:32pm | Jul 9, 2026 12:32pm | Jul 9, 2026 1:02pm | Jul 9, 2026 1:02pm | Jul 9, 2026 1:02pm | Jul 9, 2026 11:40am | Jul 9, 2026 1:04pm | Jul 9, 2026 1:04pm |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.07.07441 | C001844535 | Omar King | St.Ann | Completed | Load_259193 | Roaring River - 210 | Jul 9, 2026 12:30pm | Jul 9, 2026 12:30pm | Jul 9, 2026 1:01pm | Jul 9, 2026 1:01pm | Jul 9, 2026 1:50pm | Jul 9, 2026 2:01pm | Jul 9, 2026 2:02pm | Jul 9, 2026 2:02pm |  |  | Fair | No | Found 40 amp junction fuse blow cause by lightning fuse as been replaced a section of the primary line is still out due to no access to switch point please bear in mind for a follow up
Outage | J.E.26.07.09266 | C001844528 | Javid Vernon | Westmoreland | Completed | Load_259377 | Paradise - 310 | Jul 9, 2026 12:29pm | Jul 9, 2026 12:29pm | Jul 9, 2026 1:54pm | Jul 9, 2026 1:54pm | Jul 9, 2026 2:41pm | Jul 9, 2026 3:13pm | Jul 9, 2026 3:15pm | Jul 9, 2026 3:15pm |  |  | Fair | No | Refuse two 15amp junction fuse at pole #582390
Non-Outage | J.E.26.07.08306 | C001844525 | Edward Royal | KSAN | Completed | Load_245677 | West Kings House - 210 | Jul 9, 2026 12:22pm | Jul 9, 2026 1:50pm | Jul 9, 2026 2:40pm | Jul 9, 2026 2:40pm | Jul 9, 2026 2:40pm | Jul 9, 2026 3:43pm | Jul 9, 2026 3:44pm | Jul 9, 2026 3:44pm |  |  | Fair | No | Replaced 10A transformer fuse
Outage | J.E.26.07.08928 | C001844517 | Moses Elliston | St.Catherine | Completed | Load_1001544 | Tredegar - 510 | Jul 9, 2026 12:14pm | Jul 9, 2026 12:14pm | Jul 9, 2026 2:05pm | Jul 9, 2026 2:05pm | Jul 9, 2026 2:05pm | Jul 9, 2026 2:05pm | Jul 9, 2026 2:07pm | Jul 9, 2026 2:07pm |  |  | Fair | No | Customer breakers opened ,same reclosed
Non-Outage | J.E.26.07.08722 | C001844515 | Moses Elliston | null | Completed | null | null | Jul 9, 2026 12:13pm | Jul 9, 2026 12:14pm | Jul 9, 2026 1:09pm | Jul 9, 2026 1:09pm | Jul 9, 2026 1:09pm | Jul 9, 2026 1:13pm | Jul 9, 2026 1:21pm | Jul 9, 2026 1:21pm |  |  | Fair | No | Customer has - 425.28 KWh to be clarify in Office .Was advised
Non-Outage | J.E.26.07.08949 | C001844516 | Moses Elliston | null | Completed | null | null | Jul 9, 2026 12:13pm | Jul 9, 2026 12:14pm | Jul 9, 2026 1:06pm | Jul 9, 2026 1:06pm | Jul 9, 2026 1:06pm | Jul 9, 2026 12:10pm | Jul 9, 2026 1:07pm | Jul 9, 2026 1:07pm |  |  | Fair | No | Customer to add credit to account
Outage | J.E.26.07.09065 | C001844513 | Derrick Dawkins | St.James | Completed | Load_556998 | Bogue - 310 | Jul 9, 2026 12:12pm | Jul 9, 2026 12:12pm | Jul 9, 2026 12:39pm | Jul 9, 2026 12:39pm | Jul 9, 2026 12:39pm | Jul 9, 2026 2:21pm | Jul 9, 2026 2:23pm | Jul 9, 2026 2:23pm |  |  | Fair | No | Found a junction fuse blown 50 amp due to vegetation removed vegetation replaced a 50 amp junction fuse no pole # available
Outage | J.E.26.07.09069 | C001844514 | Derrick Dawkins | St.James | Completed | Load_248547 | Bogue - 310 | Jul 9, 2026 12:12pm | Jul 9, 2026 12:12pm | Jul 9, 2026 2:23pm | Jul 9, 2026 2:23pm | Jul 9, 2026 2:23pm | Jul 9, 2026 2:24pm | Jul 9, 2026 2:24pm | Jul 9, 2026 2:24pm |  |  | Fair | No | Related to the 50 amp junction fuse checked and found ok
Outage | J.E.26.07.09283 | C001844506 | Selvin White | St.Elizabeth | Completed | Load_242242 | Maggotty - 210 | Jul 9, 2026 12:06pm | Jul 9, 2026 5:13pm | Jul 9, 2026 5:48pm | Jul 9, 2026 8:07pm | Jul 9, 2026 9:00pm | Jul 9, 2026 9:05pm | Jul 9, 2026 9:05pm | Jul 9, 2026 9:05pm | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Customer cannot be reconnected due to defect that to be corrected. Customer was advised to get a licensed electrician to carry out repairs and then contact JPSCo. for reconnection.
Outage | J.E.26.07.09189 | C001844495 | Daniel Francis | St.Ann | Completed | Load_263260 | Roaring River - 410 | Jul 9, 2026 11:55am | Jul 9, 2026 11:55am | Jul 9, 2026 12:34pm | Jul 9, 2026 12:34pm | Jul 9, 2026 1:01pm | Jul 9, 2026 1:30pm | Jul 9, 2026 1:33pm | Jul 9, 2026 1:33pm |  |  | Rains | No | Replace junction near scotchies 25amp
Outage | J.E.26.07.08970 | C001844490 | Cliton Henry | St.Mary | Completed | Load_240121 | Blackstonedge - 110 | Jul 9, 2026 11:54am | Jul 9, 2026 11:55am | Jul 9, 2026 12:20pm | Jul 9, 2026 12:20pm | Jul 9, 2026 1:05pm | Jul 9, 2026 2:53pm | Jul 9, 2026 2:56pm | Jul 9, 2026 2:56pm | BrokenWire |  | Fair | No | A blown 30 amp junction fuse found at Windsor Castle main rd.at pole #0177019 due to a broken single phase primary conductor. Corrective work done to spliced and retention primary conductor using approximately 25 feet #2 AA conductor, 1#2 preform and1 one bolt clamps. Supply restored using 1-30 amp fuse.
Outage | J.E.26.07.09322 | C001844488 | Tyrese Williams | St.Ann | Completed | Load_252427 | Cardiff Hall - 310 | Jul 9, 2026 11:52am | Jul 9, 2026 11:56am | Jul 9, 2026 1:26pm | Jul 9, 2026 1:29pm | Jul 9, 2026 1:31pm | Jul 9, 2026 1:31pm | Jul 9, 2026 1:31pm | Jul 9, 2026 1:31pm |  |  | Fair | No | Premises found ok customer said light just came back
Outage | J.E.26.07.08719 | C001844482 | Raymond Carr | St.Mary | Completed | Load_354661 | Oracabessa - 110 | Jul 9, 2026 11:46am | Jul 9, 2026 11:47am | Jul 9, 2026 1:10pm | Jul 9, 2026 1:10pm | Jul 9, 2026 1:47pm | Jul 9, 2026 2:27pm | Jul 9, 2026 2:20pm | Jul 9, 2026 2:20pm |  |  | Fair | No | 50 kva transformer found tripped at pole number 0013409, line patrol and found okay, lightening was suspected. Supply was restored.
Outage | J.E.26.07.09287 | C001844477 | Raymond Lewis | St.Ann | Completed | Load_269998 | Ocho Rios - 310 | Jul 9, 2026 11:42am | Jul 9, 2026 1:54pm | Jul 9, 2026 2:20pm | Jul 9, 2026 2:20pm | Jul 9, 2026 3:21pm | Jul 9, 2026 3:51pm | Jul 9, 2026 3:51pm | Jul 9, 2026 3:51pm | Fire |  | SevereWind | No | Open 25kva x former to retention secondary splice and retention 3 wire service
Outage | J.E.26.07.09275 | C001844465 | Romaine Roberts | St.Mary | Completed | Load_576739 | Annotto Bay - 210 | Jul 9, 2026 11:37am | Jul 9, 2026 11:38am | Jul 9, 2026 12:46pm | Jul 9, 2026 12:46pm | Jul 9, 2026 4:03pm | Jul 9, 2026 4:26pm | Jul 9, 2026 4:27pm | Jul 9, 2026 4:27pm | Fire |  | Fair | No | High wind and vegetation bang and burn down 3 span of secondary phase and neutral open and close 25 kva transformer to splice and retention conductor also clear vegetation from line
Outage | J.E.26.07.08743 | C001844464 | Omar King | St.Ann | Completed | Load_239077 | Ocho Rios - 310 | Jul 9, 2026 11:36am | Jul 9, 2026 11:38am | Jul 9, 2026 11:58am | Jul 9, 2026 11:58am | Jul 9, 2026 12:04pm | Jul 9, 2026 12:08pm | Jul 9, 2026 12:09pm | Jul 9, 2026 12:09pm | LeakingTransformer |  | Fair | No | Found a 50 amp junction fuse blow cause by lightning fuse as been replaced area is now with supply
Outage | J.E.26.07.09187 | C001844463 | Barrington Brown | St.James | Completed | Load_248671 | Queens Drive - 710 | Jul 9, 2026 11:35am | Jul 9, 2026 11:35am | Jul 9, 2026 11:51am | Jul 9, 2026 11:51am | Jul 9, 2026 12:19pm | Jul 9, 2026 1:03pm | Jul 9, 2026 1:04pm | Jul 9, 2026 1:04pm | Fire |  | Fair | No | Crew found a leaning/rotten guy pole which leaned on open secondary causing wires to bang and burn down. Crew opened secondary jumper and isolated fault. In order for wire to be retentioned guy pole needs to be removed and replaced. Guy pole needed due to load baring dead end pole. Please refer to maintenance department to have pole replaced ASAP. Seven customers on location have been left without supply.
Outage | J.E.26.07.08627 | C001844445 | Wan Carlos Scarlett | St.Catherine | Completed | Load_291664 | Twickenham - 210 | Jul 9, 2026 11:26am | Jul 9, 2026 11:49am | Jul 9, 2026 12:20pm | Jul 9, 2026 12:20pm | Jul 9, 2026 12:48pm | Jul 9, 2026 1:39pm | Jul 9, 2026 1:41pm | Jul 9, 2026 1:41pm |  |  | Fair | No | Refuse 20amp junction no pole # was found clear bird from off single primary line
Outage | J.E.26.07.08644 | C001844444 | Moses Elliston | St.Catherine | Completed | Load_291951 | Twickenham - 210 | Jul 9, 2026 11:26am | Jul 9, 2026 11:27am | Jul 10, 2026 11:22am | Jul 10, 2026 11:22am | Jul 10, 2026 11:22am | Jul 10, 2026 11:24am | Jul 10, 2026 11:25am | Jul 10, 2026 11:25am |  |  | Fair | No | Supply ok ,outage was in area.
Outage | J.E.26.07.08689 | C001844436 | Rodclif Dawkins | Portmore | Completed | Load_570083 | Naggo Head - 610 | Jul 9, 2026 11:24am | Jul 9, 2026 3:36pm | Jul 9, 2026 7:16pm | Jul 9, 2026 8:20pm | Jul 9, 2026 8:53pm | Jul 9, 2026 8:53pm | Jul 9, 2026 8:58pm | Jul 9, 2026 8:58pm |  |  | Fair | No | Customer not present at time of visit. Customer requesting a re-visit by morning crew
Outage | J.E.26.07.09207 | C001844435 | Rodclif Dawkins | Portmore | Completed | Load_254077 | Naggo Head - 510 | Jul 9, 2026 11:24am | Jul 9, 2026 3:36pm | Jul 9, 2026 7:16pm | Jul 9, 2026 7:35pm | Jul 9, 2026 7:48pm | Jul 9, 2026 8:19pm | Jul 9, 2026 8:19pm | Jul 9, 2026 8:19pm | Fire |  | Fair | No | On location, crew observed no fire or signs of fire at the time of visit
Outage | J.E.26.07.09068 | C001844429 | Derrick Dawkins | Manchester | Completed | Load_243336 | Kendal - 210 | Jul 9, 2026 11:16am | Jul 9, 2026 11:16am | Jul 9, 2026 11:43am | Jul 9, 2026 11:43am | Jul 9, 2026 12:03pm | Jul 9, 2026 12:23pm | Jul 9, 2026 12:24pm | Jul 9, 2026 12:24pm |  |  | Fair | No | Found a junction fuse blown 30 amp replaced a 30 amp junction fuse
Outage | J.E.26.07.09172 | C001844417 | Fitzroy Turner | KSAN | Completed | Load_249367 | Washington Blvd - 810 | Jul 9, 2026 11:14am | Jul 9, 2026 11:15am | Jul 9, 2026 12:45pm | Jul 9, 2026 1:30pm | Jul 9, 2026 1:47pm | Jul 9, 2026 1:56pm | Jul 9, 2026 1:57pm | Jul 9, 2026 1:57pm |  |  | Fair | No | Customer supply reconnected
Outage | J.E.26.07.09175 | C001844416 | Eric Williams | KSAS | Completed | Load_239161 | Duhaney - 310 | Jul 9, 2026 11:14am | Jul 9, 2026 4:54pm | Jul 9, 2026 9:38pm | Jul 9, 2026 9:38pm | Jul 9, 2026 10:02pm | Jul 9, 2026 10:18pm | Jul 9, 2026 10:19pm | Jul 9, 2026 10:19pm |  |  | Fair | No | Electricity in the area, call to customer went unanswered.
Non-Outage | J.E.26.07.07942 | C001844412 | Floyd Taylor | Trelawny | Completed | Load_249410 | Greenwood - 210 | Jul 9, 2026 11:07am | Jul 9, 2026 11:07am | Jul 9, 2026 1:11pm | Jul 9, 2026 1:11pm | Jul 9, 2026 1:11pm | Jul 9, 2026 2:01pm | Jul 9, 2026 2:05pm | Jul 9, 2026 2:05pm |  |  | Fair | No | Remake joint at pole using two clamp, voltage reading 107,104,213
Non-Outage | J.E.26.07.08527 | C001844411 | Floyd Taylor | Trelawny | Completed | Load_239800 | Greenwood - 210 | Jul 9, 2026 11:07am | Jul 9, 2026 11:07am | Jul 9, 2026 2:34pm | Jul 9, 2026 2:34pm | Jul 9, 2026 2:44pm | Jul 9, 2026 2:45pm | Jul 9, 2026 2:50pm | Jul 9, 2026 2:50pm | BrokenPole |  | Fair | No | 40ft wooden pole leaning, construction of pole DE with single phase primary with transformer and open secondary. Refer to maintenance.
Outage | J.E.26.07.09144 | C001844409 | Floyd Taylor | Trelawny | Completed | Load_292876 | Greenwood - 210 | Jul 9, 2026 11:06am | Jul 9, 2026 11:06am | Jul 9, 2026 11:26am | Jul 9, 2026 11:26am | Jul 9, 2026 11:52am | Jul 9, 2026 1:05pm | Jul 9, 2026 1:11pm | Jul 9, 2026 1:11pm |  |  | Fair | No | Replaced one 30Amp fuse after line was patrolled and nothing was found, voltage reading 117,118,236
Outage | J.E.26.07.08612 | C001844408 | Hartley Chin | Clarendon | Completed | Load_269341 | Monymusk - 210 | Jul 9, 2026 11:05am | Jul 9, 2026 11:05am | Jul 9, 2026 11:25am | Jul 9, 2026 11:36am | Jul 9, 2026 1:54pm | Jul 9, 2026 2:17pm | Jul 9, 2026 2:19pm | Jul 9, 2026 2:19pm |  |  | Fair | No | Ref to field service. !!! Found no voltage read @ customer pot head … customer is receiving supply from HX 26552224 .. note : customer is the only person currently affected…
Outage | J.E.26.07.08779 | C001844407 | Hopeton Henry | St.Thomas | Completed | Load_266684 | Good Year - 210 | Jul 9, 2026 11:05am | Jul 9, 2026 11:05am | Jul 9, 2026 12:10pm | Jul 9, 2026 12:45pm | Jul 9, 2026 12:55pm | Jul 9, 2026 12:55pm | Jul 9, 2026 12:57pm | Jul 9, 2026 12:57pm | BrokenWire |  | Fair | No | Splice and retention secondary conductors, issue resolved
Outage | J.E.26.07.08855 | C001844406 | Hopeton Henry | St.Thomas | Completed | Load_246479 | Good Year - 210 | Jul 9, 2026 11:05am | Jul 9, 2026 11:05am | Jul 9, 2026 12:59pm | Jul 9, 2026 12:59pm | Jul 9, 2026 1:02pm | Jul 9, 2026 1:02pm | Jul 9, 2026 1:04pm | Jul 9, 2026 1:04pm | BrokenWire |  | Fair | No | Check and found ok , issue resolved
Non-Outage | J.E.26.07.07468 | C001844398 | Roemello Brown | Trelawny | Completed | Load_244593 | Greenwood - 110 | Jul 9, 2026 10:58am | Jul 9, 2026 10:58am | Jul 9, 2026 12:50pm | Jul 9, 2026 12:53pm | Jul 9, 2026 2:57pm | Jul 9, 2026 2:57pm | Jul 9, 2026 3:22pm | Jul 9, 2026 3:22pm |  |  | Fair | No | Premises found working okay problem not on jps side inform the customer to get an private electrician to get premises check Voltage found 113/113/226Voltage leave 113/113/226
Non-Outage | J.E.26.07.07500 | C001844397 | Roemello Brown | Trelawny | Completed | Load_240895 | Greenwood - 110 | Jul 9, 2026 10:58am | Jul 9, 2026 10:58am | Jul 9, 2026 11:15am | Jul 9, 2026 11:15am | Jul 9, 2026 12:38pm | Jul 9, 2026 12:38pm | Jul 9, 2026 12:50pm | Jul 9, 2026 12:50pm |  |  | Fair | Yes | Premises found working okay Voltage found 116/117/233Voltage leave 116/117/233
Non-Outage | J.E.26.07.07642 | C001844396 | Roemello Brown | Trelawny | Completed | Load_266091 | Greenwood - 110 | Jul 9, 2026 10:58am | Jul 9, 2026 10:58am | Jul 9, 2026 12:51pm | Jul 9, 2026 12:51pm | Jul 9, 2026 12:51pm | Aug 7, 2026 12:51pm | Jul 9, 2026 12:53pm | Jul 9, 2026 12:53pm | LowHangingWires |  | Fair | No | This call is for Montego Bay team please transfer to st.james team please
Non-Outage | J.E.26.07.08561 | C001844395 | Roemello Brown | Trelawny | Completed | Load_292911 | Greenwood - 110 | Jul 9, 2026 10:58am | Jul 9, 2026 10:58am | Jul 10, 2026 8:36am | Jul 10, 2026 9:09am | Jul 10, 2026 10:17am | Jul 10, 2026 10:17am | Jul 10, 2026 10:23am | Jul 10, 2026 10:23am |  |  | Fair | No | Corrosion at the pothead have clamps change Voltage found 126/106/232Voltage leave 117/117/234
Outage | J.E.26.07.08788 | C001844394 | Rusean Allen | KSAS | Completed | Load_1002859 | Rockfort - 410 | Jul 9, 2026 10:55am | Jul 9, 2026 10:55am | Jul 9, 2026 1:21pm | Jul 9, 2026 1:21pm | Jul 9, 2026 1:28pm | Jul 9, 2026 1:33pm | Jul 9, 2026 1:33pm | Jul 9, 2026 1:33pm |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.08789 | C001844393 | Rusean Allen | KSAS | Completed | Load_239308 | Rockfort - 410 | Jul 9, 2026 10:55am | Jul 9, 2026 10:55am | Jul 9, 2026 1:33pm | Jul 9, 2026 1:33pm | Jul 9, 2026 1:53pm | Jul 9, 2026 1:53pm | Jul 9, 2026 1:53pm | Jul 9, 2026 1:53pm |  |  | Fair | No | Premises okay
Outage | J.E.26.07.08620 | C001844383 | Gregory Grossett | Portland | Completed | Load_252323 | Port Antonio - 410 | Jul 9, 2026 10:54am | Jul 9, 2026 3:55pm | Jul 9, 2026 4:03pm | Jul 9, 2026 4:03pm | Jul 9, 2026 4:48pm | Jul 9, 2026 5:25pm | Jul 9, 2026 5:37pm | Jul 9, 2026 5:37pm |  | Y | Fair | No | 10kva transformer trip cause by vegetation on line section cut and removed vegetation from secondary conductors then restore supply to the area.Also area needs maintenance bushing please refer to maintenance to have this done.
Outage | J.E.26.07.08878 | C001844381 | Marlon Brown | Trelawny | Completed | Load_248221 | Duncans - 210 | Jul 9, 2026 10:54am | Jul 9, 2026 10:54am | Jul 9, 2026 11:37am | Jul 9, 2026 11:37am | Jul 9, 2026 12:09pm | Jul 9, 2026 12:50pm | Jul 9, 2026 12:51pm | Jul 9, 2026 12:51pm | Fire |  | Rains | No | Repair service wire neutral
Outage | J.E.26.07.08918 | C001844382 | Marlon Brown | Trelawny | Completed | Load_237728 | Duncans - 210 | Jul 9, 2026 10:54am | Jul 9, 2026 10:54am | Jul 9, 2026 11:32am | Jul 9, 2026 12:54pm | Jul 9, 2026 1:10pm | Jul 9, 2026 1:51pm | Jul 9, 2026 1:52pm | Jul 9, 2026 1:52pm |  |  | Fair | No | Replaced 15amps junction fuse @ pole # 027392.
Non-Outage | J.E.26.07.08876 | C001844379 | Milton Charlton | null | Completed | null | null | Jul 9, 2026 10:49am | Jul 9, 2026 10:49am | Jul 9, 2026 11:56am | Jul 9, 2026 1:08pm | Jul 9, 2026 1:08pm | Jul 9, 2026 12:15pm | Jul 9, 2026 1:11pm | Jul 9, 2026 1:11pm | Fire |  | Fair | No | Call related to call at Brampton Road.
Non-Outage | J.E.26.07.09110 | C001844378 | Milton Charlton | null | Completed | null | null | Jul 9, 2026 10:48am | Jul 9, 2026 10:48am | Jul 9, 2026 11:57am | Jul 9, 2026 1:05pm | Jul 9, 2026 1:05pm | Jul 9, 2026 12:15pm | Jul 9, 2026 1:08pm | Jul 9, 2026 1:08pm | Fire |  | Fair | No | Call related to call at Brampton Road.
Outage | J.E.26.07.09018 | C001844377 | Milton Charlton | KSAN | Completed | Load_238339 | Hope - 410 | Jul 9, 2026 10:48am | Jul 9, 2026 10:48am | Jul 9, 2026 1:11pm | Jul 9, 2026 1:11pm | Jul 9, 2026 2:18pm | Jul 9, 2026 2:20pm | Jul 9, 2026 2:22pm | Jul 9, 2026 2:22pm |  |  | Fair | No | Customer is fed from EN#05283 and is getting on and off supply from the box Refer to field service.
Outage | J.E.26.07.08921 | C001844376 | Milton Charlton | KSAN | Completed | Load_261791 | Hope - 510 | Jul 9, 2026 10:47am | Jul 9, 2026 10:48am | Jul 9, 2026 11:53am | Jul 9, 2026 11:53am | Jul 9, 2026 12:58pm | Jul 9, 2026 12:15pm | Jul 9, 2026 1:05pm | Jul 9, 2026 1:05pm | BrokenWire |  | Fair | No | No fire or broken wire seen on any JPS wires between Papine and Irish Town Rd.
Non-Outage | J.E.26.07.09102 | C001844375 | Rodclif Dawkins | Portmore | Completed | Load_251890 | Naggo Head - 510 | Jul 9, 2026 10:44am | Jul 9, 2026 3:45pm | Jul 9, 2026 3:49pm | Jul 9, 2026 3:49pm | Jul 9, 2026 4:33pm | Jul 9, 2026 5:20pm | Jul 9, 2026 5:24pm | Jul 9, 2026 5:24pm |  |  | Fair | No | Found 1 blown fuse from 3phase junction. Line section patrolled to bank of 3 transformer, were crew found burnt switch top jumper for 100kva lighting transformer. Bank de-energized and switch top remade. At junction crew found and replaced 25amp fuse . Customer okay
Outage | J.E.26.07.08778 | C001844361 | Evan Spaulding | St.Mary | Completed | Load_264015 | Highgate -110 | Jul 9, 2026 10:34am | Jul 9, 2026 11:48am | Jul 9, 2026 3:07pm | Jul 9, 2026 3:07pm | Jul 9, 2026 3:07pm | Jul 9, 2026 3:08pm | Jul 9, 2026 3:08pm | Jul 9, 2026 3:08pm | Fire |  | SevereWind | No | Associated call.
Outage | J.E.26.07.08466 | C001844345 | Nickolas Rodriques | Clarendon | Completed | Load_257434 | Parnassus - 210 | Jul 9, 2026 10:27am | Jul 9, 2026 10:28am | Jul 9, 2026 11:23am | Jul 9, 2026 11:23am | Jul 9, 2026 11:49am | Jul 9, 2026 12:07pm | Jul 9, 2026 12:34pm | Jul 9, 2026 12:34pm |  |  | Fair | No | Call relates to the 25 KVA transformer that was found defective and needs to be replaced. The maintenance team is aware of the defective transformer that supplies 73 and 75 lane John’s road.
Outage | J.E.26.07.08780 | C001844340 | Roxroy Needham | St.Ann | Completed | Load_575875 | Cardiff Hall - 210 | Jul 9, 2026 10:26am | Jul 9, 2026 10:26am | Jul 9, 2026 1:49pm | Jul 9, 2026 1:49pm | Jul 9, 2026 1:49pm | Jul 9, 2026 1:49pm | Jul 9, 2026 1:49pm | Jul 9, 2026 1:49pm |  |  | Fair | No | PMR was out restored by maintenance
Outage | J.E.26.07.08800 | C001844342 | Roxroy Needham | St.Ann | Completed | Load_239552 | Cardiff Hall - 210 | Jul 9, 2026 10:26am | Jul 9, 2026 10:26am | Jul 9, 2026 1:47pm | Jul 9, 2026 1:47pm | Jul 9, 2026 1:47pm | Jul 9, 2026 1:47pm | Jul 9, 2026 1:48pm | Jul 9, 2026 1:48pm |  |  | Fair | No | PMR was out restored by maintenance
Outage | J.E.26.07.08845 | C001844341 | Roxroy Needham | St.Ann | Completed | Load_241608 | Cardiff Hall - 210 | Jul 9, 2026 10:26am | Jul 9, 2026 10:26am | Jul 9, 2026 1:48pm | Jul 9, 2026 1:48pm | Jul 9, 2026 1:48pm | Jul 9, 2026 1:48pm | Jul 9, 2026 1:49pm | Jul 9, 2026 1:49pm |  |  | Fair | No | PMR was out restored by maintenance
Outage | J.E.26.07.08874 | C001844343 | Roxroy Needham | St.Ann | Completed | Load_241005 | Cardiff Hall - 210 | Jul 9, 2026 10:26am | Jul 9, 2026 10:26am | Jul 9, 2026 10:55am | Jul 9, 2026 10:55am | Jul 9, 2026 11:31am | Jul 9, 2026 1:45pm | Jul 9, 2026 1:45pm | Jul 9, 2026 1:45pm |  |  | Fair | No | PMR was out restored by maintenance
Outage | J.E.26.07.08888 | C001844339 | Roxroy Needham | St.Ann | Completed | Load_248242 | Cardiff Hall - 210 | Jul 9, 2026 10:26am | Jul 9, 2026 10:26am | Jul 9, 2026 1:46pm | Jul 9, 2026 1:46pm | Jul 9, 2026 1:46pm | Jul 9, 2026 1:46pm | Jul 9, 2026 1:47pm | Jul 9, 2026 1:47pm |  |  | Fair | No | PMR was out restored by maintenance
Outage | J.E.26.07.08934 | C001844329 | Andrew Powell | Manchester | Completed | Load_259355 | Spur Tree - 210 | Jul 9, 2026 10:22am | Jul 9, 2026 3:31pm | Jul 9, 2026 5:03pm | Jul 9, 2026 5:03pm | Jul 9, 2026 5:52pm | Jul 9, 2026 6:13pm | Jul 9, 2026 6:15pm | Jul 9, 2026 6:15pm | BrokenWire |  | SevereWind | No | Splice and tension broken service wire at secondary line 3 wire using 15 feet #6 triplex and one clamp, voltage reading 116v-116v phase to neutral 232v cross phase.
Outage | J.E.26.07.08716 | C001844315 | Daniel Francis | St.Ann | Completed | Load_238405 | Roaring River - 210 | Jul 9, 2026 10:12am | Jul 9, 2026 1:07pm | Jul 9, 2026 3:30pm | Jul 9, 2026 3:30pm | Jul 9, 2026 4:39pm | Jul 9, 2026 5:13pm | Jul 9, 2026 5:17pm | Jul 9, 2026 5:17pm | BrokenWire |  | Fair | No | Found common neutral dislodge re anchor by using 1#2 preform and two one bolt clamps
Outage | J.E.26.07.08807 | C001844308 | Oshane Warren | Westmoreland | Completed | Load_260069 | Paradise - 210 | Jul 9, 2026 10:08am | Jul 9, 2026 10:26am | Jul 9, 2026 5:03pm | Jul 9, 2026 5:03pm | Jul 9, 2026 5:03pm | Jul 9, 2026 5:03pm | Jul 9, 2026 5:04pm | Jul 9, 2026 5:04pm |  |  | Fair | No | Unable to locate or contact customer
Outage | J.E.26.07.08784 | C001844298 | Denton Williams | Portland | Completed | Load_263895 | Port Antonio - 410 | Jul 9, 2026 10:02am | Jul 9, 2026 10:54am | Jul 9, 2026 12:10pm | Jul 9, 2026 12:10pm | Jul 9, 2026 12:10pm | Jul 9, 2026 12:11pm | Jul 9, 2026 12:15pm | Jul 9, 2026 12:15pm |  |  | LandSlide | No | Remove bamboo from line and close 3 30 amp tripsaver
Outage | J.E.26.07.08129 | C001844266 | Edward Royal | KSAS | Completed | Load_266177 | Three Miles - 410 | Jul 9, 2026 9:33am | Jul 9, 2026 9:33am | Jul 9, 2026 11:46am | Jul 9, 2026 11:46am | Jul 9, 2026 11:46am | Jul 9, 2026 11:46am | Jul 9, 2026 11:46am | Jul 9, 2026 11:46am |  |  | Fair | No | Call related
Outage | J.E.26.07.08649 | C001844249 | Richard Watson | St.Elizabeth | Completed | Load_265624 | Maggotty - 110 | Jul 9, 2026 9:16am | Jul 9, 2026 9:19am | Jul 9, 2026 12:16pm | Jul 9, 2026 12:16pm | Jul 9, 2026 1:41pm | Jul 9, 2026 2:53pm | Jul 9, 2026 3:17pm | Jul 9, 2026 3:17pm |  |  | Fair | No | Voltage found at customer meter 99v, 104v, 203v, voltage taken at transformer location 104v, 106v, 210v and load reading 39amp X2 phase, 50amp X1 phase and 7.3amp through Neutral, Voltage regulators to be commissioned soon to correct low voltage on primary.
Non-Outage | J.E.26.07.07884 | C001844248 | Elvis Trowers | KSAN | Completed | Load_267483 | Washington Blvd - 610 | Jul 9, 2026 9:15am | Jul 9, 2026 9:15am | Jul 9, 2026 12:52pm | Jul 9, 2026 12:52pm | Jul 9, 2026 12:53pm | Jul 9, 2026 1:03pm | Jul 9, 2026 1:04pm | Jul 9, 2026 1:04pm |  |  | Fair | Yes | Customer was found having single phasing when checked and dislodged twisted wire phase was found and reconnect with one clamp, voltage when checked was left at 118+117=235 volts.
Non-Outage | J.E.26.07.05711 | C001844243 | Elvis Trowers | KSAN | Completed | Load_268870 | Washington Blvd - 610 | Jul 9, 2026 9:14am | Jul 9, 2026 9:14am | Jul 9, 2026 1:31pm | Jul 9, 2026 1:31pm | Jul 9, 2026 1:41pm | Jul 9, 2026 2:20pm | Jul 9, 2026 2:20pm | Jul 9, 2026 2:20pm |  |  | Fair | Yes | Customer was found having fluctuating voltages when checked and corroded joints was found at pat head, rap joints was replaced with 3 one bolt clamps, voltage when checked was left at 117+118=235 volts
Non-Outage | J.E.26.07.06755 | C001844244 | Elvis Trowers | KSAN | Completed | Load_265506 | Washington Blvd - 610 | Jul 9, 2026 9:14am | Jul 9, 2026 9:14am | Jul 9, 2026 2:22pm | Jul 9, 2026 2:22pm | Jul 9, 2026 2:52pm | Jul 9, 2026 2:57pm | Jul 9, 2026 2:57pm | Jul 9, 2026 2:57pm | Fire | Y | Fair | Yes | No sparks or fire was seen upon arrival, except for some primary bushings needs to be done.
Outage | J.E.26.07.08628 | C001844242 | Elvis Trowers | KSAN | Completed | Load_254220 | Washington Blvd - 610 | Jul 9, 2026 9:13am | Jul 9, 2026 9:13am | Jul 9, 2026 11:10am | Jul 9, 2026 11:10am | Jul 9, 2026 11:23am | Jul 9, 2026 11:25am | Jul 9, 2026 11:25am | Jul 9, 2026 11:25am |  |  | Fair | Yes | Premises checked and found ok, customer was also spoken with however he suggested that the power supply was restored from earlier.
Outage | J.E.26.07.08610 | C001844241 | Christopher Edwards | KSAN | Completed | Load_259305 | Constant Spring - 410 | Jul 9, 2026 9:12am | Jul 9, 2026 9:12am | Jul 9, 2026 10:34am | Jul 9, 2026 10:34am | Jul 9, 2026 11:23am | Jul 9, 2026 11:42am | Jul 9, 2026 11:44am | Jul 9, 2026 11:44am | BrokenWire |  | Fair | No | Tree burst down customer service line Unable to re run service wireDue to trees on customer premises needs to be cutCustomer was advised to clear tree before service can be restored
Outage | J.E.26.07.07990 | C001844238 | Edward Royal | KSAS | Completed | Load_262511 | Three Miles - 410 | Jul 9, 2026 9:08am | Jul 9, 2026 9:09am | Jul 9, 2026 11:38am | Jul 9, 2026 11:38am | Jul 9, 2026 11:38am | Jul 9, 2026 11:46am | Jul 9, 2026 11:46am | Jul 9, 2026 11:46am |  |  | Fair | No | HEXin caught on fire hexin need to be change reffered to field service transformer still ok box # HEX 01074
Outage | J.E.26.07.08668 | C001844237 | Raymond Carr | St.Mary | Completed | Load_352644 | Oracabessa - 110 | Jul 9, 2026 9:05am | Jul 9, 2026 10:51am | Jul 9, 2026 11:23am | Jul 9, 2026 11:23am | Jul 9, 2026 12:22pm | Jul 9, 2026 12:32am | Jul 9, 2026 12:49pm | Jul 9, 2026 12:49pm | LeakingTransformer |  | Flood | No | Blown junction fuse found at pole number 0013384, line patrol and found a 15 kva transformer fuse found blown, after several test same was found to be defective. Two customers are affected, kindly refer to maintenance department for replacement.
Non-Outage | J.E.26.07.08414 | C001844231 | Denton Williams | Portland | Completed | Load_255161 | Port Antonio - 410 | Jul 9, 2026 9:03am | Jul 9, 2026 10:49am | Jul 9, 2026 3:33pm | Jul 9, 2026 3:33pm | Jul 9, 2026 3:33pm | Jul 9, 2026 3:33pm | Jul 9, 2026 3:36pm | Jul 9, 2026 3:36pm | Fire | Y | Fair | No | The customer stated that the area was windy which resulting tree contact with primary lines. Customer supply is okay. Area need de-bushing.
Non-Outage | J.E.26.07.07265 | C001844230 | Andrae Clarke | Portland | Completed | Load_267555 | Port Antonio - 410 | Jul 9, 2026 9:01am | Jul 9, 2026 9:09am | Jul 9, 2026 12:14pm | Jul 9, 2026 12:14pm | Jul 9, 2026 12:14pm | Jul 9, 2026 12:46pm | Jul 9, 2026 1:11pm | Jul 9, 2026 1:11pm |  |  | Rains | No | Changed burnt wire 50 ft of wire two ones bold claims Check voltage 106/105/211
Non-Outage | J.E.26.07.07655 | C001844228 | Andrae Clarke | Portland | Completed | Load_260631 | Port Antonio - 410 | Jul 9, 2026 9:01am | Jul 9, 2026 9:20am | Jul 9, 2026 1:13pm | Jul 9, 2026 1:13pm | Jul 9, 2026 1:35pm | Jul 9, 2026 2:16pm | Jul 9, 2026 2:03pm | Jul 9, 2026 2:03pm |  |  | Fair | No | Premises found okCheck voltage 121/123/244
Non-Outage | J.E.26.07.08118 | C001844227 | Andrae Clarke | Portland | Completed | Load_238553 | Port Antonio - 310 | Jul 9, 2026 9:01am | Jul 10, 2026 8:07am | Jul 10, 2026 11:01am | Jul 10, 2026 11:01am | Jul 10, 2026 11:01am | Jul 10, 2026 11:00am | Jul 10, 2026 11:05am | Jul 10, 2026 11:05am |  |  | Fair | No | Lead from transformer neede cleaning Emergency crew needed Voltage 236/115/120
Non-Outage | J.E.26.07.08530 | C001844226 | Andrae Clarke | Portland | Completed | Load_251129 | Port Antonio - 410 | Jul 9, 2026 9:01am | Jul 9, 2026 9:20am | Jul 9, 2026 2:55pm | Jul 9, 2026 2:56pm | Jul 9, 2026 3:15pm | Jul 9, 2026 3:22pm | Jul 9, 2026 3:17pm | Jul 9, 2026 3:17pm |  |  | Fair | No | Transformer pole needs cleaning Refer to Emergency 121/117/236
Non-Outage | J.E.26.07.08618 | C001844223 | Andrae Clarke | Portland | Completed | Load_267555 | Port Antonio - 410 | Jul 9, 2026 9:01am | Jul 9, 2026 9:20am | Jul 9, 2026 9:27am | Jul 9, 2026 9:27am | Jul 9, 2026 11:31am | Jul 9, 2026 11:48am | Jul 9, 2026 12:14pm | Jul 9, 2026 12:14pm |  |  | Rains | No | Repair corroded wires use two one bolt clamp clamps Check voltage 119
Non-Outage | J.E.26.07.07226 | C001844219 | Rochaine Hussey | KSAN | Completed | Load_265414 | Constant Spring - 210 | Jul 9, 2026 8:58am | Jul 9, 2026 8:58am | Jul 9, 2026 1:38pm | Jul 9, 2026 1:38pm | Jul 9, 2026 1:38pm | Jul 9, 2026 1:39pm | Jul 9, 2026 1:40pm | Jul 9, 2026 1:40pm |  |  | Fair | No | Customer was called multiple times No answer Unable to locate
Non-Outage | J.E.26.07.07696 | C001844218 | Rochaine Hussey | KSAN | Completed | Load_257446 | Constant Spring - 210 | Jul 9, 2026 8:58am | Jul 9, 2026 8:58am | Jul 9, 2026 1:49pm | Jul 9, 2026 1:59pm | Jul 9, 2026 2:02pm | Jul 9, 2026 2:32pm | Jul 9, 2026 2:32pm | Jul 9, 2026 2:32pm |  |  | Fair | No | Service wire was checkNo issue was found on pole or pothead Voltage at premises found ok117/115/233v
Non-Outage | J.E.26.07.07801 | C001844220 | Rochaine Hussey | KSAN | Completed | Load_250328 | Constant Spring - 210 | Jul 9, 2026 8:58am | Jul 9, 2026 8:58am | Jul 9, 2026 2:34pm | Jul 9, 2026 2:40pm | Jul 9, 2026 2:40pm | Jul 9, 2026 2:41pm | Jul 9, 2026 2:41pm | Jul 9, 2026 2:41pm |  |  | Fair | No | Customer said issue was already resolved
Non-Outage | J.E.26.07.07987 | C001844221 | Rochaine Hussey | KSAN | Completed | Load_257446 | Constant Spring - 210 | Jul 9, 2026 8:58am | Jul 9, 2026 8:58am | Jul 9, 2026 2:45pm | Jul 9, 2026 3:43pm | Jul 9, 2026 3:43pm | Jul 9, 2026 3:44pm | Jul 9, 2026 3:48pm | Jul 9, 2026 3:48pm |  |  | Fair | No | Bucket needed to check slicing sleeve Between pole#039502 and 060962Voltage from transformer 117/115/233vVoltage behind slicing sleeve 117/95Bucket truck needed More than one customer affected
Non-Outage | J.E.26.07.08054 | C001844222 | Rochaine Hussey | KSAN | Completed | Load_257446 | Constant Spring - 210 | Jul 9, 2026 8:58am | Jul 9, 2026 8:58am | Jul 9, 2026 2:32pm | Jul 9, 2026 2:32pm | Jul 9, 2026 2:32pm | Jul 9, 2026 2:34pm | Jul 9, 2026 2:34pm | Jul 9, 2026 2:34pm |  |  | Fair | No | Voltage at meter found ok115/117/233vCustomer was called multiple times no answer
Non-Outage | J.E.26.07.06976 | C001844217 | Rochaine Hussey | KSAN | Completed | Load_244592 | Constant Spring - 210 | Jul 9, 2026 8:57am | Jul 9, 2026 8:58am | Jul 9, 2026 12:31pm | Jul 9, 2026 12:32pm | Jul 9, 2026 12:38pm | Jul 9, 2026 1:26pm | Jul 9, 2026 1:27pm | Jul 9, 2026 1:27pm |  |  | Fair | No | Corrosion on pothead 1clamp used Issue resolved 115/117/232v
Non-Outage | J.E.26.07.07280 | C001844216 | Andre Smith | KSAS | Completed | Load_243491 | Duhaney - 310 | Jul 9, 2026 8:57am | Jul 9, 2026 8:57am | Jul 10, 2026 8:11am | Jul 10, 2026 8:11am | Jul 10, 2026 10:17am | Jul 10, 2026 10:28am | Jul 10, 2026 10:28am | Jul 10, 2026 10:28am | Fire |  | Fair | No | Customer complaint about streetlights not working
Outage | J.E.26.07.08632 | C001844215 | Damion Reid | Manchester | Completed | Load_242761 | Kendal - 210 | Jul 9, 2026 8:56am | Jul 9, 2026 8:56am | Jul 9, 2026 9:17am | Jul 9, 2026 9:17am | Jul 9, 2026 12:26pm | Jul 9, 2026 1:19pm | Jul 9, 2026 1:21pm | Jul 9, 2026 1:21pm |  |  | Rains | No | Reconnect service wire for 3 wire service that was disconnected for repairs using 70ft of #6 triplex service wire 3 one bolt clamp and 3 pen union
Non-Outage | J.E.26.07.07292 | C001844211 | Oraine Minto | St.Ann | Completed | Load_269625 | Roaring River - 410 | Jul 9, 2026 8:55am | Jul 9, 2026 8:56am | Jul 9, 2026 11:33am | Jul 9, 2026 11:39am | Jul 9, 2026 11:39am | Jul 9, 2026 1:47pm | Jul 9, 2026 1:48pm | Jul 9, 2026 1:48pm |  |  | Fair | No | 1 one bolt was used Issue resolved
Non-Outage | J.E.26.07.07432 | C001844209 | Oraine Minto | St.Ann | Completed | Load_248191 | Roaring River - 210 | Jul 9, 2026 8:55am | Jul 9, 2026 8:55am | Jul 9, 2026 2:05pm | Jul 9, 2026 2:05pm | Jul 9, 2026 2:07pm | Jul 9, 2026 2:08pm | Jul 9, 2026 2:08pm | Jul 9, 2026 2:08pm |  |  | Fair | No | Refer to maintenance
Non-Outage | J.E.26.07.07549 | C001844210 | Oraine Minto | St.Ann | Completed | Load_246075 | Roaring River - 410 | Jul 9, 2026 8:55am | Jul 9, 2026 8:56am | Jul 9, 2026 1:49pm | Jul 9, 2026 1:49pm | Jul 9, 2026 1:49pm | Jul 9, 2026 1:50pm | Jul 9, 2026 1:50pm | Jul 9, 2026 1:50pm |  |  | Fair | No | Refer to emergency All customer affected
Non-Outage | J.E.26.07.07856 | C001844213 | Oraine Minto | St.Ann | Completed | Load_239944 | Roaring River - 410 | Jul 9, 2026 8:55am | Jul 9, 2026 8:56am | Jul 9, 2026 2:09pm | Jul 9, 2026 2:10pm | Jul 9, 2026 2:10pm | Jul 9, 2026 2:10pm | Jul 9, 2026 2:11pm | Jul 9, 2026 2:11pm |  |  | Fair | No | Customer states that the issue was resolved
Non-Outage | J.E.26.07.07932 | C001844212 | Oraine Minto | St.Ann | Completed | Load_246075 | Roaring River - 410 | Jul 9, 2026 8:55am | Jul 9, 2026 8:56am | Jul 9, 2026 11:35am | Jul 9, 2026 11:36am | Jul 9, 2026 11:36am | Jul 9, 2026 11:39am | Jul 9, 2026 11:39am | Jul 9, 2026 11:39am |  |  | Fair | No | Refer to emergency Customer states that someone came yesterday but from he left the voltage is fluctuating and that is affecting the entire area
Outage | J.E.26.07.08637 | C001844203 | Marlon Authors | St.Elizabeth | Completed | Load_256341 | Maggotty - 210 | Jul 9, 2026 8:54am | Jul 9, 2026 8:54am | Jul 9, 2026 11:35am | Jul 9, 2026 11:35am | Jul 9, 2026 1:01pm | Jul 9, 2026 1:09pm | Jul 9, 2026 1:10pm | Jul 9, 2026 1:10pm |  |  | Fair | No | Supply checked and found service wire neutral broken at pothead. Splice and retention same using one feet of # conductor and two clamps.. supply leave working ok rdg 115v,116v and cross phased 231 volts
Non-Outage | J.E.26.07.07589 | C001844202 | Richard Watson | St.Elizabeth | Completed | Load_292191 | Maggotty - 110 | Jul 9, 2026 8:53am | Jul 9, 2026 8:53am | Jul 9, 2026 10:23am | Jul 9, 2026 12:11pm | Jul 9, 2026 12:11pm | Jul 9, 2026 12:11pm | Jul 9, 2026 12:13pm | Jul 9, 2026 12:13pm |  |  | Fair | No | Customer contacted by phone and stated that the supply was restored from yesterday.
Non-Outage | J.E.26.07.08592 | C001844201 | Richard Watson | St.Elizabeth | Completed | Load_237715 | Maggotty - 110 | Jul 9, 2026 8:52am | Jul 9, 2026 8:52am | Jul 9, 2026 10:23am | Jul 9, 2026 10:23am | Jul 9, 2026 10:54am | Jul 9, 2026 12:01pm | Jul 9, 2026 12:07pm | Jul 9, 2026 12:07pm | BrokenPole |  | Fair | No | Splice and retention two spans of broken secondary neutral, cause but truck tipping off aggregate, use approximately 50ft of #2 aluminum conductor, one #2 splicing sleeve and one #2 preform, supply restored to area.
Non-Outage | J.E.26.07.07606 | C001844200 | Tyrese Williams | St.Ann | Completed | Load_249546 | Cardiff Hall - 310 | Jul 9, 2026 8:50am | Jul 9, 2026 8:52am | Jul 9, 2026 9:40am | Jul 9, 2026 9:41am | Jul 9, 2026 9:41am | Jul 9, 2026 9:42am | Jul 9, 2026 9:42am | Jul 9, 2026 9:42am | Fire |  | Rains | No | Premises found ok customer said the problem was resolved
Non-Outage | J.E.26.07.07495 | C001844194 | Andrew Powell | Manchester | Completed | Load_266906 | Spur Tree - 210 | Jul 9, 2026 8:49am | Jul 9, 2026 3:31pm | Jul 9, 2026 4:49pm | Jul 9, 2026 4:49pm | Jul 9, 2026 4:49pm | Jul 9, 2026 4:49pm | Jul 9, 2026 4:50pm | Jul 9, 2026 4:50pm | BrokenWire |  | Fair | No | Premises found okay customer stated that fault resolved last night.
Non-Outage | J.E.26.07.07518 | C001844192 | Marlon Authors | null | Completed | null | null | Jul 9, 2026 8:49am | Jul 9, 2026 8:53am | Jul 9, 2026 1:39pm | Jul 9, 2026 1:40pm | Jul 9, 2026 1:40pm | Jul 9, 2026 1:41pm | Jul 9, 2026 1:41pm | Jul 9, 2026 1:41pm | Fire |  | Fair | No | Customer said supply was fixed
Non-Outage | J.E.26.07.08019 | C001844193 | Cliton Henry | St.Mary | Completed | Load_262038 | Blackstonedge - 110 | Jul 9, 2026 8:49am | Jul 9, 2026 10:36am | Jul 9, 2026 6:29pm | Jul 9, 2026 6:29pm | Jul 9, 2026 6:29pm | Jul 9, 2026 6:31pm | Jul 9, 2026 6:31pm | Jul 9, 2026 6:31pm |  |  | Fair | No | The customer stated that the supply is ok, Theon and was related to the feeder cycling earlier today.
Non-Outage | J.E.26.06.36659 | C001844182 | Fitzroy Turner | KSAN | Completed | Load_259801 | Washington Blvd - 710 | Jul 9, 2026 8:48am | Jul 9, 2026 8:49am | Jul 9, 2026 9:47am | Jul 9, 2026 9:47am | Jul 9, 2026 9:55am | Jul 9, 2026 9:55am | Jul 9, 2026 9:55am | Jul 9, 2026 9:55am |  |  | Fair | No | Customer premises found with electricity supply
Non-Outage | J.E.26.07.05216 | C001844187 | Andrae Dawkins | St.James | Completed | Load_239243 | Queens Drive - 710 | Jul 9, 2026 8:48am | Jul 9, 2026 8:49am | Jul 9, 2026 4:03pm | Jul 9, 2026 4:07pm | Jul 9, 2026 4:07pm | Jul 9, 2026 1:23pm | Jul 9, 2026 4:08pm | Jul 9, 2026 4:08pm |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.07.05749 | C001844181 | Andrae Dawkins | St.James | Completed | Load_264284 | Bogue - 310 | Jul 9, 2026 8:48am | Jul 9, 2026 8:49am | Jul 9, 2026 12:31pm | Jul 9, 2026 12:31pm | Jul 9, 2026 12:31pm | Jul 9, 2026 12:33pm | Jul 9, 2026 12:42pm | Jul 9, 2026 12:42pm |  |  | Fair | No | Found customer meter burnt and needs to be replaced refer back to field service
Non-Outage | J.E.26.07.05831 | C001844186 | Andrae Dawkins | St.James | Completed | Load_1002045 | Queens Drive - 710 | Jul 9, 2026 8:48am | Jul 9, 2026 8:49am | Jul 9, 2026 8:59am | Jul 9, 2026 10:41am | Jul 9, 2026 11:27am | Jul 9, 2026 12:00pm | Jul 9, 2026 12:22pm | Jul 9, 2026 12:22pm |  |  | Fair | No | Check and found okay voltage found 116/115/232
Non-Outage | J.E.26.07.06415 | C001844188 | Andrae Dawkins | St.James | Completed | Load_260177 | Queens Drive - 710 | Jul 9, 2026 8:48am | Jul 9, 2026 8:49am | Jul 9, 2026 4:03pm | Jul 9, 2026 4:05pm | Jul 9, 2026 4:05pm | Jul 9, 2026 1:03pm | Jul 9, 2026 4:07pm | Jul 9, 2026 4:07pm |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.07.06683 | C001844189 | Fitzroy Turner | KSAN | Completed | Load_259248 | Washington Blvd - 310 | Jul 9, 2026 8:48am | Jul 9, 2026 8:49am | Jul 9, 2026 1:05pm | Jul 9, 2026 1:21pm | Jul 9, 2026 1:21pm | Jul 9, 2026 1:22pm | Jul 9, 2026 1:23pm | Jul 9, 2026 1:23pm |  |  | Fair | No | Found breaker found trip customer advised to have breaker reset
Non-Outage | J.E.26.07.07742 | C001844190 | Andrae Dawkins | St.James | Completed | Load_253173 | Queens Drive - 710 | Jul 9, 2026 8:48am | Jul 9, 2026 8:49am | Jul 9, 2026 4:03pm | Jul 9, 2026 4:03pm | Jul 9, 2026 4:03pm | Jul 9, 2026 12:47pm | Jul 9, 2026 4:05pm | Jul 9, 2026 4:05pm |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.07.08389 | C001844183 | Andrae Dawkins | St.James | Completed | Load_302142 | Queens Drive - 710 | Jul 9, 2026 8:48am | Jul 9, 2026 8:49am | Jul 9, 2026 8:59am | Jul 9, 2026 10:22am | Jul 9, 2026 10:23am | Jul 9, 2026 10:29am | Jul 9, 2026 10:29am | Jul 9, 2026 10:29am |  |  | Fair | No | Check and found ok customer said that the power came back
Non-Outage | J.E.26.07.08391 | C001844184 | Andrae Dawkins | St.James | Completed | Load_238603 | Queens Drive - 710 | Jul 9, 2026 8:48am | Jul 9, 2026 8:49am | Jul 9, 2026 8:59am | Jul 9, 2026 12:24pm | Jul 9, 2026 12:25pm | Jul 9, 2026 10:46am | Jul 9, 2026 12:26pm | Jul 9, 2026 12:26pm |  |  | Fair | No | Check and found ok power already came back
Non-Outage | J.E.26.07.08433 | C001844185 | Andrae Dawkins | St.James | Completed | Load_259518 | Queens Drive - 710 | Jul 9, 2026 8:48am | Jul 9, 2026 8:49am | Jul 9, 2026 8:59am | Jul 9, 2026 10:18am | Jul 9, 2026 10:18am | Jul 9, 2026 9:43am | Jul 9, 2026 10:22am | Jul 9, 2026 10:22am |  |  | Fair | No | Check and found ok customer said that the power came back last night
Non-Outage | J.E.26.02.43497 | C001844178 | Andrae Dawkins | St.James | Completed | Load_262334 | Bogue - 310 | Jul 9, 2026 8:47am | Jul 9, 2026 8:49am | Jul 9, 2026 4:03pm | Jul 9, 2026 4:08pm | Jul 9, 2026 4:08pm | Jul 9, 2026 1:54pm | Jul 9, 2026 4:09pm | Jul 9, 2026 4:09pm |  |  | Fair | No | Check and found okay
Non-Outage | J.E.26.07.00543 | C001844180 | Fitzroy Turner | KSAN | Completed | Load_293564 | Washington Blvd - 710 | Jul 9, 2026 8:47am | Jul 9, 2026 8:49am | Jul 9, 2026 9:12am | Jul 9, 2026 9:40am | Jul 9, 2026 9:41am | Jul 9, 2026 9:41am | Jul 9, 2026 9:42am | Jul 9, 2026 9:42am |  |  | Fair | No | Customer premises found with electricity supply. Issue was resolved earlier
Non-Outage | J.E.26.07.00708 | C001844179 | Fitzroy Turner | KSAN | Completed | Load_267773 | Washington Blvd - 710 | Jul 9, 2026 8:47am | Jul 9, 2026 8:49am | Jul 9, 2026 9:58am | Jul 9, 2026 9:58am | Jul 9, 2026 9:59am | Jul 9, 2026 9:59am | Jul 9, 2026 9:59am | Jul 9, 2026 9:59am |  |  | Fair | No | Customer premises found with electricity supply
Non-Outage | J.E.26.07.01852 | C001844177 | Fitzroy Turner | KSAN | Completed | Load_241754 | Washington Blvd - 710 | Jul 9, 2026 8:47am | Jul 9, 2026 8:49am | Jul 9, 2026 11:58am | Jul 9, 2026 11:58am | Jul 9, 2026 12:25pm | Jul 9, 2026 12:41pm | Jul 9, 2026 12:42pm | Jul 9, 2026 12:42pm |  |  | Fair | No | Found three wire service phase corroded at pothead use one clamp to carry repairs supply restored
Non-Outage | J.E.26.07.06742 | C001844176 | Fitzroy Turner | KSAN | Completed | Load_251103 | Washington Blvd - 710 | Jul 9, 2026 8:47am | Jul 9, 2026 8:49am | Jul 9, 2026 10:14am | Jul 9, 2026 10:19am | Jul 9, 2026 10:55am | Jul 9, 2026 10:55am | Jul 9, 2026 11:08am | Jul 9, 2026 11:08am |  |  | Fair | No | Found 4wire service neutral burnt off at meter pole use two one bolt clamps and one ft of service wire to carry out repair supply restored to customer
Non-Outage | J.E.26.07.07726 | C001844175 | Marlon Authors | St.Elizabeth | Completed | Load_237787 | Maggotty - 210 | Jul 9, 2026 8:47am | Jul 9, 2026 8:51am | Jul 9, 2026 9:17am | Jul 9, 2026 9:17am | Jul 9, 2026 10:52am | Jul 9, 2026 11:30am | Jul 9, 2026 11:31am | Jul 9, 2026 11:31am |  |  | Fair | No | Supply checked and found one fuse holder that protects 100 kva transformer in banker three damaged. Replace same and use one 5 amp fuse. Restored supply ok
Non-Outage | J.E.26.07.08274 | C001844174 | Andrae Dawkins | St.James | Completed | Load_575863 | Bogue - 410 | Jul 9, 2026 8:47am | Jul 9, 2026 8:49am | Jul 9, 2026 4:03pm | Jul 9, 2026 4:10pm | Jul 9, 2026 4:10pm | Jul 9, 2026 2:17pm | Jul 9, 2026 4:13pm | Jul 9, 2026 4:13pm |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.08613 | C001844168 | Denton Williams | Portland | Completed | Load_240419 | Port Antonio - 410 | Jul 9, 2026 8:43am | Jul 9, 2026 8:44am | Jul 9, 2026 10:17am | Jul 9, 2026 10:52am | Jul 9, 2026 10:52am | Jul 9, 2026 12:03pm | Jul 9, 2026 12:05pm | Jul 9, 2026 12:05pm |  | Y | Fair | No | Remove bamboo from 3phase line and close three 30 amp tripsaver. All customers are res
Non-Outage | J.E.26.07.07835 | C001844164 | Hopeton Henry | null | Completed | null | null | Jul 9, 2026 8:41am | Jul 9, 2026 8:41am | Jul 9, 2026 8:49am | Jul 9, 2026 9:35am | Jul 9, 2026 9:35am | Jul 9, 2026 9:35am | Jul 9, 2026 9:36am | Jul 9, 2026 9:36am | BrokenWire |  | Fair | Yes | Bushing required, maintenance is aware
Non-Outage | J.E.26.07.08042 | C001844165 | Hopeton Henry | St.Thomas | Completed | Load_329870 | Lysson - 410 | Jul 9, 2026 8:41am | Jul 9, 2026 8:43am | Jul 9, 2026 8:49am | Jul 9, 2026 3:30pm | Jul 9, 2026 3:31pm | Jul 9, 2026 3:45pm | Jul 9, 2026 3:46pm | Jul 9, 2026 3:46pm |  |  | Fair | No | Refuse Transformer at bank of 3 transformers, no pole number
Non-Outage | J.E.26.07.08114 | C001844167 | Hopeton Henry | St.Thomas | Completed | Load_239111 | Lysson - 410 | Jul 9, 2026 8:41am | Jul 9, 2026 8:43am | Jul 9, 2026 8:49am | Jul 9, 2026 5:14pm | Jul 9, 2026 5:14pm | Jul 9, 2026 5:14pm | Jul 9, 2026 5:15pm | Jul 9, 2026 5:15pm |  |  | Fair | No | Check and found ok, issue was related to previous outage
Non-Outage | J.E.26.06.29689 | C001844161 | Hopeton Henry | St.James | Completed | Load_302381 | Bogue - 510 | Jul 9, 2026 8:40am | Jul 9, 2026 8:41am | Jul 9, 2026 8:49am | Jul 9, 2026 9:39am | Jul 9, 2026 9:39am | Jul 9, 2026 9:40am | Jul 9, 2026 9:40am | Jul 9, 2026 9:40am |  |  | Fair | No | Send to st James dispatch
Non-Outage | J.E.26.07.08281 | C001844156 | Junior Scarlett | St.James | Completed | Load_267492 | Bogue - 610 | Jul 9, 2026 8:40am | Jul 9, 2026 8:43am | Jul 9, 2026 8:53am | Jul 9, 2026 11:39am | Jul 9, 2026 12:40pm | Jul 9, 2026 1:59am | Jul 9, 2026 2:37pm | Jul 9, 2026 2:37pm |  |  | Fair | No | Refer to RPD Install tow clamp on poleToo much illegal connections on the line causes voltage dropVoltage found 109v 98v 224v
Non-Outage | J.E.26.07.08325 | C001844162 | Hopeton Henry | St.Thomas | Completed | Load_266684 | Good Year - 210 | Jul 9, 2026 8:40am | Jul 9, 2026 8:41am | Jul 9, 2026 8:49am | Jul 9, 2026 9:36am | Jul 9, 2026 9:36am | Jul 9, 2026 9:39am | Jul 9, 2026 9:39am | Jul 9, 2026 9:39am |  |  | Fair | No | Bushing required, maintenance is aware
Non-Outage | J.E.26.07.08345 | C001844153 | Junior Scarlett | St.James | Completed | Load_247713 | Bogue - 610 | Jul 9, 2026 8:40am | Jul 9, 2026 8:43am | Jul 9, 2026 8:53am | Jul 9, 2026 9:25am | Jul 9, 2026 9:39am | Jul 9, 2026 9:42am | Jul 9, 2026 10:42am | Jul 9, 2026 10:42am |  |  | Fair | No | Install 3 clamp on poleVoltage found 115v 116v 231vVoltage leave 115v 115v 230vJob completed
Non-Outage | J.E.26.07.08360 | C001844154 | Junior Scarlett | St.James | Completed | Load_247713 | Bogue - 610 | Jul 9, 2026 8:40am | Jul 9, 2026 8:43am | Jul 9, 2026 8:53am | Jul 9, 2026 10:43am | Jul 9, 2026 10:48am | Jul 9, 2026 11:26am | Jul 9, 2026 11:24am | Jul 9, 2026 11:24am |  |  | Fair | No | Install two clamp on poleVoltage found 115 115v 230vVoltage leave 115v 115 230v
Non-Outage | J.E.26.07.08363 | C001844157 | Hopeton Henry | St.Thomas | Completed | Load_246479 | Good Year - 210 | Jul 9, 2026 8:40am | Jul 9, 2026 8:41am | Jul 9, 2026 8:49am | Jul 9, 2026 9:44am | Jul 9, 2026 10:29am | Jul 9, 2026 12:09pm | Jul 9, 2026 12:09pm | Jul 9, 2026 12:09pm | Fire | Y | Fair | No | Cut tree and reconnect transformer drop lead
Non-Outage | J.E.26.07.08421 | C001844155 | Junior Scarlett | St.James | Completed | Load_240027 | Bogue - 610 | Jul 9, 2026 8:40am | Jul 9, 2026 8:43am | Jul 9, 2026 8:53am | Jul 9, 2026 2:38pm | Jul 9, 2026 2:38pm | Jul 9, 2026 3:37pm | Jul 9, 2026 3:39pm | Jul 9, 2026 3:39pm |  |  | Fair | No | Corrosion at pole and pothead wire burn offInstall 6 clampVoltage found 187v 98v 238vVoltage leave 113v 113v 226vJob completed
Non-Outage | J.E.26.07.08105 | C001844150 | Royston Montague | St.Catherine | Completed | Load_568938 | Twickenham - 310 | Jul 9, 2026 8:36am | Jul 9, 2026 8:36am | Jul 9, 2026 8:39am | Jul 9, 2026 8:46am | Jul 9, 2026 9:24am | Jul 9, 2026 9:41am | Jul 9, 2026 9:44am | Jul 9, 2026 9:44am |  |  | Fair | No | Customer over growth tree damage one leg of twisted wire #6, customer ask to make arrangement to get tree cut and ask for a disconnection during that time.
Outage | J.E.26.07.08128 | C001844134 | Marlon Brown | Trelawny | Completed | Load_250973 | Martha Brae - 110 | Jul 9, 2026 8:33am | Jul 9, 2026 8:34am | Jul 9, 2026 10:49am | Jul 9, 2026 10:49am | Jul 9, 2026 11:05am | Jul 9, 2026 11:28am | Jul 9, 2026 11:28am | Jul 9, 2026 11:28am |  |  | Rains | No | Clean and remake joint at pole, use 1 pg clampVoltage found 116/45Voltage leaving 116/115=231.
Outage | J.E.26.07.08547 | C001844141 | Marlon Brown | Trelawny | Completed | Load_265828 | Duncans - 110 | Jul 9, 2026 8:33am | Jul 9, 2026 8:34am | Jul 9, 2026 9:57am | Jul 9, 2026 9:58am | Jul 9, 2026 10:19am | Jul 9, 2026 10:37am | Jul 9, 2026 10:37am | Jul 9, 2026 10:37am |  |  | Fair | No | Defective 50kva transformer please refer to O. Ellis.
Outage | J.E.26.07.08608 | C001844144 | Gregory Grossett | Portland | Completed | Load_253884 | Port Antonio - 410 | Jul 9, 2026 8:33am | Jul 9, 2026 3:55pm | Jul 9, 2026 7:22pm | Jul 9, 2026 7:22pm | Jul 9, 2026 7:22pm | Jul 9, 2026 7:22pm | Jul 9, 2026 7:23pm | Jul 9, 2026 7:23pm |  |  | Rains | No | 20amp junction fuse blown patrol line section then restore supply to the area suspected cause heavy rain and high wind.
Outage | J.E.26.07.08398 | C001844131 | Marlon Brown | Trelawny | Completed | Load_260629 | Duncans - 110 | Jul 9, 2026 8:32am | Jul 9, 2026 8:34am | Jul 9, 2026 9:01am | Jul 9, 2026 9:01am | Jul 9, 2026 9:24am | Jul 9, 2026 9:49am | Jul 9, 2026 9:49am | Jul 9, 2026 9:49am |  |  | Fair | No | Replaced 2amps 10kva transformer Voltage found 118/118/120=234/237/118/117/190=234/235/234v.
Non-Outage | J.E.26.01.26136 | C001844127 | Rayon Foster | Hanover | Completed | Load_1001406 | Orange Bay - 310 | Jul 9, 2026 8:25am | Jul 9, 2026 8:26am | Jul 9, 2026 10:50am | Jul 9, 2026 12:36pm | Jul 9, 2026 12:52pm | Jul 9, 2026 1:18pm | Jul 9, 2026 1:18pm | Jul 9, 2026 1:18pm |  |  | Fair | No | When spoke with customer they said they did not make any report
Non-Outage | J.E.26.06.27881 | C001844124 | Rayon Foster | Hanover | Completed | Load_248861 | Orange Bay - 310 | Jul 9, 2026 8:24am | Jul 9, 2026 8:26am | Jul 9, 2026 10:50am | Jul 9, 2026 11:43am | Jul 9, 2026 12:27pm | Jul 9, 2026 12:35pm | Jul 9, 2026 12:36pm | Jul 9, 2026 12:36pm |  |  | Fair | No | Check and found working ok customer said that the issue was already resolved
Outage | J.E.26.07.08590 | C001844126 | Rusean Allen | KSAS | Completed | Load_239591 | Cane River - 610 | Jul 9, 2026 8:24am | Jul 9, 2026 8:24am | Jul 9, 2026 10:31am | Jul 9, 2026 10:31am | Jul 9, 2026 10:36am | Jul 9, 2026 10:36am | Jul 9, 2026 10:37am | Jul 9, 2026 10:37am |  |  | Fair | No | Found okay
Non-Outage | J.E.26.07.06969 | C001844118 | Fredrick Hamilton | KSAN | Completed | Load_557676 | West Kings House - 310 | Jul 9, 2026 8:18am | Jul 9, 2026 8:19am | Jul 9, 2026 8:23am | Jul 9, 2026 8:27am | Jul 9, 2026 8:27am | Jul 9, 2026 8:28am | Jul 9, 2026 8:28am | Jul 9, 2026 8:28am |  |  | Fair | No | Please assign to emergency customer reported a blown transformer
Non-Outage | J.E.26.07.08036 | C001844121 | Fredrick Hamilton | KSAN | Completed | Load_257725 | Washington Blvd - 610 | Jul 9, 2026 8:18am | Jul 9, 2026 8:19am | Jul 9, 2026 8:23am | Jul 9, 2026 8:31am | Jul 9, 2026 9:21am | Jul 9, 2026 9:52am | Jul 9, 2026 9:52am | Jul 9, 2026 9:52am |  |  | Fair | No | Open neutral detected at pothead same was corrected Supply fully restored to premises
Non-Outage | J.E.26.07.08306 | C001844120 | Fredrick Hamilton | KSAN | Completed | Load_245677 | West Kings House - 210 | Jul 9, 2026 8:18am | Jul 9, 2026 8:19am | Jul 9, 2026 8:23am | Jul 9, 2026 10:31am | Jul 9, 2026 10:32am | Jul 9, 2026 10:41am | Jul 9, 2026 10:41am | Jul 9, 2026 10:41am |  |  | Fair | No | Fuse link open emergency requiredPole#0018849
Non-Outage | J.E.26.07.08535 | C001844119 | Fredrick Hamilton | KSAN | Completed | Load_257150 | West Kings House - 210 | Jul 9, 2026 8:18am | Jul 9, 2026 8:19am | Jul 9, 2026 8:23am | Jul 9, 2026 9:53am | Jul 9, 2026 10:10am | Jul 9, 2026 10:27am | Jul 9, 2026 10:27am | Jul 9, 2026 10:27am |  |  | Fair | No | Recommend emergency to follow up corrosion at pothead affecting customer CT metering at location
Non-Outage | J.E.26.01.26493 | C001844116 | Tajay Bernard | Hanover | Completed | Load_255167 | Orange Bay - 310 | Jul 9, 2026 8:17am | Jul 9, 2026 8:17am | Jul 9, 2026 8:28am | Jul 9, 2026 8:28am | Jul 9, 2026 8:50am | Jul 9, 2026 8:50am | Jul 9, 2026 8:51am | Jul 9, 2026 8:51am |  |  | Fair | No | Customer stated that the issue has been resolved
Non-Outage | J.E.26.02.02107 | C001844115 | Tajay Bernard | Hanover | Completed | Load_255167 | Orange Bay - 310 | Jul 9, 2026 8:16am | Jul 9, 2026 8:17am | Jul 9, 2026 8:51am | Jul 9, 2026 8:51am | Jul 9, 2026 8:51am | Jul 9, 2026 8:51am | Jul 9, 2026 8:52am | Jul 9, 2026 8:52am |  |  | Fair | No | Customer stated that the issue has been resolved
Non-Outage | J.E.26.07.07457 | C001844114 | Tajay Bernard | Hanover | Completed | Load_238061 | Orange Bay - 310 | Jul 9, 2026 8:16am | Jul 9, 2026 8:17am | Jul 9, 2026 8:52am | Jul 9, 2026 8:52am | Jul 9, 2026 8:52am | Jul 9, 2026 8:52am | Jul 9, 2026 8:52am | Jul 9, 2026 8:52am |  |  | Fair | No
Non-Outage | J.E.26.06.31838 | C001844111 | Orville Lee | St.Catherine | Completed | Load_1000333 | Twickenham - 210 | Jul 9, 2026 8:15am | Jul 9, 2026 8:16am | Jul 9, 2026 8:56am | Jul 9, 2026 2:27pm | Jul 9, 2026 2:45pm | Jul 9, 2026 3:21pm | Jul 9, 2026 3:24pm | Jul 9, 2026 3:24pm |  |  | Fair | No | Checks made and voltage readings 104V102V206VLine patrol and found multiple splice sleeve on secondary line Transformer may need topping up. Refer to bucket truck
Non-Outage | J.E.26.06.31959 | C001844110 | Orville Lee | St.Catherine | Completed | Load_269986 | Twickenham - 210 | Jul 9, 2026 8:15am | Jul 9, 2026 8:16am | Jul 9, 2026 8:56am | Jul 9, 2026 10:06am | Jul 9, 2026 10:10am | Jul 9, 2026 10:17am | Jul 9, 2026 10:18am | Jul 9, 2026 10:18am |  |  | Fair | No | Meter was changed Meter 3024151Voltage 116V117V234V
Non-Outage | J.E.26.06.32171 | C001844109 | Orville Lee | Portmore | Completed | Load_252357 | Naggo Head - 510 | Jul 9, 2026 8:15am | Jul 9, 2026 8:16am | Jul 9, 2026 8:56am | Jul 9, 2026 1:45pm | Jul 9, 2026 1:54pm | Jul 9, 2026 1:58pm | Jul 9, 2026 2:00pm | Jul 9, 2026 2:00pm |  |  | Fair | No | Issue appears to cause from a ring feed. Line patrol and found switch wire at junction disconnected Refer to maintenance team
Non-Outage | J.E.26.06.32185 | C001844108 | Moses Elliston | Portmore | Completed | Load_237940 | Naggo Head - 610 | Jul 9, 2026 8:15am | Jul 9, 2026 11:09am | Jul 9, 2026 11:53am | Jul 9, 2026 11:53am | Jul 9, 2026 11:53am | Jul 9, 2026 11:53am | Jul 9, 2026 12:08pm | Jul 9, 2026 12:08pm |  |  | Fair | No | For next crew
Non-Outage | J.E.26.06.34431 | C001844107 | Orville Lee | St.Catherine | Completed | Load_249167 | Twickenham - 210 | Jul 9, 2026 8:15am | Jul 9, 2026 8:16am | Jul 9, 2026 8:56am | Jul 9, 2026 10:32am | Jul 9, 2026 10:42am | Jul 9, 2026 11:00am | Jul 9, 2026 11:02am | Jul 9, 2026 11:02am |  |  | Fair | No | Checks made and found pothead connections corroded 4 Penn union used Voltage 116V117V234VPole 0027419 Badly leaned and causing secondary line to sag while pulling on customer Stantion
Non-Outage | J.E.26.06.34621 | C001844105 | Orville Lee | St.Catherine | Completed | Load_267622 | Twickenham - 210 | Jul 9, 2026 8:15am | Jul 9, 2026 8:16am | Jul 9, 2026 8:56am | Jul 9, 2026 3:25pm | Jul 9, 2026 3:33pm | Jul 9, 2026 3:34pm | Jul 9, 2026 3:35pm | Jul 9, 2026 3:35pm |  |  | Fair | No | Premises closed
Non-Outage | J.E.26.06.34821 | C001844106 | Orville Lee | St.Catherine | Completed | Load_241645 | Twickenham - 210 | Jul 9, 2026 8:15am | Jul 9, 2026 8:16am | Jul 9, 2026 8:56am | Jul 9, 2026 10:18am | Jul 9, 2026 10:23am | Jul 9, 2026 10:31am | Jul 9, 2026 10:31am | Jul 9, 2026 10:31am | LeaningPole |  | Fair | No | Pole 618664 rotten at the base and leaning on customer perimeter fencePole consist of 25Kv Transformer, open secondary and 3 take off to customers Refer to maintenance
Outage | J.E.26.07.08472 | C001844112 | Rayon Foster | Hanover | Completed | Load_257115 | Orange Bay - 310 | Jul 9, 2026 8:15am | Jul 9, 2026 9:06am | Jul 9, 2026 10:50am | Jul 9, 2026 11:02am | Jul 9, 2026 11:24am | Jul 9, 2026 11:36am | Jul 9, 2026 11:42am | Jul 9, 2026 11:42am |  |  | Fair | No | Check and found voltage working ok voltage found at pothead 122v/123v/245v customer was advised to get a electrician to do some internal checks
Outage | J.E.26.07.08583 | C001844104 | Marlon Authors | Manchester | Completed | Load_260083 | Spur Tree - 210 | Jul 9, 2026 8:15am | Jul 9, 2026 8:18am | Jul 9, 2026 9:09am | Jul 9, 2026 9:09am | Jul 9, 2026 9:09am | Jul 9, 2026 9:14am | Jul 9, 2026 9:15am | Jul 9, 2026 9:15am |  |  | Fair | No | Customer said supply is okay
Non-Outage | J.E.26.07.08474 | C001844102 | Elvis Trowers | KSAN | Completed | Load_249367 | Washington Blvd - 810 | Jul 9, 2026 8:14am | Jul 9, 2026 8:14am | Jul 9, 2026 9:16am | Jul 9, 2026 9:16am | Jul 9, 2026 9:52am | Jul 9, 2026 10:08am | Jul 9, 2026 10:08am | Jul 9, 2026 10:08am |  | Y | Fair | Yes | Disconnection was granted by disconnecting service wire on pole.
Non-Outage | J.E.26.07.02200 | C001844101 | Dwain Samuels | Westmoreland | Completed | Load_255089 | Paradise - 110 | Jul 9, 2026 8:13am | Jul 9, 2026 8:14am | Jul 9, 2026 8:50am | Jul 9, 2026 11:25am | Jul 9, 2026 11:25am | Jul 9, 2026 11:31am | Jul 9, 2026 11:31am | Jul 9, 2026 11:31am |  |  | Fair | No | Transformer fuse link down
Non-Outage | J.E.26.07.02703 | C001844100 | Dwain Samuels | Hanover | Completed | Load_266295 | Orange Bay - 310 | Jul 9, 2026 8:13am | Jul 9, 2026 8:14am | Jul 9, 2026 8:50am | Jul 10, 2026 9:37am | Jul 10, 2026 10:15am | Jul 10, 2026 10:54am | Jul 10, 2026 10:56am | Jul 10, 2026 10:56am |  |  | Fair | No | Corrosion found at 3 wire pole. Voltage check 101-100-201. Corrosion clear use 3 one bolt clamp. Voltage check 115-115-230
Non-Outage | J.E.26.07.07208 | C001844097 | Dwain Samuels | Westmoreland | Completed | Load_249211 | Paradise - 110 | Jul 9, 2026 8:13am | Jul 9, 2026 8:14am | Jul 9, 2026 8:50am | Jul 9, 2026 11:47am | Jul 9, 2026 11:53am | Jul 9, 2026 11:53am | Jul 9, 2026 12:14pm | Jul 9, 2026 12:14pm |  |  | Fair | No | Couldn’t locate premises. Need a proper contact and directions
Non-Outage | J.E.26.07.08258 | C001844099 | Dwain Samuels | Westmoreland | Completed | Load_258236 | Paradise - 110 | Jul 9, 2026 8:13am | Jul 9, 2026 8:14am | Jul 9, 2026 8:50am | Jul 9, 2026 9:13am | Jul 9, 2026 10:02am | Jul 9, 2026 10:13am | Jul 9, 2026 10:15am | Jul 9, 2026 10:15am |  |  | Fair | No | Meter socket found defective at premises
Non-Outage | J.E.26.07.08354 | C001844096 | Raymond Carr | null | Completed | null | null | Jul 9, 2026 8:13am | Jul 9, 2026 8:15am | Jul 9, 2026 10:55am | Jul 9, 2026 10:55am | Jul 9, 2026 11:19am | Jul 9, 2026 11:10am | Jul 9, 2026 11:20am | Jul 9, 2026 11:20am | BrokenWire |  | Rains | No | Several calls to contact number went straight to voicemail.
Non-Outage | J.E.26.07.08564 | C001844098 | Javid Vernon | Westmoreland | Completed | Load_253644 | Paradise - 310 | Jul 9, 2026 8:13am | Jul 10, 2026 7:36am | Jul 10, 2026 10:45am | Jul 10, 2026 10:45am | Jul 10, 2026 10:45am | Jul 10, 2026 10:47am | Jul 10, 2026 10:47am | Jul 10, 2026 10:47am |  |  | Fair | No | Customer stated that the issue has been resolved he got his electrician to check and they had an internal problem
Non-Outage | J.E.26.07.00377 | C001844095 | Odeanie Davis | KSAS | Completed | Load_239090 | Greenwich - 510 | Jul 9, 2026 8:12am | Jul 9, 2026 8:24am | Jul 9, 2026 9:54am | Jul 9, 2026 9:54am | Jul 9, 2026 9:54am | Jul 9, 2026 9:59am | Jul 9, 2026 9:55am | Jul 9, 2026 9:55am |  |  | Fair | No | 120v/120v & 240v under load at location, no power issue observed at this time,
Non-Outage | J.E.26.07.00380 | C001844094 | Odeanie Davis | KSAS | Completed | Load_239090 | Greenwich - 510 | Jul 9, 2026 8:12am | Jul 9, 2026 8:23am | Jul 9, 2026 9:39am | Jul 9, 2026 9:39am | Jul 9, 2026 9:42am | Jul 9, 2026 9:54am | Jul 9, 2026 9:54am | Jul 9, 2026 9:54am |  |  | Fair | No | 120v/120v & 240v under load at location, no power issue observed at this time,
Non-Outage | J.E.26.07.05999 | C001844093 | Error Coore | Manchester | Completed | Load_256281 | Spur Tree - 310 | Jul 9, 2026 8:12am | Jul 9, 2026 8:12am | Jul 10, 2026 8:34am | Jul 10, 2026 8:34am | Jul 10, 2026 9:12am | Jul 10, 2026 10:19am | Jul 10, 2026 10:19am | Jul 10, 2026 10:19am |  |  | Fair | No | Found customer with wrap connection at pothead remade phase and neutral using 3 one bolt clamp voltage reading 110/111/221 volts
Non-Outage | J.E.26.07.06008 | C001844092 | Error Coore | Manchester | Completed | Load_266810 | Spur Tree - 310 | Jul 9, 2026 8:11am | Jul 9, 2026 8:12am | Jul 10, 2026 3:17pm | Jul 10, 2026 3:17pm | Jul 10, 2026 3:43pm | Jul 10, 2026 3:51pm | Jul 10, 2026 3:53pm | Jul 10, 2026 3:53pm |  |  | Fair | No | Premise not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.06368 | C001844091 | Damion Reid | Manchester | Completed | Load_1002392 | Spur Tree - 310 | Jul 9, 2026 8:11am | Jul 10, 2026 7:34am | Jul 10, 2026 12:50pm | Jul 10, 2026 12:50pm | Jul 10, 2026 1:56pm | Jul 10, 2026 2:15pm | Jul 10, 2026 2:17pm | Jul 10, 2026 2:17pm |  |  | SevereWind | No | Remade corroded phase at secondary pole for 3 wire service using one 1 bolt clamp voltage reading at meter socket phase to neutral 116v-115v across phase 233v
Non-Outage | J.E.26.07.08264 | C001844087 | Damion Reid | Manchester | Completed | Load_292941 | Spur Tree - 310 | Jul 9, 2026 8:11am | Jul 10, 2026 7:30am | Jul 10, 2026 2:17pm | Jul 10, 2026 2:43pm | Jul 10, 2026 3:16pm | Jul 10, 2026 4:29pm | Jul 10, 2026 4:32pm | Jul 10, 2026 4:32pm |  |  | SevereWind | No | Premises found ok voltage reading at load side of meter socket phase to neutral 113v
Non-Outage | J.E.26.07.08283 | C001844089 | Odeanie Davis | KSAS | Completed | Load_269212 | Rockfort - 410 | Jul 9, 2026 8:11am | Jul 9, 2026 8:11am | Jul 9, 2026 10:28am | Jul 9, 2026 10:28am | Jul 9, 2026 10:42am | Jul 9, 2026 11:23am | Jul 9, 2026 11:24am | Jul 9, 2026 11:24am |  |  | Fair | No | 117v/90v at secondary line, dried vegetation on secondary line, 112v/112v & 225v at transformer, service wire needs to be changed, irregularities on secondary line, field service team needed, bucket truck needed.
Non-Outage | J.E.26.07.07120 | C001844085 | Error Coore | Manchester | Completed | Load_248521 | Spur Tree - 310 | Jul 9, 2026 8:10am | Jul 9, 2026 8:12am | Jul 10, 2026 10:20am | Jul 10, 2026 12:48pm | Jul 10, 2026 1:57pm | Jul 10, 2026 2:14pm | Jul 10, 2026 2:15pm | Jul 10, 2026 2:15pm |  |  | Fair | No | Premise found ok customer said that the problem was resolved
Outage | J.E.26.07.07896 | C001844069 | Barrington Brown | St.James | Completed | Load_254071 | Rose Hall - 210 | Jul 9, 2026 8:07am | Jul 9, 2026 8:08am | Jul 9, 2026 8:32am | Jul 9, 2026 8:35am | Jul 9, 2026 8:54am | Jul 9, 2026 8:55am | Jul 9, 2026 8:55am | Jul 9, 2026 8:55am |  |  | Fair | No | Checked and found ok
Outage | J.E.26.07.07920 | C001844075 | Barrington Brown | St.James | Completed | Load_239368 | Queens Drive - 310 | Jul 9, 2026 8:07am | Jul 9, 2026 8:08am | Jul 9, 2026 9:45am | Jul 9, 2026 9:45am | Jul 9, 2026 10:30am | Jul 9, 2026 11:06am | Jul 9, 2026 11:06am | Jul 9, 2026 11:06am |  |  | Fair | No | Check and found ok
Outage | J.E.26.07.07960 | C001844071 | Michael Christian | St.James | Completed | Load_240097 | Rose Hall - 210 | Jul 9, 2026 8:07am | Jul 9, 2026 4:08pm | Jul 9, 2026 5:27pm | Jul 9, 2026 5:27pm | Jul 9, 2026 6:49pm | Jul 9, 2026 7:09pm | Jul 9, 2026 7:09pm | Jul 9, 2026 7:09pm |  |  | Fair | No | Found 1 20 amp out replace no pole # cause by tee
Outage | J.E.26.07.07980 | C001844076 | Barrington Brown | St.James | Completed | Load_302647 | Bogue - 410 | Jul 9, 2026 8:07am | Jul 9, 2026 8:08am | Jul 9, 2026 8:56am | Jul 9, 2026 8:56am | Jul 9, 2026 9:33am | Jul 9, 2026 9:34am | Jul 9, 2026 9:44am | Jul 9, 2026 9:44am |  |  | Fair | No | Checked and found ok power was restored
Outage | J.E.26.07.07071 | C001844065 | Derrick Dawkins | St.James | Completed | Load_255304 | Bogue - 310 | Jul 9, 2026 8:04am | Jul 9, 2026 8:04am | Jul 9, 2026 10:12am | Jul 9, 2026 10:12am | Jul 9, 2026 10:57am | Jul 9, 2026 10:58am | Jul 9, 2026 10:58am | Jul 9, 2026 10:58am |  |  | Fair | No | No location was provided calls to customer went unanswered cannot locate
Outage | J.E.26.07.07163 | C001844068 | Oshane Warren | Westmoreland | Completed | Load_247636 | Paradise - 210 | Jul 9, 2026 8:04am | Jul 9, 2026 8:04am | Jul 9, 2026 11:09am | Jul 9, 2026 11:09am | Jul 9, 2026 1:21pm | Jul 9, 2026 2:36pm | Jul 9, 2026 2:42pm | Jul 9, 2026 2:42pm |  |  | Fair | No | Reconnect back service wire at secondary line
Outage | J.E.26.07.08312 | C001844067 | Hopeton Henry | St.Thomas | Completed | Load_261421 | Lysson - 410 | Jul 9, 2026 8:04am | Jul 9, 2026 8:05am | Jul 9, 2026 8:37am | Jul 9, 2026 1:05pm | Jul 9, 2026 3:10pm | Jul 9, 2026 3:28pm | Jul 9, 2026 3:29pm | Jul 9, 2026 3:29pm |  |  | Fair | No | Customer not located
Outage | J.E.26.07.08470 | C001844066 | Hopeton Henry | St.Thomas | Completed | Load_266684 | Good Year - 210 | Jul 9, 2026 8:04am | Jul 9, 2026 8:05am | Jul 9, 2026 8:37am | Jul 9, 2026 8:38am | Jul 9, 2026 9:06am | Jul 9, 2026 9:18am | Jul 9, 2026 9:23am | Jul 9, 2026 9:23am |  | Y | SevereWind | No | Found 2 spon broken secondary conductors , bushing required kindly refer to maintenance department
Outage | J.E.26.07.08291 | C001844063 | Edward Royal | KSAS | Completed | Load_291495 | Greenwich - 510 | Jul 9, 2026 8:03am | Jul 9, 2026 8:04am | Jul 9, 2026 12:12pm | Jul 9, 2026 12:12pm | Jul 9, 2026 12:12pm | Jul 9, 2026 1:21pm | Jul 9, 2026 1:21pm | Jul 9, 2026 1:21pm |  |  | Fair | No | Reset 15kva transformer
Outage | J.E.26.07.08539 | C001844062 | Edward Royal | KSAS | Completed | Load_267274 | Greenwich - 310 | Jul 9, 2026 8:03am | Jul 9, 2026 8:04am | Jul 9, 2026 10:50am | Jul 9, 2026 10:50am | Jul 9, 2026 10:50am | Jul 9, 2026 11:20am | Jul 9, 2026 11:20am | Jul 9, 2026 11:20am |  |  | Fair | No | Defective 100kva transformer need to be change reffered to maintenance pole #0051409.
Outage | J.E.26.07.08111 | C001844061 | Rusean Allen | KSAS | Completed | Load_556758 | Cane River - 410 | Jul 9, 2026 8:02am | Jul 9, 2026 8:02am | Jul 9, 2026 10:58am | Jul 9, 2026 10:58am | Jul 9, 2026 11:41am | Jul 9, 2026 11:52am | Jul 9, 2026 11:52am | Jul 9, 2026 11:52am |  |  | Fair | No | 1x 2amp fuse found 1x 15amp fuse replaced
Non-Outage | J.E.26.07.07252 | C001844056 | Rusean Allen | KSAS | Completed | Load_244933 | Hunts Bay - 810 | Jul 9, 2026 8:01am | Jul 9, 2026 8:02am | Jul 9, 2026 9:09am | Jul 9, 2026 9:09am | Jul 9, 2026 10:03am | Jul 9, 2026 10:04am | Jul 9, 2026 10:04am | Jul 9, 2026 10:04am | BrokenWire |  | Fair | No | Problem was already resolved
Non-Outage | J.E.26.07.07524 | C001844059 | Rusean Allen | KSAS | Completed | Load_556749 | Cane River - 410 | Jul 9, 2026 8:01am | Jul 9, 2026 8:02am | Jul 9, 2026 11:08am | Jul 9, 2026 11:52am | Jul 9, 2026 11:54am | Jul 9, 2026 11:54am | Jul 9, 2026 11:55am | Jul 9, 2026 11:55am |  |  | Fair | No | Found okay. Voltage: 115 115 229
Non-Outage | J.E.26.07.08293 | C001844055 | Rusean Allen | KSAS | Completed | Load_269212 | Rockfort - 410 | Jul 9, 2026 8:01am | Jul 9, 2026 8:02am | Jul 9, 2026 10:05am | Jul 9, 2026 10:05am | Jul 9, 2026 10:18am | Jul 9, 2026 10:20am | Jul 9, 2026 10:20am | Jul 9, 2026 10:20am |  |  | Fair | No | Excessive illegal connections needs to be removed.
Outage | J.E.26.07.07639 | C001844060 | Romeo Brissett | St.James | Completed | Load_292538 | Bogue - 610 | Jul 9, 2026 8:01am | Jul 9, 2026 8:02am | Jul 9, 2026 8:13am | Jul 9, 2026 8:13am | Jul 9, 2026 8:58am | Jul 9, 2026 9:15am | Jul 9, 2026 9:32am | Jul 9, 2026 9:32am |  |  | Fair | No | Line patrolled and found power in the area, neighbors stated it’s streetlight they reporting about.
Outage | J.E.26.07.07899 | C001844058 | Romeo Brissett | St.James | Completed | Load_240161 | Bogue - 610 | Jul 9, 2026 8:01am | Jul 9, 2026 8:02am | Jul 9, 2026 9:32am | Jul 9, 2026 9:32am | Jul 9, 2026 9:40am | Jul 9, 2026 9:50am | Jul 9, 2026 9:58am | Jul 9, 2026 9:58am |  |  | Fair | No | Check and found pump running, Voltage reading 236-237-240-409-411-415
Outage | J.E.26.07.08545 | C001844057 | Romeo Brissett | St.James | Completed | Load_268384 | Bogue - 610 | Jul 9, 2026 8:01am | Jul 9, 2026 8:02am | Jul 9, 2026 9:58am | Jul 9, 2026 9:58am | Jul 9, 2026 10:18am | Jul 9, 2026 11:27am | Jul 9, 2026 11:32am | Jul 9, 2026 11:32am | Fire |  | Rains | No | Found secondary broken due to illegal connections, Isolated (1)25 kva transformer Removed illegal connection, spliced and retention secondary and reset (1)25
Non-Outage | J.E.26.07.08380 | C001844053 | Rusean Allen | KSAS | Completed | Load_267551 | Cane River - 410 | Jul 9, 2026 8:00am | Jul 9, 2026 8:02am | Jul 9, 2026 10:52am | Jul 9, 2026 10:52am | Jul 9, 2026 10:54am | Jul 9, 2026 10:55am | Jul 9, 2026 10:56am | Jul 9, 2026 10:56am |  |  | Fair | No | Unable to locate premises.
Non-Outage | J.E.26.07.08407 | C001844052 | Rusean Allen | KSAS | Completed | Load_253645 | Cane River - 310 | Jul 9, 2026 8:00am | Jul 9, 2026 8:02am | Jul 9, 2026 11:19am | Jul 9, 2026 11:55am | Jul 9, 2026 12:04pm | Jul 9, 2026 12:05pm | Jul 9, 2026 12:05pm | Jul 9, 2026 12:05pm |  |  | Fair | No | Premises found locked.voltage: 117 115 231
Outage | J.E.26.07.08542 | C001844054 | Richard Watson | St.Elizabeth | Completed | Load_266765 | Maggotty - 110 | Jul 9, 2026 8:00am | Jul 9, 2026 8:02am | Jul 9, 2026 8:15am | Jul 9, 2026 8:15am | Jul 9, 2026 9:17am | Jul 9, 2026 10:01am | Jul 9, 2026 10:14am | Jul 9, 2026 10:14am |  |  | Fair | No | Found blown 1amp fuse for 15kva transformer no pole#, transformer found to be defective with hexing system, hexing# HEX01859, HX17473432. Please refer to Mr Delroy Crew for replacement& Clint Johnson for replacement.
Outage | J.E.26.07.07433 | C001844051 | Hartley Chin | Clarendon | Completed | Load_294648 | Monymusk - 210 | Jul 9, 2026 7:59am | Jul 9, 2026 7:59am | Jul 9, 2026 8:11am | Jul 9, 2026 9:33am | Jul 9, 2026 10:00am | Jul 9, 2026 10:03am | Jul 9, 2026 10:08am | Jul 9, 2026 10:08am |  |  | Fair | No | Found okay .. customer supply was restored yesterday…
Non-Outage | J.E.26.07.08288 | C001844050 | Milton Charlton | KSAN | Completed | Load_573544 | Hope - 410 | Jul 9, 2026 7:58am | Jul 9, 2026 7:59am | Jul 9, 2026 10:04am | Jul 9, 2026 10:08am | Jul 9, 2026 10:59am | Jul 9, 2026 10:40am | Jul 9, 2026 11:02am | Jul 9, 2026 11:02am |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.07.06434 | C001844048 | Richard Nicholas | St.Catherine | Completed | Load_248658 | Rhodens Pen - 210 | Jul 9, 2026 7:57am | Jul 9, 2026 7:58am | Jul 9, 2026 8:50am | Jul 9, 2026 8:50am | Jul 9, 2026 9:52am | Jul 9, 2026 10:43am | Jul 9, 2026 10:44am | Jul 9, 2026 10:44am |  |  | Fair | No | Found ok
Outage | J.E.26.07.08260 | C001844047 | Romaine Roberts | St.Mary | Completed | Load_267206 | Highgate - 210 | Jul 9, 2026 7:57am | Jul 9, 2026 8:52am | Jul 9, 2026 9:12am | Jul 9, 2026 9:12am | Jul 9, 2026 9:12am | Jul 9, 2026 9:13am | Jul 9, 2026 9:13am | Jul 9, 2026 9:13am |  |  | Fair | No | Junction fuse found blown patrol line and found 25 kva transformer defective oil leak out one circuit is left out, replace 15 amp and one 20 amp to restore sone supply
Outage | J.E.26.07.08317 | C001844049 | Richard Nicholas | St.Catherine | Completed | Load_556341 | Rhodens Pen - 210 | Jul 9, 2026 7:57am | Jul 9, 2026 7:58am | Jul 9, 2026 10:45am | Jul 9, 2026 10:45am | Jul 9, 2026 11:33am | Jul 9, 2026 11:49am | Jul 9, 2026 11:52am | Jul 9, 2026 11:52am |  |  | Fair | No | Found ok
Non-Outage | J.E.26.07.07818 | C001844040 | Derrick Dawkins | null | Completed | null | null | Jul 9, 2026 7:54am | Jul 9, 2026 7:58am | Jul 9, 2026 9:56am | Jul 9, 2026 9:59am | Jul 9, 2026 9:59am | Jul 9, 2026 10:00am | Jul 9, 2026 10:00am | Jul 9, 2026 10:00am |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.07.07841 | C001844042 | Derrick Dawkins | null | Completed | null | null | Jul 9, 2026 7:54am | Jul 9, 2026 7:58am | Jul 9, 2026 8:57am | Jul 9, 2026 10:00am | Jul 9, 2026 10:00am | Jul 9, 2026 10:01am | Jul 9, 2026 10:01am | Jul 9, 2026 10:01am |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.07.07934 | C001844028 | Milton Charlton | KSAN | Completed | Load_255959 | West Kings House - 410 | Jul 9, 2026 7:54am | Jul 9, 2026 7:55am | Jul 9, 2026 8:47am | Jul 9, 2026 8:47am | Jul 9, 2026 10:03am | Jul 9, 2026 9:45am | Jul 9, 2026 10:04am | Jul 9, 2026 10:04am | BrokenWire |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.07.07384 | C001844045 | Evan Spaulding | St.Mary | Completed | Load_265922 | Highgate - 210 | Jul 9, 2026 7:54am | Jul 9, 2026 8:21am | Jul 9, 2026 8:27am | Jul 9, 2026 8:27am | Jul 9, 2026 8:27am | Jul 9, 2026 8:27am | Jul 9, 2026 8:28am | Jul 9, 2026 8:28am |  |  | Fair | No | Power was restored yesterday.
Outage | J.E.26.07.07399 | C001844046 | Evan Spaulding | St.Mary | Completed | Load_264015 | Highgate -110 | Jul 9, 2026 7:54am | Jul 9, 2026 8:20am | Jul 9, 2026 9:50am | Jul 9, 2026 10:58am | Jul 9, 2026 10:58am | Jul 9, 2026 12:02pm | Jul 9, 2026 12:04pm | Jul 9, 2026 12:04pm | Fire |  | SevereWind | No | Splice and retention secondary conductors using 120ft #2 AAAC conductor,2-2/0 preform,3-1 bolt clamps and replace 1-2amps Transformer fuse,no pole number.
Outage | J.E.26.07.07895 | C001844035 | Derrick Dawkins | St.James | Completed | Load_243318 | Bogue - 610 | Jul 9, 2026 7:54am | Jul 9, 2026 7:58am | Jul 9, 2026 8:56am | Jul 9, 2026 9:58am | Jul 9, 2026 9:58am | Jul 9, 2026 9:59am | Jul 9, 2026 9:59am | Jul 9, 2026 9:59am |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.08177 | C001844041 | Derrick Dawkins | St.James | Completed | Load_245082 | Bogue - 310 | Jul 9, 2026 7:54am | Jul 9, 2026 7:58am | Jul 9, 2026 10:59am | Jul 9, 2026 10:59am | Jul 9, 2026 11:05am | Jul 9, 2026 11:06am | Jul 9, 2026 11:08am | Jul 9, 2026 11:08am |  |  | Fair | No | Premises checked found ok
Outage | J.E.26.07.08233 | C001844043 | Neckell Ormsby | St.Mary | Completed | Load_244250 | Highgate - 210 | Jul 9, 2026 7:54am | Jul 9, 2026 4:12pm | Jul 9, 2026 4:18pm | Jul 9, 2026 4:18pm | Jul 9, 2026 4:46pm | Jul 9, 2026 5:44pm | Jul 9, 2026 6:15pm | Jul 9, 2026 6:15pm |  |  | Rains | No | Found fuse blown for 25 kva transformer patrol and found tree on secondary, cut and remove tree retention secondary neutral and replace 1-3amp fuse
Outage | J.E.26.07.08333 | C001844039 | Derrick Dawkins | St.James | Completed | Load_301724 | Bogue - 310 | Jul 9, 2026 7:54am | Jul 9, 2026 7:58am | Jul 9, 2026 11:09am | Jul 9, 2026 2:24pm | Jul 9, 2026 2:24pm | Jul 9, 2026 2:36pm | Jul 9, 2026 2:36pm | Jul 9, 2026 2:36pm |  |  | Fair | No | Checked and found ok
Outage | J.E.26.07.08134 | C001844023 | Derrick Dawkins | St.James | Completed | Load_237906 | Rose Hall - 210 | Jul 9, 2026 7:53am | Jul 9, 2026 7:58am | Jul 9, 2026 8:09am | Jul 9, 2026 8:09am | Jul 9, 2026 9:56am | Jul 9, 2026 8:55am | Jul 9, 2026 9:58am | Jul 9, 2026 9:58am |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.08502 | C001844021 | Richard Grant | St.Catherine | Completed | Load_252028 | New Michelton - 210 | Jul 9, 2026 7:53am | Jul 9, 2026 7:53am | Jul 9, 2026 12:37pm | Jul 9, 2026 12:37pm | Jul 9, 2026 1:24pm | Jul 9, 2026 1:58pm | Jul 9, 2026 1:58pm | Jul 9, 2026 1:58pm | BrokenWire |  | Fair | No | Corrosion found at pole. 1 onebolt clamp used to correct fault. Supply restored and premises left okay.
Outage | J.E.26.07.08538 | C001844022 | Richard Grant | St.Catherine | Completed | Load_248407 | New Michelton - 410 | Jul 9, 2026 7:53am | Jul 9, 2026 7:53am | Jul 9, 2026 8:38am | Jul 9, 2026 8:39am | Jul 9, 2026 10:00am | Jul 9, 2026 12:37pm | Jul 9, 2026 12:37pm | Jul 9, 2026 12:37pm | BrokenWire | Y | Fair | No | 2 pole span of broken opened secondary phases and neutral found caused by tree being cut down onto line by JPS bushing contractor. 4 sleeves, 2 preform, 3 onebolt clamps, approximately 50ft #2 wire and approximately 30ft 2/0 wire used to retention wire. Supply restored and area left okay.
Outage | J.E.26.07.07281 | C001844020 | Nickolas Rodriques | St.Catherine | Completed | Load_1000955 | Tredegar - 410 | Jul 9, 2026 7:52am | Jul 9, 2026 7:53am | Jul 9, 2026 12:34pm | Jul 9, 2026 12:43pm | Jul 9, 2026 1:28pm | Jul 9, 2026 2:08pm | Jul 9, 2026 2:10pm | Jul 9, 2026 2:10pm |  |  | Fair | No | Unable to locate or communicate with this specific customer after several attempts. However, the area was patrolled and no noticeable outage was found.
Outage | J.E.26.07.08524 | C001844019 | Nickolas Rodriques | St.Catherine | Completed | Load_258086 | Tredegar - 310 | Jul 9, 2026 7:52am | Jul 9, 2026 7:53am | Jul 9, 2026 9:20am | Jul 9, 2026 9:34am | Jul 9, 2026 10:34am | Jul 9, 2026 10:54am | Jul 9, 2026 11:02am | Jul 9, 2026 11:02am |  |  | Fair | No | Checked and found a 30 amp junction fuse blown. Patrol and found tree contacting with primary line. Repaired by removing the tree limb and replaced the fuse after conducting patrols.
Outage | J.E.26.07.08525 | C001844018 | Nickolas Rodriques | St.Catherine | Completed | Load_254602 | Tredegar - 310 | Jul 9, 2026 7:52am | Jul 9, 2026 7:53am | Jul 9, 2026 11:02am | Jul 9, 2026 11:05am | Jul 9, 2026 11:05am | Jul 9, 2026 11:08am | Jul 9, 2026 11:20am | Jul 9, 2026 11:20am |  |  | Fair | No | Checked and found a 30 amp junction fuse blown. Patrol and found tree contacting with primary line. Repaired by removing the tree limb and replaced the fuse after completing patrol.
Outage | J.E.26.07.08557 | C001844016 | Ryan Richards | Manchester | Completed | Load_249300 | Spur Tree - 310 | Jul 9, 2026 7:52am | Jul 9, 2026 7:53am | Jul 9, 2026 12:30pm | Jul 9, 2026 12:30pm | Jul 9, 2026 12:30pm | Jul 9, 2026 12:31pm | Jul 9, 2026 12:32pm | Jul 9, 2026 12:32pm |  |  | Fair | No | Same as the other 3 span of secondary neutral splice and retention and spot bushing carried out
Outage | J.E.26.07.08329 | C001844015 | Milton Charlton | KSAN | Completed | Load_243463 | Hope - 510 | Jul 9, 2026 7:51am | Jul 9, 2026 7:51am | Jul 9, 2026 11:02am | Jul 9, 2026 11:02am | Jul 9, 2026 11:52am | Jul 9, 2026 11:15am | Jul 9, 2026 11:53am | Jul 9, 2026 11:53am |  |  | Fair | No | Reconnect customer by J.P.S. Escalation.
Outage | J.E.26.07.06750 | C001844011 | Rodclif Dawkins | Portmore | Completed | Load_243381 | Naggo Head - 610 | Jul 9, 2026 7:50am | Jul 9, 2026 3:40pm | Jul 9, 2026 5:30pm | Jul 9, 2026 5:51pm | Jul 9, 2026 6:11pm | Jul 9, 2026 6:12pm | Jul 9, 2026 6:12pm | Jul 9, 2026 6:12pm |  |  | Fair | No | Customer found. Okay.
Outage | J.E.26.07.07576 | C001844013 | Wan Carlos Scarlett | St.Catherine | Completed | Load_289246 | Twickenham - 210 | Jul 9, 2026 7:50am | Jul 9, 2026 7:51am | Jul 9, 2026 8:02am | Jul 9, 2026 8:02am | Jul 9, 2026 9:53am | Jul 9, 2026 10:00am | Jul 9, 2026 10:03am | Jul 9, 2026 10:03am |  |  | Fair | No | Found customer with internal problem customer breaker defective advised customer to contact licensed electrician readings from pothead 116 116 232
Outage | J.E.26.07.08070 | C001844008 | Romaine Roberts | St.Mary | Completed | Load_238891 | Annotto Bay - 310 | Jul 9, 2026 7:50am | Jul 9, 2026 4:15pm | Jul 9, 2026 7:32pm | Jul 9, 2026 8:58pm | Jul 9, 2026 10:32pm | Jul 9, 2026 10:33pm | Jul 9, 2026 10:35pm | Jul 9, 2026 10:35pm |  |  | Fair | No | High wind and vegetation blow junction fuse patrol line and clear tree from line and replace 8 amp junction power restore no pole number
Outage | J.E.26.07.08245 | C001844012 | Wan Carlos Scarlett | St.Catherine | Completed | Load_253883 | Twickenham - 210 | Jul 9, 2026 7:50am | Jul 9, 2026 7:51am | Jul 9, 2026 9:55am | Jul 10, 2026 10:18am | Jul 10, 2026 10:57am | Jul 10, 2026 11:52am | Jul 10, 2026 11:53am | Jul 10, 2026 11:53am |  |  | Fair | No | Found customer 3 wire service at pole with one of the phase corroded use one bolt clamp at open secondary line phase readings 115-114-230
Outage | J.E.26.07.08429 | C001844009 | Wan Carlos Scarlett | St.Catherine | Completed | Load_267622 | Twickenham - 210 | Jul 9, 2026 7:50am | Jul 9, 2026 7:51am | Jul 9, 2026 10:04am | Jul 9, 2026 10:04am | Jul 9, 2026 11:08am | Jul 9, 2026 12:14pm | Jul 9, 2026 12:19pm | Jul 9, 2026 12:19pm |  |  | Fair | No | Found 20ft of # 2 north twisted wire damage replaced 20ft of # 2 north twisted wire use 8 one bolt clamps at pole readings to 116-117-234
Outage | J.E.26.07.08485 | C001844010 | Wan Carlos Scarlett | Portmore | Completed | Load_257303 | Naggo Head - 510 | Jul 9, 2026 7:50am | Jul 9, 2026 7:51am | Jul 9, 2026 11:45am | Jul 10, 2026 11:53am | Jul 10, 2026 12:29pm | Jul 10, 2026 12:59pm | Jul 10, 2026 1:01pm | Jul 10, 2026 1:01pm |  |  | Fair | No | Hexing service box customer getting single phasing coming from the hexing call refer to Moses
Outage | J.E.26.07.07374 | C001844006 | Christopher Edwards | KSAN | Completed | Load_243251 | Constant Spring - 410 | Jul 9, 2026 7:49am | Jul 9, 2026 7:49am | Jul 9, 2026 8:04am | Jul 9, 2026 8:43am | Jul 9, 2026 9:49am | Jul 9, 2026 10:33am | Jul 9, 2026 10:34am | Jul 9, 2026 10:34am | TreeContact,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Refuse blown junction fuseUsing (1) 20 ampsAlso clear bamboo off primary line
Outage | J.E.26.07.08471 | C001844003 | Raymond Lewis | Clarendon | Completed | Load_354502 | May Pen - 110 | Jul 9, 2026 7:47am | Jul 9, 2026 9:51am | Jul 9, 2026 11:42am | Jul 9, 2026 11:42am | Jul 9, 2026 12:25pm | Jul 9, 2026 12:48pm | Jul 9, 2026 12:48pm | Jul 9, 2026 12:48pm |  |  | SevereWind | No | Refuse and close 50amp junction
Outage | J.E.26.07.08475 | C001844002 | Raymond Lewis | Clarendon | Completed | Load_246998 | May Pen - 110 | Jul 9, 2026 7:47am | Jul 9, 2026 9:51am | Jul 9, 2026 12:48pm | Jul 9, 2026 12:48pm | Jul 9, 2026 12:48pm | Jul 9, 2026 12:49pm | Jul 9, 2026 12:49pm | Jul 9, 2026 12:49pm |  |  | SevereWind | No | Supply restored
Outage | J.E.26.07.07871 | C001843998 | Raymond Carr | St.Ann | Completed | Load_243350 | Upper White River - 110 | Jul 9, 2026 7:46am | Jul 9, 2026 7:47am | Jul 9, 2026 8:29am | Jul 9, 2026 8:29am | Jul 9, 2026 10:51am | Jul 9, 2026 9:19am | Jul 9, 2026 10:53am | Jul 9, 2026 10:53am |  |  | Flood | No | Several calls to contact number went unanswered.
Outage | J.E.26.07.08020 | C001843996 | Cliton Henry | St.Mary | Completed | Load_262319 | Blackstonedge - 110 | Jul 9, 2026 7:46am | Jul 9, 2026 10:36am | Jul 9, 2026 4:33pm | Jul 9, 2026 4:33pm | Jul 9, 2026 4:59pm | Jul 9, 2026 5:04pm | Jul 9, 2026 5:05pm | Jul 9, 2026 5:05pm |  |  | Fair | No | A blown 20 amp junction fuse found at Waterford pole #091352. Supply restored using 1-20 amp fuse.
Outage | J.E.26.07.08112 | C001843997 | Raymond Carr | St.Mary | Completed | Load_350137 | Oracabessa - 210 | Jul 9, 2026 7:46am | Jul 9, 2026 7:47am | Jul 9, 2026 3:16pm | Jul 9, 2026 3:16pm | Jul 9, 2026 3:16pm | Jul 9, 2026 2:56am | Jul 9, 2026 3:18pm | Jul 9, 2026 3:18pm |  |  | Fair | No | No access to rammy box.
Outage | J.E.26.07.08276 | C001843992 | Raymond Carr | St.Mary | Completed | Load_241403 | Oracabessa - 210 | Jul 9, 2026 7:46am | Jul 9, 2026 7:47am | Jul 9, 2026 2:23pm | Jul 9, 2026 2:23pm | Jul 9, 2026 2:49pm | Jul 9, 2026 2:57pm | Jul 9, 2026 3:09pm | Jul 9, 2026 3:09pm |  |  | Fair | No | No access to rammy box.
Outage | J.E.26.07.08541 | C001843990 | Raymond Carr | St.Mary | Completed | Load_245218 | Oracabessa - 110 | Jul 9, 2026 7:46am | Jul 9, 2026 7:47am | Jul 9, 2026 12:50pm | Jul 9, 2026 12:50pm | Jul 9, 2026 1:07pm | Jul 9, 2026 1:00pm | Jul 9, 2026 1:09pm | Jul 9, 2026 1:09pm |  |  | Rains | No | Broken secondary conductors found, however area requires heavy bushing. Transformer was opened to make safe. Refer to maintenance department.
Non-Outage | J.E.26.07.07408 | C001843989 | Raymond Lewis | null | Completed | null | null | Jul 9, 2026 7:44am | Jul 9, 2026 7:44am | Jul 9, 2026 8:52am | Jul 9, 2026 8:52am | Jul 9, 2026 9:59am | Jul 9, 2026 9:55am | Jul 9, 2026 10:03am | Jul 9, 2026 10:03am |  |  | Rains | No | Customer complained about bill going up,please refer to field service
Outage | J.E.26.07.07175 | C001843987 | Hartley Chin | Clarendon | Completed | Load_574467 | Parnassus - 310 | Jul 9, 2026 7:42am | Jul 9, 2026 7:43am | Jul 9, 2026 7:49am | Jul 9, 2026 8:39am | Jul 9, 2026 8:51am | Jul 9, 2026 8:55am | Jul 9, 2026 8:56am | Jul 9, 2026 8:56am |  |  | SevereWind | No | Premisis found ok. Customer stated supply was restored from last night.
Outage | J.E.26.07.08204 | C001843984 | Hartley Chin | Clarendon | Completed | Load_238944 | Parnassus - 210 | Jul 9, 2026 7:42am | Jul 9, 2026 7:43am | Jul 9, 2026 7:49am | Jul 9, 2026 10:38am | Jul 9, 2026 10:38am | Jul 9, 2026 10:43am | Jul 9, 2026 10:53am | Jul 9, 2026 10:53am |  |  | Fair | No | Isolate 25 KVA transformer @ pole # 0112654 due to broken open secondary neutral found in 1 span ,… Note : Span of neutral was missing … replace approximately 120 ft #2 Conductor, re-energized transformer… use 2 clamp , 120 ft #2 Conductor…
Outage | J.E.26.07.08244 | C001843985 | Hartley Chin | Clarendon | Completed | Load_257776 | Parnassus - 310 | Jul 9, 2026 7:42am | Jul 9, 2026 7:43am | Jul 9, 2026 7:49am | Jul 9, 2026 8:56am | Jul 9, 2026 8:56am | Jul 9, 2026 9:29am | Jul 9, 2026 9:31am | Jul 9, 2026 9:31am | BrokenWire |  | SevereWind | No | Isolate 25KVA transformer @ pole # 0125507 due to broken open secondary phase found in 1 span , broken phase repaired, re-energized transformer… use : 10 ft #2 Conductor, 2 clamp , 1 - #2 preform …
Outage | J.E.26.07.08466 | C001843983 | Hartley Chin | Clarendon | Completed | Load_257434 | Parnassus - 210 | Jul 9, 2026 7:42am | Jul 9, 2026 7:43am | Jul 9, 2026 8:34am | Jul 9, 2026 8:34am | Jul 9, 2026 8:34am | Jul 9, 2026 8:34am | Jul 9, 2026 8:34am | Jul 9, 2026 8:34am |  |  | Fair | No | Wrong parish… St . Catherine..
Non-Outage | J.E.26.07.07598 | C001843980 | Daniel Francis | null | Completed | null | null | Jul 9, 2026 7:37am | Jul 9, 2026 11:40am | Jul 9, 2026 11:51am | Jul 9, 2026 11:51am | Jul 9, 2026 11:52am | Jul 9, 2026 12:00pm | Jul 9, 2026 12:00pm | Jul 9, 2026 12:00pm |  |  | Rains | No | Please refer to field service customer have issues adding credit
Non-Outage | J.E.26.07.07621 | C001843981 | Tyrese Williams | null | Completed | null | null | Jul 9, 2026 7:37am | Jul 9, 2026 7:43am | Jul 9, 2026 9:47am | Jul 9, 2026 1:22pm | Jul 9, 2026 1:22pm | Jul 9, 2026 1:25pm | Jul 9, 2026 1:25pm | Jul 9, 2026 1:25pm |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.07.07181 | C001843979 | Tyrese Williams | St.Ann | Completed | Load_269493 | Cardiff Hall - 310 | Jul 9, 2026 7:36am | Jul 9, 2026 7:38am | Jul 9, 2026 1:44pm | Jul 9, 2026 5:16pm | Jul 9, 2026 6:03pm | Jul 9, 2026 6:11pm | Jul 9, 2026 6:11pm | Jul 9, 2026 6:11pm |  |  | Fair | No | Customer said he didn’t make any report
Outage | J.E.26.07.07395 | C001843978 | Tyrese Williams | St.Ann | Completed | Load_252558 | Cardiff Hall - 310 | Jul 9, 2026 7:36am | Jul 9, 2026 7:36am | Jul 9, 2026 9:44am | Jul 9, 2026 1:21pm | Jul 9, 2026 1:21pm | Jul 9, 2026 1:22pm | Jul 9, 2026 1:22pm | Jul 9, 2026 1:22pm |  |  | Fair | No | Premises found ok call related to the 25kva transformer
Outage | J.E.26.07.08289 | C001843976 | Tyrese Williams | St.Ann | Completed | Load_244118 | Cardiff Hall - 310 | Jul 9, 2026 7:36am | Jul 9, 2026 7:36am | Jul 9, 2026 9:05am | Jul 9, 2026 9:52am | Jul 9, 2026 9:53am | Jul 9, 2026 9:54am | Jul 9, 2026 9:56am | Jul 9, 2026 9:56am |  |  | Rains | No | Premise not found not getting customer on phone
Outage | J.E.26.07.08322 | C001843977 | Tyrese Williams | St.Ann | Completed | Load_252066 | Cardiff Hall - 310 | Jul 9, 2026 7:36am | Jul 9, 2026 9:50am | Jul 9, 2026 9:53am | Jul 9, 2026 9:56am | Jul 9, 2026 11:01am | Jul 9, 2026 11:33am | Jul 9, 2026 11:35am | Jul 9, 2026 11:35am |  |  | Rains | No | Recommend field service team meter barrel lock voltage check at pothead 124/123/247meter found blank
Outage | J.E.26.07.08327 | C001843974 | Tyrese Williams | St.Ann | Completed | Load_252558 | Cardiff Hall - 310 | Jul 9, 2026 7:36am | Jul 9, 2026 7:36am | Jul 9, 2026 9:45am | Jul 9, 2026 11:36am | Jul 9, 2026 1:04pm | Jul 9, 2026 1:20pm | Jul 9, 2026 1:20pm | Jul 9, 2026 1:20pm |  |  | Rains | No | Replace a 25kva transformer fuse at 3 amp at pole
Outage | J.E.26.07.08554 | C001843975 | Tyrese Williams | St.Ann | Completed | Load_251818 | Cardiff Hall - 310 | Jul 9, 2026 7:36am | Jul 9, 2026 7:36am | Jul 9, 2026 9:48am | Jul 9, 2026 2:10pm | Jul 9, 2026 2:40pm | Jul 9, 2026 5:14pm | Jul 9, 2026 5:14pm | Jul 9, 2026 5:14pm | Fire |  | Fair | No | Disconnected burnt customer service wire and replaced a 25 kva transformer fuse with a 3amp at pole
Outage | J.E.26.07.07053 | C001843969 | Omar King | St.Ann | Completed | Load_266109 | Ocho Rios - 310 | Jul 9, 2026 7:34am | Jul 9, 2026 8:31am | Jul 9, 2026 12:07pm | Jul 9, 2026 12:09pm | Jul 9, 2026 12:09pm | Jul 9, 2026 12:09pm | Jul 9, 2026 12:09pm | Jul 9, 2026 12:09pm | Fire |  | Fair | No | Found a 50 amp junction fuse blow cause by lightning fuse as been replaced area is now with supply
Outage | J.E.26.07.08246 | C001843968 | Omar King | St.Ann | Completed | Load_241824 | Ocho Rios - 310 | Jul 9, 2026 7:34am | Jul 9, 2026 8:31am | Jul 9, 2026 12:15pm | Jul 9, 2026 12:15pm | Jul 9, 2026 12:15pm | Jul 9, 2026 12:15pm | Jul 9, 2026 12:15pm | Jul 9, 2026 12:15pm |  |  | Fair | No | Problem as been resolved
Outage | J.E.26.07.07320 | C001843963 | Omar King | St.Ann | Completed | Load_264820 | Upper White River - 210 | Jul 9, 2026 7:30am | Jul 9, 2026 8:32am | Jul 9, 2026 12:13pm | Jul 9, 2026 12:13pm | Jul 9, 2026 12:13pm | Jul 9, 2026 12:14pm | Jul 9, 2026 12:14pm | Jul 9, 2026 12:14pm | BrokenPole |  | Fair | No | Premises check and found ok cable wire was reported
Outage | J.E.26.07.07970 | C001843964 | Omar King | St.Ann | Completed | Load_263915 | Upper White River - 210 | Jul 9, 2026 7:30am | Jul 9, 2026 8:32am | Jul 9, 2026 10:40am | Jul 9, 2026 10:46am | Jul 9, 2026 11:57am | Jul 9, 2026 11:58am | Jul 9, 2026 11:58am | Jul 9, 2026 11:58am |  |  | Fair | No | Problem found internal I advise customer to use electrician
Outage | J.E.26.07.08340 | C001843965 | Omar King | St.Ann | Completed | Load_253007 | Upper White River - 210 | Jul 9, 2026 7:30am | Jul 9, 2026 8:32am | Jul 9, 2026 8:38am | Jul 9, 2026 8:38am | Jul 9, 2026 9:20am | Jul 9, 2026 10:46am | Jul 9, 2026 10:46am | Jul 9, 2026 10:46am |  |  | Rains | No | Found two span of secondary phase and neutral broken as been repaired customer is now with supply
Outage | J.E.26.07.08540 | C001843966 | Omar King | St.Ann | Completed | Load_262635 | Upper White River - 210 | Jul 9, 2026 7:30am | Jul 9, 2026 3:50pm | Jul 9, 2026 5:24pm | Jul 9, 2026 5:28pm | Jul 9, 2026 7:01pm | Jul 9, 2026 7:01pm | Jul 9, 2026 7:02pm | Jul 9, 2026 7:02pm |  |  | Fair | No | Problem as been resolved
Outage | J.E.26.07.07441 | C001843962 | Raymond Lewis | St.Ann | Completed | Load_259193 | Roaring River - 210 | Jul 9, 2026 7:29am | Jul 9, 2026 7:31am | Jul 9, 2026 8:47am | Jul 9, 2026 8:47am | Jul 9, 2026 8:47am | Jul 9, 2026 8:42am | Jul 9, 2026 8:49am | Jul 9, 2026 8:49am |  |  | Fair | No | Supply was restored
Non-Outage | J.E.26.07.06018 | C001843958 | Milton Charlton | null | Completed | null | null | Jul 9, 2026 7:26am | Jul 9, 2026 3:15pm | Jul 9, 2026 4:30pm | Jul 9, 2026 4:31pm | Jul 9, 2026 4:58pm | Jul 9, 2026 5:00pm | Jul 9, 2026 5:00pm | Jul 9, 2026 5:00pm | BangingWires |  | Fair | No | Need to install 30ft pole in order to raise conductor.
Non-Outage | J.E.26.07.08447 | C001843954 | Denton Williams | null | Completed | null | null | Jul 9, 2026 7:15am | Jul 9, 2026 7:21am | Jul 9, 2026 3:31pm | Jul 9, 2026 3:31pm | Jul 9, 2026 3:31pm | Jul 9, 2026 3:31pm | Jul 9, 2026 3:32pm | Jul 9, 2026 3:32pm | TreeContact |  | Fair | No | Tree fell on line resulting broken wires and a blown 10amps fuse. Cut and remove tree from line, and split and retention broken wires, using 30ft of no.2aaa wire and 6 one bolt clamps. Replace 10amps fuse to restore area.
Outage | J.E.26.07.08412 | C001843950 | Denton Williams | Portland | Completed | Load_351343 | Port Antonio - 410 | Jul 9, 2026 7:15am | Jul 9, 2026 7:21am | Jul 9, 2026 7:31am | Jul 9, 2026 7:31am | Jul 9, 2026 7:43am | Jul 9, 2026 10:09am | Jul 9, 2026 10:17am | Jul 9, 2026 10:17am | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards | Y | Fair | No | Splice and tension broken secondary neutral. Some customers is complaining about damage equipment.
Outage | J.E.26.07.08431 | C001843951 | Denton Williams | Portland | Completed | Load_249419 | Port Antonio - 410 | Jul 9, 2026 7:15am | Jul 9, 2026 7:21am | Jul 9, 2026 2:00pm | Jul 9, 2026 2:01pm | Jul 9, 2026 2:14pm | Jul 9, 2026 3:25pm | Jul 9, 2026 3:30pm | Jul 9, 2026 3:30pm | Fire | Y | Fair | No | Tree fell on line resulting broken wires and a blown 10amps fuse. Cut and remove tree from line, and split and retention broken wires, using 30ft of no.2aaa wire and 6 one bolt clamps. Replace 10amps fuse to restore area.
Outage | J.E.26.07.08490 | C001843890 | Swon Miller | St.James | Completed | Load_290370 | Queens Drive - 310 | Jul 9, 2026 2:55am | Jul 9, 2026 2:58am | Jul 9, 2026 3:28am | Jul 9, 2026 3:28am | Jul 9, 2026 5:07am | Jul 21, 2026 5:40am | Jul 9, 2026 5:40am | Jul 9, 2026 5:40am |  |  | Fair | No | Found 1,50 amp junction fuse blown cause by severe wind voltage found 0.000 replace 1,50 amp junction fuse no pole number available voltage left 114 /115/232
Outage | J.E.26.07.08461 | C001843884 | Delano Gayle | St.Catherine | Completed | Load_259907 | Tredegar - 510 | Jul 9, 2026 12:02am | Jul 9, 2026 12:06am | Jul 9, 2026 4:31am | Jul 9, 2026 4:31am | Jul 9, 2026 5:10am | Jul 9, 2026 5:38am | Jul 9, 2026 5:39am | Jul 9, 2026 5:39am |  |  | Fair | No | Defective 25kva transformer no pole#, oil running from transformer, send call to maintenance
Outage | J.E.26.07.08428 | C001843878 | Delano Gayle | St.Catherine | Completed | Load_252020 | Twickenham - 210 | Jul 8, 2026 11:01pm | Jul 8, 2026 11:01pm | Jul 9, 2026 5:39am | Jul 9, 2026 5:39am | Jul 9, 2026 6:11am | Jul 9, 2026 6:22am | Jul 9, 2026 6:22am | Jul 9, 2026 6:22am | Fire |  | Fair | No | Burnt 2/0 triplex secondary wire, need approximately 15ft 2/0 triplex to carry out repairs as wire was burnt to a crisp, numerous customers still remain without supply
Outage | J.E.26.07.08427 | C001843877 | Delano Gayle | St.Catherine | Completed | Load_1000347 | Twickenham - 210 | Jul 8, 2026 11:00pm | Jul 8, 2026 11:01pm | Jul 9, 2026 6:25am | Jul 9, 2026 6:25am | Jul 9, 2026 6:27am | Jul 9, 2026 6:29am | Jul 9, 2026 6:29am | Jul 9, 2026 6:29am |  |  | Fair | No | Related to call in big lane where burnt 2/0 triplex wire is located
Outage | J.E.26.07.08426 | C001843874 | Rusean Allen | KSAN | Completed | Load_247082 | West Kings House - 310 | Jul 8, 2026 10:55pm | Jul 8, 2026 10:55pm | Jul 9, 2026 12:58am | Jul 9, 2026 12:58am | Jul 9, 2026 1:12am | Jul 9, 2026 1:15am | Jul 9, 2026 1:15am | Jul 9, 2026 1:15am |  |  | Fair | No | Meter center closed, single customer is without power.
Outage | J.E.26.07.08308 | C001843873 | Delano Gayle | St.Catherine | Completed | Load_248407 | New Michelton - 410 | Jul 8, 2026 10:53pm | Jul 8, 2026 10:54pm | Jul 8, 2026 11:09pm | Jul 8, 2026 11:09pm | Jul 8, 2026 11:36pm | Jul 8, 2026 11:38pm | Jul 8, 2026 11:38pm | Jul 8, 2026 11:38pm | BrokenWire |  | Fair | No | Premises found okay via phone call
Outage | J.E.26.07.07936 | C001843870 | Swon Miller | St.James | Completed | Load_267656 | Queens Drive - 710 | Jul 8, 2026 10:49pm | Jul 8, 2026 10:50pm | Jul 8, 2026 11:46pm | Jul 8, 2026 11:46pm | Jul 9, 2026 12:16am | Jul 22, 2026 5:46am | Jul 9, 2026 12:47am | Jul 9, 2026 12:47am | Fire |  | Fair | No | Found 1, 50 kva transformer trip cause by illegal connections remove illegal and reset 50 kva transformer voltage found 0.0000 voltage left 115/114/229
Outage | J.E.26.07.08023 | C001843871 | Swon Miller | St.James | Completed | Load_257396 | Bogue - 610 | Jul 8, 2026 10:49pm | Jul 8, 2026 10:50pm | Jul 9, 2026 12:47am | Jul 9, 2026 12:49am | Jul 9, 2026 2:08am | Jul 9, 2026 3:26pm | Jul 9, 2026 3:28am | Jul 9, 2026 3:28am |  |  | Fair | No | Found 10 kva transformer trip cause by illegal connections remove illegal connections from secondary lines and reset 10 kva transformer at pole number 569114
Outage | J.E.26.07.08378 | C001843869 | Swon Miller | St.James | Completed | Load_259518 | Queens Drive - 710 | Jul 8, 2026 10:48pm | Jul 8, 2026 10:48pm | Jul 8, 2026 10:57pm | Jul 8, 2026 10:57pm | Jul 8, 2026 11:24pm | Jul 22, 2026 11:46pm | Jul 8, 2026 11:46pm | Jul 8, 2026 11:46pm |  |  | Fair | No | Found 1,30 amp junction fuse blown cause by contamination replace 1,30 amp junction fuse at pole number 215404 voltage found 0.000 voltage left 115/114/227
Outage | J.E.26.07.08088 | C001843867 | Edward Royal | KSAN | Completed | Load_246500 | Constant Spring - 410 | Jul 8, 2026 10:28pm | Jul 8, 2026 10:28pm | Jul 8, 2026 10:43pm | Jul 8, 2026 10:43pm | Jul 8, 2026 11:16pm | Jul 8, 2026 11:21pm | Jul 8, 2026 11:24pm | Jul 8, 2026 11:24pm |  |  | Fair | No | Hotline clamp burned from primary main line referred to live line crew
Outage | J.E.26.07.08356 | C001843860 | Donald Cunningham | St.Catherine | Completed | Load_1001612 | Tredegar - 310 | Jul 8, 2026 9:41pm | Jul 8, 2026 9:41pm | Jul 8, 2026 10:29pm | Jul 8, 2026 10:29pm | Jul 8, 2026 11:05pm | Jul 8, 2026 11:18pm | Jul 8, 2026 11:19pm | Jul 8, 2026 11:19pm |  |  | Fair | No | Reset 25 kva transformer across from cash pot shop on Gordon blvd
Outage | J.E.26.07.07955 | C001843858 | Fitzroy Turner | KSAN | Completed | Load_575430 | Washington Blvd - 710 | Jul 8, 2026 9:33pm | Jul 9, 2026 8:44am | Jul 9, 2026 10:04am | Jul 9, 2026 10:06am | Jul 9, 2026 10:07am | Jul 9, 2026 10:07am | Jul 9, 2026 10:12am | Jul 9, 2026 10:12am |  |  | Fair | No | Customer supply needs to resolve issues from top up customer switch over.please send email to field service department to charge on the system
Outage | J.E.26.07.07449 | C001843857 | Edward Royal | KSAN | Completed | Load_293698 | Washington Blvd - 710 | Jul 8, 2026 9:31pm | Jul 8, 2026 9:32pm | Jul 9, 2026 9:07am | Jul 9, 2026 9:07am | Jul 9, 2026 9:08am | Jul 9, 2026 9:08am | Jul 9, 2026 9:08am | Jul 9, 2026 9:08am |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.07.07324 | C001843854 | Nickolas Rodriques | KSAN | Completed | Load_575939 | Washington Blvd - 510 | Jul 8, 2026 9:19pm | Jul 8, 2026 9:19pm | Jul 9, 2026 12:09am | Jul 9, 2026 12:09am | Jul 9, 2026 12:37am | Jul 9, 2026 1:01am | Jul 9, 2026 3:54am | Jul 9, 2026 3:54am |  |  | Fair | No | Customer confirmed that power was restored.
Outage | J.E.26.07.08183 | C001843848 | Cliton Henry | St.Mary | Completed | Load_261992 | Blackstonedge - 110 | Jul 8, 2026 9:18pm | Jul 8, 2026 9:19pm | Jul 8, 2026 9:23pm | Jul 8, 2026 9:23pm | Jul 8, 2026 9:44pm | Jul 8, 2026 10:25pm | Jul 8, 2026 10:26pm | Jul 8, 2026 10:26pm |  |  | Fair | No | A blown 20 amp junction fuse found at Derry square Poe #0014181. Supply restored using 1.20 amp fuse. This line section need bushing, kindly refer to St.Mary Operations for vegetation management.
Outage | J.E.26.07.08064 | C001843843 | Marlon Brown | Trelawny | Completed | Load_255254 | Duncans - 110 | Jul 8, 2026 9:06pm | Jul 8, 2026 9:07pm | Jul 8, 2026 9:16pm | Jul 8, 2026 9:16pm | Jul 8, 2026 9:37pm | Jul 8, 2026 10:36pm | Jul 8, 2026 10:36pm | Jul 8, 2026 10:36pm |  |  | Fair | No | Replaced 15amps junction fuse and retention 1 span primary neutral.
Outage | J.E.26.07.07998 | C001843838 | Edward Royal | KSAN | Completed | Load_1002632 | Washington Blvd - 710 | Jul 8, 2026 8:32pm | Jul 8, 2026 9:09pm | Jul 8, 2026 9:16pm | Jul 8, 2026 9:16pm | Jul 8, 2026 9:21pm | Jul 8, 2026 10:42pm | Jul 8, 2026 10:43pm | Jul 8, 2026 10:43pm | Fire |  | Fair | No | Removed tree branches from secondary line and customer service cables spliced and reconnected secondary cable.
Outage | J.E.26.07.08223 | C001843839 | Eric Williams | KSAN | Completed | Load_248430 | Washington Blvd - 310 | Jul 8, 2026 8:32pm | Jul 8, 2026 8:48pm | Jul 8, 2026 9:19pm | Jul 8, 2026 9:20pm | Jul 8, 2026 9:35pm | Jul 8, 2026 10:01pm | Jul 8, 2026 10:02pm | Jul 8, 2026 10:02pm |  |  | Fair | No | Blown 3amps fuse found and replace,
Outage | J.E.26.07.08224 | C001843836 | Ryan Richards | Manchester | Completed | Load_249300 | Spur Tree - 310 | Jul 8, 2026 8:24pm | Jul 9, 2026 7:55am | Jul 9, 2026 8:28am | Jul 9, 2026 8:28am | Jul 9, 2026 10:05am | Jul 9, 2026 12:28pm | Jul 9, 2026 12:28pm | Jul 9, 2026 12:28pm |  |  | Fair | No | 2 span of broken secondary neutral found cause by bamboos open 25 kva transformer carry out spot bushing while trimming the bushes a next phase was broken split and retention all 3 span using 50ft#2 aluminum 2#2 preform 4 one bolt clamp and reclose transformer all customers are now with supply
Outage | J.E.26.07.08214 | C001843834 | Richman Whyte | Westmoreland | Completed | Load_237747 | Paradise - 310 | Jul 8, 2026 8:18pm | Jul 8, 2026 8:19pm | Jul 8, 2026 9:41pm | Jul 8, 2026 9:41pm | Jul 8, 2026 9:41pm | Jul 8, 2026 9:54pm | Jul 8, 2026 9:54pm | Jul 8, 2026 9:54pm |  |  | Fair | No | Replace fifty amp junction fuse
Outage | J.E.26.07.08261 | C001843833 | Richman Whyte | Westmoreland | Completed | Load_253644 | Paradise - 310 | Jul 8, 2026 8:18pm | Jul 8, 2026 8:19pm | Jul 8, 2026 10:00pm | Jul 8, 2026 10:00pm | Jul 8, 2026 11:23pm | Jul 8, 2026 11:23pm | Jul 8, 2026 11:26pm | Jul 8, 2026 11:26pm |  |  | Fair | No | Need daylight attention poor visibility
Outage | J.E.26.07.08161 | C001843832 | Richman Whyte | Westmoreland | Completed | Load_240510 | Paradise - 310 | Jul 8, 2026 8:17pm | Jul 8, 2026 8:19pm | Jul 8, 2026 9:54pm | Jul 8, 2026 9:54pm | Jul 8, 2026 9:54pm | Jul 8, 2026 9:55pm | Jul 8, 2026 9:56pm | Jul 8, 2026 9:56pm |  |  | Fair | No | Related to the the other Brighton call
Outage | J.E.26.07.08145 | C001843830 | Stephen Taylor | St.Thomas | Completed | Load_266684 | Good Year - 210 | Jul 8, 2026 7:58pm | Jul 8, 2026 7:59pm | Jul 8, 2026 8:44pm | Jul 8, 2026 8:44pm | Jul 8, 2026 9:07pm | Jul 8, 2026 9:07pm | Jul 8, 2026 9:11pm | Jul 8, 2026 9:11pm | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Broken wire was made safe 90% of customer is with power a lot of bushing needs to be done on mango trees to restore the the next 10% of customer
Outage | J.E.26.07.08220 | C001843829 | Stephen Taylor | St.Thomas | Completed | Load_259440 | Good Year - 210 | Jul 8, 2026 7:58pm | Jul 8, 2026 7:59pm | Jul 8, 2026 9:12pm | Jul 8, 2026 9:12pm | Jul 8, 2026 9:13pm | Jul 8, 2026 9:13pm | Jul 8, 2026 9:14pm | Jul 8, 2026 9:14pm |  |  | Fair | No | Contact customer and customer say that power was restored and now okay
Outage | J.E.26.07.08247 | C001843826 | Jermaine Williams | Clarendon | Completed | Load_1002788 | Monymusk - 410 | Jul 8, 2026 7:58pm | Jul 8, 2026 7:58pm | Jul 8, 2026 10:10pm | Jul 8, 2026 10:10pm | Jul 8, 2026 10:38pm | Jul 8, 2026 10:38pm | Jul 8, 2026 10:38pm | Jul 8, 2026 10:38pm | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Defective customer service wire.
Outage | J.E.26.07.07977 | C001843824 | Hopeton Henry | St.Thomas | Completed | Load_239111 | Lysson - 410 | Jul 8, 2026 7:55pm | Jul 9, 2026 8:04am | Jul 9, 2026 8:37am | Jul 9, 2026 3:47pm | Jul 9, 2026 4:40pm | Jul 9, 2026 5:12pm | Jul 9, 2026 5:13pm | Jul 9, 2026 5:13pm |  |  | Fair | No | Remove tree and reset 25 kva transformer
Outage | J.E.26.07.08148 | C001843823 | Hopeton Henry | St.Thomas | Completed | Load_242150 | Lysson - 410 | Jul 8, 2026 7:54pm | Jul 9, 2026 8:04am | Jul 9, 2026 8:37am | Jul 9, 2026 5:15pm | Jul 9, 2026 6:05pm | Jul 9, 2026 6:30pm | Jul 9, 2026 6:31pm | Jul 9, 2026 6:31pm |  |  | Fair | No | Check and found ok
Outage | J.E.26.07.08180 | C001843820 | Michael Christian | St.James | Completed | Load_269225 | Queens Drive - 710 | Jul 8, 2026 7:54pm | Jul 8, 2026 7:54pm | Jul 8, 2026 8:07pm | Jul 8, 2026 8:07pm | Jul 8, 2026 8:30pm | Jul 8, 2026 8:47pm | Jul 8, 2026 8:47pm | Jul 8, 2026 8:47pm |  |  | Fair | No | Found 1 50 amp junction out replace 1 50 amp no pole #
Non-Outage | J.E.26.07.07686 | C001843816 | Ricky Hall | Portmore | Completed | Load_251890 | Naggo Head - 510 | Jul 8, 2026 7:26pm | Jul 8, 2026 7:26pm | Jul 8, 2026 7:42pm | Jul 8, 2026 7:42pm | Jul 8, 2026 8:02pm | Jul 8, 2026 8:16pm | Jul 8, 2026 8:17pm | Jul 8, 2026 8:17pm |  |  | Fair | No | Burnt odd switch top jumper in bank of 3*100 kva xfmr however based on location of xfmr call would be best dealt with in daytime plz ref to morning crew
Outage | J.E.26.07.08043 | C001843811 | Romaine Roberts | St.Mary | Completed | Load_265922 | Highgate - 210 | Jul 8, 2026 7:08pm | Jul 8, 2026 7:08pm | Jul 8, 2026 9:28pm | Jul 8, 2026 9:28pm | Jul 8, 2026 9:28pm | Jul 8, 2026 9:30pm | Jul 8, 2026 9:30pm | Jul 8, 2026 9:30pm | Fire | Y | Fair | No | Power restore outage associated with 07351
Outage | J.E.26.07.08143 | C001843810 | Richard Samuda | Manchester | Completed | Load_253163 | Spur Tree - 310 | Jul 8, 2026 7:06pm | Jul 8, 2026 7:07pm | Jul 8, 2026 8:17pm | Jul 8, 2026 8:17pm | Jul 8, 2026 8:17pm | Jul 8, 2026 8:17pm | Jul 8, 2026 8:24pm | Jul 8, 2026 8:24pm | Fire |  | Fair | No | Found insulator dislodge fr cross arm causing line to bang against pole shed load by open tripped saver at feeds wik walk and open three phase line that feeds TV J site than open tripped saver at mt prospect that feeds the main line 0137229than carry out repair customer back normal
Outage | J.E.26.07.08131 | C001843808 | Lancelot Brown | Hanover | Completed | Load_258040 | Orange Bay - 210 | Jul 8, 2026 7:00pm | Jul 8, 2026 7:01pm | Jul 8, 2026 8:07pm | Jul 8, 2026 8:34pm | Jul 8, 2026 9:00pm | Jul 8, 2026 9:53pm | Jul 8, 2026 9:53pm | Jul 8, 2026 9:53pm |  |  | Fair | No | Carry out voltage reading at secondary also pothead found customer breaker trip voltage reading found and leave 112-112-200 -224-226-231 reset customer breaker supply restore
Outage | J.E.26.07.08069 | C001843805 | Edward Royal | KSAN | Completed | Load_250649 | Constant Spring - 410 | Jul 8, 2026 6:55pm | Jul 8, 2026 10:29pm | Jul 9, 2026 8:55am | Jul 9, 2026 8:55am | Jul 9, 2026 8:55am | Jul 9, 2026 8:55am | Jul 9, 2026 8:55am | Jul 9, 2026 8:55am |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.07.07991 | C001843802 | Jermaine Williams | Clarendon | Completed | Load_269437 | May Pen - 210 | Jul 8, 2026 6:46pm | Jul 8, 2026 6:47pm | Jul 8, 2026 9:17pm | Jul 8, 2026 9:17pm | Jul 8, 2026 9:17pm | Jul 8, 2026 9:45pm | Jul 8, 2026 10:08pm | Jul 8, 2026 10:08pm | BrokenWire |  | Fair | No | Splice and retention broken service wire using 40’ #6 triplex.
Non-Outage | J.E.26.07.08056 | C001843798 | Clyde Brown | null | Completed | null | null | Jul 8, 2026 6:34pm | Jul 8, 2026 6:46pm | Jul 8, 2026 9:30pm | Jul 8, 2026 9:30pm | Jul 8, 2026 11:16pm | Jul 8, 2026 11:13pm | Jul 8, 2026 11:22pm | Jul 8, 2026 11:22pm |  |  | Fair | No | Blown 25kva transformer,line patrolled and no fault seen,blown fuse replaced.
Outage | J.E.26.07.08026 | C001843795 | Ricky Hall | Portmore | Completed | Load_249629 | Naggo Head - 610 | Jul 8, 2026 6:26pm | Jul 8, 2026 6:30pm | Jul 8, 2026 6:48pm | Jul 8, 2026 7:08pm | Jul 8, 2026 7:22pm | Jul 8, 2026 7:41pm | Jul 8, 2026 7:41pm | Jul 8, 2026 7:41pm |  |  | Fair | No | Replaced blown 50 amps junction fuse
Outage | J.E.26.07.07910 | C001843791 | Daniel Francis | St.Ann | Completed | Load_267230 | Ocho Rios - 410 | Jul 8, 2026 6:10pm | Jul 8, 2026 6:10pm | Jul 8, 2026 8:13pm | Jul 8, 2026 8:13pm | Jul 8, 2026 9:00pm | Jul 8, 2026 9:01pm | Jul 8, 2026 9:12pm | Jul 8, 2026 9:12pm |  |  | Fair | No | Found secondary phase conducter broken splice and retention also found secondary line isolated
Outage | J.E.26.07.07959 | C001843790 | Daniel Francis | St.Ann | Completed | Load_267230 | Ocho Rios - 410 | Jul 8, 2026 6:10pm | Jul 8, 2026 6:10pm | Jul 8, 2026 9:19pm | Jul 8, 2026 9:19pm | Jul 8, 2026 9:19pm | Jul 8, 2026 9:19pm | Jul 8, 2026 9:22pm | Jul 8, 2026 9:22pm |  |  | Fair | No | Powered restored call relate to shop 5 Brownplaza
Outage | J.E.26.07.07624 | C001843783 | Wayne Dillion | St.James | Completed | Load_263214 | Bogue - 310 | Jul 8, 2026 6:09pm | Jul 8, 2026 6:09pm | Jul 8, 2026 7:54pm | Jul 8, 2026 7:54pm | Jul 8, 2026 7:54pm | Jul 8, 2026 7:54pm | Jul 8, 2026 7:58pm | Jul 8, 2026 7:58pm |  |  | Fair | No | Supply check and found connected.
Outage | J.E.26.07.07810 | C001843789 | Kemark Slue | St.Catherine | Completed | Load_569929 | Tredegar - 210 | Jul 8, 2026 6:09pm | Jul 8, 2026 6:11pm | Jul 8, 2026 7:31pm | Jul 8, 2026 7:39pm | Jul 8, 2026 7:39pm | Jul 8, 2026 8:21pm | Jul 8, 2026 9:27pm | Jul 8, 2026 9:27pm |  |  | Fair | No | Upon arrival at the location the crew discovered that 20 amps bush phase from two phases at pole # 0092613 was blown, further patrol revealed a house that’s under construction is within close proximity to said primary conductor, it would appears that the conductor came into contact with a steel during construction, refuse link and re-energized line section.
Outage | J.E.26.07.07953 | C001843782 | Jermaine Williams | Clarendon | Completed | Load_405556 | Parnassus - 310 | Jul 8, 2026 6:08pm | Jul 8, 2026 6:09pm | Jul 8, 2026 10:09pm | Jul 8, 2026 10:09pm | Jul 8, 2026 10:09pm | Jul 8, 2026 10:09pm | Jul 8, 2026 10:09pm | Jul 8, 2026 10:09pm | BrokenWire |  | Fair | No | Repair defective service wire.
Outage | J.E.26.07.07958 | C001843781 | Lancelot Brown | Hanover | Completed | Load_252795 | Orange Bay - 310 | Jul 8, 2026 6:07pm | Jul 8, 2026 6:07pm | Jul 8, 2026 8:06pm | Jul 8, 2026 8:06pm | Jul 8, 2026 8:31pm | Jul 8, 2026 8:33pm | Jul 8, 2026 8:34pm | Jul 8, 2026 8:34pm |  |  | Fair | No | Found 10kva trip patroll found nothing suspect over load reset10kva supply restore
Outage | J.E.26.07.07875 | C001843776 | Kemark Slue | St.Catherine | Completed | Load_246631 | Tredegar - 510 | Jul 8, 2026 5:42pm | Jul 8, 2026 5:42pm | Jul 8, 2026 5:46pm | Jul 8, 2026 5:46pm | Jul 8, 2026 6:38pm | Jul 8, 2026 7:00pm | Jul 8, 2026 7:38pm | Jul 8, 2026 7:38pm |  |  | Fair | No | Upon arrival at the location the crew discovered that road 20 amps junction from three phase T-off was blown resulting from the said primary line section being sagging and making contact with the telecommunications cable, retention conductor, refuse link and re-energized line section.
Outage | J.E.26.07.07780 | C001843772 | Richman Whyte | Westmoreland | Completed | Load_266309 | Paradise - 310 | Jul 8, 2026 5:39pm | Jul 8, 2026 6:32pm | Jul 8, 2026 9:56pm | Jul 8, 2026 9:56pm | Jul 8, 2026 9:56pm | Jul 8, 2026 9:57pm | Jul 8, 2026 9:58pm | Jul 8, 2026 9:58pm |  |  | Fair | No | Related to the Brighton call
Outage | J.E.26.07.07610 | C001843771 | Moses Elliston | St.Catherine | Completed | Load_266292 | Tredegar - 310 | Jul 8, 2026 5:38pm | Jul 8, 2026 5:38pm | Jul 9, 2026 6:07am | Jul 9, 2026 6:08am | Jul 9, 2026 6:08am | Jul 8, 2026 5:30pm | Jul 9, 2026 6:11am | Jul 9, 2026 6:11am |  |  | Fair | No | Defective transformer to be change . R. Brown is aware the matter.
Outage | J.E.26.07.07582 | C001843770 | Marlon Brown | Trelawny | Completed | Load_249733 | Martha Brae - 110 | Jul 8, 2026 5:36pm | Jul 8, 2026 5:37pm | Jul 8, 2026 5:49pm | Jul 8, 2026 5:49pm | Jul 8, 2026 6:57pm | Jul 8, 2026 6:57pm | Jul 8, 2026 6:57pm | Jul 8, 2026 6:57pm |  |  | Fair | No | Unable to locate customer via telephone nor direction
Outage | J.E.26.07.07901 | C001843758 | Neckell Ormsby | St.Mary | Completed | Load_264015 | Highgate -110 | Jul 8, 2026 5:28pm | Jul 8, 2026 5:29pm | Jul 8, 2026 7:26pm | Jul 8, 2026 7:26pm | Jul 8, 2026 9:06pm | Jul 8, 2026 9:57pm | Jul 8, 2026 9:58pm | Jul 8, 2026 9:58pm |  |  | Fair | No | Unable to locate customer after several calls also patrol area and found supply in area
Outage | J.E.26.07.07768 | C001843754 | Jermaine Williams | Clarendon | Completed | Load_267981 | Parnassus - 310 | Jul 8, 2026 5:26pm | Jul 8, 2026 5:26pm | Jul 8, 2026 7:52pm | Jul 8, 2026 7:52pm | Jul 8, 2026 8:21pm | Jul 8, 2026 8:22pm | Jul 8, 2026 8:23pm | Jul 8, 2026 8:23pm |  |  | SevereWind | No | Remade burnt out drop lead at xfmr using two clamps.
Outage | J.E.26.07.07871 | C001843756 | Cliton Henry | St.Ann | Completed | Load_243350 | Upper White River - 110 | Jul 8, 2026 5:26pm | Jul 8, 2026 5:26pm | Jul 8, 2026 8:36pm | Jul 8, 2026 8:36pm | Jul 8, 2026 8:37pm | Jul 8, 2026 8:41pm | Jul 8, 2026 8:42pm | Jul 8, 2026 8:42pm |  |  | Fair | No | Day light attention required to execute patrol due poor visibility. Customer gate open and bad dog running all over the property.
Outage | J.E.26.07.07900 | C001843755 | Cliton Henry | St.Mary | Completed | Load_264056 | Oracabessa - 210 | Jul 8, 2026 5:26pm | Jul 8, 2026 5:26pm | Jul 8, 2026 8:34pm | Jul 8, 2026 8:34pm | Jul 8, 2026 8:34pm | Jul 8, 2026 8:34pm | Jul 8, 2026 8:36pm | Jul 8, 2026 8:36pm |  |  | Fair | No | The customer meter was off. Supply restored with the help from the Escalation team.
Outage | J.E.26.07.07675 | C001843750 | Michael Christian | St.James | Completed | Load_259211 | Queens Drive - 710 | Jul 8, 2026 5:24pm | Jul 8, 2026 5:25pm | Jul 8, 2026 7:46pm | Jul 8, 2026 7:46pm | Jul 8, 2026 7:48pm | Jul 8, 2026 7:50pm | Jul 8, 2026 7:50pm | Jul 8, 2026 7:50pm |  |  | Fair | No | Found 1 50 amp junction out replace 1 50 amp time 6 pm
Non-Outage | J.E.26.07.07644 | C001843746 | Edward Royal | KSAS | Completed | Load_244933 | Hunts Bay - 810 | Jul 8, 2026 5:19pm | Jul 8, 2026 5:21pm | Jul 8, 2026 5:34pm | Jul 8, 2026 7:03pm | Jul 8, 2026 8:04pm | Jul 8, 2026 8:04pm | Jul 8, 2026 8:05pm | Jul 8, 2026 8:05pm | BrokenWire |  | Fair | No | Spliced and reconnected service neutral using 2 single bolt clamp
Non-Outage | J.E.26.07.07455 | C001843742 | Eric Williams | null | Completed | null | null | Jul 8, 2026 5:08pm | Jul 8, 2026 5:09pm | Jul 8, 2026 7:45pm | Jul 8, 2026 7:45pm | Jul 8, 2026 7:45pm | Jul 8, 2026 7:51pm | Jul 8, 2026 7:52pm | Jul 8, 2026 7:52pm | BrokenWire |  | Fair | No | Broken 3 wire open secondary neutral cause by illegal connections, wire cut and splice usi4 one bolt clamps, 1 #6 preeform
Non-Outage | J.E.26.07.06901 | C001843741 | Eric Williams | null | Completed | null | null | Jul 8, 2026 5:07pm | Jul 8, 2026 5:09pm | Jul 8, 2026 7:55pm | Jul 8, 2026 7:55pm | Jul 8, 2026 8:22pm | Jul 8, 2026 9:08pm | Jul 8, 2026 9:10pm | Jul 8, 2026 9:10pm | Fire |  | Fair | No | Secondary neutral drop lead joint burnt same corrected with 1 - one bolt clamp, section restored.
Outage | J.E.26.07.07614 | C001843740 | Edward Royal | KSAS | Completed | Load_253600 | Cane River - 310 | Jul 8, 2026 5:06pm | Jul 8, 2026 5:09pm | Jul 8, 2026 5:34pm | Jul 8, 2026 6:54pm | Jul 8, 2026 6:54pm | Jul 8, 2026 7:02pm | Jul 8, 2026 7:02pm | Jul 8, 2026 7:02pm |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.07.07447 | C001843736 | Edward Royal | KSAS | Completed | Load_255943 | Three Miles - 510 | Jul 8, 2026 5:03pm | Jul 8, 2026 9:31pm | Jul 9, 2026 9:00am | Jul 9, 2026 9:00am | Jul 9, 2026 9:00am | Jul 9, 2026 9:07am | Jul 9, 2026 9:07am | Jul 9, 2026 9:07am |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.07.07064 | C001843732 | Eric Williams | KSAN | Completed | Load_251103 | Washington Blvd - 710 | Jul 8, 2026 4:56pm | Jul 8, 2026 5:00pm | Jul 8, 2026 7:52pm | Jul 8, 2026 7:53pm | Jul 8, 2026 7:54pm | Jul 8, 2026 7:54pm | Jul 8, 2026 7:55pm | Jul 8, 2026 7:55pm | Fire |  | Fair | No | Broken 3 wire open secondary neutral cause by illegal connections, wire cut and splice usi4 one bolt clamps, 1 #6 preeform
Outage | J.E.26.07.07612 | C001843731 | Eric Williams | KSAN | Completed | Load_262116 | Washington Blvd - 710 | Jul 8, 2026 4:55pm | Jul 8, 2026 4:55pm | Jul 8, 2026 6:24pm | Jul 8, 2026 6:24pm | Jul 8, 2026 6:38pm | Jul 8, 2026 7:39pm | Jul 8, 2026 7:45pm | Jul 8, 2026 7:45pm | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Broken 3 wire open secondary neutral cause by illegal connections, wire cut and splice usi4 one bolt clamps, 1 #6 preeform
Outage | J.E.26.07.07760 | C001843730 | Eric Williams | KSAN | Completed | Load_250320 | Washington Blvd - 710 | Jul 8, 2026 4:55pm | Jul 8, 2026 4:55pm | Jul 8, 2026 4:58pm | Jul 8, 2026 4:58pm | Jul 8, 2026 5:14pm | Jul 8, 2026 6:19pm | Jul 8, 2026 6:24pm | Jul 8, 2026 6:24pm | BrokenWire |  | Fair | No | Broken 3 wire service cause by truck, used 100 feet #6 triplex and 6 onebolt clamps
Outage | J.E.26.07.07503 | C001843715 | Daniel Francis | St.Ann | Completed | Load_249727 | Roaring River - 210 | Jul 8, 2026 4:42pm | Jul 8, 2026 4:44pm | Jul 8, 2026 9:22pm | Jul 8, 2026 9:32pm | Jul 8, 2026 10:06pm | Jul 8, 2026 10:00pm | Jul 8, 2026 10:08pm | Jul 8, 2026 10:08pm |  |  | Fair | No | Meter need to be replaced
Outage | J.E.26.07.07615 | C001843716 | Daniel Francis | St.Ann | Completed | Load_246197 | Roaring River - 210 | Jul 8, 2026 4:42pm | Jul 8, 2026 4:44pm | Jul 8, 2026 6:32pm | Jul 8, 2026 6:32pm | Jul 8, 2026 7:04pm | Jul 8, 2026 7:31pm | Jul 8, 2026 8:13pm | Jul 8, 2026 8:13pm |  |  | Fair | No | Remade joint at pole
Outage | J.E.26.07.07355 | C001843712 | Daniel Francis | St.Ann | Completed | Load_240361 | Roaring River - 210 | Jul 8, 2026 4:41pm | Jul 8, 2026 4:44pm | Jul 8, 2026 10:08pm | Jul 8, 2026 10:08pm | Jul 8, 2026 10:21pm | Jul 8, 2026 10:28pm | Jul 8, 2026 10:28pm | Jul 8, 2026 10:28pm |  |  | Fair | No | Found okay
Outage | J.E.26.07.07373 | C001843713 | Daniel Francis | St.Ann | Completed | Load_250195 | Roaring River - 210 | Jul 8, 2026 4:41pm | Jul 8, 2026 4:44pm | Jul 8, 2026 10:28pm | Jul 8, 2026 10:28pm | Jul 8, 2026 10:32pm | Jul 8, 2026 10:33pm | Jul 8, 2026 10:34pm | Jul 8, 2026 10:34pm |  |  | Fair | No | Premises lock
Outage | J.E.26.07.07781 | C001843705 | Ricky Hall | Portmore | Completed | Load_260751 | Naggo Head - 610 | Jul 8, 2026 4:30pm | Jul 8, 2026 5:30pm | Jul 8, 2026 5:52pm | Jul 8, 2026 5:52pm | Jul 8, 2026 5:52pm | Jul 8, 2026 5:52pm | Jul 8, 2026 5:53pm | Jul 8, 2026 5:53pm |  |  | Fair | No | Area was restored previously
Outage | J.E.26.07.07762 | C001843698 | Richard Samuda | Manchester | Completed | Load_261332 | Spur Tree - 310 | Jul 8, 2026 4:24pm | Jul 8, 2026 4:28pm | Jul 8, 2026 9:52pm | Jul 8, 2026 9:52pm | Jul 8, 2026 10:02pm | Jul 8, 2026 10:02pm | Jul 8, 2026 10:05pm | Jul 8, 2026 10:05pm |  |  | Fair | No | Customer say other crew came there
Non-Outage | J.E.26.07.07659 | C001843697 | Marlon Brown | null | Completed | null | null | Jul 8, 2026 4:23pm | Jul 8, 2026 4:31pm | Jul 8, 2026 4:37pm | Jul 8, 2026 4:37pm | Jul 8, 2026 5:15pm | Jul 8, 2026 5:19pm | Jul 8, 2026 5:19pm | Jul 8, 2026 5:19pm | BrokenWire |  | Fair | No | Refer to maintenance personnel O Ellis. Primary conductor on the main line is broken
Outage | J.E.26.07.07757 | C001843692 | Cliton Henry | St.Mary | Completed | Load_354886 | Blackstonedge - 110 | Jul 8, 2026 4:18pm | Jul 8, 2026 4:21pm | Jul 8, 2026 8:42pm | Jul 8, 2026 8:42pm | Jul 8, 2026 9:09pm | Jul 8, 2026 9:22pm | Jul 8, 2026 9:22pm | Jul 8, 2026 9:22pm |  |  | Fair | No | A blown 7 amp junction fuse found at Labrynth Rd. at pole # 596367 . Supply restored using 1-7 amp fuse.
Outage | J.E.26.07.07716 | C001843682 | Richard Samuda | Manchester | Completed | Load_251145 | Spur Tree - 310 | Jul 8, 2026 4:05pm | Jul 8, 2026 4:06pm | Jul 8, 2026 10:06pm | Jul 8, 2026 10:06pm | Jul 8, 2026 10:06pm | Jul 8, 2026 10:06pm | Jul 8, 2026 10:08pm | Jul 8, 2026 10:08pm | Fire |  | Fair | No | Customer he back to normal
Outage | J.E.26.07.07721 | C001843683 | Richard Samuda | Manchester | Completed | Load_251592 | Spur Tree - 310 | Jul 8, 2026 4:05pm | Jul 8, 2026 4:06pm | Jul 8, 2026 9:23pm | Jul 8, 2026 9:23pm | Jul 8, 2026 9:51pm | Jul 8, 2026 9:51pm | Jul 8, 2026 9:52pm | Jul 8, 2026 9:52pm |  |  | Fair | No | Customer say he back to normal
Outage | J.E.26.07.07140 | C001843671 | Edward Royal | KSAS | Completed | Load_247391 | Rockfort - 410 | Jul 8, 2026 3:57pm | Jul 8, 2026 5:01pm | Jul 8, 2026 5:24pm | Jul 8, 2026 5:24pm | Jul 8, 2026 5:44pm | Jul 8, 2026 5:45pm | Jul 8, 2026 5:45pm | Jul 8, 2026 5:45pm | Fire |  | Fair | No | Premises not found unable to communicate with customer via phone
Outage | J.E.26.07.07239 | C001843668 | Neckell Ormsby | St.Mary | Completed | Load_257269 | Highgate -110 | Jul 8, 2026 3:57pm | Jul 8, 2026 4:00pm | Jul 8, 2026 6:48pm | Jul 8, 2026 6:48pm | Jul 8, 2026 6:48pm | Jul 8, 2026 6:49pm | Jul 8, 2026 6:49pm | Jul 8, 2026 6:49pm |  |  | Fair | No | Found 25 kva transformer trip no pole # seen also broken secondary phase caused by fallen bamboo, open fuse to splice and retention 2- pole span secondary phase using approximately 30ft #2 AA, 3- one bolt clamps and 1-#2 preform reclose transformer and reset trip switch
Outage | J.E.26.07.07284 | C001843669 | Neckell Ormsby | St.Mary | Completed | Load_250151 | Highgate -110 | Jul 8, 2026 3:57pm | Jul 8, 2026 4:00pm | Jul 8, 2026 6:49pm | Jul 8, 2026 6:49pm | Jul 8, 2026 7:24pm | Jul 8, 2026 7:26pm | Jul 8, 2026 7:26pm | Jul 8, 2026 7:26pm |  |  | Fair | No | Found 25 kva transformer trip no pole # seen also broken secondary phase caused by fallen bamboo, open fuse to splice and retention 2- pole span secondary phase using approximately 30ft #2 AA, 3- one bolt clamps and 1-#2 preform reclose transformer and reset trip switch
Outage | J.E.26.07.07475 | C001843670 | Neckell Ormsby | St.Mary | Completed | Load_261725 | Highgate -110 | Jul 8, 2026 3:57pm | Jul 8, 2026 4:00pm | Jul 8, 2026 6:47pm | Jul 8, 2026 6:47pm | Jul 8, 2026 6:47pm | Jul 8, 2026 6:47pm | Jul 8, 2026 6:48pm | Jul 8, 2026 6:48pm |  |  | Fair | No | Found 25 kva transformer trip no pole # seen also broken secondary phase caused by fallen bamboo, open fuse to splice and retention 2- pole span secondary phase using approximately 30ft #2 AA, 3- one bolt clamps and 1-#2 preform reclose transformer and reset trip switch
Outage | J.E.26.07.07711 | C001843667 | Stephen Taylor | St.Thomas | Completed | Load_243194 | Good Year - 210 | Jul 8, 2026 3:57pm | Jul 8, 2026 3:58pm | Jul 8, 2026 5:17pm | Jul 8, 2026 7:03pm | Jul 8, 2026 7:39pm | Jul 8, 2026 7:39pm | Jul 8, 2026 7:40pm | Jul 8, 2026 7:40pm |  |  | Fair | No | Patrol see nothing and close up back junction with a 20 amp fuse safely all customer is now okay
Outage | J.E.26.07.07681 | C001843666 | Milton Charlton | KSAN | Completed | Load_555973 | Hope - 510 | Jul 8, 2026 3:55pm | Jul 8, 2026 3:56pm | Jul 8, 2026 6:02pm | Jul 8, 2026 6:02pm | Jul 8, 2026 6:41pm | Jul 8, 2026 6:45pm | Jul 8, 2026 6:53pm | Jul 8, 2026 6:53pm |  |  | Fair | No | Customer fed from hexing #00120 and is getting no supply from the box contact J.P.S. Escalation and they state there is no communication whit the box. Refer to field service.
Outage | J.E.26.07.07656 | C001843658 | Richman Whyte | Westmoreland | Completed | Load_259377 | Paradise - 310 | Jul 8, 2026 3:54pm | Jul 8, 2026 3:54pm | Jul 8, 2026 7:29pm | Jul 8, 2026 7:29pm | Jul 8, 2026 7:29pm | Jul 8, 2026 8:23pm | Jul 8, 2026 8:28pm | Jul 8, 2026 8:28pm |  |  | Fair | No | Replace two twenty amp junction fuse however line section needs urgent maintenance concrete pole need to straighten need crane truck and primary conductor need to retention please send referral to the maintenance department
Outage | J.E.26.07.07546 | C001843656 | Javid Vernon | Westmoreland | Completed | Load_240855 | Paradise - 310 | Jul 8, 2026 3:53pm | Jul 9, 2026 8:07am | Jul 9, 2026 8:26am | Jul 9, 2026 8:26am | Jul 9, 2026 9:56am | Jul 9, 2026 10:24am | Jul 9, 2026 10:24am | Jul 9, 2026 10:24am |  |  | Fair | No | Splice and retention customer service wire use 40ft #6 triplex and 2 clamps voltage reading 115/116/231
Outage | J.E.26.07.07591 | C001843657 | Javid Vernon | Westmoreland | Completed | Load_270211 | Paradise - 310 | Jul 8, 2026 3:53pm | Jul 9, 2026 8:07am | Jul 9, 2026 10:24am | Jul 9, 2026 10:24am | Jul 9, 2026 11:44am | Jul 9, 2026 12:13pm | Jul 9, 2026 12:13pm | Jul 9, 2026 12:13pm |  |  | Fair | No | Customer requesting a reconnection at the supermarket 150ft of #2 triplex wire refer to field service customer need urgent assistance they are still without power
Outage | J.E.26.06.01165 | C001843647 | Richman Whyte | Westmoreland | Completed | Load_240510 | Paradise - 310 | Jul 8, 2026 3:52pm | Jul 8, 2026 3:54pm | Jul 8, 2026 5:44pm | Jul 8, 2026 5:44pm | Jul 8, 2026 5:59pm | Jul 8, 2026 6:00pm | Jul 8, 2026 6:00pm | Jul 8, 2026 6:00pm |  |  | Fair | No | Premises found already connect
Outage | J.E.26.07.07311 | C001843651 | Cliton Henry | St.Ann | Completed | Load_354897 | Upper White River - 110 | Jul 8, 2026 3:52pm | Jul 8, 2026 3:53pm | Jul 8, 2026 8:15pm | Jul 8, 2026 8:15pm | Jul 8, 2026 8:15pm | Jul 8, 2026 8:15pm | Jul 8, 2026 8:16pm | Jul 8, 2026 8:16pm |  |  | Fair | No | Supply restored, related to outage #07672
Outage | J.E.26.07.07317 | C001843650 | Cliton Henry | St.Ann | Completed | Load_245937 | Upper White River - 110 | Jul 8, 2026 3:52pm | Jul 8, 2026 3:53pm | Jul 8, 2026 8:16pm | Jul 8, 2026 8:16pm | Jul 8, 2026 8:16pm | Jul 8, 2026 8:16pm | Jul 8, 2026 8:17pm | Jul 8, 2026 8:17pm |  |  | Fair | No | Supply restored, related to outage #07672
Outage | J.E.26.07.07372 | C001843654 | Cliton Henry | St.Ann | Completed | Load_247829 | Upper White River - 110 | Jul 8, 2026 3:52pm | Jul 8, 2026 3:53pm | Jul 8, 2026 8:12pm | Jul 8, 2026 8:12pm | Jul 8, 2026 8:12pm | Jul 8, 2026 8:13pm | Jul 8, 2026 8:14pm | Jul 8, 2026 8:14pm |  |  | Fair | No | Supply restored, related to outage # 07672
Outage | J.E.26.07.07488 | C001843652 | Richman Whyte | Westmoreland | Completed | Load_292085 | Paradise - 310 | Jul 8, 2026 3:52pm | Jul 8, 2026 3:54pm | Jul 8, 2026 4:02pm | Jul 8, 2026 4:02pm | Jul 8, 2026 4:48pm | Jul 8, 2026 5:08pm | Jul 8, 2026 5:09pm | Jul 8, 2026 5:09pm |  |  | Fair | No | Replace fuel holder and two amp twenty five kva transformer fuse
Outage | J.E.26.07.07672 | C001843653 | Cliton Henry | St.Ann | Completed | Load_245937 | Upper White River - 110 | Jul 8, 2026 3:52pm | Jul 8, 2026 3:53pm | Jul 8, 2026 6:08pm | Jul 8, 2026 6:08pm | Jul 8, 2026 7:10pm | Jul 8, 2026 8:07pm | Jul 8, 2026 8:09pm | Jul 8, 2026 8:09pm |  |  | Fair | No | A blown 30 amp junction fuse found at Cascade near Mr. Cole Property.. Supply restored using 1- 30 amp fuses
Outage | J.E.26.07.07690 | C001843655 | Cliton Henry | St.Mary | Completed | Load_261992 | Blackstonedge - 110 | Jul 8, 2026 3:52pm | Jul 8, 2026 9:18pm | Jul 8, 2026 10:26pm | Jul 8, 2026 10:26pm | Jul 8, 2026 10:27pm | Jul 8, 2026 10:27pm | Jul 8, 2026 10:28pm | Jul 8, 2026 10:28pm |  |  | Fair | No | Supply restored, related to outage 08183
Non-Outage | J.E.26.07.07272 | C001843643 | Richman Whyte | null | Completed | null | null | Jul 8, 2026 3:49pm | Jul 8, 2026 6:19pm | Jul 8, 2026 9:58pm | Jul 8, 2026 9:58pm | Jul 8, 2026 9:58pm | Jul 8, 2026 9:59pm | Jul 8, 2026 9:59pm | Jul 8, 2026 9:59pm |  |  | Fair | No | Related to the Brighton call
Non-Outage | J.E.26.07.07354 | C001843646 | Oshane Warren | null | Completed | null | null | Jul 8, 2026 3:49pm | Jul 8, 2026 3:50pm | Jul 8, 2026 6:04pm | Jul 8, 2026 6:04pm | Jul 8, 2026 6:16pm | Jul 8, 2026 6:17pm | Jul 8, 2026 6:23pm | Jul 8, 2026 6:23pm | LeaningPole |  | Fair | No | 40 foot wood pole with primary and xformer on it needs over head guy
Outage | J.E.26.07.07163 | C001843641 | Oshane Warren | Westmoreland | Completed | Load_247636 | Paradise - 210 | Jul 8, 2026 3:49pm | Jul 8, 2026 3:50pm | Jul 8, 2026 6:55pm | Jul 8, 2026 6:55pm | Jul 8, 2026 6:55pm | Jul 8, 2026 6:55pm | Jul 8, 2026 6:56pm | Jul 8, 2026 6:56pm |  |  | Fair | No | Customer stated that crew should visit in the morning
Outage | J.E.26.07.07393 | C001843642 | Oshane Warren | Westmoreland | Completed | Load_242053 | Paradise - 210 | Jul 8, 2026 3:49pm | Jul 8, 2026 3:50pm | Jul 8, 2026 4:41pm | Jul 8, 2026 4:41pm | Jul 8, 2026 5:35pm | Jul 8, 2026 5:36pm | Jul 8, 2026 5:36pm | Jul 8, 2026 5:36pm |  |  | Fair | No | Replace 5amp 50kva xformer fuse
Outage | J.E.26.07.07625 | C001843640 | Oshane Warren | Hanover | Completed | Load_247383 | Orange Bay - 310 | Jul 8, 2026 3:48pm | Jul 8, 2026 3:50pm | Jul 8, 2026 6:23pm | Jul 8, 2026 6:23pm | Jul 8, 2026 6:23pm | Jul 8, 2026 6:23pm | Jul 8, 2026 6:23pm | Jul 8, 2026 6:23pm |  |  | Fair | No | Unable to locate or contact customer
Outage | J.E.26.07.07491 | C001843639 | Roxroy Needham | St.Ann | Completed | Load_264147 | Cardiff Hall - 210 | Jul 8, 2026 3:47pm | Jul 8, 2026 3:49pm | Jul 8, 2026 3:57pm | Jul 8, 2026 3:57pm | Jul 8, 2026 4:04pm | Jul 8, 2026 4:05pm | Jul 8, 2026 4:05pm | Jul 8, 2026 4:05pm |  |  | Fair | No | Premises found ok customer have internal problem
Outage | J.E.26.07.07651 | C001843638 | Roxroy Needham | St.Ann | Completed | Load_257187 | Cardiff Hall - 310 | Jul 8, 2026 3:47pm | Jul 8, 2026 3:49pm | Jul 8, 2026 4:05pm | Jul 8, 2026 4:31pm | Jul 8, 2026 5:26pm | Jul 8, 2026 5:29pm | Jul 8, 2026 5:29pm | Jul 8, 2026 5:29pm |  |  | Fair | No | Use switch stick to Separate secondary phase from neutral and replace 1- 3 amp for a 25 KVA transformer
Outage | J.E.26.07.07592 | C001843632 | Barnett Brown | Manchester | Completed | Load_247360 | Kendal - 210 | Jul 8, 2026 3:40pm | Jul 8, 2026 3:42pm | Jul 8, 2026 4:36pm | Jul 8, 2026 4:36pm | Jul 8, 2026 6:43pm | Jul 8, 2026 6:59pm | Jul 8, 2026 7:04pm | Jul 8, 2026 7:04pm |  |  | Fair | No | Customer has internal fault, voltage 112 111 223
Non-Outage | J.E.26.07.07149 | C001843623 | Kaydon Taylor | null | Completed | null | null | Jul 8, 2026 3:38pm | Jul 8, 2026 3:48pm | Jul 8, 2026 6:25pm | Jul 8, 2026 7:18pm | Jul 8, 2026 7:18pm | Jul 8, 2026 8:52pm | Jul 8, 2026 8:52pm | Jul 8, 2026 8:52pm | BrokenWire |  | Fair | No | Splice broken neutral wire 150’ of #2 aaa conductors wire 2 #2 splicing sleeve 8 one bolt clamps also found a 25kva transformer fuse blown and replace at pole #0000706 3 amp.
Non-Outage | J.E.26.07.07322 | C001843624 | Milton Charlton | null | Completed | null | null | Jul 8, 2026 3:38pm | Jul 8, 2026 8:50pm | Jul 8, 2026 9:08pm | Jul 8, 2026 9:08pm | Jul 8, 2026 10:25pm | Jul 8, 2026 10:25pm | Jul 8, 2026 10:31pm | Jul 8, 2026 10:31pm | BrokenWire |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.07.07374 | C001843622 | Rusean Allen | KSAN | Completed | Load_243251 | Constant Spring - 410 | Jul 8, 2026 3:37pm | Jul 8, 2026 10:53pm | Jul 9, 2026 12:46am | Jul 9, 2026 12:46am | Jul 9, 2026 12:55am | Jul 9, 2026 12:57am | Jul 9, 2026 12:57am | Jul 9, 2026 12:57am | TreeContact,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Daylight attention required, customer stated it is better to visit in the morning.
Outage | J.E.26.07.07158 | C001843619 | Kaydon Taylor | KSAN | Completed | Load_262426 | Constant Spring - 410 | Jul 8, 2026 3:35pm | Jul 8, 2026 3:48pm | Jul 8, 2026 8:58pm | Jul 8, 2026 9:00pm | Jul 9, 2026 12:18am | Jul 9, 2026 12:25am | Jul 9, 2026 12:25am | Jul 9, 2026 12:25am | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Isolate 25kva transformer at pole # 0001491 to carry out repairs. Medium bushing of bamboo. Splicing 200’ of #2 aaa conductors wire with 3 splicing sleeves along with 7 one bolt clamps.
Outage | J.E.26.07.07560 | C001843614 | Romaine Roberts | St.Mary | Completed | Load_255395 | Highgate - 210 | Jul 8, 2026 3:33pm | Jul 8, 2026 3:34pm | Jul 8, 2026 6:40pm | Jul 8, 2026 6:40pm | Jul 8, 2026 6:40pm | Jul 8, 2026 6:40pm | Jul 8, 2026 6:41pm | Jul 8, 2026 6:41pm |  | Y | Fair | No | Tree fall on primary and secondary line and blown junction fuse patrol and spear tree lim from line and replace 30 amp power restore
Outage | J.E.26.07.07652 | C001843615 | Romaine Roberts | St.Mary | Completed | Load_269725 | Highgate - 210 | Jul 8, 2026 3:33pm | Jul 8, 2026 3:34pm | Jul 8, 2026 6:41pm | Jul 8, 2026 6:41pm | Jul 8, 2026 6:41pm | Jul 8, 2026 6:41pm | Jul 8, 2026 6:41pm | Jul 8, 2026 6:41pm |  |  | Fair | No | Tree fall on primary and secondary line and blown junction fuse patrol and spear tree lim from line and replace 30 amp power restore
Non-Outage | J.E.26.07.05997 | C001843613 | Lancelot Brown | Hanover | Completed | Load_555701 | Orange Bay - 210 | Jul 8, 2026 3:30pm | Jul 8, 2026 3:54pm | Jul 8, 2026 5:48pm | Jul 8, 2026 5:48pm | Jul 8, 2026 5:48pm | Jul 8, 2026 5:59pm | Jul 8, 2026 6:00pm | Jul 8, 2026 6:00pm | BrokenPole |  | Fair | No | Motor vehicle accident caused 35c4 wooden pole broke need to replace construction of pole is T pole with stand off bracket supply is still in the area please pass on to maintenance department in Hanover mr Richards need ergent attention
Outage | J.E.26.07.07341 | C001843609 | Andre Williams | Trelawny | Completed | Load_242493 | Greenwood - 110 | Jul 8, 2026 3:29pm | Jul 8, 2026 5:19pm | Jul 8, 2026 5:23pm | Jul 8, 2026 5:23pm | Jul 8, 2026 5:37pm | Jul 8, 2026 5:43pm | Jul 8, 2026 5:43pm | Jul 8, 2026 5:43pm |  |  | Fair | No | Area ok power was restored to area confirmed by call
Outage | J.E.26.07.07351 | C001843608 | Romaine Roberts | St.Mary | Completed | Load_242382 | Highgate - 210 | Jul 8, 2026 3:28pm | Jul 8, 2026 3:29pm | Jul 8, 2026 6:42pm | Jul 8, 2026 6:42pm | Jul 8, 2026 8:53pm | Jul 8, 2026 9:10pm | Jul 8, 2026 9:27pm | Jul 8, 2026 9:27pm | BangingWires | Y | Fair | No | Tree lim fall on primary line and blow junction fuse patrol and clear line replace a10 amp and 15 amp power restore line need bushing
Outage | J.E.26.07.07202 | C001843605 | Kaydon Taylor | KSAN | Completed | Load_247843 | Constant Spring - 210 | Jul 8, 2026 3:27pm | Jul 8, 2026 3:29pm | Jul 8, 2026 4:48pm | Jul 8, 2026 4:49pm | Jul 8, 2026 5:22pm | Jul 8, 2026 5:39pm | Jul 8, 2026 5:39pm | Jul 8, 2026 5:39pm |  |  | Fair | No | 15 amp junction fuse found blown and replaced at pole #0011758
Outage | J.E.26.07.07333 | C001843607 | Kaydon Taylor | KSAN | Completed | Load_254232 | Constant Spring - 310 | Jul 8, 2026 3:27pm | Jul 8, 2026 3:29pm | Jul 8, 2026 5:40pm | Jul 8, 2026 5:41pm | Jul 8, 2026 6:23pm | Jul 8, 2026 6:24pm | Jul 8, 2026 6:24pm | Jul 8, 2026 6:24pm | BrokenPole |  | Fair | No | 30’ pole found rotten needs urgent replacement
Outage | J.E.26.07.07477 | C001843606 | Kaydon Taylor | KSAN | Completed | Load_246923 | Constant Spring - 210 | Jul 8, 2026 3:27pm | Jul 8, 2026 3:29pm | Jul 8, 2026 3:45pm | Jul 8, 2026 3:45pm | Jul 8, 2026 4:26pm | Jul 8, 2026 4:46pm | Jul 8, 2026 4:46pm | Jul 8, 2026 4:46pm | BrokenWire |  | Fair | No | Defective #6 service wire was changed . 15’ of #2 triplex and (6) one bolt clamps. V 117-118-235
Outage | J.E.26.07.07135 | C001843602 | Selvin White | Manchester | Completed | Load_239389 | Spur Tree - 210 | Jul 8, 2026 3:26pm | Jul 8, 2026 3:27pm | Jul 8, 2026 4:20pm | Jul 8, 2026 4:38pm | Jul 8, 2026 5:51pm | Jul 8, 2026 6:14pm | Jul 8, 2026 6:14pm | Jul 8, 2026 6:14pm |  |  | Fair | No | Remade burnt off connection at secondary on customer’s service wire phase conductor caused by slack connection. Supply restored to the customer. Voltage readings left inside customer’s meter socket are 219, 110,109 volt.
Outage | J.E.26.07.07476 | C001843601 | Andrew Powell | Manchester | Completed | Load_252647 | Spur Tree - 210 | Jul 8, 2026 3:26pm | Jul 8, 2026 3:27pm | Jul 8, 2026 3:55pm | Jul 8, 2026 3:58pm | Jul 8, 2026 4:35pm | Jul 8, 2026 5:45pm | Jul 8, 2026 5:47pm | Jul 8, 2026 5:47pm | BrokenWire |  | SevereWind | No | Isolate and close 25 kva transformer circuit to repair two pole span of broken secondary lower phase conductor using one automatic splicing sleeves, 80 feet 2/0 AA conductor and three clamps, no pole number by switch location, restore supply okay.
Outage | J.E.26.07.07512 | C001843604 | Andrew Powell | Manchester | Completed | Load_266906 | Spur Tree - 210 | Jul 8, 2026 3:26pm | Jul 8, 2026 3:27pm | Jul 8, 2026 6:20pm | Jul 8, 2026 6:20pm | Jul 8, 2026 7:07pm | Jul 8, 2026 7:18pm | Jul 8, 2026 7:22pm | Jul 8, 2026 7:22pm | BrokenWire |  | SevereWind | No | Clear telephone strand from secondary lower phase conductor, restored supply to normal okay.
Outage | J.E.26.07.07435 | C001843600 | Romaine Roberts | St.Mary | Completed | Load_254941 | Highgate - 210 | Jul 8, 2026 3:25pm | Jul 8, 2026 3:25pm | Jul 8, 2026 6:39pm | Jul 8, 2026 6:39pm | Jul 8, 2026 6:39pm | Jul 8, 2026 6:40pm | Jul 8, 2026 6:40pm | Jul 8, 2026 6:40pm | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards | Y | Fair | No | Tree fall on primary and secondary line and blown junction fuse patrol and spear tree lim from line and replace 30 amp power restore
Outage | J.E.26.07.07632 | C001843598 | Kenroy Dale | Manchester | Completed | Load_270012 | Porus - 310 | Jul 8, 2026 3:23pm | Jul 8, 2026 3:23pm | Jul 8, 2026 3:33pm | Jul 8, 2026 5:14pm | Jul 8, 2026 9:07pm | Jul 8, 2026 9:49pm | Jul 8, 2026 9:55pm | Jul 8, 2026 9:55pm | Fire |  | Fair | No | 25 amp trip saver found, trip line patrol bamboo found on primary conductor, bamboo was removed and trip saver re-closed area now with supply
Outage | J.E.26.07.07367 | C001843596 | Michael Christian | St.James | Completed | Load_257668 | Queens Drive - 710 | Jul 8, 2026 3:21pm | Jul 8, 2026 3:22pm | Jul 8, 2026 4:46pm | Jul 8, 2026 4:47pm | Jul 8, 2026 5:29pm | Jul 8, 2026 5:34pm | Jul 8, 2026 5:34pm | Jul 8, 2026 5:34pm | Fire |  | Fair | No | Check and found okay no fire found
Outage | J.E.26.07.05765 | C001843593 | Shamour Haughton | Hanover | Completed | Load_269922 | Orange Bay - 310 | Jul 8, 2026 3:20pm | Jul 8, 2026 3:22pm | Jul 8, 2026 8:40pm | Jul 8, 2026 8:42pm | Jul 8, 2026 8:42pm | Jul 8, 2026 8:42pm | Jul 8, 2026 8:42pm | Jul 8, 2026 8:42pm |  |  | Fair | No | Customer states power was restored
Outage | J.E.26.07.07036 | C001843592 | Michael Christian | St.James | Completed | Load_292251 | Queens Drive - 710 | Jul 8, 2026 3:20pm | Jul 8, 2026 3:22pm | Jul 8, 2026 8:48pm | Jul 8, 2026 8:48pm | Jul 8, 2026 9:21pm | Jul 8, 2026 9:54pm | Jul 8, 2026 9:55pm | Jul 8, 2026 9:55pm |  |  | Fair | No | Found 1 defective clamp at secondary jumper replace voltage 110 109 221 at meter
Outage | J.E.26.07.07480 | C001843589 | Jermaine Williams | Clarendon | Completed | Load_301018 | Monymusk - 210 | Jul 8, 2026 3:19pm | Jul 8, 2026 3:26pm | Jul 8, 2026 5:26pm | Jul 8, 2026 5:26pm | Jul 8, 2026 5:45pm | Jul 8, 2026 5:48pm | Jul 8, 2026 6:15pm | Jul 8, 2026 6:15pm |  |  | SevereWind | No | Premises found ok.
Outage | J.E.26.07.07595 | C001843588 | Jermaine Williams | Clarendon | Completed | Load_251002 | Parnassus - 310 | Jul 8, 2026 3:19pm | Jul 8, 2026 3:25pm | Jul 8, 2026 4:14pm | Jul 8, 2026 4:18pm | Jul 8, 2026 4:46pm | Jul 8, 2026 4:55pm | Jul 8, 2026 5:22pm | Jul 8, 2026 5:22pm | Fire |  | Fair | No | Isolate 25kva xfmr clear banging conductors. Bushing required.
Non-Outage | J.E.26.07.07600 | C001843580 | Donald Cunningham | null | Completed | null | null | Jul 8, 2026 3:18pm | Jul 8, 2026 3:32pm | Jul 8, 2026 4:16pm | Jul 8, 2026 4:16pm | Jul 8, 2026 4:16pm | Jul 8, 2026 4:17pm | Jul 8, 2026 4:18pm | Jul 8, 2026 4:18pm | BrokenWire |  | Fair | No | Plan outage that side
Outage | J.E.26.07.07473 | C001843586 | Nickolas Rodriques | St.Catherine | Completed | Load_252004 | Tredegar - 510 | Jul 8, 2026 3:18pm | Jul 8, 2026 3:32pm | Jul 8, 2026 4:18pm | Jul 8, 2026 4:18pm | Jul 8, 2026 5:50pm | Jul 8, 2026 6:23pm | Jul 8, 2026 6:38pm | Jul 8, 2026 6:38pm | BrokenWire |  | Fair | No | Checked and found six(6) pole span of secondary phase and neutral down due to a tree that grows on to the wires. Isolate jumper at the transformer pole for safety to restore the other customers. The fuse was replaced after numerous patrols. Approximately 10 customers are still without power. Refer to maintenance.
Outage | J.E.26.07.07489 | C001843585 | Nickolas Rodriques | St.Catherine | Completed | Load_557299 | Tredegar - 410 | Jul 8, 2026 3:18pm | Jul 8, 2026 6:11pm | Jul 8, 2026 10:37pm | Jul 8, 2026 10:37pm | Jul 8, 2026 11:27pm | Jul 9, 2026 12:08am | Jul 9, 2026 12:09am | Jul 9, 2026 12:09am |  |  | Fair | No | Customer is having issues topping up her CIU box. Refer to field service.
Outage | J.E.26.07.07544 | C001843583 | Kemark Slue | St.Catherine | Completed | Load_1000334 | Tredegar - 210 | Jul 8, 2026 3:18pm | Jul 8, 2026 6:12pm | Jul 8, 2026 7:30pm | Jul 8, 2026 9:28pm | Jul 8, 2026 9:28pm | Jul 8, 2026 8:32pm | Jul 8, 2026 9:30pm | Jul 8, 2026 9:30pm |  |  | Fair | No | Upon arrival at the location the crew discovered that 20 amps bush phase from two phases at pole # 0092613 was blown, further patrol revealed a house that’s under construction is within close proximity to said primary conductor, it would appears that the conductor came into contact with a steel during construction, refuse link and re-energized line section.
Outage | J.E.26.07.07580 | C001843582 | Kemark Slue | St.Catherine | Completed | Load_568507 | Tredegar - 510 | Jul 8, 2026 3:18pm | Jul 8, 2026 4:52pm | Jul 8, 2026 6:19pm | Jul 8, 2026 7:38pm | Jul 8, 2026 7:38pm | Jul 8, 2026 7:01pm | Jul 8, 2026 7:39pm | Jul 8, 2026 7:39pm |  |  | Fair | No | Upon arrival at the location the crew discovered that road 20 amps junction from three phase T-off was blown resulting from the said primary line section being sagging and making contact with the telecommunications cable, retention conductor, refuse link and re-energized line section.
Outage | J.E.26.07.07610 | C001843581 | Ricky Hall | St.Catherine | Completed | Load_266292 | Tredegar - 310 | Jul 8, 2026 3:18pm | Jul 8, 2026 3:31pm | Jul 8, 2026 4:29pm | Jul 8, 2026 4:29pm | Jul 8, 2026 4:52pm | Jul 8, 2026 5:27pm | Jul 8, 2026 5:29pm | Jul 8, 2026 5:29pm |  |  | Fair | No | Leaking 25 kva xfmr in hexing enclosure request to have enclosure open to facilitate xfmr troubleshooting
Non-Outage | J.E.26.07.07584 | C001843575 | Ricky Hall | null | Completed | null | null | Jul 8, 2026 3:17pm | Jul 8, 2026 4:54pm | Jul 8, 2026 6:11pm | Jul 8, 2026 6:12pm | Jul 8, 2026 6:48pm | Jul 8, 2026 7:07pm | Jul 8, 2026 7:08pm | Jul 8, 2026 7:08pm | BrokenWire |  | Fair | No | Repair broken 3W service at pole use 1 clamp 120*2/240
Outage | J.E.26.07.07437 | C001843578 | Ricky Hall | Portmore | Completed | Load_252141 | Naggo Head - 510 | Jul 8, 2026 3:17pm | Jul 8, 2026 4:54pm | Jul 8, 2026 5:27pm | Jul 8, 2026 5:54pm | Jul 8, 2026 6:04pm | Jul 8, 2026 6:09pm | Jul 8, 2026 6:10pm | Jul 8, 2026 6:10pm |  |  | Fair | No | Area was restored previously
Outage | J.E.26.07.07472 | C001843579 | Ricky Hall | Portmore | Completed | Load_556710 | Naggo Head - 610 | Jul 8, 2026 3:17pm | Jul 8, 2026 4:54pm | Jul 8, 2026 5:13pm | Jul 8, 2026 5:34pm | Jul 8, 2026 5:45pm | Jul 8, 2026 5:50pm | Jul 8, 2026 5:50pm | Jul 8, 2026 5:50pm |  |  | Fair | No | Customer found with supply
Outage | J.E.26.07.07535 | C001843577 | Horace Malcolm | St.James | Completed | Load_412840 | Bogue - 310 | Jul 8, 2026 3:17pm | Jul 8, 2026 3:23pm | Jul 8, 2026 3:54pm | Jul 8, 2026 3:54pm | Jul 8, 2026 6:01pm | Jul 8, 2026 7:57pm | Jul 8, 2026 7:57pm | Jul 8, 2026 7:57pm |  | Y | Fair | No | Remove broken tree limb from primary and secondary lines to splice and retention 2pole span secondary phase and nuetral and 2pole span primary lines used 80 ft #2 conductor (4)#2 preforms and (4) clamps and refuse one 10amp junction fuse
Outage | J.E.26.07.07241 | C001843572 | Eric Williams | KSAN | Completed | Load_248430 | Washington Blvd - 310 | Jul 8, 2026 3:16pm | Jul 8, 2026 5:02pm | Jul 8, 2026 10:02pm | Jul 8, 2026 10:02pm | Jul 8, 2026 10:19pm | Jul 8, 2026 10:21pm | Jul 8, 2026 10:23pm | Jul 8, 2026 10:23pm |  |  | Fair | No | Blown 3amps fuse found and replace
Outage | J.E.26.07.07513 | C001843573 | Wayne Dillion | St.Elizabeth | Completed | Load_245938 | Maggotty - 110 | Jul 8, 2026 3:16pm | Jul 8, 2026 3:16pm | Jul 8, 2026 5:09pm | Jul 8, 2026 5:09pm | Jul 8, 2026 6:03pm | Jul 8, 2026 7:05pm | Jul 8, 2026 7:05pm | Jul 8, 2026 7:05pm |  |  | Fair | No | Patrol and found one blown 20amp junction fuse no pole #. Further checks reveals that a primary jumper was touching against the pole. Use hot stick to remove conductor from pole. Replace one 20amp junction fuse and supply restored okay.
Outage | J.E.26.07.07624 | C001843574 | Horace Malcolm | St.James | Completed | Load_263214 | Bogue - 310 | Jul 8, 2026 3:16pm | Jul 8, 2026 3:23pm | Jul 8, 2026 3:29pm | Jul 8, 2026 3:29pm | Jul 8, 2026 3:31pm | Jul 8, 2026 3:32pm | Jul 8, 2026 3:32pm | Jul 8, 2026 3:32pm |  |  | Fair | No | Call belongs to st Elizabeth
Outage | J.E.26.07.07326 | C001843567 | Edward Royal | KSAS | Completed | Load_266654 | Hunts Bay - 510 | Jul 8, 2026 3:15pm | Jul 8, 2026 5:16pm | Jul 8, 2026 5:34pm | Jul 8, 2026 5:45pm | Jul 8, 2026 5:45pm | Jul 8, 2026 5:45pm | Jul 8, 2026 5:46pm | Jul 8, 2026 5:46pm | BrokenWire |  | Fair | No | When contacted customer by phone customer stated nobody is at premises
Outage | J.E.26.07.07448 | C001843568 | Edward Royal | KSAS | Completed | Load_265406 | Hunts Bay - 210 | Jul 8, 2026 3:15pm | Jul 8, 2026 5:15pm | Jul 8, 2026 5:34pm | Jul 8, 2026 5:46pm | Jul 8, 2026 5:55pm | Jul 8, 2026 6:11pm | Jul 8, 2026 6:13pm | Jul 8, 2026 6:13pm | BrokenWire |  | Fair | No | Replaced 10A transformer fuse pole #0137817
Outage | J.E.26.07.07508 | C001843569 | Michael Christian | St.James | Completed | Load_261958 | Queens Drive - 710 | Jul 8, 2026 3:15pm | Jul 8, 2026 3:16pm | Jul 8, 2026 5:36pm | Jul 8, 2026 5:36pm | Jul 8, 2026 7:07pm | Jul 8, 2026 7:44pm | Jul 8, 2026 7:44pm | Jul 8, 2026 7:44pm |  |  | Fair | No | Found 1 25 amp junction out cause by truck replace 1 25 amp no pole #
Outage | J.E.26.07.07520 | C001843570 | Michael Christian | St.James | Completed | Load_291010 | Queens Drive - 310 | Jul 8, 2026 3:15pm | Jul 8, 2026 3:16pm | Jul 8, 2026 7:51pm | Jul 8, 2026 7:51pm | Jul 8, 2026 8:00pm | Jul 8, 2026 8:06pm | Jul 8, 2026 8:06pm | Jul 8, 2026 8:06pm |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.07038 | C001843559 | Shamour Haughton | St.James | Completed | Load_239760 | Bogue - 610 | Jul 8, 2026 3:14pm | Jul 8, 2026 3:17pm | Jul 8, 2026 4:07pm | Jul 8, 2026 4:08pm | Jul 8, 2026 4:16pm | Jul 8, 2026 5:24pm | Jul 8, 2026 5:34pm | Jul 8, 2026 5:34pm |  |  | Fair | No | Check and found customer experiencing internal problem, meter socket wire burnt, advise customer to get it fixed, voltage left 116,117,233
Outage | J.E.26.07.07114 | C001843560 | Shamour Haughton | St.James | Completed | Load_257498 | Bogue - 610 | Jul 8, 2026 3:14pm | Jul 8, 2026 3:17pm | Jul 8, 2026 8:10pm | Jul 8, 2026 8:10pm | Jul 8, 2026 8:27pm | Jul 8, 2026 8:28pm | Jul 8, 2026 8:32pm | Jul 8, 2026 8:32pm | LeaningPole |  | Fair | No | Found 40ft T pole leaning towards customers house, pole needs to straighten, please refer to maintenance
Outage | J.E.26.07.07626 | C001843565 | Shamour Haughton | St.James | Completed | Load_252450 | Bogue - 610 | Jul 8, 2026 3:14pm | Jul 8, 2026 3:17pm | Jul 8, 2026 3:59pm | Jul 8, 2026 5:38pm | Jul 8, 2026 6:25pm | Jul 8, 2026 8:04pm | Jul 8, 2026 8:09pm | Jul 8, 2026 8:09pm |  | Y | Fair | No | Found 4 pole span of secondary broken caused by tree falling on secondary,cut and remove tree from secondary, isolate 25kva to splice and retention secondary using 80ft #2 conductor and 4 clamps and reclose 25kva
Outage | J.E.26.07.07277 | C001843555 | Kenroy Dale | Manchester | Completed | Load_237934 | Porus - 310 | Jul 8, 2026 3:04pm | Jul 8, 2026 3:06pm | Jul 8, 2026 3:33pm | Jul 8, 2026 3:34pm | Jul 8, 2026 4:13pm | Jul 8, 2026 5:12pm | Jul 8, 2026 5:13pm | Jul 8, 2026 5:13pm |  |  | Fair | No | Blown 20 amp junction and 3 amp transformer fuse found. Line patrol nothing found (suspected illegal connection) blown fuses were replaced and area now with supply
Outage | J.E.26.07.07572 | C001843554 | Andre Williams | Trelawny | Completed | Load_300479 | Greenwood - 110 | Jul 8, 2026 3:01pm | Jul 8, 2026 3:03pm | Jul 8, 2026 3:35pm | Jul 8, 2026 3:38pm | Jul 8, 2026 4:38pm | Jul 8, 2026 5:20pm | Jul 8, 2026 5:20pm | Jul 8, 2026 5:20pm |  |  | Fair | No | Use pole top lap and pole type insulator on 30 foot pole to put space between pole head and single phase primary that was touching,re fuse and close blown 15 amp main junction fuse
Outage | J.E.26.07.07443 | C001843529 | Jermaine Williams | Clarendon | Completed | Load_265981 | Monymusk - 410 | Jul 8, 2026 2:17pm | Jul 8, 2026 3:27pm | Jul 8, 2026 6:44pm | Jul 8, 2026 6:44pm | Jul 8, 2026 7:50pm | Jul 8, 2026 7:21pm | Jul 8, 2026 7:52pm | Jul 8, 2026 7:52pm |  |  | SevereWind | No | Splice and retention broken service wire.
Outage | J.E.26.07.07451 | C001843527 | Neckell Ormsby | St.Mary | Completed | Load_268858 | Highgate -110 | Jul 8, 2026 2:16pm | Jul 8, 2026 3:56pm | Jul 8, 2026 4:01pm | Jul 8, 2026 4:02pm | Jul 8, 2026 5:43pm | Jul 8, 2026 6:45pm | Jul 8, 2026 6:47pm | Jul 8, 2026 6:47pm | Fire |  | Fair | No | Found 25 kva transformer trip no pole # seen also broken secondary phase caused by fallen bamboo, open fuse to splice and retention 2- pole span secondary phase using approximately 30ft #2 AA, 3- one bolt clamps and 1-#2 preform reclose transformer and reset trip switch
Non-Outage | J.E.26.06.24494 | C001843521 | Odeanie Davis | KSAS | Completed | Load_238571 | Rockfort - 210 | Jul 8, 2026 2:07pm | Jul 8, 2026 2:07pm | Jul 9, 2026 7:31am | Jul 9, 2026 1:37pm | Jul 9, 2026 1:37pm | Jul 9, 2026 2:12pm | Jul 9, 2026 3:06pm | Jul 9, 2026 3:06pm |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.06.38423 | C001843520 | Odeanie Davis | KSAS | Completed | Load_266339 | Rockfort - 410 | Jul 8, 2026 2:07pm | Jul 8, 2026 2:07pm | Jul 9, 2026 7:31am | Jul 9, 2026 1:35pm | Jul 9, 2026 1:35pm | Jul 9, 2026 1:55pm | Jul 9, 2026 1:37pm | Jul 9, 2026 1:37pm |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.06.39870 | C001843519 | Odeanie Davis | KSAS | Completed | Load_266339 | Rockfort - 410 | Jul 8, 2026 2:06pm | Jul 8, 2026 2:07pm | Jul 9, 2026 7:31am | Jul 9, 2026 1:18pm | Jul 9, 2026 1:18pm | Jul 9, 2026 1:27pm | Jul 9, 2026 1:35pm | Jul 9, 2026 1:35pm |  |  | Fair | No | Customer stated that issue was resolved resolved.l?
Outage | J.E.26.07.07351 | C001843513 | Evan Spaulding | St.Mary | Completed | Load_242382 | Highgate - 210 | Jul 8, 2026 2:02pm | Jul 8, 2026 2:03pm | Jul 9, 2026 8:17am | Jul 9, 2026 8:17am | Jul 9, 2026 8:17am | Jul 9, 2026 8:17am | Jul 9, 2026 8:18am | Jul 9, 2026 8:18am | BangingWires |  | Fair | No | Power was restored yesterday
Outage | J.E.26.07.07441 | C001843512 | Raymond Lewis | St.Ann | Completed | Load_259193 | Roaring River - 210 | Jul 8, 2026 2:02pm | Jul 8, 2026 2:03pm | Jul 8, 2026 3:01pm | Jul 8, 2026 3:01pm | Jul 8, 2026 3:01pm | Jul 8, 2026 3:31pm | Jul 9, 2026 8:47am | Jul 9, 2026 8:47am |  |  | SevereWind | No | Refuse and close 30 A junction
Outage | J.E.26.07.07153 | C001843501 | Clyde Brown | St.Ann | Completed | Load_248136 | Cardiff Hall - 310 | Jul 8, 2026 1:50pm | Jul 8, 2026 3:29pm | Jul 8, 2026 3:52pm | Jul 8, 2026 3:52pm | Jul 8, 2026 4:59pm | Jul 8, 2026 5:40pm | Jul 8, 2026 5:49pm | Jul 8, 2026 5:49pm | BrokenWire |  | Fair | No | Broken secondary phase caused by truck open 25kva transformer and repaired broken secondary phase with 8ft-#2/0 conductor,2- splicing sleeve ,1- preform and 1- clamp.
Outage | J.E.26.07.07415 | C001843498 | Tyrese Williams | St.Ann | Completed | Load_242184 | Cardiff Hall - 210 | Jul 8, 2026 1:49pm | Jul 8, 2026 1:50pm | Jul 8, 2026 2:06pm | Jul 8, 2026 2:27pm | Jul 8, 2026 2:27pm | Jul 8, 2026 2:28pm | Jul 8, 2026 2:28pm | Jul 8, 2026 2:28pm |  |  | Fair | No | Premises found ok call related to the 20 amp junction fuse at pole
Outage | J.E.26.07.07236 | C001843487 | Wayne Dillion | St.Elizabeth | Completed | Load_239662 | Maggotty - 110 | Jul 8, 2026 1:32pm | Jul 8, 2026 3:18pm | Jul 8, 2026 7:58pm | Jul 8, 2026 7:58pm | Jul 8, 2026 7:58pm | Jul 8, 2026 8:01pm | Jul 8, 2026 8:01pm | Jul 8, 2026 8:01pm |  |  | Fair | No | Unable to locate and customer is not answering the phone.
Outage | J.E.26.07.07405 | C001843486 | Floyd Taylor | Trelawny | Completed | Load_267411 | Greenwood - 110 | Jul 8, 2026 1:31pm | Jul 8, 2026 1:31pm | Jul 8, 2026 2:12pm | Jul 8, 2026 2:12pm | Jul 8, 2026 2:30pm | Jul 8, 2026 2:44pm | Jul 8, 2026 2:51pm | Jul 8, 2026 2:51pm |  |  | Fair | No | Fuse holder dislodged and was re-closed, voltage reading 118,119,237
Outage | J.E.26.07.07417 | C001843485 | Andre Williams | Trelawny | Completed | Load_269894 | Greenwood - 110 | Jul 8, 2026 1:31pm | Jul 8, 2026 3:04pm | Jul 8, 2026 5:21pm | Jul 8, 2026 5:43pm | Jul 8, 2026 5:43pm | Jul 8, 2026 5:46pm | Jul 8, 2026 5:46pm | Jul 8, 2026 5:46pm | BrokenPole |  | Fair | No | Customer with supply , concern is a bout guy rod that is showing signs of rot ( picture was send need urgent attention reffer to maintenance )
Outage | J.E.26.07.07429 | C001843481 | Nickolas Rodriques | St.Catherine | Completed | Load_262986 | Tredegar - 510 | Jul 8, 2026 1:27pm | Jul 8, 2026 3:37pm | Jul 8, 2026 8:53pm | Jul 8, 2026 8:53pm | Jul 8, 2026 10:02pm | Jul 8, 2026 10:34pm | Jul 8, 2026 10:36pm | Jul 8, 2026 10:36pm | BrokenWire |  | Fair | No | Power restored. Customer confirmed that the issue was resolved earlier. No broken wire seen.
Outage | J.E.26.07.07434 | C001843480 | Tyrese Williams | St.Ann | Completed | Load_264411 | Cardiff Hall - 310 | Jul 8, 2026 1:26pm | Jul 8, 2026 1:26pm | Jul 8, 2026 1:35pm | Jul 8, 2026 2:28pm | Jul 8, 2026 3:00pm | Jul 8, 2026 3:16pm | Jul 8, 2026 3:17pm | Jul 8, 2026 3:17pm |  |  | Fair | No | Cut tree off secondary phase and neutral line and Replace a 25 kva transformer fuse with a 2 amp at pole
Outage | J.E.26.07.07362 | C001843470 | Javid Vernon | Westmoreland | Completed | Load_259377 | Paradise - 310 | Jul 8, 2026 1:19pm | Jul 8, 2026 1:22pm | Jul 8, 2026 2:37pm | Jul 8, 2026 2:37pm | Jul 9, 2026 7:47am | Jul 9, 2026 7:47am | Jul 9, 2026 7:49am | Jul 9, 2026 7:49am |  |  | Fair | No | Customer stated that another crew came and restored the power yesterday
Outage | J.E.26.07.07421 | C001843462 | Jermaine Williams | Clarendon | Completed | Load_263900 | Monymusk - 210 | Jul 8, 2026 1:18pm | Jul 8, 2026 3:27pm | Jul 8, 2026 6:17pm | Jul 8, 2026 6:17pm | Jul 8, 2026 6:43pm | Jul 8, 2026 6:43pm | Jul 8, 2026 6:43pm | Jul 8, 2026 6:43pm |  |  | SevereWind | No | Hexing at location, refer to Hopeton Daley.
Outage | J.E.26.07.07370 | C001843450 | Neville Spencer | Clarendon | Completed | Load_239213 | May Pen - 110 | Jul 8, 2026 1:04pm | Jul 8, 2026 1:21pm | Jul 8, 2026 3:19pm | Jul 8, 2026 3:19pm | Jul 8, 2026 3:19pm | Jul 8, 2026 3:19pm | Jul 8, 2026 3:21pm | Jul 8, 2026 3:21pm | Fire |  | Fair | No | Cleared bamboo from secondary lines splice and retention broken secondary phase and neutral conductor used 70 ft wire, 2 clamps voltage, 2, preform supply restored.
Outage | J.E.26.07.07363 | C001843443 | Nickolas Rodriques | St.Catherine | Completed | Load_238248 | Rhodens Pen - 210 | Jul 8, 2026 1:01pm | Jul 8, 2026 1:02pm | Jul 8, 2026 1:05pm | Jul 8, 2026 1:06pm | Jul 8, 2026 1:38pm | Jul 8, 2026 1:49pm | Jul 8, 2026 1:52pm | Jul 8, 2026 1:52pm |  |  | Fair | No | Checked and found two 50 amp junction fuses blown at three phase line caused by a defective fuse holder. Repaired by replacing the fuses and a fuse holder after numerous patrols.
Outage | J.E.26.07.07011 | C001843432 | Cliton Henry | St.Mary | Completed | Load_265293 | Blackstonedge - 110 | Jul 8, 2026 12:53pm | Jul 8, 2026 3:50pm | Jul 8, 2026 8:19pm | Jul 8, 2026 8:19pm | Jul 8, 2026 8:19pm | Jul 8, 2026 8:19pm | Jul 8, 2026 8:20pm | Jul 8, 2026 8:20pm |  |  | Fair | No | Supply restored, related to outage #07672
Outage | J.E.26.07.07238 | C001843427 | Richard Nicholas | St.Catherine | Completed | Load_263287 | Tredegar - 410 | Jul 8, 2026 12:49pm | Jul 8, 2026 12:50pm | Jul 8, 2026 1:17pm | Jul 8, 2026 1:17pm | Jul 8, 2026 2:10pm | Jul 8, 2026 3:04pm | Jul 8, 2026 3:06pm | Jul 8, 2026 3:06pm |  |  | Fair | No | Replaced blown 30amp x2 junctions fuse on pole #055532.leaning pole need to be straightened and primary conductors to retention.
Non-Outage | J.E.26.07.07287 | C001843405 | Stephen Taylor | null | Completed | null | null | Jul 8, 2026 12:34pm | Jul 8, 2026 12:56pm | Jul 8, 2026 3:31pm | Jul 8, 2026 3:31pm | Jul 8, 2026 3:31pm | Jul 8, 2026 3:31pm | Jul 8, 2026 3:31pm | Jul 8, 2026 3:31pm | TreeContact |  | Fair | No | See two 20 amp trip saver down patrol and see a tree drop on the line 3 span of primary wire are on the ground need assistance from the jps maintenance team to restore power to the community isolated at pole number 0209377
Outage | J.E.26.07.07105 | C001843389 | Stephen Taylor | St.Thomas | Completed | Load_243177 | Good Year - 110 | Jul 8, 2026 12:34pm | Jul 8, 2026 12:35pm | Jul 8, 2026 1:46pm | Jul 8, 2026 1:46pm | Jul 8, 2026 2:02pm | Jul 8, 2026 2:02pm | Jul 8, 2026 2:03pm | Jul 8, 2026 2:03pm |  |  | Fair | No | Contact customer and customer say that power was restored and now okay
Outage | J.E.26.07.07164 | C001843390 | Stephen Taylor | St.Thomas | Completed | Load_265365 | Good Year - 110 | Jul 8, 2026 12:34pm | Jul 8, 2026 12:35pm | Jul 8, 2026 12:39pm | Jul 8, 2026 12:39pm | Jul 8, 2026 1:06pm | Jul 8, 2026 1:06pm | Jul 8, 2026 1:45pm | Jul 8, 2026 1:45pm | Fire |  | Fair | No | Splice and retention 2 span of secondary wire and use 3 clamps 30 feet of aluminum wire and reset 25 kva transformer all customer is now okay
Outage | J.E.26.07.07166 | C001843403 | Stephen Taylor | St.Thomas | Completed | Load_269057 | Lysson - 410 | Jul 8, 2026 12:34pm | Jul 8, 2026 12:35pm | Jul 8, 2026 3:32pm | Jul 8, 2026 3:32pm | Jul 8, 2026 5:09pm | Jul 8, 2026 5:09pm | Jul 8, 2026 5:16pm | Jul 8, 2026 5:16pm |  |  | Fair | No | Patrol and clear line with switch stick and reset 10 amp transformer safely all customer is now ok
Outage | J.E.26.07.07305 | C001843402 | Stephen Taylor | St.Thomas | Completed | Load_267304 | Lysson - 410 | Jul 8, 2026 12:34pm | Jul 8, 2026 12:35pm | Jul 8, 2026 2:03pm | Jul 8, 2026 2:03pm | Jul 8, 2026 3:22pm | Jul 8, 2026 3:29pm | Jul 8, 2026 3:29pm | Jul 8, 2026 3:29pm |  |  | Fair | No | See two 20 amp trip saver down patrol and see a tree drop on the line 3 span of primary wire are on the ground need assistance from the jps maintenance team to restore power to the community isolated at pole number 0209377
Outage | J.E.26.07.07348 | C001843404 | Stephen Taylor | St.Thomas | Completed | Load_261193 | Lysson - 410 | Jul 8, 2026 12:34pm | Jul 8, 2026 12:37pm | Jul 8, 2026 3:30pm | Jul 8, 2026 3:30pm | Jul 8, 2026 3:30pm | Jul 8, 2026 3:30pm | Jul 8, 2026 3:30pm | Jul 8, 2026 3:30pm |  |  | Fair | No | See two 20 amp trip saver down patrol and see a tree drop on the line 3 span of primary wire are on the ground need assistance from the jps maintenance team to restore power to the community isolated at pole number 0209377
Outage | J.E.26.07.07315 | C001843381 | Oshane Warren | Hanover | Completed | Load_238747 | Orange Bay - 310 | Jul 8, 2026 12:24pm | Jul 9, 2026 8:04am | Jul 9, 2026 8:57am | Jul 9, 2026 8:57am | Jul 9, 2026 10:56am | Jul 9, 2026 11:03am | Jul 9, 2026 11:04am | Jul 9, 2026 11:04am | BrokenWire |  | Fair | No | Reconnect back service wire at secondary line
Outage | J.E.26.07.07065 | C001843365 | Christopher Edwards | KSAN | Completed | Load_242752 | Constant Spring - 410 | Jul 8, 2026 12:11pm | Jul 8, 2026 12:12pm | Jul 8, 2026 2:34pm | Jul 8, 2026 2:34pm | Jul 8, 2026 2:34pm | Jul 8, 2026 2:34pm | Jul 8, 2026 2:34pm | Jul 8, 2026 2:34pm |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Outage | J.E.26.07.07237 | C001843360 | Milton Charlton | KSAN | Completed | Load_249298 | Hope - 510 | Jul 8, 2026 12:08pm | Jul 8, 2026 12:08pm | Jul 8, 2026 2:00pm | Jul 8, 2026 3:18pm | Jul 8, 2026 3:21pm | Jul 8, 2026 3:25pm | Jul 8, 2026 3:27pm | Jul 8, 2026 3:27pm | BrokenWire |  | Fair | No | 30ft wooden pole planted at location only need to be transferred and raised secondary conductor and replace rotten crossarm that’s broken. Refer to maintenance.
Outage | J.E.26.07.07089 | C001843359 | Milton Charlton | KSAN | Completed | Load_259179 | Hope - 510 | Jul 8, 2026 12:07pm | Jul 8, 2026 12:08pm | Jul 8, 2026 3:27pm | Jul 8, 2026 3:27pm | Jul 8, 2026 6:01pm | Jul 8, 2026 6:00pm | Jul 8, 2026 6:02pm | Jul 8, 2026 6:02pm |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.07.07075 | C001843358 | Elvis Trowers | KSAS | Completed | Load_239147 | Duhaney - 310 | Jul 8, 2026 12:06pm | Jul 8, 2026 12:07pm | Jul 8, 2026 1:40pm | Jul 8, 2026 1:40pm | Jul 8, 2026 1:56pm | Jul 8, 2026 2:15pm | Jul 8, 2026 2:15pm | Jul 8, 2026 2:15pm |  |  | Fair | Yes | Areas was found without electricity supply when checked, and 2 blown fuses were found at separate locations, a 15 amp junction fuse at pole #0052729 and a 5 amp transformer fuse at pole #0017734.
Outage | J.E.26.07.07241 | C001843357 | Rusean Allen | KSAN | Completed | Load_248430 | Washington Blvd - 310 | Jul 8, 2026 12:04pm | Jul 8, 2026 12:05pm | Jul 8, 2026 12:32pm | Jul 8, 2026 12:32pm | Jul 8, 2026 1:12pm | Jul 8, 2026 1:15pm | Jul 8, 2026 1:15pm | Jul 8, 2026 1:15pm |  |  | Fair | No | Vehicle park at pole where repairs needs to be done.
Outage | J.E.26.07.07232 | C001843350 | Ryan Richards | Manchester | Completed | Load_303014 | Kendal - 210 | Jul 8, 2026 12:02pm | Jul 8, 2026 12:02pm | Jul 8, 2026 1:45pm | Jul 8, 2026 1:45pm | Jul 8, 2026 3:13pm | Jul 8, 2026 5:21pm | Jul 8, 2026 5:21pm | Jul 8, 2026 5:21pm |  |  | Fair | No | Premises found ok breaker in the meter socket his defective and needs to be replaced customer has been advised
Non-Outage | J.E.26.07.07162 | C001843344 | Raymond Lewis | St.Ann | Completed | Load_242634 | Roaring River - 410 | Jul 8, 2026 11:59am | Jul 8, 2026 12:01pm | Jul 8, 2026 12:57pm | Jul 8, 2026 12:57pm | Jul 8, 2026 1:05pm | Jul 8, 2026 1:16pm | Jul 8, 2026 1:17pm | Jul 8, 2026 1:17pm |  |  | Fair | No | Voltage found 111:112:223
Outage | J.E.26.07.07269 | C001843342 | Evan Spaulding | St.Mary | Completed | Load_250597 | Annotto Bay - 210 | Jul 8, 2026 11:59am | Jul 8, 2026 12:01pm | Jul 8, 2026 12:28pm | Jul 8, 2026 12:28pm | Jul 8, 2026 2:26pm | Jul 8, 2026 2:32pm | Jul 8, 2026 2:33pm | Jul 8, 2026 2:33pm | Fire |  | SevereWind | No | Splice and retention two spans secondary conductors using 60ft #2 AAAC conductor,1-#2 preform and 2-1bolt clamps.
Outage | J.E.26.07.07266 | C001843334 | Jermaine Williams | Clarendon | Completed | Load_263678 | May Pen - 210 | Jul 8, 2026 11:54am | Jul 8, 2026 3:27pm | Jul 8, 2026 9:16pm | Jul 8, 2026 9:16pm | Jul 8, 2026 9:16pm | Jul 8, 2026 8:21pm | Jul 8, 2026 9:17pm | Jul 8, 2026 9:17pm |  |  | Fair | No | Premises not located.
Outage | J.E.26.07.07248 | C001843325 | Raymond Carr | St.Mary | Completed | Load_353121 | Blackstonedge - 110 | Jul 8, 2026 11:45am | Jul 8, 2026 11:46am | Jul 8, 2026 1:21pm | Jul 8, 2026 1:21pm | Jul 8, 2026 1:43pm | Jul 8, 2026 2:17pm | Jul 8, 2026 2:20pm | Jul 8, 2026 2:20pm | BrokenWire |  | SevereWind | No | Spliced and retention 1 span of broken secondary conductor using 2 clamps, 1#2 preform, 50 ft#2 AA conductor. Supply was restored.
Outage | J.E.26.07.07059 | C001843321 | Hartley Chin | Clarendon | Completed | Load_247213 | Parnassus - 310 | Jul 8, 2026 11:42am | Jul 8, 2026 11:45am | Jul 8, 2026 12:17pm | Jul 8, 2026 12:17pm | Jul 8, 2026 12:26pm | Jul 8, 2026 12:32pm | Jul 8, 2026 12:41pm | Jul 8, 2026 12:41pm | BrokenWire |  | Fair | No | Prem not found … unable to contact customer.. area patrolled unable find meter … contacted escalation was told that 8762070061 is the only contact available…
Outage | J.E.26.07.07180 | C001843318 | Omar King | St.Ann | Completed | Load_246669 | Ocho Rios - 510 | Jul 8, 2026 11:39am | Jul 8, 2026 11:40am | Jul 8, 2026 1:04pm | Jul 8, 2026 1:04pm | Jul 8, 2026 2:02pm | Jul 8, 2026 2:58pm | Jul 8, 2026 2:59pm | Jul 8, 2026 2:59pm | LowHangingWires |  | Fair | No | Found 30 feet class #6 dead end pole broken effect from hurricane Melissa please refer to maintenance customer is still with supply
Non-Outage | J.E.26.07.05864 | C001843316 | Fitzroy Turner | KSAN | Completed | Load_263322 | Washington Blvd - 410 | Jul 8, 2026 11:38am | Jul 8, 2026 11:38am | Jul 8, 2026 1:02pm | Jul 8, 2026 1:02pm | Jul 8, 2026 1:03pm | Jul 8, 2026 1:05pm | Jul 8, 2026 1:10pm | Jul 8, 2026 1:10pm |  |  | Fair | No | Customer service relocated to a better feed voltage found 106/107 213 voltage readings left 116/116 234 no material use
Outage | J.E.26.07.07194 | C001843315 | Romaine Roberts | St.Mary | Completed | Load_256363 | Highgate - 210 | Jul 8, 2026 11:35am | Jul 8, 2026 3:27pm | Jul 8, 2026 4:09pm | Jul 8, 2026 4:09pm | Jul 8, 2026 5:45pm | Jul 8, 2026 6:36pm | Jul 8, 2026 6:38pm | Jul 8, 2026 6:38pm |  | Y | Fair | No | Tree fall on primary and secondary line and blown junction fuse patrol and spear tree lim from line and replace 30 amp power restore
Outage | J.E.26.07.07224 | C001843314 | Cliton Henry | St.Mary | Completed | Load_576544 | Oracabessa - 110 | Jul 8, 2026 11:35am | Jul 8, 2026 3:50pm | Jul 8, 2026 4:03pm | Jul 8, 2026 4:03pm | Jul 8, 2026 4:37pm | Jul 8, 2026 6:07pm | Jul 8, 2026 6:07pm | Jul 8, 2026 6:07pm |  |  | Fair | No | A blown 2 amp fuse found due to broken secondary conductors. Corrective work done to spliced and retention secondary phase conductors using approximately 30 feet 2/0 AA conductor, 2-2/0 splicing sleeve and 2-2/0 preform. Supply restored using 1-2 amp fuse.
Outage | J.E.26.07.07064 | C001843307 | Rusean Allen | KSAN | Completed | Load_251103 | Washington Blvd - 710 | Jul 8, 2026 11:33am | Jul 8, 2026 11:34am | Jul 8, 2026 1:16pm | Jul 8, 2026 1:16pm | Jul 8, 2026 1:22pm | Jul 8, 2026 1:22pm | Jul 8, 2026 1:23pm | Jul 8, 2026 1:23pm | Fire |  | Fair | No | Premises locked
Outage | J.E.26.07.06888 | C001843306 | Raymond Carr | St.Mary | Completed | Load_248758 | Blackstonedge - 110 | Jul 8, 2026 11:32am | Jul 8, 2026 11:32am | Jul 8, 2026 2:20pm | Jul 8, 2026 2:20pm | Jul 8, 2026 2:25pm | Jul 8, 2026 4:00pm | Jul 8, 2026 3:56pm | Jul 8, 2026 3:56pm |  |  | SevereWind | No | Three spans of sagging secondary conductors were tensioned. Supply was restored.
Non-Outage | J.E.26.07.07184 | C001843301 | Marlon Brown | Trelawny | Completed | Load_248221 | Duncans - 210 | Jul 8, 2026 11:28am | Jul 8, 2026 11:28am | Jul 8, 2026 11:41am | Jul 8, 2026 11:41am | Jul 8, 2026 11:53am | Jul 8, 2026 12:01pm | Jul 8, 2026 12:01pm | Jul 8, 2026 12:01pm | Fire |  | Fair | No | Clear broken wire from secondary.
Non-Outage | J.E.26.07.07097 | C001843299 | Tajay Bernard | Hanover | Completed | Load_240791 | Orange Bay - 310 | Jul 8, 2026 11:26am | Jul 8, 2026 11:27am | Jul 8, 2026 12:09pm | Jul 8, 2026 12:10pm | Jul 8, 2026 12:35pm | Jul 8, 2026 12:45pm | Jul 8, 2026 12:46pm | Jul 8, 2026 12:46pm |  |  | Fair | No | Customer has internal problemCustomer meter socket is defective
Non-Outage | J.E.26.07.06914 | C001843298 | Fitzroy Turner | KSAN | Completed | Load_257150 | West Kings House - 210 | Jul 8, 2026 11:25am | Jul 8, 2026 11:26am | Jul 8, 2026 1:52pm | Jul 8, 2026 1:52pm | Jul 8, 2026 1:52pm | Jul 8, 2026 1:53pm | Jul 8, 2026 1:54pm | Jul 8, 2026 1:54pm |  |  | Fair | No | Customer supply restored after replaced blown 5amp fuse found in bank of three transformer power fuse blown.supply restored
Outage | J.E.26.07.07027 | C001843296 | Fitzroy Turner | KSAN | Completed | Load_257150 | West Kings House - 210 | Jul 8, 2026 11:25am | Jul 8, 2026 11:26am | Jul 8, 2026 1:20pm | Jul 8, 2026 1:21pm | Jul 8, 2026 1:37pm | Jul 8, 2026 1:50pm | Jul 8, 2026 1:52pm | Jul 8, 2026 1:52pm |  |  | Fair | No | Found bank of three transformer 2 50 kva transformer and one 100kva transformer found one 5amp fuse blown replace one 5amp fuse supply restored to the areas
Outage | J.E.26.07.07060 | C001843297 | Fitzroy Turner | KSAN | Completed | Load_249346 | West Kings House - 210 | Jul 8, 2026 11:25am | Jul 8, 2026 11:26am | Jul 8, 2026 1:55pm | Jul 8, 2026 1:55pm | Jul 8, 2026 2:30pm | Jul 8, 2026 2:30pm | Jul 8, 2026 2:33pm | Jul 8, 2026 2:33pm |  |  | Fair | No | Found two 30 amps junction fuse blown cause by bird replaced two 30amps fuse supply restored to the areas
Outage | J.E.26.07.07199 | C001843288 | Romaine Roberts | St.Mary | Completed | Load_269725 | Highgate - 210 | Jul 8, 2026 11:24am | Jul 8, 2026 3:27pm | Jul 8, 2026 6:38pm | Jul 8, 2026 6:38pm | Jul 8, 2026 6:38pm | Jul 8, 2026 6:39pm | Jul 8, 2026 6:39pm | Jul 8, 2026 6:39pm |  | Y | Fair | No | Tree fall on primary and secondary line and blown junction fuse patrol and spear tree lim from line and replace 30 amp power restore
Non-Outage | J.E.26.07.07160 | C001843283 | Evan Spaulding | null | Completed | null | null | Jul 8, 2026 11:15am | Jul 8, 2026 11:15am | Jul 8, 2026 11:30am | Jul 8, 2026 11:30am | Jul 8, 2026 12:07pm | Jul 8, 2026 12:26pm | Jul 8, 2026 12:27pm | Jul 8, 2026 12:27pm |  | Y | Fair | No | Cut Bamboo from line and replace 1-10 amps junction fuse at pole number 0010689.
Non-Outage | J.E.26.07.07157 | C001843279 | Raymond Carr | St.Mary | Completed | Load_253688 | Blackstonedge - 110 | Jul 8, 2026 11:13am | Jul 8, 2026 11:14am | Jul 8, 2026 12:40pm | Jul 8, 2026 12:40pm | Jul 8, 2026 1:08pm | Jul 8, 2026 1:15pm | Jul 8, 2026 1:21pm | Jul 8, 2026 1:21pm |  |  | Fair | No | Supply found okay.
Outage | J.E.26.07.07095 | C001843260 | Tajay Bernard | Hanover | Completed | Load_239009 | Orange Bay - 310 | Jul 8, 2026 10:55am | Jul 8, 2026 10:56am | Jul 8, 2026 11:13am | Jul 8, 2026 11:13am | Jul 8, 2026 11:39am | Jul 8, 2026 12:08pm | Jul 8, 2026 12:09pm | Jul 8, 2026 12:09pm |  |  | Fair | No | Check and found customer meter pole defective, pole has to be straightened before any work can be done customer was advised
Outage | J.E.26.07.07132 | C001843249 | Richard Nicholas | St.Catherine | Completed | Load_569915 | Twickenham - 410 | Jul 8, 2026 10:48am | Jul 8, 2026 10:53am | Jul 9, 2026 12:54pm | Jul 9, 2026 12:54pm | Jul 9, 2026 2:13pm | Jul 9, 2026 2:41pm | Jul 9, 2026 2:42pm | Jul 9, 2026 2:42pm |  |  | Fair | No | Prepaid rammy system
Outage | J.E.26.07.07067 | C001843243 | Tyrese Williams | St.Ann | Completed | Load_242184 | Cardiff Hall - 210 | Jul 8, 2026 10:42am | Jul 8, 2026 11:46am | Jul 8, 2026 12:34pm | Jul 8, 2026 1:35pm | Jul 8, 2026 2:18pm | Jul 8, 2026 2:26pm | Jul 8, 2026 2:27pm | Jul 8, 2026 2:27pm |  |  | Fair | No | Remade a 20 amp junction fuse at pole
Outage | J.E.26.07.07085 | C001843242 | Tyrese Williams | St.Ann | Completed | Load_252558 | Cardiff Hall - 310 | Jul 8, 2026 10:42am | Jul 8, 2026 11:46am | Jul 8, 2026 12:34pm | Jul 8, 2026 12:35pm | Jul 8, 2026 1:33pm | Jul 8, 2026 1:34pm | Jul 8, 2026 1:34pm | Jul 8, 2026 1:34pm |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.07.06986 | C001843241 | Andrew Powell | Manchester | Completed | Load_258769 | Spur Tree - 210 | Jul 8, 2026 10:41am | Jul 8, 2026 3:25pm | Jul 8, 2026 5:49pm | Jul 8, 2026 5:49pm | Jul 8, 2026 6:10pm | Jul 8, 2026 6:18pm | Jul 8, 2026 6:19pm | Jul 8, 2026 6:19pm | BrokenWire |  | Fair | No | Premises not located inadequately direction contact customer by telephone unsuccessful.
Outage | J.E.26.07.06991 | C001843240 | Richard Samuda | Manchester | Completed | Load_265966 | Spur Tree - 210 | Jul 8, 2026 10:41am | Jul 8, 2026 3:19pm | Jul 8, 2026 3:21pm | Jul 8, 2026 8:31pm | Jul 8, 2026 8:59pm | Jul 8, 2026 9:22pm | Jul 8, 2026 9:22pm | Jul 8, 2026 9:22pm | BrokenWire |  | Fair | No | Change corroded 1bolt clamp on service wire that lead to customer premises that was corroded causing customer to experience low voltage 116/104/220/before 116/116/232
Outage | J.E.26.07.07074 | C001843224 | Richard Nicholas | St.Catherine | Completed | Load_255779 | Tredegar - 210 | Jul 8, 2026 10:22am | Jul 8, 2026 10:53am | Jul 8, 2026 12:17pm | Jul 8, 2026 12:17pm | Jul 8, 2026 1:04pm | Jul 8, 2026 1:15pm | Jul 8, 2026 1:16pm | Jul 8, 2026 1:16pm |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.07.07057 | C001843199 | Ricky Hall | null | Completed | null | null | Jul 8, 2026 10:08am | Jul 8, 2026 5:28pm | Jul 8, 2026 5:54pm | Jul 8, 2026 6:10pm | Jul 8, 2026 6:10pm | Jul 8, 2026 6:10pm | Jul 8, 2026 6:10pm | Jul 8, 2026 6:10pm |  |  | Fair | No | Issue was resolved previously
Non-Outage | J.E.26.07.07042 | C001843191 | Roemello Brown | Trelawny | Completed | Load_264547 | Duncans - 210 | Jul 8, 2026 10:04am | Jul 8, 2026 10:04am | Jul 8, 2026 12:37pm | Jul 8, 2026 12:37pm | Jul 8, 2026 2:30pm | Jul 8, 2026 2:31pm | Jul 8, 2026 3:18pm | Jul 8, 2026 3:18pm |  |  | Fair | No | Have clamps change at the pole side clamps corroded Voltage found 102/114/216Voltage leave 113/114/227
Non-Outage | J.E.26.07.02928 | C001843190 | Moses Elliston | Portmore | Completed | Load_258293 | Naggo Head - 510 | Jul 8, 2026 10:03am | Jul 8, 2026 10:03am | Jul 8, 2026 11:42am | Jul 8, 2026 11:42am | Jul 8, 2026 1:41pm | Jul 8, 2026 1:41pm | Jul 8, 2026 1:44pm | Jul 8, 2026 1:44pm |  |  | Fair | No | 3 Corroaded linkets changed at 3 wire service pothead 117-117-234 volts
Non-Outage | J.E.26.07.07033 | C001843189 | Roemello Brown | Trelawny | Completed | Load_269195 | Martha Brae - 210 | Jul 8, 2026 10:03am | Jul 8, 2026 10:04am | Jul 9, 2026 8:10am | Jul 9, 2026 8:10am | Jul 9, 2026 8:45am | Jul 9, 2026 8:45am | Jul 9, 2026 8:52am | Jul 9, 2026 8:52am |  |  | Fair | No | Premises found working okay however customer was reporting an over grown tree needs to be cut Voltage found 117/115/233Voltage leave 117/115/233
Outage | J.E.26.07.07025 | C001843185 | Michael Christian | St.James | Completed | Load_270234 | Queens Drive - 710 | Jul 8, 2026 9:59am | Jul 8, 2026 3:27pm | Jul 8, 2026 3:50pm | Jul 8, 2026 3:50pm | Jul 8, 2026 4:45pm | Jul 8, 2026 4:46pm | Jul 8, 2026 4:46pm | Jul 8, 2026 4:46pm | Fire |  | Fair | No | Check and found okay no fire found
Non-Outage | J.E.26.07.06979 | C001843184 | Omar King | St.Ann | Completed | Load_255188 | Ocho Rios - 310 | Jul 8, 2026 9:58am | Jul 8, 2026 10:06am | Jul 8, 2026 10:49am | Jul 8, 2026 10:49am | Jul 8, 2026 11:13am | Jul 8, 2026 12:49pm | Jul 8, 2026 12:49pm | Jul 8, 2026 12:49pm |  |  | Fair | No | Found a secondary neutral jumper one bolt clamp defective as been repaired customer is now with supply
Outage | J.E.26.07.06819 | C001843182 | Raymond Carr | St.Mary | Completed | Load_262319 | Blackstonedge - 110 | Jul 8, 2026 9:54am | Jul 8, 2026 9:54am | Jul 8, 2026 11:49am | Jul 8, 2026 11:49am | Jul 8, 2026 12:22pm | Jul 8, 2026 12:29pm | Jul 8, 2026 12:38pm | Jul 8, 2026 12:38pm |  |  | SevereWind | No | Blown junction fuse found at pole number 0194928, line patrol and found okay, unable to ascertain cause of outage. A 20 amp fuse fuse was used to renew supply was restored.
Outage | J.E.26.07.06878 | C001843180 | Evan Spaulding | St.Mary | Completed | Load_250597 | Annotto Bay - 210 | Jul 8, 2026 9:54am | Jul 8, 2026 9:54am | Jul 8, 2026 2:34pm | Jul 8, 2026 2:34pm | Jul 8, 2026 2:34pm | Jul 8, 2026 2:35pm | Jul 8, 2026 2:35pm | Jul 8, 2026 2:35pm | Fire |  | SevereWind | No | Associated call.
Non-Outage | J.E.26.07.07010 | C001843170 | Daniel Francis | null | Completed | null | null | Jul 8, 2026 9:46am | Jul 9, 2026 11:40am | Jul 9, 2026 1:58pm | Jul 9, 2026 1:58pm | Jul 9, 2026 3:16pm | Jul 9, 2026 3:29pm | Jul 9, 2026 3:30pm | Jul 9, 2026 3:30pm | LowHangingWires |  | Fair | No | Found secondary line making contact with flow strand cables seperate and safe
Outage | J.E.26.07.07008 | C001843163 | Hartley Chin | Clarendon | Completed | Load_241598 | Parnassus - 310 | Jul 8, 2026 9:44am | Jul 8, 2026 9:44am | Jul 8, 2026 9:55am | Jul 8, 2026 10:26am | Jul 8, 2026 10:26am | Jul 8, 2026 11:24am | Jul 8, 2026 11:35am | Jul 8, 2026 11:35am | BrokenWire |  | Fair | No | Isolate 25KVA transformer @ pole # 0125596 due to broken open secondary neutral found in 2 span … repair broken neutral, re-tension phase in 1 span … re-energized transformer… use 40 ft #2 Conductor, 4 clamp , 1 - #2 splicing sleeve , 2 - #2 preform , 1- 2/0 preform …
Outage | J.E.26.07.06939 | C001843153 | Derrick Dawkins | St.James | Completed | Load_266743 | Bogue - 310 | Jul 8, 2026 9:37am | Jul 8, 2026 9:37am | Jul 8, 2026 10:47am | Jul 8, 2026 10:47am | Jul 8, 2026 10:54am | Jul 8, 2026 11:01am | Jul 8, 2026 11:01am | Jul 8, 2026 11:01am |  |  | Fair | No | Customer single phasing due to defective meter voltage 118/119=237 refer back to field service
Non-Outage | J.E.26.07.06988 | C001843145 | Gregory Grossett | null | Completed | null | null | Jul 8, 2026 9:31am | Jul 8, 2026 9:33am | Jul 8, 2026 1:58pm | Jul 8, 2026 1:58pm | Jul 8, 2026 2:08pm | Jul 8, 2026 2:09pm | Jul 8, 2026 2:09pm | Jul 8, 2026 2:09pm |  |  | Fair | No | Maintenance teams having plan outage in area.
Outage | J.E.26.07.06989 | C001843140 | Oshane Warren | Westmoreland | Completed | Load_249211 | Paradise - 110 | Jul 8, 2026 9:29am | Jul 8, 2026 10:46am | Jul 8, 2026 11:22am | Jul 8, 2026 12:13pm | Jul 8, 2026 12:13pm | Jul 8, 2026 12:14pm | Jul 8, 2026 12:14pm | Jul 8, 2026 12:14pm | Fire |  | Fair | No | Unable to locate or contact customer
Outage | J.E.26.07.06983 | C001843133 | Gregory Grossett | Portland | Completed | Load_266500 | Port Antonio - 410 | Jul 8, 2026 9:17am | Jul 8, 2026 9:33am | Jul 8, 2026 12:25pm | Jul 8, 2026 12:25pm | Jul 8, 2026 1:17pm | Jul 8, 2026 1:54pm | Jul 8, 2026 1:56pm | Jul 8, 2026 1:56pm |  | Y | SevereWind | No | 15amps junction fuse blown cause by vegetation on line section cut and removed vegetation then restore supply to the area.Material use 15amps fuse.
Outage | J.E.26.07.06973 | C001843114 | Hartley Chin | Clarendon | Completed | Load_266446 | May Pen - 210 | Jul 8, 2026 9:02am | Jul 8, 2026 9:16am | Jul 8, 2026 9:56am | Jul 8, 2026 12:12pm | Jul 8, 2026 12:12pm | Jul 8, 2026 12:12pm | Jul 8, 2026 12:17pm | Jul 8, 2026 12:17pm |  |  | SevereWind | No | Prem not found .. unable to contact customer with contact # provided… direction inconclusive… contacted escalation was told that meter was unable to ping … … Ref to field service!!! Report stated that customer meter is burnt…
Non-Outage | J.E.26.05.33319 | C001843109 | Rochaine Hussey | KSAS | Completed | Load_243023 | Greenwich - 710 | Jul 8, 2026 8:59am | Jul 8, 2026 8:59am | Jul 8, 2026 9:26am | Jul 8, 2026 4:15pm | Jul 8, 2026 4:15pm | Jul 8, 2026 4:17pm | Jul 8, 2026 4:17pm | Jul 8, 2026 4:17pm | Fire |  | Fair | No | Customer said issue was already resolved
Non-Outage | J.E.26.06.18675 | C001843108 | Rochaine Hussey | KSAS | Completed | Load_267104 | Greenwich - 710 | Jul 8, 2026 8:59am | Jul 8, 2026 8:59am | Jul 8, 2026 12:09pm | Jul 8, 2026 12:10pm | Jul 8, 2026 12:23pm | Jul 8, 2026 12:32pm | Jul 8, 2026 12:32pm | Jul 8, 2026 12:32pm |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.06.28620 | C001843110 | Rochaine Hussey | KSAS | Completed | Load_241259 | Greenwich - 710 | Jul 8, 2026 8:59am | Jul 8, 2026 8:59am | Jul 8, 2026 1:41pm | Jul 8, 2026 1:41pm | Jul 8, 2026 1:41pm | Jul 8, 2026 2:16pm | Jul 8, 2026 2:16pm | Jul 8, 2026 2:16pm |  |  | Fair | No | Broken cross arm on pole which cause customer service wire to hang low and it is also causing unstable voltage EmergencyReferring to the maintenance team Pole # 0025659
Non-Outage | J.E.26.07.04579 | C001843106 | Rochaine Hussey | KSAS | Completed | Load_255166 | Greenwich - 710 | Jul 8, 2026 8:58am | Jul 8, 2026 8:59am | Jul 8, 2026 12:34pm | Jul 8, 2026 12:49pm | Jul 8, 2026 12:49pm | Jul 8, 2026 1:39pm | Jul 8, 2026 1:39pm | Jul 8, 2026 1:39pm |  |  | Fair | No | Corrosion on pole1 clamp used Issue resolved
Non-Outage | J.E.26.07.05134 | C001843107 | Rochaine Hussey | KSAS | Completed | Load_244948 | Greenwich - 710 | Jul 8, 2026 8:58am | Jul 8, 2026 8:59am | Jul 8, 2026 11:22am | Jul 8, 2026 11:22am | Jul 8, 2026 11:31am | Jul 8, 2026 12:07pm | Jul 8, 2026 12:07pm | Jul 8, 2026 12:07pm |  |  | Fair | No | Corrosion on pothead One clamp usedIssue resolved 114/114/228v
Non-Outage | J.E.26.07.04468 | C001843104 | Royston Montague | St.Catherine | Completed | Load_269589 | Rhodens Pen - 410 | Jul 8, 2026 8:56am | Jul 8, 2026 8:56am | Jul 8, 2026 9:00am | Jul 8, 2026 12:55pm | Jul 8, 2026 1:32pm | Jul 8, 2026 1:33pm | Jul 8, 2026 1:33pm | Jul 8, 2026 1:33pm |  |  | Fair | No | Full voltage found 226v 112v 112v
Non-Outage | J.E.26.07.04153 | C001843103 | Royston Montague | St.Catherine | Completed | Load_556367 | Rhodens Pen - 210 | Jul 8, 2026 8:55am | Jul 8, 2026 8:56am | Jul 8, 2026 9:00am | Jul 8, 2026 12:51pm | Jul 8, 2026 12:51pm | Jul 8, 2026 12:52pm | Jul 8, 2026 12:52pm | Jul 8, 2026 12:52pm |  |  | Fair | No | Not locating this premises. Eg box in area.
Non-Outage | J.E.26.07.04395 | C001843101 | Royston Montague | St.Catherine | Completed | Load_556350 | Rhodens Pen - 210 | Jul 8, 2026 8:55am | Jul 8, 2026 8:56am | Jul 8, 2026 9:00am | Jul 8, 2026 12:35pm | Jul 8, 2026 12:37pm | Jul 8, 2026 12:38pm | Jul 8, 2026 12:38pm | Jul 8, 2026 12:38pm |  |  | Fair | No | Customer confirmed issue resolved yesterday.
Non-Outage | J.E.26.07.04478 | C001843102 | Royston Montague | St.Catherine | Completed | Load_288537 | Rhodens Pen - 310 | Jul 8, 2026 8:55am | Jul 8, 2026 8:56am | Jul 8, 2026 9:00am | Jul 8, 2026 1:33pm | Jul 8, 2026 1:43pm | Jul 8, 2026 1:43pm | Jul 8, 2026 1:43pm | Jul 8, 2026 1:43pm |  |  | Fair | No | Full voltage found 226v 112v 112v
Non-Outage | J.E.26.07.04693 | C001843100 | Royston Montague | St.Catherine | Completed | Load_249185 | Rhodens Pen - 410 | Jul 8, 2026 8:54am | Jul 8, 2026 8:56am | Jul 8, 2026 9:00am | Jul 9, 2026 11:46am | Jul 9, 2026 12:07pm | Jul 9, 2026 12:08pm | Jul 9, 2026 12:08pm | Jul 9, 2026 12:08pm |  |  | Fair | No | Multiple calls to customer phone go without answer. GPS coordinate on job not working.
Non-Outage | J.E.26.07.04905 | C001843099 | Royston Montague | St.Catherine | Completed | Load_288537 | Rhodens Pen - 310 | Jul 8, 2026 8:54am | Jul 8, 2026 8:56am | Jul 8, 2026 9:00am | Jul 8, 2026 3:58pm | Jul 8, 2026 4:27pm | Jul 8, 2026 4:27pm | Jul 8, 2026 4:27pm | Jul 8, 2026 4:27pm |  |  | Fair | No | Location found ok.
Non-Outage | J.E.26.07.04947 | C001843085 | Royston Montague | St.Catherine | Completed | Load_288537 | Rhodens Pen - 310 | Jul 8, 2026 8:54am | Jul 8, 2026 8:56am | Jul 8, 2026 9:00am | Jul 8, 2026 4:27pm | Jul 8, 2026 4:27pm | Jul 8, 2026 4:28pm | Jul 8, 2026 4:28pm | Jul 8, 2026 4:28pm |  |  | Fair | No | Location found ok 226v 112v 112v
Non-Outage | J.E.26.06.26338 | C001843080 | Odeanie Davis | KSAS | Completed | Load_242243 | Rockfort - 410 | Jul 8, 2026 8:51am | Jul 8, 2026 8:51am | Jul 8, 2026 9:02am | Jul 9, 2026 11:33am | Jul 9, 2026 11:35am | Jul 9, 2026 12:37pm | Jul 9, 2026 12:37pm | Jul 9, 2026 12:37pm |  |  | Fair | No | 112v at arrival, open circuit at pothead and on customer’s line corrected, 3 one bolt clamps & 1 penn union, 115v after correction
Non-Outage | J.E.26.07.05592 | C001843079 | Odeanie Davis | KSAS | Completed | Load_247452 | Rockfort - 210 | Jul 8, 2026 8:51am | Jul 8, 2026 8:51am | Jul 8, 2026 9:02am | Jul 8, 2026 1:46pm | Jul 8, 2026 3:02pm | Jul 8, 2026 3:09pm | Jul 8, 2026 3:09pm | Jul 8, 2026 3:09pm |  |  | Fair | No | 155v/68v at arrival, open circuit at secondary corrected, 4 penn union, 3 one bolt clamps & 20ft twisted wire, 112v/116v & 228v after correction.
Non-Outage | J.E.26.06.35976 | C001843074 | Odeanie Davis | KSAS | Completed | Load_242836 | Cane River - 310 | Jul 8, 2026 8:50am | Jul 8, 2026 8:51am | Jul 8, 2026 9:02am | Jul 8, 2026 12:55pm | Jul 8, 2026 12:55pm | Jul 8, 2026 12:50pm | Jul 8, 2026 12:55pm | Jul 8, 2026 12:55pm |  |  | Fair | No | Customer stated that issue was resolved by their electrician
Non-Outage | J.E.26.06.38227 | C001843075 | Odeanie Davis | KSAS | Completed | Load_267729 | Rockfort - 410 | Jul 8, 2026 8:50am | Jul 8, 2026 8:51am | Jul 8, 2026 9:02am | Jul 8, 2026 1:09pm | Jul 8, 2026 1:09pm | Jul 8, 2026 1:37pm | Jul 8, 2026 1:37pm | Jul 8, 2026 1:37pm |  |  | Fair | No | 95v/123v in meter socket at location, 99v/119v on secondary line, emergency team needed, customer also has a defective pole at location, customer was advised to make corrections
Non-Outage | J.E.26.07.00241 | C001843078 | Odeanie Davis | KSAS | Completed | Load_251064 | Rockfort - 210 | Jul 8, 2026 8:50am | Jul 8, 2026 8:51am | Jul 8, 2026 9:02am | Jul 8, 2026 3:53pm | Jul 8, 2026 3:53pm | Jul 8, 2026 4:02pm | Jul 8, 2026 3:54pm | Jul 8, 2026 3:54pm |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.07.05211 | C001843073 | Odeanie Davis | KSAS | Completed | Load_261164 | Cane River - 310 | Jul 8, 2026 8:50am | Jul 8, 2026 8:51am | Jul 8, 2026 9:02am | Jul 8, 2026 9:23am | Jul 8, 2026 9:23am | Jul 8, 2026 10:22am | Jul 8, 2026 10:22am | Jul 8, 2026 10:22am |  |  | Fair | No | 120v/106v at arrival, open circuit at secondary corrected, 3 one bolt clamps, 119v/119v & 239v after completion.
Non-Outage | J.E.26.07.05847 | C001843072 | Odeanie Davis | KSAS | Completed | Load_300787 | Cane River - 310 | Jul 8, 2026 8:50am | Jul 8, 2026 8:51am | Jul 8, 2026 9:02am | Jul 8, 2026 10:33am | Jul 8, 2026 10:38am | Jul 8, 2026 10:59am | Jul 8, 2026 11:00am | Jul 8, 2026 11:00am |  |  | Fair | No | 121v/0V at location, customer getting single phase, bucket truck needed, rammi team needed
Non-Outage | J.E.26.07.06215 | C001843076 | Odeanie Davis | KSAS | Completed | Load_255918 | Rockfort - 410 | Jul 8, 2026 8:50am | Jul 8, 2026 8:51am | Jul 8, 2026 9:02am | Jul 8, 2026 3:09pm | Jul 8, 2026 3:17pm | Jul 8, 2026 3:37pm | Jul 8, 2026 3:35pm | Jul 8, 2026 3:35pm |  |  | Fair | No | 106v at arrival, open circuit at pothead corrected, 1 one bolt clamp, 112v after correction,
Non-Outage | J.E.26.07.06417 | C001843077 | Odeanie Davis | KSAS | Completed | Load_269273 | Rockfort - 410 | Jul 8, 2026 8:50am | Jul 8, 2026 8:51am | Jul 8, 2026 9:02am | Jul 9, 2026 12:38pm | Jul 9, 2026 12:40pm | Jul 9, 2026 1:05pm | Jul 9, 2026 1:05pm | Jul 9, 2026 1:05pm |  |  | Fair | No | 110v/121v at arrival, open circuit at pothead corrected, 2 one bolt clamps, 116v/116 & 233 after correction
Outage | J.E.26.07.06786 | C001843062 | Richard Watson | St.Elizabeth | Completed | Load_246804 | Maggotty - 110 | Jul 8, 2026 8:47am | Jul 8, 2026 8:47am | Jul 8, 2026 1:36pm | Jul 8, 2026 1:36pm | Jul 8, 2026 2:06pm | Jul 8, 2026 2:16pm | Jul 8, 2026 2:16pm | Jul 8, 2026 2:16pm |  |  | Fair | No | Unable to locate premises.
Non-Outage | J.E.26.07.06040 | C001843059 | Fredrick Hamilton | KSAN | Completed | Load_264069 | Constant Spring - 210 | Jul 8, 2026 8:44am | Jul 8, 2026 8:44am | Jul 8, 2026 8:49am | Jul 8, 2026 9:44am | Jul 8, 2026 10:22am | Jul 8, 2026 10:26am | Jul 8, 2026 10:26am | Jul 8, 2026 10:26am | BrokenWire |  | Fair | No | Flow cable wire seen hanging low at location no JPS related issue observed
Non-Outage | J.E.26.07.06203 | C001843060 | Fredrick Hamilton | KSAN | Completed | Load_258670 | Constant Spring - 410 | Jul 8, 2026 8:44am | Jul 8, 2026 8:44am | Jul 8, 2026 8:49am | Jul 8, 2026 10:29am | Jul 8, 2026 11:03am | Jul 8, 2026 11:26am | Jul 8, 2026 11:26am | Jul 8, 2026 11:26am |  |  | Fair | No | 239v/120v/120v obtained Defective meter socket and meter (#2314520) at location customer advised
Non-Outage | J.E.26.07.06955 | C001843047 | Omar King | null | Completed | null | null | Jul 8, 2026 8:39am | Jul 8, 2026 8:40am | Jul 8, 2026 8:52am | Jul 8, 2026 8:52am | Jul 8, 2026 10:43am | Jul 8, 2026 10:47am | Jul 8, 2026 10:48am | Jul 8, 2026 10:48am |  |  | Fair | No | Need bucket truck assistance to carry out repair
Outage | J.E.26.07.06950 | C001843046 | Tyrese Williams | St.Ann | Completed | Load_260345 | Cardiff Hall - 310 | Jul 8, 2026 8:39am | Jul 8, 2026 8:40am | Jul 8, 2026 9:10am | Jul 8, 2026 9:10am | Jul 8, 2026 10:28am | Jul 8, 2026 10:51am | Jul 8, 2026 10:51am | Jul 8, 2026 10:51am | Fire |  | Fair | No | Remade service wire connection at pole
Outage | J.E.26.07.04714 | C001843044 | Stephen Taylor | St.Thomas | Completed | Load_263661 | Good Year - 110 | Jul 8, 2026 8:35am | Jul 8, 2026 8:35am | Jul 8, 2026 11:21am | Jul 8, 2026 11:21am | Jul 8, 2026 11:21am | Jul 8, 2026 11:22am | Jul 8, 2026 11:22am | Jul 8, 2026 11:22am | LeaningPole |  | Fair | No | See three 30 amp trip saver down patrol and see a tree drop on the line 4 span of primary wire are on the ground need assistance from the jps maintenance team to restore power to the community
Outage | J.E.26.07.06824 | C001843045 | Stephen Taylor | St.Thomas | Completed | Load_259964 | Good Year - 110 | Jul 8, 2026 8:35am | Jul 8, 2026 8:35am | Jul 8, 2026 11:23am | Jul 8, 2026 11:23am | Jul 8, 2026 11:24am | Jul 8, 2026 11:24am | Jul 8, 2026 11:24am | Jul 8, 2026 11:24am |  |  | Fair | No | See three 30 amp trip saver down patrol and see a tree drop on the line 4 span of primary wire are on the ground need assistance from the jps maintenance team to restore power to the community
Outage | J.E.26.07.06828 | C001843043 | Stephen Taylor | St.Thomas | Completed | Load_245527 | Good Year - 110 | Jul 8, 2026 8:35am | Jul 8, 2026 8:35am | Jul 8, 2026 11:25am | Jul 8, 2026 11:25am | Jul 8, 2026 11:25am | Jul 8, 2026 11:25am | Jul 8, 2026 11:25am | Jul 8, 2026 11:25am |  |  | Fair | No | See three 30 amp trip saver down patrol and see a tree drop on the line 4 span of primary wire are on the ground need assistance from the jps maintenance team to restore power to the community
Outage | J.E.26.07.06869 | C001843042 | Stephen Taylor | St.Thomas | Completed | Load_238788 | Good Year - 110 | Jul 8, 2026 8:35am | Jul 8, 2026 8:35am | Jul 8, 2026 11:23am | Jul 8, 2026 11:23am | Jul 8, 2026 11:23am | Jul 8, 2026 11:23am | Jul 8, 2026 11:23am | Jul 8, 2026 11:23am |  |  | Fair | No | See three 30 amp trip saver down patrol and see a tree drop on the line 4 span of primary wire are on the ground need assistance from the jps maintenance team to restore power to the community
Outage | J.E.26.07.06872 | C001843041 | Stephen Taylor | St.Thomas | Completed | Load_265360 | Good Year - 110 | Jul 8, 2026 8:35am | Jul 8, 2026 8:35am | Jul 8, 2026 9:02am | Jul 8, 2026 9:02am | Jul 8, 2026 11:02am | Jul 8, 2026 11:02am | Jul 8, 2026 11:21am | Jul 8, 2026 11:21am |  |  | Fair | No | See three 30 amp trip saver down patrol and see a tree drop on the line 4 span of primary wire are on the ground need assistance from the jps maintenance team to restore power to the community
Outage | J.E.26.07.06884 | C001843040 | Stephen Taylor | St.Thomas | Completed | Load_354445 | Good Year - 110 | Jul 8, 2026 8:35am | Jul 8, 2026 8:35am | Jul 8, 2026 11:25am | Jul 8, 2026 11:25am | Jul 8, 2026 11:25am | Jul 8, 2026 11:26am | Jul 8, 2026 11:26am | Jul 8, 2026 11:26am |  |  | Fair | No | See three 30 amp trip saver down patrol and see a tree drop on the line 4 span of primary wire are on the ground need assistance from the jps maintenance team to restore power to the community
Outage | J.E.26.07.06912 | C001843039 | Stephen Taylor | St.Thomas | Completed | Load_260211 | Good Year - 110 | Jul 8, 2026 8:35am | Jul 8, 2026 8:35am | Jul 8, 2026 11:24am | Jul 8, 2026 11:24am | Jul 8, 2026 11:24am | Jul 8, 2026 11:24am | Jul 8, 2026 11:25am | Jul 8, 2026 11:25am |  |  | Fair | No | See three 30 amp trip saver down patrol and see a tree drop on the line 4 span of primary wire are on the ground need assistance from the jps maintenance team to restore power to the community
Outage | J.E.26.07.06935 | C001843038 | Stephen Taylor | St.Thomas | Completed | Load_261266 | Good Year - 110 | Jul 8, 2026 8:35am | Jul 8, 2026 8:35am | Jul 8, 2026 11:22am | Jul 8, 2026 11:22am | Jul 8, 2026 11:22am | Jul 8, 2026 11:22am | Jul 8, 2026 11:23am | Jul 8, 2026 11:23am |  |  | Fair | No | See three 30 amp trip saver down patrol and see a tree drop on the line 4 span of primary wire are on the ground need assistance from the jps maintenance team to restore power to the community
Non-Outage | J.E.26.06.29856 | C001843033 | Rayon Foster | Hanover | Completed | Load_239423 | Orange Bay - 310 | Jul 8, 2026 8:33am | Jul 8, 2026 8:33am | Jul 8, 2026 9:43am | Jul 8, 2026 1:31pm | Jul 8, 2026 2:08pm | Jul 8, 2026 2:10pm | Jul 8, 2026 2:10pm | Jul 8, 2026 2:10pm |  |  | Fair | No | Unable reach on cell phone voicemail and unable to locate premises directions are unclear
Outage | J.E.26.07.06933 | C001843034 | Christopher Edwards | KSAN | Completed | Load_238675 | Constant Spring - 410 | Jul 8, 2026 8:33am | Jul 8, 2026 8:33am | Jul 8, 2026 10:36am | Jul 8, 2026 10:37am | Jul 8, 2026 11:46am | Jul 8, 2026 12:26pm | Jul 8, 2026 12:28pm | Jul 8, 2026 12:28pm |  |  | Fair | No | Refuse blown 25 kva transformer using (1) 2 ampsAlso clear vegetation off transformer pole
Outage | J.E.26.07.06615 | C001843031 | Milton Charlton | KSAN | Completed | Load_268204 | Constant Spring - 410 | Jul 8, 2026 8:31am | Jul 8, 2026 8:31am | Jul 8, 2026 11:35am | Jul 8, 2026 11:35am | Jul 8, 2026 12:00pm | Jul 8, 2026 12:00pm | Jul 8, 2026 12:00pm | Jul 8, 2026 12:00pm |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Non-Outage | J.E.26.07.05706 | C001843024 | Oraine Minto | St.Ann | Completed | Load_239143 | Cardiff Hall - 310 | Jul 8, 2026 8:28am | Jul 8, 2026 8:28am | Jul 8, 2026 11:08am | Jul 8, 2026 7:46pm | Jul 8, 2026 7:46pm | Jul 9, 2026 8:08am | Jul 9, 2026 8:09am | Jul 9, 2026 8:09am |  |  | Fair | No | 121v 1 one bolt clamp was used
Non-Outage | J.E.26.07.06665 | C001843025 | Oraine Minto | St.Ann | Completed | Load_254321 | Cardiff Hall - 210 | Jul 8, 2026 8:28am | Jul 8, 2026 8:28am | Jul 8, 2026 11:08am | Jul 8, 2026 11:20am | Jul 8, 2026 11:20am | Jul 8, 2026 11:25am | Jul 8, 2026 11:25am | Jul 8, 2026 11:25am |  |  | Fair | No | 236v 118v 118v
Non-Outage | J.E.26.07.06858 | C001843026 | Oraine Minto | St.Ann | Completed | Load_573918 | Cardiff Hall - 310 | Jul 8, 2026 8:28am | Jul 8, 2026 8:28am | Jul 8, 2026 9:45am | Jul 8, 2026 11:33am | Jul 8, 2026 11:33am | Jul 8, 2026 11:33am | Jul 8, 2026 11:35am | Jul 8, 2026 11:35am |  |  | Fair | No | Refer to maintenance Vegetation on lines said customer Power was restored
Non-Outage | J.E.26.07.05189 | C001843023 | Royston Montague | St.Catherine | Completed | Load_243118 | Rhodens Pen - 410 | Jul 8, 2026 8:27am | Jul 8, 2026 8:28am | Jul 8, 2026 8:32am | Jul 8, 2026 3:08pm | Jul 8, 2026 3:40pm | Jul 8, 2026 3:55pm | Jul 8, 2026 3:57pm | Jul 8, 2026 3:57pm |  |  | Fair | No | Area having fluctuations of voltage. Unable to use ladder to check transformer drop lead joint and customer take of point. Post cover with illegal connections. Voltage at pothead 193v 112v 79v bucket truck recommended to check same.
Non-Outage | J.E.26.07.05349 | C001843022 | Royston Montague | St.Catherine | Completed | Load_568109 | Rhodens Pen - 210 | Jul 8, 2026 8:27am | Jul 8, 2026 8:28am | Jul 8, 2026 8:32am | Jul 8, 2026 12:34pm | Jul 8, 2026 12:34pm | Jul 8, 2026 12:34pm | Jul 8, 2026 12:35pm | Jul 8, 2026 12:35pm |  |  | Fair | No | Customer confirmed issue resolved. Please update thanks.
Non-Outage | J.E.26.07.05639 | C001843021 | Royston Montague | St.Catherine | Completed | Load_237883 | Rhodens Pen - 210 | Jul 8, 2026 8:27am | Jul 8, 2026 8:28am | Jul 8, 2026 8:32am | Jul 9, 2026 9:48am | Jul 9, 2026 10:14am | Jul 9, 2026 10:31am | Jul 9, 2026 10:31am | Jul 9, 2026 10:31am |  |  | Fair | No | Not locating this premises. Multiple calls to customer phone go without. Rami system in area.
Non-Outage | J.E.26.07.05676 | C001843019 | Royston Montague | St.Catherine | Completed | Load_302294 | Rhodens Pen - 210 | Jul 8, 2026 8:27am | Jul 8, 2026 8:28am | Jul 8, 2026 8:32am | Jul 8, 2026 11:10am | Jul 8, 2026 11:46am | Jul 8, 2026 12:33pm | Jul 8, 2026 12:33pm | Jul 8, 2026 12:33pm |  |  | Fair | No | Faulty main breaker, customer asked to get an electrician to change same . Voltage found 232v 115v 115v
Non-Outage | J.E.26.07.05900 | C001843018 | Royston Montague | St.Catherine | Completed | Load_263836 | Tredegar - 310 | Jul 8, 2026 8:26am | Jul 8, 2026 8:28am | Jul 8, 2026 8:32am | Jul 8, 2026 8:47am | Jul 8, 2026 10:09am | Jul 8, 2026 10:10am | Jul 8, 2026 10:10am | Jul 8, 2026 10:10am |  |  | Fair | No | Customer confirmed her electrician corrected issue.
Non-Outage | J.E.26.07.06183 | C001843008 | Locksley Allen | St.Mary | Completed | Load_238939 | Blackstonedge - 110 | Jul 8, 2026 8:26am | Jul 8, 2026 10:04am | Jul 8, 2026 1:38pm | Jul 8, 2026 1:52pm | Jul 8, 2026 1:52pm | Jul 8, 2026 1:56pm | Jul 8, 2026 1:56pm | Jul 8, 2026 1:56pm |  |  | Fair | No | Gate lock. Several customers in this area is having the same on and off problem
Non-Outage | J.E.26.07.06267 | C001843010 | Locksley Allen | St.Mary | Completed | Load_243968 | Blackstonedge - 110 | Jul 8, 2026 8:26am | Jul 8, 2026 10:04am | Jul 8, 2026 4:34pm | Jul 8, 2026 4:34pm | Jul 8, 2026 4:34pm | Jul 8, 2026 4:36pm | Jul 8, 2026 4:37pm | Jul 8, 2026 4:37pm |  |  | Fair | No | Customer not answering her phone. Need better direction
Non-Outage | J.E.26.07.06329 | C001843009 | Locksley Allen | St.Mary | Completed | Load_248681 | Blackstonedge - 110 | Jul 8, 2026 8:26am | Jul 8, 2026 10:04am | Jul 8, 2026 11:15am | Jul 8, 2026 11:55am | Jul 8, 2026 11:55am | Jul 8, 2026 12:09pm | Jul 8, 2026 12:11pm | Jul 8, 2026 12:11pm |  |  | Fair | No | Voltage at meter socket phase to neutral 118v. Bamboo tree is entangle in the secondary line. Several customers in this area is having the same
Non-Outage | J.E.26.07.06444 | C001843011 | Locksley Allen | St.Mary | Completed | Load_262038 | Blackstonedge - 110 | Jul 8, 2026 8:26am | Jul 8, 2026 10:03am | Jul 8, 2026 3:34pm | Jul 8, 2026 3:34pm | Jul 8, 2026 3:35pm | Jul 8, 2026 3:41pm | Jul 8, 2026 3:41pm | Jul 8, 2026 3:41pm |  |  | Fair | No | Several customers in this area is having the same problem.90% of the customers from Blue Gate to Copper is having the same on and off problem
Non-Outage | J.E.26.07.06579 | C001843013 | Locksley Allen | St.Mary | Completed | Load_251509 | Blackstonedge - 110 | Jul 8, 2026 8:26am | Jul 8, 2026 10:03am | Jul 8, 2026 3:42pm | Jul 8, 2026 3:42pm | Jul 8, 2026 3:42pm | Jul 8, 2026 3:44pm | Jul 8, 2026 3:44pm | Jul 8, 2026 3:44pm |  |  | Fair | No | Secondary line needs to be bush. Several customers in this area is having the same problem
Non-Outage | J.E.26.07.06584 | C001843012 | Locksley Allen | St.Mary | Completed | Load_260263 | Blackstonedge - 110 | Jul 8, 2026 8:26am | Jul 8, 2026 10:03am | Jul 8, 2026 12:48pm | Jul 8, 2026 1:27pm | Jul 8, 2026 1:27pm | Jul 8, 2026 1:36pm | Jul 8, 2026 1:37pm | Jul 8, 2026 1:37pm |  |  | Fair | No | Pothead found corroded,clean up pothead Voltage at meter socket phase to phase 234v. Phase to neutral 117&117vMeter left working
Non-Outage | J.E.26.07.06596 | C001843015 | Locksley Allen | St.Mary | Completed | Load_241027 | Blackstonedge - 110 | Jul 8, 2026 8:26am | Jul 8, 2026 10:02am | Jul 8, 2026 2:49pm | Jul 8, 2026 2:50pm | Jul 8, 2026 2:50pm | Jul 8, 2026 2:53pm | Jul 8, 2026 2:53pm | Jul 8, 2026 2:53pm |  |  | Fair | No | Pothead found corroded,clean up pothead. Voltage at meter socket phase to neutral 118v. Meter left working Several customers in this area is having the same on and off problem
Non-Outage | J.E.26.07.06619 | C001843016 | Locksley Allen | St.Mary | Completed | Load_260233 | Blackstonedge - 110 | Jul 8, 2026 8:26am | Jul 8, 2026 10:02am | Jul 8, 2026 12:12pm | Jul 8, 2026 12:44pm | Jul 8, 2026 12:44pm | Jul 8, 2026 12:46pm | Jul 8, 2026 12:46pm | Jul 8, 2026 12:46pm |  |  | Fair | No | Pothead found corroded. Clean up pothead Voltage at meter socket phase to phase 228v. Phase to neutral 117&111vMeter left working
Non-Outage | J.E.26.07.06686 | C001843014 | Royston Montague | St.Catherine | Completed | Load_258819 | Rhodens Pen - 410 | Jul 8, 2026 8:26am | Jul 8, 2026 8:28am | Jul 8, 2026 8:32am | Jul 9, 2026 10:31am | Jul 9, 2026 11:17am | Jul 9, 2026 11:46am | Jul 9, 2026 11:46am | Jul 9, 2026 11:46am |  |  | Fair | No | Faulty neutral joint on customer load side, same ask to get an electrician to do repair , voltage 217v 107v 108v
Non-Outage | J.E.26.07.06769 | C001843017 | Royston Montague | St.Catherine | Completed | Load_264536 | Rhodens Pen - 410 | Jul 8, 2026 8:26am | Jul 8, 2026 8:28am | Jul 8, 2026 8:32am | Jul 8, 2026 1:44pm | Jul 8, 2026 2:11pm | Jul 8, 2026 3:07pm | Jul 8, 2026 3:07pm | Jul 8, 2026 3:07pm |  |  | Fair | No | Open phase at pothead, same corrected. Voltage found 112v voltage after job completion are 220v 110v 108v
Non-Outage | J.E.26.07.06796 | C001843004 | Omar King | St.Ann | Completed | Load_255188 | Ocho Rios - 310 | Jul 8, 2026 8:24am | Jul 8, 2026 8:24am | Jul 8, 2026 12:51pm | Jul 8, 2026 12:51pm | Jul 8, 2026 12:51pm | Jul 8, 2026 1:03pm | Jul 8, 2026 1:04pm | Jul 8, 2026 1:04pm |  |  | Fair | No | Found a secondary neutral jumper clamp defective as been replaced area is no with supply
Non-Outage | J.E.26.07.02415 | C001843000 | Rayon Foster | Hanover | Completed | Load_230038 | Orange Bay - 310 | Jul 8, 2026 8:23am | Jul 8, 2026 8:24am | Jul 8, 2026 9:42am | Jul 8, 2026 1:07pm | Jul 8, 2026 1:17pm | Jul 8, 2026 12:49pm | Jul 8, 2026 1:31pm | Jul 8, 2026 1:31pm |  |  | Fair | No | When spoke with customer they said that the issue was already resolved earlier this week by a jps team
Non-Outage | J.E.26.07.03007 | C001842999 | Rayon Foster | Hanover | Completed | Load_230038 | Orange Bay - 310 | Jul 8, 2026 8:23am | Jul 8, 2026 8:24am | Jul 8, 2026 9:43am | Jul 8, 2026 11:01am | Jul 8, 2026 12:16pm | Jul 8, 2026 12:41pm | Jul 8, 2026 1:06pm | Jul 8, 2026 1:06pm |  |  | Fair | No | When spoke with customer they said that the issue was already resolved earlier this week by a jps team
Non-Outage | J.E.26.07.05404 | C001842998 | Raymond Lewis | St.Ann | Completed | Load_243782 | Roaring River - 210 | Jul 8, 2026 8:23am | Jul 8, 2026 8:24am | Jul 8, 2026 9:32am | Jul 8, 2026 9:32am | Jul 8, 2026 10:50am | Jul 8, 2026 11:21am | Jul 8, 2026 11:22am | Jul 8, 2026 11:22am |  |  | Fair | No | Remade joint at pothead phase and neutral 3 wire service voltage 107:107:215
Non-Outage | J.E.26.07.05839 | C001842997 | Oraine Minto | St.Ann | Completed | Load_242723 | Roaring River - 210 | Jul 8, 2026 8:23am | Jul 9, 2026 8:53am | Jul 9, 2026 2:12pm | Jul 9, 2026 2:12pm | Jul 9, 2026 2:12pm | Jul 9, 2026 2:13pm | Jul 9, 2026 2:13pm | Jul 9, 2026 2:13pm |  |  | Fair | No | Issue was resolved
Non-Outage | J.E.26.07.06001 | C001842996 | Raymond Lewis | St.Ann | Completed | Load_267596 | Roaring River - 410 | Jul 8, 2026 8:23am | Jul 8, 2026 8:24am | Jul 8, 2026 12:54pm | Jul 8, 2026 12:54pm | Jul 8, 2026 12:54pm | Jul 8, 2026 12:56pm | Jul 8, 2026 12:57pm | Jul 8, 2026 12:57pm |  |  | Fair | No | Customer say that a team stop bye
Non-Outage | J.E.26.07.06056 | C001842995 | Raymond Lewis | St.Ann | Completed | Load_241493 | Roaring River - 210 | Jul 8, 2026 8:23am | Jul 8, 2026 8:24am | Jul 8, 2026 8:42am | Jul 8, 2026 8:42am | Jul 8, 2026 8:56am | Jul 8, 2026 8:58am | Jul 8, 2026 8:58am | Jul 8, 2026 8:58am |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.07.06345 | C001843001 | Rayon Foster | Hanover | Completed | Load_257720 | Orange Bay - 310 | Jul 8, 2026 8:23am | Jul 8, 2026 8:24am | Jul 8, 2026 9:46am | Jul 8, 2026 9:53am | Jul 8, 2026 9:53am | Jul 8, 2026 10:35am | Jul 8, 2026 10:38am | Jul 8, 2026 10:38am |  |  | Fair | No | Check and found voltage at customer pothead working ok voltage found 115v/115v/230v
Non-Outage | J.E.26.07.06586 | C001842994 | Oraine Minto | St.Ann | Completed | Load_238536 | Roaring River - 210 | Jul 8, 2026 8:23am | Jul 9, 2026 8:54am | Jul 9, 2026 2:01pm | Jul 9, 2026 2:01pm | Jul 9, 2026 2:01pm | Jul 9, 2026 2:02pm | Jul 9, 2026 2:05pm | Jul 9, 2026 2:05pm |  |  | Fair | No | Refer to maintenance Customer states that the entire area was going on and off this morning but it’s ok now that the winds die down
Non-Outage | J.E.26.07.06606 | C001842992 | Raymond Lewis | St.Ann | Completed | Load_246075 | Roaring River - 410 | Jul 8, 2026 8:23am | Jul 8, 2026 8:24am | Jul 8, 2026 11:44am | Jul 8, 2026 11:44am | Jul 8, 2026 12:01pm | Jul 8, 2026 12:49pm | Jul 8, 2026 12:50pm | Jul 8, 2026 12:50pm |  |  | SevereWind | No | Remove illegal connection cut tree from secondary refuse and close 25 kva x former
Non-Outage | J.E.26.03.41069 | C001842990 | Andrae Dawkins | St.James | Completed | Load_256744 | Bogue - 310 | Jul 8, 2026 8:22am | Jul 8, 2026 8:23am | Jul 8, 2026 11:39am | Jul 8, 2026 12:07pm | Jul 8, 2026 12:11pm | Jul 8, 2026 12:11pm | Jul 8, 2026 12:18pm | Jul 8, 2026 12:18pm |  |  | Fair | No | Check and found ok customer said that they didn’t make any report and that they don’t have any issues with the power
Non-Outage | J.E.26.03.45740 | C001842991 | Andrae Dawkins | St.James | Completed | Load_255029 | Bogue - 310 | Jul 8, 2026 8:22am | Jul 8, 2026 8:23am | Jul 8, 2026 11:39am | Jul 8, 2026 12:20pm | Jul 8, 2026 12:21pm | Jul 8, 2026 12:22pm | Jul 8, 2026 12:23pm | Jul 8, 2026 12:23pm |  |  | Fair | No | Check and found okay customer said that they didn’t make any report
Non-Outage | J.E.26.04.01181 | C001842989 | Andrae Dawkins | St.James | Completed | Load_555736 | Bogue - 310 | Jul 8, 2026 8:22am | Jul 8, 2026 8:22am | Jul 8, 2026 11:39am | Jul 8, 2026 12:25pm | Jul 8, 2026 12:25pm | Jul 8, 2026 12:26pm | Jul 8, 2026 12:28pm | Jul 8, 2026 12:28pm |  |  | Fair | No | Check and found okay customer said that they didn’t make any report
Non-Outage | J.E.26.04.02679 | C001842986 | Andrae Dawkins | St.James | Completed | Load_251692 | Bogue - 310 | Jul 8, 2026 8:22am | Jul 8, 2026 8:22am | Jul 8, 2026 9:16am | Jul 8, 2026 12:01pm | Jul 8, 2026 12:01pm | Jul 8, 2026 11:47am | Jul 8, 2026 12:06pm | Jul 8, 2026 12:06pm |  |  | Fair | No | Check and found ok customer said that the report was made long ago and that she not having any issues with the light
Outage | J.E.26.07.06748 | C001842988 | Jermaine Williams | Clarendon | Completed | Load_303086 | Monymusk - 410 | Jul 8, 2026 8:22am | Jul 8, 2026 3:27pm | Jul 8, 2026 6:16pm | Jul 8, 2026 6:16pm | Jul 8, 2026 6:16pm | Jul 8, 2026 6:16pm | Jul 8, 2026 6:17pm | Jul 8, 2026 6:17pm |  |  | SevereWind | No | Premises locked.
Outage | J.E.26.07.06787 | C001842985 | Hartley Chin | Clarendon | Completed | Load_265981 | Monymusk - 410 | Jul 8, 2026 8:22am | Jul 8, 2026 8:23am | Jul 8, 2026 11:38am | Jul 8, 2026 12:42pm | Jul 8, 2026 1:47pm | Jul 8, 2026 2:04pm | Jul 8, 2026 2:10pm | Jul 8, 2026 2:10pm | Fire |  | Fair | No | Customer requires approximately 110 ft service wire to restore supply … customer is the only person affected…
Outage | J.E.26.07.06826 | C001842984 | Hartley Chin | Clarendon | Completed | Load_264051 | Parnassus - 310 | Jul 8, 2026 8:22am | Jul 8, 2026 8:23am | Jul 8, 2026 9:57am | Jul 8, 2026 11:36am | Jul 8, 2026 11:36am | Jul 8, 2026 11:36am | Jul 8, 2026 11:37am | Jul 8, 2026 11:37am |  |  | SevereWind | No | Call related to job # 07008 ..
Non-Outage | J.E.26.04.05705 | C001842981 | Andrae Dawkins | St.James | Completed | Load_267594 | Bogue - 310 | Jul 8, 2026 8:21am | Jul 8, 2026 8:22am | Jul 8, 2026 12:44pm | Jul 8, 2026 12:49pm | Jul 8, 2026 12:49pm | Jul 8, 2026 12:48am | Jul 8, 2026 12:51pm | Jul 8, 2026 12:51pm |  |  | Fair | No | Check and found okay customer said that the problem was already resoved
Non-Outage | J.E.26.04.06910 | C001842978 | Andrae Dawkins | St.James | Completed | Load_301680 | Bogue - 310 | Jul 8, 2026 8:21am | Jul 8, 2026 8:22am | Jul 8, 2026 12:34pm | Jul 8, 2026 12:45pm | Jul 8, 2026 12:45pm | Jul 8, 2026 12:39am | Jul 8, 2026 12:48pm | Jul 8, 2026 12:48pm |  |  | Fair | No | Check and found okay customer said that the problem was already resolved
Non-Outage | J.E.26.04.07441 | C001842980 | Andrae Dawkins | St.James | Completed | Load_263882 | Bogue - 310 | Jul 8, 2026 8:21am | Jul 8, 2026 8:22am | Jul 8, 2026 9:15am | Jul 8, 2026 11:26am | Jul 8, 2026 11:28am | Jul 8, 2026 11:08am | Jul 8, 2026 11:35am | Jul 8, 2026 11:35am |  |  | Fair | No | Found customer experiencing on and off supply from EG Box 00573
Non-Outage | J.E.26.04.07701 | C001842977 | Andrae Dawkins | St.James | Completed | Load_243897 | Bogue - 310 | Jul 8, 2026 8:21am | Jul 8, 2026 8:22am | Jul 8, 2026 9:13am | Jul 8, 2026 9:40am | Jul 8, 2026 10:31am | Jul 8, 2026 10:50am | Jul 8, 2026 10:57am | Jul 8, 2026 10:57am |  |  | Fair | No | Found customer experiencing low voltage due to service wire neutral broken due to hurricane spliced and retention neutral voltage left 117/117/235
Non-Outage | J.E.26.07.06185 | C001842975 | Ryan Richards | Manchester | Completed | Load_262141 | Kendal - 210 | Jul 8, 2026 8:21am | Jul 8, 2026 8:21am | Jul 8, 2026 9:29am | Jul 8, 2026 9:31am | Jul 8, 2026 11:17am | Jul 8, 2026 11:44am | Jul 8, 2026 11:44am | Jul 8, 2026 11:44am |  |  | Fair | No | Corroded neutral jumper found corroded causing multiple customers to experience low voltage remade jumper using 1 one bolt clamp voltage 115/117/233 volts
Outage | J.E.26.07.06889 | C001842983 | Hartley Chin | Clarendon | Completed | Load_238944 | Parnassus - 210 | Jul 8, 2026 8:21am | Jul 8, 2026 8:23am | Jul 8, 2026 1:47pm | Jul 8, 2026 2:10pm | Jul 8, 2026 2:44pm | Jul 8, 2026 2:55pm | Jul 8, 2026 2:56pm | Jul 8, 2026 2:56pm |  |  | Fair | No | Unable to contact customer .. was able to find meter … voltage read 112v , 113v ..
Outage | J.E.26.07.06905 | C001842982 | Hartley Chin | Clarendon | Completed | Load_405556 | Parnassus - 310 | Jul 8, 2026 8:21am | Jul 8, 2026 8:23am | Jul 8, 2026 8:36am | Jul 8, 2026 9:56am | Jul 8, 2026 9:56am | Jul 8, 2026 9:57am | Jul 8, 2026 9:57am | Jul 8, 2026 9:57am |  |  | Fair | No | Found okay … voltage read 114v , 115v ..
Non-Outage | J.E.26.06.38285 | C001842974 | Richard Watson | St.Elizabeth | Completed | Load_243100 | Maggotty - 110 | Jul 8, 2026 8:20am | Jul 8, 2026 8:20am | Jul 8, 2026 9:10am | Jul 8, 2026 9:17am | Jul 8, 2026 9:17am | Jul 8, 2026 9:17am | Jul 8, 2026 9:18am | Jul 8, 2026 9:18am |  |  | Fair | No | Customer contacted by phone and stated that the issue was resolved by electrician.
Non-Outage | J.E.26.07.00929 | C001842973 | Richard Watson | St.Elizabeth | Completed | Load_247338 | Maggotty - 110 | Jul 8, 2026 8:20am | Jul 8, 2026 8:20am | Jul 8, 2026 11:40am | Jul 8, 2026 11:40am | Jul 8, 2026 12:51pm | Jul 8, 2026 1:27pm | Jul 8, 2026 1:31pm | Jul 8, 2026 1:31pm |  |  | Fair | No | Corrosion found at pothead, use three #6-#6 service sleeves, voltages left 114v, 116v, 230v, on load.
Non-Outage | J.E.26.07.05203 | C001842971 | Richard Watson | St.Elizabeth | Completed | Load_266017 | Maggotty - 110 | Jul 8, 2026 8:20am | Jul 8, 2026 8:20am | Jul 8, 2026 9:19am | Jul 8, 2026 9:19am | Jul 8, 2026 10:21am | Jul 8, 2026 11:18am | Jul 8, 2026 11:32am | Jul 8, 2026 11:32am |  |  | Fair | No | Voltage found inside meter socket 106v, 106v, 212v, customer is connected at deadend of secondary circuit, bucket truck required to top up transformer please refer to evening contractor crew.
Non-Outage | J.E.26.07.05864 | C001842968 | Fitzroy Turner | KSAN | Completed | Load_263322 | Washington Blvd - 410 | Jul 8, 2026 8:18am | Jul 8, 2026 8:18am | Jul 8, 2026 10:21am | Jul 8, 2026 10:21am | Jul 8, 2026 10:22am | Jul 8, 2026 10:45am | Jul 8, 2026 10:49am | Jul 8, 2026 10:49am |  |  | Fair | No | Customer having voltage issues.customer service can relocate to the front of the building to bank of three 167 transformer
Non-Outage | J.E.26.07.06614 | C001842967 | Milton Charlton | KSAN | Completed | Load_250041 | Constant Spring - 410 | Jul 8, 2026 8:17am | Jul 8, 2026 8:17am | Jul 8, 2026 10:27am | Jul 8, 2026 10:28am | Jul 8, 2026 11:29am | Jul 8, 2026 11:30am | Jul 8, 2026 11:31am | Jul 8, 2026 11:31am |  |  | Fair | No | Customer service wire #2 triplex phase and neutral corroded at pothead. Repair using four 1- bolt clamps. Readings at pothead 117-116-234 volts.
Non-Outage | J.E.26.07.06638 | C001842965 | Milton Charlton | KSAN | Completed | Load_250041 | Constant Spring - 410 | Jul 8, 2026 8:17am | Jul 8, 2026 8:17am | Jul 8, 2026 10:27am | Jul 8, 2026 11:33am | Jul 8, 2026 11:33am | Jul 8, 2026 11:40am | Jul 8, 2026 11:35am | Jul 8, 2026 11:35am |  |  | Fair | No | Call related to call at APT #2A 14 Charlton Road.
Non-Outage | J.E.26.07.06640 | C001842966 | Milton Charlton | KSAN | Completed | Load_250041 | Constant Spring - 410 | Jul 8, 2026 8:17am | Jul 8, 2026 8:17am | Jul 8, 2026 10:27am | Jul 8, 2026 11:31am | Jul 8, 2026 11:32am | Jul 8, 2026 11:35am | Jul 8, 2026 11:33am | Jul 8, 2026 11:33am |  |  | Fair | No | Duplicate call.
Non-Outage | J.E.26.07.06552 | C001842964 | Junior Scarlett | St.James | Completed | Load_260420 | Bogue - 610 | Jul 8, 2026 8:16am | Jul 8, 2026 8:17am | Jul 8, 2026 8:28am | Jul 8, 2026 8:36am | Jul 8, 2026 9:34am | Jul 8, 2026 10:18am | Jul 8, 2026 10:18am | Jul 8, 2026 10:18am |  |  | Fair | No | Refer to emergency team Jumper burn offVoltage found 115v 0.88v 115v
Non-Outage | J.E.26.07.06924 | C001842963 | Derrick Dawkins | null | Completed | null | null | Jul 8, 2026 8:14am | Jul 8, 2026 8:15am | Jul 8, 2026 9:50am | Jul 8, 2026 9:50am | Jul 8, 2026 9:57am | Jul 8, 2026 10:22am | Jul 8, 2026 10:23am | Jul 8, 2026 10:23am |  |  | Fair | No | Found a 25 kva transformer fuse blown 3 amp due to vegetation removed vegetation switch is defective need to be changed replaced a 3 amp transformer fuse pole # 0162798 refer back to maintenance
Outage | J.E.26.07.06397 | C001842961 | Michael Christian | St.James | Completed | Load_251546 | Queens Drive - 710 | Jul 8, 2026 8:14am | Jul 8, 2026 3:27pm | Jul 8, 2026 9:56pm | Jul 8, 2026 9:56pm | Jul 8, 2026 10:54pm | Jul 8, 2026 11:03pm | Jul 8, 2026 11:04pm | Jul 8, 2026 11:04pm |  |  | Fair | No | Check found okay
Non-Outage | J.E.26.06.39233 | C001842958 | Fitzroy Turner | KSAN | Completed | Load_246933 | Washington Blvd - 610 | Jul 8, 2026 8:12am | Jul 8, 2026 8:12am | Jul 8, 2026 8:28am | Jul 8, 2026 8:28am | Jul 8, 2026 9:28am | Jul 8, 2026 10:09am | Jul 8, 2026 10:21am | Jul 8, 2026 10:21am |  |  | Fair | No | Found bank of three 25kva transformer 415 supply voltage readings 235/235/235/413/413/413 at the transformer and at the top of the meter socket same readings from the transformer bank.at the bottom of the meter socket readings 247 /235/235/customer advised to carry out repairs and meter socket.customer say new AC install burnt up same time when power up .wrong connections was carry out
Outage | J.E.26.07.06744 | C001842960 | Milton Charlton | KSAN | Completed | Load_249646 | Hope - 310 | Jul 8, 2026 8:12am | Jul 8, 2026 8:13am | Jul 8, 2026 12:00pm | Jul 8, 2026 12:00pm | Jul 8, 2026 1:50pm | Jul 8, 2026 1:50pm | Jul 8, 2026 1:51pm | Jul 8, 2026 1:51pm |  |  | Fair | No | Found okay upon arrival. Customer has an internal problem.
Outage | J.E.26.07.06813 | C001842959 | Milton Charlton | KSAN | Completed | Load_573544 | Hope - 410 | Jul 8, 2026 8:12am | Jul 8, 2026 8:13am | Jul 8, 2026 9:42am | Jul 8, 2026 9:42am | Jul 8, 2026 10:01am | Jul 8, 2026 10:05am | Jul 8, 2026 10:27am | Jul 8, 2026 10:27am |  |  | Fair | No | Found okay upon arrival. Readings at pothead 117-117-205 volts. Customer has an internal problem.
Non-Outage | J.E.26.07.05913 | C001842949 | Richard Nicholas | St.Catherine | Completed | Load_239483 | Tredegar - 510 | Jul 8, 2026 8:11am | Jul 8, 2026 8:11am | Jul 8, 2026 8:33am | Jul 8, 2026 8:33am | Jul 8, 2026 9:48am | Jul 8, 2026 11:06am | Jul 8, 2026 11:13am | Jul 8, 2026 11:13am | BrokenWire |  | Fair | No | Up on arrival the crew,customer complain that cable company crew was working on a concrete pole yesterday and get shick by electric current however during a drive patrol of the secondary line the crew observed that the lower secondary phase dislodged from the D-iron.same was repaired and secured by using tie wire.
Non-Outage | J.E.26.07.06921 | C001842954 | Nickolas Rodriques | St.Catherine | Completed | Load_263862 | Rhodens Pen - 410 | Jul 8, 2026 8:11am | Jul 8, 2026 8:12am | Jul 8, 2026 8:30am | Jul 8, 2026 9:05am | Jul 8, 2026 10:04am | Jul 8, 2026 10:33am | Jul 8, 2026 10:36am | Jul 8, 2026 10:36am | Fire |  | Fair | No | Unable to locate or communicate with the customer after several attempts. However, the area was patrolled and no noticeable fire or outage was found.
Outage | J.E.26.07.06029 | C001842956 | Michael Christian | St.James | Completed | Load_261444 | Queens Drive - 710 | Jul 8, 2026 8:11am | Jul 8, 2026 3:27pm | Jul 8, 2026 10:16pm | Jul 8, 2026 11:04pm | Jul 8, 2026 11:15pm | Jul 8, 2026 11:16pm | Jul 8, 2026 11:16pm | Jul 8, 2026 11:16pm |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.06036 | C001842955 | Romeo Brissett | St.James | Completed | Load_245113 | Queens Drive - 710 | Jul 8, 2026 8:11am | Jul 8, 2026 8:11am | Jul 8, 2026 10:15am | Jul 8, 2026 10:15am | Jul 8, 2026 10:15am | Jul 8, 2026 10:14am | Jul 8, 2026 10:16am | Jul 8, 2026 10:16am |  |  | Fair | No | Customer stated power restored from yesterday
Outage | J.E.26.07.06220 | C001842953 | Romeo Brissett | St.James | Completed | Load_1002042 | Queens Drive - 710 | Jul 8, 2026 8:11am | Jul 8, 2026 8:11am | Jul 8, 2026 8:17am | Jul 8, 2026 8:17am | Jul 8, 2026 9:28am | Jul 8, 2026 10:08am | Jul 8, 2026 10:15am | Jul 8, 2026 10:15am |  |  | Fair | No | Removed illegal connections, retention one span of 2/0 twisted, replaced (1)25KVA transformer fuse.
Outage | J.E.26.07.06915 | C001842951 | Gregory Grossett | Portland | Completed | Load_242782 | Port Antonio - 410 | Jul 8, 2026 8:11am | Jul 8, 2026 8:12am | Jul 8, 2026 11:01am | Jul 8, 2026 11:01am | Jul 8, 2026 11:42am | Jul 8, 2026 12:20pm | Jul 8, 2026 12:24pm | Jul 8, 2026 12:24pm |  |  | Fair | No | 25kva transformer fuse blown patrol line section and found one pole span of phase and neutral conductors banging retention neutral conductor then close transformer fuse to restore normal supply to the area.Material use 1 number 2 preform 2amp fuse.
Outage | J.E.26.07.06922 | C001842952 | Gregory Grossett | Portland | Completed | Load_262272 | Port Antonio - 410 | Jul 8, 2026 8:11am | Jul 8, 2026 8:12am | Jul 8, 2026 1:56pm | Jul 8, 2026 1:56pm | Jul 8, 2026 1:56pm | Jul 8, 2026 1:57pm | Jul 8, 2026 1:58pm | Jul 8, 2026 1:58pm |  |  | Fair | No | 15amps junction fuse blown cause by vegetation on line section cut and removed vegetation then restore supply to the area.Material use 15amps Fuse.
Outage | J.E.26.07.06927 | C001842950 | Romeo Brissett | St.James | Completed | Load_251817 | Queens Drive - 710 | Jul 8, 2026 8:11am | Jul 8, 2026 8:11am | Jul 8, 2026 12:15pm | Jul 8, 2026 12:15pm | Jul 8, 2026 12:36pm | Jul 8, 2026 12:40pm | Jul 8, 2026 12:40pm | Jul 8, 2026 12:40pm |  |  | Fair | No | Found clearance breach from arrester ground lead, clear breach and replaced (1)25 kva transformer fuse.
Non-Outage | J.E.26.07.06708 | C001842946 | Wan Carlos Scarlett | Portmore | Completed | Load_239998 | Naggo Head - 610 | Jul 8, 2026 8:09am | Jul 8, 2026 8:10am | Jul 8, 2026 10:08am | Jul 8, 2026 10:08am | Jul 8, 2026 10:42am | Jul 8, 2026 10:52am | Jul 8, 2026 10:54am | Jul 8, 2026 10:54am | BrokenWire |  | Fair | No | Found cable and wireless wire broken on the ground advised customer to contact cable provider for assistance
Non-Outage | J.E.26.07.06269 | C001842941 | Odaine Johnson | Clarendon | Completed | Load_259723 | Monymusk - 410 | Jul 8, 2026 8:08am | Jul 8, 2026 8:08am | Jul 8, 2026 9:39am | Jul 8, 2026 10:56am | Jul 8, 2026 10:56am | Jul 8, 2026 10:57am | Jul 8, 2026 10:59am | Jul 8, 2026 10:59am |  |  | Fair | No | Corrosion was found at pothead and service pole one bolt clamps and pen union was replaced and problem was fixed Voltage reading before A112 B81 AB193voltage reading after A116 B116 AB233
Non-Outage | J.E.26.07.06282 | C001842942 | Odaine Johnson | Clarendon | Completed | Load_260400 | Monymusk - 410 | Jul 8, 2026 8:08am | Jul 8, 2026 8:08am | Jul 8, 2026 9:39am | Jul 8, 2026 1:01pm | Jul 8, 2026 1:01pm | Jul 8, 2026 1:01pm | Jul 8, 2026 1:02pm | Jul 8, 2026 1:02pm |  |  | Fair | Yes | Contacted customer and customer stated that the issue is resolved already
Non-Outage | J.E.26.07.06315 | C001842943 | Odaine Johnson | Clarendon | Completed | Load_265061 | Monymusk - 410 | Jul 8, 2026 8:08am | Jul 8, 2026 8:08am | Jul 8, 2026 9:39am | Jul 8, 2026 11:10am | Jul 8, 2026 11:10am | Jul 8, 2026 11:10am | Jul 8, 2026 11:11am | Jul 8, 2026 11:11am |  |  | Fair | No | Contacted customer and customer stated that the issue was resolved already
Non-Outage | J.E.26.07.05798 | C001842938 | Neville Spencer | Clarendon | Completed | Load_249266 | May Pen - 110 | Jul 8, 2026 8:05am | Jul 8, 2026 8:07am | Jul 8, 2026 11:28am | Jul 8, 2026 11:28am | Jul 8, 2026 12:15pm | Jul 8, 2026 12:15pm | Jul 8, 2026 12:16pm | Jul 8, 2026 12:16pm |  |  | Fair | No | Found ok call resolved last night.
Non-Outage | J.E.26.07.06358 | C001842937 | Neville Spencer | Clarendon | Completed | Load_263121 | May Pen - 110 | Jul 8, 2026 8:05am | Jul 8, 2026 8:05am | Jul 8, 2026 10:33am | Jul 8, 2026 10:34am | Jul 8, 2026 11:18am | Jul 8, 2026 11:18am | Jul 8, 2026 11:26am | Jul 8, 2026 11:26am | BrokenPole |  | Fair | No | Found 30 c6 wooden pole leaning badly with 2, wire service attached feeding 2 , customer pole needs to straighten ref to maintenance.
Non-Outage | J.E.26.07.06361 | C001842936 | Odaine Johnson | null | Completed | null | null | Jul 8, 2026 8:04am | Jul 8, 2026 8:05am | Jul 8, 2026 9:39am | Jul 8, 2026 1:28pm | Jul 8, 2026 1:28pm | Jul 8, 2026 1:28pm | Jul 8, 2026 1:28pm | Jul 8, 2026 1:28pm | Fire |  | Fair | No | Try contact customer but no one answer and no proper direction was given
Non-Outage | J.E.26.07.06519 | C001842934 | Odaine Johnson | Clarendon | Completed | Load_250524 | Parnassus - 310 | Jul 8, 2026 8:04am | Jul 8, 2026 8:06am | Jul 8, 2026 9:39am | Jul 8, 2026 12:40pm | Jul 8, 2026 12:40pm | Jul 8, 2026 12:58pm | Jul 8, 2026 1:01pm | Jul 8, 2026 1:01pm |  |  | Fair | No | Corrosion was found at pothead 3 pen union was replaced and problem was fixed Voltage reading before A116 B109 Voltage reading after A111 B110 AB221 Area have low hanging wire, phase and neutral wire kissing together causing on and off supply
Non-Outage | J.E.26.07.06678 | C001842935 | Hartley Chin | Clarendon | Completed | Load_241598 | Parnassus - 310 | Jul 8, 2026 8:04am | Jul 8, 2026 9:43am | Jul 8, 2026 9:58am | Jul 8, 2026 11:37am | Jul 8, 2026 11:37am | Jul 8, 2026 11:38am | Jul 8, 2026 11:38am | Jul 8, 2026 11:38am |  |  | SevereWind | No | Call related to job # 07008 ..
Non-Outage | J.E.26.07.06710 | C001842933 | Odaine Johnson | Clarendon | Completed | Load_301203 | Monymusk - 210 | Jul 8, 2026 8:04am | Jul 8, 2026 8:06am | Jul 8, 2026 9:39am | Jul 8, 2026 9:43am | Jul 8, 2026 9:44am | Jul 8, 2026 9:44am | Jul 8, 2026 9:46am | Jul 8, 2026 9:46am |  |  | Fair | No | Contacted customer and customer stated that the issue was resolved
Non-Outage | J.E.26.07.06738 | C001842932 | Neville Spencer | Clarendon | Completed | Load_239213 | May Pen - 110 | Jul 8, 2026 8:04am | Jul 8, 2026 8:05am | Jul 8, 2026 12:17pm | Jul 8, 2026 12:19pm | Jul 8, 2026 1:06pm | Jul 8, 2026 3:15pm | Jul 8, 2026 3:19pm | Jul 8, 2026 3:19pm |  |  | Fair | No | Cleared bamboo from secondary lines splice and retention broken secondary phase and neutral conductor used 70 ft wire, 2 clamps 2 preform supply restored.
Non-Outage | J.E.26.07.06760 | C001842931 | Clyde Brown | Clarendon | Completed | Load_247989 | May Pen - 110 | Jul 8, 2026 8:04am | Jul 8, 2026 3:29pm | Jul 8, 2026 6:52pm | Jul 8, 2026 6:52pm | Jul 8, 2026 8:15pm | Jul 8, 2026 9:17pm | Jul 8, 2026 9:29pm | Jul 8, 2026 9:29pm |  |  | Fair | No | Corroded phases at pothead and secondary line connection remade with clamps,voltage left 113/114 and 225V
Non-Outage | J.E.26.07.04741 | C001842927 | Damion Reid | Manchester | Completed | Load_248799 | Kendal - 310 | Jul 8, 2026 8:03am | Jul 8, 2026 8:03am | Jul 8, 2026 9:58am | Jul 8, 2026 9:58am | Jul 8, 2026 9:58am | Jul 8, 2026 12:06pm | Jul 8, 2026 12:19pm | Jul 8, 2026 12:19pm |  |  | Fair | No | Team found voltage reading at meter socket phase to neutral 102v-103v across phase 206v team advanced on secondary top charge from C to E voltage reading at meter socket is now phase to neutral 108-109 across phase 219v
Non-Outage | J.E.26.07.05171 | C001842925 | Damion Reid | Manchester | Completed | Load_238510 | Kendal - 310 | Jul 8, 2026 8:03am | Jul 8, 2026 8:03am | Jul 8, 2026 12:33pm | Jul 8, 2026 1:51pm | Jul 8, 2026 2:26pm | Jul 8, 2026 3:19pm | Jul 8, 2026 3:22pm | Jul 8, 2026 3:22pm |  |  | Fair | No | Remade slack phase at secondary pole for 3 wire service using one 1 bolt clamp voltage reading at pothead phase to neutral 112v-111v across phase 225v
Non-Outage | J.E.26.07.06816 | C001842929 | Odaine Johnson | Clarendon | Completed | Load_264051 | Parnassus - 310 | Jul 8, 2026 8:03am | Jul 8, 2026 8:06am | Jul 8, 2026 9:39am | Jul 9, 2026 10:17am | Jul 9, 2026 10:17am | Jul 9, 2026 10:17am | Jul 9, 2026 10:18am | Jul 9, 2026 10:18am |  |  | Fair | No | Premises was found working ok voltage reading is A112 B113 AB225
Non-Outage | J.E.26.07.06881 | C001842928 | Odaine Johnson | Clarendon | Completed | Load_238944 | Parnassus - 210 | Jul 8, 2026 8:03am | Jul 8, 2026 8:06am | Jul 8, 2026 9:39am | Jul 8, 2026 11:56am | Jul 8, 2026 11:56am | Jul 8, 2026 11:57am | Jul 8, 2026 11:59am | Jul 8, 2026 11:59am |  |  | Fair | No | Jumper wire was corroded.one bolt clamps was replaced and problem was fixed Voltage reading A113 B121 AB234
Non-Outage | J.E.26.07.03661 | C001842920 | Oshane Warren | Westmoreland | Completed | Load_251332 | Paradise - 210 | Jul 8, 2026 8:00am | Jul 8, 2026 8:00am | Jul 8, 2026 9:53am | Jul 8, 2026 9:53am | Jul 8, 2026 9:53am | Jul 8, 2026 9:53am | Jul 8, 2026 9:53am | Jul 8, 2026 9:53am |  |  | Fair | No | Check and find ok
Non-Outage | J.E.26.07.04972 | C001842921 | Oshane Warren | Westmoreland | Completed | Load_241469 | Paradise - 210 | Jul 8, 2026 8:00am | Jul 8, 2026 8:00am | Jul 8, 2026 8:16am | Jul 8, 2026 8:16am | Jul 8, 2026 9:45am | Jul 8, 2026 9:46am | Jul 8, 2026 9:46am | Jul 8, 2026 9:46am | Fire |  | Fair | No | Check and find ok
Non-Outage | J.E.26.07.04974 | C001842922 | Oshane Warren | Westmoreland | Completed | Load_241469 | Paradise - 210 | Jul 8, 2026 8:00am | Jul 8, 2026 8:00am | Jul 8, 2026 9:47am | Jul 8, 2026 9:47am | Jul 8, 2026 9:47am | Jul 8, 2026 9:47am | Jul 8, 2026 9:47am | Jul 8, 2026 9:47am | Fire |  | Fair | No | Check and find ok
Non-Outage | J.E.26.07.05160 | C001842923 | Oshane Warren | Westmoreland | Completed | Load_253108 | Paradise - 210 | Jul 8, 2026 8:00am | Jul 8, 2026 8:00am | Jul 8, 2026 11:19am | Jul 8, 2026 11:19am | Jul 8, 2026 11:19am | Jul 8, 2026 11:20am | Jul 8, 2026 11:20am | Jul 8, 2026 11:20am |  |  | Fair | No | Check and find ok
Non-Outage | J.E.26.07.06893 | C001842924 | Oshane Warren | Westmoreland | Completed | Load_255735 | Paradise - 210 | Jul 8, 2026 8:00am | Jul 8, 2026 8:00am | Jul 8, 2026 9:53am | Jul 8, 2026 9:54am | Jul 8, 2026 11:18am | Jul 8, 2026 11:18am | Jul 8, 2026 11:19am | Jul 8, 2026 11:19am |  |  | Fair | No | Change defective service wire used 15ft of number 6twisted used 3 service connector
Non-Outage | J.E.26.07.06609 | C001842918 | Neville Spencer | null | Completed | null | null | Jul 8, 2026 7:58am | Jul 8, 2026 7:59am | Jul 8, 2026 8:05am | Jul 8, 2026 8:05am | Jul 8, 2026 9:13am | Jul 8, 2026 10:31am | Jul 8, 2026 10:31am | Jul 8, 2026 10:31am |  |  | Fair | No | Open 10 kva xmfr at pole #=0100800 splice and retention broken secondary neutral conductor used 150 ft # 2 AA conductor, 2 clamps, 1, preform supply restored.voltage reading 117 118;236 .
Non-Outage | J.E.26.07.06627 | C001842915 | Evan Spaulding | null | Completed | null | null | Jul 8, 2026 7:58am | Jul 8, 2026 7:58am | Jul 8, 2026 8:14am | Jul 8, 2026 8:14am | Jul 8, 2026 8:14am | Jul 8, 2026 8:15am | Jul 8, 2026 8:15am | Jul 8, 2026 8:15am | TreeContact |  | Fair | No | Issue was resolved last night.
Non-Outage | J.E.26.07.06647 | C001842914 | Evan Spaulding | null | Completed | null | null | Jul 8, 2026 7:58am | Jul 8, 2026 7:58am | Jul 8, 2026 8:16am | Jul 8, 2026 8:16am | Jul 8, 2026 8:16am | Jul 8, 2026 8:17am | Jul 8, 2026 8:17am | Jul 8, 2026 8:17am |  |  | Fair | No | Issue was resolved last night.
Non-Outage | J.E.26.07.06692 | C001842916 | Evan Spaulding | null | Completed | null | null | Jul 8, 2026 7:58am | Jul 8, 2026 7:58am | Jul 8, 2026 10:25am | Jul 8, 2026 10:25am | Jul 8, 2026 10:50am | Jul 8, 2026 11:22am | Jul 8, 2026 11:23am | Jul 8, 2026 11:23am |  |  | SevereWind | No | Retention secondary conductors and replace 1-2 amps Transformer fuse,no pole number.
Outage | J.E.26.07.06916 | C001842917 | Clyde Brown | Clarendon | Completed | Load_237763 | May Pen - 110 | Jul 8, 2026 7:58am | Jul 8, 2026 3:29pm | Jul 8, 2026 5:50pm | Jul 8, 2026 5:50pm | Jul 8, 2026 6:25pm | Jul 8, 2026 6:42pm | Jul 8, 2026 6:51pm | Jul 8, 2026 6:51pm |  |  | Fair | No | 25kva transformer tripped line patrolled and no fault seen and transformer reset.
Non-Outage | J.E.26.07.05644 | C001842905 | Floyd Taylor | Trelawny | Completed | Load_240895 | Greenwood - 110 | Jul 8, 2026 7:54am | Jul 8, 2026 7:54am | Jul 8, 2026 9:28am | Jul 8, 2026 9:28am | Jul 8, 2026 10:44am | Jul 8, 2026 12:08pm | Jul 8, 2026 12:18pm | Jul 8, 2026 12:18pm |  |  | Fair | No | Isolated 25kva transformer, spliced and retention 2 spans of secondary phase conductor used about 20ft#2aac and 2pg clamps voltage readings left 117,116,234
Non-Outage | J.E.26.07.06901 | C001842912 | Rusean Allen | null | Completed | null | null | Jul 8, 2026 7:54am | Jul 8, 2026 7:55am | Jul 8, 2026 1:16pm | Jul 8, 2026 1:23pm | Jul 8, 2026 1:25pm | Jul 8, 2026 1:26pm | Jul 8, 2026 1:26pm | Jul 8, 2026 1:26pm | Fire |  | Fair | No | Not found
Non-Outage | J.E.26.07.06911 | C001842907 | Floyd Taylor | Trelawny | Completed | Load_294629 | Greenwood - 110 | Jul 8, 2026 7:54am | Jul 8, 2026 7:54am | Jul 8, 2026 1:13pm | Jul 8, 2026 1:13pm | Jul 8, 2026 1:36pm | Jul 8, 2026 2:03pm | Jul 8, 2026 2:06pm | Jul 8, 2026 2:06pm |  |  | Fair | No | Isolate 25kva transformer and remake joint at midspan connection using two 2pg clamps voltage reading 114,116,231
Outage | J.E.26.07.06197 | C001842906 | Rusean Allen | KSAN | Completed | Load_250320 | Washington Blvd - 710 | Jul 8, 2026 7:54am | Jul 8, 2026 7:55am | Jul 8, 2026 11:09am | Jul 8, 2026 11:09am | Jul 8, 2026 11:15am | Jul 8, 2026 11:15am | Jul 8, 2026 11:15am | Jul 8, 2026 11:15am | BrokenWire |  | Fair | No | Premises locked
Outage | J.E.26.07.06363 | C001842908 | Rusean Allen | KSAN | Completed | Load_249802 | Washington Blvd - 310 | Jul 8, 2026 7:54am | Jul 8, 2026 7:55am | Jul 8, 2026 10:45am | Jul 8, 2026 10:45am | Jul 8, 2026 10:53am | Jul 8, 2026 10:53am | Jul 8, 2026 10:54am | Jul 8, 2026 10:54am |  |  | Fair | No | Premises locked
Outage | J.E.26.07.06420 | C001842911 | Rusean Allen | KSAS | Completed | Load_251222 | Greenwich - 310 | Jul 8, 2026 7:54am | Jul 8, 2026 7:55am | Jul 8, 2026 9:32am | Jul 8, 2026 10:04am | Jul 8, 2026 10:31am | Jul 8, 2026 10:38am | Jul 8, 2026 10:38am | Jul 8, 2026 10:38am |  |  | Fair | No | Meter mixed up at premises, customer was advised to go to ruthven rd
Outage | J.E.26.07.06479 | C001842910 | Rusean Allen | KSAS | Completed | Load_246833 | Greenwich - 710 | Jul 8, 2026 7:54am | Jul 8, 2026 7:55am | Jul 8, 2026 10:11am | Jul 8, 2026 10:38am | Jul 8, 2026 10:42am | Jul 8, 2026 10:43am | Jul 8, 2026 10:43am | Jul 8, 2026 10:43am | TreeContact |  | Fair | No | Found okay
Outage | J.E.26.07.06561 | C001842909 | Rusean Allen | KSAN | Completed | Load_254664 | Washington Blvd - 310 | Jul 8, 2026 7:54am | Jul 8, 2026 7:55am | Jul 8, 2026 11:01am | Jul 8, 2026 11:01am | Jul 8, 2026 11:06am | Jul 8, 2026 11:09am | Jul 8, 2026 11:09am | Jul 8, 2026 11:09am |  |  | Fair | No | Rami failure, customer is the only one without power Yp#02692Refer to field service department.
Outage | J.E.26.07.06902 | C001842903 | Evan Spaulding | St.Mary | Completed | Load_246569 | Highgate -110 | Jul 8, 2026 7:53am | Jul 8, 2026 7:54am | Jul 8, 2026 8:22am | Jul 8, 2026 8:22am | Jul 8, 2026 9:14am | Jul 8, 2026 9:41am | Jul 8, 2026 9:42am | Jul 8, 2026 9:42am | Fire |  | Fair | No | Replace 60ft #6 Triplex service wire and 3-1 bolt clamps,voltage left 117v,117v,234v.
Non-Outage | J.E.26.07.04574 | C001842901 | Edward Royal | KSAN | Completed | Load_258770 | Washington Blvd - 510 | Jul 8, 2026 7:51am | Jul 8, 2026 7:51am | Jul 8, 2026 4:24pm | Jul 8, 2026 4:24pm | Jul 8, 2026 4:24pm | Jul 8, 2026 4:25pm | Jul 8, 2026 4:25pm | Jul 8, 2026 4:25pm |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.07.00136 | C001842899 | Edward Royal | KSAN | Completed | Load_238618 | Hope - 510 | Jul 8, 2026 7:50am | Jul 8, 2026 7:50am | Jul 8, 2026 12:23pm | Jul 8, 2026 12:23pm | Jul 8, 2026 12:23pm | Jul 8, 2026 4:24pm | Jul 8, 2026 4:24pm | Jul 8, 2026 4:24pm |  |  | Fair | No | Spliced and reconnected drop lead to secondary neutral spliced and reconnected secondary phase and neutral using 50ft open number 2 conductor 6 single bolt clamp voltage reading 239.9 121 120
Non-Outage | J.E.26.07.00745 | C001842898 | Edward Royal | KSAN | Completed | Load_238618 | Hope - 510 | Jul 8, 2026 7:50am | Jul 8, 2026 7:50am | Jul 8, 2026 4:24pm | Jul 8, 2026 4:24pm | Jul 8, 2026 4:24pm | Jul 8, 2026 4:24pm | Jul 8, 2026 4:24pm | Jul 8, 2026 4:24pm |  |  | Fair | No | Premises found ok related to outage
Non-Outage | J.E.26.07.01830 | C001842896 | Javid Vernon | Westmoreland | Completed | Load_261697 | Paradise - 310 | Jul 8, 2026 7:47am | Jul 8, 2026 7:47am | Jul 8, 2026 9:43am | Jul 8, 2026 9:43am | Jul 8, 2026 10:15am | Jul 8, 2026 10:37am | Jul 8, 2026 10:37am | Jul 8, 2026 10:37am |  |  | Fair | No | Replace two clamps at customer pothead voltage found 104/96/200 voltage left 117/115/233
Non-Outage | J.E.26.07.01857 | C001842893 | Javid Vernon | Westmoreland | Completed | Load_243785 | Paradise - 310 | Jul 8, 2026 7:47am | Jul 8, 2026 7:47am | Jul 8, 2026 1:17pm | Jul 8, 2026 1:17pm | Jul 8, 2026 2:31pm | Jul 8, 2026 2:37pm | Jul 8, 2026 2:37pm | Jul 8, 2026 2:37pm |  |  | Fair | No | Premises check and found okay customer has and internal problem voltage reading 114/111/225 customer was advice
Non-Outage | J.E.26.07.02755 | C001842895 | Javid Vernon | Westmoreland | Completed | Load_247850 | Paradise - 310 | Jul 8, 2026 7:47am | Jul 8, 2026 7:47am | Jul 8, 2026 8:55am | Jul 8, 2026 8:55am | Jul 8, 2026 9:32am | Jul 8, 2026 9:43am | Jul 8, 2026 9:43am | Jul 8, 2026 9:43am |  |  | Fair | No | Premises check and found okay customer has internal problem voltage reading 115/116/232
Non-Outage | J.E.26.07.04147 | C001842894 | Javid Vernon | Westmoreland | Completed | Load_268740 | Paradise - 310 | Jul 8, 2026 7:47am | Jul 8, 2026 7:47am | Jul 9, 2026 7:52am | Jul 9, 2026 7:52am | Jul 9, 2026 7:52am | Jul 9, 2026 7:52am | Jul 9, 2026 7:53am | Jul 9, 2026 7:53am |  |  | Fair | No | Customer stated that the issue has been resolved
Non-Outage | J.E.26.07.06782 | C001842892 | Roemello Brown | Trelawny | Completed | Load_247105 | Martha Brae - 110 | Jul 8, 2026 7:46am | Jul 8, 2026 7:46am | Jul 8, 2026 8:45am | Jul 8, 2026 8:45am | Jul 8, 2026 9:02am | Jul 8, 2026 9:02am | Jul 8, 2026 9:37am | Jul 8, 2026 9:37am |  |  | Fair | No | Neutral broke have it re-join Voltage found 146/91/237Voltage leave 119/118/237
Non-Outage | J.E.26.07.02093 | C001842889 | Elvis Trowers | KSAS | Completed | Load_241282 | Duhaney - 310 | Jul 8, 2026 7:45am | Jul 8, 2026 7:46am | Jul 8, 2026 2:26pm | Jul 8, 2026 2:27pm | Jul 8, 2026 2:38pm | Jul 8, 2026 2:41pm | Jul 8, 2026 2:41pm | Jul 8, 2026 2:41pm | LeaningPole |  | Fair | Yes | Checked and found ok, C/W pole.
Non-Outage | J.E.26.07.03269 | C001842886 | Elvis Trowers | KSAS | Completed | Load_267072 | Duhaney - 310 | Jul 8, 2026 7:45am | Jul 8, 2026 7:46am | Jul 8, 2026 11:53am | Jul 8, 2026 11:53am | Jul 8, 2026 12:12pm | Jul 8, 2026 1:35pm | Jul 8, 2026 1:35pm | Jul 8, 2026 1:35pm |  |  | Fair | Yes | Customer was found having fluctuating voltages when checked, at the back of some of these buildings can’t be accessed as theirs no one home.
Non-Outage | J.E.26.07.05713 | C001842887 | Elvis Trowers | KSAS | Completed | Load_260462 | Duhaney - 310 | Jul 8, 2026 7:45am | Jul 8, 2026 7:46am | Jul 8, 2026 10:09am | Jul 8, 2026 10:09am | Jul 8, 2026 10:57am | Jul 8, 2026 11:45am | Jul 8, 2026 11:45am | Jul 8, 2026 11:45am |  |  | Fair | Yes | Happened to be internal when checked out customer was advised to contact an electrician, voltage when checked was left at 118+118=236 volts
Non-Outage | J.E.26.07.05887 | C001842888 | Elvis Trowers | KSAS | Completed | Load_251395 | Duhaney - 310 | Jul 8, 2026 7:45am | Jul 8, 2026 7:46am | Jul 8, 2026 9:15am | Jul 8, 2026 9:15am | Jul 8, 2026 9:49am | Jul 8, 2026 10:04am | Jul 8, 2026 10:05am | Jul 8, 2026 10:05am | BrokenWire |  | Fair | Yes | Premises checked and found ok upon arrival, broken wires are not belonging to JPS but to other cable companies.
Outage | J.E.26.07.06899 | C001842890 | Tajay Bernard | Hanover | Completed | Load_302811 | Orange Bay - 310 | Jul 8, 2026 7:45am | Jul 8, 2026 7:46am | Jul 8, 2026 10:14am | Jul 8, 2026 10:14am | Jul 8, 2026 10:35am | Jul 8, 2026 11:11am | Jul 8, 2026 11:13am | Jul 8, 2026 11:13am |  |  | Fair | No | Refuse 1 15amp junction fuse
Non-Outage | J.E.26.07.06674 | C001842883 | Roemello Brown | Trelawny | Completed | Load_250629 | Martha Brae - 210 | Jul 8, 2026 7:44am | Jul 8, 2026 7:45am | Jul 9, 2026 8:52am | Jul 9, 2026 10:04am | Jul 9, 2026 10:04am | Jul 9, 2026 10:05am | Jul 9, 2026 10:11am | Jul 9, 2026 10:11am |  |  | Fair | No | Corrosion at the pothead have 3 linkets installed Voltage found 117/68.8/185Voltage leave 116/119/235
Non-Outage | J.E.26.07.06850 | C001842885 | Elvis Trowers | KSAS | Completed | Load_260462 | Duhaney - 310 | Jul 8, 2026 7:44am | Jul 8, 2026 7:46am | Jul 8, 2026 2:20pm | Jul 8, 2026 2:20pm | Jul 8, 2026 2:25pm | Jul 8, 2026 2:26pm | Jul 8, 2026 2:26pm | Jul 8, 2026 2:26pm |  |  | Fair | Yes | Happened to be internal when checked, customer was advised to contact an electrician.
Non-Outage | J.E.26.07.06696 | C001842882 | Floyd Taylor | Trelawny | Completed | Load_261016 | Greenwood - 210 | Jul 8, 2026 7:43am | Jul 8, 2026 7:43am | Jul 8, 2026 7:54am | Jul 8, 2026 7:55am | Jul 8, 2026 7:55am | Jul 8, 2026 9:28am | Jul 8, 2026 9:28am | Jul 8, 2026 9:28am |  |  | Fair | No | Replace 100ft of number 6 wire using 3 clamps and 3pen union voltage readings left. 112,114,232.
Non-Outage | J.E.26.07.06773 | C001842881 | Junior Scarlett | St.James | Completed | Load_247713 | Bogue - 610 | Jul 8, 2026 7:40am | Jul 8, 2026 8:16am | Jul 8, 2026 8:28am | Jul 8, 2026 1:33pm | Jul 8, 2026 2:38pm | Jul 8, 2026 3:03pm | Jul 8, 2026 3:05pm | Jul 8, 2026 3:05pm |  |  | Fair | No | Check and found okVoltage found 113v 112v 225v
Non-Outage | J.E.26.07.06563 | C001842880 | Junior Scarlett | St.James | Completed | Load_260420 | Bogue - 610 | Jul 8, 2026 7:39am | Jul 8, 2026 8:16am | Jul 8, 2026 8:28am | Jul 8, 2026 10:18am | Jul 8, 2026 10:22am | Jul 8, 2026 10:36am | Jul 8, 2026 10:37am | Jul 8, 2026 10:37am |  |  | Fair | No | Refer to emergency teamJumper burn offVoltage found 115v 0.88v 115
Outage | J.E.26.07.06604 | C001842879 | Romeo Brissett | St.James | Completed | Load_260420 | Bogue - 610 | Jul 8, 2026 7:39am | Jul 8, 2026 1:00pm | Jul 8, 2026 2:24pm | Jul 8, 2026 2:24pm | Jul 8, 2026 2:24pm | Jul 8, 2026 2:30pm | Jul 8, 2026 2:30pm | Jul 8, 2026 2:30pm |  |  | Fair | No | Isolated (2)25 kva transformer, removed illegal connections, cut and removed tree limbs, spliced and retention 2 span of secondary. Used 50ft of #2 and 4 clamps
Non-Outage | J.E.26.07.06509 | C001842877 | Marlon Brown | Trelawny | Completed | Load_248221 | Duncans - 210 | Jul 8, 2026 7:36am | Jul 8, 2026 7:42am | Jul 8, 2026 8:14am | Jul 8, 2026 8:14am | Jul 8, 2026 8:34am | Jul 8, 2026 8:39am | Jul 8, 2026 8:39am | Jul 8, 2026 8:39am | Fire |  | Fair | No | Check and found ok. Customer says he didn’t make any report to jps.
Non-Outage | J.E.26.07.06725 | C001842875 | Marlon Brown | null | Completed | null | null | Jul 8, 2026 7:36am | Jul 8, 2026 7:43am | Jul 8, 2026 7:47am | Jul 8, 2026 10:27am | Jul 8, 2026 11:39am | Jul 8, 2026 11:40am | Jul 8, 2026 11:40am | Jul 8, 2026 11:40am |  |  | Fair | No | Unable to locate customer via telephone nor direction
Outage | J.E.26.07.06790 | C001842878 | Nickolas Rodriques | St.Catherine | Completed | Load_249185 | Rhodens Pen - 410 | Jul 8, 2026 7:36am | Jul 8, 2026 7:36am | Jul 8, 2026 2:57pm | Jul 8, 2026 6:40pm | Jul 8, 2026 6:58pm | Jul 8, 2026 7:01pm | Jul 8, 2026 7:15pm | Jul 8, 2026 7:15pm |  |  | Fair | No | Unable to locate or communicate with the customer after several attempts. (Area has electricity).
Outage | J.E.26.07.06794 | C001842876 | Marlon Brown | Trelawny | Completed | Load_266884 | Duncans - 210 | Jul 8, 2026 7:36am | Jul 8, 2026 7:42am | Jul 8, 2026 8:39am | Jul 8, 2026 8:39am | Jul 8, 2026 9:27am | Jul 8, 2026 10:27am | Jul 8, 2026 10:27am | Jul 8, 2026 10:27am | Fire |  | Fair | No | Isolated 50kva transformer to clear primary broken conductor. Use 2 pg clamps and 2 #2 preforms.
Outage | J.E.26.07.06842 | C001842873 | Raymond Carr | St.Mary | Completed | Load_269605 | Blackstonedge - 110 | Jul 8, 2026 7:34am | Jul 8, 2026 7:35am | Jul 8, 2026 11:02am | Jul 8, 2026 11:02am | Jul 8, 2026 11:07am | Jul 8, 2026 12:39am | Jul 8, 2026 11:44am | Jul 8, 2026 11:44am |  |  | SevereWind | No | A 20 amp Tripp saver found operated at pole number 0014199, line patrol and found okay, however tree contact suspected. Tripp saver reset and supply was restored
Outage | J.E.26.07.06898 | C001842874 | Raymond Carr | St.Mary | Completed | Load_246350 | Blackstonedge - 110 | Jul 8, 2026 7:34am | Jul 8, 2026 7:35am | Jul 8, 2026 8:10am | Jul 8, 2026 8:10am | Jul 8, 2026 10:18am | Jul 8, 2026 10:50am | Jul 8, 2026 11:01am | Jul 8, 2026 11:01am |  |  | Fair | No | Blown junction fuse found at pole number 0014181, line patrol and found okay, however tree contact was suspected. A 25 amp fuse fuse was used to renew supply was restored.
Non-Outage | J.E.26.06.38864 | C001842871 | Damion Reid | Manchester | Completed | Load_245911 | Kendal - 310 | Jul 8, 2026 7:30am | Jul 8, 2026 7:30am | Jul 8, 2026 8:25am | Jul 8, 2026 8:25am | Jul 8, 2026 9:01am | Jul 8, 2026 9:50am | Jul 8, 2026 9:52am | Jul 8, 2026 9:52am |  |  | Fair | No | Customer have internal problems customer have been advised to contact JPS when the electrician arrives
Non-Outage | J.E.26.06.23024 | C001842870 | Christopher Edwards | KSAN | Completed | Load_253373 | Constant Spring - 410 | Jul 8, 2026 7:29am | Jul 8, 2026 7:32am | Jul 8, 2026 7:55am | Jul 8, 2026 8:08am | Jul 8, 2026 9:12am | Jul 8, 2026 10:32am | Jul 8, 2026 10:36am | Jul 8, 2026 10:36am |  |  | Fair | No | Jump out splicing sleeves on open secondary neutral Voltage:114,115,230vHowever area requires secondary bushing
Non-Outage | J.E.26.06.27676 | C001842868 | Christopher Edwards | KSAN | Completed | Load_261661 | Constant Spring - 410 | Jul 8, 2026 7:29am | Jul 8, 2026 7:29am | Jul 9, 2026 11:44am | Jul 9, 2026 11:44am | Jul 9, 2026 12:00pm | Jul 9, 2026 12:43pm | Jul 9, 2026 12:44pm | Jul 9, 2026 12:44pm |  |  | Fair | No | Remake corroded neutral joint at poleUsing (1) one bolt clamps Voltage:115,115,230v
Non-Outage | J.E.26.07.03261 | C001842866 | Christopher Edwards | KSAN | Completed | Load_269049 | Constant Spring - 410 | Jul 8, 2026 7:29am | Jul 8, 2026 7:29am | Jul 8, 2026 2:35pm | Jul 8, 2026 2:35pm | Jul 8, 2026 2:35pm | Jul 9, 2026 7:37am | Jul 9, 2026 7:37am | Jul 9, 2026 7:37am |  |  | Fair | No | Customer was contacted and stated that the issue was resolved
Non-Outage | J.E.26.07.06877 | C001842864 | Christopher Edwards | KSAN | Completed | Load_269843 | Constant Spring - 410 | Jul 8, 2026 7:29am | Jul 8, 2026 7:29am | Jul 8, 2026 12:29pm | Jul 8, 2026 2:33pm | Jul 8, 2026 2:33pm | Jul 8, 2026 2:33pm | Jul 8, 2026 2:33pm | Jul 8, 2026 2:33pm |  |  | Fair | No | Related to previous call that has been resolved
Non-Outage | J.E.26.07.06883 | C001842865 | Christopher Edwards | KSAN | Completed | Load_242752 | Constant Spring - 410 | Jul 8, 2026 7:29am | Jul 8, 2026 7:29am | Jul 8, 2026 12:29pm | Jul 8, 2026 12:29pm | Jul 8, 2026 1:12pm | Jul 8, 2026 2:29pm | Jul 8, 2026 2:32pm | Jul 8, 2026 2:32pm |  |  | Fair | No | Remake burnt open secondary neutral joint Using (4) one bolt clamps Voltage:115,114,230v
Outage | J.E.26.07.05855 | C001842859 | Derrick Dawkins | St.James | Completed | Load_264619 | Bogue - 310 | Jul 8, 2026 7:26am | Jul 8, 2026 7:26am | Jul 8, 2026 10:23am | Jul 8, 2026 10:23am | Jul 8, 2026 10:23am | Jul 8, 2026 10:24am | Jul 8, 2026 10:24am | Jul 8, 2026 10:24am |  |  | Fair | No | Related to the previous call where the transformer fuse was blown
Outage | J.E.26.07.06429 | C001842860 | Derrick Dawkins | St.James | Completed | Load_557017 | Bogue - 310 | Jul 8, 2026 7:26am | Jul 8, 2026 7:26am | Jul 8, 2026 9:47am | Jul 8, 2026 9:47am | Jul 8, 2026 9:47am | Jul 8, 2026 9:31am | Jul 8, 2026 9:48am | Jul 8, 2026 9:48am |  |  | Fair | No | Refer back to field service
Outage | J.E.26.07.06675 | C001842861 | Derrick Dawkins | St.James | Completed | Load_243460 | Bogue - 310 | Jul 8, 2026 7:26am | Jul 8, 2026 7:26am | Jul 8, 2026 12:32pm | Jul 8, 2026 12:32pm | Jul 8, 2026 2:46pm | Jul 8, 2026 2:47pm | Jul 8, 2026 2:49pm | Jul 8, 2026 2:49pm |  |  | Fair | No | Calls to customer went unanswered can not locate customer
Outage | J.E.26.07.06727 | C001842862 | Derrick Dawkins | St.James | Completed | Load_1002429 | Bogue - 310 | Jul 8, 2026 7:26am | Jul 8, 2026 7:26am | Jul 8, 2026 10:38am | Jul 8, 2026 11:01am | Jul 8, 2026 11:26am | Jul 8, 2026 12:30pm | Jul 8, 2026 12:30pm | Jul 8, 2026 12:30pm |  |  | Fair | No | Found a junction fuse blown 50 amp replaced a 50 amp junction fuse no pole # available
Outage | J.E.26.07.06459 | C001842858 | Derrick Dawkins | St.James | Completed | Load_259996 | Bogue - 410 | Jul 8, 2026 7:25am | Jul 8, 2026 7:26am | Jul 8, 2026 7:55am | Jul 8, 2026 7:55am | Jul 8, 2026 9:40am | Jul 8, 2026 9:21am | Jul 8, 2026 9:46am | Jul 8, 2026 9:46am |  |  | Fair | No | Calls to customer went unanswered cannot locate customer checked and found area ok
Outage | J.E.26.07.05790 | C001842855 | Wan Carlos Scarlett | Portmore | Completed | Load_412901 | Naggo Head - 510 | Jul 8, 2026 7:15am | Jul 8, 2026 7:16am | Jul 8, 2026 8:12am | Jul 8, 2026 8:12am | Jul 8, 2026 8:56am | Jul 8, 2026 9:08am | Jul 8, 2026 9:09am | Jul 8, 2026 9:09am |  |  | Fair | No | Customer confirm that power supply has been restored
Outage | J.E.26.07.06873 | C001842857 | Wan Carlos Scarlett | Portmore | Completed | Load_1003637 | Naggo Head - 610 | Jul 8, 2026 7:15am | Jul 8, 2026 7:16am | Jul 8, 2026 11:00am | Jul 8, 2026 2:13pm | Jul 8, 2026 3:13pm | Jul 8, 2026 4:27pm | Jul 8, 2026 4:28pm | Jul 8, 2026 4:28pm |  |  | Fair | No | Customer was reconnected from escalation department power supply has been restored
Outage | J.E.26.07.06860 | C001842854 | Tyrese Williams | St.Ann | Completed | Load_573918 | Cardiff Hall - 310 | Jul 8, 2026 7:10am | Jul 8, 2026 7:13am | Jul 8, 2026 7:52am | Jul 8, 2026 8:52am | Jul 8, 2026 8:52am | Jul 8, 2026 8:52am | Jul 8, 2026 8:52am | Jul 8, 2026 8:52am |  |  | Fair | No | Premises found ok call related to 20amp junction fuse
Outage | J.E.26.07.06830 | C001842849 | Gregory Grossett | Portland | Completed | Load_249419 | Port Antonio - 410 | Jul 8, 2026 7:07am | Jul 8, 2026 7:08am | Jul 8, 2026 9:20am | Jul 8, 2026 9:20am | Jul 8, 2026 10:52am | Jul 8, 2026 11:00am | Jul 8, 2026 11:00am | Jul 8, 2026 11:00am |  | Y | Rains | No | 10kva transformer trip at pole#042250 cause by tree limb fall on secondary conductors reset transformer to restore power to the area.
Outage | J.E.26.07.06851 | C001842850 | Gregory Grossett | Portland | Completed | Load_237695 | Port Antonio - 410 | Jul 8, 2026 7:07am | Jul 8, 2026 7:08am | Jul 8, 2026 9:19am | Jul 8, 2026 9:19am | Jul 8, 2026 9:19am | Jul 8, 2026 9:19am | Jul 8, 2026 9:19am | Jul 8, 2026 9:19am |  | Y | Fair | No | 25kva transformer fuse blown cause by bamboo fall on secondary conductors cut and removed bamboo then restore supply to the area.Material use 2amp fuse.
Outage | J.E.26.07.06886 | C001842851 | Gregory Grossett | Portland | Completed | Load_237695 | Port Antonio - 410 | Jul 8, 2026 7:07am | Jul 8, 2026 7:08am | Jul 8, 2026 7:38am | Jul 8, 2026 7:38am | Jul 8, 2026 8:39am | Jul 8, 2026 9:07am | Jul 8, 2026 9:18am | Jul 8, 2026 9:18am |  | Y | Fair | No | 25kva transformer fuse blown cause by bamboo fall on secondary conductors cut and removed bamboo then restore supply to the area.Material use 2amp fuse.
Outage | J.E.26.07.06894 | C001842852 | Andrae Clarke | Portland | Completed | Load_265014 | Port Antonio - 410 | Jul 8, 2026 7:07am | Jul 8, 2026 9:18am | Jul 8, 2026 2:09pm | Jul 8, 2026 2:09pm | Jul 8, 2026 3:38pm | Jul 8, 2026 4:37pm | Jul 8, 2026 5:19pm | Jul 8, 2026 5:19pm |  |  | Fair | No | Made several phone calls to the customer and got no response
Outage | J.E.26.07.06836 | C001842848 | Tajay Bernard | Hanover | Completed | Load_292056 | Orange Bay - 310 | Jul 8, 2026 7:04am | Jul 8, 2026 7:08am | Jul 8, 2026 7:18am | Jul 8, 2026 7:18am | Jul 8, 2026 8:15am | Jul 8, 2026 10:12am | Jul 8, 2026 10:14am | Jul 8, 2026 10:14am | BrokenWire |  | Fair | No | Replace 70ft of #6 triplex wire and also clean and remake joints at (4) customers pot head use 4 clampsVoltage found 110Voltage left 110/109/220Cause( customer service wire was defective)
Outage | J.E.26.07.06070 | C001842808 | Romeo Brissett | St.James | Completed | Load_240137 | Queens Drive - 810 | Jul 8, 2026 2:25am | Jul 8, 2026 9:29am | Jul 8, 2026 10:24am | Jul 8, 2026 10:24am | Jul 8, 2026 11:43am | Jul 8, 2026 12:08am | Jul 8, 2026 12:15pm | Jul 8, 2026 12:15pm |  |  | Fair | No | Check and found internal fault, V/R 114-115-229
Outage | J.E.26.07.06498 | C001842806 | Swon Miller | St.James | Completed | Load_245573 | Queens Drive - 710 | Jul 8, 2026 2:24am | Jul 8, 2026 2:26am | Jul 8, 2026 5:21am | Jul 8, 2026 5:21am | Jul 8, 2026 5:50am | Jul 8, 2026 5:57am | Jul 8, 2026 6:00am | Jul 8, 2026 6:00am |  |  | Fair | No | Check and found area ok voltage found 117/116/234 voltage left 116/117/234
Outage | J.E.26.07.06690 | C001842807 | Swon Miller | St.James | Completed | Load_247173 | Queens Drive - 710 | Jul 8, 2026 2:24am | Jul 8, 2026 2:26am | Jul 8, 2026 3:52am | Jul 8, 2026 3:52am | Jul 8, 2026 4:50am | Jul 8, 2026 5:13am | Jul 8, 2026 5:20am | Jul 8, 2026 5:20am |  |  | Fair | No | Check and found area okay unable to locate customer phone calls to customer Number went unanswered
Outage | J.E.26.07.06785 | C001842805 | Omar King | St.Ann | Completed | Load_576574 | Ocho Rios - 510 | Jul 8, 2026 2:12am | Jul 8, 2026 7:12am | Jul 8, 2026 8:00am | Jul 8, 2026 8:00am | Jul 8, 2026 8:20am | Jul 8, 2026 8:48am | Jul 8, 2026 8:48am | Jul 8, 2026 8:48am |  |  | Fair | No | Found 10 KVA transformer fuse blow fuse as been replaced area is now with supply
Outage | J.E.26.07.06856 | C001842804 | Tyrese Williams | St.Ann | Completed | Load_573919 | Cardiff Hall - 310 | Jul 8, 2026 2:11am | Jul 8, 2026 7:11am | Jul 8, 2026 7:52am | Jul 8, 2026 8:00am | Jul 8, 2026 8:37am | Jul 8, 2026 8:50am | Jul 8, 2026 8:50am | Jul 8, 2026 8:50am |  |  | Fair | No | Replace a 20 junction fuse at pole
Outage | J.E.26.07.06359 | C001842799 | Roxroy Needham | St.Ann | Completed | Load_246075 | Roaring River - 410 | Jul 8, 2026 12:20am | Jul 8, 2026 12:22am | Jul 8, 2026 12:26am | Jul 8, 2026 1:30am | Jul 8, 2026 1:30am | Jul 8, 2026 1:29am | Jul 8, 2026 1:33am | Jul 8, 2026 1:33am |  |  | Rains | No | Premises not found not getting customer on phone
Outage | J.E.26.07.05331 | C001842797 | Roxroy Needham | St.Ann | Completed | Load_249727 | Roaring River - 210 | Jul 8, 2026 12:17am | Jul 8, 2026 12:22am | Jul 8, 2026 12:35am | Jul 8, 2026 12:35am | Jul 8, 2026 1:26am | Jul 8, 2026 1:28am | Jul 8, 2026 1:28am | Jul 8, 2026 1:28am |  | Y | Rains | No | Replace a 8 amps junction fuse at pole
Outage | J.E.26.07.05693 | C001842796 | Roxroy Needham | St.Ann | Completed | Load_247617 | Roaring River - 210 | Jul 8, 2026 12:15am | Jul 8, 2026 12:16am | Jul 8, 2026 1:28am | Jul 8, 2026 1:28am | Jul 8, 2026 1:28am | Jul 8, 2026 1:25am | Jul 8, 2026 1:30am | Jul 8, 2026 1:30am |  |  | Rains | No | Premises not found not getting customer on phone
Outage | J.E.26.07.05969 | C001842794 | Delano Gayle | St.Catherine | Completed | Load_557158 | Tredegar - 210 | Jul 8, 2026 12:06am | Jul 8, 2026 12:16am | Jul 8, 2026 3:52am | Jul 8, 2026 3:52am | Jul 8, 2026 4:45am | Jul 8, 2026 4:59am | Jul 8, 2026 4:59am | Jul 8, 2026 4:59am | LeakingTransformer |  | Fair | No | Hexing transformer leaking oil from what appears to be drop leads bushing as oil is running down through box which is connected on the face of transformer, found transformer isolated as fuse linked was open, send call to maintenance urgent attention required as approximately 30 customers are without supply from sunday
Non-Outage | J.E.26.07.06645 | C001842791 | Richard Nicholas | null | Completed | null | null | Jul 7, 2026 11:52pm | Jul 8, 2026 10:57am | Jul 8, 2026 11:16am | Jul 8, 2026 11:16am | Jul 8, 2026 11:48am | Jul 8, 2026 12:16pm | Jul 8, 2026 12:17pm | Jul 8, 2026 12:17pm | BrokenWire |  | Fair | No | No broken wire seen,area found ok
Non-Outage | J.E.26.07.06694 | C001842790 | Swon Miller | null | Completed | null | null | Jul 7, 2026 11:41pm | Jul 7, 2026 11:42pm | Jul 8, 2026 3:43am | Jul 8, 2026 3:47am | Jul 8, 2026 3:47am | Jul 8, 2026 3:51am | Jul 8, 2026 3:51am | Jul 8, 2026 3:51am | BrokenWire |  | Fair | No | Check and found area ok voltage found 115/114/232 voltage left 115/114/232
Non-Outage | J.E.26.07.06699 | C001842786 | Swon Miller | null | Completed | null | null | Jul 7, 2026 11:29pm | Jul 7, 2026 11:31pm | Jul 8, 2026 3:03am | Jul 8, 2026 3:03am | Jul 8, 2026 3:32am | Jul 8, 2026 3:43am | Jul 8, 2026 3:43am | Jul 8, 2026 3:43am | Fire |  | Fair | No | Check and found areas okay voltage found 116/115/232 customer states that power supply has been restored voltage left 116/115/232
Outage | J.E.26.07.06807 | C001842787 | Swon Miller | St.James | Completed | Load_1002045 | Queens Drive - 710 | Jul 7, 2026 11:29pm | Jul 7, 2026 11:31pm | Jul 7, 2026 11:38pm | Jul 7, 2026 11:38pm | Jul 8, 2026 12:17am | Jul 21, 2026 12:35am | Jul 8, 2026 12:35am | Jul 8, 2026 12:35am |  |  | Fair | No | Check and found area okay
Outage | J.E.26.07.06661 | C001842785 | Christopher Edwards | KSAS | Completed | Load_239147 | Duhaney - 310 | Jul 7, 2026 11:24pm | Jul 7, 2026 11:24pm | Jul 7, 2026 11:35pm | Jul 7, 2026 11:57pm | Jul 7, 2026 11:57pm | Jul 8, 2026 12:18am | Jul 8, 2026 12:20am | Jul 8, 2026 12:20am |  |  | Fair | No | Refuse blown junction Fuse using (1) 25 amps
Non-Outage | J.E.26.07.06670 | C001842784 | Swon Miller | St.James | Completed | Load_250164 | Rose Hall - 210 | Jul 7, 2026 11:12pm | Jul 7, 2026 11:12pm | Jul 8, 2026 12:47am | Jul 8, 2026 12:47am | Jul 8, 2026 1:08am | Jul 21, 2026 1:58am | Jul 8, 2026 2:01am | Jul 8, 2026 2:01am |  |  | Fair | No | Check and found 1,50 amp junction fuse blown cause by contamination replace 50 amp junction fuse voltage found 117/ voltage 117/115/203/203/202 two switch defective and needs changing please refer to maintenance/kerron Frazier
Outage | J.E.26.07.06327 | C001842780 | Christopher Edwards | KSAS | Completed | Load_1003139 | Hunts Bay - 410 | Jul 7, 2026 11:05pm | Jul 7, 2026 11:15pm | Jul 8, 2026 5:56am | Jul 8, 2026 5:56am | Jul 8, 2026 6:27am | Jul 8, 2026 6:42am | Jul 8, 2026 6:43am | Jul 8, 2026 6:43am | Fire |  | Fair | No | Customer meter is burnt and needs to be replaced Customer 3 phase meter is burnt resulting in no supply
Outage | J.E.26.07.06798 | C001842779 | Daniel Francis | St.Ann | Completed | Load_255188 | Ocho Rios - 310 | Jul 7, 2026 10:51pm | Jul 7, 2026 10:54pm | Jul 7, 2026 11:02pm | Jul 7, 2026 11:02pm | Jul 7, 2026 11:02pm | Jul 7, 2026 11:50pm | Jul 7, 2026 11:53pm | Jul 7, 2026 11:53pm |  |  | Fair | No | Found secondary phase conducter broken splice and retention using 20ft 2/0
Outage | J.E.26.07.06780 | C001842777 | Evan Spaulding | St.Mary | Completed | Load_269725 | Highgate - 210 | Jul 7, 2026 10:39pm | Jul 8, 2026 7:54am | Jul 8, 2026 9:43am | Jul 8, 2026 9:43am | Jul 8, 2026 9:59am | Jul 8, 2026 10:21am | Jul 8, 2026 10:23am | Jul 8, 2026 10:23am | BrokenPole |  | Fair | No | Use 2-1 bolt clamps at pole, left 109v.
Outage | J.E.26.07.06418 | C001842776 | Hopeton Henry | St.Thomas | Completed | Load_243194 | Good Year - 210 | Jul 7, 2026 10:36pm | Jul 7, 2026 10:36pm | Jul 7, 2026 10:53pm | Jul 7, 2026 10:53pm | Jul 7, 2026 10:53pm | Jul 7, 2026 10:53pm | Jul 7, 2026 10:54pm | Jul 7, 2026 10:54pm |  |  | Fair | No | Reset 30 amp trip saver , no pole number seen
Outage | J.E.26.07.05967 | C001842769 | Horace Malcolm | St.James | Completed | Load_1002436 | Queens Drive - 810 | Jul 7, 2026 10:02pm | Jul 7, 2026 10:15pm | Jul 7, 2026 10:42pm | Jul 7, 2026 10:42pm | Jul 7, 2026 10:46pm | Jul 7, 2026 10:48pm | Jul 7, 2026 10:48pm | Jul 7, 2026 10:48pm |  |  | Fair | No | Reclosed (3) padmount junction switch
Outage | J.E.26.07.06487 | C001842767 | Roxroy Needham | St.Ann | Completed | Load_266799 | Cardiff Hall - 310 | Jul 7, 2026 9:46pm | Jul 7, 2026 9:48pm | Jul 7, 2026 10:37pm | Jul 7, 2026 10:37pm | Jul 7, 2026 10:37pm | Jul 7, 2026 10:38pm | Jul 7, 2026 10:39pm | Jul 7, 2026 10:39pm |  |  | Fair | No | Customer say light was restored
Non-Outage | J.E.26.07.06059 | C001842761 | Andrae Clarke | Portland | Completed | Load_243638 | Port Antonio - 410 | Jul 7, 2026 9:37pm | Jul 8, 2026 9:12am | Jul 8, 2026 11:43am | Jul 8, 2026 11:43am | Jul 8, 2026 12:01pm | Jul 8, 2026 11:56am | Jul 8, 2026 12:24pm | Jul 8, 2026 12:24pm |  |  | Fair | No | Check voltage 121/121/242 Customer to get an electrician to ch internal
Non-Outage | J.E.26.07.06658 | C001842763 | Andrae Clarke | Portland | Completed | Load_238553 | Port Antonio - 310 | Jul 7, 2026 9:37pm | Jul 8, 2026 8:45am | Jul 8, 2026 9:12am | Jul 8, 2026 10:21am | Jul 8, 2026 11:27am | Jul 8, 2026 10:44am | Jul 8, 2026 11:41am | Jul 8, 2026 11:41am |  |  | Fair | No | Transformer pole number 0014265 connections need cleaning Check voltage 96/98/194Emergency crew needed
Outage | J.E.26.07.06778 | C001842759 | Richard Samuda | Manchester | Completed | Load_257533 | Spur Tree - 310 | Jul 7, 2026 9:28pm | Jul 7, 2026 9:31pm | Jul 7, 2026 9:36pm | Jul 7, 2026 9:36pm | Jul 7, 2026 9:57pm | Jul 7, 2026 11:41pm | Jul 7, 2026 11:48pm | Jul 7, 2026 11:48pm |  |  | Fair | No | Defective 25kva transformer 30 customer affected refer call
Outage | J.E.26.07.06661 | C001842747 | Kaydon Taylor | KSAS | Completed | Load_239147 | Duhaney - 310 | Jul 7, 2026 9:00pm | Jul 7, 2026 9:04pm | Jul 7, 2026 9:11pm | Jul 7, 2026 9:11pm | Jul 7, 2026 10:47pm | Jul 7, 2026 11:04pm | Jul 7, 2026 11:04pm | Jul 7, 2026 11:04pm |  |  | Fair | No | 15 amp fuse found blown and replace.
Outage | J.E.26.07.06190 | C001842739 | Moses Elliston | St.Catherine | Completed | Load_245608 | Twickenham - 210 | Jul 7, 2026 8:24pm | Jul 7, 2026 8:25pm | Jul 8, 2026 2:28pm | Jul 8, 2026 2:28pm | Jul 8, 2026 3:36pm | Jul 8, 2026 12:21pm | Jul 8, 2026 3:48pm | Jul 8, 2026 3:48pm |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.07.06745 | C001842738 | Marlon Authors | Manchester | Completed | Load_268532 | Spur Tree - 210 | Jul 7, 2026 8:18pm | Jul 7, 2026 8:19pm | Jul 7, 2026 10:15pm | Jul 7, 2026 10:15pm | Jul 7, 2026 10:15pm | Jul 7, 2026 10:54pm | Jul 7, 2026 10:54pm | Jul 7, 2026 10:54pm | Fire |  | Fair | No | Patrol and found secondary lower phase and neutral banging against cable guy wires. Isolate and close transformer circuit no pole # to retention same. Restored supply ok
Outage | J.E.26.07.06567 | C001842737 | Donald Cunningham | St.Catherine | Completed | Load_556504 | Tredegar - 510 | Jul 7, 2026 8:14pm | Jul 7, 2026 8:17pm | Jul 7, 2026 8:32pm | Jul 7, 2026 8:32pm | Jul 7, 2026 9:32pm | Jul 7, 2026 9:47pm | Jul 7, 2026 9:55pm | Jul 7, 2026 9:55pm |  |  | Fair | No | Entrance to Oscar drive blown junction found and replace with 8 amp fuse
Outage | J.E.26.07.06746 | C001842736 | Nickolas Rodriques | St.Catherine | Completed | Load_261782 | Rhodens Pen - 410 | Jul 7, 2026 8:13pm | Jul 8, 2026 7:27am | Jul 8, 2026 10:40am | Jul 8, 2026 10:44am | Jul 8, 2026 11:19am | Jul 8, 2026 12:01pm | Jul 8, 2026 12:01pm | Jul 8, 2026 12:01pm |  |  | Fair | No | Found customer with electricity. Reading found (116-116-232).
Outage | J.E.26.07.06472 | C001842735 | Michael Christian | St.James | Completed | Load_260793 | Queens Drive - 710 | Jul 7, 2026 8:11pm | Jul 7, 2026 8:12pm | Jul 7, 2026 8:25pm | Jul 7, 2026 8:26pm | Jul 7, 2026 8:37pm | Jul 7, 2026 9:45pm | Jul 7, 2026 9:48pm | Jul 7, 2026 9:48pm |  |  | Fair | No | Found 1 15 amp out at pole # 171565 by cable men
Outage | J.E.26.07.06624 | C001842732 | Michael Christian | St.James | Completed | Load_256990 | Queens Drive - 710 | Jul 7, 2026 8:10pm | Jul 7, 2026 8:12pm | Jul 7, 2026 10:47pm | Jul 7, 2026 10:47pm | Jul 7, 2026 10:59pm | Jul 7, 2026 11:00pm | Jul 7, 2026 11:01pm | Jul 7, 2026 11:01pm |  |  | Fair | No | Reset 1 25 kava transformer cause cable wires
Outage | J.E.26.07.06732 | C001842734 | Delano Gayle | St.Catherine | Completed | Load_263862 | Rhodens Pen - 410 | Jul 7, 2026 8:10pm | Jul 8, 2026 12:04am | Jul 8, 2026 12:07am | Jul 8, 2026 12:07am | Jul 8, 2026 3:50am | Jul 8, 2026 3:51am | Jul 8, 2026 3:51am | Jul 8, 2026 3:51am | Fire |  | Fair | No | Premises not found no answer from customer phone, area patrolled and found okay
Outage | J.E.26.07.06327 | C001842730 | Eric Williams | KSAS | Completed | Load_1003139 | Hunts Bay - 410 | Jul 7, 2026 8:05pm | Jul 7, 2026 8:05pm | Jul 7, 2026 8:56pm | Jul 7, 2026 8:56pm | Jul 7, 2026 9:55pm | Jul 7, 2026 9:56pm | Jul 7, 2026 9:58pm | Jul 7, 2026 9:58pm | Fire |  | Fair | No | Premises lock customers won’t be at the location until 5am in the morning.customer request a 5am visit, urgent attention
Outage | J.E.26.07.06520 | C001842726 | Wan Carlos Scarlett | Portmore | Completed | Load_244214 | Naggo Head - 510 | Jul 7, 2026 8:04pm | Jul 8, 2026 7:13am | Jul 8, 2026 12:31pm | Jul 8, 2026 12:31pm | Jul 8, 2026 1:38pm | Jul 8, 2026 2:11pm | Jul 8, 2026 2:13pm | Jul 8, 2026 2:13pm |  |  | Fair | No | Found customer 3 wire service at pole with one of the phase broken off use one bolt clamp at open secondary line phase readings 114-116-231
Outage | J.E.26.07.06556 | C001842727 | Wan Carlos Scarlett | Portmore | Completed | Load_572625 | Naggo Head - 610 | Jul 7, 2026 8:04pm | Jul 8, 2026 7:13am | Jul 8, 2026 11:05am | Jul 8, 2026 11:06am | Jul 8, 2026 11:36am | Jul 8, 2026 12:22pm | Jul 8, 2026 12:24pm | Jul 8, 2026 12:24pm | Fire |  | Fair | No | Found customer 3 wire service at pole with bout phase corroded use 2 one bolt clamps at secondary line readings 115-114-231
Outage | J.E.26.07.06728 | C001842725 | Marlon Authors | Manchester | Completed | Load_255818 | Spur Tree - 210 | Jul 7, 2026 8:02pm | Jul 7, 2026 8:19pm | Jul 7, 2026 8:57pm | Jul 7, 2026 8:57pm | Jul 7, 2026 8:58pm | Jul 7, 2026 9:06pm | Jul 7, 2026 9:06pm | Jul 7, 2026 9:06pm |  |  | Fair | No | Supply checked and found three service wires tourn down by truck. Unable to replace same as customers pothead needs to be repaired, customers were advised to have same repaired
Outage | J.E.26.07.06711 | C001842724 | Jermaine Williams | Clarendon | Completed | Load_241598 | Parnassus - 310 | Jul 7, 2026 7:56pm | Jul 7, 2026 7:57pm | Jul 7, 2026 9:26pm | Jul 7, 2026 9:27pm | Jul 7, 2026 10:33pm | Jul 7, 2026 10:33pm | Jul 7, 2026 10:34pm | Jul 7, 2026 10:34pm | Fire |  | Fair | No | Premises not located.
Outage | J.E.26.07.06730 | C001842723 | Jermaine Williams | Clarendon | Completed | Load_246356 | Parnassus - 310 | Jul 7, 2026 7:56pm | Jul 7, 2026 7:57pm | Jul 7, 2026 8:21pm | Jul 7, 2026 8:21pm | Jul 7, 2026 9:19pm | Jul 7, 2026 9:26pm | Jul 7, 2026 9:26pm | Jul 7, 2026 9:26pm |  |  | Fair | No | Premises found ok.
Outage | J.E.26.07.06219 | C001842720 | Edward Royal | KSAN | Completed | Load_249748 | Washington Blvd - 710 | Jul 7, 2026 7:48pm | Jul 7, 2026 7:48pm | Jul 7, 2026 8:59pm | Jul 7, 2026 8:59pm | Jul 7, 2026 9:24pm | Jul 7, 2026 9:58pm | Jul 7, 2026 9:58pm | Jul 7, 2026 9:58pm |  |  | Fair | No | Replaced 20A junction fuse l
Non-Outage | J.E.26.07.06175 | C001842717 | Edward Royal | null | Completed | null | null | Jul 7, 2026 7:43pm | Jul 7, 2026 7:43pm | Jul 7, 2026 8:14pm | Jul 7, 2026 8:14pm | Jul 7, 2026 8:14pm | Jul 7, 2026 8:16pm | Jul 7, 2026 8:17pm | Jul 7, 2026 8:17pm | BrokenWire |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.07.06582 | C001842706 | Andrew Powell | Manchester | Completed | Load_249470 | Spur Tree - 210 | Jul 7, 2026 7:12pm | Jul 7, 2026 7:14pm | Jul 7, 2026 8:34pm | Jul 7, 2026 8:34pm | Jul 7, 2026 8:34pm | Jul 7, 2026 8:59pm | Jul 7, 2026 9:03pm | Jul 7, 2026 9:03pm |  |  | SevereWind | No | Clear secondary neutral from lower phase conductor. Retention two pole span of sagging neutral conductor using two preform, restore supply to normal okay.
Non-Outage | J.E.26.07.06496 | C001842695 | Swon Miller | null | Completed | null | null | Jul 7, 2026 6:47pm | Jul 7, 2026 11:30pm | Jul 8, 2026 2:01am | Jul 8, 2026 2:01am | Jul 8, 2026 2:30am | Jul 15, 2026 2:50am | Jul 8, 2026 3:02am | Jul 8, 2026 3:02am | Fire |  | Fair | No | Unable to locate customer calls to customer went unanswered
Outage | J.E.26.07.06484 | C001842694 | Michael Christian | St.James | Completed | Load_291442 | Queens Drive - 310 | Jul 7, 2026 6:46pm | Jul 7, 2026 6:47pm | Jul 7, 2026 10:21pm | Jul 7, 2026 10:21pm | Jul 7, 2026 10:39pm | Jul 7, 2026 10:43pm | Jul 7, 2026 10:43pm | Jul 7, 2026 10:43pm |  |  | Fair | No | Found 1 40 amp junction out cause by lightning replace 1 40 amp
Outage | J.E.26.07.06421 | C001842692 | Horace Malcolm | St.James | Completed | Load_259585 | Bogue - 510 | Jul 7, 2026 6:44pm | Jul 7, 2026 6:44pm | Jul 7, 2026 7:14pm | Jul 7, 2026 7:26pm | Jul 7, 2026 8:10pm | Jul 7, 2026 8:55pm | Jul 7, 2026 8:55pm | Jul 7, 2026 8:55pm |  |  | Fair | No | Refused one 100kva transformer used one 5amp fuse voltage 119-117-205-234
Outage | J.E.26.07.06602 | C001842691 | Marlon Authors | St.Elizabeth | Completed | Load_265509 | Maggotty - 210 | Jul 7, 2026 6:43pm | Jul 7, 2026 6:43pm | Jul 7, 2026 6:57pm | Jul 7, 2026 6:57pm | Jul 7, 2026 7:47pm | Jul 7, 2026 9:00pm | Jul 7, 2026 8:09pm | Jul 7, 2026 8:09pm |  |  | Fair | No | Patrol and found clear. Replace one blown 1 amp fuse that protects 15 kva transformer circuit at pole #004409. Restored supply ok
Outage | J.E.26.07.06296 | C001842690 | Shamour Haughton | St.James | Completed | Load_576009 | Bogue - 310 | Jul 7, 2026 6:42pm | Jul 7, 2026 6:43pm | Jul 7, 2026 7:14pm | Jul 7, 2026 9:37pm | Jul 7, 2026 10:11pm | Jul 7, 2026 10:28pm | Jul 7, 2026 10:31pm | Jul 7, 2026 10:31pm |  |  | Fair | No | Found 1,25amp junction fuse blown, refuse 25amp junction
Non-Outage | J.E.26.07.06622 | C001842686 | Milton Charlton | null | Completed | null | null | Jul 7, 2026 6:33pm | Jul 7, 2026 6:36pm | Jul 7, 2026 6:43pm | Jul 7, 2026 6:50pm | Jul 7, 2026 7:29pm | Jul 7, 2026 7:31pm | Jul 7, 2026 7:31pm | Jul 7, 2026 7:31pm | Fire |  | Fair | No | Disconnect 60ft #2 quaduplex service wire broken in motor vehicle accident
Non-Outage | J.E.26.07.05866 | C001842677 | Clyde Brown | Clarendon | Completed | Load_249266 | May Pen - 110 | Jul 7, 2026 6:21pm | Jul 7, 2026 6:21pm | Jul 7, 2026 6:32pm | Jul 7, 2026 6:32pm | Jul 7, 2026 7:26pm | Jul 7, 2026 8:02pm | Jul 7, 2026 8:12pm | Jul 7, 2026 8:12pm |  |  | Fair | No | Illegal connection caused phase and neutral to entangled,illegal connection removed and voltage now 112/112 and 224V
Outage | J.E.26.07.05906 | C001842678 | Shamour Haughton | St.James | Completed | Load_245091 | Bogue - 310 | Jul 7, 2026 6:21pm | Jul 7, 2026 6:22pm | Jul 7, 2026 7:35pm | Jul 7, 2026 7:36pm | Jul 7, 2026 9:27pm | Jul 7, 2026 9:27pm | Jul 7, 2026 9:34pm | Jul 7, 2026 9:34pm |  | Y | Fair | No | Found 15amp tripsaver down caused by tree limb, cut and remove tree limb from primary and reclose 15amp tripsaver
Non-Outage | J.E.26.07.00745 | C001842676 | Milton Charlton | KSAN | Completed | Load_238618 | Hope - 510 | Jul 7, 2026 6:20pm | Jul 7, 2026 6:39pm | Jul 7, 2026 6:43pm | Jul 7, 2026 8:22pm | Jul 7, 2026 9:59pm | Jul 7, 2026 10:00pm | Jul 7, 2026 10:02pm | Jul 7, 2026 10:02pm |  |  | Fair | No | Need bucket truck to check mid span connection on twisted #2/0 secondary with joint and connection on concrete pole. Unable to check concrete pole twisted secondary to open wire secondary.
Outage | J.E.26.07.06600 | C001842674 | Kaydon Taylor | KSAS | Completed | Load_264287 | Duhaney - 310 | Jul 7, 2026 6:12pm | Jul 7, 2026 6:18pm | Jul 7, 2026 6:24pm | Jul 7, 2026 6:29pm | Jul 7, 2026 7:53pm | Jul 7, 2026 8:05pm | Jul 7, 2026 8:05pm | Jul 7, 2026 8:05pm |  |  | Fair | No | After several attempts reaching out to the customer still no answer via phone call
Outage | J.E.26.07.06445 | C001842671 | Michael Christian | St.James | Completed | Load_251817 | Queens Drive - 710 | Jul 7, 2026 6:09pm | Jul 7, 2026 6:09pm | Jul 7, 2026 11:05pm | Jul 7, 2026 11:05pm | Jul 7, 2026 11:05pm | Jul 7, 2026 11:20pm | Jul 7, 2026 11:21pm | Jul 7, 2026 11:21pm |  |  | Fair | No | Premises not found
Non-Outage | J.E.26.07.05728 | C001842669 | Kaydon Taylor | KSAN | Completed | Load_258770 | Constant Spring - 410 | Jul 7, 2026 6:06pm | Jul 7, 2026 6:10pm | Jul 7, 2026 8:21pm | Jul 7, 2026 8:28pm | Jul 7, 2026 9:06pm | Jul 7, 2026 9:08pm | Jul 7, 2026 9:08pm | Jul 7, 2026 9:08pm |  |  | Fair | No | Found okay
Non-Outage | J.E.26.07.05887 | C001842667 | Kaydon Taylor | KSAS | Completed | Load_251395 | Duhaney - 310 | Jul 7, 2026 6:06pm | Jul 7, 2026 6:07pm | Jul 7, 2026 8:15pm | Jul 7, 2026 8:18pm | Jul 7, 2026 8:18pm | Jul 7, 2026 8:21pm | Jul 7, 2026 8:21pm | Jul 7, 2026 8:21pm | BrokenWire |  | Fair | No | Customer advised to come in the day time due to safety concerns.
Non-Outage | J.E.26.07.06545 | C001842663 | Kaydon Taylor | KSAN | Completed | Load_241582 | Constant Spring - 210 | Jul 7, 2026 6:04pm | Jul 7, 2026 6:07pm | Jul 7, 2026 8:09pm | Jul 7, 2026 8:11pm | Jul 7, 2026 8:11pm | Jul 7, 2026 8:14pm | Jul 7, 2026 8:14pm | Jul 7, 2026 8:14pm | BrokenWire |  | Fair | No | Found okay
Outage | J.E.26.07.06570 | C001842660 | Daniel Francis | St.Ann | Completed | Load_260906 | Ocho Rios - 410 | Jul 7, 2026 5:59pm | Jul 7, 2026 6:07pm | Jul 7, 2026 9:24pm | Jul 7, 2026 9:24pm | Jul 7, 2026 9:34pm | Jul 7, 2026 9:35pm | Jul 7, 2026 9:36pm | Jul 7, 2026 9:36pm |  |  | Fair | No | Premises lock
Outage | J.E.26.07.06492 | C001842656 | Collin Robinson | Portland | Completed | Load_241333 | Port Antonio - 410 | Jul 7, 2026 5:53pm | Jul 7, 2026 6:07pm | Jul 7, 2026 10:20pm | Jul 7, 2026 10:20pm | Jul 7, 2026 10:35pm | Jul 7, 2026 10:35pm | Jul 7, 2026 10:36pm | Jul 7, 2026 10:36pm |  |  | Rains | No | Information received from customer that supply was restored
Outage | J.E.26.07.06503 | C001842657 | Collin Robinson | Portland | Completed | Load_240240 | Port Antonio - 410 | Jul 7, 2026 5:53pm | Jul 7, 2026 6:07pm | Jul 7, 2026 7:24pm | Jul 7, 2026 7:24pm | Jul 7, 2026 8:11pm | Jul 7, 2026 8:26pm | Jul 7, 2026 8:26pm | Jul 7, 2026 8:26pm |  | Y | Fair | No | Tree contact replace 20 amps junction
Outage | J.E.26.07.06554 | C001842655 | Andrew Powell | Manchester | Completed | Load_239389 | Spur Tree - 210 | Jul 7, 2026 5:51pm | Jul 7, 2026 5:51pm | Jul 7, 2026 9:04pm | Jul 7, 2026 9:04pm | Jul 7, 2026 9:04pm | Jul 7, 2026 9:04pm | Jul 7, 2026 9:05pm | Jul 7, 2026 9:05pm |  |  | SevereWind | No | Called related to banging conductor by Goshen fault resolved supply restored.
Outage | J.E.26.07.06353 | C001842653 | Ricky Hall | St.Catherine | Completed | Load_240609 | New Michelton - 210 | Jul 7, 2026 5:49pm | Jul 7, 2026 5:49pm | Jul 7, 2026 9:23pm | Jul 7, 2026 10:02pm | Jul 7, 2026 10:43pm | Jul 7, 2026 10:45pm | Jul 7, 2026 10:45pm | Jul 7, 2026 10:45pm |  |  | Fair | No | Premises closed
Outage | J.E.26.07.06469 | C001842652 | Ricky Hall | St.Catherine | Completed | Load_250626 | New Michelton - 310 | Jul 7, 2026 5:49pm | Jul 7, 2026 5:49pm | Jul 7, 2026 7:04pm | Jul 7, 2026 7:05pm | Jul 7, 2026 7:59pm | Jul 7, 2026 9:00pm | Jul 7, 2026 9:01pm | Jul 7, 2026 9:01pm | BrokenWire |  | Fair | No | Splice and retention broken 3W service use 1 clamp
Outage | J.E.26.07.05909 | C001842651 | Rodclif Dawkins | St.Catherine | Completed | Load_246666 | Twickenham - 210 | Jul 7, 2026 5:47pm | Jul 7, 2026 5:48pm | Jul 7, 2026 6:41pm | Jul 7, 2026 7:07pm | Jul 7, 2026 7:45pm | Jul 7, 2026 8:13pm | Jul 7, 2026 8:13pm | Jul 7, 2026 8:13pm |  |  | Fair | No | Customer has internal issues
Outage | J.E.26.07.06550 | C001842650 | Selvin White | St.Elizabeth | Completed | Load_248325 | Maggotty - 110 | Jul 7, 2026 5:45pm | Jul 7, 2026 5:45pm | Jul 7, 2026 5:53pm | Jul 7, 2026 5:58pm | Jul 7, 2026 6:30pm | Jul 7, 2026 7:03pm | Jul 7, 2026 7:03pm | Jul 7, 2026 7:03pm |  |  | Fair | No | Customer was contacted and said premises is currently damaged from Hurricane Mellisa and quoted in use but they are still being billed. Please refer to the field service department, Simone Bicarie and C Johnson so premises can be visit by the field service technician.
Outage | J.E.26.07.04875 | C001842647 | Lancelot Brown | Hanover | Completed | Load_269526 | Orange Bay - 310 | Jul 7, 2026 5:39pm | Jul 7, 2026 5:40pm | Jul 7, 2026 10:45pm | Jul 7, 2026 10:46pm | Jul 7, 2026 10:46pm | Jul 7, 2026 10:49pm | Jul 7, 2026 10:49pm | Jul 7, 2026 10:49pm |  |  | Fair | No | Customer said he is not coming out in the night to give proper direction
Outage | J.E.26.07.05742 | C001842644 | Lancelot Brown | Hanover | Completed | Load_255356 | Orange Bay - 210 | Jul 7, 2026 5:39pm | Jul 7, 2026 5:40pm | Jul 7, 2026 6:15pm | Jul 7, 2026 6:15pm | Jul 7, 2026 7:39pm | Jul 7, 2026 8:13pm | Jul 7, 2026 8:13pm | Jul 7, 2026 8:13pm |  |  | Fair | No | Check and found ok voltage leave at pothead on customer copper side 110-110-220 cannot check voltage at meter point meter has a locking bond also this call is for westmoreland crew carry out checks
Outage | J.E.26.07.06511 | C001842640 | Neckell Ormsby | St.Mary | Completed | Load_257358 | Highgate -110 | Jul 7, 2026 5:39pm | Jul 7, 2026 5:40pm | Jul 7, 2026 8:41pm | Jul 7, 2026 8:41pm | Jul 7, 2026 8:41pm | Jul 7, 2026 8:41pm | Jul 7, 2026 8:41pm | Jul 7, 2026 8:41pm |  |  | Fair | No | Found 40 amp trip saver operated new pole # seen, patrol and found several bamboo’s on primary caused by bush fire we had to wait until fire department reduce fire to cut and remove bamboo’s from primary and reset tripsaver new pole # seen
Outage | J.E.26.07.06517 | C001842641 | Neckell Ormsby | St.Mary | Completed | Load_238782 | Highgate -110 | Jul 7, 2026 5:39pm | Jul 7, 2026 5:40pm | Jul 7, 2026 6:24pm | Jul 7, 2026 6:24pm | Jul 7, 2026 7:00pm | Jul 7, 2026 8:22pm | Jul 7, 2026 8:25pm | Jul 7, 2026 8:25pm |  |  | Fair | No | Found 40 amp trip saver operated new pole # seen, patrol and found several bamboo’s on primary caused by bush fire we had to wait until fire department reduce fire to cut and remove bamboo’s from primary and reset tripsaver new pole # seen
Outage | J.E.26.07.06543 | C001842643 | Neckell Ormsby | St.Mary | Completed | Load_268627 | Highgate -110 | Jul 7, 2026 5:39pm | Jul 7, 2026 5:40pm | Jul 7, 2026 8:39pm | Jul 7, 2026 8:39pm | Jul 7, 2026 8:39pm | Jul 7, 2026 8:39pm | Jul 7, 2026 8:40pm | Jul 7, 2026 8:40pm |  |  | Fair | No | Found 40 amp trip saver operated new pole # seen, patrol and found several bamboo’s on primary caused by bush fire we had to wait until fire department reduce fire to cut and remove bamboo’s from primary and reset tripsaver new pole # seen
Outage | J.E.26.07.06505 | C001842639 | Neckell Ormsby | St.Mary | Completed | Load_267726 | Highgate -110 | Jul 7, 2026 5:38pm | Jul 7, 2026 5:40pm | Jul 7, 2026 8:25pm | Jul 7, 2026 8:25pm | Jul 7, 2026 8:25pm | Jul 7, 2026 8:27pm | Jul 7, 2026 8:27pm | Jul 7, 2026 8:27pm |  |  | Fair | No | Found 40 amp trip saver operated new pole # seen, patrol and found several bamboo’s on primary caused by bush fire we had to wait until fire department reduce fire to cut and remove bamboo’s from primary and reset tripsaver new pole # seen
Outage | J.E.26.07.05891 | C001842638 | Edward Royal | KSAS | Completed | Load_266520 | Rockfort - 210 | Jul 7, 2026 5:36pm | Jul 7, 2026 5:36pm | Jul 7, 2026 8:10pm | Jul 7, 2026 8:10pm | Jul 7, 2026 8:10pm | Jul 7, 2026 8:10pm | Jul 7, 2026 8:10pm | Jul 7, 2026 8:10pm | BrokenWire |  | Fair | No | Premises found ok
Outage | J.E.26.07.05689 | C001842634 | Edward Royal | KSAS | Completed | Load_237939 | Hunts Bay - 310 | Jul 7, 2026 5:32pm | Jul 7, 2026 5:33pm | Jul 7, 2026 6:18pm | Jul 7, 2026 6:18pm | Jul 7, 2026 6:18pm | Jul 7, 2026 6:54pm | Jul 7, 2026 6:54pm | Jul 7, 2026 6:54pm |  |  | Fair | No | Spliced and reconnected primary jumper to switch
Outage | J.E.26.07.05745 | C001842632 | Edward Royal | KSAS | Completed | Load_300858 | Cane River - 410 | Jul 7, 2026 5:32pm | Jul 7, 2026 5:33pm | Jul 7, 2026 8:11pm | Jul 7, 2026 8:11pm | Jul 7, 2026 8:11pm | Jul 7, 2026 8:11pm | Jul 7, 2026 8:11pm | Jul 7, 2026 8:11pm | BrokenWire |  | Fair | No | Premises not found unable to communicate with customer
Outage | J.E.26.07.05770 | C001842633 | Edward Royal | KSAS | Completed | Load_267677 | Hunts Bay - 810 | Jul 7, 2026 5:32pm | Jul 7, 2026 5:33pm | Jul 7, 2026 5:41pm | Jul 7, 2026 5:41pm | Jul 7, 2026 5:41pm | Jul 7, 2026 5:42pm | Jul 7, 2026 5:42pm | Jul 7, 2026 5:42pm | Fire |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.07.05642 | C001842631 | Edward Royal | KSAS | Completed | Load_266654 | Hunts Bay - 510 | Jul 7, 2026 5:31pm | Jul 7, 2026 5:33pm | Jul 7, 2026 7:24pm | Jul 7, 2026 7:24pm | Jul 7, 2026 7:24pm | Jul 7, 2026 7:29pm | Jul 7, 2026 7:29pm | Jul 7, 2026 7:29pm | BrokenWire |  | Fair | No | Premises found with supply no broken wire was found unable to communicate with customer
Outage | J.E.26.07.06337 | C001842628 | Dwayne Samuels | Trelawny | Completed | Load_294629 | Greenwood - 110 | Jul 7, 2026 5:26pm | Jul 7, 2026 8:04pm | Jul 7, 2026 8:13pm | Jul 7, 2026 8:13pm | Jul 7, 2026 9:27pm | Jul 7, 2026 9:45pm | Jul 7, 2026 9:47pm | Jul 7, 2026 9:47pm | BrokenWire |  | Fair | No | Unable to locate customer premises and unable to reach customer on cellphone voicemail
Non-Outage | J.E.26.07.04431 | C001842625 | Eric Williams | KSAN | Completed | Load_293845 | Washington Blvd - 710 | Jul 7, 2026 5:23pm | Jul 7, 2026 5:31pm | Jul 7, 2026 7:23pm | Jul 7, 2026 7:23pm | Jul 7, 2026 7:48pm | Jul 7, 2026 8:50pm | Jul 7, 2026 8:56pm | Jul 7, 2026 8:56pm |  |  | Fair | No | 3 wire service burnt joint a ypp and corroded joint, wire cut and splice, voltage readings left 119,119,238volts
Outage | J.E.26.07.05604 | C001842618 | Daniel Francis | St.Ann | Completed | Load_240910 | Roaring River - 210 | Jul 7, 2026 5:12pm | Jul 7, 2026 5:17pm | Jul 7, 2026 6:03pm | Jul 7, 2026 6:04pm | Jul 7, 2026 6:53pm | Jul 7, 2026 6:53pm | Jul 7, 2026 6:55pm | Jul 7, 2026 6:55pm |  |  | Fair | No | Found 15kva transformer fuse blown renew 2amp pole #0180937
Outage | J.E.26.07.06002 | C001842616 | Daniel Francis | St.Ann | Completed | Load_256734 | Upper White River - 110 | Jul 7, 2026 5:11pm | Jul 7, 2026 5:17pm | Jul 7, 2026 9:36pm | Jul 7, 2026 9:36pm | Jul 7, 2026 10:06pm | Jul 7, 2026 10:14pm | Jul 7, 2026 10:21pm | Jul 7, 2026 10:21pm |  |  | Fair | No | Change one, one bolt clamp
Outage | J.E.26.07.06491 | C001842615 | Cliton Henry | St.Mary | Completed | Load_251609 | Oracabessa - 210 | Jul 7, 2026 5:10pm | Jul 7, 2026 5:14pm | Jul 7, 2026 5:21pm | Jul 7, 2026 5:21pm | Jul 7, 2026 5:21pm | Jul 7, 2026 6:35pm | Jul 7, 2026 6:42pm | Jul 7, 2026 6:42pm | BrokenWire |  | Fair | No | A blown 5 amp fuse found for a 50 kva transformer at pole number 0013676 due a tree fell on the secondary line by workmen clearing property. Corrective work done to carryout spot bushing, string and tension secondary phase conductor using approximately 10 feet 2/0 AA conductor,4 2/0 preform, 2 #2 preform and 4 one bolt clamps. Supply restored using 1- 5 amp fuse.
Outage | J.E.26.07.05351 | C001842608 | Denton Williams | Portland | Completed | Load_249141 | Port Antonio - 310 | Jul 7, 2026 5:01pm | Jul 7, 2026 5:14pm | Jul 7, 2026 5:17pm | Jul 7, 2026 5:17pm | Jul 7, 2026 5:17pm | Jul 7, 2026 6:51pm | Jul 7, 2026 6:55pm | Jul 7, 2026 6:55pm |  |  | Fair | No | Replace defective 25kva transformer. New 25kva transformer no. ER01120. Voltage readings at transformer drop leads 120v, 120v & 241, amps readings 18amps, 23amps and neutral 12amps.
Non-Outage | J.E.26.07.05699 | C001842601 | Marlon Authors | Manchester | Completed | Load_261681 | Spur Tree - 210 | Jul 7, 2026 4:56pm | Jul 7, 2026 6:01pm | Jul 8, 2026 8:54am | Jul 8, 2026 8:54am | Jul 8, 2026 9:22am | Jul 8, 2026 9:31am | Jul 8, 2026 9:31am | Jul 8, 2026 9:31am |  |  | Fair | No | Supply checked and found working ok rdg 109v,109v and cross phased 218 volts
Non-Outage | J.E.26.07.05972 | C001842602 | Marlon Authors | Manchester | Completed | Load_556490 | Spur Tree - 210 | Jul 7, 2026 4:56pm | Jul 7, 2026 6:00pm | Jul 8, 2026 9:34am | Jul 8, 2026 9:34am | Jul 8, 2026 10:08am | Jul 8, 2026 11:44am | Jul 8, 2026 11:44am | Jul 8, 2026 11:44am |  |  | Fair | No | Supply checked and found low voltage rdg 105v,105v and cross phased 210 volts. Isolate and close 25 kva transformer circuit to tap up transformer to tap 5. Supply leave working ok rgd 110v,110v and cross phased 221 volts
Non-Outage | J.E.26.07.05982 | C001842600 | Andrew Powell | null | Completed | null | null | Jul 7, 2026 4:56pm | Jul 7, 2026 4:57pm | Jul 7, 2026 5:47pm | Jul 7, 2026 5:47pm | Jul 7, 2026 6:51pm | Jul 7, 2026 7:06pm | Jul 7, 2026 7:07pm | Jul 7, 2026 7:07pm | Fire |  | SevereWind | No | Clear telephone strand from secondary lower phase conductor.
Outage | J.E.26.07.06446 | C001842599 | Richman Whyte | Westmoreland | Completed | Load_259377 | Paradise - 310 | Jul 7, 2026 4:55pm | Jul 7, 2026 4:55pm | Jul 7, 2026 5:30pm | Jul 7, 2026 5:30pm | Jul 7, 2026 6:31pm | Jul 7, 2026 7:23pm | Jul 7, 2026 7:28pm | Jul 7, 2026 7:28pm |  |  | Rains | No | Replace two twenty amp junction fuse
Outage | J.E.26.07.06458 | C001842598 | Oshane Warren | Westmoreland | Completed | Load_253108 | Paradise - 210 | Jul 7, 2026 4:55pm | Jul 7, 2026 4:55pm | Jul 7, 2026 5:55pm | Jul 7, 2026 5:55pm | Jul 7, 2026 6:56pm | Jul 7, 2026 7:00pm | Jul 7, 2026 7:01pm | Jul 7, 2026 7:01pm |  |  | Fair | No | Defective meter refe to field service
Outage | J.E.26.07.06405 | C001842583 | Roxroy Needham | St.Ann | Completed | Load_242214 | Cardiff Hall - 210 | Jul 7, 2026 4:46pm | Jul 7, 2026 4:57pm | Jul 7, 2026 5:39pm | Jul 7, 2026 5:39pm | Jul 7, 2026 6:14pm | Jul 7, 2026 6:15pm | Jul 7, 2026 6:18pm | Jul 7, 2026 6:18pm |  |  | Fair | No | Replace 1- 25 amp junction fuse after line was patrol
Outage | J.E.26.07.06428 | C001842575 | Cliton Henry | St.Mary | Completed | Load_238300 | Oracabessa - 110 | Jul 7, 2026 4:43pm | Jul 7, 2026 5:42pm | Jul 7, 2026 8:12pm | Jul 7, 2026 8:12pm | Jul 7, 2026 8:18pm | Jul 7, 2026 8:23pm | Jul 7, 2026 8:23pm | Jul 7, 2026 8:23pm | BrokenPole |  | Fair | No | A broken pole found 40-c4 with secondary conductors only. kindly refer to St. Mary Operations for a replacement. NB. Referred several times no replacement done.
Outage | J.E.26.07.06433 | C001842574 | Cliton Henry | St.Mary | Completed | Load_576544 | Oracabessa - 110 | Jul 7, 2026 4:42pm | Jul 7, 2026 5:42pm | Jul 7, 2026 6:51pm | Jul 7, 2026 6:51pm | Jul 7, 2026 7:35pm | Jul 7, 2026 8:00pm | Jul 7, 2026 8:09pm | Jul 7, 2026 8:09pm |  |  | Fair | No | A slack joint found at the drop lead for a 25 kva transformer at pole #0013185. The transformer was de energized to carryout repairs. Corrective work done to reconnected the transformer drop lead using 2- one bolt clamps. Supply restored to energized the 25 kva transformer.
Outage | J.E.26.07.06450 | C001842573 | Roxroy Needham | St.Ann | Completed | Load_248321 | Cardiff Hall - 310 | Jul 7, 2026 4:42pm | Jul 7, 2026 4:58pm | Jul 7, 2026 6:18pm | Jul 7, 2026 6:18pm | Jul 7, 2026 7:11pm | Jul 7, 2026 7:14pm | Jul 7, 2026 7:14pm | Jul 7, 2026 7:14pm |  |  | Fair | No | Remove kite from line and replace 1- 25 amp junction fuse
Outage | J.E.26.07.06062 | C001842566 | Jermaine Williams | Clarendon | Completed | Load_263640 | Parnassus - 310 | Jul 7, 2026 4:30pm | Jul 7, 2026 4:30pm | Jul 7, 2026 5:51pm | Jul 7, 2026 5:51pm | Jul 7, 2026 6:36pm | Jul 7, 2026 6:40pm | Jul 7, 2026 6:41pm | Jul 7, 2026 6:41pm | Fire |  | SevereWind | No | Splice and retention broken service wire using 10’ #6 triplex.
Outage | J.E.26.07.06213 | C001842567 | Jermaine Williams | Clarendon | Completed | Load_263805 | Parnassus - 310 | Jul 7, 2026 4:30pm | Jul 7, 2026 4:30pm | Jul 7, 2026 5:04pm | Jul 7, 2026 5:04pm | Jul 7, 2026 5:30pm | Jul 7, 2026 5:54pm | Jul 7, 2026 5:51pm | Jul 7, 2026 5:51pm | Fire |  | SevereWind | No | Isolate 25kva xfmr to splice and retention three spans broken secondary neutral conductors using two sleeves, 50’ #2aaa and three clamps.
Outage | J.E.26.07.06221 | C001842565 | Michael Christian | St.James | Completed | Load_575863 | Bogue - 410 | Jul 7, 2026 4:30pm | Jul 7, 2026 4:30pm | Jul 7, 2026 11:04pm | Jul 7, 2026 11:04pm | Jul 7, 2026 11:04pm | Jul 7, 2026 11:04pm | Jul 7, 2026 11:05pm | Jul 7, 2026 11:05pm |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.06393 | C001842564 | Michael Christian | St.James | Completed | Load_248983 | Bogue - 310 | Jul 7, 2026 4:30pm | Jul 7, 2026 4:30pm | Jul 7, 2026 11:01pm | Jul 7, 2026 11:01pm | Jul 7, 2026 11:01pm | Jul 7, 2026 11:03pm | Jul 7, 2026 11:04pm | Jul 7, 2026 11:04pm |  |  | Fair | No | Banging wires causes fire open 1 25 kava to work
Outage | J.E.26.07.05802 | C001842561 | Jermaine Williams | Clarendon | Completed | Load_268788 | Monymusk - 210 | Jul 7, 2026 4:29pm | Jul 7, 2026 4:29pm | Jul 7, 2026 6:41pm | Jul 7, 2026 6:41pm | Jul 7, 2026 7:25pm | Jul 7, 2026 7:25pm | Jul 7, 2026 7:27pm | Jul 7, 2026 7:27pm |  |  | SevereWind | No | Patrol and replaced two blown 25amp junction fuse.
Outage | J.E.26.07.05763 | C001842560 | Rodclif Dawkins | KSAS | Completed | Load_288269 | Duhaney - 210 | Jul 7, 2026 4:27pm | Jul 7, 2026 4:29pm | Jul 7, 2026 6:09pm | Jul 7, 2026 6:09pm | Jul 7, 2026 6:23pm | Jul 7, 2026 6:23pm | Jul 7, 2026 6:34pm | Jul 7, 2026 6:34pm |  |  | Fair | No | On location crew found sealed meter. Seal cut , on inspection crew observed burning on plastic of meter terminal on left load side. Meter was checked with volt meter, to determine all contacts closed. Meter placed back in socket. Customer okay. However customer was advised to have electrician replace the other slack meter socket terminal. As to not have the issue re occur.
Outage | J.E.26.07.05837 | C001842559 | Rodclif Dawkins | St.Catherine | Completed | Load_569977 | Twickenham - 210 | Jul 7, 2026 4:27pm | Jul 7, 2026 4:29pm | Jul 7, 2026 8:14pm | Jul 7, 2026 8:14pm | Jul 7, 2026 9:32pm | Jul 7, 2026 10:16pm | Jul 7, 2026 10:16pm | Jul 7, 2026 10:16pm |  |  | Fair | No | At times of visit crew found customer with customer with supply. Customer advise crew that situation was resolved earlier today.
Outage | J.E.26.07.06190 | C001842558 | Rodclif Dawkins | St.Catherine | Completed | Load_245608 | Twickenham - 210 | Jul 7, 2026 4:27pm | Jul 7, 2026 4:29pm | Jul 7, 2026 6:37pm | Jul 7, 2026 6:37pm | Jul 7, 2026 6:37pm | Jul 7, 2026 6:38pm | Jul 7, 2026 6:38pm | Jul 7, 2026 6:38pm |  |  | Fair | No | Please refer to Moses customer unable to top up
Outage | J.E.26.07.06346 | C001842557 | Rodclif Dawkins | KSAS | Completed | Load_405457 | Duhaney - 210 | Jul 7, 2026 4:27pm | Jul 7, 2026 4:29pm | Jul 7, 2026 5:15pm | Jul 7, 2026 5:15pm | Jul 7, 2026 5:36pm | Jul 7, 2026 6:05pm | Jul 7, 2026 6:09pm | Jul 7, 2026 6:09pm |  |  | Fair | No | Found blown fuse for 100kva transformer in bank of 3 100kva interphase transformer. No faults were observed at time. Found and replaced 15amp .
Outage | J.E.26.07.06379 | C001842535 | Eric Williams | KSAN | Completed | Load_245669 | Constant Spring - 210 | Jul 7, 2026 4:14pm | Jul 7, 2026 4:17pm | Jul 7, 2026 4:54pm | Jul 7, 2026 4:54pm | Jul 7, 2026 6:05pm | Jul 7, 2026 7:23pm | Jul 7, 2026 7:23pm | Jul 7, 2026 7:23pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.06207 | C001842534 | Kaydon Taylor | KSAN | Completed | Load_241758 | Constant Spring - 310 | Jul 7, 2026 4:13pm | Jul 7, 2026 4:18pm | Jul 7, 2026 5:54pm | Jul 7, 2026 5:56pm | Jul 7, 2026 5:56pm | Jul 7, 2026 5:57pm | Jul 7, 2026 5:57pm | Jul 7, 2026 5:57pm |  |  | Fair | No | Found okay
Outage | J.E.26.07.06180 | C001842529 | Shamour Haughton | St.James | Completed | Load_268772 | Bogue - 310 | Jul 7, 2026 4:00pm | Jul 7, 2026 4:01pm | Jul 7, 2026 9:36pm | Jul 7, 2026 9:36pm | Jul 7, 2026 9:36pm | Jul 7, 2026 9:36pm | Jul 7, 2026 9:37pm | Jul 7, 2026 9:37pm | BrokenWire |  | Fair | No | Related to previous call
Outage | J.E.26.07.06313 | C001842528 | Shamour Haughton | St.James | Completed | Load_256318 | Bogue - 310 | Jul 7, 2026 4:00pm | Jul 7, 2026 4:01pm | Jul 7, 2026 9:35pm | Jul 7, 2026 9:35pm | Jul 7, 2026 9:35pm | Jul 7, 2026 9:35pm | Jul 7, 2026 9:35pm | Jul 7, 2026 9:35pm | BrokenWire |  | Fair | No | Related to previous call
Non-Outage | J.E.26.07.05811 | C001842523 | Daniel Francis | St.Ann | Completed | Load_240922 | Upper White River - 210 | Jul 7, 2026 3:57pm | Jul 7, 2026 3:58pm | Jul 7, 2026 10:24pm | Jul 7, 2026 10:24pm | Jul 7, 2026 10:42pm | Jul 7, 2026 10:42pm | Jul 7, 2026 10:50pm | Jul 7, 2026 10:50pm | BrokenWire |  | Fair | No | Not found customer not answering phone
Outage | J.E.26.07.05921 | C001842522 | Shamour Haughton | St.James | Completed | Load_292555 | Bogue - 310 | Jul 7, 2026 3:55pm | Jul 7, 2026 3:55pm | Jul 7, 2026 4:48pm | Jul 7, 2026 4:48pm | Jul 7, 2026 4:48pm | Jul 7, 2026 7:08pm | Jul 7, 2026 7:11pm | Jul 7, 2026 7:11pm |  |  | Fair | No | Found 2, 65amp tripsaver down, reclose 65amp tripsaver at pole number 057819
Non-Outage | J.E.26.07.05458 | C001842516 | Daniel Francis | null | Completed | null | null | Jul 7, 2026 3:51pm | Jul 7, 2026 3:52pm | Jul 7, 2026 6:01pm | Jul 7, 2026 6:01pm | Jul 7, 2026 6:01pm | Jul 7, 2026 6:02pm | Jul 7, 2026 6:02pm | Jul 7, 2026 6:02pm |  |  | Fair | No | Power restored
Outage | J.E.26.07.05678 | C001842518 | Daniel Francis | St.Ann | Completed | Load_242723 | Roaring River - 210 | Jul 7, 2026 3:51pm | Jul 7, 2026 3:51pm | Jul 7, 2026 6:57pm | Jul 7, 2026 6:57pm | Jul 7, 2026 7:27pm | Jul 7, 2026 8:40pm | Jul 7, 2026 8:43pm | Jul 7, 2026 8:43pm |  |  | Fair | No | found 25kva drops lead clamp burnt out at pole#0012793
Outage | J.E.26.07.05682 | C001842517 | Daniel Francis | St.Ann | Completed | Load_1000252 | Roaring River - 410 | Jul 7, 2026 3:51pm | Jul 7, 2026 3:51pm | Jul 7, 2026 5:01pm | Jul 7, 2026 5:01pm | Jul 7, 2026 5:01pm | Jul 7, 2026 5:02pm | Jul 7, 2026 5:03pm | Jul 7, 2026 5:03pm | BangingWires |  | Fair | No | Internal fault not jps
Outage | J.E.26.07.05747 | C001842515 | Daniel Francis | null | Completed | Load_268042 | Ocho Rios - 310 | Jul 7, 2026 3:51pm | Jul 7, 2026 3:52pm | Jul 7, 2026 5:06pm | Jul 7, 2026 5:06pm | Jul 7, 2026 5:47pm | Jul 7, 2026 5:55pm | Jul 7, 2026 5:58pm | Jul 7, 2026 5:58pm |  |  | Fair | No | Power restored
Outage | J.E.26.07.06031 | C001842514 | Daniel Francis | St.Ann | Completed | Load_238582 | Ocho Rios - 310 | Jul 7, 2026 3:50pm | Jul 7, 2026 3:51pm | Jul 7, 2026 8:44pm | Jul 7, 2026 8:44pm | Jul 7, 2026 9:21pm | Jul 7, 2026 9:21pm | Jul 7, 2026 9:24pm | Jul 7, 2026 9:24pm | BrokenWire |  | Fair | No | Customer. need tocarry out repair to pothead
Outage | J.E.26.07.05851 | C001842507 | Donald Cunningham | St.Catherine | Completed | Load_254532 | Tredegar - 210 | Jul 7, 2026 3:49pm | Jul 7, 2026 3:49pm | Jul 7, 2026 3:52pm | Jul 7, 2026 3:52pm | Jul 7, 2026 4:55pm | Jul 7, 2026 5:19pm | Jul 7, 2026 5:19pm | Jul 7, 2026 5:19pm |  |  | Fair | No | Premises found ok with supply
Outage | J.E.26.07.06333 | C001842509 | Roxroy Needham | St.Ann | Completed | Load_258300 | Cardiff Hall - 310 | Jul 7, 2026 3:49pm | Jul 7, 2026 3:50pm | Jul 7, 2026 7:15pm | Jul 7, 2026 7:15pm | Jul 7, 2026 7:45pm | Jul 7, 2026 7:49pm | Jul 7, 2026 7:50pm | Jul 7, 2026 7:50pm | BrokenWire |  | Fair | No | Reconnect customer at pole used 3- 1bolt clamps voltage reading left 112,113,225
Non-Outage | J.E.26.07.05786 | C001842506 | Stephen Taylor | St.Thomas | Completed | Load_269505 | Lysson - 410 | Jul 7, 2026 3:47pm | Jul 7, 2026 3:48pm | Jul 7, 2026 6:32pm | Jul 7, 2026 6:32pm | Jul 7, 2026 7:57pm | Jul 7, 2026 7:58pm | Jul 7, 2026 8:37pm | Jul 7, 2026 8:37pm |  |  | Fair | No | Clean up transformer lead an close up 25kva transformer customer is now back in service
Non-Outage | J.E.26.07.05897 | C001842500 | Dwayne Samuels | Trelawny | Completed | Load_292776 | Greenwood - 210 | Jul 7, 2026 3:39pm | Jul 7, 2026 3:39pm | Jul 7, 2026 4:06pm | Jul 7, 2026 4:14pm | Jul 7, 2026 5:04pm | Jul 7, 2026 6:21pm | Jul 7, 2026 6:22pm | Jul 7, 2026 6:22pm |  |  | Fair | No | Check and found voltage at customer pothead on arrival 104v/110v/214v after further investigation illegal connections in area is the cause of customer low voltage after removing some of the illegal connections voltage left at customer pothead 106/111/217 refer to losses team for further checks
Outage | J.E.26.07.06307 | C001842497 | Selvin White | St.Elizabeth | Completed | Load_261138 | Maggotty - 110 | Jul 7, 2026 3:39pm | Jul 7, 2026 3:39pm | Jul 7, 2026 3:57pm | Jul 7, 2026 4:15pm | Jul 7, 2026 4:41pm | Jul 7, 2026 4:58pm | Jul 7, 2026 4:58pm | Jul 7, 2026 4:58pm |  |  | Fair | No | Replace a fuse holder along with a 1.5 amp fuse for a 10 KVA transformer that supply 2 customers. Supply restored. Voltage readings left inside customer’s meter socket are 223,112,111 volts.
Outage | J.E.26.07.05662 | C001842494 | Roxroy Needham | St.Ann | Completed | Load_256510 | Cardiff Hall - 210 | Jul 7, 2026 3:38pm | Jul 7, 2026 3:49pm | Jul 7, 2026 4:39pm | Jul 7, 2026 4:39pm | Jul 7, 2026 5:13pm | Jul 7, 2026 5:14pm | Jul 7, 2026 5:19pm | Jul 7, 2026 5:19pm |  |  | Fair | No | Clean and remake joints at pole used 2- 1bolt clamps voltage readings left 112,114,226
Outage | J.E.26.07.06041 | C001842495 | Roxroy Needham | St.Ann | Completed | Load_269168 | Cardiff Hall - 210 | Jul 7, 2026 3:38pm | Jul 7, 2026 3:48pm | Jul 7, 2026 7:50pm | Jul 7, 2026 7:50pm | Jul 7, 2026 7:50pm | Jul 7, 2026 7:51pm | Jul 7, 2026 7:51pm | Jul 7, 2026 7:51pm |  |  | Fair | No | Customer issue was resolved
Non-Outage | J.E.26.07.05633 | C001842493 | Ricky Hall | null | Completed | null | null | Jul 7, 2026 3:37pm | Jul 7, 2026 3:38pm | Jul 7, 2026 3:47pm | Jul 7, 2026 3:47pm | Jul 7, 2026 6:35pm | Jul 7, 2026 7:03pm | Jul 7, 2026 7:04pm | Jul 7, 2026 7:04pm | Fire |  | SevereWind | No | Conduct spot bushing replaced blown 2 amps fuse 10 kva xfmr
Non-Outage | J.E.26.07.05754 | C001842492 | Collin Robinson | Portland | Completed | Load_249469 | Port Antonio - 410 | Jul 7, 2026 3:37pm | Jul 7, 2026 4:22pm | Jul 7, 2026 8:26pm | Jul 7, 2026 8:26pm | Jul 7, 2026 9:29pm | Jul 7, 2026 9:30pm | Jul 7, 2026 9:30pm | Jul 7, 2026 9:30pm |  |  | Fair | No | Area found with supply
Outage | J.E.26.07.06019 | C001842488 | Horace Malcolm | St.James | Completed | Load_292378 | Bogue - 510 | Jul 7, 2026 3:36pm | Jul 7, 2026 3:36pm | Jul 7, 2026 3:45pm | Jul 7, 2026 3:45pm | Jul 7, 2026 4:04pm | Jul 7, 2026 4:37pm | Jul 7, 2026 4:37pm | Jul 7, 2026 4:37pm |  |  | Fair | No | Refused one 50amp and one 40amp junction fuse
Outage | J.E.26.07.06023 | C001842489 | Collin Robinson | Portland | Completed | Load_245474 | Port Antonio - 410 | Jul 7, 2026 3:36pm | Jul 7, 2026 4:22pm | Jul 7, 2026 4:54pm | Jul 7, 2026 4:54pm | Jul 7, 2026 6:18pm | Jul 7, 2026 7:20pm | Jul 7, 2026 7:20pm | Jul 7, 2026 7:20pm |  |  | Flood | No | Remove rotten tree from both primary phase and neutral conductor And replace 10 amps junction
Outage | J.E.26.07.06299 | C001842487 | Richard Samuda | Manchester | Completed | Load_237730 | Spur Tree - 310 | Jul 7, 2026 3:36pm | Jul 7, 2026 3:38pm | Jul 7, 2026 3:49pm | Jul 7, 2026 3:49pm | Jul 7, 2026 4:03pm | Jul 7, 2026 4:03pm | Jul 7, 2026 4:07pm | Jul 7, 2026 4:07pm |  |  | Fair | No | Customer is on a rami system and her breaker was tripped but with the help of the escalation customer is no back to normal
Outage | J.E.26.07.06205 | C001842485 | Cliton Henry | St.Mary | Completed | Load_261553 | Blackstonedge - 110 | Jul 7, 2026 3:35pm | Jul 7, 2026 3:36pm | Jul 7, 2026 8:29pm | Jul 7, 2026 8:30pm | Jul 7, 2026 8:30pm | Jul 7, 2026 8:30pm | Jul 7, 2026 8:31pm | Jul 7, 2026 8:31pm |  |  | Fair | No | Supply restored, related to feeder outage at Blackstonedge
Outage | J.E.26.07.06218 | C001842484 | Cliton Henry | St.Mary | Completed | Load_258854 | Blackstonedge - 110 | Jul 7, 2026 3:35pm | Jul 7, 2026 3:36pm | Jul 7, 2026 8:31pm | Jul 7, 2026 8:31pm | Jul 7, 2026 8:31pm | Jul 7, 2026 8:32pm | Jul 7, 2026 8:32pm | Jul 7, 2026 8:32pm |  |  | Fair | No | Supply restored, related to feeder outage Blackstonedge
Outage | J.E.26.07.06251 | C001842486 | Cliton Henry | St.Mary | Completed | Load_266316 | Oracabessa - 210 | Jul 7, 2026 3:35pm | Jul 7, 2026 3:36pm | Jul 7, 2026 3:44pm | Jul 7, 2026 3:45pm | Jul 7, 2026 4:37pm | Jul 7, 2026 4:57pm | Jul 7, 2026 5:00pm | Jul 7, 2026 5:00pm | Fire |  | Fair | No | A secondary neutral conductor found making contact when the wind blows was retention using 1-#2 preform.
Outage | J.E.26.07.06254 | C001842483 | Cliton Henry | St.Mary | Completed | Load_352949 | Blackstonedge - 110 | Jul 7, 2026 3:35pm | Jul 7, 2026 3:36pm | Jul 7, 2026 8:32pm | Jul 7, 2026 8:32pm | Jul 7, 2026 8:32pm | Jul 7, 2026 8:33pm | Jul 7, 2026 8:33pm | Jul 7, 2026 8:33pm |  |  | Fair | No | Supply restored, related to feeder outage Blackstonedge
Outage | J.E.26.07.06263 | C001842480 | Cliton Henry | St.Mary | Completed | Load_265477 | Blackstonedge - 110 | Jul 7, 2026 3:35pm | Jul 7, 2026 3:36pm | Jul 7, 2026 8:36pm | Jul 7, 2026 8:36pm | Jul 7, 2026 8:36pm | Jul 7, 2026 8:36pm | Jul 7, 2026 8:37pm | Jul 7, 2026 8:37pm |  |  | Fair | No | Supply restored, related to feeder outage Blackstonedge
Outage | J.E.26.07.06270 | C001842482 | Cliton Henry | St.Mary | Completed | Load_260154 | Blackstonedge - 110 | Jul 7, 2026 3:35pm | Jul 7, 2026 3:36pm | Jul 7, 2026 8:33pm | Jul 7, 2026 8:33pm | Jul 7, 2026 8:33pm | Jul 7, 2026 8:34pm | Jul 7, 2026 8:34pm | Jul 7, 2026 8:34pm |  |  | Fair | No | Supply restored, related to feeder outage Blackstonedge
Outage | J.E.26.07.06273 | C001842481 | Cliton Henry | St.Mary | Completed | Load_247343 | Blackstonedge - 110 | Jul 7, 2026 3:35pm | Jul 7, 2026 3:36pm | Jul 7, 2026 8:35pm | Jul 7, 2026 8:35pm | Jul 7, 2026 8:35pm | Jul 7, 2026 8:35pm | Jul 7, 2026 8:35pm | Jul 7, 2026 8:35pm |  |  | Fair | No | Supply restored, related to feeder outage Blackstonedge
Outage | J.E.26.07.06198 | C001842472 | Romaine Roberts | St.Mary | Completed | Load_261325 | Blackstonedge - 110 | Jul 7, 2026 3:34pm | Jul 7, 2026 3:34pm | Jul 7, 2026 9:12pm | Jul 7, 2026 9:12pm | Jul 7, 2026 9:12pm | Jul 7, 2026 9:13pm | Jul 7, 2026 9:13pm | Jul 7, 2026 9:13pm |  |  | Fair | No
Outage | J.E.26.07.06201 | C001842473 | Romaine Roberts | St.Mary | Completed | Load_260263 | Blackstonedge - 110 | Jul 7, 2026 3:34pm | Jul 7, 2026 3:34pm | Jul 7, 2026 9:08pm | Jul 7, 2026 9:08pm | Jul 7, 2026 9:09pm | Jul 7, 2026 9:12pm | Jul 7, 2026 9:12pm | Jul 7, 2026 9:12pm |  |  | Fair | No | Power restore
Outage | J.E.26.07.06206 | C001842470 | Romaine Roberts | St.Mary | Completed | Load_250162 | Blackstonedge - 110 | Jul 7, 2026 3:34pm | Jul 7, 2026 3:34pm | Jul 7, 2026 9:14pm | Jul 7, 2026 9:14pm | Jul 7, 2026 9:14pm | Jul 7, 2026 9:14pm | Jul 7, 2026 9:14pm | Jul 7, 2026 9:14pm |  |  | Fair | No | Found ok
Outage | J.E.26.07.06253 | C001842469 | Romaine Roberts | St.Mary | Completed | Load_240991 | Blackstonedge - 110 | Jul 7, 2026 3:34pm | Jul 7, 2026 3:34pm | Jul 7, 2026 3:56pm | Jul 7, 2026 3:56pm | Jul 7, 2026 7:18pm | Jul 7, 2026 7:26pm | Jul 7, 2026 7:28pm | Jul 7, 2026 7:28pm |  |  | Fair | No | Found ok feeder was down
Outage | J.E.26.07.06280 | C001842471 | Romaine Roberts | St.Mary | Completed | Load_240121 | Blackstonedge - 110 | Jul 7, 2026 3:34pm | Jul 7, 2026 3:34pm | Jul 7, 2026 9:13pm | Jul 7, 2026 9:13pm | Jul 7, 2026 9:13pm | Jul 7, 2026 9:13pm | Jul 7, 2026 9:14pm | Jul 7, 2026 9:14pm |  |  | Fair | No | Found ok
Outage | J.E.26.07.06303 | C001842468 | Romaine Roberts | St.Mary | Completed | Load_237637 | Blackstonedge - 110 | Jul 7, 2026 3:34pm | Jul 7, 2026 3:34pm | Jul 7, 2026 9:15pm | Jul 7, 2026 9:15pm | Jul 7, 2026 9:15pm | Jul 7, 2026 9:15pm | Jul 7, 2026 9:15pm | Jul 7, 2026 9:15pm |  |  | Fair | No | Found ok feeder was out restore by pjs crew
Non-Outage | J.E.26.07.06258 | C001842466 | Richman Whyte | null | Completed | null | null | Jul 7, 2026 3:33pm | Jul 7, 2026 3:34pm | Jul 7, 2026 3:55pm | Jul 7, 2026 3:55pm | Jul 7, 2026 3:55pm | Jul 7, 2026 3:56pm | Jul 7, 2026 3:57pm | Jul 7, 2026 3:57pm |  |  | Fair | No | Refer to field service hexing connection customer finished repair after hurricane
Outage | J.E.26.07.05840 | C001842465 | Oshane Warren | Hanover | Completed | Load_259967 | Orange Bay - 310 | Jul 7, 2026 3:33pm | Jul 7, 2026 3:34pm | Jul 7, 2026 4:36pm | Jul 7, 2026 4:36pm | Jul 7, 2026 4:37pm | Jul 7, 2026 4:37pm | Jul 7, 2026 4:38pm | Jul 7, 2026 4:38pm |  |  | Fair | No | Unable to locate or contact customer on the phone
Outage | J.E.26.07.05875 | C001842467 | Dwayne Samuels | Trelawny | Completed | Load_292776 | Greenwood - 210 | Jul 7, 2026 3:33pm | Jul 7, 2026 8:04pm | Jul 7, 2026 9:48pm | Jul 7, 2026 9:50pm | Jul 7, 2026 10:11pm | Jul 7, 2026 10:13pm | Jul 7, 2026 10:15pm | Jul 7, 2026 10:15pm |  |  | Fair | No | Call is linked to illegal connections in area that is causing low voltage that was sent off earlier today refer to losses team for further checks
Outage | J.E.26.07.05842 | C001842464 | Marlon Authors | Manchester | Completed | Load_260730 | Spur Tree - 210 | Jul 7, 2026 3:32pm | Jul 7, 2026 3:53pm | Jul 7, 2026 4:31pm | Jul 7, 2026 4:31pm | Jul 7, 2026 5:26pm | Jul 7, 2026 5:47pm | Jul 7, 2026 5:47pm | Jul 7, 2026 5:47pm |  |  | Fair | No | Patrol and found illegal connections banning the conductors together. Remove same and replace one blown 3 amp fuse that protects 25 kva transformer circuit at pole #619014. Further checks revealed that the insulation from the transformer lug is damaged. Unable to restore supply transformer is damaged and needs to be replaced. Please refer same to the maintenance department for replacement
Outage | J.E.26.07.05848 | C001842463 | Andre Williams | Trelawny | Completed | Load_572246 | Duncans - 210 | Jul 7, 2026 3:32pm | Jul 7, 2026 3:33pm | Jul 7, 2026 4:37pm | Jul 7, 2026 4:37pm | Jul 7, 2026 4:37pm | Jul 7, 2026 4:48pm | Jul 7, 2026 4:49pm | Jul 7, 2026 4:49pm |  |  | Fair | No | Patrol line section no visible fault seen on line refuse and close 15 amp junction fuse at pole027392
Outage | J.E.26.07.05871 | C001842461 | Andre Williams | Trelawny | Completed | Load_237728 | Duncans - 210 | Jul 7, 2026 3:32pm | Jul 7, 2026 3:33pm | Jul 7, 2026 3:38pm | Jul 7, 2026 4:49pm | Jul 7, 2026 4:49pm | Jul 7, 2026 4:49pm | Jul 7, 2026 4:50pm | Jul 7, 2026 4:50pm |  |  | Fair | No | Patrol line section no visible fault seen on line refuse and close 15 amp junction fuse at pole027392
Outage | J.E.26.07.06284 | C001842462 | Marlon Authors | St.Elizabeth | Completed | Load_254136 | Maggotty - 110 | Jul 7, 2026 3:32pm | Jul 7, 2026 3:54pm | Jul 7, 2026 6:25pm | Jul 7, 2026 6:25pm | Jul 7, 2026 6:45pm | Jul 7, 2026 6:56pm | Jul 7, 2026 6:56pm | Jul 7, 2026 6:56pm | BrokenPole |  | Fair | No | Patrol and found one 40 feet TA wooden pole with overhead guy pole missing and it’s badly leaning over the school premises. Please refer same to the maintenance department for further assistance
Outage | J.E.26.07.06012 | C001842460 | Andre Williams | Trelawny | Completed | Load_254068 | Duncans - 210 | Jul 7, 2026 3:31pm | Jul 7, 2026 8:04pm | Jul 7, 2026 8:48pm | Jul 7, 2026 8:48pm | Jul 7, 2026 9:11pm | Jul 7, 2026 9:17pm | Jul 7, 2026 9:17pm | Jul 7, 2026 9:17pm | BrokenWire |  | Fair | No | Repair burnt off phase on customer 3 wire service at Jps pole
Outage | J.E.26.07.06046 | C001842459 | Michael Christian | St.James | Completed | Load_254864 | Queens Drive - 710 | Jul 7, 2026 3:30pm | Jul 7, 2026 3:31pm | Jul 7, 2026 9:50pm | Jul 7, 2026 9:50pm | Jul 7, 2026 10:12pm | Jul 7, 2026 10:13pm | Jul 7, 2026 10:14pm | Jul 7, 2026 10:14pm |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.06222 | C001842449 | Michael Christian | St.James | Completed | Load_258942 | Queens Drive - 710 | Jul 7, 2026 3:29pm | Jul 7, 2026 3:31pm | Jul 7, 2026 3:42pm | Jul 7, 2026 3:42pm | Jul 7, 2026 4:05pm | Jul 7, 2026 4:28pm | Jul 7, 2026 4:28pm | Jul 7, 2026 4:28pm |  |  | Fair | No | Found 1 50 amp out at pole # 212962 replace
Outage | J.E.26.07.06245 | C001842450 | Michael Christian | St.James | Completed | Load_293371 | Queens Drive - 310 | Jul 7, 2026 3:29pm | Jul 7, 2026 3:31pm | Jul 7, 2026 10:44pm | Jul 7, 2026 10:44pm | Jul 7, 2026 10:44pm | Jul 7, 2026 10:46pm | Jul 7, 2026 10:46pm | Jul 7, 2026 10:46pm |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.06256 | C001842448 | Michael Christian | St.James | Completed | Load_242949 | Queens Drive - 710 | Jul 7, 2026 3:29pm | Jul 7, 2026 4:47pm | Jul 7, 2026 5:10pm | Jul 7, 2026 5:10pm | Jul 7, 2026 6:17pm | Jul 7, 2026 8:18pm | Jul 7, 2026 8:19pm | Jul 7, 2026 8:19pm | Fire |  | Fair | No | Open 100 kava transformer to work and secondary line cause by t o j wire
Outage | J.E.26.07.05962 | C001842447 | Neckell Ormsby | St.Mary | Completed | Load_240723 | Highgate -110 | Jul 7, 2026 3:26pm | Jul 7, 2026 3:33pm | Jul 7, 2026 5:26pm | Jul 7, 2026 5:26pm | Jul 7, 2026 6:23pm | Jul 7, 2026 6:23pm | Jul 7, 2026 6:24pm | Jul 7, 2026 6:24pm |  |  | Fair | No | Found supply ok at customer premises Customer said a team came earlier
Outage | J.E.26.07.06194 | C001842446 | Neckell Ormsby | St.Mary | Completed | Load_249623 | Highgate -110 | Jul 7, 2026 3:26pm | Jul 7, 2026 3:33pm | Jul 7, 2026 3:41pm | Jul 7, 2026 3:41pm | Jul 7, 2026 4:54pm | Jul 7, 2026 5:26pm | Jul 7, 2026 5:26pm | Jul 7, 2026 5:26pm |  |  | Fair | No | Found bamboo on secondary causing phase and neutral to entangled cut and remove bamboo and conductors were cleared no transformer fuse opened or blown voltage left at pole 231v 116v 115v
Outage | J.E.26.07.05795 | C001842445 | Kenroy Dale | Manchester | Completed | Load_253741 | Kendal - 210 | Jul 7, 2026 3:25pm | Jul 7, 2026 3:30pm | Jul 7, 2026 3:53pm | Jul 7, 2026 3:53pm | Jul 7, 2026 5:49pm | Jul 7, 2026 6:11pm | Jul 7, 2026 6:12pm | Jul 7, 2026 6:12pm |  |  | Fair | No | Corrosion found at pothead, remade connection using one penn union. Voltage reading 112/112/224
Outage | J.E.26.07.05902 | C001842444 | Kenroy Dale | Manchester | Completed | Load_255147 | Kendal - 210 | Jul 7, 2026 3:25pm | Jul 7, 2026 3:30pm | Jul 7, 2026 6:34pm | Jul 7, 2026 6:34pm | Jul 7, 2026 6:34pm | Jul 7, 2026 6:35pm | Jul 7, 2026 6:39pm | Jul 7, 2026 6:39pm |  |  | Fair | No | Effort to contact customer multiple time was unsuccessful area visited and still not found with the advise of dispatcher call was written off
Outage | J.E.26.07.05915 | C001842443 | Richard Samuda | Manchester | Completed | Load_244090 | Spur Tree - 310 | Jul 7, 2026 3:25pm | Jul 7, 2026 3:30pm | Jul 7, 2026 5:39pm | Jul 7, 2026 5:39pm | Jul 7, 2026 7:25pm | Jul 7, 2026 7:25pm | Jul 7, 2026 7:29pm | Jul 7, 2026 7:29pm |  |  | Fair | No | Customer say issue was resolved earlier
Outage | J.E.26.07.05750 | C001842439 | Nickolas Rodriques | St.Catherine | Completed | Load_264536 | Rhodens Pen - 410 | Jul 7, 2026 3:24pm | Jul 8, 2026 7:27am | Jul 8, 2026 2:05pm | Jul 8, 2026 2:15pm | Jul 8, 2026 2:31pm | Jul 8, 2026 2:48pm | Jul 8, 2026 2:54pm | Jul 8, 2026 2:54pm |  |  | Fair | No | Customer confirmed that the issue was resolved.
Outage | J.E.26.07.05822 | C001842437 | Collin Robinson | Portland | Completed | Load_265550 | Port Antonio - 310 | Jul 7, 2026 3:19pm | Jul 7, 2026 3:27pm | Jul 7, 2026 4:00pm | Jul 7, 2026 4:03pm | Jul 7, 2026 4:30pm | Jul 7, 2026 4:37pm | Jul 7, 2026 4:37pm | Jul 7, 2026 4:37pm | TreeContact |  | Fair | No | Area found with supply Cut and clear tree branches from near open secondary conductor
Outage | J.E.26.07.06011 | C001842414 | Edward Royal | KSAS | Completed | Load_241282 | Duhaney - 310 | Jul 7, 2026 2:55pm | Jul 7, 2026 2:55pm | Jul 7, 2026 3:09pm | Jul 7, 2026 3:09pm | Jul 7, 2026 3:09pm | Jul 7, 2026 3:26pm | Jul 7, 2026 3:26pm | Jul 7, 2026 3:26pm |  |  | Fair | No | Customer was reconnected by escalation
Outage | J.E.26.07.06015 | C001842413 | Edward Royal | KSAN | Completed | Load_260114 | Constant Spring - 210 | Jul 7, 2026 2:55pm | Jul 7, 2026 2:56pm | Jul 7, 2026 3:26pm | Jul 7, 2026 3:26pm | Jul 7, 2026 3:26pm | Jul 7, 2026 3:26pm | Jul 7, 2026 3:27pm | Jul 7, 2026 3:27pm |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.07.05774 | C001842381 | Milton Charlton | KSAN | Completed | Load_265781 | Hope - 510 | Jul 7, 2026 2:30pm | Jul 7, 2026 6:19pm | Jul 7, 2026 6:43pm | Jul 7, 2026 7:32pm | Jul 7, 2026 8:10pm | Jul 7, 2026 8:20pm | Jul 7, 2026 8:22pm | Jul 7, 2026 8:22pm |  |  | Fair | No | Found okay upon arrival. Customer has no problem at the premises.
Non-Outage | J.E.26.07.05590 | C001842352 | Evan Spaulding | null | Completed | null | null | Jul 7, 2026 2:13pm | Jul 7, 2026 2:13pm | Jul 8, 2026 11:25am | Jul 8, 2026 11:25am | Jul 8, 2026 11:25am | Jul 8, 2026 11:25am | Jul 8, 2026 11:26am | Jul 8, 2026 11:26am | Fire |  | SevereWind | No | Associated call.
Non-Outage | J.E.26.07.05636 | C001842342 | Evan Spaulding | St.Mary | Completed | Load_240723 | Highgate -110 | Jul 7, 2026 2:09pm | Jul 7, 2026 2:09pm | Jul 7, 2026 2:12pm | Jul 7, 2026 2:13pm | Jul 7, 2026 4:16pm | Jul 7, 2026 4:17pm | Jul 7, 2026 4:19pm | Jul 7, 2026 4:19pm |  |  | Fair | No | Retention secondary conductors and remake jumper using 1-1bolt clamp.
Non-Outage | J.E.26.07.05807 | C001842341 | Raymond Carr | St.Mary | Completed | Load_251609 | Oracabessa - 210 | Jul 7, 2026 2:09pm | Jul 7, 2026 2:11pm | Jul 7, 2026 2:16pm | Jul 7, 2026 2:16pm | Jul 7, 2026 2:54pm | Jul 7, 2026 3:00pm | Jul 7, 2026 2:55pm | Jul 7, 2026 2:55pm | Fire |  | Fair | No | Customer couldn’t be contacted.
Outage | J.E.26.07.05907 | C001842326 | Neville Spencer | Clarendon | Completed | Load_568435 | May Pen - 110 | Jul 7, 2026 2:04pm | Jul 7, 2026 2:04pm | Jul 7, 2026 2:13pm | Jul 7, 2026 2:13pm | Jul 7, 2026 2:24pm | Jul 7, 2026 2:25pm | Jul 7, 2026 3:07pm | Jul 7, 2026 3:07pm |  |  | Fair | No | Renew blown 8 amp j/ fuse area restored.
Non-Outage | J.E.26.07.05894 | C001842307 | Stephen Taylor | St.Thomas | Completed | Load_261596 | Good Year - 210 | Jul 7, 2026 1:45pm | Jul 7, 2026 1:45pm | Jul 7, 2026 8:40pm | Jul 7, 2026 8:40pm | Jul 7, 2026 8:40pm | Jul 7, 2026 8:44pm | Jul 7, 2026 8:45pm | Jul 7, 2026 8:45pm | BrokenWire |  | Fair | No | Patrol the area power is in the area several call to single customer and no one answer need more information
Outage | J.E.26.07.05612 | C001842303 | Moses Elliston | St.Catherine | Completed | Load_556350 | Rhodens Pen - 210 | Jul 7, 2026 1:44pm | Jul 7, 2026 1:45pm | Jul 7, 2026 2:34pm | Jul 7, 2026 2:34pm | Jul 7, 2026 3:16pm | Jul 7, 2026 3:17pm | Jul 7, 2026 3:20pm | Jul 7, 2026 3:20pm |  |  | Fair | No | Meter changed to # 1365992 due to single phasing condition.114-114 -228 volts at meter
Outage | J.E.26.07.05788 | C001842301 | Stephen Taylor | St.Thomas | Completed | Load_239912 | Lysson - 410 | Jul 7, 2026 1:44pm | Jul 7, 2026 1:44pm | Jul 7, 2026 2:00pm | Jul 7, 2026 2:01pm | Jul 7, 2026 2:01pm | Jul 7, 2026 2:01pm | Jul 7, 2026 2:02pm | Jul 7, 2026 2:02pm |  |  | Fair | No | Contact customer and customer say that is the wrong number him have light
Outage | J.E.26.07.05832 | C001842302 | Stephen Taylor | St.Thomas | Completed | Load_269505 | Lysson - 410 | Jul 7, 2026 1:44pm | Jul 7, 2026 1:44pm | Jul 7, 2026 8:55pm | Jul 7, 2026 8:55pm | Jul 7, 2026 8:55pm | Jul 7, 2026 8:55pm | Jul 7, 2026 8:57pm | Jul 7, 2026 8:57pm | Fire |  | Fair | No | Check with customer and customer say power is back and there are now ok
Non-Outage | J.E.26.07.05784 | C001842295 | Nickolas Rodriques | St.Catherine | Completed | Load_1000336 | Tredegar - 210 | Jul 7, 2026 1:39pm | Jul 7, 2026 1:39pm | Jul 7, 2026 2:58pm | Jul 7, 2026 3:11pm | Jul 7, 2026 3:26pm | Jul 7, 2026 3:38pm | Jul 7, 2026 3:42pm | Jul 7, 2026 3:42pm |  |  | Fair | No | Unable to communicate with the customer in order to gain access to the gated community.
Outage | J.E.26.07.05701 | C001842292 | Moses Elliston | St.Catherine | Completed | Load_251672 | Twickenham - 310 | Jul 7, 2026 1:37pm | Jul 7, 2026 1:39pm | Jul 8, 2026 9:26am | Jul 8, 2026 9:26am | Jul 8, 2026 9:26am | Jul 7, 2026 5:00pm | Jul 8, 2026 9:28am | Jul 8, 2026 9:28am |  |  | Fair | No | Credit added to prepaid account.
Non-Outage | J.E.26.07.05887 | C001842290 | Edward Royal | KSAS | Completed | Load_251395 | Duhaney - 310 | Jul 7, 2026 1:35pm | Jul 7, 2026 1:35pm | Jul 7, 2026 2:58pm | Jul 7, 2026 2:58pm | Jul 7, 2026 2:58pm | Jul 7, 2026 2:59pm | Jul 7, 2026 2:59pm | Jul 7, 2026 2:59pm | BrokenWire |  | Fair | No | Premises not found unable to communicate with customer
Outage | J.E.26.07.05815 | C001842281 | Raymond Carr | St.Mary | Completed | Load_247804 | Blackstonedge - 110 | Jul 7, 2026 1:29pm | Jul 7, 2026 1:30pm | Jul 7, 2026 1:32pm | Jul 7, 2026 1:32pm | Jul 7, 2026 2:08pm | Jul 7, 2026 2:00pm | Jul 7, 2026 2:10pm | Jul 7, 2026 2:10pm |  |  | Fair | No | Customer couldn’t be contacted. No driving directions were given.
Outage | J.E.26.07.05791 | C001842273 | Wan Carlos Scarlett | Portmore | Completed | Load_237810 | Naggo Head - 510 | Jul 7, 2026 1:22pm | Jul 7, 2026 1:24pm | Jul 7, 2026 2:13pm | Jul 7, 2026 2:13pm | Jul 7, 2026 3:13pm | Jul 7, 2026 4:42pm | Jul 7, 2026 4:45pm | Jul 7, 2026 4:45pm |  |  | Fair | No | Refuse 40amp junction no pole # was found nothing was found on the primary line suspect bird take out the power supply
Outage | J.E.26.07.05851 | C001842272 | Nickolas Rodriques | St.Catherine | Completed | Load_254532 | Tredegar - 210 | Jul 7, 2026 1:21pm | Jul 7, 2026 1:22pm | Jul 7, 2026 5:25pm | Jul 7, 2026 6:07pm | Jul 7, 2026 6:33pm | Jul 7, 2026 6:52pm | Jul 7, 2026 6:54pm | Jul 7, 2026 6:54pm |  |  | Fair | No | Customer was located and confirmed that the power outage was restored.
Outage | J.E.26.07.05833 | C001842258 | Derrick Dawkins | St.James | Completed | Load_249619 | Bogue - 310 | Jul 7, 2026 1:13pm | Jul 7, 2026 1:14pm | Jul 7, 2026 1:31pm | Jul 7, 2026 1:53pm | Jul 7, 2026 1:59pm | Jul 7, 2026 2:50pm | Jul 7, 2026 2:51pm | Jul 7, 2026 2:51pm |  |  | Fair | No | Customer was disconnected due to the hurricane reconnected customer used 3 pg clamp voltage left 116/117=233
Outage | J.E.26.07.05764 | C001842248 | Barnett Brown | Manchester | Completed | Load_269161 | Porus - 310 | Jul 7, 2026 1:06pm | Jul 7, 2026 3:36pm | Jul 7, 2026 3:39pm | Jul 7, 2026 3:44pm | Jul 7, 2026 5:44pm | Jul 7, 2026 6:49pm | Jul 7, 2026 6:52pm | Jul 7, 2026 6:52pm |  |  | Fair | No | Patrol line, found nothing, replace blown 20 amp junction fuse
Non-Outage | J.E.26.07.05483 | C001842247 | Roemello Brown | Trelawny | Completed | Load_241855 | Duncans - 210 | Jul 7, 2026 1:05pm | Jul 7, 2026 1:06pm | Jul 8, 2026 9:44am | Jul 8, 2026 9:44am | Jul 8, 2026 11:29am | Jul 8, 2026 11:29am | Jul 8, 2026 12:24pm | Jul 8, 2026 12:24pm |  |  | Fair | No | Service wire burn off at pothead have it reclamp Voltage found 106/112/219Voltage leave 109/109/219
Non-Outage | J.E.26.07.05644 | C001842246 | Roemello Brown | Trelawny | Completed | Load_240895 | Greenwood - 110 | Jul 7, 2026 1:05pm | Jul 7, 2026 1:06pm | Jul 7, 2026 1:43pm | Jul 7, 2026 3:42pm | Jul 7, 2026 4:11pm | Jul 7, 2026 4:11pm | Jul 7, 2026 4:35pm | Jul 7, 2026 4:35pm |  |  | Fair | No | One leg of the secondary line broke down needs emergency team to assist please a section of the community single phasing Voltage found 116/34.41/98Voltage leave 116/34.41/98
Non-Outage | J.E.26.07.05780 | C001842245 | Roemello Brown | Trelawny | Completed | Load_261797 | Martha Brae - 210 | Jul 7, 2026 1:04pm | Jul 7, 2026 1:06pm | Jul 7, 2026 1:37pm | Jul 7, 2026 1:37pm | Jul 7, 2026 3:01pm | Jul 7, 2026 3:01pm | Jul 7, 2026 3:42pm | Jul 7, 2026 3:42pm |  |  | Fair | No | Corrosion at pothead have clamps change Voltage found 99Voltage leave 116
Non-Outage | J.E.26.07.05820 | C001842236 | Marlon Brown | Trelawny | Completed | Load_1001461 | Martha Brae - 110 | Jul 7, 2026 1:03pm | Jul 7, 2026 1:05pm | Jul 7, 2026 1:10pm | Jul 7, 2026 1:11pm | Jul 7, 2026 1:27pm | Jul 7, 2026 3:00pm | Jul 7, 2026 3:00pm | Jul 7, 2026 3:00pm | Fire |  | Fair | No | Isolated 25kva transformer to retention 3 spans of secondary phase and neutral conductors and do spot bushing.
Outage | J.E.26.07.05812 | C001842222 | Derrick Dawkins | St.James | Completed | Load_250412 | Bogue - 310 | Jul 7, 2026 12:50pm | Jul 7, 2026 12:51pm | Jul 7, 2026 1:42pm | Jul 7, 2026 1:42pm | Jul 7, 2026 1:47pm | Jul 7, 2026 1:53pm | Jul 7, 2026 1:53pm | Jul 7, 2026 1:53pm |  |  | Fair | No | Only customer out of the rammy system without light refer back to field service box # 04493
Outage | J.E.26.07.05756 | C001842212 | Raymond Carr | St.Mary | Completed | Load_251609 | Oracabessa - 210 | Jul 7, 2026 12:39pm | Jul 7, 2026 12:40pm | Jul 7, 2026 12:50pm | Jul 7, 2026 12:53pm | Jul 7, 2026 12:53pm | Jul 7, 2026 1:00pm | Jul 7, 2026 12:55pm | Jul 7, 2026 12:55pm | Fire |  | Fair | No | Customer did not make a report.
Outage | J.E.26.07.05766 | C001842210 | Hartley Chin | Clarendon | Completed | Load_257105 | Monymusk - 410 | Jul 7, 2026 12:37pm | Jul 7, 2026 12:45pm | Jul 7, 2026 1:34pm | Jul 7, 2026 1:34pm | Jul 7, 2026 2:47pm | Jul 7, 2026 3:09pm | Jul 7, 2026 3:10pm | Jul 7, 2026 3:10pm |  |  | Fair | No | Prem not found …area patrolled and found oaky …unable to contact customer…
Outage | J.E.26.07.05746 | C001842201 | Neville Spencer | Clarendon | Completed | Load_262048 | May Pen - 110 | Jul 7, 2026 12:24pm | Jul 7, 2026 12:24pm | Jul 7, 2026 1:16pm | Jul 7, 2026 1:16pm | Jul 7, 2026 1:41pm | Jul 7, 2026 2:08pm | Jul 7, 2026 2:11pm | Jul 7, 2026 2:11pm | Fire |  | Fair | No | Found defective 3, wire service.Installed 60 ft #6 triplex, y3, 6/6 sleeves, 2 clamps voltage reading 114 118 233 supply restored.
Non-Outage | J.E.26.07.05776 | C001842200 | Fredrick Hamilton | KSAS | Completed | Load_241201 | Duhaney - 310 | Jul 7, 2026 12:23pm | Jul 7, 2026 12:24pm | Jul 7, 2026 12:30pm | Jul 7, 2026 12:31pm | Jul 7, 2026 12:37pm | Jul 7, 2026 12:48pm | Jul 7, 2026 12:48pm | Jul 7, 2026 12:48pm |  |  | Fair | No | 227v/115v/114v obtained Defective meterBurnt meter detected at location and stuck in single phase position Recommend meter change
Outage | J.E.26.07.05688 | C001842199 | Hopeton Henry | St.Thomas | Completed | Load_238303 | Good Year - 210 | Jul 7, 2026 12:23pm | Jul 7, 2026 3:47pm | Jul 7, 2026 5:14pm | Jul 7, 2026 6:20pm | Jul 7, 2026 7:18pm | Jul 7, 2026 7:53pm | Jul 7, 2026 7:57pm | Jul 7, 2026 7:57pm | BrokenWire |  | Fair | No | Found corrosion at pole and pot head Use 3 connector 3 clamps 116-114-230 volts of
Outage | J.E.26.07.05715 | C001842198 | Stephen Taylor | St.Thomas | Completed | Load_268190 | Lysson - 410 | Jul 7, 2026 12:22pm | Jul 7, 2026 12:23pm | Jul 7, 2026 2:11pm | Jul 7, 2026 2:11pm | Jul 7, 2026 2:11pm | Jul 7, 2026 2:11pm | Jul 7, 2026 2:12pm | Jul 7, 2026 2:12pm |  |  | Fair | No | Contact customer and customer say that power is back and now okay
Outage | J.E.26.07.05765 | C001842189 | Tajay Bernard | Hanover | Completed | Load_269922 | Orange Bay - 310 | Jul 7, 2026 12:09pm | Jul 7, 2026 12:10pm | Jul 7, 2026 12:13pm | Jul 7, 2026 12:14pm | Jul 7, 2026 12:14pm | Jul 7, 2026 12:15pm | Jul 7, 2026 12:15pm | Jul 7, 2026 12:15pm |  |  | Fair | No | This call belongs to st James
Outage | J.E.26.07.05731 | C001842177 | Raymond Lewis | St.Ann | Completed | Load_248125 | Ocho Rios - 310 | Jul 7, 2026 12:03pm | Jul 7, 2026 12:04pm | Jul 7, 2026 12:07pm | Jul 7, 2026 12:07pm | Jul 7, 2026 12:08pm | Jul 7, 2026 2:31pm | Jul 7, 2026 2:31pm | Jul 7, 2026 2:31pm |  |  | Fair | No | Cut and remove tree from line Splice and retention secondary phase and neutral two span and refuse and close 50 kva x former
Non-Outage | J.E.26.07.05730 | C001842176 | Edward Royal | null | Completed | null | null | Jul 7, 2026 12:01pm | Jul 7, 2026 12:03pm | Jul 7, 2026 1:39pm | Jul 7, 2026 1:39pm | Jul 7, 2026 1:39pm | Jul 7, 2026 2:08pm | Jul 7, 2026 2:09pm | Jul 7, 2026 2:09pm | BrokenWire |  | Fair | No | Spliced and reconnected service cable using 20ft service cables 3 single bolt clamp
Outage | J.E.26.07.05743 | C001842173 | Richard Samuda | Manchester | Completed | Load_261060 | Spur Tree - 310 | Jul 7, 2026 12:00pm | Jul 7, 2026 3:31pm | Jul 7, 2026 4:11pm | Jul 7, 2026 4:11pm | Jul 7, 2026 5:33pm | Jul 7, 2026 5:33pm | Jul 7, 2026 5:35pm | Jul 7, 2026 5:35pm |  |  | Fair | No | Customer have internal issues advised customer to contact electrician voltage 117/118/235
Outage | J.E.26.07.05750 | C001842162 | Nickolas Rodriques | St.Catherine | Completed | Load_264536 | Rhodens Pen - 410 | Jul 7, 2026 11:57am | Jul 7, 2026 11:57am | Jul 7, 2026 6:00pm | Jul 7, 2026 6:00pm | Jul 7, 2026 6:05pm | Jul 7, 2026 6:06pm | Jul 7, 2026 6:07pm | Jul 7, 2026 6:07pm |  |  | Fair | No | Unable to locate or communicate with the customer after dialogue earlier.
Non-Outage | J.E.26.06.35227 | C001842158 | Nickolas Rodriques | St.Catherine | Completed | Load_264438 | Twickenham - 210 | Jul 7, 2026 11:56am | Jul 7, 2026 11:56am | Jul 7, 2026 1:16pm | Jul 7, 2026 1:43pm | Jul 7, 2026 2:01pm | Jul 7, 2026 2:52pm | Jul 7, 2026 2:56pm | Jul 7, 2026 2:56pm |  |  | Fair | No | Checked and found customer with unstable voltage caused by broken service wire phase and neutral due to an apple tree that grew on wire. Repaired by doing minor vegetation and splice and retention wire using three service sleeves, current reading is (115-114-229). Customer confirmed that all is well now.
Outage | J.E.26.07.05735 | C001842159 | Elvis Trowers | KSAN | Completed | Load_245669 | Constant Spring - 210 | Jul 7, 2026 11:56am | Jul 7, 2026 12:04pm | Jul 7, 2026 1:06pm | Jul 7, 2026 1:06pm | Jul 7, 2026 1:44pm | Jul 7, 2026 2:37pm | Jul 7, 2026 2:37pm | Jul 7, 2026 2:37pm |  |  | Fair | Yes | Areas found without electricity supply when checked and a blown 8 amp junction fuse found and replaced after patrol was completed at pole #0011173, tree contact was the cause.
Outage | J.E.26.07.05460 | C001842148 | Dwain Samuels | St.James | Completed | Load_244424 | Bogue - 310 | Jul 7, 2026 11:50am | Jul 7, 2026 3:15pm | Jul 8, 2026 6:01am | Jul 8, 2026 2:55pm | Jul 8, 2026 2:55pm | Jul 8, 2026 2:55pm | Jul 8, 2026 2:56pm | Jul 8, 2026 2:56pm |  |  | Fair | No | Assigned to wrong parish
Non-Outage | J.E.26.07.05719 | C001842135 | Nickolas Rodriques | null | Completed | null | null | Jul 7, 2026 11:43am | Jul 8, 2026 7:31am | Jul 8, 2026 12:01pm | Jul 8, 2026 12:03pm | Jul 8, 2026 12:30pm | Jul 8, 2026 12:40pm | Jul 8, 2026 12:43pm | Jul 8, 2026 12:43pm |  |  | Fair | No | Checked and found customer without electricity. All necessary checks were done and it was found that the issue is stemming from the hexing box hexing (01105). Refer to field service.
Outage | J.E.26.07.05696 | C001842136 | Neville Spencer | Clarendon | Completed | Load_568435 | May Pen - 110 | Jul 7, 2026 11:43am | Jul 7, 2026 11:44am | Jul 7, 2026 12:19pm | Jul 7, 2026 12:19pm | Jul 7, 2026 1:14pm | Jul 7, 2026 1:15pm | Jul 7, 2026 1:15pm | Jul 7, 2026 1:15pm |  |  | Fair | No | Found supply in area .
Outage | J.E.26.07.05701 | C001842123 | Nickolas Rodriques | St.Catherine | Completed | Load_251672 | Twickenham - 310 | Jul 7, 2026 11:37am | Jul 7, 2026 11:40am | Jul 7, 2026 12:22pm | Jul 7, 2026 12:35pm | Jul 7, 2026 1:09pm | Jul 7, 2026 1:15pm | Jul 7, 2026 1:16pm | Jul 7, 2026 1:16pm |  |  | Fair | No | Customer is having issues topping up his CIU box. Refer to field service.
Outage | J.E.26.07.05720 | C001842122 | Nickolas Rodriques | St.Catherine | Completed | Load_254315 | Tredegar - 310 | Jul 7, 2026 11:37am | Jul 7, 2026 11:40am | Jul 7, 2026 3:44pm | Jul 7, 2026 3:46pm | Jul 7, 2026 4:11pm | Jul 7, 2026 5:21pm | Jul 7, 2026 5:24pm | Jul 7, 2026 5:24pm |  |  | Fair | No | Checked and found customer with unstable voltage caused by defective service wire. Repaired by replacing 46ft of #6 twisted using two service sleeves and two clamps, current reading is (119).
Outage | J.E.26.07.05700 | C001842107 | Swon Miller | St.James | Completed | Load_1002045 | Queens Drive - 710 | Jul 7, 2026 11:28am | Jul 7, 2026 11:42pm | Jul 8, 2026 12:35am | Jul 8, 2026 12:35am | Jul 8, 2026 12:41am | Jul 22, 2026 12:46am | Jul 8, 2026 12:46am | Jul 8, 2026 12:46am | BrokenWire |  | Fair | No | Check and found area okay unable to locate customer calls to customer went unanswered
Outage | J.E.26.07.05683 | C001842105 | Floyd Taylor | St.James | Completed | Load_241722 | Queens Drive - 810 | Jul 7, 2026 11:25am | Jul 7, 2026 11:26am | Jul 7, 2026 1:10pm | Jul 7, 2026 1:10pm | Jul 7, 2026 2:41pm | Jul 7, 2026 3:09pm | Jul 7, 2026 3:12pm | Jul 7, 2026 3:12pm | BrokenWire |  | Fair | No | Splice and retention customer service wire using 1 penunion voltage readings 117,115,233
Non-Outage | J.E.26.07.05695 | C001842093 | Fitzroy Turner | KSAN | Completed | Load_567617 | Constant Spring - 310 | Jul 7, 2026 11:23am | Jul 7, 2026 11:23am | Jul 7, 2026 11:38am | Jul 7, 2026 11:39am | Jul 7, 2026 12:32pm | Jul 7, 2026 1:16pm | Jul 7, 2026 1:21pm | Jul 7, 2026 1:21pm | LowHangingWires |  | Fair | No | Found tree and tree two phases primary line and crossarm broken use insulator to carry out repair supply restored to the areas
Non-Outage | J.E.26.07.05590 | C001842092 | Locksley Allen | null | Completed | null | null | Jul 7, 2026 11:22am | Jul 7, 2026 11:23am | Jul 7, 2026 11:50am | Jul 7, 2026 12:35pm | Jul 7, 2026 12:35pm | Jul 7, 2026 12:42pm | Jul 7, 2026 12:41pm | Jul 7, 2026 12:41pm | Fire |  | Fair | No | The neutral and the lower conductor is entangle, because of this several customers don’t have any supply
Non-Outage | J.E.26.07.05636 | C001842091 | Locksley Allen | St.Mary | Completed | Load_240723 | Highgate -110 | Jul 7, 2026 11:22am | Jul 7, 2026 11:23am | Jul 7, 2026 12:41pm | Jul 7, 2026 1:12pm | Jul 7, 2026 1:12pm | Jul 7, 2026 1:27pm | Jul 7, 2026 1:26pm | Jul 7, 2026 1:26pm |  |  | Fair | No | Meter found blank. Several customers in this area is without supply. Check the transformer near the school
Outage | J.E.26.07.05432 | C001842056 | Gregory Grossett | Portland | Completed | Load_266103 | Port Antonio - 410 | Jul 7, 2026 11:09am | Jul 7, 2026 11:09am | Jul 7, 2026 11:11am | Jul 7, 2026 11:11am | Jul 7, 2026 12:20pm | Jul 7, 2026 12:20pm | Jul 7, 2026 12:23pm | Jul 7, 2026 12:23pm | BrokenWire |  | Fair | No | Customer meter pole was broken and since been replaced,advised customer to get certified electrician and connect their service wire ,
Outage | J.E.26.07.05668 | C001842055 | Wan Carlos Scarlett | Portmore | Completed | Load_263104 | Naggo Head - 510 | Jul 7, 2026 11:05am | Jul 7, 2026 11:07am | Jul 7, 2026 12:10pm | Jul 7, 2026 12:10pm | Jul 7, 2026 12:45pm | Jul 7, 2026 2:10pm | Jul 7, 2026 2:12pm | Jul 7, 2026 2:12pm |  |  | Fair | No | Refuse 2,25KVA transformer with 2,3amp fuse no pole # was found nothing was found on the primary line
Outage | J.E.26.07.05671 | C001842054 | Elvis Trowers | KSAN | Completed | Load_250361 | Washington Blvd - 610 | Jul 7, 2026 11:05am | Jul 7, 2026 11:05am | Jul 7, 2026 12:26pm | Jul 7, 2026 12:26pm | Jul 7, 2026 12:51pm | Jul 7, 2026 1:05pm | Jul 7, 2026 1:06pm | Jul 7, 2026 1:06pm |  |  | Fair | Yes | Happened to be internal when checked defective 3 wire meter socket, meter socket burnt out,customer was also advised to contact an electrician, voltage when checked was left at 119+118=237 volts.
Non-Outage | J.E.26.07.05641 | C001842026 | Stephen Taylor | null | Completed | null | null | Jul 7, 2026 10:53am | Jul 7, 2026 10:54am | Jul 7, 2026 11:43am | Jul 7, 2026 11:43am | Jul 7, 2026 11:43am | Jul 7, 2026 11:44am | Jul 7, 2026 11:45am | Jul 7, 2026 11:45am |  |  | Fair | No | Jps maintenance team are working into the area
Outage | J.E.26.07.05462 | C001842024 | Hartley Chin | Clarendon | Completed | Load_406198 | Parnassus - 310 | Jul 7, 2026 10:53am | Jul 7, 2026 10:53am | Jul 7, 2026 12:39pm | Jul 7, 2026 12:39pm | Jul 7, 2026 1:21pm | Jul 7, 2026 1:22pm | Jul 7, 2026 1:27pm | Jul 7, 2026 1:27pm | BrokenWire |  | Fair | No | Customer is the only person affected… meter # 2550976 … customer requires approximately 130 ft of #6 twisted to restore customer supply …
Outage | J.E.26.07.05610 | C001842023 | Hartley Chin | Clarendon | Completed | Load_240599 | May Pen - 210 | Jul 7, 2026 10:53am | Jul 7, 2026 10:53am | Jul 7, 2026 11:20am | Jul 7, 2026 11:20am | Jul 7, 2026 12:21pm | Jul 7, 2026 12:39pm | Jul 7, 2026 12:39pm | Jul 7, 2026 12:39pm |  |  | Fair | No | Ref to field service!!! Found burn mark on back of customer meter … voltage read in line side 115v , 112v … no voltage read found on load side … customer meter # 2819701 .. customer requires 3W meter ..
Outage | J.E.26.07.05669 | C001842027 | Stephen Taylor | St.Thomas | Completed | Load_266680 | Lysson - 410 | Jul 7, 2026 10:53am | Jul 7, 2026 10:54am | Jul 7, 2026 11:47am | Jul 7, 2026 11:47am | Jul 7, 2026 11:47am | Jul 7, 2026 11:47am | Jul 7, 2026 11:47am | Jul 7, 2026 11:47am |  |  | Fair | No | Jps maintenance team are working into the area
Outage | J.E.26.07.05665 | C001842022 | Romeo Brissett | St.James | Completed | Load_302249 | Bogue - 510 | Jul 7, 2026 10:52am | Jul 7, 2026 10:53am | Jul 7, 2026 12:21pm | Jul 7, 2026 12:21pm | Jul 7, 2026 1:02pm | Jul 7, 2026 1:00pm | Jul 7, 2026 1:08pm | Jul 7, 2026 1:08pm |  |  | Fair | No | Customer stated power restored.
Outage | J.E.26.07.05670 | C001842021 | Romeo Brissett | St.James | Completed | Load_252083 | Bogue - 510 | Jul 7, 2026 10:52am | Jul 7, 2026 10:53am | Jul 7, 2026 2:30pm | Jul 7, 2026 2:30pm | Jul 7, 2026 2:30pm | Jul 7, 2026 2:28pm | Jul 7, 2026 2:31pm | Jul 7, 2026 2:31pm |  |  | Fair | No | Unable to locate customer. Phone ring to voicemail
Outage | J.E.26.07.05467 | C001842020 | Romeo Brissett | St.James | Completed | Load_261361 | Bogue - 510 | Jul 7, 2026 10:50am | Jul 7, 2026 10:53am | Jul 7, 2026 1:08pm | Jul 7, 2026 1:08pm | Jul 7, 2026 1:35pm | Jul 7, 2026 2:25pm | Jul 7, 2026 2:29pm | Jul 7, 2026 2:29pm |  |  | Fair | No | Removed bird and replaced (1)8amps junction fuse.
Non-Outage | J.E.26.07.04598 | C001842003 | Raymond Carr | St.Mary | Completed | Load_248758 | Blackstonedge - 110 | Jul 7, 2026 10:48am | Jul 7, 2026 10:48am | Jul 7, 2026 12:19pm | Jul 7, 2026 12:19pm | Jul 7, 2026 12:19pm | Jul 7, 2026 12:38pm | Jul 7, 2026 12:22pm | Jul 7, 2026 12:22pm |  |  | Fair | No | Several calls to contact number went straight to voicemail.
Non-Outage | J.E.26.07.05650 | C001842002 | Rusean Allen | null | Completed | null | null | Jul 7, 2026 10:46am | Jul 7, 2026 10:46am | Jul 7, 2026 2:05pm | Jul 7, 2026 2:05pm | Jul 7, 2026 2:18pm | Jul 7, 2026 2:45pm | Jul 7, 2026 2:45pm | Jul 7, 2026 2:45pm | BrokenWire |  | Fair | No | 1 span broken secondary wire found, wire was spliced retention and reconnected.
Outage | J.E.26.07.05370 | C001841987 | Tyrese Williams | St.Ann | Completed | Load_264960 | Cardiff Hall - 310 | Jul 7, 2026 10:43am | Jul 7, 2026 10:43am | Jul 7, 2026 11:06am | Jul 7, 2026 11:06am | Jul 7, 2026 11:42am | Jul 7, 2026 12:00pm | Jul 7, 2026 12:01pm | Jul 7, 2026 12:01pm |  |  | Fair | No | Open a 50 kva transformer fuse to repair transformer drop leed use 1 pg clamp and 3ft of copper wire
Outage | J.E.26.07.05431 | C001841988 | Derrick Dawkins | St.James | Completed | Load_556791 | Bogue - 310 | Jul 7, 2026 10:43am | Jul 7, 2026 10:43am | Jul 7, 2026 11:08am | Jul 7, 2026 11:37am | Jul 7, 2026 11:57am | Jul 7, 2026 12:03pm | Jul 7, 2026 12:03pm | Jul 7, 2026 12:03pm |  |  | Fair | No | Only customer in the hexing box without light refer back to field service kadian hexing box # 00111
Outage | J.E.26.07.05347 | C001841985 | Tyrese Williams | St.Ann | Completed | Load_294552 | Cardiff Hall - 210 | Jul 7, 2026 10:42am | Jul 7, 2026 10:43am | Jul 7, 2026 11:08am | Jul 7, 2026 12:08pm | Jul 7, 2026 12:08pm | Jul 7, 2026 12:33pm | Jul 7, 2026 12:33pm | Jul 7, 2026 12:33pm |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.07.05460 | C001841986 | Derrick Dawkins | St.James | Completed | Load_244424 | Bogue - 310 | Jul 7, 2026 10:42am | Jul 7, 2026 10:43am | Jul 7, 2026 11:36am | Jul 7, 2026 11:36am | Jul 7, 2026 11:36am | Jul 7, 2026 11:37am | Jul 7, 2026 11:37am | Jul 7, 2026 11:37am |  |  | Fair | No | Trelawny call
Outage | J.E.26.07.05556 | C001841984 | Tyrese Williams | St.Ann | Completed | Load_246792 | Cardiff Hall - 310 | Jul 7, 2026 10:42am | Jul 7, 2026 10:43am | Jul 7, 2026 11:08am | Jul 7, 2026 12:33pm | Jul 7, 2026 2:13pm | Jul 7, 2026 2:27pm | Jul 7, 2026 2:28pm | Jul 7, 2026 2:28pm |  |  | Fair | No | Replace a 10 kva transformer fuse at pole use a 2 amp at pole
Outage | J.E.26.07.05656 | C001841983 | Richard Nicholas | St.Catherine | Completed | Load_251090 | Rhodens Pen - 410 | Jul 7, 2026 10:41am | Jul 7, 2026 10:43am | Jul 7, 2026 12:08pm | Jul 7, 2026 12:08pm | Jul 7, 2026 12:42pm | Jul 7, 2026 1:04pm | Jul 7, 2026 1:06pm | Jul 7, 2026 1:06pm |  |  | EarthMovement | No | Premises found ok,no broken wire seen however customer wanted to transfer service wire to another building but there is no stanchion for the service wire to anchor on.
Outage | J.E.26.07.05647 | C001841976 | Wayne Dillion | Manchester | Completed | Load_269147 | Spur Tree - 210 | Jul 7, 2026 10:39am | Jul 7, 2026 11:36am | Jul 7, 2026 1:02pm | Jul 7, 2026 1:02pm | Jul 7, 2026 1:02pm | Jul 7, 2026 1:03pm | Jul 7, 2026 1:03pm | Jul 7, 2026 1:03pm |  |  | Fair | No | Customer said supply ok
Outage | J.E.26.07.03710 | C001841969 | Moses Elliston | St.Catherine | Completed | Load_568213 | New Michelton - 210 | Jul 7, 2026 10:35am | Jul 7, 2026 10:37am | Jul 7, 2026 11:44am | Jul 7, 2026 11:44am | Jul 7, 2026 11:44am | Jul 7, 2026 11:45am | Jul 7, 2026 11:47am | Jul 7, 2026 11:47am |  |  | Fair | No | Premises disconnected for debt
Outage | J.E.26.07.05459 | C001841959 | Ryan Richards | Manchester | Completed | Load_240784 | Porus - 210 | Jul 7, 2026 10:30am | Jul 7, 2026 10:32am | Jul 7, 2026 1:31pm | Jul 7, 2026 1:31pm | Jul 7, 2026 2:18pm | Jul 7, 2026 3:42pm | Jul 7, 2026 3:43pm | Jul 7, 2026 3:43pm |  |  | Fair | No | Customer found disconnected call center was contacted and they where able to reconnect customer
Non-Outage | J.E.26.07.05602 | C001841934 | Wayne Dillion | null | Completed | null | null | Jul 7, 2026 10:23am | Jul 7, 2026 10:24am | Jul 7, 2026 10:55am | Jul 7, 2026 10:55am | Jul 7, 2026 10:55am | Jul 7, 2026 10:55am | Jul 7, 2026 10:55am | Jul 7, 2026 10:55am |  |  | Fair | No | Customer said supply ok
Outage | J.E.26.07.05256 | C001841933 | Romeo Brissett | St.James | Completed | Load_249506 | Bogue - 510 | Jul 7, 2026 10:23am | Jul 7, 2026 10:24am | Jul 7, 2026 2:31pm | Jul 7, 2026 2:31pm | Jul 7, 2026 3:04pm | Jul 7, 2026 3:47pm | Jul 7, 2026 3:56pm | Jul 7, 2026 3:56pm |  |  | Fair | No | Replaced (1)50kva transformer fuse.
Outage | J.E.26.07.05575 | C001841931 | Rusean Allen | KSAS | Completed | Load_269212 | Rockfort - 410 | Jul 7, 2026 10:22am | Jul 7, 2026 10:22am | Jul 7, 2026 12:04pm | Jul 7, 2026 2:45pm | Jul 7, 2026 2:52pm | Jul 7, 2026 2:53pm | Jul 7, 2026 2:53pm | Jul 7, 2026 2:53pm |  |  | Fair | No | Corroded wires found at pothead, wires were disconnected and reconnected with one bolt clamps.
Outage | J.E.26.07.05612 | C001841932 | Richard Nicholas | St.Catherine | Completed | Load_556350 | Rhodens Pen - 210 | Jul 7, 2026 10:22am | Jul 7, 2026 10:41am | Jul 7, 2026 1:06pm | Jul 7, 2026 1:06pm | Jul 7, 2026 1:36pm | Jul 7, 2026 1:37pm | Jul 7, 2026 1:38pm | Jul 7, 2026 1:38pm |  |  | Fair | No | Fault detected at EG 06052 box.please refer to Mr.moses
Non-Outage | J.E.26.07.05074 | C001841930 | Fredrick Hamilton | KSAS | Completed | Load_261930 | Duhaney - 310 | Jul 7, 2026 10:21am | Jul 7, 2026 10:23am | Jul 7, 2026 11:21am | Jul 7, 2026 12:05pm | Jul 7, 2026 12:08pm | Jul 7, 2026 12:16pm | Jul 7, 2026 12:16pm | Jul 7, 2026 12:16pm |  |  | Fair | No | 235v/116.4v/117v obtained Defective meter at location recommend meter changed Meter found burnt and in single phase mode
Outage | J.E.26.07.05465 | C001841916 | Moses Elliston | St.Catherine | Completed | Load_266264 | Twickenham - 310 | Jul 7, 2026 10:16am | Jul 7, 2026 12:01pm | Jul 7, 2026 12:04pm | Jul 7, 2026 12:04pm | Jul 7, 2026 12:04pm | Jul 7, 2026 12:09pm | Jul 7, 2026 12:10pm | Jul 7, 2026 12:10pm |  |  | Fair | No | Credit added to prepaid account
Outage | J.E.26.07.05382 | C001841903 | Richard Watson | St.Elizabeth | Completed | Load_265795 | Maggotty - 110 | Jul 7, 2026 10:07am | Jul 7, 2026 10:08am | Jul 7, 2026 10:53am | Jul 7, 2026 10:53am | Jul 7, 2026 11:27am | Jul 7, 2026 11:37am | Jul 7, 2026 11:38am | Jul 7, 2026 11:38am |  |  | Fair | No | Replace blown 5amp fuse for 50kva transformer no pole#, patrol revealed no visible fault, however inspection on transformer revealed that transformer casing ground not connected, supply restored to area.
Non-Outage | J.E.26.07.05451 | C001841893 | Wayne Dillion | null | Completed | null | null | Jul 7, 2026 10:04am | Jul 7, 2026 10:12am | Jul 7, 2026 11:51am | Jul 7, 2026 11:51am | Jul 7, 2026 11:51am | Jul 7, 2026 11:52am | Jul 7, 2026 11:52am | Jul 7, 2026 11:52am | Fire |  | Fair | No | Cellphone number provided for customer not working and premises not found
Outage | J.E.26.07.05405 | C001841890 | Wayne Dillion | St.Elizabeth | Completed | Load_292116 | Maggotty - 110 | Jul 7, 2026 10:03am | Jul 7, 2026 10:12am | Jul 7, 2026 10:34am | Jul 7, 2026 10:34am | Jul 7, 2026 10:34am | Jul 7, 2026 10:43am | Jul 7, 2026 10:43am | Jul 7, 2026 10:43am |  |  | Fair | No | Please refer this call to field service hexing box #01584 found last night open with caution tape call customer care to reconnect customer but customers got disconnected this morning and caution tape pull
Outage | J.E.26.07.05566 | C001841889 | Wayne Dillion | Manchester | Completed | Load_266153 | Spur Tree - 210 | Jul 7, 2026 10:03am | Jul 7, 2026 10:12am | Jul 7, 2026 11:50am | Jul 7, 2026 11:50am | Jul 7, 2026 11:50am | Jul 7, 2026 11:51am | Jul 7, 2026 11:51am | Jul 7, 2026 11:51am |  |  | Fair | No | Customer said supply ok
Non-Outage | J.E.26.07.00612 | C001841841 | Rayon Foster | Hanover | Completed | Load_264233 | Orange Bay - 310 | Jul 7, 2026 9:36am | Jul 7, 2026 9:37am | Jul 7, 2026 11:04am | Jul 7, 2026 12:22pm | Jul 7, 2026 1:05pm | Jul 7, 2026 1:06pm | Jul 7, 2026 1:07pm | Jul 7, 2026 1:07pm |  |  | Fair | No | When spoke with customer they said that the issue was already resolved by a electrician
Non-Outage | J.E.26.07.05426 | C001841728 | Rusean Allen | null | Completed | null | null | Jul 7, 2026 9:35am | Jul 7, 2026 10:56am | Jul 7, 2026 1:21pm | Jul 7, 2026 1:21pm | Jul 7, 2026 1:40pm | Jul 7, 2026 2:05pm | Jul 7, 2026 2:05pm | Jul 7, 2026 2:05pm | BrokenWire |  | Fair | No | Not found
Outage | J.E.26.07.05429 | C001841839 | Fitzroy Turner | KSAN | Completed | Load_293845 | Washington Blvd - 710 | Jul 7, 2026 9:35am | Jul 7, 2026 9:36am | Jul 7, 2026 10:50am | Jul 7, 2026 10:50am | Jul 7, 2026 10:54am | Jul 7, 2026 10:55am | Jul 7, 2026 10:56am | Jul 7, 2026 10:56am |  |  | Fair | No | Customer premises close at this time.please send email to field service department to check customer YPP meter
Non-Outage | J.E.26.06.35932 | C001841725 | Odaine Johnson | null | Completed | null | null | Jul 7, 2026 9:07am | Jul 7, 2026 9:08am | Jul 7, 2026 10:06am | Jul 7, 2026 10:06am | Jul 7, 2026 10:06am | Jul 7, 2026 10:07am | Jul 7, 2026 10:07am | Jul 7, 2026 10:07am |  |  | Fair | No | Contacted customer and customer stated they did not make any report
Non-Outage | J.E.26.07.03696 | C001841724 | Odaine Johnson | Clarendon | Completed | Load_237834 | Parnassus - 210 | Jul 7, 2026 9:04am | Jul 7, 2026 9:05am | Jul 7, 2026 10:06am | Jul 7, 2026 2:55pm | Jul 7, 2026 2:55pm | Jul 7, 2026 2:56pm | Jul 7, 2026 3:00pm | Jul 7, 2026 3:00pm |  |  | Fair | No | Corrosion was found at pothead 3 pen union was replaced and problem was fixed Voltage reading before A109 B87 AB196Voltage reading after A113 B112 AB225
Non-Outage | J.E.26.07.04010 | C001841722 | Odaine Johnson | Clarendon | Completed | Load_261483 | Monymusk - 210 | Jul 7, 2026 9:04am | Jul 7, 2026 9:05am | Jul 7, 2026 10:06am | Jul 8, 2026 12:00pm | Jul 8, 2026 12:00pm | Jul 8, 2026 12:00pm | Jul 8, 2026 12:00pm | Jul 8, 2026 12:00pm |  |  | Fair | No | Contacted customer and customer stated that the issue was resolved already
Non-Outage | J.E.26.07.04655 | C001841723 | Odaine Johnson | Clarendon | Completed | Load_406114 | Parnassus - 310 | Jul 7, 2026 9:04am | Jul 7, 2026 9:05am | Jul 7, 2026 10:06am | Jul 7, 2026 10:54am | Jul 7, 2026 10:54am | Jul 7, 2026 10:55am | Jul 7, 2026 10:56am | Jul 7, 2026 10:56am |  |  | Fair | No | Premises was found working ok problem was found and customer side of the line Voltage reading is A116 B116 AB232
Non-Outage | J.E.26.07.05389 | C001841721 | Fredrick Hamilton | KSAN | Completed | Load_259593 | Constant Spring - 210 | Jul 7, 2026 9:03am | Jul 7, 2026 10:20am | Jul 7, 2026 11:21am | Jul 7, 2026 11:23am | Jul 7, 2026 11:32am | Jul 7, 2026 11:52am | Jul 7, 2026 11:52am | Jul 7, 2026 11:52am |  |  | Fair | No | Burnt wires detected in meter socket customer advised
Outage | J.E.26.07.05390 | C001841718 | Stephen Taylor | St.Thomas | Completed | Load_577147 | Lysson - 410 | Jul 7, 2026 9:02am | Jul 7, 2026 9:02am | Jul 7, 2026 11:45am | Jul 7, 2026 11:45am | Jul 7, 2026 11:45am | Jul 7, 2026 11:46am | Jul 7, 2026 11:46am | Jul 7, 2026 11:46am |  |  | Fair | No | Jps maintenance team are working into the area
Non-Outage | J.E.26.07.05002 | C001841717 | Damion Reid | null | Completed | null | null | Jul 7, 2026 9:01am | Jul 7, 2026 9:02am | Jul 7, 2026 1:24pm | Jul 7, 2026 1:24pm | Jul 7, 2026 2:33pm | Jul 7, 2026 2:36pm | Jul 7, 2026 2:37pm | Jul 7, 2026 2:37pm | BrokenPole |  | SevereWind | No | Leaning 35ft T construction pole found pole need to rectify soon
Non-Outage | J.E.26.07.05385 | C001841716 | Damion Reid | null | Completed | null | null | Jul 7, 2026 8:59am | Jul 7, 2026 9:02am | Jul 7, 2026 3:03pm | Jul 8, 2026 7:15am | Jul 8, 2026 8:13am | Jul 8, 2026 8:17am | Jul 8, 2026 8:24am | Jul 8, 2026 8:24am | BrokenWire |  | Fair | No | Two span of broken secondary phase conductor found cause by banging of conductor open 25kva transformer fuse link splice an retention conductor using 30ft of #2 aluminum conductor two #2 preform two one bolt clamp and restore power
Non-Outage | J.E.26.06.17391 | C001841714 | Error Coore | Manchester | Completed | Load_238024 | Kendal - 210 | Jul 7, 2026 8:53am | Jul 7, 2026 8:54am | Jul 8, 2026 9:54am | Jul 8, 2026 11:05am | Jul 8, 2026 12:27pm | Jul 8, 2026 12:44pm | Jul 8, 2026 12:47pm | Jul 8, 2026 12:47pm |  |  | Fair | No | Premise found ok voltage reading 114/113/227 volts
Non-Outage | J.E.26.06.34289 | C001841715 | Error Coore | Manchester | Completed | Load_292450 | Spur Tree - 310 | Jul 7, 2026 8:53am | Jul 7, 2026 8:54am | Jul 7, 2026 9:18am | Jul 8, 2026 8:22am | Jul 8, 2026 8:22am | Jul 8, 2026 8:22am | Jul 8, 2026 8:23am | Jul 8, 2026 8:23am |  |  | Fair | No | Premise found ok call customer and customer said that the problem was resolved
Non-Outage | J.E.26.05.32368 | C001841711 | Error Coore | Manchester | Completed | Load_268132 | Spur Tree - 310 | Jul 7, 2026 8:52am | Jul 7, 2026 8:54am | Jul 7, 2026 10:29am | Jul 8, 2026 8:20am | Jul 8, 2026 8:20am | Jul 8, 2026 8:21am | Jul 8, 2026 8:22am | Jul 8, 2026 8:22am |  |  | Fair | No | Premise found ok call customer and customer said that the problem was resolved
Non-Outage | J.E.26.06.37532 | C001841713 | Error Coore | Manchester | Completed | Load_269024 | Spur Tree - 310 | Jul 7, 2026 8:52am | Jul 7, 2026 8:54am | Jul 7, 2026 10:24am | Jul 7, 2026 1:55pm | Jul 7, 2026 3:05pm | Jul 7, 2026 3:10pm | Jul 7, 2026 3:13pm | Jul 7, 2026 3:13pm |  |  | Fair | No | Premise found ok voltage reading 118/117/235 volts
Non-Outage | J.E.26.07.00401 | C001841706 | Royston Montague | St.Catherine | Completed | Load_256288 | Twickenham - 310 | Jul 7, 2026 8:52am | Jul 7, 2026 8:56am | Jul 7, 2026 8:59am | Jul 7, 2026 1:29pm | Jul 7, 2026 4:13pm | Jul 7, 2026 4:26pm | Jul 7, 2026 4:26pm | Jul 7, 2026 4:26pm | LeaningPole |  | Fair | No | Customer concern about a leading pole beside her premises. Please inform maintenance department thanks.
Non-Outage | J.E.26.07.01065 | C001841709 | Error Coore | Manchester | Completed | Load_239098 | Kendal - 210 | Jul 7, 2026 8:52am | Jul 7, 2026 8:54am | Jul 8, 2026 8:20am | Jul 8, 2026 8:30am | Jul 8, 2026 9:19am | Jul 8, 2026 9:48am | Jul 8, 2026 9:51am | Jul 8, 2026 9:51am |  |  | Fair | No | Premise found ok customer have internal problem voltage reading 110/111/222 volts
Non-Outage | J.E.26.07.03565 | C001841708 | Royston Montague | St.Catherine | Completed | Load_250042 | Twickenham - 410 | Jul 7, 2026 8:52am | Jul 7, 2026 8:56am | Jul 7, 2026 8:59am | Jul 7, 2026 1:27pm | Jul 7, 2026 1:27pm | Jul 7, 2026 1:27pm | Jul 7, 2026 1:28pm | Jul 7, 2026 1:28pm |  |  | Fair | No | Multiple calls to customer phone go without answer. GPS coordinate on job not working.
Non-Outage | J.E.26.07.03717 | C001841707 | Error Coore | Manchester | Completed | Load_265753 | Spur Tree - 310 | Jul 7, 2026 8:52am | Jul 7, 2026 8:54am | Jul 7, 2026 10:32am | Jul 7, 2026 10:32am | Jul 7, 2026 11:35am | Jul 7, 2026 11:53am | Jul 7, 2026 11:56am | Jul 7, 2026 11:56am |  |  | Fair | No | Premise found ok customer have internal problem voltage reading 110/111/221 volts
Non-Outage | J.E.26.07.03793 | C001841710 | Royston Montague | St.Catherine | Completed | Load_243462 | Twickenham - 410 | Jul 7, 2026 8:52am | Jul 7, 2026 8:56am | Jul 7, 2026 8:59am | Jul 7, 2026 1:28pm | Jul 7, 2026 1:28pm | Jul 7, 2026 1:28pm | Jul 7, 2026 1:29pm | Jul 7, 2026 1:29pm |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.06.01491 | C001841701 | Error Coore | Manchester | Completed | Load_292080 | Kendal - 210 | Jul 7, 2026 8:51am | Jul 7, 2026 8:54am | Jul 8, 2026 9:54am | Jul 8, 2026 9:54am | Jul 8, 2026 10:55am | Jul 8, 2026 11:02am | Jul 8, 2026 11:04am | Jul 8, 2026 11:04am |  |  | Fair | No | Premise not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.06.18050 | C001841702 | Error Coore | Manchester | Completed | Load_242353 | Kendal - 210 | Jul 7, 2026 8:51am | Jul 7, 2026 8:54am | Jul 8, 2026 8:26am | Jul 8, 2026 2:01pm | Jul 8, 2026 3:09pm | Jul 8, 2026 3:23pm | Jul 8, 2026 3:25pm | Jul 8, 2026 3:25pm |  |  | Fair | No | Premise not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.06.18851 | C001841698 | Error Coore | Manchester | Completed | Load_238207 | Kendal - 210 | Jul 7, 2026 8:51am | Jul 7, 2026 8:54am | Jul 8, 2026 8:29am | Jul 8, 2026 12:47pm | Jul 8, 2026 1:34pm | Jul 8, 2026 1:59pm | Jul 8, 2026 2:01pm | Jul 8, 2026 2:01pm |  |  | Fair | No | Premise found ok customer customer said that the problem was resolved
Non-Outage | J.E.26.07.04505 | C001841700 | Error Coore | Manchester | Completed | Load_292975 | Spur Tree - 310 | Jul 7, 2026 8:51am | Jul 7, 2026 8:54am | Jul 7, 2026 9:23am | Jul 7, 2026 9:24am | Jul 7, 2026 10:03am | Jul 7, 2026 10:12am | Jul 7, 2026 10:13am | Jul 7, 2026 10:13am |  |  | Fair | No | Premise found ok voltage reading 119/117/236 volts
Non-Outage | J.E.26.07.04585 | C001841699 | Ryan Richards | Manchester | Completed | Load_249926 | Kendal - 210 | Jul 7, 2026 8:51am | Jul 8, 2026 8:09am | Jul 8, 2026 9:29am | Jul 8, 2026 11:44am | Jul 8, 2026 12:47pm | Jul 8, 2026 1:45pm | Jul 8, 2026 1:45pm | Jul 8, 2026 1:45pm |  |  | Fair | No | Burn offf phase found at pole remade burn off phase using 2 one bolt clamp voltage 112/114/227 volts
Non-Outage | J.E.26.06.01155 | C001841694 | Error Coore | Manchester | Completed | Load_269056 | Spur Tree - 310 | Jul 7, 2026 8:50am | Jul 7, 2026 8:55am | Jul 7, 2026 10:20am | Jul 7, 2026 12:22pm | Jul 7, 2026 1:34pm | Jul 7, 2026 1:54pm | Jul 7, 2026 1:55pm | Jul 7, 2026 1:55pm |  |  | Fair | No | Premise found ok voltage reading 114/115/229 volts
Non-Outage | J.E.26.06.08960 | C001841696 | Error Coore | Manchester | Completed | Load_261375 | Spur Tree - 310 | Jul 7, 2026 8:50am | Jul 7, 2026 8:54am | Jul 7, 2026 10:17am | Jul 7, 2026 3:13pm | Jul 7, 2026 4:05pm | Jul 7, 2026 4:30pm | Jul 7, 2026 4:31pm | Jul 7, 2026 4:31pm |  |  | Fair | No | Premise found ok voltage reading 119/118/237 volts
Non-Outage | J.E.26.05.31440 | C001841684 | Royston Montague | St.Catherine | Completed | Load_263499 | Tredegar - 510 | Jul 7, 2026 8:48am | Jul 7, 2026 8:54am | Jul 7, 2026 8:59am | Jul 7, 2026 9:07am | Jul 7, 2026 9:35am | Jul 7, 2026 9:35am | Jul 7, 2026 9:36am | Jul 7, 2026 9:36am |  |  | Fair | No | Customer confirmed issue resolved. Please update thanks.
Non-Outage | J.E.26.06.10679 | C001841685 | Royston Montague | St.Catherine | Completed | Load_245205 | Tredegar - 510 | Jul 7, 2026 8:48am | Jul 7, 2026 8:54am | Jul 7, 2026 8:59am | Jul 7, 2026 9:36am | Jul 7, 2026 10:44am | Jul 7, 2026 10:45am | Jul 7, 2026 10:45am | Jul 7, 2026 10:45am |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.06.11100 | C001841686 | Royston Montague | St.Catherine | Completed | Load_241100 | Tredegar - 510 | Jul 7, 2026 8:48am | Jul 7, 2026 8:54am | Jul 7, 2026 8:59am | Jul 7, 2026 10:46am | Jul 7, 2026 11:32am | Jul 7, 2026 11:33am | Jul 7, 2026 11:33am | Jul 7, 2026 11:33am |  |  | Fair | No | Premises found ok. 228v 113v 114v customer customer issue resolved few days ago.
Non-Outage | J.E.26.06.11573 | C001841687 | Royston Montague | St.Catherine | Completed | Load_252710 | Tredegar - 510 | Jul 7, 2026 8:48am | Jul 7, 2026 8:54am | Jul 7, 2026 8:59am | Jul 7, 2026 11:34am | Jul 7, 2026 12:19pm | Jul 7, 2026 12:20pm | Jul 7, 2026 12:20pm | Jul 7, 2026 12:20pm |  |  | Fair | No | Customer confirmed issue resolved.please update.
Non-Outage | J.E.26.07.00105 | C001841688 | Royston Montague | St.Catherine | Completed | Load_568932 | Twickenham - 310 | Jul 7, 2026 8:48am | Jul 7, 2026 8:54am | Jul 7, 2026 8:59am | Jul 7, 2026 12:20pm | Jul 7, 2026 1:26pm | Jul 7, 2026 1:26pm | Jul 7, 2026 1:27pm | Jul 7, 2026 1:27pm | LowHangingWires |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.03.10765 | C001841677 | Andrae Dawkins | St.James | Completed | Load_242949 | Queens Drive - 710 | Jul 7, 2026 8:47am | Jul 7, 2026 8:47am | Jul 7, 2026 11:15am | Jul 7, 2026 12:41pm | Jul 7, 2026 12:41pm | Jul 7, 2026 11:33am | Jul 7, 2026 12:43pm | Jul 7, 2026 12:43pm |  |  | Fair | No | Unable to reach customer phone customer locate customer
Non-Outage | J.E.26.03.46262 | C001841679 | Andrae Dawkins | St.James | Completed | Load_302202 | Queens Drive - 710 | Jul 7, 2026 8:47am | Jul 7, 2026 8:47am | Jul 7, 2026 1:10pm | Jul 7, 2026 1:10pm | Jul 7, 2026 2:04pm | Jul 7, 2026 11:53am | Jul 7, 2026 2:06pm | Jul 7, 2026 2:06pm |  |  | Fair | No | Unable to reach customer mobile phone
Non-Outage | J.E.26.04.05463 | C001841678 | Andrae Dawkins | St.James | Completed | Load_302338 | Queens Drive - 710 | Jul 7, 2026 8:47am | Jul 7, 2026 8:47am | Jul 7, 2026 11:08am | Jul 7, 2026 11:18am | Jul 7, 2026 11:18am | Jul 7, 2026 11:10am | Jul 7, 2026 11:20am | Jul 7, 2026 11:20am |  |  | Fair | No | Check and found okay customer said that the problem was already resolved
Non-Outage | J.E.26.04.05863 | C001841680 | Andrae Dawkins | St.James | Completed | Load_302338 | Queens Drive - 710 | Jul 7, 2026 8:47am | Jul 7, 2026 8:47am | Jul 7, 2026 11:11am | Jul 7, 2026 11:29am | Jul 7, 2026 11:29am | Jul 7, 2026 11:14am | Jul 7, 2026 11:35am | Jul 7, 2026 11:35am |  |  | Fair | No | Cannot locate customer unable to reach customer phone
Non-Outage | J.E.26.04.13791 | C001841681 | Andrae Dawkins | St.James | Completed | Load_243259 | Queens Drive - 710 | Jul 7, 2026 8:47am | Jul 7, 2026 8:47am | Jul 7, 2026 11:12am | Jul 7, 2026 12:05pm | Jul 7, 2026 12:05pm | Jul 7, 2026 11:25am | Jul 7, 2026 12:41pm | Jul 7, 2026 12:41pm |  |  | Fair | No | Unable to reach customer phone cannot locate customer
Outage | J.E.26.07.05362 | C001841682 | Neville Spencer | Clarendon | Completed | Load_579438 | May Pen - 110 | Jul 7, 2026 8:47am | Jul 7, 2026 8:47am | Jul 7, 2026 10:55am | Jul 7, 2026 10:55am | Jul 7, 2026 11:31am | Jul 7, 2026 12:19pm | Jul 7, 2026 12:19pm | Jul 7, 2026 12:19pm | BrokenWire |  | Fair | No | Remade slack phase joints in meter socket voltage reading 110 112 223 supply restored.
Outage | J.E.26.07.05372 | C001841683 | Hartley Chin | Clarendon | Completed | Load_246809 | May Pen - 210 | Jul 7, 2026 8:47am | Jul 7, 2026 8:48am | Jul 7, 2026 10:01am | Jul 7, 2026 10:01am | Jul 7, 2026 11:07am | Jul 7, 2026 11:09am | Jul 7, 2026 11:09am | Jul 7, 2026 11:09am |  |  | Fair | No | Found okay … voltage read 116v , 115v ..
Non-Outage | J.E.26.02.16247 | C001841674 | Andrae Dawkins | St.James | Completed | Load_250208 | Queens Drive - 710 | Jul 7, 2026 8:46am | Jul 7, 2026 8:47am | Jul 7, 2026 9:43am | Jul 7, 2026 10:42am | Jul 7, 2026 10:42am | Jul 7, 2026 10:43am | Jul 7, 2026 10:45am | Jul 7, 2026 10:45am |  |  | Fair | No | Check and found okay customer said that they didn’t make any report and they don’t have any problem there
Non-Outage | J.E.26.02.16903 | C001841675 | Andrae Dawkins | St.James | Completed | Load_250761 | Queens Drive - 710 | Jul 7, 2026 8:46am | Jul 7, 2026 8:47am | Jul 7, 2026 2:06pm | Jul 7, 2026 2:06pm | Jul 7, 2026 2:06pm | Jul 7, 2026 12:10pm | Jul 7, 2026 2:07pm | Jul 7, 2026 2:07pm |  |  | Fair | No | Customer said that they didn’t make any report and that they don’t have any issue at the premises
Non-Outage | J.E.26.02.18979 | C001841676 | Andrae Dawkins | St.James | Completed | Load_251205 | Queens Drive - 710 | Jul 7, 2026 8:46am | Jul 7, 2026 8:47am | Jul 7, 2026 9:44am | Jul 7, 2026 10:18am | Jul 7, 2026 10:38am | Jul 7, 2026 10:39am | Jul 7, 2026 10:39am | Jul 7, 2026 10:39am |  |  | Fair | No | Check and found okay customer said that they didn’t make any report
Non-Outage | J.E.26.02.32155 | C001841671 | Dwain Samuels | Westmoreland | Completed | Load_264618 | Paradise - 210 | Jul 7, 2026 8:46am | Jul 7, 2026 8:46am | Jul 7, 2026 9:00am | Jul 7, 2026 11:48am | Jul 7, 2026 11:48am | Jul 7, 2026 11:53am | Jul 7, 2026 11:54am | Jul 7, 2026 11:54am |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.03.01896 | C001841670 | Dwain Samuels | Westmoreland | Completed | Load_303218 | Paradise - 310 | Jul 7, 2026 8:46am | Jul 7, 2026 8:46am | Jul 7, 2026 9:00am | Jul 7, 2026 12:27pm | Jul 8, 2026 9:12am | Jul 8, 2026 9:16am | Jul 8, 2026 9:17am | Jul 8, 2026 9:17am |  |  | Fair | No | Found working okay. Voltage check115-115-230
Non-Outage | J.E.26.06.38318 | C001841673 | Andrae Dawkins | St.James | Completed | Load_269636 | Queens Drive - 310 | Jul 7, 2026 8:46am | Jul 7, 2026 8:47am | Jul 7, 2026 10:50am | Jul 7, 2026 10:51am | Jul 7, 2026 10:51am | Jul 7, 2026 10:51am | Jul 7, 2026 10:52am | Jul 7, 2026 10:52am |  |  | Fair | No | Check and found okay customer said that the problem was already resolved
Non-Outage | J.E.26.01.25571 | C001841666 | Dwain Samuels | Westmoreland | Completed | Load_246285 | Paradise - 210 | Jul 7, 2026 8:45am | Jul 7, 2026 8:46am | Jul 7, 2026 9:00am | Jul 7, 2026 11:45am | Jul 7, 2026 11:45am | Jul 7, 2026 11:45am | Jul 7, 2026 11:46am | Jul 7, 2026 11:46am |  |  | Fair | No | Need a proper directions and contact information
Non-Outage | J.E.26.01.26971 | C001841667 | Dwain Samuels | Westmoreland | Completed | Load_292903 | Paradise - 110 | Jul 7, 2026 8:45am | Jul 7, 2026 8:46am | Jul 7, 2026 9:00am | Jul 7, 2026 11:32am | Jul 7, 2026 11:32am | Jul 7, 2026 11:32am | Jul 7, 2026 11:34am | Jul 7, 2026 11:34am |  |  | Fair | No | Corrosion found at 3 wire pole. Voltage check 102-101-203. Corrosion clear use 3 one bolt clamp. Voltage check 113-114-227
Non-Outage | J.E.26.01.37885 | C001841668 | Dwain Samuels | Westmoreland | Completed | Load_260268 | Paradise - 210 | Jul 7, 2026 8:45am | Jul 7, 2026 8:46am | Jul 7, 2026 9:00am | Jul 7, 2026 11:21am | Jul 7, 2026 11:21am | Jul 7, 2026 11:21am | Jul 7, 2026 11:22am | Jul 7, 2026 11:22am |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.01.38035 | C001841664 | Dwain Samuels | Westmoreland | Completed | Load_239020 | Paradise - 210 | Jul 7, 2026 8:45am | Jul 7, 2026 8:46am | Jul 7, 2026 9:00am | Jul 7, 2026 11:42am | Jul 7, 2026 11:42am | Jul 7, 2026 11:42am | Jul 7, 2026 11:43am | Jul 7, 2026 11:43am |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.02.06561 | C001841665 | Dwain Samuels | Westmoreland | Completed | Load_257700 | Orange Bay - 210 | Jul 7, 2026 8:45am | Jul 7, 2026 8:46am | Jul 7, 2026 9:00am | Jul 8, 2026 9:42am | Jul 8, 2026 10:26am | Jul 8, 2026 10:35am | Jul 8, 2026 10:36am | Jul 8, 2026 10:36am |  |  | Fair | No | Found working okay. Voltage check 115-116-231
Non-Outage | J.E.26.03.03203 | C001841669 | Dwain Samuels | Westmoreland | Completed | Load_268976 | Paradise - 210 | Jul 7, 2026 8:45am | Jul 7, 2026 8:46am | Jul 7, 2026 9:00am | Jul 7, 2026 10:58am | Jul 7, 2026 11:01am | Jul 7, 2026 11:13am | Jul 7, 2026 11:15am | Jul 7, 2026 11:15am |  |  | Fair | No | Corrosion found at 3 wire pole. Corrosion clear use 2 one bolt clamp. Voltage check 118-114-232
Non-Outage | J.E.26.02.24943 | C001841663 | Dwain Samuels | Westmoreland | Completed | Load_240178 | Paradise - 210 | Jul 7, 2026 8:44am | Jul 7, 2026 8:46am | Jul 7, 2026 9:00am | Jul 8, 2026 10:36am | Jul 8, 2026 10:45am | Jul 8, 2026 10:52am | Jul 8, 2026 10:53am | Jul 8, 2026 10:53am |  |  | Fair | No | Found working okay. Voltage check 118-118-236
Outage | J.E.26.07.05374 | C001841662 | Fitzroy Turner | KSAN | Completed | Load_293758 | Washington Blvd - 710 | Jul 7, 2026 8:39am | Jul 7, 2026 8:40am | Jul 7, 2026 8:51am | Jul 7, 2026 8:51am | Jul 7, 2026 10:22am | Jul 7, 2026 10:46am | Jul 7, 2026 10:46am | Jul 7, 2026 10:46am | BrokenWire |  | Fair | No | Found three wire service phase burnt off mid span use one clamp to carry out repair supply restored to customer
Outage | J.E.26.07.05282 | C001841657 | Evan Spaulding | St.Mary | Completed | Load_310056 | Highgate - 210 | Jul 7, 2026 8:29am | Jul 7, 2026 8:32am | Jul 7, 2026 8:38am | Jul 7, 2026 8:38am | Jul 7, 2026 9:31am | Jul 7, 2026 9:32am | Jul 7, 2026 9:35am | Jul 7, 2026 9:35am |  |  | Fair | No | Remove kite tails from Transformer pole and replace 2-junction fuses 1-30amps at pole number 0013117,1-15 amps at pole number 176509 and 1-5amps Transformer fuse at pole number 0013114.
Outage | J.E.26.07.05316 | C001841659 | Evan Spaulding | St.Mary | Completed | Load_262307 | Highgate - 210 | Jul 7, 2026 8:29am | Jul 7, 2026 8:32am | Jul 7, 2026 9:35am | Jul 7, 2026 9:35am | Jul 7, 2026 9:35am | Jul 7, 2026 9:36am | Jul 7, 2026 9:36am | Jul 7, 2026 9:36am |  |  | Fair | No | Associated call.
Outage | J.E.26.07.05361 | C001841658 | Nickolas Rodriques | St.Catherine | Completed | Load_557158 | Tredegar - 210 | Jul 7, 2026 8:29am | Jul 7, 2026 8:31am | Jul 7, 2026 8:36am | Jul 7, 2026 8:44am | Jul 7, 2026 9:53am | Jul 7, 2026 10:16am | Jul 7, 2026 10:19am | Jul 7, 2026 10:19am |  |  | Fair | No | Call relates to the 15 KVA transformer with hexing box attached that was found defective.
Outage | J.E.26.07.05296 | C001841656 | Evan Spaulding | St.Mary | Completed | Load_252159 | Highgate - 210 | Jul 7, 2026 8:28am | Jul 7, 2026 8:32am | Jul 7, 2026 9:36am | Jul 7, 2026 9:36am | Jul 7, 2026 9:37am | Jul 7, 2026 9:37am | Jul 7, 2026 9:37am | Jul 7, 2026 9:37am |  |  | Fair | No | Associated call.
Outage | J.E.26.07.05345 | C001841655 | Raymond Carr | St.Mary | Completed | Load_350548 | Oracabessa - 110 | Jul 7, 2026 8:28am | Jul 7, 2026 8:33am | Jul 7, 2026 8:56am | Jul 7, 2026 8:56am | Jul 7, 2026 8:56am | Jul 7, 2026 8:55am | Jul 7, 2026 8:57am | Jul 7, 2026 8:57am | Fire |  | Fair | No | Several calls to contact number went unanswered.
Outage | J.E.26.07.05351 | C001841654 | Gregory Grossett | Portland | Completed | Load_249141 | Port Antonio - 310 | Jul 7, 2026 8:28am | Jul 7, 2026 8:34am | Jul 7, 2026 9:03am | Jul 7, 2026 9:03am | Jul 7, 2026 9:20am | Jul 7, 2026 9:22am | Jul 7, 2026 9:24am | Jul 7, 2026 9:24am |  |  | Fair | No | 25 kva transformer defective and need to be replaced.please refer to Mr Devon Willis
Outage | J.E.26.07.04643 | C001841653 | Javid Vernon | Manchester | Completed | Load_302066 | Spur Tree - 310 | Jul 7, 2026 8:19am | Jul 7, 2026 8:23am | Jul 8, 2026 10:38am | Jul 8, 2026 10:38am | Jul 8, 2026 12:39pm | Jul 8, 2026 1:15pm | Jul 8, 2026 1:17pm | Jul 8, 2026 1:17pm |  |  | Fair | No | Reconnect customer pothead use three clamp voltage reading 115/115/230
Outage | J.E.26.07.05302 | C001841652 | Raymond Lewis | St.Ann | Completed | Load_257919 | Ocho Rios - 310 | Jul 7, 2026 8:17am | Jul 7, 2026 8:26am | Jul 7, 2026 11:06am | Jul 7, 2026 11:06am | Jul 7, 2026 11:06am | Jul 7, 2026 11:06am | Jul 7, 2026 11:07am | Jul 7, 2026 11:07am |  |  | Fair | No | Supply restored
Outage | J.E.26.07.05305 | C001841649 | Raymond Lewis | St.Ann | Completed | Load_237772 | Ocho Rios - 310 | Jul 7, 2026 8:16am | Jul 7, 2026 8:26am | Jul 7, 2026 8:52am | Jul 7, 2026 8:52am | Jul 7, 2026 10:25am | Jul 7, 2026 11:05am | Jul 7, 2026 11:05am | Jul 7, 2026 11:05am |  |  | Fair | No | Remove vegetation from line and Refuse and close 50 amp junction
Non-Outage | J.E.26.07.02928 | C001841646 | Orville Lee | Portmore | Completed | Load_258293 | Naggo Head - 510 | Jul 7, 2026 8:13am | Jul 7, 2026 8:13am | Jul 7, 2026 3:08pm | Jul 7, 2026 3:09pm | Jul 7, 2026 3:10pm | Jul 7, 2026 3:14pm | Jul 7, 2026 3:16pm | Jul 7, 2026 3:16pm |  |  | Fair | No | Customer connected to Rami System Customer experiencing fluctuation of voltage Refer to Moses for further inspection Customer request for a technician to visit July 08, 2026
Non-Outage | J.E.26.07.03608 | C001841645 | Orville Lee | St.Catherine | Completed | Load_264001 | Twickenham - 210 | Jul 7, 2026 8:12am | Jul 7, 2026 8:13am | Jul 8, 2026 9:15am | Jul 8, 2026 11:40am | Jul 8, 2026 11:47am | Jul 8, 2026 11:49am | Jul 8, 2026 11:53am | Jul 8, 2026 11:53am | LeaningPole |  | Fair | No | Customer reporting a pole that is shaking whenever wind blowsPole was cut and secondary line transfer to a concrete poleBottom of pole rotten and urgently need to be removed Refer to maintenance
Non-Outage | J.E.26.07.03652 | C001841644 | Orville Lee | Portmore | Completed | Load_253066 | Naggo Head - 610 | Jul 7, 2026 8:12am | Jul 7, 2026 8:13am | Jul 7, 2026 8:47am | Jul 7, 2026 9:52am | Jul 7, 2026 10:09am | Jul 7, 2026 10:16am | Jul 7, 2026 10:16am | Jul 7, 2026 10:16am |  |  | Fair | No | Meter terminals burn offVoltage 120V120V240vMeter change recommended Refer to field service
Non-Outage | J.E.26.07.03658 | C001841643 | Orville Lee | Portmore | Completed | Load_572623 | Naggo Head - 610 | Jul 7, 2026 8:11am | Jul 7, 2026 8:13am | Jul 8, 2026 9:15am | Jul 8, 2026 1:37pm | Jul 8, 2026 1:58pm | Jul 8, 2026 2:06pm | Jul 8, 2026 2:06pm | Jul 8, 2026 2:06pm |  |  | Fair | No | Premises found ok upon arrival Issue was resolved by a technician Voltage117v118237v
Non-Outage | J.E.26.07.03756 | C001841642 | Orville Lee | Portmore | Completed | Load_256476 | Naggo Head - 610 | Jul 7, 2026 8:11am | Jul 7, 2026 8:13am | Jul 8, 2026 9:15am | Jul 8, 2026 2:23pm | Jul 8, 2026 2:23pm | Jul 8, 2026 2:24pm | Jul 8, 2026 2:24pm | Jul 8, 2026 2:24pm |  |  | Fair | No | Checks made and found drop lead clamps corroded Unable to reach drop lead to change clampsDrop wire touching against transformer casing causing arcing
Non-Outage | J.E.26.07.04188 | C001841640 | Orville Lee | St.Catherine | Completed | Load_261627 | Twickenham - 210 | Jul 7, 2026 8:11am | Jul 7, 2026 8:12am | Jul 8, 2026 9:15am | Jul 8, 2026 10:54am | Jul 8, 2026 10:58am | Jul 8, 2026 11:36am | Jul 8, 2026 11:39am | Jul 8, 2026 11:39am |  |  | Fair | No | Change corroded clamps at pothead and secondary lineVoltage114vThree one bolt clamp and1 penunion
Non-Outage | J.E.26.07.04363 | C001841639 | Orville Lee | Portmore | Completed | Load_260502 | Naggo Head - 610 | Jul 7, 2026 8:11am | Jul 7, 2026 8:12am | Jul 7, 2026 9:14am | Jul 7, 2026 12:21pm | Jul 7, 2026 12:37pm | Jul 7, 2026 1:02pm | Jul 7, 2026 1:06pm | Jul 7, 2026 1:06pm |  |  | Fair | No | Checks made and found pothead connection corroded 1one bolt clamp and 1 Penn union used Voltag119v120v240v
Non-Outage | J.E.26.07.04370 | C001841638 | Orville Lee | St.Catherine | Completed | Load_576216 | Twickenham - 210 | Jul 7, 2026 8:11am | Jul 7, 2026 8:12am | Jul 8, 2026 9:15am | Jul 8, 2026 9:16am | Jul 8, 2026 10:07am | Jul 8, 2026 10:13am | Jul 8, 2026 10:15am | Jul 8, 2026 10:15am |  |  | Fair | No | Premises closedCall to customer unanswered Meter closed behind grill
Non-Outage | J.E.26.07.04650 | C001841637 | Orville Lee | Portmore | Completed | Load_266600 | Naggo Head - 610 | Jul 7, 2026 8:11am | Jul 7, 2026 8:12am | Jul 7, 2026 8:49am | Jul 7, 2026 11:19am | Jul 7, 2026 11:39am | Jul 7, 2026 12:18pm | Jul 7, 2026 12:19pm | Jul 7, 2026 12:19pm |  |  | Fair | No | Checks made and found service wire disconnected from secondary line Service wire reconnected Voltage115v116v231v
Non-Outage | J.E.26.07.04683 | C001841636 | Orville Lee | Portmore | Completed | Load_238762 | Naggo Head - 510 | Jul 7, 2026 8:10am | Jul 7, 2026 8:12am | Jul 7, 2026 9:14am | Jul 7, 2026 9:16am | Jul 7, 2026 9:36am | Jul 7, 2026 9:49am | Jul 7, 2026 9:49am | Jul 7, 2026 9:49am |  |  | Fair | No | Customer mentioned that he was making a report for his mom premises at Clarendon Premises in Portmore voltage ok upon arrival Voltage 116V117V234V
Non-Outage | J.E.26.07.04806 | C001841635 | Orville Lee | St.Catherine | Completed | Load_264001 | Twickenham - 210 | Jul 7, 2026 8:10am | Jul 7, 2026 8:12am | Jul 8, 2026 9:15am | Jul 8, 2026 10:19am | Jul 8, 2026 10:21am | Jul 8, 2026 10:48am | Jul 8, 2026 10:50am | Jul 8, 2026 10:50am |  |  | Fair | No | Pothead connection corroded 1 one bolt clamp 1 Penn union usedVoltage 115v
Non-Outage | J.E.26.07.04886 | C001841634 | Orville Lee | St.Catherine | Completed | Load_268709 | Twickenham - 210 | Jul 7, 2026 8:10am | Jul 7, 2026 8:12am | Jul 8, 2026 9:15am | Jul 8, 2026 11:53am | Jul 8, 2026 12:14pm | Jul 8, 2026 12:24pm | Jul 8, 2026 12:24pm | Jul 8, 2026 12:24pm |  |  | Fair | No | Premise closed Customer number not assigned Meter closed behind grill
Non-Outage | J.E.26.07.05029 | C001841633 | Orville Lee | St.Catherine | Completed | Load_270044 | Twickenham - 210 | Jul 7, 2026 8:10am | Jul 7, 2026 8:12am | Jul 7, 2026 3:57pm | Jul 7, 2026 3:57pm | Jul 7, 2026 4:08pm | Jul 7, 2026 4:29pm | Jul 7, 2026 4:30pm | Jul 7, 2026 4:30pm |  |  | Fair | No | Refer to bucket truck Unable to reach secondary line and transformer drop leadVoltage 105V115V
Non-Outage | J.E.26.06.17779 | C001841631 | Fredrick Hamilton | null | Completed | null | null | Jul 7, 2026 8:09am | Jul 7, 2026 8:09am | Jul 7, 2026 8:16am | Jul 7, 2026 8:28am | Jul 7, 2026 8:28am | Jul 7, 2026 8:30am | Jul 7, 2026 8:30am | Jul 7, 2026 8:30am |  |  | Fair | No | Customer contacted and stated that power was restored fully previously Premises is ok
Non-Outage | J.E.26.07.05166 | C001841630 | Orville Lee | Portmore | Completed | Load_255528 | Naggo Head - 510 | Jul 7, 2026 8:09am | Jul 7, 2026 8:12am | Jul 7, 2026 1:42pm | Jul 7, 2026 1:42pm | Jul 7, 2026 2:04pm | Jul 7, 2026 2:12pm | Jul 7, 2026 2:13pm | Jul 7, 2026 2:13pm |  |  | Fair | No | Customer reporting defective street light that flicker on Dodge rd
Non-Outage | J.E.26.07.05225 | C001841629 | Orville Lee | Portmore | Completed | Load_258761 | Naggo Head - 610 | Jul 7, 2026 8:08am | Jul 7, 2026 8:12am | Jul 7, 2026 8:48am | Jul 7, 2026 10:47am | Jul 7, 2026 10:53am | Jul 7, 2026 11:18am | Jul 7, 2026 11:19am | Jul 7, 2026 11:19am |  |  | Fair | No | Checks made and found pothead connection corroded 2 pen union and 1one bolt clamp usedVoltage119v120v240v
Non-Outage | J.E.26.07.05253 | C001841628 | Orville Lee | Portmore | Completed | Load_260624 | Naggo Head - 610 | Jul 7, 2026 8:08am | Jul 7, 2026 8:12am | Jul 7, 2026 8:48am | Jul 7, 2026 10:22am | Jul 7, 2026 10:27am | Jul 7, 2026 10:46am | Jul 7, 2026 10:46am | Jul 7, 2026 10:46am |  |  | Fair | No | Customer mentioned that they saw sparks coming from the connection of the transformer on pole 618613Upon arrival no sparks seen and joint connection seem okVoltage 119V120V240V
Non-Outage | J.E.26.07.04306 | C001841627 | Rochaine Hussey | KSAN | Completed | Load_269774 | Constant Spring - 410 | Jul 7, 2026 8:07am | Jul 7, 2026 8:07am | Jul 7, 2026 1:57pm | Jul 7, 2026 3:02pm | Jul 7, 2026 3:02pm | Jul 7, 2026 3:02pm | Jul 7, 2026 3:03pm | Jul 7, 2026 3:03pm |  |  | Fair | No | Customer said issue was already resolved
Non-Outage | J.E.26.06.38864 | C001841626 | Ryan Richards | Manchester | Completed | Load_245911 | Kendal - 310 | Jul 7, 2026 8:06am | Jul 7, 2026 8:08am | Jul 7, 2026 9:06am | Jul 7, 2026 10:06am | Jul 7, 2026 11:19am | Jul 7, 2026 1:30pm | Jul 7, 2026 1:30pm | Jul 7, 2026 1:30pm |  |  | Fair | No | Corroded phase and neutral Found remade pothead and pole and still getting low voltage power transformer in open bank was checked and 112 coming from the lead transformer suspected to be defective fallow up need to down by maintenance crew
Non-Outage | J.E.26.07.03777 | C001841623 | Hopeton Henry | St.Thomas | Completed | Load_263546 | Good Year - 110 | Jul 7, 2026 8:03am | Jul 7, 2026 8:36am | Jul 7, 2026 9:01am | Jul 7, 2026 10:56am | Jul 7, 2026 10:56am | Jul 7, 2026 10:57am | Jul 7, 2026 10:58am | Jul 7, 2026 10:58am |  |  | Fair | No | Transformer was replaced by maintenance crew
Non-Outage | J.E.26.07.04703 | C001841624 | Hopeton Henry | St.Thomas | Completed | Load_350229 | Good Year - 210 | Jul 7, 2026 8:03am | Jul 7, 2026 8:37am | Jul 7, 2026 9:01am | Jul 7, 2026 12:50pm | Jul 7, 2026 4:31pm | Jul 7, 2026 6:15pm | Jul 7, 2026 6:16pm | Jul 7, 2026 6:16pm |  |  | Fair | No | Change defective service wire 20 ft 3 clamps 115-115-230 volts
Outage | J.E.26.07.04548 | C001841622 | Richard Grant | St.Catherine | Completed | Load_239883 | New Michelton - 210 | Jul 7, 2026 8:02am | Jul 7, 2026 8:03am | Jul 7, 2026 12:03pm | Jul 7, 2026 12:04pm | Jul 7, 2026 1:49pm | Jul 7, 2026 2:38pm | Jul 7, 2026 2:38pm | Jul 7, 2026 2:38pm | BrokenWire |  | Fair | No | 25kva transformer found isolated and 2 pole span of opened secondary lower phase and neutral found caused by fire by sugar cane worker. 4 preform, 3 onebolt clamps, 4 sleeves, approximately 200ft #2 and approximately 100ft 2/0 wire used to retention line. Supply restored and area left okay
Outage | J.E.26.07.05357 | C001841621 | Richard Grant | St.Catherine | Completed | Load_258785 | New Michelton - 310 | Jul 7, 2026 8:00am | Jul 7, 2026 8:01am | Jul 7, 2026 9:45am | Jul 7, 2026 12:02pm | Jul 7, 2026 12:02pm | Jul 7, 2026 12:03pm | Jul 7, 2026 12:03pm | Jul 7, 2026 12:03pm |  |  | Fair | No | 8amps and 5amps fuse found blown for single phase junction and 50kva transformer, respectively, caused by wisp growing onto tranx switch bottom droplead. Wisp removed, fuses replaced with same and placed back respective switches. Supply restored and area left okay.
Non-Outage | J.E.26.07.04761 | C001841617 | Tyrese Williams | St.Ann | Completed | Load_258297 | Cardiff Hall - 210 | Jul 7, 2026 7:56am | Jul 7, 2026 8:39am | Jul 7, 2026 8:43am | Jul 7, 2026 10:16am | Jul 7, 2026 11:00am | Jul 7, 2026 11:03am | Jul 7, 2026 11:04am | Jul 7, 2026 11:04am |  |  | Fair | No | Premises found ok customer said she didn’t make any report
Non-Outage | J.E.26.07.04767 | C001841619 | Tyrese Williams | St.Ann | Completed | Load_268918 | Cardiff Hall - 210 | Jul 7, 2026 7:56am | Jul 7, 2026 8:39am | Jul 7, 2026 8:43am | Jul 7, 2026 9:06am | Jul 7, 2026 10:04am | Jul 7, 2026 10:16am | Jul 7, 2026 10:16am | Jul 7, 2026 10:16am |  |  | Fair | No | Premises not found not getting customer on phone
Non-Outage | J.E.26.07.04858 | C001841618 | Oraine Minto | St.Ann | Completed | Load_249379 | Roaring River - 210 | Jul 7, 2026 7:56am | Jul 7, 2026 7:56am | Jul 7, 2026 1:29pm | Jul 7, 2026 5:21pm | Jul 7, 2026 5:21pm | Jul 7, 2026 5:21pm | Jul 7, 2026 5:22pm | Jul 7, 2026 5:22pm |  |  | Fair | No | 222v 111v 110v issue resolved at premises
Non-Outage | J.E.26.07.05008 | C001841620 | Oraine Minto | St.Ann | Completed | Load_264883 | Ocho Rios - 510 | Jul 7, 2026 7:56am | Jul 7, 2026 7:56am | Jul 7, 2026 1:10pm | Jul 7, 2026 1:14pm | Jul 7, 2026 1:14pm | Jul 7, 2026 1:15pm | Jul 7, 2026 1:16pm | Jul 7, 2026 1:16pm |  |  | Fair | No | 237v 117v 118v
Non-Outage | J.E.26.07.04710 | C001841616 | Oraine Minto | St.Ann | Completed | Load_242953 | Roaring River - 410 | Jul 7, 2026 7:55am | Jul 7, 2026 7:56am | Jul 8, 2026 11:08am | Jul 8, 2026 11:28am | Jul 8, 2026 11:28am | Jul 8, 2026 11:29am | Jul 8, 2026 11:29am | Jul 8, 2026 11:29am |  |  | Fair | No | Premises not found an customer number not working
Outage | J.E.26.07.05277 | C001841615 | Oshane Warren | Westmoreland | Completed | Load_574993 | Paradise - 210 | Jul 7, 2026 7:54am | Jul 7, 2026 7:57am | Jul 7, 2026 11:31am | Jul 7, 2026 11:31am | Jul 7, 2026 11:31am | Jul 7, 2026 11:32am | Jul 7, 2026 11:32am | Jul 7, 2026 11:32am |  |  | Fair | No | Reclose 20amp junction trip saver
Outage | J.E.26.07.05289 | C001841614 | Oshane Warren | Hanover | Completed | Load_245791 | Orange Bay - 310 | Jul 7, 2026 7:54am | Jul 7, 2026 7:57am | Jul 7, 2026 8:05am | Jul 7, 2026 8:05am | Jul 7, 2026 11:23am | Jul 7, 2026 11:27am | Jul 7, 2026 11:27am | Jul 7, 2026 11:27am |  |  | Fair | No | Reclose 20 amp junction trip saver
Outage | J.E.26.07.05342 | C001841613 | Oshane Warren | Westmoreland | Completed | Load_264741 | Paradise - 210 | Jul 7, 2026 7:54am | Jul 7, 2026 7:57am | Jul 7, 2026 11:30am | Jul 7, 2026 11:30am | Jul 7, 2026 11:30am | Jul 7, 2026 11:30am | Jul 7, 2026 11:31am | Jul 7, 2026 11:31am |  |  | Fair | No | Reclose 20amp junction trip saver
Outage | J.E.26.07.05193 | C001841611 | Floyd Taylor | Trelawny | Completed | Load_260052 | Greenwood - 110 | Jul 7, 2026 7:52am | Jul 7, 2026 7:52am | Jul 7, 2026 8:07am | Jul 7, 2026 8:08am | Jul 7, 2026 8:39am | Jul 7, 2026 8:54am | Jul 7, 2026 8:55am | Jul 7, 2026 8:55am |  |  | Fair | No | Premises locked no one at premises
Outage | J.E.26.07.04896 | C001841610 | Damion Reid | Manchester | Completed | Load_240305 | Spur Tree - 210 | Jul 7, 2026 7:50am | Jul 7, 2026 7:51am | Jul 7, 2026 11:32am | Jul 7, 2026 11:32am | Jul 7, 2026 12:40pm | Jul 7, 2026 1:18pm | Jul 7, 2026 1:23pm | Jul 7, 2026 1:23pm | BangingWires |  | SevereWind | No | Customer is with power however three phase of primary conductor need to retention whenever severe wind blows they bang together
Non-Outage | J.E.26.07.04799 | C001841608 | Fredrick Hamilton | KSAN | Completed | Load_257446 | Constant Spring - 210 | Jul 7, 2026 7:49am | Jul 7, 2026 7:50am | Jul 7, 2026 7:56am | Jul 7, 2026 9:42am | Jul 7, 2026 9:42am | Jul 7, 2026 9:45am | Jul 7, 2026 9:45am | Jul 7, 2026 9:45am |  |  | Fair | No | Customer contacted and stated that power was restored fully previously Premises is ok
Non-Outage | J.E.26.04.09330 | C001841607 | Derrick Dawkins | St.James | Completed | Load_245469 | Bogue - 310 | Jul 7, 2026 7:47am | Jul 7, 2026 7:47am | Jul 7, 2026 9:45am | Jul 7, 2026 9:45am | Jul 7, 2026 10:11am | Jul 7, 2026 10:12am | Jul 7, 2026 10:12am | Jul 7, 2026 10:12am |  |  | Fair | No | Premises checked and found ok
Non-Outage | J.E.26.04.12962 | C001841606 | Derrick Dawkins | St.James | Completed | Load_301824 | Bogue - 310 | Jul 7, 2026 7:47am | Jul 7, 2026 7:47am | Jul 7, 2026 8:11am | Jul 7, 2026 8:15am | Jul 7, 2026 9:21am | Jul 7, 2026 8:46am | Jul 7, 2026 9:45am | Jul 7, 2026 9:45am |  |  | Fair | No | Checked and found ok
Non-Outage | J.E.26.04.14150 | C001841605 | Derrick Dawkins | St.James | Completed | Load_242526 | Bogue - 310 | Jul 7, 2026 7:47am | Jul 7, 2026 7:47am | Jul 7, 2026 10:12am | Jul 7, 2026 10:12am | Jul 7, 2026 10:17am | Jul 7, 2026 10:17am | Jul 7, 2026 10:18am | Jul 7, 2026 10:18am |  |  | Fair | No | Premises found ok customer stated he did not make a report
Non-Outage | J.E.26.07.02537 | C001841604 | Derrick Dawkins | St.James | Completed | Load_576009 | Bogue - 310 | Jul 7, 2026 7:46am | Jul 7, 2026 7:47am | Jul 7, 2026 10:19am | Jul 7, 2026 10:19am | Jul 7, 2026 10:49am | Jul 7, 2026 10:51am | Jul 7, 2026 10:51am | Jul 7, 2026 10:51am |  |  | Fair | No | Only customer in the hexing box experiencing single phasing refer back to field service kadian
Non-Outage | J.E.26.07.04954 | C001841603 | Derrick Dawkins | St.James | Completed | Load_555850 | Bogue - 310 | Jul 7, 2026 7:46am | Jul 7, 2026 7:47am | Jul 7, 2026 10:52am | Jul 7, 2026 10:52am | Jul 7, 2026 11:05am | Jul 7, 2026 11:07am | Jul 7, 2026 11:07am | Jul 7, 2026 11:07am |  |  | Fair | No | Only customer out of the EG box experiencing single phasing refer back to field service kadian
Non-Outage | J.E.26.02.41611 | C001841602 | Barrington Brown | St.James | Completed | Load_568774 | Rose Hall - 210 | Jul 7, 2026 7:45am | Jul 7, 2026 7:45am | Jul 7, 2026 9:45am | Jul 7, 2026 9:46am | Jul 7, 2026 10:15am | Jul 7, 2026 10:49am | Jul 7, 2026 10:49am | Jul 7, 2026 10:49am |  |  | Fair | No | Checked and found ok issue was resolved.
Non-Outage | J.E.26.03.46308 | C001841599 | Barrington Brown | St.James | Completed | Load_248508 | Rose Hall - 210 | Jul 7, 2026 7:43am | Jul 7, 2026 7:43am | Jul 7, 2026 12:46pm | Jul 7, 2026 12:46pm | Jul 7, 2026 2:48pm | Jul 7, 2026 2:53pm | Jul 7, 2026 2:53pm | Jul 7, 2026 2:53pm | Fire |  | Fair | No | Checked and found ok. However found several rotten and leaning poles on location. Please refer to maintenance department to have pole changed. Several are being held by customer service wires
Non-Outage | J.E.26.04.09281 | C001841600 | Barrington Brown | St.James | Completed | Load_263264 | Rose Hall - 210 | Jul 7, 2026 7:43am | Jul 7, 2026 7:43am | Jul 7, 2026 10:49am | Jul 7, 2026 10:49am | Jul 7, 2026 11:06am | Jul 7, 2026 12:45pm | Jul 7, 2026 12:45pm | Jul 7, 2026 12:45pm | LeaningPole |  | Fair | No | Crew found leaning old Jps pole not in use. Crew removed pole making area safe.
Non-Outage | J.E.26.07.01557 | C001841601 | Hopeton Henry | St.Thomas | Completed | Load_252941 | Good Year - 110 | Jul 7, 2026 7:43am | Jul 7, 2026 7:43am | Jul 7, 2026 8:10am | Jul 7, 2026 10:58am | Jul 7, 2026 11:30am | Jul 7, 2026 12:44pm | Jul 7, 2026 12:47pm | Jul 7, 2026 12:47pm | Fire |  | Fair | No | Found ok
Outage | J.E.26.06.01165 | C001841596 | Javid Vernon | Westmoreland | Completed | Load_240510 | Paradise - 310 | Jul 7, 2026 7:41am | Jul 7, 2026 7:44am | Jul 7, 2026 12:29pm | Jul 7, 2026 12:29pm | Jul 7, 2026 12:47pm | Jul 7, 2026 1:23pm | Jul 7, 2026 1:24pm | Jul 7, 2026 1:24pm |  |  | Fair | No | Splice and retention customer service wire use 10ft #6 triplex wire and three clamps voltage reading 116/114/230
Outage | J.E.26.06.02052 | C001841595 | Javid Vernon | Westmoreland | Completed | Load_258767 | Paradise - 310 | Jul 7, 2026 7:41am | Jul 7, 2026 7:44am | Jul 7, 2026 7:49am | Jul 7, 2026 7:49am | Jul 7, 2026 8:45am | Jul 7, 2026 9:20am | Jul 7, 2026 9:20am | Jul 7, 2026 9:20am |  |  | Fair | No | Replace 100 ft #6 triplex wire and use 6 clamp voltage reading 115/113/228
Outage | J.E.26.06.22493 | C001841594 | Javid Vernon | Westmoreland | Completed | Load_246302 | null | Jul 7, 2026 7:41am | Jul 7, 2026 7:44am | Jul 7, 2026 1:25pm | Jul 7, 2026 1:25pm | Jul 7, 2026 2:30pm | Jul 7, 2026 2:48pm | Jul 7, 2026 2:50pm | Jul 7, 2026 2:50pm |  |  | Fair | No | Area check and found okay unable to locate customer and premises with directions given phone calls to customer number went unanswered
Non-Outage | J.E.25.12.08020 | C001841593 | Romeo Brissett | St.James | Completed | Load_264951 | Bogue - 610 | Jul 7, 2026 7:39am | Jul 7, 2026 7:40am | Jul 7, 2026 9:09am | Jul 7, 2026 9:09am | Jul 7, 2026 9:23am | Jul 7, 2026 9:58am | Jul 7, 2026 9:59am | Jul 7, 2026 9:59am |  |  | Fair | No | Removed illegal connections and Retention one span of sys Neutral. Used (1)#2 preformed
Non-Outage | J.E.26.07.01243 | C001841588 | Romeo Brissett | St.James | Completed | Load_292578 | Bogue - 610 | Jul 7, 2026 7:37am | Jul 7, 2026 7:37am | Jul 7, 2026 8:10am | Jul 7, 2026 8:10am | Jul 7, 2026 8:28am | Jul 7, 2026 9:00am | Jul 7, 2026 9:09am | Jul 7, 2026 9:09am |  |  | Fair | No | Check and found internal fault, V/R 114-116-230. Customer was advised.
Outage | J.E.26.07.05112 | C001841587 | Tajay Bernard | Hanover | Completed | Load_265902 | Orange Bay - 310 | Jul 7, 2026 7:36am | Jul 7, 2026 7:36am | Jul 7, 2026 9:41am | Jul 7, 2026 9:41am | Jul 7, 2026 9:42am | Jul 7, 2026 9:42am | Jul 7, 2026 9:42am | Jul 7, 2026 9:42am |  |  | Fair | No | Customer stated that the issues has been resolved
Outage | J.E.26.07.05015 | C001841584 | Stephen Taylor | St.Thomas | Completed | Load_261497 | Lysson - 410 | Jul 7, 2026 7:35am | Jul 7, 2026 7:35am | Jul 7, 2026 11:19am | Jul 7, 2026 11:19am | Jul 7, 2026 11:19am | Jul 7, 2026 11:27am | Jul 7, 2026 11:34am | Jul 7, 2026 11:34am |  |  | Fair | No | Class 4 secondary pole need to straighten urgent
Outage | J.E.26.07.05024 | C001841586 | Stephen Taylor | St.Thomas | Completed | Load_269881 | Lysson - 410 | Jul 7, 2026 7:35am | Jul 7, 2026 7:35am | Jul 7, 2026 7:51am | Jul 7, 2026 7:51am | Jul 7, 2026 8:55am | Jul 7, 2026 8:55am | Jul 7, 2026 9:18am | Jul 7, 2026 9:18am |  |  | Fair | No | See trip saver out no number on pole patrol and see 3 span of primary line on the ground tree drop on line need assistance of jps maintenance team
Non-Outage | J.E.26.07.04658 | C001841583 | Rayon Foster | Hanover | Completed | Load_259222 | Orange Bay - 310 | Jul 7, 2026 7:34am | Jul 7, 2026 7:36am | Jul 7, 2026 8:15am | Jul 7, 2026 8:15am | Jul 7, 2026 8:46am | Jul 7, 2026 10:38am | Jul 7, 2026 10:38am | Jul 7, 2026 10:38am |  |  | Fair | No | Open 1 50kva transformer to repair damaged drop lead using 4 one bolt clamps and 7 feet of 2/0 copper wire and top up transformer from top 4 to top five voltage after repair at transformer pole 119/119AB238 voltage in customer meter socket 111/110AB221 volts
Outage | J.E.26.07.05131 | C001841582 | Elvis Trowers | KSAN | Completed | Load_263454 | Washington Blvd - 610 | Jul 7, 2026 7:33am | Jul 7, 2026 7:43am | Jul 7, 2026 9:29am | Jul 7, 2026 9:29am | Jul 7, 2026 9:49am | Jul 7, 2026 11:01am | Jul 7, 2026 11:02am | Jul 7, 2026 11:02am |  |  | Fair | Yes | Customers was found without electricity supply when checked and defective twisted wire was found, about 80’ feet of #6 triplex and 6 one bolt clamps was used to install defective wire, voltage when checked was left at 119+121=240 volts.
Non-Outage | J.E.26.07.03244 | C001841581 | Romeo Brissett | St.James | Completed | Load_262140 | Bogue - 610 | Jul 7, 2026 7:32am | Jul 7, 2026 7:32am | Jul 7, 2026 7:37am | Jul 7, 2026 7:37am | Jul 7, 2026 7:37am | Jul 7, 2026 8:08am | Jul 7, 2026 8:10am | Jul 7, 2026 8:10am | BrokenWire |  | Fair | No | Found customer service crystallized and contaminated, installed 100ft of #6, V/R 120-121-242
Outage | J.E.26.07.05318 | C001841580 | Richard Nicholas | St.Catherine | Completed | Load_238835 | Rhodens Pen - 310 | Jul 7, 2026 7:29am | Jul 7, 2026 7:30am | Jul 7, 2026 8:15am | Jul 7, 2026 8:16am | Jul 7, 2026 11:54am | Jul 7, 2026 12:05pm | Jul 7, 2026 12:07pm | Jul 7, 2026 12:07pm |  |  | Fair | No | Premises checked and found ok,voltage reading taking at meter socket,115,116 and 231v.customer advised to get private electrician to do internal checks.
Outage | J.E.26.07.04639 | C001841579 | Richard Nicholas | St.Catherine | Completed | Load_252827 | Rhodens Pen - 210 | Jul 7, 2026 7:28am | Jul 7, 2026 7:30am | Jul 7, 2026 1:39pm | Jul 7, 2026 1:39pm | Jul 7, 2026 2:55pm | Jul 7, 2026 4:02pm | Jul 7, 2026 4:05pm | Jul 7, 2026 4:05pm |  |  | Fair | No | Defective service wire detected,same was removed and 110ft of new #6 triplex installed,3 clamp and 3 linket.voltage reading 108,110 and 218v.
Outage | J.E.26.07.04580 | C001841578 | Richard Grant | St.Catherine | Completed | Load_243610 | New Michelton - 210 | Jul 7, 2026 7:27am | Jul 7, 2026 7:27am | Jul 7, 2026 12:03pm | Jul 7, 2026 2:39pm | Jul 7, 2026 2:40pm | Jul 7, 2026 2:41pm | Jul 7, 2026 2:41pm | Jul 7, 2026 2:41pm | BrokenWire |  | Fair | No | 25kva transformer found isolated and 2 pole span of opened secondary lower phase and neutral found caused by fire by sugar cane worker. 4 preform, 3 onebolt clamps, 4 sleeves, approximately 200ft #2 and approximately 100ft 2/0 wire used to retention line. Supply restored and area left okay
Outage | J.E.26.07.05256 | C001841577 | Tajay Bernard | St.James | Completed | Load_249506 | Bogue - 510 | Jul 7, 2026 7:27am | Jul 7, 2026 7:29am | Jul 7, 2026 9:59am | Jul 7, 2026 9:59am | Jul 7, 2026 10:02am | Jul 7, 2026 10:03am | Jul 7, 2026 10:03am | Jul 7, 2026 10:03am |  |  | Fair | No | This call belongs to st james
Outage | J.E.26.07.05334 | C001841576 | Tajay Bernard | St.James | Completed | Load_269275 | Bogue - 510 | Jul 7, 2026 7:26am | Jul 7, 2026 7:26am | Jul 7, 2026 11:32am | Jul 7, 2026 11:32am | Jul 7, 2026 11:32am | Jul 7, 2026 11:33am | Jul 7, 2026 11:33am | Jul 7, 2026 11:33am |  |  | Fair | No | Customer stated that powers was restored
Outage | J.E.26.07.05319 | C001841574 | Tajay Bernard | St.James | Completed | Load_573360 | Bogue - 510 | Jul 7, 2026 7:24am | Jul 7, 2026 9:23am | Jul 7, 2026 11:36am | Jul 7, 2026 11:36am | Jul 7, 2026 11:36am | Jul 7, 2026 11:36am | Jul 7, 2026 11:36am | Jul 7, 2026 11:36am |  |  | Fair | No | Customer stated that powers was restored
Outage | J.E.26.07.05328 | C001841575 | Tajay Bernard | St.James | Completed | Load_573363 | Bogue - 510 | Jul 7, 2026 7:24am | Jul 7, 2026 7:24am | Jul 7, 2026 11:36am | Jul 7, 2026 11:36am | Jul 7, 2026 11:37am | Jul 7, 2026 11:37am | Jul 7, 2026 11:37am | Jul 7, 2026 11:37am |  |  | Fair | No | Customer stated that powers was restored
Outage | J.E.26.07.04815 | C001841573 | Javid Vernon | Westmoreland | Completed | Load_241093 | Paradise - 310 | Jul 7, 2026 7:23am | Jul 7, 2026 7:24am | Jul 7, 2026 11:26am | Jul 7, 2026 11:26am | Jul 7, 2026 11:54am | Jul 7, 2026 12:27pm | Jul 7, 2026 12:29pm | Jul 7, 2026 12:29pm |  |  | Fair | No | Customer requesting a reconnection of 25kva transformer switch top to the main line and 100ft of #2 triplex wire and a meter replacement customer needs urgent assistance refer to operation and field service
Outage | J.E.26.07.05340 | C001841572 | Tajay Bernard | St.James | Completed | Load_1001253 | Bogue - 510 | Jul 7, 2026 7:23am | Jul 7, 2026 7:24am | Jul 7, 2026 11:33am | Jul 7, 2026 11:33am | Jul 7, 2026 11:33am | Jul 7, 2026 11:35am | Jul 7, 2026 11:35am | Jul 7, 2026 11:35am |  |  | Fair | No | Customer stated that powers was restored
Outage | J.E.26.07.05226 | C001841570 | Neville Spencer | Clarendon | Completed | Load_241583 | May Pen - 110 | Jul 7, 2026 7:17am | Jul 7, 2026 7:17am | Jul 7, 2026 7:33am | Jul 7, 2026 7:33am | Jul 7, 2026 9:50am | Jul 7, 2026 10:52am | Jul 7, 2026 10:52am | Jul 7, 2026 10:52am |  |  | Fair | No | Repair defective joints at secondary and pothead on 3, wire service used 1, clamp, 3, 6/6 sleeves voltage 111 113 224 supply restored.
Outage | J.E.26.07.04976 | C001841568 | Moses Elliston | St.Catherine | Completed | Load_269801 | Twickenham - 210 | Jul 7, 2026 7:14am | Jul 7, 2026 10:12am | Jul 7, 2026 10:39am | Jul 7, 2026 10:39am | Jul 7, 2026 10:39am | Jul 7, 2026 10:41am | Jul 7, 2026 10:42am | Jul 7, 2026 10:42am |  |  | Fair | No | Supply reconnected.Power cut was in area.
Outage | J.E.26.07.05258 | C001841566 | Wan Carlos Scarlett | Portmore | Completed | Load_257047 | Naggo Head - 610 | Jul 7, 2026 7:14am | Jul 7, 2026 7:15am | Jul 7, 2026 7:31am | Jul 7, 2026 9:32am | Jul 7, 2026 9:54am | Jul 7, 2026 10:18am | Jul 7, 2026 10:19am | Jul 7, 2026 10:19am |  |  | Fair | No | Call related to defective transformer Roy Brown is aware of the situation
Outage | J.E.26.07.05333 | C001841565 | Gregory Grossett | Portland | Completed | Load_249641 | Port Antonio - 310 | Jul 7, 2026 7:06am | Jul 7, 2026 7:07am | Jul 7, 2026 7:59am | Jul 7, 2026 7:59am | Jul 7, 2026 8:39am | Jul 7, 2026 8:58am | Jul 7, 2026 9:03am | Jul 7, 2026 9:03am |  | Y | Fair | No | 50 kva transformer fuse blown at pole number 013374 , cause by tree limb fall on line, clear and restore line section, material used 1-5 amps fuse.
Non-Outage | J.E.26.07.05081 | C001841563 | Edward Royal | KSAN | Completed | Load_573987 | Washington Blvd - 410 | Jul 7, 2026 7:03am | Jul 7, 2026 7:34am | Jul 7, 2026 8:30am | Jul 7, 2026 8:30am | Jul 7, 2026 8:30am | Jul 7, 2026 8:32am | Jul 7, 2026 8:32am | Jul 7, 2026 8:32am |  |  | Fair | No | Related to transformer drop lead that burn off from last night
Outage | J.E.26.07.05285 | C001841556 | Raymond Lewis | St.Ann | Completed | Load_269944 | Roaring River - 210 | Jul 7, 2026 6:18am | Jul 7, 2026 8:36am | Jul 7, 2026 3:08pm | Jul 7, 2026 3:08pm | Jul 7, 2026 3:26pm | Jul 7, 2026 3:28pm | Jul 7, 2026 3:28pm | Jul 7, 2026 3:28pm |  |  | Fair | No | Refuse and close 20 amp junction
Outage | J.E.26.07.05261 | C001841541 | Rusean Allen | KSAS | Completed | Load_242427 | Duhaney - 310 | Jul 7, 2026 2:39am | Jul 7, 2026 4:22am | null | null | null | Jul 7, 2026 7:24am | Jul 7, 2026 7:25am | Jul 7, 2026 7:23am |  |  | Fair | No | Related to cleopatra ave
Outage | J.E.26.07.04390 | C001841535 | Moses Elliston | St.Catherine | Completed | Load_270195 | Tredegar - 410 | Jul 7, 2026 1:35am | Jul 7, 2026 2:41am | Jul 7, 2026 9:14am | Jul 7, 2026 9:14am | Jul 7, 2026 9:14am | Jul 6, 2026 1:29pm | Jul 7, 2026 9:22am | Jul 7, 2026 9:22am |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.07.05180 | C001841528 | Rusean Allen | KSAS | Completed | Load_259445 | Rockfort - 410 | Jul 7, 2026 12:21am | Jul 7, 2026 12:22am | Jul 7, 2026 8:59am | Jul 7, 2026 8:59am | Jul 7, 2026 9:54am | Jul 7, 2026 9:58am | Jul 7, 2026 9:59am | Jul 7, 2026 9:59am |  |  | Fair | No | Meter has been disconnected from 2021, irregularity was also found at meter socket. Meter was removed from premises.
Outage | J.E.26.07.05250 | C001841527 | Rusean Allen | KSAS | Completed | Load_257407 | Duhaney - 310 | Jul 7, 2026 12:21am | Jul 7, 2026 12:22am | Jul 7, 2026 4:25am | Jul 7, 2026 4:26am | Jul 7, 2026 5:01am | Jul 7, 2026 6:25am | Jul 7, 2026 6:25am | Jul 7, 2026 6:25am |  |  | Fair | No | 1x 50amp fuse found 1x 50amp fuse replaced
Outage | J.E.26.07.05241 | C001841526 | Rusean Allen | KSAS | Completed | Load_242427 | Duhaney - 310 | Jul 7, 2026 12:20am | Jul 7, 2026 5:32am | Jul 7, 2026 5:33am | null | null | Jul 7, 2026 7:22am | Jul 7, 2026 7:22am | Jul 7, 2026 7:20am |  |  | Fair | No | Related to cleopatra ave
Outage | J.E.26.07.05243 | C001841525 | Rusean Allen | KSAS | Completed | Load_242830 | Duhaney - 310 | Jul 7, 2026 12:20am | Jul 7, 2026 4:45am | Jul 7, 2026 4:47am | null | null | Jul 7, 2026 7:20am | Jul 7, 2026 7:20am | Jul 7, 2026 7:18am | TreeContact |  | Fair | No | Related
Outage | J.E.26.07.05244 | C001841522 | Swon Miller | St.James | Completed | Load_573348 | Bogue - 510 | Jul 6, 2026 11:51pm | Jul 7, 2026 12:16am | Jul 7, 2026 1:46am | Jul 7, 2026 1:46am | Jul 7, 2026 3:28am | Jul 14, 2026 3:37am | Jul 7, 2026 3:38am | Jul 7, 2026 3:38am |  |  | Fair | No | Found 1,25 kva transformer defective needs replacing voltage found 0.000 voltage left 0’000 please refer to operations/kerron frazier
Outage | J.E.26.07.05077 | C001841517 | Rusean Allen | KSAN | Completed | Load_257208 | Constant Spring - 310 | Jul 6, 2026 11:16pm | Jul 6, 2026 11:16pm | Jul 6, 2026 11:25pm | Jul 6, 2026 11:25pm | Jul 7, 2026 12:09am | Jul 7, 2026 12:09am | Jul 7, 2026 12:10am | Jul 7, 2026 12:10am |  |  | Fair | No | Found okay
Outage | J.E.26.07.05124 | C001841516 | Rusean Allen | KSAN | Completed | Load_257166 | Hope - 510 | Jul 6, 2026 11:15pm | Jul 6, 2026 11:16pm | Jul 7, 2026 12:10am | Jul 7, 2026 12:10am | Jul 7, 2026 12:24am | Jul 7, 2026 12:25am | Jul 7, 2026 12:25am | Jul 7, 2026 12:25am |  |  | Fair | No | Meter was reconnected by customer service.
Outage | J.E.26.07.05231 | C001841515 | Christopher Edwards | KSAN | Completed | Load_269049 | Constant Spring - 410 | Jul 6, 2026 11:15pm | Jul 7, 2026 7:25am | Jul 7, 2026 8:28am | Jul 7, 2026 8:42am | Jul 7, 2026 9:50am | Jul 7, 2026 12:03pm | Jul 7, 2026 12:05pm | Jul 7, 2026 12:05pm | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Isolate 25 kva transformer To splice and retention broken open secondary neutral Using:50ft #2 AA conductor (1) #2 preform (3) one bolt clamps Also clear bamboo from open secondary wires
Outage | J.E.26.07.05234 | C001841514 | Swon Miller | St.James | Completed | Load_243892 | Bogue - 510 | Jul 6, 2026 11:01pm | Jul 6, 2026 11:02pm | Jul 6, 2026 11:24pm | Jul 6, 2026 11:25pm | Jul 6, 2026 11:26pm | Jul 28, 2026 1:44am | Jul 7, 2026 1:46am | Jul 7, 2026 1:46am |  |  | Fair | No | Found customer service burnt off at pole and pothead cause by customer underground cables customers is having an internal problem voltage found 0.000 voltage left 0.000 disconnect customer from pothead advice customer to have underground cables rectified before repair can be carried out
Outage | J.E.26.07.05157 | C001841504 | Hartley Chin | Clarendon | Completed | Load_242545 | Parnassus - 210 | Jul 6, 2026 9:29pm | Jul 6, 2026 9:30pm | Jul 7, 2026 8:11am | Jul 7, 2026 8:11am | Jul 7, 2026 9:49am | Jul 7, 2026 10:00am | Jul 7, 2026 10:01am | Jul 7, 2026 10:01am | BrokenWire |  | Fair | No | Isolate broken service wire from service pole due to customer meter pole being tore down by truck … customer was advised to rectify issue before making another report to have service wire remounted… meter # 2568494 ..
Outage | J.E.26.07.05178 | C001841502 | Hartley Chin | Clarendon | Completed | Load_264794 | Monymusk - 410 | Jul 6, 2026 9:23pm | Jul 6, 2026 9:27pm | Jul 6, 2026 9:38pm | Jul 6, 2026 10:12pm | Jul 6, 2026 11:01pm | Jul 6, 2026 11:47pm | Jul 7, 2026 7:46am | Jul 7, 2026 7:46am |  |  | Fair | No | Foun blown 3 amp fuse on 25 KVA transformer (no pole #) due to sagging neutral, retention neutral, refused transformer…
Outage | J.E.26.07.05183 | C001841498 | Roxroy Needham | St.Ann | Completed | Load_264960 | Cardiff Hall - 310 | Jul 6, 2026 9:06pm | Jul 6, 2026 9:06pm | Jul 6, 2026 9:24pm | Jul 6, 2026 9:27pm | Jul 6, 2026 10:57pm | Jul 6, 2026 10:51pm | Jul 6, 2026 11:00pm | Jul 6, 2026 11:00pm |  |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.07.05155 | C001841497 | Wan Carlos Scarlett | Portmore | Completed | Load_248619 | Naggo Head - 510 | Jul 6, 2026 8:59pm | Jul 7, 2026 7:13am | Jul 7, 2026 7:35am | Jul 7, 2026 10:19am | Jul 7, 2026 10:57am | Jul 7, 2026 11:12am | Jul 7, 2026 11:14am | Jul 7, 2026 11:14am |  |  | Fair | No | Found customer 3 wire service at pothead with one of the phase corroded use 3 Penn union at service wire phase readings 117–116-234
Outage | J.E.26.07.05169 | C001841496 | Wan Carlos Scarlett | Portmore | Completed | Load_263851 | Naggo Head - 610 | Jul 6, 2026 8:59pm | Jul 7, 2026 7:13am | Jul 7, 2026 11:18am | Jul 7, 2026 11:18am | Jul 7, 2026 11:55am | Jul 7, 2026 12:09pm | Jul 7, 2026 12:10pm | Jul 7, 2026 12:10pm |  |  | Fair | No | Customer not available at this time premises closed
Outage | J.E.26.07.05139 | C001841491 | Rayon Foster | Hanover | Completed | Load_245599 | Orange Bay - 310 | Jul 6, 2026 8:31pm | Jul 7, 2026 7:33am | Jul 7, 2026 10:49am | Jul 7, 2026 1:07pm | Jul 7, 2026 2:12pm | Jul 7, 2026 2:19pm | Jul 7, 2026 2:20pm | Jul 7, 2026 2:20pm |  |  | Fair | No | Check and found working ok voltage found in meter socket 118/117AB235 volts
Outage | J.E.26.07.05148 | C001841490 | Lancelot Brown | Hanover | Completed | Load_257564 | Orange Bay - 310 | Jul 6, 2026 8:31pm | Jul 6, 2026 8:43pm | Jul 6, 2026 9:51pm | Jul 6, 2026 9:51pm | Jul 6, 2026 10:52pm | Jul 6, 2026 10:54pm | Jul 6, 2026 10:55pm | Jul 6, 2026 10:55pm | Fire |  | SevereWind | No | Found 25kva fuse blown patroll found vegetation on 25kva removed vegetation from 25kva replace 1-2amps fuse supply restore
Non-Outage | J.E.26.07.04731 | C001841488 | Richard Samuda | Manchester | Completed | Load_249671 | Kendal - 210 | Jul 6, 2026 8:23pm | Jul 6, 2026 8:23pm | Jul 6, 2026 8:47pm | Jul 6, 2026 8:47pm | Jul 6, 2026 9:08pm | Jul 6, 2026 9:08pm | Jul 6, 2026 9:50pm | Jul 6, 2026 9:50pm |  |  | Fair | No | Change corroded 1bolt clamp on customer service wire that cause customer to experience low voltage 114/116/230
Non-Outage | J.E.26.07.05162 | C001841487 | Milton Charlton | null | Completed | null | null | Jul 6, 2026 8:19pm | Jul 6, 2026 8:21pm | Jul 6, 2026 8:55pm | Jul 6, 2026 8:56pm | Jul 6, 2026 9:51pm | Jul 6, 2026 9:50pm | Jul 6, 2026 9:52pm | Jul 6, 2026 9:52pm | BrokenPole |  | Fair | No | Customer need to top up their account.
Outage | J.E.26.07.05168 | C001841486 | Gregory Grossett | Portland | Completed | Load_260163 | Port Antonio - 410 | Jul 6, 2026 8:14pm | Jul 6, 2026 8:15pm | Jul 6, 2026 8:18pm | Jul 6, 2026 8:18pm | Jul 6, 2026 8:51pm | Jul 6, 2026 10:25pm | Jul 6, 2026 10:41pm | Jul 6, 2026 10:41pm |  | Y | Fair | No | 25kva transformer trip cause by tree Fall on line section and burst down conductors open transformer fuse link then splice and retention several span of conductors along line section close transformer fuse and reset transformer to restore supply to the area.Material use 6 one bolt clamps 10ft of 2/0 conductor.
Outage | J.E.26.07.05138 | C001841485 | Shamour Haughton | Westmoreland | Completed | Load_303231 | Paradise - 310 | Jul 6, 2026 8:10pm | Jul 6, 2026 8:18pm | Jul 6, 2026 8:39pm | Jul 6, 2026 10:11pm | Jul 6, 2026 10:11pm | Jul 6, 2026 10:11pm | Jul 6, 2026 10:18pm | Jul 6, 2026 10:18pm | Fire |  | Fair | No | Found customer pothead corroded, clean and remake joint use 3 clamps,meter not displaying, voltage left 109,111,220
Non-Outage | J.E.26.06.32333 | C001841484 | Horace Malcolm | St.James | Completed | Load_256792 | Bogue - 410 | Jul 6, 2026 7:45pm | Jul 6, 2026 7:46pm | Jul 6, 2026 7:57pm | Jul 6, 2026 7:57pm | Jul 6, 2026 8:13pm | Jul 6, 2026 8:14pm | Jul 6, 2026 8:14pm | Jul 6, 2026 8:14pm | LeaningPole |  | Fair | No | No leaning pole found
Non-Outage | J.E.26.07.04981 | C001841483 | Horace Malcolm | St.James | Completed | Load_253392 | Queens Drive - 810 | Jul 6, 2026 7:45pm | Jul 6, 2026 7:46pm | Jul 6, 2026 9:21pm | Jul 6, 2026 9:21pm | Jul 6, 2026 9:46pm | Jul 6, 2026 10:17pm | Jul 6, 2026 10:17pm | Jul 6, 2026 10:17pm |  |  | Fair | No | Unable to locate premises from direction given multiple calls to customer unavailable
Non-Outage | J.E.26.07.05089 | C001841482 | Horace Malcolm | St.James | Completed | Load_264461 | Bogue - 310 | Jul 6, 2026 7:45pm | Jul 6, 2026 7:46pm | Jul 6, 2026 8:43pm | Jul 6, 2026 8:43pm | Jul 6, 2026 8:59pm | Jul 6, 2026 9:19pm | Jul 6, 2026 9:19pm | Jul 6, 2026 9:19pm |  |  | Fair | No | Clean and joints at customer pothead and pole used 2clamps voltage 112-115-227
Outage | J.E.26.07.05121 | C001841481 | Horace Malcolm | St.James | Completed | Load_303208 | Bogue - 310 | Jul 6, 2026 7:45pm | Jul 6, 2026 7:46pm | Jul 6, 2026 8:16pm | Jul 6, 2026 8:16pm | Jul 6, 2026 8:38pm | Jul 6, 2026 8:42pm | Jul 6, 2026 8:42pm | Jul 6, 2026 8:42pm | BrokenWire |  | Fair | No | Check and found customer stsntion torn down found premises closed no occupants multiple phone calls to customer unavailable
Non-Outage | J.E.26.07.04991 | C001841480 | Andre Smith | null | Completed | null | null | Jul 6, 2026 7:44pm | Jul 6, 2026 7:48pm | Jul 6, 2026 8:20pm | Jul 6, 2026 8:20pm | Jul 6, 2026 8:41pm | Jul 6, 2026 9:36pm | Jul 6, 2026 9:36pm | Jul 6, 2026 9:36pm |  |  | Fair | No | Premises found close
Outage | J.E.26.07.05131 | C001841477 | Milton Charlton | KSAN | Completed | Load_263454 | Washington Blvd - 610 | Jul 6, 2026 7:15pm | Jul 6, 2026 7:25pm | Jul 6, 2026 8:00pm | Jul 6, 2026 8:00pm | Jul 6, 2026 8:51pm | Jul 6, 2026 9:00pm | Jul 6, 2026 8:54pm | Jul 6, 2026 8:54pm |  |  | Fair | No | Customer service wire #6 triplex feeding about six meters service wire is crystalize and causing customer to get a low voltage problem. Need about 100ft #6 triplex to change crystalize service wire .
Outage | J.E.26.07.05111 | C001841474 | Oshane Warren | Westmoreland | Completed | Load_253896 | Paradise - 210 | Jul 6, 2026 7:11pm | Jul 6, 2026 7:11pm | Jul 6, 2026 8:42pm | Jul 6, 2026 8:42pm | Jul 6, 2026 8:42pm | Jul 6, 2026 8:44pm | Jul 6, 2026 8:45pm | Jul 6, 2026 8:45pm |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.05132 | C001841476 | Tajay Bernard | Hanover | Completed | Load_261211 | Orange Bay - 310 | Jul 6, 2026 7:11pm | Jul 7, 2026 7:27am | Jul 7, 2026 9:49am | Jul 7, 2026 9:49am | Jul 7, 2026 9:54am | Jul 7, 2026 9:58am | Jul 7, 2026 9:59am | Jul 7, 2026 9:59am |  |  | Fair | No | Check and found customer meter burned causing customer to be single phasing, meter needs to be replaced urgently, refer to field service
Outage | J.E.26.07.05107 | C001841473 | Delano Gayle | St.Catherine | Completed | Load_250626 | New Michelton - 310 | Jul 6, 2026 7:10pm | Jul 6, 2026 11:56pm | Jul 7, 2026 3:09am | Jul 7, 2026 3:09am | Jul 7, 2026 6:05am | Jul 7, 2026 6:32am | Jul 7, 2026 6:32am | Jul 7, 2026 6:32am | BrokenWire |  | Fair | No | Premises not found no answer from customer phone, area of berry hill patrolled no broken wire seen
Outage | J.E.26.07.05067 | C001841468 | Edward Royal | KSAN | Completed | Load_573987 | Washington Blvd - 410 | Jul 6, 2026 6:42pm | Jul 6, 2026 6:43pm | Jul 6, 2026 7:23pm | Jul 6, 2026 7:23pm | Jul 6, 2026 7:23pm | Jul 6, 2026 7:56pm | Jul 6, 2026 7:58pm | Jul 6, 2026 7:58pm |  |  | Fair | No | Spliced and reconnected drop lead to secondary line using 3 single bolt clamp replaced 10A transformer fuse
Outage | J.E.26.07.05099 | C001841465 | Gregory Grossett | Portland | Completed | Load_252087 | Port Antonio - 410 | Jul 6, 2026 6:25pm | Jul 6, 2026 6:26pm | Jul 6, 2026 6:34pm | Jul 6, 2026 6:34pm | Jul 6, 2026 6:54pm | Jul 6, 2026 7:30pm | Jul 6, 2026 7:40pm | Jul 6, 2026 7:40pm |  |  | Fair | No | 220 service wire corroded at pothead joints repair and ok material use 3 one bolt clamps.
Outage | J.E.26.07.05086 | C001841463 | Collin Robinson | Portland | Completed | Load_241391 | Port Antonio - 310 | Jul 6, 2026 6:18pm | Jul 6, 2026 6:25pm | Jul 6, 2026 6:59pm | Jul 6, 2026 6:59pm | Jul 6, 2026 7:26pm | Jul 6, 2026 7:45pm | Jul 6, 2026 7:45pm | Jul 6, 2026 7:45pm |  |  | Fair | No | Customer meter socket defective Two wire meter Voltage reading 118v
Non-Outage | J.E.26.07.04940 | C001841461 | Damion Reid | null | Completed | null | null | Jul 6, 2026 6:11pm | Jul 7, 2026 7:53am | Jul 7, 2026 7:57am | Jul 7, 2026 7:57am | Jul 7, 2026 10:30am | Jul 7, 2026 11:29am | Jul 7, 2026 11:32am | Jul 7, 2026 11:32am |  |  | SevereWind | No | Remade corroded phase at secondary jumper using one 1 bolt clamp voltage reading at meter socket phase to neutral 116v-115v across phase 233v
Non-Outage | J.E.26.07.05040 | C001841459 | Rodclif Dawkins | null | Completed | null | null | Jul 6, 2026 6:08pm | Jul 6, 2026 6:20pm | Jul 6, 2026 10:02pm | Jul 6, 2026 10:02pm | Jul 7, 2026 5:11pm | Jul 7, 2026 5:11pm | Jul 7, 2026 5:11pm | Jul 7, 2026 5:11pm | LeakingTransformer |  | Fair | No | Transformer was changed
Outage | J.E.26.07.04982 | C001841455 | Edward Royal | KSAN | Completed | Load_253830 | Washington Blvd - 710 | Jul 6, 2026 6:00pm | Jul 6, 2026 6:22pm | Jul 6, 2026 6:45pm | Jul 6, 2026 6:45pm | Jul 6, 2026 6:45pm | Jul 6, 2026 6:46pm | Jul 6, 2026 6:46pm | Jul 6, 2026 6:46pm |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.07.04999 | C001841456 | Andre Smith | KSAS | Completed | Load_238569 | Rockfort - 410 | Jul 6, 2026 6:00pm | Jul 6, 2026 6:22pm | Jul 6, 2026 6:46pm | Jul 6, 2026 6:46pm | Jul 6, 2026 7:24pm | Jul 6, 2026 8:19pm | Jul 6, 2026 8:19pm | Jul 6, 2026 8:19pm |  |  | Fair | No | Premises found okay supply restored already
Non-Outage | J.E.26.07.05071 | C001841451 | Rodclif Dawkins | Portmore | Completed | Load_245174 | Naggo Head - 610 | Jul 6, 2026 5:56pm | Jul 6, 2026 5:58pm | Jul 6, 2026 8:30pm | Jul 6, 2026 9:41pm | Jul 6, 2026 9:42pm | Jul 6, 2026 9:42pm | Jul 6, 2026 9:59pm | Jul 6, 2026 9:59pm |  |  | Fair | No | Crew observed top phase of open secondary resting on d iron . 50kva transformer was de-engerzied at pole# 010363 . Using 4,2/0 pre-form, 4-1bolt clamp and 5ft of aa2/0 conductor, repairs were done and transformer energized. Area okay
Outage | J.E.26.07.05042 | C001841452 | Rodclif Dawkins | Portmore | Completed | Load_253267 | Naggo Head - 610 | Jul 6, 2026 5:56pm | Jul 6, 2026 5:58pm | Jul 6, 2026 8:28pm | Jul 6, 2026 8:28pm | Jul 6, 2026 8:28pm | Jul 6, 2026 8:29pm | Jul 6, 2026 8:29pm | Jul 6, 2026 8:29pm |  |  | Fair | No | Found blown junction fuse for single phase T-off. Line section patrolled, crew found defective 10 kva transformer. Transformer isolated from line section. Crew found and replaced 20amp . 13 customers are without supply. Please refer to kymani Alman Aston Murray
Outage | J.E.26.07.05061 | C001841453 | Rodclif Dawkins | Portmore | Completed | Load_257047 | Naggo Head - 610 | Jul 6, 2026 5:56pm | Jul 6, 2026 5:58pm | Jul 6, 2026 6:15pm | Jul 6, 2026 7:00pm | Jul 6, 2026 7:00pm | Jul 6, 2026 7:01pm | Jul 6, 2026 8:27pm | Jul 6, 2026 8:27pm |  |  | Fair | No | Found blown junction fuse for single phase T-off. Line section patrolled, crew found defective 10 kva transformer. Transformer isolated from line section. Crew found and replaced 20amp . 13 customers are without supply. Please refer to kymani Alman Aston Murray
Outage | J.E.26.07.05049 | C001841450 | Richard Grant | St.Catherine | Completed | Load_253539 | New Michelton - 210 | Jul 6, 2026 5:55pm | Jul 7, 2026 7:26am | Jul 7, 2026 12:04pm | Jul 7, 2026 2:38pm | Jul 7, 2026 2:39pm | Jul 7, 2026 2:39pm | Jul 7, 2026 2:39pm | Jul 7, 2026 2:39pm |  |  | Fair | No | 25kva transformer found isolated and 2 pole span of opened secondary lower phase and neutral found caused by fire by sugar cane worker. 4 preform, 3 onebolt clamps, 4 sleeves, approximately 200ft #2 and approximately 100ft 2/0 wire used to retention line. Supply restored and area left okay
Outage | J.E.26.07.04583 | C001841448 | Moses Elliston | St.Catherine | Completed | Load_568931 | Twickenham - 310 | Jul 6, 2026 5:54pm | Jul 6, 2026 5:59pm | Jul 7, 2026 9:42am | Jul 7, 2026 9:42am | Jul 7, 2026 9:42am | Jul 7, 2026 9:42am | Jul 7, 2026 9:42am | Jul 7, 2026 9:42am |  |  | Fair | No | Customer said crew already attended
Outage | J.E.26.07.05051 | C001841449 | Donald Cunningham | St.Catherine | Completed | Load_249297 | New Michelton - 310 | Jul 6, 2026 5:54pm | Jul 6, 2026 5:57pm | Jul 6, 2026 6:10pm | Jul 6, 2026 7:37pm | Jul 6, 2026 9:16pm | Jul 6, 2026 9:18pm | Jul 6, 2026 9:18pm | Jul 6, 2026 9:18pm |  |  | Fair | No | Supply restored
Outage | J.E.26.07.05041 | C001841445 | Clyde Brown | Clarendon | Completed | Load_260045 | May Pen - 110 | Jul 6, 2026 5:45pm | Jul 6, 2026 5:47pm | Jul 6, 2026 9:44pm | Jul 6, 2026 9:44pm | Jul 6, 2026 10:12pm | Jul 6, 2026 10:16pm | Jul 6, 2026 10:19pm | Jul 6, 2026 10:19pm |  |  | Fair | No | 25kva transformer tripped,line patrolled and no fault seen, transformer reset and supply now ok
Outage | J.E.26.07.05063 | C001841444 | Hartley Chin | Clarendon | Completed | Load_247305 | Parnassus - 210 | Jul 6, 2026 5:45pm | Jul 6, 2026 5:47pm | Jul 6, 2026 7:01pm | Jul 6, 2026 7:10pm | Jul 6, 2026 8:13pm | Jul 6, 2026 8:19pm | Jul 6, 2026 8:19pm | Jul 6, 2026 8:19pm |  |  | Fair | No | Unable to contact customer .. was able to find meter … voltage read 112v , 114v …
Outage | J.E.26.07.05044 | C001841443 | Hartley Chin | Clarendon | Completed | Load_301188 | Monymusk - 210 | Jul 6, 2026 5:44pm | Jul 6, 2026 5:47pm | Jul 6, 2026 8:20pm | Jul 6, 2026 8:20pm | Jul 6, 2026 9:52pm | Jul 6, 2026 10:10pm | Jul 6, 2026 10:12pm | Jul 6, 2026 10:12pm | BrokenWire |  | Fair | No | Retention customer service wire …
Outage | J.E.26.07.05056 | C001841439 | Edward Royal | KSAS | Completed | Load_264287 | Duhaney - 310 | Jul 6, 2026 5:29pm | Jul 6, 2026 5:37pm | Jul 6, 2026 6:41pm | Jul 6, 2026 6:41pm | Jul 6, 2026 6:41pm | Jul 6, 2026 6:42pm | Jul 6, 2026 6:42pm | Jul 6, 2026 6:42pm |  |  | Fair | No | Customer was reconnected by escalation
Outage | J.E.26.07.05020 | C001841437 | Selvin White | St.Elizabeth | Completed | Load_570258 | Maggotty - 110 | Jul 6, 2026 5:26pm | Jul 6, 2026 5:26pm | Jul 6, 2026 5:46pm | Jul 6, 2026 5:46pm | Jul 6, 2026 6:56pm | Jul 6, 2026 7:08pm | Jul 6, 2026 7:08pm | Jul 6, 2026 7:08pm |  |  | Fair | No | Customer cannot be contacted or located.
Outage | J.E.26.07.05037 | C001841436 | Barnett Brown | Manchester | Completed | Load_237730 | Spur Tree - 310 | Jul 6, 2026 5:25pm | Jul 6, 2026 5:25pm | Jul 6, 2026 7:46pm | Jul 6, 2026 7:46pm | Jul 6, 2026 9:06pm | Jul 6, 2026 9:52pm | Jul 6, 2026 9:55pm | Jul 6, 2026 9:55pm |  |  | Fair | No | Reconnect customer via customer care
Non-Outage | J.E.26.07.04741 | C001841435 | Kenroy Dale | Manchester | Completed | Load_248799 | Kendal - 310 | Jul 6, 2026 5:24pm | Jul 6, 2026 5:24pm | Jul 6, 2026 6:33pm | Jul 6, 2026 9:48pm | Jul 6, 2026 11:56pm | Jul 6, 2026 11:57pm | Jul 6, 2026 11:59pm | Jul 6, 2026 11:59pm |  |  | Fair | No | Customer is requesting daylight attention
Non-Outage | J.E.26.07.04785 | C001841433 | Kenroy Dale | Manchester | Completed | Load_301461 | Kendal - 310 | Jul 6, 2026 5:24pm | Jul 6, 2026 5:24pm | Jul 6, 2026 6:14pm | Jul 6, 2026 6:14pm | Jul 6, 2026 7:17pm | Jul 6, 2026 7:24pm | Jul 6, 2026 7:25pm | Jul 6, 2026 7:25pm |  |  | Fair | No | Customer said they did not make any report and refuse to give us precise information, call was then written off with the advise of dispatcher
Non-Outage | J.E.26.07.04861 | C001841434 | Kenroy Dale | Manchester | Completed | Load_257847 | Kendal - 310 | Jul 6, 2026 5:24pm | Jul 6, 2026 5:24pm | Jul 6, 2026 6:37pm | Jul 6, 2026 7:30pm | Jul 6, 2026 9:11pm | Jul 6, 2026 9:44pm | Jul 6, 2026 9:48pm | Jul 6, 2026 9:48pm |  |  | Fair | No | Supply found okay voltage reading 117/120/238 customers was advised to get an electrician to check premises
Outage | J.E.26.07.05026 | C001841428 | Wan Carlos Scarlett | St.Catherine | Completed | Load_569977 | Twickenham - 210 | Jul 6, 2026 5:06pm | Jul 7, 2026 7:13am | Jul 7, 2026 7:20am | Jul 7, 2026 7:20am | Jul 7, 2026 8:15am | Jul 7, 2026 9:15am | Jul 7, 2026 9:18am | Jul 7, 2026 9:18am |  |  | Fair | No | Customer not available at this time customer request for next visit midday
Outage | J.E.26.07.05032 | C001841429 | Rodclif Dawkins | Portmore | Completed | Load_253186 | Naggo Head - 610 | Jul 6, 2026 5:06pm | Jul 6, 2026 5:07pm | Jul 6, 2026 8:29pm | Jul 6, 2026 8:29pm | Jul 6, 2026 8:29pm | Jul 6, 2026 8:29pm | Jul 6, 2026 8:30pm | Jul 6, 2026 8:30pm |  |  | Fair | No | Found blown junction fuse for single phase T-off. Line section patrolled, crew found defective 10 kva transformer. Transformer isolated from line section. Crew found and replaced 20amp . 13 customers are without supply. Please refer to kymani Alman Aston Murray
Outage | J.E.26.07.04880 | C001841424 | Moses Elliston | St.Catherine | Completed | Load_1001076 | Tredegar - 210 | Jul 6, 2026 5:00pm | Jul 6, 2026 5:01pm | Jul 7, 2026 12:27pm | Jul 7, 2026 12:27pm | Jul 7, 2026 12:27pm | Jul 7, 2026 12:36pm | Jul 7, 2026 12:37pm | Jul 7, 2026 12:37pm |  |  | Fair | No | Credit added to prepaid account.
Non-Outage | J.E.26.07.04956 | C001841421 | Swon Miller | null | Completed | null | null | Jul 6, 2026 4:56pm | Jul 6, 2026 4:57pm | Jul 6, 2026 7:00pm | Jul 6, 2026 7:00pm | Jul 6, 2026 7:11pm | Jul 27, 2026 7:16am | Jul 6, 2026 7:16pm | Jul 6, 2026 7:16pm |  |  | Fair | No | Call related to previous
Outage | J.E.26.07.05025 | C001841420 | Shamour Haughton | St.James | Completed | Load_257529 | Bogue - 610 | Jul 6, 2026 4:56pm | Jul 6, 2026 4:56pm | Jul 6, 2026 5:00pm | Jul 6, 2026 5:00pm | Jul 6, 2026 6:16pm | Jul 6, 2026 6:49pm | Jul 6, 2026 6:53pm | Jul 6, 2026 6:53pm |  |  | Fair | No | Found 1,25kva blown caused by banging secondary, retention secondary using 1 #2 preform and refuse 25kva using 1,3amp fuse
Outage | J.E.26.07.05031 | C001841419 | Moses Elliston | St.Catherine | Completed | Load_1000940 | Tredegar - 410 | Jul 6, 2026 4:56pm | Jul 6, 2026 4:56pm | Jul 6, 2026 5:36pm | Jul 6, 2026 5:36pm | Jul 6, 2026 5:36pm | Jul 6, 2026 5:15pm | Jul 6, 2026 5:38pm | Jul 6, 2026 5:38pm |  |  | Fair | No | Credit added to prepaid account.
Outage | J.E.26.07.05022 | C001841418 | Clyde Brown | Clarendon | Completed | Load_568435 | May Pen - 110 | Jul 6, 2026 4:54pm | Jul 6, 2026 5:08pm | Jul 6, 2026 8:34pm | Jul 6, 2026 8:34pm | Jul 6, 2026 9:16pm | Jul 6, 2026 9:31pm | Jul 6, 2026 9:40pm | Jul 6, 2026 9:40pm |  | Y | Fair | No | Blown 15 amps junction fuse near Mears Bridge,Trout hall,caused by men cut tree on primary line,line cleared and blown fuse replaced.
Outage | J.E.26.07.05023 | C001841417 | Milton Charlton | KSAN | Completed | Load_267757 | Washington Blvd - 510 | Jul 6, 2026 4:53pm | Jul 6, 2026 4:55pm | Jul 6, 2026 7:06pm | Jul 6, 2026 7:06pm | Jul 6, 2026 7:57pm | Jul 6, 2026 8:00pm | Jul 6, 2026 8:00pm | Jul 6, 2026 8:00pm |  |  | Fair | No | Customer disconnected for debt.
Outage | J.E.26.07.05006 | C001841405 | Hartley Chin | Clarendon | Completed | Load_263846 | May Pen - 210 | Jul 6, 2026 4:44pm | Jul 6, 2026 4:45pm | Jul 6, 2026 5:42pm | Jul 6, 2026 5:42pm | Jul 6, 2026 6:56pm | Jul 6, 2026 7:00pm | Jul 6, 2026 7:01pm | Jul 6, 2026 7:01pm | BrokenWire |  | Fair | No | Prem not found …. unable to contact customer.. area patrolled and found oaky .. contacted escalation was told that this contact is the only contact # 8768993012 available …
Outage | J.E.26.07.04909 | C001841403 | Milton Charlton | KSAN | Completed | Load_243112 | Washington Blvd - 610 | Jul 6, 2026 4:41pm | Jul 6, 2026 4:42pm | Jul 6, 2026 5:01pm | Jul 6, 2026 5:01pm | Jul 6, 2026 6:09pm | Jul 6, 2026 6:45pm | Jul 6, 2026 6:50pm | Jul 6, 2026 6:50pm |  |  | Fair | No | Customer service wire #2 triplex feeding three meter phase burn off at pole . Repair using two 1- bolt clamps. Readings at pothead and meter socket 117-117-234 volts.
Outage | J.E.26.07.04986 | C001841400 | Selvin White | St.Elizabeth | Completed | Load_258957 | Maggotty - 210 | Jul 6, 2026 4:40pm | Jul 6, 2026 4:42pm | Jul 6, 2026 7:08pm | Jul 6, 2026 7:08pm | Jul 6, 2026 7:37pm | Jul 6, 2026 7:39pm | Jul 6, 2026 7:39pm | Jul 6, 2026 7:39pm |  |  | Fair | No | Customer says supply was restored about an hour or two ago.
Outage | J.E.26.07.04994 | C001841401 | Wayne Dillion | St.Elizabeth | Completed | Load_266535 | Maggotty - 110 | Jul 6, 2026 4:40pm | Jul 6, 2026 4:42pm | Jul 6, 2026 7:24pm | Jul 6, 2026 7:24pm | Jul 6, 2026 8:19pm | Jul 6, 2026 8:21pm | Jul 6, 2026 8:27pm | Jul 6, 2026 8:27pm | BrokenWire |  | Fair | No | Supply check and found corrosion at customer pot head. Repair same using 3 linkets. Supply leave working okay reading 110v, 108v and cross phase 228volts.
Outage | J.E.26.07.05005 | C001841402 | Neckell Ormsby | St.Mary | Completed | Load_247804 | Blackstonedge - 110 | Jul 6, 2026 4:40pm | Jul 6, 2026 4:42pm | Jul 6, 2026 5:34pm | Jul 6, 2026 5:37pm | Jul 6, 2026 6:40pm | Jul 6, 2026 7:10pm | Jul 6, 2026 7:10pm | Jul 6, 2026 7:10pm |  |  | Fair | No | Patrol and Found supply ok in area
Outage | J.E.26.07.05010 | C001841399 | Richard Samuda | Manchester | Completed | Load_265840 | Kendal - 210 | Jul 6, 2026 4:38pm | Jul 6, 2026 4:41pm | Jul 6, 2026 5:16pm | Jul 6, 2026 5:16pm | Jul 6, 2026 6:05pm | Jul 6, 2026 6:57pm | Jul 6, 2026 7:01pm | Jul 6, 2026 7:01pm |  |  | Fair | No | Reconnect customer meter to secondary line that was damaged in hurricane using three 1bolt clamps and 25ft of #6service wire 111/112 /223 meter # 2931513/2931514
Non-Outage | J.E.26.07.04272 | C001841379 | Tajay Bernard | Hanover | Completed | Load_240604 | Orange Bay - 310 | Jul 6, 2026 4:22pm | Jul 7, 2026 11:56am | Jul 7, 2026 12:08pm | Jul 7, 2026 12:20pm | Jul 7, 2026 12:42pm | Jul 7, 2026 12:53pm | Jul 7, 2026 12:54pm | Jul 7, 2026 12:54pm |  |  | Fair | No | Area check and found okay unable to locate customer on premises multiple phone call to customer number went unanswered
Outage | J.E.26.07.04978 | C001841370 | Oshane Warren | Westmoreland | Completed | Load_241469 | Paradise - 210 | Jul 6, 2026 4:13pm | Jul 6, 2026 4:13pm | Jul 6, 2026 4:52pm | Jul 6, 2026 4:52pm | Jul 6, 2026 8:37pm | Jul 6, 2026 8:38pm | Jul 6, 2026 8:42pm | Jul 6, 2026 8:42pm | Fire |  | Fair | No | Open 100 kva transformer fuse spice and retention one spand secondary conductor use 6pg clamp and dead end perform and disconnect illegal connection
Outage | J.E.26.07.04952 | C001841367 | Lancelot Brown | Hanover | Completed | Load_255828 | Orange Bay - 310 | Jul 6, 2026 4:09pm | Jul 6, 2026 4:23pm | Jul 6, 2026 4:26pm | Jul 6, 2026 6:39pm | Jul 6, 2026 6:39pm | Jul 6, 2026 6:40pm | Jul 6, 2026 6:40pm | Jul 6, 2026 6:40pm |  |  | SevereWind | No | This call related to 8amps junction fuse no pole number supply restore
Outage | J.E.26.07.04970 | C001841368 | Lancelot Brown | Hanover | Completed | Load_252019 | Orange Bay - 310 | Jul 6, 2026 4:09pm | Jul 6, 2026 4:23pm | Jul 6, 2026 4:27pm | Jul 6, 2026 5:45pm | Jul 6, 2026 6:36pm | Jul 6, 2026 6:39pm | Jul 6, 2026 6:39pm | Jul 6, 2026 6:39pm |  |  | SevereWind | No | Found junction fuse blown patroll found primary jumper contact with wooden pole make primary jumper clear also cut and remove vegetation from primary line replace 1-8amps junction no pole number supply restore
Outage | J.E.26.07.04156 | C001841346 | Edward Royal | KSAN | Completed | Load_245528 | Washington Blvd - 310 | Jul 6, 2026 3:47pm | Jul 6, 2026 3:47pm | Jul 6, 2026 4:44pm | Jul 6, 2026 4:44pm | Jul 6, 2026 4:44pm | Jul 6, 2026 4:47pm | Jul 6, 2026 4:47pm | Jul 6, 2026 4:47pm |  |  | Fair | No | Premises found close unable to communicate with customer
Outage | J.E.26.07.04964 | C001841345 | Edward Royal | KSAN | Completed | Load_250320 | Washington Blvd - 710 | Jul 6, 2026 3:46pm | Jul 6, 2026 3:47pm | Jul 6, 2026 4:22pm | Jul 6, 2026 4:22pm | Jul 6, 2026 4:22pm | Jul 6, 2026 4:34pm | Jul 6, 2026 4:34pm | Jul 6, 2026 4:34pm | BrokenWire |  | Fair | No | Customer have internal problems customer have defective stanchion pole advise customer to get a electrician to fix the problem customer was disconnected
Outage | J.E.26.07.04417 | C001841344 | Andre Smith | KSAS | Completed | Load_238916 | Three Miles - 410 | Jul 6, 2026 3:45pm | Jul 6, 2026 3:46pm | Jul 6, 2026 5:11pm | Jul 6, 2026 5:11pm | Jul 6, 2026 5:25pm | Jul 6, 2026 5:25pm | Jul 6, 2026 5:25pm | Jul 6, 2026 5:25pm |  |  | Fair | No | Premises found close
Outage | J.E.26.07.04677 | C001841343 | Andre Smith | KSAS | Completed | Load_1002955 | Hunts Bay - 210 | Jul 6, 2026 3:45pm | Jul 6, 2026 3:46pm | Jul 6, 2026 4:02pm | Jul 6, 2026 4:02pm | Jul 6, 2026 5:07pm | Jul 6, 2026 5:10pm | Jul 6, 2026 5:11pm | Jul 6, 2026 5:11pm |  |  | Fair | No | Defective cable found and maintenance department is in process of replacing it
Outage | J.E.26.07.04928 | C001841331 | Clyde Brown | Clarendon | Completed | Load_262821 | May Pen - 110 | Jul 6, 2026 3:41pm | Jul 6, 2026 3:43pm | Jul 6, 2026 3:54pm | Jul 6, 2026 3:54pm | Jul 6, 2026 5:29pm | Jul 6, 2026 5:25pm | Jul 6, 2026 5:35pm | Jul 6, 2026 5:35pm |  |  | Fair | No | Corroded phase on 3 wire service at secondary line connection remade with 1- clamp,voltage left 114/110 and 224V.
Outage | J.E.26.07.04756 | C001841330 | Romaine Roberts | St.Mary | Completed | Load_242233 | Annotto Bay - 310 | Jul 6, 2026 3:39pm | Jul 6, 2026 3:40pm | Jul 6, 2026 4:09pm | Jul 6, 2026 4:09pm | Jul 6, 2026 6:28pm | Jul 6, 2026 6:30pm | Jul 6, 2026 6:30pm | Jul 6, 2026 6:30pm | Fire | Y | Fair | No | High wind bang secondary conductor open and close 25 kva transformer to clear line
Non-Outage | J.E.26.07.04788 | C001841323 | Rodclif Dawkins | null | Completed | null | null | Jul 6, 2026 3:37pm | Jul 6, 2026 3:41pm | Jul 6, 2026 6:02pm | Jul 6, 2026 6:02pm | Jul 6, 2026 6:02pm | Jul 6, 2026 6:02pm | Jul 6, 2026 6:03pm | Jul 6, 2026 6:03pm |  |  | Fair | No | Premises locked
Outage | J.E.26.07.04937 | C001841324 | Rodclif Dawkins | Portmore | Completed | Load_239523 | Naggo Head - 610 | Jul 6, 2026 3:37pm | Jul 6, 2026 3:41pm | Jul 6, 2026 10:00pm | Jul 6, 2026 10:00pm | Jul 6, 2026 10:00pm | Jul 6, 2026 10:00pm | Jul 6, 2026 10:01pm | Jul 6, 2026 10:01pm | BangingWires,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Crew observed top phase of open secondary resting on d iron . 50kva transformer was de-engerzied at pole# 010363 . Using 4,2/0 pre-form, 4-1bolt clamp and 5ft of aa2/0 conductor, repairs were done and transformer energized. Area okay
Outage | J.E.26.07.04583 | C001841322 | Rodclif Dawkins | St.Catherine | Completed | Load_568931 | Twickenham - 310 | Jul 6, 2026 3:36pm | Jul 6, 2026 3:41pm | Jul 6, 2026 5:52pm | Jul 6, 2026 5:53pm | Jul 6, 2026 5:53pm | Jul 6, 2026 5:53pm | Jul 6, 2026 5:54pm | Jul 6, 2026 5:54pm |  |  | Fair | No | Customer supplied by hexing, refer to Moses Elleston
Outage | J.E.26.07.04775 | C001841320 | Donald Cunningham | St.Catherine | Completed | Load_1000940 | Tredegar - 410 | Jul 6, 2026 3:34pm | Jul 6, 2026 3:35pm | Jul 6, 2026 3:50pm | Jul 6, 2026 3:50pm | Jul 6, 2026 4:21pm | Jul 6, 2026 4:21pm | Jul 6, 2026 4:22pm | Jul 6, 2026 4:22pm |  |  | Fair | No | Premises closed
Outage | J.E.26.07.04880 | C001841321 | Donald Cunningham | St.Catherine | Completed | Load_1001076 | Tredegar - 210 | Jul 6, 2026 3:34pm | Jul 6, 2026 3:35pm | Jul 6, 2026 4:22pm | Jul 6, 2026 4:22pm | Jul 6, 2026 4:53pm | Jul 6, 2026 4:53pm | Jul 6, 2026 4:55pm | Jul 6, 2026 4:55pm |  |  | Fair | No | Customer unable to add credit refer to mr Ellison to assist
Outage | J.E.26.07.04266 | C001841309 | Cliton Henry | St.Mary | Completed | Load_261992 | Blackstonedge - 110 | Jul 6, 2026 3:33pm | Jul 6, 2026 3:35pm | Jul 6, 2026 5:20pm | Jul 6, 2026 5:20pm | Jul 6, 2026 5:42pm | Jul 6, 2026 6:54pm | Jul 6, 2026 6:57pm | Jul 6, 2026 6:57pm |  |  | Fair | No | A blown 20 amp fuse found at Derry square due to tree contact at Hazard Dist. The tree was cut at remove from contact. Supply restored using 1-20amp fuse.
Outage | J.E.26.07.04910 | C001841315 | Hopeton Henry | St.Thomas | Completed | Load_238353 | Good Year - 110 | Jul 6, 2026 3:33pm | Jul 6, 2026 3:34pm | Jul 6, 2026 5:27pm | Jul 6, 2026 8:48pm | Jul 6, 2026 8:48pm | Jul 6, 2026 8:48pm | Jul 6, 2026 8:48pm | Jul 6, 2026 8:48pm |  |  | Fair | No | Check and found ok
Outage | J.E.26.07.04919 | C001841313 | Hopeton Henry | St.Thomas | Completed | Load_268598 | Good Year - 110 | Jul 6, 2026 3:33pm | Jul 6, 2026 3:34pm | Jul 6, 2026 5:27pm | Jul 6, 2026 6:45pm | Jul 6, 2026 7:38pm | Jul 6, 2026 8:47pm | Jul 6, 2026 8:48pm | Jul 6, 2026 8:48pm |  |  | Fair | No | Check and found ok
Outage | J.E.26.07.04926 | C001841310 | Hopeton Henry | St.Thomas | Completed | Load_253180 | Good Year - 110 | Jul 6, 2026 3:33pm | Jul 6, 2026 3:33pm | Jul 6, 2026 5:27pm | Jul 6, 2026 5:28pm | Jul 6, 2026 6:42pm | Jul 6, 2026 6:42pm | Jul 6, 2026 6:44pm | Jul 6, 2026 6:44pm |  |  | Fair | Yes | Check and f
Outage | J.E.26.07.04948 | C001841311 | Hopeton Henry | St.Thomas | Completed | Load_261520 | Good Year - 110 | Jul 6, 2026 3:33pm | Jul 6, 2026 3:33pm | Jul 6, 2026 5:27pm | Jul 6, 2026 8:49pm | Jul 6, 2026 8:51pm | Jul 6, 2026 8:51pm | Jul 6, 2026 8:51pm | Jul 6, 2026 8:51pm |  |  | Fair | No | Check and found ok
Outage | J.E.26.07.04962 | C001841312 | Cliton Henry | St.Mary | Completed | Load_251954 | Highgate - 210 | Jul 6, 2026 3:33pm | Jul 6, 2026 3:35pm | Jul 6, 2026 3:46pm | Jul 6, 2026 3:46pm | Jul 6, 2026 5:09pm | Jul 6, 2026 5:20pm | Jul 6, 2026 5:20pm | Jul 6, 2026 5:20pm |  |  | Fair | No | A slack service wire neutral joint found was reconnected using 1- one bolt lamp. Voltages left 14-117/231 volts.
Outage | J.E.26.07.04952 | C001841307 | Lancelot Brown | Hanover | Completed | Load_255828 | Orange Bay - 310 | Jul 6, 2026 3:30pm | Jul 6, 2026 8:43pm | Jul 6, 2026 9:00pm | Jul 6, 2026 9:03pm | Jul 6, 2026 9:03pm | Jul 6, 2026 9:04pm | Jul 6, 2026 9:04pm | Jul 6, 2026 9:04pm |  |  | Fair | No | This call related to 8amps junction fuse supply restore
Non-Outage | J.E.26.07.04355 | C001841305 | Selvin White | St.Elizabeth | Completed | Load_240726 | Maggotty - 110 | Jul 6, 2026 3:29pm | Jul 6, 2026 3:30pm | Jul 6, 2026 4:09pm | Jul 6, 2026 4:09pm | Jul 6, 2026 4:09pm | Jul 6, 2026 4:11pm | Jul 6, 2026 4:11pm | Jul 6, 2026 4:11pm |  |  | Fair | No | Customer was contacted and said supply was restored from Sunday morning about 10 am.
Outage | J.E.26.07.02270 | C001841296 | Donald Cunningham | St.Catherine | Completed | Load_243352 | New Michelton - 310 | Jul 6, 2026 3:27pm | Jul 6, 2026 4:58pm | Jul 6, 2026 5:05pm | Jul 6, 2026 5:05pm | Jul 6, 2026 7:29pm | Jul 6, 2026 7:31pm | Jul 6, 2026 7:37pm | Jul 6, 2026 7:37pm |  |  | Fair | No | Supply restored to area
Outage | J.E.26.07.02690 | C001841295 | Delano Gayle | St.Catherine | Completed | Load_240025 | New Michelton - 310 | Jul 6, 2026 3:27pm | Jul 6, 2026 11:56pm | Jul 7, 2026 12:18am | Jul 7, 2026 12:18am | Jul 7, 2026 2:10am | Jul 7, 2026 2:17am | Jul 7, 2026 2:17am | Jul 7, 2026 2:17am |  |  | Fair | No | Premises found okay power restored
Outage | J.E.26.07.04888 | C001841294 | Wayne Dillion | St.Elizabeth | Completed | Load_292116 | Maggotty - 110 | Jul 6, 2026 3:27pm | Jul 6, 2026 3:28pm | Jul 6, 2026 6:39pm | Jul 6, 2026 6:39pm | Jul 6, 2026 6:39pm | Jul 6, 2026 6:44pm | Jul 6, 2026 6:44pm | Jul 6, 2026 6:44pm |  |  | Fair | No | Supply check and found hexing box # 01584 chip. Call customer care and have them reset box. Restored supply to the area.
Outage | J.E.26.07.04961 | C001841297 | Wayne Dillion | St.Elizabeth | Completed | Load_243624 | Maggotty - 110 | Jul 6, 2026 3:27pm | Jul 6, 2026 3:28pm | Jul 6, 2026 5:35pm | Jul 6, 2026 5:35pm | Jul 6, 2026 5:35pm | Jul 6, 2026 5:36pm | Jul 6, 2026 5:42pm | Jul 6, 2026 5:42pm |  |  | Fair | No | Supply is in area.
Non-Outage | J.E.26.07.04103 | C001841292 | Ricky Hall | null | Completed | null | null | Jul 6, 2026 3:26pm | Jul 6, 2026 3:32pm | Jul 6, 2026 6:44pm | Jul 6, 2026 6:44pm | Jul 6, 2026 7:08pm | Jul 6, 2026 7:13pm | Jul 6, 2026 7:13pm | Jul 6, 2026 7:13pm |  |  | Fair | No | Premises not located
Outage | J.E.26.07.04336 | C001841289 | Richard Grant | St.Catherine | Completed | Load_568270 | New Michelton - 310 | Jul 6, 2026 3:26pm | Jul 7, 2026 7:26am | Jul 7, 2026 9:46am | Jul 7, 2026 11:59am | Jul 7, 2026 11:59am | Jul 7, 2026 12:00pm | Jul 7, 2026 12:00pm | Jul 7, 2026 12:00pm |  |  | Fair | No | 8amps and 5amps fuse found blown for single phase junction and 50kva transformer, respectively, caused by wisp growing onto tranx switch bottom droplead. Wisp removed, fuses replaced with same and placed back respective switches. Supply restored and area left okay.
Outage | J.E.26.07.04699 | C001841290 | Daniel Francis | St.Ann | Completed | Load_242953 | Roaring River - 410 | Jul 6, 2026 3:26pm | Jul 6, 2026 3:26pm | Jul 6, 2026 4:26pm | Jul 6, 2026 4:26pm | Jul 6, 2026 4:35pm | Jul 6, 2026 5:23pm | Jul 6, 2026 5:24pm | Jul 6, 2026 5:24pm |  |  | Fair | No | Remade secondary phase jumper
Outage | J.E.26.07.04546 | C001841288 | Richard Grant | St.Catherine | Completed | Load_267525 | New Michelton - 310 | Jul 6, 2026 3:25pm | Jul 7, 2026 7:26am | Jul 7, 2026 9:45am | Jul 7, 2026 10:17am | Jul 7, 2026 10:55am | Jul 7, 2026 11:59am | Jul 7, 2026 11:59am | Jul 7, 2026 11:59am | LeakingTransformer |  | Fair | No | 8amps and 5amps fuse found blown for single phase junction and 50kva transformer, respectively, caused by wisp growing onto tranx switch bottom droplead. Wisp removed, fuses replaced with same and placed back respective switches. Supply restored and area left okay.
Outage | J.E.26.07.04548 | C001841287 | Delano Gayle | St.Catherine | Completed | Load_239883 | New Michelton - 210 | Jul 6, 2026 3:25pm | Jul 6, 2026 11:56pm | Jul 7, 2026 2:17am | Jul 7, 2026 2:17am | Jul 7, 2026 2:50am | Jul 7, 2026 3:00am | Jul 7, 2026 3:01am | Jul 7, 2026 3:01am | BrokenWire |  | Fair | No | Broken secondary phase and neutral in 1 span, which runs over cane field which was lit, secondary phase and neutral run back in other span,25kva transformer fuse blown, need approximately 200ft of #2 aa to carry out repairs along with daylight attention, 2 customer affected
Outage | J.E.26.07.04580 | C001841286 | Delano Gayle | St.Catherine | Completed | Load_243610 | New Michelton - 210 | Jul 6, 2026 3:25pm | Jul 6, 2026 11:56pm | Jul 7, 2026 3:01am | Jul 7, 2026 3:01am | Jul 7, 2026 3:08am | Jul 7, 2026 3:09am | Jul 7, 2026 3:09am | Jul 7, 2026 3:09am | BrokenWire |  | Fair | No | Premises not found no answer from customer phone
Outage | J.E.26.07.04627 | C001841285 | Rodclif Dawkins | St.Catherine | Completed | Load_260714 | Twickenham - 310 | Jul 6, 2026 3:25pm | Jul 6, 2026 3:31pm | Jul 6, 2026 6:12pm | Jul 6, 2026 6:12pm | Jul 6, 2026 6:12pm | Jul 6, 2026 6:12pm | Jul 6, 2026 6:12pm | Jul 6, 2026 6:12pm | LeaningPole,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Premises closed
Non-Outage | J.E.26.07.04040 | C001841282 | Gregory Grossett | Portland | Completed | Load_253288 | Port Antonio - 410 | Jul 6, 2026 3:24pm | Jul 6, 2026 3:28pm | Jul 6, 2026 3:48pm | Jul 6, 2026 3:48pm | Jul 6, 2026 4:43pm | Jul 6, 2026 6:00pm | Jul 6, 2026 6:19pm | Jul 6, 2026 6:19pm |  |  | Fair | No | Open secondary neutral joints corroded also another customer 220 service neutral broken repair and ok material use 2 one bolt clamps 5ft of service neutral customers now ok.
Non-Outage | J.E.26.07.04883 | C001841280 | Ricky Hall | null | Completed | null | null | Jul 6, 2026 3:24pm | Jul 6, 2026 3:32pm | Jul 6, 2026 4:14pm | Jul 6, 2026 4:27pm | Jul 6, 2026 5:25pm | Jul 6, 2026 6:43pm | Jul 6, 2026 6:44pm | Jul 6, 2026 6:44pm | BrokenWire |  | Fair | No | Splice and retention broken 3W service use 1 automatic splice 3 clamps 120*2/240
Outage | J.E.26.07.04672 | C001841284 | Rodclif Dawkins | St.Catherine | Completed | Load_238151 | Twickenham - 310 | Jul 6, 2026 3:24pm | Jul 6, 2026 3:31pm | Jul 6, 2026 5:36pm | Jul 6, 2026 5:36pm | Jul 6, 2026 5:49pm | Jul 6, 2026 5:49pm | Jul 6, 2026 5:50pm | Jul 6, 2026 5:50pm |  |  | Fair | No | Prepaid account, please refer to Moses Elleston
Outage | J.E.26.07.04729 | C001841281 | Donald Cunningham | St.Catherine | Completed | Load_254609 | New Michelton - 310 | Jul 6, 2026 3:24pm | Jul 6, 2026 4:58pm | Jul 6, 2026 10:00pm | Jul 6, 2026 10:00pm | Jul 6, 2026 10:13pm | Jul 6, 2026 10:22pm | Jul 6, 2026 10:23pm | Jul 6, 2026 10:23pm |  |  | Fair | No | Premises closed
Outage | J.E.26.07.04897 | C001841283 | Wayne Dillion | Manchester | Completed | Load_261991 | Spur Tree - 210 | Jul 6, 2026 3:24pm | Jul 6, 2026 3:25pm | Jul 6, 2026 8:29pm | Jul 6, 2026 8:29pm | Jul 6, 2026 8:29pm | Jul 6, 2026 8:32pm | Jul 6, 2026 8:32pm | Jul 6, 2026 8:32pm |  |  | Fair | No | Call was related to a outage that was in the area today.
Outage | J.E.26.07.04927 | C001841272 | Barnett Brown | Manchester | Completed | Load_239023 | Spur Tree - 310 | Jul 6, 2026 3:22pm | Jul 6, 2026 3:23pm | Jul 6, 2026 5:59pm | Jul 6, 2026 5:59pm | Jul 6, 2026 7:12pm | Jul 6, 2026 7:45pm | Jul 6, 2026 7:45pm | Jul 6, 2026 7:45pm | BrokenWire |  | Fair | No | Remade service joint at secondary line
Outage | J.E.26.07.04950 | C001841273 | Richard Samuda | Manchester | Completed | Load_247561 | Kendal - 210 | Jul 6, 2026 3:22pm | Jul 6, 2026 3:23pm | Jul 6, 2026 3:40pm | Jul 6, 2026 5:14pm | Jul 6, 2026 5:14pm | Jul 6, 2026 5:15pm | Jul 6, 2026 5:15pm | Jul 6, 2026 5:15pm | TreeContact |  | Fair | No | Premises not located and call to check no answer
Outage | J.E.26.07.04560 | C001841262 | Roxroy Needham | St.Ann | Completed | Load_261857 | Cardiff Hall - 310 | Jul 6, 2026 3:18pm | Jul 6, 2026 3:19pm | Jul 6, 2026 4:39pm | Jul 6, 2026 4:39pm | Jul 6, 2026 6:03pm | Jul 6, 2026 6:30pm | Jul 6, 2026 6:30pm | Jul 6, 2026 6:30pm |  |  | Fair | No | Replace 1- 2 amp for a 10 KVA transformer (rami)
Outage | J.E.26.07.04931 | C001841263 | Daniel Francis | St.Ann | Completed | Load_260410 | Roaring River - 410 | Jul 6, 2026 3:18pm | Jul 6, 2026 3:20pm | Jul 6, 2026 6:23pm | Jul 6, 2026 6:23pm | Jul 6, 2026 6:47pm | Jul 6, 2026 6:50pm | Jul 6, 2026 6:51pm | Jul 6, 2026 6:51pm |  |  | Fair | No | Found ok power restored
Outage | J.E.26.07.04848 | C001841260 | Roxroy Needham | St.Ann | Completed | Load_247311 | Cardiff Hall - 210 | Jul 6, 2026 3:17pm | Jul 6, 2026 3:19pm | Jul 6, 2026 3:28pm | Jul 6, 2026 3:28pm | Jul 6, 2026 4:38pm | Jul 6, 2026 4:39pm | Jul 6, 2026 4:39pm | Jul 6, 2026 4:39pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.04923 | C001841261 | Daniel Francis | St.Ann | Completed | Load_255392 | Cardiff Hall - 210 | Jul 6, 2026 3:17pm | Jul 6, 2026 3:21pm | Jul 6, 2026 6:53pm | Jul 6, 2026 6:53pm | Jul 6, 2026 6:53pm | Jul 6, 2026 6:54pm | Jul 6, 2026 6:55pm | Jul 6, 2026 6:55pm |  |  | Fair | No | Found ok power restored P
Outage | J.E.26.07.04943 | C001841259 | Shamour Haughton | St.James | Completed | Load_292055 | Bogue - 310 | Jul 6, 2026 3:17pm | Jul 6, 2026 3:17pm | Jul 6, 2026 3:42pm | Jul 6, 2026 3:42pm | Jul 6, 2026 3:52pm | Jul 6, 2026 4:01pm | Jul 6, 2026 4:02pm | Jul 6, 2026 4:02pm | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Found 1,30ft pole broken caused by car, please refer to maintenance
Non-Outage | J.E.26.07.03898 | C001841252 | Dwayne Samuels | Trelawny | Completed | Load_246009 | Greenwood - 110 | Jul 6, 2026 3:12pm | Jul 6, 2026 3:13pm | Jul 6, 2026 9:08pm | Jul 6, 2026 9:08pm | Jul 6, 2026 9:08pm | Jul 6, 2026 9:27pm | Jul 6, 2026 9:27pm | Jul 6, 2026 9:27pm |  |  | Fair | No | When spoke with customer said they did not make a report and customer failed to to provide any direction to locate premise
Non-Outage | J.E.26.07.04811 | C001841249 | Dwayne Samuels | Trelawny | Completed | Load_266915 | Greenwood - 210 | Jul 6, 2026 3:12pm | Jul 6, 2026 3:13pm | Jul 6, 2026 3:37pm | Jul 6, 2026 6:38pm | Jul 6, 2026 7:25pm | Jul 6, 2026 8:10pm | Jul 6, 2026 8:11pm | Jul 6, 2026 8:11pm |  |  | Fair | No | Customer meter is burnt on load side and meter socket is defective voltage found in customer meter 117v/116v/233v customer was advised to get a electrician for internal repair and refer to field service to have meter replaced
Non-Outage | J.E.26.07.04933 | C001841251 | Dwayne Samuels | Trelawny | Completed | Load_246434 | Greenwood - 110 | Jul 6, 2026 3:12pm | Jul 6, 2026 3:13pm | Jul 6, 2026 3:40pm | Jul 6, 2026 3:41pm | Jul 6, 2026 4:58pm | Jul 6, 2026 5:30pm | Jul 6, 2026 5:30pm | Jul 6, 2026 5:30pm |  |  | Fair | No | Check and found working ok voltage found at meter 112v/110v/222v customer was advised to have a electrician do internal checks
Non-Outage | J.E.26.07.04936 | C001841250 | Dwayne Samuels | Trelawny | Completed | Load_247321 | Martha Brae - 110 | Jul 6, 2026 3:12pm | Jul 6, 2026 3:13pm | Jul 6, 2026 3:39pm | Jul 6, 2026 5:30pm | Jul 6, 2026 6:36pm | Jul 6, 2026 6:38pm | Jul 6, 2026 6:38pm | Jul 6, 2026 6:38pm |  |  | Fair | No | Customer meter socket is defective caused by a lizard use 2 one bolt clamp at pothead to repair corroded joints voltage left at meter 112v/113v/225v
Outage | J.E.26.07.04876 | C001841245 | Swon Miller | St.James | Completed | Load_302057 | Queens Drive - 810 | Jul 6, 2026 3:09pm | Jul 6, 2026 3:10pm | Jul 6, 2026 5:35pm | Jul 6, 2026 5:35pm | Jul 6, 2026 5:54pm | Jul 6, 2026 6:41pm | Jul 6, 2026 6:59pm | Jul 6, 2026 6:59pm |  |  | Fair | No | Found one 80 amp junction fuse blown one 25 amp fuse blown cause by banging conductors replace one 80 amp junction fuse at pole number 200348 and one 25 amp junction fuse voltage found 0.000 voltage left 116/117/234
Outage | J.E.26.07.04920 | C001841244 | Swon Miller | St.James | Completed | Load_261444 | Queens Drive - 710 | Jul 6, 2026 3:09pm | Jul 6, 2026 3:10pm | Jul 6, 2026 8:24pm | Jul 6, 2026 8:24pm | Jul 6, 2026 9:08pm | Jul 21, 2026 9:20pm | Jul 6, 2026 9:20pm | Jul 6, 2026 9:20pm |  |  | Fair | No | Check and found area okay voltage found 115/114/232 customer states that the problem has been resolved voltage left 114/115/232
Outage | J.E.26.07.04929 | C001841246 | Swon Miller | St.James | Completed | Load_302143 | Queens Drive - 710 | Jul 6, 2026 3:09pm | Jul 6, 2026 3:10pm | Jul 6, 2026 7:17pm | Jul 6, 2026 7:17pm | Jul 6, 2026 7:54pm | Jul 27, 2026 8:24am | Jul 6, 2026 8:24pm | Jul 6, 2026 8:24pm |  |  | Fair | No | Found customer service wire disconnected for nonpayment of bill voltage found 0.000 clean and remake joints use 2pg voltage left 115/114/232
Outage | J.E.26.07.04941 | C001841247 | Swon Miller | St.James | Completed | Load_267656 | Queens Drive - 710 | Jul 6, 2026 3:09pm | Jul 6, 2026 3:10pm | Jul 6, 2026 3:25pm | Jul 6, 2026 3:25pm | Jul 6, 2026 3:59pm | Jul 14, 2026 5:10am | Jul 6, 2026 5:35pm | Jul 6, 2026 5:35pm |  |  | Fair | No | Found 2 span of secondary phase down cause by sagging conductors used 30ft # 2 aaAA conductors 1 2/o preform and 2pg to carry out repairs voltage found 0.000. Voltage left 115/115/232
Outage | J.E.26.07.04797 | C001841243 | Swon Miller | St.James | Completed | Load_239994 | Queens Drive - 710 | Jul 6, 2026 3:08pm | Jul 6, 2026 3:10pm | Jul 6, 2026 9:20pm | Jul 6, 2026 9:20pm | Jul 6, 2026 10:15pm | Jul 6, 2026 10:40pm | Jul 6, 2026 10:44pm | Jul 6, 2026 10:44pm | BrokenWire |  | Fair | No | Check and found okay voltage found 116/115/233 voltage left 115/116/233
Outage | J.E.26.07.04894 | C001841145 | Elvis Trowers | KSAN | Completed | Load_248638 | Constant Spring - 210 | Jul 6, 2026 2:02pm | Jul 6, 2026 2:02pm | Jul 6, 2026 2:53pm | Jul 6, 2026 2:53pm | Jul 6, 2026 3:31pm | Jul 6, 2026 3:46pm | Jul 6, 2026 3:47pm | Jul 6, 2026 3:47pm |  | Y | Fair | Yes | A section checked out and found without electricity supply and a blown 3 amp transformer fuse was found and replaced after patrol was completed at pole #0011848.
Outage | J.E.26.07.04892 | C001841141 | Barnett Brown | Manchester | Completed | Load_268132 | Spur Tree - 310 | Jul 6, 2026 1:54pm | Jul 6, 2026 3:20pm | Jul 6, 2026 3:41pm | Jul 6, 2026 3:41pm | Jul 6, 2026 4:55pm | Jul 6, 2026 5:55pm | Jul 6, 2026 5:59pm | Jul 6, 2026 5:59pm |  |  | Fair | No | Cut and clear tree, balance secondary line, replace blown 3 amp transformer fuse
Outage | J.E.26.07.04870 | C001841134 | Daniel Francis | Clarendon | Completed | Load_353287 | May Pen - 110 | Jul 6, 2026 1:46pm | Jul 6, 2026 4:47pm | Jul 6, 2026 6:56pm | Jul 6, 2026 6:56pm | Jul 6, 2026 9:35pm | Jul 6, 2026 9:40pm | Jul 6, 2026 9:40pm | Jul 6, 2026 9:40pm |  |  | Fair | No | Pole # 204553 change one 8 amp fuse
Outage | J.E.26.07.04639 | C001841132 | Ricky Hall | St.Catherine | Completed | Load_252827 | Rhodens Pen - 210 | Jul 6, 2026 1:45pm | Jul 6, 2026 5:04pm | Jul 6, 2026 7:16pm | Jul 6, 2026 7:16pm | Jul 6, 2026 8:20pm | Jul 6, 2026 8:38pm | Jul 6, 2026 8:38pm | Jul 6, 2026 8:38pm |  |  | Fair | No | Daylight attention required area unsafe
Outage | J.E.26.07.04887 | C001841133 | Christopher Edwards | KSAN | Completed | Load_251063 | Constant Spring - 410 | Jul 6, 2026 1:45pm | Jul 7, 2026 7:25am | Jul 7, 2026 12:05pm | Jul 7, 2026 12:05pm | Jul 7, 2026 12:11pm | Jul 7, 2026 12:41pm | Jul 7, 2026 12:44pm | Jul 7, 2026 12:44pm |  |  | Fair | No | Remake corroded phase joint Using (2) one bolt clamps AlsoVoltage:115,vCustomer has 110 meter
Non-Outage | J.E.26.07.04866 | C001841124 | Hartley Chin | null | Completed | null | null | Jul 6, 2026 1:43pm | Jul 6, 2026 1:43pm | Jul 6, 2026 2:51pm | Jul 6, 2026 4:46pm | Jul 6, 2026 4:58pm | Jul 6, 2026 5:03pm | Jul 6, 2026 5:04pm | Jul 6, 2026 5:04pm | BrokenWire |  | Fair | No | Premise not found. Unable to contact customer ,phone is ringing but no response. Area patrolled an found ok.
Outage | J.E.26.07.02099 | C001841129 | Richard Grant | St.Catherine | Completed | Load_260364 | New Michelton - 310 | Jul 6, 2026 1:43pm | Jul 6, 2026 1:44pm | Jul 6, 2026 2:53pm | Jul 6, 2026 2:53pm | Jul 6, 2026 2:53pm | Jul 6, 2026 2:54pm | Jul 6, 2026 2:54pm | Jul 6, 2026 2:54pm |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.04877 | C001841130 | Edward Royal | KSAN | Completed | Load_270241 | Washington Blvd - 410 | Jul 6, 2026 1:43pm | Jul 6, 2026 1:44pm | Jul 6, 2026 2:40pm | Jul 6, 2026 2:40pm | Jul 6, 2026 2:40pm | Jul 6, 2026 2:42pm | Jul 6, 2026 2:42pm | Jul 6, 2026 2:42pm |  |  | Fair | No | Premises found close
Non-Outage | J.E.26.07.04539 | C001841114 | Oraine Minto | St.Ann | Completed | Load_266903 | Ocho Rios - 310 | Jul 6, 2026 1:33pm | Jul 7, 2026 7:57am | Jul 7, 2026 11:43am | Jul 7, 2026 11:43am | Jul 7, 2026 12:51pm | Jul 7, 2026 12:51pm | Jul 7, 2026 12:52pm | Jul 7, 2026 12:52pm |  |  | Fair | No | 238v 118v 119v
Non-Outage | J.E.26.07.04868 | C001841115 | Rusean Allen | KSAS | Completed | Load_300824 | Cane River - 410 | Jul 6, 2026 1:33pm | Jul 6, 2026 1:38pm | Jul 7, 2026 12:25am | Jul 7, 2026 12:25am | Jul 7, 2026 3:44am | Jul 7, 2026 3:45am | Jul 7, 2026 3:45am | Jul 7, 2026 3:45am | BrokenWire |  | Fair | No | More info needed
Non-Outage | J.E.26.07.00910 | C001841113 | Fitzroy Turner | KSAS | Completed | Load_249899 | Hunts Bay - 110 | Jul 6, 2026 1:31pm | Jul 6, 2026 1:36pm | Jul 6, 2026 2:07pm | Jul 6, 2026 2:07pm | Jul 6, 2026 2:43pm | Jul 6, 2026 2:59pm | Jul 6, 2026 3:02pm | Jul 6, 2026 3:02pm |  |  | Fair | No | Found bank of three transformer one 167 and 2 100kva transformer one fuse blown replace one 10amps fuses supply restored to customer
Outage | J.E.26.07.04815 | C001841102 | Richman Whyte | Westmoreland | Completed | Load_241093 | Paradise - 310 | Jul 6, 2026 1:19pm | Jul 6, 2026 4:14pm | Jul 6, 2026 8:19pm | Jul 6, 2026 8:19pm | Jul 6, 2026 8:19pm | Jul 6, 2026 8:53pm | Jul 6, 2026 8:54pm | Jul 6, 2026 8:54pm |  |  | Fair | No | Need daylight attention premises lock
Non-Outage | J.E.26.07.04674 | C001841100 | Moses Elliston | null | Completed | null | null | Jul 6, 2026 1:17pm | Jul 6, 2026 1:17pm | Jul 6, 2026 1:27pm | Jul 6, 2026 1:27pm | Jul 6, 2026 1:27pm | Jul 6, 2026 12:14pm | Jul 6, 2026 1:29pm | Jul 6, 2026 1:29pm |  |  | Fair | No | Credit added to prepaid account
Non-Outage | J.E.26.07.04853 | C001841094 | Derrick Dawkins | St.James | Completed | Load_242384 | Bogue - 310 | Jul 6, 2026 1:13pm | Jul 6, 2026 1:14pm | Jul 6, 2026 2:30pm | Jul 7, 2026 12:03pm | Jul 7, 2026 12:03pm | Jul 7, 2026 12:04pm | Jul 7, 2026 12:05pm | Jul 7, 2026 12:05pm |  |  | Fair | No | Unable to reach customer due to vehicle accident on the road
Outage | J.E.26.07.04847 | C001841086 | Barrington Brown | St.James | Completed | Load_293371 | Queens Drive - 310 | Jul 6, 2026 1:05pm | Jul 6, 2026 1:09pm | Jul 6, 2026 1:13pm | Jul 6, 2026 1:49pm | Jul 6, 2026 1:49pm | Jul 6, 2026 2:49pm | Jul 6, 2026 2:49pm | Jul 6, 2026 2:49pm |  |  | SevereWind | No | 20 amps junction fuse found blown on location no pole #. Removed bird from primary conductor then replaced fuse all customers restored
Outage | J.E.26.07.04777 | C001841074 | Hartley Chin | Clarendon | Completed | Load_255084 | Monymusk - 410 | Jul 6, 2026 12:58pm | Jul 6, 2026 1:07pm | Jul 6, 2026 3:02pm | Jul 6, 2026 5:04pm | Jul 6, 2026 5:13pm | Jul 6, 2026 5:39pm | Jul 6, 2026 5:42pm | Jul 6, 2026 5:42pm | BrokenWire |  | Fair | No | Isolate 15 KVA transformer @ pole # 0156577 due to broken open secondary phase found in 1 span , repair broken joint … re-energized transformer…. Use : 20 ft conductor , 2 clamp …
Non-Outage | J.E.26.07.04795 | C001841046 | Denton Williams | null | Completed | null | null | Jul 6, 2026 12:34pm | Jul 6, 2026 12:34pm | Jul 6, 2026 12:59pm | Jul 6, 2026 1:27pm | Jul 6, 2026 3:04pm | Jul 6, 2026 3:07pm | Jul 6, 2026 3:11pm | Jul 6, 2026 3:11pm | Fire |  | Fair | No | Customer not found, nobody in the area knows the name of customer. No, fire observed on service wire.
Outage | J.E.26.07.04791 | C001841032 | Derrick Dawkins | St.James | Completed | Load_412876 | Bogue - 310 | Jul 6, 2026 12:28pm | Jul 6, 2026 12:29pm | Jul 6, 2026 12:32pm | Jul 6, 2026 12:32pm | Jul 6, 2026 12:47pm | Jul 6, 2026 12:47pm | Jul 6, 2026 12:50pm | Jul 6, 2026 12:50pm |  |  | Fair | No | Planned outaged
Non-Outage | J.E.26.07.04753 | C001841030 | Marlon Brown | Trelawny | Completed | Load_251680 | Martha Brae - 210 | Jul 6, 2026 12:23pm | Jul 6, 2026 1:01pm | Jul 6, 2026 1:09pm | Jul 6, 2026 1:09pm | Jul 6, 2026 1:10pm | Jul 6, 2026 1:29pm | Jul 6, 2026 1:29pm | Jul 6, 2026 1:29pm |  |  | Fair | No | Check and found ok Voltage found at meter socket 114/116=230Voltage leaving at meter socket 114/116=230. Customer having internal issues.
Non-Outage | J.E.26.07.04772 | C001841020 | Fitzroy Turner | KSAS | Completed | Load_262186 | Hunts Bay - 210 | Jul 6, 2026 12:15pm | Jul 6, 2026 12:15pm | Jul 6, 2026 12:45pm | Jul 6, 2026 12:45pm | Jul 6, 2026 12:45pm | Jul 6, 2026 12:47pm | Jul 6, 2026 12:58pm | Jul 6, 2026 12:58pm |  |  | Fair | No | Found three phases primary underground cables burnt off at the cross arm needs to take down and splice and reconnected CUSTOMERS OUT
Outage | J.E.26.07.04770 | C001841015 | Rayon Foster | Hanover | Completed | Load_269922 | Orange Bay - 310 | Jul 6, 2026 12:13pm | Jul 6, 2026 12:13pm | Jul 6, 2026 1:51pm | Jul 6, 2026 1:51pm | Jul 6, 2026 1:51pm | Jul 6, 2026 2:43pm | Jul 6, 2026 2:43pm | Jul 6, 2026 2:43pm |  |  | Fair | No | Defective meter socket customer was advised to have meter socket changed incoming voltage from jps 113/114AB 227volts
Outage | J.E.26.07.04757 | C001841013 | Milton Charlton | KSAN | Completed | Load_255354 | Hope - 510 | Jul 6, 2026 12:10pm | Jul 6, 2026 12:11pm | Jul 6, 2026 1:40pm | Jul 6, 2026 1:40pm | Jul 6, 2026 2:54pm | Jul 6, 2026 3:00pm | Jul 6, 2026 2:55pm | Jul 6, 2026 2:55pm |  |  | Fair | No | Found one 15 amps junction fuse blown at pole #617988. Refused using one 15 amps fuse and reclosed junction switch.
Non-Outage | J.E.26.07.04763 | C001841012 | Richard Watson | null | Completed | null | null | Jul 6, 2026 12:09pm | Jul 6, 2026 12:09pm | Jul 6, 2026 12:27pm | Jul 6, 2026 12:27pm | Jul 6, 2026 1:13pm | Jul 6, 2026 1:35pm | Jul 6, 2026 1:46pm | Jul 6, 2026 1:46pm |  |  | Fair | No | Load reading taken at 10kva transformer, 34amp, 46.7amp and 10.2amp through neutral, voltage readings at transformer 110v, 110v, 220v and voltage readings at customer premises 105v, 111v, 216v, please refer to maintenance department for transformer upgrade or splitting circuit.transformer also leaking oil at trip switch.
Non-Outage | J.E.26.06.32877 | C001841005 | Fitzroy Turner | KSAS | Completed | Load_570293 | Hunts Bay - 210 | Jul 6, 2026 12:07pm | Jul 6, 2026 12:07pm | Jul 6, 2026 1:10pm | Jul 6, 2026 1:10pm | Jul 6, 2026 1:58pm | Jul 6, 2026 2:02pm | Jul 6, 2026 2:07pm | Jul 6, 2026 2:07pm |  |  | Fair | No | Readings at customer meter socket and breaker box 118/119/238 208/ 238/239 customer install equipment in breaker box that readings 242 voltage cross phases at 1:30 pm customer advised to have electrician check equipment
Non-Outage | J.E.26.07.04658 | C001841004 | Lancelot Brown | Hanover | Completed | Load_259222 | Orange Bay - 310 | Jul 6, 2026 12:05pm | Jul 6, 2026 3:51pm | Jul 6, 2026 4:26pm | Jul 6, 2026 7:26pm | Jul 6, 2026 7:26pm | Jul 6, 2026 8:13pm | Jul 6, 2026 8:13pm | Jul 6, 2026 8:13pm |  |  | Rains | No | Please carry forward for daylight attention on the 07-07-2026
Non-Outage | J.E.26.07.04734 | C001840996 | Dwain Samuels | Westmoreland | Completed | Load_254469 | Paradise - 110 | Jul 6, 2026 12:00pm | Jul 6, 2026 12:00pm | Jul 6, 2026 12:11pm | Jul 6, 2026 12:12pm | Jul 6, 2026 12:12pm | Jul 6, 2026 12:20pm | Jul 6, 2026 12:21pm | Jul 6, 2026 12:21pm |  |  | Fair | No | Found service wire damaged. Replaced 17feet of service wire
Non-Outage | J.E.26.07.04744 | C001840953 | Romeo Brissett | null | Completed | null | null | Jul 6, 2026 11:44am | Jul 6, 2026 11:47am | Jul 6, 2026 1:04pm | Jul 6, 2026 1:04pm | Jul 6, 2026 1:22pm | Jul 6, 2026 1:42pm | Jul 6, 2026 1:43pm | Jul 6, 2026 1:43pm |  |  | Fair | No | Line patrolled and found power in area , not getting through with customer on the phone.
Outage | J.E.26.07.04739 | C001840941 | Floyd Taylor | Trelawny | Completed | Load_302923 | Greenwood - 110 | Jul 6, 2026 11:43am | Jul 6, 2026 11:47am | Jul 6, 2026 12:09pm | Jul 6, 2026 12:09pm | Jul 6, 2026 1:01pm | Jul 6, 2026 1:21pm | Jul 6, 2026 1:28pm | Jul 6, 2026 1:28pm | LeaningPole |  | Fair | No | Customer meter pole leaning customer was advised to get an electrician
Non-Outage | J.E.26.07.04299 | C001840937 | Fredrick Hamilton | KSAN | Completed | Load_266843 | Hope - 410 | Jul 6, 2026 11:42am | Jul 6, 2026 11:43am | Jul 6, 2026 12:07pm | Jul 6, 2026 1:48pm | Jul 6, 2026 1:48pm | Jul 6, 2026 1:52pm | Jul 6, 2026 1:52pm | Jul 6, 2026 1:52pm |  |  | Fair | No | Premises found located at time of visit Unable to access apartment complex customer not home at time of visit
Non-Outage | J.E.26.07.04616 | C001840939 | Fredrick Hamilton | KSAN | Completed | Load_249087 | West Kings House - 410 | Jul 6, 2026 11:42am | Jul 6, 2026 11:43am | Jul 6, 2026 12:07pm | Jul 6, 2026 1:17pm | Jul 6, 2026 1:28pm | Jul 6, 2026 1:38pm | Jul 6, 2026 1:39pm | Jul 6, 2026 1:39pm |  |  | Fair | No | 240v/119v/119v obtained Low voltageNo issue detected on the JPS supply Customer advised to have electrician do internal checks
Non-Outage | J.E.26.07.04668 | C001840938 | Rochaine Hussey | KSAN | Completed | Load_262953 | Constant Spring - 410 | Jul 6, 2026 11:42am | Jul 6, 2026 11:42am | Jul 7, 2026 3:32pm | Jul 7, 2026 3:32pm | Jul 7, 2026 3:33pm | Jul 7, 2026 3:45pm | Jul 7, 2026 3:45pm | Jul 7, 2026 3:45pm |  |  | Fair | No | Customer is called multiple time and no answer Unable to locate Premesis
Non-Outage | J.E.26.06.29318 | C001840936 | Milton Charlton | KSAN | Completed | Load_248378 | Hope - 410 | Jul 6, 2026 11:41am | Jul 6, 2026 11:41am | Jul 6, 2026 12:49pm | Jul 6, 2026 12:49pm | Jul 6, 2026 1:38pm | Jul 6, 2026 1:35pm | Jul 6, 2026 1:40pm | Jul 6, 2026 1:40pm |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.07.04711 | C001840927 | Javid Vernon | Westmoreland | Completed | Load_263776 | Paradise - 310 | Jul 6, 2026 11:35am | Jul 6, 2026 11:36am | Jul 6, 2026 12:05pm | Jul 6, 2026 12:06pm | Jul 6, 2026 12:06pm | Jul 6, 2026 12:09pm | Jul 6, 2026 12:09pm | Jul 6, 2026 12:09pm |  |  | Fair | No | Customer stated she has power at her premises she is just making a report for a next customer in Hanover parish refer to Hanover crew
Non-Outage | J.E.26.07.04630 | C001840921 | Hartley Chin | Clarendon | Completed | Load_254018 | Monymusk - 410 | Jul 6, 2026 11:25am | Jul 6, 2026 11:25am | Jul 6, 2026 2:51pm | Jul 6, 2026 3:02pm | Jul 6, 2026 4:03pm | Jul 6, 2026 4:10pm | Jul 6, 2026 4:11pm | Jul 6, 2026 4:11pm | BrokenWire |  | Fair | No | Note : customer service wire is not broken … however customer Stantion is broken … she requested to have service wire retention but customer was advised to fix stantion and make another report to re-tension service wire ..
Non-Outage | J.E.26.07.04637 | C001840919 | Clyde Brown | null | Completed | null | null | Jul 6, 2026 11:24am | Jul 6, 2026 5:46pm | Jul 6, 2026 7:42pm | Jul 6, 2026 7:42pm | Jul 6, 2026 8:04pm | Jul 6, 2026 8:26pm | Jul 6, 2026 8:34pm | Jul 6, 2026 8:34pm |  |  | Fair | No | Blown 3 amps fuse for 25 kva transformer,line patrolled and no fault seen,blown fuse replaced.
Non-Outage | J.E.26.07.04701 | C001840920 | Hartley Chin | null | Completed | null | null | Jul 6, 2026 11:24am | Jul 6, 2026 11:25am | Jul 6, 2026 2:51pm | Jul 6, 2026 4:11pm | Jul 6, 2026 4:43pm | Jul 6, 2026 4:45pm | Jul 6, 2026 4:46pm | Jul 6, 2026 4:46pm |  |  | Fair | No | Contacted escalation… customer is now connected… HX 23632479 …
Outage | J.E.26.07.04714 | C001840887 | Stephen Taylor | St.Thomas | Completed | Load_263661 | Good Year - 110 | Jul 6, 2026 11:00am | Jul 7, 2026 7:35am | Jul 7, 2026 3:47pm | Jul 7, 2026 3:47pm | Jul 7, 2026 3:47pm | Jul 7, 2026 3:47pm | Jul 7, 2026 3:48pm | Jul 7, 2026 3:48pm | LeaningPole |  | Fair | No | Need more information a lot of call to customer no one answered the phone
Outage | J.E.26.07.04623 | C001840854 | Wan Carlos Scarlett | St.Catherine | Completed | Load_264213 | Twickenham - 210 | Jul 6, 2026 10:43am | Jul 6, 2026 10:44am | Jul 6, 2026 11:39am | Jul 6, 2026 11:39am | Jul 6, 2026 11:49am | Jul 6, 2026 12:41pm | Jul 6, 2026 12:42pm | Jul 6, 2026 12:42pm |  |  | Fair | No | Found customer with internal problem advised customer to get a licensed electrician to fix the problem.found wires from meter socket to breaker defective
Outage | J.E.26.07.04706 | C001840852 | Dwain Samuels | Westmoreland | Completed | Load_254487 | Paradise - 110 | Jul 6, 2026 10:43am | Jul 6, 2026 10:43am | Jul 6, 2026 12:00pm | Jul 6, 2026 12:24pm | Jul 6, 2026 12:24pm | Jul 6, 2026 12:26pm | Jul 6, 2026 12:27pm | Jul 6, 2026 12:27pm |  |  | Fair | No | Connected 3 wire meter
Outage | J.E.26.07.04638 | C001840851 | Nickolas Rodriques | St.Catherine | Completed | Load_267740 | Tredegar - 410 | Jul 6, 2026 10:39am | Jul 6, 2026 10:39am | Jul 6, 2026 12:26pm | Jul 6, 2026 12:39pm | Jul 6, 2026 1:04pm | Jul 6, 2026 1:26pm | Jul 6, 2026 1:30pm | Jul 6, 2026 1:30pm |  |  | Fair | No | Customer stated that he is having low voltage. Checks were done and it was found that the customer 4w meter socket is defective. Isolate customer pothead for safety to repair. The customer was advised to consult a licensed electrician to do repairs.
Outage | J.E.26.07.04676 | C001840850 | Moses Elliston | St.Catherine | Completed | Load_268274 | Tredegar - 410 | Jul 6, 2026 10:39am | Jul 6, 2026 11:35am | Jul 6, 2026 2:39pm | Jul 6, 2026 2:39pm | Jul 6, 2026 2:39pm | Jul 6, 2026 2:25pm | Jul 6, 2026 2:44pm | Jul 6, 2026 2:44pm |  |  | Fair | No | 109-109-218 volts at meter socket.Customer not at home for further checks
Non-Outage | J.E.26.07.04695 | C001840843 | Rayon Foster | null | Completed | null | null | Jul 6, 2026 10:36am | Jul 6, 2026 10:37am | Jul 6, 2026 11:19am | Jul 6, 2026 11:55am | Jul 6, 2026 11:55am | Jul 6, 2026 12:00pm | Jul 6, 2026 12:03pm | Jul 6, 2026 12:03pm |  |  | Fair | No | Patrol secondary to find 1 blown 25kva transformer fuse isolate cable wire from banging with the lower secondary phase and replace 1 3amp transformer fuse at same and close
Outage | J.E.26.07.04697 | C001840841 | Neckell Ormsby | St.Mary | Completed | Load_240991 | Blackstonedge - 110 | Jul 6, 2026 10:35am | Jul 6, 2026 3:43pm | Jul 6, 2026 3:49pm | Jul 6, 2026 3:49pm | Jul 6, 2026 5:11pm | Jul 6, 2026 5:33pm | Jul 6, 2026 5:33pm | Jul 6, 2026 5:33pm |  |  | Fair | No | Unable to locate customer after several calls however found supply ok in area
Outage | J.E.26.07.04699 | C001840842 | Raymond Lewis | St.Ann | Completed | Load_242953 | Roaring River - 410 | Jul 6, 2026 10:35am | Jul 6, 2026 10:36am | Jul 6, 2026 11:25am | Jul 6, 2026 12:42pm | Jul 6, 2026 1:34pm | Jul 6, 2026 1:35pm | Jul 6, 2026 1:35pm | Jul 6, 2026 1:35pm |  |  | Fair | No | Phone not answering
Non-Outage | J.E.26.07.02040 | C001840840 | Wan Carlos Scarlett | Portmore | Completed | Load_249133 | Naggo Head - 510 | Jul 6, 2026 10:34am | Jul 6, 2026 10:35am | Jul 6, 2026 10:52am | Jul 6, 2026 10:52am | Jul 6, 2026 11:03am | Jul 6, 2026 11:36am | Jul 6, 2026 11:39am | Jul 6, 2026 11:39am |  |  | Fair | No | Found customer 3 wire service at pole with 1 of the phase wire broken off use 1 one bolt clamp at pole readings 116 116 232
Non-Outage | J.E.26.07.04620 | C001840817 | Romeo Brissett | St.James | Completed | Load_302114 | Bogue - 610 | Jul 6, 2026 10:24am | Jul 6, 2026 10:34am | Jul 6, 2026 11:43am | Jul 6, 2026 11:43am | Jul 6, 2026 12:27pm | Jul 6, 2026 12:55pm | Jul 6, 2026 1:04pm | Jul 6, 2026 1:04pm |  |  | Fair | No | Used 2 clamps on pothead V/R 114-116-230
Non-Outage | J.E.26.07.04634 | C001840818 | Romeo Brissett | St.James | Completed | Load_239811 | Bogue - 610 | Jul 6, 2026 10:24am | Jul 6, 2026 10:34am | Jul 6, 2026 11:41am | Jul 6, 2026 11:41am | Jul 6, 2026 11:42am | Jul 6, 2026 11:42am | Jul 6, 2026 11:43am | Jul 6, 2026 11:43am |  |  | Fair | No | Check and found ok, customer stated power restored.
Outage | J.E.26.07.04665 | C001840815 | Stephen Taylor | St.Thomas | Completed | Load_256242 | Lysson - 410 | Jul 6, 2026 10:24am | Jul 6, 2026 10:24am | Jul 6, 2026 11:25am | Jul 6, 2026 11:25am | Jul 6, 2026 12:24pm | Jul 6, 2026 12:24pm | Jul 6, 2026 12:26pm | Jul 6, 2026 12:26pm |  |  | Fair | No | Clean up single phase use 2 clamps reading 112,223,225 customer is now okay
Outage | J.E.26.07.04690 | C001840816 | Stephen Taylor | St.Thomas | Completed | Load_254225 | Lysson - 410 | Jul 6, 2026 10:24am | Jul 7, 2026 7:33am | Jul 7, 2026 11:17am | Jul 7, 2026 11:17am | Jul 7, 2026 11:18am | Jul 7, 2026 11:18am | Jul 7, 2026 11:19am | Jul 7, 2026 11:19am |  |  | Fair | No | Patrol the area power is in the area a lot of call to customer no one answered the phone
Outage | J.E.26.07.04689 | C001840803 | Edward Royal | KSAN | Completed | Load_270241 | Washington Blvd - 410 | Jul 6, 2026 10:20am | Jul 6, 2026 10:21am | Jul 6, 2026 11:18am | Jul 6, 2026 11:18am | Jul 6, 2026 11:18am | Jul 6, 2026 11:18am | Jul 6, 2026 11:18am | Jul 6, 2026 11:18am |  |  | Fair | No | When contacted customer said that no one is at home
Non-Outage | J.E.26.07.04598 | C001840800 | Locksley Allen | St.Mary | Completed | Load_248758 | Blackstonedge - 110 | Jul 6, 2026 10:15am | Jul 6, 2026 10:15am | Jul 6, 2026 12:13pm | Jul 6, 2026 1:32pm | Jul 6, 2026 1:32pm | Jul 6, 2026 2:02pm | Jul 6, 2026 2:01pm | Jul 6, 2026 2:01pm |  |  | Fair | No | Meter found blank,low voltage problem found at the premises. Several customers in this area is having the same problem.The switch at the transformer is open and the secondary lines are touching
Non-Outage | J.E.26.06.02232 | C001840798 | Orville Lee | Portmore | Completed | Load_252770 | Naggo Head - 610 | Jul 6, 2026 10:14am | Jul 6, 2026 10:14am | Jul 6, 2026 11:06am | Jul 6, 2026 12:44pm | Jul 6, 2026 1:17pm | Jul 6, 2026 1:21pm | Jul 6, 2026 1:21pm | Jul 6, 2026 1:21pm |  |  | Fair | No | Checks made and found pothead connection corroded 2 Penn union and 1 one bolt clamp usedVoltage 119V120V240V
Non-Outage | J.E.26.07.04430 | C001840799 | Locksley Allen | St.Mary | Completed | Load_238714 | Highgate -110 | Jul 6, 2026 10:14am | Jul 6, 2026 10:15am | Jul 7, 2026 9:39am | Jul 7, 2026 10:42am | Jul 7, 2026 10:42am | Jul 7, 2026 10:47am | Jul 7, 2026 10:46am | Jul 7, 2026 10:46am |  |  | Fair | No | Meter socket defective,customer was advised to change as soon as possible. Voltage at meter socket phase to phase 234vPhase to neutral 117&117v
Non-Outage | J.E.26.07.04661 | C001840793 | Damion Reid | Trelawny | Completed | Load_245410 | Duncans - 210 | Jul 6, 2026 10:11am | Jul 6, 2026 10:15am | Jul 6, 2026 1:15pm | Jul 6, 2026 1:15pm | Jul 6, 2026 2:40pm | Jul 6, 2026 2:40pm | Jul 6, 2026 2:40pm | Jul 6, 2026 2:40pm |  |  | Fair | No | Unable to contact or locate customer
Outage | J.E.26.07.04669 | C001840792 | Denton Williams | Portland | Completed | Load_250722 | Port Antonio - 410 | Jul 6, 2026 10:11am | Jul 6, 2026 10:11am | Jul 6, 2026 11:13am | Jul 6, 2026 11:13am | Jul 6, 2026 11:13am | Jul 6, 2026 11:13am | Jul 6, 2026 11:17am | Jul 6, 2026 11:17am | LowHangingWires |  | Fair | No | Trailer truck allegedly pulled down customer service line, resulting broken wire. Remove broken service line and reconnect customer with another existing service line that was not in use.
Non-Outage | J.E.26.07.01859 | C001840784 | Orville Lee | Portmore | Completed | Load_576149 | Naggo Head - 610 | Jul 6, 2026 10:10am | Jul 6, 2026 10:10am | Jul 6, 2026 1:23pm | Jul 6, 2026 1:23pm | Jul 6, 2026 1:52pm | Jul 6, 2026 2:36pm | Jul 6, 2026 2:37pm | Jul 6, 2026 2:37pm |  |  | Fair | No | Premise found ok upon arrival Issue was resolved by a technician
Non-Outage | J.E.26.07.01884 | C001840785 | Orville Lee | Portmore | Completed | Load_576227 | Naggo Head - 610 | Jul 6, 2026 10:10am | Jul 6, 2026 10:10am | Jul 6, 2026 11:06am | Jul 6, 2026 11:08am | Jul 6, 2026 11:10am | Jul 6, 2026 11:23am | Jul 6, 2026 11:23am | Jul 6, 2026 11:23am |  |  | Fair | No
Non-Outage | J.E.26.07.01902 | C001840786 | Orville Lee | Portmore | Completed | Load_253066 | Naggo Head - 610 | Jul 6, 2026 10:10am | Jul 6, 2026 10:10am | Jul 6, 2026 10:16am | Jul 6, 2026 11:24am | Jul 6, 2026 11:30am | Jul 6, 2026 12:01pm | Jul 6, 2026 12:02pm | Jul 6, 2026 12:02pm | LowHangingWires |  | Fair | No | Customer is requesting for secondary line to be removed and push away from touching his house.
Non-Outage | J.E.26.07.01909 | C001840787 | Orville Lee | Portmore | Completed | Load_243381 | Naggo Head - 610 | Jul 6, 2026 10:10am | Jul 6, 2026 10:10am | Jul 6, 2026 10:16am | Jul 6, 2026 12:02pm | Jul 6, 2026 12:22pm | Jul 6, 2026 12:38pm | Jul 6, 2026 12:39pm | Jul 6, 2026 12:39pm |  |  | Fair | No | Customer meter socket load wire and terminals burnVoltage 119V120V240VCustomer was advised to get defective meter Socket repair by an electrician
Non-Outage | J.E.26.07.01909 | C001840788 | Orville Lee | Portmore | Completed | Load_243381 | Naggo Head - 610 | Jul 6, 2026 10:10am | Jul 6, 2026 10:10am | Jul 6, 2026 10:16am | Jul 6, 2026 3:41pm | Jul 6, 2026 3:58pm | Jul 6, 2026 4:03pm | Jul 6, 2026 4:03pm | Jul 6, 2026 4:03pm |  |  | Fair | No | Customer meter socket load wire and terminals burnVoltage 119v120v240V Customer was advised to get defective meter socket repair
Non-Outage | J.E.26.06.38003 | C001840774 | Royston Montague | St.Catherine | Completed | Load_248862 | Tredegar - 510 | Jul 6, 2026 10:08am | Jul 6, 2026 10:10am | Jul 6, 2026 10:16am | Jul 6, 2026 3:09pm | Jul 6, 2026 4:05pm | Jul 6, 2026 4:16pm | Jul 6, 2026 4:16pm | Jul 6, 2026 4:16pm |  |  | Fair | No | Phone number not correct. Person answered the call said she didn’t make a report and she don’t know who is Clive Johnson.
Non-Outage | J.E.26.06.39573 | C001840773 | Royston Montague | St.Catherine | Completed | Load_293982 | Tredegar - 210 | Jul 6, 2026 10:08am | Jul 6, 2026 10:09am | Jul 6, 2026 10:16am | Jul 6, 2026 12:49pm | Jul 6, 2026 2:08pm | Jul 6, 2026 2:11pm | Jul 6, 2026 2:11pm | Jul 6, 2026 2:11pm |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.07.00250 | C001840772 | Royston Montague | St.Catherine | Completed | Load_245774 | Tredegar - 210 | Jul 6, 2026 10:08am | Jul 6, 2026 10:09am | Jul 6, 2026 10:16am | Jul 6, 2026 12:12pm | Jul 6, 2026 12:23pm | Jul 6, 2026 12:29pm | Jul 6, 2026 12:48pm | Jul 6, 2026 12:48pm | BrokenPole |  | Fair | No | Broken pole with telecommunications wires. Customer ask to contact same. Wires do belong to JPS.
Non-Outage | J.E.26.07.00581 | C001840771 | Royston Montague | St.Catherine | Completed | Load_251480 | Tredegar - 210 | Jul 6, 2026 10:08am | Jul 6, 2026 10:09am | Jul 6, 2026 10:16am | Jul 6, 2026 2:12pm | Jul 6, 2026 3:00pm | Jul 6, 2026 3:04pm | Jul 6, 2026 3:09pm | Jul 6, 2026 3:09pm | Fire |  | Fair | No | Location found ok. No sign of fire are sparking.
Non-Outage | J.E.26.07.00645 | C001840770 | Royston Montague | St.Catherine | Completed | Load_256082 | Tredegar - 210 | Jul 6, 2026 10:08am | Jul 6, 2026 10:09am | Jul 6, 2026 10:16am | Jul 6, 2026 10:34am | Jul 6, 2026 11:28am | Jul 6, 2026 11:28am | Jul 6, 2026 11:28am | Jul 6, 2026 11:28am |  |  | Fair | No | Premises found ok. Customer confirmed issue resolved
Non-Outage | J.E.26.07.01365 | C001840768 | Royston Montague | St.Catherine | Completed | Load_255593 | Tredegar - 210 | Jul 6, 2026 10:08am | Jul 6, 2026 10:09am | Jul 6, 2026 10:16am | Jul 6, 2026 11:29am | Jul 6, 2026 11:39am | Jul 6, 2026 12:01pm | Jul 6, 2026 12:01pm | Jul 6, 2026 12:01pm |  |  | Fair | No | Broken #6 twisted wire. Same repair, voltage found. 114v voltage after job completion are 229v 114v 114v
Non-Outage | J.E.26.07.03905 | C001840769 | Royston Montague | St.Catherine | Completed | Load_255999 | Tredegar - 410 | Jul 6, 2026 10:08am | Jul 6, 2026 10:09am | Jul 6, 2026 10:16am | Jul 6, 2026 10:23am | Jul 6, 2026 10:33am | Jul 6, 2026 10:33am | Jul 6, 2026 10:34am | Jul 6, 2026 10:34am | Fire |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.07.04608 | C001840767 | Damion Reid | Manchester | Completed | Load_238149 | Kendal - 310 | Jul 6, 2026 10:05am | Jul 6, 2026 10:06am | Jul 6, 2026 10:25am | Jul 6, 2026 10:26am | Jul 6, 2026 11:55am | Jul 6, 2026 1:13pm | Jul 6, 2026 1:15pm | Jul 6, 2026 1:15pm | Fire |  | Fair | No | Remade corroded neutral at secondary jumper voltage reading at meter socket after correction phase to neutral 111v-112v across phase 225v
Non-Outage | J.E.26.07.04648 | C001840766 | Ryan Richards | Manchester | Completed | Load_292798 | Spur Tree - 310 | Jul 6, 2026 10:05am | Jul 6, 2026 10:06am | Jul 6, 2026 10:37am | Jul 6, 2026 10:37am | Jul 6, 2026 11:49am | Jul 6, 2026 1:13pm | Jul 6, 2026 1:13pm | Jul 6, 2026 1:13pm | BrokenWire |  | Fair | Yes | Defective service wire found rotten an entangled with plum tree chop plum tree and replaced 70 ft#6 triplex 3 penunion 3 one bolt clamps voltage 113/115/229 volts
Outage | J.E.26.07.04666 | C001840765 | Christopher Edwards | KSAN | Completed | Load_239178 | Constant Spring - 410 | Jul 6, 2026 10:05am | Jul 6, 2026 10:05am | Jul 6, 2026 10:24am | Jul 6, 2026 11:07am | Jul 6, 2026 11:07am | Jul 6, 2026 11:07am | Jul 6, 2026 11:08am | Jul 6, 2026 11:08am | Fire |  | Fair | No | Unable to locate premises Unable to reach customer by phone for proper direction to premises
Outage | J.E.26.07.04493 | C001840747 | Raymond Lewis | St.Ann | Completed | Load_294552 | Cardiff Hall - 210 | Jul 6, 2026 9:57am | Jul 6, 2026 10:11am | Jul 6, 2026 11:43am | Jul 6, 2026 11:43am | Jul 6, 2026 12:38pm | Jul 6, 2026 12:39pm | Jul 6, 2026 12:39pm | Jul 6, 2026 12:39pm |  |  | Fair | No | Supply restored
Non-Outage | J.E.26.07.04604 | C001840741 | Barrington Brown | St.James | Completed | Load_263252 | Queens Drive - 710 | Jul 6, 2026 9:50am | Jul 6, 2026 9:50am | Jul 6, 2026 11:39am | Jul 6, 2026 11:39am | Jul 6, 2026 12:56pm | Jul 6, 2026 1:13pm | Jul 6, 2026 1:13pm | Jul 6, 2026 1:13pm |  |  | Fair | No | Checked and found ok voltage readings 118 117 235
Outage | J.E.26.07.04379 | C001840736 | Rayon Foster | Hanover | Completed | Load_268094 | Orange Bay - 310 | Jul 6, 2026 9:48am | Jul 6, 2026 9:49am | Jul 6, 2026 12:04pm | Jul 6, 2026 12:04pm | Jul 6, 2026 12:43pm | Jul 6, 2026 1:40pm | Jul 6, 2026 1:41pm | Jul 6, 2026 1:41pm |  |  | Fair | No | Patrol secondary to find 1 spand of broken secondary neutral and top phase open 1 25kva transformer to splice and retention broken phase and neutral using 8 one bolt clamp about 50 ft of number 2 wire and close voltage left after repair 116v/117v/233v
Outage | J.E.26.07.04653 | C001840735 | Lancelot Brown | Hanover | Completed | Load_1001393 | Orange Bay - 310 | Jul 6, 2026 9:48am | Jul 6, 2026 3:51pm | Jul 6, 2026 4:27pm | Jul 6, 2026 9:00pm | Jul 6, 2026 9:00pm | Jul 6, 2026 9:02pm | Jul 6, 2026 9:03pm | Jul 6, 2026 9:03pm | LeakingTransformer |  | Rains | No | Found 5kva fuse blown carry checks found out 5kva diffective need to replace please pass on to maintenance department in Hanover mr Richards need ergent attention
Outage | J.E.26.07.04621 | C001840733 | Denton Williams | Portland | Completed | Load_266103 | Port Antonio - 410 | Jul 6, 2026 9:44am | Jul 6, 2026 9:44am | Jul 6, 2026 11:17am | Jul 6, 2026 11:17am | Jul 6, 2026 11:47am | Jul 6, 2026 11:53am | Jul 6, 2026 11:55am | Jul 6, 2026 11:55am | BrokenWire |  | Fair | No | Customer meter pole fell down. Customer was advised to contact a licensed electrician.
Outage | J.E.26.07.04624 | C001840728 | Marlon Authors | St.Elizabeth | Completed | Load_575581 | Maggotty - 210 | Jul 6, 2026 9:42am | Jul 6, 2026 9:43am | Jul 6, 2026 11:18am | Jul 6, 2026 11:18am | Jul 6, 2026 11:18am | Jul 6, 2026 11:04am | Jul 6, 2026 11:22am | Jul 6, 2026 11:22am |  |  | Fair | No | Supply restored to the area
Outage | J.E.26.07.04643 | C001840727 | Barnett Brown | Manchester | Completed | Load_302066 | Spur Tree - 310 | Jul 6, 2026 9:41am | Jul 6, 2026 3:20pm | Jul 6, 2026 9:55pm | Jul 6, 2026 9:55pm | Jul 6, 2026 11:18pm | Jul 6, 2026 11:25pm | Jul 6, 2026 11:26pm | Jul 6, 2026 11:26pm |  |  | Fair | No | Call does not belong to Manchester
Outage | J.E.26.07.04642 | C001840720 | Rusean Allen | KSAS | Completed | Load_304946 | Cane River - 410 | Jul 6, 2026 9:38am | Jul 6, 2026 9:40am | Jul 6, 2026 11:08am | Jul 6, 2026 11:29am | Jul 6, 2026 11:38am | Jul 6, 2026 11:40am | Jul 6, 2026 11:40am | Jul 6, 2026 11:40am |  |  | Fair | No | 1x 5amp fuse found 1x 5amp fuse replaced.
Non-Outage | J.E.26.07.04043 | C001840706 | Hopeton Henry | St.Thomas | Completed | Load_259831 | Good Year - 210 | Jul 6, 2026 9:23am | Jul 7, 2026 7:36am | Jul 7, 2026 8:09am | Jul 7, 2026 9:00am | Jul 7, 2026 9:00am | Jul 7, 2026 9:16am | Jul 7, 2026 9:16am | Jul 7, 2026 9:16am |  |  | Fair | No | Reconnect broken service 117-115-233 volts
Non-Outage | J.E.26.07.01955 | C001840702 | Hartley Chin | Clarendon | Completed | Load_262045 | May Pen - 210 | Jul 6, 2026 9:21am | Jul 6, 2026 9:22am | Jul 6, 2026 11:28am | Jul 6, 2026 11:28am | Jul 6, 2026 12:51pm | Jul 6, 2026 1:46pm | Jul 6, 2026 1:53pm | Jul 6, 2026 1:53pm |  |  | Fair | No | Voltage read found @ customer pot head 129v , 110v … line patrolled and after detail inspection found a burn splicing sleeve on open secondary circuit neutral… repair broken joint … voltage read 120v , 120v … use 3 ft #2 conductor, 2 clamp …
Non-Outage | J.E.26.07.02737 | C001840703 | Hartley Chin | Clarendon | Completed | Load_247003 | May Pen - 210 | Jul 6, 2026 9:21am | Jul 6, 2026 9:22am | Jul 6, 2026 10:46am | Jul 6, 2026 11:19am | Jul 6, 2026 11:19am | Jul 6, 2026 11:20am | Jul 6, 2026 11:20am | Jul 6, 2026 11:20am |  |  | Fair | No | Call related to job # 03789
Non-Outage | J.E.26.07.03590 | C001840704 | Hartley Chin | Clarendon | Completed | Load_239638 | May Pen - 210 | Jul 6, 2026 9:21am | Jul 6, 2026 9:22am | Jul 6, 2026 1:53pm | Jul 6, 2026 1:53pm | Jul 6, 2026 2:36pm | Jul 6, 2026 2:49pm | Jul 6, 2026 2:51pm | Jul 6, 2026 2:51pm |  |  | Fair | No | Prem not found … unable to contact customer with contact # provided … area patrolled according to directions , unable to find meter …
Non-Outage | J.E.26.07.03655 | C001840705 | Hartley Chin | Clarendon | Completed | Load_247003 | May Pen - 210 | Jul 6, 2026 9:21am | Jul 6, 2026 9:22am | Jul 6, 2026 10:48am | Jul 6, 2026 11:20am | Jul 6, 2026 11:21am | Jul 6, 2026 11:21am | Jul 6, 2026 11:21am | Jul 6, 2026 11:21am |  |  | Fair | No | Call related to job # 03789 …
Non-Outage | J.E.26.07.04453 | C001840701 | Clyde Brown | Clarendon | Completed | Load_242425 | May Pen - 110 | Jul 6, 2026 9:20am | Jul 6, 2026 9:21am | Jul 6, 2026 5:37pm | Jul 6, 2026 5:37pm | Jul 6, 2026 6:53pm | Jul 6, 2026 6:31pm | Jul 6, 2026 6:58pm | Jul 6, 2026 6:58pm |  |  | Fair | No | Found ok,voltage reading 112/111 and 223 Volts
Outage | J.E.26.07.04605 | C001840691 | Marlon Brown | Trelawny | Completed | Load_239073 | Duncans - 210 | Jul 6, 2026 9:11am | Jul 6, 2026 9:12am | Jul 6, 2026 12:15pm | Jul 6, 2026 12:15pm | Jul 6, 2026 12:15pm | Jul 6, 2026 12:16pm | Jul 6, 2026 12:16pm | Jul 6, 2026 12:16pm | BrokenWire |  | Fair | No | Unable to locate customer via telephone nor direction
Outage | J.E.26.07.04612 | C001840692 | Marlon Brown | Trelawny | Completed | Load_302478 | Duncans - 210 | Jul 6, 2026 9:11am | Jul 6, 2026 9:12am | Jul 6, 2026 12:14pm | Jul 6, 2026 12:14pm | Jul 6, 2026 12:14pm | Jul 6, 2026 12:15pm | Jul 6, 2026 12:15pm | Jul 6, 2026 12:15pm | BrokenWire |  | Fair | No | Same as call number 4335.
Outage | J.E.26.07.02099 | C001840683 | Richard Grant | St.Catherine | Completed | Load_260364 | New Michelton - 310 | Jul 6, 2026 9:01am | Jul 6, 2026 9:01am | Jul 6, 2026 12:41pm | Jul 6, 2026 1:41pm | Jul 6, 2026 1:42pm | Jul 6, 2026 1:42pm | Jul 6, 2026 1:42pm | Jul 6, 2026 1:42pm |  |  | Fair | No | Premises and area found okay
Outage | J.E.26.07.02219 | C001840684 | Richard Grant | St.Catherine | Completed | Load_249906 | New Michelton - 310 | Jul 6, 2026 9:01am | Jul 6, 2026 9:01am | Jul 6, 2026 12:41pm | Jul 6, 2026 12:41pm | Jul 6, 2026 1:39pm | Jul 6, 2026 1:40pm | Jul 6, 2026 1:41pm | Jul 6, 2026 1:41pm |  |  | Fair | No | Premises and area found okay
Outage | J.E.26.07.04601 | C001840681 | Marlon Authors | St.Elizabeth | Completed | Load_575583 | Maggotty - 210 | Jul 6, 2026 9:00am | Jul 6, 2026 9:00am | Jul 6, 2026 11:04am | Jul 6, 2026 11:04am | Jul 6, 2026 11:04am | Jul 6, 2026 11:01am | Jul 6, 2026 11:10am | Jul 6, 2026 11:10am |  |  | Fair | No | Patrol and found clear. Replace one blown 10 amp fuse no pole #. Restored supply ok
Outage | J.E.26.07.04570 | C001840678 | Wan Carlos Scarlett | St.Catherine | Completed | Load_576216 | Twickenham - 210 | Jul 6, 2026 8:58am | Jul 6, 2026 8:59am | Jul 6, 2026 10:16am | Jul 6, 2026 12:42pm | Jul 6, 2026 1:15pm | Jul 6, 2026 2:08pm | Jul 6, 2026 2:10pm | Jul 6, 2026 2:10pm |  |  | Fair | No | Found customer 2 wire service at pole with phase corroded use 1 one bolt clamp readings 117
Outage | J.E.26.07.04577 | C001840680 | Nickolas Rodriques | St.Catherine | Completed | Load_250553 | Tredegar - 410 | Jul 6, 2026 8:58am | Jul 6, 2026 8:59am | Jul 6, 2026 11:22am | Jul 6, 2026 11:25am | Jul 6, 2026 12:08pm | Jul 6, 2026 12:19pm | Jul 6, 2026 12:25pm | Jul 6, 2026 12:25pm |  |  | Fair | No | Call relates to the 15 KVA transformer with hexing box attached that was found defective.
Outage | J.E.26.07.04600 | C001840677 | Hartley Chin | Clarendon | Completed | Load_260924 | May Pen - 210 | Jul 6, 2026 8:54am | Jul 6, 2026 8:57am | Jul 6, 2026 9:05am | Jul 6, 2026 9:05am | Jul 6, 2026 10:32am | Jul 6, 2026 11:04am | Jul 6, 2026 11:19am | Jul 6, 2026 11:19am |  |  | Fair | No | Found 1 of 3 blown 15 amp junction (no pole #) line patrolled and found 2 blown 2 amp fuse on 5 KVA transformer (no pole #) bank of 3 , line patrolled and found okay … refused junction.. refused transformers…
Outage | J.E.26.07.04586 | C001840672 | Cliton Henry | St.Mary | Completed | Load_263041 | Blackstonedge - 110 | Jul 6, 2026 8:52am | Jul 6, 2026 3:37pm | Jul 6, 2026 7:53pm | Jul 6, 2026 7:53pm | Jul 6, 2026 8:08pm | Jul 6, 2026 8:22pm | Jul 6, 2026 8:44pm | Jul 6, 2026 8:44pm |  |  | Fair | No | The customer found disconnected for debt. The customer was advised accordingly. Voltages found at the metering point were 118-119/238 volts.
Non-Outage | J.E.26.07.04588 | C001840670 | Derrick Dawkins | St.James | Completed | Load_248233 | Bogue - 310 | Jul 6, 2026 8:44am | Jul 6, 2026 10:11am | Jul 6, 2026 11:00am | Jul 6, 2026 11:00am | Jul 6, 2026 11:11am | Jul 6, 2026 11:25am | Jul 6, 2026 11:25am | Jul 6, 2026 11:25am |  |  | Fair | No | Only customer in the hexing box single phasing voltage 119/58.4=187.4 hexing box#00503
Non-Outage | J.E.26.07.04574 | C001840665 | Fredrick Hamilton | KSAN | Completed | Load_258770 | Washington Blvd - 510 | Jul 6, 2026 8:42am | Jul 7, 2026 8:07am | Jul 7, 2026 8:16am | Jul 7, 2026 10:12am | Jul 7, 2026 10:42am | Jul 7, 2026 11:21am | Jul 7, 2026 11:21am | Jul 7, 2026 11:21am |  |  | Fair | No | 231.5v/115.5v/115.4v obtained Please have emergency check transformer leads for possible corrosion
Outage | J.E.26.07.04593 | C001840664 | Barrington Brown | St.James | Completed | Load_238785 | Queens Drive - 710 | Jul 6, 2026 8:42am | Jul 6, 2026 8:44am | Jul 6, 2026 9:04am | Jul 6, 2026 9:06am | Jul 6, 2026 11:36am | Jul 6, 2026 11:39am | Jul 6, 2026 11:39am | Jul 6, 2026 11:39am | BrokenWire |  | Fair | No | Crew found burnt neutral on location cause by slack clamps. Crew used 50ft of #6 triplex and 5 clamps to remake connection. Customer now restored.
Non-Outage | J.E.26.07.03512 | C001840661 | Oraine Minto | St.Ann | Completed | Load_269325 | Upper White River - 110 | Jul 6, 2026 8:34am | Jul 6, 2026 8:34am | Jul 6, 2026 11:25am | Jul 6, 2026 11:25am | Jul 6, 2026 1:54pm | Jul 6, 2026 2:01pm | Jul 6, 2026 2:02pm | Jul 6, 2026 2:02pm |  |  | Fair | No | Refer to emergency Pole 115519 neutral burst Transformer is a 15kva Pole 0155634Transformer is having a neutral issue Customers say it mostly affects them at night
Non-Outage | J.E.26.07.04555 | C001840655 | Derrick Dawkins | St.James | Completed | Load_301732 | Bogue - 310 | Jul 6, 2026 8:27am | Jul 6, 2026 8:44am | Jul 6, 2026 10:18am | Jul 6, 2026 10:19am | Jul 6, 2026 10:31am | Jul 6, 2026 10:58am | Jul 6, 2026 10:58am | Jul 6, 2026 10:58am |  |  | Fair | No | Found customer pothead corroded clean and remade joints used 1 pg clamp voltage 117/1188=233
Outage | J.E.26.07.04581 | C001840654 | Derrick Dawkins | St.James | Completed | Load_575159 | Bogue - 310 | Jul 6, 2026 8:27am | Jul 6, 2026 8:44am | Jul 6, 2026 9:04am | Jul 6, 2026 9:04am | Jul 6, 2026 10:16am | Jul 6, 2026 10:17am | Jul 6, 2026 10:18am | Jul 6, 2026 10:18am |  |  | Fair | No | Was not able to locate call to customer went unanswered
Outage | J.E.26.07.04566 | C001840653 | Fitzroy Turner | KSAN | Completed | Load_293767 | Washington Blvd - 710 | Jul 6, 2026 8:24am | Jul 6, 2026 8:39am | Jul 6, 2026 11:19am | Jul 6, 2026 11:19am | Jul 6, 2026 11:36am | Jul 6, 2026 12:43pm | Jul 6, 2026 12:45pm | Jul 6, 2026 12:45pm |  |  | Fair | No | Found blown 2amps fuse for 10kva YPP transformer replaced one one 2amp fuse supply restored to customer
Outage | J.E.26.07.04438 | C001840651 | Ryan Richards | Manchester | Completed | Load_250942 | Spur Tree - 310 | Jul 6, 2026 8:22am | Jul 6, 2026 8:23am | Jul 6, 2026 8:40am | Jul 6, 2026 8:43am | Jul 6, 2026 10:07am | Jul 6, 2026 10:36am | Jul 6, 2026 10:36am | Jul 6, 2026 10:36am | TreeContact |  | Fair | No | Area found with supply customer concerns about a ackee tree limb that his touching the secondary conductors and causes them to bang sometimes when there’s heavy winds at times limb was cut and cleared from line
Outage | J.E.26.07.04496 | C001840649 | Richard Watson | St.Elizabeth | Completed | Load_270243 | Maggotty - 210 | Jul 6, 2026 8:14am | Jul 6, 2026 8:20am | Jul 6, 2026 10:45am | Jul 6, 2026 12:01pm | Jul 6, 2026 12:01pm | Jul 6, 2026 12:03pm | Jul 6, 2026 12:24pm | Jul 6, 2026 12:24pm |  |  | Fair | No | Customer is making a complaint about getting an electricity bill, even though she has no supply since hurricane Melissa, she also stated that work is currently taking place on the roof. Customer advised to visit nearest commercial office to log report.
Outage | J.E.26.07.04522 | C001840650 | Javid Vernon | St.Elizabeth | Completed | Load_557806 | Maggotty - 110 | Jul 6, 2026 8:14am | Jul 6, 2026 8:19am | Jul 6, 2026 8:55am | Jul 6, 2026 8:55am | Jul 6, 2026 10:10am | Jul 6, 2026 10:34am | Jul 6, 2026 10:35am | Jul 6, 2026 10:35am |  |  | Fair | No | Customer requesting a reconnection in hexing box # 01689
Outage | J.E.26.07.04567 | C001840646 | Marlon Authors | St.Elizabeth | Completed | Load_240639 | Maggotty - 210 | Jul 6, 2026 8:13am | Jul 6, 2026 8:16am | Jul 6, 2026 11:41am | Jul 6, 2026 11:41am | Jul 6, 2026 11:53am | Jul 6, 2026 12:01am | Jul 6, 2026 12:01pm | Jul 6, 2026 12:01pm |  |  | Fair | No | Supply checked and found one phase of the service wire broken. Repair same using one clamp, supply leave working ok rdg 118v,119v and cross phased 237 volts
Outage | J.E.26.07.04575 | C001840645 | Richard Watson | St.Elizabeth | Completed | Load_265735 | Maggotty - 110 | Jul 6, 2026 8:13am | Jul 6, 2026 8:15am | Jul 7, 2026 8:44am | Jul 7, 2026 8:48am | Jul 7, 2026 10:22am | Jul 7, 2026 10:30am | Jul 7, 2026 10:52am | Jul 7, 2026 10:52am |  |  | Fair | No | Unable to reconnect customer due to family dispute over ownership of meter pole, customer advised to electrician to rectify issue and call back.
Non-Outage | J.E.26.06.38098 | C001840643 | Andrae Dawkins | St.James | Completed | Load_241044 | Queens Drive - 710 | Jul 6, 2026 8:10am | Jul 6, 2026 11:50am | Jul 6, 2026 12:07pm | Jul 6, 2026 12:07pm | Jul 6, 2026 12:52pm | Jul 6, 2026 12:52pm | Jul 6, 2026 12:54pm | Jul 6, 2026 12:54pm |  |  | Fair | No | Check and found okay customer said that they didn’t make any report
Non-Outage | J.E.26.07.03771 | C001840642 | Romeo Brissett | St.James | Completed | Load_240799 | Bogue - 510 | Jul 6, 2026 8:10am | Jul 6, 2026 8:10am | Jul 6, 2026 8:43am | Jul 6, 2026 9:23am | Jul 6, 2026 9:47am | Jul 6, 2026 10:00am | Jul 6, 2026 10:01am | Jul 6, 2026 10:01am |  |  | Fair | No | Check and found internal fault V/R 111-118-211-233-234-236, customer was advised to check breaker.
Non-Outage | J.E.26.06.32225 | C001840641 | Andrae Dawkins | St.James | Completed | Load_302338 | Queens Drive - 710 | Jul 6, 2026 8:09am | Jul 6, 2026 8:10am | Jul 6, 2026 11:33am | Jul 6, 2026 11:45am | Jul 6, 2026 12:04pm | Jul 6, 2026 12:05pm | Jul 6, 2026 12:06pm | Jul 6, 2026 12:06pm |  |  | Fair | No | Check and found okay customer said that the problem was already resolved
Non-Outage | J.E.26.06.32270 | C001840638 | Andrae Dawkins | St.James | Completed | Load_259086 | Queens Drive - 710 | Jul 6, 2026 8:09am | Jul 6, 2026 8:10am | Jul 6, 2026 8:24am | Jul 6, 2026 9:55am | Jul 6, 2026 9:56am | Jul 6, 2026 9:49am | Jul 6, 2026 10:01am | Jul 6, 2026 10:01am |  |  | Fair | No | Check and found ok customer said that they don’t have any issue with the power
Non-Outage | J.E.26.06.33418 | C001840640 | Andrae Dawkins | St.James | Completed | Load_250345 | Queens Drive - 710 | Jul 6, 2026 8:09am | Jul 6, 2026 8:10am | Jul 6, 2026 8:24am | Jul 6, 2026 10:06am | Jul 6, 2026 10:06am | Jul 6, 2026 9:57am | Jul 6, 2026 10:10am | Jul 6, 2026 10:10am |  |  | Fair | No | Cannot locate customer unable to to reach customer mobile phone
Non-Outage | J.E.26.06.34179 | C001840639 | Andrae Dawkins | St.James | Completed | Load_253846 | Queens Drive - 710 | Jul 6, 2026 8:09am | Jul 6, 2026 8:10am | Jul 6, 2026 1:08pm | Jul 6, 2026 1:47pm | Jul 6, 2026 1:49pm | Jul 6, 2026 1:19pm | Jul 6, 2026 1:50pm | Jul 6, 2026 1:50pm |  |  | Fair | No | Cannot locate customer unable to reach customer phone
Non-Outage | J.E.26.07.03475 | C001840636 | Andrae Dawkins | St.James | Completed | Load_248976 | Queens Drive - 710 | Jul 6, 2026 8:09am | Jul 6, 2026 8:10am | Jul 6, 2026 8:24am | Jul 6, 2026 11:39am | Jul 6, 2026 11:40am | Jul 6, 2026 11:41am | Jul 6, 2026 11:44am | Jul 6, 2026 11:44am |  |  | Fair | No | Customer single phasing from EG box 00518 refer back to field service
Non-Outage | J.E.26.07.04001 | C001840637 | Andrae Dawkins | St.James | Completed | Load_239243 | Queens Drive - 710 | Jul 6, 2026 8:09am | Jul 6, 2026 8:10am | Jul 6, 2026 8:24am | Jul 6, 2026 10:25am | Jul 6, 2026 10:47am | Jul 6, 2026 11:30am | Jul 6, 2026 11:30am | Jul 6, 2026 11:30am |  |  | Fair | No | Found customer experiencing low voltage due to corrosion at pothead clean and remade joints voltage found 101/103/204 voltage left 110/112/222
Non-Outage | J.E.26.07.00136 | C001840632 | Milton Charlton | KSAN | Completed | Load_238618 | Hope - 510 | Jul 6, 2026 8:06am | Jul 6, 2026 8:06am | Jul 6, 2026 10:15am | Jul 6, 2026 10:16am | Jul 6, 2026 12:26pm | Jul 6, 2026 12:30pm | Jul 6, 2026 12:49pm | Jul 6, 2026 12:49pm |  |  | Fair | No | Customer service wire #6 triplex connected to open wire secondary fed by #2 triplex and #6 triplex joined. Readings at pothead 109-111-220 volts at take off pole 115-104-220 volts and two pole span down the road 116-110-226 volts. Concrete pole need to be checked and triplex joints. Need bucket truck to check mid- span connection on triplex.
Non-Outage | J.E.26.07.03775 | C001840631 | Floyd Taylor | Trelawny | Completed | Load_258502 | Greenwood - 110 | Jul 6, 2026 8:06am | Jul 6, 2026 11:09am | Jul 6, 2026 1:28pm | Jul 6, 2026 1:28pm | Jul 6, 2026 2:16pm | Jul 6, 2026 2:40pm | Jul 6, 2026 2:41pm | Jul 6, 2026 2:41pm |  |  | Fair | No | Unable to locate customer due to poor information
Non-Outage | J.E.26.07.03898 | C001840628 | Roemello Brown | Trelawny | Completed | Load_246009 | Greenwood - 110 | Jul 6, 2026 8:05am | Jul 6, 2026 8:08am | Jul 7, 2026 8:42am | Jul 7, 2026 8:42am | Jul 7, 2026 9:15am | Jul 7, 2026 9:15am | Jul 7, 2026 9:58am | Jul 7, 2026 9:58am |  |  | Fair | No | Unable to find customer also customer needs to update proper directions an the phone number provided went straight to voicemail phone number not assigned
Non-Outage | J.E.26.07.04052 | C001840626 | Floyd Taylor | Trelawny | Completed | Load_238828 | Martha Brae - 110 | Jul 6, 2026 8:05am | Jul 6, 2026 9:06am | Jul 6, 2026 9:15am | Jul 6, 2026 9:15am | Jul 6, 2026 9:51am | Jul 6, 2026 10:18am | Jul 6, 2026 10:21am | Jul 6, 2026 10:21am | BrokenPole |  | Fair | No | Pole doesn’t belong to Jps
Non-Outage | J.E.26.07.04082 | C001840630 | Roemello Brown | Trelawny | Completed | Load_248283 | Duncans - 210 | Jul 6, 2026 8:05am | Jul 6, 2026 8:08am | Jul 6, 2026 10:04am | Jul 6, 2026 10:28am | Jul 6, 2026 11:39am | Jul 6, 2026 11:39am | Jul 6, 2026 12:02pm | Jul 6, 2026 12:02pm |  |  | Fair | No | Have voltage test done problem is not on jps side inform customer to get an private electrician to check premises Voltage found 117/118/235Voltage leave 117/118/235
Non-Outage | J.E.26.07.04274 | C001840629 | Roemello Brown | Trelawny | Completed | Load_264256 | Duncans - 210 | Jul 6, 2026 8:05am | Jul 6, 2026 8:08am | Jul 6, 2026 10:00am | Jul 6, 2026 12:02pm | Jul 6, 2026 1:13pm | Jul 6, 2026 1:13pm | Jul 6, 2026 1:16pm | Jul 6, 2026 1:16pm |  |  | Fair | No | Premises found working okay customer meter disconnected because the tenant remove their name of the account so the account inactive Voltage found 118/118/236Voltage leave 118/118/236
Non-Outage | J.E.26.07.04335 | C001840625 | Marlon Brown | null | Completed | null | null | Jul 6, 2026 8:05am | Jul 6, 2026 8:52am | Jul 6, 2026 9:04am | Jul 6, 2026 9:04am | Jul 6, 2026 10:31am | Jul 6, 2026 12:13pm | Jul 6, 2026 12:13pm | Jul 6, 2026 12:13pm | Fire |  | Fair | No | Isolated 25kva transformer to repair 2 spans secondary phase and neutral, use se 50ft #2 AAC, 50ft #2/0 AAC & 3 pg clamps 1 #2 &1#2/0 preform. Voltage found 200vVoltage leaving 120/120=240v.
Non-Outage | J.E.26.07.03891 | C001840623 | Fredrick Hamilton | KSAN | Completed | Load_257446 | Constant Spring - 210 | Jul 6, 2026 8:03am | Jul 6, 2026 8:03am | Jul 6, 2026 8:09am | Jul 6, 2026 12:10pm | Jul 6, 2026 12:17pm | Jul 6, 2026 12:58pm | Jul 6, 2026 12:58pm | Jul 6, 2026 12:58pm |  |  | Fair | No | 215v/115v/100v obtained 3 penunions used at pothead 2 clamps at pole Voltage still low Please have emergency check transformer
Non-Outage | J.E.26.07.04231 | C001840622 | Tajay Bernard | Hanover | Completed | Load_261288 | Orange Bay - 310 | Jul 6, 2026 8:02am | Jul 7, 2026 7:35am | Jul 7, 2026 9:08am | Jul 7, 2026 9:24am | Jul 7, 2026 9:32am | Jul 7, 2026 9:39am | Jul 7, 2026 9:40am | Jul 7, 2026 9:40am | Fire |  | Fair | No | Area and premises check and found okay voltage reading 114/113/227Cause(there’s a lot off illegal connections at that specific area)
Outage | J.E.26.07.04390 | C001840621 | Nickolas Rodriques | St.Catherine | Completed | Load_270195 | Tredegar - 410 | Jul 6, 2026 8:02am | Jul 6, 2026 8:03am | Jul 6, 2026 10:10am | Jul 6, 2026 10:17am | Jul 6, 2026 11:00am | Jul 6, 2026 11:18am | Jul 6, 2026 11:19am | Jul 6, 2026 11:19am |  |  | Fair | No | Customer having issue topping up her CIU box. Refer to field service.
Outage | J.E.26.07.04434 | C001840619 | Nickolas Rodriques | St.Catherine | Completed | Load_258349 | Tredegar - 210 | Jul 6, 2026 8:02am | Jul 6, 2026 8:03am | Jul 6, 2026 8:40am | Jul 6, 2026 8:41am | Jul 6, 2026 9:42am | Jul 6, 2026 10:02am | Jul 6, 2026 10:10am | Jul 6, 2026 10:10am | BrokenPole |  | Fair | No | No broken pole seen upon arrival. The customer is reporting a defective streetlight. Refer to streetlight department.
Non-Outage | J.E.26.07.03541 | C001840612 | Tyrese Williams | null | Completed | null | null | Jul 6, 2026 8:00am | Jul 6, 2026 8:01am | Jul 6, 2026 8:09am | Jul 6, 2026 1:42pm | Jul 6, 2026 1:49pm | Jul 6, 2026 1:51pm | Jul 6, 2026 1:52pm | Jul 6, 2026 1:52pm | Fire |  | Fair | No | Premises found ok
Non-Outage | J.E.26.07.03643 | C001840614 | Tyrese Williams | St.Ann | Completed | Load_269131 | Cardiff Hall - 310 | Jul 6, 2026 8:00am | Jul 6, 2026 8:01am | Jul 6, 2026 8:09am | Jul 6, 2026 11:35am | Jul 6, 2026 12:22pm | Jul 6, 2026 1:41pm | Jul 6, 2026 1:42pm | Jul 6, 2026 1:42pm |  |  | Fair | Yes | Remade service joint at pothead use 1 pg clamp voltage check 113/113/226
Non-Outage | J.E.26.07.03742 | C001840613 | Tyrese Williams | St.Ann | Completed | Load_251665 | Cardiff Hall - 310 | Jul 6, 2026 8:00am | Jul 6, 2026 8:01am | Jul 6, 2026 8:09am | Jul 6, 2026 10:39am | Jul 6, 2026 11:25am | Jul 6, 2026 11:35am | Jul 6, 2026 11:35am | Jul 6, 2026 11:35am |  |  | Fair | No | Premises found ok voltage left at premise 115/118/234
Non-Outage | J.E.26.07.03751 | C001840615 | Tyrese Williams | St.Ann | Completed | Load_250330 | Cardiff Hall - 310 | Jul 6, 2026 8:00am | Jul 6, 2026 8:01am | Jul 6, 2026 8:09am | Jul 6, 2026 10:16am | Jul 6, 2026 10:29am | Jul 6, 2026 10:39am | Jul 6, 2026 10:39am | Jul 6, 2026 10:39am |  |  | Fair | No | Premise not found not getting customer on phone
Non-Outage | J.E.26.07.03754 | C001840616 | Tyrese Williams | St.Ann | Completed | Load_255456 | Cardiff Hall - 310 | Jul 6, 2026 8:00am | Jul 6, 2026 8:01am | Jul 6, 2026 8:09am | Jul 6, 2026 10:13am | Jul 6, 2026 10:13am | Jul 6, 2026 10:14am | Jul 6, 2026 10:15am | Jul 6, 2026 10:15am |  |  | Fair | No | Premise not found not getting customer on phone
Non-Outage | J.E.26.07.03769 | C001840617 | Tyrese Williams | St.Ann | Completed | Load_251665 | Cardiff Hall - 310 | Jul 6, 2026 8:00am | Jul 6, 2026 8:01am | Jul 6, 2026 8:09am | Jul 6, 2026 8:58am | Jul 6, 2026 9:57am | Jul 6, 2026 10:10am | Jul 6, 2026 10:12am | Jul 6, 2026 10:12am |  |  | Fair | No | Remade service wire connection at pole at pothead
Non-Outage | J.E.26.07.04422 | C001840618 | Tyrese Williams | St.Ann | Completed | Load_243723 | Cardiff Hall - 310 | Jul 6, 2026 8:00am | Jul 7, 2026 8:39am | Jul 7, 2026 8:43am | Jul 7, 2026 2:28pm | Jul 7, 2026 3:12pm | Jul 7, 2026 3:13pm | Jul 7, 2026 3:13pm | Jul 7, 2026 3:13pm |  |  | Fair | No | Premises found ok customer has internal problem
Non-Outage | J.E.26.06.35174 | C001840611 | Stephen Taylor | St.Thomas | Completed | Load_269349 | Lysson - 410 | Jul 6, 2026 7:59am | Jul 6, 2026 8:00am | Jul 6, 2026 12:27pm | Jul 6, 2026 12:27pm | Jul 6, 2026 2:04pm | Jul 6, 2026 2:04pm | Jul 6, 2026 2:06pm | Jul 6, 2026 2:06pm |  |  | Fair | No | Clean up single phase reading 112,113,225 customer is now okay
Non-Outage | J.E.26.07.00786 | C001840608 | Odeanie Davis | KSAS | Completed | Load_255860 | Hunts Bay - 310 | Jul 6, 2026 7:49am | Jul 6, 2026 7:50am | Jul 6, 2026 9:22am | Jul 6, 2026 9:22am | Jul 6, 2026 9:23am | Jul 6, 2026 11:35am | Jul 6, 2026 11:35am | Jul 6, 2026 11:35am |  |  | Fair | No | 119v/0V on load side in meter socket, meter found burnt on one side, JPS meter defective and needs to be replaced, open neutral at secondary corrected, 1 one bolt clamp, 118v/119v & 237v in meter socket on line side, FIELD service team needed.
Non-Outage | J.E.26.07.04406 | C001840607 | Odeanie Davis | KSAS | Completed | Load_264749 | Rockfort - 210 | Jul 6, 2026 7:49am | Jul 6, 2026 7:50am | Jul 6, 2026 12:05pm | Jul 6, 2026 12:05pm | Jul 6, 2026 12:10pm | Jul 6, 2026 12:28pm | Jul 6, 2026 12:28pm | Jul 6, 2026 12:28pm |  |  | Fair | No | 111v at arrival, open neutral at pothead corrected, 1 penn union, 115v after correction
Outage | J.E.26.07.03333 | C001840603 | Richard Nicholas | St.Catherine | Completed | Load_1004030 | Rhodens Pen - 410 | Jul 6, 2026 7:44am | Jul 6, 2026 8:00am | Jul 6, 2026 11:44am | Jul 6, 2026 11:44am | Jul 6, 2026 1:08pm | Jul 6, 2026 1:30pm | Jul 6, 2026 1:31pm | Jul 6, 2026 1:31pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.03343 | C001840602 | Richard Nicholas | St.Catherine | Completed | Load_267102 | Rhodens Pen - 410 | Jul 6, 2026 7:44am | Jul 6, 2026 8:00am | Jul 6, 2026 1:31pm | Jul 6, 2026 1:31pm | Jul 6, 2026 2:17pm | Jul 6, 2026 2:43pm | Jul 6, 2026 2:44pm | Jul 6, 2026 2:44pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.04236 | C001840601 | Richard Nicholas | St.Catherine | Completed | Load_263974 | Rhodens Pen - 410 | Jul 6, 2026 7:44am | Jul 6, 2026 8:00am | Jul 6, 2026 8:42am | Jul 6, 2026 8:42am | Jul 6, 2026 11:22am | Jul 6, 2026 11:43am | Jul 6, 2026 11:44am | Jul 6, 2026 11:44am |  |  | EarthMovement | No | Supply found ok in the area
Outage | J.E.26.07.04559 | C001840597 | Rusean Allen | KSAS | Completed | Load_238569 | Rockfort - 410 | Jul 6, 2026 7:40am | Jul 6, 2026 7:41am | Jul 6, 2026 10:41am | Jul 6, 2026 10:51am | Jul 6, 2026 11:08am | Jul 6, 2026 11:15am | Jul 6, 2026 11:15am | Jul 6, 2026 11:15am |  |  | Fair | No | 1x 10amp fuse found 1x 10amp fuse replaced.
Outage | J.E.26.07.04559 | C001840598 | Rusean Allen | KSAS | Completed | Load_238569 | Rockfort - 410 | Jul 6, 2026 7:40am | Jul 6, 2026 7:50am | Jul 6, 2026 10:41am | Jul 6, 2026 3:23pm | Jul 6, 2026 3:23pm | Jul 6, 2026 3:23pm | Jul 6, 2026 3:23pm | Jul 6, 2026 3:23pm |  |  | Fair | No | Duplicate order
Non-Outage | J.E.26.07.04551 | C001840595 | Romeo Brissett | St.James | Completed | Load_243318 | Bogue - 610 | Jul 6, 2026 7:34am | Jul 6, 2026 7:35am | Jul 6, 2026 7:38am | Jul 6, 2026 7:38am | Jul 6, 2026 8:43am | Jul 6, 2026 9:18am | Jul 6, 2026 9:23am | Jul 6, 2026 9:23am | BrokenWire |  | Fair | No | Spliced and retention customer service wire, used 15ft of #6 and 3 clamps, V/R 114-115-229
Outage | J.E.26.07.04536 | C001840594 | Romeo Brissett | St.James | Completed | Load_249519 | Bogue - 610 | Jul 6, 2026 7:32am | Jul 6, 2026 7:34am | Jul 6, 2026 8:43am | Jul 6, 2026 10:01am | Jul 6, 2026 10:52am | Jul 6, 2026 11:38am | Jul 6, 2026 11:40am | Jul 6, 2026 11:40am |  |  | Fair | No | Cut and removed bamboo, replaced (1)15KVA transformer fuse.
Non-Outage | J.E.26.07.01836 | C001840592 | Edward Royal | KSAS | Completed | Load_238539 | Duhaney - 310 | Jul 6, 2026 7:28am | Jul 6, 2026 7:49am | Jul 6, 2026 9:06am | Jul 6, 2026 9:06am | Jul 6, 2026 9:06am | Jul 6, 2026 9:07am | Jul 6, 2026 9:08am | Jul 6, 2026 9:08am | Fire |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.05.34181 | C001840590 | Odeanie Davis | KSAS | Completed | Load_242532 | Cane River - 610 | Jul 6, 2026 7:26am | Jul 6, 2026 7:27am | Jul 7, 2026 8:16am | Jul 7, 2026 8:16am | Jul 7, 2026 8:16am | Jul 7, 2026 8:17am | Jul 7, 2026 8:17am | Jul 7, 2026 8:17am |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.06.31283 | C001840583 | Odeanie Davis | KSAS | Completed | Load_241207 | Cane River - 310 | Jul 6, 2026 7:26am | Jul 6, 2026 7:27am | Jul 6, 2026 12:29pm | Jul 6, 2026 12:42pm | Jul 6, 2026 12:42pm | Jul 6, 2026 12:43pm | Jul 6, 2026 12:43pm | Jul 6, 2026 12:43pm |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.06.34306 | C001840587 | Odeanie Davis | KSAS | Completed | Load_556760 | Cane River - 410 | Jul 6, 2026 7:26am | Jul 6, 2026 7:27am | Jul 6, 2026 12:30pm | Jul 6, 2026 2:41pm | Jul 6, 2026 2:54pm | Jul 6, 2026 3:25pm | Jul 6, 2026 3:31pm | Jul 6, 2026 3:31pm |  |  | Fair | No | 110v/ 118v at arrival, open neutral on customer’s line corrected, 2 one bolt, 117v/118v & 235v after correction.
Non-Outage | J.E.26.06.38991 | C001840586 | Odeanie Davis | KSAS | Completed | Load_254034 | Cane River - 410 | Jul 6, 2026 7:26am | Jul 6, 2026 7:27am | Jul 7, 2026 9:28am | Jul 7, 2026 9:28am | Jul 7, 2026 9:33am | Jul 7, 2026 10:51am | Jul 7, 2026 10:52am | Jul 7, 2026 10:52am |  |  | Fair | No | 111v/117v at arrival, twisted wire was removed and reinstalled, 3 one bolt clamps, 3 penn union & 60 ft twisted wire, 112v/114 & 226v
Non-Outage | J.E.26.07.00342 | C001840588 | Odeanie Davis | KSAS | Completed | Load_266521 | Cane River - 410 | Jul 6, 2026 7:26am | Jul 6, 2026 7:27am | Jul 7, 2026 9:28am | Jul 7, 2026 10:57am | Jul 7, 2026 10:58am | Jul 7, 2026 11:20am | Jul 7, 2026 11:20am | Jul 7, 2026 11:20am |  |  | Fair | No | Customer’s power found ok, 111v/112v & 224v at location, customer was advised to contact their electrician.
Non-Outage | J.E.26.07.00477 | C001840589 | Odeanie Davis | KSAS | Completed | Load_260234 | Cane River - 610 | Jul 6, 2026 7:26am | Jul 6, 2026 7:27am | Jul 7, 2026 8:33am | Jul 7, 2026 8:33am | Jul 7, 2026 8:48am | Jul 7, 2026 9:26am | Jul 7, 2026 9:26am | Jul 7, 2026 9:26am |  |  | Fair | No | 100v/124 at arrival. Open neutral on secondary line corrected, 1 penn union, 117v/116v & 234v after correction.
Non-Outage | J.E.26.07.00717 | C001840584 | Odeanie Davis | KSAS | Completed | Load_264816 | Cane River - 310 | Jul 6, 2026 7:26am | Jul 6, 2026 7:27am | Jul 6, 2026 12:29pm | Jul 6, 2026 12:53pm | Jul 6, 2026 12:53pm | Jul 6, 2026 1:45pm | Jul 6, 2026 1:45pm | Jul 6, 2026 1:45pm |  |  | Fair | No | 118v/ 0V under load, open circuit at secondary corrected, 1 penn union & 2 one bolt clamps, 117v/118v & 235v after
Non-Outage | J.E.26.07.03803 | C001840585 | Odeanie Davis | KSAS | Completed | Load_266609 | Cane River - 310 | Jul 6, 2026 7:26am | Jul 6, 2026 7:27am | Jul 7, 2026 9:28am | Jul 7, 2026 11:20am | Jul 7, 2026 11:25am | Jul 7, 2026 12:53pm | Jul 7, 2026 12:54pm | Jul 7, 2026 12:54pm |  |  | Fair | No | Twisted wire was removed and reinstalled, 3 one bolt clamps, 3 penn union & 40ft twisted wire, 113v/116v & 229v after completion
Non-Outage | J.E.26.06.30281 | C001840582 | Odeanie Davis | KSAS | Completed | Load_265826 | Cane River - 310 | Jul 6, 2026 7:25am | Jul 6, 2026 7:27am | Jul 6, 2026 12:29pm | Jul 6, 2026 2:13pm | Jul 6, 2026 2:17pm | Jul 6, 2026 2:39pm | Jul 6, 2026 2:41pm | Jul 6, 2026 2:41pm |  |  | Fair | No | 110v/130v at arrival, open circuit at pothead corrected, 3 penn union, 120v/120v & 240v after correction
Non-Outage | J.E.26.07.00932 | C001840578 | Odeanie Davis | KSAS | Completed | Load_251755 | Rockfort - 410 | Jul 6, 2026 7:25am | Jul 6, 2026 7:27am | Jul 6, 2026 8:35am | Jul 6, 2026 8:35am | Jul 6, 2026 8:36am | Jul 6, 2026 8:37am | Jul 6, 2026 8:38am | Jul 6, 2026 8:38am |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.07.01763 | C001840580 | Odeanie Davis | KSAS | Completed | Load_238767 | Rockfort - 410 | Jul 6, 2026 7:25am | Jul 6, 2026 7:27am | Jul 6, 2026 11:50am | Jul 6, 2026 11:50am | Jul 6, 2026 11:50am | Jul 6, 2026 12:00pm | Jul 6, 2026 12:01pm | Jul 6, 2026 12:01pm |  |  | Fair | No | 112v in meter socket, meter found burnt on one side, power found ok & meter was pinged and working fine.
Non-Outage | J.E.26.07.04557 | C001840579 | Odeanie Davis | KSAS | Completed | Load_238569 | Rockfort - 410 | Jul 6, 2026 7:25am | Jul 6, 2026 7:27am | Jul 6, 2026 8:46am | Jul 6, 2026 8:46am | Jul 6, 2026 8:46am | Jul 6, 2026 8:55am | Jul 6, 2026 8:54am | Jul 6, 2026 8:54am |  |  | Fair | No | Fuse seen open, customer has partial supply at location, emergency team needed,
Non-Outage | J.E.26.07.02045 | C001840574 | Fredrick Hamilton | KSAS | Completed | Load_246657 | Duhaney - 310 | Jul 6, 2026 7:24am | Jul 6, 2026 7:24am | Jul 6, 2026 8:09am | Jul 6, 2026 10:02am | Jul 6, 2026 10:06am | Jul 6, 2026 10:48am | Jul 6, 2026 10:48am | Jul 6, 2026 10:48am |  |  | Fair | No | Single phase detected and corrected at pole1 clamp used
Non-Outage | J.E.26.07.02616 | C001840573 | Edward Royal | KSAS | Completed | Load_238539 | Duhaney - 310 | Jul 6, 2026 7:24am | Jul 6, 2026 7:48am | Jul 6, 2026 9:08am | Jul 6, 2026 9:08am | Jul 6, 2026 9:08am | Jul 6, 2026 9:08am | Jul 6, 2026 9:08am | Jul 6, 2026 9:08am |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.07.03269 | C001840576 | Fredrick Hamilton | KSAS | Completed | Load_267072 | Duhaney - 310 | Jul 6, 2026 7:24am | Jul 6, 2026 7:24am | Jul 6, 2026 8:09am | Jul 6, 2026 9:06am | Jul 6, 2026 9:24am | Jul 6, 2026 9:46am | Jul 6, 2026 9:46am | Jul 6, 2026 9:46am |  |  | Fair | No | 215v/111v/105v obtained Low voltage affecting multiple customers Please have emergency check line
Non-Outage | J.E.26.07.03563 | C001840575 | Fredrick Hamilton | KSAS | Completed | Load_241997 | Duhaney - 310 | Jul 6, 2026 7:24am | Jul 6, 2026 7:24am | Jul 6, 2026 8:09am | Jul 6, 2026 10:51am | Jul 6, 2026 10:55am | Jul 6, 2026 10:59am | Jul 6, 2026 10:59am | Jul 6, 2026 10:59am |  |  | Fair | No | Issue resolved previously by emergency crewPremises is ok
Non-Outage | J.E.26.07.00857 | C001840568 | Fredrick Hamilton | KSAN | Completed | Load_302267 | Washington Blvd - 510 | Jul 6, 2026 7:22am | Jul 6, 2026 7:22am | Jul 6, 2026 8:09am | Jul 6, 2026 11:47am | Jul 6, 2026 11:53am | Jul 6, 2026 12:07pm | Jul 6, 2026 12:07pm | Jul 6, 2026 12:07pm |  |  | Fair | No | 238.4v/118.7v/119.3v obtained Premises checked and found ok at time of visit
Non-Outage | J.E.26.07.03326 | C001840569 | Fredrick Hamilton | KSAN | Completed | Load_250041 | Constant Spring - 410 | Jul 6, 2026 7:22am | Jul 6, 2026 7:22am | Jul 6, 2026 8:09am | Jul 6, 2026 11:41am | Jul 6, 2026 11:44am | Jul 6, 2026 11:46am | Jul 6, 2026 11:46am | Jul 6, 2026 11:46am |  |  | Fair | No | Customer contacted and stated that electrician had rectified issue Premises is ok
Non-Outage | J.E.26.07.03407 | C001840571 | Elvis Trowers | KSAN | Completed | Load_569891 | Washington Blvd - 810 | Jul 6, 2026 7:22am | Jul 6, 2026 7:38am | Jul 6, 2026 9:01am | Jul 6, 2026 9:01am | Jul 6, 2026 9:19am | Jul 6, 2026 9:34am | Jul 6, 2026 9:34am | Jul 6, 2026 9:34am | BrokenWire |  | Fair | Yes | Checked out and found ok upon arrival, broken wires are not belonging to JPS but to other cable companies.
Non-Outage | J.E.26.07.03988 | C001840570 | Fredrick Hamilton | KSAN | Completed | Load_263329 | Washington Blvd - 510 | Jul 6, 2026 7:22am | Jul 6, 2026 7:22am | Jul 6, 2026 8:09am | Jul 6, 2026 11:02am | Jul 6, 2026 11:04am | Jul 6, 2026 11:05am | Jul 6, 2026 11:05am | Jul 6, 2026 11:05am |  |  | Fair | No | Customer contacted and stated that power was restored fully previously Premises is ok
Non-Outage | J.E.26.07.03748 | C001840567 | Rochaine Hussey | KSAN | Completed | Load_269774 | Constant Spring - 410 | Jul 6, 2026 7:21am | Jul 6, 2026 7:21am | Jul 6, 2026 9:38am | Jul 6, 2026 9:38am | Jul 6, 2026 9:41am | Jul 6, 2026 9:42am | Jul 6, 2026 9:42am | Jul 6, 2026 9:42am |  |  | Fair | No | Customer say the issue was resolved and power was restored
Non-Outage | J.E.26.07.00198 | C001840558 | Rochaine Hussey | KSAN | Completed | Load_250012 | Constant Spring - 410 | Jul 6, 2026 7:20am | Jul 6, 2026 7:21am | Jul 7, 2026 11:29am | Jul 7, 2026 11:29am | Jul 7, 2026 11:41am | Jul 7, 2026 11:42am | Jul 7, 2026 11:42am | Jul 7, 2026 11:42am |  |  | Fair | No | Customer said issue was already resolved
Non-Outage | J.E.26.07.00919 | C001840562 | Rochaine Hussey | KSAN | Completed | Load_246237 | Constant Spring - 410 | Jul 6, 2026 7:20am | Jul 6, 2026 7:21am | Jul 6, 2026 12:47pm | Jul 6, 2026 12:47pm | Jul 6, 2026 12:47pm | Jul 6, 2026 12:52pm | Jul 6, 2026 12:52pm | Jul 6, 2026 12:52pm |  |  | Fair | No | Unable to locate Customer was called multiple times no answer
Non-Outage | J.E.26.07.01114 | C001840563 | Rochaine Hussey | KSAN | Completed | Load_252158 | Constant Spring - 410 | Jul 6, 2026 7:20am | Jul 6, 2026 7:21am | Jul 6, 2026 12:33pm | Jul 6, 2026 3:26pm | Jul 6, 2026 3:26pm | Jul 6, 2026 3:26pm | Jul 6, 2026 3:26pm | Jul 6, 2026 3:26pm |  |  | Fair | No | Customer said issue was already resolved
Non-Outage | J.E.26.07.01494 | C001840561 | Rochaine Hussey | KSAN | Completed | Load_253819 | Constant Spring - 410 | Jul 6, 2026 7:20am | Jul 6, 2026 7:21am | Jul 6, 2026 12:53pm | Jul 6, 2026 12:55pm | Jul 6, 2026 12:55pm | Jul 6, 2026 1:51pm | Jul 6, 2026 3:15pm | Jul 6, 2026 3:15pm |  |  | Fair | No | Neutral was corroded 1clamp used120/121/241v
Non-Outage | J.E.26.07.01992 | C001840564 | Rochaine Hussey | KSAN | Completed | Load_242752 | Constant Spring - 410 | Jul 6, 2026 7:20am | Jul 6, 2026 7:21am | Jul 6, 2026 9:49am | Jul 6, 2026 10:59am | Jul 6, 2026 11:42am | Jul 6, 2026 11:50am | Jul 6, 2026 11:55am | Jul 6, 2026 11:55am |  |  | Fair | No | Customer meter burnt which causes single phase112/110/222vReferring to field service
Non-Outage | J.E.26.07.02071 | C001840565 | Rochaine Hussey | KSAN | Completed | Load_249723 | Constant Spring - 410 | Jul 6, 2026 7:20am | Jul 6, 2026 7:21am | Jul 6, 2026 9:46am | Jul 6, 2026 11:55am | Jul 6, 2026 11:55am | Jul 6, 2026 12:21pm | Jul 6, 2026 12:21pm | Jul 6, 2026 12:21pm |  |  | Fair | No | Customer was advised to get electrician 120/121/241vVoltage at meter found ok
Non-Outage | J.E.26.07.02638 | C001840556 | Edward Royal | KSAN | Completed | Load_257373 | Constant Spring - 210 | Jul 6, 2026 7:20am | Jul 6, 2026 8:06am | Jul 6, 2026 9:09am | Jul 6, 2026 9:09am | Jul 6, 2026 9:09am | Jul 6, 2026 9:09am | Jul 6, 2026 9:09am | Jul 6, 2026 9:09am |  |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.07.02651 | C001840557 | Rochaine Hussey | KSAN | Completed | Load_570000 | Constant Spring - 210 | Jul 6, 2026 7:20am | Jul 7, 2026 8:10am | Jul 7, 2026 1:59pm | Jul 7, 2026 1:59pm | Jul 7, 2026 2:25pm | Jul 7, 2026 2:36pm | Jul 7, 2026 2:38pm | Jul 7, 2026 2:38pm |  |  | Fair | No | Customer meter burnt which causes single phaseReffering to field service 120/120/240v
Non-Outage | J.E.26.07.03125 | C001840559 | Rochaine Hussey | KSAN | Completed | Load_244592 | Constant Spring - 210 | Jul 6, 2026 7:20am | Jul 6, 2026 7:21am | Jul 7, 2026 2:38pm | Jul 7, 2026 2:38pm | Jul 7, 2026 2:38pm | Jul 7, 2026 2:41pm | Jul 7, 2026 2:41pm | Jul 7, 2026 2:41pm |  |  | Fair | No | Customer was called multiple times no answer Unable to locate
Non-Outage | J.E.26.07.03261 | C001840566 | Rochaine Hussey | KSAN | Completed | Load_269049 | Constant Spring - 410 | Jul 6, 2026 7:20am | Jul 6, 2026 7:21am | Jul 6, 2026 9:46am | Jul 6, 2026 12:24pm | Jul 6, 2026 12:24pm | Jul 6, 2026 12:33pm | Jul 6, 2026 12:33pm | Jul 6, 2026 12:33pm |  |  | Fair | No | Pole#0072635Neutral wire burnt off pole Emergency team needed
Outage | J.E.26.07.04490 | C001840555 | Edward Royal | KSAS | Completed | Load_266967 | Duhaney - 410 | Jul 6, 2026 7:20am | Jul 6, 2026 2:19pm | Jul 6, 2026 3:09pm | Jul 6, 2026 3:09pm | Jul 6, 2026 3:09pm | Jul 6, 2026 4:06pm | Jul 6, 2026 4:06pm | Jul 6, 2026 4:06pm |  |  | Fair | No | Spliced and reconnected service cable using 100ft. Service cable
Outage | J.E.26.07.04278 | C001840553 | Elvis Trowers | KSAN | Completed | Load_266896 | Washington Blvd - 510 | Jul 6, 2026 7:19am | Jul 6, 2026 7:38am | Jul 6, 2026 9:35am | Jul 6, 2026 9:39am | Jul 6, 2026 10:24am | Jul 6, 2026 10:32am | Jul 6, 2026 10:32am | Jul 6, 2026 10:32am |  |  | Fair | Yes | Premises found closed upon arrival and customer could not be contacted by telephone either after several calls, even though voice messages were left.
Outage | J.E.26.07.04410 | C001840554 | Christopher Edwards | KSAN | Completed | Load_248973 | Constant Spring - 410 | Jul 6, 2026 7:19am | Jul 6, 2026 7:50am | Jul 6, 2026 8:14am | Jul 6, 2026 8:33am | Jul 6, 2026 9:36am | Jul 6, 2026 9:44am | Jul 6, 2026 9:45am | Jul 6, 2026 9:45am |  |  | Fair | No | Refuse blown 25 kva transformer Using (1)3 ampsAlso clear vegetation off transformer pole
Non-Outage | J.E.26.07.04488 | C001840550 | Raymond Lewis | null | Completed | null | null | Jul 6, 2026 7:14am | Jul 6, 2026 7:15am | Jul 6, 2026 8:51am | Jul 6, 2026 8:51am | Jul 6, 2026 9:46am | Jul 6, 2026 9:50am | Jul 6, 2026 9:50am | Jul 6, 2026 9:50am |  |  | Fair | No | Supply restored
Outage | J.E.26.07.02873 | C001840549 | Richard Grant | St.Catherine | Completed | Load_265577 | Twickenham - 310 | Jul 6, 2026 7:14am | Jul 6, 2026 7:59am | Jul 6, 2026 1:42pm | Jul 6, 2026 1:42pm | Jul 6, 2026 2:53pm | Jul 6, 2026 2:53pm | Jul 6, 2026 2:53pm | Jul 6, 2026 2:53pm |  |  | Fair | No | Premises found okay
Outage | J.E.26.07.04447 | C001840547 | Raymond Lewis | St.Ann | Completed | Load_242054 | Ocho Rios - 310 | Jul 6, 2026 7:14am | Jul 6, 2026 7:15am | Jul 6, 2026 7:31am | Jul 6, 2026 7:31am | Jul 6, 2026 7:56am | Jul 6, 2026 7:59am | Jul 6, 2026 7:59am | Jul 6, 2026 7:59am |  |  | Fair | No | Supply restored
Outage | J.E.26.07.04471 | C001840548 | Raymond Lewis | St.Ann | Completed | Load_257505 | Ocho Rios - 310 | Jul 6, 2026 7:14am | Jul 6, 2026 7:15am | Jul 6, 2026 8:00am | Jul 6, 2026 8:00am | Jul 6, 2026 8:46am | Jul 6, 2026 8:48am | Jul 6, 2026 8:49am | Jul 6, 2026 8:49am |  |  | Fair | No | Call Customer, he said supply was at the premises when he left home
Outage | J.E.26.07.04547 | C001840543 | Tajay Bernard | Hanover | Completed | Load_242340 | Orange Bay - 310 | Jul 6, 2026 7:13am | Jul 6, 2026 7:14am | Jul 6, 2026 7:38am | Jul 6, 2026 9:25am | Jul 6, 2026 10:27am | Jul 6, 2026 10:29am | Jul 6, 2026 10:29am | Jul 6, 2026 10:29am |  |  | Fair | No | This call belongs to Westmoreland
Outage | J.E.26.07.04552 | C001840540 | Tajay Bernard | Hanover | Completed | Load_238755 | Orange Bay - 310 | Jul 6, 2026 7:13am | Jul 6, 2026 7:14am | Jul 6, 2026 7:20am | Jul 6, 2026 8:00am | Jul 6, 2026 8:54am | Jul 6, 2026 9:17am | Jul 6, 2026 9:18am | Jul 6, 2026 9:18am |  |  | Fair | No | Refuse 1 8amp junction fuse
Outage | J.E.26.07.04319 | C001840538 | Rayon Foster | Hanover | Completed | Load_240604 | Orange Bay - 310 | Jul 6, 2026 7:12am | Jul 6, 2026 8:03am | Jul 6, 2026 8:07am | Jul 6, 2026 8:08am | Jul 6, 2026 11:32am | Jul 6, 2026 11:48am | Jul 6, 2026 11:49am | Jul 6, 2026 11:49am | BrokenWire |  | Fair | No | Unable to reach customer on cell phone complete a patrol in area and did not identify and broken wire on ground and no power outage was noticed with in area voltage found on line 112v/114v/226v
Outage | J.E.26.07.04403 | C001840539 | Rayon Foster | Hanover | Completed | Load_240604 | Orange Bay - 310 | Jul 6, 2026 7:12am | Jul 6, 2026 8:02am | Jul 6, 2026 8:08am | Jul 6, 2026 11:49am | Jul 6, 2026 11:49am | Jul 6, 2026 11:50am | Jul 6, 2026 11:50am | Jul 6, 2026 11:50am | BrokenWire |  | Fair | No | Unable to reach customer on cell phone complete a patrol in area and did not identify and broken wire on ground and no power outage was noticed with in area voltage found on line 112v/114v/226v
Non-Outage | J.E.26.07.02586 | C001840537 | Wan Carlos Scarlett | null | Completed | null | null | Jul 6, 2026 7:09am | Jul 6, 2026 7:42am | Jul 6, 2026 10:16am | Jul 6, 2026 2:10pm | Jul 6, 2026 2:46pm | Jul 6, 2026 3:16pm | Jul 6, 2026 3:17pm | Jul 6, 2026 3:17pm |  |  | Fair | No | Reach at location been calling customer but no answer premises closed
Outage | J.E.26.07.04535 | C001840536 | Wan Carlos Scarlett | Portmore | Completed | Load_247634 | Naggo Head - 610 | Jul 6, 2026 7:09am | Jul 6, 2026 7:42am | Jul 6, 2026 8:13am | Jul 6, 2026 8:13am | Jul 6, 2026 9:10am | Jul 6, 2026 10:34am | Jul 6, 2026 10:38am | Jul 6, 2026 10:38am |  |  | Fair | No | Customer was reconnected from escalation department power supply has been restored
Outage | J.E.26.07.04513 | C001840530 | Richard Grant | St.Catherine | Completed | Load_302434 | New Michelton - 310 | Jul 6, 2026 7:07am | Jul 6, 2026 7:08am | Jul 6, 2026 8:35am | Jul 6, 2026 8:35am | Jul 6, 2026 9:43am | Jul 6, 2026 11:49am | Jul 6, 2026 11:49am | Jul 6, 2026 11:49am |  |  | Rains | No | Two 25a, 20a & 7d amps single phase primary and 2amps for 10kva transformer all found blown. No visible cause seen after patrol conducted. 25a, 15a, 10a, 8a fuses used to do proper fuse coordination on single phase primary. 2amps fuse replaced with same and supply restored. Area left okay
Outage | J.E.26.07.04537 | C001840524 | Christopher Edwards | KSAN | Completed | Load_268534 | Washington Blvd - 310 | Jul 6, 2026 6:15am | Jul 6, 2026 6:15am | Jul 6, 2026 6:18am | Jul 6, 2026 6:43am | Jul 6, 2026 6:43am | Jul 6, 2026 8:11am | Jul 6, 2026 8:13am | Jul 6, 2026 8:13am | BrokenWire |  | Fair | No | Changed burnt X1 secondary lug Remake burnt phase drop leadUsing (2) one bolt clamps Refuse blown 50 kva transformer Using (1) 5 amps
Outage | J.E.26.07.04518 | C001840523 | Christopher Edwards | KSAS | Completed | Load_245025 | Cane River - 410 | Jul 6, 2026 2:44am | Jul 6, 2026 2:44am | Jul 6, 2026 2:47am | Jul 6, 2026 3:31am | Jul 6, 2026 4:20am | Jul 6, 2026 4:38am | Jul 6, 2026 4:39am | Jul 6, 2026 4:39am |  |  | Fair | No | Refuse blown junction fuseUsing (1) 15 ampsAlso replaced damaged fuse holder
Non-Outage | J.E.26.07.04203 | C001840521 | Michael Christian | St.James | Completed | Load_262522 | Bogue - 510 | Jul 6, 2026 1:15am | Jul 6, 2026 1:32am | Jul 6, 2026 4:35am | Jul 6, 2026 4:35am | Jul 6, 2026 5:19am | Jul 6, 2026 5:26am | Jul 6, 2026 5:26am | Jul 6, 2026 5:26am | BrokenPole |  | Fair | No | Found 1 guys pole need and 2 30 ft pole need urgent send to maintenance
Outage | J.E.26.07.04449 | C001840515 | Michael Christian | St.James | Completed | Load_245936 | Queens Drive - 710 | Jul 5, 2026 10:59pm | Jul 5, 2026 11:01pm | Jul 6, 2026 1:24am | Jul 6, 2026 1:24am | Jul 6, 2026 2:13am | Jul 6, 2026 2:27am | Jul 6, 2026 2:27am | Jul 6, 2026 2:27am |  |  | Fair | No | Found 1 50 kava transformer out no cause found replace 1 5 amp
Outage | J.E.26.07.04446 | C001840513 | Roxroy Needham | St.Ann | Completed | Load_249881 | Ocho Rios - 310 | Jul 5, 2026 10:58pm | Jul 5, 2026 10:59pm | Jul 6, 2026 1:31am | Jul 6, 2026 1:31am | Jul 6, 2026 3:10am | Jul 6, 2026 4:00am | Jul 6, 2026 4:04am | Jul 6, 2026 4:04am |  |  | Fair | No | Replace a 30 amps junction fuse at pole
Outage | J.E.26.07.04458 | C001840514 | Roxroy Needham | St.Ann | Completed | Load_242702 | Ocho Rios - 310 | Jul 5, 2026 10:58pm | Jul 5, 2026 10:59pm | Jul 6, 2026 4:04am | Jul 6, 2026 4:04am | Jul 6, 2026 4:04am | Jul 6, 2026 4:02am | Jul 6, 2026 4:06am | Jul 6, 2026 4:06am |  |  | Fair | No | Call related to 30 amps junction fuse
Outage | J.E.26.07.04423 | C001840508 | Shamour Haughton | St.James | Completed | Load_243318 | Bogue - 610 | Jul 5, 2026 9:42pm | Jul 5, 2026 9:43pm | Jul 5, 2026 10:28pm | Jul 5, 2026 10:29pm | Jul 5, 2026 10:42pm | Jul 5, 2026 10:42pm | Jul 5, 2026 10:47pm | Jul 5, 2026 10:47pm |  |  | Fair | No | Premises locked, unable to access premises
Outage | J.E.26.07.04380 | C001840507 | Andre Williams | Trelawny | Completed | Load_264552 | Duncans - 210 | Jul 5, 2026 9:33pm | Jul 5, 2026 9:38pm | Jul 5, 2026 10:11pm | Jul 5, 2026 10:11pm | Jul 5, 2026 10:53pm | Jul 5, 2026 11:07pm | Jul 5, 2026 11:08pm | Jul 5, 2026 11:08pm | BrokenWire |  | Fair | No | Splice and retention burnt off neutral on customer 2 wire service voltage 113,
Outage | J.E.26.07.04433 | C001840504 | Evan Spaulding | St.Mary | Completed | Load_265185 | Highgate -110 | Jul 5, 2026 9:27pm | Jul 6, 2026 7:47am | Jul 6, 2026 10:03am | Jul 6, 2026 10:03am | Jul 6, 2026 10:54am | Jul 6, 2026 1:00am | Jul 6, 2026 1:16pm | Jul 6, 2026 1:16pm | BrokenWire |  | Fair | No | Splice and retention three spans secondary conductors using 150 ft 2/0 AAAC conductor,4-2/0 splicing sleeves,4 -2/0 preforms and 4-1bolt clamps.
Outage | J.E.26.07.04426 | C001840503 | Denton Williams | Portland | Completed | Load_267035 | Port Antonio - 310 | Jul 5, 2026 9:26pm | Jul 6, 2026 7:15am | Jul 6, 2026 7:22am | Jul 6, 2026 8:28am | Jul 6, 2026 8:28am | Jul 6, 2026 9:22am | Jul 6, 2026 9:26am | Jul 6, 2026 9:26am |  |  | Fair | No | Dislodge pothead on customer house, advised customer to contact a licensed electrician to carry out repairs.
Outage | J.E.26.07.03784 | C001840501 | Oshane Warren | Westmoreland | Completed | Load_255089 | Paradise - 110 | Jul 5, 2026 9:07pm | Jul 5, 2026 9:07pm | Jul 6, 2026 10:01am | Jul 6, 2026 10:04am | Jul 6, 2026 12:05pm | Jul 6, 2026 12:05pm | Jul 6, 2026 12:06pm | Jul 6, 2026 12:06pm |  |  | Fair | No | Replace 2 amp 25 kva transformer fuse
Non-Outage | J.E.26.07.04399 | C001840497 | Stephen Taylor | null | Completed | null | null | Jul 5, 2026 8:32pm | Jul 5, 2026 8:32pm | Jul 5, 2026 9:58pm | Jul 5, 2026 9:58pm | Jul 5, 2026 9:58pm | Jul 5, 2026 9:58pm | Jul 5, 2026 9:59pm | Jul 5, 2026 9:59pm |  |  | Fair | No | See junction link down no number on pole patrol see nothing and close back junction with a 10 amp fuse all customer is now okay
Outage | J.E.26.07.04413 | C001840496 | Stephen Taylor | St.Thomas | Completed | Load_247075 | Good Year - 210 | Jul 5, 2026 8:32pm | Jul 5, 2026 8:32pm | Jul 5, 2026 9:55pm | Jul 5, 2026 9:55pm | Jul 5, 2026 9:55pm | Jul 5, 2026 9:56pm | Jul 5, 2026 9:56pm | Jul 5, 2026 9:56pm |  |  | Fair | No | See junction link down no number on pole patrol see nothing and close back junction with a 10 amp fuse all customer is now okay
Outage | J.E.26.07.04388 | C001840494 | Milton Charlton | KSAN | Completed | Load_264167 | Hope - 510 | Jul 5, 2026 8:26pm | Jul 6, 2026 7:37am | Jul 6, 2026 2:56pm | Jul 6, 2026 2:56pm | Jul 6, 2026 3:56pm | Jul 6, 2026 4:00pm | Jul 6, 2026 3:57pm | Jul 6, 2026 3:57pm |  |  | Fair | No | Reconnect customer meter #1681540 by J.P.S. Escalation.
Outage | J.E.26.07.04415 | C001840495 | Milton Charlton | KSAN | Completed | Load_252653 | West Kings House - 310 | Jul 5, 2026 8:26pm | Jul 6, 2026 7:37am | Jul 6, 2026 8:57am | Jul 6, 2026 8:57am | Jul 6, 2026 10:14am | Jul 6, 2026 9:40am | Jul 6, 2026 10:15am | Jul 6, 2026 10:15am |  |  | Fair | No | Found okay upon arrival. Customer has an internal problem.
Outage | J.E.26.07.04396 | C001840488 | Romeo Brissett | St.James | Completed | Load_265097 | Bogue - 310 | Jul 5, 2026 7:57pm | Jul 5, 2026 7:58pm | Jul 5, 2026 8:53pm | Jul 5, 2026 8:53pm | Jul 5, 2026 9:26pm | Jul 5, 2026 10:00pm | Jul 5, 2026 10:06pm | Jul 5, 2026 10:06pm |  |  | Fair | No | Line patrolled and found power in the area, lot number was found power found at the premises.
Non-Outage | J.E.26.07.04262 | C001840485 | Richard Samuda | Manchester | Completed | Load_252232 | Spur Tree - 310 | Jul 5, 2026 7:48pm | Jul 5, 2026 7:48pm | Jul 5, 2026 8:35pm | Jul 5, 2026 8:35pm | Jul 5, 2026 8:35pm | Jul 5, 2026 9:26pm | Jul 5, 2026 10:09pm | Jul 5, 2026 10:09pm |  |  | Fair | No | Splice and reconnect customer service wire that was broken causing customer to experience single 114/before 116/114/230
Outage | J.E.26.07.04372 | C001840484 | Kenroy Dale | Manchester | Completed | Load_265961 | Kendal - 210 | Jul 5, 2026 7:48pm | Jul 5, 2026 7:48pm | Jul 5, 2026 8:51pm | Jul 5, 2026 8:51pm | Jul 5, 2026 10:32pm | Jul 5, 2026 10:49pm | Jul 5, 2026 10:52pm | Jul 5, 2026 10:52pm |  |  | Fair | No | Blown 8 amp junction fuse found causing from a tree branch that was. Cut on conductor, tree branch was removed blown fuse replaced and area now with supply
Outage | J.E.26.07.04313 | C001840483 | Richard Watson | St.Elizabeth | Completed | Load_258532 | Maggotty - 110 | Jul 5, 2026 7:41pm | Jul 6, 2026 8:15am | Jul 6, 2026 8:26am | Jul 6, 2026 9:01am | Jul 6, 2026 10:24am | Jul 6, 2026 10:40am | Jul 6, 2026 10:42am | Jul 6, 2026 10:42am |  |  | Fair | No | Reset trip 10kva transformer at pole# 047988, patrol on line section reveal no visible fault, supply restored.
Outage | J.E.26.07.04382 | C001840482 | Marlon Authors | Manchester | Completed | Load_268938 | Spur Tree - 210 | Jul 5, 2026 7:41pm | Jul 5, 2026 7:41pm | Jul 5, 2026 8:44pm | Jul 5, 2026 8:44pm | Jul 5, 2026 8:44pm | Jul 5, 2026 8:51pm | Jul 5, 2026 8:51pm | Jul 5, 2026 8:51pm |  |  | Fair | No | Supply checked and found service wire neutral broken at pole. Splice and retention same using 5 feet of #6 triplex service wire and two clamps. Supply leave working ok rdg 108v,109v and cross phased 217 volts
Outage | J.E.26.07.04260 | C001840478 | Richman Whyte | Westmoreland | Completed | Load_292952 | Paradise - 310 | Jul 5, 2026 7:26pm | Jul 5, 2026 7:45pm | Jul 5, 2026 8:49pm | Jul 5, 2026 8:49pm | Jul 5, 2026 8:49pm | Jul 5, 2026 8:49pm | Jul 5, 2026 8:50pm | Jul 5, 2026 8:50pm |  |  | Fair | No | Restore from earlier today
Outage | J.E.26.07.04348 | C001840477 | Richman Whyte | St.Elizabeth | Completed | Load_238633 | Maggotty - 110 | Jul 5, 2026 7:15pm | Jul 5, 2026 7:22pm | Jul 5, 2026 8:50pm | Jul 5, 2026 8:51pm | Jul 5, 2026 10:13pm | Jul 5, 2026 10:14pm | Jul 5, 2026 10:14pm | Jul 5, 2026 10:14pm | Fire |  | Fair | No | Check and found okay
Outage | J.E.26.07.04264 | C001840476 | Milton Charlton | KSAN | Completed | Load_258272 | Washington Blvd - 510 | Jul 5, 2026 7:14pm | Jul 5, 2026 7:14pm | Jul 5, 2026 9:31pm | Jul 5, 2026 9:36pm | Jul 5, 2026 10:29pm | Jul 5, 2026 10:30pm | Jul 5, 2026 10:30pm | Jul 5, 2026 10:30pm |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.07.04101 | C001840475 | Rusean Allen | KSAS | Completed | Load_251115 | Rockfort - 410 | Jul 5, 2026 6:57pm | Jul 6, 2026 7:42am | Jul 6, 2026 9:14am | Jul 6, 2026 9:50am | Jul 6, 2026 10:40am | Jul 6, 2026 10:51am | Jul 6, 2026 10:51am | Jul 6, 2026 10:51am |  |  | Fair | No | 1x 10amp fuse found 1x 10amp fuse replaced.
Non-Outage | J.E.26.07.04316 | C001840473 | Fitzroy Turner | null | Completed | null | null | Jul 5, 2026 6:50pm | Jul 6, 2026 7:39am | Jul 6, 2026 10:44am | Jul 6, 2026 10:44am | Jul 6, 2026 11:15am | Jul 6, 2026 11:16am | Jul 6, 2026 11:17am | Jul 6, 2026 11:17am |  |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.07.04063 | C001840470 | Stephen Taylor | St.Thomas | Completed | Load_259831 | Good Year - 210 | Jul 5, 2026 6:46pm | Jul 5, 2026 6:46pm | Jul 5, 2026 8:10pm | Jul 5, 2026 8:10pm | Jul 5, 2026 8:10pm | Jul 5, 2026 8:10pm | Jul 5, 2026 8:11pm | Jul 5, 2026 8:11pm |  |  | Fair | No | Failed to locate customer several calls and no one answering the phone need more information to contact customer
Outage | J.E.26.07.04291 | C001840468 | Stephen Taylor | St.Thomas | Completed | Load_254225 | Lysson - 410 | Jul 5, 2026 6:46pm | Jul 5, 2026 6:46pm | Jul 5, 2026 8:29pm | Jul 5, 2026 8:29pm | Jul 5, 2026 8:29pm | Jul 5, 2026 8:33pm | Jul 5, 2026 8:37pm | Jul 5, 2026 8:37pm |  |  | Fair | No | Patrol erea and power is in the area but several calls to single customer and no one answering the phone
Outage | J.E.26.07.04293 | C001840471 | Stephen Taylor | St.Thomas | Completed | Load_241378 | Good Year - 210 | Jul 5, 2026 6:46pm | Jul 5, 2026 6:46pm | Jul 5, 2026 8:37pm | Jul 5, 2026 8:37pm | Jul 5, 2026 9:30pm | Jul 5, 2026 9:30pm | Jul 5, 2026 9:55pm | Jul 5, 2026 9:55pm |  |  | Fair | No | See junction link down no number on pole patrol see nothing and close back junction with a 10 amp fuse all customer is now okay
Outage | J.E.26.07.04359 | C001840467 | Roxroy Needham | St.Ann | Completed | Load_269911 | Cardiff Hall - 310 | Jul 5, 2026 6:39pm | Jul 5, 2026 6:39pm | Jul 5, 2026 7:37pm | Jul 5, 2026 7:37pm | Jul 5, 2026 8:18pm | Jul 5, 2026 8:50pm | Jul 5, 2026 8:55pm | Jul 5, 2026 8:55pm |  |  | Fair | No | Replace 1 - 2 amp for a 10 KVA transformer after illegal wire was remove voltage left 115,112,227
Outage | J.E.26.07.04342 | C001840464 | Hartley Chin | Clarendon | Completed | Load_239131 | May Pen - 110 | Jul 5, 2026 6:32pm | Jul 5, 2026 6:43pm | Jul 5, 2026 6:46pm | Jul 5, 2026 6:46pm | Jul 5, 2026 7:50pm | Jul 5, 2026 8:45pm | Jul 5, 2026 8:45pm | Jul 5, 2026 8:45pm | BrokenWire |  | Fair | No | Found blown 5 amp fuse on 50 KVA transformer @ pole # 0100839 due to broken open secondary phase found across 2 span … was told that incident was caused by truck … repair phase … refused transformer… use 50 ft conductor , 2 clamp …
Non-Outage | J.E.26.07.04344 | C001840461 | Edward Royal | KSAN | Completed | Load_567618 | Constant Spring - 310 | Jul 5, 2026 6:13pm | Jul 5, 2026 6:13pm | Jul 5, 2026 9:47pm | Jul 5, 2026 9:47pm | Jul 5, 2026 9:47pm | Jul 5, 2026 9:48pm | Jul 5, 2026 9:49pm | Jul 5, 2026 9:49pm |  |  | Fair | No | Defective meter need to be change referred to field service
Non-Outage | J.E.26.07.03993 | C001840460 | Roxroy Needham | St.Ann | Completed | Load_240297 | Cardiff Hall - 310 | Jul 5, 2026 6:01pm | Jul 5, 2026 6:01pm | Jul 5, 2026 6:07pm | Jul 5, 2026 6:07pm | Jul 5, 2026 7:23pm | Jul 5, 2026 7:25pm | Jul 5, 2026 7:28pm | Jul 5, 2026 7:28pm |  |  | Fair | No | Clean and remake joint at pole used 1- 1bolt clamp voltage readings left 118,119,237
Outage | J.E.26.07.04078 | C001840457 | Lancelot Brown | Hanover | Completed | Load_303168 | Orange Bay - 210 | Jul 5, 2026 5:42pm | Jul 5, 2026 5:42pm | Jul 5, 2026 5:50pm | Jul 5, 2026 8:13pm | Jul 5, 2026 8:13pm | Jul 5, 2026 8:14pm | Jul 5, 2026 8:14pm | Jul 5, 2026 8:14pm | BrokenWire |  | Rains | No | Cannot locate customer no answer from contact number need proper direction
Outage | J.E.26.07.04229 | C001840456 | Tajay Bernard | Hanover | Completed | Load_265073 | Orange Bay - 310 | Jul 5, 2026 5:42pm | Jul 6, 2026 7:14am | Jul 6, 2026 7:38am | Jul 6, 2026 9:20am | Jul 6, 2026 9:20am | Jul 6, 2026 9:21am | Jul 6, 2026 9:22am | Jul 6, 2026 9:22am |  |  | Fair | No | Related to previous call job number 04552
Outage | J.E.26.07.04284 | C001840458 | Lancelot Brown | Hanover | Completed | Load_303168 | Orange Bay - 210 | Jul 5, 2026 5:42pm | Jul 5, 2026 5:42pm | Jul 5, 2026 5:49pm | Jul 5, 2026 5:50pm | Jul 5, 2026 8:09pm | Jul 5, 2026 8:11pm | Jul 5, 2026 8:12pm | Jul 5, 2026 8:12pm |  |  | Rains | No | Found junction fuse blown patroll found another junction fuse blown patroll found nothing replace 1-20amps junction fuse no pole number also replace 1-8amps junction fuse no pole number supply restore caused by lightning and rain
Non-Outage | J.E.26.07.04330 | C001840455 | Omar King | null | Completed | null | null | Jul 5, 2026 5:40pm | Jul 5, 2026 5:42pm | Jul 5, 2026 5:50pm | Jul 5, 2026 5:50pm | Jul 5, 2026 6:29pm | Jul 5, 2026 6:34pm | Jul 5, 2026 6:34pm | Jul 5, 2026 6:34pm | BrokenWire |  | Fair | No | Found main line neutral broken please refer to maintenance to carry out repair
Outage | J.E.26.07.04320 | C001840454 | Evan Spaulding | St.Mary | Completed | Load_253478 | Highgate -110 | Jul 5, 2026 5:36pm | Jul 6, 2026 7:47am | Jul 6, 2026 8:11am | Jul 6, 2026 8:11am | Jul 6, 2026 9:29am | Jul 6, 2026 9:59am | Jul 6, 2026 10:01am | Jul 6, 2026 10:01am | BrokenWire |  | Fair | No | Carry out spot bushing, splice and retention secondary conductors using 90ft #2AAAC conductor,2-2/0 preforms,1- #2 splicing sleeve and 2-1 bolt clamps.
Outage | J.E.26.07.04226 | C001840453 | Andre Smith | KSAS | Completed | Load_247742 | Rockfort - 210 | Jul 5, 2026 5:35pm | Jul 5, 2026 5:35pm | Jul 5, 2026 7:20pm | Jul 5, 2026 7:20pm | Jul 5, 2026 7:54pm | Jul 5, 2026 8:23pm | Jul 5, 2026 8:23pm | Jul 5, 2026 8:23pm |  |  | Fair | No | Repair burnt switch bottom jumper supply restored
Non-Outage | J.E.26.07.03923 | C001840446 | Roxroy Needham | St.Ann | Completed | Load_240297 | Cardiff Hall - 310 | Jul 5, 2026 5:17pm | Jul 5, 2026 5:18pm | Jul 5, 2026 7:28pm | Jul 5, 2026 7:28pm | Jul 5, 2026 7:28pm | Jul 5, 2026 7:30pm | Jul 5, 2026 7:30pm | Jul 5, 2026 7:30pm |  |  | Fair | No | Clean and remake joint at pole used 1- 1bolt clamp voltage reading left 119,117,237
Non-Outage | J.E.26.07.03983 | C001840445 | Roxroy Needham | St.Ann | Completed | Load_238381 | Cardiff Hall - 210 | Jul 5, 2026 5:16pm | Jul 5, 2026 5:17pm | Jul 5, 2026 5:29pm | Jul 5, 2026 5:29pm | Jul 5, 2026 6:01pm | Jul 5, 2026 6:01pm | Jul 5, 2026 6:04pm | Jul 5, 2026 6:04pm |  |  | Fair | No | Found premises ok
Outage | J.E.26.07.04150 | C001840444 | Romeo Brissett | St.James | Completed | Load_266743 | Bogue - 310 | Jul 5, 2026 5:12pm | Jul 5, 2026 5:12pm | Jul 5, 2026 5:14pm | Jul 5, 2026 5:14pm | Jul 5, 2026 6:15pm | Jul 5, 2026 8:42pm | Jul 5, 2026 8:53pm | Jul 5, 2026 8:53pm |  |  | Fair | No | Isolated (1)50kva transformer, removed several illegal connections, retention 1 span of secondary, V/R before 132-99-208-after 112-114-227
Outage | J.E.26.07.04168 | C001840443 | Neville Spencer | Clarendon | Completed | Load_579438 | May Pen - 110 | Jul 5, 2026 5:10pm | Jul 5, 2026 7:30pm | Jul 5, 2026 7:37pm | Jul 5, 2026 7:37pm | Jul 6, 2026 8:24am | Jul 6, 2026 8:25am | Jul 6, 2026 8:26am | Jul 6, 2026 8:26am | BangingWires |  | Fair | No | Not located.
Outage | J.E.26.07.04158 | C001840442 | Shamour Haughton | St.James | Completed | Load_261398 | Bogue - 610 | Jul 5, 2026 4:35pm | Jul 5, 2026 5:10pm | Jul 5, 2026 5:14pm | Jul 5, 2026 5:14pm | Jul 5, 2026 7:33pm | Jul 5, 2026 7:33pm | Jul 5, 2026 7:43pm | Jul 5, 2026 7:43pm |  |  | Fair | No | Found 1 ,25kva fuse blown caused by banging secondary, retention secondary neutral use 1#2 preform and 1 clamp and refuse 25kva use 1,3amp fuse
Outage | J.E.26.07.04247 | C001840440 | Dwayne Samuels | Trelawny | Completed | Load_240177 | Martha Brae - 110 | Jul 5, 2026 4:33pm | Jul 5, 2026 4:34pm | Jul 5, 2026 4:57pm | Jul 5, 2026 4:59pm | Jul 5, 2026 5:55pm | Jul 5, 2026 6:23pm | Jul 5, 2026 6:23pm | Jul 5, 2026 6:23pm |  |  | Fair | No | customer meter is in locking band unable to access meter voltage found at pothead line side 114v/113v/227 voltage check on load side 113v refer to field service to have further checks done.
Outage | J.E.26.07.04288 | C001840441 | Edward Royal | KSAN | Completed | Load_238279 | Constant Spring - 410 | Jul 5, 2026 4:33pm | Jul 5, 2026 4:33pm | Jul 5, 2026 7:13pm | Jul 5, 2026 7:13pm | Jul 5, 2026 7:53pm | Jul 5, 2026 8:44pm | Jul 5, 2026 8:44pm | Jul 5, 2026 8:44pm |  |  | Fair | No | Primary line voltage is to high from substation reffered to SMD
Outage | J.E.26.07.04092 | C001840439 | Donald Cunningham | St.Catherine | Completed | Load_260475 | New Michelton - 210 | Jul 5, 2026 4:29pm | Jul 5, 2026 4:30pm | Jul 5, 2026 6:03pm | Jul 5, 2026 6:03pm | Jul 5, 2026 6:26pm | Jul 5, 2026 6:26pm | Jul 5, 2026 6:27pm | Jul 5, 2026 6:27pm |  |  | Fair | No | Supply restored
Outage | J.E.26.07.04277 | C001840438 | Andre Smith | KSAS | Completed | Load_257065 | Cane River - 410 | Jul 5, 2026 4:22pm | Jul 5, 2026 4:22pm | Jul 5, 2026 9:01pm | Jul 5, 2026 9:53pm | Jul 5, 2026 10:16pm | Jul 5, 2026 10:19pm | Jul 5, 2026 10:20pm | Jul 5, 2026 10:20pm |  |  | Fair | No | Premises found okay supply restored already
Outage | J.E.26.07.04266 | C001840437 | Romaine Roberts | St.Mary | Completed | Load_261992 | Blackstonedge - 110 | Jul 5, 2026 4:18pm | Jul 5, 2026 4:18pm | Jul 5, 2026 6:47pm | Jul 5, 2026 6:47pm | Jul 5, 2026 7:44pm | Jul 5, 2026 9:38pm | Jul 5, 2026 9:41pm | Jul 5, 2026 9:41pm |  |  | Fair | No | Found that the secondary line need a day light attention to carry out patrol good checks voltage at the end of line 123-1129-227and the transformer dropped lead found 119-119 -242 please to fallow up
Outage | J.E.26.07.04221 | C001840436 | Omar King | St.Ann | Completed | Load_253871 | Ocho Rios - 510 | Jul 5, 2026 4:17pm | Jul 5, 2026 4:17pm | Jul 5, 2026 5:12pm | Jul 5, 2026 5:12pm | Jul 5, 2026 5:12pm | Jul 5, 2026 5:14pm | Jul 5, 2026 5:14pm | Jul 5, 2026 5:14pm |  |  | Fair | No | Call giving is in Kingston and ST Andrew area
Non-Outage | J.E.26.07.04269 | C001840434 | Edward Royal | null | Completed | null | null | Jul 5, 2026 4:14pm | Jul 5, 2026 4:29pm | Jul 5, 2026 6:16pm | Jul 5, 2026 6:16pm | Jul 5, 2026 6:57pm | Jul 5, 2026 7:08pm | Jul 5, 2026 7:09pm | Jul 5, 2026 7:09pm |  |  | Fair | No | Replaced 2A transformer fuse pole#0000813
Outage | J.E.26.07.03138 | C001840435 | Ricky Hall | St.Catherine | Completed | Load_568931 | Twickenham - 310 | Jul 5, 2026 4:14pm | Jul 5, 2026 4:15pm | Jul 5, 2026 4:34pm | Jul 5, 2026 4:35pm | Jul 5, 2026 4:43pm | Jul 5, 2026 4:44pm | Jul 5, 2026 4:44pm | Jul 5, 2026 4:44pm |  |  | Fair | No | Premises not located
Outage | J.E.26.07.04263 | C001840432 | Milton Charlton | KSAN | Completed | Load_253362 | West Kings House - 310 | Jul 5, 2026 4:12pm | Jul 5, 2026 4:13pm | Jul 5, 2026 6:00pm | Jul 5, 2026 6:02pm | Jul 5, 2026 6:54pm | Jul 5, 2026 6:55pm | Jul 5, 2026 6:56pm | Jul 5, 2026 6:56pm |  |  | Fair | No | Reset customer circuit breaker tripped at meter socket.
Outage | J.E.26.07.04265 | C001840431 | Edward Royal | KSAN | Completed | Load_243726 | Constant Spring - 410 | Jul 5, 2026 4:08pm | Jul 5, 2026 4:13pm | Jul 5, 2026 7:09pm | Jul 5, 2026 7:09pm | Jul 5, 2026 7:09pm | Jul 5, 2026 7:10pm | Jul 5, 2026 7:10pm | Jul 5, 2026 7:10pm |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.07.04239 | C001840428 | Donald Cunningham | St.Catherine | Completed | Load_244982 | New Michelton - 210 | Jul 5, 2026 3:54pm | Jul 5, 2026 3:55pm | Jul 5, 2026 8:25pm | Jul 5, 2026 8:25pm | Jul 5, 2026 9:12pm | Jul 5, 2026 9:13pm | Jul 5, 2026 9:19pm | Jul 5, 2026 9:19pm |  |  | Fair | No | Premises found ok with supply
Outage | J.E.26.07.04246 | C001840429 | Ricky Hall | St.Catherine | Completed | Load_250553 | Tredegar - 410 | Jul 5, 2026 3:54pm | Jul 5, 2026 3:55pm | Jul 5, 2026 4:45pm | Jul 5, 2026 4:45pm | Jul 5, 2026 5:11pm | Jul 5, 2026 5:12pm | Jul 5, 2026 5:14pm | Jul 5, 2026 5:14pm |  |  | Fair | No | Leaking 25 kva xfmr with EG enclosure request to have the same open for further troubleshooting
Outage | J.E.26.06.39265 | C001840426 | Nickolas Rodriques | Portmore | Completed | Load_257303 | Naggo Head - 510 | Jul 5, 2026 3:52pm | Jul 5, 2026 3:53pm | Jul 5, 2026 7:03pm | Jul 5, 2026 7:17pm | Jul 5, 2026 8:00pm | Jul 5, 2026 8:10pm | Jul 5, 2026 8:10pm | Jul 5, 2026 8:10pm |  |  | Fair | No | Customer stated that she is having unstable voltage. Reading found (120-118-238). All necessary checks were done and the issue appears to be coming from the hexing box. Refer to field service.
Non-Outage | J.E.26.07.04065 | C001840423 | Andre Smith | null | Completed | null | null | Jul 5, 2026 3:42pm | Jul 5, 2026 3:43pm | Jul 5, 2026 4:02pm | Jul 5, 2026 4:02pm | Jul 5, 2026 4:41pm | Jul 5, 2026 4:59pm | Jul 5, 2026 4:59pm | Jul 5, 2026 4:59pm |  |  | Fair | No | Premises found okay supply restored already
Non-Outage | J.E.26.07.04162 | C001840424 | Andre Smith | null | Completed | null | null | Jul 5, 2026 3:42pm | Jul 5, 2026 3:43pm | Jul 5, 2026 5:01pm | Jul 5, 2026 5:01pm | Jul 5, 2026 5:38pm | Jul 5, 2026 5:39pm | Jul 5, 2026 5:39pm | Jul 5, 2026 5:39pm |  |  | Fair | No | Premises found okay supply restored already
Outage | J.E.26.07.04197 | C001840422 | Milton Charlton | KSAN | Completed | Load_257632 | Washington Blvd - 510 | Jul 5, 2026 3:41pm | Jul 5, 2026 3:41pm | Jul 5, 2026 5:09pm | Jul 5, 2026 5:09pm | Jul 5, 2026 5:25pm | Jul 5, 2026 6:00pm | Jul 5, 2026 5:59pm | Jul 5, 2026 5:59pm |  |  | Fair | No | Customer service wire # 2/0 phase corroded at pothead. Repair using one 1- bolt clamp. Readings at meter socket and pothead 119-120-240 volts.
Outage | J.E.26.07.04097 | C001840421 | Andre Smith | KSAS | Completed | Load_258205 | Cane River - 610 | Jul 5, 2026 3:40pm | Jul 5, 2026 3:42pm | Jul 5, 2026 8:24pm | Jul 5, 2026 8:24pm | Jul 5, 2026 8:47pm | Jul 5, 2026 8:59pm | Jul 5, 2026 8:59pm | Jul 5, 2026 8:59pm |  |  | Fair | No | Repair burnt switch bottom jumper supply restored
Outage | J.E.26.07.04237 | C001840419 | Marlon Authors | Manchester | Completed | Load_265385 | Spur Tree - 210 | Jul 5, 2026 3:35pm | Jul 5, 2026 3:36pm | Jul 5, 2026 6:41pm | Jul 5, 2026 6:41pm | Jul 5, 2026 6:41pm | Jul 5, 2026 6:42pm | Jul 5, 2026 6:42pm | Jul 5, 2026 6:42pm |  |  | Fair | No | Customer said supply was restored
Outage | J.E.26.07.04185 | C001840417 | Richman Whyte | Westmoreland | Completed | Load_292536 | Paradise - 310 | Jul 5, 2026 3:33pm | Jul 5, 2026 3:34pm | Jul 5, 2026 4:41pm | Jul 5, 2026 4:41pm | Jul 5, 2026 5:25pm | Jul 5, 2026 6:35pm | Jul 5, 2026 6:39pm | Jul 5, 2026 6:39pm |  |  | Rains | No | Replace twenty and ten amp junction also two three amp twenty five kva transformer fuse
Outage | J.E.26.07.04227 | C001840418 | Oshane Warren | Westmoreland | Completed | Load_238357 | Paradise - 210 | Jul 5, 2026 3:33pm | Jul 5, 2026 3:34pm | Jul 5, 2026 7:39pm | Jul 5, 2026 7:39pm | Jul 5, 2026 7:53pm | Jul 5, 2026 7:57pm | Jul 5, 2026 7:57pm | Jul 5, 2026 7:57pm |  |  | Fair | No | Replace 2 15 amp junction fuse
Outage | J.E.26.07.04207 | C001840416 | Richman Whyte | Westmoreland | Completed | Load_292895 | Paradise - 310 | Jul 5, 2026 3:31pm | Jul 5, 2026 3:34pm | Jul 5, 2026 8:39pm | Jul 5, 2026 8:39pm | Jul 5, 2026 8:39pm | Jul 5, 2026 8:45pm | Jul 5, 2026 8:46pm | Jul 5, 2026 8:46pm | BrokenWire |  | Rains | No | Replace 8 amp junction fuse
Outage | J.E.26.07.04243 | C001840415 | Oshane Warren | Westmoreland | Completed | Load_241469 | Paradise - 210 | Jul 5, 2026 3:31pm | Jul 5, 2026 3:32pm | Jul 5, 2026 4:06pm | Jul 5, 2026 4:06pm | Jul 5, 2026 5:44pm | Jul 5, 2026 7:35pm | Jul 5, 2026 7:39pm | Jul 5, 2026 7:39pm | Fire |  | Fair | No | Open 100 kva transformer fuse and splice and retention one spand secondary conductor used 6pg clamps
Outage | J.E.26.07.03822 | C001840414 | Nickolas Rodriques | Portmore | Completed | Load_1004100 | Naggo Head - 510 | Jul 5, 2026 3:30pm | Jul 5, 2026 3:32pm | Jul 5, 2026 3:44pm | Jul 5, 2026 3:46pm | Jul 5, 2026 4:15pm | Jul 5, 2026 4:36pm | Jul 5, 2026 4:37pm | Jul 5, 2026 4:37pm |  |  | Fair | No | Unable to locate the customer. However, she was contacted and stated that no one is currently home to accommodate the team and she would like to request a team for tomorrow July 6/2026 at anytime.
Outage | J.E.26.07.04163 | C001840411 | Edward Royal | KSAN | Completed | Load_237815 | Constant Spring - 410 | Jul 5, 2026 3:29pm | Jul 5, 2026 3:30pm | Jul 5, 2026 5:19pm | Jul 5, 2026 5:20pm | Jul 5, 2026 5:20pm | Jul 5, 2026 6:14pm | Jul 5, 2026 6:14pm | Jul 5, 2026 6:14pm |  |  | Fair | No | Replaced 20A junction fuse
Outage | J.E.26.07.04109 | C001840410 | Derrick Dawkins | St.James | Completed | Load_266978 | Queens Drive - 710 | Jul 5, 2026 3:28pm | Jul 5, 2026 3:29pm | Jul 5, 2026 7:53pm | Jul 5, 2026 7:53pm | Jul 5, 2026 7:53pm | Jul 5, 2026 5:18pm | Jul 5, 2026 7:55pm | Jul 5, 2026 7:55pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.04003 | C001840409 | Neville Spencer | Clarendon | Completed | Load_260600 | May Pen - 110 | Jul 5, 2026 3:14pm | Jul 5, 2026 3:29pm | Jul 5, 2026 4:38pm | Jul 5, 2026 4:39pm | Jul 5, 2026 5:46pm | Jul 5, 2026 5:46pm | Jul 5, 2026 6:42pm | Jul 5, 2026 6:42pm |  |  | Fair | No | Remade burnt out clamp on phase jumper used 1, clamp supply restored.
Outage | J.E.26.07.04222 | C001840407 | Kenroy Dale | Manchester | Completed | Load_252526 | Kendal - 210 | Jul 5, 2026 2:59pm | Jul 5, 2026 2:59pm | Jul 5, 2026 5:47pm | Jul 5, 2026 5:47pm | Jul 5, 2026 6:48pm | Jul 5, 2026 6:50pm | Jul 5, 2026 6:58pm | Jul 5, 2026 6:58pm |  |  | Fair | No | Corroded phase found at pole, remade connection using one 1bolt clamp. Voltage reading 111/113/224
Outage | J.E.26.07.04223 | C001840406 | Kenroy Dale | Manchester | Completed | Load_258296 | Kendal - 310 | Jul 5, 2026 2:59pm | Jul 6, 2026 3:22pm | Jul 6, 2026 3:55pm | Jul 6, 2026 3:55pm | Jul 6, 2026 5:09pm | Jul 6, 2026 5:28pm | Jul 6, 2026 5:29pm | Jul 6, 2026 5:29pm |  |  | Fair | No | Area checked and found with supply customer also confirmed that supply was restored
Non-Outage | J.E.26.06.12133 | C001840403 | Richard Samuda | Manchester | Completed | Load_250211 | Porus - 210 | Jul 5, 2026 2:44pm | Jul 5, 2026 2:44pm | Jul 5, 2026 3:47pm | Jul 5, 2026 3:47pm | Jul 5, 2026 3:48pm | Jul 5, 2026 4:04pm | Jul 5, 2026 4:04pm | Jul 5, 2026 4:04pm |  |  | Fair | No | Change corroded 1bolt clamps on service wire that lead to customer premises that was corroded causing customer to experience hi voltage voltage 117/117/234
Outage | J.E.26.07.04200 | C001840402 | Andre Smith | KSAN | Completed | Load_250584 | Washington Blvd - 710 | Jul 5, 2026 2:20pm | Jul 5, 2026 3:42pm | Jul 5, 2026 5:39pm | Jul 5, 2026 5:39pm | Jul 5, 2026 5:53pm | Jul 5, 2026 5:55pm | Jul 5, 2026 5:55pm | Jul 5, 2026 5:55pm |  |  | Fair | No | Reconnection done in ypp box supply restored
Outage | J.E.26.07.04168 | C001840400 | Clyde Brown | Clarendon | Completed | Load_579438 | May Pen - 110 | Jul 5, 2026 2:09pm | Jul 5, 2026 2:10pm | Jul 5, 2026 2:26pm | Jul 5, 2026 2:26pm | Jul 5, 2026 2:26pm | Jul 5, 2026 2:26pm | Jul 5, 2026 2:30pm | Jul 5, 2026 2:30pm | BangingWires |  | Fair | No | Call need service and I am without service wire
Outage | J.E.26.07.04174 | C001840397 | Marlon Authors | Manchester | Completed | Load_1002339 | Spur Tree - 210 | Jul 5, 2026 1:46pm | Jul 5, 2026 1:48pm | Jul 5, 2026 6:47pm | Jul 5, 2026 6:47pm | Jul 5, 2026 7:44pm | Jul 5, 2026 8:09pm | Jul 5, 2026 8:09pm | Jul 5, 2026 8:09pm |  |  | Fair | No | Patrol and found overgrown vegetation covering the transformer. Cut and remove same and replace one blown 1 amp fuse that protects 25 kva transformer circuit no pole #, Restored supply ok
Outage | J.E.26.07.04159 | C001840395 | Donald Cunningham | St.Catherine | Completed | Load_412895 | New Michelton - 210 | Jul 5, 2026 1:40pm | Jul 5, 2026 1:40pm | Jul 5, 2026 6:38pm | Jul 5, 2026 6:38pm | Jul 5, 2026 6:58pm | Jul 5, 2026 6:58pm | Jul 5, 2026 7:06pm | Jul 5, 2026 7:06pm |  |  | Fair | No | Supply restored
Outage | J.E.26.07.04163 | C001840392 | Christopher Edwards | KSAN | Completed | Load_252388 | Constant Spring - 410 | Jul 5, 2026 1:33pm | Jul 5, 2026 1:35pm | Jul 5, 2026 1:49pm | Jul 5, 2026 1:49pm | Jul 5, 2026 1:49pm | Jul 5, 2026 3:24pm | Jul 5, 2026 3:25pm | Jul 5, 2026 3:25pm |  |  | Fair | No | Premises not located unable to reach customer by phone
Outage | J.E.26.07.04135 | C001840390 | Edward Royal | KSAN | Completed | Load_266896 | Washington Blvd - 510 | Jul 5, 2026 1:19pm | Jul 5, 2026 1:20pm | Jul 5, 2026 3:26pm | Jul 5, 2026 3:26pm | Jul 5, 2026 3:27pm | Jul 5, 2026 3:27pm | Jul 5, 2026 3:27pm | Jul 5, 2026 3:27pm |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.07.04148 | C001840391 | Edward Royal | KSAN | Completed | Load_240328 | Washington Blvd - 510 | Jul 5, 2026 1:19pm | Jul 5, 2026 1:20pm | Jul 5, 2026 3:27pm | Jul 5, 2026 3:27pm | Jul 5, 2026 3:27pm | Jul 5, 2026 3:28pm | Jul 5, 2026 3:29pm | Jul 5, 2026 3:29pm |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.07.04136 | C001840388 | Marlon Authors | St.Elizabeth | Completed | Load_260548 | Maggotty - 110 | Jul 5, 2026 1:06pm | Jul 5, 2026 1:09pm | Jul 5, 2026 8:51pm | Jul 5, 2026 8:51pm | Jul 5, 2026 9:40pm | Jul 5, 2026 10:31pm | Jul 5, 2026 10:32pm | Jul 5, 2026 10:32pm |  |  | Fair | No | Patrol and found clear, further checks revealed that 50 kva transformer is burnt. There were two transformers at this location mounted on a concrete pole banker two which only the 50 kva remains and only supplies one customer. A 25 kva transformer would be best suitable to replace same as banker two supply in no longer required at this time. Please refer same to the maintenance department for replacement
Outage | J.E.26.07.04079 | C001840387 | Tajay Bernard | Hanover | Completed | Load_302650 | Orange Bay - 310 | Jul 5, 2026 12:46pm | Jul 6, 2026 9:47am | Jul 6, 2026 12:52pm | Jul 6, 2026 12:52pm | Jul 6, 2026 1:16pm | Jul 6, 2026 1:39pm | Jul 6, 2026 1:39pm | Jul 6, 2026 1:39pm |  |  | Fair | No | Area check and found okay unable to locate customer on premises multiple phone calls to customer number went unanswered
Outage | J.E.26.07.04104 | C001840386 | Tajay Bernard | Hanover | Completed | Load_244461 | Orange Bay - 310 | Jul 5, 2026 12:46pm | Jul 6, 2026 9:47am | Jul 6, 2026 10:43am | Jul 6, 2026 10:44am | Jul 6, 2026 12:00pm | Jul 6, 2026 12:48pm | Jul 6, 2026 12:52pm | Jul 6, 2026 12:52pm |  |  | Fair | No | Replaced 80ft #6 triplex wire use 2 clamps Voltage found 109Voltage left 111/110/220Cause( customer service wire was defective)
Outage | J.E.26.07.04112 | C001840385 | Ricky Hall | St.Catherine | Completed | Load_259014 | Tredegar - 210 | Jul 5, 2026 12:44pm | Jul 5, 2026 12:45pm | Jul 5, 2026 1:19pm | Jul 5, 2026 1:19pm | Jul 5, 2026 2:07pm | Jul 5, 2026 3:31pm | Jul 5, 2026 3:32pm | Jul 5, 2026 3:32pm |  |  | SevereWind | No | Conduct spot bushing replaced blown 5 amps fuse 50 kva xfmr
Non-Outage | J.E.26.07.04035 | C001840382 | Derrick Dawkins | null | Completed | null | null | Jul 5, 2026 12:41pm | Jul 5, 2026 12:41pm | Jul 5, 2026 2:25pm | Jul 5, 2026 2:25pm | Jul 5, 2026 3:04pm | Jul 5, 2026 3:17pm | Jul 5, 2026 7:53pm | Jul 5, 2026 7:53pm | BrokenWire |  | Fair | No | Check and found ok
Outage | J.E.26.07.03974 | C001840383 | Shamour Haughton | St.James | Completed | Load_302849 | Bogue - 610 | Jul 5, 2026 12:41pm | Jul 5, 2026 12:41pm | Jul 5, 2026 12:56pm | Jul 5, 2026 12:56pm | Jul 5, 2026 12:56pm | Jul 5, 2026 12:57pm | Jul 5, 2026 12:58pm | Jul 5, 2026 12:58pm |  |  | Fair | No | Customer stated that power was restored
Outage | J.E.26.07.04100 | C001840384 | Edward Royal | KSAN | Completed | Load_255761 | Washington Blvd - 510 | Jul 5, 2026 12:41pm | Jul 5, 2026 12:44pm | Jul 5, 2026 1:29pm | Jul 5, 2026 1:29pm | Jul 5, 2026 1:47pm | Jul 5, 2026 3:26pm | Jul 5, 2026 3:26pm | Jul 5, 2026 3:26pm |  |  | Fair | No | Spliced and reconnected primary jumper using 2 single bolt clamp
Outage | J.E.26.07.04110 | C001840381 | Marlon Authors | St.Elizabeth | Completed | Load_255808 | Maggotty - 210 | Jul 5, 2026 12:38pm | Jul 5, 2026 12:43pm | Jul 5, 2026 1:49pm | Jul 5, 2026 1:49pm | Jul 5, 2026 3:12pm | Jul 5, 2026 3:23pm | Jul 5, 2026 3:23pm | Jul 5, 2026 3:23pm |  |  | Fair | No | Supply checked and found corrosion at pole. Repair same using two clamps, supply leave working ok rdg 112v,113v and cross phased 225 volts
Outage | J.E.26.07.04098 | C001840379 | Andre Smith | KSAS | Completed | Load_256919 | Hunts Bay - 510 | Jul 5, 2026 12:35pm | Jul 5, 2026 3:42pm | Jul 5, 2026 5:55pm | Jul 5, 2026 5:55pm | Jul 5, 2026 6:09pm | Jul 5, 2026 6:39pm | Jul 5, 2026 6:39pm | Jul 5, 2026 6:39pm |  |  | Fair | No | Supply restored already
Outage | J.E.26.07.03946 | C001840377 | Nickolas Rodriques | Portmore | Completed | Load_243774 | Naggo Head - 510 | Jul 5, 2026 12:03pm | Jul 5, 2026 12:04pm | Jul 5, 2026 1:12pm | Jul 5, 2026 1:24pm | Jul 5, 2026 2:12pm | Jul 5, 2026 2:51pm | Jul 5, 2026 2:55pm | Jul 5, 2026 2:55pm |  |  | Fair | No | Checked and found customer single phasing (118) caused by broken service wire at pole. Repaired by connecting wire using two clamps, current reading is (120-118-238).
Outage | J.E.26.07.04071 | C001840376 | Edward Royal | KSAS | Completed | Load_254287 | Duhaney - 310 | Jul 5, 2026 11:59am | Jul 5, 2026 12:44pm | Jul 5, 2026 3:47pm | Jul 5, 2026 3:47pm | Jul 5, 2026 3:47pm | Jul 5, 2026 3:48pm | Jul 5, 2026 3:49pm | Jul 5, 2026 3:49pm |  |  | Fair | No | Replaced 10A junction fuse pole #0180512
Outage | J.E.26.07.04073 | C001840375 | Edward Royal | KSAN | Completed | Load_240328 | Washington Blvd - 510 | Jul 5, 2026 11:56am | Jul 5, 2026 11:57am | Jul 5, 2026 12:15pm | Jul 5, 2026 12:15pm | Jul 5, 2026 12:15pm | Jul 5, 2026 12:16pm | Jul 5, 2026 12:16pm | Jul 5, 2026 12:16pm |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.07.03933 | C001840372 | Ricky Hall | St.Catherine | Completed | Load_267985 | Twickenham - 310 | Jul 5, 2026 11:51am | Jul 5, 2026 11:52am | Jul 5, 2026 1:11pm | Jul 5, 2026 1:18pm | Jul 5, 2026 1:18pm | Jul 5, 2026 1:18pm | Jul 5, 2026 1:19pm | Jul 5, 2026 1:19pm |  |  | Fair | No | Call associated with outage #03779
Outage | J.E.26.07.04061 | C001840374 | Ricky Hall | St.Catherine | Completed | Load_264063 | Twickenham - 310 | Jul 5, 2026 11:51am | Jul 5, 2026 11:52am | Jul 5, 2026 3:34pm | Jul 5, 2026 3:48pm | Jul 5, 2026 4:15pm | Jul 5, 2026 4:33pm | Jul 5, 2026 4:33pm | Jul 5, 2026 4:33pm |  |  | Fair | No | Replaced blown 15 amps junction fuse
Outage | J.E.26.07.04060 | C001840371 | Donald Cunningham | St.Catherine | Completed | Load_238144 | New Michelton - 210 | Jul 5, 2026 11:48am | Jul 5, 2026 11:49am | Jul 5, 2026 3:28pm | Jul 5, 2026 3:28pm | Jul 5, 2026 5:52pm | Jul 5, 2026 5:54pm | Jul 5, 2026 5:57pm | Jul 5, 2026 5:57pm |  |  | Fair | No | Blown junction by entrance to rose mount housing scheme replace 10 amp fuse also by end of primary replace 2 amp fuse for 10 kva transformer also by grove road blown junction fuse replace 20 amp fuse
Outage | J.E.26.07.04012 | C001840370 | Hartley Chin | Clarendon | Completed | Load_237768 | Monymusk - 410 | Jul 5, 2026 11:47am | Jul 5, 2026 12:47pm | Jul 5, 2026 2:19pm | Jul 5, 2026 2:20pm | Jul 5, 2026 3:15pm | Jul 5, 2026 4:02pm | Jul 5, 2026 4:05pm | Jul 5, 2026 4:05pm |  |  | Fair | No | Isolate 25 KVA transformer @ pole # 0162866 due to broken open secondary phase found in 1 span … repair broken joint , re-energize transformer… use 2 clamp , 20ft #2 conductor…
Outage | J.E.26.07.03885 | C001840367 | Dwayne Samuels | Trelawny | Completed | Load_1001670 | Greenwood - 210 | Jul 5, 2026 11:45am | Jul 5, 2026 11:46am | Jul 5, 2026 1:21pm | Jul 5, 2026 1:21pm | Jul 5, 2026 3:29pm | Jul 5, 2026 3:32pm | Jul 5, 2026 3:33pm | Jul 5, 2026 3:33pm |  |  | Fair | No | Unable to locate customer no answer from telephone
Outage | J.E.26.07.04041 | C001840368 | Dwayne Samuels | Trelawny | Completed | Load_1001654 | Greenwood - 210 | Jul 5, 2026 11:45am | Jul 5, 2026 11:46am | Jul 5, 2026 12:09pm | Jul 5, 2026 12:09pm | Jul 5, 2026 12:33pm | Jul 5, 2026 1:08pm | Jul 5, 2026 1:09pm | Jul 5, 2026 1:09pm |  |  | Fair | No | Patrol to find 1 blown 30amp pad mounted transformer fuse replace 1 30amp fuse at same and close no pole number
Non-Outage | J.E.26.07.04058 | C001840363 | Edward Royal | null | Completed | null | null | Jul 5, 2026 11:31am | Jul 5, 2026 11:34am | Jul 5, 2026 12:16pm | Jul 5, 2026 12:16pm | Jul 5, 2026 12:16pm | Jul 5, 2026 12:20pm | Jul 5, 2026 12:20pm | Jul 5, 2026 12:20pm |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.07.03912 | C001840362 | Nickolas Rodriques | Portmore | Completed | Load_252837 | Naggo Head - 510 | Jul 5, 2026 11:16am | Jul 5, 2026 2:38pm | Jul 5, 2026 2:55pm | Jul 5, 2026 2:55pm | Jul 5, 2026 3:10pm | Jul 5, 2026 3:33pm | Jul 5, 2026 3:36pm | Jul 5, 2026 3:36pm |  |  | Fair | No | Checked and found customer single phasing (118) caused by broken service wire at pole. Repaired by connecting wire using two clamps, current reading is (120-118-238).
Outage | J.E.26.07.04002 | C001840359 | Andre Smith | KSAS | Completed | Load_268761 | Rockfort - 410 | Jul 5, 2026 10:46am | Jul 5, 2026 3:41pm | Jul 5, 2026 6:39pm | Jul 5, 2026 6:39pm | Jul 5, 2026 6:50pm | Jul 5, 2026 7:20pm | Jul 5, 2026 7:20pm | Jul 5, 2026 7:20pm |  |  | Fair | No | Replace blown junction fuses 25A/2 supply restored cause by truck making contact with conductor supply restored
Non-Outage | J.E.26.07.01995 | C001840355 | Marlon Authors | null | Completed | null | null | Jul 5, 2026 10:40am | Jul 5, 2026 10:41am | Jul 5, 2026 11:26am | Jul 5, 2026 11:26am | Jul 5, 2026 11:27am | Jul 5, 2026 11:36am | Jul 5, 2026 11:36am | Jul 5, 2026 11:36am | LowHangingWires |  | Fair | No | Supply checked and found customers meter pole leaning that cause the service wire to hang low. Customer needs to have same repair, no one seen at the time of visit
Non-Outage | J.E.26.07.02876 | C001840357 | Marlon Authors | Manchester | Completed | Load_302733 | Spur Tree - 210 | Jul 5, 2026 10:40am | Jul 5, 2026 10:41am | Jul 5, 2026 3:31pm | Jul 5, 2026 3:32pm | Jul 5, 2026 4:29pm | Jul 5, 2026 4:30pm | Jul 5, 2026 4:31pm | Jul 5, 2026 4:31pm |  |  | Fair | No | Unable to check supply, meter room locked
Outage | J.E.26.07.04020 | C001840356 | Edward Royal | KSAN | Completed | Load_266896 | Washington Blvd - 510 | Jul 5, 2026 10:40am | Jul 5, 2026 10:41am | Jul 5, 2026 11:58am | Jul 5, 2026 11:58am | Jul 5, 2026 11:58am | Jul 5, 2026 11:59am | Jul 5, 2026 11:59am | Jul 5, 2026 11:59am |  |  | Fair | No | Premises found ok related to outage
Non-Outage | J.E.26.07.04024 | C001840354 | Donald Cunningham | St.Catherine | Completed | Load_245596 | Tredegar - 410 | Jul 5, 2026 10:37am | Jul 5, 2026 10:39am | Jul 5, 2026 3:21pm | Jul 5, 2026 3:21pm | Jul 5, 2026 3:21pm | Jul 5, 2026 3:21pm | Jul 5, 2026 3:26pm | Jul 5, 2026 3:26pm | LeakingTransformer |  | Fair | No | Defective rami transformer leaking oil urgent attention required Feardene meadow buck town
Outage | J.E.26.07.03888 | C001840353 | Nickolas Rodriques | Portmore | Completed | Load_300748 | Naggo Head - 610 | Jul 5, 2026 10:37am | Jul 5, 2026 10:37am | Jul 5, 2026 10:47am | Jul 5, 2026 10:51am | Jul 5, 2026 10:56am | Jul 5, 2026 11:02am | Jul 5, 2026 11:08am | Jul 5, 2026 11:08am |  |  | Fair | No | Power restored. Call relates to the 30 amp junction fuse that was replaced.
Outage | J.E.26.07.03959 | C001840352 | Nickolas Rodriques | Portmore | Completed | Load_261057 | Naggo Head - 610 | Jul 5, 2026 10:37am | Jul 5, 2026 10:37am | Jul 5, 2026 11:09am | Jul 5, 2026 11:09am | Jul 5, 2026 11:28am | Jul 5, 2026 11:52am | Jul 5, 2026 12:10pm | Jul 5, 2026 12:10pm | Fire |  | Fair | No | Checked and found a 10 amp junction fuse blown. Patrol and found nothing on line. Repaired by replacing the fuse after numerous patrols.
Outage | J.E.26.07.03964 | C001840351 | Derrick Dawkins | St.James | Completed | Load_268331 | Queens Drive - 710 | Jul 5, 2026 10:33am | Jul 5, 2026 10:33am | Jul 5, 2026 2:17pm | Jul 5, 2026 2:17pm | Jul 5, 2026 2:17pm | Jul 28, 2026 2:20am | Jul 5, 2026 2:25pm | Jul 5, 2026 2:25pm | BrokenWire |  | Fair | No | Check and found area okay customer states that she did not make any report
Outage | J.E.26.07.04015 | C001840349 | Shamour Haughton | St.James | Completed | Load_257529 | Bogue - 610 | Jul 5, 2026 10:33am | Jul 5, 2026 10:33am | Jul 5, 2026 10:45am | Jul 5, 2026 10:45am | Jul 5, 2026 12:12pm | Jul 5, 2026 12:12pm | Jul 5, 2026 12:16pm | Jul 5, 2026 12:16pm |  |  | Fair | No | Found 1,25kva fuse blown, refuse 25kva use 1,3amp
Outage | J.E.26.07.04016 | C001840350 | Derrick Dawkins | St.James | Completed | Load_244546 | Bogue - 310 | Jul 5, 2026 10:33am | Jul 5, 2026 10:33am | Jul 5, 2026 12:18pm | Jul 5, 2026 12:18pm | Jul 5, 2026 12:31pm | Aug 3, 2026 12:05am | Jul 5, 2026 2:17pm | Jul 5, 2026 2:17pm |  |  | Fair | No | Call related to previous
Outage | J.E.26.07.03986 | C001840348 | Edward Royal | KSAN | Completed | Load_255761 | Washington Blvd - 510 | Jul 5, 2026 10:32am | Jul 5, 2026 10:40am | Jul 5, 2026 10:55am | Jul 5, 2026 10:55am | Jul 5, 2026 11:31am | Jul 5, 2026 11:43am | Jul 5, 2026 11:43am | Jul 5, 2026 11:43am |  |  | Fair | No | Replaced 30A junction fuse pole #007505
Outage | J.E.26.07.03995 | C001840347 | Edward Royal | KSAN | Completed | Load_240328 | Washington Blvd - 510 | Jul 5, 2026 10:32am | Jul 5, 2026 10:40am | Jul 5, 2026 12:13pm | Jul 5, 2026 12:13pm | Jul 5, 2026 12:14pm | Jul 5, 2026 12:15pm | Jul 5, 2026 12:15pm | Jul 5, 2026 12:15pm |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.07.04014 | C001840346 | Raymond Lewis | St.Ann | Completed | Load_264624 | Ocho Rios - 310 | Jul 5, 2026 10:26am | Jul 5, 2026 10:27am | Jul 5, 2026 11:01am | Jul 5, 2026 11:01am | Jul 5, 2026 11:11am | Jul 5, 2026 11:13am | Jul 5, 2026 11:13am | Jul 5, 2026 11:13am |  |  | Fair | No | Premises not found and phone not available
Non-Outage | J.E.26.07.03612 | C001840344 | Oraine Minto | St.Ann | Completed | Load_265457 | Cardiff Hall - 210 | Jul 5, 2026 10:13am | Jul 6, 2026 8:19am | Jul 6, 2026 10:58am | Jul 6, 2026 10:58am | Jul 6, 2026 11:18am | Jul 6, 2026 11:18am | Jul 6, 2026 11:20am | Jul 6, 2026 11:20am |  |  | Fair | No | Unable to reach customer via contact number in the area and not seeing any damage pole
Outage | J.E.26.07.03960 | C001840343 | Clyde Brown | Clarendon | Completed | Load_268304 | May Pen - 110 | Jul 5, 2026 10:08am | Jul 5, 2026 10:09am | Jul 5, 2026 10:19am | Jul 5, 2026 10:19am | Jul 5, 2026 11:29am | Jul 5, 2026 12:15pm | Jul 5, 2026 12:25pm | Jul 5, 2026 12:25pm |  |  | Fair | No | Blown 3 amps fuse for 25kva transformer caused by secondary phase and neutral entangled,line cleared and blown fuse replaced.
Outage | J.E.26.07.03789 | C001840342 | Hartley Chin | Clarendon | Completed | Load_247003 | May Pen - 210 | Jul 5, 2026 10:07am | Jul 5, 2026 10:08am | Jul 5, 2026 10:21am | Jul 5, 2026 11:12am | Jul 5, 2026 11:36am | Jul 5, 2026 1:25pm | Jul 5, 2026 1:27pm | Jul 5, 2026 1:27pm |  |  | Fair | No | Found customer single phasing … voltage read 112v … line patrolled and Found burnt #2 twisted due to overgrown mango tree … cut tree from line … dismount twisted… repaired #2 twisted… voltage read 112v , 110v .. use 6 clamp …
Outage | J.E.26.07.03973 | C001840340 | Richard Samuda | Manchester | Completed | Load_293145 | Spur Tree - 310 | Jul 5, 2026 9:35am | Jul 5, 2026 9:39am | Jul 5, 2026 10:43am | Jul 5, 2026 11:50am | Jul 5, 2026 12:16pm | Jul 5, 2026 12:56pm | Jul 5, 2026 12:55pm | Jul 5, 2026 12:55pm | BrokenWire |  | Fair | No | Reconnect customer service wire to existing line that was broken off customer back to normal voltage 114\116/230
Outage | J.E.26.07.03968 | C001840339 | Marlon Authors | Manchester | Completed | Load_240445 | Spur Tree - 210 | Jul 5, 2026 9:34am | Jul 5, 2026 9:39am | Jul 5, 2026 12:45pm | Jul 5, 2026 12:45pm | Jul 5, 2026 12:58pm | Jul 5, 2026 1:26pm | Jul 5, 2026 1:26pm | Jul 5, 2026 1:26pm | BrokenPole |  | Fair | No | Patrol and found one 40 feet TA wooden over head guy load bearing pole and the transformer resting on the upper phase secondary conductor, approximately 30 customers are without supply. Please refer same to the maintenance department for replacement
Outage | J.E.26.07.03963 | C001840338 | Richard Samuda | Manchester | Completed | Load_246581 | Spur Tree - 310 | Jul 5, 2026 9:20am | Jul 5, 2026 9:21am | Jul 5, 2026 9:39am | Jul 5, 2026 10:07am | Jul 5, 2026 10:08am | Jul 5, 2026 10:38am | Jul 5, 2026 10:39am | Jul 5, 2026 10:39am | BrokenWire |  | Fair | No | Remake secondary neutral jumper that was broken causing to experience unstable voltage 116/118/234 customer back to normal
Non-Outage | J.E.26.07.03744 | C001840337 | Milton Charlton | null | Completed | null | null | Jul 5, 2026 9:10am | Jul 5, 2026 9:11am | Jul 5, 2026 9:49am | Jul 5, 2026 12:12pm | Jul 5, 2026 12:12pm | Jul 5, 2026 12:15pm | Jul 5, 2026 12:17pm | Jul 5, 2026 12:17pm |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.07.03798 | C001840335 | Fitzroy Turner | KSAS | Completed | Load_288528 | Hunts Bay - 810 | Jul 5, 2026 9:09am | Jul 5, 2026 9:11am | Jul 5, 2026 10:20am | Jul 5, 2026 10:40am | Jul 5, 2026 11:49am | Jul 5, 2026 11:49am | Jul 5, 2026 11:52am | Jul 5, 2026 11:52am |  |  | Fair | No | Customer referring to broken pole tied up close to her gate with 4 service wire
Outage | J.E.26.07.03804 | C001840334 | Fitzroy Turner | KSAS | Completed | Load_243805 | Greenwich - 710 | Jul 5, 2026 9:09am | Jul 5, 2026 9:11am | Jul 5, 2026 10:20am | Jul 5, 2026 11:52am | Jul 5, 2026 11:52am | Jul 5, 2026 12:15pm | Jul 5, 2026 12:19pm | Jul 5, 2026 12:19pm |  |  | Fair | No | Broken 35/6 wooden pole with service wire pole already tie up customer concerns about pole
Outage | J.E.26.07.03873 | C001840333 | Fitzroy Turner | KSAN | Completed | Load_261386 | Washington Blvd - 710 | Jul 5, 2026 9:09am | Jul 5, 2026 9:11am | Jul 5, 2026 10:20am | Jul 5, 2026 10:38am | Jul 5, 2026 10:39am | Jul 5, 2026 10:39am | Jul 5, 2026 10:40am | Jul 5, 2026 10:40am |  |  | Fair | No | Customer supply restored after replace blown fuse at tower avenue
Non-Outage | J.E.26.07.03958 | C001840330 | Kenroy Dale | null | Completed | null | null | Jul 5, 2026 9:08am | Jul 5, 2026 9:23am | Jul 5, 2026 10:14am | Jul 5, 2026 10:14am | Jul 5, 2026 10:15am | Jul 5, 2026 10:15am | Jul 5, 2026 10:15am | Jul 5, 2026 10:15am |  |  | Fair | No | Call related to theft of underground cables
Outage | J.E.26.07.03954 | C001840332 | Fitzroy Turner | KSAN | Completed | Load_264813 | Washington Blvd - 710 | Jul 5, 2026 9:08am | Jul 5, 2026 9:11am | Jul 5, 2026 10:20am | Jul 5, 2026 12:19pm | Jul 5, 2026 1:55pm | Jul 5, 2026 1:56pm | Jul 5, 2026 1:56pm | Jul 5, 2026 1:56pm |  |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.07.03955 | C001840331 | Fitzroy Turner | KSAN | Completed | Load_1002625 | Washington Blvd - 710 | Jul 5, 2026 9:08am | Jul 5, 2026 9:11am | Jul 5, 2026 9:30am | Jul 5, 2026 9:30am | Jul 5, 2026 10:19am | Jul 5, 2026 10:35am | Jul 5, 2026 10:38am | Jul 5, 2026 10:38am |  |  | EarthMovement | No | Found 10 amp junction fuse blown at the intersection of tower avenue and AlaAmanda Avenue replaced with same 10 amps fuse supply restored to areas
Outage | J.E.26.07.03926 | C001840329 | Rusean Allen | KSAS | Completed | Load_256911 | Hunts Bay - 510 | Jul 5, 2026 9:07am | Jul 5, 2026 9:08am | Jul 5, 2026 9:25am | Jul 5, 2026 9:26am | Jul 5, 2026 11:08am | Jul 5, 2026 11:11am | Jul 5, 2026 11:11am | Jul 5, 2026 11:11am |  |  | Fair | No | Defective 100KVA transformer needs to be changed.Refer to the maintenance department.
Outage | J.E.26.07.03780 | C001840326 | Rusean Allen | KSAS | Completed | Load_243128 | Rockfort - 210 | Jul 5, 2026 9:06am | Jul 6, 2026 10:04am | Jul 6, 2026 11:15am | Jul 6, 2026 11:15am | Jul 6, 2026 11:27am | Jul 6, 2026 11:28am | Jul 6, 2026 11:29am | Jul 6, 2026 11:29am |  |  | Fair | No | Found okay
Outage | J.E.26.07.03807 | C001840327 | Rusean Allen | KSAS | Completed | Load_266609 | Cane River - 310 | Jul 5, 2026 9:06am | Jul 5, 2026 9:08am | Jul 5, 2026 12:21pm | Jul 5, 2026 12:27pm | Jul 5, 2026 12:34pm | Jul 5, 2026 12:34pm | Jul 5, 2026 12:34pm | Jul 5, 2026 12:34pm |  |  | Fair | No | Internal problems, customer was advised to contact electrician.
Outage | J.E.26.07.03927 | C001840328 | Rusean Allen | KSAS | Completed | Load_269099 | Cane River - 310 | Jul 5, 2026 9:06am | Jul 5, 2026 9:08am | Jul 5, 2026 12:17pm | Jul 5, 2026 12:17pm | Jul 5, 2026 12:25pm | Jul 5, 2026 12:25pm | Jul 5, 2026 12:25pm | Jul 5, 2026 12:25pm |  |  | Fair | No | Premises okay
Outage | J.E.26.07.03635 | C001840324 | Milton Charlton | KSAN | Completed | Load_238415 | Constant Spring - 410 | Jul 5, 2026 9:01am | Jul 5, 2026 9:02am | Jul 5, 2026 9:07am | Jul 5, 2026 10:49am | Jul 5, 2026 12:10pm | Jul 5, 2026 12:05pm | Jul 5, 2026 12:12pm | Jul 5, 2026 12:12pm |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.07.03641 | C001840323 | Milton Charlton | KSAN | Completed | Load_251266 | Constant Spring - 410 | Jul 5, 2026 8:59am | Jul 5, 2026 9:00am | Jul 5, 2026 9:54am | Jul 5, 2026 9:54am | Jul 5, 2026 10:39am | Jul 5, 2026 10:10am | Jul 5, 2026 10:41am | Jul 5, 2026 10:41am |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.07.03639 | C001840322 | Milton Charlton | KSAN | Completed | Load_568471 | Hope - 510 | Jul 5, 2026 8:58am | Jul 5, 2026 11:37am | Jul 5, 2026 12:17pm | Jul 5, 2026 12:17pm | Jul 5, 2026 12:34pm | Jul 5, 2026 12:40pm | Jul 5, 2026 12:40pm | Jul 5, 2026 12:40pm |  |  | Fair | No | 35ft wooden pole broken from hurricane Melissa and line section was isolated by maintenance crew and power was restored to other sections of line but nothing was ever done to the isolated section of the line feeding Valerie McNeil farm. Customer need power to be restored.Refer to maintenance.
Outage | J.E.26.07.03810 | C001840321 | Milton Charlton | KSAN | Completed | Load_266843 | Hope - 410 | Jul 5, 2026 8:57am | Jul 5, 2026 9:00am | Jul 5, 2026 10:44am | Jul 5, 2026 10:45am | Jul 5, 2026 10:47am | Jul 5, 2026 10:50am | Jul 5, 2026 10:49am | Jul 5, 2026 10:49am |  |  | Fair | No | Reconnect customer meter #2325618 by J.P.S. Escalation.
Outage | J.E.26.07.03800 | C001840319 | Kenroy Dale | Manchester | Completed | Load_265578 | Kendal - 210 | Jul 5, 2026 8:56am | Jul 5, 2026 8:57am | Jul 5, 2026 1:51pm | Jul 5, 2026 1:51pm | Jul 5, 2026 1:51pm | Jul 5, 2026 1:52pm | Jul 5, 2026 1:53pm | Jul 5, 2026 1:53pm |  |  | Fair | No | Call related to earlier outages
Outage | J.E.26.07.03801 | C001840320 | Kenroy Dale | Manchester | Completed | Load_252315 | Kendal - 210 | Jul 5, 2026 8:56am | Jul 5, 2026 8:57am | Jul 5, 2026 10:15am | Jul 5, 2026 10:16am | Jul 5, 2026 1:04pm | Jul 5, 2026 1:48pm | Jul 5, 2026 1:51pm | Jul 5, 2026 1:51pm |  |  | Fair | No | Blown 3 amp fuse found for 25 kva transformer line patrol nothing found blown fuse was replaced and area now with supply
Outage | J.E.26.07.03951 | C001840318 | Edward Royal | KSAS | Completed | null | null | Jul 5, 2026 8:49am | Jul 5, 2026 8:51am | Jul 5, 2026 9:46am | Jul 5, 2026 9:46am | Jul 5, 2026 9:46am | Jul 5, 2026 9:53am | Jul 5, 2026 9:53am | Jul 5, 2026 9:53am |  |  | Fair | No | On hughenden on ave and Molynes road intersection replaced 40A junction fuse that supply marverly pole# 007774
Outage | J.E.26.07.03937 | C001840316 | Derrick Dawkins | St.James | Completed | Load_247062 | Bogue - 310 | Jul 5, 2026 8:35am | Jul 5, 2026 8:36am | Jul 5, 2026 11:07am | Jul 5, 2026 11:07am | Jul 5, 2026 11:07am | Aug 3, 2026 10:36am | Jul 5, 2026 11:12am | Jul 5, 2026 11:12am |  |  | Fair | No | Found 1,10 kva transformer fuse blown caused by birds replace 1.5 fuse in 10 kva transformer no pole number available
Outage | J.E.26.07.02906 | C001840315 | Elvis Trowers | KSAN | Completed | Load_579095 | Constant Spring - 210 | Jul 5, 2026 8:29am | Jul 5, 2026 8:29am | Jul 5, 2026 11:29am | Jul 5, 2026 11:29am | Jul 5, 2026 12:59pm | Jul 5, 2026 1:05pm | Jul 5, 2026 1:05pm | Jul 5, 2026 1:05pm |  |  | Fair | Yes | Premises checked and found ok upon arrival,GNOC was also contacted to make checks.
Outage | J.E.26.07.03122 | C001840314 | Elvis Trowers | KSAN | Completed | Load_248397 | Constant Spring - 210 | Jul 5, 2026 8:28am | Jul 5, 2026 8:29am | Jul 5, 2026 9:00am | Jul 5, 2026 9:00am | Jul 5, 2026 10:19am | Jul 5, 2026 10:22am | Jul 5, 2026 10:22am | Jul 5, 2026 10:22am |  |  | Fair | Yes | Checked and found ok,happened to be internal and an electrician was there getting the problem resolved.
Outage | J.E.26.07.03596 | C001840313 | Elvis Trowers | KSAN | Completed | Load_240204 | Constant Spring - 210 | Jul 5, 2026 8:28am | Jul 5, 2026 8:29am | Jul 5, 2026 1:08pm | Jul 5, 2026 1:08pm | Jul 5, 2026 2:43pm | Jul 5, 2026 3:07pm | Jul 5, 2026 3:07pm | Jul 5, 2026 3:07pm |  |  | Fair | Yes | Premises checked and found ok.
Outage | J.E.26.07.03932 | C001840312 | Kenroy Dale | Manchester | Completed | Load_263096 | Porus - 310 | Jul 5, 2026 8:23am | Jul 5, 2026 8:24am | Jul 5, 2026 9:12am | Jul 5, 2026 9:12am | Jul 5, 2026 9:53am | Jul 5, 2026 10:13am | Jul 5, 2026 10:14am | Jul 5, 2026 10:14am |  |  | Fair | No | Sets of knife switch found open and underground cables found cut due to attempted theft. Operations was made aware of the situation
Outage | J.E.26.07.03896 | C001840311 | Romaine Roberts | St.Mary | Completed | Load_252639 | Oracabessa - 110 | Jul 5, 2026 8:22am | Jul 5, 2026 8:25am | Jul 5, 2026 9:24am | Jul 5, 2026 9:24am | Jul 5, 2026 10:33am | Jul 5, 2026 11:26am | Jul 5, 2026 11:32am | Jul 5, 2026 11:32am |  |  | Fair | No | Bird nest make contact with secondary switch bottom and blow transformer fuse clear line and replace 5 amp at 50 kva transformer power restore
Outage | J.E.26.07.02852 | C001840305 | Nickolas Rodriques | Portmore | Completed | Load_576149 | Naggo Head - 610 | Jul 5, 2026 8:12am | Jul 5, 2026 3:46pm | Jul 5, 2026 5:58pm | Jul 5, 2026 5:58pm | Jul 5, 2026 6:59pm | Jul 5, 2026 7:00pm | Jul 5, 2026 7:02pm | Jul 5, 2026 7:02pm |  |  | Fair | No | Checked and found customer single phasing (118) caused by broken service wire at pothead. Repaired by connecting wire using one service sleeve, current reading is (118-118-236). Customer confirmed that all is well now.
Outage | J.E.26.07.02874 | C001840307 | Delano Gayle | Portmore | Completed | Load_260088 | Naggo Head - 510 | Jul 5, 2026 8:12am | Jul 5, 2026 8:12am | Jul 5, 2026 11:16am | Jul 5, 2026 11:16am | Jul 5, 2026 11:27am | Jul 5, 2026 11:29am | Jul 5, 2026 11:30am | Jul 5, 2026 11:30am |  |  | Fair | No | Premises found okay advised customer
Outage | J.E.26.07.02956 | C001840308 | Nickolas Rodriques | Portmore | Completed | Load_239358 | Naggo Head - 510 | Jul 5, 2026 8:12am | Jul 5, 2026 3:45pm | Jul 5, 2026 8:11pm | Jul 5, 2026 8:12pm | Jul 5, 2026 9:29pm | Jul 5, 2026 9:42pm | Jul 5, 2026 9:43pm | Jul 5, 2026 9:43pm |  |  | Fair | No | Unable to communicate with the customer after several attempts. However, the area was patrolled and no noticeable outage was found.
Outage | J.E.26.07.03107 | C001840310 | Delano Gayle | St.Catherine | Completed | Load_259718 | Twickenham - 210 | Jul 5, 2026 8:12am | Jul 5, 2026 8:12am | Jul 5, 2026 11:30am | Jul 5, 2026 11:30am | Jul 5, 2026 11:45am | Jul 5, 2026 12:00pm | Jul 5, 2026 12:01pm | Jul 5, 2026 12:01pm |  |  | Fair | No | Premises found okay power was restored
Outage | J.E.26.07.03726 | C001840309 | Delano Gayle | St.Catherine | Completed | Load_264582 | Twickenham - 210 | Jul 5, 2026 8:12am | Jul 5, 2026 8:12am | Jul 5, 2026 10:10am | Jul 5, 2026 10:10am | Jul 5, 2026 11:09am | Jul 5, 2026 11:14am | Jul 5, 2026 11:14am | Jul 5, 2026 11:14am |  |  | Fair | No | Premises not found no answer from customer phone, area patrolled and found okay
Outage | J.E.26.07.03854 | C001840304 | Nickolas Rodriques | Portmore | Completed | Load_247634 | Naggo Head - 610 | Jul 5, 2026 8:11am | Jul 5, 2026 8:11am | Jul 5, 2026 12:10pm | Jul 5, 2026 12:10pm | Jul 5, 2026 12:40pm | Jul 5, 2026 1:09pm | Jul 5, 2026 1:10pm | Jul 5, 2026 1:10pm |  |  | Fair | No | Customer was located and confirmed that the power outage was resolved.
Outage | J.E.26.07.03877 | C001840303 | Nickolas Rodriques | Portmore | Completed | Load_244738 | Naggo Head - 610 | Jul 5, 2026 8:11am | Jul 5, 2026 8:11am | Jul 5, 2026 10:20am | Jul 5, 2026 10:26am | Jul 5, 2026 10:35am | Jul 5, 2026 10:46am | Jul 5, 2026 10:47am | Jul 5, 2026 10:47am |  |  | Fair | No | Power restored. Call relates to the 30 amp junction fuse that was replaced.
Outage | J.E.26.07.03875 | C001840302 | Nickolas Rodriques | Portmore | Completed | Load_576084 | Naggo Head - 610 | Jul 5, 2026 8:10am | Jul 5, 2026 8:11am | Jul 5, 2026 8:22am | Jul 5, 2026 8:27am | Jul 5, 2026 9:19am | Jul 5, 2026 10:12am | Jul 5, 2026 10:17am | Jul 5, 2026 10:17am |  |  | Fair | No | Checked and found a 30 amp junction fuse blown due to a 25KVA transformer that was found defective by the midnight team and isolated. Repaired by replacing the fuse after numerous patrols.
Outage | J.E.26.07.03779 | C001840301 | Ricky Hall | St.Catherine | Completed | Load_239948 | Twickenham - 410 | Jul 5, 2026 8:09am | Jul 5, 2026 8:09am | Jul 5, 2026 11:03am | Jul 5, 2026 11:03am | Jul 5, 2026 12:25pm | Jul 5, 2026 1:17pm | Jul 5, 2026 1:18pm | Jul 5, 2026 1:18pm |  |  | SevereWind | No | Replaced blown 20 amps junction fuse
Outage | J.E.26.07.03850 | C001840300 | Ricky Hall | St.Catherine | Completed | Load_259014 | Tredegar - 210 | Jul 5, 2026 8:09am | Jul 5, 2026 8:09am | Jul 5, 2026 9:10am | Jul 5, 2026 10:18am | Jul 5, 2026 11:00am | Jul 5, 2026 11:02am | Jul 5, 2026 11:02am | Jul 5, 2026 11:02am |  |  | Fair | No | Premises not located
Outage | J.E.26.07.03871 | C001840299 | Edward Royal | St.Catherine | Completed | Load_267853 | Twickenham - 310 | Jul 5, 2026 8:09am | Jul 6, 2026 3:54pm | Jul 6, 2026 4:47pm | Jul 6, 2026 4:47pm | Jul 6, 2026 5:03pm | Jul 6, 2026 5:04pm | Jul 6, 2026 5:04pm | Jul 6, 2026 5:04pm |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.07.02790 | C001840298 | Donald Cunningham | St.Catherine | Completed | Load_268424 | New Michelton - 310 | Jul 5, 2026 8:08am | Jul 5, 2026 11:50am | Jul 5, 2026 7:07pm | Jul 5, 2026 7:07pm | Jul 5, 2026 8:04pm | Jul 5, 2026 8:07pm | Jul 5, 2026 8:25pm | Jul 5, 2026 8:25pm |  |  | Fair | No | Reconnect 3 wire service after pole change 2 clamps use voltage readings 119/2/239
Outage | J.E.26.07.03710 | C001840293 | Donald Cunningham | St.Catherine | Completed | Load_568213 | New Michelton - 210 | Jul 5, 2026 8:08am | Jul 5, 2026 8:08am | Jul 5, 2026 10:03am | Jul 5, 2026 10:03am | Jul 5, 2026 11:39am | Jul 5, 2026 11:51am | Jul 5, 2026 11:52am | Jul 5, 2026 11:52am |  |  | Fair | No | Rami system box need to check
Outage | J.E.26.07.03914 | C001840292 | Donald Cunningham | St.Catherine | Completed | Load_266640 | New Michelton - 210 | Jul 5, 2026 8:08am | Jul 5, 2026 8:08am | Jul 5, 2026 11:54am | Jul 5, 2026 11:54am | Jul 5, 2026 12:51pm | Jul 5, 2026 3:17pm | Jul 5, 2026 3:17pm | Jul 5, 2026 3:17pm |  |  | Fair | No | Broken secondary neural splice and retention using 4 feet of #2 aa 4 clamps 1 #2 preform for repair also replace blown junction fuse with 7 amp and 2 amp by 10 kva transformer rain in area
Outage | J.E.26.07.03841 | C001840290 | Stephen Taylor | St.Thomas | Completed | Load_256242 | Lysson - 410 | Jul 5, 2026 8:02am | Jul 5, 2026 8:15am | Jul 5, 2026 10:08am | Jul 5, 2026 10:08am | Jul 5, 2026 12:36pm | Jul 5, 2026 12:37pm | Jul 5, 2026 12:38pm | Jul 5, 2026 12:38pm |  |  | Fair | No | Failed to locate customer needs more information several calls and no one answering the phone
Outage | J.E.26.07.03925 | C001840291 | Stephen Taylor | St.Thomas | Completed | Load_250741 | Lysson - 410 | Jul 5, 2026 8:02am | Jul 5, 2026 8:15am | Jul 5, 2026 10:06am | Jul 5, 2026 10:06am | Jul 5, 2026 10:06am | Jul 5, 2026 10:06am | Jul 5, 2026 10:08am | Jul 5, 2026 10:08am | Fire |  | Fair | No | Patrol clear dead bird from line and close up 25 kva transformer safely all customer is now okay
Non-Outage | J.E.26.07.03734 | C001840288 | Richard Samuda | null | Completed | null | null | Jul 5, 2026 7:59am | Jul 5, 2026 8:00am | Jul 5, 2026 8:19am | Jul 5, 2026 8:19am | Jul 5, 2026 8:22am | Jul 5, 2026 8:22am | Jul 5, 2026 8:23am | Jul 5, 2026 8:23am |  |  | Fair | No | Customer say she’s back to normal
Non-Outage | J.E.26.07.03766 | C001840289 | Richard Samuda | null | Completed | null | null | Jul 5, 2026 7:59am | Jul 5, 2026 8:00am | Jul 5, 2026 8:16am | Jul 5, 2026 8:16am | Jul 5, 2026 8:16am | Jul 5, 2026 8:16am | Jul 5, 2026 8:18am | Jul 5, 2026 8:18am |  |  | EarthMovement | No | Found ok
Outage | J.E.26.07.03279 | C001840287 | Christopher Edwards | KSAN | Completed | Load_262628 | Constant Spring - 410 | Jul 5, 2026 7:58am | Jul 5, 2026 7:58am | Jul 5, 2026 10:36am | Jul 5, 2026 10:36am | Jul 5, 2026 11:07am | Jul 5, 2026 12:20pm | Jul 5, 2026 12:21pm | Jul 5, 2026 12:21pm | TreeContact |  | Fair | No | Remake burnt open secondary phase jumper joint Using (2) one bolt clamps Voltage:116,115,230v
Outage | J.E.26.07.03812 | C001840286 | Christopher Edwards | KSAN | Completed | Load_237815 | Constant Spring - 410 | Jul 5, 2026 7:57am | Jul 5, 2026 7:58am | Jul 5, 2026 12:21pm | Jul 5, 2026 12:21pm | Jul 5, 2026 12:45pm | Jul 5, 2026 1:07pm | Jul 5, 2026 1:07pm | Jul 5, 2026 1:07pm |  |  | Fair | No | Refuse blown 25 kva transformer Using (1) 2 amps
Outage | J.E.26.07.03928 | C001840284 | Christopher Edwards | KSAN | Completed | Load_238279 | Constant Spring - 410 | Jul 5, 2026 7:57am | Jul 5, 2026 7:58am | Jul 5, 2026 8:32am | Jul 5, 2026 9:02am | Jul 5, 2026 9:43am | Jul 5, 2026 10:30am | Jul 5, 2026 10:36am | Jul 5, 2026 10:36am |  |  | Fair | No | Refuse blown 25 kva transformer Using (1) 2 amps
Outage | J.E.26.07.03555 | C001840283 | Delano Gayle | St.Catherine | Completed | Load_269676 | New Michelton - 310 | Jul 5, 2026 7:52am | Jul 5, 2026 7:52am | Jul 5, 2026 7:55am | Jul 5, 2026 7:55am | Jul 5, 2026 8:59am | Jul 5, 2026 10:04am | Jul 5, 2026 10:04am | Jul 5, 2026 10:04am |  |  | Fair | No | Blown junction on main no pole#, blown junction leading to windover great house, foot patrolled line section and found tree branch touching line, remove branch, found 10amps at junction leading to great house use 7amps, replace 10amps
Outage | J.E.26.07.03811 | C001840282 | Derrick Dawkins | St.James | Completed | Load_244546 | Bogue - 310 | Jul 5, 2026 7:47am | Jul 5, 2026 7:48am | Jul 5, 2026 11:13am | Jul 5, 2026 11:13am | Jul 5, 2026 12:00pm | Aug 4, 2026 12:17am | Jul 5, 2026 12:18pm | Jul 5, 2026 12:18pm |  |  | Fair | No | Found 1,50 kva transformer fuse blown caused by illegal connection removed illegal from secondary line and replaced 4amp in 50 kva transformer voltage found 0.000 voltage left 115/116/232
Outage | J.E.26.07.03910 | C001840281 | Lancelot Brown | Hanover | Completed | Load_245605 | Orange Bay - 210 | Jul 5, 2026 7:46am | Jul 5, 2026 7:46am | Jul 5, 2026 8:16am | Jul 5, 2026 10:29am | Jul 5, 2026 11:49am | Jul 5, 2026 11:50am | Jul 5, 2026 11:50am | Jul 5, 2026 11:50am |  |  | Fair | No | Cannot locate customer no answer from contact number need proper direction
Outage | J.E.26.07.03879 | C001840280 | Lancelot Brown | Hanover | Completed | Load_252500 | Orange Bay - 310 | Jul 5, 2026 7:45am | Jul 5, 2026 7:46am | Jul 5, 2026 8:16am | Jul 5, 2026 8:17am | Jul 5, 2026 9:38am | Jul 5, 2026 10:28am | Jul 5, 2026 10:28am | Jul 5, 2026 10:28am |  |  | Fair | No | Isolate 15amps junction fuse remake burnt off switch to led used five feet #2 copper one pg clamp energise 15amps junction fuse feeder is out as soon as feeder is back supply will restore
Outage | J.E.26.07.03738 | C001840276 | Marlon Authors | Manchester | Completed | Load_569969 | Spur Tree - 210 | Jul 5, 2026 7:44am | Jul 5, 2026 7:44am | Jul 5, 2026 6:36pm | Jul 5, 2026 6:36pm | Jul 5, 2026 6:36pm | Jul 5, 2026 6:38pm | Jul 5, 2026 6:38pm | Jul 5, 2026 6:38pm |  |  | Fair | No | Unable to locate and the customer is saying that the phone # is incorrect
Non-Outage | J.E.26.07.03857 | C001840275 | Fitzroy Turner | KSAS | Completed | Load_256919 | Hunts Bay - 510 | Jul 5, 2026 7:30am | Jul 5, 2026 7:30am | Jul 5, 2026 7:41am | Jul 5, 2026 7:42am | Jul 5, 2026 8:09am | Jul 5, 2026 8:10am | Jul 5, 2026 8:12am | Jul 5, 2026 8:12am |  |  | Fair | No | Have bank off three 167 kva transformer disconnected for customer to carry out repair on there systems
Outage | J.E.26.07.03829 | C001840274 | Delano Gayle | St.Catherine | Completed | Load_259907 | Tredegar - 510 | Jul 5, 2026 5:33am | Jul 5, 2026 5:34am | Jul 5, 2026 5:42am | Jul 5, 2026 5:42am | Jul 5, 2026 6:32am | Jul 5, 2026 6:42am | Jul 5, 2026 6:42am | Jul 5, 2026 6:42am |  |  | Fair | No | Blown 25kva transformer fuse no pole number, patrolled circuit and found okay for closure replace 3amps
Non-Outage | J.E.26.07.03760 | C001840270 | Omar King | null | Completed | null | null | Jul 5, 2026 12:06am | Jul 5, 2026 12:06am | Jul 5, 2026 12:54am | Jul 5, 2026 12:54am | Jul 5, 2026 1:48am | Jul 5, 2026 1:49am | Jul 5, 2026 1:50am | Jul 5, 2026 1:50am |  |  | Fair | No | Found #2 splicing sleeve defective on secondary line as been repaired customer is now with supply
Outage | J.E.26.07.03779 | C001840268 | Delano Gayle | St.Catherine | Completed | Load_239948 | Twickenham - 410 | Jul 4, 2026 11:02pm | Jul 4, 2026 11:02pm | Jul 5, 2026 2:02am | Jul 5, 2026 2:02am | Jul 5, 2026 2:40am | Jul 5, 2026 2:41am | Jul 5, 2026 2:41am | Jul 5, 2026 2:41am |  |  | Fair | No | Daylight attention required
Outage | J.E.26.07.03650 | C001840267 | Delano Gayle | Portmore | Completed | Load_572629 | Naggo Head - 610 | Jul 4, 2026 10:59pm | Jul 4, 2026 11:00pm | Jul 5, 2026 1:10am | Jul 5, 2026 1:10am | Jul 5, 2026 1:51am | Jul 5, 2026 2:01am | Jul 5, 2026 2:01am | Jul 5, 2026 2:01am |  |  | Fair | No | Defective 25kva transformer in bank of 2 transformers 25x10, 25kva transformer top burst open, send call to maintenance, found 10kva transformer open,
Outage | J.E.26.07.03740 | C001840266 | Rusean Allen | KSAN | Completed | Load_257632 | Washington Blvd - 510 | Jul 4, 2026 10:58pm | Jul 4, 2026 10:59pm | Jul 5, 2026 4:19am | Jul 5, 2026 4:20am | Jul 5, 2026 4:32am | Jul 5, 2026 4:33am | Jul 5, 2026 4:33am | Jul 5, 2026 4:33am |  |  | Fair | No | Premises locked
Outage | J.E.26.07.03739 | C001840265 | Rusean Allen | KSAS | Completed | Load_579014 | Duhaney - 310 | Jul 4, 2026 10:57pm | Jul 4, 2026 10:58pm | Jul 5, 2026 4:19am | Jul 5, 2026 4:19am | Jul 5, 2026 4:19am | Jul 5, 2026 4:19am | Jul 5, 2026 4:19am | Jul 5, 2026 4:19am |  |  | Fair | No | Power was already restored
Outage | J.E.26.07.03684 | C001840263 | Rusean Allen | KSAS | Completed | Load_260462 | Duhaney - 310 | Jul 4, 2026 10:55pm | Jul 4, 2026 10:55pm | Jul 4, 2026 11:22pm | Jul 5, 2026 12:16am | Jul 5, 2026 1:48am | Jul 5, 2026 1:48am | Jul 5, 2026 1:49am | Jul 5, 2026 1:49am |  |  | Fair | No | Power was already restored
Outage | J.E.26.07.03725 | C001840262 | Michael Christian | St.James | Completed | Load_249519 | Bogue - 610 | Jul 4, 2026 10:53pm | Jul 4, 2026 10:54pm | Jul 5, 2026 2:58am | Jul 5, 2026 2:58am | Jul 5, 2026 4:06am | Jul 5, 2026 5:15am | Jul 5, 2026 5:15am | Jul 5, 2026 5:15am |  |  | Rains | No | Found 1 30 amp junction at pole # 564500 cause by lightning replace
Outage | J.E.26.07.03785 | C001840261 | Michael Christian | St.James | Completed | Load_245936 | Queens Drive - 710 | Jul 4, 2026 10:52pm | Jul 4, 2026 10:53pm | Jul 4, 2026 11:55pm | Jul 4, 2026 11:55pm | Jul 5, 2026 1:38am | Jul 5, 2026 2:58am | Jul 5, 2026 2:58am | Jul 5, 2026 2:58am |  |  | Fair | No | Found 1 50 kava out cause by broken wire replace 1 5 amp and 20 ft # 2 aa 2 clamps
Outage | J.E.26.07.03773 | C001840255 | Clyde Brown | Clarendon | Completed | Load_260521 | May Pen - 110 | Jul 4, 2026 10:08pm | Jul 4, 2026 10:12pm | Jul 4, 2026 10:21pm | Jul 4, 2026 10:21pm | Jul 4, 2026 10:21pm | Jul 4, 2026 10:25pm | Jul 4, 2026 10:26pm | Jul 4, 2026 10:26pm |  |  | Fair | No | 3amps fuse for 25kva transformer blown caused by defective fuse holder same string fuse temporarily and now ok
Outage | J.E.26.07.03468 | C001840254 | Michael Christian | St.James | Completed | Load_250995 | Bogue - 610 | Jul 4, 2026 10:02pm | Jul 4, 2026 10:44pm | Jul 5, 2026 5:15am | Jul 5, 2026 5:15am | Jul 5, 2026 5:51am | Jul 5, 2026 6:04am | Jul 5, 2026 6:04am | Jul 5, 2026 6:04am |  |  | Fair | No | Found 1 25 kava out cause by cable wire reset voltage 110 113 224 at pothead
Outage | J.E.26.07.03680 | C001840252 | Christopher Edwards | KSAN | Completed | Load_301574 | Constant Spring - 410 | Jul 4, 2026 9:41pm | Jul 4, 2026 9:41pm | Jul 4, 2026 9:50pm | Jul 4, 2026 9:50pm | Jul 4, 2026 9:51pm | Jul 4, 2026 10:34pm | Jul 4, 2026 10:36pm | Jul 4, 2026 10:36pm |  |  | Fair | No | Remake corroded phase joint Using (2) one bolt clamps Voltage:114,115,230v
Outage | J.E.26.07.03752 | C001840251 | Donald Cunningham | Portmore | Completed | Load_576084 | Naggo Head - 610 | Jul 4, 2026 9:37pm | Jul 4, 2026 9:39pm | Jul 4, 2026 10:13pm | Jul 4, 2026 10:13pm | Jul 4, 2026 10:30pm | Jul 4, 2026 10:31pm | Jul 4, 2026 10:31pm | Jul 4, 2026 10:31pm |  |  | Fair | No | Supply restored
Non-Outage | J.E.26.07.03762 | C001840249 | Richman Whyte | null | Completed | null | null | Jul 4, 2026 9:32pm | Jul 4, 2026 9:32pm | Jul 4, 2026 9:43pm | Jul 4, 2026 9:43pm | Jul 5, 2026 1:20am | Jul 5, 2026 1:25am | Jul 5, 2026 1:27am | Jul 5, 2026 1:27am | BrokenWire |  | Fair | No | Repair and retention two span open secondary conductor and replace three amp twenty five kva transformer fuse use three one bolt clamps twenty feet #2 and 15ft 2/0 open aluminum conductor voltage 113 114 228
Outage | J.E.26.07.03683 | C001840247 | Elvis Trowers | KSAS | Completed | Load_264287 | Duhaney - 310 | Jul 4, 2026 9:24pm | Jul 4, 2026 9:26pm | Jul 4, 2026 10:06pm | Jul 4, 2026 10:06pm | Jul 4, 2026 10:26pm | Jul 4, 2026 11:00pm | Jul 4, 2026 11:01pm | Jul 4, 2026 11:01pm |  |  | Fair | Yes | Areas found without electricity supply when checked and a blown 25 amp junction fuse was found and replaced after patrol was completed at pole #0079987.
Outage | J.E.26.07.03712 | C001840244 | Hartley Chin | Clarendon | Completed | Load_247003 | May Pen - 210 | Jul 4, 2026 8:55pm | Jul 5, 2026 10:07am | Jul 5, 2026 10:21am | Jul 5, 2026 1:27pm | Jul 5, 2026 1:27pm | Jul 5, 2026 1:27pm | Jul 5, 2026 1:27pm | Jul 5, 2026 1:27pm |  |  | Fair | No | Call related to job # 03789 …
Outage | J.E.26.07.03701 | C001840242 | Damion Reid | Manchester | Completed | null | null | Jul 4, 2026 8:43pm | Jul 4, 2026 8:44pm | Jul 4, 2026 9:05pm | Jul 4, 2026 9:05pm | Jul 4, 2026 9:05pm | Jul 4, 2026 9:05pm | Jul 4, 2026 9:10pm | Jul 4, 2026 9:10pm | BrokenWire |  | Rains | No | Blown 8amp junction found cause by contamination line patrol and replace blown fuses
Outage | J.E.26.07.03673 | C001840238 | Wayne Dillion | St.Elizabeth | Completed | Load_255742 | Maggotty - 110 | Jul 4, 2026 8:13pm | Jul 4, 2026 8:13pm | Jul 4, 2026 10:30pm | Jul 4, 2026 10:30pm | Jul 4, 2026 10:53pm | Jul 4, 2026 11:05pm | Jul 4, 2026 11:09pm | Jul 4, 2026 11:09pm |  |  | Fair | No | Patrol and found one blown 10amp junction fuse no pole #. Replace same and restored supply okay.
Outage | J.E.26.07.03685 | C001840237 | Wayne Dillion | St.Elizabeth | Completed | Load_265227 | Maggotty - 110 | Jul 4, 2026 8:13pm | Jul 4, 2026 8:13pm | Jul 4, 2026 9:25pm | Jul 4, 2026 9:25pm | Jul 4, 2026 9:25pm | Jul 4, 2026 10:24pm | Jul 4, 2026 10:30pm | Jul 4, 2026 10:30pm |  |  | Fair | No | Patrol and found illegal connection causing one pole span of the secondary neutral and phase to bang. Isolate and close 25kva transformer circuit no pole # to splice and retention same using one #2 preform and 1 clamp. Restored supply okay.
Outage | J.E.26.07.03629 | C001840234 | Romeo Brissett | St.James | Completed | Load_245062 | Bogue - 610 | Jul 4, 2026 8:12pm | Jul 4, 2026 8:24pm | Jul 4, 2026 9:50pm | Jul 4, 2026 9:50pm | Jul 4, 2026 9:50pm | Jul 4, 2026 10:28pm | Jul 4, 2026 10:29pm | Jul 4, 2026 10:29pm |  |  | Fair | No | Cut and removed tree limbs, replaced (1)8amps junction fuse.
Outage | J.E.26.07.03703 | C001840235 | Andrew Powell | Manchester | Completed | Load_256523 | Spur Tree - 210 | Jul 4, 2026 8:12pm | Jul 4, 2026 8:14pm | Jul 4, 2026 8:32pm | Jul 4, 2026 8:32pm | Jul 4, 2026 9:34pm | Jul 4, 2026 9:49pm | Jul 4, 2026 9:52pm | Jul 4, 2026 9:52pm |  |  | Fair | No | Internal fault at customer premises trip breaker, voltage reading 114v-114v phase to neutral 228v cross phase inside meter socket 3 wire.
Outage | J.E.26.07.03715 | C001840236 | Collin Robinson | Portland | Completed | Load_240782 | Port Antonio - 310 | Jul 4, 2026 8:12pm | Jul 4, 2026 8:13pm | Jul 4, 2026 9:02pm | Jul 4, 2026 9:02pm | Jul 4, 2026 9:34pm | Jul 4, 2026 9:42pm | Jul 4, 2026 9:43pm | Jul 4, 2026 9:43pm |  |  | Fair | No | Defective 25KVA transformer found at location leaking oil refer to maintenance
Outage | J.E.26.07.03664 | C001840232 | Richard Samuda | Manchester | Completed | Load_265753 | Spur Tree - 310 | Jul 4, 2026 7:57pm | Jul 5, 2026 8:02am | Jul 5, 2026 3:46pm | Jul 5, 2026 3:46pm | Jul 5, 2026 3:47pm | Jul 5, 2026 3:47pm | Jul 5, 2026 3:47pm | Jul 5, 2026 3:47pm |  |  | Fair | No | Premises not located and call to check no answer
Outage | J.E.26.07.03690 | C001840231 | Clyde Brown | Clarendon | Completed | Load_237834 | Parnassus - 210 | Jul 4, 2026 7:47pm | Jul 4, 2026 7:48pm | Jul 4, 2026 7:58pm | Jul 4, 2026 7:58pm | Jul 4, 2026 10:10pm | Jul 4, 2026 10:12pm | Jul 4, 2026 10:20pm | Jul 4, 2026 10:20pm |  |  | Fair | No | Secondary phase and neutral entangled caused by motor vehicle accident open 25 kva transformer and cleared secondary conductors.
Non-Outage | J.E.26.07.03614 | C001840230 | Marlon Brown | Trelawny | Completed | Load_247153 | Greenwood - 210 | Jul 4, 2026 7:41pm | Jul 4, 2026 7:46pm | Jul 4, 2026 8:12pm | Jul 4, 2026 8:12pm | Jul 4, 2026 9:54pm | Jul 4, 2026 9:55pm | Jul 4, 2026 9:57pm | Jul 4, 2026 9:57pm |  |  | Fair | No | Clean and remake joint at pothead Voltage found 117/117=234vVoltage leaving at pothead 117/117=234v.
Outage | J.E.26.07.03667 | C001840228 | Horace Malcolm | St.James | Completed | Load_1002073 | Bogue - 310 | Jul 4, 2026 7:40pm | Jul 4, 2026 7:40pm | Jul 4, 2026 8:24pm | Jul 4, 2026 8:24pm | Jul 4, 2026 9:50pm | Jul 4, 2026 10:24pm | Jul 4, 2026 10:24pm | Jul 4, 2026 10:24pm |  |  | Fair | No | Refused one 10kva transformer used one 1amp fuse
Outage | J.E.26.07.03656 | C001840227 | Horace Malcolm | St.James | Completed | Load_254250 | Bogue - 310 | Jul 4, 2026 7:37pm | Jul 4, 2026 7:39pm | Jul 4, 2026 10:24pm | Jul 4, 2026 10:24pm | Jul 4, 2026 10:24pm | Jul 4, 2026 10:27pm | Jul 4, 2026 10:27pm | Jul 4, 2026 10:27pm |  |  | Fair | No | Check and found ok related to previous call job number 03667
Outage | J.E.26.07.03679 | C001840225 | Stephen Taylor | St.Thomas | Completed | Load_254225 | Lysson - 410 | Jul 4, 2026 7:36pm | Jul 4, 2026 7:37pm | Jul 4, 2026 8:45pm | Jul 4, 2026 8:45pm | Jul 4, 2026 8:45pm | Jul 4, 2026 8:45pm | Jul 4, 2026 8:47pm | Jul 4, 2026 8:47pm |  |  | Fair | No | Call to customer and customer say that power is back now
Outage | J.E.26.07.03692 | C001840226 | Floyd Taylor | Trelawny | Completed | Load_264256 | Duncans - 210 | Jul 4, 2026 7:36pm | Jul 4, 2026 7:37pm | Jul 4, 2026 9:26pm | Jul 4, 2026 9:26pm | Jul 4, 2026 9:26pm | Jul 4, 2026 9:28pm | Jul 4, 2026 9:28pm | Jul 4, 2026 9:28pm |  |  | Fair | No | Not getting tru to the customer
Non-Outage | J.E.26.07.03671 | C001840224 | Floyd Taylor | null | Completed | null | null | Jul 4, 2026 7:33pm | Jul 4, 2026 7:38pm | Jul 4, 2026 7:52pm | Jul 4, 2026 7:52pm | Jul 4, 2026 8:34pm | Jul 4, 2026 9:12pm | Jul 4, 2026 9:16pm | Jul 4, 2026 9:16pm | BrokenWire |  | Fair | No | Replace 1-3amp damaged fuse .Voltage readings left 114,116,232
Non-Outage | J.E.26.07.03676 | C001840222 | Daniel Francis | null | Completed | null | null | Jul 4, 2026 7:23pm | Jul 5, 2026 8:12am | Jul 5, 2026 8:55am | Jul 5, 2026 9:12am | Jul 5, 2026 9:12am | Jul 5, 2026 9:13am | Jul 5, 2026 9:15am | Jul 5, 2026 9:15am |  |  | Fair | No | Disconnected for nonpayment from may
Outage | J.E.26.07.03665 | C001840221 | Omar King | St.Ann | Completed | Load_572666 | Roaring River - 410 | Jul 4, 2026 7:19pm | Jul 4, 2026 7:20pm | Jul 4, 2026 8:56pm | Jul 4, 2026 8:56pm | Jul 4, 2026 10:04pm | Jul 4, 2026 10:09pm | Jul 4, 2026 10:09pm | Jul 4, 2026 10:09pm |  |  | Fair | No | Unable to find customer call several times no answer
Outage | J.E.26.07.03650 | C001840220 | Donald Cunningham | Portmore | Completed | Load_572623 | Naggo Head - 610 | Jul 4, 2026 7:16pm | Jul 4, 2026 7:17pm | Jul 4, 2026 7:51pm | Jul 4, 2026 7:51pm | Jul 4, 2026 9:19pm | Jul 4, 2026 10:08pm | Jul 4, 2026 10:13pm | Jul 4, 2026 10:13pm |  |  | Fair | No | Blown junction fuse found and replace with 25 amp fuse 1 transformer circuit leave out for a proper assessment of bank of 2 close transformer fuse and it blown back junction fuse
Outage | J.E.26.07.03497 | C001840212 | Clyde Brown | Clarendon | Completed | Load_260521 | May Pen - 110 | Jul 4, 2026 6:49pm | Jul 4, 2026 6:50pm | Jul 4, 2026 7:11pm | Jul 4, 2026 7:11pm | Jul 4, 2026 7:48pm | Jul 4, 2026 8:54pm | Jul 4, 2026 7:58pm | Jul 4, 2026 7:58pm |  |  | Fair | No | Blown 10 amps junction fuse at Buckner line patrolled and no fault seen,blown fuse replaced
Outage | J.E.26.07.03189 | C001840211 | Andre Smith | KSAN | Completed | Load_249530 | Hope - 510 | Jul 4, 2026 6:46pm | Jul 4, 2026 6:46pm | Jul 4, 2026 8:29pm | Jul 4, 2026 8:29pm | Jul 4, 2026 9:12pm | Jul 4, 2026 9:40pm | Jul 4, 2026 9:56pm | Jul 4, 2026 9:56pm |  |  | Fair | No | Repair burnt primary jumper using one onebolt clamp supply restored
Non-Outage | J.E.26.07.03622 | C001840210 | Raymond Lewis | null | Completed | null | null | Jul 4, 2026 6:42pm | Jul 4, 2026 6:43pm | Jul 4, 2026 10:17pm | Jul 4, 2026 10:17pm | Jul 4, 2026 10:17pm | Jul 5, 2026 1:22pm | Jul 5, 2026 1:24am | Jul 5, 2026 1:24am | Fire |  | Fair | No | Splice and retention phase and neutral 3 span secondary refuse and close 50 kva x former
Outage | J.E.26.07.03542 | C001840208 | Andrew Powell | Manchester | Completed | Load_268017 | Spur Tree - 210 | Jul 4, 2026 6:41pm | Jul 4, 2026 6:42pm | Jul 4, 2026 6:55pm | Jul 4, 2026 6:55pm | Jul 4, 2026 8:09pm | Jul 4, 2026 8:25pm | Jul 4, 2026 8:28pm | Jul 4, 2026 8:28pm |  |  | Fair | No | Patrol and found clear, replace blown 10 amp junction by Alligator pond square to coast road, no pole number by switch location, restore supply okay.
Non-Outage | J.E.26.07.03560 | C001840206 | Omar King | null | Completed | null | null | Jul 4, 2026 6:39pm | Jul 4, 2026 6:39pm | Jul 4, 2026 7:12pm | Jul 4, 2026 7:12pm | Jul 4, 2026 7:55pm | Jul 4, 2026 7:56pm | Jul 4, 2026 7:56pm | Jul 4, 2026 7:56pm | BrokenWire |  | Fair | No | Premises found ok
Outage | J.E.26.07.03626 | C001840207 | Andrew Powell | St.Elizabeth | Completed | Load_256959 | Maggotty - 210 | Jul 4, 2026 6:39pm | Jul 4, 2026 6:41pm | Jul 4, 2026 6:53pm | Jul 4, 2026 6:53pm | Jul 4, 2026 6:53pm | Jul 4, 2026 6:53pm | Jul 4, 2026 6:54pm | Jul 4, 2026 6:54pm |  |  | Fair | No | Premises found okay customer stated that it was an internal issue breaker tripped.
Outage | J.E.26.07.03623 | C001840205 | Richman Whyte | St.Elizabeth | Completed | Load_568694 | Maggotty - 110 | Jul 4, 2026 6:37pm | Jul 4, 2026 6:38pm | Jul 4, 2026 9:37pm | Jul 4, 2026 9:37pm | Jul 4, 2026 9:37pm | Jul 4, 2026 9:37pm | Jul 4, 2026 9:38pm | Jul 4, 2026 9:38pm | BrokenWire |  | Fair | No | Customer required connection after restoration hexing area referr to field service
Non-Outage | J.E.26.07.03610 | C001840204 | Richman Whyte | null | Completed | null | null | Jul 4, 2026 6:35pm | Jul 4, 2026 6:35pm | Jul 4, 2026 9:38pm | Jul 4, 2026 9:38pm | Jul 4, 2026 9:38pm | Jul 4, 2026 9:39pm | Jul 4, 2026 9:39pm | Jul 4, 2026 9:39pm |  |  | Fair | No | St James call
Outage | J.E.26.07.03599 | C001840202 | Damion Reid | Manchester | Completed | Load_248582 | Kendal - 210 | Jul 4, 2026 6:27pm | Jul 4, 2026 6:28pm | Jul 4, 2026 10:36pm | Jul 4, 2026 11:43pm | Jul 4, 2026 11:43pm | Jul 4, 2026 11:44pm | Jul 4, 2026 11:55pm | Jul 4, 2026 11:55pm |  |  | Rains | No | Burnt off primary phase jumper found cause by defective one bolt clamp open 50Amp trip saver remade jumper and reset trip saver
Outage | J.E.26.07.03602 | C001840203 | Richman Whyte | Westmoreland | Completed | Load_251069 | Paradise - 310 | Jul 4, 2026 6:27pm | Jul 4, 2026 6:28pm | Jul 5, 2026 6:39pm | Jul 5, 2026 6:39pm | Jul 5, 2026 6:39pm | Jul 5, 2026 6:39pm | Jul 5, 2026 6:40pm | Jul 5, 2026 6:40pm |  |  | Rains | No | Replace three amp twenty five kva transformer fuse
Outage | J.E.26.07.02103 | C001840198 | Ricky Hall | St.Catherine | Completed | Load_252997 | New Michelton - 310 | Jul 4, 2026 6:20pm | Jul 4, 2026 6:20pm | Jul 4, 2026 9:28pm | Jul 5, 2026 11:02am | Jul 5, 2026 11:02am | Jul 5, 2026 11:03am | Jul 5, 2026 11:03am | Jul 5, 2026 11:03am |  |  | Fair | No | Shift ended
Non-Outage | J.E.26.07.02364 | C001840194 | Marlon Brown | Trelawny | Completed | Load_239746 | Greenwood - 210 | Jul 4, 2026 6:15pm | Jul 4, 2026 6:16pm | Jul 4, 2026 8:02pm | Jul 4, 2026 9:59pm | Jul 4, 2026 10:56pm | Jul 4, 2026 10:56pm | Jul 4, 2026 10:56pm | Jul 4, 2026 10:56pm |  |  | Fair | No | Unable to locate customer via telephone nor direction
Outage | J.E.26.07.03561 | C001840193 | Milton Charlton | KSAN | Completed | Load_578844 | Hope - 510 | Jul 4, 2026 6:14pm | Jul 4, 2026 6:15pm | Jul 4, 2026 6:36pm | Jul 4, 2026 6:36pm | Jul 4, 2026 6:37pm | Jul 4, 2026 6:40pm | Jul 4, 2026 6:41pm | Jul 4, 2026 6:41pm |  |  | Fair | No | Call related to call at #18 Silvera terrace
Outage | J.E.26.07.03596 | C001840192 | Milton Charlton | KSAN | Completed | Load_240204 | Constant Spring - 210 | Jul 4, 2026 6:14pm | Jul 5, 2026 8:34am | Jul 5, 2026 9:07am | Jul 5, 2026 12:40pm | Jul 5, 2026 2:16pm | Jul 5, 2026 2:20pm | Jul 5, 2026 2:17pm | Jul 5, 2026 2:17pm |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.07.03570 | C001840191 | Andrew Powell | St.Elizabeth | Completed | Load_268577 | Maggotty - 210 | Jul 4, 2026 6:12pm | Jul 4, 2026 6:13pm | Jul 4, 2026 6:20pm | Jul 4, 2026 6:20pm | Jul 4, 2026 6:20pm | Jul 4, 2026 6:45pm | Jul 4, 2026 6:50pm | Jul 4, 2026 6:50pm |  |  | Fair | No | Patrol and found clear, replace two blown 50 amp junction fuse by Pedro Cross looking towards Pedro Plane, no pole number by switch location, restore supply okay.
Outage | J.E.26.07.03547 | C001840187 | Omar King | St.Ann | Completed | Load_243784 | Roaring River - 410 | Jul 4, 2026 6:10pm | Jul 4, 2026 6:13pm | Jul 4, 2026 7:58pm | Jul 4, 2026 7:58pm | Jul 4, 2026 8:51pm | Jul 4, 2026 8:52pm | Jul 4, 2026 8:53pm | Jul 4, 2026 8:53pm |  |  | Fair | No | Found three (3) span of secondary neutral broken as been splice and retention customer is now with supply
Outage | J.E.26.07.03583 | C001840186 | Raymond Lewis | St.Ann | Completed | Load_241057 | Cardiff Hall - 310 | Jul 4, 2026 6:10pm | Jul 4, 2026 6:12pm | Jul 4, 2026 10:12pm | Jul 4, 2026 10:12pm | Jul 4, 2026 10:12pm | Jul 4, 2026 10:14pm | Jul 4, 2026 10:14pm | Jul 4, 2026 10:14pm |  |  | Fair | No | Phone out of service
Non-Outage | J.E.26.07.03585 | C001840185 | Romeo Brissett | null | Completed | null | null | Jul 4, 2026 6:09pm | Jul 4, 2026 6:09pm | Jul 4, 2026 6:13pm | Jul 4, 2026 6:14pm | Jul 4, 2026 6:36pm | Jul 4, 2026 6:38pm | Jul 4, 2026 6:41pm | Jul 4, 2026 6:41pm | BrokenWire |  | Fair | No | Line patrolled and found power in the area there is no broken wire found in the area.
Outage | J.E.26.07.03548 | C001840184 | Romeo Brissett | St.James | Completed | Load_260332 | Bogue - 610 | Jul 4, 2026 5:27pm | Jul 4, 2026 5:28pm | Jul 4, 2026 6:41pm | Jul 4, 2026 6:41pm | Jul 4, 2026 7:08pm | Jul 4, 2026 7:47pm | Jul 4, 2026 7:52pm | Jul 4, 2026 7:52pm |  |  | Fair | No | Replaced (1)50kva transformer fuse.
Outage | J.E.26.07.03556 | C001840183 | Swon Miller | St.James | Completed | Load_245262 | Queens Drive - 710 | Jul 4, 2026 5:27pm | Jul 4, 2026 5:28pm | Jul 4, 2026 6:50pm | Jul 4, 2026 6:50pm | Jul 4, 2026 7:25pm | Jul 4, 2026 7:48pm | Jul 4, 2026 7:56pm | Jul 4, 2026 7:56pm |  |  | Fair | No | Check and found okay voltage found voltage found 114/115/232 voltage left 115/114/232
Outage | J.E.26.07.03535 | C001840182 | Richard Nicholas | KSAS | Completed | Load_1001008 | Duhaney - 210 | Jul 4, 2026 5:24pm | Jul 4, 2026 5:24pm | Jul 4, 2026 7:22pm | Jul 4, 2026 7:22pm | Jul 4, 2026 9:19pm | Jul 4, 2026 9:31pm | Jul 4, 2026 9:32pm | Jul 4, 2026 9:32pm |  |  | Fair | No | Replaced blown 25kva transformer 5amp fuse on pole #0104439.
Outage | J.E.26.07.03555 | C001840180 | Delano Gayle | St.Catherine | Completed | Load_269676 | New Michelton - 310 | Jul 4, 2026 5:23pm | Jul 4, 2026 11:25pm | Jul 5, 2026 2:41am | Jul 5, 2026 3:06am | Jul 5, 2026 3:06am | Jul 5, 2026 3:07am | Jul 5, 2026 3:07am | Jul 5, 2026 3:07am |  |  | Fair | No | Foggy area daylight attention required
Outage | J.E.26.07.03545 | C001840179 | Richman Whyte | Westmoreland | Completed | Load_264613 | Paradise - 310 | Jul 4, 2026 5:16pm | Jul 4, 2026 5:16pm | Jul 4, 2026 6:03pm | Jul 4, 2026 6:03pm | Jul 4, 2026 6:03pm | Jul 4, 2026 6:03pm | Jul 4, 2026 6:04pm | Jul 4, 2026 6:04pm |  |  | Fair | No | Already restored earlier today
Outage | J.E.26.07.03471 | C001840177 | Wayne Dillion | St.Elizabeth | Completed | Load_244984 | Maggotty - 110 | Jul 4, 2026 5:14pm | Jul 4, 2026 5:15pm | Jul 4, 2026 6:09pm | Jul 4, 2026 6:09pm | Jul 4, 2026 6:09pm | Jul 4, 2026 6:33pm | Jul 4, 2026 6:33pm | Jul 4, 2026 6:33pm |  |  | Fair | No | Patrol and found clear. Replace one 15amp junction fuse no pole #. Restored supply okay.
Outage | J.E.26.07.03487 | C001840178 | Wayne Dillion | St.Elizabeth | Completed | Load_262812 | Maggotty - 110 | Jul 4, 2026 5:14pm | Jul 4, 2026 5:15pm | Jul 4, 2026 6:33pm | Jul 4, 2026 6:33pm | Jul 4, 2026 6:33pm | Jul 4, 2026 6:35pm | Jul 4, 2026 6:35pm | Jul 4, 2026 6:35pm |  |  | Fair | No | Supply restored to the area.
Outage | J.E.26.07.03482 | C001840174 | Ryan Richards | Manchester | Completed | Load_293094 | Porus - 310 | Jul 4, 2026 5:10pm | Jul 4, 2026 5:10pm | Jul 4, 2026 6:14pm | Jul 4, 2026 6:16pm | Jul 4, 2026 7:18pm | Jul 5, 2026 12:41am | Jul 5, 2026 12:41am | Jul 5, 2026 12:41am |  |  | Fair | No | Blown 3 amp fuse found for 25 kva transformer line patrol 2 span of broken secondary neutral found cause by fig tree carry out 2 span of spot bushing spliced an retention using 40ft#2 aluminum 4 one bolt clamps 2#2 preforms and replace blown 3 amp fuse all customers are now with supply
Outage | J.E.26.07.03515 | C001840175 | Barnett Brown | Manchester | Completed | Load_264906 | Spur Tree - 310 | Jul 4, 2026 5:10pm | Jul 4, 2026 5:11pm | Jul 4, 2026 7:20pm | Jul 4, 2026 7:20pm | Jul 4, 2026 8:16pm | Jul 4, 2026 9:14pm | Jul 4, 2026 9:15pm | Jul 4, 2026 9:15pm |  |  | Fair | No | Bridge splicing sleeve at secondary neutral
Outage | J.E.26.07.03544 | C001840173 | Neville Spencer | Clarendon | Completed | Load_262821 | May Pen - 110 | Jul 4, 2026 5:10pm | Jul 4, 2026 5:12pm | Jul 4, 2026 6:17pm | Jul 4, 2026 6:17pm | Jul 4, 2026 7:06pm | Jul 4, 2026 9:05pm | Jul 4, 2026 9:09pm | Jul 4, 2026 9:09pm |  |  | Fair | No | Removed illegal connection from secondary line reset trip 10: kva xmfr supply restored.
Outage | J.E.26.07.03146 | C001840172 | Christopher Edwards | KSAN | Completed | Load_301573 | Constant Spring - 410 | Jul 4, 2026 5:02pm | Jul 4, 2026 5:03pm | Jul 4, 2026 7:40pm | Jul 4, 2026 7:40pm | Jul 4, 2026 8:43pm | Jul 4, 2026 9:48pm | Jul 4, 2026 9:50pm | Jul 4, 2026 9:50pm |  |  | Fair | No | Removed illegal connections from 2/0 twisted wire Taped exposed phase joint Refuse blown 25 kva transformer Using:(1) 2amps
Outage | J.E.26.07.03295 | C001840171 | Christopher Edwards | KSAN | Completed | Load_237815 | Constant Spring - 410 | Jul 4, 2026 5:01pm | Jul 4, 2026 5:03pm | Jul 4, 2026 6:14pm | Jul 4, 2026 6:14pm | Jul 4, 2026 7:04pm | Jul 4, 2026 7:39pm | Jul 4, 2026 7:39pm | Jul 4, 2026 7:39pm |  |  | Fair | No | Refuse blown junction fuse Using (1) 15 ampsClear tree limb off primary line
Outage | J.E.26.07.03502 | C001840170 | Elvis Trowers | KSAS | Completed | Load_267072 | Duhaney - 310 | Jul 4, 2026 5:00pm | Jul 4, 2026 5:01pm | Jul 4, 2026 7:37pm | Jul 4, 2026 7:37pm | Jul 4, 2026 7:54pm | Jul 4, 2026 9:15pm | Jul 4, 2026 9:15pm | Jul 4, 2026 9:15pm |  |  | Fair | Yes | Areas was found having single phasing when checked and a 100 kva transformer was isolated at pole #0039998 to repair broken secondary wires, phase and neutral, about 40’ feet of #2AA wire 2 preforms and 4 one bolt clamps was used to splice and retention broken wires then reclose 100 kva at the above pole number.
Outage | J.E.26.07.03543 | C001840169 | Elvis Trowers | KSAS | Completed | Load_241997 | Duhaney - 310 | Jul 4, 2026 5:00pm | Jul 4, 2026 5:01pm | Jul 4, 2026 9:18pm | Jul 4, 2026 9:18pm | Jul 4, 2026 9:20pm | Jul 4, 2026 9:26pm | Jul 4, 2026 9:26pm | Jul 4, 2026 9:26pm | LowHangingWires |  | Fair | Yes | Premises checked and found ok, call related to the 100 kva transformer that was isolated at pole #0039998.
Non-Outage | J.E.26.07.02884 | C001840167 | Clyde Brown | null | Completed | null | null | Jul 4, 2026 4:44pm | Jul 4, 2026 5:15pm | Jul 4, 2026 7:08pm | Jul 4, 2026 7:08pm | Jul 4, 2026 7:08pm | Jul 4, 2026 7:05pm | Jul 4, 2026 7:10pm | Jul 4, 2026 7:10pm |  |  | Fair | No | Call refer to field service
Outage | J.E.26.07.03521 | C001840166 | Stephen Taylor | Portland | Completed | Load_257367 | Port Antonio - 310 | Jul 4, 2026 4:43pm | Jul 4, 2026 4:46pm | Jul 4, 2026 6:57pm | Jul 4, 2026 6:57pm | Jul 4, 2026 6:57pm | Jul 4, 2026 6:57pm | Jul 4, 2026 6:58pm | Jul 4, 2026 6:58pm |  |  | Fair | No | See 20 amp trip saver down no number on pole patrol clear line with switch stick and close up back 20 amp trip saver safely all customer is now okay
Outage | J.E.26.07.03518 | C001840165 | Stephen Taylor | Portland | Completed | Load_251492 | Port Antonio - 310 | Jul 4, 2026 4:42pm | Jul 4, 2026 4:46pm | Jul 4, 2026 4:56pm | Jul 4, 2026 4:56pm | Jul 4, 2026 6:12pm | Jul 4, 2026 6:12pm | Jul 4, 2026 6:57pm | Jul 4, 2026 6:57pm |  |  | Fair | No | See 20 amp trip saver down no number on pole patrol clear line with switch stick and close up back 20 amp trip saver safely all customer is now okay
Outage | J.E.26.07.03311 | C001840164 | Richard Nicholas | St.Catherine | Completed | Load_1000361 | Rhodens Pen - 410 | Jul 4, 2026 4:33pm | Jul 4, 2026 4:34pm | Jul 4, 2026 6:22pm | Jul 4, 2026 6:23pm | Jul 4, 2026 7:10pm | Jul 4, 2026 7:22pm | Jul 4, 2026 7:22pm | Jul 4, 2026 7:22pm |  |  | Fair | No | Found ok
Non-Outage | J.E.26.07.03263 | C001840162 | Andre Smith | KSAS | Completed | Load_241896 | Rockfort - 410 | Jul 4, 2026 4:29pm | Jul 4, 2026 4:29pm | Jul 4, 2026 7:39pm | Jul 4, 2026 7:39pm | Jul 4, 2026 8:24pm | Jul 4, 2026 8:29pm | Jul 4, 2026 8:29pm | Jul 4, 2026 8:29pm |  |  | Fair | No | Replace defective one bolt clamp at pole on neutral supply restored
Outage | J.E.26.07.03495 | C001840160 | Andre Smith | KSAN | Completed | Load_293885 | Washington Blvd - 710 | Jul 4, 2026 4:27pm | Jul 4, 2026 4:28pm | Jul 4, 2026 5:10pm | Jul 4, 2026 5:10pm | Jul 4, 2026 5:48pm | Jul 4, 2026 6:00pm | Jul 4, 2026 6:00pm | Jul 4, 2026 6:00pm |  |  | Fair | No | Reconnection done in ypp box with the assistance of callcenter supply restored
Outage | J.E.26.07.03503 | C001840158 | Rusean Allen | KSAS | Completed | Load_256563 | Cane River - 310 | Jul 4, 2026 4:27pm | Jul 5, 2026 9:15am | Jul 5, 2026 11:48am | Jul 5, 2026 11:48am | Jul 5, 2026 12:15pm | Jul 5, 2026 12:16pm | Jul 5, 2026 12:17pm | Jul 5, 2026 12:17pm |  |  | Fair | No | Defective meter socket found at premises, customer was advised to contact an electrician.
Outage | J.E.26.07.03504 | C001840159 | Elvis Trowers | KSAN | Completed | Load_575320 | Washington Blvd - 710 | Jul 4, 2026 4:27pm | Jul 4, 2026 5:09pm | Jul 4, 2026 9:27pm | Jul 4, 2026 9:27pm | Jul 4, 2026 10:03pm | Jul 4, 2026 10:06pm | Jul 4, 2026 10:06pm | Jul 4, 2026 10:06pm |  |  | Fair | Yes | Premises checked and found ok.
Outage | J.E.26.07.03497 | C001840157 | Clyde Brown | Clarendon | Completed | Load_260521 | May Pen - 110 | Jul 4, 2026 4:26pm | Jul 4, 2026 4:27pm | Jul 4, 2026 6:23pm | Jul 4, 2026 6:23pm | Jul 4, 2026 6:23pm | Jul 4, 2026 6:20pm | Jul 4, 2026 6:27pm | Jul 4, 2026 6:27pm |  |  | Fair | No | Cannot be located customer not answering phone
Outage | J.E.26.07.03493 | C001840154 | Omar King | St.Ann | Completed | Load_269408 | Ocho Rios - 310 | Jul 4, 2026 4:14pm | Jul 4, 2026 4:14pm | Jul 4, 2026 6:02pm | Jul 4, 2026 6:02pm | Jul 4, 2026 6:40pm | Jul 4, 2026 6:48pm | Jul 4, 2026 6:48pm | Jul 4, 2026 6:48pm |  |  | Fair | No | Found 25 KVA transformer fuse blow cause by defective lightning arrester temporary has been done and fuse as been replaced area is now with supply
Outage | J.E.26.07.03468 | C001840152 | Richman Whyte | St.James | Completed | Load_250995 | Bogue - 610 | Jul 4, 2026 3:52pm | Jul 4, 2026 8:11pm | Jul 4, 2026 9:39pm | Jul 4, 2026 9:39pm | Jul 4, 2026 9:39pm | Jul 4, 2026 9:40pm | Jul 4, 2026 9:40pm | Jul 4, 2026 9:40pm |  |  | Fair | No | St James call
Outage | J.E.26.07.03486 | C001840151 | Horace Malcolm | St.James | Completed | Load_266793 | Bogue - 310 | Jul 4, 2026 3:52pm | Jul 4, 2026 3:53pm | Jul 4, 2026 4:32pm | Jul 4, 2026 4:34pm | Jul 4, 2026 5:29pm | Jul 4, 2026 8:01pm | Jul 4, 2026 8:01pm | Jul 4, 2026 8:01pm | BrokenPole | Y | Fair | No | Found one 40ft class 6 wooden pole broken and two pole span primary and one pole span secondary line broken due to fallen tree repair primary and secondary line used 70ft #2 conductor (3) #2 preforms 3clamps and replace one 10amp junction fuse primary line has been floated in customer premises pole need replacement urgent
Outage | J.E.26.07.03455 | C001840150 | Elvis Trowers | KSAS | Completed | Load_578715 | Duhaney - 310 | Jul 4, 2026 3:48pm | Jul 4, 2026 3:59pm | Jul 4, 2026 4:55pm | Jul 4, 2026 4:55pm | Jul 4, 2026 5:52pm | Jul 4, 2026 7:03pm | Jul 4, 2026 7:03pm | Jul 4, 2026 7:03pm |  |  | Fair | Yes | Areas was found without electricity supply during patrol and a blown 40 amp junction fuse was replaced at pole #515983 after kite tails were removed.
Outage | J.E.26.07.02290 | C001840149 | Donald Cunningham | Portmore | Completed | Load_257513 | Naggo Head - 510 | Jul 4, 2026 3:39pm | Jul 4, 2026 3:41pm | Jul 4, 2026 6:31pm | Jul 4, 2026 6:31pm | Jul 4, 2026 7:23pm | Jul 4, 2026 7:31pm | Jul 4, 2026 7:33pm | Jul 4, 2026 7:33pm | BrokenWire |  | Fair | No | Burnt off phase by pole corrected one clamp use
Outage | J.E.26.07.03136 | C001840148 | Donald Cunningham | St.Catherine | Completed | Load_256285 | Twickenham - 210 | Jul 4, 2026 3:39pm | Jul 4, 2026 3:41pm | Jul 4, 2026 3:52pm | Jul 4, 2026 3:52pm | Jul 4, 2026 5:57pm | Jul 4, 2026 6:30pm | Jul 4, 2026 6:31pm | Jul 4, 2026 6:31pm | BrokenWire |  | Fair | No | Broken service wire splice and retention using 6 feet of #6 triplex and 6 penunion voltage readings 116/2/232
Outage | J.E.26.07.03140 | C001840147 | Delano Gayle | Portmore | Completed | Load_246278 | Naggo Head - 510 | Jul 4, 2026 3:39pm | Jul 4, 2026 11:00pm | Jul 4, 2026 11:09pm | Jul 4, 2026 11:09pm | Jul 5, 2026 1:04am | Jul 5, 2026 1:09am | Jul 5, 2026 1:09am | Jul 5, 2026 1:09am | BrokenWire |  | Fair | No | Premises not found no answer from customer phone
Outage | J.E.26.07.03128 | C001840146 | Oshane Warren | Westmoreland | Completed | Load_249359 | Paradise - 110 | Jul 4, 2026 3:37pm | Jul 4, 2026 3:44pm | Jul 4, 2026 5:57pm | Jul 4, 2026 5:57pm | Jul 4, 2026 5:57pm | Jul 4, 2026 5:57pm | Jul 4, 2026 5:58pm | Jul 4, 2026 5:58pm |  |  | Fair | No | Check and find ok
Outage | J.E.26.07.03273 | C001840145 | Richman Whyte | Westmoreland | Completed | Load_263263 | Paradise - 310 | Jul 4, 2026 3:37pm | Jul 4, 2026 3:45pm | Jul 4, 2026 3:53pm | Jul 4, 2026 3:53pm | Jul 4, 2026 4:12pm | Jul 4, 2026 4:38pm | Jul 4, 2026 4:39pm | Jul 4, 2026 4:39pm |  |  | Rains | No | Replace twenty amp junction fuse
Outage | J.E.26.07.03245 | C001840139 | Barnett Brown | Manchester | Completed | Load_241366 | Spur Tree - 310 | Jul 4, 2026 3:32pm | Jul 4, 2026 3:35pm | Jul 4, 2026 4:35pm | Jul 4, 2026 4:35pm | Jul 4, 2026 5:52pm | Jul 4, 2026 7:17pm | Jul 4, 2026 7:19pm | Jul 4, 2026 7:19pm | BrokenWire |  | Fair | No | Open 25 kva transformer, splice and retention secondary phase
Outage | J.E.26.07.03254 | C001840141 | Richard Samuda | Manchester | Completed | Load_252522 | Spur Tree - 310 | Jul 4, 2026 3:32pm | Jul 5, 2026 8:02am | Jul 5, 2026 8:59am | Jul 5, 2026 9:16am | Jul 5, 2026 9:16am | Jul 5, 2026 9:16am | Jul 5, 2026 9:17am | Jul 5, 2026 9:17am | Fire |  | Fair | No | Customer say situation was resolved
Outage | J.E.26.07.03266 | C001840143 | Damion Reid | Manchester | Completed | Load_251216 | Kendal - 210 | Jul 4, 2026 3:32pm | Jul 4, 2026 3:35pm | Jul 4, 2026 5:34pm | Jul 4, 2026 5:34pm | Jul 4, 2026 5:41pm | Jul 4, 2026 5:48pm | Jul 4, 2026 5:50pm | Jul 4, 2026 5:50pm |  |  | Rains | No | Two 50Amp trip saver found down cause by lightning line patrol and replace blown fuse
Outage | J.E.26.07.02849 | C001840136 | Omar King | Clarendon | Completed | Load_354585 | May Pen - 110 | Jul 4, 2026 3:29pm | Jul 4, 2026 3:52pm | Jul 4, 2026 5:31pm | Jul 4, 2026 5:31pm | Jul 4, 2026 5:31pm | Jul 4, 2026 5:33pm | Jul 4, 2026 5:33pm | Jul 4, 2026 5:33pm |  |  | Fair | No | Unable locate customer call several times no answer directions not sufficient
Outage | J.E.26.07.03092 | C001840137 | Clyde Brown | Clarendon | Completed | Load_237973 | Parnassus - 210 | Jul 4, 2026 3:29pm | Jul 4, 2026 3:30pm | Jul 4, 2026 4:05pm | Jul 4, 2026 4:05pm | Jul 4, 2026 4:48pm | Jul 4, 2026 4:42pm | Jul 4, 2026 5:04pm | Jul 4, 2026 5:04pm |  |  | Fair | No | Blown 25 amps junction fuse on York Town road,line patrolled and no fault seen and blown fuse replaced.
Outage | J.E.26.07.03271 | C001840131 | Andrew Powell | St.Elizabeth | Completed | Load_250102 | Maggotty - 210 | Jul 4, 2026 3:29pm | Jul 4, 2026 3:30pm | Jul 4, 2026 3:50pm | Jul 4, 2026 3:50pm | Jul 4, 2026 5:08pm | Jul 4, 2026 5:55pm | Jul 4, 2026 5:57pm | Jul 4, 2026 5:57pm | BrokenWire | Y | Fair | No | Clear vegetation, splice and tension broken service wire at secondary line using 15 feet #6 triplex, voltage reading 112v-113v phase to neutral 225v cross phase.
Outage | J.E.26.07.03310 | C001840132 | Andrew Powell | Manchester | Completed | Load_263222 | Spur Tree - 210 | Jul 4, 2026 3:29pm | Jul 4, 2026 3:30pm | Jul 4, 2026 3:42pm | Jul 4, 2026 3:42pm | Jul 4, 2026 3:42pm | Jul 4, 2026 3:42pm | Jul 4, 2026 3:43pm | Jul 4, 2026 3:43pm |  |  | Fair | No | Premises found okay customer stated that supply restored.
Outage | J.E.26.07.03348 | C001840134 | Richard Samuda | Manchester | Completed | Load_243817 | Spur Tree - 210 | Jul 4, 2026 3:29pm | Jul 5, 2026 7:59am | Jul 5, 2026 8:28am | Jul 5, 2026 8:29am | Jul 5, 2026 8:58am | Jul 5, 2026 8:58am | Jul 5, 2026 8:59am | Jul 5, 2026 8:59am |  |  | Fair | No | Found ok
Outage | J.E.26.07.03428 | C001840133 | Andrew Powell | Manchester | Completed | Load_258771 | Spur Tree - 210 | Jul 4, 2026 3:29pm | Jul 4, 2026 3:30pm | Jul 4, 2026 3:44pm | Jul 4, 2026 3:44pm | Jul 4, 2026 3:44pm | Jul 4, 2026 3:44pm | Jul 4, 2026 3:45pm | Jul 4, 2026 3:45pm |  |  | Fair | No | Premises not located no direction contact customer by telephone unsuccessful.
Outage | J.E.26.07.03442 | C001840135 | Andrew Powell | Manchester | Completed | Load_251338 | Spur Tree - 210 | Jul 4, 2026 3:29pm | Jul 4, 2026 3:30pm | Jul 4, 2026 3:38pm | Jul 4, 2026 3:46pm | Jul 4, 2026 3:46pm | Jul 4, 2026 3:47pm | Jul 4, 2026 3:47pm | Jul 4, 2026 3:47pm |  |  | Fair | No | Premises found okay customer stated that supply restored.
Outage | J.E.26.07.03115 | C001840128 | Clyde Brown | Clarendon | Completed | Load_248927 | Parnassus - 310 | Jul 4, 2026 3:26pm | Jul 4, 2026 3:26pm | Jul 4, 2026 5:05pm | Jul 4, 2026 5:05pm | Jul 4, 2026 5:42pm | Jul 4, 2026 5:57pm | Jul 4, 2026 6:14pm | Jul 4, 2026 6:14pm |  |  | Fair | No | 25 kva transformer found burnt same isolated and about 8 customers are affected,transformer need to be replaced.
Outage | J.E.26.07.03249 | C001840129 | Neville Spencer | Clarendon | Completed | Load_254653 | May Pen - 110 | Jul 4, 2026 3:26pm | Jul 4, 2026 3:26pm | Jul 4, 2026 3:50pm | Jul 4, 2026 3:50pm | Jul 4, 2026 5:12pm | Jul 4, 2026 6:12pm | Jul 4, 2026 6:15pm | Jul 4, 2026 6:15pm | TreeContact | Y | Fair | No | Cleared bamboo from 13.8 kv line renew blown 10 amp j/ fuse at pole # 051066 area restored.
Outage | J.E.26.07.03301 | C001840130 | Neville Spencer | Clarendon | Completed | Load_239213 | May Pen - 110 | Jul 4, 2026 3:26pm | Jul 4, 2026 3:26pm | Jul 4, 2026 9:09pm | Jul 4, 2026 9:09pm | Jul 4, 2026 9:09pm | Jul 4, 2026 9:09pm | Jul 4, 2026 9:11pm | Jul 4, 2026 9:11pm |  |  | Fair | No | Removed illegal connection from secondary line reset trip 10 kva xmfr supply restored.
Outage | J.E.26.07.03299 | C001840125 | Derrick Dawkins | St.James | Completed | Load_248976 | Queens Drive - 710 | Jul 4, 2026 3:18pm | Jul 5, 2026 7:48am | Jul 5, 2026 8:14am | Jul 5, 2026 8:14am | Jul 5, 2026 10:56am | Jul 5, 2026 9:50am | Jul 5, 2026 11:07am | Jul 5, 2026 11:07am |  |  | Fair | No | Check and found customer experiencing phaseing from the hexing box refer back to field service kaydian voltage left 119/45
Outage | J.E.26.07.03316 | C001840123 | Swon Miller | St.James | Completed | Load_261409 | Queens Drive - 710 | Jul 4, 2026 3:18pm | Jul 4, 2026 3:19pm | Jul 4, 2026 4:07pm | Jul 4, 2026 4:07pm | Jul 4, 2026 4:42pm | Jul 26, 2026 5:16am | Jul 4, 2026 5:28pm | Jul 4, 2026 5:28pm |  |  | Fair | No | Unable to locate customer calls to customer went unanswered
Outage | J.E.26.07.03317 | C001840124 | Swon Miller | St.James | Completed | Load_238603 | Queens Drive - 710 | Jul 4, 2026 3:18pm | Jul 4, 2026 3:19pm | Jul 4, 2026 5:28pm | Jul 4, 2026 5:29pm | Jul 4, 2026 6:23pm | Jul 21, 2026 6:44am | Jul 4, 2026 6:48pm | Jul 4, 2026 6:48pm |  |  | Fair | No | Unable to locate customer calls to customer went unanswered
Outage | J.E.26.07.02190 | C001840121 | Ricky Hall | St.Catherine | Completed | Load_256212 | New Michelton - 210 | Jul 4, 2026 3:10pm | Jul 4, 2026 3:17pm | Jul 4, 2026 6:13pm | Jul 4, 2026 6:50pm | Jul 4, 2026 6:50pm | Jul 4, 2026 9:26pm | Jul 4, 2026 9:28pm | Jul 4, 2026 9:28pm | Fire |  | Rains | No | Conduct spot bushing splice and retention broken secondary lines use 200”#2 aa 4 preform 6 clamps
Outage | J.E.26.07.03281 | C001840120 | Romeo Brissett | St.James | Completed | Load_260332 | Bogue - 610 | Jul 4, 2026 3:07pm | Jul 4, 2026 3:10pm | Jul 4, 2026 7:53pm | Jul 4, 2026 7:53pm | Jul 4, 2026 7:54pm | Jul 4, 2026 8:24pm | Jul 4, 2026 8:24pm | Jul 4, 2026 8:24pm |  |  | Fair | No | Removed bird and replaced(1)25KVA transformer fuse at the church
Outage | J.E.26.07.03274 | C001840118 | Richard Nicholas | St.Catherine | Completed | Load_1000417 | Rhodens Pen - 210 | Jul 4, 2026 3:05pm | Jul 4, 2026 4:33pm | Jul 4, 2026 5:31pm | Jul 4, 2026 5:31pm | Jul 4, 2026 6:14pm | Jul 4, 2026 6:19pm | Jul 4, 2026 6:22pm | Jul 4, 2026 6:22pm |  |  | Fair | No | Replaced blown 25amp junctions with a 40amp junctions fuse on pole #623942.fuse melt due to load.
Non-Outage | J.E.26.07.03244 | C001840116 | Romeo Brissett | St.James | Completed | Load_262140 | Bogue - 610 | Jul 4, 2026 2:56pm | Jul 4, 2026 2:56pm | Jul 4, 2026 5:48pm | Jul 4, 2026 5:48pm | Jul 4, 2026 6:09pm | Jul 4, 2026 6:10pm | Jul 4, 2026 6:13pm | Jul 4, 2026 6:13pm | BrokenWire |  | Fair | No | Found customer service wire crystallized, contaminated and need to be Change. Emergency stores is currently closed, service wire will be collect on Monday morning.
Outage | J.E.26.07.03197 | C001840115 | Romeo Brissett | Trelawny | Completed | Load_255143 | Greenwood - 110 | Jul 4, 2026 2:55pm | Jul 4, 2026 2:55pm | Jul 4, 2026 4:16pm | Jul 4, 2026 4:56pm | Jul 4, 2026 5:25pm | Jul 4, 2026 5:40pm | Jul 4, 2026 5:48pm | Jul 4, 2026 5:48pm |  |  | Fair | No | Customer was connected by escalation technician.
Outage | J.E.26.07.03111 | C001840114 | Richard Nicholas | St.Catherine | Completed | Load_269718 | Tredegar - 510 | Jul 4, 2026 2:52pm | Jul 4, 2026 2:52pm | Jul 4, 2026 9:32pm | Jul 4, 2026 9:33pm | Jul 4, 2026 10:51pm | Jul 4, 2026 10:52pm | Jul 4, 2026 10:52pm | Jul 4, 2026 10:52pm |  |  | Fair | No | Cannot locate,directions needed
Outage | J.E.26.07.03258 | C001840113 | Richard Nicholas | St.Catherine | Completed | Load_245058 | Tredegar - 510 | Jul 4, 2026 2:51pm | Jul 4, 2026 2:52pm | Jul 4, 2026 3:58pm | Jul 4, 2026 3:58pm | Jul 4, 2026 5:18pm | Jul 4, 2026 5:30pm | Jul 4, 2026 5:30pm | Jul 4, 2026 5:30pm |  |  | Fair | No | Area found ok
Non-Outage | J.E.26.07.03253 | C001840111 | Floyd Taylor | Trelawny | Completed | Load_1001458 | Martha Brae - 110 | Jul 4, 2026 2:50pm | Jul 4, 2026 2:52pm | Jul 4, 2026 3:23pm | Jul 4, 2026 3:23pm | Jul 4, 2026 4:21pm | Jul 4, 2026 4:24pm | Jul 4, 2026 4:25pm | Jul 4, 2026 4:25pm | BangingWires |  | Fair | No | Found ok customer say issues was resolved
Outage | J.E.26.07.03264 | C001840112 | Milton Charlton | KSAN | Completed | Load_254380 | Constant Spring - 410 | Jul 4, 2026 2:50pm | Jul 5, 2026 8:36am | Jul 5, 2026 8:47am | Jul 5, 2026 8:47am | Jul 5, 2026 9:50am | Jul 5, 2026 9:20am | Jul 5, 2026 9:54am | Jul 5, 2026 9:54am |  |  | Fair | No | Customer meter #2379845 disconnected. JPS escalation is unable to reconnect meter. Meter not responding. Refer to field service.
Outage | J.E.26.07.03238 | C001840109 | Christopher Edwards | KSAN | Completed | Load_240491 | Constant Spring - 410 | Jul 4, 2026 2:33pm | Jul 4, 2026 2:34pm | Jul 4, 2026 4:16pm | Jul 4, 2026 4:17pm | Jul 4, 2026 4:22pm | Jul 4, 2026 4:51pm | Jul 4, 2026 4:51pm | Jul 4, 2026 4:51pm |  |  | Fair | No | Customer was contacted and stated that issue was resolved
Outage | J.E.26.07.02741 | C001840107 | Lancelot Brown | Hanover | Completed | Load_241495 | Orange Bay - 310 | Jul 4, 2026 2:25pm | Jul 4, 2026 2:31pm | Jul 4, 2026 4:38pm | Jul 4, 2026 4:38pm | Jul 4, 2026 7:42pm | Jul 4, 2026 7:43pm | Jul 4, 2026 7:43pm | Jul 4, 2026 7:43pm |  |  | Rains | No | Remake corroded joint in mid air used one pg clamps vl at meter socket 112-113-225 supply restore
Outage | J.E.26.07.03189 | C001840106 | Milton Charlton | KSAN | Completed | Load_249530 | Hope - 510 | Jul 4, 2026 2:14pm | Jul 4, 2026 2:18pm | Jul 4, 2026 4:37pm | Jul 4, 2026 4:37pm | Jul 4, 2026 6:33pm | Jul 4, 2026 6:35pm | Jul 4, 2026 6:36pm | Jul 4, 2026 6:36pm |  |  | Fair | No | 40ft concrete pole #0110367 TDE construction single phase 1- wire primary burn off at primary jumper . Need bucket truck to repair jumper.
Outage | J.E.26.07.03180 | C001840105 | Christopher Edwards | KSAN | Completed | Load_249614 | Constant Spring - 410 | Jul 4, 2026 2:04pm | Jul 4, 2026 2:07pm | Jul 4, 2026 2:43pm | Jul 4, 2026 2:43pm | Jul 4, 2026 2:53pm | Jul 4, 2026 4:15pm | Jul 4, 2026 4:15pm | Jul 4, 2026 4:15pm |  |  | Rains | No | Re close 3 30 ampsTrip saverAt Lawrence tavern square
Outage | J.E.26.07.03169 | C001840099 | Romeo Brissett | St.James | Completed | Load_254106 | Bogue - 610 | Jul 4, 2026 1:55pm | Jul 4, 2026 9:03pm | Jul 4, 2026 10:29pm | Jul 4, 2026 10:29pm | Jul 4, 2026 10:30pm | Jul 4, 2026 10:30pm | Jul 4, 2026 10:31pm | Jul 4, 2026 10:31pm |  |  | Fair | No | Check and found
Outage | J.E.26.07.03147 | C001840098 | Raymond Lewis | St.Ann | Completed | Load_252066 | Cardiff Hall - 310 | Jul 4, 2026 1:53pm | Jul 4, 2026 3:16pm | Jul 4, 2026 6:40pm | Jul 4, 2026 6:40pm | Jul 4, 2026 6:41pm | Jul 4, 2026 6:54pm | Jul 4, 2026 6:54pm | Jul 4, 2026 6:54pm |  |  | Fair | No | Phone not answering
Non-Outage | J.E.26.07.02376 | C001840093 | Ricky Hall | St.Catherine | Completed | Load_250866 | New Michelton - 210 | Jul 4, 2026 1:20pm | Jul 4, 2026 1:21pm | Jul 4, 2026 4:04pm | Jul 4, 2026 4:04pm | Jul 4, 2026 4:59pm | Jul 4, 2026 5:19pm | Jul 4, 2026 5:19pm | Jul 4, 2026 5:19pm |  |  | Rains | No | Replaced blown 5 amps junction 50 kva xfmr
Outage | J.E.26.07.03034 | C001840091 | Andre Smith | KSAN | Completed | Load_567704 | Washington Blvd - 310 | Jul 4, 2026 1:17pm | Jul 4, 2026 3:48pm | Jul 4, 2026 6:59pm | Jul 4, 2026 6:59pm | Jul 4, 2026 7:39pm | Jul 4, 2026 7:39pm | Jul 4, 2026 7:39pm | Jul 4, 2026 7:39pm |  |  | Fair | No | Premises found close
Outage | J.E.26.07.03112 | C001840092 | Andre Smith | KSAS | Completed | Load_260300 | Greenwich - 710 | Jul 4, 2026 1:17pm | Jul 4, 2026 3:48pm | Jul 4, 2026 4:06pm | Jul 4, 2026 4:06pm | Jul 4, 2026 4:41pm | Jul 4, 2026 4:50pm | Jul 4, 2026 5:10pm | Jul 4, 2026 5:10pm |  |  | Fair | No | Replace blown junction fuses 25A and 15A cause by bird making contact with conductor supply restored
Outage | J.E.26.07.02848 | C001840089 | Roxroy Needham | St.Ann | Completed | Load_238381 | Cardiff Hall - 210 | Jul 4, 2026 1:00pm | Jul 4, 2026 1:00pm | Jul 4, 2026 2:24pm | Jul 4, 2026 2:24pm | Jul 4, 2026 2:39pm | Jul 4, 2026 2:16pm | Jul 4, 2026 2:42pm | Jul 4, 2026 2:42pm |  |  | Fair | No | Open a 50 KVA transformer at pole to repair drop Leeds use 6 pg clamp and repair joint at pothead use 8 pg clamp voltage left at meter 118-117-238
Outage | J.E.26.07.01999 | C001840087 | Moses Elliston | St.Catherine | Completed | Load_556507 | Tredegar - 510 | Jul 4, 2026 12:55pm | Jul 4, 2026 12:56pm | Jul 4, 2026 1:21pm | Jul 4, 2026 1:21pm | Jul 4, 2026 1:21pm | Jul 4, 2026 11:40am | Jul 4, 2026 1:25pm | Jul 4, 2026 1:25pm |  |  | Fair | No | Credit added to prepaid account
Outage | J.E.26.07.03098 | C001840084 | Ricky Hall | St.Catherine | Completed | Load_240447 | New Michelton - 210 | Jul 4, 2026 12:48pm | Jul 4, 2026 12:51pm | Jul 4, 2026 3:36pm | Jul 4, 2026 3:58pm | Jul 4, 2026 3:58pm | Jul 4, 2026 3:59pm | Jul 4, 2026 3:59pm | Jul 4, 2026 3:59pm |  |  | Fair | No | Call associated with outage #02701
Non-Outage | J.E.26.07.03064 | C001840083 | Romeo Brissett | null | Completed | null | null | Jul 4, 2026 12:45pm | Jul 4, 2026 3:07pm | Jul 4, 2026 4:36pm | Jul 4, 2026 4:36pm | Jul 4, 2026 4:36pm | Jul 4, 2026 4:54pm | Jul 4, 2026 4:55pm | Jul 4, 2026 4:55pm | BrokenPole |  | Fair | No | Found two(2)retired concrete pole laying, customer is requesting for them to be taken up and removed from the road way, please send to maintenance.
Outage | J.E.26.07.03089 | C001840082 | Cliton Henry | St.Mary | Completed | Load_354721 | Oracabessa - 210 | Jul 4, 2026 12:42pm | Jul 4, 2026 12:42pm | Jul 4, 2026 7:12pm | Jul 4, 2026 7:12pm | Jul 4, 2026 7:35pm | Jul 4, 2026 7:35pm | Jul 4, 2026 7:47pm | Jul 4, 2026 7:47pm |  |  | Fair | No | Supply restored
Outage | J.E.26.07.03097 | C001840081 | Daniel Francis | St.Ann | Completed | Load_575119 | Ocho Rios - 310 | Jul 4, 2026 12:41pm | Jul 4, 2026 12:42pm | Jul 4, 2026 12:56pm | Jul 4, 2026 12:56pm | Jul 4, 2026 1:56pm | Jul 4, 2026 1:57pm | Jul 4, 2026 1:59pm | Jul 4, 2026 1:59pm |  |  | Fair | No | Change two 50 amp fuse no pole #
Non-Outage | J.E.26.07.03064 | C001840078 | Marlon Brown | null | Completed | null | null | Jul 4, 2026 12:37pm | Jul 4, 2026 12:38pm | Jul 4, 2026 12:42pm | Jul 4, 2026 12:42pm | Jul 4, 2026 12:42pm | Jul 4, 2026 12:42pm | Jul 4, 2026 12:42pm | Jul 4, 2026 12:42pm | BrokenPole |  | Fair | No | St James call
Outage | J.E.26.07.03093 | C001840077 | Raymond Lewis | St.Ann | Completed | Load_255456 | Cardiff Hall - 310 | Jul 4, 2026 12:37pm | Jul 4, 2026 3:16pm | Jul 4, 2026 9:58pm | Jul 4, 2026 9:58pm | Jul 4, 2026 9:59pm | Jul 4, 2026 9:59pm | Jul 4, 2026 10:00pm | Jul 4, 2026 10:00pm |  |  | Fair | No | Supply restored
Outage | J.E.26.07.03083 | C001840070 | Cliton Henry | St.Mary | Completed | Load_260951 | Oracabessa - 210 | Jul 4, 2026 12:30pm | Jul 4, 2026 12:30pm | Jul 4, 2026 6:53pm | Jul 4, 2026 6:54pm | Jul 4, 2026 6:54pm | Jul 4, 2026 6:56pm | Jul 4, 2026 6:56pm | Jul 4, 2026 6:56pm | LowHangingWires |  | Fair | No | The line found clear, the tree was already removed.
Outage | J.E.26.07.03084 | C001840071 | Raymond Lewis | St.Ann | Completed | Load_248487 | Cardiff Hall - 310 | Jul 4, 2026 12:30pm | Jul 4, 2026 3:16pm | Jul 4, 2026 10:06pm | Jul 4, 2026 10:06pm | Jul 4, 2026 10:06pm | Jul 4, 2026 10:09pm | Jul 4, 2026 10:10pm | Jul 4, 2026 10:10pm |  |  | Fair | No | Supply restored
Non-Outage | J.E.26.06.38205 | C001840068 | Tajay Bernard | Hanover | Completed | Load_247572 | Orange Bay - 210 | Jul 4, 2026 12:26pm | Jul 4, 2026 12:26pm | Jul 4, 2026 1:04pm | Jul 4, 2026 1:04pm | Jul 4, 2026 1:24pm | Jul 4, 2026 1:53pm | Jul 4, 2026 1:53pm | Jul 4, 2026 1:53pm |  |  | Fair | No | Clean and remake customer service neutral at customer pothead use 1 clamp voltage reading 108/107/216
Outage | J.E.26.07.03053 | C001840067 | Romeo Brissett | St.James | Completed | Load_302411 | Bogue - 610 | Jul 4, 2026 12:23pm | Jul 4, 2026 12:26pm | Jul 4, 2026 1:08pm | Jul 4, 2026 1:08pm | Jul 4, 2026 1:48pm | Jul 4, 2026 2:28pm | Jul 4, 2026 2:34pm | Jul 4, 2026 2:34pm |  |  | Fair | No | Spliced and retention customer service wire.
Outage | J.E.26.07.03074 | C001840066 | Cliton Henry | St.Mary | Completed | Load_260285 | Blackstonedge - 110 | Jul 4, 2026 12:21pm | Jul 4, 2026 12:24pm | Jul 4, 2026 3:22pm | Jul 4, 2026 3:22pm | Jul 4, 2026 3:22pm | Jul 4, 2026 3:22pm | Jul 4, 2026 3:28pm | Jul 4, 2026 3:28pm |  |  | Fair | No | The customer stated that the supply restored,
Outage | J.E.26.07.03062 | C001840064 | Oshane Warren | Westmoreland | Completed | Load_253691 | Paradise - 210 | Jul 4, 2026 12:13pm | Jul 4, 2026 12:15pm | Jul 4, 2026 12:46pm | Jul 4, 2026 12:46pm | Jul 4, 2026 4:01pm | Jul 4, 2026 4:04pm | Jul 4, 2026 4:04pm | Jul 4, 2026 4:04pm |  |  | Fair | No | Replace 3amp 25kva xformer fuse and replace 10amps junction fuse
Outage | J.E.26.07.03052 | C001840063 | Romeo Brissett | St.James | Completed | Load_258453 | Bogue - 510 | Jul 4, 2026 12:09pm | Jul 4, 2026 12:11pm | Jul 4, 2026 2:34pm | Jul 4, 2026 2:34pm | Jul 4, 2026 3:22pm | Jul 4, 2026 4:00pm | Jul 4, 2026 4:16pm | Jul 4, 2026 4:16pm |  |  | Fair | No | Removed several illegal connections, repaired secondary jumper
Outage | J.E.26.07.03058 | C001840062 | Richard Nicholas | St.Catherine | Completed | Load_263070 | Tredegar - 510 | Jul 4, 2026 12:08pm | Jul 4, 2026 12:11pm | Jul 4, 2026 12:36pm | Jul 4, 2026 12:36pm | Jul 4, 2026 1:11pm | Jul 4, 2026 1:55pm | Jul 4, 2026 1:56pm | Jul 4, 2026 1:56pm |  |  | Fair | No | Replaced blown 5amp junctions fuse on pole #040872.
Non-Outage | J.E.26.07.03046 | C001840061 | Moses Elliston | null | Completed | null | null | Jul 4, 2026 12:01pm | Jul 4, 2026 12:01pm | Jul 4, 2026 1:18pm | Jul 4, 2026 1:18pm | Jul 4, 2026 1:18pm | Jul 4, 2026 1:18pm | Jul 4, 2026 1:19pm | Jul 4, 2026 1:19pm |  |  | Fair | No | Credit added to prepaid account
Outage | J.E.26.07.03050 | C001840060 | Romaine Roberts | St.Mary | Completed | Load_258005 | Highgate - 210 | Jul 4, 2026 12:00pm | Jul 4, 2026 12:04pm | Jul 4, 2026 1:17pm | Jul 4, 2026 1:17pm | Jul 4, 2026 2:18pm | Jul 4, 2026 3:12pm | Jul 4, 2026 3:12pm | Jul 4, 2026 3:12pm |  |  | Fair | No | High wind bang secondary conductor blow fuse patrol line and replace 3 amp power restore
Outage | J.E.26.07.02960 | C001840059 | Richman Whyte | Westmoreland | Completed | Load_245455 | Paradise - 310 | Jul 4, 2026 11:58am | Jul 4, 2026 12:11pm | Jul 4, 2026 12:22pm | Jul 4, 2026 12:22pm | Jul 4, 2026 3:11pm | Jul 4, 2026 3:13pm | Jul 4, 2026 3:14pm | Jul 4, 2026 3:14pm |  |  | Rains | No | Check and found okay voltage 114 115 230
Outage | J.E.26.07.03049 | C001840058 | Omar King | St.Ann | Completed | Load_268103 | Upper White River - 210 | Jul 4, 2026 11:57am | Jul 4, 2026 3:18pm | Jul 4, 2026 3:50pm | Jul 4, 2026 3:50pm | Jul 4, 2026 4:57pm | Jul 4, 2026 5:29pm | Jul 4, 2026 5:29pm | Jul 4, 2026 5:29pm | BrokenWire |  | Fair | No | Found secondary neutral and phase broken cause by falling tree secondary line as been splice and retention customer is now with supply
Non-Outage | J.E.26.07.02914 | C001840057 | Elvis Trowers | KSAN | Completed | Load_250041 | Constant Spring - 410 | Jul 4, 2026 11:46am | Jul 4, 2026 11:53am | Jul 4, 2026 2:05pm | Jul 4, 2026 2:05pm | Jul 4, 2026 2:40pm | Jul 4, 2026 3:07pm | Jul 4, 2026 3:07pm | Jul 4, 2026 3:07pm |  |  | Fair | Yes | Happened to be internal when checked, customer was advised to contact an electrician, voltage when checked was left at 118+118=236 volts.
Non-Outage | J.E.26.07.02901 | C001840053 | Clyde Brown | null | Completed | null | null | Jul 4, 2026 11:31am | Jul 4, 2026 3:21pm | Jul 4, 2026 3:43pm | Jul 4, 2026 3:43pm | Jul 4, 2026 3:54pm | Jul 4, 2026 3:55pm | Jul 4, 2026 4:05pm | Jul 4, 2026 4:05pm | BrokenPole |  | Fair | No | 35c6 TA pole broken and lean over badly and need to be replace urgently rotten at base and broken in middle need urgent attention.
Outage | J.E.26.07.02848 | C001840054 | Roxroy Needham | St.Ann | Completed | Load_238381 | Cardiff Hall - 210 | Jul 4, 2026 11:31am | Jul 4, 2026 11:32am | Jul 4, 2026 12:33pm | Jul 4, 2026 12:33pm | Jul 4, 2026 12:33pm | Jul 4, 2026 12:35pm | Jul 4, 2026 12:35pm | Jul 4, 2026 12:35pm |  |  | Fair | No | Customer not at the premises
Outage | J.E.26.07.03008 | C001840055 | Raymond Lewis | St.Ann | Completed | Load_246247 | Roaring River - 210 | Jul 4, 2026 11:31am | Jul 4, 2026 3:16pm | Jul 4, 2026 6:40pm | Jul 4, 2026 6:55pm | Jul 4, 2026 8:32pm | Jul 4, 2026 9:29pm | Jul 4, 2026 9:29pm | Jul 4, 2026 9:29pm |  |  | Fair | No | Refuse and close two 20 amp junction
Non-Outage | J.E.26.07.03004 | C001840052 | Hopeton Henry | null | Completed | null | null | Jul 4, 2026 11:30am | Jul 4, 2026 11:35am | Jul 4, 2026 12:35pm | Jul 4, 2026 12:35pm | Jul 4, 2026 1:21pm | Jul 4, 2026 2:25pm | Jul 4, 2026 2:27pm | Jul 4, 2026 2:27pm |  |  | Fair | No | Found defective 25 kva transformer at bank of 2 transformers, only the pump station is affected Also defective transformer fuse link
Outage | J.E.26.07.02986 | C001840048 | Lancelot Brown | Hanover | Completed | Load_250447 | Orange Bay - 310 | Jul 4, 2026 11:26am | Jul 4, 2026 11:27am | Jul 4, 2026 1:16pm | Jul 4, 2026 1:17pm | Jul 4, 2026 2:17pm | Jul 4, 2026 3:28pm | Jul 4, 2026 3:29pm | Jul 4, 2026 3:29pm |  |  | Rains | No | Found junction fuse blown patroll found another junction fuse blown carrry out another junction fuse blown found diffective lightning arrester disconnected and removed diffective lightning arrester replace 18amps junction fuse no pole number replace 1-15amps junction fuse at pole number 524601 also replace 1-20amps junction fuse at pole number 007920 supply restore
Outage | J.E.26.07.02908 | C001840046 | Elvis Trowers | KSAN | Completed | Load_263454 | Washington Blvd - 610 | Jul 4, 2026 11:21am | Jul 4, 2026 11:22am | Jul 4, 2026 3:11pm | Jul 4, 2026 3:11pm | Jul 4, 2026 3:58pm | Jul 4, 2026 4:01pm | Jul 4, 2026 4:01pm | Jul 4, 2026 4:01pm |  |  | Fair | Yes | Happened to be a disconnection and was reconnected with the assistant of escalation service department.
Outage | J.E.26.07.02980 | C001840043 | Hopeton Henry | St.Thomas | Completed | Load_261596 | Good Year - 210 | Jul 4, 2026 11:14am | Jul 4, 2026 11:15am | Jul 4, 2026 2:25pm | Jul 4, 2026 6:43pm | Jul 4, 2026 7:03pm | Jul 4, 2026 7:03pm | Jul 4, 2026 7:04pm | Jul 4, 2026 7:04pm | BrokenWire |  | Fair | No | Customer not located
Outage | J.E.26.07.02761 | C001840042 | Ricky Hall | St.Catherine | Completed | Load_259587 | New Michelton - 210 | Jul 4, 2026 11:06am | Jul 4, 2026 11:06am | Jul 4, 2026 3:36pm | Jul 4, 2026 3:37pm | Jul 4, 2026 3:37pm | Jul 4, 2026 3:55pm | Jul 4, 2026 3:58pm | Jul 4, 2026 3:58pm |  |  | Rains | No | Conduct spot bushing change defective D/E insulator replaced blown 65amp junction fuse
Outage | J.E.26.07.02905 | C001840041 | Ricky Hall | St.Catherine | Completed | Load_256214 | New Michelton - 210 | Jul 4, 2026 11:05am | Jul 4, 2026 11:06am | Jul 4, 2026 4:03pm | Jul 4, 2026 5:33pm | Jul 4, 2026 6:11pm | Jul 4, 2026 6:13pm | Jul 4, 2026 6:13pm | Jul 4, 2026 6:13pm |  |  | Rains | No | Area found with supply
Non-Outage | J.E.26.06.35504 | C001840040 | Stephen Taylor | St.Thomas | Completed | Load_577147 | Lysson - 410 | Jul 4, 2026 11:00am | Jul 4, 2026 11:01am | Jul 4, 2026 3:12pm | Jul 4, 2026 3:12pm | Jul 4, 2026 3:12pm | Jul 4, 2026 3:12pm | Jul 4, 2026 3:13pm | Jul 4, 2026 3:13pm |  |  | Fair | No | Customer meter socket defective customer advise to fix meter socket and contact back jps for connection
Non-Outage | J.E.26.06.38039 | C001840039 | Lancelot Brown | Hanover | Completed | Load_268987 | Orange Bay - 310 | Jul 4, 2026 10:53am | Jul 4, 2026 10:53am | Jul 4, 2026 1:17pm | Jul 4, 2026 3:33pm | Jul 4, 2026 4:35pm | Jul 4, 2026 4:35pm | Jul 4, 2026 4:38pm | Jul 4, 2026 4:38pm |  |  | Fair | No | Isolate 25kva no pole remake corroded dropleed joint used two pg clamps vl secondary 114-119-234 supply restore
Outage | J.E.26.07.02907 | C001840038 | Oshane Warren | Hanover | Completed | Load_256472 | Orange Bay - 310 | Jul 4, 2026 10:52am | Jul 4, 2026 10:54am | Jul 4, 2026 12:42pm | Jul 4, 2026 5:47pm | Jul 4, 2026 5:48pm | Jul 4, 2026 5:50pm | Jul 4, 2026 5:55pm | Jul 4, 2026 5:55pm |  |  | Fair | No | Replace 2amps xformer fuse and replace 5amps junction fuse
Outage | J.E.26.07.02851 | C001840035 | Roxroy Needham | St.Ann | Completed | Load_242214 | Cardiff Hall - 210 | Jul 4, 2026 10:38am | Jul 4, 2026 10:50am | Jul 4, 2026 11:29am | Jul 4, 2026 11:29am | Jul 4, 2026 12:01pm | Jul 4, 2026 12:33pm | Jul 4, 2026 12:29pm | Jul 4, 2026 12:29pm |  |  | Fair | No | Replace 1- 25 amp junction after line was patrol
Non-Outage | J.E.26.07.02409 | C001840034 | Floyd Taylor | Trelawny | Completed | Load_265828 | Duncans - 110 | Jul 4, 2026 10:23am | Jul 4, 2026 10:23am | Jul 4, 2026 12:23pm | Jul 4, 2026 1:55pm | Jul 4, 2026 2:41pm | Jul 4, 2026 3:21pm | Jul 4, 2026 3:23pm | Jul 4, 2026 3:23pm |  |  | Fair | No | Clean and remake joint at pole voltage readings left 109,107,218
Outage | J.E.26.07.02806 | C001840033 | Oshane Warren | Westmoreland | Completed | Load_257539 | Paradise - 210 | Jul 4, 2026 10:21am | Jul 4, 2026 10:23am | Jul 4, 2026 11:10am | Jul 4, 2026 11:10am | Jul 4, 2026 12:42pm | Jul 4, 2026 12:43pm | Jul 4, 2026 12:43pm | Jul 4, 2026 12:43pm |  |  | Fair | No | Check and find ok
Outage | J.E.26.07.02735 | C001840031 | Ryan Richards | Clarendon | Completed | Load_254405 | Parnassus - 210 | Jul 4, 2026 10:18am | Jul 4, 2026 10:20am | Jul 4, 2026 2:21pm | Jul 4, 2026 2:25pm | Jul 4, 2026 4:31pm | Jul 4, 2026 4:38pm | Jul 4, 2026 4:38pm | Jul 4, 2026 4:38pm |  |  | Fair | No | Area found with supply customer that made report also has supply at her premises
Non-Outage | J.E.26.07.02799 | C001840030 | Barnett Brown | null | Completed | null | null | Jul 4, 2026 10:15am | Jul 4, 2026 10:17am | Jul 4, 2026 4:28pm | Jul 4, 2026 4:28pm | Jul 4, 2026 4:29pm | Jul 4, 2026 4:29pm | Jul 4, 2026 4:31pm | Jul 4, 2026 4:31pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.02861 | C001840029 | Ryan Richards | Manchester | Completed | Load_294633 | Spur Tree - 310 | Jul 4, 2026 10:15am | Jul 4, 2026 10:18am | Jul 4, 2026 4:39pm | Jul 4, 2026 4:39pm | Jul 4, 2026 5:25pm | Jul 4, 2026 6:16pm | Jul 4, 2026 6:16pm | Jul 4, 2026 6:16pm |  |  | Fair | No | Customer found with out supply call center was contacted and they where able to reconnect meter customer are now with supply
Outage | J.E.26.07.02859 | C001840028 | Barnett Brown | Manchester | Completed | Load_269303 | Spur Tree - 310 | Jul 4, 2026 10:14am | Jul 4, 2026 10:17am | Jul 4, 2026 12:38pm | Jul 4, 2026 12:38pm | Jul 4, 2026 1:37pm | Jul 4, 2026 1:37pm | Jul 4, 2026 1:40pm | Jul 4, 2026 1:40pm | BrokenWire |  | Fair | No | Related to previous Cross keys call where tree was cut and wire splice and retention after 10 amp junction fuse was opened
Outage | J.E.26.07.02855 | C001840026 | Wayne Dillion | Manchester | Completed | Load_249866 | Spur Tree - 210 | Jul 4, 2026 10:07am | Jul 4, 2026 10:10am | Jul 4, 2026 10:15am | Jul 4, 2026 10:15am | Jul 4, 2026 10:15am | Jul 4, 2026 10:18am | Jul 4, 2026 10:18am | Jul 4, 2026 10:18am |  |  | Fair | No | Customer said supply was restored.
Outage | J.E.26.07.02856 | C001840025 | Andrew Powell | Manchester | Completed | Load_302753 | Spur Tree - 210 | Jul 4, 2026 10:07am | Jul 4, 2026 10:11am | Jul 4, 2026 10:20am | Jul 4, 2026 10:20am | Jul 4, 2026 10:20am | Jul 4, 2026 10:21am | Jul 4, 2026 10:21am | Jul 4, 2026 10:21am |  |  | Fair | No | Premises found okay customer stated that supply restored.
Outage | J.E.26.07.02857 | C001840027 | Wayne Dillion | Manchester | Completed | Load_269147 | Spur Tree - 210 | Jul 4, 2026 10:07am | Jul 4, 2026 10:10am | Jul 4, 2026 10:19am | Jul 4, 2026 1:43pm | Jul 4, 2026 1:43pm | Jul 4, 2026 1:46pm | Jul 4, 2026 1:47pm | Jul 4, 2026 1:47pm |  |  | Fair | No | Unable to locate and customer phone is not working.
Outage | J.E.26.07.02848 | C001840023 | Roxroy Needham | St.Ann | Completed | Load_238381 | Cardiff Hall - 210 | Jul 4, 2026 10:01am | Jul 4, 2026 10:02am | Jul 4, 2026 11:02am | Jul 4, 2026 11:02am | Jul 4, 2026 11:27am | Jul 4, 2026 11:27am | Jul 4, 2026 11:28am | Jul 4, 2026 11:28am |  |  | Fair | No | Not getting through customer on phone
Non-Outage | J.E.26.07.02835 | C001840022 | Andre Smith | KSAS | Completed | Load_267677 | Hunts Bay - 810 | Jul 4, 2026 9:58am | Jul 4, 2026 3:49pm | Jul 4, 2026 6:00pm | Jul 4, 2026 6:00pm | Jul 4, 2026 6:56pm | Jul 4, 2026 6:59pm | Jul 4, 2026 6:59pm | Jul 4, 2026 6:59pm | Fire |  | Fair | No | Premises found okay supply restored already
Outage | J.E.26.07.02791 | C001840021 | Wayne Dillion | Manchester | Completed | Load_240150 | Spur Tree - 210 | Jul 4, 2026 9:54am | Jul 4, 2026 10:01am | Jul 4, 2026 10:47am | Jul 4, 2026 10:48am | Jul 4, 2026 11:18am | Jul 4, 2026 12:40pm | Jul 4, 2026 12:48pm | Jul 4, 2026 12:48pm |  |  | Fair | No | Patrol and found one blown 20amp junction fuse at pole #045705. Replace same and restore supply okay.
Outage | J.E.26.07.02830 | C001840020 | Andrew Powell | Manchester | Completed | Load_254818 | Spur Tree - 210 | Jul 4, 2026 9:53am | Jul 4, 2026 10:03am | Jul 4, 2026 10:07am | Jul 4, 2026 10:07am | Jul 4, 2026 10:07am | Jul 4, 2026 10:08am | Jul 4, 2026 10:08am | Jul 4, 2026 10:08am |  |  | Fair | No | Premises found okay customer stated that supply restored.
Outage | J.E.26.07.02845 | C001840009 | Roxroy Needham | St.Ann | Completed | Load_245873 | Cardiff Hall - 210 | Jul 4, 2026 9:46am | Jul 4, 2026 9:48am | Jul 4, 2026 12:29pm | Jul 4, 2026 12:29pm | Jul 4, 2026 12:29pm | Jul 4, 2026 12:34pm | Jul 4, 2026 12:32pm | Jul 4, 2026 12:32pm |  |  | Fair | No | Replace 1- 25 amp junction after line was patrol
Non-Outage | J.E.26.04.05454 | C001840002 | Dwain Samuels | Westmoreland | Completed | Load_244638 | Paradise - 210 | Jul 4, 2026 9:21am | Jul 4, 2026 9:49am | Jul 4, 2026 9:53am | Jul 4, 2026 10:14am | Jul 4, 2026 10:14am | Jul 4, 2026 10:14am | Jul 4, 2026 10:16am | Jul 4, 2026 10:16am |  |  | Fair | No | Called got no answer. Need proper contact information an directions
Non-Outage | J.E.26.03.39113 | C001839996 | Dwain Samuels | Westmoreland | Completed | Load_263519 | Paradise - 210 | Jul 4, 2026 9:20am | Jul 4, 2026 9:21am | Jul 4, 2026 9:47am | Jul 4, 2026 10:40am | Jul 4, 2026 10:41am | Jul 4, 2026 10:45am | Jul 4, 2026 10:45am | Jul 4, 2026 10:45am |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.03.39113 | C001839999 | Dwain Samuels | Westmoreland | Completed | Load_263519 | Paradise - 210 | Jul 4, 2026 9:20am | Jul 4, 2026 9:21am | Jul 4, 2026 9:47am | Jul 4, 2026 10:46am | Jul 4, 2026 10:46am | Jul 4, 2026 10:47am | Jul 4, 2026 10:47am | Jul 4, 2026 10:47am |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.03.16934 | C001839991 | Dwain Samuels | Westmoreland | Completed | Load_292514 | Paradise - 110 | Jul 4, 2026 9:19am | Jul 4, 2026 9:21am | Jul 4, 2026 9:47am | Jul 4, 2026 11:08am | Jul 4, 2026 11:08am | Jul 4, 2026 11:15am | Jul 4, 2026 11:16am | Jul 4, 2026 11:16am |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.02.41381 | C001839987 | Dwain Samuels | Westmoreland | Completed | Load_258649 | Paradise - 210 | Jul 4, 2026 9:18am | Jul 4, 2026 9:22am | Jul 4, 2026 9:47am | Jul 4, 2026 10:53am | Jul 4, 2026 10:53am | Jul 4, 2026 11:04am | Jul 4, 2026 11:06am | Jul 4, 2026 11:06am |  |  | Fair | No | Corrosion found at 3 wire pole. Voltage check 90-91-181. Corrosion clear use 2 one bolt clamp.118-118-236
Non-Outage | J.E.26.01.13984 | C001839983 | Dwain Samuels | Westmoreland | Completed | Load_253896 | Paradise - 310 | Jul 4, 2026 9:17am | Jul 4, 2026 9:22am | Jul 4, 2026 9:47am | Jul 4, 2026 10:30am | Jul 4, 2026 10:30am | Jul 4, 2026 10:36am | Jul 4, 2026 10:38am | Jul 4, 2026 10:38am |  |  | Fair | No | Corrosion fount at 3 wire pole. Voltage check 115-0-115. Corrosion clear use 1 one bolt Clamp. Voltage check 115-116-231
Non-Outage | J.E.26.01.14276 | C001839984 | Dwain Samuels | Westmoreland | Completed | Load_260069 | Paradise - 310 | Jul 4, 2026 9:17am | Jul 4, 2026 9:22am | Jul 4, 2026 9:47am | Jul 4, 2026 10:04am | Jul 4, 2026 10:04am | Jul 4, 2026 10:12am | Jul 4, 2026 10:13am | Jul 4, 2026 10:13am |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.01.26128 | C001839985 | Dwain Samuels | Westmoreland | Completed | Load_238268 | Paradise - 210 | Jul 4, 2026 9:17am | Jul 4, 2026 9:22am | Jul 4, 2026 9:47am | Jul 4, 2026 9:56am | Jul 4, 2026 9:56am | Jul 4, 2026 9:58am | Jul 4, 2026 10:01am | Jul 4, 2026 10:01am |  |  | Fair | No | Corrosion found at 3 wire pot head. Voltage check 110-109-219. Corrosion clear use 2 one bolt clamp. Voltage check 115-115-230
Outage | J.E.26.07.02781 | C001839982 | Edward Royal | KSAS | Completed | Load_264287 | Duhaney - 310 | Jul 4, 2026 9:12am | Jul 4, 2026 9:13am | Jul 4, 2026 2:54pm | Jul 4, 2026 2:54pm | Jul 4, 2026 2:54pm | Jul 4, 2026 2:54pm | Jul 4, 2026 2:55pm | Jul 4, 2026 2:55pm |  |  | Fair | No | Premises found ok related to outage
Outage | J.E.26.07.02783 | C001839981 | Elvis Trowers | KSAS | Completed | Load_265307 | Duhaney - 310 | Jul 4, 2026 9:12am | Jul 4, 2026 3:14pm | Jul 4, 2026 4:02pm | Jul 4, 2026 4:02pm | Jul 4, 2026 4:47pm | Jul 4, 2026 4:50pm | Jul 4, 2026 4:50pm | Jul 4, 2026 4:50pm |  |  | Fair | Yes | Areas was checked and found ok, customers was also spoken with however they suggested that the power supply was restored.
Outage | J.E.26.07.02789 | C001839979 | Hopeton Henry | St.Thomas | Completed | Load_556320 | Good Year - 210 | Jul 4, 2026 9:04am | Jul 4, 2026 9:05am | Jul 4, 2026 10:02am | Jul 4, 2026 7:55pm | Jul 4, 2026 7:55pm | Jul 4, 2026 7:57pm | Jul 4, 2026 7:58pm | Jul 4, 2026 7:58pm |  |  | Fair | No | Reconnect service wire at pole 115-114-229 volts
Outage | J.E.26.07.02757 | C001839976 | Neville Spencer | Clarendon | Completed | Load_262299 | May Pen - 110 | Jul 4, 2026 8:47am | Jul 4, 2026 8:47am | Jul 4, 2026 12:47pm | Jul 4, 2026 12:47pm | Jul 4, 2026 12:47pm | Jul 4, 2026 12:47pm | Jul 4, 2026 12:52pm | Jul 4, 2026 12:52pm | BrokenWire |  | Fair | No | Open 25 kva at pole # 0106347 retention one of secondary phase Conductor used 1, preform supply restored..
Outage | J.E.26.07.02780 | C001839973 | Oshane Warren | Westmoreland | Completed | Load_261865 | Paradise - 110 | Jul 4, 2026 8:44am | Jul 4, 2026 8:46am | Jul 4, 2026 8:54am | Jul 4, 2026 8:54am | Jul 4, 2026 9:32am | Jul 4, 2026 9:32am | Jul 4, 2026 9:33am | Jul 4, 2026 9:33am |  |  | Fair | No | Unable to locate or contact customer
Outage | J.E.26.07.02779 | C001839972 | Andrew Powell | Manchester | Completed | Load_302593 | Spur Tree - 210 | Jul 4, 2026 8:41am | Jul 4, 2026 8:41am | Jul 4, 2026 8:47am | Jul 4, 2026 8:48am | Jul 4, 2026 9:22am | Jul 4, 2026 10:02am | Jul 4, 2026 10:06am | Jul 4, 2026 10:06am |  |  | Fair | No | Isolate and close 25 kva transformer circuit to splice and tension two pole span of broken secondary lower phase conductor and repair burnt off phase drop lead using 12 feet #4 pvc copper, two clamps and one automatic splicing sleeves, no pole number by switch location, restore supply okay.
Outage | J.E.26.07.01108 | C001839970 | Wayne Dillion | St.Elizabeth | Completed | Load_242242 | Maggotty - 210 | Jul 4, 2026 8:36am | Jul 4, 2026 8:40am | Jul 4, 2026 9:13am | Jul 4, 2026 9:13am | Jul 4, 2026 9:13am | Jul 4, 2026 9:16am | Jul 4, 2026 9:16am | Jul 4, 2026 9:16am | BrokenWire |  | Fair | No | This report keep sending to team over on over when contact the number provided the person said she didn’t make any report and don’t have an account with JPS
Outage | J.E.26.07.02773 | C001839968 | Wayne Dillion | St.Elizabeth | Completed | Load_264254 | Maggotty - 110 | Jul 4, 2026 8:35am | Jul 4, 2026 8:38am | Jul 4, 2026 1:48pm | Jul 4, 2026 1:48pm | Jul 4, 2026 1:48pm | Jul 4, 2026 1:50pm | Jul 4, 2026 1:50pm | Jul 4, 2026 1:50pm |  |  | Fair | No | Unable to locate and customer phone is not working.
Outage | J.E.26.07.02756 | C001839967 | Romeo Brissett | St.James | Completed | Load_241154 | Bogue - 510 | Jul 4, 2026 8:27am | Jul 4, 2026 8:28am | Jul 4, 2026 11:05am | Jul 4, 2026 11:05am | Jul 4, 2026 11:05am | Jul 4, 2026 11:01am | Jul 4, 2026 11:06am | Jul 4, 2026 11:06am |  |  | Fair | No | Hanover cal
Outage | J.E.26.07.02767 | C001839966 | Swon Miller | St.James | Completed | Load_245262 | Queens Drive - 710 | Jul 4, 2026 8:27am | Jul 4, 2026 8:27am | Jul 4, 2026 9:38am | Jul 4, 2026 9:38am | Jul 4, 2026 10:59am | Jul 4, 2026 11:19am | Jul 4, 2026 11:28am | Jul 4, 2026 11:28am |  |  | Fair | No | Check and found okay voltage found 115/114/232 voltage left 115/114/232
Outage | J.E.26.07.02768 | C001839965 | Romeo Brissett | St.James | Completed | Load_258453 | Bogue - 510 | Jul 4, 2026 8:26am | Jul 4, 2026 8:26am | Jul 4, 2026 10:09am | Jul 4, 2026 10:09am | Jul 4, 2026 10:09am | Jul 4, 2026 10:03am | Jul 4, 2026 10:10am | Jul 4, 2026 10:10am |  |  | Fair | No | Check and found ok
Non-Outage | J.E.26.07.01069 | C001839964 | Hopeton Henry | St.Thomas | Completed | Load_577170 | Good Year - 110 | Jul 4, 2026 8:23am | Jul 4, 2026 8:23am | Jul 4, 2026 10:02am | Jul 4, 2026 4:37pm | Jul 4, 2026 4:58pm | Jul 4, 2026 6:40pm | Jul 4, 2026 6:42pm | Jul 4, 2026 6:42pm |  |  | Fair | No | Internal problem, customer advised 120-120-193 P/ N 242-243-240 P/P
Non-Outage | J.E.26.07.00912 | C001839963 | Hopeton Henry | St.Thomas | Completed | Load_266032 | Good Year - 210 | Jul 4, 2026 8:22am | Jul 4, 2026 8:22am | Jul 4, 2026 10:02am | Jul 4, 2026 7:58pm | Jul 4, 2026 9:30pm | Jul 4, 2026 9:31pm | Jul 4, 2026 9:31pm | Jul 4, 2026 9:31pm |  |  | Fair | No | Internal problem, customer advised
Non-Outage | J.E.26.07.01546 | C001839962 | Hopeton Henry | St.Thomas | Completed | Load_246172 | Good Year - 110 | Jul 4, 2026 8:21am | Jul 4, 2026 8:21am | Jul 4, 2026 10:02am | Jul 4, 2026 2:29pm | Jul 4, 2026 2:53pm | Jul 4, 2026 12:59pm | Jul 4, 2026 2:59pm | Jul 4, 2026 2:59pm | Fire |  | Fair | No | Found ok , issue was resolved
Outage | J.E.26.07.02769 | C001839961 | Daniel Francis | St.Ann | Completed | Load_254549 | Roaring River - 210 | Jul 4, 2026 8:21am | Jul 4, 2026 8:22am | Jul 4, 2026 11:09am | Jul 4, 2026 11:09am | Jul 4, 2026 11:26am | Jul 4, 2026 11:43am | Jul 4, 2026 11:47am | Jul 4, 2026 11:47am |  |  | Fair | No | Wrapped joints at pothead pole private pole leaning unable to carry out repair
Non-Outage | J.E.26.07.01882 | C001839960 | Hopeton Henry | St.Thomas | Completed | Load_252007 | Good Year - 210 | Jul 4, 2026 8:20am | Jul 4, 2026 8:21am | Jul 4, 2026 10:02am | Jul 4, 2026 7:05pm | Jul 4, 2026 7:50pm | Jul 4, 2026 7:51pm | Jul 4, 2026 7:55pm | Jul 4, 2026 7:55pm |  |  | Fair | No | Customer not located
Non-Outage | J.E.26.07.02765 | C001839958 | Stephen Taylor | St.Thomas | Completed | Load_257874 | Lysson - 410 | Jul 4, 2026 8:20am | Jul 4, 2026 8:20am | Jul 4, 2026 2:50pm | Jul 4, 2026 2:50pm | Jul 4, 2026 3:04pm | Jul 4, 2026 3:04pm | Jul 4, 2026 3:08pm | Jul 4, 2026 3:08pm |  |  | Fair | No | Meter was defective and changed by a jps technician
Non-Outage | J.E.26.07.00560 | C001839956 | Tyrese Williams | St.Ann | Completed | Load_256369 | Roaring River - 210 | Jul 4, 2026 8:17am | Jul 4, 2026 8:18am | Jul 4, 2026 8:53am | Jul 4, 2026 1:26pm | Jul 4, 2026 1:39pm | Jul 4, 2026 1:40pm | Jul 4, 2026 1:40pm | Jul 4, 2026 1:40pm |  |  | Fair | No | Premises not found not getting customer on phone
Non-Outage | J.E.26.07.00567 | C001839957 | Tyrese Williams | St.Ann | Completed | Load_249631 | Roaring River - 210 | Jul 4, 2026 8:17am | Jul 4, 2026 8:18am | Jul 4, 2026 8:53am | Jul 4, 2026 12:57pm | Jul 4, 2026 1:23pm | Jul 4, 2026 1:24pm | Jul 4, 2026 1:25pm | Jul 4, 2026 1:25pm |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.06.39485 | C001839955 | Tyrese Williams | St.Ann | Completed | Load_555713 | Ocho Rios - 310 | Jul 4, 2026 8:16am | Jul 4, 2026 8:18am | Jul 4, 2026 8:53am | Jul 4, 2026 9:07am | Jul 4, 2026 12:08pm | Jul 4, 2026 12:55pm | Jul 4, 2026 12:56pm | Jul 4, 2026 12:56pm |  |  | Fair | No | Secondary line seen hanging low in bush, customer pothead neutral was corroded voltage now is 116/116/232
Non-Outage | J.E.26.07.00132 | C001839953 | Stephen Taylor | St.Thomas | Completed | Load_260487 | Lysson - 410 | Jul 4, 2026 8:11am | Jul 4, 2026 8:12am | Jul 4, 2026 10:26am | Jul 4, 2026 10:26am | Jul 4, 2026 10:56am | Jul 4, 2026 10:56am | Jul 4, 2026 10:57am | Jul 4, 2026 10:57am |  |  | Fair | No | Clean up single phase use 2 clamps customer is now okay reading 112,113,225
Non-Outage | J.E.26.07.02371 | C001839954 | Collin Robinson | Portland | Completed | Load_252574 | Port Antonio - 410 | Jul 4, 2026 8:11am | Jul 4, 2026 8:18am | Jul 4, 2026 12:50pm | Jul 4, 2026 12:50pm | Jul 4, 2026 1:27pm | Jul 4, 2026 1:36pm | Jul 4, 2026 1:36pm | Jul 4, 2026 1:36pm |  |  | Fair | No | Meter burn refer to field service Voltage reading 118 v 117v 235v
Outage | J.E.26.07.02560 | C001839951 | Collin Robinson | Portland | Completed | Load_259342 | Port Antonio - 410 | Jul 4, 2026 8:10am | Jul 4, 2026 8:10am | Jul 4, 2026 1:36pm | Jul 4, 2026 1:36pm | Jul 4, 2026 1:37pm | Jul 4, 2026 1:39pm | Jul 4, 2026 1:39pm | Jul 4, 2026 1:39pm |  |  | Fair | No | Unable to locate customer
Outage | J.E.26.07.02649 | C001839952 | Collin Robinson | Portland | Completed | Load_348300 | Port Antonio - 410 | Jul 4, 2026 8:10am | Jul 4, 2026 8:10am | Jul 4, 2026 11:06am | Jul 4, 2026 11:06am | Jul 4, 2026 12:35pm | Jul 4, 2026 12:50pm | Jul 4, 2026 12:50pm | Jul 4, 2026 12:50pm |  |  | Fair | No | Cut tree limb from near primary conductor and replace 8 amps junction fuse at pole 556692
Non-Outage | J.E.26.06.34777 | C001839949 | Stephen Taylor | St.Thomas | Completed | Load_335584 | Lysson - 410 | Jul 4, 2026 8:08am | Jul 4, 2026 8:10am | Jul 4, 2026 8:35am | Jul 4, 2026 8:35am | Jul 4, 2026 8:36am | Jul 4, 2026 8:36am | Jul 4, 2026 8:36am | Jul 4, 2026 8:36am |  |  | Fair | No | Call to customer and customer say that power was restored from last night
Non-Outage | J.E.26.06.35182 | C001839950 | Stephen Taylor | St.Thomas | Completed | Load_269505 | Lysson - 410 | Jul 4, 2026 8:08am | Jul 4, 2026 8:08am | Jul 4, 2026 11:46am | Jul 4, 2026 11:46am | Jul 4, 2026 12:17pm | Jul 4, 2026 12:17pm | Jul 4, 2026 12:18pm | Jul 4, 2026 12:18pm |  |  | Fair | No | Premise found okay reading 111,112,224
Non-Outage | J.E.26.07.01237 | C001839948 | Stephen Taylor | St.Thomas | Completed | Load_238093 | Lysson - 410 | Jul 4, 2026 8:07am | Jul 4, 2026 8:07am | Jul 4, 2026 3:22pm | Jul 4, 2026 3:22pm | Jul 4, 2026 3:22pm | Jul 4, 2026 3:22pm | Jul 4, 2026 3:24pm | Jul 4, 2026 3:24pm |  |  | Fair | No | Clean up single phase use 2 clamps customer is now okay
Non-Outage | J.E.26.06.38518 | C001839947 | Stephen Taylor | St.Thomas | Completed | Load_237738 | Lysson - 410 | Jul 4, 2026 8:06am | Jul 4, 2026 8:06am | Jul 4, 2026 3:25pm | Jul 4, 2026 3:25pm | Jul 4, 2026 3:25pm | Jul 4, 2026 3:26pm | Jul 4, 2026 3:26pm | Jul 4, 2026 3:26pm |  |  | Fair | No | Need more information a lot of call to customer no one answered the phone
Non-Outage | J.E.26.06.39053 | C001839946 | Donald Cunningham | St.Catherine | Completed | Load_568126 | Rhodens Pen - 210 | Jul 4, 2026 8:03am | Jul 4, 2026 8:04am | Jul 4, 2026 9:45am | Jul 4, 2026 9:45am | Jul 4, 2026 11:17am | Jul 4, 2026 11:18am | Jul 4, 2026 11:30am | Jul 4, 2026 11:30am |  |  | Fair | No | Brunt and defective meter need to replace refer to field service
Non-Outage | J.E.26.07.00552 | C001839944 | Donald Cunningham | St.Catherine | Completed | Load_266925 | Rhodens Pen - 410 | Jul 4, 2026 8:03am | Jul 4, 2026 8:04am | Jul 4, 2026 11:31am | Jul 4, 2026 11:31am | Jul 4, 2026 1:49pm | Jul 4, 2026 1:51pm | Jul 4, 2026 1:59pm | Jul 4, 2026 1:59pm | LeaningPole |  | Fair | No | Pole need to dig and straighten temporary work was done T /A construction single phase primary and secondary refer to maintenance
Non-Outage | J.E.26.07.02264 | C001839945 | Donald Cunningham | St.Catherine | Completed | Load_1000336 | Tredegar - 210 | Jul 4, 2026 8:03am | Jul 4, 2026 8:04am | Jul 4, 2026 9:08am | Jul 4, 2026 9:08am | Jul 4, 2026 9:39am | Jul 4, 2026 9:44am | Jul 4, 2026 9:44am | Jul 4, 2026 9:44am |  |  | Fair | No | Premises not located customer not reachable
Non-Outage | J.E.26.07.02126 | C001839942 | Tajay Bernard | Hanover | Completed | Load_243282 | Orange Bay - 210 | Jul 4, 2026 8:02am | Jul 4, 2026 8:02am | Jul 4, 2026 12:31pm | Jul 4, 2026 12:31pm | Jul 4, 2026 1:01pm | Jul 4, 2026 1:04pm | Jul 4, 2026 1:04pm | Jul 4, 2026 1:04pm |  |  | Fair | No | Area check and found okay unable to locate customer on premises multiple phone to customer number went unanswered
Non-Outage | J.E.26.07.02143 | C001839940 | Wan Carlos Scarlett | Portmore | Completed | Load_258650 | Naggo Head - 610 | Jul 4, 2026 8:00am | Jul 4, 2026 8:00am | Jul 4, 2026 1:34pm | Jul 4, 2026 1:34pm | Jul 4, 2026 2:35pm | Jul 4, 2026 2:59pm | Jul 4, 2026 3:02pm | Jul 4, 2026 3:02pm | BrokenWire |  | Fair | No | Found customer 3 wire service at pothead with the neutral broken off use 2 Penn union and use one bolt clamps at service wire phase and neutral readings 115-114-230
Non-Outage | J.E.26.07.02203 | C001839939 | Hartley Chin | Clarendon | Completed | Load_247079 | Parnassus - 210 | Jul 4, 2026 7:59am | Jul 4, 2026 8:00am | Jul 4, 2026 11:44am | Jul 4, 2026 11:44am | Jul 4, 2026 11:45am | Jul 4, 2026 11:45am | Jul 4, 2026 11:45am | Jul 4, 2026 11:45am | BrokenPole |  | Fair | No | Found okay … issue was resolved last night (maintenance crew) …
Non-Outage | J.E.26.07.01778 | C001839938 | Neville Spencer | Clarendon | Completed | Load_262299 | May Pen - 110 | Jul 4, 2026 7:58am | Jul 4, 2026 7:59am | Jul 4, 2026 11:17am | Jul 4, 2026 11:17am | Jul 4, 2026 11:55am | Jul 4, 2026 12:46pm | Jul 4, 2026 12:46pm | Jul 4, 2026 12:46pm |  |  | Fair | No | Open 25 kva xmfr at pole # 0106347 retention one span of secondary phase Conductor used 1, 2/0 preform supply restored.
Non-Outage | J.E.26.07.01979 | C001839937 | Neville Spencer | Clarendon | Completed | Load_255751 | May Pen - 110 | Jul 4, 2026 7:58am | Jul 4, 2026 7:59am | Jul 4, 2026 8:41am | Jul 4, 2026 8:41am | Jul 4, 2026 10:28am | Jul 4, 2026 10:28am | Jul 4, 2026 11:16am | Jul 4, 2026 11:16am |  |  | Fair | No | Found defective 3.wire meter socket voltage reading 114+116 231 customer advised.
Outage | J.E.26.07.00208 | C001839935 | Richard Samuda | Manchester | Completed | Load_254867 | Spur Tree - 210 | Jul 4, 2026 7:54am | Jul 5, 2026 8:07am | Jul 5, 2026 9:18am | Jul 5, 2026 9:18am | Jul 5, 2026 9:38am | Jul 5, 2026 9:38am | Jul 5, 2026 9:39am | Jul 5, 2026 9:39am |  |  | Fair | No | Customer say supply was restored
Outage | J.E.26.07.02748 | C001839936 | Richard Nicholas | St.Catherine | Completed | Load_247477 | Tredegar - 410 | Jul 4, 2026 7:54am | Jul 4, 2026 7:55am | Jul 4, 2026 10:22am | Jul 4, 2026 10:22am | Jul 4, 2026 11:10am | Jul 4, 2026 11:36am | Jul 4, 2026 11:38am | Jul 4, 2026 11:38am |  |  | Fair | No | Meter seems to install in wrong meter socket,please refer to the field service department.
Outage | J.E.26.07.02082 | C001839933 | Wayne Dillion | St.Elizabeth | Completed | Load_261527 | Maggotty - 110 | Jul 4, 2026 7:53am | Jul 4, 2026 7:54am | Jul 4, 2026 4:11pm | Jul 4, 2026 4:11pm | Jul 4, 2026 5:03pm | Jul 4, 2026 5:03pm | Jul 4, 2026 5:08pm | Jul 4, 2026 5:08pm |  |  | Rains | No | Supply check and found no service wire. Connect same using 65ft of #6 triplex service wire, 3 clamps and 3 linkets. Supply leave working okay reading 112v, 113v and cross phase 225volts.
Outage | J.E.26.07.02382 | C001839932 | Wan Carlos Scarlett | Portmore | Completed | Load_247746 | Naggo Head - 510 | Jul 4, 2026 7:52am | Jul 4, 2026 7:53am | Jul 4, 2026 8:16am | Jul 4, 2026 10:18am | Jul 4, 2026 10:46am | Jul 4, 2026 11:57am | Jul 4, 2026 11:59am | Jul 4, 2026 11:59am |  |  | Fair | No | Found customer 3 wire service at pothead with one of the phase broken off use one bolt clamp at open secondary line phase readings 116-117-234
Outage | J.E.26.07.02716 | C001839929 | Wan Carlos Scarlett | Portmore | Completed | Load_258707 | Naggo Head - 510 | Jul 4, 2026 7:52am | Jul 4, 2026 7:53am | Jul 4, 2026 8:17am | Jul 4, 2026 8:17am | Jul 4, 2026 9:35am | Jul 4, 2026 10:17am | Jul 4, 2026 10:18am | Jul 4, 2026 10:18am |  |  | Fair | No | Found customer 3 wire service at pole with one of the phase broken off use 3 one bolt clamps at open secondary line readings 115-116-231
Outage | J.E.26.07.02739 | C001839931 | Wan Carlos Scarlett | Portmore | Completed | Load_239358 | Naggo Head - 510 | Jul 4, 2026 7:52am | Jul 4, 2026 7:53am | Jul 4, 2026 11:59am | Jul 4, 2026 11:59am | Jul 4, 2026 11:59am | Jul 4, 2026 12:25pm | Jul 4, 2026 12:26pm | Jul 4, 2026 12:26pm |  |  | Fair | No | Found customer 3 wire service at pole with bout phase burn off use 2 one bolt clamps at open secondary line phase readings 117-118-236
Non-Outage | J.E.26.07.02520 | C001839928 | Stephen Taylor | St.Thomas | Completed | Load_335584 | Lysson - 410 | Jul 4, 2026 7:51am | Jul 4, 2026 7:51am | Jul 4, 2026 8:33am | Jul 4, 2026 8:33am | Jul 4, 2026 8:33am | Jul 4, 2026 8:34am | Jul 4, 2026 8:35am | Jul 4, 2026 8:35am |  |  | Fair | No | Call to customer and customer say that power was restored from last night
Non-Outage | J.E.26.07.01487 | C001839924 | Milton Charlton | KSAN | Completed | Load_264476 | Hope - 410 | Jul 4, 2026 7:50am | Jul 4, 2026 7:51am | Jul 4, 2026 11:19am | Jul 4, 2026 11:19am | Jul 4, 2026 11:30am | Jul 4, 2026 11:30am | Jul 4, 2026 11:39am | Jul 4, 2026 11:39am |  |  | Fair | No | Found okay upon arrival readings at the meter 118-119-238 volts. Customer problem is meter #2451918 on the display screen is showing error 5. Refresh to field service.
Non-Outage | J.E.26.07.02688 | C001839923 | Elvis Trowers | KSAN | Completed | Load_245979 | West Kings House - 210 | Jul 4, 2026 7:50am | Jul 4, 2026 7:51am | Jul 4, 2026 11:23am | Jul 4, 2026 11:23am | Jul 4, 2026 12:19pm | Jul 4, 2026 12:23pm | Jul 4, 2026 12:23pm | Jul 4, 2026 12:23pm |  |  | Fair | Yes | Premises checked and found okay upon arrival, customer was also spoken with however he said that the power supply was normalized earlier this morning.
Outage | J.E.26.07.02639 | C001839925 | Hartley Chin | Clarendon | Completed | Load_266723 | Parnassus - 210 | Jul 4, 2026 7:50am | Jul 4, 2026 7:50am | Jul 4, 2026 9:32am | Jul 4, 2026 9:40am | Jul 4, 2026 9:40am | Jul 4, 2026 9:40am | Jul 4, 2026 9:42am | Jul 4, 2026 9:42am |  |  | Fair | No | Found 1 of 3 junction blown (25 amp) no pole # , line patrolled and found okay , junction refused…
Non-Outage | J.E.26.07.01074 | C001839921 | Elvis Trowers | KSAN | Completed | Load_249030 | West Kings House - 410 | Jul 4, 2026 7:49am | Jul 4, 2026 7:51am | Jul 4, 2026 9:01am | Jul 4, 2026 9:01am | Jul 4, 2026 9:39am | Jul 4, 2026 10:48am | Jul 4, 2026 10:48am | Jul 4, 2026 10:48am | LowHangingWires |  | Fair | Yes | Splice and reconnect broken #6 triplex with about 10’ foot of wire and 3 one bolt clamps and a 3 wire meter also.
Outage | J.E.26.07.02723 | C001839922 | Hartley Chin | Clarendon | Completed | Load_251474 | Parnassus - 210 | Jul 4, 2026 7:49am | Jul 4, 2026 7:50am | Jul 4, 2026 8:07am | Jul 4, 2026 9:42am | Jul 4, 2026 11:08am | Jul 4, 2026 11:35am | Jul 4, 2026 11:40am | Jul 4, 2026 11:40am |  |  | Fair | No | Found 1 of 3 blown 40 amp junction fuse @ pole # 0177669 line patrolled and found okay , junction refused…
Outage | J.E.26.07.02729 | C001839920 | Hartley Chin | Clarendon | Completed | Load_257573 | Parnassus - 210 | Jul 4, 2026 7:49am | Jul 4, 2026 7:50am | Jul 4, 2026 8:06am | Jul 4, 2026 11:42am | Jul 4, 2026 11:42am | Jul 4, 2026 11:43am | Jul 4, 2026 11:43am | Jul 4, 2026 11:43am |  |  | Fair | No | Call related to job # 02723 …
Outage | J.E.26.07.02590 | C001839917 | Wayne Dillion | St.Elizabeth | Completed | Load_257015 | Maggotty - 110 | Jul 4, 2026 7:48am | Jul 4, 2026 7:54am | Jul 4, 2026 12:49pm | Jul 4, 2026 12:49pm | Jul 4, 2026 1:12pm | Jul 4, 2026 1:38pm | Jul 4, 2026 1:43pm | Jul 4, 2026 1:43pm |  |  | Fair | No | Supply check and found corrosion at pot head. Repair same using 1 clamp and 2 linkets. Supply leave working okay reading 114v, 119v and cross phase 233volts.
Outage | J.E.26.07.02627 | C001839916 | Wayne Dillion | St.Elizabeth | Completed | Load_265310 | Maggotty - 110 | Jul 4, 2026 7:48am | Jul 4, 2026 7:54am | Jul 4, 2026 3:15pm | Jul 4, 2026 3:15pm | Jul 4, 2026 3:15pm | Jul 4, 2026 4:07pm | Jul 4, 2026 4:10pm | Jul 4, 2026 4:10pm |  |  | Rains | No | Supply check and found no service wire. Connect same using 30ft of #6 triplex service wire, 3 linkets and 3 clamps. Supply leave working okay reading 114v, 115v and cross phase 229volts.
Outage | J.E.26.07.02742 | C001839918 | Roxroy Needham | St.Ann | Completed | Load_244049 | Cardiff Hall - 310 | Jul 4, 2026 7:48am | Jul 4, 2026 7:52am | Jul 4, 2026 8:49am | Jul 4, 2026 8:49am | Jul 4, 2026 10:26am | Jul 4, 2026 10:58am | Jul 4, 2026 10:57am | Jul 4, 2026 10:57am |  |  | Fair | No | Separate switch bottom from transformer pole and replace 1- 3 amp for a 25 KVA transformer and 1- 8 amp junction fuse voltage left 116,113,229
Non-Outage | J.E.26.07.00633 | C001839914 | Rusean Allen | null | Completed | null | null | Jul 4, 2026 7:46am | Jul 4, 2026 7:46am | Jul 4, 2026 9:16am | Jul 4, 2026 9:16am | Jul 4, 2026 11:30am | Jul 4, 2026 11:31am | Jul 4, 2026 11:31am | Jul 4, 2026 11:31am | Fire |  | Fair | No | Not found
Non-Outage | J.E.26.07.00668 | C001839915 | Rusean Allen | KSAS | Completed | Load_251064 | Rockfort - 210 | Jul 4, 2026 7:46am | Jul 4, 2026 7:46am | Jul 4, 2026 12:09pm | Jul 4, 2026 12:09pm | Jul 4, 2026 12:35pm | Jul 4, 2026 12:37pm | Jul 4, 2026 12:37pm | Jul 4, 2026 12:37pm | Fire |  | Fair | No | Excessive illegal connections needs to be removed.
Non-Outage | J.E.26.07.02620 | C001839913 | Cliton Henry | null | Completed | null | null | Jul 4, 2026 7:45am | Jul 4, 2026 7:47am | Jul 4, 2026 3:08pm | Jul 4, 2026 3:10pm | Jul 4, 2026 3:10pm | Jul 4, 2026 3:12pm | Jul 4, 2026 3:14pm | Jul 4, 2026 3:14pm | Fire |  | Fair | No | Supply restored, related to outage #02604.
Outage | J.E.26.07.02613 | C001839911 | Cliton Henry | St.Mary | Completed | Load_250803 | Blackstonedge - 110 | Jul 4, 2026 7:45am | Jul 4, 2026 7:45am | Jul 4, 2026 3:04pm | Jul 4, 2026 3:04pm | Jul 4, 2026 3:04pm | Jul 4, 2026 3:07pm | Jul 4, 2026 3:08pm | Jul 4, 2026 3:08pm |  |  | Fair | No | A broken 35–C4 DV pole with secondary found on White Spring Road.A secondary jumper was open at pole #0177024. Kindly refer to St.Mary operations for a pole replacement urgently.
Non-Outage | J.E.26.07.00519 | C001839909 | Rusean Allen | null | Completed | null | null | Jul 4, 2026 7:44am | Jul 4, 2026 7:45am | Jul 4, 2026 11:57am | Jul 4, 2026 11:57am | Jul 4, 2026 11:57am | Jul 4, 2026 11:58am | Jul 4, 2026 11:58am | Jul 4, 2026 11:58am | BrokenPole |  | Fair | No | Not found
Non-Outage | J.E.26.07.02352 | C001839908 | Rusean Allen | null | Completed | null | null | Jul 4, 2026 7:44am | Jul 4, 2026 7:45am | Jul 4, 2026 11:57am | Jul 4, 2026 12:38pm | Jul 4, 2026 1:52pm | Jul 4, 2026 1:53pm | Jul 4, 2026 1:53pm | Jul 4, 2026 1:53pm | BrokenPole |  | Fair | No | Not found
Outage | J.E.26.07.02741 | C001839910 | Lancelot Brown | Hanover | Completed | Load_241495 | Orange Bay - 310 | Jul 4, 2026 7:44am | Jul 4, 2026 7:47am | Jul 4, 2026 8:17am | Jul 4, 2026 10:11am | Jul 4, 2026 12:29pm | Jul 4, 2026 1:15pm | Jul 4, 2026 1:16pm | Jul 4, 2026 1:16pm |  |  | Rains | No | Check voltage at transformer dropleed found 114-114-228 also voltage at pothead 113-114-227 cannot get to check voltage at meter point premises is lock customer need to get their electrician and check meter socket please pass on to Digicel personnel
Outage | J.E.26.07.02595 | C001839907 | Elvis Trowers | KSAN | Completed | Load_239696 | Constant Spring - 410 | Jul 4, 2026 7:43am | Jul 4, 2026 7:49am | Jul 4, 2026 12:26pm | Jul 4, 2026 12:26pm | Jul 4, 2026 12:49pm | Jul 4, 2026 2:04pm | Jul 4, 2026 2:04pm | Jul 4, 2026 2:04pm |  |  | Rains | Yes | Customer was found having fluctuating voltage when checked and corroded joints were found at pole and pat head, 3 linketts was replaced with with 3 one bolt clamps, voltage when checked was left at 119+120=239.
Non-Outage | J.E.26.07.02435 | C001839905 | Marlon Brown | Trelawny | Completed | Load_292238 | Greenwood - 210 | Jul 4, 2026 7:42am | Jul 4, 2026 8:05am | Jul 4, 2026 8:28am | Jul 4, 2026 8:28am | Jul 4, 2026 8:28am | Jul 4, 2026 8:30am | Jul 4, 2026 8:30am | Jul 4, 2026 8:30am |  |  | Fair | No | Fixed on the 3rd of July associated with call number 2564.
Outage | J.E.26.07.01900 | C001839904 | Edward Royal | KSAN | Completed | null | null | Jul 4, 2026 7:42am | Jul 4, 2026 7:43am | Jul 4, 2026 2:53pm | Jul 4, 2026 2:53pm | Jul 4, 2026 2:53pm | Jul 4, 2026 2:54pm | Jul 4, 2026 2:54pm | Jul 4, 2026 2:54pm | BrokenWire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards |  | Fair | No | Premises found ok related to outage
Non-Outage | J.E.26.07.02218 | C001839902 | Romaine Roberts | St.Mary | Completed | Load_244039 | Highgate - 210 | Jul 4, 2026 7:39am | Jul 4, 2026 7:42am | Jul 4, 2026 9:53am | Jul 4, 2026 9:53am | Jul 4, 2026 10:47am | Jul 4, 2026 10:48am | Jul 4, 2026 10:48am | Jul 4, 2026 10:48am | LeaningPole |  | Fair | No | Found ok caller said this call was a long time call
Non-Outage | J.E.26.07.02432 | C001839901 | Marlon Brown | Trelawny | Completed | Load_292238 | Greenwood - 210 | Jul 4, 2026 7:39am | Jul 4, 2026 8:05am | Jul 4, 2026 8:30am | Jul 4, 2026 8:30am | Jul 4, 2026 8:30am | Jul 4, 2026 8:30am | Jul 4, 2026 8:30am | Jul 4, 2026 8:30am |  |  | Fair | No | Associated with call number 2564.
Outage | J.E.26.07.02345 | C001839895 | Ricky Hall | St.Catherine | Completed | Load_248047 | New Michelton - 210 | Jul 4, 2026 7:35am | Jul 4, 2026 7:36am | Jul 4, 2026 4:03pm | Jul 4, 2026 5:20pm | Jul 4, 2026 5:32pm | Jul 4, 2026 5:33pm | Jul 4, 2026 5:33pm | Jul 4, 2026 5:33pm |  |  | Rains | No | Area found with supply
Non-Outage | J.E.26.07.00583 | C001839890 | Daniel Francis | St.Ann | Completed | Load_250885 | Ocho Rios - 410 | Jul 4, 2026 7:33am | Jul 4, 2026 8:17am | Jul 4, 2026 11:57am | Jul 4, 2026 11:57am | Jul 4, 2026 12:55pm | Jul 4, 2026 12:51pm | Jul 4, 2026 12:56pm | Jul 4, 2026 12:56pm |  |  | Fair | No | Found okay
Non-Outage | J.E.26.07.02400 | C001839891 | Roxroy Needham | St.Ann | Completed | Load_250632 | Cardiff Hall - 310 | Jul 4, 2026 7:33am | Jul 4, 2026 7:44am | Jul 4, 2026 10:57am | Jul 4, 2026 10:57am | Jul 4, 2026 11:00am | Jul 4, 2026 11:01am | Jul 4, 2026 11:01am | Jul 4, 2026 11:01am |  |  | Fair | No | Customer issue was resolved
Outage | J.E.26.07.02701 | C001839892 | Ricky Hall | St.Catherine | Completed | Load_253833 | New Michelton - 210 | Jul 4, 2026 7:33am | Jul 4, 2026 7:34am | Jul 4, 2026 8:11am | Jul 4, 2026 8:41am | Jul 4, 2026 10:21am | Jul 4, 2026 10:45am | Jul 4, 2026 10:45am | Jul 4, 2026 10:45am |  |  | Rains | No | Found and replaced blown 65 amps junction fuse
Outage | J.E.26.07.01307 | C001839887 | Lancelot Brown | St.James | Completed | Load_259607 | Bogue - 510 | Jul 4, 2026 7:31am | Jul 4, 2026 12:13pm | Jul 4, 2026 1:17pm | Jul 5, 2026 4:12pm | Jul 5, 2026 4:12pm | Jul 5, 2026 5:40pm | Jul 5, 2026 5:41pm | Jul 5, 2026 5:41pm |  |  | Fair | No | Remake corroded joint at pothead also drop and splice and retention triplex service nutral used twenty feet #6 triplex three connectors vl at meter socket 114-115-230 supply restore
Non-Outage | J.E.26.07.00935 | C001839886 | Christopher Edwards | null | Completed | null | null | Jul 4, 2026 7:30am | Jul 4, 2026 7:31am | Jul 4, 2026 12:55pm | Jul 4, 2026 12:55pm | Jul 4, 2026 1:14pm | Jul 4, 2026 2:32pm | Jul 4, 2026 2:42pm | Jul 4, 2026 2:42pm | BrokenWire |  | Rains | No | Check and found okNo broken wire found at location
Non-Outage | J.E.26.07.01631 | C001839884 | Tajay Bernard | Hanover | Completed | Load_250960 | Orange Bay - 310 | Jul 4, 2026 7:29am | Jul 4, 2026 7:29am | Jul 4, 2026 7:37am | Jul 4, 2026 7:37am | Jul 4, 2026 8:39am | Jul 4, 2026 9:28am | Jul 4, 2026 9:32am | Jul 4, 2026 9:32am |  |  | Fair | No | Replace 100ft of #6 triplex wire use 4 clamps voltage readings 113/113/226Cause ( service wire was defective resulting fire on pole)
Outage | J.E.26.07.01627 | C001839882 | Tajay Bernard | Hanover | Completed | Load_250960 | Orange Bay - 310 | Jul 4, 2026 7:29am | Jul 4, 2026 7:30am | Jul 4, 2026 9:33am | Jul 4, 2026 9:33am | Jul 4, 2026 9:33am | Jul 4, 2026 9:34am | Jul 4, 2026 9:34am | Jul 4, 2026 9:34am | Fire |  | Fair | No | Related to previous call job number 01631
Outage | J.E.26.07.02566 | C001839883 | Christopher Edwards | KSAN | Completed | Load_257180 | Constant Spring - 410 | Jul 4, 2026 7:29am | Jul 4, 2026 7:29am | Jul 4, 2026 8:15am | Jul 4, 2026 9:35am | Jul 4, 2026 11:24am | Jul 4, 2026 12:54pm | Jul 4, 2026 12:55pm | Jul 4, 2026 12:55pm |  |  | Fair | No | Isolate 25 kva transformer to splice and retention broken open secondary neutral Using :80ft #2 AA conductor (3) one bolt clamps (1) #2 preform Also clear bamboo off secondary lines
Outage | J.E.26.07.02509 | C001839880 | Lancelot Brown | Hanover | Completed | Load_267429 | Orange Bay - 310 | Jul 4, 2026 7:24am | Jul 4, 2026 7:28am | Jul 4, 2026 8:17am | Jul 4, 2026 8:17am | Jul 4, 2026 10:08am | Jul 4, 2026 10:09am | Jul 4, 2026 10:10am | Jul 4, 2026 10:10am |  |  | Fair | No | Check and found area ok supply restore
Outage | J.E.26.07.02608 | C001839881 | Tajay Bernard | Hanover | Completed | Load_246605 | Orange Bay - 210 | Jul 4, 2026 7:24am | Jul 4, 2026 7:25am | Jul 4, 2026 9:36am | Jul 4, 2026 9:37am | Jul 4, 2026 10:14am | Jul 4, 2026 11:33am | Jul 4, 2026 11:35am | Jul 4, 2026 11:35am |  |  | Fair | No | Check and found 3 30amp junction fuse blown, replaced a defective lighting arrestor and 2 drop out switch. Power has not restored to the premises due (to suspecting defective pad mount transformer)
Outage | J.E.26.07.01517 | C001839878 | Damion Reid | Manchester | Completed | Load_250282 | Kendal - 210 | Jul 4, 2026 7:22am | Jul 4, 2026 7:34am | Jul 4, 2026 1:31pm | Jul 4, 2026 1:31pm | Jul 4, 2026 1:33pm | Jul 4, 2026 2:59pm | Jul 4, 2026 3:00pm | Jul 4, 2026 3:00pm | Fire |  | Fair | No | Premises found ok
Outage | J.E.26.07.01679 | C001839877 | Damion Reid | Manchester | Completed | Load_239588 | Kendal - 310 | Jul 4, 2026 7:22am | Jul 4, 2026 7:34am | Jul 4, 2026 8:28am | Jul 4, 2026 8:29am | Jul 4, 2026 10:49am | Jul 4, 2026 11:32am | Jul 4, 2026 11:33am | Jul 4, 2026 11:33am |  |  | Fair | No | Unable to contact or locate customer
Outage | J.E.26.07.02418 | C001839874 | Swon Miller | St.James | Completed | Load_266361 | Bogue - 610 | Jul 4, 2026 7:22am | Jul 4, 2026 7:22am | Jul 4, 2026 7:31am | Jul 4, 2026 7:31am | Jul 4, 2026 8:09am | Jul 29, 2026 8:18am | Jul 4, 2026 8:19am | Jul 4, 2026 8:19am |  |  | Fair | No | Check and found okay customer states that power supply was restored around 10:00 last night voltage found 115/115/231 voltage left 115/115/231
Outage | J.E.26.07.02313 | C001839873 | Damion Reid | Manchester | Completed | Load_257714 | Kendal - 210 | Jul 4, 2026 7:21am | Jul 4, 2026 7:34am | Jul 4, 2026 11:33am | Jul 4, 2026 11:33am | Jul 4, 2026 12:40pm | Jul 4, 2026 1:08pm | Jul 4, 2026 1:12pm | Jul 4, 2026 1:12pm |  |  | Fair | No | Remade corroded phase at pothead and at secondary pole for 3 wire service using one 1 bolt clamp and one pen union voltage reading at meter socket phase to neutral 114v—115v access phase 231v
Outage | J.E.26.07.02617 | C001839871 | Swon Miller | St.James | Completed | Load_288441 | Queens Drive - 310 | Jul 4, 2026 7:20am | Jul 4, 2026 7:20am | Jul 4, 2026 8:53am | Jul 4, 2026 8:53am | Jul 4, 2026 9:24am | Jul 21, 2026 9:34am | Jul 4, 2026 9:34am | Jul 4, 2026 9:34am |  |  | Fair | No | Check and found area okay unable to locate customer calls to customer went unanswered
Outage | J.E.26.07.02625 | C001839870 | Romeo Brissett | St.James | Completed | Load_302411 | Bogue - 610 | Jul 4, 2026 7:19am | Jul 4, 2026 7:20am | Jul 4, 2026 7:32am | Jul 4, 2026 7:32am | Jul 4, 2026 8:25am | Jul 4, 2026 8:35am | Jul 4, 2026 8:39am | Jul 4, 2026 8:39am |  |  | Fair | No | Unable to locate customer, location was visited resident isn’t familiar with customer name.
Outage | J.E.26.07.02532 | C001839860 | Horace Malcolm | St.James | Completed | Load_244718 | Bogue - 410 | Jul 4, 2026 6:29am | Jul 4, 2026 7:10am | Jul 4, 2026 8:18am | Jul 4, 2026 8:18am | Jul 4, 2026 8:18am | Jul 4, 2026 9:49am | Jul 4, 2026 9:49am | Jul 4, 2026 9:49am |  |  | Fair | No | Found one 30amp junction switch bottom wire burnt off from three phase primary line isolate (3) 30amp junction fuse to repair wire used 2ft #2 copper wire and one clamp voltage 117-119-208-234
Outage | J.E.26.07.02709 | C001839783 | Daniel Francis | St.Ann | Completed | Load_239757 | Roaring River - 410 | Jul 4, 2026 6:03am | Jul 4, 2026 7:30am | Jul 4, 2026 9:01am | Jul 4, 2026 9:01am | Jul 4, 2026 9:17am | Jul 4, 2026 9:47am | Jul 4, 2026 9:54am | Jul 4, 2026 9:54am |  |  | Fair | No | Found junction blown at pole #0056147 also further patrol and found 25kva transformer defective at 0056144
Outage | J.E.26.07.02666 | C001839782 | Rusean Allen | KSAS | Completed | Load_243699 | Rockfort - 210 | Jul 4, 2026 5:57am | Jul 4, 2026 7:46am | Jul 4, 2026 11:43am | Jul 4, 2026 11:43am | Jul 4, 2026 11:54am | Jul 4, 2026 11:56am | Jul 4, 2026 11:56am | Jul 4, 2026 11:56am |  |  | Fair | No | Premises locked
Outage | J.E.26.07.02696 | C001839781 | Daniel Francis | St.Ann | Completed | Load_264877 | Roaring River - 410 | Jul 4, 2026 5:19am | Jul 4, 2026 7:31am | Jul 4, 2026 8:26am | Jul 4, 2026 8:26am | Jul 4, 2026 8:26am | Jul 4, 2026 8:49am | Jul 4, 2026 9:01am | Jul 4, 2026 9:01am |  |  | Fair | No | Meter missing break in location crime seen at moment
Outage | J.E.26.07.02661 | C001839780 | Delano Gayle | St.Catherine | Completed | Load_263230 | New Michelton - 210 | Jul 4, 2026 5:01am | Jul 4, 2026 5:16am | Jul 4, 2026 5:32am | Jul 4, 2026 5:34am | Jul 4, 2026 7:06am | Jul 4, 2026 7:06am | Jul 4, 2026 7:07am | Jul 4, 2026 7:07am |  |  | Fair | No | Premises not found no answer from customer phone
Outage | J.E.26.07.02626 | C001839777 | Edward Royal | KSAS | Completed | Load_242007 | Duhaney - 310 | Jul 4, 2026 12:46am | Jul 4, 2026 12:46am | Jul 4, 2026 5:00am | Jul 4, 2026 5:00am | Jul 4, 2026 5:00am | Jul 4, 2026 5:01am | Jul 4, 2026 5:01am | Jul 4, 2026 5:01am |  |  | Fair | No | When contacted customer said that the power was restored
Outage | J.E.26.07.02643 | C001839776 | Edward Royal | KSAS | Completed | Load_247896 | Duhaney - 310 | Jul 4, 2026 12:46am | Jul 4, 2026 7:42am | Jul 4, 2026 11:47am | Jul 4, 2026 11:47am | Jul 4, 2026 11:48am | Jul 4, 2026 2:52pm | Jul 4, 2026 2:52pm | Jul 4, 2026 2:52pm |  |  | Fair | No | Replaced 4 north quad cable using 8 ampack 2 perform 4 single bolt clamp
Outage | J.E.26.07.02642 | C001839775 | Edward Royal | KSAS | Completed | Load_243699 | Rockfort - 210 | Jul 4, 2026 12:45am | Jul 4, 2026 12:46am | Jul 4, 2026 1:41am | Jul 4, 2026 1:41am | Jul 4, 2026 2:00am | Jul 4, 2026 2:00am | Jul 4, 2026 2:01am | Jul 4, 2026 2:01am | Fire |  | Fair | No | Premises found close
Outage | J.E.26.07.02554 | C001839773 | Michael Christian | St.James | Completed | Load_269658 | Queens Drive - 810 | Jul 3, 2026 11:53pm | Jul 3, 2026 11:54pm | Jul 4, 2026 1:47am | Jul 4, 2026 1:54am | Jul 4, 2026 2:26am | Jul 4, 2026 2:34am | Jul 4, 2026 2:35am | Jul 4, 2026 2:35am |  |  | Fair | No | Found 1 25 kava transformer out cause by fire found open replace
Outage | J.E.26.07.02609 | C001839772 | Michael Christian | St.James | Completed | Load_259109 | Queens Drive - 710 | Jul 3, 2026 11:53pm | Jul 3, 2026 11:54pm | Jul 4, 2026 12:12am | Jul 4, 2026 12:12am | Jul 4, 2026 1:47am | Jul 4, 2026 1:53am | Jul 4, 2026 1:53am | Jul 4, 2026 1:53am |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.02621 | C001839770 | Omar King | St.Ann | Completed | Load_239757 | Roaring River - 410 | Jul 3, 2026 11:45pm | Jul 3, 2026 11:46pm | Jul 4, 2026 12:45am | Jul 4, 2026 12:45am | Jul 4, 2026 1:56am | Jul 4, 2026 2:11am | Jul 4, 2026 2:11am | Jul 4, 2026 2:11am |  |  | Fair | No | Found a 25 amp junction fuse blow cause by bird fuse as been replaced area is now with supply
Outage | J.E.26.07.02604 | C001839766 | Cliton Henry | St.Mary | Completed | Load_240121 | Blackstonedge - 110 | Jul 3, 2026 10:23pm | Jul 4, 2026 7:45am | Jul 4, 2026 9:20am | Jul 4, 2026 9:20am | Jul 4, 2026 10:49am | Jul 4, 2026 2:55pm | Jul 4, 2026 3:02pm | Jul 4, 2026 3:02pm |  |  | Fair | No | Two span of secondary conductors burnt and fell to the ground. A 25 kva transformer was de energized at pole # p0100727 to carryout repairs. Corrective work done to spliced and retention secondary conductors using approximately 140 feet #2AA conductor,4 #2 preform and 8 one bolt clamps. A secondary jumper was open at White Spring Road at pole #0177024. Supply restored to energized the 25 kva transformer at pole #0100727
Outage | J.E.26.07.02566 | C001839761 | Christopher Edwards | KSAN | Completed | Load_257180 | Constant Spring - 410 | Jul 3, 2026 10:02pm | Jul 3, 2026 10:03pm | Jul 3, 2026 10:07pm | Jul 3, 2026 10:07pm | Jul 3, 2026 10:07pm | Jul 3, 2026 10:07pm | Jul 3, 2026 10:09pm | Jul 3, 2026 10:09pm |  |  | Fair | No | Broken open secondary neutral wireRequired 80ft #2AA conductor to carry out repairs Approximately 10 customers are affected by broken wire
Non-Outage | J.E.26.07.02606 | C001839759 | Floyd Taylor | null | Completed | null | null | Jul 3, 2026 9:54pm | Jul 3, 2026 9:55pm | Jul 4, 2026 7:44am | Jul 4, 2026 7:44am | Jul 4, 2026 9:08am | Jul 4, 2026 10:20am | Jul 4, 2026 10:21am | Jul 4, 2026 10:21am | Fire |  | Fair | No | Remove tree limb off line and replace one 8amp junction fuse.
Outage | J.E.26.07.02578 | C001839756 | Richman Whyte | Westmoreland | Completed | Load_239277 | Paradise - 310 | Jul 3, 2026 9:45pm | Jul 4, 2026 7:45am | Jul 4, 2026 3:14pm | Jul 4, 2026 3:14pm | Jul 4, 2026 3:14pm | Jul 4, 2026 3:49pm | Jul 4, 2026 3:52pm | Jul 4, 2026 3:52pm | Fire |  | Fair | No | Replace 5amp junction fuse
Outage | J.E.26.07.02255 | C001839755 | Rusean Allen | KSAS | Completed | Load_254034 | Cane River - 410 | Jul 3, 2026 9:34pm | Jul 3, 2026 9:34pm | Jul 3, 2026 10:15pm | Jul 3, 2026 10:15pm | Jul 3, 2026 10:15pm | Jul 3, 2026 10:17pm | Jul 3, 2026 10:17pm | Jul 3, 2026 10:17pm |  |  | Fair | No | Customer premises under investigation customer advised to go office
Outage | J.E.26.07.02358 | C001839750 | Derrick Dawkins | Trelawny | Completed | Load_266091 | Greenwood - 110 | Jul 3, 2026 8:54pm | Jul 3, 2026 8:56pm | Jul 3, 2026 9:12pm | Jul 3, 2026 9:12pm | Jul 3, 2026 10:06pm | Jul 3, 2026 9:37am | Jul 3, 2026 10:33pm | Jul 3, 2026 10:33pm |  |  | Fair | No | Check and found premises ok
Outage | J.E.26.07.02564 | C001839748 | Marlon Brown | Trelawny | Completed | Load_292238 | Greenwood - 210 | Jul 3, 2026 8:54pm | Jul 3, 2026 8:55pm | Jul 3, 2026 10:08pm | Jul 3, 2026 10:08pm | Jul 3, 2026 11:34pm | Jul 4, 2026 12:06am | Jul 4, 2026 12:06am | Jul 4, 2026 12:06am |  |  | Fair | No | Isolated 100kva transformer to repair burnt joint use 2 pg clamps and 10ft #2/0
Outage | J.E.26.07.02573 | C001839749 | Marlon Brown | Trelawny | Completed | Load_257322 | Greenwood - 210 | Jul 3, 2026 8:54pm | Jul 3, 2026 8:55pm | Jul 3, 2026 9:56pm | Jul 3, 2026 9:56pm | Jul 3, 2026 9:56pm | Jul 3, 2026 9:57pm | Jul 3, 2026 9:57pm | Jul 3, 2026 9:57pm |  |  | Fair | No | St James call
Outage | J.E.26.07.02436 | C001839747 | Romeo Brissett | St.James | Completed | Load_302358 | Bogue - 510 | Jul 3, 2026 8:52pm | Jul 3, 2026 8:55pm | Jul 4, 2026 10:10am | Jul 4, 2026 10:10am | Jul 4, 2026 10:20am | Jul 4, 2026 11:00am | Jul 4, 2026 11:04am | Jul 4, 2026 11:04am |  |  | Fair | No | Repaired secondary jumper, used 2 clamps
Outage | J.E.26.07.02551 | C001839746 | Romeo Brissett | St.James | Completed | Load_258453 | Bogue - 510 | Jul 3, 2026 8:51pm | Jul 3, 2026 8:55pm | Jul 4, 2026 8:39am | Jul 4, 2026 8:39am | Jul 4, 2026 8:59am | Jul 4, 2026 10:00am | Jul 4, 2026 10:08am | Jul 4, 2026 10:08am | BrokenWire |  | Fair | No | Isolated (1)100kva transformer, removed illegal connections, spliced and retention 1 span of secondary, repaired transformer drop lead. Used 2 clamps.
Outage | J.E.26.07.02445 | C001839745 | Delano Gayle | St.Catherine | Completed | Load_251054 | New Michelton - 210 | Jul 3, 2026 8:27pm | Jul 3, 2026 11:48pm | Jul 4, 2026 12:14am | Jul 4, 2026 12:14am | Jul 4, 2026 3:07am | Jul 4, 2026 3:14am | Jul 4, 2026 3:14am | Jul 4, 2026 3:14am |  |  | Fair | No | Premises and area found okay
Outage | J.E.26.07.02497 | C001839743 | Barrington Brown | St.James | Completed | Load_240544 | Queens Drive - 310 | Jul 3, 2026 8:25pm | Jul 3, 2026 8:25pm | Jul 3, 2026 9:55pm | Jul 3, 2026 9:55pm | Jul 3, 2026 10:18pm | Jul 3, 2026 10:59pm | Jul 3, 2026 11:00pm | Jul 3, 2026 11:00pm |  |  | Fair | No | Crew found blown 8k junction fuse on location. Cre found clearance breach on location, switch top jumper was close to pole. Crew reshaped jumper. All customers restored.
Outage | J.E.26.07.02401 | C001839741 | Cliton Henry | St.Ann | Completed | Load_244965 | Upper White River - 110 | Jul 3, 2026 8:10pm | Jul 4, 2026 7:46am | Jul 4, 2026 3:28pm | Jul 4, 2026 3:28pm | Jul 4, 2026 4:31pm | Jul 4, 2026 4:32pm | Jul 4, 2026 5:03pm | Jul 4, 2026 5:03pm |  |  | Fair | No | A blown 10 amp junction fuse found at Labrynth square pole #0145073. Supply restored using 1- 10 amp fuse
Outage | J.E.26.07.02477 | C001839738 | Evan Spaulding | St.Mary | Completed | Load_251602 | Highgate - 210 | Jul 3, 2026 8:09pm | Jul 3, 2026 8:10pm | Jul 3, 2026 9:21pm | Jul 3, 2026 9:21pm | Jul 3, 2026 9:54pm | Jul 3, 2026 10:48pm | Jul 3, 2026 10:49pm | Jul 3, 2026 10:49pm |  |  | Fair | No | Remove dry limb from primary conductor and replace 1-15 amps junction fuse,no pole number.
Outage | J.E.26.07.02539 | C001839737 | Hartley Chin | Clarendon | Completed | Load_251249 | Monymusk - 410 | Jul 3, 2026 8:09pm | Jul 3, 2026 8:11pm | Jul 3, 2026 8:36pm | Jul 3, 2026 8:39pm | Jul 3, 2026 9:05pm | Jul 3, 2026 9:21pm | Jul 3, 2026 9:21pm | Jul 3, 2026 9:21pm |  |  | Fair | No | Found blown 3 amp fuse on 25 KVA transformer @ pole # 0159206 line patrolled and found okay , transformer refused…
Outage | J.E.26.07.02555 | C001839739 | Evan Spaulding | St.Mary | Completed | Load_254493 | Highgate - 210 | Jul 3, 2026 8:09pm | Jul 3, 2026 8:10pm | Jul 3, 2026 10:49pm | Jul 3, 2026 10:49pm | Jul 3, 2026 10:49pm | Jul 3, 2026 10:50pm | Jul 3, 2026 10:50pm | Jul 3, 2026 10:50pm |  |  | Fair | No | Associated call.
Outage | J.E.26.07.02493 | C001839736 | Nickolas Rodriques | Portmore | Completed | Load_266997 | Naggo Head - 510 | Jul 3, 2026 8:05pm | Jul 3, 2026 8:05pm | Jul 3, 2026 8:16pm | Jul 3, 2026 8:24pm | Jul 3, 2026 10:06pm | Jul 3, 2026 10:36pm | Jul 3, 2026 10:37pm | Jul 3, 2026 10:37pm |  |  | Fair | No | Checked and found a 8 amp junction fuse blown. Patrol and found nothing on line. Repaired by replacing the fuse after numerous patrols.
Outage | J.E.26.07.02325 | C001839735 | Selvin White | St.Elizabeth | Completed | Load_249923 | Maggotty - 110 | Jul 3, 2026 8:03pm | Jul 3, 2026 8:07pm | Jul 3, 2026 10:00pm | Jul 3, 2026 10:00pm | Jul 3, 2026 10:29pm | Jul 3, 2026 10:36pm | Jul 3, 2026 10:36pm | Jul 3, 2026 10:36pm |  |  | Fair | No | Please refer to Simone Bicarie and C Johnson at the field service department so arrangements can be made to inspect repairs done by customer and reconnect them as customer says supply has not been restored since the hurricane
Outage | J.E.26.07.02327 | C001839732 | Marlon Brown | Trelawny | Completed | Load_267433 | Greenwood - 110 | Jul 3, 2026 7:44pm | Jul 3, 2026 7:49pm | Jul 3, 2026 8:11pm | Jul 3, 2026 8:11pm | Jul 3, 2026 8:52pm | Jul 3, 2026 9:56pm | Jul 3, 2026 9:56pm | Jul 3, 2026 9:56pm |  |  | Fair | No | Clear vegetation from poles and replaced 15amps junction fuse
Outage | J.E.26.07.02451 | C001839734 | Floyd Taylor | Trelawny | Completed | Load_253904 | Duncans - 210 | Jul 3, 2026 7:44pm | Jul 3, 2026 7:47pm | Jul 3, 2026 8:33pm | Jul 3, 2026 8:33pm | Jul 3, 2026 9:15pm | Jul 3, 2026 9:47pm | Jul 3, 2026 9:47pm | Jul 3, 2026 9:47pm | Fire |  | Fair | No | No fire was found
Outage | J.E.26.07.02525 | C001839733 | Floyd Taylor | Trelawny | Completed | Load_1001459 | Martha Brae - 110 | Jul 3, 2026 7:44pm | Jul 3, 2026 10:08pm | Jul 3, 2026 10:26pm | Jul 4, 2026 7:18am | Jul 4, 2026 7:18am | Jul 4, 2026 7:20am | Jul 4, 2026 7:44am | Jul 4, 2026 7:44am |  |  | Fair | No | Customer light was restored
Outage | J.E.26.07.02480 | C001839729 | Tyrese Williams | St.Ann | Completed | Load_259471 | Cardiff Hall - 310 | Jul 3, 2026 7:27pm | Jul 3, 2026 7:27pm | Jul 3, 2026 7:56pm | Jul 3, 2026 7:58pm | Jul 3, 2026 7:58pm | Jul 3, 2026 7:58pm | Jul 3, 2026 7:58pm | Jul 3, 2026 7:58pm |  |  | Fair | No | Premises found ok customer said it was a internal problem
Outage | J.E.26.07.02433 | C001839725 | Barnett Brown | Manchester | Completed | Load_242124 | Spur Tree - 310 | Jul 3, 2026 7:14pm | Jul 4, 2026 8:09am | Jul 4, 2026 1:41pm | Jul 4, 2026 1:41pm | Jul 4, 2026 2:20pm | Jul 4, 2026 2:38pm | Jul 4, 2026 2:40pm | Jul 4, 2026 2:40pm |  |  | Fair | No | Area has light, can’t get customer on phone
Outage | J.E.26.07.02442 | C001839724 | Barrington Brown | St.James | Completed | Load_257087 | Queens Drive - 710 | Jul 3, 2026 7:12pm | Jul 3, 2026 7:21pm | Jul 3, 2026 8:44pm | Jul 3, 2026 8:44pm | Jul 3, 2026 8:44pm | Jul 3, 2026 8:45pm | Jul 3, 2026 8:45pm | Jul 3, 2026 8:45pm |  |  | Fair | No | Crew found blown 50k junction fuse on location caused by bird making contact with line. Crew re energized circuit all customers restored.
Outage | J.E.26.07.02450 | C001839722 | Barrington Brown | St.James | Completed | Load_245810 | Queens Drive - 710 | Jul 3, 2026 7:12pm | Jul 3, 2026 7:21pm | Jul 3, 2026 8:44pm | Jul 3, 2026 8:44pm | Jul 3, 2026 8:44pm | Jul 3, 2026 8:44pm | Jul 3, 2026 8:44pm | Jul 3, 2026 8:44pm |  |  | Fair | No | Crew found blown 50k junction fuse on location caused by bird making contact with line. Crew re energized circuit all customers restored.
Outage | J.E.26.07.02455 | C001839723 | Barrington Brown | St.James | Completed | Load_1002045 | Queens Drive - 710 | Jul 3, 2026 7:12pm | Jul 3, 2026 7:21pm | Jul 3, 2026 7:29pm | Jul 3, 2026 7:29pm | Jul 3, 2026 7:48pm | Jul 3, 2026 8:43pm | Jul 3, 2026 8:43pm | Jul 3, 2026 8:43pm |  |  | Fair | No | Crew found blown 50k junction fuse on location caused by bird making contact with line. Crew re energized circuit all customers restored.
Outage | J.E.26.07.02440 | C001839719 | Hopeton Henry | St.Thomas | Completed | Load_263661 | Good Year - 110 | Jul 3, 2026 7:04pm | Jul 4, 2026 8:20am | Jul 4, 2026 10:02am | Jul 4, 2026 10:03am | Jul 4, 2026 11:02am | Jul 4, 2026 12:34pm | Jul 4, 2026 12:35pm | Jul 4, 2026 12:35pm | Fire |  | Fair | No | Found banging secondary, retention conductors and reset 10 kva transformer, no pole number
Outage | J.E.26.07.02319 | C001839718 | Neville Spencer | Clarendon | Completed | Load_243768 | May Pen - 110 | Jul 3, 2026 7:02pm | Jul 3, 2026 7:03pm | Jul 3, 2026 8:28pm | Jul 3, 2026 8:28pm | Jul 3, 2026 9:23pm | Jul 3, 2026 10:05pm | Jul 3, 2026 10:06pm | Jul 3, 2026 10:06pm |  |  | Fair | No | Renew blown 10 amp j/ fuse area restored.
Non-Outage | J.E.26.07.01750 | C001839717 | Romeo Brissett | St.James | Completed | Load_247713 | Bogue - 610 | Jul 3, 2026 7:01pm | Jul 3, 2026 7:02pm | Jul 4, 2026 11:06am | Jul 4, 2026 11:06am | Jul 4, 2026 12:39pm | Jul 4, 2026 1:00pm | Jul 4, 2026 1:08pm | Jul 4, 2026 1:08pm |  |  | Fair | No | Spliced and retention customer service wire, V/R 115-116-232
Outage | J.E.26.07.02405 | C001839714 | Andre Smith | KSAN | Completed | Load_293696 | Washington Blvd - 710 | Jul 3, 2026 7:00pm | Jul 3, 2026 7:00pm | Jul 3, 2026 7:48pm | Jul 3, 2026 7:48pm | Jul 3, 2026 8:42pm | Jul 3, 2026 9:03pm | Jul 3, 2026 9:03pm | Jul 3, 2026 9:03pm |  |  | Fair | No | No one home
Outage | J.E.26.07.02383 | C001839713 | Neville Spencer | Clarendon | Completed | Load_262299 | May Pen - 110 | Jul 3, 2026 6:52pm | Jul 3, 2026 7:02pm | Jul 3, 2026 7:39pm | Jul 3, 2026 7:39pm | Jul 3, 2026 8:26pm | Jul 3, 2026 8:26pm | Jul 3, 2026 8:28pm | Jul 3, 2026 8:28pm | BrokenWire |  | Fair | No | Unable to locate customer.
Non-Outage | J.E.26.07.02439 | C001839711 | Richard Nicholas | null | Completed | null | null | Jul 3, 2026 6:50pm | Jul 3, 2026 7:46pm | Jul 3, 2026 8:44pm | Jul 3, 2026 8:44pm | Jul 3, 2026 8:44pm | Jul 3, 2026 10:04pm | Jul 3, 2026 10:09pm | Jul 3, 2026 10:09pm | BrokenPole |  | Fair | No | Up on arrival the crew observed a broken 30ft open secondary dead end pole fell and leaned against a building,further observation taken and open secondary rest on top of the building roof top which is sink.open secondary was disconnected at one pole spa from broken pole and a dead end created.1 set of burnt off jumper was remade.2 lamp was used.supply left ok in the area.
Non-Outage | J.E.26.07.01780 | C001839710 | Romeo Brissett | St.James | Completed | Load_237873 | Bogue - 510 | Jul 3, 2026 6:49pm | Jul 3, 2026 7:12pm | Jul 3, 2026 10:16pm | Jul 3, 2026 10:16pm | Jul 3, 2026 10:24pm | Jul 3, 2026 11:05pm | Jul 3, 2026 11:05pm | Jul 3, 2026 11:05pm |  |  | Fair | No | Removed illegal connections and repaired secondary jumper. Used 1 clamp.
Outage | J.E.26.07.02397 | C001839709 | Omar King | St.Ann | Completed | Load_245204 | Ocho Rios - 410 | Jul 3, 2026 6:48pm | Jul 3, 2026 7:27pm | Jul 3, 2026 9:02pm | Jul 3, 2026 9:02pm | Jul 3, 2026 9:54pm | Jul 3, 2026 9:56pm | Jul 3, 2026 9:58pm | Jul 3, 2026 9:58pm |  |  | Fair | No | Customer encoring about new connection
Non-Outage | J.E.26.07.02396 | C001839704 | Selvin White | St.Elizabeth | Completed | Load_293002 | Maggotty - 210 | Jul 3, 2026 6:43pm | Jul 3, 2026 6:48pm | Jul 3, 2026 7:09pm | Jul 3, 2026 7:09pm | Jul 3, 2026 7:35pm | Jul 3, 2026 7:56pm | Jul 3, 2026 7:59pm | Jul 3, 2026 7:59pm |  |  | Fair | No | Re- energized a bank of three 50 KVA transformer circuit that was de energized in order for customer to carry out repairs which was completed. Supply restored.
Non-Outage | J.E.26.07.02387 | C001839690 | Richman Whyte | null | Completed | null | null | Jul 3, 2026 6:12pm | Jul 3, 2026 6:15pm | Jul 3, 2026 9:38pm | Jul 3, 2026 9:38pm | Jul 3, 2026 9:38pm | Jul 3, 2026 9:39pm | Jul 3, 2026 9:40pm | Jul 3, 2026 9:40pm | Fire |  | Fair | No | Repair and retention two span open secondary conductor use two one bolt clamps thirty feet open #2 conductor and replace 8 amp 100 kva transformer fuse voltage 116 117 234
Outage | J.E.26.07.02312 | C001839683 | Denton Williams | Portland | Completed | Load_244251 | Port Antonio - 310 | Jul 3, 2026 6:04pm | Jul 3, 2026 6:05pm | Jul 3, 2026 6:20pm | Jul 3, 2026 6:21pm | Jul 3, 2026 6:22pm | Jul 3, 2026 6:23pm | Jul 3, 2026 6:23pm | Jul 3, 2026 6:23pm |  |  | Fair | No | 30amps trip saver operates. Customer stated that there was heavy wind in the area. Suspect tree contact caused outage. Closed 30amps tripsaver to restore power supply.
Outage | J.E.26.07.00829 | C001839682 | Tajay Bernard | Hanover | Completed | Load_244461 | Orange Bay - 310 | Jul 3, 2026 6:01pm | Jul 3, 2026 6:01pm | Jul 3, 2026 7:55pm | Jul 3, 2026 7:55pm | Jul 3, 2026 8:43pm | Jul 3, 2026 8:58pm | Jul 3, 2026 8:59pm | Jul 3, 2026 8:59pm |  |  | Fair | No | Area check and found okay unable to locate customer on premises multiple phone call to customer number went unanswered
Non-Outage | J.E.26.07.01840 | C001839678 | Romeo Brissett | null | Completed | null | null | Jul 3, 2026 5:59pm | Jul 3, 2026 5:59pm | Jul 3, 2026 6:03pm | Jul 3, 2026 6:03pm | Jul 3, 2026 7:17pm | Jul 3, 2026 7:34pm | Jul 3, 2026 7:37pm | Jul 3, 2026 7:37pm | BrokenWire |  | Fair | No | Lines was patrolled only telephone lines was found broken and hanging low, wires not related to JPS.
Outage | J.E.26.07.02390 | C001839677 | Romeo Brissett | St.James | Completed | Load_237873 | Bogue - 510 | Jul 3, 2026 5:56pm | Jul 3, 2026 5:58pm | Jul 3, 2026 7:38pm | Jul 3, 2026 7:38pm | Jul 3, 2026 9:22pm | Jul 3, 2026 10:10pm | Jul 3, 2026 10:16pm | Jul 3, 2026 10:16pm |  |  | Fair | No | Installed 120 of #6 used 120ft of #6 and 6 clamps 113-113-226
Outage | J.E.26.07.02337 | C001839670 | Barrington Brown | St.James | Completed | Load_257022 | Rose Hall - 210 | Jul 3, 2026 5:49pm | Jul 3, 2026 5:49pm | Jul 3, 2026 8:46pm | Jul 3, 2026 8:46pm | Jul 3, 2026 8:57pm | Jul 3, 2026 9:54pm | Jul 3, 2026 9:54pm | Jul 3, 2026 9:54pm |  |  | Fair | No | Crew found two junction fuse blown on location. One 20k and 30k. Crew conducted patrol and re energized circuit. All customers restored. Crew also found a defective @ pole number #0008346
Outage | J.E.26.07.02342 | C001839671 | Barrington Brown | St.James | Completed | Load_239852 | Rose Hall - 210 | Jul 3, 2026 5:49pm | Jul 3, 2026 5:52pm | Jul 3, 2026 9:54pm | Jul 3, 2026 9:54pm | Jul 3, 2026 9:54pm | Jul 3, 2026 9:54pm | Jul 3, 2026 9:55pm | Jul 3, 2026 9:55pm |  |  | Fair | No | Crew found two junction fuse blown on location. One 20k and 30k. Crew conducted patrol and re energized circuit. All customers restored. Crew also found a defective @ pole number #0008346
Outage | J.E.26.07.02269 | C001839669 | Barrington Brown | St.James | Completed | Load_253589 | Queens Drive - 710 | Jul 3, 2026 5:48pm | Jul 3, 2026 5:49pm | Jul 3, 2026 6:28pm | Jul 3, 2026 6:28pm | Jul 3, 2026 6:28pm | Jul 3, 2026 7:01pm | Jul 3, 2026 7:01pm | Jul 3, 2026 7:01pm |  |  | Fair | No | Crew found one 25kva transformer and one 30k junction on location crew conducted patrol. Crew removed bird from transformer tank and re energized circuit. All customers restored.
Outage | J.E.26.07.02389 | C001839666 | Richman Whyte | Westmoreland | Completed | Load_241469 | Paradise - 210 | Jul 3, 2026 5:42pm | Jul 3, 2026 5:43pm | Jul 3, 2026 6:50pm | Jul 3, 2026 6:50pm | Jul 3, 2026 8:12pm | Jul 3, 2026 8:13pm | Jul 3, 2026 9:38pm | Jul 3, 2026 9:38pm | Fire |  | Fair | No | Repair and retention two span open secondary conductor use two one bolt clamps thirty feet open #2 conductor and replace 8 amp 100 kva transformer fuse voltage 116 117 234
Outage | J.E.26.07.02268 | C001839658 | Marlon Authors | Manchester | Completed | Load_292829 | Spur Tree - 210 | Jul 3, 2026 5:13pm | Jul 3, 2026 5:16pm | Jul 3, 2026 6:04pm | Jul 3, 2026 6:04pm | Jul 3, 2026 6:04pm | Jul 3, 2026 6:06pm | Jul 3, 2026 6:07pm | Jul 3, 2026 6:07pm |  |  | Fair | No | Supply checked and found corrosion at pole. Repair same using two clamps supply leave working ok,rdg 109v,110v and cross phased 219 volts
Outage | J.E.26.07.02111 | C001839655 | Romaine Roberts | St.Mary | Completed | Load_259506 | Oracabessa - 210 | Jul 3, 2026 5:11pm | Jul 3, 2026 5:11pm | Jul 3, 2026 9:35pm | Jul 3, 2026 9:36pm | Jul 3, 2026 10:47pm | Jul 3, 2026 10:50pm | Jul 3, 2026 10:51pm | Jul 3, 2026 10:51pm | LeaningPole |  | Fair | No | Rap joints on 3 wire service phase clean and remake joints 123-124 243
Outage | J.E.26.07.02328 | C001839654 | Romaine Roberts | St.Mary | Completed | Load_350137 | Oracabessa - 210 | Jul 3, 2026 5:10pm | Jul 3, 2026 5:11pm | Jul 3, 2026 6:03pm | Jul 3, 2026 6:03pm | Jul 3, 2026 8:08pm | Jul 3, 2026 8:21pm | Jul 3, 2026 8:21pm | Jul 3, 2026 8:21pm |  |  | Fair | No | Found several customer meter turn off in rammy box , box number Hx29171383 /hex 05629 call was made to call center resulting reconnection to most customer ,a advise was given to the additional customer to call back customer service fro further advise
Outage | J.E.26.07.02360 | C001839652 | Tyrese Williams | St.Ann | Completed | Load_253129 | Cardiff Hall - 310 | Jul 3, 2026 5:10pm | Jul 3, 2026 5:11pm | Jul 3, 2026 6:24pm | Jul 3, 2026 6:38pm | Jul 3, 2026 6:38pm | Jul 3, 2026 6:39pm | Jul 3, 2026 6:39pm | Jul 3, 2026 6:39pm |  |  | Fair | No | Premise not found not getting customer on phone
Outage | J.E.26.07.02335 | C001839650 | Tyrese Williams | St.Ann | Completed | Load_266542 | Cardiff Hall - 310 | Jul 3, 2026 5:09pm | Jul 3, 2026 5:11pm | Jul 3, 2026 6:24pm | Jul 3, 2026 6:31pm | Jul 3, 2026 6:31pm | Jul 3, 2026 6:33pm | Jul 3, 2026 6:33pm | Jul 3, 2026 6:33pm |  |  | Fair | No | Premises found ok call related to 25kva Transformer that was reset
Outage | J.E.26.07.02340 | C001839651 | Tyrese Williams | St.Ann | Completed | Load_246599 | Cardiff Hall - 310 | Jul 3, 2026 5:09pm | Jul 3, 2026 5:11pm | Jul 3, 2026 6:33pm | Jul 3, 2026 6:39pm | Jul 3, 2026 6:39pm | Jul 3, 2026 6:39pm | Jul 3, 2026 6:40pm | Jul 3, 2026 6:40pm | BrokenWire |  | Fair | No | Premises not found not getting customer on phone
Outage | J.E.26.07.02249 | C001839644 | Tajay Bernard | Hanover | Completed | Load_555702 | Orange Bay - 210 | Jul 3, 2026 4:59pm | Jul 4, 2026 7:28am | Jul 4, 2026 11:36am | Jul 4, 2026 11:36am | Jul 4, 2026 12:24pm | Jul 4, 2026 12:31pm | Jul 4, 2026 12:31pm | Jul 4, 2026 12:31pm |  |  | Fair | No | Area check and found okay unable to locate customer on premises multiple phone call to customer number went unanswered
Outage | J.E.26.07.02141 | C001839643 | Richard Grant | St.Catherine | Completed | Load_252307 | New Michelton - 210 | Jul 3, 2026 4:58pm | Jul 3, 2026 4:59pm | Jul 3, 2026 7:14pm | Jul 3, 2026 7:14pm | Jul 3, 2026 7:53pm | Jul 3, 2026 8:48pm | Jul 3, 2026 9:44pm | Jul 3, 2026 9:44pm |  |  | Rains | No | 25amps fuse found blown for single phase primary. No visible cause seen after patrol conducted. Lightening is suspected to be the cause. 25amps replaced with same and supply restored. Area left okay.
Non-Outage | J.E.26.07.01741 | C001839637 | Marlon Authors | Manchester | Completed | Load_292829 | Spur Tree - 210 | Jul 3, 2026 4:52pm | Jul 3, 2026 4:53pm | Jul 3, 2026 5:03pm | Jul 3, 2026 5:03pm | Jul 3, 2026 5:49pm | Jul 3, 2026 6:01pm | Jul 3, 2026 6:01pm | Jul 3, 2026 6:01pm |  |  | Fair | No | Supply checked and found corrosion at pole. Repair same using two clamps. Supply leave working ok rdg 109v,110v and cross phased 219 volts
Outage | J.E.26.07.02354 | C001839638 | Richman Whyte | Westmoreland | Completed | Load_258236 | Paradise - 110 | Jul 3, 2026 4:52pm | Jul 3, 2026 4:53pm | Jul 3, 2026 5:39pm | Jul 3, 2026 5:40pm | Jul 3, 2026 6:48pm | Jul 3, 2026 6:48pm | Jul 3, 2026 6:49pm | Jul 3, 2026 6:49pm |  |  | Fair | No | Connect back customer after hurricane use 39ft #6 triplex and 6 one bolt clamps voltage 114 115 230
Outage | J.E.26.07.01307 | C001839636 | Tajay Bernard | St.James | Completed | Load_259607 | Bogue - 510 | Jul 3, 2026 4:50pm | Jul 3, 2026 5:28pm | Jul 3, 2026 6:12pm | Jul 3, 2026 6:12pm | Jul 3, 2026 7:26pm | Jul 3, 2026 7:46pm | Jul 3, 2026 7:55pm | Jul 3, 2026 7:55pm |  |  | Fair | No | Check and found customer having high voltage on 1 leg(125/108/232) unable to find the cause due to not having access to the jps pole (multiple vehicle park beside the pole and excessive traffic ) and due to the current football game that’s playing
Outage | J.E.26.07.02174 | C001839635 | Rayon Foster | Hanover | Completed | Load_257370 | Orange Bay - 310 | Jul 3, 2026 4:49pm | Jul 3, 2026 4:50pm | Jul 3, 2026 8:08pm | Jul 3, 2026 8:08pm | Jul 3, 2026 9:58pm | Jul 3, 2026 10:01pm | Jul 3, 2026 10:02pm | Jul 3, 2026 10:02pm |  |  | Fair | No | Patrol primary line to fine 1 blown 8amp junction fuse complete line patrol before replacing 1 8amp junction fuse at same and close
Outage | J.E.26.07.02159 | C001839634 | Rayon Foster | Hanover | Completed | Load_267389 | Orange Bay - 310 | Jul 3, 2026 4:48pm | Jul 3, 2026 4:50pm | Jul 3, 2026 8:08pm | Jul 3, 2026 10:02pm | Jul 3, 2026 10:10pm | Jul 3, 2026 10:24pm | Jul 3, 2026 10:25pm | Jul 3, 2026 10:25pm |  |  | Fair | No | Patrol primary line to fine 1 blown 8amp junction fuse complete line patrol before replacing 1 8amp junction fuse at same and close
Outage | J.E.26.07.02336 | C001839632 | Richard Nicholas | St.Catherine | Completed | Load_269423 | Tredegar - 210 | Jul 3, 2026 4:42pm | Jul 3, 2026 4:42pm | Jul 3, 2026 6:04pm | Jul 3, 2026 6:04pm | Jul 3, 2026 7:16pm | Jul 3, 2026 7:59pm | Jul 3, 2026 8:00pm | Jul 3, 2026 8:00pm |  |  | Fair | No | Replaced blown 100kva power transformer 10amp fuse on pole #008209.
Outage | J.E.26.07.01900 | C001839625 | Milton Charlton | KSAN | Completed | Load_255998 | Washington Blvd - 610 | Jul 3, 2026 4:25pm | Jul 3, 2026 4:26pm | Jul 3, 2026 4:56pm | Jul 3, 2026 4:56pm | Jul 3, 2026 9:26pm | Jul 3, 2026 9:25pm | Jul 3, 2026 10:02pm | Jul 3, 2026 10:02pm |  |  | Fair | No | Open wire 3-wire secondary phase burn off on Hopkins Ave Kgn. 20; Bank of transformers (1-100 and 1-50kva) transformer fuses blown at pole #0113320. Repair broken wire using 15ft #2AA conductor, two #2/0 preform and four 1- bolt clamps. One span (100ft) 2/0 quaduplex feeding open wire secondary from transformer pole crystalize and need to be replaced.. Unable to reclosed transformer bank. About 100 customers affected.
Outage | J.E.26.07.02162 | C001839622 | Milton Charlton | KSAN | Completed | Load_238339 | Hope - 410 | Jul 3, 2026 4:23pm | Jul 3, 2026 4:26pm | Jul 4, 2026 9:03am | Jul 4, 2026 9:03am | Jul 4, 2026 11:06am | Jul 4, 2026 10:40am | Jul 4, 2026 11:19am | Jul 4, 2026 11:19am |  |  | Fair | No | Customer fed from EN box when we check the voltage getting 119-119-239 volts but customer complaining that is on and off. Refer to field service.
Outage | J.E.26.07.02258 | C001839621 | Christopher Edwards | KSAN | Completed | Load_579095 | Constant Spring - 210 | Jul 3, 2026 4:23pm | Jul 3, 2026 4:42pm | Jul 3, 2026 7:21pm | Jul 3, 2026 7:22pm | Jul 3, 2026 8:16pm | Jul 3, 2026 9:16pm | Jul 3, 2026 9:16pm | Jul 3, 2026 9:16pm |  |  | Fair | No | Refuse blown junction fuseUsing (1) 10 ampsClear vegetation off switch pole
Non-Outage | J.E.26.07.01593 | C001839620 | Christopher Edwards | KSAN | Completed | Load_257180 | Constant Spring - 410 | Jul 3, 2026 4:21pm | Jul 3, 2026 4:25pm | Jul 3, 2026 4:44pm | Jul 3, 2026 4:44pm | Jul 3, 2026 5:38pm | Jul 3, 2026 7:20pm | Jul 3, 2026 7:21pm | Jul 3, 2026 7:21pm |  |  | Fair | No | Required 80ft #2 AA conductor To carry out repairs Approximately 15 customers are affected as a result of broken wire
Outage | J.E.26.07.02323 | C001839617 | Denton Williams | Portland | Completed | Load_265615 | Port Antonio - 310 | Jul 3, 2026 4:20pm | Jul 3, 2026 4:20pm | Jul 3, 2026 4:31pm | Jul 3, 2026 4:31pm | Jul 3, 2026 5:42pm | Jul 3, 2026 6:13pm | Jul 3, 2026 6:20pm | Jul 3, 2026 6:20pm |  |  | Fair | No | 30amps trip saver operates. Customer stated that there was heavy wind in the area. Suspect tree contact caused outage. Closed 30amps tripsaver to restore power supply.
Outage | J.E.26.07.02306 | C001839616 | Rayon Foster | Hanover | Completed | Load_241167 | Orange Bay - 310 | Jul 3, 2026 4:19pm | Jul 3, 2026 4:19pm | Jul 3, 2026 6:28pm | Jul 3, 2026 6:28pm | Jul 3, 2026 7:07pm | Jul 3, 2026 7:48pm | Jul 3, 2026 7:50pm | Jul 3, 2026 7:50pm | BrokenPole |  | Fair | No | Patrol primary line to find 2 blown junction fuse complete patrol before replacing 1 15amp junction fuse and 1 20amp junction fuse and close
Outage | J.E.26.07.02311 | C001839615 | Hopeton Henry | St.Thomas | Completed | Load_335584 | Lysson - 410 | Jul 3, 2026 4:14pm | Jul 3, 2026 4:14pm | Jul 3, 2026 4:22pm | Jul 3, 2026 7:06pm | Jul 3, 2026 7:06pm | Jul 3, 2026 8:57pm | Jul 3, 2026 8:58pm | Jul 3, 2026 8:58pm | Fire |  | Fair | Yes | Splice and retention secondary, reset 25 kva transformer
Outage | J.E.26.07.02255 | C001839614 | Rusean Allen | KSAS | Completed | Load_254034 | Cane River - 410 | Jul 3, 2026 4:11pm | Jul 3, 2026 4:11pm | Jul 3, 2026 7:18pm | Jul 3, 2026 7:22pm | Jul 3, 2026 8:52pm | Jul 3, 2026 8:53pm | Jul 3, 2026 8:53pm | Jul 3, 2026 8:53pm |  |  | Fair | No | Customer not aware of any problems reported
Outage | J.E.26.07.02064 | C001839612 | Andre Smith | KSAN | Completed | Load_257312 | Washington Blvd - 310 | Jul 3, 2026 4:10pm | Jul 3, 2026 4:11pm | Jul 3, 2026 4:28pm | Jul 3, 2026 4:28pm | Jul 3, 2026 5:00pm | Jul 3, 2026 5:30pm | Jul 3, 2026 5:30pm | Jul 3, 2026 5:30pm | BrokenWire |  | Fair | No | Premises found okay customer complaint about illegal connections maintenance department required
Outage | J.E.26.07.02246 | C001839613 | Andre Smith | KSAS | Completed | Load_243805 | Greenwich - 710 | Jul 3, 2026 4:10pm | Jul 3, 2026 4:11pm | Jul 3, 2026 5:31pm | Jul 3, 2026 5:31pm | Jul 3, 2026 6:39pm | Jul 3, 2026 6:39pm | Jul 3, 2026 6:39pm | Jul 3, 2026 6:39pm |  |  | Fair | No | Premises found okay supply restored already
Outage | J.E.26.07.02231 | C001839611 | Floyd Taylor | Trelawny | Completed | Load_246819 | Duncans - 210 | Jul 3, 2026 4:09pm | Jul 3, 2026 4:10pm | Jul 3, 2026 5:22pm | Jul 3, 2026 5:22pm | Jul 3, 2026 7:06pm | Jul 3, 2026 7:45pm | Jul 3, 2026 7:45pm | Jul 3, 2026 7:45pm |  |  | Fair | No | Replace 100ft#6 triplex using 3 pg 3 penunion voltage readings left 115,116,234
Non-Outage | J.E.26.07.01952 | C001839605 | Nickolas Rodriques | St.Catherine | Completed | Load_568109 | Rhodens Pen - 210 | Jul 3, 2026 4:05pm | Jul 3, 2026 4:05pm | Jul 3, 2026 6:36pm | Jul 3, 2026 6:57pm | Jul 3, 2026 7:17pm | Jul 3, 2026 8:03pm | Jul 3, 2026 8:04pm | Jul 3, 2026 8:04pm |  |  | Fair | No | Checked and found customer single phasing (115). All necessary checks were done and it was found that the issue is stemming from the EG box (EG 005045). Refer to field service.
Outage | J.E.26.07.02192 | C001839604 | Nickolas Rodriques | St.Catherine | Completed | Load_251436 | Rhodens Pen - 210 | Jul 3, 2026 4:03pm | Jul 3, 2026 4:04pm | Jul 3, 2026 4:32pm | Jul 3, 2026 4:49pm | Jul 3, 2026 6:21pm | Jul 3, 2026 6:25pm | Jul 3, 2026 6:36pm | Jul 3, 2026 6:36pm |  |  | Fair | No | Checked and found customer without electricity caused by corroded connection at pole. Repaired by placing one clamp at pole, current reading is (116). Customer confirmed that all is well now.
Non-Outage | J.E.26.07.02297 | C001839602 | Evan Spaulding | null | Completed | null | null | Jul 3, 2026 4:01pm | Jul 3, 2026 4:01pm | Jul 3, 2026 6:38pm | Jul 3, 2026 6:38pm | Jul 3, 2026 6:38pm | Jul 3, 2026 6:39pm | Jul 3, 2026 6:39pm | Jul 3, 2026 6:39pm | BrokenWire |  | Fair | No | Associated call.
Outage | J.E.26.07.01999 | C001839600 | Richard Nicholas | St.Catherine | Completed | Load_556507 | Tredegar - 510 | Jul 3, 2026 4:01pm | Jul 3, 2026 4:03pm | Jul 3, 2026 5:01pm | Jul 3, 2026 5:01pm | Jul 3, 2026 5:43pm | Jul 3, 2026 5:59pm | Jul 3, 2026 6:00pm | Jul 3, 2026 6:00pm |  |  | Fair | No | Prepaid rammy system failure,please refer to the relevant department.
Outage | J.E.26.07.02091 | C001839603 | Richard Nicholas | St.Catherine | Completed | Load_248981 | Tredegar - 510 | Jul 3, 2026 4:01pm | Jul 3, 2026 4:04pm | Jul 3, 2026 10:56pm | Jul 3, 2026 10:56pm | Jul 3, 2026 10:56pm | Jul 3, 2026 11:28pm | Jul 3, 2026 11:30pm | Jul 3, 2026 11:30pm | BrokenPole |  | Fair | No | Broken 40ft class 6 T- Construction with 2 phase primary and primary neutral needed to replace urgently.
Outage | J.E.26.07.02234 | C001839601 | Richard Nicholas | St.Catherine | Completed | Load_255597 | Tredegar - 310 | Jul 3, 2026 4:01pm | Jul 3, 2026 4:03pm | Jul 4, 2026 11:38am | Jul 4, 2026 11:38am | Jul 4, 2026 12:17pm | Jul 4, 2026 12:34pm | Jul 4, 2026 12:35pm | Jul 4, 2026 12:35pm |  |  | Fair | No | Rammy system failure
Non-Outage | J.E.26.07.01791 | C001839594 | Denton Williams | Portland | Completed | Load_243555 | Port Antonio - 410 | Jul 3, 2026 4:00pm | Jul 3, 2026 4:00pm | Jul 3, 2026 6:24pm | Jul 3, 2026 6:24pm | Jul 3, 2026 8:19pm | Jul 3, 2026 8:49pm | Jul 3, 2026 8:53pm | Jul 3, 2026 8:53pm |  |  | Fair | No | Visited location and customer wasn’t found.
Non-Outage | J.E.26.07.02181 | C001839592 | Collin Robinson | null | Completed | null | null | Jul 3, 2026 4:00pm | Jul 4, 2026 8:10am | Jul 4, 2026 8:43am | Jul 4, 2026 8:43am | Jul 4, 2026 10:21am | Jul 4, 2026 10:22am | Jul 4, 2026 10:23am | Jul 4, 2026 10:23am | BrokenWire |  | Fair | No | Premises with supply
Outage | J.E.26.07.02256 | C001839593 | Denton Williams | Portland | Completed | Load_265014 | Port Antonio - 410 | Jul 3, 2026 4:00pm | Jul 3, 2026 4:00pm | Jul 3, 2026 8:54pm | Jul 3, 2026 8:54pm | Jul 3, 2026 9:32pm | Jul 3, 2026 9:34pm | Jul 3, 2026 9:36pm | Jul 3, 2026 9:36pm |  |  | Fair | No | The customer stated that their meter socket is dislocated. The customer was advised to contact a licensed electrician to fix problem.
Outage | J.E.26.07.02119 | C001839589 | Christopher West | KSAS | Completed | Load_250434 | Duhaney - 210 | Jul 3, 2026 3:55pm | Jul 3, 2026 3:57pm | Jul 3, 2026 4:16pm | Jul 3, 2026 4:16pm | Jul 3, 2026 4:52pm | Jul 3, 2026 4:59pm | Jul 3, 2026 5:02pm | Jul 3, 2026 5:02pm |  |  | Fair | No
Non-Outage | J.E.26.07.01981 | C001839585 | Derrick Dawkins | St.James | Completed | Load_265224 | Bogue - 410 | Jul 3, 2026 3:46pm | Jul 3, 2026 3:58pm | Jul 3, 2026 4:07pm | Jul 3, 2026 4:07pm | Jul 3, 2026 5:03pm | Jul 3, 2026 5:20pm | Jul 3, 2026 5:21pm | Jul 3, 2026 5:21pm |  |  | Fair | No | Check and found premises ok voltage left 215/218/218/415/418/417
Non-Outage | J.E.26.07.02059 | C001839584 | Derrick Dawkins | St.James | Completed | Load_557029 | Bogue - 310 | Jul 3, 2026 3:46pm | Jul 3, 2026 3:58pm | Jul 3, 2026 5:21pm | Jul 3, 2026 5:21pm | Jul 3, 2026 6:10pm | Jul 3, 2026 6:18pm | Jul 3, 2026 7:26pm | Jul 3, 2026 7:26pm | LowHangingWires |  | Fair | No | Customer complained about low hanging service wire buckets truck needs pole with hexing box leaning need to straighten refers to maintenance
Non-Outage | J.E.26.07.01975 | C001839579 | Swon Miller | St.James | Completed | Load_405862 | Rose Hall - 210 | Jul 3, 2026 3:42pm | Jul 4, 2026 7:23am | Jul 4, 2026 8:19am | Jul 4, 2026 8:20am | Jul 4, 2026 8:32am | Jul 22, 2026 10:43am | Jul 4, 2026 8:44am | Jul 4, 2026 8:44am | BrokenWire |  | Fair | No | Check and found multiple cable wires hanging down at customer gate advise customer to contact the cable company to have them removed
Non-Outage | J.E.26.07.02067 | C001839577 | Barrington Brown | St.James | Completed | Load_256804 | Queens Drive - 710 | Jul 3, 2026 3:41pm | Jul 3, 2026 3:43pm | Jul 3, 2026 5:36pm | Jul 3, 2026 7:03pm | Jul 3, 2026 7:27pm | Jul 3, 2026 7:28pm | Jul 3, 2026 7:28pm | Jul 3, 2026 7:28pm |  |  | Fair | No | Checked and found ok
Non-Outage | J.E.26.07.02222 | C001839578 | Swon Miller | St.James | Completed | Load_267346 | Queens Drive - 710 | Jul 3, 2026 3:41pm | Jul 4, 2026 12:45pm | Jul 4, 2026 1:42pm | Jul 4, 2026 1:42pm | Jul 4, 2026 3:05pm | Jul 8, 2026 3:50am | Jul 4, 2026 4:06pm | Jul 4, 2026 4:06pm |  |  | Fair | No | Found customer single phasing cause by contamination at pole clean and remake joints use 1 pg voltage found 117 voltage left 117/118/235
Non-Outage | J.E.26.07.02241 | C001839573 | Selvin White | null | Completed | null | null | Jul 3, 2026 3:37pm | Jul 3, 2026 7:12pm | Jul 3, 2026 8:18pm | Jul 3, 2026 8:19pm | Jul 3, 2026 9:17pm | Jul 3, 2026 9:20pm | Jul 3, 2026 9:20pm | Jul 3, 2026 9:20pm | BrokenWire |  | Fair | No | Customer says supply was okay and he did not make any report.
Non-Outage | J.E.26.07.02244 | C001839572 | Marlon Authors | null | Completed | null | null | Jul 3, 2026 3:37pm | Jul 3, 2026 3:40pm | Jul 3, 2026 8:01pm | Jul 3, 2026 8:01pm | Jul 3, 2026 8:01pm | Jul 3, 2026 8:03pm | Jul 3, 2026 8:03pm | Jul 3, 2026 8:03pm |  |  | Fair | No | Customer said supply is already fixed
Outage | J.E.26.07.02173 | C001839569 | Marlon Authors | St.Elizabeth | Completed | Load_248132 | Maggotty - 210 | Jul 3, 2026 3:37pm | Jul 3, 2026 3:40pm | Jul 3, 2026 6:28pm | Jul 3, 2026 6:28pm | Jul 3, 2026 7:01pm | Jul 3, 2026 7:36pm | Jul 3, 2026 7:36pm | Jul 3, 2026 7:36pm | BrokenWire |  | Fair | No | Patrol and found service wire tourn down by truck and bonded together. Splice and retention same using sixty feet of #6 triplex service wire, one clamp, five linkets and reset trip type transformer no pole #. Restored supply okay
Outage | J.E.26.07.02220 | C001839570 | Selvin White | Manchester | Completed | Load_243051 | Spur Tree - 210 | Jul 3, 2026 3:37pm | Jul 3, 2026 3:40pm | Jul 3, 2026 4:10pm | Jul 3, 2026 4:10pm | Jul 3, 2026 5:04pm | Jul 3, 2026 6:04pm | Jul 3, 2026 6:09pm | Jul 3, 2026 6:09pm |  |  | Rains | No | Isolate a 25 KVA transformer circuit in order to clear dislodged neutral grounding conductor that was coming into contact with phase conductor. Also replace burnt out one bolt clamp at transformer phase drop lead. Supply restored to the affected customers.
Outage | J.E.26.07.02260 | C001839571 | Marlon Authors | St.Elizabeth | Completed | Load_265222 | Maggotty - 210 | Jul 3, 2026 3:37pm | Jul 3, 2026 3:40pm | Jul 3, 2026 7:38pm | Jul 3, 2026 7:38pm | Jul 3, 2026 7:39pm | Jul 3, 2026 7:40pm | Jul 3, 2026 7:40pm | Jul 3, 2026 7:40pm |  |  | Fair | No | Supply restored to the area
Outage | J.E.26.07.01939 | C001839564 | Swon Miller | St.James | Completed | Load_267668 | Queens Drive - 710 | Jul 3, 2026 3:35pm | Jul 4, 2026 7:31am | Jul 4, 2026 11:28am | Jul 4, 2026 11:28am | Jul 4, 2026 12:56pm | Jul 29, 2026 1:42am | Jul 4, 2026 1:42pm | Jul 4, 2026 1:42pm | LeaningPole |  | Fair | No | Found 2, 30 ft class 6 pole with 2/o twisted and one span of open span secondary broken at the base both poles have street lights on the customer states that the pole are broken before Melisa please refer to maintenance
Outage | J.E.26.07.02138 | C001839568 | Romeo Brissett | St.James | Completed | Load_556243 | Bogue - 610 | Jul 3, 2026 3:35pm | Jul 3, 2026 3:38pm | Jul 3, 2026 3:44pm | Jul 3, 2026 3:44pm | Jul 3, 2026 4:47pm | Jul 3, 2026 5:10pm | Jul 3, 2026 5:12pm | Jul 3, 2026 5:12pm |  |  | Rains | No | Check and found premises closed neighbor stated premises won’t be open until next week.
Outage | J.E.26.07.02073 | C001839561 | Hopeton Henry | St.Thomas | Completed | Load_243826 | Lysson - 410 | Jul 3, 2026 3:33pm | Jul 3, 2026 3:33pm | Jul 3, 2026 4:22pm | Jul 3, 2026 9:32pm | Jul 3, 2026 9:32pm | Jul 3, 2026 9:33pm | Jul 3, 2026 9:33pm | Jul 3, 2026 9:33pm |  |  | Fair | No | Check and found ok
Outage | J.E.26.07.02186 | C001839560 | Hopeton Henry | St.Thomas | Completed | Load_247673 | Lysson - 410 | Jul 3, 2026 3:33pm | Jul 3, 2026 3:33pm | Jul 3, 2026 4:22pm | Jul 3, 2026 9:37pm | Jul 3, 2026 10:51pm | Jul 3, 2026 11:37pm | Jul 3, 2026 11:38pm | Jul 3, 2026 11:38pm | Fire |  | Fair | No | Reconnect broken service wire Use 3 connector 113-116-229 volts
Outage | J.E.26.07.02205 | C001839562 | Hopeton Henry | St.Thomas | Completed | Load_252337 | Lysson - 410 | Jul 3, 2026 3:33pm | Jul 3, 2026 3:33pm | Jul 3, 2026 4:22pm | Jul 3, 2026 9:33pm | Jul 3, 2026 9:33pm | Jul 3, 2026 9:33pm | Jul 3, 2026 9:34pm | Jul 3, 2026 9:34pm |  |  | Fair | Yes | Check and found ok
Outage | J.E.26.07.02245 | C001839563 | Hopeton Henry | St.Thomas | Completed | Load_575858 | Good Year - 110 | Jul 3, 2026 3:33pm | Jul 3, 2026 3:33pm | Jul 3, 2026 4:22pm | Jul 3, 2026 4:24pm | Jul 3, 2026 5:26pm | Jul 3, 2026 5:28pm | Jul 3, 2026 5:28pm | Jul 3, 2026 5:28pm |  |  | Fair | No | Check and found ok
Outage | J.E.26.07.02021 | C001839559 | Hopeton Henry | St.Thomas | Completed | Load_260059 | Good Year - 110 | Jul 3, 2026 3:32pm | Jul 3, 2026 3:33pm | Jul 3, 2026 4:22pm | Jul 3, 2026 5:57pm | Jul 3, 2026 6:25pm | Jul 3, 2026 6:31pm | Jul 3, 2026 7:06pm | Jul 3, 2026 7:06pm |  |  | Fair | Yes | Found corrosion Use 6 connector 4 clamps 117-118-236 volts
Outage | J.E.26.07.02250 | C001839558 | Damion Reid | Manchester | Completed | Load_1002612 | Porus - 310 | Jul 3, 2026 3:31pm | Jul 3, 2026 3:37pm | Jul 3, 2026 3:45pm | Jul 3, 2026 5:08pm | Jul 3, 2026 5:22pm | Jul 3, 2026 6:09pm | Jul 3, 2026 6:11pm | Jul 3, 2026 6:11pm | BrokenWire |  | Fair | No | Replaced 100ft of defensive #6 triplex service wire for 3 wire service using 3 pen union and three one bolt clamp
Outage | J.E.26.07.01871 | C001839548 | Richman Whyte | Hanover | Completed | Load_247031 | Orange Bay - 310 | Jul 3, 2026 3:24pm | Jul 3, 2026 3:30pm | Jul 3, 2026 9:41pm | Jul 3, 2026 9:41pm | Jul 3, 2026 9:41pm | Jul 3, 2026 9:42pm | Jul 3, 2026 9:42pm | Jul 3, 2026 9:42pm |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.02179 | C001839549 | Richman Whyte | Westmoreland | Completed | Load_263330 | Paradise - 210 | Jul 3, 2026 3:24pm | Jul 3, 2026 3:29pm | Jul 3, 2026 9:40pm | Jul 3, 2026 9:40pm | Jul 3, 2026 9:41pm | Jul 3, 2026 9:41pm | Jul 3, 2026 9:41pm | Jul 3, 2026 9:41pm |  |  | Fair | No | Check and found okay
Outage | J.E.26.07.02213 | C001839547 | Javid Vernon | Westmoreland | Completed | Load_262591 | Paradise - 310 | Jul 3, 2026 3:24pm | Jul 3, 2026 3:28pm | Jul 3, 2026 7:26pm | Jul 3, 2026 7:26pm | Jul 3, 2026 9:04pm | Jul 3, 2026 9:24pm | Jul 3, 2026 9:24pm | Jul 3, 2026 9:24pm |  |  | Rains | No | Refuse one 25kva transformer use 3amp fuse
Outage | J.E.26.07.02235 | C001839546 | Javid Vernon | Westmoreland | Completed | Load_268226 | Paradise - 310 | Jul 3, 2026 3:24pm | Jul 3, 2026 3:28pm | Jul 3, 2026 3:50pm | Jul 3, 2026 3:50pm | Jul 3, 2026 6:06pm | Jul 3, 2026 7:24pm | Jul 3, 2026 7:25pm | Jul 3, 2026 7:25pm | Fire | Y | Fair | No | Cut and remove tree limbs from single phase primary line and reclose one 20amp trip saver
Outage | J.E.26.07.02238 | C001839545 | Tyrese Williams | St.Ann | Completed | Load_266542 | Cardiff Hall - 310 | Jul 3, 2026 3:22pm | Jul 3, 2026 3:22pm | Jul 3, 2026 3:42pm | Jul 3, 2026 4:12pm | Jul 3, 2026 5:40pm | Jul 3, 2026 6:30pm | Jul 3, 2026 6:31pm | Jul 3, 2026 6:31pm |  |  | Fair | No | Splice and retention 3 span of secondary phase and neutral and reset a 25 kva transformer at pole
Outage | J.E.26.07.00991 | C001839536 | Evan Spaulding | St.Mary | Completed | Load_248728 | Highgate -110 | Jul 3, 2026 3:19pm | Jul 3, 2026 3:20pm | Jul 3, 2026 5:31pm | Jul 3, 2026 5:32pm | Jul 3, 2026 5:32pm | Jul 3, 2026 5:32pm | Jul 3, 2026 5:32pm | Jul 3, 2026 5:32pm |  |  | Fair | No | Customer say issue was resolved from the other day
Outage | J.E.26.07.01801 | C001839535 | Evan Spaulding | St.Mary | Completed | Load_260174 | Highgate - 210 | Jul 3, 2026 3:19pm | Jul 3, 2026 3:20pm | Jul 3, 2026 3:38pm | Jul 3, 2026 3:38pm | Jul 3, 2026 3:38pm | Jul 3, 2026 3:38pm | Jul 3, 2026 3:38pm | Jul 3, 2026 3:38pm |  |  | Fair | No | Customer says power was restored.
Outage | J.E.26.07.02100 | C001839534 | Hartley Chin | Clarendon | Completed | Load_250181 | Monymusk - 410 | Jul 3, 2026 3:19pm | Jul 3, 2026 3:20pm | Jul 3, 2026 5:53pm | Jul 3, 2026 5:53pm | Jul 3, 2026 7:24pm | Jul 3, 2026 7:57pm | Jul 3, 2026 7:58pm | Jul 3, 2026 7:58pm | BrokenWire |  | Fair | No | Isolate 25KAV transformer (no pole #) due to broken open secondary phase found , repair broken phase , re- energized transformer… use 2 clamp , 1 - #2 splicing sleeve , 30ft #2 conductor…
Outage | J.E.26.07.02177 | C001839533 | Evan Spaulding | St.Mary | Completed | Load_252458 | Highgate - 210 | Jul 3, 2026 3:19pm | Jul 3, 2026 3:20pm | Jul 3, 2026 3:53pm | Jul 3, 2026 3:53pm | Jul 3, 2026 4:23pm | Jul 3, 2026 5:21pm | Jul 3, 2026 5:23pm | Jul 3, 2026 5:23pm |  |  | SevereWind | No | Retention one secondary conductors ,voltage left 113v,112v,225v.
Outage | J.E.26.07.02223 | C001839537 | Hartley Chin | Clarendon | Completed | Load_264794 | Monymusk - 410 | Jul 3, 2026 3:19pm | Jul 3, 2026 3:20pm | Jul 3, 2026 8:04pm | Jul 3, 2026 8:05pm | Jul 3, 2026 8:35pm | Jul 3, 2026 8:38pm | Jul 3, 2026 8:39pm | Jul 3, 2026 8:39pm |  |  | Fair | No | Customer reported broken pole … maintenance crew currently on-site ...
Outage | J.E.26.07.02229 | C001839532 | Evan Spaulding | St.Mary | Completed | Load_254414 | Highgate - 210 | Jul 3, 2026 3:19pm | Jul 3, 2026 3:20pm | Jul 3, 2026 5:34pm | Jul 3, 2026 5:34pm | Jul 3, 2026 5:47pm | Jul 3, 2026 6:38pm | Jul 3, 2026 6:38pm | Jul 3, 2026 6:38pm | BrokenWire |  | Fair | No | Replace 90ft #6 Triplex service wire and 6-1bolt clamps,voltage left 112v,114v,226v.
Outage | J.E.26.07.02233 | C001839538 | Hartley Chin | Clarendon | Completed | Load_240599 | May Pen - 210 | Jul 3, 2026 3:19pm | Jul 3, 2026 3:20pm | Jul 3, 2026 9:22pm | Jul 3, 2026 9:22pm | Jul 3, 2026 10:27pm | Jul 3, 2026 10:46pm | Jul 3, 2026 10:58pm | Jul 3, 2026 10:58pm |  |  | Fair | No | Prem not found.. unable to contact customer with contact # provided.. phone is ring but no answer.., Time : 10:41 …
Outage | J.E.26.07.02239 | C001839539 | Hartley Chin | Clarendon | Completed | Load_268922 | Parnassus - 310 | Jul 3, 2026 3:19pm | Jul 3, 2026 3:20pm | Jul 3, 2026 3:44pm | Jul 3, 2026 4:09pm | Jul 3, 2026 5:26pm | Jul 3, 2026 5:45pm | Jul 3, 2026 5:52pm | Jul 3, 2026 5:52pm |  |  | Fair | No | Ref to field service!!!! Found back of customer meter burnt , customer meter # 3011124 … customer requires urgent meter change due to premises being an HOME FOR THE ELDERLY!!!! Voltage read found on line side 112v , 114v … cus currently has no supply …
Outage | J.E.26.07.02163 | C001839523 | Richard Grant | St.Catherine | Completed | Load_250825 | New Michelton - 210 | Jul 3, 2026 3:09pm | Jul 3, 2026 3:10pm | Jul 3, 2026 10:23pm | Jul 3, 2026 10:38pm | Jul 3, 2026 10:38pm | Jul 3, 2026 10:39pm | Jul 3, 2026 10:39pm | Jul 3, 2026 10:39pm |  |  | Rains | No | 25amps, 20amps, 5d amps, 10d amps fuses all found blown for 2phase junction pole #028682, single phase junction pole (no pole number), single phase junction pole # 0061560 and for 25kva transformer, respectively, caused by wisp growing into tranx switch jumper. Wisp removed, 25amps replaced with same size fuse, 20amps fuse replaced with 10amps fuse, 5d amps replaced with 8k amps fuse & 10d amps fuse replaced with 3d amps to correct fuse coordination. Supply restored and area left okay.
Outage | J.E.26.07.02204 | C001839522 | Richard Grant | St.Catherine | Completed | Load_244637 | New Michelton - 210 | Jul 3, 2026 3:09pm | Jul 3, 2026 3:10pm | Jul 3, 2026 9:44pm | Jul 3, 2026 9:44pm | Jul 3, 2026 9:44pm | Jul 3, 2026 10:35pm | Jul 3, 2026 10:35pm | Jul 3, 2026 10:35pm |  |  | Rains | No | 25amps, 20amps, 5d amps, 10d amps fuses all found blown for 2phase junction pole #028682, single phase junction pole (no pole number), single phase junction pole # 0061560 and for 25kva transformer, respectively, caused by wisp growing into tranx switch jumper. Wisp removed, 25amps replaced with same size fuse, 20amps fuse replaced with 10amps fuse, 5d amps replaced with 8k amps fuse & 10d amps fuse replaced with 3d amps to correct fuse coordination. Supply restored and area left okay.
Outage | J.E.26.07.02232 | C001839519 | Richard Grant | St.Catherine | Completed | Load_242872 | New Michelton - 210 | Jul 3, 2026 3:08pm | Jul 3, 2026 3:08pm | Jul 3, 2026 10:23pm | Jul 3, 2026 10:35pm | Jul 3, 2026 10:35pm | Jul 3, 2026 10:36pm | Jul 3, 2026 10:36pm | Jul 3, 2026 10:36pm |  |  | Rains | No | 25amps, 20amps, 5d amps, 10d amps fuses all found blown for 2phase junction pole #028682, single phase junction pole (no pole number), single phase junction pole # 0061560 and for 25kva transformer, respectively, caused by wisp growing into tranx switch jumper. Wisp removed, 25amps replaced with same size fuse, 20amps fuse replaced with 10amps fuse, 5d amps replaced with 8k amps fuse & 10d amps fuse replaced with 3d amps to correct fuse coordination. Supply restored and area left okay.
Outage | J.E.26.07.02236 | C001839518 | Richard Grant | St.Catherine | Completed | Load_238748 | New Michelton - 210 | Jul 3, 2026 3:08pm | Jul 3, 2026 3:08pm | Jul 3, 2026 3:21pm | Jul 3, 2026 3:21pm | Jul 3, 2026 7:05pm | Jul 3, 2026 7:09pm | Jul 3, 2026 7:10pm | Jul 3, 2026 7:10pm |  |  | Rains | No | 30amps fuse found blown for single phase junction. No visible cause seen after patrol conducted. Lightning strike is suspected to be cause. 30amps fuse replaced with same and supply restored. Area left okay
Outage | J.E.26.07.02182 | C001839504 | Tyrese Williams | St.Ann | Completed | Load_255787 | Cardiff Hall - 210 | Jul 3, 2026 2:59pm | Jul 3, 2026 2:59pm | Jul 3, 2026 3:50pm | Jul 3, 2026 4:08pm | Jul 3, 2026 4:08pm | Jul 3, 2026 4:11pm | Jul 3, 2026 4:12pm | Jul 3, 2026 4:12pm |  |  | Fair | No | Replace a 25kva transformer fuse with a 3 amp at pole
Outage | J.E.26.07.02020 | C001839493 | Moses Elliston | St.Catherine | Completed | Load_302508 | Tredegar - 210 | Jul 3, 2026 2:41pm | Jul 3, 2026 2:42pm | Jul 4, 2026 9:48am | Jul 4, 2026 9:48am | Jul 4, 2026 9:48am | Jul 4, 2026 9:48am | Jul 4, 2026 9:49am | Jul 4, 2026 9:49am |  |  | Fair | No | Credit added to prepaid account
Outage | J.E.26.07.02088 | C001839484 | Christopher Edwards | KSAN | Completed | Load_248707 | Constant Spring - 410 | Jul 3, 2026 2:30pm | Jul 3, 2026 2:30pm | Jul 3, 2026 2:55pm | Jul 3, 2026 2:55pm | Jul 3, 2026 3:45pm | Jul 3, 2026 4:43pm | Jul 3, 2026 4:44pm | Jul 3, 2026 4:44pm |  |  | Fair | No | Refuse blown junction fuseUsing (2) 30 amps
Outage | J.E.26.07.02140 | C001839480 | Javid Vernon | Westmoreland | Completed | Load_249897 | Paradise - 310 | Jul 3, 2026 2:29pm | Jul 3, 2026 3:31pm | Jul 3, 2026 9:24pm | Jul 3, 2026 9:24pm | Jul 3, 2026 9:25pm | Jul 3, 2026 9:25pm | Jul 3, 2026 9:25pm | Jul 3, 2026 9:25pm |  |  | Fair | No | Related to previous call job #02213
Outage | J.E.26.07.02160 | C001839460 | Horace Malcolm | St.James | Completed | Load_242717 | Bogue - 310 | Jul 3, 2026 2:05pm | Jul 3, 2026 2:05pm | Jul 4, 2026 10:26am | Jul 4, 2026 10:26am | Jul 4, 2026 10:35am | Jul 4, 2026 11:24am | Jul 4, 2026 11:24am | Jul 4, 2026 11:24am |  |  | Fair | No | Reconnect customer service wires touching each at pole used 2clamps voltage 113-111-224
Outage | J.E.26.07.02076 | C001839421 | Kemark Slue | St.Catherine | Completed | Load_250825 | New Michelton - 210 | Jul 3, 2026 1:30pm | Jul 3, 2026 1:31pm | Jul 3, 2026 1:39pm | Jul 3, 2026 2:03pm | Jul 3, 2026 2:03pm | Jul 3, 2026 2:18pm | Jul 3, 2026 2:42pm | Jul 3, 2026 2:42pm |  |  | Rains | No | Unable to attend to call due to heavy showers and lightning, please refer to the evening crew.
Non-Outage | J.E.26.07.02062 | C001839419 | Wan Carlos Scarlett | St.Catherine | Completed | Load_265320 | Twickenham - 210 | Jul 3, 2026 1:26pm | Jul 4, 2026 11:39am | Jul 4, 2026 11:48am | Jul 4, 2026 12:26pm | Jul 4, 2026 12:26pm | Jul 4, 2026 1:28pm | Jul 4, 2026 1:34pm | Jul 4, 2026 1:34pm |  |  | Fair | No | Found customer 3 wire service at pole with phase and neutral corroded use 4 one bolt clamps at open secondary line phase and neutral readings 115-114-230
Non-Outage | J.E.26.07.02051 | C001839360 | Oraine Minto | St.Ann | Completed | Load_264124 | Ocho Rios - 310 | Jul 3, 2026 12:50pm | Jul 3, 2026 12:51pm | Jul 3, 2026 1:58pm | Jul 3, 2026 2:04pm | Jul 3, 2026 5:01pm | Jul 3, 2026 5:01pm | Jul 3, 2026 5:03pm | Jul 3, 2026 5:03pm |  |  | Fair | No | Issue resolved 234v 117v 116v Pole reconnection
Outage | J.E.26.06.37484 | C001839354 | Richard Samuda | Manchester | Completed | Load_262255 | Kendal - 210 | Jul 3, 2026 12:48pm | Jul 3, 2026 1:15pm | Jul 3, 2026 1:57pm | Jul 3, 2026 1:57pm | Jul 3, 2026 1:57pm | Jul 3, 2026 1:57pm | Jul 3, 2026 1:59pm | Jul 3, 2026 1:59pm |  |  | Fair | No | Customer having issues with paying bill while meter is disconnected advised customer to use app are visit the off
Outage | J.E.26.06.39265 | C001839346 | Moses Elliston | Portmore | Completed | Load_257303 | Naggo Head - 510 | Jul 3, 2026 12:45pm | Jul 3, 2026 12:47pm | Jul 3, 2026 5:09pm | Jul 3, 2026 5:09pm | Jul 3, 2026 5:09pm | Jul 3, 2026 5:09pm | Jul 3, 2026 5:14pm | Jul 3, 2026 5:14pm |  |  | Fair | No | Corroaded joints ,and broken primary neural lines at location that need to rectify voltage problems . For 2nd time refer to D.Wilkie .Roy Brown
Non-Outage | J.E.26.07.01907 | C001839333 | Cliton Henry | St.Mary | Completed | Load_242057 | Oracabessa - 210 | Jul 3, 2026 12:35pm | Jul 3, 2026 12:35pm | Jul 4, 2026 6:24pm | Jul 4, 2026 6:24pm | Jul 4, 2026 6:24pm | Jul 4, 2026 6:40pm | Jul 4, 2026 6:54pm | Jul 4, 2026 6:54pm |  |  | Fair | No
Non-Outage | J.E.26.07.01382 | C001839332 | Cliton Henry | St.Mary | Completed | Load_250654 | Oracabessa - 210 | Jul 3, 2026 12:34pm | Jul 3, 2026 12:35pm | Jul 3, 2026 1:00pm | Jul 3, 2026 1:00pm | Jul 3, 2026 1:00pm | Jul 3, 2026 3:25pm | Jul 3, 2026 3:34pm | Jul 3, 2026 3:34pm |  |  | Fair | No | A 50 kva transformer was de energized and the transformer drop leads ampacted using 1#2-2/0 and 2-2/0-2/0 ampact. The voltages left at the customer metering point were 109-111/220 volt. The secondary line need a rehabilitation. Kindly refer to St. Mary Operations
Outage | J.E.26.07.01913 | C001839323 | Swon Miller | St.James | Completed | Load_259218 | Queens Drive - 710 | Jul 3, 2026 12:30pm | Jul 3, 2026 12:31pm | Jul 3, 2026 2:16pm | Jul 3, 2026 2:16pm | Jul 3, 2026 2:41pm | Jul 28, 2026 2:55am | Jul 3, 2026 2:56pm | Jul 3, 2026 2:56pm |  |  | Fair | No | Found 1,100 kva transformer fuse blown cause by contamination replace 15 in 100 kva transformer no pole number available voltage found 0.000 voltage left 115/116/231
Outage | J.E.26.07.01930 | C001839324 | Swon Miller | St.James | Completed | Load_261979 | Queens Drive - 310 | Jul 3, 2026 12:30pm | Jul 3, 2026 12:31pm | Jul 3, 2026 12:38pm | Jul 3, 2026 12:38pm | Jul 3, 2026 1:18pm | Jul 29, 2026 2:04pm | Jul 3, 2026 2:16pm | Jul 3, 2026 2:16pm | BrokenWire |  | Fair | No | Found 1,50 kva transformer defective due to transformer lug burnt out and leaking oil 3 customer leaves out of power supply please refer to maintenance/ kerron Frazier
Outage | J.E.26.07.01972 | C001839321 | Horace Malcolm | St.James | Completed | Load_293041 | Bogue - 310 | Jul 3, 2026 12:30pm | Jul 3, 2026 12:31pm | Jul 4, 2026 2:28pm | Jul 4, 2026 2:28pm | Jul 4, 2026 4:23pm | Jul 4, 2026 4:32pm | Jul 4, 2026 4:32pm | Jul 4, 2026 4:32pm |  |  | Fair | No | Unable to locate customer or premises multiple calls to customer unavailable
Outage | J.E.26.07.02025 | C001839322 | Swon Miller | St.James | Completed | Load_261827 | Queens Drive - 710 | Jul 3, 2026 12:30pm | Jul 3, 2026 12:31pm | Jul 3, 2026 2:56pm | Jul 3, 2026 2:56pm | Jul 3, 2026 2:56pm | Jul 21, 2026 2:59am | Jul 3, 2026 2:58pm | Jul 3, 2026 2:58pm |  |  | Fair | No | Call related to previous
Non-Outage | J.E.26.04.10164 | C001839318 | Horace Malcolm | St.James | Completed | Load_555835 | Bogue - 310 | Jul 3, 2026 12:29pm | Jul 3, 2026 12:31pm | Jul 4, 2026 11:25am | Jul 4, 2026 11:25am | Jul 4, 2026 12:34pm | Jul 4, 2026 1:05pm | Jul 4, 2026 1:07pm | Jul 4, 2026 1:07pm |  |  | Fair | No | Check and found premises issue resolved voltage 115-117-232
Non-Outage | J.E.26.04.10936 | C001839320 | Horace Malcolm | St.James | Completed | Load_292133 | Bogue - 310 | Jul 3, 2026 12:29pm | Jul 3, 2026 12:31pm | Jul 3, 2026 2:16pm | Jul 3, 2026 2:16pm | Jul 3, 2026 2:16pm | Jul 3, 2026 2:16pm | Jul 3, 2026 2:16pm | Jul 3, 2026 2:16pm |  |  | Fair | No | Call belongs to trelawny
Non-Outage | J.E.26.04.12378 | C001839319 | Horace Malcolm | St.James | Completed | Load_556952 | Bogue - 310 | Jul 3, 2026 12:29pm | Jul 3, 2026 12:31pm | Jul 3, 2026 2:17pm | Jul 3, 2026 2:17pm | Jul 3, 2026 2:47pm | Jul 3, 2026 2:54pm | Jul 3, 2026 2:54pm | Jul 3, 2026 2:54pm | LowHangingWires |  | Fair | No | Check and found low hanging cable wires on brooks dale close
Outage | J.E.26.07.02046 | C001839312 | Christopher West | Portmore | Completed | Load_239574 | Naggo Head - 510 | Jul 3, 2026 12:24pm | Jul 3, 2026 3:57pm | Jul 3, 2026 5:02pm | Jul 3, 2026 5:02pm | Jul 3, 2026 6:25pm | Jul 3, 2026 6:28pm | Jul 3, 2026 6:28pm | Jul 3, 2026 6:28pm |  |  | Fair | No | New customer, hexing meter was in prepaid mode, same was subsequently changed and meter was turned on, customer now ok.
Outage | J.E.26.07.02041 | C001839310 | Rodclif Dawkins | Portmore | Completed | Load_265238 | Naggo Head - 510 | Jul 3, 2026 12:22pm | Jul 3, 2026 12:23pm | Jul 3, 2026 12:54pm | Jul 3, 2026 1:05pm | Jul 3, 2026 1:05pm | Jul 3, 2026 1:05pm | Jul 3, 2026 1:26pm | Jul 3, 2026 1:26pm |  |  | Fair | No | At location crew found 2 blown fuse from bank of 3 transformers. Crew observed defective 50kva lighting transformer leaking oil from tap changer. Power transformer was de-energized. Please refer to Aston Murray and Kymani Allman. Advise crew to bring spill bag
Outage | J.E.26.07.02012 | C001839297 | Ryan Richards | Manchester | Completed | Load_239023 | Spur Tree - 310 | Jul 3, 2026 12:16pm | Jul 4, 2026 8:17am | Jul 4, 2026 10:57am | Jul 4, 2026 2:18pm | Jul 4, 2026 2:18pm | Jul 4, 2026 2:21pm | Jul 4, 2026 2:21pm | Jul 4, 2026 2:21pm | TreeContact |  | Fair | No | 3 palms tree found growing into secondary conductors that’s the customer concern carry out spot bushing and cutt all 3 trees from line
Outage | J.E.26.07.02034 | C001839298 | Barnett Brown | Manchester | Completed | Load_292265 | Spur Tree - 310 | Jul 3, 2026 12:16pm | Jul 3, 2026 12:16pm | null | Jul 3, 2026 12:39pm | Jul 3, 2026 2:34pm | Jul 3, 2026 3:46pm | Jul 3, 2026 3:49pm | Jul 3, 2026 3:49pm | Fire |  | Fair | No | Open 25 kva transformer, pole number 0208909, remade joints at drop lead
Outage | J.E.26.07.01929 | C001839283 | Richman Whyte | Westmoreland | Completed | Load_238085 | Paradise - 310 | Jul 3, 2026 12:03pm | Jul 3, 2026 12:03pm | Jul 4, 2026 10:24am | Jul 4, 2026 10:24am | Jul 4, 2026 11:25am | Jul 4, 2026 11:52am | Jul 4, 2026 11:53am | Jul 4, 2026 11:53am |  |  | Fair | No | Close twenty five kva transformer
Outage | J.E.26.07.02019 | C001839282 | Richard Nicholas | St.Catherine | Completed | Load_574142 | Tredegar - 210 | Jul 3, 2026 12:01pm | Jul 4, 2026 7:56am | Jul 4, 2026 9:21am | Jul 4, 2026 9:21am | Jul 4, 2026 10:00am | Jul 4, 2026 10:18am | Jul 4, 2026 10:19am | Jul 4, 2026 10:19am | BrokenWire |  | Fair | No | Found ok,customer say broken wire was repaired.
Outage | J.E.26.07.02020 | C001839277 | Ricky Hall | St.Catherine | Completed | Load_302508 | Tredegar - 210 | Jul 3, 2026 11:59am | Jul 3, 2026 12:00pm | Jul 3, 2026 12:07pm | Jul 3, 2026 12:07pm | Jul 3, 2026 2:04pm | Jul 3, 2026 2:05pm | Jul 3, 2026 2:05pm | Jul 3, 2026 2:05pm |  |  | Fair | No | Prepaid customer unable to top up plz refer to the relevant team
Outage | J.E.26.07.01891 | C001839275 | Marlon Brown | Trelawny | Completed | Load_292058 | Greenwood - 110 | Jul 3, 2026 11:58am | Jul 4, 2026 7:37am | Jul 4, 2026 7:45am | Jul 4, 2026 7:45am | Jul 4, 2026 8:25am | Jul 4, 2026 8:26am | Jul 4, 2026 8:26am | Jul 4, 2026 8:26am |  |  | Fair | No | Check and found ok Voltage found 117/117=234Voltage leaving 117/117=234
Outage | J.E.26.07.01999 | C001839276 | Donald Cunningham | St.Catherine | Completed | Load_556507 | Tredegar - 510 | Jul 3, 2026 11:58am | Jul 3, 2026 11:58am | Jul 3, 2026 1:53pm | Jul 3, 2026 1:53pm | Jul 3, 2026 2:50pm | Jul 3, 2026 2:55pm | Jul 3, 2026 2:58pm | Jul 3, 2026 2:58pm |  |  | Fair | No | Customer unable to add credit refer to mr Ellison
Outage | J.E.26.07.01403 | C001839274 | Marlon Brown | Trelawny | Completed | Load_264155 | Greenwood - 110 | Jul 3, 2026 11:57am | Jul 3, 2026 2:22pm | Jul 3, 2026 3:25pm | Jul 3, 2026 3:25pm | Jul 3, 2026 7:59pm | Jul 3, 2026 8:10pm | Jul 3, 2026 8:10pm | Jul 3, 2026 8:10pm |  |  | Fair | No | Customer needs to have pothead repair.
Outage | J.E.26.07.02017 | C001839272 | Tyrese Williams | St.Ann | Completed | Load_413060 | Roaring River - 410 | Jul 3, 2026 11:57am | Jul 3, 2026 11:58am | Jul 3, 2026 12:02pm | Jul 3, 2026 12:02pm | Jul 3, 2026 12:49pm | Jul 3, 2026 1:58pm | Jul 3, 2026 1:58pm | Jul 3, 2026 1:58pm |  |  | Fair | No | Customer got meter socket fixed, recommend a new meter to be replaced
Outage | J.E.26.07.01949 | C001839244 | Milton Charlton | KSAS | Completed | Load_569790 | Up Park Camp - 510 | Jul 3, 2026 11:39am | Jul 3, 2026 11:40am | Jul 3, 2026 11:52am | Jul 3, 2026 11:52am | Jul 3, 2026 12:47pm | Jul 3, 2026 12:45pm | Jul 3, 2026 12:49pm | Jul 3, 2026 12:49pm |  |  | Fair | No | Found okay upon arrival. Customer has n internal problem. Readings at meter socket 117-117-234 volts.
Outage | J.E.26.07.01997 | C001839243 | Milton Charlton | KSAN | Completed | Load_574783 | Washington Blvd - 610 | Jul 3, 2026 11:39am | Jul 3, 2026 11:40am | Jul 3, 2026 12:49pm | Jul 3, 2026 12:49pm | Jul 3, 2026 2:17pm | Jul 3, 2026 2:25pm | Jul 3, 2026 2:19pm | Jul 3, 2026 2:19pm |  |  | Fair | No | Customer service wire #6 phase corroded in mid span . Lower splice and retention using two 1- bolt clamps. Readings 117-118-235 volts.
Outage | J.E.26.07.01993 | C001839241 | Donald Cunningham | St.Catherine | Completed | Load_267575 | Tredegar - 510 | Jul 3, 2026 11:37am | Jul 3, 2026 11:39am | Jul 3, 2026 12:29pm | Jul 3, 2026 12:29pm | Jul 3, 2026 1:24pm | Jul 3, 2026 1:46pm | Jul 3, 2026 1:51pm | Jul 3, 2026 1:51pm |  |  | Fair | No | Blown transformer fuse by by Sydenham plaza replace 7 amp fuse for 50 kva
Outage | J.E.26.07.01970 | C001839224 | Tajay Bernard | Hanover | Completed | Load_245732 | Orange Bay - 310 | Jul 3, 2026 11:28am | Jul 3, 2026 4:59pm | Jul 3, 2026 5:28pm | Jul 3, 2026 5:28pm | Jul 3, 2026 6:05pm | Jul 3, 2026 6:12pm | Jul 3, 2026 6:12pm | Jul 3, 2026 6:12pm |  |  | Fair | No | Area check and found okay unable to locate customer on premises multiple phone call to customer number went unanswered
Outage | J.E.26.07.01986 | C001839223 | Jermaine Williams | Clarendon | Completed | Load_268922 | Parnassus - 310 | Jul 3, 2026 11:28am | Jul 3, 2026 11:29am | Jul 3, 2026 11:51am | Jul 3, 2026 11:51am | Jul 3, 2026 12:39pm | Jul 3, 2026 12:39pm | Jul 3, 2026 12:40pm | Jul 3, 2026 12:40pm |  |  | Fair | No | Defective meter socket, customer advised to get electrician.
Outage | J.E.26.07.01965 | C001839222 | Wayne Dillion | Manchester | Completed | Load_256854 | Spur Tree - 210 | Jul 3, 2026 11:27am | Jul 3, 2026 11:27am | Jul 3, 2026 11:44am | Jul 3, 2026 11:44am | Jul 3, 2026 11:44am | Jul 3, 2026 11:46am | Jul 3, 2026 11:46am | Jul 3, 2026 11:46am |  |  | Fair | No | Customer said supply was restored.
Outage | J.E.26.07.01987 | C001839221 | Ricky Hall | St.Catherine | Completed | Load_251436 | Rhodens Pen - 210 | Jul 3, 2026 11:26am | Jul 3, 2026 11:27am | Jul 3, 2026 11:42am | Jul 3, 2026 11:42am | Jul 3, 2026 12:04pm | Jul 3, 2026 12:06pm | Jul 3, 2026 12:07pm | Jul 3, 2026 12:07pm |  |  | Fair | No | Premises closed
Outage | J.E.26.07.01967 | C001839215 | Richard Watson | St.Elizabeth | Completed | Load_255608 | Maggotty - 110 | Jul 3, 2026 11:25am | Jul 3, 2026 11:26am | Jul 3, 2026 12:58pm | Jul 3, 2026 12:58pm | Jul 3, 2026 12:58pm | Jul 3, 2026 1:01pm | Jul 3, 2026 1:05pm | Jul 3, 2026 1:05pm | BrokenWire |  | Fair | No | Customer contacted by phone and stated that the supply was restored.
Non-Outage | J.E.26.07.00186 | C001839183 | Horace Malcolm | St.James | Completed | Load_575159 | Bogue - 310 | Jul 3, 2026 10:55am | Jul 3, 2026 10:58am | Jul 3, 2026 12:55pm | Jul 3, 2026 12:55pm | Jul 3, 2026 1:24pm | Jul 3, 2026 2:15pm | Jul 3, 2026 2:15pm | Jul 3, 2026 2:15pm |  |  | Fair | No | Clean and remake joints at customer pothead used 2linkets and one clamp voltage 115-113-228
Non-Outage | J.E.26.07.00900 | C001839176 | Horace Malcolm | St.James | Completed | Load_256966 | Bogue - 310 | Jul 3, 2026 10:55am | Jul 3, 2026 10:58am | Jul 3, 2026 11:22am | Jul 3, 2026 11:22am | Jul 3, 2026 11:48am | Jul 3, 2026 12:51pm | Jul 3, 2026 12:52pm | Jul 3, 2026 12:52pm |  |  | Fair | No | Clean and remake joints at pole and customer pothead used 3clamps voltage 114-114-228
Outage | J.E.26.07.01918 | C001839168 | Andrew Powell | Manchester | Completed | Load_251464 | Spur Tree - 210 | Jul 3, 2026 10:46am | Jul 3, 2026 10:46am | Jul 3, 2026 10:51am | Jul 3, 2026 10:51am | Jul 3, 2026 11:32am | Jul 3, 2026 11:32am | Jul 3, 2026 11:33am | Jul 3, 2026 11:33am |  |  | Fair | No | Premises not located no direction contact customer by telephone unsuccessful.
Non-Outage | J.E.26.07.01756 | C001839160 | Cliton Henry | St.Mary | Completed | Load_269079 | Oracabessa - 210 | Jul 3, 2026 10:41am | Jul 3, 2026 10:41am | Jul 3, 2026 11:07am | Jul 3, 2026 11:09am | Jul 3, 2026 11:09am | Jul 3, 2026 11:48am | Jul 3, 2026 11:49am | Jul 3, 2026 11:49am |  |  | Fair | No | The customer service wire was reconnected at pole using 3- one bolt clamps. Voltages left at the metering point were 115-117/233 volts. The customer was advised to get a licensed electrician to carryout repairs internally
Outage | J.E.26.07.01919 | C001839161 | Kemark Slue | St.Catherine | Completed | Load_252089 | New Michelton - 210 | Jul 3, 2026 10:41am | Jul 3, 2026 10:47am | Jul 3, 2026 11:34am | Jul 3, 2026 12:04pm | Jul 3, 2026 12:39pm | Jul 3, 2026 12:39pm | Jul 3, 2026 12:41pm | Jul 3, 2026 12:41pm |  |  | Fair | No | Unable to locate premises due to inadequate directions and all calls to number given are unsuccessful, however the crew drove through the general vicinity which had supply.
Outage | J.E.26.07.01905 | C001839150 | Edward Royal | KSAS | Completed | Load_249206 | Three Miles - 410 | Jul 3, 2026 10:37am | Jul 3, 2026 10:38am | Jul 3, 2026 11:33am | Jul 3, 2026 11:33am | Jul 3, 2026 11:55am | Jul 3, 2026 12:05pm | Jul 3, 2026 12:05pm | Jul 3, 2026 12:05pm | Fire |  | Fair | No | YP rami system caught on fire box need to be change reffered to field service pole #0024038
Outage | J.E.26.07.01916 | C001839149 | Daniel Francis | St.Ann | Completed | Load_318423 | Ocho Rios - 310 | Jul 3, 2026 10:37am | Jul 3, 2026 10:37am | Jul 3, 2026 11:43am | Jul 3, 2026 11:43am | Jul 3, 2026 12:45pm | Jul 3, 2026 12:46pm | Jul 3, 2026 12:48pm | Jul 3, 2026 12:48pm |  |  | Fair | No
Non-Outage | J.E.26.07.01890 | C001839140 | Ryan Richards | null | Completed | null | null | Jul 3, 2026 10:30am | Jul 3, 2026 3:36pm | Jul 3, 2026 3:42pm | Jul 3, 2026 3:43pm | Jul 3, 2026 5:14pm | Jul 3, 2026 5:55pm | Jul 3, 2026 5:55pm | Jul 3, 2026 5:55pm |  |  | Fair | No | Area found ok area was checked to the end of the line and it appears to be ok
Outage | J.E.26.07.01904 | C001839137 | Richard Watson | St.Elizabeth | Completed | Load_253594 | Maggotty - 110 | Jul 3, 2026 10:28am | Jul 3, 2026 10:45am | Jul 3, 2026 12:11pm | Jul 3, 2026 12:11pm | Jul 3, 2026 12:40pm | Jul 3, 2026 12:46pm | Jul 3, 2026 12:46pm | Jul 3, 2026 12:46pm | BrokenPole |  | Fair | No | Fallen pole during the passage of hurricane Melissa resting on customer fence and property, transformer also laying down on customer property, please refer to maintenance department to have pole and transformer removed.
Outage | J.E.26.07.01887 | C001839114 | Shamour Haughton | St.James | Completed | Load_255239 | Bogue - 610 | Jul 3, 2026 10:13am | Jul 3, 2026 10:14am | Jul 3, 2026 11:20am | Jul 3, 2026 11:20am | Jul 3, 2026 11:47am | Jul 3, 2026 11:53am | Jul 3, 2026 12:03pm | Jul 3, 2026 12:03pm |  |  | Fair | No | Customer just needed reconnection, reconnect at meter, voltage left 119,119,205,234,234,236
Outage | J.E.26.07.01866 | C001839101 | Romaine Roberts | St.Mary | Completed | Load_238391 | Highgate - 210 | Jul 3, 2026 10:09am | Jul 3, 2026 10:13am | Jul 3, 2026 2:09pm | Jul 3, 2026 2:09pm | Jul 3, 2026 3:32pm | Jul 3, 2026 4:04pm | Jul 3, 2026 4:06pm | Jul 3, 2026 4:06pm |  |  | Fair | No | Customer 2 wire service was disconnected from the storm a reconnection carry out to restore supply
Outage | J.E.26.07.01820 | C001839099 | Edward Royal | KSAS | Completed | Load_230020 | Hunts Bay - 810 | Jul 3, 2026 10:08am | Jul 3, 2026 10:08am | Jul 3, 2026 10:22am | Jul 3, 2026 10:22am | Jul 3, 2026 10:22am | Jul 3, 2026 10:25am | Jul 3, 2026 10:25am | Jul 3, 2026 10:25am | Fire |  | Fair | No | When contacted customer said that the power was restored
Non-Outage | J.E.26.06.17837 | C001839094 | Fredrick Hamilton | null | Completed | null | null | Jul 3, 2026 10:06am | Jul 3, 2026 10:07am | Jul 3, 2026 10:10am | Jul 3, 2026 11:25am | Jul 3, 2026 11:26am | Jul 3, 2026 11:27am | Jul 3, 2026 11:27am | Jul 3, 2026 11:27am |  |  | Fair | No | Multiple calls to customer went straight to voicemail directions required
Non-Outage | J.E.26.06.39575 | C001839093 | Fredrick Hamilton | KSAN | Completed | Load_245000 | Washington Blvd - 710 | Jul 3, 2026 10:06am | Jul 3, 2026 10:07am | Jul 3, 2026 10:10am | Jul 3, 2026 10:16am | Jul 3, 2026 10:30am | Jul 3, 2026 10:38am | Jul 3, 2026 10:38am | Jul 3, 2026 10:38am |  |  | Fair | No | 225.5v/112v/112v obtained No issues detected on the JPS supply Premises found ok
Non-Outage | J.E.26.07.00447 | C001839097 | Fredrick Hamilton | KSAN | Completed | Load_268679 | Constant Spring - 310 | Jul 3, 2026 10:06am | Jul 3, 2026 10:07am | Jul 3, 2026 10:10am | Jul 3, 2026 10:47am | Jul 3, 2026 11:03am | Jul 3, 2026 11:24am | Jul 3, 2026 11:25am | Jul 3, 2026 11:25am |  |  | Fair | No | 245v/123v/122v obtained Customer defect detected at premises customer advised
Non-Outage | J.E.26.07.00498 | C001839095 | Fredrick Hamilton | KSAN | Completed | Load_265603 | Constant Spring - 210 | Jul 3, 2026 10:06am | Jul 3, 2026 10:07am | Jul 3, 2026 10:10am | Jul 3, 2026 11:59am | Jul 3, 2026 11:59am | Jul 3, 2026 12:01pm | Jul 3, 2026 12:01pm | Jul 3, 2026 12:01pm |  |  | Fair | No | Customer contacted and stated that power was restored fully previously Premises is ok
Non-Outage | J.E.26.07.00591 | C001839096 | Fredrick Hamilton | KSAN | Completed | Load_240530 | Constant Spring - 210 | Jul 3, 2026 10:06am | Jul 3, 2026 10:07am | Jul 3, 2026 10:10am | Jul 3, 2026 11:28am | Jul 3, 2026 11:28am | Jul 3, 2026 11:30am | Jul 3, 2026 11:30am | Jul 3, 2026 11:30am |  |  | Fair | No | Customer contacted and stated that power was restored fully previously Premises is ok
Outage | J.E.26.07.01870 | C001839083 | Andrew Powell | St.Elizabeth | Completed | Load_293002 | Maggotty - 210 | Jul 3, 2026 10:04am | Jul 3, 2026 10:04am | Jul 3, 2026 10:09am | Jul 3, 2026 10:09am | Jul 3, 2026 10:43am | Jul 3, 2026 10:48am | Jul 3, 2026 10:50am | Jul 3, 2026 10:50am |  |  | Fair | No | Isolate three drop out switches protect bank of three 50 kva transformer circuit which facilitate NWC pumping station only, no pole number by switch location.
Non-Outage | J.E.26.07.01228 | C001839082 | Odaine Johnson | Clarendon | Completed | Load_267981 | Parnassus - 310 | Jul 3, 2026 10:03am | Jul 3, 2026 10:04am | Jul 3, 2026 10:08am | Jul 3, 2026 11:05am | Jul 3, 2026 11:05am | Jul 3, 2026 11:06am | Jul 3, 2026 11:09am | Jul 3, 2026 11:09am |  |  | Fair | No | Corrosion was found at service pole and pothead 3 pen union and one bolt clamps was replaced and problem was fixed Voltage reading before A115 B87 AB202Voltage reading after A115 B115 AB230
Non-Outage | J.E.26.07.01873 | C001839081 | Devon Grant | null | Completed | null | null | Jul 3, 2026 10:03am | Jul 3, 2026 10:03am | Jul 3, 2026 12:24pm | Jul 3, 2026 12:38pm | Jul 3, 2026 1:02pm | Jul 3, 2026 1:17pm | Jul 3, 2026 1:24pm | Jul 3, 2026 1:24pm | BrokenWire |  | Fair | No | 3 wire Open secondary , one phase found broken cause by breadfruit tree. Refer this report to a team with ladder and cutting equipment in order to cut tree and repair conductor. (Transformers Open)
Outage | J.E.26.07.01837 | C001839080 | Devon Grant | KSAS | Completed | Load_238539 | Duhaney - 310 | Jul 3, 2026 10:03am | Jul 3, 2026 10:03am | Jul 3, 2026 1:24pm | Jul 3, 2026 1:24pm | Jul 3, 2026 1:24pm | Jul 3, 2026 1:24pm | Jul 3, 2026 1:24pm | Jul 3, 2026 1:24pm | BrokenWire |  | Fair | No | 3 wire Open secondary , one phase found broken cause by breadfruit tree. Refer this report to a team with ladder and cutting equipment in order to cut tree and repair conductor. (Transformers Open)
Non-Outage | J.E.26.07.01338 | C001839078 | Odaine Johnson | Clarendon | Completed | Load_244161 | Parnassus - 210 | Jul 3, 2026 10:02am | Jul 3, 2026 10:04am | Jul 3, 2026 10:08am | Jul 3, 2026 1:44pm | Jul 3, 2026 1:44pm | Jul 3, 2026 1:45pm | Jul 3, 2026 1:45pm | Jul 3, 2026 1:45pm |  |  | Fair | No | Corrosion found at pole remade connection using 1 one bolt clamp voltage reading 116/115/231 volts
Non-Outage | J.E.26.07.01642 | C001839076 | Odaine Johnson | Clarendon | Completed | Load_258571 | May Pen - 210 | Jul 3, 2026 10:02am | Jul 3, 2026 10:04am | Jul 3, 2026 10:08am | Jul 3, 2026 12:01pm | Jul 3, 2026 12:01pm | Jul 3, 2026 12:59pm | Jul 3, 2026 1:00pm | Jul 3, 2026 1:00pm |  |  | Fair | No | Corroded jumper found remade connection using 2 one bolt clamps voltage reading 118/119/238
Non-Outage | J.E.26.07.01703 | C001839077 | Odaine Johnson | Clarendon | Completed | Load_258571 | May Pen - 210 | Jul 3, 2026 10:02am | Jul 3, 2026 10:04am | Jul 3, 2026 10:08am | Jul 3, 2026 1:50pm | Jul 3, 2026 1:50pm | Jul 3, 2026 1:50pm | Jul 3, 2026 1:51pm | Jul 3, 2026 1:51pm |  |  | Fair | No | Corroded jumper found remade connection using 2 one bolt clamps voltage reading 118 volts
Non-Outage | J.E.26.05.32194 | C001839070 | Odeanie Davis | KSAS | Completed | Load_239090 | Up Park Camp - 310 | Jul 3, 2026 10:01am | Jul 3, 2026 10:02am | Jul 3, 2026 10:16am | Jul 3, 2026 10:16am | Jul 3, 2026 10:25am | Jul 3, 2026 10:55am | Jul 3, 2026 10:55am | Jul 3, 2026 10:55am |  |  | Fair | No | 117/119v & 237v in meter socket at arrival. 120v/120v & 240v under load, customer stated that their electrician got up to 265v in customers apartment. Transformer team need. Bucket truck needed.
Non-Outage | J.E.26.06.08807 | C001839069 | Odeanie Davis | KSAS | Completed | Load_264573 | Up Park Camp - 310 | Jul 3, 2026 10:01am | Jul 3, 2026 10:02am | Jul 3, 2026 11:55am | Jul 3, 2026 1:23pm | Jul 3, 2026 1:23pm | Jul 3, 2026 1:29pm | Jul 3, 2026 1:23pm | Jul 3, 2026 1:23pm |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.06.23278 | C001839071 | Odeanie Davis | KSAS | Completed | Load_254908 | Up Park Camp - 310 | Jul 3, 2026 10:01am | Jul 3, 2026 10:02am | Jul 3, 2026 11:08am | Jul 3, 2026 11:24am | Jul 3, 2026 11:24am | Jul 3, 2026 11:27am | Jul 3, 2026 11:27am | Jul 3, 2026 11:27am |  |  | Fair | No | 119v/118v & 238v in meter socket at location, no power issues at location.
Non-Outage | J.E.26.06.31463 | C001839072 | Odeanie Davis | KSAS | Completed | Load_241686 | Rockfort - 410 | Jul 3, 2026 10:01am | Jul 3, 2026 10:02am | Jul 3, 2026 11:55am | Jul 3, 2026 11:55am | Jul 3, 2026 11:55am | Jul 3, 2026 12:36pm | Jul 3, 2026 12:36pm | Jul 3, 2026 12:36pm |  |  | Fair | No | Customer defective wires at pothead and in meter socket, customer was advised to contact their electrician,116v/112v & 228v at pothead
Non-Outage | J.E.26.06.32162 | C001839073 | Odeanie Davis | KSAS | Completed | Load_239504 | Rockfort - 410 | Jul 3, 2026 10:01am | Jul 3, 2026 10:02am | Jul 3, 2026 11:55am | Jul 3, 2026 1:39pm | Jul 3, 2026 1:39pm | Jul 3, 2026 1:46pm | Jul 3, 2026 1:40pm | Jul 3, 2026 1:40pm |  |  | Fair | No | Customer stated that issue was resolved by Jps
Non-Outage | J.E.26.06.32174 | C001839074 | Odeanie Davis | KSAS | Completed | Load_239504 | Rockfort - 410 | Jul 3, 2026 10:01am | Jul 3, 2026 10:02am | Jul 3, 2026 11:55am | Jul 3, 2026 4:01pm | Jul 3, 2026 4:01pm | Jul 3, 2026 4:09pm | Jul 3, 2026 4:02pm | Jul 3, 2026 4:02pm |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.06.33408 | C001839075 | Odeanie Davis | KSAS | Completed | Load_245749 | Rockfort - 210 | Jul 3, 2026 10:01am | Jul 3, 2026 10:02am | Jul 3, 2026 11:55am | Jul 3, 2026 12:36pm | Jul 3, 2026 12:50pm | Jul 3, 2026 12:59pm | Jul 3, 2026 1:18pm | Jul 3, 2026 1:18pm |  |  | Fair | No | 107v/ 107v & 214v at location from secondary, this is also affecting the other all the customers on this secondary line, EMERGENCY team needed, c
Non-Outage | J.E.26.07.01840 | C001839060 | Shamour Haughton | null | Completed | null | null | Jul 3, 2026 9:51am | Jul 3, 2026 9:54am | Jul 3, 2026 10:54am | Jul 3, 2026 10:54am | Jul 3, 2026 11:15am | Jul 3, 2026 11:15am | Jul 3, 2026 11:18am | Jul 3, 2026 11:18am | BrokenWire |  | Fair | No | Unable to locate customer, premises not found, need proper direction and a contract number also needs meter number
Non-Outage | J.E.26.06.10694 | C001839054 | Donald Cunningham | St.Catherine | Completed | Load_242081 | Tredegar - 510 | Jul 3, 2026 9:50am | Jul 3, 2026 9:50am | Jul 3, 2026 10:36am | Jul 3, 2026 10:36am | Jul 3, 2026 11:12am | Jul 3, 2026 11:18am | Jul 3, 2026 11:37am | Jul 3, 2026 11:37am | Fire |  | Fair | No | No fire seen customer stated he didn’t make any report
Non-Outage | J.E.26.05.07093 | C001839053 | Donald Cunningham | St.Catherine | Completed | Load_556519 | Tredegar - 510 | Jul 3, 2026 9:48am | Jul 3, 2026 9:49am | Jul 3, 2026 11:44am | Jul 3, 2026 11:44am | Jul 3, 2026 12:24pm | Jul 3, 2026 12:26pm | Jul 3, 2026 12:28pm | Jul 3, 2026 12:28pm | LeaningPole |  | Fair | No | 30 class 6 need to dig and straighten
Non-Outage | J.E.26.07.01222 | C001839052 | Wan Carlos Scarlett | null | Completed | null | null | Jul 3, 2026 9:47am | Jul 3, 2026 9:48am | Jul 3, 2026 10:40am | Jul 3, 2026 10:40am | Jul 3, 2026 10:56am | Jul 3, 2026 11:05am | Jul 3, 2026 11:08am | Jul 3, 2026 11:08am | LowHangingWires |  | Fair | No | Call related to vechile accident advised customer to contact a licensed electrician to resolve the issue and contact JPS when issues has resolved
Outage | J.E.26.07.01863 | C001839046 | Ryan Richards | Manchester | Completed | Load_267284 | Spur Tree - 310 | Jul 3, 2026 9:43am | Jul 3, 2026 3:36pm | Jul 3, 2026 6:48pm | Jul 3, 2026 7:31pm | Jul 3, 2026 8:46pm | Jul 3, 2026 9:30pm | Jul 3, 2026 9:31pm | Jul 3, 2026 9:31pm |  |  | Fair | No | Corroded phase and neutral found at pothead and pole remade pothead using 3 penunion remade pole using 3 one bolt clamps voltage 115/116/232 volts
Non-Outage | J.E.26.07.01776 | C001839020 | Clyde Brown | null | Completed | null | null | Jul 3, 2026 9:32am | Jul 3, 2026 9:33am | Jul 3, 2026 9:40am | Jul 3, 2026 9:40am | Jul 3, 2026 10:59am | Jul 3, 2026 10:52am | Jul 3, 2026 11:09am | Jul 3, 2026 11:09am |  | Y | Fair | No | Secondary open wire and #2 service line in bushes across gully and 1-30c6 pole broken and neutral wire also broken ,line need extensive bushing and broken pole to be replaced for 2 customers that are without supply.
Outage | J.E.26.07.01823 | C001839018 | Clyde Brown | Clarendon | Completed | Load_579438 | May Pen - 110 | Jul 3, 2026 9:32am | Jul 3, 2026 9:33am | Jul 3, 2026 1:37pm | Jul 3, 2026 1:37pm | Jul 3, 2026 1:37pm | Jul 3, 2026 1:30pm | Jul 3, 2026 1:42pm | Jul 3, 2026 1:42pm | BrokenWire |  | Fair | No | Cannot be located customer not answering phone
Outage | J.E.26.07.01848 | C001839019 | Clyde Brown | Clarendon | Completed | Load_247364 | May Pen - 110 | Jul 3, 2026 9:32am | Jul 3, 2026 9:33am | Jul 3, 2026 11:09am | Jul 3, 2026 11:09am | Jul 3, 2026 1:28pm | Jul 3, 2026 1:25pm | Jul 3, 2026 1:33pm | Jul 3, 2026 1:33pm |  |  | Fair | No | Blown 3 amps fuse for 25 kva transformer,line patrolled and no fault seen,blown fuse replaced.
Outage | J.E.26.07.01844 | C001839001 | Richard Watson | St.Elizabeth | Completed | Load_302924 | Maggotty - 110 | Jul 3, 2026 9:23am | Jul 3, 2026 9:24am | Jul 3, 2026 11:54am | Jul 3, 2026 11:54am | Jul 3, 2026 11:55am | Jul 3, 2026 11:57am | Jul 3, 2026 11:57am | Jul 3, 2026 11:57am |  |  | Fair | No | Customer contacted by phone and stated that the supply was restored.
Outage | J.E.26.07.01850 | C001839000 | Richard Watson | St.Elizabeth | Completed | Load_1002145 | Maggotty - 110 | Jul 3, 2026 9:23am | Jul 3, 2026 9:24am | Jul 3, 2026 1:05pm | Jul 3, 2026 1:05pm | Jul 3, 2026 1:05pm | Jul 3, 2026 1:06pm | Jul 3, 2026 1:07pm | Jul 3, 2026 1:07pm |  |  | Fair | No | Report referred to field service department for re-connection.
Non-Outage | J.E.26.02.22885 | C001838998 | Ricky Hall | St.Catherine | Completed | Load_241966 | Rhodens Pen - 210 | Jul 3, 2026 9:21am | Jul 3, 2026 9:27am | Jul 3, 2026 10:45am | Jul 3, 2026 10:45am | Jul 3, 2026 11:37am | Jul 3, 2026 11:40am | Jul 3, 2026 11:41am | Jul 3, 2026 11:41am | LowHangingWires |  | Fair | No | Issue was resolved previously
Outage | J.E.26.07.01849 | C001838999 | Kenroy Dale | Manchester | Completed | Load_242146 | Porus - 310 | Jul 3, 2026 9:21am | Jul 3, 2026 9:21am | Jul 3, 2026 10:11am | Jul 3, 2026 11:42am | Jul 3, 2026 1:23pm | Jul 3, 2026 2:18pm | Jul 3, 2026 2:19pm | Jul 3, 2026 2:19pm |  |  | Fair | No | Blown 10 amp junction fuse found. Line patrol tree branch found touching primary, switch stick was used to remove tree branch and blown fuse replaced, site now with supply
Outage | J.E.26.07.01812 | C001838993 | Wan Carlos Scarlett | St.Catherine | Completed | Load_240687 | Tredegar - 210 | Jul 3, 2026 9:18am | Jul 3, 2026 9:19am | Jul 3, 2026 10:36am | Jul 3, 2026 11:08am | Jul 3, 2026 11:50am | Jul 3, 2026 12:18pm | Jul 3, 2026 12:20pm | Jul 3, 2026 12:20pm |  |  | Fair | No | Found customer 3 wire service at pothead with phase and neutral corroded use 2 Penn union at service wire phase readings 115-116-231
Outage | J.E.26.07.01826 | C001838985 | Daniel Francis | St.Ann | Completed | Load_254787 | Roaring River - 210 | Jul 3, 2026 9:06am | Jul 3, 2026 9:08am | Jul 3, 2026 1:02pm | Jul 3, 2026 1:02pm | Jul 3, 2026 1:39pm | Jul 3, 2026 1:43pm | Jul 3, 2026 1:43pm | Jul 3, 2026 1:43pm |  |  | Fair | No | Found ok power restored
Outage | J.E.26.07.01811 | C001838978 | Shamour Haughton | St.James | Completed | Load_237873 | Bogue - 510 | Jul 3, 2026 9:02am | Jul 3, 2026 9:03am | Jul 3, 2026 9:13am | Jul 3, 2026 9:13am | Jul 3, 2026 10:48am | Jul 3, 2026 10:48am | Jul 3, 2026 10:52am | Jul 3, 2026 10:52am | Fire |  | Fair | No | Customer service wire burnt up, meter socket defective and pothead corroded, customer is advised to get an electrician and after, they can reach out to JPS for reconnection
Outage | J.E.26.07.01296 | C001838977 | Dean Smith | Hanover | Completed | Load_239009 | Orange Bay - 310 | Jul 3, 2026 9:01am | Jul 3, 2026 9:02am | Jul 3, 2026 2:31pm | Jul 3, 2026 2:31pm | Jul 3, 2026 2:31pm | Jul 3, 2026 2:31pm | Jul 3, 2026 2:32pm | Jul 3, 2026 2:32pm |  |  | Rains | No | Check and found ok, electricity was confirmed at the school. Voltage left 115v,115v,230v
Non-Outage | J.E.26.07.01815 | C001838964 | Romaine Roberts | St.Mary | Completed | Load_247430 | Highgate - 210 | Jul 3, 2026 8:57am | Jul 3, 2026 9:06am | Jul 3, 2026 11:48am | Jul 3, 2026 11:48am | Jul 3, 2026 1:49pm | Jul 3, 2026 12:18pm | Jul 3, 2026 2:02pm | Jul 3, 2026 2:02pm |  |  | Fair | No | High wind and vegetation bang secondary conductor cedar line and retention secondary phase
Non-Outage | J.E.26.07.01212 | C001838957 | Gregory Grossett | Portland | Completed | Load_266237 | Port Antonio - 410 | Jul 3, 2026 8:51am | Jul 3, 2026 8:52am | Jul 3, 2026 10:53am | Jul 3, 2026 10:54am | Jul 3, 2026 11:33am | Jul 3, 2026 12:27pm | Jul 3, 2026 12:28pm | Jul 3, 2026 12:28pm |  |  | Fair | No | 220 service wire corroded at pothead joints repair and ok material use 6 penunion sleeves voltage reading 118/119/237 on both phase.
Non-Outage | J.E.26.07.01793 | C001838950 | Collin Robinson | Portland | Completed | Load_249793 | Port Antonio - 310 | Jul 3, 2026 8:50am | Jul 3, 2026 8:50am | Jul 3, 2026 10:14am | Jul 3, 2026 10:14am | Jul 3, 2026 11:13am | Jul 3, 2026 11:30am | Jul 3, 2026 11:30am | Jul 3, 2026 11:30am |  |  | Fair | No | Customer meter defective Voltage reading 117v 118v 235v
Non-Outage | J.E.26.06.38999 | C001838947 | Royston Montague | St.Catherine | Completed | Load_267379 | Tredegar - 310 | Jul 3, 2026 8:46am | Jul 3, 2026 8:48am | Jul 3, 2026 8:57am | Jul 3, 2026 9:52am | Jul 3, 2026 10:32am | Jul 3, 2026 10:33am | Jul 3, 2026 10:33am | Jul 3, 2026 10:33am |  |  | Fair | No | Customer confirmed issue resolved few days ago.
Non-Outage | J.E.26.07.00569 | C001838948 | Royston Montague | St.Catherine | Completed | Load_241753 | Tredegar - 310 | Jul 3, 2026 8:46am | Jul 3, 2026 8:48am | Jul 3, 2026 8:57am | Jul 3, 2026 9:34am | Jul 3, 2026 9:48am | Jul 3, 2026 9:50am | Jul 3, 2026 9:51am | Jul 3, 2026 9:51am |  |  | Fair | No | Faulty meter socket in pmc box, same needs to repair. Customer having this problem over many months now. Please inform field service department thanks. Voltage 228v 112v 113v
Outage | J.E.26.07.01809 | C001838946 | Daniel Francis | St.Ann | Completed | Load_249727 | Roaring River - 210 | Jul 3, 2026 8:45am | Jul 3, 2026 8:47am | Jul 3, 2026 10:23am | Jul 3, 2026 10:23am | Jul 3, 2026 11:15am | Jul 3, 2026 11:18am | Jul 3, 2026 11:18am | Jul 3, 2026 11:18am |  |  | Fair | No | Premises lock
Outage | J.E.26.07.01766 | C001838940 | Richard Watson | St.Elizabeth | Completed | Load_241313 | Maggotty - 110 | Jul 3, 2026 8:44am | Jul 3, 2026 8:44am | Jul 3, 2026 9:12am | Jul 3, 2026 9:12am | Jul 3, 2026 9:12am | Jul 3, 2026 9:14am | Jul 3, 2026 9:22am | Jul 3, 2026 9:22am |  |  | Fair | No | Customer is making a report that stating that he received a bill for $3538.76 even though there is no supply to the premises and the house is also undergoing construction work. Customer advised to make a report at the nearest JPS commercial office.
Outage | J.E.26.07.01769 | C001838941 | Wayne Dillion | Manchester | Completed | Load_1002239 | Spur Tree - 210 | Jul 3, 2026 8:44am | Jul 3, 2026 8:44am | Jul 3, 2026 9:52am | Jul 3, 2026 9:52am | Jul 3, 2026 10:07am | Jul 3, 2026 10:30am | Jul 3, 2026 11:02am | Jul 3, 2026 11:02am |  |  | Fair | No | Supply check and found customer single phasing remade joint at pole and pot head and using 3 linket 3 one bolt voltage reading 109v 108v 218v supply working ok
Non-Outage | J.E.26.06.28651 | C001838937 | Royston Montague | St.Catherine | Completed | Load_245034 | Tredegar - 410 | Jul 3, 2026 8:43am | Jul 3, 2026 8:45am | Jul 3, 2026 8:57am | Jul 3, 2026 3:27pm | Jul 3, 2026 4:02pm | Jul 3, 2026 4:02pm | Jul 3, 2026 4:02pm | Jul 3, 2026 4:02pm |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.06.35297 | C001838938 | Royston Montague | St.Catherine | Completed | Load_240973 | Tredegar - 410 | Jul 3, 2026 8:43am | Jul 3, 2026 8:45am | Jul 3, 2026 8:57am | Jul 3, 2026 11:56am | Jul 3, 2026 12:46pm | Jul 3, 2026 12:48pm | Jul 3, 2026 12:48pm | Jul 3, 2026 12:48pm |  |  | Fair | No | Customer confirmed she has no issue with her supply.
Non-Outage | J.E.26.07.01653 | C001838939 | Royston Montague | St.Catherine | Completed | Load_250553 | Tredegar - 410 | Jul 3, 2026 8:43am | Jul 3, 2026 8:45am | Jul 3, 2026 8:57am | Jul 3, 2026 2:49pm | Jul 3, 2026 3:26pm | Jul 3, 2026 3:27pm | Jul 3, 2026 3:27pm | Jul 3, 2026 3:27pm |  |  | Fair | No | Customer confirmed issue resolved
Non-Outage | J.E.26.06.11326 | C001838934 | Royston Montague | St.Catherine | Completed | Load_1000960 | Tredegar - 410 | Jul 3, 2026 8:42am | Jul 3, 2026 8:45am | Jul 3, 2026 8:57am | Jul 3, 2026 1:06pm | Jul 3, 2026 2:48pm | Jul 3, 2026 2:48pm | Jul 3, 2026 2:48pm | Jul 3, 2026 2:48pm |  |  | Fair | No | Customer confirmed issue resolved. Please update thanks.
Outage | J.E.26.07.01796 | C001838932 | Richard Samuda | Manchester | Completed | Load_292103 | Kendal - 210 | Jul 3, 2026 8:37am | Jul 3, 2026 8:38am | Jul 3, 2026 11:31am | Jul 3, 2026 11:31am | Jul 3, 2026 11:31am | Jul 3, 2026 11:31am | Jul 3, 2026 11:32am | Jul 3, 2026 11:32am |  |  | Fair | No | Found okay other crew went there
Outage | J.E.26.07.01800 | C001838931 | Oshane Warren | Westmoreland | Completed | Load_262638 | Paradise - 110 | Jul 3, 2026 8:36am | Jul 3, 2026 8:37am | Jul 3, 2026 9:54am | Jul 3, 2026 9:54am | Jul 3, 2026 10:51am | Jul 3, 2026 10:51am | Jul 3, 2026 10:52am | Jul 3, 2026 10:52am |  |  | Fair | No | Customer meter is disconnected need to reconnect voltage 111 111 222
Outage | J.E.26.07.01786 | C001838924 | Oshane Warren | Westmoreland | Completed | Load_254102 | Paradise - 210 | Jul 3, 2026 8:30am | Jul 3, 2026 8:30am | Jul 3, 2026 12:31pm | Jul 3, 2026 12:31pm | Jul 3, 2026 2:24pm | Jul 3, 2026 2:26pm | Jul 3, 2026 2:28pm | Jul 3, 2026 2:28pm |  |  | Rains | No | Reconnection back service wire neutral at pathead voltage 121 121 242
Non-Outage | J.E.26.06.39006 | C001838920 | Marlon Brown | Trelawny | Completed | Load_257854 | Greenwood - 110 | Jul 3, 2026 8:23am | Jul 4, 2026 9:20am | Jul 4, 2026 10:34am | Jul 4, 2026 10:34am | Jul 4, 2026 12:40pm | Jul 4, 2026 12:41pm | Jul 4, 2026 12:42pm | Jul 4, 2026 12:42pm |  |  | Fair | No | Unable to locate customer via telephone nor direction
Non-Outage | J.E.26.07.00691 | C001838915 | Orville Lee | Portmore | Completed | Load_1004132 | Naggo Head - 510 | Jul 3, 2026 8:15am | Jul 3, 2026 8:16am | Jul 3, 2026 3:58pm | Jul 3, 2026 3:58pm | Jul 3, 2026 4:03pm | Jul 3, 2026 4:04pm | Jul 3, 2026 4:05pm | Jul 3, 2026 4:05pm |  |  | Fair | No | Premise found ok upon arrival Issues appears to be feeder related
Non-Outage | J.E.26.07.00697 | C001838914 | Orville Lee | Portmore | Completed | Load_1004099 | Naggo Head - 510 | Jul 3, 2026 8:15am | Jul 3, 2026 8:16am | Jul 3, 2026 3:39pm | Jul 3, 2026 3:40pm | Jul 3, 2026 3:51pm | Jul 3, 2026 3:57pm | Jul 3, 2026 3:58pm | Jul 3, 2026 3:58pm |  |  | Fair | No | Premise found ok upon arrival Issues appears to be feeder related
Non-Outage | J.E.26.07.00926 | C001838913 | Rodclif Dawkins | Portmore | Completed | Load_248667 | Naggo Head - 510 | Jul 3, 2026 8:15am | Jul 3, 2026 12:06pm | Jul 3, 2026 1:32pm | Jul 3, 2026 1:35pm | Jul 3, 2026 1:47pm | Jul 3, 2026 11:58am | Jul 3, 2026 2:26pm | Jul 3, 2026 2:26pm |  |  | Fair | No | Customer service wire connection in mid span.Mid Span connections corroded Refer to bucket truck to change mid span wrap on connectionsUsing 2 penunion and 3-1bolt clamps joints remade. Customer okay
Non-Outage | J.E.26.07.01288 | C001838909 | Orville Lee | Portmore | Completed | Load_266766 | Naggo Head - 610 | Jul 3, 2026 8:14am | Jul 3, 2026 8:16am | Jul 3, 2026 8:57am | Jul 3, 2026 9:49am | Jul 3, 2026 9:50am | Jul 3, 2026 10:17am | Jul 3, 2026 10:18am | Jul 3, 2026 10:18am |  |  | Fair | No | Checks made and found service wire disconnected from secondary line Service wire reconnected Voltage 117V118V237V
Non-Outage | J.E.26.07.01340 | C001838908 | Orville Lee | Portmore | Completed | Load_253463 | Naggo Head - 610 | Jul 3, 2026 8:14am | Jul 3, 2026 8:16am | Jul 3, 2026 8:58am | Jul 3, 2026 10:23am | Jul 3, 2026 10:28am | Jul 3, 2026 11:34am | Jul 3, 2026 11:34am | Jul 3, 2026 11:34am |  |  | Fair | No | Checks made and found secondary connection corroded 5- one bolt clamps use and a Penn unionVoltage 120V118V237V
Non-Outage | J.E.26.07.01782 | C001838911 | Dwain Samuels | Westmoreland | Completed | Load_252353 | Paradise - 310 | Jul 3, 2026 8:14am | Jul 3, 2026 12:01pm | Jul 3, 2026 12:06pm | Jul 3, 2026 1:15pm | Jul 3, 2026 1:15pm | Jul 3, 2026 1:19pm | Jul 3, 2026 1:22pm | Jul 3, 2026 1:22pm |  |  | Fair | No | Connected 3 wire meter. Use 17ft #6 service wire. Voltage check 118-119-237
Non-Outage | J.E.26.07.01342 | C001838907 | Orville Lee | St.Catherine | Completed | Load_254535 | Twickenham - 210 | Jul 3, 2026 8:13am | Jul 3, 2026 8:16am | Jul 3, 2026 3:12pm | Jul 3, 2026 3:12pm | Jul 3, 2026 3:29pm | Jul 3, 2026 3:32pm | Jul 3, 2026 3:32pm | Jul 3, 2026 3:32pm |  |  | Fair | No | Premises not foundMultiple calls to customer unanswered
Non-Outage | J.E.26.07.01359 | C001838906 | Orville Lee | St.Catherine | Completed | Load_266814 | Twickenham - 210 | Jul 3, 2026 8:13am | Jul 3, 2026 8:16am | Jul 3, 2026 2:15pm | Jul 3, 2026 2:48pm | Jul 3, 2026 2:50pm | Jul 3, 2026 3:10pm | Jul 3, 2026 3:10pm | Jul 3, 2026 3:10pm |  |  | Fair | No | Pole 0006787 Badly leaning Pole hold in position by customer Stantion Multiple customer experience fluctuations of voltage Voltage 114V115V229V
Non-Outage | J.E.26.07.01730 | C001838904 | Roemello Brown | Trelawny | Completed | Load_292776 | Greenwood - 210 | Jul 3, 2026 8:13am | Jul 3, 2026 8:14am | Jul 3, 2026 10:52am | Jul 3, 2026 1:32pm | Jul 3, 2026 1:33pm | Jul 3, 2026 1:43pm | Jul 3, 2026 1:48pm | Jul 3, 2026 1:48pm |  |  | Fair | No | Transformer overload lots of illegal connections in the area need strike force team to assist Voltage found 107/101/208Voltage leave 107/101/208
Non-Outage | J.E.26.07.01735 | C001838903 | Roemello Brown | Trelawny | Completed | Load_259114 | Greenwood - 210 | Jul 3, 2026 8:13am | Jul 3, 2026 8:14am | Jul 3, 2026 10:51am | Jul 3, 2026 11:58am | Jul 3, 2026 12:48pm | Jul 3, 2026 12:49pm | Jul 3, 2026 12:56pm | Jul 3, 2026 12:56pm |  |  | Fair | No | Transformer drop lead burn off need emergency team to assist a section off the community single phasing Voltage found 111/21.63/99Voltage leave 111/21.63/99
Outage | J.E.26.07.01490 | C001838905 | Richard Watson | St.Elizabeth | Completed | Load_237951 | Maggotty - 110 | Jul 3, 2026 8:13am | Jul 3, 2026 8:13am | Jul 3, 2026 8:27am | Jul 3, 2026 8:27am | Jul 3, 2026 8:28am | Jul 3, 2026 8:29am | Jul 3, 2026 8:33am | Jul 3, 2026 8:33am |  |  | Fair | No | Unable to reach customer by phone or locate customer premises.
Non-Outage | J.E.26.07.01374 | C001838901 | Orville Lee | Portmore | Completed | Load_253463 | Naggo Head - 610 | Jul 3, 2026 8:12am | Jul 3, 2026 8:16am | Jul 3, 2026 8:57am | Jul 3, 2026 11:35am | Jul 3, 2026 11:35am | Jul 3, 2026 11:36am | Jul 3, 2026 11:37am | Jul 3, 2026 11:37am |  |  | Fair | No | Checks made and found secondary connection corroded 5- one bolt clamps use and a Penn unionVoltage 120V118V237V
Non-Outage | J.E.26.07.01398 | C001838900 | Orville Lee | Portmore | Completed | Load_264295 | Naggo Head - 610 | Jul 3, 2026 8:12am | Jul 3, 2026 8:16am | Jul 3, 2026 8:57am | Jul 3, 2026 8:58am | Jul 3, 2026 9:03am | Jul 3, 2026 9:36am | Jul 3, 2026 9:39am | Jul 3, 2026 9:39am | LeaningPole |  | Fair | No | Relocate service wire from broken Stantion6 Penn union used Voltage 117V118V236V
Non-Outage | J.E.26.07.01715 | C001838902 | Roemello Brown | Trelawny | Completed | Load_292361 | Greenwood - 210 | Jul 3, 2026 8:12am | Jul 3, 2026 8:14am | Jul 3, 2026 10:51am | Jul 3, 2026 1:11pm | Jul 3, 2026 1:11pm | Jul 3, 2026 1:11pm | Jul 3, 2026 1:32pm | Jul 3, 2026 1:32pm | Fire |  | Fair | No | Premises found working okay Voltage found 116/117/233Voltage leave 116/117/233
Non-Outage | J.E.26.07.00614 | C001838897 | Dwain Samuels | Westmoreland | Completed | Load_268696 | Paradise - 210 | Jul 3, 2026 8:11am | Jul 3, 2026 8:11am | Jul 3, 2026 8:15am | Jul 3, 2026 9:59am | Jul 3, 2026 9:59am | Jul 3, 2026 10:03am | Jul 3, 2026 10:05am | Jul 3, 2026 10:05am |  |  | Fair | No | Corrosion found at 3 wire pole. Corrosion cleared use 3 one bolt clamp. Voltage check 126-117-233
Non-Outage | J.E.26.07.00654 | C001838896 | Dwain Samuels | Westmoreland | Completed | Load_260662 | Paradise - 210 | Jul 3, 2026 8:11am | Jul 3, 2026 8:11am | Jul 3, 2026 8:15am | Jul 3, 2026 9:55am | Jul 3, 2026 9:55am | Jul 3, 2026 9:56am | Jul 3, 2026 9:57am | Jul 3, 2026 9:57am |  |  | Fair | No | Found working okay. Voltage check 116-118-234. Customer has internal problems
Non-Outage | J.E.26.07.01067 | C001838894 | Dwain Samuels | Westmoreland | Completed | Load_248205 | Paradise - 210 | Jul 3, 2026 8:11am | Jul 3, 2026 8:11am | Jul 3, 2026 8:15am | Jul 4, 2026 9:09am | Jul 4, 2026 9:09am | Jul 4, 2026 9:37am | Jul 4, 2026 9:38am | Jul 4, 2026 9:38am |  |  | Fair | No | Area affected by low voltage transformer feeding too far
Non-Outage | J.E.26.07.01510 | C001838893 | Dwain Samuels | Westmoreland | Completed | Load_292063 | Paradise - 210 | Jul 3, 2026 8:11am | Jul 3, 2026 8:11am | Jul 3, 2026 8:15am | Jul 3, 2026 12:12pm | Jul 3, 2026 12:12pm | Jul 3, 2026 12:33pm | Jul 3, 2026 12:34pm | Jul 3, 2026 12:34pm |  |  | Fair | No | Corrosion found at 3 wire pole. Corrosion clear at pole
Non-Outage | J.E.26.07.01677 | C001838895 | Dwain Samuels | Westmoreland | Completed | Load_255815 | Paradise - 210 | Jul 3, 2026 8:11am | Jul 3, 2026 8:11am | Jul 3, 2026 8:15am | Jul 3, 2026 8:41am | Jul 3, 2026 8:56am | Jul 3, 2026 9:03am | Jul 3, 2026 9:06am | Jul 3, 2026 9:06am |  |  | Fair | No | Meter found burnt . Needs to be changed
Outage | J.E.26.07.01771 | C001838891 | Jermaine Williams | Clarendon | Completed | Load_249529 | May Pen - 110 | Jul 3, 2026 8:04am | Jul 3, 2026 8:05am | Jul 3, 2026 9:34am | Jul 3, 2026 9:34am | Jul 3, 2026 10:28am | Jul 3, 2026 10:47am | Jul 3, 2026 10:48am | Jul 3, 2026 10:48am |  |  | Fair | No | Patrol and replaced blown 15amp junction fuse.
Non-Outage | J.E.26.07.00479 | C001838888 | Error Coore | Manchester | Completed | Load_251799 | Spur Tree - 310 | Jul 3, 2026 8:00am | Jul 3, 2026 8:03am | Jul 3, 2026 3:04pm | Jul 3, 2026 3:04pm | Jul 3, 2026 3:30pm | Jul 3, 2026 4:00pm | Jul 3, 2026 4:02pm | Jul 3, 2026 4:02pm |  |  | Fair | No | Premise found ok voltage reading 114/116/230 volts
Non-Outage | J.E.26.07.00503 | C001838887 | Error Coore | Manchester | Completed | Load_251799 | Spur Tree - 310 | Jul 3, 2026 8:00am | Jul 3, 2026 8:03am | Jul 3, 2026 4:02pm | Jul 3, 2026 4:02pm | Jul 3, 2026 4:02pm | Jul 3, 2026 4:03pm | Jul 3, 2026 4:03pm | Jul 3, 2026 4:03pm |  |  | Fair | No | Same as other
Non-Outage | J.E.26.07.00878 | C001838886 | Error Coore | Manchester | Completed | Load_257142 | Spur Tree - 310 | Jul 3, 2026 8:00am | Jul 3, 2026 8:03am | Jul 3, 2026 11:32am | Jul 3, 2026 11:32am | Jul 3, 2026 12:21pm | Jul 3, 2026 12:53pm | Jul 3, 2026 12:55pm | Jul 3, 2026 12:55pm |  |  | Flood | No | Premise not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.07.00907 | C001838885 | Error Coore | Manchester | Completed | Load_265918 | Spur Tree - 310 | Jul 3, 2026 8:00am | Jul 3, 2026 8:03am | Jul 3, 2026 12:55pm | Jul 3, 2026 12:55pm | Jul 3, 2026 1:40pm | Jul 3, 2026 2:01pm | Jul 3, 2026 2:02pm | Jul 3, 2026 2:02pm |  |  | Fair | No | Premise found ok customer said that the problem was resolved
Non-Outage | J.E.26.07.00941 | C001838884 | Error Coore | Manchester | Completed | Load_237731 | Spur Tree - 310 | Jul 3, 2026 8:00am | Jul 3, 2026 8:03am | Jul 3, 2026 9:56am | Jul 3, 2026 9:56am | Jul 3, 2026 10:43am | Jul 3, 2026 11:30am | Jul 3, 2026 11:32am | Jul 3, 2026 11:32am |  |  | Fair | No | Unable to carry out repair due to defective pole refer to emergency bucket truck team
Non-Outage | J.E.26.07.01140 | C001838882 | Error Coore | Manchester | Completed | Load_252759 | Spur Tree - 310 | Jul 3, 2026 8:00am | Jul 3, 2026 8:03am | Jul 3, 2026 8:17am | Jul 3, 2026 8:17am | Jul 3, 2026 8:48am | Jul 3, 2026 9:46am | Jul 3, 2026 9:48am | Jul 3, 2026 9:48am |  |  | Fair | No | Found customer with wrap connection at pothead remade wrap connection using 3 service sleeve however customer meter is defective customer need a new meter voltage reading 115/116/231 volts
Non-Outage | J.E.26.07.01416 | C001838883 | Error Coore | Manchester | Completed | Load_302087 | Spur Tree - 310 | Jul 3, 2026 8:00am | Jul 3, 2026 8:03am | Jul 3, 2026 2:03pm | Jul 3, 2026 2:03pm | Jul 3, 2026 2:55pm | Jul 3, 2026 3:02pm | Jul 3, 2026 3:04pm | Jul 3, 2026 3:04pm |  |  | Fair | No | Premise not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.06.38146 | C001838881 | Kenroy Dale | Manchester | Completed | Load_245958 | Kendal - 310 | Jul 3, 2026 7:58am | Jul 3, 2026 7:58am | Jul 3, 2026 8:06am | Jul 3, 2026 8:06am | Jul 3, 2026 9:09am | Jul 3, 2026 10:06am | Jul 3, 2026 10:11am | Jul 3, 2026 10:11am | BrokenPole |  | Fair | No | Area checked and pole found replaced customer also confirmed that supply has been restored
Non-Outage | J.E.26.05.13253 | C001838880 | Kemark Slue | null | Completed | null | null | Jul 3, 2026 7:56am | Jul 3, 2026 7:57am | Jul 3, 2026 12:17pm | Jul 3, 2026 1:46pm | Jul 3, 2026 2:01pm | Jul 3, 2026 1:41pm | Jul 3, 2026 2:03pm | Jul 3, 2026 2:03pm | Fire |  | Fair | No | Upon arrival at the location the crew didn’t see any form of an electrical fire, when customer was contacted via the telephone the customer stated that the issue has been resolved by a JPS crew.
Non-Outage | J.E.26.06.34594 | C001838875 | Kenroy Dale | Manchester | Completed | Load_266581 | Kendal - 310 | Jul 3, 2026 7:56am | Jul 3, 2026 7:56am | Jul 3, 2026 10:20am | Jul 3, 2026 10:20am | Jul 3, 2026 11:21am | Jul 3, 2026 11:40am | Jul 3, 2026 11:42am | Jul 3, 2026 11:42am |  |  | Fair | No | Burned off jumper found. Remade connection using one 1bolt clamp, voltage reading 115/115/230
Non-Outage | J.E.26.06.18932 | C001838867 | Kemark Slue | null | Completed | null | null | Jul 3, 2026 7:49am | Jul 3, 2026 7:51am | Jul 3, 2026 12:12pm | Jul 3, 2026 12:41pm | Jul 3, 2026 1:17pm | Jul 3, 2026 1:19pm | Jul 3, 2026 1:46pm | Jul 3, 2026 1:46pm | Fire |  | Fair | No | Upon arrival at the location the crew didn’t see any form of an electrical fire, when customer was contacted via the telephone the customer stated that the issue has been resolved by a JPS crew.
Non-Outage | J.E.26.06.19387 | C001838871 | Kemark Slue | null | Completed | null | null | Jul 3, 2026 7:49am | Jul 3, 2026 7:51am | Jul 3, 2026 9:58am | Jul 3, 2026 10:34am | Jul 3, 2026 10:34am | Jul 3, 2026 9:43am | Jul 3, 2026 10:58am | Jul 3, 2026 10:58am | Fire |  | Fair | No | Upon arrival at the location the crew didn’t see any or sign of an electrical fire, customer was contacted via telephone who stated that report was made awhile back.
Non-Outage | J.E.26.07.01658 | C001838868 | Oshane Warren | null | Completed | null | null | Jul 3, 2026 7:49am | Jul 3, 2026 7:49am | Jul 3, 2026 10:52am | Jul 3, 2026 10:53am | Jul 3, 2026 12:30pm | Jul 3, 2026 12:31pm | Jul 3, 2026 12:31pm | Jul 3, 2026 12:31pm |  |  | Fair | No | Check and found ok
Outage | J.E.26.07.01699 | C001838869 | Romaine Roberts | St.Mary | Completed | Load_260174 | Highgate - 210 | Jul 3, 2026 7:49am | Jul 3, 2026 7:53am | Jul 3, 2026 8:08am | Jul 3, 2026 8:08am | Jul 3, 2026 10:11am | Jul 3, 2026 11:47am | Jul 3, 2026 11:47am | Jul 3, 2026 11:47am |  |  | Fair | No | High wind bang and burn down 2 span secondary phase and neutral splice and retention conductor and replace 3 amp at 25 kva transformer
Outage | J.E.26.07.01549 | C001838863 | Rusean Allen | KSAS | Completed | Load_239004 | Rockfort - 410 | Jul 3, 2026 7:48am | Jul 3, 2026 7:48am | Jul 3, 2026 8:56am | Jul 3, 2026 8:56am | Jul 3, 2026 10:02am | Jul 3, 2026 10:06am | Jul 3, 2026 10:06am | Jul 3, 2026 10:06am |  |  | Fair | No | Found okay
Outage | J.E.26.07.01639 | C001838864 | Rusean Allen | KSAS | Completed | Load_266564 | Rockfort - 210 | Jul 3, 2026 7:48am | Jul 3, 2026 7:48am | Jul 3, 2026 10:11am | Jul 3, 2026 10:11am | Jul 3, 2026 10:19am | Jul 3, 2026 10:26am | Jul 3, 2026 10:27am | Jul 3, 2026 10:27am |  |  | Fair | No | Broken pole containing primary and secondary wires needs to be changed.Refer to maintenance department.
Outage | J.E.26.07.01663 | C001838865 | Rusean Allen | KSAS | Completed | Load_260265 | Up Park Camp - 510 | Jul 3, 2026 7:48am | Jul 3, 2026 7:48am | Jul 3, 2026 10:42am | Jul 3, 2026 10:42am | Jul 3, 2026 11:41am | Jul 3, 2026 11:43am | Jul 3, 2026 11:43am | Jul 3, 2026 11:43am |  |  | Fair | No | Customer reports streetlight not working.
Outage | J.E.26.07.01765 | C001838866 | Rusean Allen | KSAS | Completed | Load_266564 | Rockfort - 210 | Jul 3, 2026 7:48am | Jul 3, 2026 7:48am | Jul 3, 2026 10:27am | Jul 3, 2026 10:28am | Jul 3, 2026 10:28am | Jul 3, 2026 10:30am | Jul 3, 2026 10:31am | Jul 3, 2026 10:31am |  |  | Fair | No | Related to 12 D’Aguilar road
Outage | J.E.26.07.01360 | C001838860 | Edward Royal | KSAN | Completed | Load_239616 | Washington Blvd - 610 | Jul 3, 2026 7:47am | Jul 3, 2026 7:47am | Jul 3, 2026 9:26am | Jul 3, 2026 9:26am | Jul 3, 2026 9:52am | Jul 3, 2026 10:20am | Jul 3, 2026 10:20am | Jul 3, 2026 10:20am | TreeContact |  | Fair | No | Remove tree from service line customer also report about street light reffered to field service
Outage | J.E.26.07.01559 | C001838862 | Dwayne Samuels | Trelawny | Completed | Load_259114 | Greenwood - 210 | Jul 3, 2026 7:47am | Jul 3, 2026 10:59am | Jul 3, 2026 11:59am | Jul 3, 2026 11:59am | Jul 3, 2026 12:49pm | Jul 3, 2026 1:51pm | Jul 3, 2026 1:55pm | Jul 3, 2026 1:55pm |  |  | Fair | No | Damage transformer drop lead was the cause of customer low voltage issue open 1 25kva transformer fuse to repair damaged drop lead using about 5ft of #2 insulated copper wire and 1 one bolt clamp at same for repairs voltage left at pothead 115v/116v/231v
Outage | J.E.26.07.01584 | C001838861 | Richman Whyte | Westmoreland | Completed | Load_253644 | Paradise - 310 | Jul 3, 2026 7:47am | Jul 3, 2026 8:33am | Jul 3, 2026 12:32pm | Jul 3, 2026 12:32pm | Jul 3, 2026 12:32pm | Jul 3, 2026 2:33pm | Jul 3, 2026 2:33pm | Jul 3, 2026 2:33pm |  |  | Fair | No | Replace 10 amp junction fuse
Outage | J.E.26.07.01685 | C001838858 | Ryan Richards | Manchester | Completed | Load_249300 | Spur Tree - 310 | Jul 3, 2026 7:45am | Jul 3, 2026 3:36pm | Jul 3, 2026 5:57pm | Jul 3, 2026 5:57pm | Jul 3, 2026 7:02pm | Jul 3, 2026 7:30pm | Jul 3, 2026 7:30pm | Jul 3, 2026 7:30pm |  |  | Fair | No | Blown 2 amp fuse found for 10 kva transformer check made nothing found blown fuse was replaced and all customers are now with supply
Non-Outage | J.E.26.05.11594 | C001838856 | Kemark Slue | null | Completed | null | null | Jul 3, 2026 7:43am | Jul 3, 2026 7:44am | Jul 3, 2026 10:37am | Jul 3, 2026 11:35am | Jul 3, 2026 11:52am | Jul 3, 2026 11:58am | Jul 3, 2026 12:03pm | Jul 3, 2026 12:03pm | LeaningPole |  | Fair | No | Upon arrival at the location the crew discovered that a 30 ft Cl 6 DE secondary pole 98% rotten and badly leaning, pole consisting of three wire open secondary conductors, streetlight, three triplex service and telecommunications cable. Please refer to A. Murray to have pole changed asap.
Outage | J.E.26.07.00950 | C001838857 | Christopher Edwards | KSAN | Completed | Load_264577 | Constant Spring - 210 | Jul 3, 2026 7:43am | Jul 3, 2026 7:43am | Jul 3, 2026 9:42am | Jul 3, 2026 10:01am | Jul 3, 2026 10:34am | Jul 3, 2026 10:51am | Jul 3, 2026 10:53am | Jul 3, 2026 10:53am |  | Y | Fair | No | Refuse blown 15 kva transformer Using (1) 2 ampsClear vegetation off transformer pole
Outage | J.E.26.07.01668 | C001838854 | Hopeton Henry | St.Thomas | Completed | Load_263661 | Good Year - 110 | Jul 3, 2026 7:37am | Jul 3, 2026 7:38am | Jul 3, 2026 8:16am | Jul 3, 2026 8:16am | Jul 3, 2026 11:18am | Jul 3, 2026 11:26am | Jul 3, 2026 11:27am | Jul 3, 2026 11:27am |  |  | Fair | No | Customers not located
Non-Outage | J.E.26.07.01348 | C001838853 | Roxroy Needham | St.Ann | Completed | Load_263265 | Cardiff Hall - 210 | Jul 3, 2026 7:36am | Jul 3, 2026 7:37am | Jul 3, 2026 9:26am | Jul 3, 2026 9:26am | Jul 3, 2026 9:26am | Jul 3, 2026 9:26am | Jul 3, 2026 9:27am | Jul 3, 2026 9:27am |  |  | Fair | No | Replace a 50 amps junction fuse at pole
Outage | J.E.26.07.01680 | C001838852 | Edward Royal | KSAS | Completed | Load_266967 | Duhaney - 410 | Jul 3, 2026 7:33am | Jul 3, 2026 7:35am | Jul 3, 2026 8:38am | Jul 3, 2026 8:38am | Jul 3, 2026 8:58am | Jul 3, 2026 9:25am | Jul 3, 2026 9:25am | Jul 3, 2026 9:25am | BrokenWire |  | Fair | No | Customer have internal problems customer have defective pothead advise customer to get a electrician to fix the problem customer was disconnected
Outage | J.E.26.07.01691 | C001838851 | Horace Malcolm | St.James | Completed | Load_249162 | Bogue - 310 | Jul 3, 2026 7:32am | Jul 3, 2026 7:32am | Jul 3, 2026 7:51am | Jul 3, 2026 8:14am | Jul 3, 2026 9:28am | Jul 3, 2026 9:47am | Jul 3, 2026 9:47am | Jul 3, 2026 9:47am |  |  | Fair | No | Check and found field service issue referred to field service
Outage | J.E.26.07.01761 | C001838850 | Ricky Hall | St.Catherine | Completed | Load_261455 | Rhodens Pen - 410 | Jul 3, 2026 7:32am | Jul 3, 2026 7:32am | Jul 3, 2026 7:51am | Jul 3, 2026 8:23am | Jul 3, 2026 9:27am | Jul 3, 2026 10:43am | Jul 3, 2026 10:44am | Jul 3, 2026 10:44am |  |  | Fair | No | Splice and retention broken secondary phase Conductor remake xfmr drop lead joint use 1 automatic splice 2 clamps
Outage | J.E.26.07.01562 | C001838849 | Donald Cunningham | St.Catherine | Completed | Load_255999 | Tredegar - 410 | Jul 3, 2026 7:31am | Jul 3, 2026 7:32am | Jul 3, 2026 7:47am | Jul 3, 2026 7:47am | Jul 3, 2026 8:30am | Jul 3, 2026 8:30am | Jul 3, 2026 8:31am | Jul 3, 2026 8:31am |  |  | Fair | No | Supply restored
Outage | J.E.26.07.00957 | C001838847 | Donald Cunningham | St.Catherine | Completed | Load_237759 | Tredegar - 310 | Jul 3, 2026 7:30am | Jul 3, 2026 7:32am | Jul 3, 2026 9:18am | Jul 3, 2026 9:18am | Jul 3, 2026 9:58am | Jul 3, 2026 9:59am | Jul 3, 2026 10:00am | Jul 3, 2026 10:00am |  |  | Fair | No | Private electrician attended premises found ok
Outage | J.E.26.07.01261 | C001838848 | Donald Cunningham | St.Catherine | Completed | Load_250553 | Tredegar - 410 | Jul 3, 2026 7:30am | Jul 3, 2026 7:32am | Jul 3, 2026 8:31am | Jul 3, 2026 8:31am | Jul 3, 2026 9:16am | Jul 3, 2026 1:00am | Jul 3, 2026 9:18am | Jul 3, 2026 9:18am | Fire |  | Fair | No | Premises found ok supply restored
Outage | J.E.26.06.39265 | C001838843 | Rodclif Dawkins | Portmore | Completed | Load_257303 | Naggo Head - 510 | Jul 3, 2026 7:29am | Jul 3, 2026 7:29am | Jul 3, 2026 11:55am | Jul 3, 2026 11:55am | Jul 3, 2026 12:12pm | Jul 3, 2026 12:30pm | Jul 3, 2026 12:40pm | Jul 3, 2026 12:40pm |  |  | Fair | No | Please refer to Moses Elleston, customer is supplied by hexing box
Outage | J.E.26.07.01698 | C001838844 | Lancelot Brown | Hanover | Completed | Load_230038 | Orange Bay - 310 | Jul 3, 2026 7:29am | Jul 3, 2026 7:30am | Jul 3, 2026 8:04am | Jul 3, 2026 9:08am | Jul 3, 2026 9:43am | Jul 3, 2026 9:48am | Jul 3, 2026 9:48am | Jul 3, 2026 9:48am |  |  | Fair | No | Check and found old time 10kva single phasing one leg coming from transformer lug voltage reading at transformer lug 114-58 fluctuating down to 9.58 voltage not good from one lug 10kva need to replace please pass on to maintenance department in Hanover mr Richards need ergent attention bridge tied out the one leg that customer can have plugs
Outage | J.E.26.07.01752 | C001838846 | Lancelot Brown | Hanover | Completed | Load_230038 | Orange Bay - 310 | Jul 3, 2026 7:29am | Jul 3, 2026 7:30am | Jul 3, 2026 8:04am | Jul 3, 2026 9:48am | Jul 3, 2026 9:49am | Jul 3, 2026 9:50am | Jul 3, 2026 9:50am | Jul 3, 2026 9:50am |  |  | Fair | No | This call related to diffective 10kva pass on to maintenance department
Outage | J.E.26.07.01759 | C001838845 | Dean Smith | Hanover | Completed | Load_258562 | Orange Bay - 310 | Jul 3, 2026 7:29am | Jul 3, 2026 8:06am | Jul 3, 2026 10:05am | Jul 3, 2026 10:05am | Jul 3, 2026 12:21pm | Jul 3, 2026 12:21pm | Jul 3, 2026 2:30pm | Jul 3, 2026 2:30pm |  |  | Rains | No | Splice and retention #6 triplex service wire, voltage left 114v,115v,229v.
Outage | J.E.26.07.01544 | C001838842 | Christopher Edwards | KSAN | Completed | Load_247049 | Constant Spring - 410 | Jul 3, 2026 7:25am | Jul 3, 2026 7:26am | Jul 3, 2026 7:40am | Jul 3, 2026 10:53am | Jul 3, 2026 12:38pm | Jul 3, 2026 1:39pm | Jul 3, 2026 1:39pm | Jul 3, 2026 1:39pm |  |  | Rains | No | Refuse blown junction fuseUsing (1) 25 amps
Outage | J.E.26.07.01751 | C001838841 | Christopher Edwards | KSAN | Completed | Load_261806 | Constant Spring - 410 | Jul 3, 2026 7:25am | Jul 3, 2026 7:25am | Jul 3, 2026 1:39pm | Jul 3, 2026 1:39pm | Jul 3, 2026 2:04pm | Jul 3, 2026 2:31pm | Jul 3, 2026 2:31pm | Jul 3, 2026 2:31pm |  |  | Rains | No | Refuse blown 25 kva transformer Using (1) 3 amps
Non-Outage | J.E.26.07.00607 | C001838836 | Wayne Dillion | Manchester | Completed | Load_302937 | Spur Tree - 210 | Jul 3, 2026 7:24am | Jul 3, 2026 7:24am | Jul 3, 2026 8:35am | Jul 3, 2026 8:35am | Jul 3, 2026 8:35am | Jul 3, 2026 8:35am | Jul 3, 2026 8:36am | Jul 3, 2026 8:36am | Fire |  | Fair | No | Customer said problem has been resolved and supply is working ok
Non-Outage | J.E.26.07.01323 | C001838837 | Daniel Francis | null | Completed | null | null | Jul 3, 2026 7:24am | Jul 3, 2026 7:24am | Jul 3, 2026 8:48am | Jul 3, 2026 8:48am | Jul 3, 2026 8:53am | Jul 3, 2026 9:28am | Jul 3, 2026 9:28am | Jul 3, 2026 9:28am | Fire |  | Fair | No | Change 3 one bolt clamp on JPS pole that was on fire 0099775 pole #
Non-Outage | J.E.26.07.01409 | C001838838 | Christopher Edwards | null | Completed | null | null | Jul 3, 2026 7:24am | Jul 3, 2026 7:25am | Jul 4, 2026 4:51pm | Jul 4, 2026 4:51pm | Jul 4, 2026 4:52pm | Jul 4, 2026 5:57pm | Jul 4, 2026 6:14pm | Jul 4, 2026 6:14pm |  |  | Fair | No | Remake corroded neutral joint Using (1) one bolt clamps Voltage:114,115,230v
Outage | J.E.26.07.01547 | C001838835 | Cliton Henry | St.Mary | Completed | Load_268948 | Oracabessa - 210 | Jul 3, 2026 7:19am | Jul 3, 2026 7:19am | Jul 3, 2026 10:02am | Jul 3, 2026 10:02am | Jul 3, 2026 10:39am | Jul 3, 2026 10:40am | Jul 3, 2026 10:40am | Jul 3, 2026 10:40am |  |  | Fair | No | Supply found ok
Outage | J.E.26.07.01692 | C001838833 | Cliton Henry | St.Mary | Completed | Load_259653 | Oracabessa - 110 | Jul 3, 2026 7:17am | Jul 3, 2026 7:18am | Jul 3, 2026 9:52am | Jul 3, 2026 9:53am | Jul 3, 2026 10:00am | Jul 3, 2026 10:01am | Jul 3, 2026 10:02am | Jul 3, 2026 10:02am |  |  | Fair | No | The customer supply found ok, the customer stated that she reporting a defective street light. Kindly refer to the street light department
Outage | J.E.26.07.01753 | C001838834 | Kemark Slue | St.Catherine | Completed | Load_255817 | New Michelton - 310 | Jul 3, 2026 7:17am | Jul 3, 2026 7:18am | Jul 3, 2026 7:41am | Jul 3, 2026 7:41am | Jul 3, 2026 9:48am | Jul 3, 2026 9:00am | Jul 3, 2026 10:32am | Jul 3, 2026 10:32am |  |  | Fair | No | Upon arrival at the location the crew discovered that a 8 amps junction fuse for single phase line section is blown resulting from a broken 35 ft Cl 6 DV primary pole, pole consisting of single phase primary conductor, streetlight, 2/0 triplex secondary and telecommunications cable. Please refer to A. Murray to have pole changed asap as pole is blocking school road.
Outage | J.E.26.07.01764 | C001838832 | Swon Miller | St.James | Completed | Load_267267 | Queens Drive - 810 | Jul 3, 2026 7:15am | Jul 3, 2026 7:15am | Jul 3, 2026 7:31am | Jul 3, 2026 7:31am | Jul 3, 2026 8:12am | Jul 14, 2026 9:50am | Jul 3, 2026 10:00am | Jul 3, 2026 10:00am |  |  | Fair | No | Found 2,50 amp junction fuse and 2,100 kva transformer fuse blown cause by contamination replace 2 ,50 am junction fuse at pole number 058319 replace 10 amp in two 100 kva transformer no pole number available
Outage | J.E.26.07.01745 | C001838828 | Edward Royal | KSAN | Completed | Load_575943 | Constant Spring - 210 | Jul 3, 2026 6:44am | Jul 3, 2026 7:36am | Jul 3, 2026 7:56am | Jul 3, 2026 7:56am | Jul 3, 2026 7:56am | Jul 3, 2026 8:01am | Jul 3, 2026 8:05am | Jul 3, 2026 8:05am |  |  | Fair | No | Contact customer by phone customer said he contact is electrician and the electrician said he contacted the solar company because the solar have a problem.
Outage | J.E.26.07.01696 | C001838742 | Marlon Authors | St.Elizabeth | Completed | Load_245894 | Maggotty - 210 | Jul 2, 2026 10:29pm | Jul 2, 2026 10:29pm | Jul 2, 2026 11:12pm | Jul 2, 2026 11:12pm | Jul 3, 2026 12:37am | Jul 3, 2026 12:45am | Jul 3, 2026 1:11am | Jul 3, 2026 1:11am | BrokenWire |  | Fair | No | Supply check and found service wire burnt off at pot head. Repair same using one clamp and one linket. Supply leave working okay.
Outage | J.E.26.07.01687 | C001838737 | Jermaine Williams | Clarendon | Completed | Load_264794 | Monymusk - 410 | Jul 2, 2026 9:55pm | Jul 3, 2026 8:03am | Jul 3, 2026 8:07am | Jul 3, 2026 8:07am | Jul 3, 2026 9:11am | Jul 3, 2026 9:23am | Jul 3, 2026 9:27am | Jul 3, 2026 9:27am |  |  | Fair | No | Broken 65’ CV transmission pole with three primary under built. Caused by motor vehicle accident, blown 30amp junction fuse also found. Refer to Z McDonald transmission dept.
Outage | J.E.26.07.01662 | C001838734 | Milton Charlton | KSAN | Completed | Load_261221 | Washington Blvd - 510 | Jul 2, 2026 9:32pm | Jul 2, 2026 9:33pm | Jul 2, 2026 9:49pm | Jul 2, 2026 9:49pm | Jul 2, 2026 10:02pm | Jul 2, 2026 10:10pm | Jul 2, 2026 10:07pm | Jul 2, 2026 10:07pm |  |  | Fair | No | Call related to call at #36 Hall crescent.
Non-Outage | J.E.26.07.01661 | C001838730 | Rusean Allen | null | Completed | null | null | Jul 2, 2026 9:19pm | Jul 3, 2026 7:40am | Jul 3, 2026 10:07am | Jul 3, 2026 10:39am | Jul 3, 2026 10:39am | Jul 3, 2026 10:41am | Jul 3, 2026 10:41am | Jul 3, 2026 10:41am | BrokenWire |  | Fair | No | Related to 12 daguilar rd
Non-Outage | J.E.26.07.01666 | C001838731 | Rusean Allen | null | Completed | null | null | Jul 2, 2026 9:19pm | Jul 3, 2026 7:40am | Jul 3, 2026 1:18pm | Jul 3, 2026 1:18pm | Jul 3, 2026 2:29pm | Jul 3, 2026 2:29pm | Jul 3, 2026 2:29pm | Jul 3, 2026 2:29pm | BrokenWire |  | Fair | No | Unable to locate
Outage | J.E.26.07.01667 | C001838726 | Rayon Foster | Hanover | Completed | Load_230038 | Orange Bay - 310 | Jul 2, 2026 9:04pm | Jul 2, 2026 9:05pm | Jul 2, 2026 10:00pm | Jul 2, 2026 10:01pm | Jul 2, 2026 10:13pm | Jul 2, 2026 10:23pm | Jul 2, 2026 10:24pm | Jul 2, 2026 10:24pm |  |  | Fair | No | Patrol secondary circuit to find 1 tripped 25kva transformer complete patrol before resetting transformer
Outage | J.E.26.07.01613 | C001838725 | Ryan Richards | Manchester | Completed | Load_260536 | Spur Tree - 210 | Jul 2, 2026 9:02pm | Jul 2, 2026 9:03pm | Jul 2, 2026 9:44pm | Jul 2, 2026 9:44pm | Jul 2, 2026 9:44pm | Jul 2, 2026 11:51pm | Jul 2, 2026 11:51pm | Jul 2, 2026 11:51pm |  |  | Fair | No | Blown 30 amp junction fuse found line patrol nothing found blown fuse was replaced and all customers are now with power
Non-Outage | J.E.26.07.01647 | C001838719 | Shamour Haughton | null | Completed | null | null | Jul 2, 2026 8:58pm | Jul 3, 2026 7:16am | Jul 3, 2026 7:41am | Jul 3, 2026 7:41am | Jul 3, 2026 8:23am | Jul 3, 2026 8:36am | Jul 3, 2026 8:48am | Jul 3, 2026 8:48am | Fire |  | Fair | No | Found 1,50kva jumper burnt off, isolate 50kva to remake jumper at pole number 570438
Outage | J.E.26.07.01473 | C001838718 | Moses Elliston | St.Catherine | Completed | Load_270111 | Rhodens Pen - 210 | Jul 2, 2026 8:58pm | Jul 2, 2026 8:58pm | Jul 3, 2026 2:55pm | Jul 3, 2026 2:55pm | Jul 3, 2026 2:55pm | Jul 3, 2026 3:20pm | Jul 3, 2026 3:21pm | Jul 3, 2026 3:21pm |  |  | Fair | No | Supply reconnected from m# 2290113.
Outage | J.E.26.07.01603 | C001838720 | Michael Christian | St.James | Completed | Load_261318 | Bogue - 610 | Jul 2, 2026 8:58pm | Jul 3, 2026 5:32am | Jul 3, 2026 5:38am | Jul 3, 2026 5:38am | Jul 3, 2026 6:11am | Jul 3, 2026 7:28am | Jul 3, 2026 7:28am | Jul 3, 2026 7:28am | BrokenWire |  | Fair | No | Found secondary line broken down open 1 100 kava to work replace 30 ft # 2 aa 4 clamps voltage 112 114 227 at pothead
Outage | J.E.26.07.01654 | C001838716 | Hartley Chin | St.Catherine | Completed | Load_412848 | Rhodens Pen - 410 | Jul 2, 2026 8:50pm | Jul 2, 2026 8:50pm | Jul 2, 2026 9:22pm | Jul 2, 2026 9:31pm | Jul 2, 2026 10:33pm | Jul 2, 2026 10:33pm | Jul 2, 2026 10:37pm | Jul 2, 2026 10:37pm |  |  | Fair | No | Ref to field service!!! Found back of customer meter burnt… customer meter # 2468058 … customer needs 3W meter replaced … voltage read on line side 112v , 114v
Non-Outage | J.E.26.07.01611 | C001838712 | Ryan Richards | null | Completed | null | null | Jul 2, 2026 8:45pm | Jul 3, 2026 3:36pm | Jul 3, 2026 5:55pm | Jul 3, 2026 5:55pm | Jul 3, 2026 5:55pm | Jul 3, 2026 5:56pm | Jul 3, 2026 5:56pm | Jul 3, 2026 5:56pm |  |  | Fair | No | Area found ok same as the other
Outage | J.E.26.07.01482 | C001838709 | Tajay Bernard | Hanover | Completed | Load_302747 | Orange Bay - 310 | Jul 2, 2026 8:43pm | Jul 2, 2026 8:43pm | Jul 2, 2026 9:14pm | Jul 2, 2026 9:14pm | Jul 2, 2026 9:14pm | Jul 2, 2026 9:54pm | Jul 2, 2026 9:56pm | Jul 2, 2026 9:56pm |  |  | Fair | No | Refuse 1 25kva Transformer use 3amp fuse
Outage | J.E.26.07.01548 | C001838710 | Lancelot Brown | Hanover | Completed | Load_257352 | Orange Bay - 310 | Jul 2, 2026 8:43pm | Jul 3, 2026 7:31am | Jul 3, 2026 8:04am | Jul 3, 2026 8:17am | Jul 3, 2026 8:53am | Jul 3, 2026 9:07am | Jul 3, 2026 9:07am | Jul 3, 2026 9:07am |  |  | Fair | No | Remake corroded joint at pole used one pg clamp vl at meter socket 114 supply restore
Outage | J.E.26.07.01627 | C001838711 | Dean Smith | Hanover | Completed | Load_250960 | Orange Bay - 310 | Jul 2, 2026 8:43pm | Jul 3, 2026 7:31am | Jul 3, 2026 2:33pm | Jul 3, 2026 2:33pm | Jul 3, 2026 2:33pm | Jul 3, 2026 2:33pm | Jul 3, 2026 2:33pm | Jul 3, 2026 2:33pm | Fire |  | Fair | No | Shift ended
Non-Outage | J.E.26.07.01475 | C001838706 | Denton Williams | null | Completed | null | null | Jul 2, 2026 8:32pm | Jul 2, 2026 8:32pm | Jul 2, 2026 10:07pm | Jul 2, 2026 10:07pm | Jul 2, 2026 10:08pm | Jul 2, 2026 10:11pm | Jul 2, 2026 10:11pm | Jul 2, 2026 10:11pm |  |  | Fair | No | After calling customer we did not get an answer however we have restored supply to the area few hours earlier.
Outage | J.E.26.07.01531 | C001838705 | Denton Williams | Portland | Completed | Load_239822 | Port Antonio - 410 | Jul 2, 2026 8:32pm | Jul 2, 2026 8:32pm | Jul 2, 2026 8:51pm | Jul 2, 2026 10:11pm | Jul 2, 2026 10:28pm | Jul 2, 2026 10:29pm | Jul 2, 2026 10:29pm | Jul 2, 2026 10:29pm |  |  | Fair | No | After calling customer she stated that she was on disconnection.
Outage | J.E.26.07.01566 | C001838704 | Gregory Grossett | Portland | Completed | Load_349987 | Port Antonio - 410 | Jul 2, 2026 8:32pm | Jul 3, 2026 7:20am | Jul 3, 2026 7:58am | Jul 3, 2026 7:58am | Jul 3, 2026 9:24am | Jul 3, 2026 10:30am | Jul 3, 2026 10:53am | Jul 3, 2026 10:53am |  |  | Fair | No | Open secondary conductors banging and transformer drop leads burn open 25kva transformer fuse link then retention conductors and repair drop leads close transformer fuse link to restore normal supply to the area.Material use 4 2/0 preform 8 one bolt clamps.
Outage | J.E.26.07.01532 | C001838698 | Devon Grant | KSAN | Completed | Load_579095 | Constant Spring - 210 | Jul 2, 2026 8:20pm | Jul 3, 2026 11:17am | Jul 3, 2026 2:20pm | Jul 3, 2026 2:20pm | Jul 3, 2026 2:20pm | Jul 3, 2026 2:34pm | Jul 3, 2026 2:46pm | Jul 3, 2026 2:46pm |  |  | Fair | No | Refuse 10amps junction, supply now restore to site.
Outage | J.E.26.07.01606 | C001838697 | Milton Charlton | KSAN | Completed | Load_261826 | Washington Blvd - 510 | Jul 2, 2026 8:19pm | Jul 2, 2026 8:20pm | Jul 2, 2026 8:30pm | Jul 2, 2026 8:30pm | Jul 2, 2026 9:45pm | Jul 2, 2026 9:50pm | Jul 2, 2026 9:48pm | Jul 2, 2026 9:48pm |  |  | Fair | No | Found one 15 amps junction fuse blown at pole #( no pole #) and 10 amps transformer fuse blown at pole #0104385. Refused using one 15 amps fuse and one 10 amps fuse and reclosed transformer and junction switches.
Outage | J.E.26.07.01605 | C001838696 | Hopeton Henry | St.Thomas | Completed | Load_267420 | Good Year - 110 | Jul 2, 2026 8:16pm | Jul 3, 2026 3:33pm | Jul 3, 2026 4:22pm | Jul 3, 2026 5:28pm | Jul 3, 2026 5:29pm | Jul 3, 2026 5:55pm | Jul 3, 2026 5:56pm | Jul 3, 2026 5:56pm |  |  | Fair | No | Internal problem, customer advised
Outage | J.E.26.07.01395 | C001838695 | Floyd Taylor | Trelawny | Completed | Load_259114 | Greenwood - 210 | Jul 2, 2026 8:12pm | Jul 2, 2026 8:14pm | Jul 2, 2026 8:45pm | Jul 2, 2026 10:00pm | Jul 2, 2026 10:39pm | Jul 3, 2026 6:51am | Jul 3, 2026 6:52am | Jul 3, 2026 6:52am |  |  | Fair | No | Remake secondary jumper using 1pg clamp voltage readings left 113,111,224
Outage | J.E.26.07.01600 | C001838694 | Floyd Taylor | Trelawny | Completed | Load_255152 | Martha Brae - 110 | Jul 2, 2026 8:12pm | Jul 2, 2026 8:14pm | Jul 2, 2026 8:45pm | Jul 2, 2026 8:52pm | Jul 2, 2026 9:44pm | Jul 2, 2026 9:49pm | Jul 2, 2026 9:52pm | Jul 2, 2026 9:52pm |  |  | Fair | No | Remake joints at pole using 2pg clamps voltage readings left 121,120,241
Outage | J.E.26.07.01584 | C001838686 | Javid Vernon | Westmoreland | Completed | Load_253644 | Paradise - 310 | Jul 2, 2026 7:36pm | Jul 2, 2026 7:37pm | Jul 2, 2026 8:18pm | Jul 2, 2026 8:18pm | Jul 2, 2026 11:11pm | Jul 2, 2026 11:13pm | Jul 2, 2026 11:13pm | Jul 2, 2026 11:13pm |  |  | Fair | No | This call requires day light attention
Non-Outage | J.E.26.06.38616 | C001838685 | Ryan Richards | null | Completed | null | null | Jul 2, 2026 7:33pm | Jul 2, 2026 7:33pm | Jul 2, 2026 8:11pm | Jul 2, 2026 8:53pm | Jul 2, 2026 8:54pm | Jul 2, 2026 8:56pm | Jul 2, 2026 8:56pm | Jul 2, 2026 8:56pm |  |  | Fair | No | Premises found ok customer was disconnected for bill issues customer paid bill and call center was contacted and customer service was restored
Outage | J.E.26.07.01588 | C001838683 | Damion Reid | Manchester | Completed | Load_239398 | Kendal - 210 | Jul 2, 2026 7:32pm | Jul 2, 2026 7:34pm | Jul 2, 2026 8:46pm | Jul 2, 2026 8:47pm | Jul 2, 2026 10:14pm | Jul 2, 2026 10:32pm | Jul 2, 2026 10:34pm | Jul 2, 2026 10:34pm | BrokenWire |  | Fair | No | Remade burnt off service neutral at secondary pole for 3 wire service using one 1 bolt clamp
Outage | J.E.26.07.01589 | C001838684 | Kenroy Dale | Manchester | Completed | Load_252802 | Porus - 310 | Jul 2, 2026 7:32pm | Jul 3, 2026 7:54am | Jul 3, 2026 9:10am | Jul 3, 2026 2:20pm | Jul 3, 2026 3:04pm | Jul 3, 2026 3:05pm | Jul 3, 2026 3:06pm | Jul 3, 2026 3:06pm |  |  | Fair | No | Customer have internal problems, customer was advised to get an electrician to check the premises. Voltage reading 111/113/224
Outage | J.E.26.07.01597 | C001838682 | Delano Gayle | St.Catherine | Completed | Load_240687 | Tredegar - 210 | Jul 2, 2026 7:32pm | Jul 3, 2026 2:11am | Jul 3, 2026 2:40am | Jul 3, 2026 2:40am | Jul 3, 2026 2:57am | Jul 3, 2026 3:05am | Jul 3, 2026 3:05am | Jul 3, 2026 3:05am | Fire |  | Fair | No | Premises found okay no fire seen in area
Non-Outage | J.E.26.07.01586 | C001838681 | Derrick Dawkins | null | Completed | null | null | Jul 2, 2026 7:26pm | Jul 2, 2026 7:27pm | Jul 2, 2026 7:46pm | Jul 2, 2026 7:46pm | Jul 2, 2026 9:25pm | Jul 2, 2026 10:28pm | Jul 2, 2026 10:29pm | Jul 2, 2026 10:29pm | BrokenWire |  | Fair | No | Found one span secondary phase burned off due to guy wire banking on secondary line open 25 kva transformer to carry out repairs splice and retention use one pg clamp 2/0 freeform
Outage | J.E.26.07.01583 | C001838680 | Nickolas Rodriques | St.Catherine | Completed | Load_262365 | Twickenham - 210 | Jul 2, 2026 7:24pm | Jul 2, 2026 7:25pm | Jul 2, 2026 8:08pm | Jul 2, 2026 8:08pm | Jul 2, 2026 8:42pm | Jul 2, 2026 10:08pm | Jul 2, 2026 10:10pm | Jul 2, 2026 10:10pm |  |  | Fair | No | Checked and found one pole span of secondary phase broken down caused by slack connection. Isolate a set of bank of three transformer for safety to repair. Repaired by splice and retention wire using 30 ft of 2-north aluminum using four clamps and replaced the fuses after numerous patrols.
Outage | J.E.26.07.01564 | C001838679 | Richard Samuda | Manchester | Completed | Load_238222 | Kendal - 210 | Jul 2, 2026 7:15pm | Jul 3, 2026 7:37am | Jul 3, 2026 9:09am | Jul 3, 2026 9:24am | Jul 3, 2026 9:24am | Jul 3, 2026 9:45am | Jul 3, 2026 9:58am | Jul 3, 2026 9:58am | Fire |  | Fair | No | Change corroded 1bolt clamp on service wire that lead to customer premises that cause customer to experience single phase using 1 one bolt clamp customer back to normal 113before 113/113/226
Non-Outage | J.E.26.07.01535 | C001838676 | Richard Grant | St.Catherine | Completed | Load_250997 | New Michelton - 210 | Jul 2, 2026 6:55pm | Jul 2, 2026 7:36pm | Jul 2, 2026 9:09pm | Jul 2, 2026 9:09pm | Jul 2, 2026 10:00pm | Jul 2, 2026 10:22pm | Jul 2, 2026 10:22pm | Jul 2, 2026 10:22pm |  |  | Fair | No | 3 wire service had wrapped connections at pole & pothead, used 5 clamps & 4’ #6 service neutral for repairs however, customer has a defective meter socket, temporary repairs were done & customer was advised to have meter socket replaced.
Outage | J.E.26.07.01527 | C001838675 | Nickolas Rodriques | Portmore | Completed | Load_262556 | Naggo Head - 610 | Jul 2, 2026 6:48pm | Jul 2, 2026 7:05pm | Jul 2, 2026 10:32pm | Jul 2, 2026 10:32pm | Jul 2, 2026 10:55pm | Jul 2, 2026 11:32pm | Jul 2, 2026 11:35pm | Jul 2, 2026 11:35pm |  |  | Fair | No | Checked and found customers without electricity caused by broken service wire at pole. Repaired by connecting wire using two clamps, current reading is (116-116-232). Customer confirmed that all is well now.
Outage | J.E.26.07.01500 | C001838673 | Stephen Taylor | St.Thomas | Completed | Load_246172 | Good Year - 110 | Jul 2, 2026 6:46pm | Jul 2, 2026 6:47pm | Jul 2, 2026 7:19pm | Jul 2, 2026 7:19pm | Jul 2, 2026 8:07pm | Jul 2, 2026 8:08pm | Jul 2, 2026 8:11pm | Jul 2, 2026 8:11pm | Fire |  | Fair | No | Splice and retention secondary line and close up 25 kva transformer all customer now in service
Outage | J.E.26.07.01384 | C001838671 | Romaine Roberts | St.Mary | Completed | Load_265929 | Oracabessa - 210 | Jul 2, 2026 6:45pm | Jul 2, 2026 6:46pm | Jul 2, 2026 7:12pm | Jul 2, 2026 7:12pm | Jul 2, 2026 8:35pm | Jul 2, 2026 8:40pm | Jul 2, 2026 8:42pm | Jul 2, 2026 8:42pm |  | Y | Fair | No | High wind and vegetation bang secondary conductor and trip 25 kva transformer clear vegetation from mine and reset transformer power restore
Non-Outage | J.E.26.07.00797 | C001838667 | Romeo Brissett | St.James | Completed | Load_259109 | Queens Drive - 710 | Jul 2, 2026 6:31pm | Jul 2, 2026 6:32pm | Jul 2, 2026 7:22pm | Jul 2, 2026 9:52pm | Jul 2, 2026 10:50pm | Jul 2, 2026 10:29pm | Jul 2, 2026 10:51pm | Jul 2, 2026 10:51pm |  |  | Fair | No | Customer stated issue was resolved
Non-Outage | J.E.26.07.00824 | C001838664 | Horace Malcolm | St.James | Completed | Load_292055 | Bogue - 310 | Jul 2, 2026 6:30pm | Jul 2, 2026 6:32pm | Jul 2, 2026 8:25pm | Jul 2, 2026 8:25pm | Jul 2, 2026 8:50pm | Jul 2, 2026 9:12pm | Jul 2, 2026 9:12pm | Jul 2, 2026 9:12pm | BrokenPole |  | Fair | No | Check and found area ok no broken pole found
Non-Outage | J.E.26.07.00892 | C001838666 | Romeo Brissett | St.James | Completed | Load_262059 | Rose Hall - 210 | Jul 2, 2026 6:30pm | Jul 2, 2026 6:32pm | Jul 2, 2026 7:23pm | Jul 2, 2026 7:23pm | Jul 2, 2026 7:43pm | Jul 2, 2026 8:00pm | Jul 2, 2026 8:01pm | Jul 2, 2026 8:01pm |  |  | Fair | No | Check and found premises closed.
Non-Outage | J.E.26.07.01125 | C001838663 | Horace Malcolm | St.James | Completed | Load_249504 | Bogue - 310 | Jul 2, 2026 6:29pm | Jul 2, 2026 6:30pm | Jul 2, 2026 7:15pm | Jul 2, 2026 7:15pm | Jul 2, 2026 7:56pm | Jul 2, 2026 8:24pm | Jul 2, 2026 8:24pm | Jul 2, 2026 8:24pm | BrokenPole |  | Fair | No | Retired old pole removed customer service around from leaning pole
Non-Outage | J.E.26.07.01273 | C001838662 | Horace Malcolm | St.James | Completed | Load_244424 | Bogue - 310 | Jul 2, 2026 6:29pm | Jul 2, 2026 6:30pm | Jul 2, 2026 7:07pm | Jul 2, 2026 7:07pm | Jul 2, 2026 7:07pm | Jul 2, 2026 7:08pm | Jul 2, 2026 7:08pm | Jul 2, 2026 7:08pm |  |  | Fair | No | Call belongs to trelawny
Non-Outage | J.E.26.06.32460 | C001838660 | Floyd Taylor | null | Completed | null | null | Jul 2, 2026 6:27pm | Jul 2, 2026 6:28pm | Jul 2, 2026 7:50pm | Jul 2, 2026 7:51pm | Jul 2, 2026 8:28pm | Jul 2, 2026 8:52pm | Jul 2, 2026 8:52pm | Jul 2, 2026 8:52pm | Fire |  | Fair | No | No fire was found
Non-Outage | J.E.26.06.34221 | C001838659 | Romeo Brissett | St.James | Completed | Load_253846 | Queens Drive - 710 | Jul 2, 2026 6:27pm | Jul 2, 2026 6:27pm | Jul 2, 2026 8:31pm | Jul 2, 2026 8:32pm | Jul 2, 2026 9:20pm | Jul 2, 2026 9:50pm | Jul 2, 2026 9:52pm | Jul 2, 2026 9:52pm |  |  | Fair | No | Check and found internal fault.
Non-Outage | J.E.26.06.37657 | C001838658 | Romeo Brissett | St.James | Completed | Load_261979 | Queens Drive - 310 | Jul 2, 2026 6:26pm | Jul 2, 2026 6:27pm | Jul 2, 2026 8:01pm | Jul 2, 2026 8:01pm | Jul 2, 2026 8:15pm | Jul 2, 2026 8:30pm | Jul 2, 2026 8:31pm | Jul 2, 2026 8:31pm |  |  | Fair | No | Unable to locate providence was patrolled no cellsite found in the area, not getting through with there call center.
Outage | J.E.26.07.01495 | C001838654 | Horace Malcolm | St.James | Completed | Load_292533 | Queens Drive - 710 | Jul 2, 2026 6:20pm | Jul 2, 2026 6:22pm | Jul 2, 2026 7:05pm | Jul 2, 2026 7:05pm | Jul 2, 2026 7:05pm | Jul 2, 2026 7:07pm | Jul 2, 2026 7:07pm | Jul 2, 2026 7:07pm |  |  | Fair | No | This call belongs to field service it’s a new service installation
Non-Outage | J.E.26.07.01218 | C001838650 | Fitzroy Turner | null | Completed | null | null | Jul 2, 2026 6:17pm | Jul 2, 2026 6:45pm | Jul 2, 2026 7:01pm | Jul 2, 2026 7:01pm | Jul 2, 2026 7:38pm | Jul 2, 2026 7:38pm | Jul 2, 2026 7:40pm | Jul 2, 2026 7:40pm | Fire |  | Fair | No | No sparking seeing at this location at this time wire burnt off
Outage | J.E.26.07.00579 | C001838651 | Marlon Authors | Manchester | Completed | null | null | Jul 2, 2026 6:17pm | Jul 2, 2026 6:17pm | Jul 2, 2026 6:21pm | Jul 2, 2026 6:21pm | Jul 2, 2026 7:05pm | Jul 2, 2026 8:43pm | Jul 2, 2026 8:43pm | Jul 2, 2026 8:43pm |  |  | Fair | No | Patrol and found burnt 25 kva transformer in area, same was already referred for replacement. Isolate and close another 25 kva transformer to top up to top 5 rdg 116v,116v and cross phased 232 volts to temporary tied in both circuits. Supply leave working ok rdg 111v,112v and cross phased 223 volts
Outage | J.E.26.07.01421 | C001838649 | Fitzroy Turner | KSAS | Completed | Load_1002861 | Rockfort - 410 | Jul 2, 2026 6:17pm | Jul 2, 2026 6:45pm | Jul 2, 2026 7:40pm | Jul 2, 2026 7:40pm | Jul 2, 2026 8:07pm | Jul 2, 2026 8:29pm | Jul 2, 2026 8:31pm | Jul 2, 2026 8:31pm |  |  | EarthMovement | No | Customer premises close at this time
Outage | J.E.26.07.00846 | C001838645 | Kaydon Taylor | KSAN | Completed | Load_254232 | Constant Spring - 310 | Jul 2, 2026 6:13pm | Jul 2, 2026 6:13pm | Jul 2, 2026 8:46pm | Jul 2, 2026 10:22pm | Jul 2, 2026 10:26pm | Jul 2, 2026 10:27pm | Jul 2, 2026 10:27pm | Jul 2, 2026 10:27pm |  |  | Fair | No | Found okay
Outage | J.E.26.07.01511 | C001838644 | Richard Grant | St.Catherine | Completed | Load_253957 | New Michelton - 210 | Jul 2, 2026 6:12pm | Jul 2, 2026 6:20pm | Jul 2, 2026 7:25pm | Jul 2, 2026 7:25pm | Jul 2, 2026 8:10pm | Jul 2, 2026 9:08pm | Jul 2, 2026 9:08pm | Jul 2, 2026 9:08pm |  |  | Fair | No | 25kva transformer at Pole#0113036 is defective, no V/R coming coming from same, requesting a memo be sent to Mr. Roy Brown to have defective transformer replaced.
Outage | J.E.26.07.01435 | C001838641 | Milton Charlton | KSAN | Completed | Load_261826 | Washington Blvd - 510 | Jul 2, 2026 6:09pm | Jul 2, 2026 6:12pm | Jul 2, 2026 7:15pm | Jul 2, 2026 7:15pm | Jul 2, 2026 7:37pm | Jul 2, 2026 7:40pm | Jul 2, 2026 7:40pm | Jul 2, 2026 7:40pm |  |  | Fair | No | Found one 25amps junction fuse blown at pole #( no pole#). Refused using one 25 amps fuse and reclosed junction switch.
Outage | J.E.26.07.01490 | C001838635 | Selvin White | St.Elizabeth | Completed | Load_237951 | Maggotty - 110 | Jul 2, 2026 6:00pm | Jul 2, 2026 6:09pm | Jul 2, 2026 6:47pm | Jul 2, 2026 9:22pm | Jul 2, 2026 9:24pm | Jul 2, 2026 9:28pm | Jul 2, 2026 9:28pm | Jul 2, 2026 9:28pm |  |  | Fair | No | Customer cannot be contacted as phone number is not local. Daylight attention required.
Outage | J.E.26.07.01355 | C001838629 | Kaydon Taylor | KSAN | Completed | Load_241732 | Constant Spring - 210 | Jul 2, 2026 5:41pm | Jul 2, 2026 5:41pm | Jul 2, 2026 7:37pm | Jul 2, 2026 7:37pm | Jul 2, 2026 8:45pm | Jul 2, 2026 8:46pm | Jul 2, 2026 8:46pm | Jul 2, 2026 8:46pm |  |  | Fair | No | Found okay
Outage | J.E.26.06.37484 | C001838624 | Richard Samuda | Manchester | Completed | Load_262255 | Kendal - 210 | Jul 2, 2026 5:26pm | Jul 3, 2026 7:37am | Jul 3, 2026 10:04am | Jul 3, 2026 10:04am | Jul 3, 2026 11:04am | Jul 3, 2026 11:26am | Jul 3, 2026 11:30am | Jul 3, 2026 11:30am |  |  | Fair | No | Customer have a issue with meter and bill advised customer to visit office
Outage | J.E.26.07.01131 | C001838622 | Omar Harris | St.Ann | Completed | Load_266688 | Roaring River - 210 | Jul 2, 2026 5:25pm | Jul 2, 2026 5:25pm | Jul 2, 2026 7:01pm | Jul 2, 2026 7:06pm | Jul 2, 2026 7:06pm | Jul 2, 2026 7:07pm | Jul 2, 2026 7:07pm | Jul 2, 2026 7:07pm |  |  | Fair | No | Splice and retention 50ft of # 2 conductor, using a 2 one bolt clamp. Supply restored.
Outage | J.E.26.07.01279 | C001838621 | Omar Harris | St.Ann | Completed | Load_252355 | Roaring River - 410 | Jul 2, 2026 5:25pm | Jul 2, 2026 5:25pm | Jul 2, 2026 7:07pm | Jul 2, 2026 7:07pm | Jul 2, 2026 8:09pm | Jul 2, 2026 8:10pm | Jul 2, 2026 8:11pm | Jul 2, 2026 8:11pm |  |  | Fair | No | Splice and retention 25ft of #6 triplex using 3 pen union and 3 one bolt clamp. Supply restored.
Outage | J.E.26.07.01392 | C001838619 | Omar Harris | St.Ann | Completed | Load_246156 | Roaring River - 410 | Jul 2, 2026 5:25pm | Jul 2, 2026 5:25pm | Jul 2, 2026 8:59pm | Jul 2, 2026 9:00pm | Jul 2, 2026 10:48pm | Jul 2, 2026 10:48pm | Jul 2, 2026 10:49pm | Jul 2, 2026 10:49pm | BrokenPole |  | Fair | No
Outage | J.E.26.07.01448 | C001838620 | Omar Harris | St.Ann | Completed | Load_245204 | Ocho Rios - 410 | Jul 2, 2026 5:25pm | Jul 2, 2026 5:25pm | Jul 2, 2026 8:42pm | Jul 2, 2026 8:42pm | Jul 2, 2026 8:59pm | Jul 2, 2026 8:59pm | Jul 2, 2026 8:59pm | Jul 2, 2026 8:59pm |  |  | Fair | No
Outage | J.E.26.07.01467 | C001838618 | Omar Harris | St.Ann | Completed | Load_266688 | Roaring River - 210 | Jul 2, 2026 5:25pm | Jul 2, 2026 5:25pm | Jul 2, 2026 6:17pm | Jul 2, 2026 6:17pm | Jul 2, 2026 6:39pm | Jul 2, 2026 7:05pm | Jul 2, 2026 7:06pm | Jul 2, 2026 7:06pm | BrokenWire |  | Fair | No | Splice and retention 50ft of # 2 conductor, using a 2 one bolt clamp. Supply restored.
Non-Outage | J.E.26.07.01252 | C001838617 | Stephen Taylor | St.Thomas | Completed | Load_263695 | Good Year - 110 | Jul 2, 2026 5:23pm | Jul 2, 2026 5:23pm | Jul 2, 2026 6:21pm | Jul 2, 2026 6:21pm | Jul 2, 2026 7:16pm | Jul 2, 2026 7:17pm | Jul 2, 2026 7:18pm | Jul 2, 2026 7:18pm | BrokenWire |  | Fair | No | Close up 25 kva transformer with 3ams fuse
Non-Outage | J.E.26.07.01471 | C001838615 | Selvin White | null | Completed | null | null | Jul 2, 2026 5:19pm | Jul 2, 2026 5:23pm | Jul 2, 2026 8:10pm | Jul 2, 2026 8:10pm | Jul 2, 2026 8:35pm | Jul 2, 2026 9:12pm | Jul 2, 2026 9:13pm | Jul 2, 2026 9:13pm |  |  | Fair | No | Isolate a 25 KVA circuit to clear and make safe dislodged neutral grounding conductor that was coming into contact with secondary phase conductor. Supply restored to the affected customers.
Outage | J.E.26.07.01473 | C001838614 | Hartley Chin | St.Catherine | Completed | Load_270111 | Rhodens Pen - 210 | Jul 2, 2026 5:19pm | Jul 2, 2026 5:20pm | Jul 2, 2026 7:06pm | Jul 2, 2026 7:06pm | Jul 2, 2026 8:16pm | Jul 2, 2026 8:57pm | Jul 2, 2026 8:57pm | Jul 2, 2026 8:57pm |  |  | Fair | No | Ref to field service.. Hexing ..
Outage | J.E.26.07.01343 | C001838600 | Kaydon Taylor | KSAS | Completed | Load_243473 | Duhaney - 210 | Jul 2, 2026 5:07pm | Jul 2, 2026 5:08pm | Jul 2, 2026 7:34pm | Jul 2, 2026 7:34pm | Jul 2, 2026 7:34pm | Jul 2, 2026 7:34pm | Jul 2, 2026 7:34pm | Jul 2, 2026 7:34pm |  |  | Fair | No | Found okay
Non-Outage | J.E.26.07.01144 | C001838599 | Selvin White | St.Elizabeth | Completed | Load_268907 | Maggotty - 110 | Jul 2, 2026 5:06pm | Jul 2, 2026 5:06pm | Jul 2, 2026 5:12pm | Jul 2, 2026 5:12pm | Jul 2, 2026 5:12pm | Jul 2, 2026 6:41pm | Jul 2, 2026 6:46pm | Jul 2, 2026 6:46pm |  |  | SevereWind | No | Isolate a25 KVA transformer circuit in order to remade slack connection on transformer drop leads phase and neutral conductors. Voltage readings left at secondary and inside customer’s meter socket are 225,112,113 volts.
Non-Outage | J.E.26.07.01165 | C001838588 | Marlon Authors | null | Completed | null | null | Jul 2, 2026 5:04pm | Jul 2, 2026 5:16pm | Jul 2, 2026 5:30pm | Jul 2, 2026 5:30pm | Jul 2, 2026 5:30pm | Jul 2, 2026 5:32pm | Jul 2, 2026 5:32pm | Jul 2, 2026 5:32pm |  |  | Fair | No | Customer said supply was restored to the area
Outage | J.E.26.07.00788 | C001838585 | Selvin White | St.Elizabeth | Completed | Load_268564 | Maggotty - 110 | Jul 2, 2026 5:04pm | Jul 2, 2026 5:18pm | Jul 2, 2026 7:01pm | Jul 2, 2026 7:01pm | Jul 2, 2026 7:45pm | Jul 2, 2026 8:08pm | Jul 2, 2026 8:09pm | Jul 2, 2026 8:09pm |  |  | Fair | No | Please refer to the maintenance department as a 40ft wooden pole along with a 5 KVA transformer is required for customers supply to be restored. Please advise Nicholas Morgan so arrangements can be made.
Non-Outage | J.E.26.07.01153 | C001838567 | Selvin White | null | Completed | null | null | Jul 2, 2026 4:55pm | Jul 2, 2026 4:55pm | Jul 2, 2026 9:36pm | Jul 2, 2026 9:36pm | Jul 2, 2026 10:13pm | Jul 2, 2026 10:15pm | Jul 2, 2026 10:15pm | Jul 2, 2026 10:15pm |  |  | Fair | No | Customer says supply was restored earlier today.
Outage | J.E.26.07.01180 | C001838566 | Selvin White | St.Elizabeth | Completed | Load_240873 | Maggotty - 210 | Jul 2, 2026 4:54pm | Jul 2, 2026 4:55pm | Jul 2, 2026 5:09pm | Jul 2, 2026 5:09pm | Jul 2, 2026 5:10pm | Jul 2, 2026 5:11pm | Jul 2, 2026 5:11pm | Jul 2, 2026 5:11pm |  |  | Fair | No | Customer was contacted and it was said that supply was restored earlier.
Outage | J.E.26.07.01186 | C001838565 | Selvin White | St.Elizabeth | Completed | Load_263683 | Maggotty - 110 | Jul 2, 2026 4:54pm | Jul 2, 2026 4:55pm | Jul 2, 2026 5:04pm | Jul 2, 2026 5:04pm | Jul 2, 2026 5:05pm | Jul 2, 2026 5:06pm | Jul 2, 2026 5:07pm | Jul 2, 2026 5:07pm |  |  | Fair | No | Customer was contacted and it was said that supply was restored earlier.
Non-Outage | J.E.26.07.01258 | C001838564 | Rayon Foster | Hanover | Completed | Load_254929 | Orange Bay - 310 | Jul 2, 2026 4:53pm | Jul 2, 2026 4:57pm | Jul 2, 2026 5:10pm | Jul 2, 2026 5:10pm | Jul 2, 2026 8:12pm | Jul 2, 2026 8:25pm | Jul 2, 2026 8:33pm | Jul 2, 2026 8:33pm |  |  | Fair | No | Patrol secondary line to fine two spand of secondary bottom phase broken down open one 25 kva transformer to do repairs splice and retention two span of secondary wires using 130 feet’s of 2/0 Conductor voltage test after closing transformer circuit 114/116 AB230volts
Non-Outage | J.E.26.07.00905 | C001838563 | Tajay Bernard | Hanover | Completed | Load_243072 | Orange Bay - 310 | Jul 2, 2026 4:52pm | Jul 2, 2026 4:57pm | Jul 2, 2026 5:45pm | Jul 2, 2026 5:46pm | Jul 2, 2026 5:46pm | Jul 2, 2026 5:47pm | Jul 2, 2026 5:48pm | Jul 2, 2026 5:48pm |  |  | Fair | No | Related to previous call job number 01082
Outage | J.E.26.07.01431 | C001838526 | Neville Spencer | Clarendon | Completed | Load_247470 | Parnassus - 210 | Jul 2, 2026 4:28pm | Jul 2, 2026 4:41pm | Jul 2, 2026 9:19pm | Jul 2, 2026 9:19pm | Jul 2, 2026 10:18pm | Jul 2, 2026 10:18pm | Jul 2, 2026 10:19pm | Jul 2, 2026 10:19pm |  |  | Fair | No | Not getting trough to customer.
Outage | J.E.26.07.01403 | C001838501 | Floyd Taylor | Trelawny | Completed | Load_264155 | Greenwood - 110 | Jul 2, 2026 4:23pm | Jul 2, 2026 5:05pm | Jul 2, 2026 7:50pm | Jul 3, 2026 6:53am | Jul 3, 2026 6:53am | Jul 3, 2026 6:53am | Jul 3, 2026 6:55am | Jul 3, 2026 6:55am |  |  | Fair | No | Needs about 120ft #6 triplex in orde for customer to get back light
Outage | J.E.26.07.01413 | C001838500 | Damion Reid | Manchester | Completed | Load_251015 | Kendal - 210 | Jul 2, 2026 4:21pm | Jul 2, 2026 4:22pm | Jul 2, 2026 6:29pm | Jul 2, 2026 6:29pm | Jul 2, 2026 7:06pm | Jul 2, 2026 8:41pm | Jul 2, 2026 8:44pm | Jul 2, 2026 8:44pm |  |  | Fair | No | 40amp trip saver found down cause by defective lightning arrester disconnect arrester and reset trip saver
Non-Outage | J.E.26.07.01301 | C001838498 | Wan Carlos Scarlett | null | Completed | null | null | Jul 2, 2026 4:17pm | Jul 3, 2026 8:23am | Jul 3, 2026 8:32am | Jul 3, 2026 8:32am | Jul 3, 2026 9:43am | Jul 3, 2026 10:36am | Jul 3, 2026 10:39am | Jul 3, 2026 10:39am | BrokenWire |  | Fair | No | Found customer service wire burn down and found customer pothead wire defective advised customer to get a licensed electrician to fix the problem isolate customer 3 wire service at pole
Outage | J.E.26.07.01351 | C001838494 | Javid Vernon | Westmoreland | Completed | Load_240689 | Paradise - 310 | Jul 2, 2026 4:14pm | Jul 2, 2026 4:19pm | Jul 2, 2026 5:36pm | Jul 2, 2026 5:37pm | Jul 2, 2026 5:37pm | Jul 2, 2026 6:32pm | Jul 2, 2026 6:33pm | Jul 2, 2026 6:33pm |  |  | Fair | No | Replaced 80ft #6 triplex and use 6clamp voltage reading 114/113/227
Outage | J.E.26.07.01377 | C001838490 | Romaine Roberts | St.Mary | Completed | Load_348541 | Oracabessa - 210 | Jul 2, 2026 4:05pm | Jul 2, 2026 4:05pm | Jul 2, 2026 5:00pm | Jul 2, 2026 5:00pm | Jul 2, 2026 6:49pm | Jul 2, 2026 6:50pm | Jul 2, 2026 6:56pm | Jul 2, 2026 6:56pm | BrokenWire |  | Fair | No | After patrolling line found tree that suspect to be cut down that cause line junction to blow line was clear and 50 amp replace power restore
Non-Outage | J.E.26.07.01332 | C001838456 | Donald Cunningham | null | Completed | null | null | Jul 2, 2026 3:57pm | Jul 3, 2026 7:47am | Jul 3, 2026 10:06am | Jul 3, 2026 10:06am | Jul 3, 2026 10:33am | Jul 3, 2026 10:33am | Jul 3, 2026 10:35am | Jul 3, 2026 10:35am | Fire |  | Fair | No | Banging conductor cause by tree in lines bushing need to be done before wire can retention bucket truck required
Outage | J.E.26.07.01296 | C001838455 | Tajay Bernard | Hanover | Completed | Load_239009 | Orange Bay - 310 | Jul 2, 2026 3:55pm | Jul 2, 2026 4:06pm | Jul 2, 2026 4:10pm | Jul 2, 2026 4:15pm | Jul 2, 2026 4:36pm | Jul 2, 2026 4:46pm | Jul 2, 2026 4:51pm | Jul 2, 2026 4:51pm |  |  | Fair | No | Area check and found okay premises was found closed
Outage | J.E.26.07.01400 | C001838453 | Richard Samuda | Manchester | Completed | Load_265258 | Kendal - 210 | Jul 2, 2026 3:53pm | Jul 3, 2026 7:37am | Jul 3, 2026 8:06am | Jul 3, 2026 8:06am | Jul 3, 2026 9:09am | Jul 3, 2026 9:09am | Jul 3, 2026 9:13am | Jul 3, 2026 9:13am |  |  | Fair | No | Customer had a trip back customer back to normal u
Outage | J.E.26.07.01390 | C001838436 | Hartley Chin | St.Catherine | Completed | Load_293943 | Rhodens Pen - 310 | Jul 2, 2026 3:50pm | Jul 2, 2026 3:56pm | Jul 2, 2026 5:11pm | Jul 2, 2026 6:47pm | Jul 2, 2026 6:47pm | Jul 2, 2026 6:47pm | Jul 2, 2026 6:47pm | Jul 2, 2026 6:47pm |  |  | Fair | No | Call related to job # 01150 ..
Outage | J.E.26.07.01141 | C001838435 | Richman Whyte | Westmoreland | Completed | Load_268696 | Paradise - 210 | Jul 2, 2026 3:49pm | Jul 2, 2026 3:50pm | Jul 2, 2026 6:29pm | Jul 2, 2026 6:30pm | Jul 2, 2026 7:47pm | Jul 2, 2026 7:52pm | Jul 2, 2026 7:58pm | Jul 2, 2026 7:58pm | LeaningPole |  | Rains | No | 35c6 wood pole rotten at the bottom it’s not in any immediate danger however it needs to change tde construction with junction switch on it
Outage | J.E.26.07.01247 | C001838408 | Fitzroy Turner | KSAS | Completed | Load_263680 | Hunts Bay - 510 | Jul 2, 2026 3:42pm | Jul 2, 2026 3:43pm | Jul 2, 2026 4:24pm | Jul 2, 2026 4:24pm | Jul 2, 2026 5:00pm | Jul 2, 2026 5:00pm | Jul 2, 2026 5:08pm | Jul 2, 2026 5:08pm |  |  | Fair | No | Found two phases primary line hot line jumper burnt off at the intersection of seaga Blvd cox terrace one hot line clamps replaced supply restored to the areas
Outage | J.E.26.07.01351 | C001838407 | Javid Vernon | Westmoreland | Completed | Load_240689 | Paradise - 310 | Jul 2, 2026 3:42pm | Jul 2, 2026 4:12pm | Jul 2, 2026 6:33pm | Jul 2, 2026 6:33pm | Jul 2, 2026 6:33pm | Jul 2, 2026 6:33pm | Jul 2, 2026 6:34pm | Jul 2, 2026 6:34pm |  |  | Fair | No | Related to previous call job# 01351
Outage | J.E.26.07.01353 | C001838409 | Fitzroy Turner | KSAN | Completed | Load_270237 | Washington Blvd - 710 | Jul 2, 2026 3:42pm | Jul 2, 2026 3:43pm | Jul 2, 2026 5:11pm | Jul 2, 2026 5:11pm | Jul 2, 2026 6:30pm | Jul 2, 2026 6:55pm | Jul 2, 2026 6:57pm | Jul 2, 2026 6:57pm |  |  | Fair | No | Found bank of two transformer 100kva and one 25 kva transformer the lighting transformer switch top burnt out use one drop out switch and one 10 amps fuse to carry out repair supply restored to areas
Outage | J.E.26.07.00258 | C001838404 | Fitzroy Turner | KSAS | Completed | Load_266339 | Rockfort - 410 | Jul 2, 2026 3:40pm | Jul 2, 2026 3:41pm | Jul 2, 2026 4:19pm | Jul 2, 2026 4:22pm | Jul 2, 2026 4:22pm | Jul 2, 2026 4:23pm | Jul 2, 2026 4:23pm | Jul 2, 2026 4:23pm |  |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.07.01023 | C001838406 | Fitzroy Turner | KSAS | Completed | Load_263493 | Washington Blvd - 410 | Jul 2, 2026 3:40pm | Jul 2, 2026 3:41pm | Jul 2, 2026 7:31pm | Jul 2, 2026 8:31pm | Jul 2, 2026 9:25pm | Jul 2, 2026 9:43pm | Jul 2, 2026 9:44pm | Jul 2, 2026 9:44pm |  |  | Fair | No | Customer premises found with electricity supply
Outage | J.E.26.07.01057 | C001838402 | Fitzroy Turner | KSAS | Completed | Load_267274 | Greenwich - 310 | Jul 2, 2026 3:40pm | Jul 2, 2026 3:41pm | Jul 2, 2026 3:46pm | Jul 2, 2026 3:46pm | Jul 2, 2026 4:21pm | Jul 2, 2026 4:21pm | Jul 2, 2026 4:22pm | Jul 2, 2026 4:22pm |  |  | Fair | No | Customer premises found with electricity supply.transformer change from last night
Outage | J.E.26.07.01298 | C001838401 | Floyd Taylor | Trelawny | Completed | Load_242927 | Greenwood - 110 | Jul 2, 2026 3:40pm | Jul 2, 2026 3:47pm | Jul 2, 2026 4:46pm | Jul 2, 2026 4:46pm | Jul 2, 2026 6:31pm | Jul 2, 2026 7:48pm | Jul 2, 2026 7:50pm | Jul 2, 2026 7:50pm |  |  | Fair | No | Remove vines from line, splice and retention 1 span of secondary neutral and replace 1,8amp junction fuse voltage readings left 117,119,236
Outage | J.E.26.07.01316 | C001838403 | Marlon Brown | Trelawny | Completed | Load_302355 | Duncans - 110 | Jul 2, 2026 3:40pm | Jul 2, 2026 3:48pm | Jul 2, 2026 7:49pm | Jul 2, 2026 7:49pm | Jul 2, 2026 7:49pm | Jul 2, 2026 7:52pm | Jul 2, 2026 7:52pm | Jul 2, 2026 7:52pm |  |  | Fair | No | Reconnected by customer care.
Outage | J.E.26.07.01333 | C001838405 | Marlon Brown | Trelawny | Completed | Load_294519 | Duncans - 110 | Jul 2, 2026 3:40pm | Jul 2, 2026 3:48pm | Jul 2, 2026 4:18pm | Jul 2, 2026 4:18pm | Jul 2, 2026 7:47pm | Jul 2, 2026 7:49pm | Jul 2, 2026 7:49pm | Jul 2, 2026 7:49pm |  |  | Fair | No | Unable to locate customer via telephone nor direction
Non-Outage | J.E.26.07.01030 | C001838383 | Ryan Richards | null | Completed | null | null | Jul 2, 2026 3:35pm | Jul 2, 2026 3:35pm | Jul 2, 2026 3:43pm | Jul 2, 2026 5:23pm | Jul 2, 2026 6:37pm | Jul 2, 2026 7:00pm | Jul 2, 2026 7:00pm | Jul 2, 2026 7:00pm |  |  | Fair | No | Area found with supply customer in the area also said the power went and com back shortly
Outage | J.E.26.07.01223 | C001838384 | Ryan Richards | Manchester | Completed | Load_240485 | Spur Tree - 310 | Jul 2, 2026 3:35pm | Jul 2, 2026 3:35pm | Jul 2, 2026 7:02pm | Jul 2, 2026 7:02pm | Jul 2, 2026 8:16pm | Jul 2, 2026 8:51pm | Jul 2, 2026 8:52pm | Jul 2, 2026 8:52pm |  |  | Fair | No | Defective main entry and meter socket customer was advised to carry out repair
Non-Outage | J.E.26.07.01019 | C001838382 | Ryan Richards | null | Completed | null | null | Jul 2, 2026 3:34pm | Jul 2, 2026 3:35pm | Jul 2, 2026 3:43pm | Jul 2, 2026 7:00pm | Jul 2, 2026 7:00pm | Jul 2, 2026 7:01pm | Jul 2, 2026 7:01pm | Jul 2, 2026 7:01pm |  |  | Fair | No | Same as the other customers said that the power was restored
Outage | J.E.26.07.00960 | C001838381 | Ryan Richards | Manchester | Completed | Load_256714 | Porus - 310 | Jul 2, 2026 3:34pm | Jul 2, 2026 3:35pm | Jul 2, 2026 3:51pm | Jul 2, 2026 3:51pm | Jul 2, 2026 4:57pm | Jul 2, 2026 5:21pm | Jul 2, 2026 5:22pm | Jul 2, 2026 5:22pm |  |  | Fair | No | Area found ok and customer that made report was unable to locate multiple efforts made to contact customer but unsuccessful
Outage | J.E.26.07.01226 | C001838380 | Derrick Dawkins | St.James | Completed | Load_302411 | Bogue - 610 | Jul 2, 2026 3:33pm | Jul 2, 2026 3:33pm | Jul 2, 2026 3:42pm | Jul 2, 2026 5:21pm | Jul 2, 2026 5:21pm | Jul 2, 2026 5:28pm | Jul 2, 2026 5:49pm | Jul 2, 2026 5:49pm |  |  | Fair | No | The only customer without electricity from the hexing box.
Outage | J.E.26.07.01357 | C001838379 | Derrick Dawkins | St.James | Completed | Load_264399 | Bogue - 610 | Jul 2, 2026 3:33pm | Jul 2, 2026 3:33pm | Jul 2, 2026 5:49pm | Jul 2, 2026 5:49pm | Jul 2, 2026 6:04pm | Jul 2, 2026 6:13pm | Jul 2, 2026 6:13pm | Jul 2, 2026 6:13pm |  |  | Rains | No | Found a junction fuse blown 8 amp due to vegetation replaced a 8 amp junction fuse no pole # available
Outage | J.E.26.07.01290 | C001838378 | Derrick Dawkins | St.James | Completed | Load_302374 | Bogue - 510 | Jul 2, 2026 3:32pm | Jul 2, 2026 3:33pm | Jul 2, 2026 6:13pm | Jul 2, 2026 6:13pm | Jul 2, 2026 6:54pm | Jul 2, 2026 7:10pm | Jul 2, 2026 7:12pm | Jul 2, 2026 7:12pm |  |  | Rains | No | Found a junction fuse blown 8 amp due to vegetation removed vegetation replaced 8 amp fuse no pole # available
Outage | J.E.26.07.01307 | C001838377 | Horace Malcolm | St.James | Completed | Load_259607 | Bogue - 510 | Jul 2, 2026 3:32pm | Jul 3, 2026 7:29am | Jul 3, 2026 7:38am | Jul 3, 2026 7:38am | Jul 3, 2026 7:38am | Jul 3, 2026 7:39am | Jul 3, 2026 7:39am | Jul 3, 2026 7:39am |  |  | Fair | No | This call belongs to Hanover
Outage | J.E.26.07.01385 | C001838370 | Richard Samuda | Manchester | Completed | Load_253914 | Kendal - 210 | Jul 2, 2026 3:32pm | Jul 3, 2026 7:37am | Jul 3, 2026 11:32am | Jul 3, 2026 11:33am | Jul 3, 2026 12:12pm | Jul 3, 2026 12:13pm | Jul 3, 2026 12:13pm | Jul 3, 2026 12:13pm |  |  | Fair | No | Customer say situation was resolved fr yesterday
Non-Outage | J.E.26.06.31276 | C001838369 | Clyde Brown | Clarendon | Completed | Load_353534 | May Pen - 110 | Jul 2, 2026 3:31pm | Jul 2, 2026 3:32pm | Jul 2, 2026 4:20pm | Jul 2, 2026 4:20pm | Jul 2, 2026 4:24pm | Jul 2, 2026 4:23pm | Jul 2, 2026 4:29pm | Jul 2, 2026 4:29pm |  |  | Fair | No | Cannot be located customer not answering phone
Outage | J.E.26.07.01253 | C001838368 | Hartley Chin | St.Catherine | Completed | Load_294021 | Rhodens Pen - 310 | Jul 2, 2026 3:30pm | Jul 2, 2026 3:32pm | Jul 2, 2026 5:11pm | Jul 2, 2026 6:46pm | Jul 2, 2026 6:46pm | Jul 2, 2026 6:46pm | Jul 2, 2026 6:47pm | Jul 2, 2026 6:47pm |  |  | Fair | No | Call related to job # 01150 ..
Non-Outage | J.E.26.07.00515 | C001838365 | Romeo Brissett | St.James | Completed | Load_265113 | Rose Hall - 210 | Jul 2, 2026 3:29pm | Jul 2, 2026 3:30pm | Jul 2, 2026 4:36pm | Jul 2, 2026 4:36pm | Jul 2, 2026 6:19pm | Jul 2, 2026 7:00pm | Jul 2, 2026 7:22pm | Jul 2, 2026 7:22pm |  |  | Fair | No | Isolated (1)10KVA transformer and (1)25 kva transformer, repaired service wire joint and repaired transformer drop lead. Used 3 clamps V/R 115-115-203-231-233-230.
Outage | J.E.26.07.01031 | C001838364 | Neville Spencer | Clarendon | Completed | Load_248085 | Monymusk - 410 | Jul 2, 2026 3:29pm | Jul 2, 2026 3:30pm | Jul 2, 2026 6:47pm | Jul 2, 2026 6:47pm | Jul 2, 2026 7:04pm | Jul 2, 2026 7:06pm | Jul 2, 2026 7:07pm | Jul 2, 2026 7:07pm |  |  | Fair | No | Unable to locate customer.
Outage | J.E.26.07.01346 | C001838363 | Neville Spencer | Clarendon | Completed | Load_292121 | Parnassus - 310 | Jul 2, 2026 3:28pm | Jul 2, 2026 3:29pm | Jul 2, 2026 7:14pm | Jul 2, 2026 7:14pm | Jul 2, 2026 9:18pm | Jul 2, 2026 9:18pm | Jul 2, 2026 9:19pm | Jul 2, 2026 9:19pm |  |  | Fair | No | Not located.
Non-Outage | J.E.26.07.01059 | C001838362 | Damion Reid | null | Completed | null | null | Jul 2, 2026 3:27pm | Jul 2, 2026 3:28pm | Jul 2, 2026 3:45pm | Jul 2, 2026 3:45pm | Jul 2, 2026 6:19pm | Jul 2, 2026 6:24pm | Jul 2, 2026 6:28pm | Jul 2, 2026 6:28pm |  |  | Fair | No | Replace 90ft of #6 triplex service wire for 3 wire service using three 1 bolt clamp and 3 pen union voltage reading at meter socket phase to neutral 114v-115v across phase 231v
Outage | J.E.26.07.00944 | C001838361 | Nickolas Rodriques | Portmore | Completed | Load_239574 | Naggo Head - 510 | Jul 2, 2026 3:27pm | Jul 2, 2026 3:28pm | Jul 2, 2026 10:10pm | Jul 2, 2026 10:10pm | Jul 2, 2026 10:20pm | Jul 2, 2026 10:27pm | Jul 2, 2026 10:29pm | Jul 2, 2026 10:29pm |  |  | Fair | No | Unable to locate or communicate with the specific customer. However, the area was patrolled and no noticeable outage was found.
Outage | J.E.26.07.01271 | C001838352 | Rodclif Dawkins | Portmore | Completed | Load_245174 | Naggo Head - 610 | Jul 2, 2026 3:24pm | Jul 3, 2026 7:24am | Jul 3, 2026 10:22am | Jul 3, 2026 10:22am | Jul 3, 2026 10:31am | Jul 23, 2026 11:43am | Jul 3, 2026 11:46am | Jul 3, 2026 11:46am |  |  | Fair | No | Found triplex #6 supplying 3w meter with neutral dislodged at pothead. Using 1 penunion and 3-1bolt clamps joints changed. Voltage of 121*2,240 was recorded at meter, however customer is without supply due to defective 100amp main breaker. Customer was notified
Outage | J.E.26.07.01306 | C001838351 | Nickolas Rodriques | St.Catherine | Completed | Load_262410 | Twickenham - 210 | Jul 2, 2026 3:24pm | Jul 2, 2026 3:26pm | Jul 2, 2026 7:29pm | Jul 2, 2026 7:30pm | Jul 2, 2026 7:54pm | Jul 2, 2026 8:05pm | Jul 2, 2026 8:08pm | Jul 2, 2026 8:08pm | LeaningPole |  | Fair | No | Checked and found a 30ft wooden pole rotten at the base and leaning towards roadway that is causing service wires to hanging low. It’s a dead end pole which consists of open secondary wires and customers service wire. Refer to maintenance. (Area has electricity)
Outage | J.E.26.07.01312 | C001838350 | Nickolas Rodriques | St.Catherine | Completed | Load_246229 | Twickenham - 210 | Jul 2, 2026 3:24pm | Jul 2, 2026 3:26pm | Jul 2, 2026 5:58pm | Jul 2, 2026 6:07pm | Jul 2, 2026 6:52pm | Jul 2, 2026 7:20pm | Jul 2, 2026 7:28pm | Jul 2, 2026 7:28pm |  |  | Fair | No | Customer stated that she does not have any electricity. Reading found (116). Checks were done which revealed that the customer 2w meter was disconnected. The escalation team was contacted and reconnected the customer.
Outage | J.E.26.07.00902 | C001838342 | Denton Williams | Portland | Completed | Load_256415 | Port Antonio - 410 | Jul 2, 2026 3:20pm | Jul 2, 2026 3:22pm | Jul 2, 2026 3:57pm | Jul 2, 2026 3:58pm | Jul 2, 2026 4:13pm | Jul 2, 2026 4:36pm | Jul 2, 2026 4:38pm | Jul 2, 2026 4:38pm |  |  | Fair | No | Customer was making payment on wrong account
Outage | J.E.26.07.01329 | C001838341 | Denton Williams | Portland | Completed | Load_349025 | Port Antonio - 310 | Jul 2, 2026 3:19pm | Jul 2, 2026 3:22pm | Jul 2, 2026 4:38pm | Jul 2, 2026 4:38pm | Jul 2, 2026 4:54pm | Jul 2, 2026 5:01pm | Jul 2, 2026 5:04pm | Jul 2, 2026 5:04pm |  | Y | Fair | No | Tree fell on line, clear it self. Use one 15 amp junction fuse to energize
Non-Outage | J.E.26.07.01106 | C001838324 | Andrew Powell | null | Completed | null | null | Jul 2, 2026 3:12pm | Jul 3, 2026 7:29am | Jul 3, 2026 7:47am | Jul 3, 2026 7:47am | Jul 3, 2026 8:41am | Jul 3, 2026 9:08am | Jul 3, 2026 9:11am | Jul 3, 2026 9:11am | Fire |  | Fair | No | Disconnect and remove 100 feet burnt up #6 triplex service wire from secondary line meter #2972019 customer leaves without supply due to burnt up service entry wire, advise customer.
Non-Outage | J.E.26.07.01204 | C001838322 | Romaine Roberts | St.Mary | Completed | Load_255871 | Oracabessa - 210 | Jul 2, 2026 3:12pm | Jul 2, 2026 3:58pm | Jul 2, 2026 8:43pm | Jul 2, 2026 8:43pm | Jul 3, 2026 8:01am | Jul 2, 2026 11:20pm | Jul 3, 2026 8:05am | Jul 3, 2026 8:05am |  |  | Fair | No | Found 25 kva transformer fuse blown clear vegetation from line and replace 3 amp to restore supply
Non-Outage | J.E.26.07.01281 | C001838318 | Cliton Henry | St.Mary | Completed | Load_269698 | Oracabessa - 110 | Jul 2, 2026 3:11pm | Jul 3, 2026 8:04am | Jul 3, 2026 9:25am | Jul 3, 2026 9:25am | Jul 3, 2026 9:25am | Jul 3, 2026 9:49am | Jul 3, 2026 9:52am | Jul 3, 2026 9:52am |  |  | Fair | No | The voltages found at the customer’s pothead were 125-99/224 volts due to a corroded neutral joint. The service wire was reconnected using 3-#2-#6 pen unions and 1- one bolt clamp. Voltages left 105-112/228
Outage | J.E.26.07.00999 | C001838317 | Marlon Authors | Manchester | Completed | Load_292829 | Spur Tree - 210 | Jul 2, 2026 3:11pm | Jul 2, 2026 3:11pm | Jul 2, 2026 4:19pm | Jul 2, 2026 4:19pm | Jul 2, 2026 4:19pm | Jul 2, 2026 4:25pm | Jul 2, 2026 4:25pm | Jul 2, 2026 4:25pm |  |  | Fair | No | Customer said supply was restored
Outage | J.E.26.07.01015 | C001838315 | Richard Watson | St.Elizabeth | Completed | Load_240000 | Maggotty - 210 | Jul 2, 2026 3:10pm | Jul 3, 2026 8:42am | Jul 3, 2026 9:47am | Jul 3, 2026 9:47am | Jul 3, 2026 11:13am | Jul 3, 2026 11:13am | Jul 3, 2026 11:18am | Jul 3, 2026 11:18am |  |  | Fair | No | Meter lug terminal burnt on line side, resulting in meter single phasing, cause by defective meter socket, same was replaced by electrician, issue referred to field service department for meter replacement.
Outage | J.E.26.07.01022 | C001838316 | Marlon Authors | Manchester | Completed | Load_240801 | Spur Tree - 210 | Jul 2, 2026 3:10pm | Jul 2, 2026 3:11pm | Jul 2, 2026 4:37pm | Jul 2, 2026 4:37pm | Jul 2, 2026 4:37pm | Jul 2, 2026 4:38pm | Jul 2, 2026 4:38pm | Jul 2, 2026 4:38pm |  |  | Fair | No | Supply restored to the area
Outage | J.E.26.07.00989 | C001838314 | Marlon Authors | Manchester | Completed | Load_240173 | Spur Tree - 210 | Jul 2, 2026 3:09pm | Jul 2, 2026 3:11pm | Jul 2, 2026 5:39pm | Jul 2, 2026 5:39pm | Jul 2, 2026 5:39pm | Jul 2, 2026 5:43pm | Jul 2, 2026 5:43pm | Jul 2, 2026 5:43pm |  |  | Fair | No | Supply restored to the area
Outage | J.E.26.07.01012 | C001838313 | Marlon Authors | St.Elizabeth | Completed | Load_261414 | Maggotty - 210 | Jul 2, 2026 3:09pm | Jul 2, 2026 3:11pm | Jul 2, 2026 4:09pm | Jul 2, 2026 4:09pm | Jul 2, 2026 4:09pm | Jul 2, 2026 4:11pm | Jul 2, 2026 4:11pm | Jul 2, 2026 4:11pm |  |  | Fair | No | Customer said supply was restored
Outage | J.E.26.07.01055 | C001838311 | Marlon Authors | Manchester | Completed | Load_260212 | Spur Tree - 210 | Jul 2, 2026 3:09pm | Jul 2, 2026 3:11pm | Jul 2, 2026 5:27pm | Jul 2, 2026 5:27pm | Jul 2, 2026 5:27pm | Jul 2, 2026 5:59pm | Jul 2, 2026 5:28pm | Jul 2, 2026 5:28pm |  |  | Fair | No | Supply restored to the area
Outage | J.E.26.07.01318 | C001838312 | Evan Spaulding | St.Mary | Completed | Load_264244 | Annotto Bay - 210 | Jul 2, 2026 3:09pm | Jul 2, 2026 3:10pm | Jul 2, 2026 5:36pm | Jul 2, 2026 5:36pm | Jul 2, 2026 6:47pm | Jul 2, 2026 8:12pm | Jul 2, 2026 8:12pm | Jul 2, 2026 8:12pm |  |  | Fair | No | Customer says she didn’t mad report.
Outage | J.E.26.07.01109 | C001838310 | Marlon Authors | Manchester | Completed | Load_256355 | Spur Tree - 210 | Jul 2, 2026 3:08pm | Jul 2, 2026 3:11pm | Jul 2, 2026 8:44pm | Jul 2, 2026 8:44pm | Jul 2, 2026 10:22pm | Jul 2, 2026 10:26pm | Jul 2, 2026 10:27pm | Jul 2, 2026 10:27pm |  |  | Fair | No | Supply seen in area however the gate to the premises is locked
Outage | J.E.26.07.01325 | C001838283 | Kaydon Taylor | KSAN | Completed | Load_251677 | Constant Spring - 310 | Jul 2, 2026 2:50pm | Jul 2, 2026 2:51pm | Jul 2, 2026 4:44pm | Jul 2, 2026 4:44pm | Jul 2, 2026 5:28pm | Jul 2, 2026 5:58pm | Jul 2, 2026 5:58pm | Jul 2, 2026 5:58pm | Fire,Jps.Sim.Ops.OsiOms.Api.Application.Dto.Hazards | Y | Rains | No | 25kva transformer fuse found blown and replace3amp. Also carry out secondary bushing
Outage | J.E.26.07.01304 | C001838256 | Kaydon Taylor | KSAN | Completed | Load_261919 | Constant Spring - 310 | Jul 2, 2026 2:21pm | Jul 2, 2026 2:26pm | Jul 2, 2026 5:59pm | Jul 2, 2026 5:59pm | Jul 2, 2026 6:00pm | Jul 2, 2026 6:00pm | Jul 2, 2026 6:00pm | Jul 2, 2026 6:00pm |  |  | Fair | No | Found okay
Outage | J.E.26.07.01279 | C001838243 | Daniel Francis | St.Ann | Completed | Load_252355 | Roaring River - 410 | Jul 2, 2026 2:10pm | Jul 2, 2026 2:10pm | Jul 2, 2026 8:56pm | Jul 2, 2026 8:56pm | Jul 2, 2026 8:56pm | Jul 2, 2026 8:56pm | Jul 2, 2026 8:58pm | Jul 2, 2026 8:58pm |  |  | Fair | No | Found ok already resolved
Outage | J.E.26.07.01150 | C001838242 | Hartley Chin | St.Catherine | Completed | Load_294005 | Rhodens Pen - 310 | Jul 2, 2026 2:09pm | Jul 2, 2026 2:09pm | Jul 2, 2026 5:11pm | Jul 2, 2026 5:12pm | Jul 2, 2026 6:28pm | Jul 2, 2026 6:44pm | Jul 2, 2026 6:46pm | Jul 2, 2026 6:46pm |  |  | Fair | No | Found 1 of 3 junction blown (20 amp) no pole # , line patrolled and found kite on line … kite removed… refused junction…
Non-Outage | J.E.26.07.01276 | C001838235 | Richard Grant | null | Completed | null | null | Jul 2, 2026 2:03pm | Jul 2, 2026 4:19pm | Jul 2, 2026 7:24pm | Jul 2, 2026 7:24pm | Jul 2, 2026 7:24pm | Jul 2, 2026 7:25pm | Jul 2, 2026 7:25pm | Jul 2, 2026 7:25pm | Fire |  | Fair | No | 2/0 quad no longer being and was on the ground was accidentally cut by someone cleared out the area, service line was subsequently disconnected from source and removed.
Non-Outage | J.E.26.07.01270 | C001838228 | Richard Grant | null | Completed | null | null | Jul 2, 2026 2:01pm | Jul 2, 2026 4:18pm | Jul 2, 2026 4:59pm | Jul 2, 2026 4:59pm | Jul 2, 2026 7:04pm | Jul 2, 2026 7:24pm | Jul 2, 2026 7:24pm | Jul 2, 2026 7:24pm | BrokenWire |  | Fair | No | 2/0 quad no longer being and was on the ground was accidentally cut by someone cleared out the area, service line was subsequently disconnected from source and removed.
Outage | J.E.26.07.01199 | C001838215 | Neville Spencer | Clarendon | Completed | Load_256608 | May Pen - 210 | Jul 2, 2026 1:51pm | Jul 2, 2026 3:29pm | Jul 2, 2026 7:12pm | Jul 2, 2026 7:12pm | Jul 2, 2026 7:12pm | Jul 2, 2026 7:12pm | Jul 2, 2026 7:13pm | Jul 2, 2026 7:13pm |  |  | Fair | No | Found ok.
Outage | J.E.26.07.01259 | C001838212 | Moses Elliston | St.Catherine | Completed | Load_557299 | Tredegar - 410 | Jul 2, 2026 1:49pm | Jul 2, 2026 1:49pm | Jul 2, 2026 4:08pm | Jul 2, 2026 4:08pm | Jul 2, 2026 4:08pm | Jul 2, 2026 4:09pm | Jul 2, 2026 4:09pm | Jul 2, 2026 4:09pm |  |  | Fair | No | Credit added to prepaid account.
Non-Outage | J.E.26.06.38967 | C001838190 | Cliton Henry | St.Mary | Completed | Load_267662 | Oracabessa - 110 | Jul 2, 2026 1:31pm | Jul 2, 2026 1:32pm | Jul 3, 2026 7:39am | Jul 3, 2026 7:39am | Jul 3, 2026 7:39am | Jul 3, 2026 8:52am | Jul 3, 2026 8:55am | Jul 3, 2026 8:55am |  |  | Fair | No | A defective #6 triplex service found was replaced using approximately 150 feet #6 triplex service wire. Voltages left 119-119/238 volts.
Outage | J.E.26.07.01198 | C001838160 | Rodclif Dawkins | St.Catherine | Completed | Load_244195 | Twickenham - 210 | Jul 2, 2026 1:06pm | Jul 3, 2026 7:24am | Jul 3, 2026 1:26pm | Jul 3, 2026 1:26pm | Jul 3, 2026 1:26pm | Jul 3, 2026 1:27pm | Jul 3, 2026 1:27pm | Jul 3, 2026 1:27pm |  |  | Fair | No | At location crew found 2 blown fuse from bank of 3 transformers. Crew observed defective 50kva lighting transformer leaking oil from tap changer. Power transformer was de-energized. Please refer to Aston Murray and Kymani Allman. Advise crew to bring spill bag
Non-Outage | J.E.26.07.01202 | C001838149 | Rusean Allen | null | Completed | null | null | Jul 2, 2026 1:00pm | Jul 2, 2026 1:01pm | Jul 2, 2026 1:14pm | Jul 2, 2026 1:26pm | Jul 2, 2026 2:33pm | Jul 2, 2026 3:37pm | Jul 2, 2026 3:37pm | Jul 2, 2026 3:37pm | BrokenWire |  | Fair | No | Reconnected wire at pole
Outage | J.E.26.07.01207 | C001838148 | Horace Malcolm | St.James | Completed | Load_261331 | Bogue - 610 | Jul 2, 2026 12:58pm | Jul 2, 2026 12:59pm | Jul 2, 2026 1:33pm | Jul 2, 2026 1:33pm | Jul 2, 2026 1:52pm | Jul 2, 2026 2:43pm | Jul 2, 2026 2:43pm | Jul 2, 2026 2:43pm |  | Y | Fair | No | Refused one 8amp junction fuse
Non-Outage | J.E.26.07.01178 | C001838131 | Oraine Minto | St.Ann | Completed | Load_266688 | Roaring River - 210 | Jul 2, 2026 12:47pm | Jul 3, 2026 8:48am | Jul 3, 2026 10:23am | Jul 3, 2026 10:29am | Jul 3, 2026 10:29am | Jul 3, 2026 10:29am | Jul 3, 2026 10:30am | Jul 3, 2026 10:30am |  |  | Fair | No | Customer states that the issue was resolved last night
Non-Outage | J.E.26.07.01163 | C001838129 | Hartley Chin | null | Completed | null | null | Jul 2, 2026 12:42pm | Jul 2, 2026 12:43pm | Jul 2, 2026 12:46pm | Jul 2, 2026 2:44pm | Jul 2, 2026 2:44pm | Jul 2, 2026 2:44pm | Jul 2, 2026 2:45pm | Jul 2, 2026 2:45pm | Fire |  | Fair | No | Call related to job # 00748 …
Outage | J.E.26.07.00976 | C001838121 | Andrew Powell | Manchester | Completed | Load_292233 | Spur Tree - 210 | Jul 2, 2026 12:41pm | Jul 2, 2026 1:32pm | Jul 2, 2026 2:18pm | Jul 2, 2026 2:22pm | Jul 2, 2026 2:22pm | Jul 2, 2026 2:22pm | Jul 2, 2026 2:26pm | Jul 2, 2026 2:26pm |  |  | Fair | No | Premises found okay customers stated that supply restored last night.
Non-Outage | J.E.26.07.01160 | C001838120 | Neville Spencer | null | Completed | null | null | Jul 2, 2026 12:40pm | Jul 2, 2026 3:28pm | Jul 2, 2026 5:28pm | Jul 2, 2026 5:28pm | Jul 2, 2026 6:24pm | Jul 2, 2026 6:43pm | Jul 2, 2026 6:45pm | Jul 2, 2026 6:45pm | Fire |  | Fair | No | Open 25 kva xmfr at pole # 0156581 retention 2 spans of secondary phase and neutral conductor used 2 preform supply restored.
Outage | J.E.26.07.00927 | C001838114 | Richard Samuda | Manchester | Completed | Load_251799 | Spur Tree - 310 | Jul 2, 2026 12:38pm | Jul 2, 2026 12:39pm | Jul 2, 2026 12:51pm | Jul 2, 2026 12:52pm | Jul 2, 2026 1:15pm | Jul 2, 2026 2:16pm | Jul 2, 2026 2:17pm | Jul 2, 2026 2:17pm | BrokenWire |  | Fair | No | Remake joint at customer pothead that was brunt up using two one bolt clamps 115/after 115/115/230
Outage | J.E.26.07.01149 | C001838112 | Swon Miller | St.James | Completed | Load_258945 | Queens Drive - 710 | Jul 2, 2026 12:37pm | Jul 2, 2026 12:44pm | Jul 2, 2026 12:59pm | Jul 2, 2026 12:59pm | Jul 2, 2026 1:41pm | Jul 28, 2026 2:05pm | Jul 2, 2026 2:06pm | Jul 2, 2026 2:06pm |  |  | Fair | No | Check and found areas okay voltage found 115/114/230 customer states that power supply has been restored voltage left 115/114/230
Non-Outage | J.E.26.06.37529 | C001838103 | Moses Elliston | null | Completed | null | null | Jul 2, 2026 12:36pm | Jul 2, 2026 12:36pm | Jul 2, 2026 1:58pm | Jul 2, 2026 1:58pm | Jul 2, 2026 1:58pm | Jul 2, 2026 3:13pm | Jul 2, 2026 3:14pm | Jul 2, 2026 3:14pm |  |  | Fair | No | Meter changed to # 4069133= due to burnt terminals
Outage | J.E.26.07.01095 | C001838102 | Ricky Hall | St.Catherine | Completed | Load_261214 | New Michelton - 210 | Jul 2, 2026 12:35pm | Jul 2, 2026 12:37pm | Jul 2, 2026 12:53pm | Jul 2, 2026 12:54pm | Jul 2, 2026 1:43pm | Jul 2, 2026 2:32pm | Jul 2, 2026 3:15pm | Jul 2, 2026 3:15pm |  |  | Rains | No | Clean and reconnect 3W service at Pothead also 115/113/228 reconnect via call centre
Outage | J.E.26.07.01137 | C001838094 | Daniel Francis | St.Ann | Completed | Load_256334 | Ocho Rios - 310 | Jul 2, 2026 12:30pm | Jul 2, 2026 12:31pm | Jul 2, 2026 2:26pm | Jul 2, 2026 2:26pm | Jul 2, 2026 2:27pm | Jul 2, 2026 2:40pm | Jul 2, 2026 2:41pm | Jul 2, 2026 2:41pm |  |  | Fair | No | Found junction at 0010354 patrol and renew 20a fuse
Outage | J.E.26.07.01007 | C001838093 | Andre Williams | Trelawny | Completed | Load_249733 | Martha Brae - 110 | Jul 2, 2026 12:29pm | Jul 2, 2026 12:31pm | Jul 2, 2026 12:56pm | Jul 2, 2026 2:01pm | Jul 2, 2026 2:04pm | Jul 2, 2026 2:05pm | Jul 2, 2026 2:05pm | Jul 2, 2026 2:05pm |  |  | Fair | No | Customer carried out repairs new meter needed to resieve supply reffer to field service
Outage | J.E.26.07.01131 | C001838087 | Daniel Francis | St.Ann | Completed | Load_266688 | Roaring River - 210 | Jul 2, 2026 12:23pm | Jul 2, 2026 12:31pm | Jul 2, 2026 10:32pm | Jul 2, 2026 10:35pm | Jul 2, 2026 10:35pm | Jul 2, 2026 10:35pm | Jul 2, 2026 10:36pm | Jul 2, 2026 10:36pm |  |  | Fair | No | Found ok power restored
Non-Outage | J.E.26.07.01128 | C001838081 | Oraine Minto | St.Ann | Completed | Load_248125 | Ocho Rios - 310 | Jul 2, 2026 12:21pm | Jul 3, 2026 8:49am | Jul 3, 2026 10:23am | Jul 3, 2026 10:41am | Jul 3, 2026 10:41am | Jul 3, 2026 10:41am | Jul 3, 2026 10:43am | Jul 3, 2026 10:43am |  |  | Fair | No | Unable to reach customer after 5 attempts to reach them on the number given
Outage | J.E.26.07.00943 | C001838077 | Lancelot Brown | Hanover | Completed | Load_265979 | Orange Bay - 310 | Jul 2, 2026 12:18pm | Jul 2, 2026 12:18pm | Jul 2, 2026 3:41pm | Jul 2, 2026 3:41pm | Jul 2, 2026 3:41pm | Jul 2, 2026 3:43pm | Jul 2, 2026 3:43pm | Jul 2, 2026 3:43pm |  |  | Fair | No | Remake corroded joint at pothead used three connectors vl at meter socket 115-114-229 supply restore
Outage | J.E.26.07.01082 | C001838079 | Tajay Bernard | Hanover | Completed | Load_243072 | Orange Bay - 310 | Jul 2, 2026 12:18pm | Jul 2, 2026 4:07pm | Jul 2, 2026 4:51pm | Jul 2, 2026 4:51pm | Jul 2, 2026 5:32pm | Jul 2, 2026 5:45pm | Jul 2, 2026 5:45pm | Jul 2, 2026 5:45pm |  |  | Fair | No | Check and found okay, customer meter found burned causing customer to be single phasing, meter needs to be replaced urgently refer to field service
Outage | J.E.26.07.01120 | C001838078 | Milton Charlton | KSAS | Completed | Load_253774 | Up Park Camp - 410 | Jul 2, 2026 12:18pm | Jul 2, 2026 12:31pm | Jul 2, 2026 12:34pm | Jul 2, 2026 12:34pm | Jul 2, 2026 12:53pm | Jul 2, 2026 1:25pm | Jul 2, 2026 1:22pm | Jul 2, 2026 1:22pm |  |  | Fair | No | Customer has an internal problem. Cusmeter socket burn up and need to o be changed customer advised.
Outage | J.E.26.07.00937 | C001838076 | Dean Smith | Hanover | Completed | Load_263665 | Orange Bay - 310 | Jul 2, 2026 12:17pm | Jul 2, 2026 1:36pm | Jul 2, 2026 3:28pm | Jul 2, 2026 3:28pm | Jul 2, 2026 3:29pm | Jul 2, 2026 3:29pm | Jul 2, 2026 3:30pm | Jul 2, 2026 3:30pm | Fire |  | Fair | No | Burn meter, please forward to metering dept lucea Hanover
Outage | J.E.26.07.00979 | C001838066 | Stephen Taylor | St.Thomas | Completed | Load_351223 | Good Year - 110 | Jul 2, 2026 12:08pm | Jul 2, 2026 12:09pm | Jul 2, 2026 1:36pm | Jul 2, 2026 1:36pm | Jul 2, 2026 1:36pm | Jul 2, 2026 1:36pm | Jul 2, 2026 1:37pm | Jul 2, 2026 1:37pm |  |  | Fair | No | Need more information a lot of call to customer no one answered the phone
Non-Outage | J.E.26.07.00939 | C001838059 | Hartley Chin | Clarendon | Completed | Load_257105 | Monymusk - 410 | Jul 2, 2026 11:59am | Jul 2, 2026 12:00pm | Jul 2, 2026 2:45pm | Jul 2, 2026 2:45pm | Jul 2, 2026 3:45pm | Jul 2, 2026 4:51pm | Jul 2, 2026 5:11pm | Jul 2, 2026 5:11pm |  |  | Fair | No | Found 1 of 3 blown junction fuse (30 amp) Burnt fuse barrel , line patrolled and found okay , junction refused… Note :
Outage | J.E.26.07.01099 | C001838055 | Gregory Grossett | Portland | Completed | Load_349777 | Port Antonio - 410 | Jul 2, 2026 11:52am | Jul 2, 2026 11:52am | Jul 2, 2026 1:24pm | Jul 2, 2026 1:24pm | Jul 2, 2026 2:37pm | Jul 2, 2026 3:33pm | Jul 2, 2026 3:33pm | Jul 2, 2026 3:33pm | BrokenWire | Y | SevereWind | No | 25kva transformer fuse blown patrol line section and found one pole span of neutral conductor burst down cut and removed vegetation then splice and retention conductor then close transformer fuse to restore supply to the area.material use 100ft of aaa conductor 3 one bolt clamps one 2amp fuse.
Outage | J.E.26.07.01102 | C001838049 | Rodclif Dawkins | Portmore | Completed | Load_247162 | Naggo Head - 510 | Jul 2, 2026 11:49am | Jul 3, 2026 7:24am | Jul 3, 2026 8:18am | Jul 3, 2026 8:18am | Jul 3, 2026 9:05am | Jul 3, 2026 10:10am | Jul 3, 2026 10:18am | Jul 3, 2026 10:18am |  |  | Fair | No | Found 50kva transformer, with burnt drop leads. 50kva transformer de-energized. Using 25ft of 2/0 copper, 3 ampact and 6-1bolt clamp drop leads changed and joints remade. Transformer energized , voltage recorded at dropleads were 121*2v,243v. Customer okay
Outage | J.E.26.07.01062 | C001838023 | Kaydon Taylor | KSAN | Completed | Load_252158 | Constant Spring - 410 | Jul 2, 2026 11:39am | Jul 2, 2026 11:44am | Jul 2, 2026 1:03pm | Jul 2, 2026 1:03pm | Jul 2, 2026 1:29pm | Jul 2, 2026 1:41pm | Jul 2, 2026 1:41pm | Jul 2, 2026 1:41pm |  |  | Rains | No | 25kva transformer fuse found blown and replace at pole #0001103. 3amp
Outage | J.E.26.07.01042 | C001838021 | Hartley Chin | Clarendon | Completed | Load_258346 | Parnassus - 210 | Jul 2, 2026 11:38am | Jul 2, 2026 11:38am | Jul 2, 2026 12:32pm | Jul 2, 2026 2:43pm | Jul 2, 2026 2:43pm | Jul 2, 2026 2:43pm | Jul 2, 2026 2:44pm | Jul 2, 2026 2:44pm |  |  | Fair | No | Call related to job # 00748 ..
Outage | J.E.26.07.01032 | C001838016 | Nickolas Rodriques | St.Catherine | Completed | Load_269710 | Twickenham - 210 | Jul 2, 2026 11:36am | Jul 2, 2026 3:25pm | Jul 2, 2026 3:40pm | Jul 2, 2026 3:45pm | Jul 2, 2026 4:18pm | Jul 2, 2026 4:22pm | Jul 2, 2026 4:23pm | Jul 2, 2026 4:23pm |  |  | Fair | No | Customer was located and confirmed that the power outage was restored.
Outage | J.E.26.07.01083 | C001838010 | Moses Elliston | St.Catherine | Completed | Load_241050 | Tredegar - 410 | Jul 2, 2026 11:31am | Jul 2, 2026 11:31am | Jul 2, 2026 5:03pm | Jul 2, 2026 5:03pm | Jul 2, 2026 5:03pm | Jul 2, 2026 5:03pm | Jul 2, 2026 5:05pm | Jul 2, 2026 5:05pm |  |  | Fair | No | Not located,no answer from cell
Outage | J.E.26.07.01039 | C001838002 | Roxroy Needham | St.Ann | Completed | Load_263265 | Cardiff Hall - 210 | Jul 2, 2026 11:24am | Jul 2, 2026 11:25am | Jul 2, 2026 11:44am | Jul 2, 2026 11:44am | Jul 2, 2026 12:10pm | Jul 2, 2026 12:11pm | Jul 2, 2026 12:12pm | Jul 2, 2026 12:12pm |  |  | Fair | No | Check and found premises ok
Outage | J.E.26.07.01075 | C001838000 | Odaine Johnson | Clarendon | Completed | Load_255470 | May Pen - 210 | Jul 2, 2026 11:23am | Jul 2, 2026 11:23am | Jul 2, 2026 1:51pm | Jul 2, 2026 1:51pm | Jul 2, 2026 1:51pm | Jul 2, 2026 1:51pm | Jul 2, 2026 1:52pm | Jul 2, 2026 1:52pm |  |  | Fair | No | Customer need reconnection along with a meter
Outage | J.E.26.07.00949 | C001837992 | Neckell Ormsby | St.Mary | Completed | Load_253844 | Highgate - 210 | Jul 2, 2026 11:21am | Jul 2, 2026 11:21am | Jul 2, 2026 12:10pm | Jul 2, 2026 12:10pm | Jul 2, 2026 12:53pm | Jul 2, 2026 1:16pm | Jul 2, 2026 1:22pm | Jul 2, 2026 1:22pm |  |  | Fair | No | Unable to locate customer after several calls also patrol entire line section found supply ok in area residents said power went earlier today
Outage | J.E.26.07.00982 | C001837993 | Neville Spencer | Clarendon | Completed | Load_572086 | Parnassus - 310 | Jul 2, 2026 11:21am | Jul 2, 2026 3:28pm | Jul 2, 2026 3:48pm | Jul 2, 2026 3:48pm | Jul 2, 2026 5:18pm | Jul 2, 2026 5:18pm | Jul 2, 2026 5:23pm | Jul 2, 2026 5:23pm |  |  | Fair | No | Hexin meter REF To FIELD Service.
Outage | J.E.26.07.00947 | C001837990 | Cliton Henry | St.Mary | Completed | Load_257364 | Oracabessa - 210 | Jul 2, 2026 11:20am | Jul 2, 2026 11:20am | Jul 2, 2026 11:56am | Jul 2, 2026 11:56am | Jul 2, 2026 12:34pm | Jul 2, 2026 12:47pm | Jul 2, 2026 1:02pm | Jul 2, 2026 1:02pm |  |  | Fair | No | Two (2) blown 10 amp transformer fuse found for two(2) 100kva transformer. Supply restored using 2 10 amp fuse. Voltages left were p-n 122-122/244 volts, hp 212 volt p-p- 244,244and hp-p 245 volts
Outage | J.E.26.07.01070 | C001837989 | Gregory Grossett | Portland | Completed | Load_260425 | Port Antonio - 410 | Jul 2, 2026 11:20am | Jul 2, 2026 11:20am | Jul 2, 2026 12:38pm | Jul 2, 2026 12:38pm | Jul 2, 2026 1:09pm | Jul 2, 2026 1:24pm | Jul 2, 2026 1:24pm | Jul 2, 2026 1:24pm |  |  | Fair | No | 25kva transformer fuse blown patrol line section then restore supply to the area material use 3amps fuse.
Outage | J.E.26.07.00997 | C001837988 | Clyde Brown | Clarendon | Completed | Load_252707 | May Pen - 110 | Jul 2, 2026 11:19am | Jul 2, 2026 11:19am | Jul 2, 2026 12:17pm | Jul 2, 2026 12:21pm | Jul 2, 2026 12:21pm | Jul 2, 2026 12:11pm | Jul 2, 2026 12:22pm | Jul 2, 2026 12:22pm |  |  | Fair | No | Found ok
Outage | J.E.26.07.01026 | C001837987 | Romaine Roberts | St.Mary | Completed | Load_249545 | Annotto Bay - 210 | Jul 2, 2026 11:19am | Jul 2, 2026 11:19am | Jul 2, 2026 12:59pm | Jul 2, 2026 12:59pm | Jul 2, 2026 1:53pm | Jul 2, 2026 2:07pm | Jul 2, 2026 2:11pm | Jul 2, 2026 2:11pm |  |  | Fair | No | Found 50 kva transformer burn and need to be change maintenance crew needed
Outage | J.E.26.07.00993 | C001837986 | Cliton Henry | St.Mary | Completed | Load_269770 | Blackstonedge - 110 | Jul 2, 2026 11:18am | Jul 2, 2026 11:20am | Jul 2, 2026 1:02pm | Jul 2, 2026 1:02pm | Jul 2, 2026 1:11pm | Jul 2, 2026 1:11pm | Jul 2, 2026 1:12pm | Jul 2, 2026 1:12pm |  |  | Fair | No | Supply found ok
Outage | J.E.26.07.01008 | C001837979 | Clyde Brown | Clarendon | Completed | Load_247364 | May Pen - 110 | Jul 2, 2026 11:17am | Jul 2, 2026 11:17am | Jul 2, 2026 12:25pm | Jul 2, 2026 12:25pm | Jul 2, 2026 1:55pm | Jul 2, 2026 1:50pm | Jul 2, 2026 2:01pm | Jul 2, 2026 2:01pm |  |  | Fair | No | Blown 25 amps junction fuse in Brandon hill square caused by tree contact,line cleared and blown fuse replaced.
Outage | J.E.26.07.01028 | C001837984 | Clyde Brown | Clarendon | Completed | Load_568388 | May Pen - 110 | Jul 2, 2026 11:17am | Jul 2, 2026 11:17am | Jul 2, 2026 11:31am | Jul 2, 2026 11:31am | Jul 2, 2026 12:18pm | Jul 2, 2026 12:11pm | Jul 2, 2026 12:19pm | Jul 2, 2026 12:19pm |  |  | Fair | No | Found area ok
Outage | J.E.26.07.00729 | C001837977 | Kenroy Dale | Manchester | Completed | Load_247696 | Porus - 310 | Jul 2, 2026 11:16am | Jul 2, 2026 11:16am | Jul 2, 2026 12:06pm | Jul 2, 2026 12:13pm | Jul 2, 2026 1:53pm | Jul 2, 2026 2:40pm | Jul 2, 2026 2:55pm | Jul 2, 2026 2:55pm |  |  | Fair | No | Blown 3 amp fuse found for 25 kva transformer. Line patrol nothing found (twisted secondary) blown fuse was replaced and site now with supply
Outage | J.E.26.07.00965 | C001837975 | Rodclif Dawkins | St.Catherine | Completed | Load_269101 | Twickenham - 210 | Jul 2, 2026 11:15am | Jul 2, 2026 11:15am | Jul 2, 2026 11:33am | Jul 2, 2026 11:33am | Jul 2, 2026 12:23pm | Jul 2, 2026 12:37pm | Jul 2, 2026 12:38pm | Jul 2, 2026 12:38pm |  |  | Fair | No | Premises was checked and found okay.
Outage | J.E.26.07.01013 | C001837974 | Moses Elliston | St.Catherine | Completed | Load_249560 | Twickenham - 310 | Jul 2, 2026 11:14am | Jul 2, 2026 11:14am | Jul 2, 2026 4:15pm | Jul 2, 2026 4:15pm | Jul 2, 2026 4:15pm | Jul 2, 2026 4:15pm | Jul 2, 2026 4:16pm | Jul 2, 2026 4:16pm |  |  | Fair | No | Supply reconnected.Box went out.
Outage | J.E.26.07.00951 | C001837963 | Moses Elliston | St.Catherine | Completed | Load_249074 | Tredegar - 310 | Jul 2, 2026 11:12am | Jul 2, 2026 11:12am | Jul 2, 2026 5:25pm | Jul 2, 2026 5:25pm | Jul 2, 2026 5:25pm | Jul 2, 2026 5:25pm | Jul 2, 2026 5:27pm | Jul 2, 2026 5:27pm |  |  | Fair | No | Supply reconnected. Box was out
Non-Outage | J.E.26.06.38736 | C001837961 | Richman Whyte | Westmoreland | Completed | Load_268438 | Paradise - 310 | Jul 2, 2026 11:10am | Jul 2, 2026 11:11am | Jul 2, 2026 12:47pm | Jul 2, 2026 12:47pm | Jul 2, 2026 12:47pm | Jul 2, 2026 12:47pm | Jul 2, 2026 12:48pm | Jul 2, 2026 12:48pm |  |  | Fair | No | Internal problem advice to fix voltage #115 115 230
Outage | J.E.26.07.00920 | C001837956 | Gregory Grossett | Portland | Completed | Load_266709 | Port Antonio - 410 | Jul 2, 2026 11:00am | Jul 2, 2026 11:00am | Jul 2, 2026 11:04am | Jul 2, 2026 11:04am | Jul 2, 2026 11:22am | Jul 2, 2026 12:10pm | Jul 2, 2026 12:37pm | Jul 2, 2026 12:37pm | Fire | Y | Fair | No | Tree fall on line section and burst down secondary conductors open 10kva transformer fuse then then cut and removed tree then splice and retention conductors.Close transformer fuse to restore normal supply to the area.Material use 15ft of 2/0 conductor 2 one bolt clamps 1 2/0 splicing sleeve.
Outage | J.E.26.07.00778 | C001837952 | Oshane Warren | Hanover | Completed | Load_292400 | Orange Bay - 310 | Jul 2, 2026 10:57am | Jul 2, 2026 10:58am | Jul 2, 2026 1:11pm | Jul 2, 2026 1:11pm | Jul 2, 2026 1:23pm | Jul 2, 2026 1:23pm | Jul 2, 2026 1:24pm | Jul 2, 2026 1:24pm |  |  | Fair | No | Hexing metering system refer to field service
Outage | J.E.26.07.00850 | C001837951 | Oshane Warren | Hanover | Completed | Load_252532 | Orange Bay - 310 | Jul 2, 2026 10:57am | Jul 2, 2026 10:58am | Jul 2, 2026 12:50pm | Jul 2, 2026 12:50pm | Jul 2, 2026 1:08pm | Jul 2, 2026 1:09pm | Jul 2, 2026 1:11pm | Jul 2, 2026 1:11pm |  |  | Fair | No | Internal problem advice to fix
Outage | J.E.26.07.00814 | C001837946 | Andrew Powell | St.Elizabeth | Completed | Load_240525 | Maggotty - 210 | Jul 2, 2026 10:55am | Jul 2, 2026 10:56am | Jul 2, 2026 11:48am | Jul 2, 2026 11:48am | Jul 2, 2026 12:30pm | Jul 2, 2026 12:53pm | Jul 2, 2026 12:55pm | Jul 2, 2026 12:55pm | BrokenWire |  | SevereWind | No | Splice and tension broken service wire neutral at secondary line 3 wire using 10 feet #6 triplex, voltage reading 112v-113v phase to neutral 225v cross phase.
Outage | J.E.26.07.00880 | C001837947 | Andrew Powell | St.Elizabeth | Completed | Load_252231 | Maggotty - 210 | Jul 2, 2026 10:55am | Jul 2, 2026 10:56am | Jul 2, 2026 12:58pm | Jul 2, 2026 12:58pm | Jul 2, 2026 1:11pm | Jul 2, 2026 1:12pm | Jul 2, 2026 1:16pm | Jul 2, 2026 1:16pm |  |  | Fair | No | Internal fault at customer premises burnt up service entry wire, leave disconnect at meter pothead 3 wire.
Outage | J.E.26.07.00895 | C001837948 | Moses Elliston | St.Catherine | Completed | Load_1001067 | Tredegar - 210 | Jul 2, 2026 10:55am | Jul 2, 2026 10:55am | Jul 3, 2026 5:29pm | Jul 3, 2026 5:29pm | Jul 3, 2026 5:29pm | Jul 3, 2026 5:15pm | Jul 3, 2026 5:31pm | Jul 3, 2026 5:31pm |  |  | Fair | No | Not located,no answer from cell
Outage | J.E.26.07.00881 | C001837941 | Shamour Haughton | St.James | Completed | Load_261536 | Bogue - 310 | Jul 2, 2026 10:54am | Jul 2, 2026 11:06am | Jul 2, 2026 12:21pm | Jul 2, 2026 12:21pm | Jul 2, 2026 12:21pm | Jul 2, 2026 12:22pm | Jul 2, 2026 12:22pm | Jul 2, 2026 12:22pm |  |  | Fair | No | Customer says power was restored
Outage | J.E.26.07.00893 | C001837942 | Horace Malcolm | St.James | Completed | Load_267409 | Bogue - 610 | Jul 2, 2026 10:54am | Jul 2, 2026 11:05am | Jul 2, 2026 12:07pm | Jul 2, 2026 12:07pm | Jul 2, 2026 12:33pm | Jul 2, 2026 12:42pm | Jul 2, 2026 12:42pm | Jul 2, 2026 12:42pm |  |  | Fair | No | Customer was disconnected got back customer reconnected
Outage | J.E.26.07.00894 | C001837944 | Ricky Hall | St.Catherine | Completed | Load_268453 | New Michelton - 310 | Jul 2, 2026 10:54am | Jul 2, 2026 10:54am | Jul 2, 2026 11:43am | Jul 2, 2026 11:43am | Jul 2, 2026 12:23pm | Jul 2, 2026 12:52pm | Jul 2, 2026 12:53pm | Jul 2, 2026 12:53pm |  |  | Rains | No | Replaced blown 20 amps junction fuse
Non-Outage | J.E.26.07.00890 | C001837926 | Hartley Chin | Clarendon | Completed | Load_258346 | Parnassus - 210 | Jul 2, 2026 10:42am | Jul 2, 2026 10:42am | Jul 2, 2026 12:14pm | Jul 2, 2026 2:42pm | Jul 2, 2026 2:42pm | Jul 2, 2026 2:42pm | Jul 2, 2026 2:43pm | Jul 2, 2026 2:43pm | BrokenWire |  | Fair | No | Call related to job # 00748 …
Outage | J.E.26.07.00829 | C001837921 | Dean Smith | Hanover | Completed | Load_244461 | Orange Bay - 310 | Jul 2, 2026 10:41am | Jul 2, 2026 10:41am | Jul 2, 2026 3:34pm | Jul 2, 2026 3:34pm | Jul 2, 2026 3:34pm | Jul 2, 2026 3:34pm | Jul 2, 2026 3:34pm | Jul 2, 2026 3:34pm |  |  | Fair | No | Shift ended
Outage | J.E.26.07.00830 | C001837920 | Dean Smith | Hanover | Completed | Load_302841 | Orange Bay - 310 | Jul 2, 2026 10:41am | Jul 2, 2026 10:41am | Jul 2, 2026 11:32am | Jul 2, 2026 11:32am | Jul 2, 2026 1:01pm | Jul 2, 2026 1:01pm | Jul 2, 2026 3:26pm | Jul 2, 2026 3:26pm |  |  | Fair | No | Cut and remove tree, splice and retention “2” span of secondary phase conductor. Replace 20amp junction fuse at pole number (007920)
Non-Outage | J.E.26.06.35630 | C001837918 | Odeanie Davis | KSAS | Completed | Load_239504 | Rockfort - 410 | Jul 2, 2026 10:38am | Jul 2, 2026 10:39am | Jul 2, 2026 10:44am | Jul 2, 2026 11:39am | Jul 2, 2026 11:39am | Jul 2, 2026 11:46am | Jul 2, 2026 11:40am | Jul 2, 2026 11:40am |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.06.37775 | C001837917 | Odeanie Davis | KSAS | Completed | Load_238152 | Rockfort - 410 | Jul 2, 2026 10:38am | Jul 2, 2026 10:38am | Jul 2, 2026 10:44am | Jul 2, 2026 10:51am | Jul 2, 2026 10:53am | Jul 2, 2026 11:34am | Jul 2, 2026 11:34am | Jul 2, 2026 11:34am |  |  | Fair | No | 100v/126v at arrival, open circuit at secondary corrected, 3 one bolt clamps & 2 penn union, 112v/113v & 226v after correction
Non-Outage | J.E.26.06.38190 | C001837916 | Odeanie Davis | KSAS | Completed | Load_266339 | Rockfort - 410 | Jul 2, 2026 10:38am | Jul 2, 2026 10:38am | Jul 2, 2026 12:01pm | Jul 2, 2026 2:12pm | Jul 2, 2026 2:12pm | Jul 2, 2026 2:33pm | Jul 2, 2026 2:33pm | Jul 2, 2026 2:33pm |  |  | Fair | No | 120v at location, meter found blank, customer still has power at premise, meter needs to be replaced, field service team needed,
Non-Outage | J.E.26.06.39892 | C001837914 | Odeanie Davis | KSAS | Completed | Load_266339 | Rockfort - 410 | Jul 2, 2026 10:37am | Jul 2, 2026 10:37am | Jul 2, 2026 12:01pm | Jul 2, 2026 12:08pm | Jul 2, 2026 12:11pm | Jul 2, 2026 12:16pm | Jul 2, 2026 12:12pm | Jul 2, 2026 12:12pm |  |  | Fair | No | Customer stated that issue was resolved by Jps
Non-Outage | J.E.26.07.00871 | C001837913 | Odeanie Davis | KSAS | Completed | Load_251755 | Rockfort - 410 | Jul 2, 2026 10:37am | Jul 2, 2026 10:37am | Jul 2, 2026 12:01pm | Jul 2, 2026 1:58pm | Jul 2, 2026 1:58pm | Jul 2, 2026 2:08pm | Jul 2, 2026 2:08pm | Jul 2, 2026 2:08pm |  |  | Fair | No | 111v/118v at arrival, open circuit at pothead and secondary corrected, 3 penn union & 3 one bolt clamps, 117v/118v & 236v after correction.
Non-Outage | J.E.26.06.38423 | C001837907 | Odeanie Davis | KSAS | Completed | Load_266339 | Rockfort - 410 | Jul 2, 2026 10:36am | Jul 2, 2026 10:37am | Jul 2, 2026 12:01pm | Jul 2, 2026 12:30pm | Jul 2, 2026 12:30pm | Jul 2, 2026 12:41pm | Jul 2, 2026 12:33pm | Jul 2, 2026 12:33pm |  |  | Fair | No
Non-Outage | J.E.26.06.39038 | C001837908 | Odeanie Davis | KSAS | Completed | Load_251755 | Rockfort - 410 | Jul 2, 2026 10:36am | Jul 2, 2026 10:37am | Jul 2, 2026 12:01pm | Jul 2, 2026 1:49pm | Jul 2, 2026 1:49pm | Jul 2, 2026 2:00pm | Jul 2, 2026 1:57pm | Jul 2, 2026 1:57pm |  |  | Fair | No | 111v/118v at arrival, open circuit at pothead and secondary corrected, 3 penn union & 3 one bolt clamps, 117v/118v & 236v after correction.
Non-Outage | J.E.26.06.39134 | C001837909 | Odeanie Davis | KSAS | Completed | Load_265641 | Rockfort - 410 | Jul 2, 2026 10:36am | Jul 2, 2026 10:37am | Jul 2, 2026 10:44am | Jul 2, 2026 11:48am | Jul 2, 2026 11:48am | Jul 2, 2026 12:01pm | Jul 2, 2026 12:01pm | Jul 2, 2026 12:01pm |  |  | Fair | No | 115v/117v & 233v at location. Customer stated that issue was on their end and it was resolved by their electrician
Non-Outage | J.E.26.06.39870 | C001837911 | Odeanie Davis | KSAS | Completed | Load_266339 | Rockfort - 410 | Jul 2, 2026 10:36am | Jul 2, 2026 10:37am | Jul 2, 2026 12:01pm | Jul 2, 2026 12:12pm | Jul 2, 2026 12:13pm | Jul 2, 2026 12:24pm | Jul 2, 2026 12:14pm | Jul 2, 2026 12:14pm |  |  | Fair | No
Non-Outage | J.E.26.06.39872 | C001837910 | Odeanie Davis | KSAS | Completed | Load_266339 | Rockfort - 410 | Jul 2, 2026 10:36am | Jul 2, 2026 10:37am | Jul 2, 2026 12:01pm | Jul 2, 2026 2:08pm | Jul 2, 2026 2:08pm | Jul 2, 2026 2:20pm | Jul 2, 2026 2:12pm | Jul 2, 2026 2:12pm |  |  | Fair | No | 120v at location, meter found blank, meter needs to be replaced, field service team needed
Non-Outage | J.E.26.06.39880 | C001837912 | Odeanie Davis | KSAS | Completed | Load_266339 | Rockfort - 410 | Jul 2, 2026 10:36am | Jul 2, 2026 10:37am | Jul 2, 2026 12:01pm | Jul 2, 2026 12:15pm | Jul 2, 2026 12:16pm | Jul 2, 2026 12:36pm | Jul 2, 2026 12:27pm | Jul 2, 2026 12:27pm |  |  | Fair | No | 111v/116v & 227v , issue was resolved by jps
Non-Outage | J.E.26.07.00811 | C001837906 | Barnett Brown | Manchester | Completed | Load_265474 | Kendal - 210 | Jul 2, 2026 10:34am | Jul 2, 2026 10:35am | null | Jul 2, 2026 1:12pm | Jul 2, 2026 1:12pm | Jul 2, 2026 1:50pm | Jul 2, 2026 1:55pm | Jul 2, 2026 1:55pm |  |  | Fair | No | Customer has internal fault
Outage | J.E.26.07.00885 | C001837905 | Neckell Ormsby | St.Mary | Completed | Load_256363 | Highgate - 210 | Jul 2, 2026 10:33am | Jul 2, 2026 10:33am | Jul 2, 2026 1:22pm | Jul 2, 2026 1:22pm | Jul 2, 2026 1:23pm | Jul 2, 2026 1:24pm | Jul 2, 2026 1:24pm | Jul 2, 2026 1:24pm |  |  | Fair | No | Found supply ok in area customer said power came back
Outage | J.E.26.07.00869 | C001837895 | Nickolas Rodriques | St.Catherine | Completed | Load_576119 | Twickenham - 210 | Jul 2, 2026 10:25am | Jul 2, 2026 3:25pm | Jul 2, 2026 4:23pm | Jul 2, 2026 4:28pm | Jul 2, 2026 5:20pm | Jul 2, 2026 5:56pm | Jul 2, 2026 5:57pm | Jul 2, 2026 5:57pm |  |  | Fair | No | Customer was contacted and stated that no one is currently home to accommodate the team.
Outage | J.E.26.07.00874 | C001837894 | Moses Elliston | St.Catherine | Completed | Load_245608 | Twickenham - 210 | Jul 2, 2026 10:24am | Jul 2, 2026 10:25am | Jul 2, 2026 10:37am | Jul 2, 2026 10:37am | Jul 2, 2026 10:37am | Jul 2, 2026 10:38am | Jul 2, 2026 10:39am | Jul 2, 2026 10:39am |  |  | Fair | No | Customer said credit added to account.
Outage | J.E.26.07.00793 | C001837866 | Kaydon Taylor | KSAN | Completed | Load_238692 | Constant Spring - 410 | Jul 2, 2026 10:10am | Jul 2, 2026 10:11am | Jul 2, 2026 1:43pm | Jul 2, 2026 1:43pm | Jul 2, 2026 4:06pm | Jul 2, 2026 4:44pm | Jul 2, 2026 4:44pm | Jul 2, 2026 4:44pm | TreeContact | Y | Rains | No | Primary bushing requires. Bamboo on cover conductor single phase.In order to remove the bamboo it would required an outage which would affect areas like Glengoffe road, saint faiths road, Ashley Dist and surrounding areas. Trying to reach out via telecommunication but wasn’t successful due to poor signals.
Outage | J.E.26.07.00838 | C001837867 | Kaydon Taylor | KSAN | Completed | Load_255442 | Constant Spring - 410 | Jul 2, 2026 10:10am | Jul 2, 2026 10:11am | Jul 2, 2026 6:19pm | Jul 2, 2026 6:19pm | Jul 2, 2026 6:55pm | Jul 2, 2026 6:56pm | Jul 2, 2026 6:56pm | Jul 2, 2026 6:56pm |  |  | Rains | No | 15 amp fuse found blown and replaced at pole # 035455
Outage | J.E.26.07.00177 | C001837865 | Kaydon Taylor | KSAN | Completed | Load_261778 | Constant Spring - 310 | Jul 2, 2026 10:09am | Jul 2, 2026 10:10am | Jul 2, 2026 6:56pm | Jul 2, 2026 6:56pm | Jul 2, 2026 7:08pm | Jul 2, 2026 7:33pm | Jul 2, 2026 7:33pm | Jul 2, 2026 7:33pm |  |  | Fair | No | Reset meter
Outage | J.E.26.07.00863 | C001837864 | Shamour Haughton | St.James | Completed | Load_242717 | Bogue - 310 | Jul 2, 2026 10:08am | Jul 2, 2026 10:10am | Jul 2, 2026 11:50am | Jul 2, 2026 11:50am | Jul 2, 2026 12:11pm | Jul 2, 2026 12:11pm | Jul 2, 2026 12:12pm | Jul 2, 2026 12:12pm |  |  | Fair | No | Customer saying they didn’t make any report
Outage | J.E.26.07.00828 | C001837854 | Shamour Haughton | St.James | Completed | Load_301826 | Bogue - 310 | Jul 2, 2026 10:03am | Jul 2, 2026 10:07am | Jul 2, 2026 12:23pm | Jul 2, 2026 12:23pm | Jul 2, 2026 12:23pm | Jul 2, 2026 12:24pm | Jul 2, 2026 12:24pm | Jul 2, 2026 12:24pm |  |  | Fair | No | Customer states that power was restored
Outage | J.E.26.07.00845 | C001837855 | Shamour Haughton | St.James | Completed | Load_575863 | Bogue - 410 | Jul 2, 2026 10:03am | Jul 2, 2026 10:07am | Jul 2, 2026 11:38am | Jul 2, 2026 11:38am | Jul 2, 2026 11:48am | Jul 2, 2026 11:49am | Jul 2, 2026 11:49am | Jul 2, 2026 11:49am |  |  | Fair | No | Customer is saying that power was restored
Outage | J.E.26.07.00851 | C001837856 | Shamour Haughton | St.James | Completed | Load_1001936 | Bogue - 310 | Jul 2, 2026 10:03am | Jul 2, 2026 10:07am | Jul 2, 2026 12:22pm | Jul 2, 2026 12:22pm | Jul 2, 2026 12:22pm | Jul 2, 2026 12:23pm | Jul 2, 2026 12:23pm | Jul 2, 2026 12:23pm |  |  | Fair | No | Customer states power was restored
Non-Outage | J.E.26.06.38023 | C001837852 | Error Coore | Manchester | Completed | Load_1002357 | Spur Tree - 310 | Jul 2, 2026 10:02am | Jul 2, 2026 10:06am | Jul 2, 2026 10:37am | Jul 2, 2026 10:38am | Jul 2, 2026 11:01am | Jul 2, 2026 11:13am | Jul 2, 2026 11:16am | Jul 2, 2026 11:16am |  |  | Fair | No | Customer have some internal issues customer need to do some repair before we can make any connection due to customer wire in pothead is too short to make any connection
Non-Outage | J.E.26.06.38141 | C001837853 | Error Coore | Manchester | Completed | Load_257142 | Spur Tree - 310 | Jul 2, 2026 10:02am | Jul 2, 2026 10:06am | Jul 2, 2026 12:30pm | Jul 2, 2026 12:30pm | Jul 2, 2026 1:38pm | Jul 2, 2026 2:26pm | Jul 2, 2026 2:28pm | Jul 2, 2026 2:28pm |  |  | Fair | No | Premise not found unable to locate customer not getting customer on phone
Non-Outage | J.E.26.06.38348 | C001837851 | Error Coore | Manchester | Completed | Load_255644 | Porus - 310 | Jul 2, 2026 10:02am | Jul 2, 2026 10:06am | Jul 2, 2026 10:25am | Jul 2, 2026 11:16am | Jul 2, 2026 12:07pm | Jul 2, 2026 12:28pm | Jul 2, 2026 12:30pm | Jul 2, 2026 12:30pm |  |  | Fair | No | Premise found ok voltage reading 118/118/236 volts
Non-Outage | J.E.26.01.26095 | C001837825 | Dwain Samuels | Hanover | Completed | Load_257976 | Orange Bay - 310 | Jul 2, 2026 9:51am | Jul 2, 2026 9:57am | Jul 2, 2026 10:11am | Jul 2, 2026 12:35pm | Jul 2, 2026 12:35pm | Jul 2, 2026 12:38pm | Jul 2, 2026 12:39pm | Jul 2, 2026 12:39pm |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.01.26151 | C001837826 | Dwain Samuels | Westmoreland | Completed | Load_292432 | Orange Bay - 210 | Jul 2, 2026 9:51am | Jul 2, 2026 9:52am | Jul 2, 2026 10:11am | Jul 2, 2026 10:38am | Jul 2, 2026 10:49am | Jul 2, 2026 10:49am | Jul 2, 2026 10:52am | Jul 2, 2026 10:52am |  |  | Fair | No | Need proper contact and directions. Couldn’t locate meter in front the church
Non-Outage | J.E.26.01.26157 | C001837829 | Dwain Samuels | Hanover | Completed | Load_257650 | Orange Bay - 310 | Jul 2, 2026 9:51am | Jul 2, 2026 9:54am | Jul 2, 2026 10:11am | Jul 2, 2026 12:05pm | Jul 2, 2026 12:05pm | Jul 2, 2026 12:10pm | Jul 2, 2026 12:11pm | Jul 2, 2026 12:11pm |  |  | Fair | No | Customer said supply was restored
Non-Outage | J.E.26.01.26197 | C001837824 | Dwain Samuels | Hanover | Completed | Load_249606 | Orange Bay - 310 | Jul 2, 2026 9:51am | Jul 2, 2026 9:57am | Jul 2, 2026 10:11am | Jul 2, 2026 12:23pm | Jul 2, 2026 12:23pm | Jul 2, 2026 12:30pm | Jul 2, 2026 12:31pm | Jul 2, 2026 12:31pm |  |  | Fair | No | Corrosion found at 2 wire pot head . Voltage check 100. Corrosion clear use 2 one bolt clamp. Voltage check 115
Non-Outage | J.E.26.01.26216 | C001837830 | Dwain Samuels | Westmoreland | Completed | Load_252081 | Orange Bay - 210 | Jul 2, 2026 9:51am | Jul 2, 2026 9:52am | Jul 2, 2026 10:11am | Jul 2, 2026 10:11am | Jul 2, 2026 10:16am | Jul 2, 2026 10:17am | Jul 2, 2026 10:28am | Jul 2, 2026 10:28am |  |  | Fair | No | Corrosion found at 3 wire pole. Voltage check 105-100-205. Corrosion clear use 2 one bolt clamp. Voltage check 115-115-230
Non-Outage | J.E.26.01.26235 | C001837827 | Dwain Samuels | Westmoreland | Completed | Load_292703 | Orange Bay - 210 | Jul 2, 2026 9:51am | Jul 2, 2026 9:52am | Jul 2, 2026 10:11am | Jul 3, 2026 10:14am | Jul 3, 2026 10:14am | Jul 3, 2026 10:14am | Jul 3, 2026 10:16am | Jul 3, 2026 10:16am |  |  | Fair | No | Called multiple times got no answer. Need proper contact an directions
Non-Outage | J.E.26.07.00820 | C001837822 | Stephen Taylor | null | Completed | null | null | Jul 2, 2026 9:48am | Jul 2, 2026 9:57am | Jul 2, 2026 10:33am | Jul 2, 2026 10:33am | Jul 2, 2026 11:31am | Jul 2, 2026 11:31am | Jul 2, 2026 11:33am | Jul 2, 2026 11:33am | BrokenWire |  | Fair | No | Splice and retention services wire customer is now okay reading 112,113,225
Outage | J.E.26.07.00836 | C001837813 | Wan Carlos Scarlett | St.Catherine | Completed | Load_256082 | Tredegar - 210 | Jul 2, 2026 9:45am | Jul 2, 2026 9:46am | Jul 2, 2026 12:32pm | Jul 2, 2026 12:32pm | Jul 2, 2026 12:53pm | Jul 2, 2026 2:37pm | Jul 2, 2026 2:40pm | Jul 2, 2026 2:40pm | Fire |  | Fair | No | Found customer 3 wire service at pothead and pole with phase and neutral corroded use 6 Penn union at service wire phase and neutral readings 114-115-230
Non-Outage | J.E.26.07.00826 | C001837812 | Ricky Hall | null | Completed | null | null | Jul 2, 2026 9:44am | Jul 2, 2026 9:45am | Jul 2, 2026 10:06am | Jul 2, 2026 10:10am | Jul 2, 2026 11:35am | Jul 2, 2026 11:41am | Jul 2, 2026 11:42am | Jul 2, 2026 11:42am | Fire |  | Fair | No | Premises not found
Outage | J.E.26.07.00795 | C001837811 | Rodclif Dawkins | St.Catherine | Completed | Load_262979 | Twickenham - 210 | Jul 2, 2026 9:43am | Jul 2, 2026 9:43am | Jul 2, 2026 10:50am | Jul 2, 2026 10:50am | Jul 2, 2026 11:18am | Jul 2, 2026 11:30am | Jul 2, 2026 11:30am | Jul 2, 2026 11:30am | Fire |  | Fair | No | Customer advise crew that situation was corrected . Situation is normalize.
Outage | J.E.26.07.00800 | C001837802 | Hartley Chin | Clarendon | Completed | Load_349984 | May Pen - 210 | Jul 2, 2026 9:34am | Jul 2, 2026 9:44am | Jul 2, 2026 9:55am | Jul 2, 2026 10:18am | Jul 2, 2026 10:41am | Jul 2, 2026 11:48am | Jul 2, 2026 11:58am | Jul 2, 2026 11:58am | BrokenWire |  | Fair | No | Found blown 3 amp fuse on 25 KVA transformer @ pole # 0112148 due to broken open secondary phase found in span and broken service service wire … repair broken open phase , repair 70 ft service wire … Ref to maintenance ! Found rotten 30 ft pole with open secondary circuit, pole requires urgent attention due to it moving with the with … pole foot is 100% gone (rotten) …
Outage | J.E.26.07.00799 | C001837783 | Daniel Francis | St.Ann | Completed | Load_264468 | Roaring River - 410 | Jul 2, 2026 9:06am | Jul 2, 2026 9:07am | Jul 2, 2026 10:52am | Jul 2, 2026 10:52am | Jul 2, 2026 11:09am | Jul 2, 2026 11:46am | Jul 2, 2026 11:48am | Jul 2, 2026 11:48am |  |  | Fair | No | Replace defective service wire by erecting ft45
Non-Outage | J.E.26.06.38560 | C001837782 | Andrae Dawkins | St.James | Completed | Load_269636 | Queens Drive - 310 | Jul 2, 2026 8:57am | Jul 2, 2026 9:04am | Jul 3, 2026 9:00am | Jul 3, 2026 9:12am | Jul 3, 2026 9:31am | Jul 3, 2026 9:32am | Jul 3, 2026 9:34am | Jul 3, 2026 9:34am |  |  | Fair | No | Check and found okay customer said that the problem was already resolved
Non-Outage | J.E.26.06.39413 | C001837780 | Andrae Dawkins | St.James | Completed | Load_251289 | Queens Drive - 710 | Jul 2, 2026 8:57am | Jul 2, 2026 9:04am | Jul 2, 2026 2:03pm | Jul 3, 2026 8:10am | Jul 3, 2026 8:10am | Jul 3, 2026 8:10am | Jul 3, 2026 8:12am | Jul 3, 2026 8:12am |  |  | Fair | No | Check and found okay customer said that the problem was already resolved
Non-Outage | J.E.26.06.39914 | C001837778 | Andrae Dawkins | St.James | Completed | Load_259820 | Rose Hall - 210 | Jul 2, 2026 8:56am | Jul 2, 2026 9:04am | Jul 2, 2026 2:01pm | Jul 2, 2026 3:16pm | Jul 2, 2026 3:17pm | Jul 2, 2026 3:14pm | Jul 2, 2026 3:19pm | Jul 2, 2026 3:19pm |  |  | Fair | No | Check and found ok customer said that the problem was already resolved voltage resolved
Non-Outage | J.E.26.06.39936 | C001837777 | Andrae Dawkins | St.James | Completed | Load_1003256 | Bogue - 310 | Jul 2, 2026 8:56am | Jul 2, 2026 9:04am | Jul 2, 2026 2:01pm | Jul 2, 2026 3:19pm | Jul 2, 2026 3:19pm | Jul 2, 2026 3:20pm | Jul 2, 2026 3:21pm | Jul 2, 2026 3:21pm |  |  | Fair | No | Check and found ok customer said that the problem was already resolved
Non-Outage | J.E.26.07.00186 | C001837776 | Andrae Dawkins | St.James | Completed | Load_575159 | Bogue - 310 | Jul 2, 2026 8:56am | Jul 2, 2026 9:04am | Jul 3, 2026 8:21am | Jul 3, 2026 9:02am | Jul 3, 2026 9:02am | Jul 3, 2026 8:57am | Jul 3, 2026 9:05am | Jul 3, 2026 9:05am |  |  | Fair | No | Cannot locate customer unable to reach customer mobile phone
Non-Outage | J.E.26.07.00264 | C001837775 | Andrae Dawkins | null | Completed | null | null | Jul 2, 2026 8:52am | Jul 2, 2026 9:04am | Jul 3, 2026 8:21am | Jul 3, 2026 8:40am | Jul 3, 2026 8:40am | Jul 3, 2026 8:40am | Jul 3, 2026 8:42am | Jul 3, 2026 8:42am |  |  | Fair | No | Cannot locate customer unable to reach customers mobile phone
Non-Outage | J.E.26.07.00391 | C001837773 | Andrae Dawkins | St.James | Completed | Load_292251 | Queens Drive - 710 | Jul 2, 2026 8:52am | Jul 2, 2026 9:03am | Jul 2, 2026 2:02pm | Jul 2, 2026 2:14pm | Jul 2, 2026 2:22pm | Jul 2, 2026 2:24pm | Jul 2, 2026 2:30pm | Jul 2, 2026 2:30pm |  |  | Fair | No | Check and found okay problem was already resolved voltage left 112/117/229
Non-Outage | J.E.26.07.00396 | C001837772 | Andrae Dawkins | St.James | Completed | Load_293288 | Queens Drive - 310 | Jul 2, 2026 8:51am | Jul 2, 2026 9:03am | Jul 3, 2026 9:01am | Jul 3, 2026 11:54am | Jul 3, 2026 11:54am | Jul 3, 2026 11:55am | Jul 3, 2026 11:57am | Jul 3, 2026 11:57am |  |  | Fair | No | Found multiple customers experiencing low voltage from EG box at box number 02341 refer back to field service
Non-Outage | J.E.26.07.00500 | C001837771 | Andrae Dawkins | St.James | Completed | Load_248976 | Queens Drive - 710 | Jul 2, 2026 8:51am | Jul 2, 2026 9:03am | Jul 3, 2026 8:19am | Jul 3, 2026 9:05am | Jul 3, 2026 9:05am | Jul 3, 2026 9:04am | Jul 3, 2026 9:07am | Jul 3, 2026 9:07am |  |  | Fair | No | Cannot locate customer unable to reach customer mobile phone
Non-Outage | J.E.26.07.00515 | C001837770 | Andrae Dawkins | St.James | Completed | Load_265113 | Rose Hall - 210 | Jul 2, 2026 8:51am | Jul 2, 2026 9:03am | Jul 3, 2026 9:01am | Jul 3, 2026 11:57am | Jul 3, 2026 11:57am | Jul 3, 2026 10:55am | Jul 3, 2026 12:03pm | Jul 3, 2026 12:03pm |  |  | Fair | No | Cannot locate unable to reach customer mobile phone
Non-Outage | J.E.26.07.00639 | C001837769 | Andrae Dawkins | St.James | Completed | Load_265607 | Bogue - 310 | Jul 2, 2026 8:51am | Jul 2, 2026 9:03am | Jul 3, 2026 8:21am | Jul 3, 2026 8:34am | Jul 3, 2026 8:34am | Jul 3, 2026 8:34am | Jul 3, 2026 8:39am | Jul 3, 2026 8:39am |  |  | Fair | No | Found customer single phasng from HEX box at box number 02429
Non-Outage | J.E.26.07.00686 | C001837768 | Andrae Dawkins | St.James | Completed | Load_259109 | Queens Drive - 710 | Jul 2, 2026 8:51am | Jul 2, 2026 9:03am | Jul 2, 2026 2:00pm | Jul 2, 2026 3:23pm | Jul 2, 2026 3:29pm | Jul 2, 2026 4:37pm | Jul 2, 2026 4:40pm | Jul 2, 2026 4:40pm |  |  | Fair | No | Found customer experiencing low voltage due to corrosion at pothead clean and remade joints used one pg clamp voltage left 118/119/237
Non-Outage | J.E.26.06.35857 | C001837763 | Donald Cunningham | St.Catherine | Completed | Load_265381 | Rhodens Pen - 210 | Jul 2, 2026 8:43am | Jul 2, 2026 8:44am | Jul 2, 2026 8:50am | Jul 2, 2026 8:50am | Jul 2, 2026 10:02am | Jul 2, 2026 10:06am | Jul 2, 2026 10:06am | Jul 2, 2026 10:06am |  |  | Fair | No | Issues already resolved
Non-Outage | J.E.26.06.36401 | C001837761 | Odaine Johnson | St.Catherine | Completed | Load_567904 | Rhodens Pen - 310 | Jul 2, 2026 8:42am | Jul 2, 2026 8:42am | Jul 2, 2026 9:57am | Jul 2, 2026 9:57am | Jul 2, 2026 10:32am | Jul 2, 2026 10:32am | Jul 2, 2026 10:33am | Jul 2, 2026 10:33am |  |  | Fair | No | Premises found okay customer said problem was resolved
Non-Outage | J.E.26.06.39150 | C001837758 | Donald Cunningham | St.Catherine | Completed | Load_250547 | Rhodens Pen - 210 | Jul 2, 2026 8:40am | Jul 2, 2026 8:40am | Jul 2, 2026 10:06am | Jul 2, 2026 10:06am | Jul 2, 2026 10:51am | Jul 2, 2026 10:52am | Jul 2, 2026 10:58am | Jul 2, 2026 10:58am |  |  | Fair | No | Premises closed
Outage | J.E.26.07.00770 | C001837757 | Andre Williams | Trelawny | Completed | Load_247249 | Duncans - 210 | Jul 2, 2026 8:33am | Jul 2, 2026 8:39am | Jul 2, 2026 8:48am | Jul 2, 2026 8:54am | Jul 2, 2026 9:54am | Jul 2, 2026 10:06am | Jul 2, 2026 10:06am | Jul 2, 2026 10:06am | BrokenWire |  | Fair | No | Remake burnt off neutral on customer 3 wire service voltage 114+116=230
Outage | J.E.26.07.00779 | C001837756 | Shamour Haughton | St.James | Completed | Load_250693 | Bogue - 310 | Jul 2, 2026 8:33am | Jul 2, 2026 8:54am | Jul 2, 2026 9:24am | Jul 2, 2026 9:24am | Jul 2, 2026 9:24am | Jul 2, 2026 9:24am | Jul 2, 2026 9:25am | Jul 2, 2026 9:25am |  |  | Fair | No | Related to previous call
Outage | J.E.26.07.00784 | C001837755 | Shamour Haughton | St.James | Completed | Load_301676 | Bogue - 310 | Jul 2, 2026 8:33am | Jul 2, 2026 8:54am | Jul 2, 2026 9:26am | Jul 2, 2026 9:26am | Jul 2, 2026 9:27am | Jul 2, 2026 9:27am | Jul 2, 2026 9:27am | Jul 2, 2026 9:27am |  |  | Fair | No | Related to previous call
Non-Outage | J.E.26.07.00783 | C001837754 | Roemello Brown | Trelawny | Completed | Load_259114 | Greenwood - 210 | Jul 2, 2026 8:32am | Jul 2, 2026 8:50am | Jul 2, 2026 9:32am | Jul 2, 2026 10:14am | Jul 2, 2026 10:37am | Jul 2, 2026 10:37am | Jul 2, 2026 10:49am | Jul 2, 2026 10:49am |  |  | Fair | No | Transformer drop lead burn off need emergency team to assist section of the community affected Voltage found 111/21.63/99Voltage leave 111/21.63/99
Non-Outage | J.E.26.07.00496 | C001837751 | Hartley Chin | Clarendon | Completed | Load_260282 | Parnassus - 310 | Jul 2, 2026 8:31am | Jul 2, 2026 8:31am | Jul 2, 2026 8:45am | Jul 2, 2026 9:54am | Jul 2, 2026 9:56am | Jul 2, 2026 10:16am | Jul 2, 2026 10:16am | Jul 2, 2026 10:16am | Fire |  | Fair | No | Premises not found . unable to contact customer, unable to find meter. Area patrolled according to report ,no fire on wire.
Non-Outage | J.E.26.07.00635 | C001837749 | Hartley Chin | Clarendon | Completed | Load_349984 | May Pen - 210 | Jul 2, 2026 8:30am | Jul 2, 2026 8:30am | Jul 2, 2026 8:45am | Jul 2, 2026 12:13pm | Jul 2, 2026 12:13pm | Jul 2, 2026 12:13pm | Jul 2, 2026 12:14pm | Jul 2, 2026 12:14pm | BrokenWire |  | Fair | No | Call related to job # 00800..
Non-Outage | J.E.26.07.00505 | C001837747 | Fredrick Hamilton | null | Completed | null | null | Jul 2, 2026 8:29am | Jul 2, 2026 8:30am | Jul 2, 2026 9:24am | Jul 2, 2026 9:24am | Jul 2, 2026 9:30am | Jul 2, 2026 9:33am | Jul 2, 2026 9:33am | Jul 2, 2026 9:33am | LowHangingWires |  | Fair | No | Emergency crew required low hanging secondary wire at location
Outage | J.E.26.07.00781 | C001837748 | Moses Elliston | St.Catherine | Completed | Load_265990 | Tredegar - 310 | Jul 2, 2026 8:29am | Jul 2, 2026 8:30am | Jul 2, 2026 4:02pm | Jul 2, 2026 4:02pm | Jul 2, 2026 4:02pm | Jul 2, 2026 4:03pm | Jul 2, 2026 4:04pm | Jul 2, 2026 4:04pm |  |  | Fair | No | Supply reconnected.Box went out.
Non-Outage | J.E.26.06.27955 | C001837744 | Moses Elliston | St.Catherine | Completed | Load_258032 | Tredegar - 410 | Jul 2, 2026 8:25am | Jul 2, 2026 8:26am | Jul 2, 2026 5:16pm | Jul 2, 2026 5:16pm | Jul 2, 2026 5:16pm | Jul 2, 2026 5:17pm | Jul 2, 2026 5:18pm | Jul 2, 2026 5:18pm |  |  | Fair | No | Not located.no answer from cell phone.
Non-Outage | J.E.26.07.00556 | C001837742 | Fredrick Hamilton | KSAS | Completed | Load_267072 | Duhaney - 310 | Jul 2, 2026 8:24am | Jul 2, 2026 8:25am | Jul 2, 2026 8:29am | Jul 2, 2026 8:31am | Jul 2, 2026 8:38am | Jul 2, 2026 9:14am | Jul 2, 2026 9:14am | Jul 2, 2026 9:14am |  |  | Fair | No | 218v/104.3v/114.5v obtained before repairsCorrosion detected at pothead same was corrected 230v/115v/115.3v obtained after repairs Corrosion detected2 penunion used
Non-Outage | J.E.26.06.39152 | C001837741 | Wan Carlos Scarlett | St.Catherine | Completed | Load_243635 | Twickenham - 310 | Jul 2, 2026 8:22am | Jul 2, 2026 8:23am | Jul 2, 2026 9:34am | Jul 2, 2026 9:34am | Jul 2, 2026 10:04am | Jul 2, 2026 10:40am | Jul 2, 2026 10:42am | Jul 2, 2026 10:42am |  |  | Fair | No | Found customer 3 wire service at pole with one of the phase corroded use one bolt clamp at open secondary line phase readings 115-114-220
Non-Outage | J.E.26.06.37835 | C001837739 | Royston Montague | St.Catherine | Completed | Load_242540 | New Michelton - 210 | Jul 2, 2026 8:20am | Jul 2, 2026 8:21am | Jul 2, 2026 8:24am | Jul 2, 2026 8:47am | Jul 2, 2026 10:21am | Jul 2, 2026 10:40am | Jul 2, 2026 10:40am | Jul 2, 2026 10:40am |  |  | Fair | No | Low voltage coming from EN box , customer voltage at pothead 34v 114v please assign to the relevant team thanks.
Non-Outage | J.E.26.06.22374 | C001837737 | Royston Montague | St.Catherine | Completed | Load_255126 | New Michelton - 310 | Jul 2, 2026 8:19am | Jul 2, 2026 8:19am | Jul 2, 2026 8:21am | Jul 2, 2026 2:55pm | Jul 2, 2026 3:57pm | Jul 2, 2026 3:58pm | Jul 2, 2026 3:58pm | Jul 2, 2026 3:58pm |  |  | Fair | No | Multiple calls to customer phone go without. GPS coordinate on job not working.
Non-Outage | J.E.26.06.35789 | C001837738 | Royston Montague | St.Catherine | Completed | Load_269697 | New Michelton - 210 | Jul 2, 2026 8:19am | Jul 2, 2026 8:19am | Jul 2, 2026 8:24am | Jul 2, 2026 10:41am | Jul 2, 2026 11:01am | Jul 2, 2026 11:30am | Jul 2, 2026 11:30am | Jul 2, 2026 11:30am |  |  | Fair | No | Faulty neutral joint on 2/0 triplex. Same corrected, voltage found 124v 103v 227v voltage after 112v 113v 227v
Non-Outage | J.E.26.06.36738 | C001837736 | Royston Montague | St.Catherine | Completed | Load_250783 | New Michelton - 210 | Jul 2, 2026 8:17am | Jul 2, 2026 8:17am | Jul 2, 2026 8:21am | Jul 2, 2026 1:45pm | Jul 2, 2026 2:04pm | Jul 2, 2026 2:14pm | Jul 2, 2026 2:14pm | Jul 2, 2026 2:14pm |  |  | Fair | No | Corrosion at pothead, same corrected. Voltage 230v 114v 114v unable to check inside meter socket, same cemented in meter pole.
Non-Outage | J.E.26.07.00335 | C001837734 | Royston Montague | St.Catherine | Completed | Load_245848 | New Michelton - 210 | Jul 2, 2026 8:16am | Jul 2, 2026 8:16am | Jul 2, 2026 8:21am | Jul 2, 2026 2:15pm | Jul 2, 2026 2:31pm | Jul 2, 2026 2:55pm | Jul 2, 2026 2:55pm | Jul 2, 2026 2:55pm |  |  | Fair | No | Defective load wire leading to premises. Customer asked to get an electrician. Voltage at meter socket 112v 112v 225v
Non-Outage | J.E.26.06.38432 | C001837732 | Royston Montague | St.Catherine | Completed | Load_267145 | New Michelton - 310 | Jul 2, 2026 8:15am | Jul 2, 2026 8:15am | Jul 2, 2026 8:18am | Jul 2, 2026 11:31am | Jul 2, 2026 12:34pm | Jul 2, 2026 12:34pm | Jul 2, 2026 12:34pm | Jul 2, 2026 12:34pm |  |  | Rains | No | Customer confirmed issue resolved. Please update thanks.
Non-Outage | J.E.26.06.38541 | C001837733 | Royston Montague | St.Catherine | Completed | Load_245363 | New Michelton - 310 | Jul 2, 2026 8:15am | Jul 2, 2026 8:16am | Jul 2, 2026 8:18am | Jul 2, 2026 12:43pm | Jul 2, 2026 1:01pm | Jul 2, 2026 1:02pm | Jul 2, 2026 1:02pm | Jul 2, 2026 1:02pm |  |  | Fair | No | Not locating this premises, multiple calls to customer phone go without answer. Residents not familiar with name. GPS coordinate on job not correct.
Non-Outage | J.E.26.07.00014 | C001837731 | Royston Montague | St.Catherine | Completed | Load_261450 | New Michelton - 210 | Jul 2, 2026 8:13am | Jul 2, 2026 8:14am | Jul 2, 2026 8:18am | Jul 2, 2026 1:32pm | Jul 2, 2026 1:32pm | Jul 2, 2026 1:44pm | Jul 2, 2026 1:45pm | Jul 2, 2026 1:45pm |  |  | Fair | No | Faulty breaker in panel, customer asked to get an electrician to repair same. Voltage at meter socket 232v 116v 115v
Non-Outage | J.E.26.06.39083 | C001837729 | Ricky Hall | St.Catherine | Completed | Load_250866 | New Michelton - 210 | Jul 2, 2026 8:11am | Jul 2, 2026 8:12am | Jul 2, 2026 8:50am | Jul 2, 2026 8:50am | Jul 2, 2026 9:30am | Jul 2, 2026 9:31am | Jul 2, 2026 9:31am | Jul 2, 2026 9:31am |  |  | Fair | No | Issue resolved on previous shift
Non-Outage | J.E.26.06.38264 | C001837727 | Daniel Francis | St.Ann | Completed | Load_265652 | Roaring River - 410 | Jul 2, 2026 8:09am | Jul 2, 2026 8:09am | Jul 2, 2026 9:38am | Jul 2, 2026 9:38am | Jul 2, 2026 9:38am | Jul 2, 2026 10:32am | Jul 2, 2026 10:52am | Jul 2, 2026 10:52am | LowHangingWires |  | Fair | No | Dis connect and reposition service wire by erecting 1Diron to accommodate service wire
Non-Outage | J.E.26.07.00583 | C001837725 | Oraine Minto | St.Ann | Completed | Load_250885 | Ocho Rios - 410 | Jul 2, 2026 8:08am | Jul 2, 2026 8:08am | Jul 2, 2026 1:55pm | Jul 2, 2026 1:55pm | Jul 2, 2026 1:55pm | Jul 2, 2026 1:55pm | Jul 2, 2026 1:59pm | Jul 2, 2026 1:59pm |  |  | Fair | No | Refer to emergency The primary lines to the water pump have a static sound coming from them crossing of Main Street Pole# none 3 primary go down to the pump
Non-Outage | J.E.26.07.00560 | C001837722 | Oraine Minto | St.Ann | Completed | Load_256369 | Roaring River - 210 | Jul 2, 2026 8:07am | Jul 2, 2026 8:08am | Jul 2, 2026 12:27pm | Jul 2, 2026 12:27pm | Jul 2, 2026 12:27pm | Jul 2, 2026 12:28pm | Jul 2, 2026 12:30pm | Jul 2, 2026 12:30pm |  |  | Fair | No | Refer to maintenance Customer states that the power keeps going off for 30 seconds to a minute from about Sunday in the nights
Non-Outage | J.E.26.07.00567 | C001837723 | Oraine Minto | St.Ann | Completed | Load_249631 | Roaring River - 210 | Jul 2, 2026 8:07am | Jul 2, 2026 8:08am | Jul 2, 2026 2:00pm | Jul 2, 2026 2:00pm | Jul 2, 2026 2:00pm | Jul 2, 2026 2:01pm | Jul 2, 2026 2:02pm | Jul 2, 2026 2:02pm |  |  | Fair | No | Refer to maintenance Issues has been having for 2 weeks now says customer go off for 30 seconds to a minute an back again
Non-Outage | J.E.26.07.00688 | C001837721 | Oraine Minto | St.Ann | Completed | Load_239077 | Ocho Rios - 310 | Jul 2, 2026 8:07am | Jul 2, 2026 8:08am | Jul 2, 2026 11:38am | Jul 2, 2026 11:38am | Jul 2, 2026 11:48am | Jul 2, 2026 11:49am | Jul 2, 2026 11:52am | Jul 2, 2026 11:52am |  |  | Fair | No | Refer to maintenance secondary lines need tension and pole to be straightened
Non-Outage | J.E.26.07.00758 | C001837724 | Oraine Minto | St.Ann | Completed | Load_413060 | Roaring River - 410 | Jul 2, 2026 8:07am | Jul 2, 2026 8:09am | Jul 2, 2026 2:08pm | Jul 2, 2026 3:35pm | Jul 2, 2026 3:35pm | Jul 2, 2026 3:35pm | Jul 2, 2026 3:36pm | Jul 2, 2026 3:36pm |  |  | Fair | No | Issue fixed
Non-Outage | J.E.26.07.00462 | C001837719 | Odaine Johnson | Clarendon | Completed | Load_257473 | Parnassus - 310 | Jul 2, 2026 8:06am | Jul 2, 2026 8:07am | Jul 2, 2026 8:14am | Jul 2, 2026 10:33am | Jul 2, 2026 10:33am | Jul 2, 2026 10:33am | Jul 2, 2026 10:33am | Jul 2, 2026 10:33am |  |  | Fair | No | Corroded neutral found at pothead remade connection using one pen union voltage reading 110 volts
Outage | J.E.26.07.00209 | C001837715 | Rusean Allen | KSAS | Completed | Load_239260 | Hunts Bay - 210 | Jul 2, 2026 7:55am | Jul 2, 2026 7:56am | Jul 2, 2026 9:13am | Jul 2, 2026 9:13am | Jul 2, 2026 9:51am | Jul 2, 2026 9:54am | Jul 2, 2026 9:55am | Jul 2, 2026 9:55am |  |  | Fair | No | Burnt CT metering wires needs to be changed, refer to field service department. Power is still at premises.
Outage | J.E.26.07.00378 | C001837714 | Rusean Allen | KSAS | Completed | Load_267297 | Hunts Bay - 310 | Jul 2, 2026 7:55am | Jul 2, 2026 7:56am | Jul 2, 2026 9:55am | Jul 2, 2026 9:55am | Jul 2, 2026 10:13am | Jul 2, 2026 11:12am | Jul 2, 2026 11:14am | Jul 2, 2026 11:14am |  |  | Fair | No | Transformer found chipped, transformer reset was done.Voltage: 117 117 205 236 237 238
Outage | J.E.26.07.00768 | C001837713 | Shamour Haughton | St.James | Completed | Load_237918 | Bogue - 310 | Jul 2, 2026 7:54am | Jul 2, 2026 8:15am | Jul 2, 2026 9:57am | Jul 2, 2026 9:57am | Jul 2, 2026 11:16am | Jul 2, 2026 11:23am | Jul 2, 2026 11:26am | Jul 2, 2026 11:26am |  |  | Fair | No | Customer experiencing internal issue, voltage left 111,113,224
Non-Outage | J.E.26.07.00511 | C001837709 | Locksley Allen | St.Mary | Completed | Load_352775 | Blackstonedge - 110 | Jul 2, 2026 7:50am | Jul 2, 2026 7:52am | Jul 2, 2026 3:22pm | Jul 2, 2026 3:22pm | Jul 2, 2026 3:22pm | Jul 2, 2026 3:54pm | Jul 2, 2026 3:54pm | Jul 2, 2026 3:54pm |  |  | Fair | No | Low voltage problem found at premises. Tree drop on the line and needs to be removed as soon as possible. The line needs to be bush.Check transformer. Clean up connectors at pole. Voltage at meter socket phase to phase 44vPhase to neutral 122&47
Non-Outage | J.E.26.07.00537 | C001837710 | Neckell Ormsby | St.Mary | Completed | Load_250014 | Annotto Bay - 310 | Jul 2, 2026 7:50am | Jul 2, 2026 10:20am | Jul 2, 2026 11:53am | Jul 2, 2026 11:55am | Jul 2, 2026 11:55am | Jul 2, 2026 12:07pm | Jul 2, 2026 12:07pm | Jul 2, 2026 12:07pm |  |  | Fair | No | Unable to locate customer after several calls
Non-Outage | J.E.26.07.00760 | C001837708 | Locksley Allen | St.Mary | Completed | Load_258090 | Highgate -110 | Jul 2, 2026 7:50am | Jul 2, 2026 7:52am | Jul 2, 2026 9:11am | Jul 2, 2026 9:55am | Jul 2, 2026 9:55am | Jul 2, 2026 10:02am | Jul 2, 2026 10:02am | Jul 2, 2026 10:02am |  |  | Fair | No | Meter #2334347 not found. Meter 2414725 seen. The switch is open on one of the transformer. Please refer to emergency
Outage | J.E.26.07.00151 | C001837711 | Andre Williams | St.James | Completed | Load_244424 | Bogue - 310 | Jul 2, 2026 7:50am | Jul 3, 2026 7:41am | Jul 3, 2026 7:47am | Jul 3, 2026 8:05am | Jul 3, 2026 8:06am | Jul 3, 2026 8:14am | Jul 3, 2026 8:14am | Jul 3, 2026 8:14am |  |  | Fair | No | Call located in Montego Bay cell tower out , cell tower in Windsor trelawny with supply confirm by technician
Non-Outage | J.E.26.07.00732 | C001837706 | Andrew Powell | null | Completed | null | null | Jul 2, 2026 7:48am | Jul 2, 2026 7:48am | Jul 2, 2026 10:55am | Jul 2, 2026 10:55am | Jul 2, 2026 11:45am | Jul 2, 2026 11:45am | Jul 2, 2026 11:48am | Jul 2, 2026 11:48am |  |  | Fair | No | Found supply okay at location, voltage reading 115v-115v phase to neutral 230v cross phase at meter pothead 3 wire.
Non-Outage | J.E.26.07.00735 | C001837707 | Romaine Roberts | null | Completed | null | null | Jul 2, 2026 7:48am | Jul 2, 2026 8:38am | Jul 2, 2026 9:27am | Jul 2, 2026 9:32am | Jul 2, 2026 12:55pm | Jul 2, 2026 12:57pm | Jul 2, 2026 12:58pm | Jul 2, 2026 12:58pm |  | Y | Fair | No | Junction fuse found blown patrol line and clear several bamboo from line and replace 2 amp and 8 amp power restore
Non-Outage | J.E.26.07.00612 | C001837702 | Dean Smith | Hanover | Completed | Load_264233 | Orange Bay - 310 | Jul 2, 2026 7:47am | Jul 2, 2026 7:47am | Jul 2, 2026 3:33pm | Jul 2, 2026 3:33pm | Jul 2, 2026 3:33pm | Jul 2, 2026 3:33pm | Jul 2, 2026 3:34pm | Jul 2, 2026 3:34pm |  |  | Fair | No | Shift ended
Outage | J.E.26.07.00701 | C001837705 | Richman Whyte | St.Elizabeth | Completed | Load_557806 | Maggotty - 110 | Jul 2, 2026 7:47am | Jul 2, 2026 8:32am | Jul 2, 2026 11:42am | Jul 2, 2026 11:42am | Jul 2, 2026 11:42am | Jul 2, 2026 11:42am | Jul 2, 2026 11:42am | Jul 2, 2026 11:42am |  |  | Fair | No | Unable to locate or contact customer on the phone after several attempts
Non-Outage | J.E.26.07.00175 | C001837701 | Dean Smith | Hanover | Completed | Load_246952 | Orange Bay - 310 | Jul 2, 2026 7:46am | Jul 2, 2026 7:47am | Jul 2, 2026 3:31pm | Jul 2, 2026 3:31pm | Jul 2, 2026 3:31pm | Jul 2, 2026 3:31pm | Jul 2, 2026 3:33pm | Jul 2, 2026 3:33pm |  |  | Fair | No | Shift ended
Non-Outage | J.E.26.06.39190 | C001837699 | Wan Carlos Scarlett | St.Catherine | Completed | Load_252634 | Twickenham - 310 | Jul 2, 2026 7:45am | Jul 2, 2026 7:45am | Jul 2, 2026 7:54am | Jul 2, 2026 7:54am | Jul 2, 2026 8:43am | Jul 2, 2026 9:33am | Jul 2, 2026 9:34am | Jul 2, 2026 9:34am |  |  | Fair | No | Found customer 3 wire service at pole with phase and neutral corroded use 3 one bolt clamps at open secondary line phase and neutral readings 116-117-234
Outage | J.E.26.07.00739 | C001837700 | Richard Samuda | Manchester | Completed | Load_253176 | Spur Tree - 310 | Jul 2, 2026 7:45am | Jul 2, 2026 7:47am | Jul 2, 2026 7:56am | Jul 2, 2026 7:56am | Jul 2, 2026 8:55am | Jul 2, 2026 9:43am | Jul 2, 2026 9:47am | Jul 2, 2026 9:47am |  |  | Fair | No | Reconnect customer service wire to pothead that was broken causing customer to experience single phase voltage 116/before after 116116/232 customer back to normal
Outage | J.E.26.07.00672 | C001837698 | Wayne Dillion | Manchester | Completed | Load_262167 | Spur Tree - 210 | Jul 2, 2026 7:44am | Jul 2, 2026 7:45am | Jul 2, 2026 9:04am | Jul 2, 2026 9:04am | Jul 2, 2026 9:04am | Jul 2, 2026 9:32am | Jul 2, 2026 9:40am | Jul 2, 2026 9:40am |  |  | Fair | No | Supply check and found transformer drop lead burnt off. Isolate and close transformer 25kva transformer circuit no pole # to replace same using 5ft of 2/o copper conductor and 1 ampact. Supply leave working okay reading 111v, 112v and cross phase 223volts.
Outage | J.E.26.07.00660 | C001837697 | Andrew Powell | Manchester | Completed | Load_251844 | Spur Tree - 210 | Jul 2, 2026 7:43am | Jul 2, 2026 7:44am | Jul 2, 2026 8:12am | Jul 2, 2026 8:12am | Jul 2, 2026 8:12am | Jul 2, 2026 8:13am | Jul 2, 2026 8:13am | Jul 2, 2026 8:13am |  |  | Fair | No | Premises found okay customer stated that supply restored.
Outage | J.E.26.07.00762 | C001837696 | Rusean Allen | KSAS | Completed | Load_264835 | Cane River - 610 | Jul 2, 2026 7:43am | Jul 2, 2026 7:43am | Jul 2, 2026 8:06am | Jul 2, 2026 8:07am | Jul 2, 2026 8:42am | Jul 2, 2026 9:11am | Jul 2, 2026 9:11am | Jul 2, 2026 9:11am |  |  | Fair | No | 1x 10amp fuse found 1x 10amp fuse replaced.1x 3amp fuse found 1x 3amp fuse replaced.
Outage | J.E.26.07.00626 | C001837691 | Andrew Powell | St.Elizabeth | Completed | Load_292173 | Maggotty - 210 | Jul 2, 2026 7:41am | Jul 2, 2026 9:06am | Jul 2, 2026 10:38am | Jul 2, 2026 10:38am | Jul 2, 2026 10:38am | Jul 2, 2026 10:38am | Jul 2, 2026 10:39am | Jul 2, 2026 10:39am |  |  | Rains | No | Called related to burnt 15 kva transformer area leaves without supply.
Outage | J.E.26.07.00636 | C001837690 | Wayne Dillion | Manchester | Completed | Load_302927 | Spur Tree - 210 | Jul 2, 2026 7:41am | Jul 2, 2026 9:05am | Jul 2, 2026 9:49am | Jul 2, 2026 9:49am | Jul 2, 2026 9:49am | Jul 2, 2026 10:00am | Jul 2, 2026 10:00am | Jul 2, 2026 10:00am |  |  | Fair | No | Patrol and found clear. Replace one blown 8amp junction fuse no pole #. Restored supply okay.
Outage | J.E.26.07.00684 | C001837689 | Andrew Powell | St.Elizabeth | Completed | Load_292173 | Maggotty - 210 | Jul 2, 2026 7:41am | Jul 2, 2026 9:06am | Jul 2, 2026 10:39am | Jul 2, 2026 10:39am | Jul 2, 2026 10:40am | Jul 2, 2026 10:40am | Jul 2, 2026 10:41am | Jul 2, 2026 10:41am |  |  | Rains | No | Called related to burnt 15 kva transformer area leaves without supply.
Outage | J.E.26.07.00719 | C001837688 | Andrew Powell | St.Elizabeth | Completed | Load_292173 | Maggotty - 210 | Jul 2, 2026 7:41am | Jul 2, 2026 9:06am | Jul 2, 2026 9:10am | Jul 2, 2026 9:10am | Jul 2, 2026 10:01am | Jul 2, 2026 10:35am | Jul 2, 2026 10:37am | Jul 2, 2026 10:37am |  |  | Rains | No | Found burnt 15 kva transformer can’t tied in approximately 16 customers affected, please refer to Mr Delroy crew for replacement.
Non-Outage | J.E.26.06.38774 | C001837687 | Rodclif Dawkins | Portmore | Completed | Load_249145 | Naggo Head - 610 | Jul 2, 2026 7:39am | Jul 2, 2026 7:39am | Jul 2, 2026 11:31am | Jul 2, 2026 12:40pm | Jul 2, 2026 12:40pm | Jul 2, 2026 9:16am | Jul 2, 2026 12:41pm | Jul 2, 2026 12:41pm |  |  | Fair | No | Premises was checked and found okay.
Non-Outage | J.E.26.06.38803 | C001837685 | Rodclif Dawkins | Portmore | Completed | Load_249145 | Naggo Head - 610 | Jul 2, 2026 7:38am | Jul 2, 2026 7:38am | Jul 2, 2026 11:30am | Jul 2, 2026 12:38pm | Jul 2, 2026 12:38pm | Jul 2, 2026 8:21am | Jul 2, 2026 12:40pm | Jul 2, 2026 12:40pm |  |  | Fair | No | Premises was checked and found okay.
Outage | J.E.26.07.00736 | C001837686 | Dwayne Samuels | Trelawny | Completed | Load_259114 | Greenwood - 210 | Jul 2, 2026 7:38am | Jul 2, 2026 7:43am | Jul 2, 2026 9:04am | Jul 2, 2026 9:05am | Jul 2, 2026 12:10pm | Jul 2, 2026 12:17pm | Jul 2, 2026 12:17pm | Jul 2, 2026 12:17pm |  |  | Fair | No | One phase of service wire was burnt off from the pole use 1 one bolt clamp at same for repairs voltage left a meter 114v/116v/230v
Outage | J.E.26.07.00715 | C001837680 | Milton Charlton | KSAN | Completed | Load_244121 | Hope - 410 | Jul 2, 2026 7:37am | Jul 2, 2026 7:38am | Jul 2, 2026 9:24am | Jul 2, 2026 9:24am | Jul 2, 2026 9:53am | Jul 2, 2026 9:35am | Jul 2, 2026 9:57am | Jul 2, 2026 9:57am |  |  | Fair | No | Found okay upon arrival. Customer states they didn’t make any report.
Non-Outage | J.E.26.06.32967 | C001837678 | Moses Elliston | St.Catherine | Completed | Load_291772 | Rhodens Pen - 210 | Jul 2, 2026 7:32am | Jul 2, 2026 7:33am | Jul 3, 2026 11:31am | Jul 3, 2026 11:31am | Jul 3, 2026 11:31am | Jul 3, 2026 11:31am | Jul 3, 2026 11:33am | Jul 3, 2026 11:33am |  |  | Fair | No | Meter relay reset.117-117-234 volts
Outage | J.E.26.07.00615 | C001837676 | Elvis Trowers | KSAN | Completed | Load_574857 | Washington Blvd - 610 | Jul 2, 2026 7:29am | Jul 2, 2026 7:32am | Jul 2, 2026 9:01am | Jul 2, 2026 9:02am | Jul 2, 2026 9:31am | Jul 2, 2026 9:49am | Jul 2, 2026 9:49am | Jul 2, 2026 9:49am |  |  | Fair | Yes | Field service needs to visit this location i was told by escalation service department, they will create a LOC on the meter and then send it to field service.
Outage | J.E.26.07.00673 | C001837675 | Elvis Trowers | KSAN | Completed | Load_250641 | Washington Blvd - 610 | Jul 2, 2026 7:29am | Jul 2, 2026 7:32am | Jul 2, 2026 10:11am | Jul 2, 2026 10:11am | Jul 2, 2026 10:36am | Jul 2, 2026 10:45am | Jul 2, 2026 10:45am | Jul 2, 2026 10:45am |  |  | Fair | Yes | Premises checked and found ok upon arrival, customer was also spoken with however he suggested that it was the breaker that was tripped last night, and he got an electrician to replace it.
Outage | J.E.26.07.00709 | C001837677 | Elvis Trowers | KSAN | Completed | Load_574178 | West Kings House - 410 | Jul 2, 2026 7:29am | Jul 2, 2026 7:32am | Jul 2, 2026 9:50am | Jul 2, 2026 9:50am | Jul 2, 2026 10:04am | Jul 2, 2026 10:10am | Jul 2, 2026 10:10am | Jul 2, 2026 10:10am |  |  | Fair | Yes | Premises checked and found ok upon arrival, customer was also spoken with, however he said the power supply was restored.
Non-Outage | J.E.26.06.37687 | C001837665 | Dwayne Samuels | null | Completed | null | null | Jul 2, 2026 7:28am | Jul 2, 2026 7:49am | Jul 2, 2026 11:04am | Jul 2, 2026 12:18pm | Jul 2, 2026 1:32pm | Jul 2, 2026 2:02pm | Jul 2, 2026 2:06pm | Jul 2, 2026 2:06pm |  |  | Fair | No | Patrol to find 1 blown 15kva EG transformer fuse blown replace one 1amp at same defective 15kva transformer at same refer to Obrian Ellis hex05491-HK22655538
Outage | J.E.26.07.00692 | C001837668 | Daniel Francis | St.Ann | Completed | Load_239077 | Ocho Rios - 310 | Jul 2, 2026 7:28am | Jul 2, 2026 7:31am | Jul 2, 2026 11:48am | Jul 2, 2026 11:48am | Jul 2, 2026 1:50pm | Jul 2, 2026 1:51pm | Jul 2, 2026 1:53pm | Jul 2, 2026 1:53pm |  |  | Fair | No | Customer. need to out repair to Stanton
Outage | J.E.26.07.00710 | C001837674 | Horace Malcolm | St.James | Completed | Load_258826 | Bogue - 610 | Jul 2, 2026 7:28am | Jul 2, 2026 7:30am | Jul 2, 2026 7:49am | Jul 2, 2026 7:49am | Jul 2, 2026 8:46am | Jul 2, 2026 9:31am | Jul 2, 2026 9:32am | Jul 2, 2026 9:32am |  |  | Fair | No | Check and found area and premises ok supply was restored
Outage | J.E.26.07.00726 | C001837673 | Horace Malcolm | St.James | Completed | Load_292836 | Bogue - 510 | Jul 2, 2026 7:28am | Jul 2, 2026 7:30am | Jul 2, 2026 9:43am | Jul 2, 2026 9:43am | Jul 2, 2026 10:50am | Jul 2, 2026 11:16am | Jul 2, 2026 11:16am | Jul 2, 2026 11:16am |  |  | Fair | No | Check and found customer have internal problem voltage 114-114-228
Outage | J.E.26.07.00727 | C001837672 | Horace Malcolm | St.James | Completed | Load_249191 | Bogue - 610 | Jul 2, 2026 7:28am | Jul 2, 2026 7:30am | Jul 2, 2026 9:32am | Jul 2, 2026 9:33am | Jul 2, 2026 9:33am | Jul 2, 2026 9:42am | Jul 2, 2026 9:43am | Jul 2, 2026 9:43am |  |  | Fair | No | Check and found premises ok
Outage | J.E.26.07.00730 | C001837667 | Roxroy Needham | St.Ann | Completed | Load_305056 | Cardiff Hall - 210 | Jul 2, 2026 7:28am | Jul 2, 2026 7:29am | Jul 2, 2026 8:39am | Jul 2, 2026 8:39am | Jul 2, 2026 8:39am | Jul 2, 2026 8:40am | Jul 2, 2026 8:40am | Jul 2, 2026 8:40am |  |  | Fair | No | Replace 1- 15 amp junction fuse after line was patrolled
Outage | J.E.26.07.00738 | C001837669 | Shamour Haughton | St.James | Completed | Load_254649 | Bogue - 310 | Jul 2, 2026 7:28am | Jul 2, 2026 7:30am | Jul 2, 2026 7:49am | Jul 2, 2026 7:49am | Jul 2, 2026 8:40am | Jul 2, 2026 9:17am | Jul 2, 2026 9:21am | Jul 2, 2026 9:21am |  |  | Fair | No | Found 1,50amp junction fuse blown, refuse 50amp junction, no pole number is at pole, closest meter number is2633909
Outage | J.E.26.07.00749 | C001837666 | Shamour Haughton | St.James | Completed | Load_266817 | Bogue - 310 | Jul 2, 2026 7:28am | Jul 2, 2026 7:30am | Jul 2, 2026 9:27am | Jul 2, 2026 9:27am | Jul 2, 2026 9:27am | Jul 2, 2026 9:27am | Jul 2, 2026 9:28am | Jul 2, 2026 9:28am |  |  | Fair | No | Related to previous call
Outage | J.E.26.07.00722 | C001837664 | Hartley Chin | Clarendon | Completed | Load_349984 | May Pen - 210 | Jul 2, 2026 7:26am | Jul 2, 2026 7:27am | Jul 2, 2026 8:45am | Jul 2, 2026 12:10pm | Jul 2, 2026 12:10pm | Jul 2, 2026 12:12pm | Jul 2, 2026 12:13pm | Jul 2, 2026 12:13pm | BrokenWire |  | Fair | No | Call related to job # 00800 ..
Outage | J.E.26.07.00748 | C001837663 | Hartley Chin | Clarendon | Completed | Load_258346 | Parnassus - 210 | Jul 2, 2026 7:26am | Jul 2, 2026 7:27am | Jul 2, 2026 12:14pm | Jul 2, 2026 12:16pm | Jul 2, 2026 12:44pm | Jul 2, 2026 2:21pm | Jul 2, 2026 2:42pm | Jul 2, 2026 2:42pm | BrokenPole | Y | Fair | No | Unable to contact customer… area patrolled and found broken open secondary neutral cause by tree growing in circuit … isolate 50 KVA transformer @ pole # 0138547 .. repair secondary neutral … heavy bushing … cut tree from line … re-energized transformer… use 50 ft #2 Conductor.. 2 clamp ..
Non-Outage | J.E.26.06.30290 | C001837662 | Swon Miller | null | Completed | null | null | Jul 2, 2026 7:25am | Jul 2, 2026 7:33am | Jul 2, 2026 11:21am | Jul 2, 2026 11:21am | Jul 2, 2026 11:51am | Jul 20, 2026 12:07am | Jul 2, 2026 12:08pm | Jul 2, 2026 12:08pm | LeaningPole |  | Fair | No | Check and found okay customer states that the pole was rectified
Non-Outage | J.E.26.06.31494 | C001837661 | Dwayne Samuels | null | Completed | null | null | Jul 2, 2026 7:24am | Jul 2, 2026 12:46pm | Jul 3, 2026 8:34am | Jul 3, 2026 9:23am | Jul 3, 2026 9:28am | Jul 3, 2026 9:35am | Jul 3, 2026 9:35am | Jul 3, 2026 9:35am |  |  | Fair | No | Related to 15 kva transformer that is defective
Non-Outage | J.E.26.06.33585 | C001837659 | Rodclif Dawkins | Portmore | Completed | Load_252357 | Naggo Head - 510 | Jul 2, 2026 7:20am | Jul 2, 2026 7:21am | Jul 2, 2026 9:21am | Jul 2, 2026 9:21am | Jul 2, 2026 10:45am | Jul 2, 2026 10:47am | Jul 2, 2026 10:47am | Jul 2, 2026 10:47am |  |  | Fair | No | Customer was found with supply. Customer advice crew that situation was corrected earlier..
Outage | J.E.26.07.00741 | C001837658 | Collin Robinson | Portland | Completed | Load_263840 | Port Antonio - 310 | Jul 2, 2026 7:20am | Jul 2, 2026 7:46am | Jul 2, 2026 8:16am | Jul 2, 2026 8:18am | Jul 2, 2026 9:35am | Jul 2, 2026 10:06am | Jul 2, 2026 10:07am | Jul 2, 2026 10:07am |  |  | Fair | No | Clear vine from pole and replace 10 amps junction fuse at 0014570
Outage | J.E.26.07.00674 | C001837656 | Neckell Ormsby | St.Mary | Completed | Load_247430 | Highgate - 210 | Jul 2, 2026 7:10am | Jul 2, 2026 7:49am | Jul 2, 2026 2:25pm | Jul 2, 2026 2:25pm | Jul 2, 2026 2:57pm | Jul 2, 2026 3:11pm | Jul 2, 2026 3:17pm | Jul 2, 2026 3:17pm | Fire |  | SevereWind | No | Unable to locate customer after several calls
Outage | J.E.26.07.00725 | C001837655 | Neckell Ormsby | St.Mary | Completed | Load_260174 | Highgate - 210 | Jul 2, 2026 7:10am | Jul 2, 2026 7:49am | Jul 2, 2026 1:24pm | Jul 2, 2026 1:24pm | Jul 2, 2026 1:50pm | Jul 2, 2026 2:15pm | Jul 2, 2026 2:25pm | Jul 2, 2026 2:25pm | Fire |  | SevereWind | No | Found broken secondary open 25 kva transformer to isolate however bucket truck required to cut and clear several vines from pole and carry out repairs approximately 200ft #2 AA required
Non-Outage | J.E.26.07.00656 | C001837654 | Richard Samuda | null | Completed | null | null | Jul 2, 2026 7:00am | Jul 2, 2026 7:03am | Jul 2, 2026 7:07am | Jul 2, 2026 7:07am | Jul 2, 2026 7:08am | Jul 2, 2026 7:08am | Jul 2, 2026 7:32am | Jul 2, 2026 7:32am |  |  | SevereWind | No | Found 30 amps junction blown patrol line found 15amp junction blown patrol area found nothing replaced 30 amps fuse than close 15 amps junction customer back to normal
Outage | J.E.26.07.00699 | C001837540 | Rusean Allen | KSAS | Completed | Load_251141 | Cane River - 410 | Jul 2, 2026 1:55am | Jul 2, 2026 1:55am | Jul 2, 2026 2:57am | Jul 2, 2026 2:57am | Jul 2, 2026 2:57am | Jul 2, 2026 3:13am | Jul 2, 2026 3:13am | Jul 2, 2026 3:13am |  |  | Fair | No | 1x 30amp fuse found 1x 30amp fuse replaced.
Outage | J.E.26.07.00698 | C001837538 | Michael Christian | St.James | Completed | Load_269636 | Queens Drive - 310 | Jul 2, 2026 1:27am | Jul 2, 2026 5:24am | Jul 2, 2026 5:41am | null | Jul 2, 2026 5:41am | Jul 2, 2026 5:44am | Jul 2, 2026 5:44am | Jul 2, 2026 5:44am |  |  | Fair | No | Found 1 10 amp 1 20 amp out by bird replace no pole #
Outage | J.E.26.07.00671 | C001837535 | Michael Christian | St.James | Completed | Load_249504 | Bogue - 310 | Jul 1, 2026 11:32pm | Jul 1, 2026 11:32pm | Jul 2, 2026 3:11am | Jul 2, 2026 3:11am | Jul 2, 2026 5:11am | Jul 2, 2026 5:13am | Jul 2, 2026 5:13am | Jul 2, 2026 5:13am | BrokenPole |  | Fair | No | T O J pole no j p s pole
Outage | J.E.26.07.00675 | C001837536 | Michael Christian | St.James | Completed | Load_247962 | Bogue - 610 | Jul 1, 2026 11:32pm | Jul 1, 2026 11:32pm | Jul 2, 2026 1:33am | Jul 2, 2026 1:33am | Jul 2, 2026 2:57am | Jul 2, 2026 3:11am | Jul 2, 2026 3:11am | Jul 2, 2026 3:11am |  |  | Fair | No | Found 1 15 kava out cause by bird replace 1 1 amp in 15 transformer
Outage | J.E.26.07.00658 | C001837534 | Delano Gayle | Portmore | Completed | Load_1004117 | Naggo Head - 510 | Jul 1, 2026 11:07pm | Jul 1, 2026 11:07pm | Jul 1, 2026 11:21pm | Jul 1, 2026 11:21pm | Jul 2, 2026 12:19am | Jul 2, 2026 1:30am | Jul 2, 2026 1:31am | Jul 2, 2026 1:31am |  |  | Fair | No | 2 blown junction on main no pole number, fuse holder also burnt, 2 blown junction T off in scheme no pole number. Patrolled line section and found okay for closure replace 2 fuse holder along with 2 30amps fuse, replace 2 25amps fuses
Outage | J.E.26.07.00666 | C001837529 | Rayon Foster | Hanover | Completed | Load_230038 | Orange Bay - 310 | Jul 1, 2026 10:22pm | Jul 1, 2026 10:31pm | Jul 1, 2026 10:45pm | Jul 1, 2026 10:45pm | Jul 1, 2026 11:01pm | Jul 1, 2026 11:12pm | Jul 1, 2026 11:13pm | Jul 1, 2026 11:13pm |  |  | Fair | No | Patrol primary line to find 1 tripped 25kva transformer complete patrol before resetting 1 25kva transformer
Outage | J.E.26.07.00572 | C001837517 | Andre Williams | Trelawny | Completed | Load_240708 | Duncans - 210 | Jul 1, 2026 9:46pm | Jul 2, 2026 8:45am | Jul 2, 2026 10:45am | Jul 2, 2026 10:45am | Jul 2, 2026 10:46am | Jul 2, 2026 10:46am | Jul 2, 2026 10:46am | Jul 2, 2026 10:46am |  |  | Fair | No | Premises ok and with supply.
Outage | J.E.26.07.00627 | C001837516 | Andre Williams | Trelawny | Completed | Load_245258 | Duncans - 110 | Jul 1, 2026 9:46pm | Jul 2, 2026 8:42am | Jul 2, 2026 10:11am | Jul 2, 2026 10:46am | Jul 2, 2026 11:28am | Jul 2, 2026 11:30am | Jul 2, 2026 11:31am | Jul 2, 2026 11:31am |  |  | Fair | No | Lines on property down both 2 naut and #2 twisted conductors, customer was advice to make necessary repairs.
Outage | J.E.26.07.00643 | C001837515 | Marlon Brown | Trelawny | Completed | Load_261797 | Martha Brae - 210 | Jul 1, 2026 9:46pm | Jul 1, 2026 9:47pm | Jul 1, 2026 10:10pm | Jul 1, 2026 10:10pm | Jul 1, 2026 11:05pm | Jul 1, 2026 11:05pm | Jul 1, 2026 11:05pm | Jul 1, 2026 11:05pm |  |  | Fair | No | Unable to locate customer via telephone nor direction
Outage | J.E.26.07.00625 | C001837505 | Barrington Brown | St.James | Completed | Load_1002559 | Bogue - 310 | Jul 1, 2026 8:39pm | Jul 1, 2026 8:39pm | Jul 1, 2026 9:21pm | Jul 1, 2026 9:21pm | Jul 1, 2026 9:46pm | Jul 1, 2026 10:24pm | Jul 1, 2026 10:24pm | Jul 1, 2026 10:24pm | Fire |  | Fair | No | Crew found three junction fuse blown on location 15k 20k and 30 k. Customers near by informed crew it was caused by birds. Crew conducted patrol and re energized circuit. All customers restored.
Outage | J.E.26.07.00610 | C001837499 | Richman Whyte | Westmoreland | Completed | Load_268022 | Paradise - 310 | Jul 1, 2026 8:17pm | Jul 1, 2026 8:18pm | Jul 1, 2026 9:50pm | Jul 1, 2026 9:50pm | Jul 1, 2026 9:50pm | Jul 1, 2026 9:51pm | Jul 1, 2026 9:51pm | Jul 1, 2026 9:51pm |  |  | Rains | No | Replace thirty amp junction fuse
Outage | J.E.26.07.00596 | C001837497 | Kaydon Taylor | KSAN | Completed | Load_239719 | Constant Spring - 410 | Jul 1, 2026 8:01pm | Jul 2, 2026 10:10am | Jul 2, 2026 11:52am | Jul 2, 2026 12:05pm | Jul 2, 2026 12:31pm | Jul 2, 2026 1:00pm | Jul 2, 2026 1:01pm | Jul 2, 2026 1:01pm |  |  | Rains | No | One clamp at pole v 116- 117-233
Outage | J.E.26.07.00578 | C001837496 | Derrick Dawkins | St.James | Completed | Load_240209 | Bogue - 610 | Jul 1, 2026 8:00pm | Jul 1, 2026 8:00pm | Jul 1, 2026 8:46pm | Jul 1, 2026 8:46pm | Jul 1, 2026 9:35pm | Jul 1, 2026 9:36pm | Jul 1, 2026 9:39pm | Jul 1, 2026 9:39pm |  |  | Fair | No | Found 8amp junction blown due to vegetation remove vegetation and replace 8 amp at pole number 609363
Outage | J.E.26.07.00587 | C001837495 | Roxroy Needham | St.Ann | Completed | Load_263508 | Cardiff Hall - 210 | Jul 1, 2026 7:55pm | Jul 1, 2026 7:55pm | Jul 1, 2026 9:53pm | Jul 1, 2026 9:54pm | Jul 1, 2026 10:50pm | Jul 1, 2026 10:50pm | Jul 1, 2026 11:12pm | Jul 1, 2026 11:12pm | BrokenWire |  | Fair | No | Remake joint at pothead used 2 pg clamp voltage left at meter 114-115-231
Outage | J.E.26.07.00592 | C001837493 | Roxroy Needham | St.Ann | Completed | Load_259477 | Cardiff Hall - 310 | Jul 1, 2026 7:55pm | Jul 2, 2026 7:29am | Jul 2, 2026 8:41am | Jul 2, 2026 8:41am | Jul 2, 2026 9:26am | Jul 2, 2026 9:29am | Jul 2, 2026 9:29am | Jul 2, 2026 9:29am |  |  | Fair | No | Clean and remake secondary jumper using 1 pg clamp voltage left 115;117;232
Outage | J.E.26.07.00603 | C001837494 | Roxroy Needham | St.Ann | Completed | Load_255068 | Cardiff Hall - 310 | Jul 1, 2026 7:55pm | Jul 2, 2026 7:29am | Jul 2, 2026 8:03am | Jul 2, 2026 8:07am | Jul 2, 2026 8:35am | Jul 2, 2026 8:38am | Jul 2, 2026 8:38am | Jul 2, 2026 8:38am |  |  | Fair | No | Replace 1 - 15 amp junction fuse after line was patrol
Outage | J.E.26.07.00576 | C001837492 | Raymond Lewis | St.Ann | Completed | Load_242957 | Roaring River - 210 | Jul 1, 2026 7:54pm | Jul 1, 2026 7:55pm | Jul 1, 2026 8:13pm | Jul 1, 2026 8:13pm | Jul 1, 2026 8:31pm | Jul 1, 2026 8:53pm | Jul 1, 2026 8:53pm | Jul 1, 2026 8:53pm | BrokenWire |  | Fair | No | Refuse and close 50amp x former
Outage | J.E.26.07.00602 | C001837490 | Richman Whyte | Westmoreland | Completed | Load_262591 | Paradise - 310 | Jul 1, 2026 7:53pm | Jul 1, 2026 7:55pm | Jul 1, 2026 8:00pm | Jul 1, 2026 8:00pm | Jul 1, 2026 9:31pm | Jul 1, 2026 9:48pm | Jul 1, 2026 9:48pm | Jul 1, 2026 9:48pm |  |  | Fair | No | Replace thirty amp junction fuse
Outage | J.E.26.07.00604 | C001837489 | Selvin White | St.Elizabeth | Completed | Load_258954 | Maggotty - 110 | Jul 1, 2026 7:53pm | Jul 1, 2026 7:54pm | Jul 1, 2026 8:04pm | Jul 1, 2026 8:04pm | Jul 1, 2026 9:03pm | Jul 1, 2026 11:03pm | Jul 1, 2026 11:20pm | Jul 1, 2026 11:20pm | Fire |  | Rains | No | Isolate a 25 KVA transformer circuit in order to disconnect idle service wires that was causing a short circuit and to remade burnt off secondary neutral jumper at transformer pole after troubleshooting. Supply restored to all the affected customer with voltage readings of 239,120,119 volts.
Outage | J.E.26.07.00579 | C001837488 | Marlon Authors | Manchester | Completed | Load_302816 | Spur Tree - 210 | Jul 1, 2026 7:50pm | Jul 1, 2026 7:51pm | Jul 1, 2026 8:03pm | Jul 1, 2026 8:03pm | Jul 1, 2026 8:48pm | Jul 1, 2026 9:19pm | Jul 1, 2026 9:19pm | Jul 1, 2026 9:19pm |  |  | Fair | No | Patrol and found clear. Further checks revealed that the transformer is burnt. Please refer same to the maintenance department for replacement
Non-Outage | J.E.26.07.00475 | C001837487 | Oraine Minto | St.Ann | Completed | Load_255188 | Ocho Rios - 310 | Jul 1, 2026 7:45pm | Jul 2, 2026 8:08am | Jul 2, 2026 2:04pm | Jul 2, 2026 2:04pm | Jul 2, 2026 2:04pm | Jul 2, 2026 2:05pm | Jul 2, 2026 2:05pm | Jul 2, 2026 2:05pm |  |  | Fair | No | Customer states the issue was fixed
Non-Outage | J.E.26.07.00564 | C001837485 | Raymond Lewis | St.Ann | Completed | Load_268325 | Cardiff Hall - 310 | Jul 1, 2026 7:45pm | Jul 1, 2026 7:45pm | Jul 1, 2026 8:55pm | Jul 1, 2026 8:55pm | Jul 1, 2026 9:33pm | Jul 1, 2026 11:01pm | Jul 1, 2026 11:01pm | Jul 1, 2026 11:01pm |  |  | Fair | No | Open 25 kva x former to remade x former neutral
Outage | J.E.26.07.00601 | C001837483 | Marlon Authors | Manchester | Completed | Load_261991 | Spur Tree - 210 | Jul 1, 2026 7:43pm | Jul 1, 2026 7:44pm | Jul 1, 2026 10:19pm | Jul 1, 2026 10:19pm | Jul 1, 2026 10:19pm | Jul 1, 2026 10:30pm | Jul 1, 2026 10:30pm | Jul 1, 2026 10:30pm |  |  | Fair | No | Patrol and found clear. Replace one blown 10 amp junction fuse no pole #. Restored supply ok
Outage | J.E.26.07.00589 | C001837481 | Milton Charlton | KSAS | Completed | Load_293262 | Three Miles - 410 | Jul 1, 2026 7:40pm | Jul 1, 2026 8:03pm | Jul 1, 2026 8:19pm | Jul 1, 2026 8:31pm | Jul 1, 2026 10:00pm | Jul 1, 2026 9:55pm | Jul 1, 2026 10:04pm | Jul 1, 2026 10:04pm |  |  | Fair | No | Call related to call at 4 Balcombe Ave. Kgn.11. Burnt 15 kva transformer on Penwood Road.
Outage | J.E.26.07.00595 | C001837480 | Hartley Chin | Clarendon | Completed | Load_264946 | Parnassus - 210 | Jul 1, 2026 7:40pm | Jul 1, 2026 7:46pm | Jul 1, 2026 8:12pm | Jul 1, 2026 8:28pm | Jul 1, 2026 9:27pm | Jul 1, 2026 9:32pm | Jul 1, 2026 9:32pm | Jul 1, 2026 9:32pm |  |  | Fair | No | Found blown 15 amp junction fuse @ pole # 0210806 line patrolled and find okay, junction refused… No cell signal in area
Outage | J.E.26.07.00586 | C001837477 | Marlon Authors | Manchester | Completed | Load_292233 | Spur Tree - 210 | Jul 1, 2026 7:33pm | Jul 1, 2026 7:41pm | Jul 1, 2026 7:49pm | Jul 1, 2026 7:49pm | Jul 1, 2026 7:50pm | Jul 1, 2026 8:02pm | Jul 1, 2026 8:03pm | Jul 1, 2026 8:03pm |  |  | Fair | No | Patrol and found clear. Replace one blown 10 amp junction fuse no pole #. Restored supply ok
Outage | J.E.26.07.00565 | C001837476 | Milton Charlton | KSAS | Completed | Load_244728 | Greenwich - 710 | Jul 1, 2026 7:30pm | Jul 1, 2026 7:32pm | Jul 1, 2026 7:46pm | Jul 1, 2026 7:47pm | Jul 1, 2026 8:19pm | Jul 1, 2026 8:35pm | Jul 1, 2026 8:31pm | Jul 1, 2026 8:31pm | BrokenPole |  | Fair | No | Found okay upon arrival. Customer complaining about the street light at 46 Maverley Avenue not working.
Outage | J.E.26.07.00574 | C001837475 | Wan Carlos Scarlett | Portmore | Completed | Load_239998 | Naggo Head - 610 | Jul 1, 2026 7:26pm | Jul 1, 2026 7:37pm | Jul 1, 2026 9:09pm | Jul 1, 2026 9:09pm | Jul 1, 2026 9:33pm | Jul 1, 2026 10:35pm | Jul 1, 2026 10:38pm | Jul 1, 2026 10:38pm |  |  | Fair | No | Found one span of open secondary line top phase touching on neutral tension one span of open secondary line top phase use 3 one bolt clamps at pole refuse 25KVA transformer with a 3amp fuse no pole # was found
Outage | J.E.26.07.00577 | C001837474 | Kaydon Taylor | KSAN | Completed | Load_258089 | Constant Spring - 210 | Jul 1, 2026 7:25pm | Jul 1, 2026 7:25pm | Jul 1, 2026 7:40pm | Jul 1, 2026 7:40pm | Jul 1, 2026 8:26pm | Jul 1, 2026 8:55pm | Jul 1, 2026 8:55pm | Jul 1, 2026 8:55pm |  |  | Fair | No | 15 amp fuse found blown and replace at pole #0011758
Non-Outage | J.E.26.07.00531 | C001837470 | Fitzroy Turner | KSAS | Completed | Load_1002731 | Cane River - 610 | Jul 1, 2026 7:01pm | Jul 1, 2026 7:01pm | Jul 1, 2026 7:08pm | Jul 1, 2026 7:08pm | Jul 1, 2026 7:17pm | Jul 1, 2026 7:35pm | Jul 1, 2026 7:35pm | Jul 1, 2026 7:35pm |  |  | Fair | No | Found bank of three 25kva transformer. Found one 3amps fuse blown replaced with same 3amp supply restored to sewage plant
Outage | J.E.26.07.00540 | C001837468 | Daniel Francis | St.Ann | Completed | Load_252355 | Roaring River - 410 | Jul 1, 2026 6:59pm | Jul 2, 2026 7:31am | Jul 2, 2026 8:18am | Jul 2, 2026 8:19am | Jul 2, 2026 8:23am | Jul 2, 2026 8:23am | Jul 2, 2026 9:02am | Jul 2, 2026 9:02am | BrokenWire |  | Fair | No | Directions not clear phone number not registered
Outage | J.E.26.07.00549 | C001837467 | Raymond Lewis | St.Ann | Completed | Load_258154 | Roaring River - 410 | Jul 1, 2026 6:59pm | Jul 1, 2026 6:59pm | Jul 1, 2026 7:10pm | Jul 1, 2026 7:10pm | Jul 1, 2026 8:04pm | Jul 1, 2026 8:09pm | Jul 1, 2026 8:09pm | Jul 1, 2026 8:09pm | BrokenPole |  | Fair | No | Broken 30ft pole due to vehicle accident need to replace with over head guy pole customer still have light
Non-Outage | J.E.26.07.00547 | C001837464 | Hartley Chin | null | Completed | null | null | Jul 1, 2026 6:52pm | Jul 1, 2026 6:55pm | Jul 1, 2026 9:33pm | Jul 2, 2026 11:59am | Jul 2, 2026 11:59am | Jul 2, 2026 11:59am | Jul 2, 2026 12:10pm | Jul 2, 2026 12:10pm |  |  | Fair | No | Call related to job # 00800 ..
Outage | J.E.26.07.00550 | C001837463 | Neville Spencer | Clarendon | Completed | Load_240142 | May Pen - 110 | Jul 1, 2026 6:26pm | Jul 1, 2026 6:51pm | Jul 1, 2026 8:03pm | Jul 1, 2026 8:03pm | Jul 1, 2026 8:05pm | Jul 1, 2026 8:05pm | Jul 1, 2026 8:07pm | Jul 1, 2026 8:07pm | Fire |  | Fair | No | Cleared tree limb from 13.8 kv line .Replaced burnt up fuse holder and 25 amp j/ fuse at pole # 0199128 area restored.
Non-Outage | J.E.26.07.00517 | C001837462 | Edward Royal | KSAS | Completed | Load_241279 | Hunts Bay - 510 | Jul 1, 2026 6:17pm | Jul 1, 2026 6:20pm | Jul 1, 2026 7:16pm | Jul 1, 2026 7:16pm | Jul 1, 2026 7:54pm | Jul 1, 2026 8:49pm | Jul 1, 2026 8:50pm | Jul 1, 2026 8:50pm |  |  | Fair | No | Debush secondary line spliced reconnected # 6 cable using 5 one bolt clamps 5 ft 6 cable voltages reading 119v 119v 238v
Non-Outage | J.E.26.07.00529 | C001837457 | Richard Grant | null | Completed | null | null | Jul 1, 2026 5:27pm | Jul 1, 2026 5:28pm | Jul 1, 2026 7:52pm | Jul 1, 2026 7:52pm | Jul 1, 2026 8:33pm | Jul 1, 2026 8:43pm | Jul 1, 2026 8:43pm | Jul 1, 2026 8:43pm |  |  | Fair | No | Calls to customer goes straight to voicemail. Insufficient direction. Premises not found.
Outage | J.E.26.07.00469 | C001837455 | Hopeton Henry | St.Thomas | Completed | Load_245707 | Good Year - 210 | Jul 1, 2026 5:24pm | Jul 1, 2026 5:31pm | Jul 1, 2026 5:47pm | Jul 1, 2026 5:47pm | Jul 1, 2026 6:25pm | Jul 1, 2026 7:34pm | Jul 1, 2026 7:38pm | Jul 1, 2026 7:38pm | BrokenWire |  | Fair | No | Check and found defective pole 35 ft wooden pole No guy
Outage | J.E.26.07.00421 | C001837454 | Milton Charlton | KSAN | Completed | Load_270237 | Washington Blvd - 710 | Jul 1, 2026 5:19pm | Jul 1, 2026 5:19pm | Jul 1, 2026 5:28pm | Jul 1, 2026 5:28pm | Jul 1, 2026 5:28pm | Jul 1, 2026 5:45pm | Jul 1, 2026 5:45pm | Jul 1, 2026 5:45pm |  |  | Fair | No | Isolate bank of two transformers at pole # 0114815(1-100 & 1-25) and repair multiple burnt off #6 triplex phase using 10#2AA conductor and five 1- bolt clamps and reclosed bank of transformers switches.
Outage | J.E.26.07.00522 | C001837451 | Neville Spencer | Clarendon | Completed | Load_252707 | May Pen - 110 | Jul 1, 2026 5:13pm | Jul 1, 2026 5:21pm | Jul 1, 2026 6:01pm | Jul 1, 2026 6:01pm | Jul 1, 2026 7:34pm | Jul 1, 2026 8:00pm | Jul 1, 2026 8:03pm | Jul 1, 2026 8:03pm | Fire |  | Fair | No | Cleared tree limb from 13.8 kv line.Replaced burnt up fuse holder and 25 amp j/ fuse at pole #0199128 area restored.
Non-Outage | J.E.26.06.25773 | C001837448 | Richard Grant | St.Catherine | Completed | Load_246200 | New Michelton - 310 | Jul 1, 2026 5:06pm | Jul 1, 2026 5:08pm | Jul 1, 2026 6:46pm | Jul 1, 2026 6:46pm | Jul 1, 2026 7:47pm | Jul 1, 2026 7:52pm | Jul 1, 2026 7:52pm | Jul 1, 2026 7:52pm | Fire |  | Fair | No | No fire seen at time of visit. Premises and area found okay.
Non-Outage | J.E.26.06.35868 | C001837447 | Hartley Chin | St.Catherine | Completed | Load_240682 | Rhodens Pen - 310 | Jul 1, 2026 5:05pm | Jul 1, 2026 5:10pm | Jul 1, 2026 5:37pm | Jul 1, 2026 5:37pm | Jul 1, 2026 5:37pm | Jul 1, 2026 5:37pm | Jul 1, 2026 5:38pm | Jul 1, 2026 5:38pm | BrokenPole |  | Fair | No | Call related to job # 39139 …
Non-Outage | J.E.26.06.38488 | C001837443 | Richard Grant | St.Catherine | Completed | Load_247562 | New Michelton - 210 | Jul 1, 2026 5:05pm | Jul 1, 2026 5:08pm | Jul 1, 2026 8:44pm | Jul 1, 2026 8:44pm | Jul 1, 2026 9:21pm | Jul 1, 2026 9:35pm | Jul 1, 2026 9:35pm | Jul 1, 2026 9:35pm | Fire |  | Fair | No | Premises found okay
Non-Outage | J.E.26.06.39142 | C001837442 | Richard Nicholas | null | Completed | null | null | Jul 1, 2026 5:04pm | Jul 1, 2026 5:09pm | Jul 1, 2026 10:57pm | Jul 1, 2026 10:57pm | Jul 1, 2026 10:57pm | Jul 1, 2026 10:57pm | Jul 1, 2026 10:57pm | Jul 1, 2026 10:57pm | LowHangingWires |  | Fair | No | Found ok
Non-Outage | J.E.26.06.39175 | C001837441 | Richard Nicholas | null | Completed | null | null | Jul 1, 2026 5:04pm | Jul 1, 2026 5:09pm | Jul 1, 2026 8:36pm | Jul 1, 2026 8:36pm | Jul 1, 2026 9:55pm | Jul 1, 2026 10:54pm | Jul 1, 2026 10:56pm | Jul 1, 2026 10:56pm | LowHangingWires |  | Fair | No | Truck burst down service wire.100ft of #6 triplex,3 clamp and 3 linket was installed.voltage reading 198,102 and 200v.
Non-Outage | J.E.26.06.39455 | C001837440 | Richard Nicholas | null | Completed | null | null | Jul 1, 2026 5:04pm | Jul 1, 2026 5:09pm | Jul 1, 2026 6:41pm | Jul 1, 2026 6:41pm | Jul 1, 2026 8:34pm | Jul 1, 2026 8:35pm | Jul 1, 2026 8:36pm | Jul 1, 2026 8:36pm | LowHangingWires |  | Fair | No | Area found ok,no low JPS.co wire seen.
Non-Outage | J.E.26.03.37254 | C001837439 | Derrick Dawkins | St.James | Completed | Load_242321 | Bogue - 510 | Jul 1, 2026 5:01pm | Jul 1, 2026 5:02pm | Jul 1, 2026 6:16pm | Jul 1, 2026 6:16pm | Jul 1, 2026 6:51pm | Jul 1, 2026 6:31pm | Jul 1, 2026 6:54pm | Jul 1, 2026 6:54pm |  |  | Fair | No | Customer said that she didn’t make any report
Non-Outage | J.E.26.03.41398 | C001837438 | Derrick Dawkins | St.James | Completed | Load_258826 | Bogue - 610 | Jul 1, 2026 5:01pm | Jul 1, 2026 5:02pm | Jul 1, 2026 7:39pm | Jul 1, 2026 7:39pm | Jul 1, 2026 8:09pm | Jul 1, 2026 8:40pm | Jul 1, 2026 8:40pm | Jul 1, 2026 8:40pm |  |  | Fair | No | Found a junction fuse blown, 25 amp due to bamboo on line bamboo was removed, replaced 25 amp junction fuse no pole # available
Non-Outage | J.E.26.07.00509 | C001837434 | Ricky Hall | St.Catherine | Completed | Load_264901 | Rhodens Pen - 410 | Jul 1, 2026 5:00pm | Jul 1, 2026 5:10pm | Jul 1, 2026 6:38pm | Jul 1, 2026 6:38pm | Jul 1, 2026 7:54pm | Jul 1, 2026 9:47pm | Jul 1, 2026 9:49pm | Jul 1, 2026 9:49pm | Fire |  | Fair | No | Create dead end retire secondary phasererouted secondary circuit
Non-Outage | J.E.26.06.39923 | C001837431 | Derrick Dawkins | St.James | Completed | Load_1003256 | Bogue - 310 | Jul 1, 2026 4:59pm | Jul 1, 2026 5:02pm | Jul 1, 2026 7:20pm | Jul 1, 2026 7:20pm | Jul 1, 2026 7:21pm | Jul 1, 2026 7:26pm | Jul 1, 2026 7:23pm | Jul 1, 2026 7:23pm |  |  | Fair | No | Premises found ok
Non-Outage | J.E.26.06.39926 | C001837433 | Derrick Dawkins | St.James | Completed | Load_1003256 | Bogue - 310 | Jul 1, 2026 4:59pm | Jul 1, 2026 5:02pm | Jul 1, 2026 7:07pm | Jul 1, 2026 7:07pm | Jul 1, 2026 7:19pm | Jul 1, 2026 7:20pm | Jul 1, 2026 7:20pm | Jul 1, 2026 7:20pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.06.39265 | C001837432 | Moses Elliston | Portmore | Completed | Load_257303 | Naggo Head - 510 | Jul 1, 2026 4:59pm | Jul 1, 2026 5:00pm | Jul 2, 2026 11:09am | Jul 2, 2026 11:09am | Jul 2, 2026 12:08pm | Jul 2, 2026 1:06pm | Jul 2, 2026 1:16pm | Jul 2, 2026 1:16pm |  |  | Fair | No | Fluctuating volts at transformer pole # 0028037 due to Corroaded Joints and broken primary neutral .Urgent attention.Refer to D.Wilkie .R.Brown
Non-Outage | J.E.26.07.00311 | C001837430 | Derrick Dawkins | St.James | Completed | Load_238337 | Bogue - 610 | Jul 1, 2026 4:58pm | Jul 1, 2026 5:02pm | Jul 1, 2026 6:54pm | Jul 1, 2026 6:56pm | Jul 1, 2026 6:56pm | Jul 1, 2026 7:01pm | Jul 1, 2026 7:01pm | Jul 1, 2026 7:01pm |  |  | Fair | No | Cannot locate customer
Non-Outage | J.E.26.03.41546 | C001837429 | Derrick Dawkins | St.James | Completed | Load_256744 | Bogue - 310 | Jul 1, 2026 4:57pm | Jul 1, 2026 5:02pm | Jul 1, 2026 7:24pm | Jul 1, 2026 7:24pm | Jul 1, 2026 7:37pm | Jul 1, 2026 7:38pm | Jul 1, 2026 7:38pm | Jul 1, 2026 7:38pm |  |  | Fair | No | Checked and found ok voltage 119/118=227
Non-Outage | J.E.26.03.44635 | C001837428 | Barrington Brown | St.James | Completed | Load_251499 | Queens Drive - 710 | Jul 1, 2026 4:57pm | Jul 1, 2026 4:58pm | Jul 1, 2026 5:59pm | Jul 1, 2026 5:59pm | Jul 1, 2026 7:15pm | Jul 1, 2026 7:15pm | Jul 1, 2026 7:15pm | Jul 1, 2026 7:15pm |  |  | Fair | No | Checked and found ok
Non-Outage | J.E.26.04.03821 | C001837424 | Barrington Brown | St.James | Completed | Load_294708 | Queens Drive - 710 | Jul 1, 2026 4:57pm | Jul 1, 2026 4:58pm | Jul 1, 2026 7:15pm | Jul 1, 2026 7:15pm | Jul 1, 2026 9:20pm | Jul 1, 2026 9:21pm | Jul 1, 2026 9:21pm | Jul 1, 2026 9:21pm |  |  | Fair | No | Checked and found ok
Non-Outage | J.E.26.04.05161 | C001837423 | Barrington Brown | St.James | Completed | Load_294708 | Queens Drive - 710 | Jul 1, 2026 4:57pm | Jul 1, 2026 4:58pm | Jul 1, 2026 5:03pm | Jul 1, 2026 5:03pm | Jul 1, 2026 5:55pm | Jul 1, 2026 5:56pm | Jul 1, 2026 5:56pm | Jul 1, 2026 5:56pm |  |  | Fair | No | Checked and found ok issue was resolved
Outage | J.E.26.07.00523 | C001837420 | Evan Spaulding | St.Mary | Completed | Load_238031 | Highgate - 210 | Jul 1, 2026 4:54pm | Jul 1, 2026 4:59pm | Jul 1, 2026 5:45pm | Jul 1, 2026 5:45pm | Jul 1, 2026 6:26pm | Jul 1, 2026 7:29pm | Jul 1, 2026 7:33pm | Jul 1, 2026 7:33pm | BrokenWire |  | Fair | No | Splice and retention two spans secondary conductors using 120ft #2 AAAC ,100ft 2/0 AAAC conductors,2-#2 ,2-2/0 splicing sleeves and 1- 2/0 preform .
Outage | J.E.26.07.00173 | C001837418 | Marlon Authors | St.Elizabeth | Completed | Load_292661 | Maggotty - 210 | Jul 1, 2026 4:53pm | Jul 1, 2026 4:54pm | Jul 1, 2026 5:21pm | Jul 1, 2026 5:21pm | Jul 1, 2026 5:49pm | Jul 1, 2026 6:48pm | Jul 1, 2026 7:21pm | Jul 1, 2026 7:21pm |  |  | Fair | No | Patrol and found clear replace one blown 3 amp fuse that protects 15 kva transformer circuit no pole #, however this customer had socket type meter and hexing system is in the area now and she needs to be connected. Please refer same to the field services department for further assistance
Outage | J.E.26.07.00501 | C001837413 | Milton Charlton | KSAN | Completed | Load_268838 | Washington Blvd - 710 | Jul 1, 2026 4:45pm | Jul 1, 2026 4:49pm | Jul 1, 2026 5:07pm | Jul 1, 2026 5:07pm | Jul 1, 2026 5:07pm | Jul 1, 2026 3:45pm | Jul 1, 2026 5:28pm | Jul 1, 2026 5:28pm | BrokenPole |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.07.00513 | C001837412 | Romeo Brissett | St.James | Completed | Load_293248 | Queens Drive - 310 | Jul 1, 2026 4:28pm | Jul 1, 2026 4:28pm | Jul 1, 2026 5:34pm | Jul 1, 2026 5:34pm | Jul 1, 2026 5:47pm | Jul 1, 2026 6:33pm | Jul 1, 2026 6:35pm | Jul 1, 2026 6:35pm |  |  | Fair | No | A Dead bird was found, replaced (1)30amps junction fuse and (1)10KVA transformer fuse.
Outage | J.E.26.07.00463 | C001837406 | Kaydon Taylor | KSAN | Completed | Load_265860 | Constant Spring - 210 | Jul 1, 2026 4:19pm | Jul 1, 2026 7:24pm | Jul 1, 2026 9:06pm | Jul 1, 2026 9:06pm | Jul 1, 2026 10:06pm | Jul 1, 2026 10:36pm | Jul 1, 2026 10:36pm | Jul 1, 2026 10:36pm |  |  | Fair | No | (2) 20 amp fuse found blown and replace at pole #041908
Non-Outage | J.E.26.07.00239 | C001837399 | Javid Vernon | null | Completed | null | null | Jul 1, 2026 4:03pm | Jul 1, 2026 4:04pm | Jul 1, 2026 4:39pm | Jul 1, 2026 4:39pm | Jul 1, 2026 5:56pm | Jul 1, 2026 6:05pm | Jul 1, 2026 6:05pm | Jul 1, 2026 6:05pm | BrokenWire |  | Fair | No | Area and premises check and found okay customer stated that a team came earlier today and resolved the issue
Outage | J.E.26.07.00324 | C001837396 | Marlon Authors | St.Elizabeth | Completed | Load_250531 | Maggotty - 210 | Jul 1, 2026 3:58pm | Jul 1, 2026 3:58pm | Jul 1, 2026 4:35pm | Jul 1, 2026 4:35pm | Jul 1, 2026 4:54pm | Jul 1, 2026 5:09pm | Jul 1, 2026 5:09pm | Jul 1, 2026 5:09pm |  |  | Fair | No | Patrol and found defective customer service wire broken and on the ground. Disconnect same at pole and replace one blown 1 amp fuse that protects 25 kva transformer circuit at pole #621748. Restored supply ok
Non-Outage | J.E.26.06.39963 | C001837393 | Selvin White | null | Completed | null | null | Jul 1, 2026 3:52pm | Jul 1, 2026 3:56pm | Jul 1, 2026 4:30pm | Jul 1, 2026 4:30pm | Jul 1, 2026 5:27pm | Jul 1, 2026 5:32pm | Jul 1, 2026 5:33pm | Jul 1, 2026 5:33pm |  |  | Fair | No | Customer was contacted and said cell site is not located in St. Elizabeth.
Outage | J.E.26.07.00153 | C001837394 | Richman Whyte | St.Elizabeth | Completed | Load_256257 | Maggotty - 110 | Jul 1, 2026 3:52pm | Jul 1, 2026 3:53pm | Jul 1, 2026 6:36pm | Jul 1, 2026 6:36pm | Jul 1, 2026 6:36pm | Jul 1, 2026 6:36pm | Jul 1, 2026 6:37pm | Jul 1, 2026 6:37pm |  |  | Fair | No | Unable to locate or contact customer after several attempts
Non-Outage | J.E.26.07.00162 | C001837387 | Marlon Brown | Trelawny | Completed | Load_556060 | Martha Brae - 110 | Jul 1, 2026 3:47pm | Jul 1, 2026 3:47pm | Jul 1, 2026 5:10pm | Jul 1, 2026 5:10pm | Jul 1, 2026 5:23pm | Jul 1, 2026 5:38pm | Jul 1, 2026 5:38pm | Jul 1, 2026 5:38pm |  |  | Fair | No | Remake neutral joint at pole use 1 pg clampVoltage found at pothead 130/100=230Voltage leaving at pothead 116/114=230v
Non-Outage | J.E.26.07.00491 | C001837386 | Marlon Brown | Trelawny | Completed | Load_1001473 | Martha Brae - 210 | Jul 1, 2026 3:46pm | Jul 1, 2026 3:47pm | Jul 1, 2026 4:25pm | Jul 1, 2026 4:25pm | Jul 1, 2026 4:39pm | Jul 1, 2026 5:10pm | Jul 1, 2026 5:10pm | Jul 1, 2026 5:10pm |  |  | Fair | No | Clean and remake joints at pole use 3 pg clamps Voltage found at pothead 118/119/205=237/236/239vVoltage leaving at pothead 118/119/205=236/237/239v. Corroded joint at transformer drop leads.
Non-Outage | J.E.26.07.00149 | C001837376 | Rayon Foster | Hanover | Completed | Load_242070 | Orange Bay - 310 | Jul 1, 2026 3:44pm | Jul 1, 2026 3:45pm | Jul 1, 2026 3:53pm | Jul 1, 2026 6:21pm | Jul 1, 2026 7:15pm | Jul 1, 2026 7:16pm | Jul 1, 2026 7:18pm | Jul 1, 2026 7:18pm | BrokenWire |  | Fair | No | Unable to reach customer on cell phone and directions to premises are unclear
Outage | J.E.26.06.39750 | C001837359 | Elvis Trowers | KSAN | Completed | Load_245669 | Constant Spring - 210 | Jul 1, 2026 3:30pm | Jul 2, 2026 10:50am | Jul 2, 2026 10:55am | Jul 2, 2026 10:55am | Jul 2, 2026 11:56am | Jul 2, 2026 4:34pm | Jul 2, 2026 4:34pm | Jul 2, 2026 4:34pm |  | Y | Fair | Yes | Areas was found when without electricity supply when checked and a defective cutout switch with a 5 amp transformer fuse was replaced after patrol was completed at pole number missing and a 10 amp junction fuse at pole #0011173, also primary bushings was done.
Outage | J.E.26.07.00158 | C001837349 | Selvin White | St.Elizabeth | Completed | Load_292828 | Maggotty - 110 | Jul 1, 2026 3:22pm | Jul 1, 2026 3:59pm | Jul 1, 2026 4:05pm | Jul 1, 2026 4:05pm | Jul 1, 2026 4:07pm | Jul 1, 2026 4:08pm | Jul 1, 2026 4:09pm | Jul 1, 2026 4:09pm |  |  | Rains | No | Customer was contacted by phone and it was stated that supply was restored earlier.
Outage | J.E.26.07.00441 | C001837348 | Selvin White | St.Elizabeth | Completed | Load_569186 | Maggotty - 110 | Jul 1, 2026 3:22pm | Jul 1, 2026 4:37pm | Jul 1, 2026 5:38pm | Jul 1, 2026 5:38pm | Jul 1, 2026 6:02pm | Jul 1, 2026 6:24pm | Jul 1, 2026 6:25pm | Jul 1, 2026 6:25pm |  |  | Fair | No | Approximately 130 ft of #2 quad will be required to reconnect customer and bank of 2 transformers to be energized.after. Please advise C Johnson at the field service department.
Non-Outage | J.E.26.07.00485 | C001837346 | Roxroy Needham | null | Completed | null | null | Jul 1, 2026 3:20pm | Jul 1, 2026 3:21pm | Jul 1, 2026 7:35pm | Jul 1, 2026 7:35pm | Jul 1, 2026 8:33pm | Jul 1, 2026 8:33pm | Jul 1, 2026 8:34pm | Jul 1, 2026 8:34pm | BrokenWire |  | Fair | No | Customer say that light is back
Outage | J.E.26.07.00455 | C001837342 | Richman Whyte | Westmoreland | Completed | Load_292988 | Paradise - 310 | Jul 1, 2026 3:18pm | Jul 1, 2026 3:21pm | Jul 1, 2026 4:59pm | Jul 1, 2026 4:59pm | Jul 1, 2026 4:59pm | Jul 1, 2026 4:59pm | Jul 1, 2026 4:59pm | Jul 1, 2026 4:59pm |  |  | Fair | No | Close 3 25kva transformer fuse
Outage | J.E.26.07.00467 | C001837343 | Evan Spaulding | St.Mary | Completed | Load_267063 | Annotto Bay - 310 | Jul 1, 2026 3:18pm | Jul 1, 2026 3:19pm | Jul 1, 2026 5:04pm | Jul 1, 2026 5:04pm | Jul 1, 2026 5:04pm | Jul 1, 2026 5:04pm | Jul 1, 2026 5:05pm | Jul 1, 2026 5:05pm |  |  | Fair | No | Customer says he didn’t mad any report .
Outage | J.E.26.07.00359 | C001837337 | Romeo Brissett | St.James | Completed | Load_260155 | Queens Drive - 710 | Jul 1, 2026 3:15pm | Jul 1, 2026 3:17pm | Jul 1, 2026 3:37pm | Jul 1, 2026 3:37pm | Jul 1, 2026 4:30pm | Jul 1, 2026 4:36pm | Jul 1, 2026 4:37pm | Jul 1, 2026 4:37pm |  |  | Fair | No | Check and found ok, customer stated power restored.
Outage | J.E.26.07.00419 | C001837336 | Romeo Brissett | St.James | Completed | Load_249709 | Queens Drive - 710 | Jul 1, 2026 3:15pm | Jul 1, 2026 3:17pm | Jul 1, 2026 4:37pm | Jul 1, 2026 4:37pm | Jul 1, 2026 4:56pm | Jul 1, 2026 5:15pm | Jul 1, 2026 5:34pm | Jul 1, 2026 5:34pm | Fire |  | Fair | No | Replaced (1)20amps junction fuse.
Outage | J.E.26.07.00466 | C001837329 | Omar King | St.Ann | Completed | Load_255188 | Ocho Rios - 310 | Jul 1, 2026 3:03pm | Jul 1, 2026 3:03pm | Jul 1, 2026 3:41pm | Jul 1, 2026 3:47pm | Jul 1, 2026 4:56pm | Jul 1, 2026 4:57pm | Jul 1, 2026 4:59pm | Jul 1, 2026 4:59pm |  |  | Fair | No | Found customer service wire with corrosion at pole as been repaired customer is now with supply voltage 119 Volts before 99 volts
Non-Outage | J.E.26.07.00445 | C001837285 | Neckell Ormsby | St.Mary | Completed | Load_254695 | Annotto Bay - 310 | Jul 1, 2026 1:57pm | Jul 2, 2026 7:50am | Jul 2, 2026 9:44am | Jul 2, 2026 9:44am | Jul 2, 2026 11:06am | Jul 2, 2026 11:51am | Jul 2, 2026 11:52am | Jul 2, 2026 11:52am | BrokenWire |  | Fair | No | Cut and Remove abondon secondary conductor that customer was concerned about
Outage | J.E.26.07.00423 | C001837277 | Horace Malcolm | St.James | Completed | Load_242655 | Bogue - 310 | Jul 1, 2026 1:50pm | Jul 1, 2026 1:50pm | Jul 1, 2026 1:57pm | Jul 1, 2026 1:57pm | Jul 1, 2026 3:00pm | Jul 1, 2026 2:51pm | Jul 2, 2026 7:41am | Jul 2, 2026 7:41am |  |  | Fair | No | Isolate one 20amp junction fuse to repair one 8amp junction fuse switch bottom wire used one clamp
Non-Outage | J.E.26.07.00382 | C001837276 | Gregory Grossett | Portland | Completed | Load_240492 | Port Antonio - 410 | Jul 1, 2026 1:48pm | Jul 2, 2026 7:46am | Jul 2, 2026 7:54am | Jul 2, 2026 7:55am | Jul 2, 2026 8:43am | Jul 2, 2026 10:15am | Jul 2, 2026 10:30am | Jul 2, 2026 10:30am | BrokenWire |  | Fair | No | Section of 220 service wire oxidize across gully in mid air replace use 50ft of service wire customer is now ok.
Outage | J.E.26.07.00313 | C001837273 | Milton Charlton | KSAN | Completed | Load_266717 | Washington Blvd - 710 | Jul 1, 2026 1:47pm | Jul 1, 2026 1:48pm | Jul 1, 2026 2:57pm | Jul 1, 2026 2:57pm | Jul 1, 2026 4:30pm | Jul 1, 2026 4:30pm | Jul 1, 2026 4:31pm | Jul 1, 2026 4:31pm |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Outage | J.E.26.07.00421 | C001837274 | Milton Charlton | KSAN | Completed | Load_270237 | Washington Blvd - 710 | Jul 1, 2026 1:47pm | Jul 1, 2026 1:48pm | Jul 1, 2026 4:31pm | Jul 1, 2026 4:31pm | Jul 1, 2026 5:05pm | Jul 1, 2026 3:45pm | Jul 1, 2026 5:07pm | Jul 1, 2026 5:07pm |  |  | Fair | No | Found okay upon arrival. Matter was resolved.
Non-Outage | J.E.26.07.00437 | C001837269 | Ricky Hall | null | Completed | null | null | Jul 1, 2026 1:45pm | Jul 1, 2026 4:20pm | Jul 1, 2026 5:37pm | Jul 1, 2026 5:37pm | Jul 1, 2026 6:15pm | Jul 1, 2026 6:37pm | Jul 1, 2026 6:38pm | Jul 1, 2026 6:38pm | BrokenWire |  | Fair | No | Disconnect and remove broken 3W service to clear rdwy
Outage | J.E.26.07.00434 | C001837270 | Denton Williams | Portland | Completed | Load_246257 | Port Antonio - 410 | Jul 1, 2026 1:45pm | Jul 1, 2026 3:17pm | Jul 1, 2026 4:36pm | Jul 1, 2026 4:37pm | Jul 1, 2026 4:50pm | Jul 1, 2026 4:54pm | Jul 1, 2026 4:59pm | Jul 1, 2026 4:59pm | TreeContact |  | Fair | No | Customer supply found okay. However, customer is concerned about over grown vegetation that entangle secondary lines and is very close to primary line as well. Please refer to the vegetation department / Portland Maintenance.
Non-Outage | J.E.26.07.00410 | C001837267 | Oraine Minto | St.Ann | Completed | Load_574343 | Roaring River - 210 | Jul 1, 2026 1:44pm | Jul 1, 2026 1:44pm | Jul 1, 2026 2:42pm | Jul 1, 2026 5:39pm | Jul 1, 2026 5:39pm | Jul 1, 2026 5:40pm | Jul 1, 2026 5:40pm | Jul 1, 2026 5:40pm |  |  | Fair | No | Issue was resolved
Outage | J.E.26.07.00430 | C001837266 | Wan Carlos Scarlett | Portmore | Completed | Load_239998 | Naggo Head - 610 | Jul 1, 2026 1:42pm | Jul 1, 2026 1:43pm | Jul 1, 2026 1:56pm | Jul 1, 2026 10:39pm | Jul 1, 2026 10:39pm | Jul 1, 2026 10:39pm | Jul 1, 2026 10:40pm | Jul 1, 2026 10:40pm |  |  | Fair | No | Call related to power outage.customer confirm that power supply has been restored
Outage | J.E.26.07.00359 | C001837265 | Swon Miller | St.James | Completed | Load_260155 | Queens Drive - 710 | Jul 1, 2026 1:40pm | Jul 1, 2026 1:41pm | Jul 2, 2026 8:34am | Jul 2, 2026 8:34am | Jul 2, 2026 8:51am | Jul 21, 2026 9:24am | Jul 2, 2026 9:24am | Jul 2, 2026 9:24am |  |  | Fair | No | Check and found customer without supply cause by contamination at pole clean and remake joints use 2 pg voltage found 0.000 voltage left 115/116/232
Outage | J.E.26.07.00419 | C001837261 | Swon Miller | St.James | Completed | Load_249709 | Queens Drive - 710 | Jul 1, 2026 1:40pm | Jul 1, 2026 1:41pm | Jul 2, 2026 7:46am | Jul 2, 2026 7:46am | Jul 2, 2026 8:23am | Jul 22, 2026 8:33am | Jul 2, 2026 8:33am | Jul 2, 2026 8:33am | Fire |  | Fair | No | Check and found okay voltage found 116/116/232 voltage left 116/116/232
Outage | J.E.26.07.00422 | C001837257 | Roxroy Needham | St.Ann | Completed | Load_267528 | Cardiff Hall - 310 | Jul 1, 2026 1:31pm | Jul 1, 2026 3:21pm | Jul 1, 2026 3:40pm | Jul 1, 2026 3:40pm | Jul 1, 2026 4:34pm | Jul 1, 2026 4:36pm | Jul 1, 2026 4:37pm | Jul 1, 2026 4:37pm |  |  | Fair | No | Premises found ok voltage left at meter 115-114-231 customer have internal problem
Outage | J.E.26.07.00417 | C001837249 | Hartley Chin | Clarendon | Completed | Load_405994 | Parnassus - 210 | Jul 1, 2026 1:27pm | Jul 1, 2026 3:46pm | Jul 1, 2026 3:58pm | Jul 1, 2026 5:38pm | Jul 1, 2026 5:45pm | Jul 1, 2026 5:56pm | Jul 1, 2026 5:59pm | Jul 1, 2026 5:59pm |  |  | Fair | No | Premise found ok. Voltage v118 - v118
Outage | J.E.26.06.39079 | C001837245 | Moses Elliston | St.Catherine | Completed | Load_260579 | Tredegar - 310 | Jul 1, 2026 1:23pm | Jul 1, 2026 1:23pm | Jul 1, 2026 2:50pm | Jul 1, 2026 2:50pm | Jul 1, 2026 3:14pm | Jul 1, 2026 3:14pm | Jul 1, 2026 3:15pm | Jul 1, 2026 3:15pm |  |  | Fair | No | Supply at premises.Customer to add credit to account.
Non-Outage | J.E.26.06.39092 | C001837244 | Roemello Brown | Trelawny | Completed | Load_262115 | Duncans - 210 | Jul 1, 2026 1:20pm | Jul 1, 2026 1:20pm | Jul 2, 2026 9:08am | Jul 2, 2026 9:08am | Jul 2, 2026 9:32am | Jul 2, 2026 9:33am | Jul 2, 2026 9:44am | Jul 2, 2026 9:44am |  |  | Fair | No | Customer meter socket defective inform the customer to get an private electrician to change meter socket Voltage found 117/116/233Voltage leave 117/116/233
Non-Outage | J.E.26.07.00145 | C001837243 | Roemello Brown | Trelawny | Completed | Load_292887 | Greenwood - 210 | Jul 1, 2026 1:20pm | Jul 1, 2026 1:20pm | Jul 1, 2026 1:48pm | Jul 1, 2026 1:51pm | Jul 1, 2026 2:31pm | Jul 1, 2026 2:31pm | Jul 1, 2026 2:42pm | Jul 1, 2026 2:42pm |  |  | Fair | No | This is an hexing box needs field service to assist please line fluctuating coming from the box Voltage found 118/98/216Voltage leave 118/98/216Hex# 05328Hx# 22655780
Non-Outage | J.E.26.07.00162 | C001837242 | Roemello Brown | Trelawny | Completed | Load_556060 | Martha Brae - 110 | Jul 1, 2026 1:20pm | Jul 1, 2026 1:20pm | Jul 2, 2026 9:25am | Jul 2, 2026 9:44am | Jul 2, 2026 10:04am | Jul 2, 2026 10:04am | Jul 2, 2026 10:14am | Jul 2, 2026 10:14am |  |  | Fair | No | Premises found working okay Voltage found 116/115/231Voltage leave 116/115/231
Outage | J.E.26.07.00378 | C001837238 | Fitzroy Turner | KSAS | Completed | Load_267297 | Hunts Bay - 310 | Jul 1, 2026 1:18pm | Jul 1, 2026 4:07pm | Jul 1, 2026 8:27pm | Jul 1, 2026 8:27pm | Jul 1, 2026 8:52pm | Jul 1, 2026 9:10pm | Jul 1, 2026 9:11pm | Jul 1, 2026 9:11pm |  |  | Fair | No | Customer premises close at this time daylight attention
Outage | J.E.26.07.00339 | C001837232 | Richard Samuda | Manchester | Completed | Load_239128 | Kendal - 210 | Jul 1, 2026 1:13pm | Jul 1, 2026 1:13pm | Jul 1, 2026 1:48pm | Jul 1, 2026 1:48pm | Jul 1, 2026 2:25pm | Jul 1, 2026 2:25pm | Jul 1, 2026 2:26pm | Jul 1, 2026 2:26pm | BrokenWire |  | SevereWind | No | Customer say situation was resolved
Outage | J.E.26.07.00416 | C001837234 | Kemark Slue | St.Catherine | Completed | Load_250295 | New Michelton - 210 | Jul 1, 2026 1:13pm | Jul 1, 2026 1:14pm | Jul 1, 2026 1:44pm | Jul 1, 2026 2:23pm | Jul 1, 2026 2:23pm | Jul 1, 2026 2:23pm | Jul 1, 2026 2:23pm | Jul 1, 2026 2:23pm |  |  | Fair | No | Premises was checked and found okay.
Outage | J.E.26.07.00367 | C001837231 | Damion Reid | Manchester | Completed | Load_1002301 | Kendal - 210 | Jul 1, 2026 1:12pm | Jul 1, 2026 5:52pm | Jul 1, 2026 6:38pm | Jul 1, 2026 6:38pm | Jul 1, 2026 8:33pm | Jul 1, 2026 9:39pm | Jul 1, 2026 9:40pm | Jul 1, 2026 9:40pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.00340 | C001837230 | Barnett Brown | Manchester | Completed | Load_254566 | Spur Tree - 310 | Jul 1, 2026 1:11pm | Jul 1, 2026 1:12pm | null | Jul 1, 2026 6:10pm | Jul 1, 2026 7:07pm | Jul 1, 2026 7:20pm | Jul 1, 2026 7:21pm | Jul 1, 2026 7:21pm |  |  | Fair | No
Outage | J.E.26.07.00352 | C001837228 | Edward Royal | KSAN | Completed | Load_238439 | Washington Blvd - 610 | Jul 1, 2026 1:08pm | Jul 1, 2026 1:08pm | Jul 1, 2026 2:11pm | Jul 1, 2026 2:11pm | Jul 1, 2026 2:26pm | Jul 1, 2026 3:29pm | Jul 1, 2026 3:29pm | Jul 1, 2026 3:29pm |  |  | Fair | No | Replaced 20/ft #6 service cable and 6 one bolt clamps voltage reading 120v 120v 240v
Outage | J.E.26.07.00405 | C001837224 | Collin Robinson | Portland | Completed | Load_258243 | Port Antonio - 410 | Jul 1, 2026 1:01pm | Jul 1, 2026 1:02pm | Jul 1, 2026 1:49pm | Jul 1, 2026 1:49pm | Jul 1, 2026 2:49pm | Jul 1, 2026 3:07pm | Jul 1, 2026 3:07pm | Jul 1, 2026 3:07pm |  |  | Fair | No | Entangle open secondary conductor and replace 3 amps fuse
Non-Outage | J.E.26.07.00371 | C001837198 | Tyrese Williams | St.Ann | Completed | Load_246183 | Cardiff Hall - 210 | Jul 1, 2026 12:39pm | Jul 1, 2026 12:39pm | Jul 1, 2026 1:28pm | Jul 1, 2026 1:28pm | Jul 1, 2026 2:59pm | Jul 1, 2026 3:34pm | Jul 1, 2026 3:35pm | Jul 1, 2026 3:35pm |  |  | Fair | No | Premises found ok
Outage | J.E.26.07.00361 | C001837193 | Dwayne Samuels | Trelawny | Completed | Load_264628 | Greenwood - 110 | Jul 1, 2026 12:35pm | Jul 1, 2026 12:36pm | Jul 1, 2026 1:04pm | Jul 1, 2026 1:04pm | Jul 1, 2026 1:51pm | Jul 1, 2026 2:13pm | Jul 1, 2026 2:13pm | Jul 1, 2026 2:13pm | BrokenWire |  | Fair | No | 1 phase of customer service wire was disconnected from pole use 1 one bolt clamp at same for repair voltage left at customer meter 11v2/113v/225v
Non-Outage | J.E.26.07.00369 | C001837188 | Nickolas Rodriques | null | Completed | null | null | Jul 1, 2026 12:26pm | Jul 1, 2026 12:26pm | Jul 1, 2026 2:00pm | Jul 1, 2026 2:06pm | Jul 1, 2026 2:43pm | Jul 1, 2026 3:12pm | Jul 1, 2026 3:13pm | Jul 1, 2026 3:13pm |  |  | Fair | No | Customer confirmed that the power outage was restored. Area has electricity.
Outage | J.E.26.07.00372 | C001837180 | Nickolas Rodriques | St.Catherine | Completed | Load_246176 | Tredegar - 510 | Jul 1, 2026 12:21pm | Jul 1, 2026 12:22pm | Jul 1, 2026 3:36pm | Jul 1, 2026 3:42pm | Jul 1, 2026 3:52pm | Jul 1, 2026 3:54pm | Jul 1, 2026 4:07pm | Jul 1, 2026 4:07pm |  |  | Fair | No | Customer was contacted and stated that she is currently without a CIU box and awaiting a box as she recently moved to the location. Refer to field service.
Non-Outage | J.E.26.06.39332 | C001837175 | Orville Lee | Portmore | Completed | Load_244605 | Naggo Head - 610 | Jul 1, 2026 12:18pm | Jul 1, 2026 12:18pm | Jul 1, 2026 12:46pm | Jul 1, 2026 12:46pm | Jul 1, 2026 1:00pm | Jul 1, 2026 1:41pm | Jul 1, 2026 1:42pm | Jul 1, 2026 1:42pm |  |  | Fair | No | Checks made and found illegal connections at pothead Illegal connections was removed Pothead clamps change3 Penn union and 1 one bolt clamp usedVoltage 120V120V240V
Outage | J.E.26.07.00061 | C001837173 | Christopher Edwards | KSAN | Completed | Load_267645 | Constant Spring - 410 | Jul 1, 2026 12:11pm | Jul 1, 2026 12:39pm | Jul 1, 2026 1:04pm | Jul 1, 2026 1:04pm | Jul 1, 2026 2:29pm | Jul 1, 2026 3:31pm | Jul 1, 2026 3:32pm | Jul 1, 2026 3:32pm |  |  | Rains | No | Re-run 120ft #6 service (3) one bolt clamps
Outage | J.E.26.07.00312 | C001837167 | Wayne Dillion | St.Elizabeth | Completed | Load_292828 | Maggotty - 110 | Jul 1, 2026 12:10pm | Jul 1, 2026 12:11pm | Jul 1, 2026 1:28pm | Jul 1, 2026 1:28pm | Jul 1, 2026 1:28pm | Jul 1, 2026 1:33pm | Jul 1, 2026 1:32pm | Jul 1, 2026 1:32pm |  |  | Fair | No | Patrol and one blown 8 amp junction fuse no pole number replace the same supply restore to customer successfully
Outage | J.E.26.07.00353 | C001837166 | Richman Whyte | Westmoreland | Completed | Load_292988 | Paradise - 310 | Jul 1, 2026 12:09pm | Jul 1, 2026 12:10pm | Jul 1, 2026 1:16pm | Jul 1, 2026 1:16pm | Jul 1, 2026 1:16pm | Jul 1, 2026 1:17pm | Jul 1, 2026 1:17pm | Jul 1, 2026 1:17pm |  |  | Fair | No | Disconnected power supply by opening 3 25kva transformer fuse
Outage | J.E.26.07.00232 | C001837164 | Fitzroy Turner | KSAS | Completed | Load_241866 | Cane River - 310 | Jul 1, 2026 12:06pm | Jul 1, 2026 4:07pm | Jul 1, 2026 5:31pm | Jul 1, 2026 5:32pm | Jul 1, 2026 6:17pm | Jul 1, 2026 6:23pm | Jul 1, 2026 7:08pm | Jul 1, 2026 7:08pm |  |  | Fair | No | Found 10 amps junction fuse blown at wicke wackie Blvd cause by defective 25 kva transformer that feed wickie wackie drive 25 kva STILL OUT.please send email to district to have transformer change out from morning
Outage | J.E.26.07.00292 | C001837153 | Hartley Chin | Clarendon | Completed | Load_258346 | Parnassus - 210 | Jul 1, 2026 11:56am | Jul 1, 2026 3:46pm | Jul 1, 2026 3:58pm | Jul 1, 2026 6:06pm | Jul 1, 2026 6:36pm | Jul 1, 2026 6:36pm | Jul 1, 2026 6:41pm | Jul 1, 2026 6:41pm |  |  | Fair | No | Premise not found. unable to contact customer , person who answered (said it was the wrong number ). Unable to find meter.
Outage | J.E.26.07.00331 | C001837154 | Neville Spencer | Clarendon | Completed | Load_252530 | Parnassus - 210 | Jul 1, 2026 11:56am | Jul 1, 2026 11:57am | Jul 1, 2026 1:28pm | Jul 1, 2026 1:28pm | Jul 1, 2026 2:06pm | Jul 1, 2026 3:08pm | Jul 1, 2026 3:09pm | Jul 1, 2026 3:09pm |  |  | Fair | No | Remade burnt out clamp on secondary phase jumper used 2, clamps voltage reading 110 113=223 supply restored.
Outage | J.E.26.07.00344 | C001837152 | Evan Spaulding | St.Mary | Completed | Load_294640 | Highgate -110 | Jul 1, 2026 11:55am | Jul 1, 2026 3:19pm | Jul 1, 2026 8:05pm | Jul 1, 2026 8:05pm | Jul 1, 2026 8:58pm | Jul 1, 2026 8:59pm | Jul 1, 2026 9:00pm | Jul 1, 2026 9:00pm |  |  | Fair | No | Customers concern at street lights not working in the housing scheme.
Non-Outage | J.E.26.06.39528 | C001837142 | Collin Robinson | Portland | Completed | Load_352955 | Port Antonio - 310 | Jul 1, 2026 11:52am | Jul 1, 2026 11:52am | Jul 1, 2026 12:39pm | Jul 1, 2026 12:39pm | Jul 1, 2026 1:23pm | Jul 1, 2026 1:30pm | Jul 1, 2026 1:31pm | Jul 1, 2026 1:31pm |  |  | Fair | No | Change corroded one bolt clamp that connects twisted wire to customer pothead Voltage 120v 120v 240v
Non-Outage | J.E.26.07.00327 | C001837140 | Tyrese Williams | St.Ann | Completed | Load_264049 | Cardiff Hall - 310 | Jul 1, 2026 11:51am | Jul 1, 2026 11:52am | Jul 2, 2026 7:54am | Jul 2, 2026 7:57am | Jul 2, 2026 7:57am | Jul 2, 2026 7:58am | Jul 2, 2026 7:58am | Jul 2, 2026 7:58am | LowHangingWires |  | Fair | No | Premises found ok
Non-Outage | J.E.26.06.38221 | C001837124 | Hopeton Henry | St.Thomas | Completed | Load_265770 | Good Year - 110 | Jul 1, 2026 11:40am | Jul 1, 2026 11:41am | Jul 1, 2026 11:53am | Jul 1, 2026 2:19pm | Jul 1, 2026 3:30pm | Jul 1, 2026 3:30pm | Jul 1, 2026 3:31pm | Jul 1, 2026 3:31pm |  |  | Fair | No | Found corrosion at pot head , use 3 connector 115-113-228 v
Non-Outage | J.E.26.06.38353 | C001837123 | Hopeton Henry | St.Thomas | Completed | Load_243261 | Good Year - 110 | Jul 1, 2026 11:40am | Jul 1, 2026 11:41am | Jul 1, 2026 11:53am | Jul 1, 2026 12:56pm | Jul 1, 2026 2:17pm | Jul 1, 2026 2:17pm | Jul 1, 2026 2:17pm | Jul 1, 2026 2:17pm |  |  | Fair | No | Found ok 115-115-230 volts at meter
Non-Outage | J.E.26.06.39626 | C001837122 | Hopeton Henry | St.Thomas | Completed | Load_254720 | Good Year - 110 | Jul 1, 2026 11:40am | Jul 1, 2026 11:41am | Jul 1, 2026 11:53am | Jul 1, 2026 2:18pm | Jul 1, 2026 2:18pm | Jul 1, 2026 2:18pm | Jul 1, 2026 2:19pm | Jul 1, 2026 2:19pm |  |  | Fair | No | Found corrosion at pot head Use 3 connector 118-119-237 volts
Non-Outage | J.E.26.06.39704 | C001837121 | Hopeton Henry | St.Thomas | Completed | Load_250333 | Good Year - 110 | Jul 1, 2026 11:40am | Jul 1, 2026 11:41am | Jul 1, 2026 11:53am | Jul 1, 2026 12:17pm | Jul 1, 2026 12:31pm | Jul 1, 2026 12:55pm | Jul 1, 2026 12:56pm | Jul 1, 2026 12:56pm |  |  | Fair | No | Found ok 119-119-238 volts at meter
Non-Outage | J.E.26.06.39810 | C001837120 | Hopeton Henry | St.Thomas | Completed | Load_577220 | Good Year - 210 | Jul 1, 2026 11:40am | Jul 1, 2026 11:41am | Jul 1, 2026 11:53am | Jul 1, 2026 7:38pm | Jul 1, 2026 8:31pm | Jul 1, 2026 8:31pm | Jul 1, 2026 8:31pm | Jul 1, 2026 8:31pm |  |  | Fair | No | Found corrosion at pole 116-113-229 volts
Outage | J.E.26.07.00230 | C001837116 | Damion Reid | Manchester | Completed | Load_249527 | Porus - 310 | Jul 1, 2026 11:38am | Jul 1, 2026 4:49pm | Jul 1, 2026 5:23pm | Jul 1, 2026 5:24pm | Jul 1, 2026 6:19pm | Jul 1, 2026 6:37pm | Jul 1, 2026 6:38pm | Jul 1, 2026 6:38pm |  |  | Fair | No | Blown 25amp junction fuse an blown 3amp fuse found for 25kva transformer cause by contamination line patrol and replace blown fuse
Outage | J.E.26.07.00291 | C001837119 | Barnett Brown | Manchester | Completed | Load_248630 | Spur Tree - 310 | Jul 1, 2026 11:38am | Jul 1, 2026 11:39am | null | Jul 1, 2026 2:53pm | Jul 1, 2026 4:17pm | Jul 1, 2026 6:06pm | Jul 1, 2026 6:07pm | Jul 1, 2026 6:07pm |  |  | Fair | No | Open 25 kva transformer, remade joints at drop lead
Outage | J.E.26.07.00299 | C001837115 | Richard Samuda | Manchester | Completed | Load_268443 | Kendal - 210 | Jul 1, 2026 11:37am | Jul 1, 2026 11:38am | Jul 1, 2026 12:08pm | Jul 1, 2026 12:15pm | Jul 1, 2026 12:48pm | Jul 1, 2026 12:48pm | Jul 1, 2026 12:54pm | Jul 1, 2026 12:54pm |  |  | Fair | No | Customer has a damaged meter meter is needs to replace voltage 116/114/230 refer call to field service
Outage | J.E.26.07.00097 | C001837111 | Barnett Brown | Manchester | Completed | Load_260536 | Spur Tree - 210 | Jul 1, 2026 11:35am | Jul 1, 2026 11:37am | null | Jul 1, 2026 7:22pm | Jul 1, 2026 8:27pm | Jul 1, 2026 8:57pm | Jul 1, 2026 9:01pm | Jul 1, 2026 9:01pm |  |  | Fair | No | Related to call done earlier where 20 amp junction fuse was replaced