Outage | J.E.26.07.00117 | C001837112 | Barnett Brown | Manchester | Completed | Load_250450 | Spur Tree - 210 | Jul 1, 2026 11:35am | Jul 1, 2026 11:37am | null | Jul 1, 2026 2:17pm | Jul 1, 2026 2:43pm | Jul 1, 2026 2:43pm | Jul 1, 2026 2:53pm | Jul 1, 2026 2:53pm |  |  | Fair | No | Premises found ok,
Outage | J.E.26.07.00143 | C001837107 | Barnett Brown | Manchester | Completed | Load_246108 | Spur Tree - 210 | Jul 1, 2026 11:35am | Jul 1, 2026 11:37am | null | Jul 1, 2026 12:47pm | Jul 1, 2026 1:20pm | Jul 1, 2026 2:11pm | Jul 1, 2026 2:17pm | Jul 1, 2026 2:17pm |  |  | Fair | No | Customer has internal fault, voltage 116 117 233
Outage | J.E.26.07.00173 | C001837109 | Selvin White | St.Elizabeth | Completed | Load_292661 | Maggotty - 210 | Jul 1, 2026 11:35am | Jul 1, 2026 3:53pm | Jul 1, 2026 4:16pm | Jul 1, 2026 4:16pm | Jul 1, 2026 4:25pm | Jul 1, 2026 4:29pm | Jul 1, 2026 4:29pm | Jul 1, 2026 4:29pm |  |  | Rains | No | Please refer to C Johnson and Simone Bicarie at the field service department as customer says they need reconnection and system is RAMi .
Non-Outage | J.E.26.06.33137 | C001837099 | Rochaine Hussey | KSAS | Completed | Load_237703 | Three Miles - 410 | Jul 1, 2026 11:29am | Jul 1, 2026 11:29am | Jul 2, 2026 3:33pm | Jul 2, 2026 4:05pm | Jul 2, 2026 4:10pm | Jul 2, 2026 4:37pm | Jul 2, 2026 4:47pm | Jul 2, 2026 4:47pm |  |  | Fair | No | Pothead was cleaned 2 clamp used116/116/232vHexing box in area
Non-Outage | J.E.26.06.34712 | C001837098 | Rochaine Hussey | KSAS | Completed | Load_257993 | Three Miles - 410 | Jul 1, 2026 11:29am | Jul 1, 2026 11:29am | Jul 2, 2026 12:59pm | Jul 2, 2026 4:47pm | Jul 2, 2026 4:47pm | Jul 2, 2026 4:47pm | Jul 2, 2026 4:47pm | Jul 2, 2026 4:47pm |  |  | Fair | No | Customer said issue was already resolved
Non-Outage | J.E.26.06.34887 | C001837100 | Rochaine Hussey | KSAS | Completed | Load_257993 | Three Miles - 410 | Jul 1, 2026 11:29am | Jul 1, 2026 11:29am | Jul 2, 2026 1:00pm | Jul 2, 2026 1:03pm | Jul 2, 2026 1:03pm | Jul 2, 2026 1:04pm | Jul 2, 2026 1:04pm | Jul 2, 2026 1:04pm |  |  | Fair | No | Customer said issue was already resolved
Non-Outage | J.E.26.06.12237 | C001837089 | Rochaine Hussey | KSAS | Completed | Load_241600 | Three Miles - 410 | Jul 1, 2026 11:28am | Jul 1, 2026 11:29am | Jul 1, 2026 1:08pm | Jul 1, 2026 3:16pm | Jul 1, 2026 3:17pm | Jul 1, 2026 3:20pm | Jul 1, 2026 3:20pm | Jul 1, 2026 3:20pm |  |  | Fair | No | Customer say the issue was fixed
Non-Outage | J.E.26.06.15325 | C001837092 | Rochaine Hussey | KSAS | Completed | Load_262509 | Three Miles - 410 | Jul 1, 2026 11:28am | Jul 1, 2026 11:29am | Jul 1, 2026 12:57pm | Jul 1, 2026 3:58pm | Jul 1, 2026 3:58pm | Jul 1, 2026 4:20pm | Jul 1, 2026 4:20pm | Jul 1, 2026 4:20pm |  |  | Fair | No | Customer say the issue was resolved
Non-Outage | J.E.26.06.18924 | C001837093 | Rochaine Hussey | KSAS | Completed | Load_252375 | Three Miles - 410 | Jul 1, 2026 11:28am | Jul 1, 2026 11:29am | Jul 1, 2026 1:07pm | Jul 1, 2026 1:33pm | Jul 1, 2026 1:33pm | Jul 1, 2026 1:34pm | Jul 1, 2026 1:34pm | Jul 1, 2026 1:34pm |  |  | Fair | No | Customer say the issue was already resolved
Non-Outage | J.E.26.06.22318 | C001837090 | Rochaine Hussey | KSAS | Completed | Load_295258 | Three Miles - 310 | Jul 1, 2026 11:28am | Jul 1, 2026 11:29am | Jul 1, 2026 1:10pm | Jul 1, 2026 3:21pm | Jul 1, 2026 3:23pm | Jul 1, 2026 3:28pm | Jul 1, 2026 3:28pm | Jul 1, 2026 3:28pm |  |  | Fair | No | Customer say the issue was resolved
Non-Outage | J.E.26.06.29050 | C001837091 | Rochaine Hussey | KSAS | Completed | Load_261609 | Three Miles - 410 | Jul 1, 2026 11:28am | Jul 1, 2026 11:29am | Jul 2, 2026 1:42pm | Jul 2, 2026 1:42pm | Jul 2, 2026 2:51pm | Jul 2, 2026 3:31pm | Jul 2, 2026 3:31pm | Jul 2, 2026 3:31pm |  |  | Fair | No | Customer getting low voltage due to current theft in the area referring to the maintenance team
Non-Outage | J.E.26.06.29736 | C001837095 | Rochaine Hussey | KSAS | Completed | Load_241188 | Three Miles - 410 | Jul 1, 2026 11:28am | Jul 1, 2026 11:29am | Jul 1, 2026 1:13pm | Jul 1, 2026 4:20pm | Jul 1, 2026 4:20pm | Jul 2, 2026 9:37am | Jul 2, 2026 9:37am | Jul 2, 2026 9:37am |  |  | Fair | No | Customer say the issue was resolved
Non-Outage | J.E.26.06.30419 | C001837096 | Rochaine Hussey | KSAS | Completed | Load_255433 | Three Miles - 410 | Jul 1, 2026 11:28am | Jul 1, 2026 11:29am | Jul 2, 2026 3:32pm | Jul 2, 2026 4:48pm | Jul 2, 2026 4:48pm | Jul 2, 2026 4:49pm | Jul 2, 2026 4:49pm | Jul 2, 2026 4:49pm |  |  | Fair | No | Customer said issue was already resolved
Non-Outage | J.E.26.06.31360 | C001837094 | Rochaine Hussey | KSAS | Completed | Load_244425 | Three Miles - 410 | Jul 1, 2026 11:28am | Jul 1, 2026 11:29am | Jul 1, 2026 1:33pm | Jul 2, 2026 12:55pm | Jul 2, 2026 12:55pm | Jul 2, 2026 12:57pm | Jul 2, 2026 1:03pm | Jul 2, 2026 1:03pm |  |  | Fair | No | Customer was called multiple times no answer
Non-Outage | J.E.26.06.31999 | C001837097 | Rochaine Hussey | KSAS | Completed | Load_255433 | Three Miles - 410 | Jul 1, 2026 11:28am | Jul 1, 2026 11:29am | Jul 2, 2026 10:59am | Jul 2, 2026 10:59am | Jul 2, 2026 11:00am | Jul 2, 2026 11:33am | Jul 2, 2026 11:33am | Jul 2, 2026 11:33am |  |  | Fair | No | Customer say the issue was resolved
Outage | J.E.26.07.00307 | C001837088 | Richard Grant | St.Catherine | Completed | Load_261214 | New Michelton - 210 | Jul 1, 2026 11:27am | Jul 1, 2026 3:57pm | Jul 1, 2026 4:04pm | Jul 1, 2026 5:32pm | Jul 1, 2026 6:45pm | Jul 1, 2026 6:45pm | Jul 1, 2026 6:46pm | Jul 1, 2026 6:46pm |  |  | Fair | No | Check revealed customer has internal issue. Customer was advised.
Outage | J.E.26.07.00305 | C001837087 | Roxroy Needham | St.Ann | Completed | Load_258525 | Cardiff Hall - 310 | Jul 1, 2026 11:26am | Jul 1, 2026 3:21pm | Jul 1, 2026 4:37pm | Jul 1, 2026 4:38pm | Jul 1, 2026 5:30pm | Jul 1, 2026 5:41pm | Jul 1, 2026 5:43pm | Jul 1, 2026 5:43pm | Fire | Y | Fair | No | Open a 25 KVA transformer at pole to retention 2 span of secondary line and cut tree from line
Outage | J.E.26.07.00140 | C001837083 | Kaydon Taylor | KSAN | Completed | Load_579095 | Constant Spring - 210 | Jul 1, 2026 11:25am | Jul 2, 2026 10:08am | Jul 2, 2026 11:49am | Jul 2, 2026 11:51am | Jul 2, 2026 11:51am | Jul 2, 2026 11:52am | Jul 2, 2026 11:52am | Jul 2, 2026 11:52am |  |  | Fair | No | Found okay
Outage | J.E.26.07.00177 | C001837082 | Kaydon Taylor | KSAN | Completed | Load_261778 | Constant Spring - 310 | Jul 1, 2026 11:25am | Jul 1, 2026 7:24pm | Jul 1, 2026 7:34pm | Jul 1, 2026 7:36pm | Jul 1, 2026 7:37pm | Jul 1, 2026 7:38pm | Jul 1, 2026 7:38pm | Jul 1, 2026 7:38pm |  |  | Fair | No | Premises closed.
Outage | J.E.26.07.00297 | C001837081 | Elvis Trowers | KSAN | Completed | Load_254232 | Constant Spring - 310 | Jul 1, 2026 11:25am | Jul 1, 2026 11:26am | Jul 1, 2026 1:44pm | Jul 1, 2026 1:44pm | Jul 1, 2026 2:02pm | Jul 1, 2026 3:09pm | Jul 1, 2026 3:09pm | Jul 1, 2026 3:09pm |  |  | Fair | Yes | Areas was found without electricity supply when checked and 2 blown junction fuses were found at separate locations, 1/25 amp at pole #0001472 and 1/20 amp at pole #0001473.
Outage | J.E.26.07.00269 | C001837074 | Dwayne Samuels | Trelawny | Completed | Load_248423 | Greenwood - 110 | Jul 1, 2026 11:19am | Jul 1, 2026 11:21am | Jul 1, 2026 11:31am | Jul 1, 2026 11:31am | Jul 1, 2026 11:55am | Jul 1, 2026 11:57am | Jul 1, 2026 12:00pm | Jul 1, 2026 12:00pm |  |  | Fair | No | Customer meter socket is defective customer was advised to get a electrician to have some internal checks done
Outage | J.E.26.07.00245 | C001837072 | Lancelot Brown | Hanover | Completed | Load_245671 | Orange Bay - 310 | Jul 1, 2026 11:16am | Jul 1, 2026 11:18am | Jul 1, 2026 1:57pm | Jul 1, 2026 1:57pm | Jul 1, 2026 2:37pm | Jul 1, 2026 3:24pm | Jul 1, 2026 3:25pm | Jul 1, 2026 3:25pm | BrokenWire |  | Fair | No | Isolate 25kva no pole number splice and retention one span secondary #2 twisted used fifteen feet #2 twisted three pg clamps isolate 25kva supply restore vl at secondary 116-116-232
Outage | J.E.26.07.00288 | C001837071 | Cliton Henry | St.Mary | Completed | Load_351738 | Oracabessa - 110 | Jul 1, 2026 11:15am | Jul 1, 2026 11:16am | Jul 1, 2026 11:45am | Jul 1, 2026 11:46am | Jul 1, 2026 11:54am | Jul 1, 2026 12:06pm | Jul 1, 2026 12:09pm | Jul 1, 2026 12:09pm | TreeContact |  | Fair | No | A leaning concrete CDE 12 meter pole with 2 transformers need to be straightened, the line need bushing both at the entrance gate and the property. Kindly refer to St. Mary Operations for maintenance and vegetation management.
Non-Outage | J.E.26.07.00281 | C001837064 | Raymond Lewis | null | Completed | null | null | Jul 1, 2026 11:11am | Jul 1, 2026 3:25pm | Jul 1, 2026 4:04pm | Jul 1, 2026 4:04pm | Jul 1, 2026 5:17pm | Jul 1, 2026 5:08pm | Jul 1, 2026 5:20pm | Jul 1, 2026 5:20pm |  |  | Fair | No | Supply restored
Outage | J.E.26.07.00284 | C001837059 | Roxroy Needham | St.Ann | Completed | Load_264049 | Cardiff Hall - 310 | Jul 1, 2026 11:10am | Jul 1, 2026 3:21pm | Jul 1, 2026 5:43pm | Jul 1, 2026 5:43pm | Jul 1, 2026 7:22pm | Jul 1, 2026 7:28pm | Jul 1, 2026 7:29pm | Jul 1, 2026 7:29pm | BrokenWire |  | Fair | No | Isolate 25 KVA transformer splice and return 2 span of secondary neutral clean and remake joints at pole using 3 pg clamps and 40 ft of #2 conductor voltage left 117,115,232
Outage | J.E.26.07.00267 | C001837052 | Neville Spencer | Clarendon | Completed | Load_259757 | Parnassus - 310 | Jul 1, 2026 11:03am | Jul 1, 2026 11:04am | Jul 1, 2026 12:44pm | Jul 1, 2026 12:44pm | Jul 1, 2026 1:09pm | Jul 1, 2026 1:09pm | Jul 1, 2026 1:25pm | Jul 1, 2026 1:25pm | TreeContact | Y | Fair | No | Remade broken off phase joint at secondary on 3, wire service used 2, clamps voltage reading 112 114 227 supply restored.
Outage | J.E.26.07.00268 | C001837053 | Hartley Chin | Clarendon | Completed | Load_239995 | Parnassus - 310 | Jul 1, 2026 11:03am | Jul 1, 2026 3:46pm | Jul 1, 2026 3:58pm | Jul 1, 2026 3:58pm | Jul 1, 2026 4:29pm | Jul 1, 2026 4:44pm | Jul 1, 2026 4:48pm | Jul 1, 2026 4:48pm |  |  | Fair | No | Ref to field service !!!! voltage read found on line side of meter 115v , 116v … no voltage read found on load side of meter … meter # 2780573 …
Non-Outage | J.E.26.07.00272 | C001837047 | Roxroy Needham | null | Completed | null | null | Jul 1, 2026 11:00am | Jul 1, 2026 4:02pm | Jul 1, 2026 7:29pm | Jul 1, 2026 7:29pm | Jul 1, 2026 7:29pm | Jul 1, 2026 7:32pm | Jul 1, 2026 7:33pm | Jul 1, 2026 7:33pm | BrokenWire |  | Fair | No | Isolate 25 KVA transformer splice and return 2 span of secondary neutral clean and remake joints at pole using 3 pg clamps and 40 ft of #2 conductor voltage left 117,115,232
Non-Outage | J.E.26.06.37824 | C001837046 | Shamour Haughton | St.James | Completed | Load_248411 | Bogue - 610 | Jul 1, 2026 10:59am | Jul 1, 2026 10:59am | Jul 1, 2026 12:07pm | Jul 1, 2026 12:08pm | Jul 1, 2026 12:42pm | Jul 1, 2026 12:42pm | Jul 1, 2026 12:45pm | Jul 1, 2026 12:45pm |  |  | Fair | No | Check and found okay, voltage left, 111,112,223
Outage | J.E.26.07.00273 | C001837045 | Romaine Roberts | St.Mary | Completed | Load_266672 | Highgate - 210 | Jul 1, 2026 10:59am | Jul 1, 2026 10:59am | Jul 1, 2026 11:51am | Jul 1, 2026 11:51am | Jul 1, 2026 1:02pm | Jul 1, 2026 1:24pm | Jul 1, 2026 1:25pm | Jul 1, 2026 1:25pm | BrokenWire |  | Fair | No | Replace 100 foot of number 6 triplex 3 penunion and 3 clamps
Non-Outage | J.E.26.07.00244 | C001837044 | Swon Miller | St.James | Completed | Load_240097 | Rose Hall - 210 | Jul 1, 2026 10:57am | Jul 1, 2026 10:58am | Jul 1, 2026 1:46pm | Jul 1, 2026 1:46pm | Jul 1, 2026 2:35pm | Jul 7, 2026 2:56am | Jul 1, 2026 3:00pm | Jul 1, 2026 3:00pm | BrokenPole |  | Fair | No | Found one 40ft class six pole with single phase primary and secondary broken below the cable wires pole is inclose with customer fence wall and needs to be replaced plz refer to maintenance
Non-Outage | J.E.26.07.00067 | C001837035 | Neville Spencer | null | Completed | null | null | Jul 1, 2026 10:55am | Jul 1, 2026 10:55am | Jul 1, 2026 11:42am | Jul 1, 2026 11:42am | Jul 1, 2026 11:58am | Jul 1, 2026 11:58am | Jul 1, 2026 12:42pm | Jul 1, 2026 12:42pm |  |  | Fair | No | Found burnt 25 kva xmfr in bank of 2 at pole # 0131441 need to replaced.
Outage | J.E.26.07.00257 | C001837033 | Denton Williams | Portland | Completed | Load_268566 | Port Antonio - 410 | Jul 1, 2026 10:51am | Jul 1, 2026 7:53pm | Jul 1, 2026 8:06pm | Jul 1, 2026 8:06pm | Jul 1, 2026 8:06pm | Jul 1, 2026 8:08pm | Jul 1, 2026 8:19pm | Jul 1, 2026 8:19pm | BrokenWire |  | Fair | No | Due to the nature of our unit being a truck, we’re unable to respond to this emergency call without a smaller pick-up van. Could you please reach out to the emergency supervisor via email or telephone and have him arrange for the Portland Maintenance Team to provide assistance with this repeated call. Urgent attention is required.
Non-Outage | J.E.26.07.00205 | C001837025 | Andre Williams | Trelawny | Completed | Load_413095 | Duncans - 110 | Jul 1, 2026 10:42am | Jul 1, 2026 11:21am | Jul 1, 2026 11:40am | Jul 1, 2026 11:51am | Jul 1, 2026 12:19pm | Jul 1, 2026 12:25pm | Jul 1, 2026 12:26pm | Jul 1, 2026 12:26pm | LowHangingWires |  | Fair | No | Splice and retention broken neutral on customer 3 wire service voltage 115+115=230
Non-Outage | J.E.26.07.00237 | C001837009 | Neville Spencer | null | Completed | null | null | Jul 1, 2026 10:35am | Jul 1, 2026 3:53pm | Jul 1, 2026 3:56pm | Jul 1, 2026 3:56pm | Jul 1, 2026 4:53pm | Jul 1, 2026 5:53pm | Jul 1, 2026 5:59pm | Jul 1, 2026 5:59pm |  |  | Fair | No | Found wooden pole rotten out #2 Triplex on the ground line need maintenance work ,premises closed voltage reading 112+114 226 customer advised.
Outage | J.E.26.07.00231 | C001837008 | Daniel Francis | St.Ann | Completed | Load_242238 | Cardiff Hall - 310 | Jul 1, 2026 10:33am | Jul 1, 2026 10:33am | Jul 1, 2026 11:03am | Jul 1, 2026 11:03am | Jul 1, 2026 12:40pm | Jul 1, 2026 5:48pm | Jul 1, 2026 6:00pm | Jul 1, 2026 6:00pm |  |  | Fair | No | Found primary jumpers burnt remade using 2one bolt 3ft of #2aac near To aski land fill
Outage | J.E.26.07.00229 | C001836994 | Hartley Chin | Clarendon | Completed | Load_253375 | Parnassus - 210 | Jul 1, 2026 10:26am | Jul 1, 2026 3:46pm | Jul 1, 2026 6:59pm | Jul 1, 2026 6:59pm | Jul 1, 2026 8:06pm | Jul 1, 2026 8:28pm | Jul 1, 2026 8:28pm | Jul 1, 2026 8:28pm |  |  | Fair | No | Replace 60 ft service wire … voltage read 11v , 112v … use 4 clamp …
Outage | J.E.26.07.00213 | C001836992 | Hartley Chin | Clarendon | Completed | Load_255421 | Parnassus - 210 | Jul 1, 2026 10:24am | Jul 1, 2026 3:46pm | Jul 1, 2026 6:07pm | Jul 1, 2026 6:41pm | Jul 1, 2026 6:58pm | Jul 1, 2026 6:58pm | Jul 1, 2026 6:59pm | Jul 1, 2026 6:59pm |  |  | Fair | No | Found okay .., voltage read 112v , 110v ..
Non-Outage | J.E.26.03.18434 | C001836985 | Kemark Slue | St.Catherine | Completed | Load_256805 | New Michelton - 310 | Jul 1, 2026 10:20am | Jul 1, 2026 10:22am | Jul 1, 2026 1:17pm | Jul 1, 2026 2:13pm | Jul 1, 2026 2:13pm | Jul 1, 2026 1:49pm | Jul 1, 2026 2:23pm | Jul 1, 2026 2:23pm |  | Y | Fair | No | Upon arrival at the location the crew discovered that 20 amps road phase from three phases at pole # 157984 was blown, further patrol revealed that two large trees are in close proximity to the said conductor that may come in contact with primary phase whenever windy, please refer to A. Murray to have trees cut, refuse link and re-energized line
Outage | J.E.26.07.00201 | C001836978 | Lancelot Brown | Hanover | Completed | Load_244715 | Orange Bay - 310 | Jul 1, 2026 10:12am | Jul 1, 2026 10:13am | Jul 1, 2026 11:24am | Jul 1, 2026 11:50am | Jul 1, 2026 12:54pm | Jul 1, 2026 1:16pm | Jul 1, 2026 1:16pm | Jul 1, 2026 1:16pm |  |  | Fair | No | Customer meter burnt emergency personnel removed wire customer carry out repair on meter socket need supply to reconnected and meter to replace please pass on to field service department in montegobay bay west need ergent attention
Outage | J.E.26.07.00200 | C001836970 | Shamour Haughton | St.James | Completed | Load_240294 | Bogue - 610 | Jul 1, 2026 10:08am | Jul 1, 2026 10:09am | Jul 1, 2026 10:30am | Jul 1, 2026 10:30am | Jul 1, 2026 11:48am | Jul 1, 2026 11:59am | Jul 1, 2026 12:06pm | Jul 1, 2026 12:06pm | BrokenWire |  | Fair | No | Splice and retention customer service wire using 4 clamps and 40ft #6 conductor voltage left 112,113,226
Outage | J.E.26.07.00210 | C001836966 | Donald Cunningham | St.Catherine | Completed | Load_245944 | Rhodens Pen - 210 | Jul 1, 2026 10:04am | Jul 1, 2026 10:05am | Jul 1, 2026 1:18pm | Jul 1, 2026 1:18pm | Jul 1, 2026 1:43pm | Jul 1, 2026 2:20pm | Jul 1, 2026 2:41pm | Jul 1, 2026 2:41pm |  |  | Fair | No | 2 blown junction fuse by entrance to walkers road replace with 25 amp fuse after removing whiss from primary lines
Non-Outage | J.E.26.07.00121 | C001836945 | Richman Whyte | null | Completed | null | null | Jul 1, 2026 9:52am | Jul 1, 2026 9:53am | Jul 1, 2026 11:09am | Jul 1, 2026 11:09am | Jul 1, 2026 11:09am | Jul 1, 2026 11:09am | Jul 1, 2026 11:10am | Jul 1, 2026 11:10am |  |  | Fair | No | Replace 15 amp junction fuse
Outage | J.E.26.07.00194 | C001836935 | Elvis Trowers | KSAN | Completed | Load_248243 | Washington Blvd - 610 | Jul 1, 2026 9:49am | Jul 1, 2026 9:49am | Jul 1, 2026 12:18pm | Jul 1, 2026 12:18pm | Jul 1, 2026 12:43pm | Jul 1, 2026 1:41pm | Jul 1, 2026 1:42pm | Jul 1, 2026 1:42pm |  |  | Fair | Yes | Customer was found having single phasing when checked,problem was left unresolved due to the underground cable can’t be be found and they have no electrical drawings.
Outage | J.E.26.07.00125 | C001836934 | Nickolas Rodriques | Clarendon | Completed | Load_257434 | Parnassus - 210 | Jul 1, 2026 9:48am | Jul 1, 2026 10:23am | Jul 1, 2026 12:22pm | Jul 1, 2026 12:24pm | Jul 1, 2026 1:14pm | Jul 1, 2026 1:51pm | Jul 1, 2026 2:00pm | Jul 1, 2026 2:00pm |  |  | Fair | No | Call relates to the 25 KVA transformer that was found defective. Maintenance team is aware.
Outage | J.E.26.07.00154 | C001836931 | Richman Whyte | Westmoreland | Completed | Load_268839 | Paradise - 310 | Jul 1, 2026 9:46am | Jul 1, 2026 9:52am | Jul 1, 2026 4:18pm | Jul 1, 2026 4:18pm | Jul 1, 2026 4:18pm | Jul 1, 2026 4:18pm | Jul 1, 2026 4:18pm | Jul 1, 2026 4:18pm |  |  | Rains | No | Replace 2 20amp junction fuse
Outage | J.E.26.07.00159 | C001836932 | Richman Whyte | Westmoreland | Completed | Load_267165 | Paradise - 310 | Jul 1, 2026 9:46am | Jul 1, 2026 9:52am | Jul 1, 2026 4:17pm | Jul 1, 2026 4:17pm | Jul 1, 2026 4:17pm | Jul 1, 2026 4:17pm | Jul 1, 2026 4:18pm | Jul 1, 2026 4:18pm |  |  | Rains | No | Replace two 20amp junction fuse
Non-Outage | J.E.26.07.00192 | C001836921 | Neville Spencer | null | Completed | null | null | Jul 1, 2026 9:43am | Jul 1, 2026 9:44am | Jul 1, 2026 10:02am | Jul 1, 2026 10:02am | Jul 1, 2026 10:31am | Jul 1, 2026 10:36am | Jul 1, 2026 11:06am | Jul 1, 2026 11:06am |  |  | Fair | No | Found meter mix up at location Hex # 00814 REF to field service.
Outage | J.E.26.07.00184 | C001836920 | Collin Robinson | Portland | Completed | Load_349991 | Port Antonio - 310 | Jul 1, 2026 9:43am | Jul 1, 2026 9:43am | Jul 1, 2026 10:22am | Jul 1, 2026 10:22am | Jul 1, 2026 11:31am | Jul 1, 2026 11:32am | Jul 1, 2026 11:33am | Jul 1, 2026 11:33am |  |  | Fair | No | Replace 2 corroded pen union at pot head voltage 117 118 235v
Non-Outage | J.E.26.06.38093 | C001836915 | Omar Harris | null | Completed | null | null | Jul 1, 2026 9:36am | Jul 1, 2026 9:36am | Jul 1, 2026 9:46am | Jul 1, 2026 10:30am | Jul 1, 2026 12:12pm | Jul 1, 2026 12:46pm | Jul 1, 2026 12:47pm | Jul 1, 2026 12:47pm |  |  | Fair | No | Retention secondary phase correct single phase at jps pole using 1 one bolt clamp
Outage | J.E.26.06.39292 | C001836908 | Moses Elliston | St.Catherine | Completed | Load_568941 | Twickenham - 310 | Jul 1, 2026 9:35am | Jul 1, 2026 9:36am | Jul 1, 2026 3:13pm | Jul 2, 2026 10:58am | Jul 2, 2026 10:58am | Jul 2, 2026 11:07am | Jul 2, 2026 11:08am | Jul 2, 2026 11:08am |  |  | Fair | No | Customer not at Home.
Non-Outage | J.E.26.06.38014 | C001836901 | Omar Harris | St.Ann | Completed | Load_294711 | Ocho Rios - 310 | Jul 1, 2026 9:30am | Jul 1, 2026 9:33am | Jul 1, 2026 9:46am | Jul 1, 2026 12:48pm | Jul 1, 2026 1:34pm | Jul 1, 2026 1:35pm | Jul 1, 2026 1:35pm | Jul 1, 2026 1:35pm |  |  | Fair | No
Non-Outage | J.E.26.06.38034 | C001836900 | Omar Harris | St.Ann | Completed | Load_246430 | Ocho Rios - 310 | Jul 1, 2026 9:30am | Jul 1, 2026 9:30am | Jul 1, 2026 9:46am | Jul 1, 2026 1:51pm | Jul 1, 2026 1:51pm | Jul 1, 2026 1:51pm | Jul 1, 2026 1:52pm | Jul 1, 2026 1:52pm |  |  | Fair | No | Feeder cycle
Non-Outage | J.E.26.06.38018 | C001836899 | Omar Harris | St.Ann | Completed | Load_243790 | Ocho Rios - 310 | Jul 1, 2026 9:29am | Jul 1, 2026 9:30am | Jul 1, 2026 9:46am | Jul 1, 2026 10:05am | Jul 1, 2026 10:20am | Jul 1, 2026 10:30am | Jul 1, 2026 10:30am | Jul 1, 2026 10:30am |  |  | Fair | No | Feeder cycle
Outage | J.E.26.07.00157 | C001836898 | Tajay Bernard | St.James | Completed | Load_252200 | Bogue - 510 | Jul 1, 2026 9:27am | Jul 1, 2026 9:27am | Jul 1, 2026 10:01am | Jul 1, 2026 10:02am | Jul 1, 2026 10:32am | Jul 1, 2026 1:14pm | Jul 1, 2026 1:25pm | Jul 1, 2026 1:25pm |  |  | Fair | No | Isolate 1 50kva transformer to clean and remake transformer drop Leeds ( phase and neutral), and also remake jumpers at 4 poles use 7 clampsVoltage found 112/98/210Voltage left 116/116/232
Non-Outage | J.E.26.06.34017 | C001836892 | Milton Charlton | null | Completed | null | null | Jul 1, 2026 9:25am | Jul 1, 2026 9:26am | Jul 1, 2026 11:46am | Jul 1, 2026 11:46am | Jul 1, 2026 1:12pm | Jul 1, 2026 1:10pm | Jul 1, 2026 1:15pm | Jul 1, 2026 1:15pm | BrokenWire |  | Fair | No | Found okay upon arrival. Matter was resolved.
Non-Outage | J.E.26.06.33634 | C001836891 | Milton Charlton | null | Completed | null | null | Jul 1, 2026 9:24am | Jul 1, 2026 9:26am | Jul 1, 2026 11:16am | Jul 1, 2026 11:16am | Jul 1, 2026 11:44am | Jul 1, 2026 11:45am | Jul 1, 2026 11:46am | Jul 1, 2026 11:46am | Fire |  | Fair | No | A the time of visit no visible fire was seen. Found okay upon arrival.
Outage | J.E.26.07.00151 | C001836890 | Horace Malcolm | St.James | Completed | Load_244424 | Bogue - 310 | Jul 1, 2026 9:24am | Jul 1, 2026 9:25am | Jul 1, 2026 1:40pm | Jul 1, 2026 1:40pm | Jul 1, 2026 1:41pm | Jul 1, 2026 1:50pm | Jul 1, 2026 1:50pm | Jul 1, 2026 1:50pm |  |  | Fair | No | Call belongs to trelawny
Outage | J.E.26.07.00163 | C001836884 | Richard Nicholas | St.Catherine | Completed | Load_557180 | Tredegar - 410 | Jul 1, 2026 9:19am | Jul 1, 2026 4:02pm | Jul 1, 2026 4:59pm | Jul 1, 2026 4:59pm | Jul 1, 2026 6:07pm | Jul 1, 2026 6:34pm | Jul 1, 2026 6:38pm | Jul 1, 2026 6:38pm | BrokenWire |  | Fair | No | No one at the premises when the crew arrived however during a telephone conversation with customer she was advised to get a private electrician to repair the pothead.rammy system at the premises however the pothead conduit loosen from off the wall as a result service wire from Rammy box to pothead become saggy.
Non-Outage | J.E.26.04.15732 | C001836883 | Horace Malcolm | St.James | Completed | Load_557022 | Bogue - 310 | Jul 1, 2026 9:17am | Jul 1, 2026 9:17am | Jul 1, 2026 9:37am | Jul 1, 2026 10:02am | Jul 1, 2026 10:02am | Jul 1, 2026 10:29am | Jul 1, 2026 10:29am | Jul 1, 2026 10:29am |  |  | Fair | No | Splice and retention customer service wire used 10ft #6 triplex wire and 1clamp voltage 117-116-233
Non-Outage | J.E.26.06.31908 | C001836882 | Horace Malcolm | St.James | Completed | Load_241536 | Bogue - 310 | Jul 1, 2026 9:16am | Jul 1, 2026 9:17am | Jul 1, 2026 12:02pm | Jul 1, 2026 12:02pm | Jul 1, 2026 1:23pm | Jul 1, 2026 1:40pm | Jul 1, 2026 1:40pm | Jul 1, 2026 1:40pm | LeaningPole |  | Fair | No | Found retired wooden pole leaning down with cable wires no jps wires attached to pole
Non-Outage | J.E.26.06.32192 | C001836881 | Horace Malcolm | St.James | Completed | Load_576009 | Bogue - 310 | Jul 1, 2026 9:16am | Jul 1, 2026 9:17am | Jul 1, 2026 10:30am | Jul 1, 2026 10:30am | Jul 1, 2026 10:37am | Jul 1, 2026 11:07am | Jul 1, 2026 11:07am | Jul 1, 2026 11:07am |  |  | Fair | No | Check and found ok supply restored voltage 117-115-232
Non-Outage | J.E.26.06.32724 | C001836880 | Horace Malcolm | St.James | Completed | Load_267602 | Bogue - 310 | Jul 1, 2026 9:16am | Jul 1, 2026 9:17am | Jul 1, 2026 9:30am | Jul 1, 2026 11:07am | Jul 1, 2026 11:56am | Jul 1, 2026 11:58am | Jul 1, 2026 11:58am | Jul 1, 2026 11:58am |  |  | Fair | No | Unable to locate customer or premises multiple calls to customer unavailable
Outage | J.E.26.06.39839 | C001836866 | Marlon Authors | St.Elizabeth | Completed | Load_292396 | Maggotty - 210 | Jul 1, 2026 9:10am | Jul 1, 2026 9:11am | Jul 1, 2026 1:05pm | Jul 1, 2026 1:12pm | Jul 1, 2026 2:15pm | Jul 1, 2026 2:26pm | Jul 1, 2026 2:26pm | Jul 1, 2026 2:26pm |  |  | Fair | No | Patrol and found clear. Replace one blown 8 amp junction fuse at pole #146840. Restored supply ok
Non-Outage | J.E.26.06.38047 | C001836864 | Fitzroy Turner | KSAS | Completed | Load_251977 | Hunts Bay - 710 | Jul 1, 2026 9:09am | Jul 1, 2026 4:07pm | Jul 1, 2026 7:40pm | Jul 1, 2026 7:43pm | Jul 1, 2026 8:15pm | Jul 1, 2026 8:24pm | Jul 1, 2026 8:26pm | Jul 1, 2026 8:26pm |  |  | Fair | No | Found 4 wire service phase burnt off at transformer pole use one clamp to carry out repair supply restored to customer
Outage | J.E.26.07.00060 | C001836865 | Marlon Authors | St.Elizabeth | Completed | Load_252231 | Maggotty - 210 | Jul 1, 2026 9:09am | Jul 1, 2026 9:11am | Jul 1, 2026 11:15am | Jul 1, 2026 11:15am | Jul 1, 2026 12:41pm | Jul 1, 2026 12:52pm | Jul 1, 2026 12:52pm | Jul 1, 2026 12:52pm | Fire |  | Fair | No | Supply checked and found customer pothead wires burnt. Disconnect same at pothead, no one seen at location at the time of visit
Non-Outage | J.E.26.06.29210 | C001836857 | Odeanie Davis | KSAS | Completed | Load_256911 | Hunts Bay - 510 | Jul 1, 2026 9:02am | Jul 1, 2026 9:07am | Jul 1, 2026 9:16am | Jul 1, 2026 12:36pm | Jul 1, 2026 12:36pm | Jul 1, 2026 12:43pm | Jul 1, 2026 12:36pm | Jul 1, 2026 12:36pm |  |  | Fair | No | Customer stated that issue was resolved
Non-Outage | J.E.26.06.39737 | C001836856 | Odeanie Davis | KSAS | Completed | Load_260200 | Hunts Bay - 310 | Jul 1, 2026 9:02am | Jul 1, 2026 9:07am | Jul 1, 2026 1:01pm | Jul 1, 2026 1:01pm | Jul 1, 2026 1:02pm | Jul 1, 2026 1:18pm | Jul 1, 2026 1:18pm | Jul 1, 2026 1:18pm |  |  | Fair | No | 118v/119v & 238v at premise, defective wire at pothead, leaning pole at location, customer was advised to contact their electrician.
Non-Outage | J.E.26.06.23059 | C001836849 | Odeanie Davis | KSAS | Completed | Load_268943 | Hunts Bay - 310 | Jul 1, 2026 9:01am | Jul 1, 2026 9:07am | Jul 1, 2026 9:16am | Jul 1, 2026 9:36am | Jul 1, 2026 9:36am | Jul 1, 2026 9:41am | Jul 1, 2026 9:41am | Jul 1, 2026 9:41am |  |  | Fair | No | Customer stated that issue was resolved resolved
Non-Outage | J.E.26.06.23653 | C001836846 | Odeanie Davis | KSAS | Completed | Load_244263 | Hunts Bay - 210 | Jul 1, 2026 9:01am | Jul 1, 2026 9:07am | Jul 1, 2026 9:16am | Jul 1, 2026 10:39am | Jul 1, 2026 10:39am | Jul 1, 2026 10:57am | Jul 1, 2026 10:57am | Jul 1, 2026 10:57am |  |  | Fair | No | Meter found burnt, meter needs to be replaced, field service team needed.
Non-Outage | J.E.26.06.31964 | C001836848 | Odeanie Davis | KSAS | Completed | Load_244263 | Hunts Bay - 210 | Jul 1, 2026 9:01am | Jul 1, 2026 9:07am | Jul 1, 2026 9:16am | Jul 1, 2026 11:37am | Jul 1, 2026 11:41am | Jul 1, 2026 12:10pm | Jul 1, 2026 12:10pm | Jul 1, 2026 12:10pm |  |  | Fair | No | 115v/116v & 232v, 203v on 190 phase, 3 phase secondary line needs to be replaced, wire is sheathing and needs emergency team
Non-Outage | J.E.26.06.32215 | C001836850 | Odeanie Davis | KSAS | Completed | Load_255002 | Hunts Bay - 310 | Jul 1, 2026 9:01am | Jul 1, 2026 9:07am | Jul 1, 2026 1:21pm | Jul 1, 2026 3:00pm | Jul 1, 2026 3:00pm | Jul 1, 2026 3:24pm | Jul 1, 2026 3:24pm | Jul 1, 2026 3:24pm |  |  | Fair | No | 115v/111v at arrival, open circuit at secondary corrected, 3 one bolt clamps,115v/116v & 232v after correction.
Non-Outage | J.E.26.06.32877 | C001836847 | Odeanie Davis | KSAS | Completed | Load_570293 | Hunts Bay - 210 | Jul 1, 2026 9:01am | Jul 1, 2026 9:07am | Jul 1, 2026 9:16am | Jul 1, 2026 12:15pm | Jul 1, 2026 12:15pm | Jul 1, 2026 12:35pm | Jul 1, 2026 12:36pm | Jul 1, 2026 12:36pm |  |  | Fair | No | 117v/119v & 236v, 207v on 190 phase at arrival, high voltage 120v/121v confirmed from back off, customer stated that after the word day ends the voltage rises to 249v access phases, emergency team needed
Non-Outage | J.E.26.06.33577 | C001836851 | Odeanie Davis | KSAS | Completed | Load_245309 | Hunts Bay - 310 | Jul 1, 2026 9:01am | Jul 1, 2026 9:07am | Jul 1, 2026 12:59pm | Jul 1, 2026 12:59pm | Jul 1, 2026 12:59pm | Jul 1, 2026 1:01pm | Jul 1, 2026 1:01pm | Jul 1, 2026 1:01pm |  |  | Fair | No | Customer stated that the issue was resolved
Non-Outage | J.E.26.06.33944 | C001836852 | Odeanie Davis | KSAS | Completed | Load_267297 | Hunts Bay - 310 | Jul 1, 2026 9:01am | Jul 1, 2026 9:07am | Jul 1, 2026 9:16am | Jul 1, 2026 9:43am | Jul 1, 2026 9:47am | Jul 1, 2026 10:28am | Jul 1, 2026 10:28am | Jul 1, 2026 10:28am |  |  | Fair | No | 117v/117v & 235v , 108v on 190 phase, corrosion on transformer top lug needs to be cleaned, bucket truck needed
Non-Outage | J.E.26.06.34271 | C001836853 | Odeanie Davis | KSAS | Completed | Load_257789 | Hunts Bay - 310 | Jul 1, 2026 9:01am | Jul 1, 2026 9:07am | Jul 1, 2026 1:21pm | Jul 1, 2026 1:59pm | Jul 1, 2026 2:06pm | Jul 1, 2026 3:00pm | Jul 1, 2026 3:00pm | Jul 1, 2026 3:00pm |  |  | Fair | No | 110v at arrival, open circuit at secondary corrected, 1 one bolt clamp, 117v after correction
Non-Outage | J.E.26.06.35138 | C001836854 | Odeanie Davis | KSAS | Completed | Load_267297 | Hunts Bay - 310 | Jul 1, 2026 9:01am | Jul 1, 2026 9:07am | Jul 1, 2026 9:16am | Jul 1, 2026 10:29am | Jul 1, 2026 10:29am | Jul 1, 2026 10:39am | Jul 1, 2026 10:32am | Jul 1, 2026 10:32am |  |  | Fair | No | 117v/117v & 235v , 108v on 190 phase, corrosion on transformer top lug needs to be cleaned, bucket truck needed
Non-Outage | J.E.26.06.35360 | C001836855 | Odeanie Davis | KSAS | Completed | Load_258696 | Hunts Bay - 310 | Jul 1, 2026 9:01am | Jul 1, 2026 9:07am | Jul 1, 2026 1:21pm | Jul 1, 2026 1:21pm | Jul 1, 2026 1:25pm | Jul 1, 2026 1:51pm | Jul 1, 2026 1:54pm | Jul 1, 2026 1:54pm |  |  | Fair | No | 99v/136v & 236v from secondary line, bucket truck needed, transformer team needed,
Non-Outage | J.E.26.06.34219 | C001836833 | Shamour Haughton | Trelawny | Completed | Load_238624 | Greenwood - 210 | Jul 1, 2026 8:40am | Jul 2, 2026 8:21am | Jul 2, 2026 9:28am | Jul 2, 2026 9:28am | Jul 2, 2026 9:41am | Jul 2, 2026 9:41am | Jul 2, 2026 9:56am | Jul 2, 2026 9:56am | LeaningPole |  | Fair | No | Customer is saying that report was rectified
Non-Outage | J.E.26.06.36626 | C001836828 | Lancelot Brown | Hanover | Completed | Load_302748 | Orange Bay - 310 | Jul 1, 2026 8:25am | Jul 1, 2026 8:25am | Jul 1, 2026 11:24am | Jul 1, 2026 11:24am | Jul 1, 2026 11:42am | Jul 1, 2026 11:47am | Jul 1, 2026 11:48am | Jul 1, 2026 11:48am |  |  | Fair | No | Check and found customer meter lug burnt meter need to replace please pass on field service department in montegobay bay west need ergent attention vl at meter 115-115-230 meter socket was also diffective repair carry out meter need to replace
Non-Outage | J.E.26.06.39389 | C001836827 | Dean Smith | Hanover | Completed | Load_292700 | Orange Bay - 310 | Jul 1, 2026 8:24am | Jul 2, 2026 7:46am | Jul 2, 2026 8:08am | Jul 2, 2026 10:15am | Jul 2, 2026 10:15am | Jul 2, 2026 10:15am | Jul 2, 2026 11:25am | Jul 2, 2026 11:25am |  | Y | Fair | No | Found #6 triplex service pain broken off at jps pole . Reconnected same. Voltage left 115v,115v,230v.
Outage | J.E.26.07.00129 | C001836826 | Andre Williams | Trelawny | Completed | Load_302607 | Martha Brae - 210 | Jul 1, 2026 8:21am | Jul 1, 2026 8:21am | Jul 1, 2026 9:13am | Jul 1, 2026 9:13am | Jul 1, 2026 9:37am | Jul 1, 2026 9:37am | Jul 1, 2026 9:38am | Jul 1, 2026 9:38am |  |  | Fair | No | Power was restored to premises
Non-Outage | J.E.26.06.37099 | C001836825 | Andrae Dawkins | St.James | Completed | Load_247453 | Queens Drive - 710 | Jul 1, 2026 8:19am | Jul 1, 2026 8:21am | Jul 1, 2026 9:15am | Jul 1, 2026 10:22am | Jul 1, 2026 10:34am | Jul 1, 2026 11:14am | Jul 1, 2026 11:17am | Jul 1, 2026 11:17am |  |  | Fair | No | Found customer experiencing low voltage due to contamination at pole and pot head clean and remade joints used 3 pg clamp voltage found 67/162/229 voltage left 114/114/229
Non-Outage | J.E.26.06.37789 | C001836824 | Andrae Dawkins | St.James | Completed | Load_238334 | Queens Drive - 710 | Jul 1, 2026 8:19am | Jul 1, 2026 8:20am | Jul 1, 2026 9:15am | Jul 1, 2026 11:40am | Jul 1, 2026 11:40am | Jul 1, 2026 1:00pm | Jul 1, 2026 1:06pm | Jul 1, 2026 1:06pm |  |  | Fair | No | Found customer neutral and phase broken due to vehicle accident spliced and retention service wire voltage find 114/28/167 voltage left 116/116/233
Non-Outage | J.E.26.06.38043 | C001836821 | Andrae Dawkins | St.James | Completed | Load_260155 | Queens Drive - 710 | Jul 1, 2026 8:19am | Jul 1, 2026 8:19am | Jul 1, 2026 1:11pm | Jul 2, 2026 8:16am | Jul 2, 2026 10:22am | Jul 2, 2026 11:06am | Jul 2, 2026 11:10am | Jul 2, 2026 11:10am |  |  | Fair | No | Found customer single phasing due to corrosion at pole clean and remade joints voltage left109/116/226
Non-Outage | J.E.26.06.38091 | C001836822 | Andrae Dawkins | St.James | Completed | Load_238603 | Queens Drive - 710 | Jul 1, 2026 8:19am | Jul 1, 2026 8:19am | Jul 1, 2026 1:11pm | Jul 1, 2026 1:49pm | Jul 1, 2026 1:50pm | Jul 1, 2026 1:46pm | Jul 1, 2026 1:52pm | Jul 1, 2026 1:52pm |  |  | Fair | No | Check and found okay customer said that they didn’t make any report
Non-Outage | J.E.26.06.38096 | C001836818 | Andrae Dawkins | St.James | Completed | Load_259518 | Queens Drive - 710 | Jul 1, 2026 8:19am | Jul 1, 2026 8:19am | Jul 1, 2026 1:11pm | Jul 1, 2026 1:44pm | Jul 1, 2026 1:44pm | Jul 1, 2026 1:46pm | Jul 1, 2026 1:47pm | Jul 1, 2026 1:47pm |  |  | Fair | No | Check and found okay customer said that they didn’t make any report
Non-Outage | J.E.26.06.38098 | C001836819 | Andrae Dawkins | St.James | Completed | Load_241044 | Queens Drive - 710 | Jul 1, 2026 8:19am | Jul 1, 2026 8:19am | Jul 1, 2026 1:11pm | Jul 1, 2026 1:47pm | Jul 1, 2026 1:47pm | Jul 1, 2026 1:46pm | Jul 1, 2026 1:48pm | Jul 1, 2026 1:48pm |  |  | Fair | No
Non-Outage | J.E.26.06.38100 | C001836816 | Andrae Dawkins | St.James | Completed | Load_259518 | Queens Drive - 710 | Jul 1, 2026 8:19am | Jul 1, 2026 8:19am | Jul 2, 2026 11:11am | Jul 2, 2026 11:11am | Jul 2, 2026 11:13am | Jul 2, 2026 11:16am | Jul 2, 2026 11:17am | Jul 2, 2026 11:17am |  |  | Fair | No | Check and found ok customer said that they didn’t make any report
Non-Outage | J.E.26.06.38853 | C001836817 | Andrae Dawkins | St.James | Completed | Load_253530 | Queens Drive - 710 | Jul 1, 2026 8:19am | Jul 1, 2026 8:19am | Jul 1, 2026 2:18pm | Jul 1, 2026 2:18pm | Jul 1, 2026 2:18pm | Jul 1, 2026 3:13pm | Jul 1, 2026 3:15pm | Jul 1, 2026 3:15pm |  |  | Fair | No | Found customer single phasing due to corrosion at pole clean and remade joints voltage found 112/66/157 voltage left 112/115/227
Non-Outage | J.E.26.06.38921 | C001836815 | Andrae Dawkins | St.James | Completed | Load_252784 | Queens Drive - 710 | Jul 1, 2026 8:19am | Jul 1, 2026 8:19am | Jul 2, 2026 12:38pm | Jul 2, 2026 12:45pm | Jul 2, 2026 12:48pm | Jul 2, 2026 1:55pm | Jul 2, 2026 1:58pm | Jul 2, 2026 1:58pm |  |  | Fair | No | Found customer single phasing due to corrosion at pole and pothead clean and remade joints used one pg clamp voltage found 114/90/197 voltage left 115/116/231
Non-Outage | J.E.26.06.39012 | C001836811 | Andrae Dawkins | St.James | Completed | Load_250208 | Queens Drive - 710 | Jul 1, 2026 8:18am | Jul 1, 2026 8:19am | Jul 2, 2026 11:35am | Jul 2, 2026 11:42am | Jul 2, 2026 11:43am | Jul 2, 2026 11:26am | Jul 2, 2026 11:46am | Jul 2, 2026 11:46am |  |  | Fair | No | Cannot locate unable to reach customer’s mobile phone
Non-Outage | J.E.26.06.39227 | C001836808 | Andrae Dawkins | St.James | Completed | Load_240182 | Queens Drive - 710 | Jul 1, 2026 8:18am | Jul 1, 2026 8:19am | Jul 2, 2026 11:49am | Jul 2, 2026 11:49am | Jul 2, 2026 12:10pm | Jul 2, 2026 12:28pm | Jul 2, 2026 12:32pm | Jul 2, 2026 12:32pm |  |  | Fair | No | Found customer experiencing on and off supply due to corrosion at pothead clean and remade joints use 2 red to red linket and 1 pg clamp voltage left 117/117/234
Non-Outage | J.E.26.06.39466 | C001836810 | Romaine Roberts | St.Mary | Completed | Load_249031 | Highgate - 210 | Jul 1, 2026 8:18am | Jul 1, 2026 8:20am | Jul 1, 2026 8:24am | Jul 1, 2026 8:24am | Jul 1, 2026 9:49am | Jul 1, 2026 9:50am | Jul 1, 2026 9:50am | Jul 1, 2026 9:50am |  |  | Fair | No | Found ok call was complete from 30/June/2026
Non-Outage | J.E.26.06.39681 | C001836809 | Romaine Roberts | St.Mary | Completed | Load_249380 | Highgate - 210 | Jul 1, 2026 8:18am | Jul 1, 2026 8:20am | Jul 1, 2026 9:50am | Jul 1, 2026 9:50am | Jul 1, 2026 10:42am | Jul 1, 2026 10:43am | Jul 1, 2026 10:44am | Jul 1, 2026 10:44am |  |  | Fair | No | Cannot reach customer by phone insufficient direction
Non-Outage | J.E.26.06.33897 | C001836807 | Moses Elliston | Portmore | Completed | Load_412903 | Naggo Head - 510 | Jul 1, 2026 8:17am | Jul 1, 2026 8:17am | Jul 1, 2026 11:38am | Jul 1, 2026 11:42am | Jul 1, 2026 11:42am | Jul 1, 2026 1:59pm | Jul 1, 2026 2:04pm | Jul 1, 2026 2:04pm |  |  | Fair | No | Corroaded 25 kva transformer # RO 15132 secondary neutral ampact,1 clamp used.Other joints to be rectify due to salt spray.Refer to Operations.
Non-Outage | J.E.26.06.32903 | C001836804 | Junior Scarlett | St.James | Completed | Load_260651 | Bogue - 310 | Jul 1, 2026 8:16am | Jul 1, 2026 8:16am | Jul 1, 2026 8:21am | Jul 1, 2026 8:29am | Jul 1, 2026 9:07am | Jul 1, 2026 9:20am | Jul 1, 2026 9:18am | Jul 1, 2026 9:18am |  |  | Fair | No | Check and found okVoltage found 113v 113v 226v
Non-Outage | J.E.26.06.33228 | C001836803 | Junior Scarlett | St.James | Completed | Load_254869 | Bogue - 310 | Jul 1, 2026 8:16am | Jul 1, 2026 8:16am | Jul 1, 2026 8:21am | Jul 1, 2026 1:15pm | Jul 1, 2026 2:46pm | Jul 1, 2026 3:14pm | Jul 1, 2026 3:14pm | Jul 1, 2026 3:14pm |  |  | Fair | No | Unable to locate premises Voltage from transformer 114v 115v 229v
Non-Outage | J.E.26.06.39938 | C001836802 | Junior Scarlett | St.James | Completed | Load_1003256 | Bogue - 310 | Jul 1, 2026 8:15am | Jul 1, 2026 8:16am | Jul 1, 2026 8:21am | Jul 1, 2026 10:47am | Jul 1, 2026 11:01am | Jul 1, 2026 11:53am | Jul 1, 2026 11:53am | Jul 1, 2026 11:53am |  |  | Fair | No | Check and found okVoltage found 113v 113v 226vVoltage leave 113v 113v 226v
Non-Outage | J.E.26.06.39958 | C001836801 | Junior Scarlett | St.James | Completed | Load_1003256 | Bogue - 310 | Jul 1, 2026 8:15am | Jul 1, 2026 8:16am | Jul 1, 2026 8:21am | Jul 1, 2026 9:29am | Jul 1, 2026 9:48am | Jul 1, 2026 10:34am | Jul 1, 2026 10:47am | Jul 1, 2026 10:47am |  |  | Fair | No | Install on clamp o poleVoltage found 113v 113v 226Voltage found 113v 113v 226vJob completed
Non-Outage | J.E.26.07.00016 | C001836800 | Junior Scarlett | St.James | Completed | Load_1003257 | Bogue - 310 | Jul 1, 2026 8:15am | Jul 1, 2026 8:16am | Jul 1, 2026 8:21am | Jul 1, 2026 11:54am | Jul 1, 2026 12:20pm | Jul 1, 2026 12:39pm | Jul 1, 2026 12:39pm | Jul 1, 2026 12:39pm |  |  | Fair | No | Check and found okVoltage found 114v 113v 227vVoltage leave 114v 113v 227v
Non-Outage | J.E.26.06.38795 | C001836797 | Roemello Brown | Trelawny | Completed | Load_293110 | Greenwood - 210 | Jul 1, 2026 8:14am | Jul 1, 2026 8:14am | Jul 1, 2026 10:42am | Jul 1, 2026 12:33pm | Jul 1, 2026 12:47pm | Jul 1, 2026 12:47pm | Jul 1, 2026 12:48pm | Jul 1, 2026 12:48pm |  |  | Fair | No | Needs more direction went to the area no one knows the person also phone number provided went straight to voicemail
Non-Outage | J.E.26.06.38822 | C001836795 | Roemello Brown | Trelawny | Completed | Load_293110 | Greenwood - 210 | Jul 1, 2026 8:14am | Jul 1, 2026 8:14am | Jul 1, 2026 12:23pm | Jul 1, 2026 12:48pm | Jul 1, 2026 1:43pm | Jul 1, 2026 1:43pm | Jul 1, 2026 1:45pm | Jul 1, 2026 1:45pm |  |  | Fair | No | Went to the area no one knows the person need proper directions also phone number provided went straight to voicemail
Non-Outage | J.E.26.06.39086 | C001836799 | Tyrese Williams | St.Ann | Completed | Load_260568 | Cardiff Hall - 310 | Jul 1, 2026 8:14am | Jul 1, 2026 8:15am | Jul 1, 2026 9:11am | Jul 1, 2026 10:06am | Jul 1, 2026 10:17am | Jul 1, 2026 10:18am | Jul 1, 2026 10:18am | Jul 1, 2026 10:18am |  |  | Fair | No | Premises Found ok
Non-Outage | J.E.26.06.39247 | C001836794 | Roemello Brown | Trelawny | Completed | Load_244593 | Greenwood - 110 | Jul 1, 2026 8:14am | Jul 1, 2026 8:14am | Jul 2, 2026 10:53am | Jul 2, 2026 10:53am | Jul 2, 2026 12:15pm | Jul 2, 2026 12:16pm | Jul 2, 2026 12:21pm | Jul 2, 2026 12:21pm |  |  | Fair | No | Corrosion at the pole side and at pothead have clamps changed Voltage found 109/111/220Voltage leave 113/113/226
Non-Outage | J.E.26.06.39896 | C001836796 | Roemello Brown | Trelawny | Completed | Load_257511 | Martha Brae - 210 | Jul 1, 2026 8:14am | Jul 1, 2026 8:14am | Jul 1, 2026 8:25am | Jul 1, 2026 8:31am | Jul 1, 2026 8:31am | Jul 1, 2026 8:31am | Jul 1, 2026 9:31am | Jul 1, 2026 9:31am |  |  | Fair | No | Corrosion at the pole have clamps change Voltage found 123/84/207Voltage leave 122/122/244
Non-Outage | J.E.26.07.00128 | C001836798 | Andre Williams | Trelawny | Completed | Load_251680 | Martha Brae - 210 | Jul 1, 2026 8:14am | Jul 1, 2026 8:14am | Jul 1, 2026 9:09am | Jul 1, 2026 9:09am | Jul 1, 2026 9:09am | Jul 1, 2026 8:39am | Jul 1, 2026 9:12am | Jul 1, 2026 9:12am |  |  | Fair | No | Re make burnt of joint at pothead voltage 115+113=228
Non-Outage | J.E.26.06.34254 | C001836791 | Neville Spencer | Clarendon | Completed | Load_249062 | Parnassus - 310 | Jul 1, 2026 8:13am | Jul 1, 2026 8:13am | Jul 1, 2026 11:13am | Jul 1, 2026 11:13am | Jul 1, 2026 11:36am | Jul 1, 2026 11:37am | Jul 1, 2026 11:38am | Jul 1, 2026 11:38am | Fire |  | Fair | No | Found ok call resolved.
Non-Outage | J.E.26.06.39769 | C001836793 | Tyrese Williams | St.Ann | Completed | Load_268325 | Cardiff Hall - 310 | Jul 1, 2026 8:13am | Jul 1, 2026 8:14am | Jul 1, 2026 10:06am | Jul 1, 2026 10:19am | Jul 1, 2026 11:23am | Jul 1, 2026 11:24am | Jul 1, 2026 11:24am | Jul 1, 2026 11:24am |  |  | Fair | No | Premises found ok voltage check 117/117/234
Outage | J.E.26.07.00126 | C001836792 | Edward Royal | KSAN | Completed | Load_238618 | Hope - 510 | Jul 1, 2026 8:13am | Jul 1, 2026 8:14am | Jul 1, 2026 12:54pm | Jul 1, 2026 1:02pm | Jul 1, 2026 1:03pm | Jul 1, 2026 1:03pm | Jul 1, 2026 1:04pm | Jul 1, 2026 1:04pm |  |  | Fair | No | Call related
Outage | J.E.26.06.39595 | C001836790 | Milton Charlton | KSAN | Completed | Load_575407 | Washington Blvd - 710 | Jul 1, 2026 8:11am | Jul 1, 2026 8:12am | Jul 1, 2026 9:22am | Jul 1, 2026 9:41am | Jul 1, 2026 10:18am | Jul 1, 2026 10:00am | Jul 1, 2026 10:19am | Jul 1, 2026 10:19am |  |  | Fair | No | Found okay upon arrival.matter was resolved.
Outage | J.E.26.06.39943 | C001836789 | Milton Charlton | KSAN | Completed | Load_255789 | Washington Blvd - 310 | Jul 1, 2026 8:11am | Jul 1, 2026 8:12am | Jul 1, 2026 10:58am | Jul 1, 2026 11:15am | Jul 1, 2026 11:15am | Jul 1, 2026 11:20am | Jul 1, 2026 11:16am | Jul 1, 2026 11:16am |  |  | Fair | No | Call related to call at #4 Balcombe Avenue.
Non-Outage | J.E.26.07.00071 | C001836788 | Omar Harris | null | Completed | null | null | Jul 1, 2026 8:10am | Jul 1, 2026 8:11am | Jul 1, 2026 8:21am | Jul 1, 2026 8:21am | Jul 1, 2026 9:44am | Jul 1, 2026 9:44am | Jul 1, 2026 9:45am | Jul 1, 2026 9:45am |  |  | Fair | No | Outage in may pen
Non-Outage | J.E.26.06.39611 | C001836787 | Daniel Francis | St.Ann | Completed | Load_256166 | Cardiff Hall - 310 | Jul 1, 2026 8:07am | Jul 1, 2026 8:08am | Jul 1, 2026 10:41am | Jul 1, 2026 10:41am | Jul 1, 2026 10:47am | Jul 1, 2026 10:50am | Jul 1, 2026 10:58am | Jul 1, 2026 10:58am | LeaningPole |  | Fair | No | Pole needs to be change 100%decay conducter holding pole 30/c6 pole secondary only tee construction
Non-Outage | J.E.26.06.39495 | C001836786 | Fredrick Hamilton | KSAN | Completed | Load_267909 | Constant Spring - 410 | Jul 1, 2026 8:04am | Jul 1, 2026 8:05am | Jul 1, 2026 8:18am | Jul 1, 2026 8:29am | Jul 1, 2026 8:29am | Jul 1, 2026 8:31am | Jul 1, 2026 8:31am | Jul 1, 2026 8:31am |  |  | Fair | No | Customer contacted and stated that power was restored fully last night in area Premises is ok
Non-Outage | J.E.26.06.39688 | C001836783 | Fredrick Hamilton | KSAN | Completed | Load_261271 | Constant Spring - 410 | Jul 1, 2026 8:04am | Jul 1, 2026 8:05am | Jul 1, 2026 8:18am | Jul 1, 2026 8:43am | Jul 1, 2026 8:44am | Jul 1, 2026 8:45am | Jul 1, 2026 8:45am | Jul 1, 2026 8:45am |  |  | Fair | No | Customer contacted and stated power was restored fully yesterday Premises is ok
Outage | J.E.26.07.00111 | C001836782 | Omar King | St.Ann | Completed | Load_248186 | Ocho Rios - 510 | Jul 1, 2026 8:04am | Jul 1, 2026 8:04am | Jul 1, 2026 8:45am | Jul 1, 2026 8:45am | Jul 1, 2026 9:36am | Jul 1, 2026 9:39am | Jul 1, 2026 9:40am | Jul 1, 2026 9:40am | LeakingTransformer |  | Fair | No | Found a 15 amp junction fuse blow cause by bird fuse as been replaced area is now with supply
Non-Outage | J.E.26.06.21038 | C001836781 | Odaine Johnson | null | Completed | null | null | Jul 1, 2026 8:03am | Jul 1, 2026 8:03am | Jul 1, 2026 9:11am | Jul 1, 2026 11:50am | Jul 1, 2026 11:50am | Jul 1, 2026 11:50am | Jul 1, 2026 11:50am | Jul 1, 2026 11:50am |  |  | Fair | No | Customer said problem was resolved
Non-Outage | J.E.26.06.35792 | C001836780 | Odaine Johnson | Clarendon | Completed | Load_264794 | Monymusk - 410 | Jul 1, 2026 8:02am | Jul 1, 2026 8:03am | Jul 1, 2026 9:10am | Jul 1, 2026 10:37am | Jul 1, 2026 10:37am | Jul 1, 2026 10:38am | Jul 1, 2026 10:39am | Jul 1, 2026 10:39am | 18765367761 |  | Fair | No | Premises found okay voltage reading 110/115/226 volts customer contact number 18765367761
Non-Outage | J.E.26.06.39528 | C001836779 | Andrae Clarke | Portland | Completed | Load_352955 | Port Antonio - 310 | Jul 1, 2026 8:02am | Jul 1, 2026 8:13am | Jul 1, 2026 9:15am | Jul 1, 2026 9:16am | Jul 1, 2026 11:32am | Jul 1, 2026 11:28am | Jul 1, 2026 11:35am | Jul 1, 2026 11:35am |  |  | Fair | No | Check voltage 120/120/208/241Transformer lead to secondary needs cleaning Emergency crew needed
Non-Outage | J.E.26.07.00067 | C001836778 | Odaine Johnson | null | Completed | null | null | Jul 1, 2026 8:02am | Jul 1, 2026 8:03am | Jul 1, 2026 9:10am | Jul 1, 2026 10:54am | Jul 1, 2026 10:54am | Jul 1, 2026 10:54am | Jul 1, 2026 10:55am | Jul 1, 2026 10:55am |  |  | Fair | No | Transformer phase blown pole number 0131441 need a switcher
Non-Outage | J.E.26.06.04694 | C001836769 | Royston Montague | St.Catherine | Completed | Load_261629 | Tredegar - 410 | Jul 1, 2026 8:01am | Jul 1, 2026 8:02am | Jul 1, 2026 8:17am | Jul 1, 2026 10:32am | Jul 1, 2026 10:32am | Jul 1, 2026 10:38am | Jul 1, 2026 10:38am | Jul 1, 2026 10:38am |  |  | Fair | No | Full voltage found at meter socket, 234v 116v 115v customer asked to get an electrician.
Non-Outage | J.E.26.06.14721 | C001836773 | Royston Montague | St.Catherine | Completed | Load_244939 | Tredegar - 410 | Jul 1, 2026 8:01am | Jul 1, 2026 8:02am | Jul 1, 2026 8:17am | Jul 1, 2026 8:38am | Jul 1, 2026 9:35am | Jul 1, 2026 9:36am | Jul 1, 2026 9:37am | Jul 1, 2026 9:37am |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.06.18249 | C001836772 | Royston Montague | St.Catherine | Completed | Load_258995 | Tredegar - 410 | Jul 1, 2026 8:01am | Jul 1, 2026 8:02am | Jul 1, 2026 8:17am | Jul 1, 2026 10:30am | Jul 1, 2026 10:30am | Jul 1, 2026 10:30am | Jul 1, 2026 10:31am | Jul 1, 2026 10:31am |  |  | Fair | No | Customer confirmed issue resolved.
Non-Outage | J.E.26.06.20848 | C001836774 | Royston Montague | St.Catherine | Completed | Load_239495 | Tredegar - 410 | Jul 1, 2026 8:01am | Jul 1, 2026 8:02am | Jul 1, 2026 8:17am | Jul 1, 2026 2:10pm | Jul 1, 2026 2:26pm | Jul 1, 2026 2:26pm | Jul 1, 2026 2:26pm | Jul 1, 2026 2:26pm |  |  | Fair | No | Location found ok.
Non-Outage | J.E.26.06.31782 | C001836775 | Royston Montague | St.Catherine | Completed | Load_261629 | Tredegar - 410 | Jul 1, 2026 8:01am | Jul 1, 2026 8:02am | Jul 1, 2026 8:17am | Jul 1, 2026 9:38am | Jul 1, 2026 9:40am | Jul 1, 2026 9:41am | Jul 1, 2026 9:42am | Jul 1, 2026 9:42am |  |  | Fair | No | Full voltage found, 236v 115v 116v customer asked to get an electrician to check load side.
Non-Outage | J.E.26.06.35267 | C001836776 | Royston Montague | St.Catherine | Completed | Load_260753 | Tredegar - 410 | Jul 1, 2026 8:01am | Jul 1, 2026 8:03am | Jul 1, 2026 8:17am | Jul 2, 2026 4:02pm | Jul 2, 2026 4:26pm | Jul 2, 2026 4:27pm | Jul 2, 2026 4:27pm | Jul 2, 2026 4:27pm |  |  | Fair | No | Rami system in area, customer complained of fluctuations in voltage. Please assign to the relevant team thanks.
Non-Outage | J.E.26.06.35756 | C001836768 | Wan Carlos Scarlett | St.Catherine | Completed | Load_258925 | Tredegar - 310 | Jul 1, 2026 8:01am | Jul 2, 2026 8:53am | Jul 2, 2026 10:25am | Jul 2, 2026 10:42am | Jul 2, 2026 11:11am | Jul 2, 2026 12:30pm | Jul 2, 2026 12:32pm | Jul 2, 2026 12:32pm |  |  | Fair | No | Found customer 3 wire service at pole with one of the phase corroded use one bolt clamp at open secondary line phase readings 117-116-234
Non-Outage | J.E.26.06.36040 | C001836777 | Royston Montague | St.Catherine | Completed | Load_269823 | Tredegar - 410 | Jul 1, 2026 8:01am | Jul 1, 2026 8:03am | Jul 1, 2026 8:17am | Jul 1, 2026 1:49pm | Jul 1, 2026 2:07pm | Jul 1, 2026 2:08pm | Jul 1, 2026 2:09pm | Jul 1, 2026 2:09pm |  |  | Fair | No | Multiple calls to customer phone go without answer. GPS coordinate on job not working.
Non-Outage | J.E.26.06.38217 | C001836771 | Tajay Bernard | Hanover | Completed | Load_293082 | Orange Bay - 310 | Jul 1, 2026 8:01am | Jul 1, 2026 8:17am | Jul 1, 2026 1:25pm | Jul 1, 2026 1:25pm | Jul 1, 2026 2:26pm | Jul 1, 2026 3:42pm | Jul 1, 2026 3:44pm | Jul 1, 2026 3:44pm |  |  | Fair | No | Isolate 1 25kva transformer to tap it up, and to connect back transformer casing groundingVoltage found 106/104/212Voltage left 109/109/218
Non-Outage | J.E.26.01.08322 | C001836765 | Tajay Bernard | St.James | Completed | Load_1001253 | Bogue - 510 | Jul 1, 2026 8:00am | Jul 1, 2026 8:00am | Jul 1, 2026 3:45pm | Jul 1, 2026 3:45pm | Jul 1, 2026 3:58pm | Jul 1, 2026 3:59pm | Jul 1, 2026 3:59pm | Jul 1, 2026 3:59pm |  |  | Fair | No | Premises found okay customer stated that the issue has been resolved
Non-Outage | J.E.26.06.35544 | C001836766 | Royston Montague | St.Catherine | Completed | Load_259014 | Tredegar - 210 | Jul 1, 2026 8:00am | Jul 1, 2026 8:02am | Jul 1, 2026 8:17am | Jul 1, 2026 10:40am | Jul 1, 2026 12:14pm | Jul 1, 2026 12:15pm | Jul 1, 2026 12:15pm | Jul 1, 2026 12:15pm |  |  | Fair | No | Faulty joints at pothead. Same corrected. Observed meter socket bad condition customer informed to get an electrician to repair same. 217v 107v 108v
Non-Outage | J.E.26.06.38835 | C001836767 | Royston Montague | St.Catherine | Completed | Load_242371 | Tredegar - 210 | Jul 1, 2026 8:00am | Jul 1, 2026 8:02am | Jul 1, 2026 8:17am | Jul 1, 2026 2:29pm | Jul 1, 2026 3:42pm | Jul 1, 2026 3:43pm | Jul 1, 2026 3:43pm | Jul 1, 2026 3:43pm | Fire |  | Fair | No | Location found ok.
Non-Outage | J.E.26.01.04459 | C001836761 | Tajay Bernard | St.James | Completed | Load_244420 | Bogue - 510 | Jul 1, 2026 7:59am | Jul 1, 2026 8:00am | Jul 1, 2026 9:29am | Jul 1, 2026 9:29am | Jul 1, 2026 9:45am | Jul 1, 2026 10:01am | Jul 1, 2026 10:01am | Jul 1, 2026 10:01am |  |  | Fair | No | Clean and remake joints at customer pot head use 3 clamps.Voltage found 113/101/214Voltage left 115/115/230
Non-Outage | J.E.26.01.41557 | C001836763 | Tajay Bernard | St.James | Completed | Load_253569 | Bogue - 510 | Jul 1, 2026 7:59am | Jul 1, 2026 8:00am | Jul 1, 2026 8:45am | Jul 1, 2026 8:46am | Jul 1, 2026 8:58am | Jul 1, 2026 9:03am | Jul 1, 2026 9:04am | Jul 1, 2026 9:04am |  |  | Fair | No | Area check and found okay unable to locate customer on premises multiple phone call to customer number went unanswered
Non-Outage | J.E.26.06.35550 | C001836762 | Tajay Bernard | St.James | Completed | Load_245672 | Bogue - 510 | Jul 1, 2026 7:59am | Jul 1, 2026 8:00am | Jul 1, 2026 3:44pm | Jul 1, 2026 3:44pm | Jul 1, 2026 3:44pm | Jul 1, 2026 3:44pm | Jul 1, 2026 3:45pm | Jul 1, 2026 3:45pm |  |  | Fair | No | Customer stated that the issue has been resolved
Outage | J.E.26.06.39920 | C001836759 | Milton Charlton | KSAS | Completed | Load_293366 | Three Miles - 410 | Jul 1, 2026 7:55am | Jul 1, 2026 7:56am | Jul 1, 2026 11:11am | Jul 1, 2026 11:14am | Jul 1, 2026 11:14am | Jul 1, 2026 11:10am | Jul 1, 2026 11:15am | Jul 1, 2026 11:15am |  |  | Fair | No | Call related to call at #4 Balcombe Avenue.
Outage | J.E.26.06.39959 | C001836760 | Milton Charlton | KSAN | Completed | Load_293333 | Washington Blvd - 710 | Jul 1, 2026 7:55am | Jul 1, 2026 7:56am | Jul 1, 2026 10:58am | Jul 1, 2026 11:15am | Jul 1, 2026 11:15am | Jul 1, 2026 11:15am | Jul 1, 2026 11:15am | Jul 1, 2026 11:15am |  |  | Fair | No | Call related to call at #4 Balcombe Avenue.
Outage | J.E.26.06.39463 | C001836757 | Marlon Authors | Manchester | Completed | Load_264228 | Spur Tree - 210 | Jul 1, 2026 7:53am | Jul 1, 2026 7:55am | Jul 1, 2026 9:23am | Jul 1, 2026 9:23am | Jul 1, 2026 10:26am | Jul 1, 2026 10:49am | Jul 1, 2026 10:49am | Jul 1, 2026 10:49am | BrokenPole |  | Fair | No | Patrol and found clear. Replace one blown 10 amp junction fuse at pole #043771. Restored supply ok
Outage | J.E.26.06.39519 | C001836755 | Wayne Dillion | St.Elizabeth | Completed | Load_257007 | Maggotty - 110 | Jul 1, 2026 7:53am | Jul 1, 2026 9:11am | Jul 1, 2026 2:32pm | Jul 1, 2026 2:32pm | Jul 1, 2026 2:32pm | Jul 1, 2026 2:57pm | Jul 1, 2026 3:01pm | Jul 1, 2026 3:01pm |  |  | Fair | No | Supply check and found no service wire. Connect same using 70ft of #6 triplex service wire, 3 linkets and 3 clamps. Supply leave working okay reading 115v, 115v and cross phase 230volts.
Outage | J.E.26.06.39631 | C001836756 | Marlon Authors | St.Elizabeth | Completed | Load_259959 | Maggotty - 210 | Jul 1, 2026 7:53am | Jul 1, 2026 7:55am | Jul 1, 2026 2:27pm | Jul 1, 2026 2:27pm | Jul 1, 2026 2:27pm | Jul 1, 2026 2:28pm | Jul 1, 2026 2:28pm | Jul 1, 2026 2:28pm |  |  | Fair | No | Customer said supply was restored
Outage | J.E.26.07.00005 | C001836754 | Rusean Allen | KSAS | Completed | Load_251064 | Rockfort - 210 | Jul 1, 2026 7:53am | Jul 1, 2026 7:56am | Jul 1, 2026 11:41am | Jul 1, 2026 11:41am | Jul 1, 2026 1:08pm | Jul 1, 2026 2:36pm | Jul 1, 2026 2:37pm | Jul 1, 2026 2:37pm |  |  | Fair | No | Illegal connections needs to move so we carry out repairs Refer to RPD
Non-Outage | J.E.26.06.39745 | C001836751 | Richman Whyte | null | Completed | null | null | Jul 1, 2026 7:49am | Jul 1, 2026 7:49am | Jul 1, 2026 9:31am | Jul 1, 2026 9:31am | Jul 1, 2026 9:31am | Jul 1, 2026 9:31am | Jul 1, 2026 9:32am | Jul 1, 2026 9:32am | TreeContact |  | Fair | No | St James call however power was restored
Outage | J.E.26.07.00086 | C001836752 | Neville Spencer | Clarendon | Completed | Load_252530 | Parnassus - 210 | Jul 1, 2026 7:49am | Jul 1, 2026 7:50am | Jul 1, 2026 8:21am | Jul 1, 2026 8:21am | Jul 1, 2026 10:01am | Jul 1, 2026 10:01am | Jul 1, 2026 10:02am | Jul 1, 2026 10:02am |  |  | Fair | No | Unable to locate customer.
Non-Outage | J.E.26.07.00088 | C001836750 | Oshane Warren | null | Completed | null | null | Jul 1, 2026 7:48am | Jul 1, 2026 7:49am | Jul 1, 2026 9:58am | Jul 1, 2026 9:58am | Jul 1, 2026 10:02am | Jul 1, 2026 10:02am | Jul 1, 2026 10:03am | Jul 1, 2026 10:03am |  |  | Fair | No | Replace 2 10 amp junction fuse
Outage | J.E.26.06.39928 | C001836747 | Oshane Warren | Westmoreland | Completed | Load_253378 | Paradise - 210 | Jul 1, 2026 7:47am | Jul 1, 2026 7:47am | Jul 1, 2026 9:54am | Jul 1, 2026 9:54am | Jul 1, 2026 9:54am | Jul 1, 2026 9:55am | Jul 1, 2026 9:56am | Jul 1, 2026 9:56am |  |  | Fair | No | Reset 10 kva transformer however transformer leaking oil need to change urgently refer to maintenance
Outage | J.E.26.07.00074 | C001836748 | Oshane Warren | Westmoreland | Completed | Load_253378 | Paradise - 210 | Jul 1, 2026 7:47am | Jul 1, 2026 7:47am | Jul 1, 2026 9:30am | Jul 1, 2026 9:30am | Jul 1, 2026 9:30am | Jul 1, 2026 9:48am | Jul 1, 2026 9:54am | Jul 1, 2026 9:54am |  |  | Fair | No | Reset 10 kva transformer however oil leaking from the transformer need to change 21 customer on it need to change urgently
Outage | J.E.26.07.00027 | C001836745 | Clyde Brown | Clarendon | Completed | Load_237758 | May Pen - 110 | Jul 1, 2026 7:46am | Jul 1, 2026 7:47am | Jul 1, 2026 9:32am | Jul 1, 2026 9:33am | Jul 1, 2026 12:52pm | Jul 1, 2026 12:31pm | Jul 1, 2026 1:01pm | Jul 1, 2026 1:01pm |  |  | Fair | No | Junction switch with 50 amps fuse holder dropped out caused by defective switch same temporary closed and switch need to be replaced at Pedro River
Outage | J.E.26.06.39546 | C001836737 | Dwayne Samuels | Trelawny | Completed | Load_249733 | Martha Brae - 110 | Jul 1, 2026 7:43am | Jul 1, 2026 8:13am | Jul 1, 2026 8:57am | Jul 1, 2026 8:57am | Jul 1, 2026 9:25am | Jul 1, 2026 9:48am | Jul 1, 2026 9:49am | Jul 1, 2026 9:49am |  |  | Fair | No | Check and found customer meter is burnt on load side customer also has a internal issue refer to field service to have meter changed voltage found at meter 110v/113v/223v
Outage | J.E.26.07.00048 | C001836739 | Cliton Henry | St.Mary | Completed | Load_261992 | Blackstonedge - 110 | Jul 1, 2026 7:43am | Jul 1, 2026 7:43am | Jul 1, 2026 11:53am | Jul 1, 2026 12:10pm | Jul 1, 2026 12:10pm | Jul 1, 2026 2:12pm | Jul 1, 2026 2:21pm | Jul 1, 2026 2:21pm |  |  | Fair | No | A blown 5 amp fuse found for a 25 kva transformer due to bamboo tree fell and the secondary conductors. The bamboo tree was removed and supply restored using 1-5 amp fuse. Voltages left 118-118/236 volts.
Outage | J.E.26.07.00062 | C001836738 | Andre Williams | Trelawny | Completed | Load_555893 | Martha Brae - 210 | Jul 1, 2026 7:43am | Jul 1, 2026 7:45am | Jul 1, 2026 8:20am | Jul 1, 2026 9:12am | Jul 1, 2026 9:12am | Jul 1, 2026 9:13am | Jul 1, 2026 9:13am | Jul 1, 2026 9:13am |  |  | Fair | No | Premises ok and with supply call made yesterday due to fire in nearby building
Outage | J.E.26.06.39945 | C001836735 | Cliton Henry | St.Mary | Completed | Load_269808 | Oracabessa - 110 | Jul 1, 2026 7:42am | Jul 1, 2026 7:43am | Jul 1, 2026 8:30am | Jul 1, 2026 8:30am | Jul 1, 2026 9:18am | Jul 1, 2026 11:36am | Jul 1, 2026 11:41am | Jul 1, 2026 11:41am | Fire |  | Fair | No | A blown 30 amp junction fuse found at Galina entrance to Light House Rd. Pole #005037 due to broken secondary conductors. Corrective work done to spliced and retention secondary conductors using approximately one hundred and eighty (180) feet #2 AA conductor, three (3)-#2 splicing sleeve, three (3) #2 preform and seven (7 ) one bolt clamps
Non-Outage | J.E.26.06.39147 | C001836733 | Christopher Edwards | null | Completed | null | null | Jul 1, 2026 7:41am | Jul 1, 2026 7:41am | Jul 1, 2026 8:52am | Jul 1, 2026 8:52am | Jul 1, 2026 9:00am | Jul 1, 2026 9:00am | Jul 1, 2026 9:03am | Jul 1, 2026 9:03am |  | Y | Fair | Yes | Consumer found ok
Non-Outage | J.E.26.06.38362 | C001836732 | Richard Grant | null | Completed | null | null | Jul 1, 2026 7:38am | Jul 1, 2026 3:57pm | Jul 1, 2026 4:04pm | Jul 1, 2026 4:04pm | Jul 1, 2026 5:12pm | Jul 1, 2026 5:32pm | Jul 1, 2026 5:32pm | Jul 1, 2026 5:32pm | BrokenWire |  | Fair | No | Premises found okay
Non-Outage | J.E.26.06.39308 | C001836731 | Edward Royal | KSAN | Completed | Load_238618 | Hope - 510 | Jul 1, 2026 7:35am | Jul 1, 2026 7:36am | Jul 1, 2026 11:28am | Jul 1, 2026 11:28am | Jul 1, 2026 11:28am | Jul 1, 2026 1:01pm | Jul 1, 2026 1:02pm | Jul 1, 2026 1:02pm |  |  | Fair | No | Debush tree from secondary line and transformer replaced one bolt clamps to transformer drop lead voltage reading before 115v 94v 213v after 121v 121v 242 pole# 0110487
Non-Outage | J.E.25.12.29776 | C001836730 | Swon Miller | St.James | Completed | Load_1002042 | Queens Drive - 710 | Jul 1, 2026 7:34am | Jul 1, 2026 7:35am | Jul 1, 2026 7:44am | Jul 1, 2026 8:57am | Jul 1, 2026 9:32am | Jul 14, 2026 9:52am | Jul 1, 2026 9:54am | Jul 1, 2026 9:54am |  |  | Fair | No | Check and found area okay customer states that power supply was restored voltage found 115 /115/230 voltage left 115/115/230
Non-Outage | J.E.26.02.19692 | C001836728 | Swon Miller | St.James | Completed | Load_251205 | Queens Drive - 710 | Jul 1, 2026 7:34am | Jul 1, 2026 7:34am | Jul 2, 2026 7:40am | Jul 2, 2026 9:25am | Jul 2, 2026 10:50am | Jul 28, 2026 11:15am | Jul 2, 2026 11:21am | Jul 2, 2026 11:21am |  |  | Fair | No | Check and found okay voltage found 114 /113/227 voltage left 114/113/227
Non-Outage | J.E.26.02.34730 | C001836726 | Swon Miller | St.James | Completed | Load_251601 | Queens Drive - 710 | Jul 1, 2026 7:34am | Jul 1, 2026 7:34am | Jul 1, 2026 7:46am | Jul 1, 2026 9:57am | Jul 1, 2026 11:29am | Jul 21, 2026 12:06am | Jul 1, 2026 12:10pm | Jul 1, 2026 12:10pm |  |  | Fair | No | Check and found okay customer states that the issue was resolved voltage found 116/116/232 voltage left 116/116/232
Non-Outage | J.E.26.06.39731 | C001836729 | Fredrick Hamilton | KSAN | Completed | Load_255432 | Constant Spring - 210 | Jul 1, 2026 7:34am | Jul 1, 2026 8:03am | Jul 1, 2026 8:18am | Jul 1, 2026 10:45am | Jul 1, 2026 10:53am | Jul 1, 2026 11:11am | Jul 1, 2026 11:11am | Jul 1, 2026 11:11am |  |  | Fair | No | Corrosion detected at pothead same was corrected 3 penunion usedPower fully restored
Non-Outage | J.E.26.07.00003 | C001836727 | Fredrick Hamilton | KSAN | Completed | Load_256846 | Constant Spring - 210 | Jul 1, 2026 7:34am | Jul 1, 2026 8:04am | Jul 1, 2026 8:18am | Jul 1, 2026 11:12am | Jul 1, 2026 11:29am | Jul 1, 2026 11:55am | Jul 1, 2026 11:55am | Jul 1, 2026 11:55am |  |  | Fair | No | 244.6v/121.8v/122.2v obtained Corrosion detected at pothead same was corrected 3 clamps used
Non-Outage | J.E.26.06.39716 | C001836725 | Kemark Slue | null | Completed | null | null | Jul 1, 2026 7:32am | Jul 1, 2026 7:33am | Jul 1, 2026 11:20am | Jul 1, 2026 1:55pm | Jul 1, 2026 1:55pm | Jul 1, 2026 12:00pm | Jul 1, 2026 1:56pm | Jul 1, 2026 1:56pm |  |  | Fair | No | Premises was checked and found okay.
Outage | J.E.26.07.00077 | C001836723 | Omar Harris | St.Ann | Completed | Load_267559 | Roaring River - 410 | Jul 1, 2026 7:31am | Jul 1, 2026 7:31am | Jul 1, 2026 8:15am | Jul 1, 2026 8:15am | Jul 1, 2026 8:15am | Jul 1, 2026 8:15am | Jul 1, 2026 8:16am | Jul 1, 2026 8:16am |  |  | Fair | No | Replace 1 25A junction pole number 604623 1 20A junction pole number 613458
Outage | J.E.26.07.00082 | C001836724 | Omar Harris | St.Ann | Completed | Load_253335 | Roaring River - 410 | Jul 1, 2026 7:31am | Jul 1, 2026 7:31am | Jul 1, 2026 7:36am | Jul 1, 2026 7:38am | Jul 1, 2026 8:01am | Jul 1, 2026 8:14am | Jul 1, 2026 8:15am | Jul 1, 2026 8:15am |  |  | Fair | No | Replace 1 25A junction pole number 604623 1 20A junction pole number 613458
Outage | J.E.26.06.39148 | C001836722 | Donald Cunningham | St.Catherine | Completed | Load_253823 | Rhodens Pen - 410 | Jul 1, 2026 7:30am | Jul 1, 2026 7:32am | Jul 1, 2026 8:09am | Jul 1, 2026 8:09am | Jul 1, 2026 9:46am | Jul 1, 2026 9:48am | Jul 1, 2026 9:49am | Jul 1, 2026 9:49am |  |  | Fair | No | Need more directions customer not reachable
Outage | J.E.26.07.00069 | C001836721 | Edward Royal | KSAN | Completed | Load_264476 | Hope - 410 | Jul 1, 2026 7:30am | Jul 1, 2026 7:31am | Jul 1, 2026 1:04pm | Jul 1, 2026 1:04pm | Jul 1, 2026 1:38pm | Jul 1, 2026 2:06pm | Jul 1, 2026 2:09pm | Jul 1, 2026 2:09pm |  |  | Fair | No | Customer have internal problems advice customer to get electrician to fix the problem voltage reading 117.7 v117v.5 238v
Non-Outage | J.E.26.06.38832 | C001836719 | Nickolas Rodriques | null | Completed | null | null | Jul 1, 2026 7:29am | Jul 1, 2026 7:30am | Jul 1, 2026 8:57am | Jul 1, 2026 9:01am | Jul 1, 2026 9:53am | Jul 1, 2026 10:00am | Jul 1, 2026 10:06am | Jul 1, 2026 10:06am |  |  | Fair | No | Customer confirmed that the power was restored.
Outage | J.E.26.07.00090 | C001836718 | Omar King | St.Ann | Completed | Load_267440 | Ocho Rios - 510 | Jul 1, 2026 7:29am | Jul 1, 2026 8:04am | Jul 1, 2026 9:40am | Jul 1, 2026 9:40am | Jul 1, 2026 9:40am | Jul 1, 2026 9:42am | Jul 1, 2026 9:43am | Jul 1, 2026 9:43am |  |  | Fair | No | Problem as been resolved
Non-Outage | J.E.26.07.00064 | C001836715 | Hopeton Henry | null | Completed | null | null | Jul 1, 2026 7:28am | Jul 1, 2026 7:28am | Jul 1, 2026 8:19am | Jul 1, 2026 9:15am | Jul 1, 2026 10:01am | Jul 1, 2026 10:17am | Jul 1, 2026 10:18am | Jul 1, 2026 10:18am | BrokenWire |  | Fair | No | Related to blow 30 amp junction at qutey shop
Outage | J.E.26.06.39653 | C001836717 | Donald Cunningham | St.Catherine | Completed | Load_255316 | Rhodens Pen - 210 | Jul 1, 2026 7:28am | Jul 1, 2026 7:36am | Jul 1, 2026 9:49am | Jul 1, 2026 9:49am | Jul 1, 2026 10:30am | Jul 1, 2026 10:30am | Jul 1, 2026 10:32am | Jul 1, 2026 10:32am |  |  | Fair | No | Supply restored to area premises closed
Non-Outage | J.E.26.07.00092 | C001836711 | Barnett Brown | null | Completed | null | null | Jul 1, 2026 7:27am | Jul 1, 2026 7:27am | null | Jul 1, 2026 11:33am | Jul 1, 2026 11:33am | Jul 1, 2026 12:43pm | Jul 1, 2026 12:47pm | Jul 1, 2026 12:47pm |  |  | Fair | No | Clear bamboo from line, replace blown 20 amp junction fuse.
Outage | J.E.26.06.39487 | C001836713 | Barnett Brown | Manchester | Completed | Load_252477 | Spur Tree - 310 | Jul 1, 2026 7:27am | Jul 1, 2026 7:27am | null | Jul 1, 2026 8:29am | Jul 1, 2026 9:51am | Jul 1, 2026 9:51am | Jul 1, 2026 11:32am | Jul 1, 2026 11:32am |  |  | Fair | No
Outage | J.E.26.06.39786 | C001836708 | Wayne Dillion | St.Elizabeth | Completed | Load_251476 | Maggotty - 110 | Jul 1, 2026 7:24am | Jul 1, 2026 7:25am | Jul 1, 2026 10:20am | Jul 1, 2026 10:20am | Jul 1, 2026 10:20am | Jul 1, 2026 11:56pm | Jul 1, 2026 12:08pm | Jul 1, 2026 12:08pm |  |  | Fair | No | Patrol and found service wire neutral and one of the phase was banged together reading 78v and 145volts. Repair same using 4 linkets. Supply leave working okay reading 117v, 120v and cross phase 237volts. Further checks reveals that customer meter socket wires is burnt up. Disconnect at pot head and customer was advised to have same repaired.
Outage | J.E.26.06.39797 | C001836709 | Wayne Dillion | St.Elizabeth | Completed | Load_253932 | Maggotty - 110 | Jul 1, 2026 7:24am | Jul 1, 2026 7:25am | Jul 1, 2026 7:51am | Jul 1, 2026 7:51am | Jul 1, 2026 7:51am | Jul 1, 2026 7:52am | Jul 1, 2026 7:52am | Jul 1, 2026 7:52am |  |  | Fair | No | Customer said problem has resolved from last night and supply is working ok
Outage | J.E.26.06.39803 | C001836707 | Wayne Dillion | Manchester | Completed | Load_240150 | Spur Tree - 210 | Jul 1, 2026 7:24am | Jul 1, 2026 7:25am | Jul 1, 2026 12:10pm | Jul 1, 2026 12:10pm | Jul 1, 2026 12:10pm | Jul 1, 2026 12:12pm | Jul 1, 2026 12:12pm | Jul 1, 2026 12:12pm |  |  | Fair | No | Customer said supply was restored.
Outage | J.E.26.07.00034 | C001836710 | Kemark Slue | St.Catherine | Completed | Load_245363 | New Michelton - 310 | Jul 1, 2026 7:24am | Jul 1, 2026 7:25am | Jul 1, 2026 8:42am | Jul 1, 2026 8:42am | Jul 1, 2026 9:21am | Jul 1, 2026 8:48am | Jul 1, 2026 1:43pm | Jul 1, 2026 1:43pm | Fire | Y | Fair | No | Upon arrival at the location the crew discovered that road phase 40 amps junction from two phases at pole # 052506 was blown, further patrol revealed that creepers was the caused, cut away creepers, refuse link and re-energized line section.
Non-Outage | J.E.26.06.32348 | C001836706 | Shamour Haughton | null | Completed | null | null | Jul 1, 2026 7:23am | Jul 1, 2026 7:39am | Jul 1, 2026 9:48am | Jul 1, 2026 9:48am | Jul 1, 2026 9:55am | Jul 1, 2026 9:58am | Jul 1, 2026 10:00am | Jul 1, 2026 10:00am | Fire |  | Fair | No | Customer states that power was restored
Outage | J.E.26.06.38826 | C001836704 | Ryan Richards | Manchester | Completed | Load_247696 | Porus - 310 | Jul 1, 2026 7:20am | Jul 1, 2026 7:21am | Jul 1, 2026 8:06am | Jul 1, 2026 8:07am | Jul 1, 2026 9:40am | Jul 1, 2026 10:39am | Jul 1, 2026 10:39am | Jul 1, 2026 10:39am |  |  | Fair | No | Blown 2 amp fuse found for 25 kva transformer line patrol nothing found blown fuse was replaced site now with supply
Outage | J.E.26.06.39547 | C001836703 | Christopher Edwards | KSAN | Completed | Load_238692 | Constant Spring - 410 | Jul 1, 2026 7:20am | Jul 1, 2026 7:22am | Jul 1, 2026 9:33am | Jul 1, 2026 9:33am | Jul 1, 2026 9:34am | Jul 1, 2026 9:40am | Jul 1, 2026 9:40am | Jul 1, 2026 9:40am |  |  | Fair | Yes
Outage | J.E.26.06.39568 | C001836705 | Ryan Richards | Manchester | Completed | Load_245958 | Kendal - 310 | Jul 1, 2026 7:20am | Jul 1, 2026 7:21am | Jul 1, 2026 10:39am | Jul 1, 2026 10:39am | Jul 1, 2026 11:31am | Jul 1, 2026 12:19pm | Jul 1, 2026 12:22pm | Jul 1, 2026 12:22pm |  |  | Fair | No | Blown 2 amp fuse found for 25 kva transformer line patrol nothing found fuse replaced and rejected isolated transformer from line and refused transformer and fuse rejected transformer suspected to be burn apparently 10 customers affected
Outage | J.E.26.07.00061 | C001836702 | Christopher Edwards | KSAN | Completed | Load_267645 | Constant Spring - 410 | Jul 1, 2026 7:20am | Jul 1, 2026 7:22am | Jul 1, 2026 8:14am | Jul 1, 2026 8:14am | Jul 1, 2026 8:15am | Jul 1, 2026 8:20am | Jul 1, 2026 8:21am | Jul 1, 2026 8:21am | BrokenWire |  | Fair | Yes | Need 100 feet of nob 6 wire
Outage | J.E.26.06.38498 | C001836701 | Richard Samuda | Manchester | Completed | Load_1002467 | Kendal - 210 | Jul 1, 2026 7:18am | Jul 1, 2026 7:18am | Jul 1, 2026 9:14am | Jul 1, 2026 9:14am | Jul 1, 2026 9:40am | Jul 1, 2026 9:41am | Jul 1, 2026 9:45am | Jul 1, 2026 9:45am |  |  | Fair | No | Customer has a damaged meter that was damaged by a man of unsourced mine meter needs to be replaced voltage 116
Outage | J.E.26.06.38989 | C001836700 | Richard Samuda | Manchester | Completed | Load_238222 | Kendal - 210 | Jul 1, 2026 7:18am | Jul 1, 2026 7:18am | Jul 1, 2026 7:29am | Jul 1, 2026 8:07am | Jul 1, 2026 8:39am | Jul 1, 2026 8:39am | Jul 1, 2026 8:51am | Jul 1, 2026 8:51am | LeaningPole |  | Fair | No | 30ft class 6 secondary pole leaning on customer premises foot rotten causing line hanging over customer premises ref call
Non-Outage | J.E.26.06.39799 | C001836699 | Kemark Slue | St.Catherine | Completed | Load_555948 | New Michelton - 210 | Jul 1, 2026 7:17am | Jul 1, 2026 9:27am | Jul 1, 2026 10:13am | Jul 1, 2026 1:44pm | Jul 1, 2026 1:44pm | Jul 1, 2026 9:41am | Jul 1, 2026 1:47pm | Jul 1, 2026 1:47pm |  |  | Fair | No | Premises was checked and for okay leaving a off load voltage reading of 414,414,414,237,237,237V
Non-Outage | J.E.26.06.39793 | C001836698 | Nickolas Rodriques | St.Catherine | Completed | Load_1001559 | Tredegar - 310 | Jul 1, 2026 7:15am | Jul 1, 2026 7:16am | Jul 1, 2026 10:07am | Jul 1, 2026 10:07am | Jul 1, 2026 11:04am | Jul 1, 2026 11:21am | Jul 1, 2026 11:23am | Jul 1, 2026 11:23am |  |  | Fair | No | Power restored. The pump manager confirmed that the issue was already resolved.
Outage | J.E.26.06.39780 | C001836696 | Nickolas Rodriques | St.Catherine | Completed | Load_259511 | Twickenham - 210 | Jul 1, 2026 7:13am | Jul 1, 2026 7:19am | Jul 1, 2026 11:28am | Jul 1, 2026 11:28am | Jul 1, 2026 11:59am | Jul 1, 2026 12:15pm | Jul 1, 2026 12:22pm | Jul 1, 2026 12:22pm |  |  | Fair | No | Area has electricity. The customer was contacted and confirmed that the power was restored.
Outage | J.E.26.06.39849 | C001836697 | Wan Carlos Scarlett | St.Catherine | Completed | Load_262365 | Twickenham - 210 | Jul 1, 2026 7:13am | Jul 1, 2026 7:17am | Jul 1, 2026 7:38am | Jul 1, 2026 7:38am | Jul 1, 2026 8:37am | Jul 1, 2026 9:48am | Jul 1, 2026 9:48am | Jul 1, 2026 9:48am |  |  | Fair | No | Found 25KVA transformer drop lead wire to secondary line phase burn off use 4 one bolt clamps at pole readings 116-117-234
Non-Outage | J.E.26.02.39615 | C001836694 | Tajay Bernard | St.James | Completed | Load_238585 | Bogue - 510 | Jul 1, 2026 7:08am | Jul 1, 2026 7:08am | Jul 1, 2026 9:17am | Jul 1, 2026 9:17am | Jul 1, 2026 9:17am | Jul 1, 2026 9:18am | Jul 1, 2026 9:18am | Jul 1, 2026 9:18am |  |  | Fair | No | Customer stated that the issue has been resolved
Non-Outage | J.E.26.04.02843 | C001836693 | Tajay Bernard | St.James | Completed | Load_243895 | Bogue - 510 | Jul 1, 2026 7:08am | Jul 1, 2026 7:08am | Jul 1, 2026 9:18am | Jul 1, 2026 9:19am | Jul 1, 2026 9:19am | Jul 1, 2026 9:19am | Jul 1, 2026 9:20am | Jul 1, 2026 9:20am |  |  | Fair | No | Customer stated the the issue has been resolved
Non-Outage | J.E.26.02.18518 | C001836692 | Tajay Bernard | St.James | Completed | Load_260871 | Orange Bay - 310 | Jul 1, 2026 7:07am | Jul 1, 2026 7:08am | Jul 1, 2026 9:07am | Jul 1, 2026 9:07am | Jul 1, 2026 9:12am | Jul 1, 2026 9:16am | Jul 1, 2026 9:16am | Jul 1, 2026 9:16am |  |  | Fair | No | Premises check and found okay customer has internal problems
Outage | J.E.26.07.00075 | C001836691 | Lancelot Brown | Hanover | Completed | Load_265525 | Orange Bay - 310 | Jul 1, 2026 7:02am | Jul 1, 2026 7:58am | Jul 1, 2026 8:27am | Jul 1, 2026 8:27am | Jul 1, 2026 10:03am | Jul 1, 2026 10:08am | Jul 1, 2026 10:08am | Jul 1, 2026 10:08am |  |  | Fair | No | Check and found ok customer said her breaker was trip and some one reset it the area is having low voltage caused by distance of feed a transformer was diffective and removed and did not replace customer said from the transformer removed the area having low voltage transformer need to replace also two span primary was cut down in hurricane and did not replace eather please pass on to maintenance department in Hanover mr Richards need ergent attention
Outage | J.E.26.07.00053 | C001836680 | Horace Malcolm | St.James | Completed | Load_244365 | Bogue - 310 | Jul 1, 2026 6:08am | Jul 1, 2026 7:21am | Jul 1, 2026 7:51am | Jul 1, 2026 7:51am | Jul 1, 2026 8:10am | Jul 1, 2026 9:14am | Jul 1, 2026 9:14am | Jul 1, 2026 9:14am |  |  | Fair | No | Refused two junction fuse one 30amp and one 20amp fuse due to truck entangle wire cable lines
Outage | J.E.26.07.00010 | C001836661 | Christopher Edwards | KSAN | Completed | Load_270237 | Washington Blvd - 710 | Jul 1, 2026 3:36am | Jul 1, 2026 3:37am | Jul 1, 2026 5:02am | Jul 1, 2026 5:02am | Jul 1, 2026 5:02am | Jul 1, 2026 6:57am | Jul 1, 2026 6:57am | Jul 1, 2026 6:57am |  |  | Fair | No | Splice and retention broken open secondary Using (50ft #2 AA conductor (1) #2 preform (2) one bolt clamps Refuse blown 100 kva transformer using (1) 10 amps
Outage | J.E.26.07.00023 | C001836662 | Christopher Edwards | KSAN | Completed | Load_250296 | Washington Blvd - 310 | Jul 1, 2026 3:36am | Jul 1, 2026 3:37am | Jul 1, 2026 4:08am | Jul 1, 2026 4:10am | Jul 1, 2026 4:26am | Jul 1, 2026 5:01am | Jul 1, 2026 5:02am | Jul 1, 2026 5:02am | Fire |  | Fair | No | Isolate 50 kva transformer To remake burnt off open secondary phase jumper joint Using (2) one bolt clamps
Outage | J.E.26.07.00031 | C001836660 | Swon Miller | St.James | Completed | Load_259820 | Rose Hall - 210 | Jul 1, 2026 3:34am | Jul 1, 2026 7:21am | Jul 1, 2026 7:48am | Jul 1, 2026 12:11pm | Jul 1, 2026 12:53pm | Jul 1, 2026 1:38pm | Jul 1, 2026 1:45pm | Jul 1, 2026 1:45pm |  |  | Fair | No | Found customer single phasing due to service wire burnt off at pole due to contamination voltage found 116 clean and remake joint use 1pg voltage left 116/115/232
Outage | J.E.26.06.39316 | C001836659 | Moses Elliston | St.Catherine | Completed | Load_1001596 | Tredegar - 310 | Jul 1, 2026 3:29am | Jul 1, 2026 3:29am | Jul 1, 2026 10:11am | Jul 1, 2026 3:16pm | Jul 1, 2026 3:16pm | Jul 1, 2026 3:16pm | Jul 1, 2026 3:17pm | Jul 1, 2026 3:17pm |  |  | Fair | No | Credit added to account.(Duplication)
Outage | J.E.26.06.39250 | C001836657 | Wan Carlos Scarlett | St.Catherine | Completed | Load_579394 | Twickenham - 410 | Jul 1, 2026 1:20am | Jul 1, 2026 4:16pm | Jul 1, 2026 4:38pm | Jul 1, 2026 4:38pm | Jul 1, 2026 5:35pm | Jul 1, 2026 5:53pm | Jul 1, 2026 5:53pm | Jul 1, 2026 5:53pm |  |  | Fair | No | Customer was reconnected from escalation department power supply has been restored
Outage | J.E.26.06.39656 | C001836656 | Kemark Slue | St.Catherine | Completed | Load_256325 | New Michelton - 210 | Jul 1, 2026 1:20am | Jul 1, 2026 7:26am | Jul 1, 2026 11:20am | Jul 1, 2026 1:53pm | Jul 1, 2026 1:53pm | Jul 1, 2026 11:33am | Jul 1, 2026 1:55pm | Jul 1, 2026 1:55pm |  |  | Fair | No | Premises was checked and found okay.
Outage | J.E.26.06.39334 | C001836654 | Delano Gayle | St.Catherine | Completed | Load_1005114 | Twickenham - 410 | Jul 1, 2026 1:19am | Jul 1, 2026 1:20am | Jul 1, 2026 1:36am | Jul 1, 2026 1:36am | Jul 1, 2026 2:45am | Jul 1, 2026 2:47am | Jul 1, 2026 2:48am | Jul 1, 2026 2:48am |  |  | Fair | No | Premises found okay power restored
Outage | J.E.26.06.39316 | C001836652 | Moses Elliston | St.Catherine | Completed | Load_1001596 | Tredegar - 310 | Jul 1, 2026 1:11am | Jul 1, 2026 1:11am | Jul 1, 2026 2:48pm | Jul 1, 2026 2:48pm | Jul 1, 2026 2:49pm | Jul 1, 2026 2:49pm | Jul 1, 2026 2:49pm | Jul 1, 2026 2:49pm |  |  | Fair | No | Credit added to prepaid account
Outage | J.E.26.06.39852 | C001836650 | Delano Gayle | St.Catherine | Completed | Load_251366 | Tredegar - 310 | Jul 1, 2026 1:06am | Jul 1, 2026 1:06am | Jul 1, 2026 1:11am | Jul 1, 2026 1:11am | Jul 1, 2026 1:12am | Jul 1, 2026 1:13am | Jul 1, 2026 1:13am | Jul 1, 2026 1:13am |  |  | Fair | No | Premises found okay power was restored
Outage | J.E.26.06.39857 | C001836649 | Delano Gayle | St.Catherine | Completed | Load_249216 | Rhodens Pen - 310 | Jul 1, 2026 1:05am | Jul 1, 2026 1:06am | Jul 1, 2026 1:15am | Jul 1, 2026 1:16am | Jul 1, 2026 1:16am | Jul 1, 2026 1:16am | Jul 1, 2026 1:17am | Jul 1, 2026 1:17am |  |  | Fair | No | Premises found okay by phone customer states power restored to her premises
Outage | J.E.26.06.39946 | C001836645 | Daniel Francis | St.Ann | Completed | Load_413021 | Cardiff Hall - 310 | Jul 1, 2026 12:48am | Jul 1, 2026 8:05am | Jul 1, 2026 8:59am | Jul 1, 2026 8:59am | Jul 1, 2026 9:19am | Jul 1, 2026 10:30am | Jul 1, 2026 10:30am | Jul 1, 2026 10:30am |  |  | Fair | No | Found secondary neutral broken splice and retention also retention 3 span of3 wire secondary
Outage | J.E.26.06.39955 | C001836646 | Raymond Lewis | St.Ann | Completed | Load_413080 | Roaring River - 410 | Jul 1, 2026 12:48am | Jul 1, 2026 12:49am | Jul 1, 2026 2:19am | Jul 1, 2026 2:20am | Jul 1, 2026 4:00am | Jul 1, 2026 2:30am | Jul 1, 2026 4:03am | Jul 1, 2026 4:03am |  |  | Fair | No | Phone not answering
Outage | J.E.26.06.39790 | C001836644 | Delano Gayle | St.Catherine | Completed | Load_556598 | Tredegar - 310 | Jul 1, 2026 12:28am | Jul 1, 2026 12:29am | Jul 1, 2026 12:58am | Jul 1, 2026 1:04am | Jul 1, 2026 1:04am | Jul 1, 2026 1:05am | Jul 1, 2026 1:05am | Jul 1, 2026 1:05am |  |  | Fair | No | Premises found okay via phone call
Outage | J.E.26.06.39316 | C001836642 | Delano Gayle | St.Catherine | Completed | Load_1001596 | Tredegar - 310 | Jul 1, 2026 12:18am | Jul 1, 2026 12:19am | Jul 1, 2026 1:09am | Jul 1, 2026 1:09am | Jul 1, 2026 1:09am | Jul 1, 2026 1:10am | Jul 1, 2026 1:10am | Jul 1, 2026 1:10am |  |  | Fair | No | Customer states they are unable to top up with credit send to Moses
Outage | J.E.26.06.39867 | C001836639 | Delano Gayle | St.Catherine | Completed | Load_556601 | Tredegar - 310 | Jul 1, 2026 12:16am | Jul 1, 2026 12:19am | Jul 1, 2026 1:22am | Jul 1, 2026 1:23am | Jul 1, 2026 1:24am | Jul 1, 2026 1:25am | Jul 1, 2026 1:25am | Jul 1, 2026 1:25am |  |  | Fair | No | Premises found okay power restored